## Contents
SEPD Network Scenario Headroom Report 2024 Summary
Our Network Scenario Headroom Report (NSHR) is published to enable customers, developers, generators, local authorities and other interested third parties to view the possible headroom capacity at our Primary Substations and Bulk Supply Points (BSP) up to 2050. SSEN have used the latest Distribution Future Energy Scenarios (DFES) data to inform four scenarios of demand and generation forecasts. SSEN best view of the future demand and generation needs on our network is aligned to the Customer Transformation scenario. Although the NSHR provides a view of the future in terms of our potential available capacity and constraints on our network, we would encourage any party using this information in their decision-making process to engage with us ahead of making an application to connect or offer flexible services. Please note version 1.0 of the 2024 Network Scenario Headroom Report is subject to change before the final version is released. Updated DFES projections have yet to be finalised so the headroom calculations in version 1.0 have been based on last year's DFES. Headroom estimations, including new additions to the DFES, will be updated in the final release on the 1st of May.
Network Headroom Report Contents
Tab | Description
Key Information | This tab provides some additional detail to assist users with how to read the data presented within this report.
Primary Headroom Dem | This tab provides the demand headroom capacity at each of our Primary substations, grid references, connectivity upto the Grid Supply Point and upstream constraints.
Primary Headroom Gen | This tab provides the generation headroom capacity at each of our Primary substations, grid references, connectivity upto the Grid Supply Point and upstream constraints.
BSP Headroom Dem | This tab provides the demand headroom capacity at each of our BSP, grid references, connectivity upto the Grid Supply Point and upstream constraints.
BSP Headroom Gen | This tab provides the demand headroom capacity at each of our BSP, grid references, connectivity upto the Grid Supply Point and upstream constraints.
LEP Reference | This tab provides information on the LEPs, local authorities and the connected GSPs, BSPs and Primaries that support those areas
ESID | To indicate potential transmission constraints by 'Earliest in Service Date' per Grid Supply Point (GSP)
March 2024 Version 1.0

## Key Information
SEPD Network Scenario Headroom Report 2024 Key Information
Our Network Scenario Headroom Report (NSHR) has been developed to be used in conjunction with our other documents that combine to make the full Network Development Plan; the other documents to reference are the Network Development Plan Methodology & Assumptions and Network Development Report. The capacity that demand and generation growth is measured against is the firm capacity of the primary substation or BSP as per our Load Indices submission to Ofgem and as indicated by our Long Term Development Statement. Firm capacity means the available capacity on the network with a single feed on outage; for instance a twin transformer sites firm capacity would be the lowest capacity available on a single transformer. For single transformer sites, the firm capacity is based on the backfeed supply available to restore supplies; this may be limited by the backfeed circuit capacity rather than the transformer providing the backfeed. Where the capacity is shown as 0 MVA, this signifies that there may be no alternative supplies to restore power to these sites. When reviewing the headroom reports for demand and generation the following applies: GREEN and POSTIVE VALUES = Capacity is forecast to be available RED and NEGATIVE VALUES = There are constraints forecast It must be noted that forecasts in RED do not mean that connections cannot be made; there are opportunities through flexible services that can enable connections without triggering network reinforcement. We would encourage any developer, generator or customer to contact us to discuss their connection and available opportuinites to connect. The data shown within this NSHR is used by us to identify long term investment opportunities where there are constraints highlighted. As the forecast is scenario based, these constraints are subject to change and will be reviewed and published annually by SEPD.
March 2024
Version 1.0

## Primary Headroom Dem
Grid Supply Point | Bulk Supply Point | Primary Substation | Scenario | Grid Reference | Upstream Constraint (YES / NO) | Demand Headroom Winter (MVA) | [12 empty] | Demand Headroom Summer (MVA) | [12 empty] | Demand Headroom Spring/Autumn (MVA)
[6 empty] | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2035 | 2040 | 2045 | 2050 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2035 | 2040 | 2045 | 2050 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2035 | 2040 | 2045 | 2050
MANNINGTON GSP | BOURNEMOUTH | ALDERNEY | MINIMUM HEADROOM | SZ 04270 95141 | YES | 5.0237 | 4.7944 | 4.5139 | 4.2091 | 3.8677 | 3.4906 | 3.0753 | 2.5467 | 1.8917 | -0.40619 | -4.2616 | -5.7692 | -6.5395 | 10.9402 | 10.8155 | 10.66 | 10.5044 | 10.3316 | 10.1412 | 9.9318 | 9.6577 | 9.1659 | 7.5175 | 4.7625 | 3.6943 | 1.6453 | 8.4663 | 8.3178 | 8.1312 | 7.9391 | 7.7245 | 7.4742 | 7.1592 | 6.7479 | 6.0392 | 3.6733 | -0.066872 | -2.3825 | -3.6047
|  | ALDERNEY | CT |  |  | 5.0237 | 4.7944 | 4.5139 | 4.2091 | 3.8677 | 3.4906 | 3.0753 | 2.5467 | 1.8917 | -0.40619 | -4.2616 | -5.7692 | -6.5395 | 10.9402 | 10.8155 | 10.66 | 10.5044 | 10.3316 | 10.1412 | 9.9318 | 9.6577 | 9.1659 | 7.5175 | 4.7625 | 3.6943 | 1.6453 | 8.4663 | 8.3178 | 8.1312 | 7.9391 | 7.7245 | 7.4742 | 7.1592 | 6.7479 | 6.0392 | 3.6733 | -0.066872 | -2.3825 | -3.6047
|  | ALDERNEY | LW |  |  | 5.0237 | 4.7944 | 4.5139 | 4.2091 | 3.8677 | 3.4906 | 3.0753 | 2.5467 | 1.8917 | -0.40619 | -4.2616 | -5.7692 | -6.5395 | 10.9402 | 10.8155 | 10.66 | 10.5044 | 10.3316 | 10.1412 | 9.9318 | 9.6577 | 9.1659 | 7.5175 | 4.7625 | 3.6943 | 1.6453 | 8.4663 | 8.3178 | 8.1312 | 7.9391 | 7.7245 | 7.4742 | 7.1592 | 6.7479 | 6.0392 | 3.6733 | -0.066872 | -2.3825 | -3.6047
|  | ALDERNEY | ST |  |  | 5.0237 | 4.7944 | 4.5139 | 4.2091 | 3.8677 | 3.4906 | 3.0753 | 2.5467 | 1.8917 | -0.40619 | -4.2616 | -5.7692 | -6.5395 | 10.9402 | 10.8155 | 10.66 | 10.5044 | 10.3316 | 10.1412 | 9.9318 | 9.6577 | 9.1659 | 7.5175 | 4.7625 | 3.6943 | 1.6453 | 8.4663 | 8.3178 | 8.1312 | 7.9391 | 7.7245 | 7.4742 | 7.1592 | 6.7479 | 6.0392 | 3.6733 | -0.066872 | -2.3825 | -3.6047
|  | ALDERNEY | FS |  |  | 5.0237 | 4.7944 | 4.5139 | 4.2091 | 3.8677 | 3.4906 | 3.0753 | 2.5467 | 1.8917 | -0.40619 | -4.2616 | -5.7692 | -6.5395 | 10.9402 | 10.8155 | 10.66 | 10.5044 | 10.3316 | 10.1412 | 9.9318 | 9.6577 | 9.1659 | 7.5175 | 4.7625 | 3.6943 | 1.6453 | 8.4663 | 8.3178 | 8.1312 | 7.9391 | 7.7245 | 7.4742 | 7.1592 | 6.7479 | 6.0392 | 3.6733 | -0.066872 | -2.3825 | -3.6047
BRAMLEY (FLEE) | ALDERSHOT BSP | ALDERSHOT | MINIMUM HEADROOM | SU 85976 48834 | YES | 11.4164 | 11.0132 | 10.5292 | 9.9666 | 9.3465 | 8.6882 | 7.9701 | 7.0401 | 5.6754 | 2.4927 | -2.6596 | -6.2248 | -8.259 | 14.8942 | 14.5903 | 14.2075 | 13.8164 | 13.3818 | 12.9114 | 12.3939 | 11.7033 | 10.7619 | 8.6779 | 5.5934 | 3.3975 | 1.4479 | 12.761 | 12.3803 | 11.9155 | 11.3943 | 10.8087 | 10.1843 | 9.5012 | 8.6078 | 7.3087 | 4.3358 | -0.30268 | -3.3913 | -5.1048
|  | ALDERSHOT | CT |  |  | 11.4164 | 11.0132 | 10.5292 | 9.9666 | 9.3465 | 8.6882 | 7.9701 | 7.0401 | 5.6754 | 2.4927 | -2.6596 | -6.2248 | -8.259 | 14.8942 | 14.5903 | 14.2075 | 13.8164 | 13.3818 | 12.9114 | 12.3939 | 11.7033 | 10.7619 | 8.6779 | 5.5934 | 3.3975 | 1.4479 | 12.761 | 12.3803 | 11.9155 | 11.3943 | 10.8087 | 10.1843 | 9.5012 | 8.6078 | 7.3087 | 4.3358 | -0.30268 | -3.3913 | -5.1048
|  | ALDERSHOT | LW |  |  | 11.4164 | 11.0132 | 10.5292 | 9.9666 | 9.3465 | 8.6882 | 7.9701 | 7.0401 | 5.6754 | 2.4927 | -2.6596 | -6.2248 | -8.259 | 14.8942 | 14.5903 | 14.2075 | 13.8164 | 13.3818 | 12.9114 | 12.3939 | 11.7033 | 10.7619 | 8.6779 | 5.5934 | 3.3975 | 1.4479 | 12.761 | 12.3803 | 11.9155 | 11.3943 | 10.8087 | 10.1843 | 9.5012 | 8.6078 | 7.3087 | 4.3358 | -0.30268 | -3.3913 | -5.1048
|  | ALDERSHOT | ST |  |  | 11.4164 | 11.0132 | 10.5292 | 9.9666 | 9.3465 | 8.6882 | 7.9701 | 7.0401 | 5.6754 | 2.4927 | -2.6596 | -6.2248 | -8.259 | 14.8942 | 14.5903 | 14.2075 | 13.8164 | 13.3818 | 12.9114 | 12.3939 | 11.7033 | 10.7619 | 8.6779 | 5.5934 | 3.3975 | 1.4479 | 12.761 | 12.3803 | 11.9155 | 11.3943 | 10.8087 | 10.1843 | 9.5012 | 8.6078 | 7.3087 | 4.3358 | -0.30268 | -3.3913 | -5.1048
|  | ALDERSHOT | FS |  |  | 11.4164 | 11.0132 | 10.5292 | 9.9666 | 9.3465 | 8.6882 | 7.9701 | 7.0401 | 5.6754 | 2.4927 | -2.6596 | -6.2248 | -8.259 | 14.8942 | 14.5903 | 14.2075 | 13.8164 | 13.3818 | 12.9114 | 12.3939 | 11.7033 | 10.7619 | 8.6779 | 5.5934 | 3.3975 | 1.4479 | 12.761 | 12.3803 | 11.9155 | 11.3943 | 10.8087 | 10.1843 | 9.5012 | 8.6078 | 7.3087 | 4.3358 | -0.30268 | -3.3913 | -5.1048
MELKSHAM GSP | CHIPPENHAM | ALDERTON | MINIMUM HEADROOM | ST 84609 84059 | YES | 0.23643 | 0.11887 | -0.0032342 | -0.1754 | -0.3527 | -0.54932 | -0.76171 | -1.0021 | -1.308 | -1.8712 | -2.7264 | -3.2106 | -3.3608 | 1.654 | 1.5775 | 1.4967 | 1.4006 | 1.3008 | 1.1839 | 1.0551 | 0.90146 | 0.70887 | 0.41542 | -0.0095745 | -0.27304 | -0.44775 | 0.66874 | 0.55771 | 0.44211 | 0.2828 | 0.1186 | -0.064949 | -0.26375 | -0.49064 | -0.77966 | -1.2952 | -2.0629 | -2.4903 | -2.6219
|  | ALDERTON | CT |  |  | 0.23643 | 0.11887 | -0.0032342 | -0.1754 | -0.3527 | -0.54932 | -0.76171 | -1.0021 | -1.308 | -1.8712 | -2.7264 | -3.2106 | -3.3608 | 1.654 | 1.5775 | 1.4967 | 1.4006 | 1.3008 | 1.1839 | 1.0551 | 0.90146 | 0.70887 | 0.41542 | -0.0095745 | -0.27304 | -0.44775 | 0.66874 | 0.55771 | 0.44211 | 0.2828 | 0.1186 | -0.064949 | -0.26375 | -0.49064 | -0.77966 | -1.2952 | -2.0629 | -2.4903 | -2.6219
|  | ALDERTON | LW |  |  | 0.23643 | 0.11887 | -0.0032342 | -0.1754 | -0.3527 | -0.54932 | -0.76171 | -1.0021 | -1.308 | -1.8712 | -2.7264 | -3.2106 | -3.3608 | 1.654 | 1.5775 | 1.4967 | 1.4006 | 1.3008 | 1.1839 | 1.0551 | 0.90146 | 0.70887 | 0.41542 | -0.0095745 | -0.27304 | -0.44775 | 0.66874 | 0.55771 | 0.44211 | 0.2828 | 0.1186 | -0.064949 | -0.26375 | -0.49064 | -0.77966 | -1.2952 | -2.0629 | -2.4903 | -2.6219
|  | ALDERTON | ST |  |  | 0.23643 | 0.11887 | -0.0032342 | -0.1754 | -0.3527 | -0.54932 | -0.76171 | -1.0021 | -1.308 | -1.8712 | -2.7264 | -3.2106 | -3.3608 | 1.654 | 1.5775 | 1.4967 | 1.4006 | 1.3008 | 1.1839 | 1.0551 | 0.90146 | 0.70887 | 0.41542 | -0.0095745 | -0.27304 | -0.44775 | 0.66874 | 0.55771 | 0.44211 | 0.2828 | 0.1186 | -0.064949 | -0.26375 | -0.49064 | -0.77966 | -1.2952 | -2.0629 | -2.4903 | -2.6219
|  | ALDERTON | FS |  |  | 0.23643 | 0.11887 | -0.0032342 | -0.1754 | -0.3527 | -0.54932 | -0.76171 | -1.0021 | -1.308 | -1.8712 | -2.7264 | -3.2106 | -3.3608 | 1.654 | 1.5775 | 1.4967 | 1.4006 | 1.3008 | 1.1839 | 1.0551 | 0.90146 | 0.70887 | 0.41542 | -0.0095745 | -0.27304 | -0.44775 | 0.66874 | 0.55771 | 0.44211 | 0.2828 | 0.1186 | -0.064949 | -0.26375 | -0.49064 | -0.77966 | -1.2952 | -2.0629 | -2.4903 | -2.6219
BRAMLEY (FLEE) | ALTON | ALRESFORD | MINIMUM HEADROOM | SU 59684 32511 | YES | 3.9627 | 3.4791 | 2.9203 | 2.1791 | 1.4051 | 0.58058 | -0.3569 | -1.3693 | -2.6743 | -5.3962 | -10.0347 | -12.8757 | -13.7031 | 8.0927 | 7.7733 | 7.409 | 6.9767 | 6.5154 | 6.0107 | 5.4186 | 4.7654 | 3.9649 | 2.4896 | 0.17727 | -1.468 | -2.6671 | 5.8348 | 5.3946 | 4.8854 | 4.2413 | 3.565 | 2.8371 | 1.9979 | 1.0843 | -0.12961 | -2.6044 | -6.7383 | -9.2417 | -9.9696
|  | ALRESFORD | CT |  |  | 3.9627 | 3.4791 | 2.9203 | 2.1791 | 1.4051 | 0.58058 | -0.3569 | -1.3693 | -2.6743 | -5.3962 | -10.0347 | -12.8757 | -13.7031 | 8.0927 | 7.7733 | 7.409 | 6.9767 | 6.5154 | 6.0107 | 5.4186 | 4.7654 | 3.9649 | 2.4896 | 0.17727 | -1.468 | -2.6671 | 5.8348 | 5.3946 | 4.8854 | 4.2413 | 3.565 | 2.8371 | 1.9979 | 1.0843 | -0.12961 | -2.6044 | -6.7383 | -9.2417 | -9.9696
|  | ALRESFORD | LW |  |  | 3.9627 | 3.4791 | 2.9203 | 2.1791 | 1.4051 | 0.58058 | -0.3569 | -1.3693 | -2.6743 | -5.3962 | -10.0347 | -12.8757 | -13.7031 | 8.0927 | 7.7733 | 7.409 | 6.9767 | 6.5154 | 6.0107 | 5.4186 | 4.7654 | 3.9649 | 2.4896 | 0.17727 | -1.468 | -2.6671 | 5.8348 | 5.3946 | 4.8854 | 4.2413 | 3.565 | 2.8371 | 1.9979 | 1.0843 | -0.12961 | -2.6044 | -6.7383 | -9.2417 | -9.9696
|  | ALRESFORD | ST |  |  | 3.9627 | 3.4791 | 2.9203 | 2.1791 | 1.4051 | 0.58058 | -0.3569 | -1.3693 | -2.6743 | -5.3962 | -10.0347 | -12.8757 | -13.7031 | 8.0927 | 7.7733 | 7.409 | 6.9767 | 6.5154 | 6.0107 | 5.4186 | 4.7654 | 3.9649 | 2.4896 | 0.17727 | -1.468 | -2.6671 | 5.8348 | 5.3946 | 4.8854 | 4.2413 | 3.565 | 2.8371 | 1.9979 | 1.0843 | -0.12961 | -2.6044 | -6.7383 | -9.2417 | -9.9696
|  | ALRESFORD | FS |  |  | 3.9627 | 3.4791 | 2.9203 | 2.1791 | 1.4051 | 0.58058 | -0.3569 | -1.3693 | -2.6743 | -5.3962 | -10.0347 | -12.8757 | -13.7031 | 8.0927 | 7.7733 | 7.409 | 6.9767 | 6.5154 | 6.0107 | 5.4186 | 4.7654 | 3.9649 | 2.4896 | 0.17727 | -1.468 | -2.6671 | 5.8348 | 5.3946 | 4.8854 | 4.2413 | 3.565 | 2.8371 | 1.9979 | 1.0843 | -0.12961 | -2.6044 | -6.7383 | -9.2417 | -9.9696
BRAMLEY (FLEE) | ALTON | ALTON LOCAL | MINIMUM HEADROOM | SU 72434 39606 | YES | 10.643 | 9.5205 | 8.3653 | 7.1206 | 5.956 | 4.7174 | 3.3041 | 1.7218 | -0.61349 | -5.6985 | -14.0388 | -19.9643 | -22.6332 | 21.0999 | 20.2996 | 19.4728 | 18.6734 | 17.9069 | 17.0646 | 16.087 | 14.9664 | 13.436 | 10.3687 | 5.6951 | 2.2739 | -0.61786 | 14.1848 | 13.1563 | 12.084 | 10.9337 | 9.8383 | 8.6678 | 7.3276 | 5.8191 | 3.611 | -1.0954 | -8.6342 | -13.5969 | -15.8021
|  | ALTON LOCAL | CT |  |  | 10.643 | 9.5205 | 8.3653 | 7.1206 | 5.956 | 4.7174 | 3.3041 | 1.7218 | -0.61349 | -5.6985 | -14.0388 | -19.9643 | -22.6332 | 21.0999 | 20.2996 | 19.4728 | 18.6734 | 17.9069 | 17.0646 | 16.087 | 14.9664 | 13.436 | 10.3687 | 5.6951 | 2.2739 | -0.61786 | 14.1848 | 13.1563 | 12.084 | 10.9337 | 9.8383 | 8.6678 | 7.3276 | 5.8191 | 3.611 | -1.0954 | -8.6342 | -13.5969 | -15.8021
|  | ALTON LOCAL | LW |  |  | 10.643 | 9.5205 | 8.3653 | 7.1206 | 5.956 | 4.7174 | 3.3041 | 1.7218 | -0.61349 | -5.6985 | -14.0388 | -19.9643 | -22.6332 | 21.0999 | 20.2996 | 19.4728 | 18.6734 | 17.9069 | 17.0646 | 16.087 | 14.9664 | 13.436 | 10.3687 | 5.6951 | 2.2739 | -0.61786 | 14.1848 | 13.1563 | 12.084 | 10.9337 | 9.8383 | 8.6678 | 7.3276 | 5.8191 | 3.611 | -1.0954 | -8.6342 | -13.5969 | -15.8021
|  | ALTON LOCAL | ST |  |  | 10.643 | 9.5205 | 8.3653 | 7.1206 | 5.956 | 4.7174 | 3.3041 | 1.7218 | -0.61349 | -5.6985 | -14.0388 | -19.9643 | -22.6332 | 21.0999 | 20.2996 | 19.4728 | 18.6734 | 17.9069 | 17.0646 | 16.087 | 14.9664 | 13.436 | 10.3687 | 5.6951 | 2.2739 | -0.61786 | 14.1848 | 13.1563 | 12.084 | 10.9337 | 9.8383 | 8.6678 | 7.3276 | 5.8191 | 3.611 | -1.0954 | -8.6342 | -13.5969 | -15.8021
|  | ALTON LOCAL | FS |  |  | 10.643 | 9.5205 | 8.3653 | 7.1206 | 5.956 | 4.7174 | 3.3041 | 1.7218 | -0.61349 | -5.6985 | -14.0388 | -19.9643 | -22.6332 | 21.0999 | 20.2996 | 19.4728 | 18.6734 | 17.9069 | 17.0646 | 16.087 | 14.9664 | 13.436 | 10.3687 | 5.6951 | 2.2739 | -0.61786 | 14.1848 | 13.1563 | 12.084 | 10.9337 | 9.8383 | 8.6678 | 7.3276 | 5.8191 | 3.611 | -1.0954 | -8.6342 | -13.5969 | -15.8021
BRAMLEY (ANDO-THAT) | ANDOVER BSP | ANDOVER | MINIMUM HEADROOM | SU 35240 46643 | YES | 30.1533 | 29.9635 | 29.718 | 29.3696 | 28.997 | 28.6199 | 28.2027 | 27.7044 | 26.92 | 24.869 | 21.6842 | 19.6026 | 18.6809 | 32.5894 | 32.4617 | 32.2944 | 32.0881 | 31.8647 | 31.6316 | 31.3708 | 31.0511 | 30.5868 | 29.3954 | 27.6568 | 26.4774 | 25.5876 | 30.8792 | 30.7114 | 30.496 | 30.1803 | 29.8166 | 29.4431 | 29.0263 | 28.5194 | 27.7457 | 25.789 | 22.9956 | 21.2697 | 20.5104
|  | ANDOVER | CT |  |  | 30.1533 | 29.9635 | 29.718 | 29.3696 | 28.997 | 28.6199 | 28.2027 | 27.7044 | 26.92 | 24.869 | 21.6842 | 19.6026 | 18.6809 | 32.5894 | 32.4617 | 32.2944 | 32.0881 | 31.8647 | 31.6316 | 31.3708 | 31.0511 | 30.5868 | 29.3954 | 27.6568 | 26.4774 | 25.5876 | 30.8792 | 30.7114 | 30.496 | 30.1803 | 29.8166 | 29.4431 | 29.0263 | 28.5194 | 27.7457 | 25.789 | 22.9956 | 21.2697 | 20.5104
|  | ANDOVER | LW |  |  | 30.1533 | 29.9635 | 29.718 | 29.3696 | 28.997 | 28.6199 | 28.2027 | 27.7044 | 26.92 | 24.869 | 21.6842 | 19.6026 | 18.6809 | 32.5894 | 32.4617 | 32.2944 | 32.0881 | 31.8647 | 31.6316 | 31.3708 | 31.0511 | 30.5868 | 29.3954 | 27.6568 | 26.4774 | 25.5876 | 30.8792 | 30.7114 | 30.496 | 30.1803 | 29.8166 | 29.4431 | 29.0263 | 28.5194 | 27.7457 | 25.789 | 22.9956 | 21.2697 | 20.5104
|  | ANDOVER | ST |  |  | 30.1533 | 29.9635 | 29.718 | 29.3696 | 28.997 | 28.6199 | 28.2027 | 27.7044 | 26.92 | 24.869 | 21.6842 | 19.6026 | 18.6809 | 32.5894 | 32.4617 | 32.2944 | 32.0881 | 31.8647 | 31.6316 | 31.3708 | 31.0511 | 30.5868 | 29.3954 | 27.6568 | 26.4774 | 25.5876 | 30.8792 | 30.7114 | 30.496 | 30.1803 | 29.8166 | 29.4431 | 29.0263 | 28.5194 | 27.7457 | 25.789 | 22.9956 | 21.2697 | 20.5104
|  | ANDOVER | FS |  |  | 30.1533 | 29.9635 | 29.718 | 29.3696 | 28.997 | 28.6199 | 28.2027 | 27.7044 | 26.92 | 24.869 | 21.6842 | 19.6026 | 18.6809 | 32.5894 | 32.4617 | 32.2944 | 32.0881 | 31.8647 | 31.6316 | 31.3708 | 31.0511 | 30.5868 | 29.3954 | 27.6568 | 26.4774 | 25.5876 | 30.8792 | 30.7114 | 30.496 | 30.1803 | 29.8166 | 29.4431 | 29.0263 | 28.5194 | 27.7457 | 25.789 | 22.9956 | 21.2697 | 20.5104
BRAMLEY (ANDO-THAT) | ANDOVER BSP | ANDOVER EAST | MINIMUM HEADROOM | SU 37953 46433 | YES | 18.4734 | 18.0144 | 17.5204 | 16.8462 | 16.1223 | 15.3678 | 14.5606 | 13.7357 | 12.4975 | 9.0711 | 3.9957 | 0.67359 | -0.77401 | 18.5375 | 18.175 | 17.8295 | 17.4496 | 17.0558 | 16.6385 | 16.1932 | 15.7322 | 14.951 | 12.7024 | 9.9125 | 8.0239 | 6.4326 | 17.792 | 17.3652 | 16.8966 | 16.2743 | 15.6082 | 14.9106 | 14.1575 | 13.3824 | 12.2304 | 9.0577 | 4.4778 | 1.5423 | 0.26675
|  | ANDOVER EAST | CT |  |  | 18.4734 | 18.0144 | 17.5204 | 16.8462 | 16.1223 | 15.3678 | 14.5606 | 13.7357 | 12.4975 | 9.0711 | 3.9957 | 0.67359 | -0.77401 | 18.5375 | 18.175 | 17.8295 | 17.4496 | 17.0558 | 16.6385 | 16.1932 | 15.7322 | 14.951 | 12.7024 | 9.9125 | 8.0239 | 6.4326 | 17.792 | 17.3652 | 16.8966 | 16.2743 | 15.6082 | 14.9106 | 14.1575 | 13.3824 | 12.2304 | 9.0577 | 4.4778 | 1.5423 | 0.26675
|  | ANDOVER EAST | LW |  |  | 18.4734 | 18.0144 | 17.5204 | 16.8462 | 16.1223 | 15.3678 | 14.5606 | 13.7357 | 12.4975 | 9.0711 | 3.9957 | 0.67359 | -0.77401 | 18.5375 | 18.175 | 17.8295 | 17.4496 | 17.0558 | 16.6385 | 16.1932 | 15.7322 | 14.951 | 12.7024 | 9.9125 | 8.0239 | 6.4326 | 17.792 | 17.3652 | 16.8966 | 16.2743 | 15.6082 | 14.9106 | 14.1575 | 13.3824 | 12.2304 | 9.0577 | 4.4778 | 1.5423 | 0.26675
|  | ANDOVER EAST | ST |  |  | 18.4734 | 18.0144 | 17.5204 | 16.8462 | 16.1223 | 15.3678 | 14.5606 | 13.7357 | 12.4975 | 9.0711 | 3.9957 | 0.67359 | -0.77401 | 18.5375 | 18.175 | 17.8295 | 17.4496 | 17.0558 | 16.6385 | 16.1932 | 15.7322 | 14.951 | 12.7024 | 9.9125 | 8.0239 | 6.4326 | 17.792 | 17.3652 | 16.8966 | 16.2743 | 15.6082 | 14.9106 | 14.1575 | 13.3824 | 12.2304 | 9.0577 | 4.4778 | 1.5423 | 0.26675
|  | ANDOVER EAST | FS |  |  | 18.4734 | 18.0144 | 17.5204 | 16.8462 | 16.1223 | 15.3678 | 14.5606 | 13.7357 | 12.4975 | 9.0711 | 3.9957 | 0.67359 | -0.77401 | 18.5375 | 18.175 | 17.8295 | 17.4496 | 17.0558 | 16.6385 | 16.1932 | 15.7322 | 14.951 | 12.7024 | 9.9125 | 8.0239 | 6.4326 | 17.792 | 17.3652 | 16.8966 | 16.2743 | 15.6082 | 14.9106 | 14.1575 | 13.3824 | 12.2304 | 9.0577 | 4.4778 | 1.5423 | 0.26675
BRAMLEY (ANDO-THAT) | ANDOVER BSP | ANDOVER TOWN | MINIMUM HEADROOM | SU 36207 45078 | YES | 10.3057 | 10.1164 | 9.8614 | 9.4993 | 9.1123 | 8.7207 | 8.2987 | 7.8163 | 6.9655 | 4.8634 | 1.5094 | -0.89443 | -2.0736 | 10.0708 | 9.9143 | 9.6922 | 9.443 | 9.1696 | 8.8771 | 8.5564 | 8.1741 | 7.5665 | 6.1807 | 4.1887 | 2.5255 | 0.83421 | 9.0499 | 8.8578 | 8.5906 | 8.2396 | 7.8618 | 7.473 | 7.0518 | 6.5616 | 5.715 | 3.7112 | 0.79428 | -1.1859 | -2.1428
|  | ANDOVER TOWN | CT |  |  | 10.3057 | 10.1164 | 9.8614 | 9.4993 | 9.1123 | 8.7207 | 8.2987 | 7.8163 | 6.9655 | 4.8634 | 1.5094 | -0.89443 | -2.0736 | 10.0708 | 9.9143 | 9.6922 | 9.443 | 9.1696 | 8.8771 | 8.5564 | 8.1741 | 7.5665 | 6.1807 | 4.1887 | 2.5255 | 0.83421 | 9.0499 | 8.8578 | 8.5906 | 8.2396 | 7.8618 | 7.473 | 7.0518 | 6.5616 | 5.715 | 3.7112 | 0.79428 | -1.1859 | -2.1428
|  | ANDOVER TOWN | LW |  |  | 10.3057 | 10.1164 | 9.8614 | 9.4993 | 9.1123 | 8.7207 | 8.2987 | 7.8163 | 6.9655 | 4.8634 | 1.5094 | -0.89443 | -2.0736 | 10.0708 | 9.9143 | 9.6922 | 9.443 | 9.1696 | 8.8771 | 8.5564 | 8.1741 | 7.5665 | 6.1807 | 4.1887 | 2.5255 | 0.83421 | 9.0499 | 8.8578 | 8.5906 | 8.2396 | 7.8618 | 7.473 | 7.0518 | 6.5616 | 5.715 | 3.7112 | 0.79428 | -1.1859 | -2.1428
|  | ANDOVER TOWN | ST |  |  | 10.3057 | 10.1164 | 9.8614 | 9.4993 | 9.1123 | 8.7207 | 8.2987 | 7.8163 | 6.9655 | 4.8634 | 1.5094 | -0.89443 | -2.0736 | 10.0708 | 9.9143 | 9.6922 | 9.443 | 9.1696 | 8.8771 | 8.5564 | 8.1741 | 7.5665 | 6.1807 | 4.1887 | 2.5255 | 0.83421 | 9.0499 | 8.8578 | 8.5906 | 8.2396 | 7.8618 | 7.473 | 7.0518 | 6.5616 | 5.715 | 3.7112 | 0.79428 | -1.1859 | -2.1428
|  | ANDOVER TOWN | FS |  |  | 10.3057 | 10.1164 | 9.8614 | 9.4993 | 9.1123 | 8.7207 | 8.2987 | 7.8163 | 6.9655 | 4.8634 | 1.5094 | -0.89443 | -2.0736 | 10.0708 | 9.9143 | 9.6922 | 9.443 | 9.1696 | 8.8771 | 8.5564 | 8.1741 | 7.5665 | 6.1807 | 4.1887 | 2.5255 | 0.83421 | 9.0499 | 8.8578 | 8.5906 | 8.2396 | 7.8618 | 7.473 | 7.0518 | 6.5616 | 5.715 | 3.7112 | 0.79428 | -1.1859 | -2.1428
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | ARBORFIELD | MINIMUM HEADROOM | SU 75949 65766 | YES | 7.183 | 6.9497 | 6.7093 | 6.3748 | 6.0163 | 5.6422 | 5.2112 | 4.7181 | 3.9722 | 2.3408 | -0.57678 | -2.4208 | -3.0986 | 11.4203 | 11.2608 | 11.0927 | 10.8885 | 10.6672 | 10.4294 | 10.1507 | 9.8253 | 9.3672 | 8.3946 | 6.7189 | 5.5898 | 4.7498 | 8.6977 | 8.4789 | 8.251 | 7.951 | 7.6288 | 7.2887 | 6.8918 | 6.4217 | 5.7164 | 4.2094 | 1.5658 | 2.5671e-05 | -0.57558
|  | ARBORFIELD | CT |  |  | 7.183 | 6.9497 | 6.7093 | 6.3748 | 6.0163 | 5.6422 | 5.2112 | 4.7181 | 3.9722 | 2.3408 | -0.57678 | -2.4208 | -3.0986 | 11.4203 | 11.2608 | 11.0927 | 10.8885 | 10.6672 | 10.4294 | 10.1507 | 9.8253 | 9.3672 | 8.3946 | 6.7189 | 5.5898 | 4.7498 | 8.6977 | 8.4789 | 8.251 | 7.951 | 7.6288 | 7.2887 | 6.8918 | 6.4217 | 5.7164 | 4.2094 | 1.5658 | 2.5671e-05 | -0.57558
|  | ARBORFIELD | LW |  |  | 7.183 | 6.9497 | 6.7093 | 6.3748 | 6.0163 | 5.6422 | 5.2112 | 4.7181 | 3.9722 | 2.3408 | -0.57678 | -2.4208 | -3.0986 | 11.4203 | 11.2608 | 11.0927 | 10.8885 | 10.6672 | 10.4294 | 10.1507 | 9.8253 | 9.3672 | 8.3946 | 6.7189 | 5.5898 | 4.7498 | 8.6977 | 8.4789 | 8.251 | 7.951 | 7.6288 | 7.2887 | 6.8918 | 6.4217 | 5.7164 | 4.2094 | 1.5658 | 2.5671e-05 | -0.57558
|  | ARBORFIELD | ST |  |  | 7.183 | 6.9497 | 6.7093 | 6.3748 | 6.0163 | 5.6422 | 5.2112 | 4.7181 | 3.9722 | 2.3408 | -0.57678 | -2.4208 | -3.0986 | 11.4203 | 11.2608 | 11.0927 | 10.8885 | 10.6672 | 10.4294 | 10.1507 | 9.8253 | 9.3672 | 8.3946 | 6.7189 | 5.5898 | 4.7498 | 8.6977 | 8.4789 | 8.251 | 7.951 | 7.6288 | 7.2887 | 6.8918 | 6.4217 | 5.7164 | 4.2094 | 1.5658 | 2.5671e-05 | -0.57558
|  | ARBORFIELD | FS |  |  | 7.183 | 6.9497 | 6.7093 | 6.3748 | 6.0163 | 5.6422 | 5.2112 | 4.7181 | 3.9722 | 2.3408 | -0.57678 | -2.4208 | -3.0986 | 11.4203 | 11.2608 | 11.0927 | 10.8885 | 10.6672 | 10.4294 | 10.1507 | 9.8253 | 9.3672 | 8.3946 | 6.7189 | 5.5898 | 4.7498 | 8.6977 | 8.4789 | 8.251 | 7.951 | 7.6288 | 7.2887 | 6.8918 | 6.4217 | 5.7164 | 4.2094 | 1.5658 | 2.5671e-05 | -0.57558
LOVEDEAN GSP | CHICHESTER & HUNSTON | ARGYLE ROAD | MINIMUM HEADROOM | SZ 93193 99152 | YES | 20.0085 | 19.7794 | 19.4082 | 18.8977 | 18.3555 | 17.7539 | 17.1104 | 16.4039 | 15.2717 | 11.9944 | 6.3224 | 1.6736 | -1.0883 | 22.5792 | 22.3837 | 22.0827 | 21.7071 | 21.3036 | 20.8533 | 20.3633 | 19.8122 | 19.0266 | 16.6615 | 12.1621 | 6.9167 | 0.050448 | 20.5675 | 20.3744 | 20.0758 | 19.6357 | 19.1699 | 18.6513 | 18.098 | 17.4828 | 16.4545 | 13.4723 | 8.3293 | 4.3405 | 2.0047
|  | ARGYLE ROAD | CT |  |  | 20.0085 | 19.7794 | 19.4082 | 18.8977 | 18.3555 | 17.7539 | 17.1104 | 16.4039 | 15.2717 | 11.9944 | 6.3224 | 1.6736 | -1.0883 | 22.5792 | 22.3837 | 22.0827 | 21.7071 | 21.3036 | 20.8533 | 20.3633 | 19.8122 | 19.0266 | 16.6615 | 12.1621 | 6.9167 | 0.050448 | 20.5675 | 20.3744 | 20.0758 | 19.6357 | 19.1699 | 18.6513 | 18.098 | 17.4828 | 16.4545 | 13.4723 | 8.3293 | 4.3405 | 2.0047
|  | ARGYLE ROAD | LW |  |  | 20.0085 | 19.7794 | 19.4082 | 18.8977 | 18.3555 | 17.7539 | 17.1104 | 16.4039 | 15.2717 | 11.9944 | 6.3224 | 1.6736 | -1.0883 | 22.5792 | 22.3837 | 22.0827 | 21.7071 | 21.3036 | 20.8533 | 20.3633 | 19.8122 | 19.0266 | 16.6615 | 12.1621 | 6.9167 | 0.050448 | 20.5675 | 20.3744 | 20.0758 | 19.6357 | 19.1699 | 18.6513 | 18.098 | 17.4828 | 16.4545 | 13.4723 | 8.3293 | 4.3405 | 2.0047
|  | ARGYLE ROAD | ST |  |  | 20.0085 | 19.7794 | 19.4082 | 18.8977 | 18.3555 | 17.7539 | 17.1104 | 16.4039 | 15.2717 | 11.9944 | 6.3224 | 1.6736 | -1.0883 | 22.5792 | 22.3837 | 22.0827 | 21.7071 | 21.3036 | 20.8533 | 20.3633 | 19.8122 | 19.0266 | 16.6615 | 12.1621 | 6.9167 | 0.050448 | 20.5675 | 20.3744 | 20.0758 | 19.6357 | 19.1699 | 18.6513 | 18.098 | 17.4828 | 16.4545 | 13.4723 | 8.3293 | 4.3405 | 2.0047
|  | ARGYLE ROAD | FS |  |  | 20.0085 | 19.7794 | 19.4082 | 18.8977 | 18.3555 | 17.7539 | 17.1104 | 16.4039 | 15.2717 | 11.9944 | 6.3224 | 1.6736 | -1.0883 | 22.5792 | 22.3837 | 22.0827 | 21.7071 | 21.3036 | 20.8533 | 20.3633 | 19.8122 | 19.0266 | 16.6615 | 12.1621 | 6.9167 | 0.050448 | 20.5675 | 20.3744 | 20.0758 | 19.6357 | 19.1699 | 18.6513 | 18.098 | 17.4828 | 16.4545 | 13.4723 | 8.3293 | 4.3405 | 2.0047
COWLEY GSP | HEADINGTON BSP | ARNCOTT | MINIMUM HEADROOM | SP 60730 18095 | NO | 10.3812 | 9.89 | 9.0637 | 8.2231 | 7.2951 | 6.6422 | 5.9103 | 5.2219 | 4.4199 | 2.8463 | 0.7974 | -0.33269 | -0.73696 | 11.5428 | 11.2916 | 10.8578 | 10.3746 | 9.8061 | 9.3996 | 8.9106 | 8.4784 | 7.9852 | 7.0161 | 5.8876 | 5.2582 | 4.8394 | 10.5288 | 10.0947 | 9.3831 | 8.6636 | 7.8597 | 7.2817 | 6.6208 | 6.0004 | 5.273 | 3.8486 | 2.0143 | 1.06 | 0.72462
|  | ARNCOTT | CT |  |  | 10.3812 | 9.89 | 9.0637 | 8.2231 | 7.2951 | 6.6422 | 5.9103 | 5.2219 | 4.4199 | 2.8463 | 0.7974 | -0.33269 | -0.73696 | 11.5428 | 11.2916 | 10.8578 | 10.3746 | 9.8061 | 9.3996 | 8.9106 | 8.4784 | 7.9852 | 7.0161 | 5.8876 | 5.2582 | 4.8394 | 10.5288 | 10.0947 | 9.3831 | 8.6636 | 7.8597 | 7.2817 | 6.6208 | 6.0004 | 5.273 | 3.8486 | 2.0143 | 1.06 | 0.72462
|  | ARNCOTT | LW |  |  | 10.3812 | 9.89 | 9.0637 | 8.2231 | 7.2951 | 6.6422 | 5.9103 | 5.2219 | 4.4199 | 2.8463 | 0.7974 | -0.33269 | -0.73696 | 11.5428 | 11.2916 | 10.8578 | 10.3746 | 9.8061 | 9.3996 | 8.9106 | 8.4784 | 7.9852 | 7.0161 | 5.8876 | 5.2582 | 4.8394 | 10.5288 | 10.0947 | 9.3831 | 8.6636 | 7.8597 | 7.2817 | 6.6208 | 6.0004 | 5.273 | 3.8486 | 2.0143 | 1.06 | 0.72462
|  | ARNCOTT | ST |  |  | 10.3812 | 9.89 | 9.0637 | 8.2231 | 7.2951 | 6.6422 | 5.9103 | 5.2219 | 4.4199 | 2.8463 | 0.7974 | -0.33269 | -0.73696 | 11.5428 | 11.2916 | 10.8578 | 10.3746 | 9.8061 | 9.3996 | 8.9106 | 8.4784 | 7.9852 | 7.0161 | 5.8876 | 5.2582 | 4.8394 | 10.5288 | 10.0947 | 9.3831 | 8.6636 | 7.8597 | 7.2817 | 6.6208 | 6.0004 | 5.273 | 3.8486 | 2.0143 | 1.06 | 0.72462
|  | ARNCOTT | FS |  |  | 10.3812 | 9.89 | 9.0637 | 8.2231 | 7.2951 | 6.6422 | 5.9103 | 5.2219 | 4.4199 | 2.8463 | 0.7974 | -0.33269 | -0.73696 | 11.5428 | 11.2916 | 10.8578 | 10.3746 | 9.8061 | 9.3996 | 8.9106 | 8.4784 | 7.9852 | 7.0161 | 5.8876 | 5.2582 | 4.8394 | 10.5288 | 10.0947 | 9.3831 | 8.6636 | 7.8597 | 7.2817 | 6.6208 | 6.0004 | 5.273 | 3.8486 | 2.0143 | 1.06 | 0.72462
BRAMLEY (FLEE) | BRACKNELL MAIN | ASCOT | MINIMUM HEADROOM | SU 91615 68855 | YES | 22.4492 | 21.9365 | 21.4047 | 20.7671 | 20.1474 | 19.5333 | 18.8437 | 18.0508 | 16.8013 | 13.8887 | 9.1682 | 6.087 | 4.5905 | 26.7761 | 26.4134 | 26.0356 | 25.6304 | 25.2236 | 24.798 | 24.3136 | 23.7447 | 22.9086 | 21.051 | 18.2312 | 16.2729 | 14.5523 | 24.0421 | 23.5752 | 23.09 | 22.5256 | 21.9669 | 21.4011 | 20.7587 | 20.0082 | 18.8298 | 16.1257 | 11.8551 | 9.1623 | 7.8812
|  | ASCOT | CT |  |  | 22.4492 | 21.9365 | 21.4047 | 20.7671 | 20.1474 | 19.5333 | 18.8437 | 18.0508 | 16.8013 | 13.8887 | 9.1682 | 6.087 | 4.5905 | 26.7761 | 26.4134 | 26.0356 | 25.6304 | 25.2236 | 24.798 | 24.3136 | 23.7447 | 22.9086 | 21.051 | 18.2312 | 16.2729 | 14.5523 | 24.0421 | 23.5752 | 23.09 | 22.5256 | 21.9669 | 21.4011 | 20.7587 | 20.0082 | 18.8298 | 16.1257 | 11.8551 | 9.1623 | 7.8812
|  | ASCOT | LW |  |  | 22.4492 | 21.9365 | 21.4047 | 20.7671 | 20.1474 | 19.5333 | 18.8437 | 18.0508 | 16.8013 | 13.8887 | 9.1682 | 6.087 | 4.5905 | 26.7761 | 26.4134 | 26.0356 | 25.6304 | 25.2236 | 24.798 | 24.3136 | 23.7447 | 22.9086 | 21.051 | 18.2312 | 16.2729 | 14.5523 | 24.0421 | 23.5752 | 23.09 | 22.5256 | 21.9669 | 21.4011 | 20.7587 | 20.0082 | 18.8298 | 16.1257 | 11.8551 | 9.1623 | 7.8812
|  | ASCOT | ST |  |  | 22.4492 | 21.9365 | 21.4047 | 20.7671 | 20.1474 | 19.5333 | 18.8437 | 18.0508 | 16.8013 | 13.8887 | 9.1682 | 6.087 | 4.5905 | 26.7761 | 26.4134 | 26.0356 | 25.6304 | 25.2236 | 24.798 | 24.3136 | 23.7447 | 22.9086 | 21.051 | 18.2312 | 16.2729 | 14.5523 | 24.0421 | 23.5752 | 23.09 | 22.5256 | 21.9669 | 21.4011 | 20.7587 | 20.0082 | 18.8298 | 16.1257 | 11.8551 | 9.1623 | 7.8812
|  | ASCOT | FS |  |  | 22.4492 | 21.9365 | 21.4047 | 20.7671 | 20.1474 | 19.5333 | 18.8437 | 18.0508 | 16.8013 | 13.8887 | 9.1682 | 6.087 | 4.5905 | 26.7761 | 26.4134 | 26.0356 | 25.6304 | 25.2236 | 24.798 | 24.3136 | 23.7447 | 22.9086 | 21.051 | 18.2312 | 16.2729 | 14.5523 | 24.0421 | 23.5752 | 23.09 | 22.5256 | 21.9669 | 21.4011 | 20.7587 | 20.0082 | 18.8298 | 16.1257 | 11.8551 | 9.1623 | 7.8812
LOVEDEAN GSP | CHICHESTER & HUNSTON | ASHLING ROAD | MINIMUM HEADROOM | SU 84085 06737 | YES | 1.4514 | 0.41095 | -0.83135 | -2.6045 | -4.3874 | -6.1187 | -8.0269 | -10.2353 | -13.3426 | -21.8772 | -32.0581 | -37.5577 | -39.8817 | 9.2241 | 8.5144 | 7.6458 | 6.5594 | 5.4506 | 4.3416 | 3.1216 | 1.6806 | -0.29021 | -5.4534 | -11.4302 | -15.1126 | -18.6432 | 1.9843 | 1.0397 | -0.1159 | -1.6911 | -3.2904 | -4.8616 | -6.5791 | -8.5804 | -11.4227 | -19.0636 | -28.0402 | -32.5912 | -34.4915
|  | ASHLING ROAD | CT |  |  | 1.4514 | 0.41095 | -0.83135 | -2.6045 | -4.3874 | -6.1187 | -8.0269 | -10.2353 | -13.3426 | -21.8772 | -32.0581 | -37.5577 | -39.8817 | 9.2241 | 8.5144 | 7.6458 | 6.5594 | 5.4506 | 4.3416 | 3.1216 | 1.6806 | -0.29021 | -5.4534 | -11.4302 | -15.1126 | -18.6432 | 1.9843 | 1.0397 | -0.1159 | -1.6911 | -3.2904 | -4.8616 | -6.5791 | -8.5804 | -11.4227 | -19.0636 | -28.0402 | -32.5912 | -34.4915
|  | ASHLING ROAD | LW |  |  | 1.4514 | 0.41095 | -0.83135 | -2.6045 | -4.3874 | -6.1187 | -8.0269 | -10.2353 | -13.3426 | -21.8772 | -32.0581 | -37.5577 | -39.8817 | 9.2241 | 8.5144 | 7.6458 | 6.5594 | 5.4506 | 4.3416 | 3.1216 | 1.6806 | -0.29021 | -5.4534 | -11.4302 | -15.1126 | -18.6432 | 1.9843 | 1.0397 | -0.1159 | -1.6911 | -3.2904 | -4.8616 | -6.5791 | -8.5804 | -11.4227 | -19.0636 | -28.0402 | -32.5912 | -34.4915
|  | ASHLING ROAD | ST |  |  | 1.4514 | 0.41095 | -0.83135 | -2.6045 | -4.3874 | -6.1187 | -8.0269 | -10.2353 | -13.3426 | -21.8772 | -32.0581 | -37.5577 | -39.8817 | 9.2241 | 8.5144 | 7.6458 | 6.5594 | 5.4506 | 4.3416 | 3.1216 | 1.6806 | -0.29021 | -5.4534 | -11.4302 | -15.1126 | -18.6432 | 1.9843 | 1.0397 | -0.1159 | -1.6911 | -3.2904 | -4.8616 | -6.5791 | -8.5804 | -11.4227 | -19.0636 | -28.0402 | -32.5912 | -34.4915
|  | ASHLING ROAD | FS |  |  | 1.4514 | 0.41095 | -0.83135 | -2.6045 | -4.3874 | -6.1187 | -8.0269 | -10.2353 | -13.3426 | -21.8772 | -32.0581 | -37.5577 | -39.8817 | 9.2241 | 8.5144 | 7.6458 | 6.5594 | 5.4506 | 4.3416 | 3.1216 | 1.6806 | -0.29021 | -5.4534 | -11.4302 | -15.1126 | -18.6432 | 1.9843 | 1.0397 | -0.1159 | -1.6911 | -3.2904 | -4.8616 | -6.5791 | -8.5804 | -11.4227 | -19.0636 | -28.0402 | -32.5912 | -34.4915
MELKSHAM GSP | NORRINGTON | ASHTON PARK | MINIMUM HEADROOM | ST 87141 57741 | YES | 0.50767 | -0.76283 | -2.2481 | -3.4651 | -4.7049 | -5.9055 | -7.1581 | -8.6442 | -10.8986 | -16.2595 | -23.5682 | -28.7145 | -31.0192 | 8.3287 | 7.4857 | 6.4742 | 5.6641 | 4.7822 | 3.8991 | 2.9976 | 1.9214 | 0.39346 | -3.1149 | -7.4064 | -10.7039 | -13.8392 | 2.1742 | 1.081 | -0.21823 | -1.3201 | -2.4652 | -3.5839 | -4.7283 | -6.0574 | -8.0881 | -13.0041 | -19.7947 | -24.332 | -26.3566
|  | ASHTON PARK | CT |  |  | 0.50767 | -0.76283 | -2.2481 | -3.4651 | -4.7049 | -5.9055 | -7.1581 | -8.6442 | -10.8986 | -16.2595 | -23.5682 | -28.7145 | -31.0192 | 8.3287 | 7.4857 | 6.4742 | 5.6641 | 4.7822 | 3.8991 | 2.9976 | 1.9214 | 0.39346 | -3.1149 | -7.4064 | -10.7039 | -13.8392 | 2.1742 | 1.081 | -0.21823 | -1.3201 | -2.4652 | -3.5839 | -4.7283 | -6.0574 | -8.0881 | -13.0041 | -19.7947 | -24.332 | -26.3566
|  | ASHTON PARK | LW |  |  | 0.50767 | -0.76283 | -2.2481 | -3.4651 | -4.7049 | -5.9055 | -7.1581 | -8.6442 | -10.8986 | -16.2595 | -23.5682 | -28.7145 | -31.0192 | 8.3287 | 7.4857 | 6.4742 | 5.6641 | 4.7822 | 3.8991 | 2.9976 | 1.9214 | 0.39346 | -3.1149 | -7.4064 | -10.7039 | -13.8392 | 2.1742 | 1.081 | -0.21823 | -1.3201 | -2.4652 | -3.5839 | -4.7283 | -6.0574 | -8.0881 | -13.0041 | -19.7947 | -24.332 | -26.3566
|  | ASHTON PARK | ST |  |  | 0.50767 | -0.76283 | -2.2481 | -3.4651 | -4.7049 | -5.9055 | -7.1581 | -8.6442 | -10.8986 | -16.2595 | -23.5682 | -28.7145 | -31.0192 | 8.3287 | 7.4857 | 6.4742 | 5.6641 | 4.7822 | 3.8991 | 2.9976 | 1.9214 | 0.39346 | -3.1149 | -7.4064 | -10.7039 | -13.8392 | 2.1742 | 1.081 | -0.21823 | -1.3201 | -2.4652 | -3.5839 | -4.7283 | -6.0574 | -8.0881 | -13.0041 | -19.7947 | -24.332 | -26.3566
|  | ASHTON PARK | FS |  |  | 0.50767 | -0.76283 | -2.2481 | -3.4651 | -4.7049 | -5.9055 | -7.1581 | -8.6442 | -10.8986 | -16.2595 | -23.5682 | -28.7145 | -31.0192 | 8.3287 | 7.4857 | 6.4742 | 5.6641 | 4.7822 | 3.8991 | 2.9976 | 1.9214 | 0.39346 | -3.1149 | -7.4064 | -10.7039 | -13.8392 | 2.1742 | 1.081 | -0.21823 | -1.3201 | -2.4652 | -3.5839 | -4.7283 | -6.0574 | -8.0881 | -13.0041 | -19.7947 | -24.332 | -26.3566
BRAMLEY (FLEE) | BRACKNELL RESERVE | BAGSHOT | MINIMUM HEADROOM | SU 91122 63523 | YES | 15.9661 | 15.5759 | 15.1424 | 14.5899 | 13.9974 | 13.3517 | 12.6026 | 11.7439 | 10.415 | 7.7701 | 3.2689 | 0.17466 | -1.3105 | 19.9086 | 19.591 | 19.2354 | 18.851 | 18.4366 | 17.9618 | 17.3988 | 16.7392 | 15.8291 | 14.2068 | 11.5549 | 9.577 | 7.797 | 17.9021 | 17.5175 | 17.0891 | 16.5776 | 16.024 | 15.4056 | 14.6852 | 13.856 | 12.5895 | 10.1331 | 6.0685 | 3.3553 | 2.0724
|  | BAGSHOT | CT |  |  | 15.9661 | 15.5759 | 15.1424 | 14.5899 | 13.9974 | 13.3517 | 12.6026 | 11.7439 | 10.415 | 7.7701 | 3.2689 | 0.17466 | -1.3105 | 19.9086 | 19.591 | 19.2354 | 18.851 | 18.4366 | 17.9618 | 17.3988 | 16.7392 | 15.8291 | 14.2068 | 11.5549 | 9.577 | 7.797 | 17.9021 | 17.5175 | 17.0891 | 16.5776 | 16.024 | 15.4056 | 14.6852 | 13.856 | 12.5895 | 10.1331 | 6.0685 | 3.3553 | 2.0724
|  | BAGSHOT | LW |  |  | 15.9661 | 15.5759 | 15.1424 | 14.5899 | 13.9974 | 13.3517 | 12.6026 | 11.7439 | 10.415 | 7.7701 | 3.2689 | 0.17466 | -1.3105 | 19.9086 | 19.591 | 19.2354 | 18.851 | 18.4366 | 17.9618 | 17.3988 | 16.7392 | 15.8291 | 14.2068 | 11.5549 | 9.577 | 7.797 | 17.9021 | 17.5175 | 17.0891 | 16.5776 | 16.024 | 15.4056 | 14.6852 | 13.856 | 12.5895 | 10.1331 | 6.0685 | 3.3553 | 2.0724
|  | BAGSHOT | ST |  |  | 15.9661 | 15.5759 | 15.1424 | 14.5899 | 13.9974 | 13.3517 | 12.6026 | 11.7439 | 10.415 | 7.7701 | 3.2689 | 0.17466 | -1.3105 | 19.9086 | 19.591 | 19.2354 | 18.851 | 18.4366 | 17.9618 | 17.3988 | 16.7392 | 15.8291 | 14.2068 | 11.5549 | 9.577 | 7.797 | 17.9021 | 17.5175 | 17.0891 | 16.5776 | 16.024 | 15.4056 | 14.6852 | 13.856 | 12.5895 | 10.1331 | 6.0685 | 3.3553 | 2.0724
|  | BAGSHOT | FS |  |  | 15.9661 | 15.5759 | 15.1424 | 14.5899 | 13.9974 | 13.3517 | 12.6026 | 11.7439 | 10.415 | 7.7701 | 3.2689 | 0.17466 | -1.3105 | 19.9086 | 19.591 | 19.2354 | 18.851 | 18.4366 | 17.9618 | 17.3988 | 16.7392 | 15.8291 | 14.2068 | 11.5549 | 9.577 | 7.797 | 17.9021 | 17.5175 | 17.0891 | 16.5776 | 16.024 | 15.4056 | 14.6852 | 13.856 | 12.5895 | 10.1331 | 6.0685 | 3.3553 | 2.0724
BRAMLEY (ANDO-THAT) | THATCHAM BSP | BALL HILL | MINIMUM HEADROOM | SU 42417 63142 | YES | 12.2324 | 11.9599 | 11.7066 | 11.2966 | 10.8725 | 10.4518 | 9.9943 | 9.6629 | 9.3365 | 9.0738 | 8.7317 | 8.5945 | 8.525 | 14.7648 | 14.5998 | 14.4496 | 14.2482 | 14.036 | 13.8152 | 13.5494 | 13.3243 | 13.0697 | 12.8501 | 12.524 | 12.2753 | 11.9447 | 13.4716 | 13.2159 | 12.9814 | 12.619 | 12.2357 | 11.8537 | 11.4331 | 11.1177 | 10.7867 | 10.5354 | 10.218 | 10.0966 | 10.0373
|  | BALL HILL | CT |  |  | 12.2324 | 11.9599 | 11.7066 | 11.2966 | 10.8725 | 10.4518 | 9.9943 | 9.6629 | 9.3365 | 9.0738 | 8.7317 | 8.5945 | 8.525 | 14.7648 | 14.5998 | 14.4496 | 14.2482 | 14.036 | 13.8152 | 13.5494 | 13.3243 | 13.0697 | 12.8501 | 12.524 | 12.2753 | 11.9447 | 13.4716 | 13.2159 | 12.9814 | 12.619 | 12.2357 | 11.8537 | 11.4331 | 11.1177 | 10.7867 | 10.5354 | 10.218 | 10.0966 | 10.0373
|  | BALL HILL | LW |  |  | 12.2324 | 11.9599 | 11.7066 | 11.2966 | 10.8725 | 10.4518 | 9.9943 | 9.6629 | 9.3365 | 9.0738 | 8.7317 | 8.5945 | 8.525 | 14.7648 | 14.5998 | 14.4496 | 14.2482 | 14.036 | 13.8152 | 13.5494 | 13.3243 | 13.0697 | 12.8501 | 12.524 | 12.2753 | 11.9447 | 13.4716 | 13.2159 | 12.9814 | 12.619 | 12.2357 | 11.8537 | 11.4331 | 11.1177 | 10.7867 | 10.5354 | 10.218 | 10.0966 | 10.0373
|  | BALL HILL | ST |  |  | 12.2324 | 11.9599 | 11.7066 | 11.2966 | 10.8725 | 10.4518 | 9.9943 | 9.6629 | 9.3365 | 9.0738 | 8.7317 | 8.5945 | 8.525 | 14.7648 | 14.5998 | 14.4496 | 14.2482 | 14.036 | 13.8152 | 13.5494 | 13.3243 | 13.0697 | 12.8501 | 12.524 | 12.2753 | 11.9447 | 13.4716 | 13.2159 | 12.9814 | 12.619 | 12.2357 | 11.8537 | 11.4331 | 11.1177 | 10.7867 | 10.5354 | 10.218 | 10.0966 | 10.0373
|  | BALL HILL | FS |  |  | 12.2324 | 11.9599 | 11.7066 | 11.2966 | 10.8725 | 10.4518 | 9.9943 | 9.6629 | 9.3365 | 9.0738 | 8.7317 | 8.5945 | 8.525 | 14.7648 | 14.5998 | 14.4496 | 14.2482 | 14.036 | 13.8152 | 13.5494 | 13.3243 | 13.0697 | 12.8501 | 12.524 | 12.2753 | 11.9447 | 13.4716 | 13.2159 | 12.9814 | 12.619 | 12.2357 | 11.8537 | 11.4331 | 11.1177 | 10.7867 | 10.5354 | 10.218 | 10.0966 | 10.0373
BRAMLEY (ANDO-THAT) | ANDOVER BSP | BARTON STACEY | MINIMUM HEADROOM | SU 42075 42720 | YES | 12.9001 | 12.7443 | 12.5727 | 12.3384 | 12.0936 | 11.8342 | 11.5339 | 11.2153 | 10.7655 | 9.8684 | 8.4354 | 7.7507 | 7.6001 | 14.7761 | 14.6785 | 14.5664 | 14.4408 | 14.3065 | 14.1601 | 13.9804 | 13.7842 | 13.5084 | 13.0778 | 12.4896 | 12.1894 | 12.0071 | 13.7173 | 13.5711 | 13.4091 | 13.1928 | 12.9663 | 12.7254 | 12.4443 | 12.145 | 11.7214 | 10.9034 | 9.6081 | 8.9633 | 8.8229
|  | BARTON STACEY | CT |  |  | 12.9001 | 12.7443 | 12.5727 | 12.3384 | 12.0936 | 11.8342 | 11.5339 | 11.2153 | 10.7655 | 9.8684 | 8.4354 | 7.7507 | 7.6001 | 14.7761 | 14.6785 | 14.5664 | 14.4408 | 14.3065 | 14.1601 | 13.9804 | 13.7842 | 13.5084 | 13.0778 | 12.4896 | 12.1894 | 12.0071 | 13.7173 | 13.5711 | 13.4091 | 13.1928 | 12.9663 | 12.7254 | 12.4443 | 12.145 | 11.7214 | 10.9034 | 9.6081 | 8.9633 | 8.8229
|  | BARTON STACEY | LW |  |  | 12.9001 | 12.7443 | 12.5727 | 12.3384 | 12.0936 | 11.8342 | 11.5339 | 11.2153 | 10.7655 | 9.8684 | 8.4354 | 7.7507 | 7.6001 | 14.7761 | 14.6785 | 14.5664 | 14.4408 | 14.3065 | 14.1601 | 13.9804 | 13.7842 | 13.5084 | 13.0778 | 12.4896 | 12.1894 | 12.0071 | 13.7173 | 13.5711 | 13.4091 | 13.1928 | 12.9663 | 12.7254 | 12.4443 | 12.145 | 11.7214 | 10.9034 | 9.6081 | 8.9633 | 8.8229
|  | BARTON STACEY | ST |  |  | 12.9001 | 12.7443 | 12.5727 | 12.3384 | 12.0936 | 11.8342 | 11.5339 | 11.2153 | 10.7655 | 9.8684 | 8.4354 | 7.7507 | 7.6001 | 14.7761 | 14.6785 | 14.5664 | 14.4408 | 14.3065 | 14.1601 | 13.9804 | 13.7842 | 13.5084 | 13.0778 | 12.4896 | 12.1894 | 12.0071 | 13.7173 | 13.5711 | 13.4091 | 13.1928 | 12.9663 | 12.7254 | 12.4443 | 12.145 | 11.7214 | 10.9034 | 9.6081 | 8.9633 | 8.8229
|  | BARTON STACEY | FS |  |  | 12.9001 | 12.7443 | 12.5727 | 12.3384 | 12.0936 | 11.8342 | 11.5339 | 11.2153 | 10.7655 | 9.8684 | 8.4354 | 7.7507 | 7.6001 | 14.7761 | 14.6785 | 14.5664 | 14.4408 | 14.3065 | 14.1601 | 13.9804 | 13.7842 | 13.5084 | 13.0778 | 12.4896 | 12.1894 | 12.0071 | 13.7173 | 13.5711 | 13.4091 | 13.1928 | 12.9663 | 12.7254 | 12.4443 | 12.145 | 11.7214 | 10.9034 | 9.6081 | 8.9633 | 8.8229
BRAMLEY (BASI) | BASINGSTOKE T1A & T2A | BASINGSTOKE | MINIMUM HEADROOM | SU 65155 52705 | YES | 29.1754 | 28.8495 | 28.4821 | 28.0848 | 27.6456 | 27.2166 | 26.7591 | 26.2431 | 25.5478 | 23.2936 | 19.1815 | 17.5926 | 16.8668 | 24.506 | 24.2571 | 23.9751 | 23.7084 | 23.3839 | 23.0905 | 22.7846 | 22.4488 | 21.9864 | 20.724 | 18.6902 | 17.2149 | 15.8049 | 24.5383 | 24.2669 | 23.9613 | 23.6376 | 23.2786 | 22.9319 | 22.5615 | 22.1429 | 21.6136 | 20.0456 | 16.4335 | 14.9917 | 14.3336
|  | BASINGSTOKE | CT |  |  | 29.1754 | 28.8495 | 28.4821 | 28.0848 | 27.6456 | 27.2166 | 26.7591 | 26.2431 | 25.5478 | 23.2936 | 19.1815 | 17.5926 | 16.8668 | 24.506 | 24.2571 | 23.9751 | 23.7084 | 23.3839 | 23.0905 | 22.7846 | 22.4488 | 21.9864 | 20.724 | 18.6902 | 17.2149 | 15.8049 | 24.5383 | 24.2669 | 23.9613 | 23.6376 | 23.2786 | 22.9319 | 22.5615 | 22.1429 | 21.6136 | 20.0456 | 16.4335 | 14.9917 | 14.3336
|  | BASINGSTOKE | LW |  |  | 29.1754 | 28.8495 | 28.4821 | 28.0848 | 27.6456 | 27.2166 | 26.7591 | 26.2431 | 25.5478 | 23.2936 | 19.1815 | 17.5926 | 16.8668 | 24.506 | 24.2571 | 23.9751 | 23.7084 | 23.3839 | 23.0905 | 22.7846 | 22.4488 | 21.9864 | 20.724 | 18.6902 | 17.2149 | 15.8049 | 24.5383 | 24.2669 | 23.9613 | 23.6376 | 23.2786 | 22.9319 | 22.5615 | 22.1429 | 21.6136 | 20.0456 | 16.4335 | 14.9917 | 14.3336
|  | BASINGSTOKE | ST |  |  | 29.1754 | 28.8495 | 28.4821 | 28.0848 | 27.6456 | 27.2166 | 26.7591 | 26.2431 | 25.5478 | 23.2936 | 19.1815 | 17.5926 | 16.8668 | 24.506 | 24.2571 | 23.9751 | 23.7084 | 23.3839 | 23.0905 | 22.7846 | 22.4488 | 21.9864 | 20.724 | 18.6902 | 17.2149 | 15.8049 | 24.5383 | 24.2669 | 23.9613 | 23.6376 | 23.2786 | 22.9319 | 22.5615 | 22.1429 | 21.6136 | 20.0456 | 16.4335 | 14.9917 | 14.3336
|  | BASINGSTOKE | FS |  |  | 29.1754 | 28.8495 | 28.4821 | 28.0848 | 27.6456 | 27.2166 | 26.7591 | 26.2431 | 25.5478 | 23.2936 | 19.1815 | 17.5926 | 16.8668 | 24.506 | 24.2571 | 23.9751 | 23.7084 | 23.3839 | 23.0905 | 22.7846 | 22.4488 | 21.9864 | 20.724 | 18.6902 | 17.2149 | 15.8049 | 24.5383 | 24.2669 | 23.9613 | 23.6376 | 23.2786 | 22.9319 | 22.5615 | 22.1429 | 21.6136 | 20.0456 | 16.4335 | 14.9917 | 14.3336
NURSLING GSP | VELMORE BSP | BASSETT | MINIMUM HEADROOM | SU 42193 15958 | YES | 22.8206 | 22.6094 | 22.3428 | 21.9465 | 21.5297 | 21.0875 | 20.6131 | 20.088 | 19.1844 | 16.2368 | 11.3735 | 7.7488 | 5.5875 | 23.1455 | 22.9285 | 22.6464 | 22.3167 | 21.9637 | 21.5635 | 21.1123 | 20.588 | 19.8251 | 17.5745 | 13.9135 | 10.1009 | 5.1472 | 21.1309 | 20.8776 | 20.5388 | 20.1076 | 19.6503 | 19.155 | 18.6174 | 18.0026 | 17.0112 | 14.1567 | 9.8145 | 6.7229 | 4.9757
|  | BASSETT | CT |  |  | 22.8206 | 22.6094 | 22.3428 | 21.9465 | 21.5297 | 21.0875 | 20.6131 | 20.088 | 19.1844 | 16.2368 | 11.3735 | 7.7488 | 5.5875 | 23.1455 | 22.9285 | 22.6464 | 22.3167 | 21.9637 | 21.5635 | 21.1123 | 20.588 | 19.8251 | 17.5745 | 13.9135 | 10.1009 | 5.1472 | 21.1309 | 20.8776 | 20.5388 | 20.1076 | 19.6503 | 19.155 | 18.6174 | 18.0026 | 17.0112 | 14.1567 | 9.8145 | 6.7229 | 4.9757
|  | BASSETT | LW |  |  | 22.8206 | 22.6094 | 22.3428 | 21.9465 | 21.5297 | 21.0875 | 20.6131 | 20.088 | 19.1844 | 16.2368 | 11.3735 | 7.7488 | 5.5875 | 23.1455 | 22.9285 | 22.6464 | 22.3167 | 21.9637 | 21.5635 | 21.1123 | 20.588 | 19.8251 | 17.5745 | 13.9135 | 10.1009 | 5.1472 | 21.1309 | 20.8776 | 20.5388 | 20.1076 | 19.6503 | 19.155 | 18.6174 | 18.0026 | 17.0112 | 14.1567 | 9.8145 | 6.7229 | 4.9757
|  | BASSETT | ST |  |  | 22.8206 | 22.6094 | 22.3428 | 21.9465 | 21.5297 | 21.0875 | 20.6131 | 20.088 | 19.1844 | 16.2368 | 11.3735 | 7.7488 | 5.5875 | 23.1455 | 22.9285 | 22.6464 | 22.3167 | 21.9637 | 21.5635 | 21.1123 | 20.588 | 19.8251 | 17.5745 | 13.9135 | 10.1009 | 5.1472 | 21.1309 | 20.8776 | 20.5388 | 20.1076 | 19.6503 | 19.155 | 18.6174 | 18.0026 | 17.0112 | 14.1567 | 9.8145 | 6.7229 | 4.9757
|  | BASSETT | FS |  |  | 22.8206 | 22.6094 | 22.3428 | 21.9465 | 21.5297 | 21.0875 | 20.6131 | 20.088 | 19.1844 | 16.2368 | 11.3735 | 7.7488 | 5.5875 | 23.1455 | 22.9285 | 22.6464 | 22.3167 | 21.9637 | 21.5635 | 21.1123 | 20.588 | 19.8251 | 17.5745 | 13.9135 | 10.1009 | 5.1472 | 21.1309 | 20.8776 | 20.5388 | 20.1076 | 19.6503 | 19.155 | 18.6174 | 18.0026 | 17.0112 | 14.1567 | 9.8145 | 6.7229 | 4.9757
NORTH HYDE GSP | NORTH HYDE 22kV | BATH ROAD EAST | MINIMUM HEADROOM | TQ 09097 76885 | YES | 5.5436 | 5.4249 | 5.2494 | 5.0366 | 4.8061 | 4.5558 | 4.2763 | 3.9524 | 3.4988 | 2.0146 | -0.91897 | -3.4319 | -5.2782 | 5.821 | 5.7481 | 5.6562 | 5.5375 | 5.4086 | 5.2682 | 5.1169 | 4.9318 | 4.689 | 3.7339 | 1.7365 | -0.23076 | -2.4658 | 5.2461 | 5.138 | 4.9738 | 4.7769 | 4.5633 | 4.3303 | 4.0791 | 3.786 | 3.3804 | 2.0334 | -0.54382 | -2.6045 | -4.0938
|  | BATH ROAD EAST | CT |  |  | 5.5436 | 5.4249 | 5.2494 | 5.0366 | 4.8061 | 4.5558 | 4.2763 | 3.9524 | 3.4988 | 2.0146 | -0.91897 | -3.4319 | -5.2782 | 5.821 | 5.7481 | 5.6562 | 5.5375 | 5.4086 | 5.2682 | 5.1169 | 4.9318 | 4.689 | 3.7339 | 1.7365 | -0.23076 | -2.4658 | 5.2461 | 5.138 | 4.9738 | 4.7769 | 4.5633 | 4.3303 | 4.0791 | 3.786 | 3.3804 | 2.0334 | -0.54382 | -2.6045 | -4.0938
|  | BATH ROAD EAST | LW |  |  | 5.5436 | 5.4249 | 5.2494 | 5.0366 | 4.8061 | 4.5558 | 4.2763 | 3.9524 | 3.4988 | 2.0146 | -0.91897 | -3.4319 | -5.2782 | 5.821 | 5.7481 | 5.6562 | 5.5375 | 5.4086 | 5.2682 | 5.1169 | 4.9318 | 4.689 | 3.7339 | 1.7365 | -0.23076 | -2.4658 | 5.2461 | 5.138 | 4.9738 | 4.7769 | 4.5633 | 4.3303 | 4.0791 | 3.786 | 3.3804 | 2.0334 | -0.54382 | -2.6045 | -4.0938
|  | BATH ROAD EAST | ST |  |  | 5.5436 | 5.4249 | 5.2494 | 5.0366 | 4.8061 | 4.5558 | 4.2763 | 3.9524 | 3.4988 | 2.0146 | -0.91897 | -3.4319 | -5.2782 | 5.821 | 5.7481 | 5.6562 | 5.5375 | 5.4086 | 5.2682 | 5.1169 | 4.9318 | 4.689 | 3.7339 | 1.7365 | -0.23076 | -2.4658 | 5.2461 | 5.138 | 4.9738 | 4.7769 | 4.5633 | 4.3303 | 4.0791 | 3.786 | 3.3804 | 2.0334 | -0.54382 | -2.6045 | -4.0938
|  | BATH ROAD EAST | FS |  |  | 5.5436 | 5.4249 | 5.2494 | 5.0366 | 4.8061 | 4.5558 | 4.2763 | 3.9524 | 3.4988 | 2.0146 | -0.91897 | -3.4319 | -5.2782 | 5.821 | 5.7481 | 5.6562 | 5.5375 | 5.4086 | 5.2682 | 5.1169 | 4.9318 | 4.689 | 3.7339 | 1.7365 | -0.23076 | -2.4658 | 5.2461 | 5.138 | 4.9738 | 4.7769 | 4.5633 | 4.3303 | 4.0791 | 3.786 | 3.3804 | 2.0334 | -0.54382 | -2.6045 | -4.0938
IVER 132KV | LONGFORD | BATH ROAD WEST | MINIMUM HEADROOM | TQ 05814 76820 | YES | 13.952 | 13.8263 | 13.6872 | 13.5394 | 13.2679 | 12.9023 | 12.504 | 12.0398 | 11.4437 | 9.504 | 6.4079 | 5.7077 | 5.455 | 12.0859 | 11.9772 | 11.8614 | 11.7416 | 11.6138 | 11.4732 | 11.3196 | 11.1342 | 10.8482 | 9.4053 | 7.1617 | 6.7903 | 6.6492 | 13.1487 | 12.9884 | 12.8084 | 12.5883 | 12.2721 | 11.9225 | 11.5415 | 11.0968 | 10.5258 | 8.6561 | 5.5607 | 4.9138 | 4.6841
|  | BATH ROAD WEST | CT |  |  | 13.952 | 13.8263 | 13.6872 | 13.5394 | 13.2679 | 12.9023 | 12.504 | 12.0398 | 11.4437 | 9.504 | 6.4079 | 5.7077 | 5.455 | 12.0859 | 11.9772 | 11.8614 | 11.7416 | 11.6138 | 11.4732 | 11.3196 | 11.1342 | 10.8482 | 9.4053 | 7.1617 | 6.7903 | 6.6492 | 13.1487 | 12.9884 | 12.8084 | 12.5883 | 12.2721 | 11.9225 | 11.5415 | 11.0968 | 10.5258 | 8.6561 | 5.5607 | 4.9138 | 4.6841
|  | BATH ROAD WEST | LW |  |  | 13.952 | 13.8263 | 13.6872 | 13.5394 | 13.2679 | 12.9023 | 12.504 | 12.0398 | 11.4437 | 9.504 | 6.4079 | 5.7077 | 5.455 | 12.0859 | 11.9772 | 11.8614 | 11.7416 | 11.6138 | 11.4732 | 11.3196 | 11.1342 | 10.8482 | 9.4053 | 7.1617 | 6.7903 | 6.6492 | 13.1487 | 12.9884 | 12.8084 | 12.5883 | 12.2721 | 11.9225 | 11.5415 | 11.0968 | 10.5258 | 8.6561 | 5.5607 | 4.9138 | 4.6841
|  | BATH ROAD WEST | ST |  |  | 13.952 | 13.8263 | 13.6872 | 13.5394 | 13.2679 | 12.9023 | 12.504 | 12.0398 | 11.4437 | 9.504 | 6.4079 | 5.7077 | 5.455 | 12.0859 | 11.9772 | 11.8614 | 11.7416 | 11.6138 | 11.4732 | 11.3196 | 11.1342 | 10.8482 | 9.4053 | 7.1617 | 6.7903 | 6.6492 | 13.1487 | 12.9884 | 12.8084 | 12.5883 | 12.2721 | 11.9225 | 11.5415 | 11.0968 | 10.5258 | 8.6561 | 5.5607 | 4.9138 | 4.6841
|  | BATH ROAD WEST | FS |  |  | 13.952 | 13.8263 | 13.6872 | 13.5394 | 13.2679 | 12.9023 | 12.504 | 12.0398 | 11.4437 | 9.504 | 6.4079 | 5.7077 | 5.455 | 12.0859 | 11.9772 | 11.8614 | 11.7416 | 11.6138 | 11.4732 | 11.3196 | 11.1342 | 10.8482 | 9.4053 | 7.1617 | 6.7903 | 6.6492 | 13.1487 | 12.9884 | 12.8084 | 12.5883 | 12.2721 | 11.9225 | 11.5415 | 11.0968 | 10.5258 | 8.6561 | 5.5607 | 4.9138 | 4.6841
IVER 132KV | UPTON BSP | BEACONSFIELD (END B/B) | MINIMUM HEADROOM | SU 93668 91219 | YES | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | BEACONSFIELD (END B/B) | CT |  |  | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | BEACONSFIELD (END B/B) | LW |  |  | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | BEACONSFIELD (END B/B) | ST |  |  | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | BEACONSFIELD (END B/B) | FS |  |  | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IVER 132KV | DENHAM | BEACONSFIELD (MIDDLE B/B) | MINIMUM HEADROOM | SU 93668 91219 | YES | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
|  | BEACONSFIELD (MIDDLE B/B) | CT |  |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
|  | BEACONSFIELD (MIDDLE B/B) | LW |  |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
|  | BEACONSFIELD (MIDDLE B/B) | ST |  |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
|  | BEACONSFIELD (MIDDLE B/B) | FS |  |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
BRAMLEY (ANDO-THAT) | THATCHAM BSP | BEENHAM | MINIMUM HEADROOM | SU 58204 69025 | YES | 9.6086 | 9.4247 | 9.2276 | 8.9531 | 8.6671 | 8.365 | 7.9947 | 7.6113 | 7.0849 | 5.9878 | 4.1265 | 3.529 | 3.4316 | 12.0365 | 11.984 | 11.9232 | 11.8569 | 11.7847 | 11.7047 | 11.4719 | 11.2263 | 10.8963 | 10.3007 | 9.3339 | 8.9711 | 8.7621 | 9.2898 | 9.1165 | 8.93 | 8.676 | 8.411 | 8.1297 | 7.7814 | 7.4203 | 6.9245 | 5.9211 | 4.2391 | 3.7062 | 3.6193
|  | BEENHAM | CT |  |  | 9.6086 | 9.4247 | 9.2276 | 8.9531 | 8.6671 | 8.365 | 7.9947 | 7.6113 | 7.0849 | 5.9878 | 4.1265 | 3.529 | 3.4316 | 12.0365 | 11.984 | 11.9232 | 11.8569 | 11.7847 | 11.7047 | 11.4719 | 11.2263 | 10.8963 | 10.3007 | 9.3339 | 8.9711 | 8.7621 | 9.2898 | 9.1165 | 8.93 | 8.676 | 8.411 | 8.1297 | 7.7814 | 7.4203 | 6.9245 | 5.9211 | 4.2391 | 3.7062 | 3.6193
|  | BEENHAM | LW |  |  | 9.6086 | 9.4247 | 9.2276 | 8.9531 | 8.6671 | 8.365 | 7.9947 | 7.6113 | 7.0849 | 5.9878 | 4.1265 | 3.529 | 3.4316 | 12.0365 | 11.984 | 11.9232 | 11.8569 | 11.7847 | 11.7047 | 11.4719 | 11.2263 | 10.8963 | 10.3007 | 9.3339 | 8.9711 | 8.7621 | 9.2898 | 9.1165 | 8.93 | 8.676 | 8.411 | 8.1297 | 7.7814 | 7.4203 | 6.9245 | 5.9211 | 4.2391 | 3.7062 | 3.6193
|  | BEENHAM | ST |  |  | 9.6086 | 9.4247 | 9.2276 | 8.9531 | 8.6671 | 8.365 | 7.9947 | 7.6113 | 7.0849 | 5.9878 | 4.1265 | 3.529 | 3.4316 | 12.0365 | 11.984 | 11.9232 | 11.8569 | 11.7847 | 11.7047 | 11.4719 | 11.2263 | 10.8963 | 10.3007 | 9.3339 | 8.9711 | 8.7621 | 9.2898 | 9.1165 | 8.93 | 8.676 | 8.411 | 8.1297 | 7.7814 | 7.4203 | 6.9245 | 5.9211 | 4.2391 | 3.7062 | 3.6193
|  | BEENHAM | FS |  |  | 9.6086 | 9.4247 | 9.2276 | 8.9531 | 8.6671 | 8.365 | 7.9947 | 7.6113 | 7.0849 | 5.9878 | 4.1265 | 3.529 | 3.4316 | 12.0365 | 11.984 | 11.9232 | 11.8569 | 11.7847 | 11.7047 | 11.4719 | 11.2263 | 10.8963 | 10.3007 | 9.3339 | 8.9711 | 8.7621 | 9.2898 | 9.1165 | 8.93 | 8.676 | 8.411 | 8.1297 | 7.7814 | 7.4203 | 6.9245 | 5.9211 | 4.2391 | 3.7062 | 3.6193
MANNINGTON GSP | SALISBURY | BEMERTON | MINIMUM HEADROOM | SU 11583 31233 | YES | 26.9322 | 26.552 | 26.062 | 25.6444 | 25.2371 | 24.7858 | 24.2984 | 23.7427 | 22.8709 | 20.5396 | 17.343 | 15.1688 | 14.181 | 29.9625 | 29.7128 | 29.401 | 29.1566 | 28.892 | 28.5938 | 28.2694 | 27.8879 | 27.3303 | 25.8587 | 24.0254 | 22.6744 | 21.4547 | 28.3279 | 27.9967 | 27.5635 | 27.1773 | 26.7955 | 26.3725 | 25.9155 | 25.3902 | 24.5726 | 22.3945 | 19.505 | 17.6303 | 16.7609
|  | BEMERTON | CT |  |  | 26.9322 | 26.552 | 26.062 | 25.6444 | 25.2371 | 24.7858 | 24.2984 | 23.7427 | 22.8709 | 20.5396 | 17.343 | 15.1688 | 14.181 | 29.9625 | 29.7128 | 29.401 | 29.1566 | 28.892 | 28.5938 | 28.2694 | 27.8879 | 27.3303 | 25.8587 | 24.0254 | 22.6744 | 21.4547 | 28.3279 | 27.9967 | 27.5635 | 27.1773 | 26.7955 | 26.3725 | 25.9155 | 25.3902 | 24.5726 | 22.3945 | 19.505 | 17.6303 | 16.7609
|  | BEMERTON | LW |  |  | 26.9322 | 26.552 | 26.062 | 25.6444 | 25.2371 | 24.7858 | 24.2984 | 23.7427 | 22.8709 | 20.5396 | 17.343 | 15.1688 | 14.181 | 29.9625 | 29.7128 | 29.401 | 29.1566 | 28.892 | 28.5938 | 28.2694 | 27.8879 | 27.3303 | 25.8587 | 24.0254 | 22.6744 | 21.4547 | 28.3279 | 27.9967 | 27.5635 | 27.1773 | 26.7955 | 26.3725 | 25.9155 | 25.3902 | 24.5726 | 22.3945 | 19.505 | 17.6303 | 16.7609
|  | BEMERTON | ST |  |  | 26.9322 | 26.552 | 26.062 | 25.6444 | 25.2371 | 24.7858 | 24.2984 | 23.7427 | 22.8709 | 20.5396 | 17.343 | 15.1688 | 14.181 | 29.9625 | 29.7128 | 29.401 | 29.1566 | 28.892 | 28.5938 | 28.2694 | 27.8879 | 27.3303 | 25.8587 | 24.0254 | 22.6744 | 21.4547 | 28.3279 | 27.9967 | 27.5635 | 27.1773 | 26.7955 | 26.3725 | 25.9155 | 25.3902 | 24.5726 | 22.3945 | 19.505 | 17.6303 | 16.7609
|  | BEMERTON | FS |  |  | 26.9322 | 26.552 | 26.062 | 25.6444 | 25.2371 | 24.7858 | 24.2984 | 23.7427 | 22.8709 | 20.5396 | 17.343 | 15.1688 | 14.181 | 29.9625 | 29.7128 | 29.401 | 29.1566 | 28.892 | 28.5938 | 28.2694 | 27.8879 | 27.3303 | 25.8587 | 24.0254 | 22.6744 | 21.4547 | 28.3279 | 27.9967 | 27.5635 | 27.1773 | 26.7955 | 26.3725 | 25.9155 | 25.3902 | 24.5726 | 22.3945 | 19.505 | 17.6303 | 16.7609
COWLEY GSP | COWLEY LOCAL (2 X 45) | BERINSFIELD | MINIMUM HEADROOM | SU 58382 95467 | NO | 17.0374 | 16.5657 | 15.7411 | 14.4389 | 12.6618 | 10.7472 | 8.6061 | 6.234 | 3.4606 | -4.9232 | -15.809 | -19.0872 | -20.2788 | 21.6348 | 21.3004 | 20.771 | 20.033 | 19.0513 | 17.9956 | 16.8172 | 15.5022 | 13.9645 | 9.5966 | 4.1911 | 2.5437 | 1.5621 | 19.082 | 18.6492 | 17.9269 | 16.8257 | 15.3369 | 13.7261 | 11.919 | 9.9043 | 7.5195 | 0.49322 | -8.4993 | -11.3457 | -12.3983
|  | BERINSFIELD | CT |  |  | 17.0374 | 16.5657 | 15.7411 | 14.4389 | 12.6618 | 10.7472 | 8.6061 | 6.234 | 3.4606 | -4.9232 | -15.809 | -19.0872 | -20.2788 | 21.6348 | 21.3004 | 20.771 | 20.033 | 19.0513 | 17.9956 | 16.8172 | 15.5022 | 13.9645 | 9.5966 | 4.1911 | 2.5437 | 1.5621 | 19.082 | 18.6492 | 17.9269 | 16.8257 | 15.3369 | 13.7261 | 11.919 | 9.9043 | 7.5195 | 0.49322 | -8.4993 | -11.3457 | -12.3983
|  | BERINSFIELD | LW |  |  | 17.0374 | 16.5657 | 15.7411 | 14.4389 | 12.6618 | 10.7472 | 8.6061 | 6.234 | 3.4606 | -4.9232 | -15.809 | -19.0872 | -20.2788 | 21.6348 | 21.3004 | 20.771 | 20.033 | 19.0513 | 17.9956 | 16.8172 | 15.5022 | 13.9645 | 9.5966 | 4.1911 | 2.5437 | 1.5621 | 19.082 | 18.6492 | 17.9269 | 16.8257 | 15.3369 | 13.7261 | 11.919 | 9.9043 | 7.5195 | 0.49322 | -8.4993 | -11.3457 | -12.3983
|  | BERINSFIELD | ST |  |  | 17.0374 | 16.5657 | 15.7411 | 14.4389 | 12.6618 | 10.7472 | 8.6061 | 6.234 | 3.4606 | -4.9232 | -15.809 | -19.0872 | -20.2788 | 21.6348 | 21.3004 | 20.771 | 20.033 | 19.0513 | 17.9956 | 16.8172 | 15.5022 | 13.9645 | 9.5966 | 4.1911 | 2.5437 | 1.5621 | 19.082 | 18.6492 | 17.9269 | 16.8257 | 15.3369 | 13.7261 | 11.919 | 9.9043 | 7.5195 | 0.49322 | -8.4993 | -11.3457 | -12.3983
|  | BERINSFIELD | FS |  |  | 17.0374 | 16.5657 | 15.7411 | 14.4389 | 12.6618 | 10.7472 | 8.6061 | 6.234 | 3.4606 | -4.9232 | -15.809 | -19.0872 | -20.2788 | 21.6348 | 21.3004 | 20.771 | 20.033 | 19.0513 | 17.9956 | 16.8172 | 15.5022 | 13.9645 | 9.5966 | 4.1911 | 2.5437 | 1.5621 | 19.082 | 18.6492 | 17.9269 | 16.8257 | 15.3369 | 13.7261 | 11.919 | 9.9043 | 7.5195 | 0.49322 | -8.4993 | -11.3457 | -12.3983
NURSLING GSP | SOUTHAMPTON (2 X 60) | BEVOIS VALLEY | MINIMUM HEADROOM | SU 42648 13187 | YES | 13.6799 | 13.4903 | 13.2614 | 12.8843 | 12.5286 | 12.1496 | 11.7122 | 11.1896 | 10.315 | 6.988 | 1.2959 | -2.4213 | -4.6517 | 19.1425 | 18.9198 | 18.6493 | 18.1272 | 17.5648 | 16.9672 | 16.2863 | 15.5168 | 14.5947 | 11.5821 | 5.2257 | -2.4658 | -13.7259 | 16.4531 | 16.2791 | 16.0687 | 15.4782 | 14.955 | 14.4307 | 13.8391 | 13.1779 | 12.2753 | 9.5288 | 4.4142 | 1.2015 | -0.65575
|  | BEVOIS VALLEY | CT |  |  | 13.6799 | 13.4903 | 13.2614 | 12.8843 | 12.5286 | 12.1496 | 11.7122 | 11.1896 | 10.315 | 6.988 | 1.2959 | -2.4213 | -4.6517 | 19.1425 | 18.9198 | 18.6493 | 18.1272 | 17.5648 | 16.9672 | 16.2863 | 15.5168 | 14.5947 | 11.5821 | 5.2257 | -2.4658 | -13.7259 | 16.4531 | 16.2791 | 16.0687 | 15.4782 | 14.955 | 14.4307 | 13.8391 | 13.1779 | 12.2753 | 9.5288 | 4.4142 | 1.2015 | -0.65575
|  | BEVOIS VALLEY | LW |  |  | 13.6799 | 13.4903 | 13.2614 | 12.8843 | 12.5286 | 12.1496 | 11.7122 | 11.1896 | 10.315 | 6.988 | 1.2959 | -2.4213 | -4.6517 | 19.1425 | 18.9198 | 18.6493 | 18.1272 | 17.5648 | 16.9672 | 16.2863 | 15.5168 | 14.5947 | 11.5821 | 5.2257 | -2.4658 | -13.7259 | 16.4531 | 16.2791 | 16.0687 | 15.4782 | 14.955 | 14.4307 | 13.8391 | 13.1779 | 12.2753 | 9.5288 | 4.4142 | 1.2015 | -0.65575
|  | BEVOIS VALLEY | ST |  |  | 13.6799 | 13.4903 | 13.2614 | 12.8843 | 12.5286 | 12.1496 | 11.7122 | 11.1896 | 10.315 | 6.988 | 1.2959 | -2.4213 | -4.6517 | 19.1425 | 18.9198 | 18.6493 | 18.1272 | 17.5648 | 16.9672 | 16.2863 | 15.5168 | 14.5947 | 11.5821 | 5.2257 | -2.4658 | -13.7259 | 16.4531 | 16.2791 | 16.0687 | 15.4782 | 14.955 | 14.4307 | 13.8391 | 13.1779 | 12.2753 | 9.5288 | 4.4142 | 1.2015 | -0.65575
|  | BEVOIS VALLEY | FS |  |  | 13.6799 | 13.4903 | 13.2614 | 12.8843 | 12.5286 | 12.1496 | 11.7122 | 11.1896 | 10.315 | 6.988 | 1.2959 | -2.4213 | -4.6517 | 19.1425 | 18.9198 | 18.6493 | 18.1272 | 17.5648 | 16.9672 | 16.2863 | 15.5168 | 14.5947 | 11.5821 | 5.2257 | -2.4658 | -13.7259 | 16.4531 | 16.2791 | 16.0687 | 15.4782 | 14.955 | 14.4307 | 13.8391 | 13.1779 | 12.2753 | 9.5288 | 4.4142 | 1.2015 | -0.65575
EAST CLAYDON GSP | BICESTER NORTH BSP | BICESTER | MINIMUM HEADROOM | SP 58381 21988 | NO | 36.3428 | 34.8671 | 33.2338 | 30.756 | 28.2101 | 25.5872 | 22.713 | 19.4218 | 14.9786 | 6.7643 | -4.2598 | -11.0758 | -14.127 | 35.503 | 34.5724 | 33.5091 | 32.0701 | 30.5804 | 29.0176 | 27.2894 | 25.2749 | 22.6013 | 17.5477 | 11.2318 | 7.1239 | 3.7926 | 34.3631 | 33.1335 | 31.7504 | 29.6379 | 27.4556 | 25.2061 | 22.7338 | 19.8949 | 15.9585 | 8.4326 | -1.648 | -7.9758 | -10.6555
|  | BICESTER | CT |  |  | 36.3428 | 34.8671 | 33.2338 | 30.756 | 28.2101 | 25.5872 | 22.713 | 19.4218 | 14.9786 | 6.7643 | -4.2598 | -11.0758 | -14.127 | 35.503 | 34.5724 | 33.5091 | 32.0701 | 30.5804 | 29.0176 | 27.2894 | 25.2749 | 22.6013 | 17.5477 | 11.2318 | 7.1239 | 3.7926 | 34.3631 | 33.1335 | 31.7504 | 29.6379 | 27.4556 | 25.2061 | 22.7338 | 19.8949 | 15.9585 | 8.4326 | -1.648 | -7.9758 | -10.6555
|  | BICESTER | LW |  |  | 36.3428 | 34.8671 | 33.2338 | 30.756 | 28.2101 | 25.5872 | 22.713 | 19.4218 | 14.9786 | 6.7643 | -4.2598 | -11.0758 | -14.127 | 35.503 | 34.5724 | 33.5091 | 32.0701 | 30.5804 | 29.0176 | 27.2894 | 25.2749 | 22.6013 | 17.5477 | 11.2318 | 7.1239 | 3.7926 | 34.3631 | 33.1335 | 31.7504 | 29.6379 | 27.4556 | 25.2061 | 22.7338 | 19.8949 | 15.9585 | 8.4326 | -1.648 | -7.9758 | -10.6555
|  | BICESTER | ST |  |  | 36.3428 | 34.8671 | 33.2338 | 30.756 | 28.2101 | 25.5872 | 22.713 | 19.4218 | 14.9786 | 6.7643 | -4.2598 | -11.0758 | -14.127 | 35.503 | 34.5724 | 33.5091 | 32.0701 | 30.5804 | 29.0176 | 27.2894 | 25.2749 | 22.6013 | 17.5477 | 11.2318 | 7.1239 | 3.7926 | 34.3631 | 33.1335 | 31.7504 | 29.6379 | 27.4556 | 25.2061 | 22.7338 | 19.8949 | 15.9585 | 8.4326 | -1.648 | -7.9758 | -10.6555
|  | BICESTER | FS |  |  | 36.3428 | 34.8671 | 33.2338 | 30.756 | 28.2101 | 25.5872 | 22.713 | 19.4218 | 14.9786 | 6.7643 | -4.2598 | -11.0758 | -14.127 | 35.503 | 34.5724 | 33.5091 | 32.0701 | 30.5804 | 29.0176 | 27.2894 | 25.2749 | 22.6013 | 17.5477 | 11.2318 | 7.1239 | 3.7926 | 34.3631 | 33.1335 | 31.7504 | 29.6379 | 27.4556 | 25.2061 | 22.7338 | 19.8949 | 15.9585 | 8.4326 | -1.648 | -7.9758 | -10.6555
EAST CLAYDON GSP | BICESTER NORTH BSP | BICESTER NORTH | MINIMUM HEADROOM |  |  | 16.6188 | -26.1168 | -28.2145 | -31.237 | -34.3712 | -37.6035 | -41.1641 | -45.2313 | -50.5727 | -60.067 | -72.7994 | -80.6332 | -83.9261 | 22.4856 | -19.5268 | -20.8625 | -22.6025 | -24.4174 | -26.3224 | -28.4388 | -30.9007 | -34.0945 | -39.847 | -47.0654 | -51.6362 | -55.2809 | 18.5064 | -23.7162 | -25.2633 | -27.6177 | -30.0704 | -32.6458 | -35.5748 | -39.0797 | -43.8544 | -52.517 | -63.991 | -70.9676 | -73.9759
|  | BICESTER NORTH | CT |  |  | 16.6188 | -26.1168 | -28.2145 | -31.237 | -34.3712 | -37.6035 | -41.1641 | -45.2313 | -50.5727 | -60.067 | -72.7994 | -80.6332 | -83.9261 | 22.4856 | -19.5268 | -20.8625 | -22.6025 | -24.4174 | -26.3224 | -28.4388 | -30.9007 | -34.0945 | -39.847 | -47.0654 | -51.6362 | -55.2809 | 18.5064 | -23.7162 | -25.2633 | -27.6177 | -30.0704 | -32.6458 | -35.5748 | -39.0797 | -43.8544 | -52.517 | -63.991 | -70.9676 | -73.9759
|  | BICESTER NORTH | LW |  |  | 16.6188 | -26.1168 | -28.2145 | -31.237 | -34.3712 | -37.6035 | -41.1641 | -45.2313 | -50.5727 | -60.067 | -72.7994 | -80.6332 | -83.9261 | 22.4856 | -19.5268 | -20.8625 | -22.6025 | -24.4174 | -26.3224 | -28.4388 | -30.9007 | -34.0945 | -39.847 | -47.0654 | -51.6362 | -55.2809 | 18.5064 | -23.7162 | -25.2633 | -27.6177 | -30.0704 | -32.6458 | -35.5748 | -39.0797 | -43.8544 | -52.517 | -63.991 | -70.9676 | -73.9759
|  | BICESTER NORTH | ST |  |  | 16.6188 | -26.1168 | -28.2145 | -31.237 | -34.3712 | -37.6035 | -41.1641 | -45.2313 | -50.5727 | -60.067 | -72.7994 | -80.6332 | -83.9261 | 22.4856 | -19.5268 | -20.8625 | -22.6025 | -24.4174 | -26.3224 | -28.4388 | -30.9007 | -34.0945 | -39.847 | -47.0654 | -51.6362 | -55.2809 | 18.5064 | -23.7162 | -25.2633 | -27.6177 | -30.0704 | -32.6458 | -35.5748 | -39.0797 | -43.8544 | -52.517 | -63.991 | -70.9676 | -73.9759
|  | BICESTER NORTH | FS |  |  | 16.6188 | -26.1168 | -28.2145 | -31.237 | -34.3712 | -37.6035 | -41.1641 | -45.2313 | -50.5727 | -60.067 | -72.7994 | -80.6332 | -83.9261 | 22.4856 | -19.5268 | -20.8625 | -22.6025 | -24.4174 | -26.3224 | -28.4388 | -30.9007 | -34.0945 | -39.847 | -47.0654 | -51.6362 | -55.2809 | 18.5064 | -23.7162 | -25.2633 | -27.6177 | -30.0704 | -32.6458 | -35.5748 | -39.0797 | -43.8544 | -52.517 | -63.991 | -70.9676 | -73.9759
LOVEDEAN GSP | CHICHESTER & HUNSTON | BILLINGSHURST | MINIMUM HEADROOM | TQ 08305 26315 | YES | 1.7763 | 1.5739 | 1.3493 | 1.0394 | 0.7054 | 0.35973 | -0.015128 | -0.45411 | -1.171 | -2.8682 | -5.5418 | -7.3496 | -8.1931 | 4.8126 | 4.6664 | 4.5017 | 4.3033 | 4.0862 | 3.8536 | 3.5985 | 3.2922 | 2.8303 | 1.8081 | 0.37227 | -0.62942 | -1.4033 | 3.032 | 2.8481 | 2.6451 | 2.3499 | 2.0337 | 1.7102 | 1.3609 | 0.95809 | 0.3093 | -1.2684 | -3.7313 | -5.4197 | -6.1788
|  | BILLINGSHURST | CT |  |  | 1.7763 | 1.5739 | 1.3493 | 1.0394 | 0.7054 | 0.35973 | -0.015128 | -0.45411 | -1.171 | -2.8682 | -5.5418 | -7.3496 | -8.1931 | 4.8126 | 4.6664 | 4.5017 | 4.3033 | 4.0862 | 3.8536 | 3.5985 | 3.2922 | 2.8303 | 1.8081 | 0.37227 | -0.62942 | -1.4033 | 3.032 | 2.8481 | 2.6451 | 2.3499 | 2.0337 | 1.7102 | 1.3609 | 0.95809 | 0.3093 | -1.2684 | -3.7313 | -5.4197 | -6.1788
|  | BILLINGSHURST | LW |  |  | 1.7763 | 1.5739 | 1.3493 | 1.0394 | 0.7054 | 0.35973 | -0.015128 | -0.45411 | -1.171 | -2.8682 | -5.5418 | -7.3496 | -8.1931 | 4.8126 | 4.6664 | 4.5017 | 4.3033 | 4.0862 | 3.8536 | 3.5985 | 3.2922 | 2.8303 | 1.8081 | 0.37227 | -0.62942 | -1.4033 | 3.032 | 2.8481 | 2.6451 | 2.3499 | 2.0337 | 1.7102 | 1.3609 | 0.95809 | 0.3093 | -1.2684 | -3.7313 | -5.4197 | -6.1788
|  | BILLINGSHURST | ST |  |  | 1.7763 | 1.5739 | 1.3493 | 1.0394 | 0.7054 | 0.35973 | -0.015128 | -0.45411 | -1.171 | -2.8682 | -5.5418 | -7.3496 | -8.1931 | 4.8126 | 4.6664 | 4.5017 | 4.3033 | 4.0862 | 3.8536 | 3.5985 | 3.2922 | 2.8303 | 1.8081 | 0.37227 | -0.62942 | -1.4033 | 3.032 | 2.8481 | 2.6451 | 2.3499 | 2.0337 | 1.7102 | 1.3609 | 0.95809 | 0.3093 | -1.2684 | -3.7313 | -5.4197 | -6.1788
|  | BILLINGSHURST | FS |  |  | 1.7763 | 1.5739 | 1.3493 | 1.0394 | 0.7054 | 0.35973 | -0.015128 | -0.45411 | -1.171 | -2.8682 | -5.5418 | -7.3496 | -8.1931 | 4.8126 | 4.6664 | 4.5017 | 4.3033 | 4.0862 | 3.8536 | 3.5985 | 3.2922 | 2.8303 | 1.8081 | 0.37227 | -0.62942 | -1.4033 | 3.032 | 2.8481 | 2.6451 | 2.3499 | 2.0337 | 1.7102 | 1.3609 | 0.95809 | 0.3093 | -1.2684 | -3.7313 | -5.4197 | -6.1788
LOVEDEAN GSP | CHICHESTER & HUNSTON | BILSHAM | MINIMUM HEADROOM | SU 97366 01594 | YES | 20.742 | 19.6949 | 18.3344 | 16.6966 | 14.8996 | 13.1218 | 11.2457 | 9.2375 | 6.8971 | 0.57943 | -5.57 | -9.2072 | -10.8575 | 25.0137 | 24.3897 | 23.5707 | 22.639 | 21.6203 | 20.6015 | 19.5223 | 18.3364 | 16.9464 | 13.3442 | 9.8922 | 7.5716 | 5.5866 | 23.7474 | 22.8798 | 21.7326 | 20.3741 | 18.8483 | 17.3246 | 15.7093 | 13.9586 | 11.8748 | 6.3397 | 0.88246 | -2.3367 | -3.7478
|  | BILSHAM | CT |  |  | 20.742 | 19.6949 | 18.3344 | 16.6966 | 14.8996 | 13.1218 | 11.2457 | 9.2375 | 6.8971 | 0.57943 | -5.57 | -9.2072 | -10.8575 | 25.0137 | 24.3897 | 23.5707 | 22.639 | 21.6203 | 20.6015 | 19.5223 | 18.3364 | 16.9464 | 13.3442 | 9.8922 | 7.5716 | 5.5866 | 23.7474 | 22.8798 | 21.7326 | 20.3741 | 18.8483 | 17.3246 | 15.7093 | 13.9586 | 11.8748 | 6.3397 | 0.88246 | -2.3367 | -3.7478
|  | BILSHAM | LW |  |  | 20.742 | 19.6949 | 18.3344 | 16.6966 | 14.8996 | 13.1218 | 11.2457 | 9.2375 | 6.8971 | 0.57943 | -5.57 | -9.2072 | -10.8575 | 25.0137 | 24.3897 | 23.5707 | 22.639 | 21.6203 | 20.6015 | 19.5223 | 18.3364 | 16.9464 | 13.3442 | 9.8922 | 7.5716 | 5.5866 | 23.7474 | 22.8798 | 21.7326 | 20.3741 | 18.8483 | 17.3246 | 15.7093 | 13.9586 | 11.8748 | 6.3397 | 0.88246 | -2.3367 | -3.7478
|  | BILSHAM | ST |  |  | 20.742 | 19.6949 | 18.3344 | 16.6966 | 14.8996 | 13.1218 | 11.2457 | 9.2375 | 6.8971 | 0.57943 | -5.57 | -9.2072 | -10.8575 | 25.0137 | 24.3897 | 23.5707 | 22.639 | 21.6203 | 20.6015 | 19.5223 | 18.3364 | 16.9464 | 13.3442 | 9.8922 | 7.5716 | 5.5866 | 23.7474 | 22.8798 | 21.7326 | 20.3741 | 18.8483 | 17.3246 | 15.7093 | 13.9586 | 11.8748 | 6.3397 | 0.88246 | -2.3367 | -3.7478
|  | BILSHAM | FS |  |  | 20.742 | 19.6949 | 18.3344 | 16.6966 | 14.8996 | 13.1218 | 11.2457 | 9.2375 | 6.8971 | 0.57943 | -5.57 | -9.2072 | -10.8575 | 25.0137 | 24.3897 | 23.5707 | 22.639 | 21.6203 | 20.6015 | 19.5223 | 18.3364 | 16.9464 | 13.3442 | 9.8922 | 7.5716 | 5.5866 | 23.7474 | 22.8798 | 21.7326 | 20.3741 | 18.8483 | 17.3246 | 15.7093 | 13.9586 | 11.8748 | 6.3397 | 0.88246 | -2.3367 | -3.7478
FAWLEY GSP | COWES & WOOTTON COMMON BSP | BINSTEAD | MINIMUM HEADROOM | SZ 56409 91399 | YES | 13.243 | 13.0901 | 12.8458 | 12.5412 | 12.214 | 11.8593 | 11.4683 | 11.0083 | 10.2848 | 8.2996 | 5.7604 | 4.1988 | 3.4567 | 14.16 | 14.0613 | 13.9069 | 13.7172 | 13.5075 | 13.2785 | 13.0232 | 12.716 | 12.2642 | 11.0293 | 9.5678 | 8.6467 | 7.9204 | 13.4108 | 13.3368 | 13.2342 | 13.1254 | 12.9831 | 12.661 | 12.2891 | 11.8472 | 11.1597 | 9.2861 | 6.9817 | 5.5653 | 4.9184
|  | BINSTEAD | CT |  |  | 13.243 | 13.0901 | 12.8458 | 12.5412 | 12.214 | 11.8593 | 11.4683 | 11.0083 | 10.2848 | 8.2996 | 5.7604 | 4.1988 | 3.4567 | 14.16 | 14.0613 | 13.9069 | 13.7172 | 13.5075 | 13.2785 | 13.0232 | 12.716 | 12.2642 | 11.0293 | 9.5678 | 8.6467 | 7.9204 | 13.4108 | 13.3368 | 13.2342 | 13.1254 | 12.9831 | 12.661 | 12.2891 | 11.8472 | 11.1597 | 9.2861 | 6.9817 | 5.5653 | 4.9184
|  | BINSTEAD | LW |  |  | 13.243 | 13.0901 | 12.8458 | 12.5412 | 12.214 | 11.8593 | 11.4683 | 11.0083 | 10.2848 | 8.2996 | 5.7604 | 4.1988 | 3.4567 | 14.16 | 14.0613 | 13.9069 | 13.7172 | 13.5075 | 13.2785 | 13.0232 | 12.716 | 12.2642 | 11.0293 | 9.5678 | 8.6467 | 7.9204 | 13.4108 | 13.3368 | 13.2342 | 13.1254 | 12.9831 | 12.661 | 12.2891 | 11.8472 | 11.1597 | 9.2861 | 6.9817 | 5.5653 | 4.9184
|  | BINSTEAD | ST |  |  | 13.243 | 13.0901 | 12.8458 | 12.5412 | 12.214 | 11.8593 | 11.4683 | 11.0083 | 10.2848 | 8.2996 | 5.7604 | 4.1988 | 3.4567 | 14.16 | 14.0613 | 13.9069 | 13.7172 | 13.5075 | 13.2785 | 13.0232 | 12.716 | 12.2642 | 11.0293 | 9.5678 | 8.6467 | 7.9204 | 13.4108 | 13.3368 | 13.2342 | 13.1254 | 12.9831 | 12.661 | 12.2891 | 11.8472 | 11.1597 | 9.2861 | 6.9817 | 5.5653 | 4.9184
|  | BINSTEAD | FS |  |  | 13.243 | 13.0901 | 12.8458 | 12.5412 | 12.214 | 11.8593 | 11.4683 | 11.0083 | 10.2848 | 8.2996 | 5.7604 | 4.1988 | 3.4567 | 14.16 | 14.0613 | 13.9069 | 13.7172 | 13.5075 | 13.2785 | 13.0232 | 12.716 | 12.2642 | 11.0293 | 9.5678 | 8.6467 | 7.9204 | 13.4108 | 13.3368 | 13.2342 | 13.1254 | 12.9831 | 12.661 | 12.2891 | 11.8472 | 11.1597 | 9.2861 | 6.9817 | 5.5653 | 4.9184
LOVEDEAN GSP | CHICHESTER & HUNSTON | BIRDHAM | MINIMUM HEADROOM | SZ 81965 99422 | YES | 1.1163 | 0.86003 | 0.49907 | 0.026963 | -0.47067 | -1.0066 | -1.6377 | -2.4135 | -3.6261 | -6.6274 | -10.7446 | -13.3664 | -14.6132 | 3.9647 | 3.7962 | 3.544 | 3.2661 | 2.97 | 2.6443 | 2.2465 | 1.7686 | 1.0323 | -0.67368 | -2.63 | -3.9094 | -4.7647 | 2.1027 | 1.8604 | 1.5107 | 1.0786 | 0.60832 | 0.10016 | -0.50171 | -1.2298 | -2.3647 | -5.1101 | -8.785 | -11.0696 | -12.0944
|  | BIRDHAM | CT |  |  | 1.1163 | 0.86003 | 0.49907 | 0.026963 | -0.47067 | -1.0066 | -1.6377 | -2.4135 | -3.6261 | -6.6274 | -10.7446 | -13.3664 | -14.6132 | 3.9647 | 3.7962 | 3.544 | 3.2661 | 2.97 | 2.6443 | 2.2465 | 1.7686 | 1.0323 | -0.67368 | -2.63 | -3.9094 | -4.7647 | 2.1027 | 1.8604 | 1.5107 | 1.0786 | 0.60832 | 0.10016 | -0.50171 | -1.2298 | -2.3647 | -5.1101 | -8.785 | -11.0696 | -12.0944
|  | BIRDHAM | LW |  |  | 1.1163 | 0.86003 | 0.49907 | 0.026963 | -0.47067 | -1.0066 | -1.6377 | -2.4135 | -3.6261 | -6.6274 | -10.7446 | -13.3664 | -14.6132 | 3.9647 | 3.7962 | 3.544 | 3.2661 | 2.97 | 2.6443 | 2.2465 | 1.7686 | 1.0323 | -0.67368 | -2.63 | -3.9094 | -4.7647 | 2.1027 | 1.8604 | 1.5107 | 1.0786 | 0.60832 | 0.10016 | -0.50171 | -1.2298 | -2.3647 | -5.1101 | -8.785 | -11.0696 | -12.0944
|  | BIRDHAM | ST |  |  | 1.1163 | 0.86003 | 0.49907 | 0.026963 | -0.47067 | -1.0066 | -1.6377 | -2.4135 | -3.6261 | -6.6274 | -10.7446 | -13.3664 | -14.6132 | 3.9647 | 3.7962 | 3.544 | 3.2661 | 2.97 | 2.6443 | 2.2465 | 1.7686 | 1.0323 | -0.67368 | -2.63 | -3.9094 | -4.7647 | 2.1027 | 1.8604 | 1.5107 | 1.0786 | 0.60832 | 0.10016 | -0.50171 | -1.2298 | -2.3647 | -5.1101 | -8.785 | -11.0696 | -12.0944
|  | BIRDHAM | FS |  |  | 1.1163 | 0.86003 | 0.49907 | 0.026963 | -0.47067 | -1.0066 | -1.6377 | -2.4135 | -3.6261 | -6.6274 | -10.7446 | -13.3664 | -14.6132 | 3.9647 | 3.7962 | 3.544 | 3.2661 | 2.97 | 2.6443 | 2.2465 | 1.7686 | 1.0323 | -0.67368 | -2.63 | -3.9094 | -4.7647 | 2.1027 | 1.8604 | 1.5107 | 1.0786 | 0.60832 | 0.10016 | -0.50171 | -1.2298 | -2.3647 | -5.1101 | -8.785 | -11.0696 | -12.0944
BOTLEY WOOD GSP | NETLEY COMMON BSP | BISHOPS WALTHAM | MINIMUM HEADROOM | SU 56691 16683 | YES | 12.1779 | 11.3995 | 10.6957 | 9.7724 | 8.8073 | 7.8039 | 6.6891 | 5.4554 | 3.7281 | 0.11867 | -6.1577 | -10.1845 | -11.9394 | 15.9936 | 15.7144 | 15.4913 | 15.2397 | 14.9744 | 14.6314 | 13.8861 | 13.0392 | 11.9379 | 9.8928 | 6.6372 | 4.5823 | 3.2285 | 13.5538 | 13.164 | 12.8358 | 12.3822 | 11.91 | 11.4312 | 10.9211 | 10.0819 | 8.5357 | 5.4599 | -0.19549 | -3.7562 | -5.1959
|  | BISHOPS WALTHAM | CT |  |  | 12.1779 | 11.3995 | 10.6957 | 9.7724 | 8.8073 | 7.8039 | 6.6891 | 5.4554 | 3.7281 | 0.11867 | -6.1577 | -10.1845 | -11.9394 | 15.9936 | 15.7144 | 15.4913 | 15.2397 | 14.9744 | 14.6314 | 13.8861 | 13.0392 | 11.9379 | 9.8928 | 6.6372 | 4.5823 | 3.2285 | 13.5538 | 13.164 | 12.8358 | 12.3822 | 11.91 | 11.4312 | 10.9211 | 10.0819 | 8.5357 | 5.4599 | -0.19549 | -3.7562 | -5.1959
|  | BISHOPS WALTHAM | LW |  |  | 12.1779 | 11.3995 | 10.6957 | 9.7724 | 8.8073 | 7.8039 | 6.6891 | 5.4554 | 3.7281 | 0.11867 | -6.1577 | -10.1845 | -11.9394 | 15.9936 | 15.7144 | 15.4913 | 15.2397 | 14.9744 | 14.6314 | 13.8861 | 13.0392 | 11.9379 | 9.8928 | 6.6372 | 4.5823 | 3.2285 | 13.5538 | 13.164 | 12.8358 | 12.3822 | 11.91 | 11.4312 | 10.9211 | 10.0819 | 8.5357 | 5.4599 | -0.19549 | -3.7562 | -5.1959
|  | BISHOPS WALTHAM | ST |  |  | 12.1779 | 11.3995 | 10.6957 | 9.7724 | 8.8073 | 7.8039 | 6.6891 | 5.4554 | 3.7281 | 0.11867 | -6.1577 | -10.1845 | -11.9394 | 15.9936 | 15.7144 | 15.4913 | 15.2397 | 14.9744 | 14.6314 | 13.8861 | 13.0392 | 11.9379 | 9.8928 | 6.6372 | 4.5823 | 3.2285 | 13.5538 | 13.164 | 12.8358 | 12.3822 | 11.91 | 11.4312 | 10.9211 | 10.0819 | 8.5357 | 5.4599 | -0.19549 | -3.7562 | -5.1959
|  | BISHOPS WALTHAM | FS |  |  | 12.1779 | 11.3995 | 10.6957 | 9.7724 | 8.8073 | 7.8039 | 6.6891 | 5.4554 | 3.7281 | 0.11867 | -6.1577 | -10.1845 | -11.9394 | 15.9936 | 15.7144 | 15.4913 | 15.2397 | 14.9744 | 14.6314 | 13.8861 | 13.0392 | 11.9379 | 9.8928 | 6.6372 | 4.5823 | 3.2285 | 13.5538 | 13.164 | 12.8358 | 12.3822 | 11.91 | 11.4312 | 10.9211 | 10.0819 | 8.5357 | 5.4599 | -0.19549 | -3.7562 | -5.1959
NURSLING GSP | VELMORE BSP | BISHOPSTOKE | MINIMUM HEADROOM | SU 46463 18472 | YES | 9.9486 | 9.5502 | 9.3009 | 9.0939 | 8.9098 | 8.7305 | 8.5407 | 8.3104 | 8.0917 | 7.3991 | 6.3203 | 6.0186 | 5.8708 | 12.2445 | 11.7658 | 11.4977 | 11.2901 | 11.1179 | 10.9608 | 10.7967 | 10.6005 | 10.4384 | 9.8485 | 8.6766 | 8.3926 | 8.2656 | 10.5053 | 10.2637 | 10.1336 | 10.0426 | 9.9774 | 9.9215 | 9.8214 | 9.5373 | 9.2712 | 8.3682 | 6.8972 | 6.5374 | 6.3767
|  | BISHOPSTOKE | CT |  |  | 9.9486 | 9.5502 | 9.3009 | 9.0939 | 8.9098 | 8.7305 | 8.5407 | 8.3104 | 8.0917 | 7.3991 | 6.3203 | 6.0186 | 5.8708 | 12.2445 | 11.7658 | 11.4977 | 11.2901 | 11.1179 | 10.9608 | 10.7967 | 10.6005 | 10.4384 | 9.8485 | 8.6766 | 8.3926 | 8.2656 | 10.5053 | 10.2637 | 10.1336 | 10.0426 | 9.9774 | 9.9215 | 9.8214 | 9.5373 | 9.2712 | 8.3682 | 6.8972 | 6.5374 | 6.3767
|  | BISHOPSTOKE | LW |  |  | 9.9486 | 9.5502 | 9.3009 | 9.0939 | 8.9098 | 8.7305 | 8.5407 | 8.3104 | 8.0917 | 7.3991 | 6.3203 | 6.0186 | 5.8708 | 12.2445 | 11.7658 | 11.4977 | 11.2901 | 11.1179 | 10.9608 | 10.7967 | 10.6005 | 10.4384 | 9.8485 | 8.6766 | 8.3926 | 8.2656 | 10.5053 | 10.2637 | 10.1336 | 10.0426 | 9.9774 | 9.9215 | 9.8214 | 9.5373 | 9.2712 | 8.3682 | 6.8972 | 6.5374 | 6.3767
|  | BISHOPSTOKE | ST |  |  | 9.9486 | 9.5502 | 9.3009 | 9.0939 | 8.9098 | 8.7305 | 8.5407 | 8.3104 | 8.0917 | 7.3991 | 6.3203 | 6.0186 | 5.8708 | 12.2445 | 11.7658 | 11.4977 | 11.2901 | 11.1179 | 10.9608 | 10.7967 | 10.6005 | 10.4384 | 9.8485 | 8.6766 | 8.3926 | 8.2656 | 10.5053 | 10.2637 | 10.1336 | 10.0426 | 9.9774 | 9.9215 | 9.8214 | 9.5373 | 9.2712 | 8.3682 | 6.8972 | 6.5374 | 6.3767
|  | BISHOPSTOKE | FS |  |  | 9.9486 | 9.5502 | 9.3009 | 9.0939 | 8.9098 | 8.7305 | 8.5407 | 8.3104 | 8.0917 | 7.3991 | 6.3203 | 6.0186 | 5.8708 | 12.2445 | 11.7658 | 11.4977 | 11.2901 | 11.1179 | 10.9608 | 10.7967 | 10.6005 | 10.4384 | 9.8485 | 8.6766 | 8.3926 | 8.2656 | 10.5053 | 10.2637 | 10.1336 | 10.0426 | 9.9774 | 9.9215 | 9.8214 | 9.5373 | 9.2712 | 8.3682 | 6.8972 | 6.5374 | 6.3767
BOTLEY WOOD GSP | NETLEY COMMON BSP | BITTERNE | MINIMUM HEADROOM | SU 45116 13082 | YES | 1.8826 | 1.6991 | 1.4256 | 1.0746 | 0.69933 | 0.29685 | -0.13871 | -0.63959 | -1.45 | -3.882 | -8.5837 | -13.1726 | -16.5532 | 4.9813 | 4.8525 | 4.6537 | 4.4282 | 4.157 | 3.8521 | 3.5213 | 3.1498 | 2.5792 | 0.91321 | -1.8467 | -4.9098 | -8.2492 | 3.6032 | 3.4426 | 3.1936 | 2.8781 | 2.5401 | 2.1695 | 1.7483 | 1.2851 | 0.53425 | -1.7454 | -5.7247 | -9.5628 | -12.3447
|  | BITTERNE | CT |  |  | 1.8826 | 1.6991 | 1.4256 | 1.0746 | 0.69933 | 0.29685 | -0.13871 | -0.63959 | -1.45 | -3.882 | -8.5837 | -13.1726 | -16.5532 | 4.9813 | 4.8525 | 4.6537 | 4.4282 | 4.157 | 3.8521 | 3.5213 | 3.1498 | 2.5792 | 0.91321 | -1.8467 | -4.9098 | -8.2492 | 3.6032 | 3.4426 | 3.1936 | 2.8781 | 2.5401 | 2.1695 | 1.7483 | 1.2851 | 0.53425 | -1.7454 | -5.7247 | -9.5628 | -12.3447
|  | BITTERNE | LW |  |  | 1.8826 | 1.6991 | 1.4256 | 1.0746 | 0.69933 | 0.29685 | -0.13871 | -0.63959 | -1.45 | -3.882 | -8.5837 | -13.1726 | -16.5532 | 4.9813 | 4.8525 | 4.6537 | 4.4282 | 4.157 | 3.8521 | 3.5213 | 3.1498 | 2.5792 | 0.91321 | -1.8467 | -4.9098 | -8.2492 | 3.6032 | 3.4426 | 3.1936 | 2.8781 | 2.5401 | 2.1695 | 1.7483 | 1.2851 | 0.53425 | -1.7454 | -5.7247 | -9.5628 | -12.3447
|  | BITTERNE | ST |  |  | 1.8826 | 1.6991 | 1.4256 | 1.0746 | 0.69933 | 0.29685 | -0.13871 | -0.63959 | -1.45 | -3.882 | -8.5837 | -13.1726 | -16.5532 | 4.9813 | 4.8525 | 4.6537 | 4.4282 | 4.157 | 3.8521 | 3.5213 | 3.1498 | 2.5792 | 0.91321 | -1.8467 | -4.9098 | -8.2492 | 3.6032 | 3.4426 | 3.1936 | 2.8781 | 2.5401 | 2.1695 | 1.7483 | 1.2851 | 0.53425 | -1.7454 | -5.7247 | -9.5628 | -12.3447
|  | BITTERNE | FS |  |  | 1.8826 | 1.6991 | 1.4256 | 1.0746 | 0.69933 | 0.29685 | -0.13871 | -0.63959 | -1.45 | -3.882 | -8.5837 | -13.1726 | -16.5532 | 4.9813 | 4.8525 | 4.6537 | 4.4282 | 4.157 | 3.8521 | 3.5213 | 3.1498 | 2.5792 | 0.91321 | -1.8467 | -4.9098 | -8.2492 | 3.6032 | 3.4426 | 3.1936 | 2.8781 | 2.5401 | 2.1695 | 1.7483 | 1.2851 | 0.53425 | -1.7454 | -5.7247 | -9.5628 | -12.3447
MINETY GSP | STRATTON (2 X 60) | BLACK BOURTON | MINIMUM HEADROOM | SP 28349 03818 | YES | 6.8633 | 6.5704 | 6.3455 | 6.0145 | 5.6581 | 5.3048 | 4.9187 | 4.4956 | 3.8598 | 2.452 | 1.0941 | 0.80078 | 0.65514 | 8.2587 | 8.0806 | 7.9288 | 7.7428 | 7.5396 | 7.3293 | 7.0924 | 6.8154 | 6.4297 | 5.6331 | 4.7262 | 4.1717 | 3.4147 | 8.04 | 7.8552 | 7.7133 | 7.4912 | 7.2566 | 7.025 | 6.7758 | 6.4505 | 5.8578 | 4.5931 | 3.3642 | 3.0993 | 2.9699
|  | BLACK BOURTON | CT |  |  | 6.8633 | 6.5704 | 6.3455 | 6.0145 | 5.6581 | 5.3048 | 4.9187 | 4.4956 | 3.8598 | 2.452 | 1.0941 | 0.80078 | 0.65514 | 8.2587 | 8.0806 | 7.9288 | 7.7428 | 7.5396 | 7.3293 | 7.0924 | 6.8154 | 6.4297 | 5.6331 | 4.7262 | 4.1717 | 3.4147 | 8.04 | 7.8552 | 7.7133 | 7.4912 | 7.2566 | 7.025 | 6.7758 | 6.4505 | 5.8578 | 4.5931 | 3.3642 | 3.0993 | 2.9699
|  | BLACK BOURTON | LW |  |  | 6.8633 | 6.5704 | 6.3455 | 6.0145 | 5.6581 | 5.3048 | 4.9187 | 4.4956 | 3.8598 | 2.452 | 1.0941 | 0.80078 | 0.65514 | 8.2587 | 8.0806 | 7.9288 | 7.7428 | 7.5396 | 7.3293 | 7.0924 | 6.8154 | 6.4297 | 5.6331 | 4.7262 | 4.1717 | 3.4147 | 8.04 | 7.8552 | 7.7133 | 7.4912 | 7.2566 | 7.025 | 6.7758 | 6.4505 | 5.8578 | 4.5931 | 3.3642 | 3.0993 | 2.9699
|  | BLACK BOURTON | ST |  |  | 6.8633 | 6.5704 | 6.3455 | 6.0145 | 5.6581 | 5.3048 | 4.9187 | 4.4956 | 3.8598 | 2.452 | 1.0941 | 0.80078 | 0.65514 | 8.2587 | 8.0806 | 7.9288 | 7.7428 | 7.5396 | 7.3293 | 7.0924 | 6.8154 | 6.4297 | 5.6331 | 4.7262 | 4.1717 | 3.4147 | 8.04 | 7.8552 | 7.7133 | 7.4912 | 7.2566 | 7.025 | 6.7758 | 6.4505 | 5.8578 | 4.5931 | 3.3642 | 3.0993 | 2.9699
|  | BLACK BOURTON | FS |  |  | 6.8633 | 6.5704 | 6.3455 | 6.0145 | 5.6581 | 5.3048 | 4.9187 | 4.4956 | 3.8598 | 2.452 | 1.0941 | 0.80078 | 0.65514 | 8.2587 | 8.0806 | 7.9288 | 7.7428 | 7.5396 | 7.3293 | 7.0924 | 6.8154 | 6.4297 | 5.6331 | 4.7262 | 4.1717 | 3.4147 | 8.04 | 7.8552 | 7.7133 | 7.4912 | 7.2566 | 7.025 | 6.7758 | 6.4505 | 5.8578 | 4.5931 | 3.3642 | 3.0993 | 2.9699
MANNINGTON GSP | LYTCHETT | BLANDFORD | MINIMUM HEADROOM | ST 88810 05536 | YES | 15.5978 | 14.9886 | 14.2329 | 13.2575 | 12.2838 | 11.3012 | 10.2154 | 8.9803 | 7.1793 | 2.9596 | -3.8329 | -8.5003 | -10.6008 | 19.6112 | 19.3012 | 19.0342 | 18.7151 | 18.3391 | 18.002 | 17.5856 | 16.7983 | 15.7299 | 13.2181 | 9.5961 | 7.0625 | 4.9858 | 15.3993 | 14.8416 | 14.1513 | 13.2531 | 12.3379 | 11.4101 | 10.3812 | 9.2228 | 7.5432 | 3.6275 | -2.3643 | -6.2158 | -7.8731
|  | BLANDFORD | CT |  |  | 15.5978 | 14.9886 | 14.2329 | 13.2575 | 12.2838 | 11.3012 | 10.2154 | 8.9803 | 7.1793 | 2.9596 | -3.8329 | -8.5003 | -10.6008 | 19.6112 | 19.3012 | 19.0342 | 18.7151 | 18.3391 | 18.002 | 17.5856 | 16.7983 | 15.7299 | 13.2181 | 9.5961 | 7.0625 | 4.9858 | 15.3993 | 14.8416 | 14.1513 | 13.2531 | 12.3379 | 11.4101 | 10.3812 | 9.2228 | 7.5432 | 3.6275 | -2.3643 | -6.2158 | -7.8731
|  | BLANDFORD | LW |  |  | 15.5978 | 14.9886 | 14.2329 | 13.2575 | 12.2838 | 11.3012 | 10.2154 | 8.9803 | 7.1793 | 2.9596 | -3.8329 | -8.5003 | -10.6008 | 19.6112 | 19.3012 | 19.0342 | 18.7151 | 18.3391 | 18.002 | 17.5856 | 16.7983 | 15.7299 | 13.2181 | 9.5961 | 7.0625 | 4.9858 | 15.3993 | 14.8416 | 14.1513 | 13.2531 | 12.3379 | 11.4101 | 10.3812 | 9.2228 | 7.5432 | 3.6275 | -2.3643 | -6.2158 | -7.8731
|  | BLANDFORD | ST |  |  | 15.5978 | 14.9886 | 14.2329 | 13.2575 | 12.2838 | 11.3012 | 10.2154 | 8.9803 | 7.1793 | 2.9596 | -3.8329 | -8.5003 | -10.6008 | 19.6112 | 19.3012 | 19.0342 | 18.7151 | 18.3391 | 18.002 | 17.5856 | 16.7983 | 15.7299 | 13.2181 | 9.5961 | 7.0625 | 4.9858 | 15.3993 | 14.8416 | 14.1513 | 13.2531 | 12.3379 | 11.4101 | 10.3812 | 9.2228 | 7.5432 | 3.6275 | -2.3643 | -6.2158 | -7.8731
|  | BLANDFORD | FS |  |  | 15.5978 | 14.9886 | 14.2329 | 13.2575 | 12.2838 | 11.3012 | 10.2154 | 8.9803 | 7.1793 | 2.9596 | -3.8329 | -8.5003 | -10.6008 | 19.6112 | 19.3012 | 19.0342 | 18.7151 | 18.3391 | 18.002 | 17.5856 | 16.7983 | 15.7299 | 13.2181 | 9.5961 | 7.0625 | 4.9858 | 15.3993 | 14.8416 | 14.1513 | 13.2531 | 12.3379 | 11.4101 | 10.3812 | 9.2228 | 7.5432 | 3.6275 | -2.3643 | -6.2158 | -7.8731
COWLEY GSP | WITNEY BSP | BLEDINGTON | MINIMUM HEADROOM | SP 25641 22580 | NO | 1.2486 | 1.0961 | 0.92005 | 0.66671 | 0.40144 | 0.12034 | -0.17367 | -0.51369 | -1.004 | -2.0666 | -3.4413 | -3.8013 | -3.8926 | 2.9534 | 2.8656 | 2.7565 | 2.63 | 2.4928 | 2.346 | 2.1879 | 1.9856 | 1.7004 | 1.1974 | 0.67923 | 0.49116 | 0.34693 | 2.1062 | 1.9751 | 1.8187 | 1.6113 | 1.3914 | 1.1388 | 0.86712 | 0.54879 | 0.089945 | -0.87857 | -2.0328 | -2.3319 | -2.407
|  | BLEDINGTON | CT |  |  | 1.2486 | 1.0961 | 0.92005 | 0.66671 | 0.40144 | 0.12034 | -0.17367 | -0.51369 | -1.004 | -2.0666 | -3.4413 | -3.8013 | -3.8926 | 2.9534 | 2.8656 | 2.7565 | 2.63 | 2.4928 | 2.346 | 2.1879 | 1.9856 | 1.7004 | 1.1974 | 0.67923 | 0.49116 | 0.34693 | 2.1062 | 1.9751 | 1.8187 | 1.6113 | 1.3914 | 1.1388 | 0.86712 | 0.54879 | 0.089945 | -0.87857 | -2.0328 | -2.3319 | -2.407
|  | BLEDINGTON | LW |  |  | 1.2486 | 1.0961 | 0.92005 | 0.66671 | 0.40144 | 0.12034 | -0.17367 | -0.51369 | -1.004 | -2.0666 | -3.4413 | -3.8013 | -3.8926 | 2.9534 | 2.8656 | 2.7565 | 2.63 | 2.4928 | 2.346 | 2.1879 | 1.9856 | 1.7004 | 1.1974 | 0.67923 | 0.49116 | 0.34693 | 2.1062 | 1.9751 | 1.8187 | 1.6113 | 1.3914 | 1.1388 | 0.86712 | 0.54879 | 0.089945 | -0.87857 | -2.0328 | -2.3319 | -2.407
|  | BLEDINGTON | ST |  |  | 1.2486 | 1.0961 | 0.92005 | 0.66671 | 0.40144 | 0.12034 | -0.17367 | -0.51369 | -1.004 | -2.0666 | -3.4413 | -3.8013 | -3.8926 | 2.9534 | 2.8656 | 2.7565 | 2.63 | 2.4928 | 2.346 | 2.1879 | 1.9856 | 1.7004 | 1.1974 | 0.67923 | 0.49116 | 0.34693 | 2.1062 | 1.9751 | 1.8187 | 1.6113 | 1.3914 | 1.1388 | 0.86712 | 0.54879 | 0.089945 | -0.87857 | -2.0328 | -2.3319 | -2.407
|  | BLEDINGTON | FS |  |  | 1.2486 | 1.0961 | 0.92005 | 0.66671 | 0.40144 | 0.12034 | -0.17367 | -0.51369 | -1.004 | -2.0666 | -3.4413 | -3.8013 | -3.8926 | 2.9534 | 2.8656 | 2.7565 | 2.63 | 2.4928 | 2.346 | 2.1879 | 1.9856 | 1.7004 | 1.1974 | 0.67923 | 0.49116 | 0.34693 | 2.1062 | 1.9751 | 1.8187 | 1.6113 | 1.3914 | 1.1388 | 0.86712 | 0.54879 | 0.089945 | -0.87857 | -2.0328 | -2.3319 | -2.407
BRAMLEY (FLEE) | ALTON | BORDON | MINIMUM HEADROOM | SU 82256 35269 | YES | 12.4354 | 11.3407 | 10.1593 | 8.9283 | 7.584 | 6.1487 | 4.4786 | 2.5369 | -0.085211 | -6.0462 | -14.1807 | -19.3832 | -21.6953 | 16.7913 | 15.9592 | 15.0662 | 14.2141 | 13.3032 | 12.3183 | 11.1913 | 9.8742 | 8.1906 | 4.5851 | -0.052757 | -2.8962 | -5.0281 | 14.7729 | 13.7399 | 12.6493 | 11.4639 | 10.1791 | 8.8074 | 7.2394 | 5.4301 | 2.9992 | -2.4354 | -9.8184 | -14.2259 | -16.2622
|  | BORDON | CT |  |  | 12.4354 | 11.3407 | 10.1593 | 8.9283 | 7.584 | 6.1487 | 4.4786 | 2.5369 | -0.085211 | -6.0462 | -14.1807 | -19.3832 | -21.6953 | 16.7913 | 15.9592 | 15.0662 | 14.2141 | 13.3032 | 12.3183 | 11.1913 | 9.8742 | 8.1906 | 4.5851 | -0.052757 | -2.8962 | -5.0281 | 14.7729 | 13.7399 | 12.6493 | 11.4639 | 10.1791 | 8.8074 | 7.2394 | 5.4301 | 2.9992 | -2.4354 | -9.8184 | -14.2259 | -16.2622
|  | BORDON | LW |  |  | 12.4354 | 11.3407 | 10.1593 | 8.9283 | 7.584 | 6.1487 | 4.4786 | 2.5369 | -0.085211 | -6.0462 | -14.1807 | -19.3832 | -21.6953 | 16.7913 | 15.9592 | 15.0662 | 14.2141 | 13.3032 | 12.3183 | 11.1913 | 9.8742 | 8.1906 | 4.5851 | -0.052757 | -2.8962 | -5.0281 | 14.7729 | 13.7399 | 12.6493 | 11.4639 | 10.1791 | 8.8074 | 7.2394 | 5.4301 | 2.9992 | -2.4354 | -9.8184 | -14.2259 | -16.2622
|  | BORDON | ST |  |  | 12.4354 | 11.3407 | 10.1593 | 8.9283 | 7.584 | 6.1487 | 4.4786 | 2.5369 | -0.085211 | -6.0462 | -14.1807 | -19.3832 | -21.6953 | 16.7913 | 15.9592 | 15.0662 | 14.2141 | 13.3032 | 12.3183 | 11.1913 | 9.8742 | 8.1906 | 4.5851 | -0.052757 | -2.8962 | -5.0281 | 14.7729 | 13.7399 | 12.6493 | 11.4639 | 10.1791 | 8.8074 | 7.2394 | 5.4301 | 2.9992 | -2.4354 | -9.8184 | -14.2259 | -16.2622
|  | BORDON | FS |  |  | 12.4354 | 11.3407 | 10.1593 | 8.9283 | 7.584 | 6.1487 | 4.4786 | 2.5369 | -0.085211 | -6.0462 | -14.1807 | -19.3832 | -21.6953 | 16.7913 | 15.9592 | 15.0662 | 14.2141 | 13.3032 | 12.3183 | 11.1913 | 9.8742 | 8.1906 | 4.5851 | -0.052757 | -2.8962 | -5.0281 | 14.7729 | 13.7399 | 12.6493 | 11.4639 | 10.1791 | 8.8074 | 7.2394 | 5.4301 | 2.9992 | -2.4354 | -9.8184 | -14.2259 | -16.2622
MELKSHAM GSP | AMESBURY | BOSCOMBE DOWN | MINIMUM HEADROOM | SU 17186 41044 | YES | 21.6009 | 21.4939 | 21.3669 | 21.2553 | 21.1412 | 21.0195 | 20.8851 | 20.5771 | 20.0307 | 18.8627 | 17.1186 | 15.8664 | 15.271 | 18.6556 | 18.5591 | 18.4395 | 18.3241 | 18.2052 | 18.0806 | 17.9433 | 17.7809 | 17.535 | 16.929 | 15.8908 | 15.1486 | 14.5703 | 19.1891 | 19.0703 | 18.9267 | 18.7783 | 18.6283 | 18.4745 | 18.3064 | 18.1158 | 17.8073 | 16.9909 | 15.5217 | 14.5839 | 14.1433
|  | BOSCOMBE DOWN | CT |  |  | 21.6009 | 21.4939 | 21.3669 | 21.2553 | 21.1412 | 21.0195 | 20.8851 | 20.5771 | 20.0307 | 18.8627 | 17.1186 | 15.8664 | 15.271 | 18.6556 | 18.5591 | 18.4395 | 18.3241 | 18.2052 | 18.0806 | 17.9433 | 17.7809 | 17.535 | 16.929 | 15.8908 | 15.1486 | 14.5703 | 19.1891 | 19.0703 | 18.9267 | 18.7783 | 18.6283 | 18.4745 | 18.3064 | 18.1158 | 17.8073 | 16.9909 | 15.5217 | 14.5839 | 14.1433
|  | BOSCOMBE DOWN | LW |  |  | 21.6009 | 21.4939 | 21.3669 | 21.2553 | 21.1412 | 21.0195 | 20.8851 | 20.5771 | 20.0307 | 18.8627 | 17.1186 | 15.8664 | 15.271 | 18.6556 | 18.5591 | 18.4395 | 18.3241 | 18.2052 | 18.0806 | 17.9433 | 17.7809 | 17.535 | 16.929 | 15.8908 | 15.1486 | 14.5703 | 19.1891 | 19.0703 | 18.9267 | 18.7783 | 18.6283 | 18.4745 | 18.3064 | 18.1158 | 17.8073 | 16.9909 | 15.5217 | 14.5839 | 14.1433
|  | BOSCOMBE DOWN | ST |  |  | 21.6009 | 21.4939 | 21.3669 | 21.2553 | 21.1412 | 21.0195 | 20.8851 | 20.5771 | 20.0307 | 18.8627 | 17.1186 | 15.8664 | 15.271 | 18.6556 | 18.5591 | 18.4395 | 18.3241 | 18.2052 | 18.0806 | 17.9433 | 17.7809 | 17.535 | 16.929 | 15.8908 | 15.1486 | 14.5703 | 19.1891 | 19.0703 | 18.9267 | 18.7783 | 18.6283 | 18.4745 | 18.3064 | 18.1158 | 17.8073 | 16.9909 | 15.5217 | 14.5839 | 14.1433
|  | BOSCOMBE DOWN | FS |  |  | 21.6009 | 21.4939 | 21.3669 | 21.2553 | 21.1412 | 21.0195 | 20.8851 | 20.5771 | 20.0307 | 18.8627 | 17.1186 | 15.8664 | 15.271 | 18.6556 | 18.5591 | 18.4395 | 18.3241 | 18.2052 | 18.0806 | 17.9433 | 17.7809 | 17.535 | 16.929 | 15.8908 | 15.1486 | 14.5703 | 19.1891 | 19.0703 | 18.9267 | 18.7783 | 18.6283 | 18.4745 | 18.3064 | 18.1158 | 17.8073 | 16.9909 | 15.5217 | 14.5839 | 14.1433
MANNINGTON GSP | CHRISTCHURCH BSP | BOSCOMBE EAST | MINIMUM HEADROOM | SZ 11636 92447 | YES | 12.9019 | 12.6299 | 12.2516 | 11.7467 | 11.1977 | 10.6308 | 10.0073 | 9.2906 | 8.1652 | 4.8174 | -1.5648 | -6.5659 | -9.5931 | 17.4706 | 17.2887 | 17.0611 | 16.7505 | 16.4136 | 16.0555 | 15.661 | 15.1131 | 14.1928 | 11.3637 | 5.7968 | -0.65112 | -9.6905 | 13.3844 | 13.1587 | 12.8541 | 12.4045 | 11.916 | 11.3696 | 10.7681 | 10.0763 | 8.9841 | 5.784 | 0.20283 | -3.907 | -6.4327
|  | BOSCOMBE EAST | CT |  |  | 12.9019 | 12.6299 | 12.2516 | 11.7467 | 11.1977 | 10.6308 | 10.0073 | 9.2906 | 8.1652 | 4.8174 | -1.5648 | -6.5659 | -9.5931 | 17.4706 | 17.2887 | 17.0611 | 16.7505 | 16.4136 | 16.0555 | 15.661 | 15.1131 | 14.1928 | 11.3637 | 5.7968 | -0.65112 | -9.6905 | 13.3844 | 13.1587 | 12.8541 | 12.4045 | 11.916 | 11.3696 | 10.7681 | 10.0763 | 8.9841 | 5.784 | 0.20283 | -3.907 | -6.4327
|  | BOSCOMBE EAST | LW |  |  | 12.9019 | 12.6299 | 12.2516 | 11.7467 | 11.1977 | 10.6308 | 10.0073 | 9.2906 | 8.1652 | 4.8174 | -1.5648 | -6.5659 | -9.5931 | 17.4706 | 17.2887 | 17.0611 | 16.7505 | 16.4136 | 16.0555 | 15.661 | 15.1131 | 14.1928 | 11.3637 | 5.7968 | -0.65112 | -9.6905 | 13.3844 | 13.1587 | 12.8541 | 12.4045 | 11.916 | 11.3696 | 10.7681 | 10.0763 | 8.9841 | 5.784 | 0.20283 | -3.907 | -6.4327
|  | BOSCOMBE EAST | ST |  |  | 12.9019 | 12.6299 | 12.2516 | 11.7467 | 11.1977 | 10.6308 | 10.0073 | 9.2906 | 8.1652 | 4.8174 | -1.5648 | -6.5659 | -9.5931 | 17.4706 | 17.2887 | 17.0611 | 16.7505 | 16.4136 | 16.0555 | 15.661 | 15.1131 | 14.1928 | 11.3637 | 5.7968 | -0.65112 | -9.6905 | 13.3844 | 13.1587 | 12.8541 | 12.4045 | 11.916 | 11.3696 | 10.7681 | 10.0763 | 8.9841 | 5.784 | 0.20283 | -3.907 | -6.4327
|  | BOSCOMBE EAST | FS |  |  | 12.9019 | 12.6299 | 12.2516 | 11.7467 | 11.1977 | 10.6308 | 10.0073 | 9.2906 | 8.1652 | 4.8174 | -1.5648 | -6.5659 | -9.5931 | 17.4706 | 17.2887 | 17.0611 | 16.7505 | 16.4136 | 16.0555 | 15.661 | 15.1131 | 14.1928 | 11.3637 | 5.7968 | -0.65112 | -9.6905 | 13.3844 | 13.1587 | 12.8541 | 12.4045 | 11.916 | 11.3696 | 10.7681 | 10.0763 | 8.9841 | 5.784 | 0.20283 | -3.907 | -6.4327
EALING GSP | EALING 22kV | BOSTON MANOR ROAD | MINIMUM HEADROOM |  |  | 14.2024 | 13.8327 | 13.6001 | 13.2932 | 13.0017 | 12.6998 | 12.399 | 12.0213 | 11.5722 | 11.0731 | 10.4704 | 9.7844 | 9.4227 | 11.4174 | 11.1814 | 10.9575 | 10.7194 | 10.5186 | 10.2727 | 10.0096 | 9.7169 | 9.3512 | 8.9614 | 8.5559 | 8.0962 | 7.8246 | 16.4843 | 16.2308 | 15.9957 | 15.7388 | 15.5284 | 15.3157 | 15.0732 | 14.739 | 14.2541 | 13.7391 | 13.1541 | 12.5021 | 12.1785
|  | BOSTON MANOR ROAD | CT |  |  | 14.2024 | 13.8327 | 13.6001 | 13.2932 | 13.0017 | 12.6998 | 12.399 | 12.0213 | 11.5722 | 11.0731 | 10.4704 | 9.7844 | 9.4227 | 11.4174 | 11.1814 | 10.9575 | 10.7194 | 10.5186 | 10.2727 | 10.0096 | 9.7169 | 9.3512 | 8.9614 | 8.5559 | 8.0962 | 7.8246 | 16.4843 | 16.2308 | 15.9957 | 15.7388 | 15.5284 | 15.3157 | 15.0732 | 14.739 | 14.2541 | 13.7391 | 13.1541 | 12.5021 | 12.1785
|  | BOSTON MANOR ROAD | LW |  |  | 14.2024 | 13.8327 | 13.6001 | 13.2932 | 13.0017 | 12.6998 | 12.399 | 12.0213 | 11.5722 | 11.0731 | 10.4704 | 9.7844 | 9.4227 | 11.4174 | 11.1814 | 10.9575 | 10.7194 | 10.5186 | 10.2727 | 10.0096 | 9.7169 | 9.3512 | 8.9614 | 8.5559 | 8.0962 | 7.8246 | 16.4843 | 16.2308 | 15.9957 | 15.7388 | 15.5284 | 15.3157 | 15.0732 | 14.739 | 14.2541 | 13.7391 | 13.1541 | 12.5021 | 12.1785
|  | BOSTON MANOR ROAD | ST |  |  | 14.2024 | 13.8327 | 13.6001 | 13.2932 | 13.0017 | 12.6998 | 12.399 | 12.0213 | 11.5722 | 11.0731 | 10.4704 | 9.7844 | 9.4227 | 11.4174 | 11.1814 | 10.9575 | 10.7194 | 10.5186 | 10.2727 | 10.0096 | 9.7169 | 9.3512 | 8.9614 | 8.5559 | 8.0962 | 7.8246 | 16.4843 | 16.2308 | 15.9957 | 15.7388 | 15.5284 | 15.3157 | 15.0732 | 14.739 | 14.2541 | 13.7391 | 13.1541 | 12.5021 | 12.1785
|  | BOSTON MANOR ROAD | FS |  |  | 14.2024 | 13.8327 | 13.6001 | 13.2932 | 13.0017 | 12.6998 | 12.399 | 12.0213 | 11.5722 | 11.0731 | 10.4704 | 9.7844 | 9.4227 | 11.4174 | 11.1814 | 10.9575 | 10.7194 | 10.5186 | 10.2727 | 10.0096 | 9.7169 | 9.3512 | 8.9614 | 8.5559 | 8.0962 | 7.8246 | 16.4843 | 16.2308 | 15.9957 | 15.7388 | 15.5284 | 15.3157 | 15.0732 | 14.739 | 14.2541 | 13.7391 | 13.1541 | 12.5021 | 12.1785
MANNINGTON GSP | BOURNEMOUTH | BOURNE VALLEY | MINIMUM HEADROOM | SZ 06207 92415 | YES | 12.9174 | 12.3389 | 11.4854 | 10.3619 | 9.1455 | 7.8645 | 6.4768 | 4.9261 | 2.5034 | -4.761 | -16.2968 | -24.8045 | -29.9173 | 16.8208 | 16.3842 | 15.7353 | 14.9589 | 14.1081 | 13.1664 | 12.1156 | 10.9247 | 9.2357 | 4.1287 | -3.5479 | -10.3414 | -17.883 | 13.576 | 13.1034 | 12.4097 | 11.4418 | 10.3959 | 9.2593 | 8.0092 | 6.6204 | 4.4307 | -2.2035 | -12.6228 | -20.2903 | -24.7003
|  | BOURNE VALLEY | CT |  |  | 12.9174 | 12.3389 | 11.4854 | 10.3619 | 9.1455 | 7.8645 | 6.4768 | 4.9261 | 2.5034 | -4.761 | -16.2968 | -24.8045 | -29.9173 | 16.8208 | 16.3842 | 15.7353 | 14.9589 | 14.1081 | 13.1664 | 12.1156 | 10.9247 | 9.2357 | 4.1287 | -3.5479 | -10.3414 | -17.883 | 13.576 | 13.1034 | 12.4097 | 11.4418 | 10.3959 | 9.2593 | 8.0092 | 6.6204 | 4.4307 | -2.2035 | -12.6228 | -20.2903 | -24.7003
|  | BOURNE VALLEY | LW |  |  | 12.9174 | 12.3389 | 11.4854 | 10.3619 | 9.1455 | 7.8645 | 6.4768 | 4.9261 | 2.5034 | -4.761 | -16.2968 | -24.8045 | -29.9173 | 16.8208 | 16.3842 | 15.7353 | 14.9589 | 14.1081 | 13.1664 | 12.1156 | 10.9247 | 9.2357 | 4.1287 | -3.5479 | -10.3414 | -17.883 | 13.576 | 13.1034 | 12.4097 | 11.4418 | 10.3959 | 9.2593 | 8.0092 | 6.6204 | 4.4307 | -2.2035 | -12.6228 | -20.2903 | -24.7003
|  | BOURNE VALLEY | ST |  |  | 12.9174 | 12.3389 | 11.4854 | 10.3619 | 9.1455 | 7.8645 | 6.4768 | 4.9261 | 2.5034 | -4.761 | -16.2968 | -24.8045 | -29.9173 | 16.8208 | 16.3842 | 15.7353 | 14.9589 | 14.1081 | 13.1664 | 12.1156 | 10.9247 | 9.2357 | 4.1287 | -3.5479 | -10.3414 | -17.883 | 13.576 | 13.1034 | 12.4097 | 11.4418 | 10.3959 | 9.2593 | 8.0092 | 6.6204 | 4.4307 | -2.2035 | -12.6228 | -20.2903 | -24.7003
|  | BOURNE VALLEY | FS |  |  | 12.9174 | 12.3389 | 11.4854 | 10.3619 | 9.1455 | 7.8645 | 6.4768 | 4.9261 | 2.5034 | -4.761 | -16.2968 | -24.8045 | -29.9173 | 16.8208 | 16.3842 | 15.7353 | 14.9589 | 14.1081 | 13.1664 | 12.1156 | 10.9247 | 9.2357 | 4.1287 | -3.5479 | -10.3414 | -17.883 | 13.576 | 13.1034 | 12.4097 | 11.4418 | 10.3959 | 9.2593 | 8.0092 | 6.6204 | 4.4307 | -2.2035 | -12.6228 | -20.2903 | -24.7003
MANNINGTON GSP | SHAFTESBURY BSP | BOURTON | MINIMUM HEADROOM | ST 77363 30262 | YES | 1.6233 | 1.3823 | 1.0262 | 0.55994 | 0.063136 | -0.48087 | -1.0707 | -1.7446 | -2.7911 | -5.3183 | -9.045 | -11.5579 | -12.6198 | 4.8805 | 4.7231 | 4.4717 | 4.1894 | 3.8835 | 3.547 | 3.1744 | 2.7333 | 2.0758 | 0.59515 | -1.2466 | -2.4486 | -3.203 | 2.6028 | 2.3928 | 2.0977 | 1.6866 | 1.2511 | 0.77448 | 0.26213 | -0.3165 | -1.222 | -3.5517 | -7.1126 | -9.585 | -10.5934
|  | BOURTON | CT |  |  | 1.6233 | 1.3823 | 1.0262 | 0.55994 | 0.063136 | -0.48087 | -1.0707 | -1.7446 | -2.7911 | -5.3183 | -9.045 | -11.5579 | -12.6198 | 4.8805 | 4.7231 | 4.4717 | 4.1894 | 3.8835 | 3.547 | 3.1744 | 2.7333 | 2.0758 | 0.59515 | -1.2466 | -2.4486 | -3.203 | 2.6028 | 2.3928 | 2.0977 | 1.6866 | 1.2511 | 0.77448 | 0.26213 | -0.3165 | -1.222 | -3.5517 | -7.1126 | -9.585 | -10.5934
|  | BOURTON | LW |  |  | 1.6233 | 1.3823 | 1.0262 | 0.55994 | 0.063136 | -0.48087 | -1.0707 | -1.7446 | -2.7911 | -5.3183 | -9.045 | -11.5579 | -12.6198 | 4.8805 | 4.7231 | 4.4717 | 4.1894 | 3.8835 | 3.547 | 3.1744 | 2.7333 | 2.0758 | 0.59515 | -1.2466 | -2.4486 | -3.203 | 2.6028 | 2.3928 | 2.0977 | 1.6866 | 1.2511 | 0.77448 | 0.26213 | -0.3165 | -1.222 | -3.5517 | -7.1126 | -9.585 | -10.5934
|  | BOURTON | ST |  |  | 1.6233 | 1.3823 | 1.0262 | 0.55994 | 0.063136 | -0.48087 | -1.0707 | -1.7446 | -2.7911 | -5.3183 | -9.045 | -11.5579 | -12.6198 | 4.8805 | 4.7231 | 4.4717 | 4.1894 | 3.8835 | 3.547 | 3.1744 | 2.7333 | 2.0758 | 0.59515 | -1.2466 | -2.4486 | -3.203 | 2.6028 | 2.3928 | 2.0977 | 1.6866 | 1.2511 | 0.77448 | 0.26213 | -0.3165 | -1.222 | -3.5517 | -7.1126 | -9.585 | -10.5934
|  | BOURTON | FS |  |  | 1.6233 | 1.3823 | 1.0262 | 0.55994 | 0.063136 | -0.48087 | -1.0707 | -1.7446 | -2.7911 | -5.3183 | -9.045 | -11.5579 | -12.6198 | 4.8805 | 4.7231 | 4.4717 | 4.1894 | 3.8835 | 3.547 | 3.1744 | 2.7333 | 2.0758 | 0.59515 | -1.2466 | -2.4486 | -3.203 | 2.6028 | 2.3928 | 2.0977 | 1.6866 | 1.2511 | 0.77448 | 0.26213 | -0.3165 | -1.222 | -3.5517 | -7.1126 | -9.585 | -10.5934
MANNINGTON GSP | WAREHAM | BOVINGTON | MINIMUM HEADROOM | SY 83933 87831 | YES | 3.9678 | 3.8112 | 3.516 | 3.1319 | 2.6792 | 2.202 | 1.6925 | 1.1628 | 0.54487 | -1.0336 | -2.6122 | -3.5325 | -3.9597 | 5.6617 | 5.5636 | 5.3672 | 5.1269 | 4.8532 | 4.5557 | 4.2483 | 3.9301 | 3.5629 | 2.6166 | 1.6724 | 1.1632 | 0.86607 | 5.1356 | 4.9895 | 4.7107 | 4.34 | 3.9111 | 3.4502 | 2.9639 | 2.4597 | 1.8611 | 0.30347 | -1.378 | -2.3104 | -2.712
|  | BOVINGTON | CT |  |  | 3.9678 | 3.8112 | 3.516 | 3.1319 | 2.6792 | 2.202 | 1.6925 | 1.1628 | 0.54487 | -1.0336 | -2.6122 | -3.5325 | -3.9597 | 5.6617 | 5.5636 | 5.3672 | 5.1269 | 4.8532 | 4.5557 | 4.2483 | 3.9301 | 3.5629 | 2.6166 | 1.6724 | 1.1632 | 0.86607 | 5.1356 | 4.9895 | 4.7107 | 4.34 | 3.9111 | 3.4502 | 2.9639 | 2.4597 | 1.8611 | 0.30347 | -1.378 | -2.3104 | -2.712
|  | BOVINGTON | LW |  |  | 3.9678 | 3.8112 | 3.516 | 3.1319 | 2.6792 | 2.202 | 1.6925 | 1.1628 | 0.54487 | -1.0336 | -2.6122 | -3.5325 | -3.9597 | 5.6617 | 5.5636 | 5.3672 | 5.1269 | 4.8532 | 4.5557 | 4.2483 | 3.9301 | 3.5629 | 2.6166 | 1.6724 | 1.1632 | 0.86607 | 5.1356 | 4.9895 | 4.7107 | 4.34 | 3.9111 | 3.4502 | 2.9639 | 2.4597 | 1.8611 | 0.30347 | -1.378 | -2.3104 | -2.712
|  | BOVINGTON | ST |  |  | 3.9678 | 3.8112 | 3.516 | 3.1319 | 2.6792 | 2.202 | 1.6925 | 1.1628 | 0.54487 | -1.0336 | -2.6122 | -3.5325 | -3.9597 | 5.6617 | 5.5636 | 5.3672 | 5.1269 | 4.8532 | 4.5557 | 4.2483 | 3.9301 | 3.5629 | 2.6166 | 1.6724 | 1.1632 | 0.86607 | 5.1356 | 4.9895 | 4.7107 | 4.34 | 3.9111 | 3.4502 | 2.9639 | 2.4597 | 1.8611 | 0.30347 | -1.378 | -2.3104 | -2.712
|  | BOVINGTON | FS |  |  | 3.9678 | 3.8112 | 3.516 | 3.1319 | 2.6792 | 2.202 | 1.6925 | 1.1628 | 0.54487 | -1.0336 | -2.6122 | -3.5325 | -3.9597 | 5.6617 | 5.5636 | 5.3672 | 5.1269 | 4.8532 | 4.5557 | 4.2483 | 3.9301 | 3.5629 | 2.6166 | 1.6724 | 1.1632 | 0.86607 | 5.1356 | 4.9895 | 4.7107 | 4.34 | 3.9111 | 3.4502 | 2.9639 | 2.4597 | 1.8611 | 0.30347 | -1.378 | -2.3104 | -2.712
AMERSHAM | LOUDWATER BSP | BOWERDEAN | MINIMUM HEADROOM | SU 87718 93880 | YES | 1.4221 | 0.37343 | -0.57005 | -1.6363 | -2.7792 | -4.0099 | -5.3516 | -6.8616 | -9.195 | -13.9536 | -21.4415 | -26.7646 | -29.3984 | 8.8624 | 8.1565 | 7.4624 | 6.7523 | 5.9797 | 5.1247 | 4.1643 | 3.0499 | 1.4667 | -1.5157 | -5.8194 | -9.2843 | -12.5118 | 5.2776 | 4.397 | 3.5827 | 2.6211 | 1.5573 | 0.40376 | -0.86903 | -2.3162 | -4.5324 | -8.9449 | -15.6599 | -20.3555 | -22.6522
|  | BOWERDEAN | CT |  |  | 1.4221 | 0.37343 | -0.57005 | -1.6363 | -2.7792 | -4.0099 | -5.3516 | -6.8616 | -9.195 | -13.9536 | -21.4415 | -26.7646 | -29.3984 | 8.8624 | 8.1565 | 7.4624 | 6.7523 | 5.9797 | 5.1247 | 4.1643 | 3.0499 | 1.4667 | -1.5157 | -5.8194 | -9.2843 | -12.5118 | 5.2776 | 4.397 | 3.5827 | 2.6211 | 1.5573 | 0.40376 | -0.86903 | -2.3162 | -4.5324 | -8.9449 | -15.6599 | -20.3555 | -22.6522
|  | BOWERDEAN | LW |  |  | 1.4221 | 0.37343 | -0.57005 | -1.6363 | -2.7792 | -4.0099 | -5.3516 | -6.8616 | -9.195 | -13.9536 | -21.4415 | -26.7646 | -29.3984 | 8.8624 | 8.1565 | 7.4624 | 6.7523 | 5.9797 | 5.1247 | 4.1643 | 3.0499 | 1.4667 | -1.5157 | -5.8194 | -9.2843 | -12.5118 | 5.2776 | 4.397 | 3.5827 | 2.6211 | 1.5573 | 0.40376 | -0.86903 | -2.3162 | -4.5324 | -8.9449 | -15.6599 | -20.3555 | -22.6522
|  | BOWERDEAN | ST |  |  | 1.4221 | 0.37343 | -0.57005 | -1.6363 | -2.7792 | -4.0099 | -5.3516 | -6.8616 | -9.195 | -13.9536 | -21.4415 | -26.7646 | -29.3984 | 8.8624 | 8.1565 | 7.4624 | 6.7523 | 5.9797 | 5.1247 | 4.1643 | 3.0499 | 1.4667 | -1.5157 | -5.8194 | -9.2843 | -12.5118 | 5.2776 | 4.397 | 3.5827 | 2.6211 | 1.5573 | 0.40376 | -0.86903 | -2.3162 | -4.5324 | -8.9449 | -15.6599 | -20.3555 | -22.6522
|  | BOWERDEAN | FS |  |  | 1.4221 | 0.37343 | -0.57005 | -1.6363 | -2.7792 | -4.0099 | -5.3516 | -6.8616 | -9.195 | -13.9536 | -21.4415 | -26.7646 | -29.3984 | 8.8624 | 8.1565 | 7.4624 | 6.7523 | 5.9797 | 5.1247 | 4.1643 | 3.0499 | 1.4667 | -1.5157 | -5.8194 | -9.2843 | -12.5118 | 5.2776 | 4.397 | 3.5827 | 2.6211 | 1.5573 | 0.40376 | -0.86903 | -2.3162 | -4.5324 | -8.9449 | -15.6599 | -20.3555 | -22.6522
BRAMLEY (FLEE) | BRACKNELL MAIN | BRACKNELL | MINIMUM HEADROOM | SU 86075 69397 | YES | 29.5213 | 28.3698 | 27.0256 | 25.0655 | 23.3054 | 21.8313 | 20.1993 | 18.1504 | 15.5561 | 7.9395 | -2.2452 | -7.2064 | -9.5975 | 32.0539 | 31.1491 | 30.2709 | 29.1772 | 28.1552 | 27.1171 | 25.9731 | 24.6106 | 23.028 | 18.3095 | 11.7127 | 7.5825 | 3.3691 | 30.2942 | 29.2403 | 27.9989 | 26.2593 | 24.6865 | 23.3037 | 21.7547 | 19.8358 | 17.4258 | 10.4684 | 1.4572 | -2.9144 | -5.0067
|  | BRACKNELL | CT |  |  | 29.5213 | 28.3698 | 27.0256 | 25.0655 | 23.3054 | 21.8313 | 20.1993 | 18.1504 | 15.5561 | 7.9395 | -2.2452 | -7.2064 | -9.5975 | 32.0539 | 31.1491 | 30.2709 | 29.1772 | 28.1552 | 27.1171 | 25.9731 | 24.6106 | 23.028 | 18.3095 | 11.7127 | 7.5825 | 3.3691 | 30.2942 | 29.2403 | 27.9989 | 26.2593 | 24.6865 | 23.3037 | 21.7547 | 19.8358 | 17.4258 | 10.4684 | 1.4572 | -2.9144 | -5.0067
|  | BRACKNELL | LW |  |  | 29.5213 | 28.3698 | 27.0256 | 25.0655 | 23.3054 | 21.8313 | 20.1993 | 18.1504 | 15.5561 | 7.9395 | -2.2452 | -7.2064 | -9.5975 | 32.0539 | 31.1491 | 30.2709 | 29.1772 | 28.1552 | 27.1171 | 25.9731 | 24.6106 | 23.028 | 18.3095 | 11.7127 | 7.5825 | 3.3691 | 30.2942 | 29.2403 | 27.9989 | 26.2593 | 24.6865 | 23.3037 | 21.7547 | 19.8358 | 17.4258 | 10.4684 | 1.4572 | -2.9144 | -5.0067
|  | BRACKNELL | ST |  |  | 29.5213 | 28.3698 | 27.0256 | 25.0655 | 23.3054 | 21.8313 | 20.1993 | 18.1504 | 15.5561 | 7.9395 | -2.2452 | -7.2064 | -9.5975 | 32.0539 | 31.1491 | 30.2709 | 29.1772 | 28.1552 | 27.1171 | 25.9731 | 24.6106 | 23.028 | 18.3095 | 11.7127 | 7.5825 | 3.3691 | 30.2942 | 29.2403 | 27.9989 | 26.2593 | 24.6865 | 23.3037 | 21.7547 | 19.8358 | 17.4258 | 10.4684 | 1.4572 | -2.9144 | -5.0067
|  | BRACKNELL | FS |  |  | 29.5213 | 28.3698 | 27.0256 | 25.0655 | 23.3054 | 21.8313 | 20.1993 | 18.1504 | 15.5561 | 7.9395 | -2.2452 | -7.2064 | -9.5975 | 32.0539 | 31.1491 | 30.2709 | 29.1772 | 28.1552 | 27.1171 | 25.9731 | 24.6106 | 23.028 | 18.3095 | 11.7127 | 7.5825 | 3.3691 | 30.2942 | 29.2403 | 27.9989 | 26.2593 | 24.6865 | 23.3037 | 21.7547 | 19.8358 | 17.4258 | 10.4684 | 1.4572 | -2.9144 | -5.0067
MELKSHAM GSP | NORRINGTON | BRADFORD-ON-AVON | MINIMUM HEADROOM | ST 81260 60564 | YES | 8.3113 | 7.9895 | 7.5769 | 7.0204 | 6.4328 | 5.8035 | 5.1118 | 4.3217 | 2.9788 | -0.26867 | -4.4411 | -6.9818 | -8.1476 | 13.0802 | 12.8461 | 12.5387 | 12.1814 | 11.7989 | 11.3918 | 10.9397 | 10.404 | 9.5651 | 7.6342 | 5.3984 | 3.8966 | 2.6187 | 9.5868 | 9.28 | 8.8826 | 8.3616 | 7.81 | 7.2354 | 6.6039 | 5.871 | 4.647 | 1.7667 | -1.8543 | -4.0886 | -5.1051
|  | BRADFORD-ON-AVON | CT |  |  | 8.3113 | 7.9895 | 7.5769 | 7.0204 | 6.4328 | 5.8035 | 5.1118 | 4.3217 | 2.9788 | -0.26867 | -4.4411 | -6.9818 | -8.1476 | 13.0802 | 12.8461 | 12.5387 | 12.1814 | 11.7989 | 11.3918 | 10.9397 | 10.404 | 9.5651 | 7.6342 | 5.3984 | 3.8966 | 2.6187 | 9.5868 | 9.28 | 8.8826 | 8.3616 | 7.81 | 7.2354 | 6.6039 | 5.871 | 4.647 | 1.7667 | -1.8543 | -4.0886 | -5.1051
|  | BRADFORD-ON-AVON | LW |  |  | 8.3113 | 7.9895 | 7.5769 | 7.0204 | 6.4328 | 5.8035 | 5.1118 | 4.3217 | 2.9788 | -0.26867 | -4.4411 | -6.9818 | -8.1476 | 13.0802 | 12.8461 | 12.5387 | 12.1814 | 11.7989 | 11.3918 | 10.9397 | 10.404 | 9.5651 | 7.6342 | 5.3984 | 3.8966 | 2.6187 | 9.5868 | 9.28 | 8.8826 | 8.3616 | 7.81 | 7.2354 | 6.6039 | 5.871 | 4.647 | 1.7667 | -1.8543 | -4.0886 | -5.1051
|  | BRADFORD-ON-AVON | ST |  |  | 8.3113 | 7.9895 | 7.5769 | 7.0204 | 6.4328 | 5.8035 | 5.1118 | 4.3217 | 2.9788 | -0.26867 | -4.4411 | -6.9818 | -8.1476 | 13.0802 | 12.8461 | 12.5387 | 12.1814 | 11.7989 | 11.3918 | 10.9397 | 10.404 | 9.5651 | 7.6342 | 5.3984 | 3.8966 | 2.6187 | 9.5868 | 9.28 | 8.8826 | 8.3616 | 7.81 | 7.2354 | 6.6039 | 5.871 | 4.647 | 1.7667 | -1.8543 | -4.0886 | -5.1051
|  | BRADFORD-ON-AVON | FS |  |  | 8.3113 | 7.9895 | 7.5769 | 7.0204 | 6.4328 | 5.8035 | 5.1118 | 4.3217 | 2.9788 | -0.26867 | -4.4411 | -6.9818 | -8.1476 | 13.0802 | 12.8461 | 12.5387 | 12.1814 | 11.7989 | 11.3918 | 10.9397 | 10.404 | 9.5651 | 7.6342 | 5.3984 | 3.8966 | 2.6187 | 9.5868 | 9.28 | 8.8826 | 8.3616 | 7.81 | 7.2354 | 6.6039 | 5.871 | 4.647 | 1.7667 | -1.8543 | -4.0886 | -5.1051
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | BRAMLEY GREEN | MINIMUM HEADROOM | SU 67431 58511 | YES | 14.2417 | 14.0742 | 13.9145 | 13.695 | 13.4654 | 13.2299 | 12.9517 | 12.628 | 12.1272 | 11.0566 | 9.3205 | 8.1682 | 7.6436 | 15.8599 | 15.7282 | 15.6023 | 15.4626 | 15.3148 | 15.1518 | 14.9527 | 14.713 | 14.3778 | 13.7243 | 12.7503 | 12.0879 | 11.5824 | 14.9053 | 14.7428 | 14.5878 | 14.3825 | 14.1665 | 13.9427 | 13.6768 | 13.3655 | 12.8889 | 11.8919 | 10.3183 | 9.2985 | 8.8499
|  | BRAMLEY GREEN | CT |  |  | 14.2417 | 14.0742 | 13.9145 | 13.695 | 13.4654 | 13.2299 | 12.9517 | 12.628 | 12.1272 | 11.0566 | 9.3205 | 8.1682 | 7.6436 | 15.8599 | 15.7282 | 15.6023 | 15.4626 | 15.3148 | 15.1518 | 14.9527 | 14.713 | 14.3778 | 13.7243 | 12.7503 | 12.0879 | 11.5824 | 14.9053 | 14.7428 | 14.5878 | 14.3825 | 14.1665 | 13.9427 | 13.6768 | 13.3655 | 12.8889 | 11.8919 | 10.3183 | 9.2985 | 8.8499
|  | BRAMLEY GREEN | LW |  |  | 14.2417 | 14.0742 | 13.9145 | 13.695 | 13.4654 | 13.2299 | 12.9517 | 12.628 | 12.1272 | 11.0566 | 9.3205 | 8.1682 | 7.6436 | 15.8599 | 15.7282 | 15.6023 | 15.4626 | 15.3148 | 15.1518 | 14.9527 | 14.713 | 14.3778 | 13.7243 | 12.7503 | 12.0879 | 11.5824 | 14.9053 | 14.7428 | 14.5878 | 14.3825 | 14.1665 | 13.9427 | 13.6768 | 13.3655 | 12.8889 | 11.8919 | 10.3183 | 9.2985 | 8.8499
|  | BRAMLEY GREEN | ST |  |  | 14.2417 | 14.0742 | 13.9145 | 13.695 | 13.4654 | 13.2299 | 12.9517 | 12.628 | 12.1272 | 11.0566 | 9.3205 | 8.1682 | 7.6436 | 15.8599 | 15.7282 | 15.6023 | 15.4626 | 15.3148 | 15.1518 | 14.9527 | 14.713 | 14.3778 | 13.7243 | 12.7503 | 12.0879 | 11.5824 | 14.9053 | 14.7428 | 14.5878 | 14.3825 | 14.1665 | 13.9427 | 13.6768 | 13.3655 | 12.8889 | 11.8919 | 10.3183 | 9.2985 | 8.8499
|  | BRAMLEY GREEN | FS |  |  | 14.2417 | 14.0742 | 13.9145 | 13.695 | 13.4654 | 13.2299 | 12.9517 | 12.628 | 12.1272 | 11.0566 | 9.3205 | 8.1682 | 7.6436 | 15.8599 | 15.7282 | 15.6023 | 15.4626 | 15.3148 | 15.1518 | 14.9527 | 14.713 | 14.3778 | 13.7243 | 12.7503 | 12.0879 | 11.5824 | 14.9053 | 14.7428 | 14.5878 | 14.3825 | 14.1665 | 13.9427 | 13.6768 | 13.3655 | 12.8889 | 11.8919 | 10.3183 | 9.2985 | 8.8499
LOVEDEAN GSP | PORTSMOUTH BSP | BRANDON ROAD | MINIMUM HEADROOM | SZ 64712 98665 | YES | 19.212 | 18.7399 | 18.1648 | 17.3365 | 16.4465 | 15.5689 | 14.6207 | 13.5973 | 11.9674 | 6.8028 | -2.3153 | -8.3682 | -11.4032 | 21.8115 | 21.1901 | 20.4441 | 19.5117 | 18.492 | 17.3787 | 16.1395 | 14.7109 | 13.0123 | 7.1645 | -6.0768 | -24.5744 | -53.2777 | 19.3147 | 18.8905 | 18.359 | 17.63 | 16.8418 | 16.0517 | 15.1958 | 14.2507 | 12.7989 | 8.179 | -0.020376 | -5.3108 | -7.915
|  | BRANDON ROAD | CT |  |  | 19.212 | 18.7399 | 18.1648 | 17.3365 | 16.4465 | 15.5689 | 14.6207 | 13.5973 | 11.9674 | 6.8028 | -2.3153 | -8.3682 | -11.4032 | 21.8115 | 21.1901 | 20.4441 | 19.5117 | 18.492 | 17.3787 | 16.1395 | 14.7109 | 13.0123 | 7.1645 | -6.0768 | -24.5744 | -53.2777 | 19.3147 | 18.8905 | 18.359 | 17.63 | 16.8418 | 16.0517 | 15.1958 | 14.2507 | 12.7989 | 8.179 | -0.020376 | -5.3108 | -7.915
|  | BRANDON ROAD | LW |  |  | 19.212 | 18.7399 | 18.1648 | 17.3365 | 16.4465 | 15.5689 | 14.6207 | 13.5973 | 11.9674 | 6.8028 | -2.3153 | -8.3682 | -11.4032 | 21.8115 | 21.1901 | 20.4441 | 19.5117 | 18.492 | 17.3787 | 16.1395 | 14.7109 | 13.0123 | 7.1645 | -6.0768 | -24.5744 | -53.2777 | 19.3147 | 18.8905 | 18.359 | 17.63 | 16.8418 | 16.0517 | 15.1958 | 14.2507 | 12.7989 | 8.179 | -0.020376 | -5.3108 | -7.915
|  | BRANDON ROAD | ST |  |  | 19.212 | 18.7399 | 18.1648 | 17.3365 | 16.4465 | 15.5689 | 14.6207 | 13.5973 | 11.9674 | 6.8028 | -2.3153 | -8.3682 | -11.4032 | 21.8115 | 21.1901 | 20.4441 | 19.5117 | 18.492 | 17.3787 | 16.1395 | 14.7109 | 13.0123 | 7.1645 | -6.0768 | -24.5744 | -53.2777 | 19.3147 | 18.8905 | 18.359 | 17.63 | 16.8418 | 16.0517 | 15.1958 | 14.2507 | 12.7989 | 8.179 | -0.020376 | -5.3108 | -7.915
|  | BRANDON ROAD | FS |  |  | 19.212 | 18.7399 | 18.1648 | 17.3365 | 16.4465 | 15.5689 | 14.6207 | 13.5973 | 11.9674 | 6.8028 | -2.3153 | -8.3682 | -11.4032 | 21.8115 | 21.1901 | 20.4441 | 19.5117 | 18.492 | 17.3787 | 16.1395 | 14.7109 | 13.0123 | 7.1645 | -6.0768 | -24.5744 | -53.2777 | 19.3147 | 18.8905 | 18.359 | 17.63 | 16.8418 | 16.0517 | 15.1958 | 14.2507 | 12.7989 | 8.179 | -0.020376 | -5.3108 | -7.915
BRAMLEY (FLEE) | MAIDENHEAD BSP | BRAYWICK ROAD | MINIMUM HEADROOM | SU 88887 80726 | YES | 2.5675 | 2.2234 | 1.8334 | 1.4304 | 0.88756 | -0.16288 | -1.3562 | -2.7329 | -4.5839 | -9.6262 | -15.3687 | -18.6072 | -20.1508 | 2.4341 | 2.072 | 1.6545 | 1.1584 | 0.55288 | -0.059895 | -0.75277 | -1.5549 | -2.5814 | -5.4867 | -9.5929 | -13.0356 | -17.2075 | 0.41154 | -0.22766 | -0.98179 | -1.8804 | -2.814 | -3.7421 | -4.7985 | -6.0252 | -7.6806 | -12.1117 | -17.1909 | -19.8824 | -21.1474
|  | BRAYWICK ROAD | CT |  |  | 2.5675 | 2.2234 | 1.8334 | 1.4304 | 0.88756 | -0.16288 | -1.3562 | -2.7329 | -4.5839 | -9.6262 | -15.3687 | -18.6072 | -20.1508 | 2.4341 | 2.072 | 1.6545 | 1.1584 | 0.55288 | -0.059895 | -0.75277 | -1.5549 | -2.5814 | -5.4867 | -9.5929 | -13.0356 | -17.2075 | 0.41154 | -0.22766 | -0.98179 | -1.8804 | -2.814 | -3.7421 | -4.7985 | -6.0252 | -7.6806 | -12.1117 | -17.1909 | -19.8824 | -21.1474
|  | BRAYWICK ROAD | LW |  |  | 2.5675 | 2.2234 | 1.8334 | 1.4304 | 0.88756 | -0.16288 | -1.3562 | -2.7329 | -4.5839 | -9.6262 | -15.3687 | -18.6072 | -20.1508 | 2.4341 | 2.072 | 1.6545 | 1.1584 | 0.55288 | -0.059895 | -0.75277 | -1.5549 | -2.5814 | -5.4867 | -9.5929 | -13.0356 | -17.2075 | 0.41154 | -0.22766 | -0.98179 | -1.8804 | -2.814 | -3.7421 | -4.7985 | -6.0252 | -7.6806 | -12.1117 | -17.1909 | -19.8824 | -21.1474
|  | BRAYWICK ROAD | ST |  |  | 2.5675 | 2.2234 | 1.8334 | 1.4304 | 0.88756 | -0.16288 | -1.3562 | -2.7329 | -4.5839 | -9.6262 | -15.3687 | -18.6072 | -20.1508 | 2.4341 | 2.072 | 1.6545 | 1.1584 | 0.55288 | -0.059895 | -0.75277 | -1.5549 | -2.5814 | -5.4867 | -9.5929 | -13.0356 | -17.2075 | 0.41154 | -0.22766 | -0.98179 | -1.8804 | -2.814 | -3.7421 | -4.7985 | -6.0252 | -7.6806 | -12.1117 | -17.1909 | -19.8824 | -21.1474
|  | BRAYWICK ROAD | FS |  |  | 2.5675 | 2.2234 | 1.8334 | 1.4304 | 0.88756 | -0.16288 | -1.3562 | -2.7329 | -4.5839 | -9.6262 | -15.3687 | -18.6072 | -20.1508 | 2.4341 | 2.072 | 1.6545 | 1.1584 | 0.55288 | -0.059895 | -0.75277 | -1.5549 | -2.5814 | -5.4867 | -9.5929 | -13.0356 | -17.2075 | 0.41154 | -0.22766 | -0.98179 | -1.8804 | -2.814 | -3.7421 | -4.7985 | -6.0252 | -7.6806 | -12.1117 | -17.1909 | -19.8824 | -21.1474
EALING GSP | EALING 22kV | BRENTFORD | MINIMUM HEADROOM | TQ 17659 78277 | YES | 17.1843 | 16.4772 | 15.7906 | 14.8748 | 13.887 | 12.9414 | 11.9208 | 10.7952 | 9.2241 | 4.036 | -5.8245 | -13.0077 | -17.6027 | 22.3049 | 21.8926 | 21.4687 | 20.7541 | 19.977 | 19.1674 | 18.2789 | 17.2675 | 16.0315 | 11.7036 | 2.6344 | -7.7914 | -22.1687 | 18.6118 | 18.0063 | 17.3956 | 16.6056 | 15.7512 | 14.918 | 14.0161 | 13.0048 | 11.6179 | 7.029 | -1.4041 | -7.4416 | -11.1868
|  | BRENTFORD | CT |  |  | 17.1843 | 16.4772 | 15.7906 | 14.8748 | 13.887 | 12.9414 | 11.9208 | 10.7952 | 9.2241 | 4.036 | -5.8245 | -13.0077 | -17.6027 | 22.3049 | 21.8926 | 21.4687 | 20.7541 | 19.977 | 19.1674 | 18.2789 | 17.2675 | 16.0315 | 11.7036 | 2.6344 | -7.7914 | -22.1687 | 18.6118 | 18.0063 | 17.3956 | 16.6056 | 15.7512 | 14.918 | 14.0161 | 13.0048 | 11.6179 | 7.029 | -1.4041 | -7.4416 | -11.1868
|  | BRENTFORD | LW |  |  | 17.1843 | 16.4772 | 15.7906 | 14.8748 | 13.887 | 12.9414 | 11.9208 | 10.7952 | 9.2241 | 4.036 | -5.8245 | -13.0077 | -17.6027 | 22.3049 | 21.8926 | 21.4687 | 20.7541 | 19.977 | 19.1674 | 18.2789 | 17.2675 | 16.0315 | 11.7036 | 2.6344 | -7.7914 | -22.1687 | 18.6118 | 18.0063 | 17.3956 | 16.6056 | 15.7512 | 14.918 | 14.0161 | 13.0048 | 11.6179 | 7.029 | -1.4041 | -7.4416 | -11.1868
|  | BRENTFORD | ST |  |  | 17.1843 | 16.4772 | 15.7906 | 14.8748 | 13.887 | 12.9414 | 11.9208 | 10.7952 | 9.2241 | 4.036 | -5.8245 | -13.0077 | -17.6027 | 22.3049 | 21.8926 | 21.4687 | 20.7541 | 19.977 | 19.1674 | 18.2789 | 17.2675 | 16.0315 | 11.7036 | 2.6344 | -7.7914 | -22.1687 | 18.6118 | 18.0063 | 17.3956 | 16.6056 | 15.7512 | 14.918 | 14.0161 | 13.0048 | 11.6179 | 7.029 | -1.4041 | -7.4416 | -11.1868
|  | BRENTFORD | FS |  |  | 17.1843 | 16.4772 | 15.7906 | 14.8748 | 13.887 | 12.9414 | 11.9208 | 10.7952 | 9.2241 | 4.036 | -5.8245 | -13.0077 | -17.6027 | 22.3049 | 21.8926 | 21.4687 | 20.7541 | 19.977 | 19.1674 | 18.2789 | 17.2675 | 16.0315 | 11.7036 | 2.6344 | -7.7914 | -22.1687 | 18.6118 | 18.0063 | 17.3956 | 16.6056 | 15.7512 | 14.918 | 14.0161 | 13.0048 | 11.6179 | 7.029 | -1.4041 | -7.4416 | -11.1868
EALING GSP | EALING 22kV | BRIDGE ROAD | MINIMUM HEADROOM | TQ 14778 75741 |  | -2.6749 | -3.8709 | -5.4328 | -7.4072 | -9.5264 | -11.6512 | -13.978 | -16.1001 | -18.92 | -27.5554 | -41.6251 | -51.3912 | -56.9432 | 0.025278 | -0.89377 | -2.076 | -3.49 | -5.0208 | -6.6285 | -8.3927 | -10.1559 | -12.3288 | -19.352 | -32.1291 | -46.6682 | -66.965 | -8.6484 | -9.6823 | -11.0673 | -12.7989 | -14.6957 | -16.6133 | -18.7095 | -20.6648 | -23.2806 | -31.32 | -43.9499 | -52.3697 | -57.0521
|  | BRIDGE ROAD | CT |  |  | -2.6749 | -3.8709 | -5.4328 | -7.4072 | -9.5264 | -11.6512 | -13.978 | -16.1001 | -18.92 | -27.5554 | -41.6251 | -51.3912 | -56.9432 | 0.025278 | -0.89377 | -2.076 | -3.49 | -5.0208 | -6.6285 | -8.3927 | -10.1559 | -12.3288 | -19.352 | -32.1291 | -46.6682 | -66.965 | -8.6484 | -9.6823 | -11.0673 | -12.7989 | -14.6957 | -16.6133 | -18.7095 | -20.6648 | -23.2806 | -31.32 | -43.9499 | -52.3697 | -57.0521
|  | BRIDGE ROAD | LW |  |  | -2.6749 | -3.8709 | -5.4328 | -7.4072 | -9.5264 | -11.6512 | -13.978 | -16.1001 | -18.92 | -27.5554 | -41.6251 | -51.3912 | -56.9432 | 0.025278 | -0.89377 | -2.076 | -3.49 | -5.0208 | -6.6285 | -8.3927 | -10.1559 | -12.3288 | -19.352 | -32.1291 | -46.6682 | -66.965 | -8.6484 | -9.6823 | -11.0673 | -12.7989 | -14.6957 | -16.6133 | -18.7095 | -20.6648 | -23.2806 | -31.32 | -43.9499 | -52.3697 | -57.0521
|  | BRIDGE ROAD | ST |  |  | -2.6749 | -3.8709 | -5.4328 | -7.4072 | -9.5264 | -11.6512 | -13.978 | -16.1001 | -18.92 | -27.5554 | -41.6251 | -51.3912 | -56.9432 | 0.025278 | -0.89377 | -2.076 | -3.49 | -5.0208 | -6.6285 | -8.3927 | -10.1559 | -12.3288 | -19.352 | -32.1291 | -46.6682 | -66.965 | -8.6484 | -9.6823 | -11.0673 | -12.7989 | -14.6957 | -16.6133 | -18.7095 | -20.6648 | -23.2806 | -31.32 | -43.9499 | -52.3697 | -57.0521
|  | BRIDGE ROAD | FS |  |  | -2.6749 | -3.8709 | -5.4328 | -7.4072 | -9.5264 | -11.6512 | -13.978 | -16.1001 | -18.92 | -27.5554 | -41.6251 | -51.3912 | -56.9432 | 0.025278 | -0.89377 | -2.076 | -3.49 | -5.0208 | -6.6285 | -8.3927 | -10.1559 | -12.3288 | -19.352 | -32.1291 | -46.6682 | -66.965 | -8.6484 | -9.6823 | -11.0673 | -12.7989 | -14.6957 | -16.6133 | -18.7095 | -20.6648 | -23.2806 | -31.32 | -43.9499 | -52.3697 | -57.0521
LOVEDEAN GSP | HAVANT | BROCKHAMPTON | MINIMUM HEADROOM | SU 70868 05828 | YES | 23.9079 | 23.8491 | 23.7744 | 23.6116 | 23.3939 | 23.2088 | 23.0293 | 22.8003 | 22.5034 | 21.7759 | 20.3636 | 19.2528 | 18.6138 | 20.7115 | 20.6601 | 20.5951 | 20.4229 | 20.1915 | 20.0084 | 19.8292 | 19.6051 | 19.3244 | 18.6453 | 17.4078 | 16.4525 | 15.2684 | 23.0303 | 22.9738 | 22.9015 | 22.7412 | 22.5263 | 22.3451 | 22.1685 | 21.9441 | 21.6537 | 20.9456 | 20.0063 | 19.6385 | 19.149
|  | BROCKHAMPTON | CT |  |  | 23.9079 | 23.8491 | 23.7744 | 23.6116 | 23.3939 | 23.2088 | 23.0293 | 22.8003 | 22.5034 | 21.7759 | 20.3636 | 19.2528 | 18.6138 | 20.7115 | 20.6601 | 20.5951 | 20.4229 | 20.1915 | 20.0084 | 19.8292 | 19.6051 | 19.3244 | 18.6453 | 17.4078 | 16.4525 | 15.2684 | 23.0303 | 22.9738 | 22.9015 | 22.7412 | 22.5263 | 22.3451 | 22.1685 | 21.9441 | 21.6537 | 20.9456 | 20.0063 | 19.6385 | 19.149
|  | BROCKHAMPTON | LW |  |  | 23.9079 | 23.8491 | 23.7744 | 23.6116 | 23.3939 | 23.2088 | 23.0293 | 22.8003 | 22.5034 | 21.7759 | 20.3636 | 19.2528 | 18.6138 | 20.7115 | 20.6601 | 20.5951 | 20.4229 | 20.1915 | 20.0084 | 19.8292 | 19.6051 | 19.3244 | 18.6453 | 17.4078 | 16.4525 | 15.2684 | 23.0303 | 22.9738 | 22.9015 | 22.7412 | 22.5263 | 22.3451 | 22.1685 | 21.9441 | 21.6537 | 20.9456 | 20.0063 | 19.6385 | 19.149
|  | BROCKHAMPTON | ST |  |  | 23.9079 | 23.8491 | 23.7744 | 23.6116 | 23.3939 | 23.2088 | 23.0293 | 22.8003 | 22.5034 | 21.7759 | 20.3636 | 19.2528 | 18.6138 | 20.7115 | 20.6601 | 20.5951 | 20.4229 | 20.1915 | 20.0084 | 19.8292 | 19.6051 | 19.3244 | 18.6453 | 17.4078 | 16.4525 | 15.2684 | 23.0303 | 22.9738 | 22.9015 | 22.7412 | 22.5263 | 22.3451 | 22.1685 | 21.9441 | 21.6537 | 20.9456 | 20.0063 | 19.6385 | 19.149
|  | BROCKHAMPTON | FS |  |  | 23.9079 | 23.8491 | 23.7744 | 23.6116 | 23.3939 | 23.2088 | 23.0293 | 22.8003 | 22.5034 | 21.7759 | 20.3636 | 19.2528 | 18.6138 | 20.7115 | 20.6601 | 20.5951 | 20.4229 | 20.1915 | 20.0084 | 19.8292 | 19.6051 | 19.3244 | 18.6453 | 17.4078 | 16.4525 | 15.2684 | 23.0303 | 22.9738 | 22.9015 | 22.7412 | 22.5263 | 22.3451 | 22.1685 | 21.9441 | 21.6537 | 20.9456 | 20.0063 | 19.6385 | 19.149
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | BROCKHURST | MINIMUM HEADROOM | SU 59381 02061 | YES | 7.9829 | 7.4157 | 6.6438 | 5.6692 | 4.6045 | 3.503 | 2.4169 | 1.2976 | -0.32049 | -5.4956 | -13.0486 | -17.7644 | -20.474 | 13.1273 | 12.6913 | 12.1233 | 11.4572 | 10.7221 | 9.9478 | 9.1237 | 8.2369 | 7.0657 | 3.324 | -1.6019 | -5.3976 | -9.7255 | 9.5535 | 9.0397 | 8.3146 | 7.4218 | 6.4446 | 5.4251 | 4.4015 | 3.3218 | 1.7965 | -3.0504 | -9.6214 | -13.5944 | -15.8838
|  | BROCKHURST | CT |  |  | 7.9829 | 7.4157 | 6.6438 | 5.6692 | 4.6045 | 3.503 | 2.4169 | 1.2976 | -0.32049 | -5.4956 | -13.0486 | -17.7644 | -20.474 | 13.1273 | 12.6913 | 12.1233 | 11.4572 | 10.7221 | 9.9478 | 9.1237 | 8.2369 | 7.0657 | 3.324 | -1.6019 | -5.3976 | -9.7255 | 9.5535 | 9.0397 | 8.3146 | 7.4218 | 6.4446 | 5.4251 | 4.4015 | 3.3218 | 1.7965 | -3.0504 | -9.6214 | -13.5944 | -15.8838
|  | BROCKHURST | LW |  |  | 7.9829 | 7.4157 | 6.6438 | 5.6692 | 4.6045 | 3.503 | 2.4169 | 1.2976 | -0.32049 | -5.4956 | -13.0486 | -17.7644 | -20.474 | 13.1273 | 12.6913 | 12.1233 | 11.4572 | 10.7221 | 9.9478 | 9.1237 | 8.2369 | 7.0657 | 3.324 | -1.6019 | -5.3976 | -9.7255 | 9.5535 | 9.0397 | 8.3146 | 7.4218 | 6.4446 | 5.4251 | 4.4015 | 3.3218 | 1.7965 | -3.0504 | -9.6214 | -13.5944 | -15.8838
|  | BROCKHURST | ST |  |  | 7.9829 | 7.4157 | 6.6438 | 5.6692 | 4.6045 | 3.503 | 2.4169 | 1.2976 | -0.32049 | -5.4956 | -13.0486 | -17.7644 | -20.474 | 13.1273 | 12.6913 | 12.1233 | 11.4572 | 10.7221 | 9.9478 | 9.1237 | 8.2369 | 7.0657 | 3.324 | -1.6019 | -5.3976 | -9.7255 | 9.5535 | 9.0397 | 8.3146 | 7.4218 | 6.4446 | 5.4251 | 4.4015 | 3.3218 | 1.7965 | -3.0504 | -9.6214 | -13.5944 | -15.8838
|  | BROCKHURST | FS |  |  | 7.9829 | 7.4157 | 6.6438 | 5.6692 | 4.6045 | 3.503 | 2.4169 | 1.2976 | -0.32049 | -5.4956 | -13.0486 | -17.7644 | -20.474 | 13.1273 | 12.6913 | 12.1233 | 11.4572 | 10.7221 | 9.9478 | 9.1237 | 8.2369 | 7.0657 | 3.324 | -1.6019 | -5.3976 | -9.7255 | 9.5535 | 9.0397 | 8.3146 | 7.4218 | 6.4446 | 5.4251 | 4.4015 | 3.3218 | 1.7965 | -3.0504 | -9.6214 | -13.5944 | -15.8838
MELKSHAM GSP | NORRINGTON | BROMHAM | MINIMUM HEADROOM | ST 98670 65994 | YES | 2.4873 | 2.4148 | 2.31 | 2.1731 | 2.0298 | 1.879 | 1.6901 | 1.4871 | 1.1803 | 0.62907 | -0.30784 | -0.93367 | -1.226 | 3.2847 | 3.2231 | 3.1539 | 3.0711 | 2.984 | 2.8902 | 2.7707 | 2.641 | 2.4514 | 2.1466 | 1.665 | 1.3307 | 1.1045 | 2.5195 | 2.4405 | 2.354 | 2.2298 | 2.1005 | 1.9656 | 1.7816 | 1.5841 | 1.2855 | 0.76853 | -0.072352 | -0.66062 | -0.9262
|  | BROMHAM | CT |  |  | 2.4873 | 2.4148 | 2.31 | 2.1731 | 2.0298 | 1.879 | 1.6901 | 1.4871 | 1.1803 | 0.62907 | -0.30784 | -0.93367 | -1.226 | 3.2847 | 3.2231 | 3.1539 | 3.0711 | 2.984 | 2.8902 | 2.7707 | 2.641 | 2.4514 | 2.1466 | 1.665 | 1.3307 | 1.1045 | 2.5195 | 2.4405 | 2.354 | 2.2298 | 2.1005 | 1.9656 | 1.7816 | 1.5841 | 1.2855 | 0.76853 | -0.072352 | -0.66062 | -0.9262
|  | BROMHAM | LW |  |  | 2.4873 | 2.4148 | 2.31 | 2.1731 | 2.0298 | 1.879 | 1.6901 | 1.4871 | 1.1803 | 0.62907 | -0.30784 | -0.93367 | -1.226 | 3.2847 | 3.2231 | 3.1539 | 3.0711 | 2.984 | 2.8902 | 2.7707 | 2.641 | 2.4514 | 2.1466 | 1.665 | 1.3307 | 1.1045 | 2.5195 | 2.4405 | 2.354 | 2.2298 | 2.1005 | 1.9656 | 1.7816 | 1.5841 | 1.2855 | 0.76853 | -0.072352 | -0.66062 | -0.9262
|  | BROMHAM | ST |  |  | 2.4873 | 2.4148 | 2.31 | 2.1731 | 2.0298 | 1.879 | 1.6901 | 1.4871 | 1.1803 | 0.62907 | -0.30784 | -0.93367 | -1.226 | 3.2847 | 3.2231 | 3.1539 | 3.0711 | 2.984 | 2.8902 | 2.7707 | 2.641 | 2.4514 | 2.1466 | 1.665 | 1.3307 | 1.1045 | 2.5195 | 2.4405 | 2.354 | 2.2298 | 2.1005 | 1.9656 | 1.7816 | 1.5841 | 1.2855 | 0.76853 | -0.072352 | -0.66062 | -0.9262
|  | BROMHAM | FS |  |  | 2.4873 | 2.4148 | 2.31 | 2.1731 | 2.0298 | 1.879 | 1.6901 | 1.4871 | 1.1803 | 0.62907 | -0.30784 | -0.93367 | -1.226 | 3.2847 | 3.2231 | 3.1539 | 3.0711 | 2.984 | 2.8902 | 2.7707 | 2.641 | 2.4514 | 2.1466 | 1.665 | 1.3307 | 1.1045 | 2.5195 | 2.4405 | 2.354 | 2.2298 | 2.1005 | 1.9656 | 1.7816 | 1.5841 | 1.2855 | 0.76853 | -0.072352 | -0.66062 | -0.9262
BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | BROOK STREET | MINIMUM HEADROOM | SU 63480 52228 | YES | 25.9768 | 25.775 | 25.5361 | 25.2006 | 24.8393 | 24.4911 | 23.938 | 23.279 | 22.4649 | 20.2169 | 16.1833 | 13.2217 | 11.1093 | 22.8513 | 22.7357 | 22.6014 | 22.4503 | 22.2832 | 22.0998 | 21.8351 | 21.4418 | 20.9798 | 19.3951 | 16.6042 | 13.6234 | 9.6592 | 24.5182 | 24.3415 | 24.1322 | 23.8364 | 23.5168 | 23.1954 | 22.703 | 22.112 | 21.3837 | 19.3277 | 15.7603 | 13.2765 | 11.5285
|  | BROOK STREET | CT |  |  | 25.9768 | 25.775 | 25.5361 | 25.2006 | 24.8393 | 24.4911 | 23.938 | 23.279 | 22.4649 | 20.2169 | 16.1833 | 13.2217 | 11.1093 | 22.8513 | 22.7357 | 22.6014 | 22.4503 | 22.2832 | 22.0998 | 21.8351 | 21.4418 | 20.9798 | 19.3951 | 16.6042 | 13.6234 | 9.6592 | 24.5182 | 24.3415 | 24.1322 | 23.8364 | 23.5168 | 23.1954 | 22.703 | 22.112 | 21.3837 | 19.3277 | 15.7603 | 13.2765 | 11.5285
|  | BROOK STREET | LW |  |  | 25.9768 | 25.775 | 25.5361 | 25.2006 | 24.8393 | 24.4911 | 23.938 | 23.279 | 22.4649 | 20.2169 | 16.1833 | 13.2217 | 11.1093 | 22.8513 | 22.7357 | 22.6014 | 22.4503 | 22.2832 | 22.0998 | 21.8351 | 21.4418 | 20.9798 | 19.3951 | 16.6042 | 13.6234 | 9.6592 | 24.5182 | 24.3415 | 24.1322 | 23.8364 | 23.5168 | 23.1954 | 22.703 | 22.112 | 21.3837 | 19.3277 | 15.7603 | 13.2765 | 11.5285
|  | BROOK STREET | ST |  |  | 25.9768 | 25.775 | 25.5361 | 25.2006 | 24.8393 | 24.4911 | 23.938 | 23.279 | 22.4649 | 20.2169 | 16.1833 | 13.2217 | 11.1093 | 22.8513 | 22.7357 | 22.6014 | 22.4503 | 22.2832 | 22.0998 | 21.8351 | 21.4418 | 20.9798 | 19.3951 | 16.6042 | 13.6234 | 9.6592 | 24.5182 | 24.3415 | 24.1322 | 23.8364 | 23.5168 | 23.1954 | 22.703 | 22.112 | 21.3837 | 19.3277 | 15.7603 | 13.2765 | 11.5285
|  | BROOK STREET | FS |  |  | 25.9768 | 25.775 | 25.5361 | 25.2006 | 24.8393 | 24.4911 | 23.938 | 23.279 | 22.4649 | 20.2169 | 16.1833 | 13.2217 | 11.1093 | 22.8513 | 22.7357 | 22.6014 | 22.4503 | 22.2832 | 22.0998 | 21.8351 | 21.4418 | 20.9798 | 19.3951 | 16.6042 | 13.6234 | 9.6592 | 24.5182 | 24.3415 | 24.1322 | 23.8364 | 23.5168 | 23.1954 | 22.703 | 22.112 | 21.3837 | 19.3277 | 15.7603 | 13.2765 | 11.5285
MELKSHAM GSP | FROME BSP | BRUTON | MINIMUM HEADROOM | ST 69094 35148 | YES | 4.5188 | 4.4018 | 4.2762 | 4.1239 | 3.9684 | 3.7934 | 3.5887 | 3.3755 | 3.0541 | 2.3654 | 1.1073 | 0.20243 | -0.17676 | 4.5723 | 4.4993 | 4.4162 | 4.3207 | 4.2222 | 4.1104 | 3.9789 | 3.8401 | 3.6262 | 3.1905 | 2.5575 | 2.091 | 1.799 | 4.1743 | 4.0605 | 3.9384 | 3.7904 | 3.6391 | 3.4689 | 3.2699 | 3.0628 | 2.7505 | 2.079 | 0.94117 | 0.14158 | -0.19314
|  | BRUTON | CT |  |  | 4.5188 | 4.4018 | 4.2762 | 4.1239 | 3.9684 | 3.7934 | 3.5887 | 3.3755 | 3.0541 | 2.3654 | 1.1073 | 0.20243 | -0.17676 | 4.5723 | 4.4993 | 4.4162 | 4.3207 | 4.2222 | 4.1104 | 3.9789 | 3.8401 | 3.6262 | 3.1905 | 2.5575 | 2.091 | 1.799 | 4.1743 | 4.0605 | 3.9384 | 3.7904 | 3.6391 | 3.4689 | 3.2699 | 3.0628 | 2.7505 | 2.079 | 0.94117 | 0.14158 | -0.19314
|  | BRUTON | LW |  |  | 4.5188 | 4.4018 | 4.2762 | 4.1239 | 3.9684 | 3.7934 | 3.5887 | 3.3755 | 3.0541 | 2.3654 | 1.1073 | 0.20243 | -0.17676 | 4.5723 | 4.4993 | 4.4162 | 4.3207 | 4.2222 | 4.1104 | 3.9789 | 3.8401 | 3.6262 | 3.1905 | 2.5575 | 2.091 | 1.799 | 4.1743 | 4.0605 | 3.9384 | 3.7904 | 3.6391 | 3.4689 | 3.2699 | 3.0628 | 2.7505 | 2.079 | 0.94117 | 0.14158 | -0.19314
|  | BRUTON | ST |  |  | 4.5188 | 4.4018 | 4.2762 | 4.1239 | 3.9684 | 3.7934 | 3.5887 | 3.3755 | 3.0541 | 2.3654 | 1.1073 | 0.20243 | -0.17676 | 4.5723 | 4.4993 | 4.4162 | 4.3207 | 4.2222 | 4.1104 | 3.9789 | 3.8401 | 3.6262 | 3.1905 | 2.5575 | 2.091 | 1.799 | 4.1743 | 4.0605 | 3.9384 | 3.7904 | 3.6391 | 3.4689 | 3.2699 | 3.0628 | 2.7505 | 2.079 | 0.94117 | 0.14158 | -0.19314
|  | BRUTON | FS |  |  | 4.5188 | 4.4018 | 4.2762 | 4.1239 | 3.9684 | 3.7934 | 3.5887 | 3.3755 | 3.0541 | 2.3654 | 1.1073 | 0.20243 | -0.17676 | 4.5723 | 4.4993 | 4.4162 | 4.3207 | 4.2222 | 4.1104 | 3.9789 | 3.8401 | 3.6262 | 3.1905 | 2.5575 | 2.091 | 1.799 | 4.1743 | 4.0605 | 3.9384 | 3.7904 | 3.6391 | 3.4689 | 3.2699 | 3.0628 | 2.7505 | 2.079 | 0.94117 | 0.14158 | -0.19314
COWLEY GSP | WITNEY BSP | BURFORD | MINIMUM HEADROOM | SP 25671 12529 | NO | 1.0445 | 0.90396 | 0.80822 | 0.66284 | 0.51235 | 0.35595 | 0.19048 | 0.015882 | -0.22676 | -0.7209 | -0.88774 | -0.96296 | -1.0085 | 2.123 | 2.0603 | 2.0202 | 1.9574 | 1.8923 | 1.8245 | 1.754 | 1.6834 | 1.5839 | 1.3457 | 1.1696 | 1.1289 | 1.1087 | 1.8778 | 1.8039 | 1.7529 | 1.6792 | 1.602 | 1.5211 | 1.38 | 1.2145 | 0.98259 | 0.48953 | 0.31533 | 0.23547 | 0.18679
|  | BURFORD | CT |  |  | 1.0445 | 0.90396 | 0.80822 | 0.66284 | 0.51235 | 0.35595 | 0.19048 | 0.015882 | -0.22676 | -0.7209 | -0.88774 | -0.96296 | -1.0085 | 2.123 | 2.0603 | 2.0202 | 1.9574 | 1.8923 | 1.8245 | 1.754 | 1.6834 | 1.5839 | 1.3457 | 1.1696 | 1.1289 | 1.1087 | 1.8778 | 1.8039 | 1.7529 | 1.6792 | 1.602 | 1.5211 | 1.38 | 1.2145 | 0.98259 | 0.48953 | 0.31533 | 0.23547 | 0.18679
|  | BURFORD | LW |  |  | 1.0445 | 0.90396 | 0.80822 | 0.66284 | 0.51235 | 0.35595 | 0.19048 | 0.015882 | -0.22676 | -0.7209 | -0.88774 | -0.96296 | -1.0085 | 2.123 | 2.0603 | 2.0202 | 1.9574 | 1.8923 | 1.8245 | 1.754 | 1.6834 | 1.5839 | 1.3457 | 1.1696 | 1.1289 | 1.1087 | 1.8778 | 1.8039 | 1.7529 | 1.6792 | 1.602 | 1.5211 | 1.38 | 1.2145 | 0.98259 | 0.48953 | 0.31533 | 0.23547 | 0.18679
|  | BURFORD | ST |  |  | 1.0445 | 0.90396 | 0.80822 | 0.66284 | 0.51235 | 0.35595 | 0.19048 | 0.015882 | -0.22676 | -0.7209 | -0.88774 | -0.96296 | -1.0085 | 2.123 | 2.0603 | 2.0202 | 1.9574 | 1.8923 | 1.8245 | 1.754 | 1.6834 | 1.5839 | 1.3457 | 1.1696 | 1.1289 | 1.1087 | 1.8778 | 1.8039 | 1.7529 | 1.6792 | 1.602 | 1.5211 | 1.38 | 1.2145 | 0.98259 | 0.48953 | 0.31533 | 0.23547 | 0.18679
|  | BURFORD | FS |  |  | 1.0445 | 0.90396 | 0.80822 | 0.66284 | 0.51235 | 0.35595 | 0.19048 | 0.015882 | -0.22676 | -0.7209 | -0.88774 | -0.96296 | -1.0085 | 2.123 | 2.0603 | 2.0202 | 1.9574 | 1.8923 | 1.8245 | 1.754 | 1.6834 | 1.5839 | 1.3457 | 1.1696 | 1.1289 | 1.1087 | 1.8778 | 1.8039 | 1.7529 | 1.6792 | 1.602 | 1.5211 | 1.38 | 1.2145 | 0.98259 | 0.48953 | 0.31533 | 0.23547 | 0.18679
MANNINGTON GSP | WAREHAM | BUSHEY | MINIMUM HEADROOM | SY 97671 83532 | YES | 1.7889 | 1.7618 | 1.7208 | 1.6689 | 1.6145 | 1.5521 | 1.477 | 1.3995 | 1.2866 | 1.0592 | 0.70564 | 0.42975 | 0.309 | 1.966 | 1.9526 | 1.9302 | 1.8984 | 1.865 | 1.827 | 1.7805 | 1.7324 | 1.6635 | 1.5289 | 1.331 | 1.205 | 1.1375 | 1.86 | 1.8427 | 1.8216 | 1.7882 | 1.7536 | 1.7124 | 1.637 | 1.5595 | 1.4463 | 1.2098 | 0.83887 | 0.59563 | 0.48946
|  | BUSHEY | CT |  |  | 1.7889 | 1.7618 | 1.7208 | 1.6689 | 1.6145 | 1.5521 | 1.477 | 1.3995 | 1.2866 | 1.0592 | 0.70564 | 0.42975 | 0.309 | 1.966 | 1.9526 | 1.9302 | 1.8984 | 1.865 | 1.827 | 1.7805 | 1.7324 | 1.6635 | 1.5289 | 1.331 | 1.205 | 1.1375 | 1.86 | 1.8427 | 1.8216 | 1.7882 | 1.7536 | 1.7124 | 1.637 | 1.5595 | 1.4463 | 1.2098 | 0.83887 | 0.59563 | 0.48946
|  | BUSHEY | LW |  |  | 1.7889 | 1.7618 | 1.7208 | 1.6689 | 1.6145 | 1.5521 | 1.477 | 1.3995 | 1.2866 | 1.0592 | 0.70564 | 0.42975 | 0.309 | 1.966 | 1.9526 | 1.9302 | 1.8984 | 1.865 | 1.827 | 1.7805 | 1.7324 | 1.6635 | 1.5289 | 1.331 | 1.205 | 1.1375 | 1.86 | 1.8427 | 1.8216 | 1.7882 | 1.7536 | 1.7124 | 1.637 | 1.5595 | 1.4463 | 1.2098 | 0.83887 | 0.59563 | 0.48946
|  | BUSHEY | ST |  |  | 1.7889 | 1.7618 | 1.7208 | 1.6689 | 1.6145 | 1.5521 | 1.477 | 1.3995 | 1.2866 | 1.0592 | 0.70564 | 0.42975 | 0.309 | 1.966 | 1.9526 | 1.9302 | 1.8984 | 1.865 | 1.827 | 1.7805 | 1.7324 | 1.6635 | 1.5289 | 1.331 | 1.205 | 1.1375 | 1.86 | 1.8427 | 1.8216 | 1.7882 | 1.7536 | 1.7124 | 1.637 | 1.5595 | 1.4463 | 1.2098 | 0.83887 | 0.59563 | 0.48946
|  | BUSHEY | FS |  |  | 1.7889 | 1.7618 | 1.7208 | 1.6689 | 1.6145 | 1.5521 | 1.477 | 1.3995 | 1.2866 | 1.0592 | 0.70564 | 0.42975 | 0.309 | 1.966 | 1.9526 | 1.9302 | 1.8984 | 1.865 | 1.827 | 1.7805 | 1.7324 | 1.6635 | 1.5289 | 1.331 | 1.205 | 1.1375 | 1.86 | 1.8427 | 1.8216 | 1.7882 | 1.7536 | 1.7124 | 1.637 | 1.5595 | 1.4463 | 1.2098 | 0.83887 | 0.59563 | 0.48946
FAWLEY GSP | LANGLEY BSP | BUTTS ASH | MINIMUM HEADROOM | SU 41923 05772 | YES | 5.672 | 5.3552 | 4.9127 | 4.3117 | 3.6703 | 2.9799 | 2.1789 | 1.2088 | -0.37809 | -4.3872 | -10.2458 | -14.0959 | -15.7722 | 10.6436 | 10.3799 | 9.995 | 9.5678 | 9.1046 | 8.5983 | 8.0427 | 7.3492 | 6.314 | 3.6849 | 0.55388 | -1.4411 | -3.022 | 6.9131 | 6.6096 | 6.1799 | 5.6139 | 5.0082 | 4.3077 | 3.5434 | 2.6113 | 1.1087 | -2.6405 | -7.9312 | -11.3201 | -12.7812
|  | BUTTS ASH | CT |  |  | 5.672 | 5.3552 | 4.9127 | 4.3117 | 3.6703 | 2.9799 | 2.1789 | 1.2088 | -0.37809 | -4.3872 | -10.2458 | -14.0959 | -15.7722 | 10.6436 | 10.3799 | 9.995 | 9.5678 | 9.1046 | 8.5983 | 8.0427 | 7.3492 | 6.314 | 3.6849 | 0.55388 | -1.4411 | -3.022 | 6.9131 | 6.6096 | 6.1799 | 5.6139 | 5.0082 | 4.3077 | 3.5434 | 2.6113 | 1.1087 | -2.6405 | -7.9312 | -11.3201 | -12.7812
|  | BUTTS ASH | LW |  |  | 5.672 | 5.3552 | 4.9127 | 4.3117 | 3.6703 | 2.9799 | 2.1789 | 1.2088 | -0.37809 | -4.3872 | -10.2458 | -14.0959 | -15.7722 | 10.6436 | 10.3799 | 9.995 | 9.5678 | 9.1046 | 8.5983 | 8.0427 | 7.3492 | 6.314 | 3.6849 | 0.55388 | -1.4411 | -3.022 | 6.9131 | 6.6096 | 6.1799 | 5.6139 | 5.0082 | 4.3077 | 3.5434 | 2.6113 | 1.1087 | -2.6405 | -7.9312 | -11.3201 | -12.7812
|  | BUTTS ASH | ST |  |  | 5.672 | 5.3552 | 4.9127 | 4.3117 | 3.6703 | 2.9799 | 2.1789 | 1.2088 | -0.37809 | -4.3872 | -10.2458 | -14.0959 | -15.7722 | 10.6436 | 10.3799 | 9.995 | 9.5678 | 9.1046 | 8.5983 | 8.0427 | 7.3492 | 6.314 | 3.6849 | 0.55388 | -1.4411 | -3.022 | 6.9131 | 6.6096 | 6.1799 | 5.6139 | 5.0082 | 4.3077 | 3.5434 | 2.6113 | 1.1087 | -2.6405 | -7.9312 | -11.3201 | -12.7812
|  | BUTTS ASH | FS |  |  | 5.672 | 5.3552 | 4.9127 | 4.3117 | 3.6703 | 2.9799 | 2.1789 | 1.2088 | -0.37809 | -4.3872 | -10.2458 | -14.0959 | -15.7722 | 10.6436 | 10.3799 | 9.995 | 9.5678 | 9.1046 | 8.5983 | 8.0427 | 7.3492 | 6.314 | 3.6849 | 0.55388 | -1.4411 | -3.022 | 6.9131 | 6.6096 | 6.1799 | 5.6139 | 5.0082 | 4.3077 | 3.5434 | 2.6113 | 1.1087 | -2.6405 | -7.9312 | -11.3201 | -12.7812
MELKSHAM GSP | CHIPPENHAM | CALNE | MINIMUM HEADROOM | SU 00521 72497 | YES | 4.212 | 3.858 | 3.3934 | 2.791 | 2.1469 | 1.4588 | 0.684 | -0.21964 | -1.6255 | -5.0525 | -9.7584 | -12.5466 | -13.9873 | 7.9712 | 7.7934 | 7.5741 | 7.2763 | 6.9558 | 6.6154 | 6.2379 | 5.7955 | 5.1275 | 2.7811 | -0.53116 | -2.7667 | -4.7335 | 6.4466 | 6.1832 | 5.8487 | 5.2427 | 4.5948 | 3.9011 | 3.1195 | 2.2034 | 0.78906 | -2.7477 | -7.8824 | -10.937 | -12.2142
|  | CALNE | CT |  |  | 4.212 | 3.858 | 3.3934 | 2.791 | 2.1469 | 1.4588 | 0.684 | -0.21964 | -1.6255 | -5.0525 | -9.7584 | -12.5466 | -13.9873 | 7.9712 | 7.7934 | 7.5741 | 7.2763 | 6.9558 | 6.6154 | 6.2379 | 5.7955 | 5.1275 | 2.7811 | -0.53116 | -2.7667 | -4.7335 | 6.4466 | 6.1832 | 5.8487 | 5.2427 | 4.5948 | 3.9011 | 3.1195 | 2.2034 | 0.78906 | -2.7477 | -7.8824 | -10.937 | -12.2142
|  | CALNE | LW |  |  | 4.212 | 3.858 | 3.3934 | 2.791 | 2.1469 | 1.4588 | 0.684 | -0.21964 | -1.6255 | -5.0525 | -9.7584 | -12.5466 | -13.9873 | 7.9712 | 7.7934 | 7.5741 | 7.2763 | 6.9558 | 6.6154 | 6.2379 | 5.7955 | 5.1275 | 2.7811 | -0.53116 | -2.7667 | -4.7335 | 6.4466 | 6.1832 | 5.8487 | 5.2427 | 4.5948 | 3.9011 | 3.1195 | 2.2034 | 0.78906 | -2.7477 | -7.8824 | -10.937 | -12.2142
|  | CALNE | ST |  |  | 4.212 | 3.858 | 3.3934 | 2.791 | 2.1469 | 1.4588 | 0.684 | -0.21964 | -1.6255 | -5.0525 | -9.7584 | -12.5466 | -13.9873 | 7.9712 | 7.7934 | 7.5741 | 7.2763 | 6.9558 | 6.6154 | 6.2379 | 5.7955 | 5.1275 | 2.7811 | -0.53116 | -2.7667 | -4.7335 | 6.4466 | 6.1832 | 5.8487 | 5.2427 | 4.5948 | 3.9011 | 3.1195 | 2.2034 | 0.78906 | -2.7477 | -7.8824 | -10.937 | -12.2142
|  | CALNE | FS |  |  | 4.212 | 3.858 | 3.3934 | 2.791 | 2.1469 | 1.4588 | 0.684 | -0.21964 | -1.6255 | -5.0525 | -9.7584 | -12.5466 | -13.9873 | 7.9712 | 7.7934 | 7.5741 | 7.2763 | 6.9558 | 6.6154 | 6.2379 | 5.7955 | 5.1275 | 2.7811 | -0.53116 | -2.7667 | -4.7335 | 6.4466 | 6.1832 | 5.8487 | 5.2427 | 4.5948 | 3.9011 | 3.1195 | 2.2034 | 0.78906 | -2.7477 | -7.8824 | -10.937 | -12.2142
BRAMLEY (FLEE) | CAMBERLEY MAIN | CAMBERLEY | MINIMUM HEADROOM | SU 86584 59452 | YES | 78.4168 | 78.1535 | 77.88 | 77.5939 | 77.2819 | 76.7367 | 75.8094 | 74.715 | 73.0705 | 69.1654 | 62.4477 | 57.8109 | 55.1726 | 67.7974 | 67.5121 | 67.2204 | 66.8601 | 66.4757 | 66.0681 | 65.6143 | 65.0785 | 64.1996 | 61.5518 | 57.1767 | 53.7531 | 50.308 | 73.4666 | 72.9725 | 72.4206 | 71.7574 | 71.0418 | 70.2679 | 69.3928 | 68.3514 | 66.8185 | 63.319 | 57.2441 | 53.2047 | 50.9525
|  | CAMBERLEY | CT |  |  | 78.4168 | 78.1535 | 77.88 | 77.5939 | 77.2819 | 76.7367 | 75.8094 | 74.715 | 73.0705 | 69.1654 | 62.4477 | 57.8109 | 55.1726 | 67.7974 | 67.5121 | 67.2204 | 66.8601 | 66.4757 | 66.0681 | 65.6143 | 65.0785 | 64.1996 | 61.5518 | 57.1767 | 53.7531 | 50.308 | 73.4666 | 72.9725 | 72.4206 | 71.7574 | 71.0418 | 70.2679 | 69.3928 | 68.3514 | 66.8185 | 63.319 | 57.2441 | 53.2047 | 50.9525
|  | CAMBERLEY | LW |  |  | 78.4168 | 78.1535 | 77.88 | 77.5939 | 77.2819 | 76.7367 | 75.8094 | 74.715 | 73.0705 | 69.1654 | 62.4477 | 57.8109 | 55.1726 | 67.7974 | 67.5121 | 67.2204 | 66.8601 | 66.4757 | 66.0681 | 65.6143 | 65.0785 | 64.1996 | 61.5518 | 57.1767 | 53.7531 | 50.308 | 73.4666 | 72.9725 | 72.4206 | 71.7574 | 71.0418 | 70.2679 | 69.3928 | 68.3514 | 66.8185 | 63.319 | 57.2441 | 53.2047 | 50.9525
|  | CAMBERLEY | ST |  |  | 78.4168 | 78.1535 | 77.88 | 77.5939 | 77.2819 | 76.7367 | 75.8094 | 74.715 | 73.0705 | 69.1654 | 62.4477 | 57.8109 | 55.1726 | 67.7974 | 67.5121 | 67.2204 | 66.8601 | 66.4757 | 66.0681 | 65.6143 | 65.0785 | 64.1996 | 61.5518 | 57.1767 | 53.7531 | 50.308 | 73.4666 | 72.9725 | 72.4206 | 71.7574 | 71.0418 | 70.2679 | 69.3928 | 68.3514 | 66.8185 | 63.319 | 57.2441 | 53.2047 | 50.9525
|  | CAMBERLEY | FS |  |  | 78.4168 | 78.1535 | 77.88 | 77.5939 | 77.2819 | 76.7367 | 75.8094 | 74.715 | 73.0705 | 69.1654 | 62.4477 | 57.8109 | 55.1726 | 67.7974 | 67.5121 | 67.2204 | 66.8601 | 66.4757 | 66.0681 | 65.6143 | 65.0785 | 64.1996 | 61.5518 | 57.1767 | 53.7531 | 50.308 | 73.4666 | 72.9725 | 72.4206 | 71.7574 | 71.0418 | 70.2679 | 69.3928 | 68.3514 | 66.8185 | 63.319 | 57.2441 | 53.2047 | 50.9525
WILLESDEN GSP | CANAL BANK | CANAL BANK 11kV | MINIMUM HEADROOM | TQ 20927 83082 | YES | 6.5198 | 6.4692 | 6.4112 | 6.3468 | 6.2763 | 6.2011 | 6.1179 | 5.987 | 5.7873 | 5.1062 | 3.5406 | 2.1469 | 1.1115 | -0.68823 | -0.74208 | -0.8034 | -0.88467 | -0.97239 | -1.0591 | -1.155 | -1.263 | -1.3972 | -1.8694 | -2.9701 | -4.2332 | -6.3279 | 2.693 | 2.6353 | 2.5697 | 2.4798 | 2.3834 | 2.2938 | 2.1958 | 2.0861 | 1.9407 | 1.3227 | -0.037227 | -1.1315 | -1.9095
|  | CANAL BANK 11kV | CT |  |  | 6.5198 | 6.4692 | 6.4112 | 6.3468 | 6.2763 | 6.2011 | 6.1179 | 5.987 | 5.7873 | 5.1062 | 3.5406 | 2.1469 | 1.1115 | -0.68823 | -0.74208 | -0.8034 | -0.88467 | -0.97239 | -1.0591 | -1.155 | -1.263 | -1.3972 | -1.8694 | -2.9701 | -4.2332 | -6.3279 | 2.693 | 2.6353 | 2.5697 | 2.4798 | 2.3834 | 2.2938 | 2.1958 | 2.0861 | 1.9407 | 1.3227 | -0.037227 | -1.1315 | -1.9095
|  | CANAL BANK 11kV | LW |  |  | 6.5198 | 6.4692 | 6.4112 | 6.3468 | 6.2763 | 6.2011 | 6.1179 | 5.987 | 5.7873 | 5.1062 | 3.5406 | 2.1469 | 1.1115 | -0.68823 | -0.74208 | -0.8034 | -0.88467 | -0.97239 | -1.0591 | -1.155 | -1.263 | -1.3972 | -1.8694 | -2.9701 | -4.2332 | -6.3279 | 2.693 | 2.6353 | 2.5697 | 2.4798 | 2.3834 | 2.2938 | 2.1958 | 2.0861 | 1.9407 | 1.3227 | -0.037227 | -1.1315 | -1.9095
|  | CANAL BANK 11kV | ST |  |  | 6.5198 | 6.4692 | 6.4112 | 6.3468 | 6.2763 | 6.2011 | 6.1179 | 5.987 | 5.7873 | 5.1062 | 3.5406 | 2.1469 | 1.1115 | -0.68823 | -0.74208 | -0.8034 | -0.88467 | -0.97239 | -1.0591 | -1.155 | -1.263 | -1.3972 | -1.8694 | -2.9701 | -4.2332 | -6.3279 | 2.693 | 2.6353 | 2.5697 | 2.4798 | 2.3834 | 2.2938 | 2.1958 | 2.0861 | 1.9407 | 1.3227 | -0.037227 | -1.1315 | -1.9095
|  | CANAL BANK 11kV | FS |  |  | 6.5198 | 6.4692 | 6.4112 | 6.3468 | 6.2763 | 6.2011 | 6.1179 | 5.987 | 5.7873 | 5.1062 | 3.5406 | 2.1469 | 1.1115 | -0.68823 | -0.74208 | -0.8034 | -0.88467 | -0.97239 | -1.0591 | -1.155 | -1.263 | -1.3972 | -1.8694 | -2.9701 | -4.2332 | -6.3279 | 2.693 | 2.6353 | 2.5697 | 2.4798 | 2.3834 | 2.2938 | 2.1958 | 2.0861 | 1.9407 | 1.3227 | -0.037227 | -1.1315 | -1.9095
WILLESDEN GSP | ACTON LANE | CANAL BANK 6.6kV | MINIMUM HEADROOM | TQ 20927 83082 | YES | -0.46687 | -0.47279 | -0.47959 | -0.4872 | -0.49554 | -0.50442 | -0.51425 | -0.52571 | -0.53956 | -0.59917 | -0.72814 | -0.82427 | -0.89491 | -0.022709 | -0.02787 | -0.033817 | -0.040556 | -0.047963 | -0.055991 | -0.064925 | -0.075342 | -0.087998 | -0.13269 | -0.22594 | -0.33417 | -0.47204 | -0.33099 | -0.33633 | -0.34248 | -0.34933 | -0.35685 | -0.36492 | -0.37388 | -0.38437 | -0.39704 | -0.44208 | -0.52952 | -0.5786 | -0.61656
|  | CANAL BANK 6.6kV | CT |  |  | -0.46687 | -0.47279 | -0.47959 | -0.4872 | -0.49554 | -0.50442 | -0.51425 | -0.52571 | -0.53956 | -0.59917 | -0.72814 | -0.82427 | -0.89491 | -0.022709 | -0.02787 | -0.033817 | -0.040556 | -0.047963 | -0.055991 | -0.064925 | -0.075342 | -0.087998 | -0.13269 | -0.22594 | -0.33417 | -0.47204 | -0.33099 | -0.33633 | -0.34248 | -0.34933 | -0.35685 | -0.36492 | -0.37388 | -0.38437 | -0.39704 | -0.44208 | -0.52952 | -0.5786 | -0.61656
|  | CANAL BANK 6.6kV | LW |  |  | -0.46687 | -0.47279 | -0.47959 | -0.4872 | -0.49554 | -0.50442 | -0.51425 | -0.52571 | -0.53956 | -0.59917 | -0.72814 | -0.82427 | -0.89491 | -0.022709 | -0.02787 | -0.033817 | -0.040556 | -0.047963 | -0.055991 | -0.064925 | -0.075342 | -0.087998 | -0.13269 | -0.22594 | -0.33417 | -0.47204 | -0.33099 | -0.33633 | -0.34248 | -0.34933 | -0.35685 | -0.36492 | -0.37388 | -0.38437 | -0.39704 | -0.44208 | -0.52952 | -0.5786 | -0.61656
|  | CANAL BANK 6.6kV | ST |  |  | -0.46687 | -0.47279 | -0.47959 | -0.4872 | -0.49554 | -0.50442 | -0.51425 | -0.52571 | -0.53956 | -0.59917 | -0.72814 | -0.82427 | -0.89491 | -0.022709 | -0.02787 | -0.033817 | -0.040556 | -0.047963 | -0.055991 | -0.064925 | -0.075342 | -0.087998 | -0.13269 | -0.22594 | -0.33417 | -0.47204 | -0.33099 | -0.33633 | -0.34248 | -0.34933 | -0.35685 | -0.36492 | -0.37388 | -0.38437 | -0.39704 | -0.44208 | -0.52952 | -0.5786 | -0.61656
|  | CANAL BANK 6.6kV | FS |  |  | -0.46687 | -0.47279 | -0.47959 | -0.4872 | -0.49554 | -0.50442 | -0.51425 | -0.52571 | -0.53956 | -0.59917 | -0.72814 | -0.82427 | -0.89491 | -0.022709 | -0.02787 | -0.033817 | -0.040556 | -0.047963 | -0.055991 | -0.064925 | -0.075342 | -0.087998 | -0.13269 | -0.22594 | -0.33417 | -0.47204 | -0.33099 | -0.33633 | -0.34248 | -0.34933 | -0.35685 | -0.36492 | -0.37388 | -0.38437 | -0.39704 | -0.44208 | -0.52952 | -0.5786 | -0.61656
COWLEY GSP | WITNEY BSP | CARTERTON | MINIMUM HEADROOM | SP 28261 07823 | NO | 21.643 | 21.3628 | 21.0401 | 20.649 | 20.1912 | 19.9631 | 19.748 | 19.512 | 19.1582 | 18.1948 | 16.8752 | 16.2917 | 15.8297 | 27.6801 | 27.5147 | 27.3223 | 27.1063 | 26.855 | 26.7188 | 26.5871 | 26.4366 | 26.2261 | 25.6596 | 24.8199 | 24.2052 | 23.4394 | 23.3939 | 23.1596 | 22.8838 | 22.5515 | 22.1634 | 21.9596 | 21.7649 | 21.5483 | 21.2233 | 20.3545 | 19.2111 | 18.7247 | 18.3452
|  | CARTERTON | CT |  |  | 21.643 | 21.3628 | 21.0401 | 20.649 | 20.1912 | 19.9631 | 19.748 | 19.512 | 19.1582 | 18.1948 | 16.8752 | 16.2917 | 15.8297 | 27.6801 | 27.5147 | 27.3223 | 27.1063 | 26.855 | 26.7188 | 26.5871 | 26.4366 | 26.2261 | 25.6596 | 24.8199 | 24.2052 | 23.4394 | 23.3939 | 23.1596 | 22.8838 | 22.5515 | 22.1634 | 21.9596 | 21.7649 | 21.5483 | 21.2233 | 20.3545 | 19.2111 | 18.7247 | 18.3452
|  | CARTERTON | LW |  |  | 21.643 | 21.3628 | 21.0401 | 20.649 | 20.1912 | 19.9631 | 19.748 | 19.512 | 19.1582 | 18.1948 | 16.8752 | 16.2917 | 15.8297 | 27.6801 | 27.5147 | 27.3223 | 27.1063 | 26.855 | 26.7188 | 26.5871 | 26.4366 | 26.2261 | 25.6596 | 24.8199 | 24.2052 | 23.4394 | 23.3939 | 23.1596 | 22.8838 | 22.5515 | 22.1634 | 21.9596 | 21.7649 | 21.5483 | 21.2233 | 20.3545 | 19.2111 | 18.7247 | 18.3452
|  | CARTERTON | ST |  |  | 21.643 | 21.3628 | 21.0401 | 20.649 | 20.1912 | 19.9631 | 19.748 | 19.512 | 19.1582 | 18.1948 | 16.8752 | 16.2917 | 15.8297 | 27.6801 | 27.5147 | 27.3223 | 27.1063 | 26.855 | 26.7188 | 26.5871 | 26.4366 | 26.2261 | 25.6596 | 24.8199 | 24.2052 | 23.4394 | 23.3939 | 23.1596 | 22.8838 | 22.5515 | 22.1634 | 21.9596 | 21.7649 | 21.5483 | 21.2233 | 20.3545 | 19.2111 | 18.7247 | 18.3452
|  | CARTERTON | FS |  |  | 21.643 | 21.3628 | 21.0401 | 20.649 | 20.1912 | 19.9631 | 19.748 | 19.512 | 19.1582 | 18.1948 | 16.8752 | 16.2917 | 15.8297 | 27.6801 | 27.5147 | 27.3223 | 27.1063 | 26.855 | 26.7188 | 26.5871 | 26.4366 | 26.2261 | 25.6596 | 24.8199 | 24.2052 | 23.4394 | 23.3939 | 23.1596 | 22.8838 | 22.5515 | 22.1634 | 21.9596 | 21.7649 | 21.5483 | 21.2233 | 20.3545 | 19.2111 | 18.7247 | 18.3452
AXMINSTER | YEOVIL BSP | CASTLE CARY | MINIMUM HEADROOM | ST 64534 31039 | YES | 5.2157 | 5.0064 | 4.7678 | 4.4465 | 4.111 | 3.78 | 3.4713 | 3.1532 | 2.6937 | 1.6184 | 0.038724 | -0.47815 | -0.60859 | 7.2668 | 7.142 | 6.9943 | 6.8249 | 6.6478 | 6.4694 | 6.29 | 6.0966 | 5.8321 | 5.274 | 4.5615 | 4.2261 | 4.0294 | 5.8151 | 5.6255 | 5.4044 | 5.1126 | 4.8075 | 4.5051 | 4.2184 | 3.9197 | 3.4803 | 2.4267 | 0.87081 | 0.3647 | 0.23884
|  | CASTLE CARY | CT |  |  | 5.2157 | 5.0064 | 4.7678 | 4.4465 | 4.111 | 3.78 | 3.4713 | 3.1532 | 2.6937 | 1.6184 | 0.038724 | -0.47815 | -0.60859 | 7.2668 | 7.142 | 6.9943 | 6.8249 | 6.6478 | 6.4694 | 6.29 | 6.0966 | 5.8321 | 5.274 | 4.5615 | 4.2261 | 4.0294 | 5.8151 | 5.6255 | 5.4044 | 5.1126 | 4.8075 | 4.5051 | 4.2184 | 3.9197 | 3.4803 | 2.4267 | 0.87081 | 0.3647 | 0.23884
|  | CASTLE CARY | LW |  |  | 5.2157 | 5.0064 | 4.7678 | 4.4465 | 4.111 | 3.78 | 3.4713 | 3.1532 | 2.6937 | 1.6184 | 0.038724 | -0.47815 | -0.60859 | 7.2668 | 7.142 | 6.9943 | 6.8249 | 6.6478 | 6.4694 | 6.29 | 6.0966 | 5.8321 | 5.274 | 4.5615 | 4.2261 | 4.0294 | 5.8151 | 5.6255 | 5.4044 | 5.1126 | 4.8075 | 4.5051 | 4.2184 | 3.9197 | 3.4803 | 2.4267 | 0.87081 | 0.3647 | 0.23884
|  | CASTLE CARY | ST |  |  | 5.2157 | 5.0064 | 4.7678 | 4.4465 | 4.111 | 3.78 | 3.4713 | 3.1532 | 2.6937 | 1.6184 | 0.038724 | -0.47815 | -0.60859 | 7.2668 | 7.142 | 6.9943 | 6.8249 | 6.6478 | 6.4694 | 6.29 | 6.0966 | 5.8321 | 5.274 | 4.5615 | 4.2261 | 4.0294 | 5.8151 | 5.6255 | 5.4044 | 5.1126 | 4.8075 | 4.5051 | 4.2184 | 3.9197 | 3.4803 | 2.4267 | 0.87081 | 0.3647 | 0.23884
|  | CASTLE CARY | FS |  |  | 5.2157 | 5.0064 | 4.7678 | 4.4465 | 4.111 | 3.78 | 3.4713 | 3.1532 | 2.6937 | 1.6184 | 0.038724 | -0.47815 | -0.60859 | 7.2668 | 7.142 | 6.9943 | 6.8249 | 6.6478 | 6.4694 | 6.29 | 6.0966 | 5.8321 | 5.274 | 4.5615 | 4.2261 | 4.0294 | 5.8151 | 5.6255 | 5.4044 | 5.1126 | 4.8075 | 4.5051 | 4.2184 | 3.9197 | 3.4803 | 2.4267 | 0.87081 | 0.3647 | 0.23884
LALEHAM | STAINES | CAUSEWAY | MINIMUM HEADROOM | TQ 02763 71680 | YES | 22.4181 | 21.8589 | 21.4059 | 20.8499 | 20.0469 | 19.0652 | 17.9669 | 17.0328 | 15.7442 | 12.3838 | 6.6634 | 2.4739 | -0.21378 | 25.7147 | 25.4264 | 25.1766 | 24.8891 | 24.4759 | 23.9233 | 23.3065 | 22.7486 | 22.0163 | 20.0113 | 16.4418 | 13.4945 | 10.47 | 24.8148 | 24.5291 | 24.2892 | 24.0517 | 23.7049 | 23.1573 | 22.1756 | 21.3028 | 20.0932 | 16.9738 | 11.8611 | 8.2757 | 6.0278
|  | CAUSEWAY | CT |  |  | 22.4181 | 21.8589 | 21.4059 | 20.8499 | 20.0469 | 19.0652 | 17.9669 | 17.0328 | 15.7442 | 12.3838 | 6.6634 | 2.4739 | -0.21378 | 25.7147 | 25.4264 | 25.1766 | 24.8891 | 24.4759 | 23.9233 | 23.3065 | 22.7486 | 22.0163 | 20.0113 | 16.4418 | 13.4945 | 10.47 | 24.8148 | 24.5291 | 24.2892 | 24.0517 | 23.7049 | 23.1573 | 22.1756 | 21.3028 | 20.0932 | 16.9738 | 11.8611 | 8.2757 | 6.0278
|  | CAUSEWAY | LW |  |  | 22.4181 | 21.8589 | 21.4059 | 20.8499 | 20.0469 | 19.0652 | 17.9669 | 17.0328 | 15.7442 | 12.3838 | 6.6634 | 2.4739 | -0.21378 | 25.7147 | 25.4264 | 25.1766 | 24.8891 | 24.4759 | 23.9233 | 23.3065 | 22.7486 | 22.0163 | 20.0113 | 16.4418 | 13.4945 | 10.47 | 24.8148 | 24.5291 | 24.2892 | 24.0517 | 23.7049 | 23.1573 | 22.1756 | 21.3028 | 20.0932 | 16.9738 | 11.8611 | 8.2757 | 6.0278
|  | CAUSEWAY | ST |  |  | 22.4181 | 21.8589 | 21.4059 | 20.8499 | 20.0469 | 19.0652 | 17.9669 | 17.0328 | 15.7442 | 12.3838 | 6.6634 | 2.4739 | -0.21378 | 25.7147 | 25.4264 | 25.1766 | 24.8891 | 24.4759 | 23.9233 | 23.3065 | 22.7486 | 22.0163 | 20.0113 | 16.4418 | 13.4945 | 10.47 | 24.8148 | 24.5291 | 24.2892 | 24.0517 | 23.7049 | 23.1573 | 22.1756 | 21.3028 | 20.0932 | 16.9738 | 11.8611 | 8.2757 | 6.0278
|  | CAUSEWAY | FS |  |  | 22.4181 | 21.8589 | 21.4059 | 20.8499 | 20.0469 | 19.0652 | 17.9669 | 17.0328 | 15.7442 | 12.3838 | 6.6634 | 2.4739 | -0.21378 | 25.7147 | 25.4264 | 25.1766 | 24.8891 | 24.4759 | 23.9233 | 23.3065 | 22.7486 | 22.0163 | 20.0113 | 16.4418 | 13.4945 | 10.47 | 24.8148 | 24.5291 | 24.2892 | 24.0517 | 23.7049 | 23.1573 | 22.1756 | 21.3028 | 20.0932 | 16.9738 | 11.8611 | 8.2757 | 6.0278
BRAMLEY (FLEE) | READING TOWN BSP | CAVERSHAM | MINIMUM HEADROOM | SU 71512 75747 | YES | 23.8253 | 23.4207 | 22.9574 | 22.3457 | 21.6924 | 21.0108 | 20.27 | 19.3976 | 17.8485 | 13.9691 | 8.1685 | 3.8674 | 1.5038 | 23.1126 | 22.782 | 22.4007 | 21.9718 | 21.5083 | 21.0057 | 20.4528 | 19.7869 | 18.7126 | 16.0951 | 12.4689 | 9.315 | 6.0425 | 22.5448 | 22.1909 | 21.7856 | 21.2382 | 20.6542 | 20.0467 | 19.3871 | 18.5705 | 17.0989 | 13.4664 | 8.2814 | 4.4975 | 2.3986
|  | CAVERSHAM | CT |  |  | 23.8253 | 23.4207 | 22.9574 | 22.3457 | 21.6924 | 21.0108 | 20.27 | 19.3976 | 17.8485 | 13.9691 | 8.1685 | 3.8674 | 1.5038 | 23.1126 | 22.782 | 22.4007 | 21.9718 | 21.5083 | 21.0057 | 20.4528 | 19.7869 | 18.7126 | 16.0951 | 12.4689 | 9.315 | 6.0425 | 22.5448 | 22.1909 | 21.7856 | 21.2382 | 20.6542 | 20.0467 | 19.3871 | 18.5705 | 17.0989 | 13.4664 | 8.2814 | 4.4975 | 2.3986
|  | CAVERSHAM | LW |  |  | 23.8253 | 23.4207 | 22.9574 | 22.3457 | 21.6924 | 21.0108 | 20.27 | 19.3976 | 17.8485 | 13.9691 | 8.1685 | 3.8674 | 1.5038 | 23.1126 | 22.782 | 22.4007 | 21.9718 | 21.5083 | 21.0057 | 20.4528 | 19.7869 | 18.7126 | 16.0951 | 12.4689 | 9.315 | 6.0425 | 22.5448 | 22.1909 | 21.7856 | 21.2382 | 20.6542 | 20.0467 | 19.3871 | 18.5705 | 17.0989 | 13.4664 | 8.2814 | 4.4975 | 2.3986
|  | CAVERSHAM | ST |  |  | 23.8253 | 23.4207 | 22.9574 | 22.3457 | 21.6924 | 21.0108 | 20.27 | 19.3976 | 17.8485 | 13.9691 | 8.1685 | 3.8674 | 1.5038 | 23.1126 | 22.782 | 22.4007 | 21.9718 | 21.5083 | 21.0057 | 20.4528 | 19.7869 | 18.7126 | 16.0951 | 12.4689 | 9.315 | 6.0425 | 22.5448 | 22.1909 | 21.7856 | 21.2382 | 20.6542 | 20.0467 | 19.3871 | 18.5705 | 17.0989 | 13.4664 | 8.2814 | 4.4975 | 2.3986
|  | CAVERSHAM | FS |  |  | 23.8253 | 23.4207 | 22.9574 | 22.3457 | 21.6924 | 21.0108 | 20.27 | 19.3976 | 17.8485 | 13.9691 | 8.1685 | 3.8674 | 1.5038 | 23.1126 | 22.782 | 22.4007 | 21.9718 | 21.5083 | 21.0057 | 20.4528 | 19.7869 | 18.7126 | 16.0951 | 12.4689 | 9.315 | 6.0425 | 22.5448 | 22.1909 | 21.7856 | 21.2382 | 20.6542 | 20.0467 | 19.3871 | 18.5705 | 17.0989 | 13.4664 | 8.2814 | 4.4975 | 2.3986
MANNINGTON GSP | BOURNEMOUTH | CENTRAL | MINIMUM HEADROOM | SZ 10293 91931 | YES | 12.7253 | 12.2193 | 11.5659 | 10.5225 | 9.4073 | 8.3165 | 7.1113 | 5.7216 | 3.6526 | -2.9272 | -14.5305 | -22.0397 | -26.0696 | 18.9043 | 18.4791 | 17.9223 | 17.196 | 16.4045 | 15.5702 | 14.6384 | 13.5359 | 12.126 | 7.3961 | -1.5495 | -9.8726 | -20.6658 | 13.8716 | 13.4126 | 12.8027 | 11.8702 | 10.8412 | 9.8261 | 8.7045 | 7.4022 | 5.487 | -0.62351 | -11.1537 | -17.6239 | -20.8977
|  | CENTRAL | CT |  |  | 12.7253 | 12.2193 | 11.5659 | 10.5225 | 9.4073 | 8.3165 | 7.1113 | 5.7216 | 3.6526 | -2.9272 | -14.5305 | -22.0397 | -26.0696 | 18.9043 | 18.4791 | 17.9223 | 17.196 | 16.4045 | 15.5702 | 14.6384 | 13.5359 | 12.126 | 7.3961 | -1.5495 | -9.8726 | -20.6658 | 13.8716 | 13.4126 | 12.8027 | 11.8702 | 10.8412 | 9.8261 | 8.7045 | 7.4022 | 5.487 | -0.62351 | -11.1537 | -17.6239 | -20.8977
|  | CENTRAL | LW |  |  | 12.7253 | 12.2193 | 11.5659 | 10.5225 | 9.4073 | 8.3165 | 7.1113 | 5.7216 | 3.6526 | -2.9272 | -14.5305 | -22.0397 | -26.0696 | 18.9043 | 18.4791 | 17.9223 | 17.196 | 16.4045 | 15.5702 | 14.6384 | 13.5359 | 12.126 | 7.3961 | -1.5495 | -9.8726 | -20.6658 | 13.8716 | 13.4126 | 12.8027 | 11.8702 | 10.8412 | 9.8261 | 8.7045 | 7.4022 | 5.487 | -0.62351 | -11.1537 | -17.6239 | -20.8977
|  | CENTRAL | ST |  |  | 12.7253 | 12.2193 | 11.5659 | 10.5225 | 9.4073 | 8.3165 | 7.1113 | 5.7216 | 3.6526 | -2.9272 | -14.5305 | -22.0397 | -26.0696 | 18.9043 | 18.4791 | 17.9223 | 17.196 | 16.4045 | 15.5702 | 14.6384 | 13.5359 | 12.126 | 7.3961 | -1.5495 | -9.8726 | -20.6658 | 13.8716 | 13.4126 | 12.8027 | 11.8702 | 10.8412 | 9.8261 | 8.7045 | 7.4022 | 5.487 | -0.62351 | -11.1537 | -17.6239 | -20.8977
|  | CENTRAL | FS |  |  | 12.7253 | 12.2193 | 11.5659 | 10.5225 | 9.4073 | 8.3165 | 7.1113 | 5.7216 | 3.6526 | -2.9272 | -14.5305 | -22.0397 | -26.0696 | 18.9043 | 18.4791 | 17.9223 | 17.196 | 16.4045 | 15.5702 | 14.6384 | 13.5359 | 12.126 | 7.3961 | -1.5495 | -9.8726 | -20.6658 | 13.8716 | 13.4126 | 12.8027 | 11.8702 | 10.8412 | 9.8261 | 8.7045 | 7.4022 | 5.487 | -0.62351 | -11.1537 | -17.6239 | -20.8977
NURSLING GSP | SOUTHAMPTON (2 X 60) | CENTRAL BRIDGE | MINIMUM HEADROOM | SU 42591 11255 | YES | 35.2391 | 34.0742 | 33.3767 | 32.8043 | 32.2125 | 31.7285 | 31.1391 | 30.4891 | 29.8145 | 27.6823 | 23.5391 | 20.5543 | 18.5046 | 39.5209 | 38.7705 | 38.2588 | 37.7934 | 37.3003 | 36.8248 | 36.2181 | 35.5027 | 34.842 | 32.5934 | 27.4251 | 20.749 | 10.7203 | 35.8551 | 34.9196 | 34.3377 | 33.8527 | 33.3484 | 32.9279 | 32.3806 | 31.7486 | 31.1288 | 29.1614 | 25.546 | 23.0923 | 21.4284
|  | CENTRAL BRIDGE | CT |  |  | 35.2391 | 34.0742 | 33.3767 | 32.8043 | 32.2125 | 31.7285 | 31.1391 | 30.4891 | 29.8145 | 27.6823 | 23.5391 | 20.5543 | 18.5046 | 39.5209 | 38.7705 | 38.2588 | 37.7934 | 37.3003 | 36.8248 | 36.2181 | 35.5027 | 34.842 | 32.5934 | 27.4251 | 20.749 | 10.7203 | 35.8551 | 34.9196 | 34.3377 | 33.8527 | 33.3484 | 32.9279 | 32.3806 | 31.7486 | 31.1288 | 29.1614 | 25.546 | 23.0923 | 21.4284
|  | CENTRAL BRIDGE | LW |  |  | 35.2391 | 34.0742 | 33.3767 | 32.8043 | 32.2125 | 31.7285 | 31.1391 | 30.4891 | 29.8145 | 27.6823 | 23.5391 | 20.5543 | 18.5046 | 39.5209 | 38.7705 | 38.2588 | 37.7934 | 37.3003 | 36.8248 | 36.2181 | 35.5027 | 34.842 | 32.5934 | 27.4251 | 20.749 | 10.7203 | 35.8551 | 34.9196 | 34.3377 | 33.8527 | 33.3484 | 32.9279 | 32.3806 | 31.7486 | 31.1288 | 29.1614 | 25.546 | 23.0923 | 21.4284
|  | CENTRAL BRIDGE | ST |  |  | 35.2391 | 34.0742 | 33.3767 | 32.8043 | 32.2125 | 31.7285 | 31.1391 | 30.4891 | 29.8145 | 27.6823 | 23.5391 | 20.5543 | 18.5046 | 39.5209 | 38.7705 | 38.2588 | 37.7934 | 37.3003 | 36.8248 | 36.2181 | 35.5027 | 34.842 | 32.5934 | 27.4251 | 20.749 | 10.7203 | 35.8551 | 34.9196 | 34.3377 | 33.8527 | 33.3484 | 32.9279 | 32.3806 | 31.7486 | 31.1288 | 29.1614 | 25.546 | 23.0923 | 21.4284
|  | CENTRAL BRIDGE | FS |  |  | 35.2391 | 34.0742 | 33.3767 | 32.8043 | 32.2125 | 31.7285 | 31.1391 | 30.4891 | 29.8145 | 27.6823 | 23.5391 | 20.5543 | 18.5046 | 39.5209 | 38.7705 | 38.2588 | 37.7934 | 37.3003 | 36.8248 | 36.2181 | 35.5027 | 34.842 | 32.5934 | 27.4251 | 20.749 | 10.7203 | 35.8551 | 34.9196 | 34.3377 | 33.8527 | 33.3484 | 32.9279 | 32.3806 | 31.7486 | 31.1288 | 29.1614 | 25.546 | 23.0923 | 21.4284
CHICKERELL GSP | CHICKERELL BSP | CERNE ABBAS | MINIMUM HEADROOM | ST 66140 01039 | YES | 0.77544 | 0.75374 | 0.73165 | 0.68902 | 0.64537 | 0.59752 | 0.55021 | 0.50474 | 0.44275 | 0.24534 | -0.13464 | -0.21515 | -0.23855 | 1.0598 | 1.0503 | 1.0402 | 1.0251 | 1.0084 | 0.99089 | 0.97237 | 0.95363 | 0.92708 | 0.82629 | 0.67954 | 0.63413 | 0.60215 | 0.71853 | 0.71206 | 0.69348 | 0.65356 | 0.61212 | 0.56708 | 0.52197 | 0.47829 | 0.41815 | 0.2302 | -0.097136 | -0.16844 | -0.18929
|  | CERNE ABBAS | CT |  |  | 0.77544 | 0.75374 | 0.73165 | 0.68902 | 0.64537 | 0.59752 | 0.55021 | 0.50474 | 0.44275 | 0.24534 | -0.13464 | -0.21515 | -0.23855 | 1.0598 | 1.0503 | 1.0402 | 1.0251 | 1.0084 | 0.99089 | 0.97237 | 0.95363 | 0.92708 | 0.82629 | 0.67954 | 0.63413 | 0.60215 | 0.71853 | 0.71206 | 0.69348 | 0.65356 | 0.61212 | 0.56708 | 0.52197 | 0.47829 | 0.41815 | 0.2302 | -0.097136 | -0.16844 | -0.18929
|  | CERNE ABBAS | LW |  |  | 0.77544 | 0.75374 | 0.73165 | 0.68902 | 0.64537 | 0.59752 | 0.55021 | 0.50474 | 0.44275 | 0.24534 | -0.13464 | -0.21515 | -0.23855 | 1.0598 | 1.0503 | 1.0402 | 1.0251 | 1.0084 | 0.99089 | 0.97237 | 0.95363 | 0.92708 | 0.82629 | 0.67954 | 0.63413 | 0.60215 | 0.71853 | 0.71206 | 0.69348 | 0.65356 | 0.61212 | 0.56708 | 0.52197 | 0.47829 | 0.41815 | 0.2302 | -0.097136 | -0.16844 | -0.18929
|  | CERNE ABBAS | ST |  |  | 0.77544 | 0.75374 | 0.73165 | 0.68902 | 0.64537 | 0.59752 | 0.55021 | 0.50474 | 0.44275 | 0.24534 | -0.13464 | -0.21515 | -0.23855 | 1.0598 | 1.0503 | 1.0402 | 1.0251 | 1.0084 | 0.99089 | 0.97237 | 0.95363 | 0.92708 | 0.82629 | 0.67954 | 0.63413 | 0.60215 | 0.71853 | 0.71206 | 0.69348 | 0.65356 | 0.61212 | 0.56708 | 0.52197 | 0.47829 | 0.41815 | 0.2302 | -0.097136 | -0.16844 | -0.18929
|  | CERNE ABBAS | FS |  |  | 0.77544 | 0.75374 | 0.73165 | 0.68902 | 0.64537 | 0.59752 | 0.55021 | 0.50474 | 0.44275 | 0.24534 | -0.13464 | -0.21515 | -0.23855 | 1.0598 | 1.0503 | 1.0402 | 1.0251 | 1.0084 | 0.99089 | 0.97237 | 0.95363 | 0.92708 | 0.82629 | 0.67954 | 0.63413 | 0.60215 | 0.71853 | 0.71206 | 0.69348 | 0.65356 | 0.61212 | 0.56708 | 0.52197 | 0.47829 | 0.41815 | 0.2302 | -0.097136 | -0.16844 | -0.18929
IVER 132KV | CHALVEY BSP | CHALVEY | MINIMUM HEADROOM | SU 96669 79364 | YES | 54.4464 | 52.7799 | 50.841 | 48.587 | 46.2487 | 44.1287 | 41.7796 | 39.1165 | 35.5318 | 25.8827 | 11.5479 | 2.4659 | -2.1892 | 61.2754 | 60.1 | 58.7178 | 57.189 | 55.5886 | 54.0413 | 52.3188 | 50.3464 | 47.8138 | 40.473 | 28.4586 | 16.2315 | -0.057694 | 56.8121 | 55.3866 | 53.6823 | 51.75 | 49.7244 | 47.8466 | 45.76 | 43.3746 | 40.1712 | 31.5167 | 18.7132 | 10.7608 | 6.7544
|  | CHALVEY | CT |  |  | 54.4464 | 52.7799 | 50.841 | 48.587 | 46.2487 | 44.1287 | 41.7796 | 39.1165 | 35.5318 | 25.8827 | 11.5479 | 2.4659 | -2.1892 | 61.2754 | 60.1 | 58.7178 | 57.189 | 55.5886 | 54.0413 | 52.3188 | 50.3464 | 47.8138 | 40.473 | 28.4586 | 16.2315 | -0.057694 | 56.8121 | 55.3866 | 53.6823 | 51.75 | 49.7244 | 47.8466 | 45.76 | 43.3746 | 40.1712 | 31.5167 | 18.7132 | 10.7608 | 6.7544
|  | CHALVEY | LW |  |  | 54.4464 | 52.7799 | 50.841 | 48.587 | 46.2487 | 44.1287 | 41.7796 | 39.1165 | 35.5318 | 25.8827 | 11.5479 | 2.4659 | -2.1892 | 61.2754 | 60.1 | 58.7178 | 57.189 | 55.5886 | 54.0413 | 52.3188 | 50.3464 | 47.8138 | 40.473 | 28.4586 | 16.2315 | -0.057694 | 56.8121 | 55.3866 | 53.6823 | 51.75 | 49.7244 | 47.8466 | 45.76 | 43.3746 | 40.1712 | 31.5167 | 18.7132 | 10.7608 | 6.7544
|  | CHALVEY | ST |  |  | 54.4464 | 52.7799 | 50.841 | 48.587 | 46.2487 | 44.1287 | 41.7796 | 39.1165 | 35.5318 | 25.8827 | 11.5479 | 2.4659 | -2.1892 | 61.2754 | 60.1 | 58.7178 | 57.189 | 55.5886 | 54.0413 | 52.3188 | 50.3464 | 47.8138 | 40.473 | 28.4586 | 16.2315 | -0.057694 | 56.8121 | 55.3866 | 53.6823 | 51.75 | 49.7244 | 47.8466 | 45.76 | 43.3746 | 40.1712 | 31.5167 | 18.7132 | 10.7608 | 6.7544
|  | CHALVEY | FS |  |  | 54.4464 | 52.7799 | 50.841 | 48.587 | 46.2487 | 44.1287 | 41.7796 | 39.1165 | 35.5318 | 25.8827 | 11.5479 | 2.4659 | -2.1892 | 61.2754 | 60.1 | 58.7178 | 57.189 | 55.5886 | 54.0413 | 52.3188 | 50.3464 | 47.8138 | 40.473 | 28.4586 | 16.2315 | -0.057694 | 56.8121 | 55.3866 | 53.6823 | 51.75 | 49.7244 | 47.8466 | 45.76 | 43.3746 | 40.1712 | 31.5167 | 18.7132 | 10.7608 | 6.7544
NURSLING GSP | VELMORE BSP | CHANDLERS FORD | MINIMUM HEADROOM | SU 43494 21552 | YES | 23.6802 | 23.1522 | 22.4944 | 21.6675 | 20.7403 | 19.7904 | 18.7958 | 17.5768 | 15.6999 | 11.242 | 4.1225 | -0.7112 | -3.4823 | 22.2822 | 21.8705 | 21.3651 | 20.8001 | 20.169 | 19.5032 | 18.7836 | 17.8817 | 16.5789 | 13.6313 | 9.3263 | 6.3364 | 3.685 | 22.9378 | 22.4333 | 21.8072 | 21.0358 | 20.174 | 19.2831 | 18.3374 | 17.1703 | 15.3818 | 11.21 | 4.8 | 0.62827 | -1.7069
|  | CHANDLERS FORD | CT |  |  | 23.6802 | 23.1522 | 22.4944 | 21.6675 | 20.7403 | 19.7904 | 18.7958 | 17.5768 | 15.6999 | 11.242 | 4.1225 | -0.7112 | -3.4823 | 22.2822 | 21.8705 | 21.3651 | 20.8001 | 20.169 | 19.5032 | 18.7836 | 17.8817 | 16.5789 | 13.6313 | 9.3263 | 6.3364 | 3.685 | 22.9378 | 22.4333 | 21.8072 | 21.0358 | 20.174 | 19.2831 | 18.3374 | 17.1703 | 15.3818 | 11.21 | 4.8 | 0.62827 | -1.7069
|  | CHANDLERS FORD | LW |  |  | 23.6802 | 23.1522 | 22.4944 | 21.6675 | 20.7403 | 19.7904 | 18.7958 | 17.5768 | 15.6999 | 11.242 | 4.1225 | -0.7112 | -3.4823 | 22.2822 | 21.8705 | 21.3651 | 20.8001 | 20.169 | 19.5032 | 18.7836 | 17.8817 | 16.5789 | 13.6313 | 9.3263 | 6.3364 | 3.685 | 22.9378 | 22.4333 | 21.8072 | 21.0358 | 20.174 | 19.2831 | 18.3374 | 17.1703 | 15.3818 | 11.21 | 4.8 | 0.62827 | -1.7069
|  | CHANDLERS FORD | ST |  |  | 23.6802 | 23.1522 | 22.4944 | 21.6675 | 20.7403 | 19.7904 | 18.7958 | 17.5768 | 15.6999 | 11.242 | 4.1225 | -0.7112 | -3.4823 | 22.2822 | 21.8705 | 21.3651 | 20.8001 | 20.169 | 19.5032 | 18.7836 | 17.8817 | 16.5789 | 13.6313 | 9.3263 | 6.3364 | 3.685 | 22.9378 | 22.4333 | 21.8072 | 21.0358 | 20.174 | 19.2831 | 18.3374 | 17.1703 | 15.3818 | 11.21 | 4.8 | 0.62827 | -1.7069
|  | CHANDLERS FORD | FS |  |  | 23.6802 | 23.1522 | 22.4944 | 21.6675 | 20.7403 | 19.7904 | 18.7958 | 17.5768 | 15.6999 | 11.242 | 4.1225 | -0.7112 | -3.4823 | 22.2822 | 21.8705 | 21.3651 | 20.8001 | 20.169 | 19.5032 | 18.7836 | 17.8817 | 16.5789 | 13.6313 | 9.3263 | 6.3364 | 3.685 | 22.9378 | 22.4333 | 21.8072 | 21.0358 | 20.174 | 19.2831 | 18.3374 | 17.1703 | 15.3818 | 11.21 | 4.8 | 0.62827 | -1.7069
NURSLING GSP | SOUTHAMPTON (2 X 60) | CHAPEL | MINIMUM HEADROOM | SU 42849 11983 | YES | 7.2821 | 7.0593 | 6.754 | 6.5224 | 6.3308 | 6.1164 | 5.8424 | 5.5869 | 5.228 | 4.0688 | 1.3808 | -0.99453 | -2.6582 | 9.1943 | 9.0457 | 8.8507 | 8.6878 | 8.5403 | 8.3745 | 8.1404 | 7.9282 | 7.6739 | 6.8166 | 4.7526 | 1.7162 | -2.4015 | 8.3812 | 8.2145 | 7.9876 | 7.8142 | 7.6682 | 7.4871 | 7.2368 | 7.0084 | 6.687 | 5.6508 | 3.2831 | 1.2097 | -0.23295
|  | CHAPEL | CT |  |  | 7.2821 | 7.0593 | 6.754 | 6.5224 | 6.3308 | 6.1164 | 5.8424 | 5.5869 | 5.228 | 4.0688 | 1.3808 | -0.99453 | -2.6582 | 9.1943 | 9.0457 | 8.8507 | 8.6878 | 8.5403 | 8.3745 | 8.1404 | 7.9282 | 7.6739 | 6.8166 | 4.7526 | 1.7162 | -2.4015 | 8.3812 | 8.2145 | 7.9876 | 7.8142 | 7.6682 | 7.4871 | 7.2368 | 7.0084 | 6.687 | 5.6508 | 3.2831 | 1.2097 | -0.23295
|  | CHAPEL | LW |  |  | 7.2821 | 7.0593 | 6.754 | 6.5224 | 6.3308 | 6.1164 | 5.8424 | 5.5869 | 5.228 | 4.0688 | 1.3808 | -0.99453 | -2.6582 | 9.1943 | 9.0457 | 8.8507 | 8.6878 | 8.5403 | 8.3745 | 8.1404 | 7.9282 | 7.6739 | 6.8166 | 4.7526 | 1.7162 | -2.4015 | 8.3812 | 8.2145 | 7.9876 | 7.8142 | 7.6682 | 7.4871 | 7.2368 | 7.0084 | 6.687 | 5.6508 | 3.2831 | 1.2097 | -0.23295
|  | CHAPEL | ST |  |  | 7.2821 | 7.0593 | 6.754 | 6.5224 | 6.3308 | 6.1164 | 5.8424 | 5.5869 | 5.228 | 4.0688 | 1.3808 | -0.99453 | -2.6582 | 9.1943 | 9.0457 | 8.8507 | 8.6878 | 8.5403 | 8.3745 | 8.1404 | 7.9282 | 7.6739 | 6.8166 | 4.7526 | 1.7162 | -2.4015 | 8.3812 | 8.2145 | 7.9876 | 7.8142 | 7.6682 | 7.4871 | 7.2368 | 7.0084 | 6.687 | 5.6508 | 3.2831 | 1.2097 | -0.23295
|  | CHAPEL | FS |  |  | 7.2821 | 7.0593 | 6.754 | 6.5224 | 6.3308 | 6.1164 | 5.8424 | 5.5869 | 5.228 | 4.0688 | 1.3808 | -0.99453 | -2.6582 | 9.1943 | 9.0457 | 8.8507 | 8.6878 | 8.5403 | 8.3745 | 8.1404 | 7.9282 | 7.6739 | 6.8166 | 4.7526 | 1.7162 | -2.4015 | 8.3812 | 8.2145 | 7.9876 | 7.8142 | 7.6682 | 7.4871 | 7.2368 | 7.0084 | 6.687 | 5.6508 | 3.2831 | 1.2097 | -0.23295
COWLEY GSP | YARNTON BSP | CHARLBURY | MINIMUM HEADROOM | SP 36034 18376 | NO | 12.7609 | 12.5486 | 12.2962 | 11.9313 | 11.5479 | 11.1528 | 10.7213 | 10.2225 | 9.4085 | 7.475 | 4.3512 | 2.7378 | 2.565 | 12.3798 | 12.246 | 12.0764 | 11.8818 | 11.6706 | 11.4484 | 11.1986 | 10.8886 | 10.4221 | 9.3939 | 7.978 | 7.212 | 6.8533 | 12.3453 | 12.1526 | 11.9251 | 11.59 | 11.2385 | 10.8771 | 10.4831 | 10.031 | 9.2897 | 7.5027 | 4.56 | 3.1223 | 2.9714
|  | CHARLBURY | CT |  |  | 12.7609 | 12.5486 | 12.2962 | 11.9313 | 11.5479 | 11.1528 | 10.7213 | 10.2225 | 9.4085 | 7.475 | 4.3512 | 2.7378 | 2.565 | 12.3798 | 12.246 | 12.0764 | 11.8818 | 11.6706 | 11.4484 | 11.1986 | 10.8886 | 10.4221 | 9.3939 | 7.978 | 7.212 | 6.8533 | 12.3453 | 12.1526 | 11.9251 | 11.59 | 11.2385 | 10.8771 | 10.4831 | 10.031 | 9.2897 | 7.5027 | 4.56 | 3.1223 | 2.9714
|  | CHARLBURY | LW |  |  | 12.7609 | 12.5486 | 12.2962 | 11.9313 | 11.5479 | 11.1528 | 10.7213 | 10.2225 | 9.4085 | 7.475 | 4.3512 | 2.7378 | 2.565 | 12.3798 | 12.246 | 12.0764 | 11.8818 | 11.6706 | 11.4484 | 11.1986 | 10.8886 | 10.4221 | 9.3939 | 7.978 | 7.212 | 6.8533 | 12.3453 | 12.1526 | 11.9251 | 11.59 | 11.2385 | 10.8771 | 10.4831 | 10.031 | 9.2897 | 7.5027 | 4.56 | 3.1223 | 2.9714
|  | CHARLBURY | ST |  |  | 12.7609 | 12.5486 | 12.2962 | 11.9313 | 11.5479 | 11.1528 | 10.7213 | 10.2225 | 9.4085 | 7.475 | 4.3512 | 2.7378 | 2.565 | 12.3798 | 12.246 | 12.0764 | 11.8818 | 11.6706 | 11.4484 | 11.1986 | 10.8886 | 10.4221 | 9.3939 | 7.978 | 7.212 | 6.8533 | 12.3453 | 12.1526 | 11.9251 | 11.59 | 11.2385 | 10.8771 | 10.4831 | 10.031 | 9.2897 | 7.5027 | 4.56 | 3.1223 | 2.9714
|  | CHARLBURY | FS |  |  | 12.7609 | 12.5486 | 12.2962 | 11.9313 | 11.5479 | 11.1528 | 10.7213 | 10.2225 | 9.4085 | 7.475 | 4.3512 | 2.7378 | 2.565 | 12.3798 | 12.246 | 12.0764 | 11.8818 | 11.6706 | 11.4484 | 11.1986 | 10.8886 | 10.4221 | 9.3939 | 7.978 | 7.212 | 6.8533 | 12.3453 | 12.1526 | 11.9251 | 11.59 | 11.2385 | 10.8771 | 10.4831 | 10.031 | 9.2897 | 7.5027 | 4.56 | 3.1223 | 2.9714
CHICKERELL GSP | CHICKERELL BSP | CHARMINSTER | MINIMUM HEADROOM | SY 67309 93186 | YES | 9.841 | 9.5276 | 9.2272 | 8.8408 | 8.3129 | 7.7573 | 7.1565 | 5.8175 | 4.109 | -1.4408 | -10.2794 | -12.3371 | -12.6702 | 10.5021 | 10.3051 | 10.0877 | 9.8587 | 9.5307 | 9.1759 | 8.7835 | 7.9814 | 6.9995 | 3.9962 | -0.46426 | -1.7188 | -2.6123 | 11.8681 | 11.5822 | 11.2798 | 10.9186 | 10.4324 | 9.9162 | 9.3543 | 8.1654 | 6.6727 | 1.9981 | -5.2353 | -6.889 | -7.1539
|  | CHARMINSTER | CT |  |  | 9.841 | 9.5276 | 9.2272 | 8.8408 | 8.3129 | 7.7573 | 7.1565 | 5.8175 | 4.109 | -1.4408 | -10.2794 | -12.3371 | -12.6702 | 10.5021 | 10.3051 | 10.0877 | 9.8587 | 9.5307 | 9.1759 | 8.7835 | 7.9814 | 6.9995 | 3.9962 | -0.46426 | -1.7188 | -2.6123 | 11.8681 | 11.5822 | 11.2798 | 10.9186 | 10.4324 | 9.9162 | 9.3543 | 8.1654 | 6.6727 | 1.9981 | -5.2353 | -6.889 | -7.1539
|  | CHARMINSTER | LW |  |  | 9.841 | 9.5276 | 9.2272 | 8.8408 | 8.3129 | 7.7573 | 7.1565 | 5.8175 | 4.109 | -1.4408 | -10.2794 | -12.3371 | -12.6702 | 10.5021 | 10.3051 | 10.0877 | 9.8587 | 9.5307 | 9.1759 | 8.7835 | 7.9814 | 6.9995 | 3.9962 | -0.46426 | -1.7188 | -2.6123 | 11.8681 | 11.5822 | 11.2798 | 10.9186 | 10.4324 | 9.9162 | 9.3543 | 8.1654 | 6.6727 | 1.9981 | -5.2353 | -6.889 | -7.1539
|  | CHARMINSTER | ST |  |  | 9.841 | 9.5276 | 9.2272 | 8.8408 | 8.3129 | 7.7573 | 7.1565 | 5.8175 | 4.109 | -1.4408 | -10.2794 | -12.3371 | -12.6702 | 10.5021 | 10.3051 | 10.0877 | 9.8587 | 9.5307 | 9.1759 | 8.7835 | 7.9814 | 6.9995 | 3.9962 | -0.46426 | -1.7188 | -2.6123 | 11.8681 | 11.5822 | 11.2798 | 10.9186 | 10.4324 | 9.9162 | 9.3543 | 8.1654 | 6.6727 | 1.9981 | -5.2353 | -6.889 | -7.1539
|  | CHARMINSTER | FS |  |  | 9.841 | 9.5276 | 9.2272 | 8.8408 | 8.3129 | 7.7573 | 7.1565 | 5.8175 | 4.109 | -1.4408 | -10.2794 | -12.3371 | -12.6702 | 10.5021 | 10.3051 | 10.0877 | 9.8587 | 9.5307 | 9.1759 | 8.7835 | 7.9814 | 6.9995 | 3.9962 | -0.46426 | -1.7188 | -2.6123 | 11.8681 | 11.5822 | 11.2798 | 10.9186 | 10.4324 | 9.9162 | 9.3543 | 8.1654 | 6.6727 | 1.9981 | -5.2353 | -6.889 | -7.1539
LOVEDEAN GSP | CHICHESTER & HUNSTON | CHICHESTER | MINIMUM HEADROOM | SU 92198 07420 | YES | 10.081 | 9.0079 | 7.58 | 6.0372 | 4.3908 | 2.6968 | 0.79262 | -1.01 | -3.2089 | -8.3093 | -14.3603 | -17.9845 | -19.5381 | 13.4072 | 12.7364 | 11.8565 | 10.9538 | 9.9928 | 8.9956 | 7.8724 | 6.754 | 5.3921 | 2.3793 | -0.89218 | -2.7837 | -4.0309 | 10.8609 | 9.9452 | 8.7161 | 7.384 | 5.9578 | 4.4813 | 2.817 | 1.2033 | -0.8048 | -5.4127 | -10.8504 | -14.0538 | -15.4238
|  | CHICHESTER | CT |  |  | 10.081 | 9.0079 | 7.58 | 6.0372 | 4.3908 | 2.6968 | 0.79262 | -1.01 | -3.2089 | -8.3093 | -14.3603 | -17.9845 | -19.5381 | 13.4072 | 12.7364 | 11.8565 | 10.9538 | 9.9928 | 8.9956 | 7.8724 | 6.754 | 5.3921 | 2.3793 | -0.89218 | -2.7837 | -4.0309 | 10.8609 | 9.9452 | 8.7161 | 7.384 | 5.9578 | 4.4813 | 2.817 | 1.2033 | -0.8048 | -5.4127 | -10.8504 | -14.0538 | -15.4238
|  | CHICHESTER | LW |  |  | 10.081 | 9.0079 | 7.58 | 6.0372 | 4.3908 | 2.6968 | 0.79262 | -1.01 | -3.2089 | -8.3093 | -14.3603 | -17.9845 | -19.5381 | 13.4072 | 12.7364 | 11.8565 | 10.9538 | 9.9928 | 8.9956 | 7.8724 | 6.754 | 5.3921 | 2.3793 | -0.89218 | -2.7837 | -4.0309 | 10.8609 | 9.9452 | 8.7161 | 7.384 | 5.9578 | 4.4813 | 2.817 | 1.2033 | -0.8048 | -5.4127 | -10.8504 | -14.0538 | -15.4238
|  | CHICHESTER | ST |  |  | 10.081 | 9.0079 | 7.58 | 6.0372 | 4.3908 | 2.6968 | 0.79262 | -1.01 | -3.2089 | -8.3093 | -14.3603 | -17.9845 | -19.5381 | 13.4072 | 12.7364 | 11.8565 | 10.9538 | 9.9928 | 8.9956 | 7.8724 | 6.754 | 5.3921 | 2.3793 | -0.89218 | -2.7837 | -4.0309 | 10.8609 | 9.9452 | 8.7161 | 7.384 | 5.9578 | 4.4813 | 2.817 | 1.2033 | -0.8048 | -5.4127 | -10.8504 | -14.0538 | -15.4238
|  | CHICHESTER | FS |  |  | 10.081 | 9.0079 | 7.58 | 6.0372 | 4.3908 | 2.6968 | 0.79262 | -1.01 | -3.2089 | -8.3093 | -14.3603 | -17.9845 | -19.5381 | 13.4072 | 12.7364 | 11.8565 | 10.9538 | 9.9928 | 8.9956 | 7.8724 | 6.754 | 5.3921 | 2.3793 | -0.89218 | -2.7837 | -4.0309 | 10.8609 | 9.9452 | 8.7161 | 7.384 | 5.9578 | 4.4813 | 2.817 | 1.2033 | -0.8048 | -5.4127 | -10.8504 | -14.0538 | -15.4238
CHICKERELL GSP | CHICKERELL BSP | CHICKERELL | MINIMUM HEADROOM | SY 65479 80511 | YES | 28.8031 | 28.4268 | 27.8901 | 27.4751 | 27.0216 | 26.5346 | 26.0025 | 25.4668 | 24.7259 | 22.6373 | 19.5431 | 17.6649 | 16.6196 | 31.3102 | 31.1983 | 30.9529 | 30.799 | 30.6291 | 30.3489 | 30.0414 | 29.7255 | 29.3002 | 28.0756 | 26.3266 | 25.1382 | 24.1123 | 31.1451 | 30.8702 | 30.4152 | 30.0752 | 29.705 | 29.3069 | 28.8809 | 28.4537 | 27.849 | 26.0971 | 23.3176 | 21.5739 | 20.6358
|  | CHICKERELL | CT |  |  | 28.8031 | 28.4268 | 27.8901 | 27.4751 | 27.0216 | 26.5346 | 26.0025 | 25.4668 | 24.7259 | 22.6373 | 19.5431 | 17.6649 | 16.6196 | 31.3102 | 31.1983 | 30.9529 | 30.799 | 30.6291 | 30.3489 | 30.0414 | 29.7255 | 29.3002 | 28.0756 | 26.3266 | 25.1382 | 24.1123 | 31.1451 | 30.8702 | 30.4152 | 30.0752 | 29.705 | 29.3069 | 28.8809 | 28.4537 | 27.849 | 26.0971 | 23.3176 | 21.5739 | 20.6358
|  | CHICKERELL | LW |  |  | 28.8031 | 28.4268 | 27.8901 | 27.4751 | 27.0216 | 26.5346 | 26.0025 | 25.4668 | 24.7259 | 22.6373 | 19.5431 | 17.6649 | 16.6196 | 31.3102 | 31.1983 | 30.9529 | 30.799 | 30.6291 | 30.3489 | 30.0414 | 29.7255 | 29.3002 | 28.0756 | 26.3266 | 25.1382 | 24.1123 | 31.1451 | 30.8702 | 30.4152 | 30.0752 | 29.705 | 29.3069 | 28.8809 | 28.4537 | 27.849 | 26.0971 | 23.3176 | 21.5739 | 20.6358
|  | CHICKERELL | ST |  |  | 28.8031 | 28.4268 | 27.8901 | 27.4751 | 27.0216 | 26.5346 | 26.0025 | 25.4668 | 24.7259 | 22.6373 | 19.5431 | 17.6649 | 16.6196 | 31.3102 | 31.1983 | 30.9529 | 30.799 | 30.6291 | 30.3489 | 30.0414 | 29.7255 | 29.3002 | 28.0756 | 26.3266 | 25.1382 | 24.1123 | 31.1451 | 30.8702 | 30.4152 | 30.0752 | 29.705 | 29.3069 | 28.8809 | 28.4537 | 27.849 | 26.0971 | 23.3176 | 21.5739 | 20.6358
|  | CHICKERELL | FS |  |  | 28.8031 | 28.4268 | 27.8901 | 27.4751 | 27.0216 | 26.5346 | 26.0025 | 25.4668 | 24.7259 | 22.6373 | 19.5431 | 17.6649 | 16.6196 | 31.3102 | 31.1983 | 30.9529 | 30.799 | 30.6291 | 30.3489 | 30.0414 | 29.7255 | 29.3002 | 28.0756 | 26.3266 | 25.1382 | 24.1123 | 31.1451 | 30.8702 | 30.4152 | 30.0752 | 29.705 | 29.3069 | 28.8809 | 28.4537 | 27.849 | 26.0971 | 23.3176 | 21.5739 | 20.6358
AXMINSTER | YEOVIL BSP | CHILTON CANTELO | MINIMUM HEADROOM | ST 57910 21616 | YES | 0.13169 | -0.3124 | -0.84511 | -1.5226 | -2.2419 | -2.9563 | -3.5767 | -4.1946 | -4.7969 | -5.8481 | -7.0776 | -7.583 | -7.7715 | 3.0457 | 2.8604 | 2.6053 | 2.2555 | 1.8821 | 1.5074 | 1.167 | 0.81155 | 0.45599 | -0.20342 | -1.0101 | -1.336 | -1.5535 | 0.89772 | 0.51966 | 0.070072 | -0.5248 | -1.1554 | -1.7811 | -2.3124 | -2.8277 | -3.3282 | -4.2619 | -5.4338 | -5.917 | -6.0979
|  | CHILTON CANTELO | CT |  |  | 0.13169 | -0.3124 | -0.84511 | -1.5226 | -2.2419 | -2.9563 | -3.5767 | -4.1946 | -4.7969 | -5.8481 | -7.0776 | -7.583 | -7.7715 | 3.0457 | 2.8604 | 2.6053 | 2.2555 | 1.8821 | 1.5074 | 1.167 | 0.81155 | 0.45599 | -0.20342 | -1.0101 | -1.336 | -1.5535 | 0.89772 | 0.51966 | 0.070072 | -0.5248 | -1.1554 | -1.7811 | -2.3124 | -2.8277 | -3.3282 | -4.2619 | -5.4338 | -5.917 | -6.0979
|  | CHILTON CANTELO | LW |  |  | 0.13169 | -0.3124 | -0.84511 | -1.5226 | -2.2419 | -2.9563 | -3.5767 | -4.1946 | -4.7969 | -5.8481 | -7.0776 | -7.583 | -7.7715 | 3.0457 | 2.8604 | 2.6053 | 2.2555 | 1.8821 | 1.5074 | 1.167 | 0.81155 | 0.45599 | -0.20342 | -1.0101 | -1.336 | -1.5535 | 0.89772 | 0.51966 | 0.070072 | -0.5248 | -1.1554 | -1.7811 | -2.3124 | -2.8277 | -3.3282 | -4.2619 | -5.4338 | -5.917 | -6.0979
|  | CHILTON CANTELO | ST |  |  | 0.13169 | -0.3124 | -0.84511 | -1.5226 | -2.2419 | -2.9563 | -3.5767 | -4.1946 | -4.7969 | -5.8481 | -7.0776 | -7.583 | -7.7715 | 3.0457 | 2.8604 | 2.6053 | 2.2555 | 1.8821 | 1.5074 | 1.167 | 0.81155 | 0.45599 | -0.20342 | -1.0101 | -1.336 | -1.5535 | 0.89772 | 0.51966 | 0.070072 | -0.5248 | -1.1554 | -1.7811 | -2.3124 | -2.8277 | -3.3282 | -4.2619 | -5.4338 | -5.917 | -6.0979
|  | CHILTON CANTELO | FS |  |  | 0.13169 | -0.3124 | -0.84511 | -1.5226 | -2.2419 | -2.9563 | -3.5767 | -4.1946 | -4.7969 | -5.8481 | -7.0776 | -7.583 | -7.7715 | 3.0457 | 2.8604 | 2.6053 | 2.2555 | 1.8821 | 1.5074 | 1.167 | 0.81155 | 0.45599 | -0.20342 | -1.0101 | -1.336 | -1.5535 | 0.89772 | 0.51966 | 0.070072 | -0.5248 | -1.1554 | -1.7811 | -2.3124 | -2.8277 | -3.3282 | -4.2619 | -5.4338 | -5.917 | -6.0979
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | CHINEHAM | MINIMUM HEADROOM | SU 65105 55805 | YES | 25.33 | 25.0616 | 24.4265 | 23.8325 | 23.1993 | 22.5582 | 21.976 | 21.324 | 20.339 | 18.0739 | 14.5395 | 12.4323 | 11.5243 | 27.2603 | 27.0577 | 26.8274 | 26.6547 | 26.4165 | 26.0682 | 25.7439 | 25.3782 | 24.865 | 23.647 | 21.6797 | 20.397 | 19.4258 | 25.9373 | 25.4266 | 24.8035 | 24.2708 | 23.7015 | 23.1208 | 22.5733 | 21.9562 | 21.0222 | 18.9038 | 15.6795 | 13.821 | 13.0317
|  | CHINEHAM | CT |  |  | 25.33 | 25.0616 | 24.4265 | 23.8325 | 23.1993 | 22.5582 | 21.976 | 21.324 | 20.339 | 18.0739 | 14.5395 | 12.4323 | 11.5243 | 27.2603 | 27.0577 | 26.8274 | 26.6547 | 26.4165 | 26.0682 | 25.7439 | 25.3782 | 24.865 | 23.647 | 21.6797 | 20.397 | 19.4258 | 25.9373 | 25.4266 | 24.8035 | 24.2708 | 23.7015 | 23.1208 | 22.5733 | 21.9562 | 21.0222 | 18.9038 | 15.6795 | 13.821 | 13.0317
|  | CHINEHAM | LW |  |  | 25.33 | 25.0616 | 24.4265 | 23.8325 | 23.1993 | 22.5582 | 21.976 | 21.324 | 20.339 | 18.0739 | 14.5395 | 12.4323 | 11.5243 | 27.2603 | 27.0577 | 26.8274 | 26.6547 | 26.4165 | 26.0682 | 25.7439 | 25.3782 | 24.865 | 23.647 | 21.6797 | 20.397 | 19.4258 | 25.9373 | 25.4266 | 24.8035 | 24.2708 | 23.7015 | 23.1208 | 22.5733 | 21.9562 | 21.0222 | 18.9038 | 15.6795 | 13.821 | 13.0317
|  | CHINEHAM | ST |  |  | 25.33 | 25.0616 | 24.4265 | 23.8325 | 23.1993 | 22.5582 | 21.976 | 21.324 | 20.339 | 18.0739 | 14.5395 | 12.4323 | 11.5243 | 27.2603 | 27.0577 | 26.8274 | 26.6547 | 26.4165 | 26.0682 | 25.7439 | 25.3782 | 24.865 | 23.647 | 21.6797 | 20.397 | 19.4258 | 25.9373 | 25.4266 | 24.8035 | 24.2708 | 23.7015 | 23.1208 | 22.5733 | 21.9562 | 21.0222 | 18.9038 | 15.6795 | 13.821 | 13.0317
|  | CHINEHAM | FS |  |  | 25.33 | 25.0616 | 24.4265 | 23.8325 | 23.1993 | 22.5582 | 21.976 | 21.324 | 20.339 | 18.0739 | 14.5395 | 12.4323 | 11.5243 | 27.2603 | 27.0577 | 26.8274 | 26.6547 | 26.4165 | 26.0682 | 25.7439 | 25.3782 | 24.865 | 23.647 | 21.6797 | 20.397 | 19.4258 | 25.9373 | 25.4266 | 24.8035 | 24.2708 | 23.7015 | 23.1208 | 22.5733 | 21.9562 | 21.0222 | 18.9038 | 15.6795 | 13.821 | 13.0317
COWLEY GSP | YARNTON BSP | CHIPPING NORTON | MINIMUM HEADROOM | SP 31382 26792 | NO | 8.3435 | 7.8012 | 7.1899 | 6.4296 | 5.6388 | 4.8965 | 4.1116 | 3.2844 | 2.2121 | -0.35884 | -4.3228 | -5.9778 | -6.1805 | 9.5316 | 9.2267 | 8.8737 | 8.4899 | 8.0888 | 7.7033 | 7.2889 | 6.8321 | 6.2651 | 4.9779 | 3.2376 | 2.3154 | 1.7807 | 8.7729 | 8.3088 | 7.7848 | 7.119 | 6.427 | 5.7727 | 5.0794 | 4.3476 | 3.3813 | 1.025 | -2.5699 | -4.0257 | -4.2041
|  | CHIPPING NORTON | CT |  |  | 8.3435 | 7.8012 | 7.1899 | 6.4296 | 5.6388 | 4.8965 | 4.1116 | 3.2844 | 2.2121 | -0.35884 | -4.3228 | -5.9778 | -6.1805 | 9.5316 | 9.2267 | 8.8737 | 8.4899 | 8.0888 | 7.7033 | 7.2889 | 6.8321 | 6.2651 | 4.9779 | 3.2376 | 2.3154 | 1.7807 | 8.7729 | 8.3088 | 7.7848 | 7.119 | 6.427 | 5.7727 | 5.0794 | 4.3476 | 3.3813 | 1.025 | -2.5699 | -4.0257 | -4.2041
|  | CHIPPING NORTON | LW |  |  | 8.3435 | 7.8012 | 7.1899 | 6.4296 | 5.6388 | 4.8965 | 4.1116 | 3.2844 | 2.2121 | -0.35884 | -4.3228 | -5.9778 | -6.1805 | 9.5316 | 9.2267 | 8.8737 | 8.4899 | 8.0888 | 7.7033 | 7.2889 | 6.8321 | 6.2651 | 4.9779 | 3.2376 | 2.3154 | 1.7807 | 8.7729 | 8.3088 | 7.7848 | 7.119 | 6.427 | 5.7727 | 5.0794 | 4.3476 | 3.3813 | 1.025 | -2.5699 | -4.0257 | -4.2041
|  | CHIPPING NORTON | ST |  |  | 8.3435 | 7.8012 | 7.1899 | 6.4296 | 5.6388 | 4.8965 | 4.1116 | 3.2844 | 2.2121 | -0.35884 | -4.3228 | -5.9778 | -6.1805 | 9.5316 | 9.2267 | 8.8737 | 8.4899 | 8.0888 | 7.7033 | 7.2889 | 6.8321 | 6.2651 | 4.9779 | 3.2376 | 2.3154 | 1.7807 | 8.7729 | 8.3088 | 7.7848 | 7.119 | 6.427 | 5.7727 | 5.0794 | 4.3476 | 3.3813 | 1.025 | -2.5699 | -4.0257 | -4.2041
|  | CHIPPING NORTON | FS |  |  | 8.3435 | 7.8012 | 7.1899 | 6.4296 | 5.6388 | 4.8965 | 4.1116 | 3.2844 | 2.2121 | -0.35884 | -4.3228 | -5.9778 | -6.1805 | 9.5316 | 9.2267 | 8.8737 | 8.4899 | 8.0888 | 7.7033 | 7.2889 | 6.8321 | 6.2651 | 4.9779 | 3.2376 | 2.3154 | 1.7807 | 8.7729 | 8.3088 | 7.7848 | 7.119 | 6.427 | 5.7727 | 5.0794 | 4.3476 | 3.3813 | 1.025 | -2.5699 | -4.0257 | -4.2041
COWLEY GSP | HIGH WYCOMBE BSP | CHISBRIDGE | MINIMUM HEADROOM | SU 80226 89155 | YES | 3.6315 | 3.5456 | 3.4569 | 3.3401 | 3.2164 | 3.0703 | 2.9085 | 2.7412 | 2.5135 | 2.108 | 1.4348 | 0.98042 | 0.77646 | 4.4771 | 4.4471 | 4.4142 | 4.3709 | 4.3257 | 4.2737 | 4.2163 | 4.1588 | 4.0776 | 3.8498 | 3.4504 | 3.2632 | 3.1668 | 4.5803 | 4.4984 | 4.4136 | 4.3047 | 4.189 | 4.0516 | 3.8988 | 3.7405 | 3.5253 | 3.1558 | 2.5577 | 2.1764 | 2.0039
|  | CHISBRIDGE | CT |  |  | 3.6315 | 3.5456 | 3.4569 | 3.3401 | 3.2164 | 3.0703 | 2.9085 | 2.7412 | 2.5135 | 2.108 | 1.4348 | 0.98042 | 0.77646 | 4.4771 | 4.4471 | 4.4142 | 4.3709 | 4.3257 | 4.2737 | 4.2163 | 4.1588 | 4.0776 | 3.8498 | 3.4504 | 3.2632 | 3.1668 | 4.5803 | 4.4984 | 4.4136 | 4.3047 | 4.189 | 4.0516 | 3.8988 | 3.7405 | 3.5253 | 3.1558 | 2.5577 | 2.1764 | 2.0039
|  | CHISBRIDGE | LW |  |  | 3.6315 | 3.5456 | 3.4569 | 3.3401 | 3.2164 | 3.0703 | 2.9085 | 2.7412 | 2.5135 | 2.108 | 1.4348 | 0.98042 | 0.77646 | 4.4771 | 4.4471 | 4.4142 | 4.3709 | 4.3257 | 4.2737 | 4.2163 | 4.1588 | 4.0776 | 3.8498 | 3.4504 | 3.2632 | 3.1668 | 4.5803 | 4.4984 | 4.4136 | 4.3047 | 4.189 | 4.0516 | 3.8988 | 3.7405 | 3.5253 | 3.1558 | 2.5577 | 2.1764 | 2.0039
|  | CHISBRIDGE | ST |  |  | 3.6315 | 3.5456 | 3.4569 | 3.3401 | 3.2164 | 3.0703 | 2.9085 | 2.7412 | 2.5135 | 2.108 | 1.4348 | 0.98042 | 0.77646 | 4.4771 | 4.4471 | 4.4142 | 4.3709 | 4.3257 | 4.2737 | 4.2163 | 4.1588 | 4.0776 | 3.8498 | 3.4504 | 3.2632 | 3.1668 | 4.5803 | 4.4984 | 4.4136 | 4.3047 | 4.189 | 4.0516 | 3.8988 | 3.7405 | 3.5253 | 3.1558 | 2.5577 | 2.1764 | 2.0039
|  | CHISBRIDGE | FS |  |  | 3.6315 | 3.5456 | 3.4569 | 3.3401 | 3.2164 | 3.0703 | 2.9085 | 2.7412 | 2.5135 | 2.108 | 1.4348 | 0.98042 | 0.77646 | 4.4771 | 4.4471 | 4.4142 | 4.3709 | 4.3257 | 4.2737 | 4.2163 | 4.1588 | 4.0776 | 3.8498 | 3.4504 | 3.2632 | 3.1668 | 4.5803 | 4.4984 | 4.4136 | 4.3047 | 4.189 | 4.0516 | 3.8988 | 3.7405 | 3.5253 | 3.1558 | 2.5577 | 2.1764 | 2.0039
MINETY GSP | TOOTHILL BSP | CHISLEDON | MINIMUM HEADROOM | SU 18894 79934 | YES | 6.0494 | 1.172 | -3.8948 | -5.0026 | -6.3159 | -7.6829 | -9.2538 | -11.0253 | -12.9495 | -19.0066 | -22.7197 | -23.6923 | -24.0541 | 2.8579 | -2.6904 | -8.3389 | -8.9356 | -9.635 | -10.3607 | -11.1914 | -12.1283 | -13.151 | -16.2266 | -18.1449 | -18.6882 | -19.0535 | 3.3797 | -2.3783 | -8.2848 | -9.1907 | -10.2671 | -11.3919 | -12.6895 | -14.1577 | -15.7652 | -20.6999 | -23.7382 | -24.5385 | -24.8363
|  | CHISLEDON | CT |  |  | 6.0494 | 1.172 | -3.8948 | -5.0026 | -6.3159 | -7.6829 | -9.2538 | -11.0253 | -12.9495 | -19.0066 | -22.7197 | -23.6923 | -24.0541 | 2.8579 | -2.6904 | -8.3389 | -8.9356 | -9.635 | -10.3607 | -11.1914 | -12.1283 | -13.151 | -16.2266 | -18.1449 | -18.6882 | -19.0535 | 3.3797 | -2.3783 | -8.2848 | -9.1907 | -10.2671 | -11.3919 | -12.6895 | -14.1577 | -15.7652 | -20.6999 | -23.7382 | -24.5385 | -24.8363
|  | CHISLEDON | LW |  |  | 6.0494 | 1.172 | -3.8948 | -5.0026 | -6.3159 | -7.6829 | -9.2538 | -11.0253 | -12.9495 | -19.0066 | -22.7197 | -23.6923 | -24.0541 | 2.8579 | -2.6904 | -8.3389 | -8.9356 | -9.635 | -10.3607 | -11.1914 | -12.1283 | -13.151 | -16.2266 | -18.1449 | -18.6882 | -19.0535 | 3.3797 | -2.3783 | -8.2848 | -9.1907 | -10.2671 | -11.3919 | -12.6895 | -14.1577 | -15.7652 | -20.6999 | -23.7382 | -24.5385 | -24.8363
|  | CHISLEDON | ST |  |  | 6.0494 | 1.172 | -3.8948 | -5.0026 | -6.3159 | -7.6829 | -9.2538 | -11.0253 | -12.9495 | -19.0066 | -22.7197 | -23.6923 | -24.0541 | 2.8579 | -2.6904 | -8.3389 | -8.9356 | -9.635 | -10.3607 | -11.1914 | -12.1283 | -13.151 | -16.2266 | -18.1449 | -18.6882 | -19.0535 | 3.3797 | -2.3783 | -8.2848 | -9.1907 | -10.2671 | -11.3919 | -12.6895 | -14.1577 | -15.7652 | -20.6999 | -23.7382 | -24.5385 | -24.8363
|  | CHISLEDON | FS |  |  | 6.0494 | 1.172 | -3.8948 | -5.0026 | -6.3159 | -7.6829 | -9.2538 | -11.0253 | -12.9495 | -19.0066 | -22.7197 | -23.6923 | -24.0541 | 2.8579 | -2.6904 | -8.3389 | -8.9356 | -9.635 | -10.3607 | -11.1914 | -12.1283 | -13.151 | -16.2266 | -18.1449 | -18.6882 | -19.0535 | 3.3797 | -2.3783 | -8.2848 | -9.1907 | -10.2671 | -11.3919 | -12.6895 | -14.1577 | -15.7652 | -20.6999 | -23.7382 | -24.5385 | -24.8363
BRAMLEY (FLEE) | BRACKNELL RESERVE | CHOBHAM | MINIMUM HEADROOM | SU 97173 63223 | YES | 2.6126 | 2.4143 | 2.1973 | 1.8629 | 1.5053 | 1.1337 | 0.71903 | 0.26107 | -0.47211 | -2.2887 | -5.91 | -8.6334 | -9.9416 | 6.7727 | 6.5533 | 6.3077 | 6.0363 | 5.7366 | 5.4029 | 5.0082 | 4.5513 | 3.9544 | 2.8635 | 1.0592 | -0.24021 | -1.1943 | 4.5312 | 4.2739 | 3.9893 | 3.6149 | 3.2087 | 2.7729 | 2.2701 | 1.6666 | 0.79608 | -0.94629 | -4.1165 | -6.4439 | -7.5464
|  | CHOBHAM | CT |  |  | 2.6126 | 2.4143 | 2.1973 | 1.8629 | 1.5053 | 1.1337 | 0.71903 | 0.26107 | -0.47211 | -2.2887 | -5.91 | -8.6334 | -9.9416 | 6.7727 | 6.5533 | 6.3077 | 6.0363 | 5.7366 | 5.4029 | 5.0082 | 4.5513 | 3.9544 | 2.8635 | 1.0592 | -0.24021 | -1.1943 | 4.5312 | 4.2739 | 3.9893 | 3.6149 | 3.2087 | 2.7729 | 2.2701 | 1.6666 | 0.79608 | -0.94629 | -4.1165 | -6.4439 | -7.5464
|  | CHOBHAM | LW |  |  | 2.6126 | 2.4143 | 2.1973 | 1.8629 | 1.5053 | 1.1337 | 0.71903 | 0.26107 | -0.47211 | -2.2887 | -5.91 | -8.6334 | -9.9416 | 6.7727 | 6.5533 | 6.3077 | 6.0363 | 5.7366 | 5.4029 | 5.0082 | 4.5513 | 3.9544 | 2.8635 | 1.0592 | -0.24021 | -1.1943 | 4.5312 | 4.2739 | 3.9893 | 3.6149 | 3.2087 | 2.7729 | 2.2701 | 1.6666 | 0.79608 | -0.94629 | -4.1165 | -6.4439 | -7.5464
|  | CHOBHAM | ST |  |  | 2.6126 | 2.4143 | 2.1973 | 1.8629 | 1.5053 | 1.1337 | 0.71903 | 0.26107 | -0.47211 | -2.2887 | -5.91 | -8.6334 | -9.9416 | 6.7727 | 6.5533 | 6.3077 | 6.0363 | 5.7366 | 5.4029 | 5.0082 | 4.5513 | 3.9544 | 2.8635 | 1.0592 | -0.24021 | -1.1943 | 4.5312 | 4.2739 | 3.9893 | 3.6149 | 3.2087 | 2.7729 | 2.2701 | 1.6666 | 0.79608 | -0.94629 | -4.1165 | -6.4439 | -7.5464
|  | CHOBHAM | FS |  |  | 2.6126 | 2.4143 | 2.1973 | 1.8629 | 1.5053 | 1.1337 | 0.71903 | 0.26107 | -0.47211 | -2.2887 | -5.91 | -8.6334 | -9.9416 | 6.7727 | 6.5533 | 6.3077 | 6.0363 | 5.7366 | 5.4029 | 5.0082 | 4.5513 | 3.9544 | 2.8635 | 1.0592 | -0.24021 | -1.1943 | 4.5312 | 4.2739 | 3.9893 | 3.6149 | 3.2087 | 2.7729 | 2.2701 | 1.6666 | 0.79608 | -0.94629 | -4.1165 | -6.4439 | -7.5464
COWLEY GSP | DRAYTON BSP | CHOLSEY | MINIMUM HEADROOM | SU 58223 84685 | NO | 2.8124 | 2.627 | 2.4415 | 2.1881 | 1.9143 | 1.628 | 1.3113 | 0.9321 | 0.32037 | -0.90775 | -2.87 | -4.2519 | -4.8713 | 3.7908 | 3.6789 | 3.5619 | 3.4267 | 3.2775 | 3.1167 | 2.9354 | 2.7082 | 2.362 | 1.7624 | 0.95876 | 0.42456 | 0.10747 | 1.7683 | 1.5957 | 1.4158 | 1.1908 | 0.9412 | 0.67739 | 0.383 | 0.023566 | -0.5478 | -1.6318 | -3.3679 | -4.5881 | -5.132
|  | CHOLSEY | CT |  |  | 2.8124 | 2.627 | 2.4415 | 2.1881 | 1.9143 | 1.628 | 1.3113 | 0.9321 | 0.32037 | -0.90775 | -2.87 | -4.2519 | -4.8713 | 3.7908 | 3.6789 | 3.5619 | 3.4267 | 3.2775 | 3.1167 | 2.9354 | 2.7082 | 2.362 | 1.7624 | 0.95876 | 0.42456 | 0.10747 | 1.7683 | 1.5957 | 1.4158 | 1.1908 | 0.9412 | 0.67739 | 0.383 | 0.023566 | -0.5478 | -1.6318 | -3.3679 | -4.5881 | -5.132
|  | CHOLSEY | LW |  |  | 2.8124 | 2.627 | 2.4415 | 2.1881 | 1.9143 | 1.628 | 1.3113 | 0.9321 | 0.32037 | -0.90775 | -2.87 | -4.2519 | -4.8713 | 3.7908 | 3.6789 | 3.5619 | 3.4267 | 3.2775 | 3.1167 | 2.9354 | 2.7082 | 2.362 | 1.7624 | 0.95876 | 0.42456 | 0.10747 | 1.7683 | 1.5957 | 1.4158 | 1.1908 | 0.9412 | 0.67739 | 0.383 | 0.023566 | -0.5478 | -1.6318 | -3.3679 | -4.5881 | -5.132
|  | CHOLSEY | ST |  |  | 2.8124 | 2.627 | 2.4415 | 2.1881 | 1.9143 | 1.628 | 1.3113 | 0.9321 | 0.32037 | -0.90775 | -2.87 | -4.2519 | -4.8713 | 3.7908 | 3.6789 | 3.5619 | 3.4267 | 3.2775 | 3.1167 | 2.9354 | 2.7082 | 2.362 | 1.7624 | 0.95876 | 0.42456 | 0.10747 | 1.7683 | 1.5957 | 1.4158 | 1.1908 | 0.9412 | 0.67739 | 0.383 | 0.023566 | -0.5478 | -1.6318 | -3.3679 | -4.5881 | -5.132
|  | CHOLSEY | FS |  |  | 2.8124 | 2.627 | 2.4415 | 2.1881 | 1.9143 | 1.628 | 1.3113 | 0.9321 | 0.32037 | -0.90775 | -2.87 | -4.2519 | -4.8713 | 3.7908 | 3.6789 | 3.5619 | 3.4267 | 3.2775 | 3.1167 | 2.9354 | 2.7082 | 2.362 | 1.7624 | 0.95876 | 0.42456 | 0.10747 | 1.7683 | 1.5957 | 1.4158 | 1.1908 | 0.9412 | 0.67739 | 0.383 | 0.023566 | -0.5478 | -1.6318 | -3.3679 | -4.5881 | -5.132
MANNINGTON GSP | CHRISTCHURCH BSP | CHRISTCHURCH | MINIMUM HEADROOM | SZ 15698 93141 | YES | 14.2027 | 13.7119 | 13.0155 | 12.1578 | 11.2863 | 10.3317 | 9.2727 | 8.0305 | 5.9881 | 0.50446 | -7.3958 | -13.0645 | -15.8345 | 17.204 | 16.8357 | 16.3027 | 15.7238 | 15.122 | 14.4527 | 13.7085 | 12.7989 | 11.4283 | 7.8089 | 3.0702 | -0.6211 | -4.2021 | 18.4577 | 17.9942 | 17.3272 | 16.5165 | 15.6851 | 14.7728 | 13.7953 | 12.6732 | 10.821 | 5.8133 | -1.5291 | -6.5322 | -8.9305
|  | CHRISTCHURCH | CT |  |  | 14.2027 | 13.7119 | 13.0155 | 12.1578 | 11.2863 | 10.3317 | 9.2727 | 8.0305 | 5.9881 | 0.50446 | -7.3958 | -13.0645 | -15.8345 | 17.204 | 16.8357 | 16.3027 | 15.7238 | 15.122 | 14.4527 | 13.7085 | 12.7989 | 11.4283 | 7.8089 | 3.0702 | -0.6211 | -4.2021 | 18.4577 | 17.9942 | 17.3272 | 16.5165 | 15.6851 | 14.7728 | 13.7953 | 12.6732 | 10.821 | 5.8133 | -1.5291 | -6.5322 | -8.9305
|  | CHRISTCHURCH | LW |  |  | 14.2027 | 13.7119 | 13.0155 | 12.1578 | 11.2863 | 10.3317 | 9.2727 | 8.0305 | 5.9881 | 0.50446 | -7.3958 | -13.0645 | -15.8345 | 17.204 | 16.8357 | 16.3027 | 15.7238 | 15.122 | 14.4527 | 13.7085 | 12.7989 | 11.4283 | 7.8089 | 3.0702 | -0.6211 | -4.2021 | 18.4577 | 17.9942 | 17.3272 | 16.5165 | 15.6851 | 14.7728 | 13.7953 | 12.6732 | 10.821 | 5.8133 | -1.5291 | -6.5322 | -8.9305
|  | CHRISTCHURCH | ST |  |  | 14.2027 | 13.7119 | 13.0155 | 12.1578 | 11.2863 | 10.3317 | 9.2727 | 8.0305 | 5.9881 | 0.50446 | -7.3958 | -13.0645 | -15.8345 | 17.204 | 16.8357 | 16.3027 | 15.7238 | 15.122 | 14.4527 | 13.7085 | 12.7989 | 11.4283 | 7.8089 | 3.0702 | -0.6211 | -4.2021 | 18.4577 | 17.9942 | 17.3272 | 16.5165 | 15.6851 | 14.7728 | 13.7953 | 12.6732 | 10.821 | 5.8133 | -1.5291 | -6.5322 | -8.9305
|  | CHRISTCHURCH | FS |  |  | 14.2027 | 13.7119 | 13.0155 | 12.1578 | 11.2863 | 10.3317 | 9.2727 | 8.0305 | 5.9881 | 0.50446 | -7.3958 | -13.0645 | -15.8345 | 17.204 | 16.8357 | 16.3027 | 15.7238 | 15.122 | 14.4527 | 13.7085 | 12.7989 | 11.4283 | 7.8089 | 3.0702 | -0.6211 | -4.2021 | 18.4577 | 17.9942 | 17.3272 | 16.5165 | 15.6851 | 14.7728 | 13.7953 | 12.6732 | 10.821 | 5.8133 | -1.5291 | -6.5322 | -8.9305
LALEHAM | EAST BEDFONT A | CHURCH ROAD | MINIMUM HEADROOM | TQ 06820 71722 | YES | 3.5988 | 3.2873 | 2.6334 | 1.8727 | 1.2486 | 0.58003 | -0.15652 | -1.0603 | -2.5268 | -6.1648 | -12.1262 | -16.6909 | -19.384 | 7.6123 | 7.4014 | 6.9363 | 6.4382 | 5.9991 | 5.5202 | 4.9882 | 4.3298 | 3.3336 | 0.94915 | -2.6356 | -5.6815 | -8.6542 | 5.3389 | 5.0422 | 4.4388 | 3.7293 | 3.1279 | 2.483 | 1.7727 | 0.91037 | -0.47755 | -3.8672 | -9.1818 | -13.1122 | -15.382
|  | CHURCH ROAD | CT |  |  | 3.5988 | 3.2873 | 2.6334 | 1.8727 | 1.2486 | 0.58003 | -0.15652 | -1.0603 | -2.5268 | -6.1648 | -12.1262 | -16.6909 | -19.384 | 7.6123 | 7.4014 | 6.9363 | 6.4382 | 5.9991 | 5.5202 | 4.9882 | 4.3298 | 3.3336 | 0.94915 | -2.6356 | -5.6815 | -8.6542 | 5.3389 | 5.0422 | 4.4388 | 3.7293 | 3.1279 | 2.483 | 1.7727 | 0.91037 | -0.47755 | -3.8672 | -9.1818 | -13.1122 | -15.382
|  | CHURCH ROAD | LW |  |  | 3.5988 | 3.2873 | 2.6334 | 1.8727 | 1.2486 | 0.58003 | -0.15652 | -1.0603 | -2.5268 | -6.1648 | -12.1262 | -16.6909 | -19.384 | 7.6123 | 7.4014 | 6.9363 | 6.4382 | 5.9991 | 5.5202 | 4.9882 | 4.3298 | 3.3336 | 0.94915 | -2.6356 | -5.6815 | -8.6542 | 5.3389 | 5.0422 | 4.4388 | 3.7293 | 3.1279 | 2.483 | 1.7727 | 0.91037 | -0.47755 | -3.8672 | -9.1818 | -13.1122 | -15.382
|  | CHURCH ROAD | ST |  |  | 3.5988 | 3.2873 | 2.6334 | 1.8727 | 1.2486 | 0.58003 | -0.15652 | -1.0603 | -2.5268 | -6.1648 | -12.1262 | -16.6909 | -19.384 | 7.6123 | 7.4014 | 6.9363 | 6.4382 | 5.9991 | 5.5202 | 4.9882 | 4.3298 | 3.3336 | 0.94915 | -2.6356 | -5.6815 | -8.6542 | 5.3389 | 5.0422 | 4.4388 | 3.7293 | 3.1279 | 2.483 | 1.7727 | 0.91037 | -0.47755 | -3.8672 | -9.1818 | -13.1122 | -15.382
|  | CHURCH ROAD | FS |  |  | 3.5988 | 3.2873 | 2.6334 | 1.8727 | 1.2486 | 0.58003 | -0.15652 | -1.0603 | -2.5268 | -6.1648 | -12.1262 | -16.6909 | -19.384 | 7.6123 | 7.4014 | 6.9363 | 6.4382 | 5.9991 | 5.5202 | 4.9882 | 4.3298 | 3.3336 | 0.94915 | -2.6356 | -5.6815 | -8.6542 | 5.3389 | 5.0422 | 4.4388 | 3.7293 | 3.1279 | 2.483 | 1.7727 | 0.91037 | -0.47755 | -3.8672 | -9.1818 | -13.1122 | -15.382
MINETY GSP | CIRENCESTER BSP | CIRENCESTER TOWN | MINIMUM HEADROOM | SP 02761 00827 | YES | 0.78865 | 0.58351 | 0.39565 | 0.22778 | 0.057226 | -0.13089 | -0.659 | -1.421 | -2.6791 | -6.2177 | -12.6552 | -17.2842 | -18.3739 | 7.568 | 7.39 | 7.2243 | 7.0751 | 6.9257 | 6.6354 | 6.2408 | 5.7648 | 5.0571 | 3.0678 | -0.43264 | -3.3286 | -5.5224 | 3.9356 | 3.7195 | 3.3359 | 2.791 | 2.23 | 1.6531 | 1.035 | 0.35125 | -0.7824 | -3.9924 | -9.9082 | -14.1065 | -15.065
|  | CIRENCESTER TOWN | CT |  |  | 0.78865 | 0.58351 | 0.39565 | 0.22778 | 0.057226 | -0.13089 | -0.659 | -1.421 | -2.6791 | -6.2177 | -12.6552 | -17.2842 | -18.3739 | 7.568 | 7.39 | 7.2243 | 7.0751 | 6.9257 | 6.6354 | 6.2408 | 5.7648 | 5.0571 | 3.0678 | -0.43264 | -3.3286 | -5.5224 | 3.9356 | 3.7195 | 3.3359 | 2.791 | 2.23 | 1.6531 | 1.035 | 0.35125 | -0.7824 | -3.9924 | -9.9082 | -14.1065 | -15.065
|  | CIRENCESTER TOWN | LW |  |  | 0.78865 | 0.58351 | 0.39565 | 0.22778 | 0.057226 | -0.13089 | -0.659 | -1.421 | -2.6791 | -6.2177 | -12.6552 | -17.2842 | -18.3739 | 7.568 | 7.39 | 7.2243 | 7.0751 | 6.9257 | 6.6354 | 6.2408 | 5.7648 | 5.0571 | 3.0678 | -0.43264 | -3.3286 | -5.5224 | 3.9356 | 3.7195 | 3.3359 | 2.791 | 2.23 | 1.6531 | 1.035 | 0.35125 | -0.7824 | -3.9924 | -9.9082 | -14.1065 | -15.065
|  | CIRENCESTER TOWN | ST |  |  | 0.78865 | 0.58351 | 0.39565 | 0.22778 | 0.057226 | -0.13089 | -0.659 | -1.421 | -2.6791 | -6.2177 | -12.6552 | -17.2842 | -18.3739 | 7.568 | 7.39 | 7.2243 | 7.0751 | 6.9257 | 6.6354 | 6.2408 | 5.7648 | 5.0571 | 3.0678 | -0.43264 | -3.3286 | -5.5224 | 3.9356 | 3.7195 | 3.3359 | 2.791 | 2.23 | 1.6531 | 1.035 | 0.35125 | -0.7824 | -3.9924 | -9.9082 | -14.1065 | -15.065
|  | CIRENCESTER TOWN | FS |  |  | 0.78865 | 0.58351 | 0.39565 | 0.22778 | 0.057226 | -0.13089 | -0.659 | -1.421 | -2.6791 | -6.2177 | -12.6552 | -17.2842 | -18.3739 | 7.568 | 7.39 | 7.2243 | 7.0751 | 6.9257 | 6.6354 | 6.2408 | 5.7648 | 5.0571 | 3.0678 | -0.43264 | -3.3286 | -5.5224 | 3.9356 | 3.7195 | 3.3359 | 2.791 | 2.23 | 1.6531 | 1.035 | 0.35125 | -0.7824 | -3.9924 | -9.9082 | -14.1065 | -15.065
IVER 132KV | CIPPENHAM | CLARENCE ROAD | MINIMUM HEADROOM | SU 95654 76652 | YES | 11.6596 | 11.0048 | 10.2149 | 9.083 | 7.8009 | 6.4642 | 4.9914 | 3.3041 | 0.62959 | -6.6302 | -17.5455 | -24.2724 | -27.2198 | 23.0557 | 22.6124 | 22.081 | 21.3717 | 20.5336 | 19.5752 | 18.5074 | 17.2594 | 15.4052 | 10.2867 | 2.8867 | -2.8086 | -9.1959 | 17.1989 | 16.5355 | 15.7227 | 14.6478 | 13.4227 | 12.1247 | 10.6872 | 9.0193 | 6.4218 | -0.52362 | -10.3224 | -15.9455 | -18.3583
|  | CLARENCE ROAD | CT |  |  | 11.6596 | 11.0048 | 10.2149 | 9.083 | 7.8009 | 6.4642 | 4.9914 | 3.3041 | 0.62959 | -6.6302 | -17.5455 | -24.2724 | -27.2198 | 23.0557 | 22.6124 | 22.081 | 21.3717 | 20.5336 | 19.5752 | 18.5074 | 17.2594 | 15.4052 | 10.2867 | 2.8867 | -2.8086 | -9.1959 | 17.1989 | 16.5355 | 15.7227 | 14.6478 | 13.4227 | 12.1247 | 10.6872 | 9.0193 | 6.4218 | -0.52362 | -10.3224 | -15.9455 | -18.3583
|  | CLARENCE ROAD | LW |  |  | 11.6596 | 11.0048 | 10.2149 | 9.083 | 7.8009 | 6.4642 | 4.9914 | 3.3041 | 0.62959 | -6.6302 | -17.5455 | -24.2724 | -27.2198 | 23.0557 | 22.6124 | 22.081 | 21.3717 | 20.5336 | 19.5752 | 18.5074 | 17.2594 | 15.4052 | 10.2867 | 2.8867 | -2.8086 | -9.1959 | 17.1989 | 16.5355 | 15.7227 | 14.6478 | 13.4227 | 12.1247 | 10.6872 | 9.0193 | 6.4218 | -0.52362 | -10.3224 | -15.9455 | -18.3583
|  | CLARENCE ROAD | ST |  |  | 11.6596 | 11.0048 | 10.2149 | 9.083 | 7.8009 | 6.4642 | 4.9914 | 3.3041 | 0.62959 | -6.6302 | -17.5455 | -24.2724 | -27.2198 | 23.0557 | 22.6124 | 22.081 | 21.3717 | 20.5336 | 19.5752 | 18.5074 | 17.2594 | 15.4052 | 10.2867 | 2.8867 | -2.8086 | -9.1959 | 17.1989 | 16.5355 | 15.7227 | 14.6478 | 13.4227 | 12.1247 | 10.6872 | 9.0193 | 6.4218 | -0.52362 | -10.3224 | -15.9455 | -18.3583
|  | CLARENCE ROAD | FS |  |  | 11.6596 | 11.0048 | 10.2149 | 9.083 | 7.8009 | 6.4642 | 4.9914 | 3.3041 | 0.62959 | -6.6302 | -17.5455 | -24.2724 | -27.2198 | 23.0557 | 22.6124 | 22.081 | 21.3717 | 20.5336 | 19.5752 | 18.5074 | 17.2594 | 15.4052 | 10.2867 | 2.8867 | -2.8086 | -9.1959 | 17.1989 | 16.5355 | 15.7227 | 14.6478 | 13.4227 | 12.1247 | 10.6872 | 9.0193 | 6.4218 | -0.52362 | -10.3224 | -15.9455 | -18.3583
MELKSHAM GSP | CHIPPENHAM | COCKLEBURY | MINIMUM HEADROOM | ST 92447 73890 | YES | 18.9757 | 18.1128 | 17.1704 | 16.4042 | 15.7452 | 15.0436 | 14.2676 | 13.3933 | 12.0491 | 8.5278 | 3.1567 | -0.55167 | -2.2088 | 23.631 | 23.0693 | 22.4616 | 21.962 | 21.5212 | 21.0453 | 20.5148 | 19.9013 | 19.0269 | 16.777 | 13.6333 | 11.173 | 8.6848 | 20.7267 | 19.9936 | 19.1831 | 18.5132 | 17.9239 | 17.2939 | 16.5947 | 15.7968 | 14.5827 | 11.4671 | 6.8188 | 3.7697 | 2.4622
|  | COCKLEBURY | CT |  |  | 18.9757 | 18.1128 | 17.1704 | 16.4042 | 15.7452 | 15.0436 | 14.2676 | 13.3933 | 12.0491 | 8.5278 | 3.1567 | -0.55167 | -2.2088 | 23.631 | 23.0693 | 22.4616 | 21.962 | 21.5212 | 21.0453 | 20.5148 | 19.9013 | 19.0269 | 16.777 | 13.6333 | 11.173 | 8.6848 | 20.7267 | 19.9936 | 19.1831 | 18.5132 | 17.9239 | 17.2939 | 16.5947 | 15.7968 | 14.5827 | 11.4671 | 6.8188 | 3.7697 | 2.4622
|  | COCKLEBURY | LW |  |  | 18.9757 | 18.1128 | 17.1704 | 16.4042 | 15.7452 | 15.0436 | 14.2676 | 13.3933 | 12.0491 | 8.5278 | 3.1567 | -0.55167 | -2.2088 | 23.631 | 23.0693 | 22.4616 | 21.962 | 21.5212 | 21.0453 | 20.5148 | 19.9013 | 19.0269 | 16.777 | 13.6333 | 11.173 | 8.6848 | 20.7267 | 19.9936 | 19.1831 | 18.5132 | 17.9239 | 17.2939 | 16.5947 | 15.7968 | 14.5827 | 11.4671 | 6.8188 | 3.7697 | 2.4622
|  | COCKLEBURY | ST |  |  | 18.9757 | 18.1128 | 17.1704 | 16.4042 | 15.7452 | 15.0436 | 14.2676 | 13.3933 | 12.0491 | 8.5278 | 3.1567 | -0.55167 | -2.2088 | 23.631 | 23.0693 | 22.4616 | 21.962 | 21.5212 | 21.0453 | 20.5148 | 19.9013 | 19.0269 | 16.777 | 13.6333 | 11.173 | 8.6848 | 20.7267 | 19.9936 | 19.1831 | 18.5132 | 17.9239 | 17.2939 | 16.5947 | 15.7968 | 14.5827 | 11.4671 | 6.8188 | 3.7697 | 2.4622
|  | COCKLEBURY | FS |  |  | 18.9757 | 18.1128 | 17.1704 | 16.4042 | 15.7452 | 15.0436 | 14.2676 | 13.3933 | 12.0491 | 8.5278 | 3.1567 | -0.55167 | -2.2088 | 23.631 | 23.0693 | 22.4616 | 21.962 | 21.5212 | 21.0453 | 20.5148 | 19.9013 | 19.0269 | 16.777 | 13.6333 | 11.173 | 8.6848 | 20.7267 | 19.9936 | 19.1831 | 18.5132 | 17.9239 | 17.2939 | 16.5947 | 15.7968 | 14.5827 | 11.4671 | 6.8188 | 3.7697 | 2.4622
MELKSHAM GSP | FROME BSP | CODFORD | MINIMUM HEADROOM | ST 97372 39559 | YES | 1.3643 | 1.3085 | 1.2373 | 1.1425 | 1.0416 | 0.9298 | 0.81013 | 0.65913 | 0.47114 | 0.069779 | -0.53077 | -0.98936 | -1.1163 | 1.5406 | 1.5214 | 1.5003 | 1.4665 | 1.4311 | 1.3921 | 1.3508 | 1.3072 | 1.2492 | 1.0818 | 0.77258 | 0.5995 | 0.5488 | 1.7766 | 1.763 | 1.7418 | 1.7227 | 1.701 | 1.677 | 1.5864 | 1.4389 | 1.2551 | 0.86007 | 0.23575 | -0.15462 | -0.2633
|  | CODFORD | CT |  |  | 1.3643 | 1.3085 | 1.2373 | 1.1425 | 1.0416 | 0.9298 | 0.81013 | 0.65913 | 0.47114 | 0.069779 | -0.53077 | -0.98936 | -1.1163 | 1.5406 | 1.5214 | 1.5003 | 1.4665 | 1.4311 | 1.3921 | 1.3508 | 1.3072 | 1.2492 | 1.0818 | 0.77258 | 0.5995 | 0.5488 | 1.7766 | 1.763 | 1.7418 | 1.7227 | 1.701 | 1.677 | 1.5864 | 1.4389 | 1.2551 | 0.86007 | 0.23575 | -0.15462 | -0.2633
|  | CODFORD | LW |  |  | 1.3643 | 1.3085 | 1.2373 | 1.1425 | 1.0416 | 0.9298 | 0.81013 | 0.65913 | 0.47114 | 0.069779 | -0.53077 | -0.98936 | -1.1163 | 1.5406 | 1.5214 | 1.5003 | 1.4665 | 1.4311 | 1.3921 | 1.3508 | 1.3072 | 1.2492 | 1.0818 | 0.77258 | 0.5995 | 0.5488 | 1.7766 | 1.763 | 1.7418 | 1.7227 | 1.701 | 1.677 | 1.5864 | 1.4389 | 1.2551 | 0.86007 | 0.23575 | -0.15462 | -0.2633
|  | CODFORD | ST |  |  | 1.3643 | 1.3085 | 1.2373 | 1.1425 | 1.0416 | 0.9298 | 0.81013 | 0.65913 | 0.47114 | 0.069779 | -0.53077 | -0.98936 | -1.1163 | 1.5406 | 1.5214 | 1.5003 | 1.4665 | 1.4311 | 1.3921 | 1.3508 | 1.3072 | 1.2492 | 1.0818 | 0.77258 | 0.5995 | 0.5488 | 1.7766 | 1.763 | 1.7418 | 1.7227 | 1.701 | 1.677 | 1.5864 | 1.4389 | 1.2551 | 0.86007 | 0.23575 | -0.15462 | -0.2633
|  | CODFORD | FS |  |  | 1.3643 | 1.3085 | 1.2373 | 1.1425 | 1.0416 | 0.9298 | 0.81013 | 0.65913 | 0.47114 | 0.069779 | -0.53077 | -0.98936 | -1.1163 | 1.5406 | 1.5214 | 1.5003 | 1.4665 | 1.4311 | 1.3921 | 1.3508 | 1.3072 | 1.2492 | 1.0818 | 0.77258 | 0.5995 | 0.5488 | 1.7766 | 1.763 | 1.7418 | 1.7227 | 1.701 | 1.677 | 1.5864 | 1.4389 | 1.2551 | 0.86007 | 0.23575 | -0.15462 | -0.2633
IVER 132KV | DENHAM | COKES LANE | MINIMUM HEADROOM | SU 99240 97483 | YES | 10.2635 | 10.1245 | 9.9994 | 9.8307 | 9.6333 | 9.3771 | 9.0929 | 8.7793 | 8.3481 | 7.3545 | 5.6001 | 4.5053 | 3.8432 | 12.0245 | 11.9209 | 11.8293 | 11.7284 | 11.5996 | 11.4407 | 11.2619 | 11.0604 | 10.805 | 10.3124 | 9.4706 | 8.8716 | 8.3236 | 11.2797 | 11.148 | 11.0303 | 10.8751 | 10.6876 | 10.4554 | 10.1968 | 9.9102 | 9.5164 | 8.6492 | 7.1345 | 6.1642 | 5.6005
|  | COKES LANE | CT |  |  | 10.2635 | 10.1245 | 9.9994 | 9.8307 | 9.6333 | 9.3771 | 9.0929 | 8.7793 | 8.3481 | 7.3545 | 5.6001 | 4.5053 | 3.8432 | 12.0245 | 11.9209 | 11.8293 | 11.7284 | 11.5996 | 11.4407 | 11.2619 | 11.0604 | 10.805 | 10.3124 | 9.4706 | 8.8716 | 8.3236 | 11.2797 | 11.148 | 11.0303 | 10.8751 | 10.6876 | 10.4554 | 10.1968 | 9.9102 | 9.5164 | 8.6492 | 7.1345 | 6.1642 | 5.6005
|  | COKES LANE | LW |  |  | 10.2635 | 10.1245 | 9.9994 | 9.8307 | 9.6333 | 9.3771 | 9.0929 | 8.7793 | 8.3481 | 7.3545 | 5.6001 | 4.5053 | 3.8432 | 12.0245 | 11.9209 | 11.8293 | 11.7284 | 11.5996 | 11.4407 | 11.2619 | 11.0604 | 10.805 | 10.3124 | 9.4706 | 8.8716 | 8.3236 | 11.2797 | 11.148 | 11.0303 | 10.8751 | 10.6876 | 10.4554 | 10.1968 | 9.9102 | 9.5164 | 8.6492 | 7.1345 | 6.1642 | 5.6005
|  | COKES LANE | ST |  |  | 10.2635 | 10.1245 | 9.9994 | 9.8307 | 9.6333 | 9.3771 | 9.0929 | 8.7793 | 8.3481 | 7.3545 | 5.6001 | 4.5053 | 3.8432 | 12.0245 | 11.9209 | 11.8293 | 11.7284 | 11.5996 | 11.4407 | 11.2619 | 11.0604 | 10.805 | 10.3124 | 9.4706 | 8.8716 | 8.3236 | 11.2797 | 11.148 | 11.0303 | 10.8751 | 10.6876 | 10.4554 | 10.1968 | 9.9102 | 9.5164 | 8.6492 | 7.1345 | 6.1642 | 5.6005
|  | COKES LANE | FS |  |  | 10.2635 | 10.1245 | 9.9994 | 9.8307 | 9.6333 | 9.3771 | 9.0929 | 8.7793 | 8.3481 | 7.3545 | 5.6001 | 4.5053 | 3.8432 | 12.0245 | 11.9209 | 11.8293 | 11.7284 | 11.5996 | 11.4407 | 11.2619 | 11.0604 | 10.805 | 10.3124 | 9.4706 | 8.8716 | 8.3236 | 11.2797 | 11.148 | 11.0303 | 10.8751 | 10.6876 | 10.4554 | 10.1968 | 9.9102 | 9.5164 | 8.6492 | 7.1345 | 6.1642 | 5.6005
LOVEDEAN GSP | WYMERING BSP | COLLEGE PARK | MINIMUM HEADROOM | SU 65893 02686 | YES | 7.7372 | 7.5255 | 7.1846 | 6.7576 | 6.2976 | 5.7988 | 5.2558 | 4.6485 | 3.6824 | 0.54656 | -4.5971 | -8.446 | -10.7214 | 11.212 | 10.9968 | 10.6819 | 10.3146 | 9.9153 | 9.4756 | 8.9906 | 8.4399 | 7.6885 | 5.0994 | 0.27401 | -5.6532 | -13.9335 | 9.1149 | 8.9423 | 8.6725 | 8.3156 | 7.9328 | 7.5177 | 7.0682 | 6.5707 | 5.7419 | 2.8168 | -1.7982 | -5.1792 | -7.1796
|  | COLLEGE PARK | CT |  |  | 7.7372 | 7.5255 | 7.1846 | 6.7576 | 6.2976 | 5.7988 | 5.2558 | 4.6485 | 3.6824 | 0.54656 | -4.5971 | -8.446 | -10.7214 | 11.212 | 10.9968 | 10.6819 | 10.3146 | 9.9153 | 9.4756 | 8.9906 | 8.4399 | 7.6885 | 5.0994 | 0.27401 | -5.6532 | -13.9335 | 9.1149 | 8.9423 | 8.6725 | 8.3156 | 7.9328 | 7.5177 | 7.0682 | 6.5707 | 5.7419 | 2.8168 | -1.7982 | -5.1792 | -7.1796
|  | COLLEGE PARK | LW |  |  | 7.7372 | 7.5255 | 7.1846 | 6.7576 | 6.2976 | 5.7988 | 5.2558 | 4.6485 | 3.6824 | 0.54656 | -4.5971 | -8.446 | -10.7214 | 11.212 | 10.9968 | 10.6819 | 10.3146 | 9.9153 | 9.4756 | 8.9906 | 8.4399 | 7.6885 | 5.0994 | 0.27401 | -5.6532 | -13.9335 | 9.1149 | 8.9423 | 8.6725 | 8.3156 | 7.9328 | 7.5177 | 7.0682 | 6.5707 | 5.7419 | 2.8168 | -1.7982 | -5.1792 | -7.1796
|  | COLLEGE PARK | ST |  |  | 7.7372 | 7.5255 | 7.1846 | 6.7576 | 6.2976 | 5.7988 | 5.2558 | 4.6485 | 3.6824 | 0.54656 | -4.5971 | -8.446 | -10.7214 | 11.212 | 10.9968 | 10.6819 | 10.3146 | 9.9153 | 9.4756 | 8.9906 | 8.4399 | 7.6885 | 5.0994 | 0.27401 | -5.6532 | -13.9335 | 9.1149 | 8.9423 | 8.6725 | 8.3156 | 7.9328 | 7.5177 | 7.0682 | 6.5707 | 5.7419 | 2.8168 | -1.7982 | -5.1792 | -7.1796
|  | COLLEGE PARK | FS |  |  | 7.7372 | 7.5255 | 7.1846 | 6.7576 | 6.2976 | 5.7988 | 5.2558 | 4.6485 | 3.6824 | 0.54656 | -4.5971 | -8.446 | -10.7214 | 11.212 | 10.9968 | 10.6819 | 10.3146 | 9.9153 | 9.4756 | 8.9906 | 8.4399 | 7.6885 | 5.0994 | 0.27401 | -5.6532 | -13.9335 | 9.1149 | 8.9423 | 8.6725 | 8.3156 | 7.9328 | 7.5177 | 7.0682 | 6.5707 | 5.7419 | 2.8168 | -1.7982 | -5.1792 | -7.1796
EALING GSP | EALING 22kV | COPLEY DENE | MINIMUM HEADROOM | TQ 17445 80798 |  | 4.583 | 4.0724 | 3.4867 | 2.6073 | 1.6495 | 0.71466 | -0.29522 | -1.4438 | -3.2962 | -9.343 | -20.0047 | -27.3688 | -31.3887 | 15.2282 | 14.7107 | 14.1213 | 13.3337 | 12.473 | 11.5678 | 10.5719 | 9.4346 | 7.924 | 2.6848 | -8.367 | -21.629 | -41.063 | 7.2764 | 6.7949 | 6.2341 | 5.4393 | 4.5712 | 3.7079 | 2.7705 | 1.6919 | 0.0045714 | -5.5916 | -15.2173 | -21.4755 | -24.809
|  | COPLEY DENE | CT |  |  | 4.583 | 4.0724 | 3.4867 | 2.6073 | 1.6495 | 0.71466 | -0.29522 | -1.4438 | -3.2962 | -9.343 | -20.0047 | -27.3688 | -31.3887 | 15.2282 | 14.7107 | 14.1213 | 13.3337 | 12.473 | 11.5678 | 10.5719 | 9.4346 | 7.924 | 2.6848 | -8.367 | -21.629 | -41.063 | 7.2764 | 6.7949 | 6.2341 | 5.4393 | 4.5712 | 3.7079 | 2.7705 | 1.6919 | 0.0045714 | -5.5916 | -15.2173 | -21.4755 | -24.809
|  | COPLEY DENE | LW |  |  | 4.583 | 4.0724 | 3.4867 | 2.6073 | 1.6495 | 0.71466 | -0.29522 | -1.4438 | -3.2962 | -9.343 | -20.0047 | -27.3688 | -31.3887 | 15.2282 | 14.7107 | 14.1213 | 13.3337 | 12.473 | 11.5678 | 10.5719 | 9.4346 | 7.924 | 2.6848 | -8.367 | -21.629 | -41.063 | 7.2764 | 6.7949 | 6.2341 | 5.4393 | 4.5712 | 3.7079 | 2.7705 | 1.6919 | 0.0045714 | -5.5916 | -15.2173 | -21.4755 | -24.809
|  | COPLEY DENE | ST |  |  | 4.583 | 4.0724 | 3.4867 | 2.6073 | 1.6495 | 0.71466 | -0.29522 | -1.4438 | -3.2962 | -9.343 | -20.0047 | -27.3688 | -31.3887 | 15.2282 | 14.7107 | 14.1213 | 13.3337 | 12.473 | 11.5678 | 10.5719 | 9.4346 | 7.924 | 2.6848 | -8.367 | -21.629 | -41.063 | 7.2764 | 6.7949 | 6.2341 | 5.4393 | 4.5712 | 3.7079 | 2.7705 | 1.6919 | 0.0045714 | -5.5916 | -15.2173 | -21.4755 | -24.809
|  | COPLEY DENE | FS |  |  | 4.583 | 4.0724 | 3.4867 | 2.6073 | 1.6495 | 0.71466 | -0.29522 | -1.4438 | -3.2962 | -9.343 | -20.0047 | -27.3688 | -31.3887 | 15.2282 | 14.7107 | 14.1213 | 13.3337 | 12.473 | 11.5678 | 10.5719 | 9.4346 | 7.924 | 2.6848 | -8.367 | -21.629 | -41.063 | 7.2764 | 6.7949 | 6.2341 | 5.4393 | 4.5712 | 3.7079 | 2.7705 | 1.6919 | 0.0045714 | -5.5916 | -15.2173 | -21.4755 | -24.809
BRAMLEY (FLEE) | MAIDENHEAD BSP | CORDWALLIS | MINIMUM HEADROOM | SU 88285 81857 | YES | 19.7259 | 19.2084 | 18.5928 | 17.8888 | 17.1459 | 16.4551 | 15.6739 | 14.7825 | 13.3419 | 9.5836 | 3.8599 | -0.27487 | -2.5733 | 20.0841 | 19.7407 | 19.3342 | 18.9021 | 18.4427 | 17.9948 | 17.4843 | 16.8783 | 15.9304 | 13.4966 | 10.0312 | 7.196 | 4.4357 | 19.0342 | 18.593 | 18.0677 | 17.4478 | 16.7937 | 16.1809 | 15.4893 | 14.703 | 13.3911 | 9.909 | 4.7811 | 1.0418 | -0.95751
|  | CORDWALLIS | CT |  |  | 19.7259 | 19.2084 | 18.5928 | 17.8888 | 17.1459 | 16.4551 | 15.6739 | 14.7825 | 13.3419 | 9.5836 | 3.8599 | -0.27487 | -2.5733 | 20.0841 | 19.7407 | 19.3342 | 18.9021 | 18.4427 | 17.9948 | 17.4843 | 16.8783 | 15.9304 | 13.4966 | 10.0312 | 7.196 | 4.4357 | 19.0342 | 18.593 | 18.0677 | 17.4478 | 16.7937 | 16.1809 | 15.4893 | 14.703 | 13.3911 | 9.909 | 4.7811 | 1.0418 | -0.95751
|  | CORDWALLIS | LW |  |  | 19.7259 | 19.2084 | 18.5928 | 17.8888 | 17.1459 | 16.4551 | 15.6739 | 14.7825 | 13.3419 | 9.5836 | 3.8599 | -0.27487 | -2.5733 | 20.0841 | 19.7407 | 19.3342 | 18.9021 | 18.4427 | 17.9948 | 17.4843 | 16.8783 | 15.9304 | 13.4966 | 10.0312 | 7.196 | 4.4357 | 19.0342 | 18.593 | 18.0677 | 17.4478 | 16.7937 | 16.1809 | 15.4893 | 14.703 | 13.3911 | 9.909 | 4.7811 | 1.0418 | -0.95751
|  | CORDWALLIS | ST |  |  | 19.7259 | 19.2084 | 18.5928 | 17.8888 | 17.1459 | 16.4551 | 15.6739 | 14.7825 | 13.3419 | 9.5836 | 3.8599 | -0.27487 | -2.5733 | 20.0841 | 19.7407 | 19.3342 | 18.9021 | 18.4427 | 17.9948 | 17.4843 | 16.8783 | 15.9304 | 13.4966 | 10.0312 | 7.196 | 4.4357 | 19.0342 | 18.593 | 18.0677 | 17.4478 | 16.7937 | 16.1809 | 15.4893 | 14.703 | 13.3911 | 9.909 | 4.7811 | 1.0418 | -0.95751
|  | CORDWALLIS | FS |  |  | 19.7259 | 19.2084 | 18.5928 | 17.8888 | 17.1459 | 16.4551 | 15.6739 | 14.7825 | 13.3419 | 9.5836 | 3.8599 | -0.27487 | -2.5733 | 20.0841 | 19.7407 | 19.3342 | 18.9021 | 18.4427 | 17.9948 | 17.4843 | 16.8783 | 15.9304 | 13.4966 | 10.0312 | 7.196 | 4.4357 | 19.0342 | 18.593 | 18.0677 | 17.4478 | 16.7937 | 16.1809 | 15.4893 | 14.703 | 13.3911 | 9.909 | 4.7811 | 1.0418 | -0.95751
MANNINGTON GSP | LYTCHETT | CORFE MULLEN | MINIMUM HEADROOM | SY 98583 96071 | YES | 26.2969 | 25.9512 | 25.5793 | 25.0065 | 24.3458 | 23.6533 | 22.8243 | 21.8631 | 20.4285 | 17.2095 | 12.2044 | 8.3725 | 6.3293 | 25.6131 | 25.345 | 25.0295 | 24.64 | 24.1926 | 23.714 | 23.1536 | 22.4872 | 21.5599 | 19.6744 | 16.9512 | 14.8564 | 13.058 | 27.8637 | 27.5447 | 27.1875 | 26.6614 | 26.0589 | 25.426 | 24.6988 | 23.8571 | 22.583 | 19.7004 | 15.1337 | 11.8089 | 10.065
|  | CORFE MULLEN | CT |  |  | 26.2969 | 25.9512 | 25.5793 | 25.0065 | 24.3458 | 23.6533 | 22.8243 | 21.8631 | 20.4285 | 17.2095 | 12.2044 | 8.3725 | 6.3293 | 25.6131 | 25.345 | 25.0295 | 24.64 | 24.1926 | 23.714 | 23.1536 | 22.4872 | 21.5599 | 19.6744 | 16.9512 | 14.8564 | 13.058 | 27.8637 | 27.5447 | 27.1875 | 26.6614 | 26.0589 | 25.426 | 24.6988 | 23.8571 | 22.583 | 19.7004 | 15.1337 | 11.8089 | 10.065
|  | CORFE MULLEN | LW |  |  | 26.2969 | 25.9512 | 25.5793 | 25.0065 | 24.3458 | 23.6533 | 22.8243 | 21.8631 | 20.4285 | 17.2095 | 12.2044 | 8.3725 | 6.3293 | 25.6131 | 25.345 | 25.0295 | 24.64 | 24.1926 | 23.714 | 23.1536 | 22.4872 | 21.5599 | 19.6744 | 16.9512 | 14.8564 | 13.058 | 27.8637 | 27.5447 | 27.1875 | 26.6614 | 26.0589 | 25.426 | 24.6988 | 23.8571 | 22.583 | 19.7004 | 15.1337 | 11.8089 | 10.065
|  | CORFE MULLEN | ST |  |  | 26.2969 | 25.9512 | 25.5793 | 25.0065 | 24.3458 | 23.6533 | 22.8243 | 21.8631 | 20.4285 | 17.2095 | 12.2044 | 8.3725 | 6.3293 | 25.6131 | 25.345 | 25.0295 | 24.64 | 24.1926 | 23.714 | 23.1536 | 22.4872 | 21.5599 | 19.6744 | 16.9512 | 14.8564 | 13.058 | 27.8637 | 27.5447 | 27.1875 | 26.6614 | 26.0589 | 25.426 | 24.6988 | 23.8571 | 22.583 | 19.7004 | 15.1337 | 11.8089 | 10.065
|  | CORFE MULLEN | FS |  |  | 26.2969 | 25.9512 | 25.5793 | 25.0065 | 24.3458 | 23.6533 | 22.8243 | 21.8631 | 20.4285 | 17.2095 | 12.2044 | 8.3725 | 6.3293 | 25.6131 | 25.345 | 25.0295 | 24.64 | 24.1926 | 23.714 | 23.1536 | 22.4872 | 21.5599 | 19.6744 | 16.9512 | 14.8564 | 13.058 | 27.8637 | 27.5447 | 27.1875 | 26.6614 | 26.0589 | 25.426 | 24.6988 | 23.8571 | 22.583 | 19.7004 | 15.1337 | 11.8089 | 10.065
MELKSHAM GSP | NORRINGTON | CORSHAM | MINIMUM HEADROOM | ST 86766 69583 | YES | 2.8387 | 2.6109 | 2.3238 | 1.9401 | 1.5304 | 1.091 | 0.60882 | 0.055666 | -0.87307 | -3.2651 | -6.6715 | -8.832 | -9.8148 | 4.924 | 4.7587 | 4.5491 | 4.3012 | 4.0335 | 3.7393 | 3.4133 | 3.0321 | 2.4416 | 0.92765 | -1.1773 | -2.7252 | -4.15 | 3.4829 | 3.2939 | 3.0599 | 2.7243 | 2.3514 | 1.9446 | 1.485 | 0.95537 | 0.072771 | -2.1758 | -5.2718 | -7.2437 | -8.1591
|  | CORSHAM | CT |  |  | 2.8387 | 2.6109 | 2.3238 | 1.9401 | 1.5304 | 1.091 | 0.60882 | 0.055666 | -0.87307 | -3.2651 | -6.6715 | -8.832 | -9.8148 | 4.924 | 4.7587 | 4.5491 | 4.3012 | 4.0335 | 3.7393 | 3.4133 | 3.0321 | 2.4416 | 0.92765 | -1.1773 | -2.7252 | -4.15 | 3.4829 | 3.2939 | 3.0599 | 2.7243 | 2.3514 | 1.9446 | 1.485 | 0.95537 | 0.072771 | -2.1758 | -5.2718 | -7.2437 | -8.1591
|  | CORSHAM | LW |  |  | 2.8387 | 2.6109 | 2.3238 | 1.9401 | 1.5304 | 1.091 | 0.60882 | 0.055666 | -0.87307 | -3.2651 | -6.6715 | -8.832 | -9.8148 | 4.924 | 4.7587 | 4.5491 | 4.3012 | 4.0335 | 3.7393 | 3.4133 | 3.0321 | 2.4416 | 0.92765 | -1.1773 | -2.7252 | -4.15 | 3.4829 | 3.2939 | 3.0599 | 2.7243 | 2.3514 | 1.9446 | 1.485 | 0.95537 | 0.072771 | -2.1758 | -5.2718 | -7.2437 | -8.1591
|  | CORSHAM | ST |  |  | 2.8387 | 2.6109 | 2.3238 | 1.9401 | 1.5304 | 1.091 | 0.60882 | 0.055666 | -0.87307 | -3.2651 | -6.6715 | -8.832 | -9.8148 | 4.924 | 4.7587 | 4.5491 | 4.3012 | 4.0335 | 3.7393 | 3.4133 | 3.0321 | 2.4416 | 0.92765 | -1.1773 | -2.7252 | -4.15 | 3.4829 | 3.2939 | 3.0599 | 2.7243 | 2.3514 | 1.9446 | 1.485 | 0.95537 | 0.072771 | -2.1758 | -5.2718 | -7.2437 | -8.1591
|  | CORSHAM | FS |  |  | 2.8387 | 2.6109 | 2.3238 | 1.9401 | 1.5304 | 1.091 | 0.60882 | 0.055666 | -0.87307 | -3.2651 | -6.6715 | -8.832 | -9.8148 | 4.924 | 4.7587 | 4.5491 | 4.3012 | 4.0335 | 3.7393 | 3.4133 | 3.0321 | 2.4416 | 0.92765 | -1.1773 | -2.7252 | -4.15 | 3.4829 | 3.2939 | 3.0599 | 2.7243 | 2.3514 | 1.9446 | 1.485 | 0.95537 | 0.072771 | -2.1758 | -5.2718 | -7.2437 | -8.1591
EAST CLAYDON GSP | BICESTER NORTH BSP | COTTISFORD | MINIMUM HEADROOM | SP 59021 31128 | NO | -1.4984 | -1.5565 | -1.6133 | -1.6868 | -1.7626 | -1.8495 | -1.9488 | -2.057 | -2.1981 | -2.4738 | -2.9689 | -3.1735 | -3.2263 | 0.075463 | 0.028816 | -0.016094 | -0.065616 | -0.11786 | -0.1799 | -0.25355 | -0.33818 | -0.44352 | -0.58905 | -0.82321 | -0.94119 | -1.0308 | -0.92239 | -0.98495 | -1.0452 | -1.1181 | -1.1939 | -1.2824 | -1.3855 | -1.5011 | -1.6497 | -1.8911 | -2.2995 | -2.4664 | -2.5111
|  | COTTISFORD | CT |  |  | -1.4984 | -1.5565 | -1.6133 | -1.6868 | -1.7626 | -1.8495 | -1.9488 | -2.057 | -2.1981 | -2.4738 | -2.9689 | -3.1735 | -3.2263 | 0.075463 | 0.028816 | -0.016094 | -0.065616 | -0.11786 | -0.1799 | -0.25355 | -0.33818 | -0.44352 | -0.58905 | -0.82321 | -0.94119 | -1.0308 | -0.92239 | -0.98495 | -1.0452 | -1.1181 | -1.1939 | -1.2824 | -1.3855 | -1.5011 | -1.6497 | -1.8911 | -2.2995 | -2.4664 | -2.5111
|  | COTTISFORD | LW |  |  | -1.4984 | -1.5565 | -1.6133 | -1.6868 | -1.7626 | -1.8495 | -1.9488 | -2.057 | -2.1981 | -2.4738 | -2.9689 | -3.1735 | -3.2263 | 0.075463 | 0.028816 | -0.016094 | -0.065616 | -0.11786 | -0.1799 | -0.25355 | -0.33818 | -0.44352 | -0.58905 | -0.82321 | -0.94119 | -1.0308 | -0.92239 | -0.98495 | -1.0452 | -1.1181 | -1.1939 | -1.2824 | -1.3855 | -1.5011 | -1.6497 | -1.8911 | -2.2995 | -2.4664 | -2.5111
|  | COTTISFORD | ST |  |  | -1.4984 | -1.5565 | -1.6133 | -1.6868 | -1.7626 | -1.8495 | -1.9488 | -2.057 | -2.1981 | -2.4738 | -2.9689 | -3.1735 | -3.2263 | 0.075463 | 0.028816 | -0.016094 | -0.065616 | -0.11786 | -0.1799 | -0.25355 | -0.33818 | -0.44352 | -0.58905 | -0.82321 | -0.94119 | -1.0308 | -0.92239 | -0.98495 | -1.0452 | -1.1181 | -1.1939 | -1.2824 | -1.3855 | -1.5011 | -1.6497 | -1.8911 | -2.2995 | -2.4664 | -2.5111
|  | COTTISFORD | FS |  |  | -1.4984 | -1.5565 | -1.6133 | -1.6868 | -1.7626 | -1.8495 | -1.9488 | -2.057 | -2.1981 | -2.4738 | -2.9689 | -3.1735 | -3.2263 | 0.075463 | 0.028816 | -0.016094 | -0.065616 | -0.11786 | -0.1799 | -0.25355 | -0.33818 | -0.44352 | -0.58905 | -0.82321 | -0.94119 | -1.0308 | -0.92239 | -0.98495 | -1.0452 | -1.1181 | -1.1939 | -1.2824 | -1.3855 | -1.5011 | -1.6497 | -1.8911 | -2.2995 | -2.4664 | -2.5111
BRAMLEY (FLEE) | BURGHFIELD MAIN | COURAGES | MINIMUM HEADROOM | SU 70990 69570 | YES | 14.3428 | 13.921 | 13.3771 | 12.8714 | 12.4645 | 11.9604 | 11.4783 | 10.7017 | 9.9497 | 7.0278 | 3.8245 | 3.2517 | 3.0444 | 15.3827 | 15.0077 | 14.5188 | 14.0542 | 13.6937 | 13.2509 | 12.8816 | 12.3867 | 11.8043 | 9.3196 | 6.7826 | 6.3548 | 6.1914 | 15.0403 | 14.648 | 14.1438 | 13.6539 | 13.2513 | 12.7724 | 12.3606 | 11.8093 | 11.2743 | 8.9658 | 5.8744 | 5.3303 | 5.1371
|  | COURAGES | CT |  |  | 14.3428 | 13.921 | 13.3771 | 12.8714 | 12.4645 | 11.9604 | 11.4783 | 10.7017 | 9.9497 | 7.0278 | 3.8245 | 3.2517 | 3.0444 | 15.3827 | 15.0077 | 14.5188 | 14.0542 | 13.6937 | 13.2509 | 12.8816 | 12.3867 | 11.8043 | 9.3196 | 6.7826 | 6.3548 | 6.1914 | 15.0403 | 14.648 | 14.1438 | 13.6539 | 13.2513 | 12.7724 | 12.3606 | 11.8093 | 11.2743 | 8.9658 | 5.8744 | 5.3303 | 5.1371
|  | COURAGES | LW |  |  | 14.3428 | 13.921 | 13.3771 | 12.8714 | 12.4645 | 11.9604 | 11.4783 | 10.7017 | 9.9497 | 7.0278 | 3.8245 | 3.2517 | 3.0444 | 15.3827 | 15.0077 | 14.5188 | 14.0542 | 13.6937 | 13.2509 | 12.8816 | 12.3867 | 11.8043 | 9.3196 | 6.7826 | 6.3548 | 6.1914 | 15.0403 | 14.648 | 14.1438 | 13.6539 | 13.2513 | 12.7724 | 12.3606 | 11.8093 | 11.2743 | 8.9658 | 5.8744 | 5.3303 | 5.1371
|  | COURAGES | ST |  |  | 14.3428 | 13.921 | 13.3771 | 12.8714 | 12.4645 | 11.9604 | 11.4783 | 10.7017 | 9.9497 | 7.0278 | 3.8245 | 3.2517 | 3.0444 | 15.3827 | 15.0077 | 14.5188 | 14.0542 | 13.6937 | 13.2509 | 12.8816 | 12.3867 | 11.8043 | 9.3196 | 6.7826 | 6.3548 | 6.1914 | 15.0403 | 14.648 | 14.1438 | 13.6539 | 13.2513 | 12.7724 | 12.3606 | 11.8093 | 11.2743 | 8.9658 | 5.8744 | 5.3303 | 5.1371
|  | COURAGES | FS |  |  | 14.3428 | 13.921 | 13.3771 | 12.8714 | 12.4645 | 11.9604 | 11.4783 | 10.7017 | 9.9497 | 7.0278 | 3.8245 | 3.2517 | 3.0444 | 15.3827 | 15.0077 | 14.5188 | 14.0542 | 13.6937 | 13.2509 | 12.8816 | 12.3867 | 11.8043 | 9.3196 | 6.7826 | 6.3548 | 6.1914 | 15.0403 | 14.648 | 14.1438 | 13.6539 | 13.2513 | 12.7724 | 12.3606 | 11.8093 | 11.2743 | 8.9658 | 5.8744 | 5.3303 | 5.1371
BRAMLEY (FLEE) | CAMBERLEY RESERVE | COVE | MINIMUM HEADROOM | SU 85415 55937 | YES | 20.1223 | 19.653 | 19.1457 | 18.6391 | 18.0881 | 17.5028 | 16.8699 | 16.1036 | 14.9434 | 12.0617 | 7.6434 | 4.6544 | 3.0031 | 19.0332 | 18.6779 | 18.2528 | 17.8784 | 17.4697 | 17.0327 | 16.559 | 15.9742 | 15.1512 | 13.1576 | 10.2875 | 8.1093 | 5.9873 | 21.6569 | 21.2428 | 20.7778 | 20.3147 | 19.8122 | 19.2802 | 18.6994 | 17.9638 | 16.859 | 14.1517 | 10.1368 | 7.443 | 5.9539
|  | COVE | CT |  |  | 20.1223 | 19.653 | 19.1457 | 18.6391 | 18.0881 | 17.5028 | 16.8699 | 16.1036 | 14.9434 | 12.0617 | 7.6434 | 4.6544 | 3.0031 | 19.0332 | 18.6779 | 18.2528 | 17.8784 | 17.4697 | 17.0327 | 16.559 | 15.9742 | 15.1512 | 13.1576 | 10.2875 | 8.1093 | 5.9873 | 21.6569 | 21.2428 | 20.7778 | 20.3147 | 19.8122 | 19.2802 | 18.6994 | 17.9638 | 16.859 | 14.1517 | 10.1368 | 7.443 | 5.9539
|  | COVE | LW |  |  | 20.1223 | 19.653 | 19.1457 | 18.6391 | 18.0881 | 17.5028 | 16.8699 | 16.1036 | 14.9434 | 12.0617 | 7.6434 | 4.6544 | 3.0031 | 19.0332 | 18.6779 | 18.2528 | 17.8784 | 17.4697 | 17.0327 | 16.559 | 15.9742 | 15.1512 | 13.1576 | 10.2875 | 8.1093 | 5.9873 | 21.6569 | 21.2428 | 20.7778 | 20.3147 | 19.8122 | 19.2802 | 18.6994 | 17.9638 | 16.859 | 14.1517 | 10.1368 | 7.443 | 5.9539
|  | COVE | ST |  |  | 20.1223 | 19.653 | 19.1457 | 18.6391 | 18.0881 | 17.5028 | 16.8699 | 16.1036 | 14.9434 | 12.0617 | 7.6434 | 4.6544 | 3.0031 | 19.0332 | 18.6779 | 18.2528 | 17.8784 | 17.4697 | 17.0327 | 16.559 | 15.9742 | 15.1512 | 13.1576 | 10.2875 | 8.1093 | 5.9873 | 21.6569 | 21.2428 | 20.7778 | 20.3147 | 19.8122 | 19.2802 | 18.6994 | 17.9638 | 16.859 | 14.1517 | 10.1368 | 7.443 | 5.9539
|  | COVE | FS |  |  | 20.1223 | 19.653 | 19.1457 | 18.6391 | 18.0881 | 17.5028 | 16.8699 | 16.1036 | 14.9434 | 12.0617 | 7.6434 | 4.6544 | 3.0031 | 19.0332 | 18.6779 | 18.2528 | 17.8784 | 17.4697 | 17.0327 | 16.559 | 15.9742 | 15.1512 | 13.1576 | 10.2875 | 8.1093 | 5.9873 | 21.6569 | 21.2428 | 20.7778 | 20.3147 | 19.8122 | 19.2802 | 18.6994 | 17.9638 | 16.859 | 14.1517 | 10.1368 | 7.443 | 5.9539
FAWLEY GSP | COWES & WOOTTON COMMON BSP | COWES | MINIMUM HEADROOM | SP 56113 03074 | YES | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88
|  | COWES | CT |  |  | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88
|  | COWES | LW |  |  | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88
|  | COWES | ST |  |  | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88
|  | COWES | FS |  |  | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88
COWLEY GSP | COWLEY LOCAL (2 X 90) | COWLEY LOCAL | MINIMUM HEADROOM | SP 56113 03074 | YES | 13.7391 | 13.1192 | 12.2547 | 11.1451 | 9.8769 | 8.4211 | 7.0419 | 5.4896 | 3.3644 | -2.4897 | -11.7441 | -18.1774 | -21.6875 | 16.8778 | 16.3878 | 15.7689 | 14.9791 | 14.0796 | 13.0745 | 12.1073 | 10.9254 | 9.397 | 5.1829 | -1.4445 | -7.5112 | -14.7335 | 16.7559 | 16.2124 | 15.4898 | 14.4991 | 13.3748 | 12.1049 | 10.8977 | 9.5264 | 7.6126 | 2.1741 | -6.3767 | -12.1487 | -15.1987
|  | COWLEY LOCAL | CT |  |  | 13.7391 | 13.1192 | 12.2547 | 11.1451 | 9.8769 | 8.4211 | 7.0419 | 5.4896 | 3.3644 | -2.4897 | -11.7441 | -18.1774 | -21.6875 | 16.8778 | 16.3878 | 15.7689 | 14.9791 | 14.0796 | 13.0745 | 12.1073 | 10.9254 | 9.397 | 5.1829 | -1.4445 | -7.5112 | -14.7335 | 16.7559 | 16.2124 | 15.4898 | 14.4991 | 13.3748 | 12.1049 | 10.8977 | 9.5264 | 7.6126 | 2.1741 | -6.3767 | -12.1487 | -15.1987
|  | COWLEY LOCAL | LW |  |  | 13.7391 | 13.1192 | 12.2547 | 11.1451 | 9.8769 | 8.4211 | 7.0419 | 5.4896 | 3.3644 | -2.4897 | -11.7441 | -18.1774 | -21.6875 | 16.8778 | 16.3878 | 15.7689 | 14.9791 | 14.0796 | 13.0745 | 12.1073 | 10.9254 | 9.397 | 5.1829 | -1.4445 | -7.5112 | -14.7335 | 16.7559 | 16.2124 | 15.4898 | 14.4991 | 13.3748 | 12.1049 | 10.8977 | 9.5264 | 7.6126 | 2.1741 | -6.3767 | -12.1487 | -15.1987
|  | COWLEY LOCAL | ST |  |  | 13.7391 | 13.1192 | 12.2547 | 11.1451 | 9.8769 | 8.4211 | 7.0419 | 5.4896 | 3.3644 | -2.4897 | -11.7441 | -18.1774 | -21.6875 | 16.8778 | 16.3878 | 15.7689 | 14.9791 | 14.0796 | 13.0745 | 12.1073 | 10.9254 | 9.397 | 5.1829 | -1.4445 | -7.5112 | -14.7335 | 16.7559 | 16.2124 | 15.4898 | 14.4991 | 13.3748 | 12.1049 | 10.8977 | 9.5264 | 7.6126 | 2.1741 | -6.3767 | -12.1487 | -15.1987
|  | COWLEY LOCAL | FS |  |  | 13.7391 | 13.1192 | 12.2547 | 11.1451 | 9.8769 | 8.4211 | 7.0419 | 5.4896 | 3.3644 | -2.4897 | -11.7441 | -18.1774 | -21.6875 | 16.8778 | 16.3878 | 15.7689 | 14.9791 | 14.0796 | 13.0745 | 12.1073 | 10.9254 | 9.397 | 5.1829 | -1.4445 | -7.5112 | -14.7335 | 16.7559 | 16.2124 | 15.4898 | 14.4991 | 13.3748 | 12.1049 | 10.8977 | 9.5264 | 7.6126 | 2.1741 | -6.3767 | -12.1487 | -15.1987
BRAMLEY (FLEE) | COXMOOR WOOD BSP | COXMOOR WOOD | MINIMUM HEADROOM | SU 78275 50779 | YES | 1.7785 | 1.645 | 1.485 | 1.2917 | 1.1467 | 1.0001 | 0.66901 | 0.2363 | -0.4103 | -1.7264 | -3.911 | -5.3806 | -6.0245 | 4.7248 | 4.6357 | 4.521 | 4.4051 | 4.3118 | 4.1917 | 3.9391 | 3.624 | 3.1929 | 2.3916 | 1.1667 | 0.31118 | -0.35766 | 2.9277 | 2.6618 | 2.3735 | 2.0456 | 1.7613 | 1.462 | 1.1227 | 0.70782 | 0.094702 | -1.1248 | -3.1001 | -4.4007 | -4.9672
|  | COXMOOR WOOD | CT |  |  | 1.7785 | 1.645 | 1.485 | 1.2917 | 1.1467 | 1.0001 | 0.66901 | 0.2363 | -0.4103 | -1.7264 | -3.911 | -5.3806 | -6.0245 | 4.7248 | 4.6357 | 4.521 | 4.4051 | 4.3118 | 4.1917 | 3.9391 | 3.624 | 3.1929 | 2.3916 | 1.1667 | 0.31118 | -0.35766 | 2.9277 | 2.6618 | 2.3735 | 2.0456 | 1.7613 | 1.462 | 1.1227 | 0.70782 | 0.094702 | -1.1248 | -3.1001 | -4.4007 | -4.9672
|  | COXMOOR WOOD | LW |  |  | 1.7785 | 1.645 | 1.485 | 1.2917 | 1.1467 | 1.0001 | 0.66901 | 0.2363 | -0.4103 | -1.7264 | -3.911 | -5.3806 | -6.0245 | 4.7248 | 4.6357 | 4.521 | 4.4051 | 4.3118 | 4.1917 | 3.9391 | 3.624 | 3.1929 | 2.3916 | 1.1667 | 0.31118 | -0.35766 | 2.9277 | 2.6618 | 2.3735 | 2.0456 | 1.7613 | 1.462 | 1.1227 | 0.70782 | 0.094702 | -1.1248 | -3.1001 | -4.4007 | -4.9672
|  | COXMOOR WOOD | ST |  |  | 1.7785 | 1.645 | 1.485 | 1.2917 | 1.1467 | 1.0001 | 0.66901 | 0.2363 | -0.4103 | -1.7264 | -3.911 | -5.3806 | -6.0245 | 4.7248 | 4.6357 | 4.521 | 4.4051 | 4.3118 | 4.1917 | 3.9391 | 3.624 | 3.1929 | 2.3916 | 1.1667 | 0.31118 | -0.35766 | 2.9277 | 2.6618 | 2.3735 | 2.0456 | 1.7613 | 1.462 | 1.1227 | 0.70782 | 0.094702 | -1.1248 | -3.1001 | -4.4007 | -4.9672
|  | COXMOOR WOOD | FS |  |  | 1.7785 | 1.645 | 1.485 | 1.2917 | 1.1467 | 1.0001 | 0.66901 | 0.2363 | -0.4103 | -1.7264 | -3.911 | -5.3806 | -6.0245 | 4.7248 | 4.6357 | 4.521 | 4.4051 | 4.3118 | 4.1917 | 3.9391 | 3.624 | 3.1929 | 2.3916 | 1.1667 | 0.31118 | -0.35766 | 2.9277 | 2.6618 | 2.3735 | 2.0456 | 1.7613 | 1.462 | 1.1227 | 0.70782 | 0.094702 | -1.1248 | -3.1001 | -4.4007 | -4.9672
MANNINGTON GSP | LYTCHETT | CREEKMOOR | MINIMUM HEADROOM | SZ 00552 94121 | YES | 23.3778 | 23.2125 | 23.0345 | 22.8437 | 22.6295 | 22.393 | 21.8708 | 21.0136 | 19.7094 | 16.315 | 11.1342 | 7.4341 | 5.4113 | 26.4504 | 26.1943 | 25.8626 | 25.4943 | 25.0923 | 24.6444 | 24.1324 | 23.5106 | 22.6357 | 20.4311 | 17.4231 | 15.2834 | 13.4361 | 25.4584 | 25.1549 | 24.7829 | 24.3051 | 23.7861 | 23.2141 | 22.5714 | 21.8078 | 20.6269 | 17.4505 | 12.767 | 9.4769 | 7.7527
|  | CREEKMOOR | CT |  |  | 23.3778 | 23.2125 | 23.0345 | 22.8437 | 22.6295 | 22.393 | 21.8708 | 21.0136 | 19.7094 | 16.315 | 11.1342 | 7.4341 | 5.4113 | 26.4504 | 26.1943 | 25.8626 | 25.4943 | 25.0923 | 24.6444 | 24.1324 | 23.5106 | 22.6357 | 20.4311 | 17.4231 | 15.2834 | 13.4361 | 25.4584 | 25.1549 | 24.7829 | 24.3051 | 23.7861 | 23.2141 | 22.5714 | 21.8078 | 20.6269 | 17.4505 | 12.767 | 9.4769 | 7.7527
|  | CREEKMOOR | LW |  |  | 23.3778 | 23.2125 | 23.0345 | 22.8437 | 22.6295 | 22.393 | 21.8708 | 21.0136 | 19.7094 | 16.315 | 11.1342 | 7.4341 | 5.4113 | 26.4504 | 26.1943 | 25.8626 | 25.4943 | 25.0923 | 24.6444 | 24.1324 | 23.5106 | 22.6357 | 20.4311 | 17.4231 | 15.2834 | 13.4361 | 25.4584 | 25.1549 | 24.7829 | 24.3051 | 23.7861 | 23.2141 | 22.5714 | 21.8078 | 20.6269 | 17.4505 | 12.767 | 9.4769 | 7.7527
|  | CREEKMOOR | ST |  |  | 23.3778 | 23.2125 | 23.0345 | 22.8437 | 22.6295 | 22.393 | 21.8708 | 21.0136 | 19.7094 | 16.315 | 11.1342 | 7.4341 | 5.4113 | 26.4504 | 26.1943 | 25.8626 | 25.4943 | 25.0923 | 24.6444 | 24.1324 | 23.5106 | 22.6357 | 20.4311 | 17.4231 | 15.2834 | 13.4361 | 25.4584 | 25.1549 | 24.7829 | 24.3051 | 23.7861 | 23.2141 | 22.5714 | 21.8078 | 20.6269 | 17.4505 | 12.767 | 9.4769 | 7.7527
|  | CREEKMOOR | FS |  |  | 23.3778 | 23.2125 | 23.0345 | 22.8437 | 22.6295 | 22.393 | 21.8708 | 21.0136 | 19.7094 | 16.315 | 11.1342 | 7.4341 | 5.4113 | 26.4504 | 26.1943 | 25.8626 | 25.4943 | 25.0923 | 24.6444 | 24.1324 | 23.5106 | 22.6357 | 20.4311 | 17.4231 | 15.2834 | 13.4361 | 25.4584 | 25.1549 | 24.7829 | 24.3051 | 23.7861 | 23.2141 | 22.5714 | 21.8078 | 20.6269 | 17.4505 | 12.767 | 9.4769 | 7.7527
MINETY GSP | CIRENCESTER BSP | CRICKLADE | MINIMUM HEADROOM | SU 09400 93270 | YES | 7.655 | 7.4636 | 7.2575 | 6.9488 | 6.6274 | 6.2981 | 5.9211 | 5.5096 | 4.8678 | 3.4151 | 0.97172 | -0.58003 | -1.1984 | 10.1265 | 10.0109 | 9.8841 | 9.7212 | 9.5497 | 9.3677 | 9.1541 | 8.9158 | 8.4952 | 7.7034 | 6.6523 | 5.8757 | 5.367 | 8.9641 | 8.7549 | 8.5262 | 8.2224 | 7.9039 | 7.5684 | 7.1729 | 6.731 | 6.0591 | 4.707 | 2.662 | 1.4251 | 0.93669
|  | CRICKLADE | CT |  |  | 7.655 | 7.4636 | 7.2575 | 6.9488 | 6.6274 | 6.2981 | 5.9211 | 5.5096 | 4.8678 | 3.4151 | 0.97172 | -0.58003 | -1.1984 | 10.1265 | 10.0109 | 9.8841 | 9.7212 | 9.5497 | 9.3677 | 9.1541 | 8.9158 | 8.4952 | 7.7034 | 6.6523 | 5.8757 | 5.367 | 8.9641 | 8.7549 | 8.5262 | 8.2224 | 7.9039 | 7.5684 | 7.1729 | 6.731 | 6.0591 | 4.707 | 2.662 | 1.4251 | 0.93669
|  | CRICKLADE | LW |  |  | 7.655 | 7.4636 | 7.2575 | 6.9488 | 6.6274 | 6.2981 | 5.9211 | 5.5096 | 4.8678 | 3.4151 | 0.97172 | -0.58003 | -1.1984 | 10.1265 | 10.0109 | 9.8841 | 9.7212 | 9.5497 | 9.3677 | 9.1541 | 8.9158 | 8.4952 | 7.7034 | 6.6523 | 5.8757 | 5.367 | 8.9641 | 8.7549 | 8.5262 | 8.2224 | 7.9039 | 7.5684 | 7.1729 | 6.731 | 6.0591 | 4.707 | 2.662 | 1.4251 | 0.93669
|  | CRICKLADE | ST |  |  | 7.655 | 7.4636 | 7.2575 | 6.9488 | 6.6274 | 6.2981 | 5.9211 | 5.5096 | 4.8678 | 3.4151 | 0.97172 | -0.58003 | -1.1984 | 10.1265 | 10.0109 | 9.8841 | 9.7212 | 9.5497 | 9.3677 | 9.1541 | 8.9158 | 8.4952 | 7.7034 | 6.6523 | 5.8757 | 5.367 | 8.9641 | 8.7549 | 8.5262 | 8.2224 | 7.9039 | 7.5684 | 7.1729 | 6.731 | 6.0591 | 4.707 | 2.662 | 1.4251 | 0.93669
|  | CRICKLADE | FS |  |  | 7.655 | 7.4636 | 7.2575 | 6.9488 | 6.6274 | 6.2981 | 5.9211 | 5.5096 | 4.8678 | 3.4151 | 0.97172 | -0.58003 | -1.1984 | 10.1265 | 10.0109 | 9.8841 | 9.7212 | 9.5497 | 9.3677 | 9.1541 | 8.9158 | 8.4952 | 7.7034 | 6.6523 | 5.8757 | 5.367 | 8.9641 | 8.7549 | 8.5262 | 8.2224 | 7.9039 | 7.5684 | 7.1729 | 6.731 | 6.0591 | 4.707 | 2.662 | 1.4251 | 0.93669
MELKSHAM GSP | FROME BSP | CROCKERTON | MINIMUM HEADROOM | ST 87736 43371 | YES | 5.4542 | 5.1579 | 4.7718 | 4.1803 | 3.5638 | 2.9197 | 2.2306 | 1.466 | 0.2606 | -3.042 | -8.753 | -12.7369 | -14.2916 | 6.8847 | 6.8072 | 6.6211 | 6.2871 | 5.9267 | 5.537 | 5.1005 | 4.5703 | 3.7981 | 1.8518 | -0.8393 | -2.7809 | -4.2329 | 7.045 | 6.9534 | 6.8259 | 6.6929 | 6.5444 | 6.2614 | 5.6036 | 4.8402 | 3.6599 | 0.58704 | -4.3213 | -7.8195 | -9.1887
|  | CROCKERTON | CT |  |  | 5.4542 | 5.1579 | 4.7718 | 4.1803 | 3.5638 | 2.9197 | 2.2306 | 1.466 | 0.2606 | -3.042 | -8.753 | -12.7369 | -14.2916 | 6.8847 | 6.8072 | 6.6211 | 6.2871 | 5.9267 | 5.537 | 5.1005 | 4.5703 | 3.7981 | 1.8518 | -0.8393 | -2.7809 | -4.2329 | 7.045 | 6.9534 | 6.8259 | 6.6929 | 6.5444 | 6.2614 | 5.6036 | 4.8402 | 3.6599 | 0.58704 | -4.3213 | -7.8195 | -9.1887
|  | CROCKERTON | LW |  |  | 5.4542 | 5.1579 | 4.7718 | 4.1803 | 3.5638 | 2.9197 | 2.2306 | 1.466 | 0.2606 | -3.042 | -8.753 | -12.7369 | -14.2916 | 6.8847 | 6.8072 | 6.6211 | 6.2871 | 5.9267 | 5.537 | 5.1005 | 4.5703 | 3.7981 | 1.8518 | -0.8393 | -2.7809 | -4.2329 | 7.045 | 6.9534 | 6.8259 | 6.6929 | 6.5444 | 6.2614 | 5.6036 | 4.8402 | 3.6599 | 0.58704 | -4.3213 | -7.8195 | -9.1887
|  | CROCKERTON | ST |  |  | 5.4542 | 5.1579 | 4.7718 | 4.1803 | 3.5638 | 2.9197 | 2.2306 | 1.466 | 0.2606 | -3.042 | -8.753 | -12.7369 | -14.2916 | 6.8847 | 6.8072 | 6.6211 | 6.2871 | 5.9267 | 5.537 | 5.1005 | 4.5703 | 3.7981 | 1.8518 | -0.8393 | -2.7809 | -4.2329 | 7.045 | 6.9534 | 6.8259 | 6.6929 | 6.5444 | 6.2614 | 5.6036 | 4.8402 | 3.6599 | 0.58704 | -4.3213 | -7.8195 | -9.1887
|  | CROCKERTON | FS |  |  | 5.4542 | 5.1579 | 4.7718 | 4.1803 | 3.5638 | 2.9197 | 2.2306 | 1.466 | 0.2606 | -3.042 | -8.753 | -12.7369 | -14.2916 | 6.8847 | 6.8072 | 6.6211 | 6.2871 | 5.9267 | 5.537 | 5.1005 | 4.5703 | 3.7981 | 1.8518 | -0.8393 | -2.7809 | -4.2329 | 7.045 | 6.9534 | 6.8259 | 6.6929 | 6.5444 | 6.2614 | 5.6036 | 4.8402 | 3.6599 | 0.58704 | -4.3213 | -7.8195 | -9.1887
BRAMLEY (FLEE) | PYESTOCK BSP | CROOKHAM | MINIMUM HEADROOM | SU 81702 53403 | YES | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88
|  | CROOKHAM | CT |  |  | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88
|  | CROOKHAM | LW |  |  | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88
|  | CROOKHAM | ST |  |  | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88
|  | CROOKHAM | FS |  |  | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88 | 35.88
BRAMLEY (FLEE) | CAMBERLEY MAIN | CROWTHORNE | MINIMUM HEADROOM | SU 84470 64352 | YES | 13.2048 | 11.7597 | 10.3664 | 8.89 | 7.2615 | 5.4774 | 3.6673 | 1.7537 | -0.70923 | -5.7642 | -13.296 | -18.1435 | -20.3952 | 16.4763 | 15.4076 | 14.4451 | 13.4856 | 12.4406 | 11.2887 | 10.071 | 8.7414 | 7.1143 | 4.0919 | -0.31224 | -3.3847 | -6.0761 | 16.5341 | 15.1831 | 13.926 | 12.5885 | 11.1231 | 9.5211 | 7.8638 | 6.0881 | 3.789 | -0.7734 | -7.521 | -11.683 | -13.5373
|  | CROWTHORNE | CT |  |  | 13.2048 | 11.7597 | 10.3664 | 8.89 | 7.2615 | 5.4774 | 3.6673 | 1.7537 | -0.70923 | -5.7642 | -13.296 | -18.1435 | -20.3952 | 16.4763 | 15.4076 | 14.4451 | 13.4856 | 12.4406 | 11.2887 | 10.071 | 8.7414 | 7.1143 | 4.0919 | -0.31224 | -3.3847 | -6.0761 | 16.5341 | 15.1831 | 13.926 | 12.5885 | 11.1231 | 9.5211 | 7.8638 | 6.0881 | 3.789 | -0.7734 | -7.521 | -11.683 | -13.5373
|  | CROWTHORNE | LW |  |  | 13.2048 | 11.7597 | 10.3664 | 8.89 | 7.2615 | 5.4774 | 3.6673 | 1.7537 | -0.70923 | -5.7642 | -13.296 | -18.1435 | -20.3952 | 16.4763 | 15.4076 | 14.4451 | 13.4856 | 12.4406 | 11.2887 | 10.071 | 8.7414 | 7.1143 | 4.0919 | -0.31224 | -3.3847 | -6.0761 | 16.5341 | 15.1831 | 13.926 | 12.5885 | 11.1231 | 9.5211 | 7.8638 | 6.0881 | 3.789 | -0.7734 | -7.521 | -11.683 | -13.5373
|  | CROWTHORNE | ST |  |  | 13.2048 | 11.7597 | 10.3664 | 8.89 | 7.2615 | 5.4774 | 3.6673 | 1.7537 | -0.70923 | -5.7642 | -13.296 | -18.1435 | -20.3952 | 16.4763 | 15.4076 | 14.4451 | 13.4856 | 12.4406 | 11.2887 | 10.071 | 8.7414 | 7.1143 | 4.0919 | -0.31224 | -3.3847 | -6.0761 | 16.5341 | 15.1831 | 13.926 | 12.5885 | 11.1231 | 9.5211 | 7.8638 | 6.0881 | 3.789 | -0.7734 | -7.521 | -11.683 | -13.5373
|  | CROWTHORNE | FS |  |  | 13.2048 | 11.7597 | 10.3664 | 8.89 | 7.2615 | 5.4774 | 3.6673 | 1.7537 | -0.70923 | -5.7642 | -13.296 | -18.1435 | -20.3952 | 16.4763 | 15.4076 | 14.4451 | 13.4856 | 12.4406 | 11.2887 | 10.071 | 8.7414 | 7.1143 | 4.0919 | -0.31224 | -3.3847 | -6.0761 | 16.5341 | 15.1831 | 13.926 | 12.5885 | 11.1231 | 9.5211 | 7.8638 | 6.0881 | 3.789 | -0.7734 | -7.521 | -11.683 | -13.5373
COWLEY GSP |  | CULHAM | MINIMUM HEADROOM |  |  | -1.6241 | -1.743 | -1.8353 | -1.9782 | -2.143 | -2.3053 | -2.4721 | -2.649 | -2.9097 | -3.766 | -5.6776 | -7.3892 | -8.607 | 0.31385 | 0.21035 | 0.11285 | -0.013511 | -0.15648 | -0.30948 | -0.47396 | -0.65705 | -0.87409 | -1.6208 | -3.3974 | -5.7125 | -9.0827 | -1.0522 | -1.1534 | -1.2367 | -1.3642 | -1.5104 | -1.6552 | -1.8051 | -1.9658 | -2.2029 | -2.9776 | -4.6357 | -6.0275 | -7.0088
|  | CULHAM | CT |  |  | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
|  | CULHAM | LW |  |  | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
|  | CULHAM | ST |  |  | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
|  | CULHAM | FS |  |  | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
EALING GSP | EALING 22kV | DEAN GARDENS | MINIMUM HEADROOM | TQ 16546 80368 | YES | -1.6241 | -1.743 | -1.8353 | -1.9782 | -2.143 | -2.3053 | -2.4721 | -2.649 | -2.9097 | -3.766 | -5.6776 | -7.3892 | -8.607 | 0.31385 | 0.21035 | 0.11285 | -0.013511 | -0.15648 | -0.30948 | -0.47396 | -0.65705 | -0.87409 | -1.6208 | -3.3974 | -5.7125 | -9.0827 | -1.0522 | -1.1534 | -1.2367 | -1.3642 | -1.5104 | -1.6552 | -1.8051 | -1.9658 | -2.2029 | -2.9776 | -4.6357 | -6.0275 | -7.0088
|  | DEAN GARDENS | CT |  |  | -1.6241 | -1.743 | -1.8353 | -1.9782 | -2.143 | -2.3053 | -2.4721 | -2.649 | -2.9097 | -3.766 | -5.6776 | -7.3892 | -8.607 | 0.31385 | 0.21035 | 0.11285 | -0.013511 | -0.15648 | -0.30948 | -0.47396 | -0.65705 | -0.87409 | -1.6208 | -3.3974 | -5.7125 | -9.0827 | -1.0522 | -1.1534 | -1.2367 | -1.3642 | -1.5104 | -1.6552 | -1.8051 | -1.9658 | -2.2029 | -2.9776 | -4.6357 | -6.0275 | -7.0088
|  | DEAN GARDENS | LW |  |  | -1.6241 | -1.743 | -1.8353 | -1.9782 | -2.143 | -2.3053 | -2.4721 | -2.649 | -2.9097 | -3.766 | -5.6776 | -7.3892 | -8.607 | 0.31385 | 0.21035 | 0.11285 | -0.013511 | -0.15648 | -0.30948 | -0.47396 | -0.65705 | -0.87409 | -1.6208 | -3.3974 | -5.7125 | -9.0827 | -1.0522 | -1.1534 | -1.2367 | -1.3642 | -1.5104 | -1.6552 | -1.8051 | -1.9658 | -2.2029 | -2.9776 | -4.6357 | -6.0275 | -7.0088
|  | DEAN GARDENS | ST |  |  | -1.6241 | -1.743 | -1.8353 | -1.9782 | -2.143 | -2.3053 | -2.4721 | -2.649 | -2.9097 | -3.766 | -5.6776 | -7.3892 | -8.607 | 0.31385 | 0.21035 | 0.11285 | -0.013511 | -0.15648 | -0.30948 | -0.47396 | -0.65705 | -0.87409 | -1.6208 | -3.3974 | -5.7125 | -9.0827 | -1.0522 | -1.1534 | -1.2367 | -1.3642 | -1.5104 | -1.6552 | -1.8051 | -1.9658 | -2.2029 | -2.9776 | -4.6357 | -6.0275 | -7.0088
|  | DEAN GARDENS | FS |  |  | -1.6241 | -1.743 | -1.8353 | -1.9782 | -2.143 | -2.3053 | -2.4721 | -2.649 | -2.9097 | -3.766 | -5.6776 | -7.3892 | -8.607 | 0.31385 | 0.21035 | 0.11285 | -0.013511 | -0.15648 | -0.30948 | -0.47396 | -0.65705 | -0.87409 | -1.6208 | -3.3974 | -5.7125 | -9.0827 | -1.0522 | -1.1534 | -1.2367 | -1.3642 | -1.5104 | -1.6552 | -1.8051 | -1.9658 | -2.2029 | -2.9776 | -4.6357 | -6.0275 | -7.0088
COWLEY GSP | YARNTON BSP | DEDDINGTON | MINIMUM HEADROOM | SP 46729 30325 | NO | -0.79729 | -0.90288 | -1.0179 | -1.1661 | -1.3228 | -1.496 | -1.7095 | -1.9576 | -2.2837 | -2.8631 | -3.7217 | -4.1713 | -4.3321 | 1.3712 | 1.2905 | 1.2005 | 1.1008 | 0.99531 | 0.87986 | 0.73233 | 0.55504 | 0.3303 | -0.012403 | -0.47128 | -0.76407 | -1.0253 | -0.048745 | -0.14928 | -0.25917 | -0.40091 | -0.5525 | -0.71646 | -0.92004 | -1.1581 | -1.4702 | -2.0079 | -2.7833 | -3.1722 | -3.3076
|  | DEDDINGTON | CT |  |  | -0.79729 | -0.90288 | -1.0179 | -1.1661 | -1.3228 | -1.496 | -1.7095 | -1.9576 | -2.2837 | -2.8631 | -3.7217 | -4.1713 | -4.3321 | 1.3712 | 1.2905 | 1.2005 | 1.1008 | 0.99531 | 0.87986 | 0.73233 | 0.55504 | 0.3303 | -0.012403 | -0.47128 | -0.76407 | -1.0253 | -0.048745 | -0.14928 | -0.25917 | -0.40091 | -0.5525 | -0.71646 | -0.92004 | -1.1581 | -1.4702 | -2.0079 | -2.7833 | -3.1722 | -3.3076
|  | DEDDINGTON | LW |  |  | -0.79729 | -0.90288 | -1.0179 | -1.1661 | -1.3228 | -1.496 | -1.7095 | -1.9576 | -2.2837 | -2.8631 | -3.7217 | -4.1713 | -4.3321 | 1.3712 | 1.2905 | 1.2005 | 1.1008 | 0.99531 | 0.87986 | 0.73233 | 0.55504 | 0.3303 | -0.012403 | -0.47128 | -0.76407 | -1.0253 | -0.048745 | -0.14928 | -0.25917 | -0.40091 | -0.5525 | -0.71646 | -0.92004 | -1.1581 | -1.4702 | -2.0079 | -2.7833 | -3.1722 | -3.3076
|  | DEDDINGTON | ST |  |  | -0.79729 | -0.90288 | -1.0179 | -1.1661 | -1.3228 | -1.496 | -1.7095 | -1.9576 | -2.2837 | -2.8631 | -3.7217 | -4.1713 | -4.3321 | 1.3712 | 1.2905 | 1.2005 | 1.1008 | 0.99531 | 0.87986 | 0.73233 | 0.55504 | 0.3303 | -0.012403 | -0.47128 | -0.76407 | -1.0253 | -0.048745 | -0.14928 | -0.25917 | -0.40091 | -0.5525 | -0.71646 | -0.92004 | -1.1581 | -1.4702 | -2.0079 | -2.7833 | -3.1722 | -3.3076
|  | DEDDINGTON | FS |  |  | -0.79729 | -0.90288 | -1.0179 | -1.1661 | -1.3228 | -1.496 | -1.7095 | -1.9576 | -2.2837 | -2.8631 | -3.7217 | -4.1713 | -4.3321 | 1.3712 | 1.2905 | 1.2005 | 1.1008 | 0.99531 | 0.87986 | 0.73233 | 0.55504 | 0.3303 | -0.012403 | -0.47128 | -0.76407 | -1.0253 | -0.048745 | -0.14928 | -0.25917 | -0.40091 | -0.5525 | -0.71646 | -0.92004 | -1.1581 | -1.4702 | -2.0079 | -2.7833 | -3.1722 | -3.3076
IVER 132KV | DENHAM | DENHAM AVENUE | MINIMUM HEADROOM | TQ 03761 86587 | YES | 3.0785 | 2.9667 | 2.8111 | 2.6098 | 2.3696 | 2.1118 | 1.8219 | 1.485 | 0.98063 | -0.24731 | -1.9747 | -3.0168 | -3.5014 | 5.0343 | 4.9775 | 4.9032 | 4.8028 | 4.684 | 4.5487 | 4.3562 | 4.1157 | 3.7775 | 2.9999 | 1.9914 | 1.3604 | 0.83494 | 4.131 | 4.0235 | 3.8724 | 3.6811 | 3.4561 | 3.2138 | 2.9403 | 2.6204 | 2.144 | 1.0066 | -0.55532 | -1.4691 | -1.8865
|  | DENHAM AVENUE | CT |  |  | 3.0785 | 2.9667 | 2.8111 | 2.6098 | 2.3696 | 2.1118 | 1.8219 | 1.485 | 0.98063 | -0.24731 | -1.9747 | -3.0168 | -3.5014 | 5.0343 | 4.9775 | 4.9032 | 4.8028 | 4.684 | 4.5487 | 4.3562 | 4.1157 | 3.7775 | 2.9999 | 1.9914 | 1.3604 | 0.83494 | 4.131 | 4.0235 | 3.8724 | 3.6811 | 3.4561 | 3.2138 | 2.9403 | 2.6204 | 2.144 | 1.0066 | -0.55532 | -1.4691 | -1.8865
|  | DENHAM AVENUE | LW |  |  | 3.0785 | 2.9667 | 2.8111 | 2.6098 | 2.3696 | 2.1118 | 1.8219 | 1.485 | 0.98063 | -0.24731 | -1.9747 | -3.0168 | -3.5014 | 5.0343 | 4.9775 | 4.9032 | 4.8028 | 4.684 | 4.5487 | 4.3562 | 4.1157 | 3.7775 | 2.9999 | 1.9914 | 1.3604 | 0.83494 | 4.131 | 4.0235 | 3.8724 | 3.6811 | 3.4561 | 3.2138 | 2.9403 | 2.6204 | 2.144 | 1.0066 | -0.55532 | -1.4691 | -1.8865
|  | DENHAM AVENUE | ST |  |  | 3.0785 | 2.9667 | 2.8111 | 2.6098 | 2.3696 | 2.1118 | 1.8219 | 1.485 | 0.98063 | -0.24731 | -1.9747 | -3.0168 | -3.5014 | 5.0343 | 4.9775 | 4.9032 | 4.8028 | 4.684 | 4.5487 | 4.3562 | 4.1157 | 3.7775 | 2.9999 | 1.9914 | 1.3604 | 0.83494 | 4.131 | 4.0235 | 3.8724 | 3.6811 | 3.4561 | 3.2138 | 2.9403 | 2.6204 | 2.144 | 1.0066 | -0.55532 | -1.4691 | -1.8865
|  | DENHAM AVENUE | FS |  |  | 3.0785 | 2.9667 | 2.8111 | 2.6098 | 2.3696 | 2.1118 | 1.8219 | 1.485 | 0.98063 | -0.24731 | -1.9747 | -3.0168 | -3.5014 | 5.0343 | 4.9775 | 4.9032 | 4.8028 | 4.684 | 4.5487 | 4.3562 | 4.1157 | 3.7775 | 2.9999 | 1.9914 | 1.3604 | 0.83494 | 4.131 | 4.0235 | 3.8724 | 3.6811 | 3.4561 | 3.2138 | 2.9403 | 2.6204 | 2.144 | 1.0066 | -0.55532 | -1.4691 | -1.8865
MELKSHAM GSP | NORRINGTON | DEVIZES | MINIMUM HEADROOM | SU 00106 60986 | YES | 2.6825 | 2.2244 | 1.681 | 0.87391 | 0.041936 | -0.83857 | -1.777 | -2.8129 | -4.4814 | -9.0567 | -16.5041 | -21.785 | -24.0485 | 10.1589 | 9.8102 | 9.3559 | 8.8295 | 8.2782 | 7.6773 | 7.0227 | 6.2542 | 5.1257 | 2.2917 | -1.4677 | -4.3444 | -6.7967 | 4.0222 | 3.5944 | 3.079 | 2.3349 | 1.5667 | 0.75083 | -0.12081 | -1.0899 | -2.6388 | -6.8619 | -13.5044 | -18.166 | -20.1619
|  | DEVIZES | CT |  |  | 2.6825 | 2.2244 | 1.681 | 0.87391 | 0.041936 | -0.83857 | -1.777 | -2.8129 | -4.4814 | -9.0567 | -16.5041 | -21.785 | -24.0485 | 10.1589 | 9.8102 | 9.3559 | 8.8295 | 8.2782 | 7.6773 | 7.0227 | 6.2542 | 5.1257 | 2.2917 | -1.4677 | -4.3444 | -6.7967 | 4.0222 | 3.5944 | 3.079 | 2.3349 | 1.5667 | 0.75083 | -0.12081 | -1.0899 | -2.6388 | -6.8619 | -13.5044 | -18.166 | -20.1619
|  | DEVIZES | LW |  |  | 2.6825 | 2.2244 | 1.681 | 0.87391 | 0.041936 | -0.83857 | -1.777 | -2.8129 | -4.4814 | -9.0567 | -16.5041 | -21.785 | -24.0485 | 10.1589 | 9.8102 | 9.3559 | 8.8295 | 8.2782 | 7.6773 | 7.0227 | 6.2542 | 5.1257 | 2.2917 | -1.4677 | -4.3444 | -6.7967 | 4.0222 | 3.5944 | 3.079 | 2.3349 | 1.5667 | 0.75083 | -0.12081 | -1.0899 | -2.6388 | -6.8619 | -13.5044 | -18.166 | -20.1619
|  | DEVIZES | ST |  |  | 2.6825 | 2.2244 | 1.681 | 0.87391 | 0.041936 | -0.83857 | -1.777 | -2.8129 | -4.4814 | -9.0567 | -16.5041 | -21.785 | -24.0485 | 10.1589 | 9.8102 | 9.3559 | 8.8295 | 8.2782 | 7.6773 | 7.0227 | 6.2542 | 5.1257 | 2.2917 | -1.4677 | -4.3444 | -6.7967 | 4.0222 | 3.5944 | 3.079 | 2.3349 | 1.5667 | 0.75083 | -0.12081 | -1.0899 | -2.6388 | -6.8619 | -13.5044 | -18.166 | -20.1619
|  | DEVIZES | FS |  |  | 2.6825 | 2.2244 | 1.681 | 0.87391 | 0.041936 | -0.83857 | -1.777 | -2.8129 | -4.4814 | -9.0567 | -16.5041 | -21.785 | -24.0485 | 10.1589 | 9.8102 | 9.3559 | 8.8295 | 8.2782 | 7.6773 | 7.0227 | 6.2542 | 5.1257 | 2.2917 | -1.4677 | -4.3444 | -6.7967 | 4.0222 | 3.5944 | 3.079 | 2.3349 | 1.5667 | 0.75083 | -0.12081 | -1.0899 | -2.6388 | -6.8619 | -13.5044 | -18.166 | -20.1619
MINETY GSP | TOOTHILL BSP | DORCAN SOUTH | MINIMUM HEADROOM | SU 19288 83540 | YES | 11.629 | 11.5785 | 11.5159 | 11.4379 | 11.3518 | 11.2589 | 11.1573 | 11.052 | 10.8901 | 10.376 | 9.3721 | 8.6102 | 8.1281 | 14.1728 | 14.1332 | 14.0721 | 14.0006 | 13.921 | 13.8364 | 13.7438 | 13.6411 | 13.4771 | 12.9751 | 12.1553 | 11.4245 | 10.7279 | 13.2946 | 13.2377 | 13.1438 | 13.0338 | 12.911 | 12.7811 | 12.6393 | 12.4808 | 12.2252 | 11.5155 | 10.292 | 9.2903 | 8.6243
|  | DORCAN SOUTH | CT |  |  | 11.629 | 11.5785 | 11.5159 | 11.4379 | 11.3518 | 11.2589 | 11.1573 | 11.052 | 10.8901 | 10.376 | 9.3721 | 8.6102 | 8.1281 | 14.1728 | 14.1332 | 14.0721 | 14.0006 | 13.921 | 13.8364 | 13.7438 | 13.6411 | 13.4771 | 12.9751 | 12.1553 | 11.4245 | 10.7279 | 13.2946 | 13.2377 | 13.1438 | 13.0338 | 12.911 | 12.7811 | 12.6393 | 12.4808 | 12.2252 | 11.5155 | 10.292 | 9.2903 | 8.6243
|  | DORCAN SOUTH | LW |  |  | 11.629 | 11.5785 | 11.5159 | 11.4379 | 11.3518 | 11.2589 | 11.1573 | 11.052 | 10.8901 | 10.376 | 9.3721 | 8.6102 | 8.1281 | 14.1728 | 14.1332 | 14.0721 | 14.0006 | 13.921 | 13.8364 | 13.7438 | 13.6411 | 13.4771 | 12.9751 | 12.1553 | 11.4245 | 10.7279 | 13.2946 | 13.2377 | 13.1438 | 13.0338 | 12.911 | 12.7811 | 12.6393 | 12.4808 | 12.2252 | 11.5155 | 10.292 | 9.2903 | 8.6243
|  | DORCAN SOUTH | ST |  |  | 11.629 | 11.5785 | 11.5159 | 11.4379 | 11.3518 | 11.2589 | 11.1573 | 11.052 | 10.8901 | 10.376 | 9.3721 | 8.6102 | 8.1281 | 14.1728 | 14.1332 | 14.0721 | 14.0006 | 13.921 | 13.8364 | 13.7438 | 13.6411 | 13.4771 | 12.9751 | 12.1553 | 11.4245 | 10.7279 | 13.2946 | 13.2377 | 13.1438 | 13.0338 | 12.911 | 12.7811 | 12.6393 | 12.4808 | 12.2252 | 11.5155 | 10.292 | 9.2903 | 8.6243
|  | DORCAN SOUTH | FS |  |  | 11.629 | 11.5785 | 11.5159 | 11.4379 | 11.3518 | 11.2589 | 11.1573 | 11.052 | 10.8901 | 10.376 | 9.3721 | 8.6102 | 8.1281 | 14.1728 | 14.1332 | 14.0721 | 14.0006 | 13.921 | 13.8364 | 13.7438 | 13.6411 | 13.4771 | 12.9751 | 12.1553 | 11.4245 | 10.7279 | 13.2946 | 13.2377 | 13.1438 | 13.0338 | 12.911 | 12.7811 | 12.6393 | 12.4808 | 12.2252 | 11.5155 | 10.292 | 9.2903 | 8.6243
CHICKERELL GSP | CHICKERELL BSP | DORCHESTER | MINIMUM HEADROOM | SY 69113 90401 | YES | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
|  | DORCHESTER | CT |  |  | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
|  | DORCHESTER | LW |  |  | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
|  | DORCHESTER | ST |  |  | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
|  | DORCHESTER | FS |  |  | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | DOWN GRANGE | MINIMUM HEADROOM | SU 61604 50238 | YES | 23.2064 | 22.4775 | 21.6178 | 20.5316 | 19.3745 | 18.1716 | 16.7291 | 15.0146 | 12.4431 | 6.6535 | -1.8888 | -8.0202 | -11.1505 | 20.0645 | 19.4518 | 18.7367 | 17.9644 | 17.1377 | 16.2531 | 15.2322 | 13.9959 | 12.2827 | 8.5862 | 3.5136 | -0.46414 | -4.2663 | 24.151 | 23.4494 | 22.6368 | 21.6307 | 20.5599 | 19.3933 | 18.0353 | 16.4133 | 14.0004 | 8.6428 | 0.97308 | -4.2109 | -6.8689
|  | DOWN GRANGE | CT |  |  | 23.2064 | 22.4775 | 21.6178 | 20.5316 | 19.3745 | 18.1716 | 16.7291 | 15.0146 | 12.4431 | 6.6535 | -1.8888 | -8.0202 | -11.1505 | 20.0645 | 19.4518 | 18.7367 | 17.9644 | 17.1377 | 16.2531 | 15.2322 | 13.9959 | 12.2827 | 8.5862 | 3.5136 | -0.46414 | -4.2663 | 24.151 | 23.4494 | 22.6368 | 21.6307 | 20.5599 | 19.3933 | 18.0353 | 16.4133 | 14.0004 | 8.6428 | 0.97308 | -4.2109 | -6.8689
|  | DOWN GRANGE | LW |  |  | 23.2064 | 22.4775 | 21.6178 | 20.5316 | 19.3745 | 18.1716 | 16.7291 | 15.0146 | 12.4431 | 6.6535 | -1.8888 | -8.0202 | -11.1505 | 20.0645 | 19.4518 | 18.7367 | 17.9644 | 17.1377 | 16.2531 | 15.2322 | 13.9959 | 12.2827 | 8.5862 | 3.5136 | -0.46414 | -4.2663 | 24.151 | 23.4494 | 22.6368 | 21.6307 | 20.5599 | 19.3933 | 18.0353 | 16.4133 | 14.0004 | 8.6428 | 0.97308 | -4.2109 | -6.8689
|  | DOWN GRANGE | ST |  |  | 23.2064 | 22.4775 | 21.6178 | 20.5316 | 19.3745 | 18.1716 | 16.7291 | 15.0146 | 12.4431 | 6.6535 | -1.8888 | -8.0202 | -11.1505 | 20.0645 | 19.4518 | 18.7367 | 17.9644 | 17.1377 | 16.2531 | 15.2322 | 13.9959 | 12.2827 | 8.5862 | 3.5136 | -0.46414 | -4.2663 | 24.151 | 23.4494 | 22.6368 | 21.6307 | 20.5599 | 19.3933 | 18.0353 | 16.4133 | 14.0004 | 8.6428 | 0.97308 | -4.2109 | -6.8689
|  | DOWN GRANGE | FS |  |  | 23.2064 | 22.4775 | 21.6178 | 20.5316 | 19.3745 | 18.1716 | 16.7291 | 15.0146 | 12.4431 | 6.6535 | -1.8888 | -8.0202 | -11.1505 | 20.0645 | 19.4518 | 18.7367 | 17.9644 | 17.1377 | 16.2531 | 15.2322 | 13.9959 | 12.2827 | 8.5862 | 3.5136 | -0.46414 | -4.2663 | 24.151 | 23.4494 | 22.6368 | 21.6307 | 20.5599 | 19.3933 | 18.0353 | 16.4133 | 14.0004 | 8.6428 | 0.97308 | -4.2109 | -6.8689
MINETY GSP | STRATTON (2 X 90) | DRAKES WAY | MINIMUM HEADROOM | SU 16899 85647 | YES | 11.9564 | 11.8475 | 11.7127 | 11.5674 | 11.4052 | 11.2261 | 11.0312 | 10.7567 | 10.3962 | 8.7244 | 5.9518 | 4.7007 | 3.6324 | 13.2082 | 13.1236 | 13.0199 | 12.9075 | 12.7819 | 12.6363 | 12.4248 | 12.1414 | 11.8165 | 10.5787 | 8.5219 | 7.8774 | 6.9939 | 13.0548 | 12.8909 | 12.693 | 12.4741 | 12.2294 | 11.9581 | 11.6624 | 11.2696 | 10.8128 | 9.2056 | 6.6017 | 5.783 | 5.3135
|  | DRAKES WAY | CT |  |  | 11.9564 | 11.8475 | 11.7127 | 11.5674 | 11.4052 | 11.2261 | 11.0312 | 10.7567 | 10.3962 | 8.7244 | 5.9518 | 4.7007 | 3.6324 | 13.2082 | 13.1236 | 13.0199 | 12.9075 | 12.7819 | 12.6363 | 12.4248 | 12.1414 | 11.8165 | 10.5787 | 8.5219 | 7.8774 | 6.9939 | 13.0548 | 12.8909 | 12.693 | 12.4741 | 12.2294 | 11.9581 | 11.6624 | 11.2696 | 10.8128 | 9.2056 | 6.6017 | 5.783 | 5.3135
|  | DRAKES WAY | LW |  |  | 11.9564 | 11.8475 | 11.7127 | 11.5674 | 11.4052 | 11.2261 | 11.0312 | 10.7567 | 10.3962 | 8.7244 | 5.9518 | 4.7007 | 3.6324 | 13.2082 | 13.1236 | 13.0199 | 12.9075 | 12.7819 | 12.6363 | 12.4248 | 12.1414 | 11.8165 | 10.5787 | 8.5219 | 7.8774 | 6.9939 | 13.0548 | 12.8909 | 12.693 | 12.4741 | 12.2294 | 11.9581 | 11.6624 | 11.2696 | 10.8128 | 9.2056 | 6.6017 | 5.783 | 5.3135
|  | DRAKES WAY | ST |  |  | 11.9564 | 11.8475 | 11.7127 | 11.5674 | 11.4052 | 11.2261 | 11.0312 | 10.7567 | 10.3962 | 8.7244 | 5.9518 | 4.7007 | 3.6324 | 13.2082 | 13.1236 | 13.0199 | 12.9075 | 12.7819 | 12.6363 | 12.4248 | 12.1414 | 11.8165 | 10.5787 | 8.5219 | 7.8774 | 6.9939 | 13.0548 | 12.8909 | 12.693 | 12.4741 | 12.2294 | 11.9581 | 11.6624 | 11.2696 | 10.8128 | 9.2056 | 6.6017 | 5.783 | 5.3135
|  | DRAKES WAY | FS |  |  | 11.9564 | 11.8475 | 11.7127 | 11.5674 | 11.4052 | 11.2261 | 11.0312 | 10.7567 | 10.3962 | 8.7244 | 5.9518 | 4.7007 | 3.6324 | 13.2082 | 13.1236 | 13.0199 | 12.9075 | 12.7819 | 12.6363 | 12.4248 | 12.1414 | 11.8165 | 10.5787 | 8.5219 | 7.8774 | 6.9939 | 13.0548 | 12.8909 | 12.693 | 12.4741 | 12.2294 | 11.9581 | 11.6624 | 11.2696 | 10.8128 | 9.2056 | 6.6017 | 5.783 | 5.3135
NURSLING GSP | WINCHESTER | DUNBRIDGE | MINIMUM HEADROOM | SU 31520 26244 | YES | 1.8044 | 1.5588 | 1.3092 | 0.97043 | 0.62236 | 0.24289 | -0.2142 | -0.67702 | -1.295 | -2.3987 | -4.4292 | -5.7443 | -6.3085 | 4.2071 | 4.0232 | 3.8354 | 3.6251 | 3.4067 | 3.1572 | 2.8386 | 2.5175 | 2.1218 | 1.5597 | 0.59246 | -0.06683 | -0.53548 | 1.9365 | 1.718 | 1.4969 | 1.1926 | 0.88056 | 0.54172 | 0.13658 | -0.27009 | -0.80026 | -1.8385 | -3.7141 | -4.924 | -5.4426
|  | DUNBRIDGE | CT |  |  | 1.8044 | 1.5588 | 1.3092 | 0.97043 | 0.62236 | 0.24289 | -0.2142 | -0.67702 | -1.295 | -2.3987 | -4.4292 | -5.7443 | -6.3085 | 4.2071 | 4.0232 | 3.8354 | 3.6251 | 3.4067 | 3.1572 | 2.8386 | 2.5175 | 2.1218 | 1.5597 | 0.59246 | -0.06683 | -0.53548 | 1.9365 | 1.718 | 1.4969 | 1.1926 | 0.88056 | 0.54172 | 0.13658 | -0.27009 | -0.80026 | -1.8385 | -3.7141 | -4.924 | -5.4426
|  | DUNBRIDGE | LW |  |  | 1.8044 | 1.5588 | 1.3092 | 0.97043 | 0.62236 | 0.24289 | -0.2142 | -0.67702 | -1.295 | -2.3987 | -4.4292 | -5.7443 | -6.3085 | 4.2071 | 4.0232 | 3.8354 | 3.6251 | 3.4067 | 3.1572 | 2.8386 | 2.5175 | 2.1218 | 1.5597 | 0.59246 | -0.06683 | -0.53548 | 1.9365 | 1.718 | 1.4969 | 1.1926 | 0.88056 | 0.54172 | 0.13658 | -0.27009 | -0.80026 | -1.8385 | -3.7141 | -4.924 | -5.4426
|  | DUNBRIDGE | ST |  |  | 1.8044 | 1.5588 | 1.3092 | 0.97043 | 0.62236 | 0.24289 | -0.2142 | -0.67702 | -1.295 | -2.3987 | -4.4292 | -5.7443 | -6.3085 | 4.2071 | 4.0232 | 3.8354 | 3.6251 | 3.4067 | 3.1572 | 2.8386 | 2.5175 | 2.1218 | 1.5597 | 0.59246 | -0.06683 | -0.53548 | 1.9365 | 1.718 | 1.4969 | 1.1926 | 0.88056 | 0.54172 | 0.13658 | -0.27009 | -0.80026 | -1.8385 | -3.7141 | -4.924 | -5.4426
|  | DUNBRIDGE | FS |  |  | 1.8044 | 1.5588 | 1.3092 | 0.97043 | 0.62236 | 0.24289 | -0.2142 | -0.67702 | -1.295 | -2.3987 | -4.4292 | -5.7443 | -6.3085 | 4.2071 | 4.0232 | 3.8354 | 3.6251 | 3.4067 | 3.1572 | 2.8386 | 2.5175 | 2.1218 | 1.5597 | 0.59246 | -0.06683 | -0.53548 | 1.9365 | 1.718 | 1.4969 | 1.1926 | 0.88056 | 0.54172 | 0.13658 | -0.27009 | -0.80026 | -1.8385 | -3.7141 | -4.924 | -5.4426
EALING GSP | EALING 22kV | EALING 11kV | MINIMUM HEADROOM | SZ 06789 95116 | YES | 17.9424 | 16.9931 | 16.0499 | 14.8701 | 13.576 | 12.3477 | 11.0277 | 9.7947 | 8.0329 | 2.6269 | -7.0405 | -14.0139 | -18.1057 | 22.925 | 22.5935 | 22.1497 | 21.3547 | 20.4414 | 19.4664 | 18.4078 | 17.3349 | 16.0186 | 11.7758 | 3.5685 | -5.2598 | -17.2466 | 19.3979 | 18.5904 | 17.7679 | 16.7546 | 15.613 | 14.5158 | 13.3354 | 12.207 | 10.5859 | 5.6027 | -3.0375 | -9.0258 | -12.4638
|  | EALING 11kV | CT |  |  | 17.9424 | 16.9931 | 16.0499 | 14.8701 | 13.576 | 12.3477 | 11.0277 | 9.7947 | 8.0329 | 2.6269 | -7.0405 | -14.0139 | -18.1057 | 22.925 | 22.5935 | 22.1497 | 21.3547 | 20.4414 | 19.4664 | 18.4078 | 17.3349 | 16.0186 | 11.7758 | 3.5685 | -5.2598 | -17.2466 | 19.3979 | 18.5904 | 17.7679 | 16.7546 | 15.613 | 14.5158 | 13.3354 | 12.207 | 10.5859 | 5.6027 | -3.0375 | -9.0258 | -12.4638
|  | EALING 11kV | LW |  |  | 17.9424 | 16.9931 | 16.0499 | 14.8701 | 13.576 | 12.3477 | 11.0277 | 9.7947 | 8.0329 | 2.6269 | -7.0405 | -14.0139 | -18.1057 | 22.925 | 22.5935 | 22.1497 | 21.3547 | 20.4414 | 19.4664 | 18.4078 | 17.3349 | 16.0186 | 11.7758 | 3.5685 | -5.2598 | -17.2466 | 19.3979 | 18.5904 | 17.7679 | 16.7546 | 15.613 | 14.5158 | 13.3354 | 12.207 | 10.5859 | 5.6027 | -3.0375 | -9.0258 | -12.4638
|  | EALING 11kV | ST |  |  | 17.9424 | 16.9931 | 16.0499 | 14.8701 | 13.576 | 12.3477 | 11.0277 | 9.7947 | 8.0329 | 2.6269 | -7.0405 | -14.0139 | -18.1057 | 22.925 | 22.5935 | 22.1497 | 21.3547 | 20.4414 | 19.4664 | 18.4078 | 17.3349 | 16.0186 | 11.7758 | 3.5685 | -5.2598 | -17.2466 | 19.3979 | 18.5904 | 17.7679 | 16.7546 | 15.613 | 14.5158 | 13.3354 | 12.207 | 10.5859 | 5.6027 | -3.0375 | -9.0258 | -12.4638
|  | EALING 11kV | FS |  |  | 17.9424 | 16.9931 | 16.0499 | 14.8701 | 13.576 | 12.3477 | 11.0277 | 9.7947 | 8.0329 | 2.6269 | -7.0405 | -14.0139 | -18.1057 | 22.925 | 22.5935 | 22.1497 | 21.3547 | 20.4414 | 19.4664 | 18.4078 | 17.3349 | 16.0186 | 11.7758 | 3.5685 | -5.2598 | -17.2466 | 19.3979 | 18.5904 | 17.7679 | 16.7546 | 15.613 | 14.5158 | 13.3354 | 12.207 | 10.5859 | 5.6027 | -3.0375 | -9.0258 | -12.4638
MANNINGTON GSP | REDHILL BSP | EAST HOWE | MINIMUM HEADROOM | SZ 06789 95116 | YES | 8.3536 | 7.7806 | 6.9504 | 5.9335 | 4.8483 | 3.6503 | 2.3506 | 0.89042 | -1.3084 | -7.4322 | -17.0191 | -24.2964 | -28.3014 | 11.4575 | 11.0399 | 10.423 | 9.7576 | 9.047 | 8.2604 | 7.4018 | 6.419 | 4.9749 | 0.90752 | -4.4409 | -8.6598 | -12.4614 | 11.1694 | 10.6425 | 9.8619 | 8.9266 | 7.9288 | 6.824 | 5.6236 | 4.2674 | 2.229 | -3.4583 | -12.0305 | -18.3709 | -21.8107
|  | EAST HOWE | CT |  |  | 8.3536 | 7.7806 | 6.9504 | 5.9335 | 4.8483 | 3.6503 | 2.3506 | 0.89042 | -1.3084 | -7.4322 | -17.0191 | -24.2964 | -28.3014 | 11.4575 | 11.0399 | 10.423 | 9.7576 | 9.047 | 8.2604 | 7.4018 | 6.419 | 4.9749 | 0.90752 | -4.4409 | -8.6598 | -12.4614 | 11.1694 | 10.6425 | 9.8619 | 8.9266 | 7.9288 | 6.824 | 5.6236 | 4.2674 | 2.229 | -3.4583 | -12.0305 | -18.3709 | -21.8107
|  | EAST HOWE | LW |  |  | 8.3536 | 7.7806 | 6.9504 | 5.9335 | 4.8483 | 3.6503 | 2.3506 | 0.89042 | -1.3084 | -7.4322 | -17.0191 | -24.2964 | -28.3014 | 11.4575 | 11.0399 | 10.423 | 9.7576 | 9.047 | 8.2604 | 7.4018 | 6.419 | 4.9749 | 0.90752 | -4.4409 | -8.6598 | -12.4614 | 11.1694 | 10.6425 | 9.8619 | 8.9266 | 7.9288 | 6.824 | 5.6236 | 4.2674 | 2.229 | -3.4583 | -12.0305 | -18.3709 | -21.8107
|  | EAST HOWE | ST |  |  | 8.3536 | 7.7806 | 6.9504 | 5.9335 | 4.8483 | 3.6503 | 2.3506 | 0.89042 | -1.3084 | -7.4322 | -17.0191 | -24.2964 | -28.3014 | 11.4575 | 11.0399 | 10.423 | 9.7576 | 9.047 | 8.2604 | 7.4018 | 6.419 | 4.9749 | 0.90752 | -4.4409 | -8.6598 | -12.4614 | 11.1694 | 10.6425 | 9.8619 | 8.9266 | 7.9288 | 6.824 | 5.6236 | 4.2674 | 2.229 | -3.4583 | -12.0305 | -18.3709 | -21.8107
|  | EAST HOWE | FS |  |  | 8.3536 | 7.7806 | 6.9504 | 5.9335 | 4.8483 | 3.6503 | 2.3506 | 0.89042 | -1.3084 | -7.4322 | -17.0191 | -24.2964 | -28.3014 | 11.4575 | 11.0399 | 10.423 | 9.7576 | 9.047 | 8.2604 | 7.4018 | 6.419 | 4.9749 | 0.90752 | -4.4409 | -8.6598 | -12.4614 | 11.1694 | 10.6425 | 9.8619 | 8.9266 | 7.9288 | 6.824 | 5.6236 | 4.2674 | 2.229 | -3.4583 | -12.0305 | -18.3709 | -21.8107
MELKSHAM GSP | NORRINGTON | EASTERTON | MINIMUM HEADROOM | SU 01568 54730 | YES | 10.4444 | 10.2296 | 9.959 | 9.6025 | 9.2283 | 8.8058 | 8.3283 | 7.7753 | 7.0627 | 5.7134 | 3.7932 | 2.5527 | 2.0512 | 11.0579 | 10.9183 | 10.732 | 10.5195 | 10.2934 | 10.0391 | 9.7427 | 9.3841 | 8.9291 | 8.1939 | 7.2828 | 6.6921 | 6.2832 | 10.1611 | 9.9586 | 9.7003 | 9.368 | 9.0185 | 8.6242 | 8.176 | 7.6526 | 6.978 | 5.7402 | 4.047 | 2.9877 | 2.5471
|  | EASTERTON | CT |  |  | 10.4444 | 10.2296 | 9.959 | 9.6025 | 9.2283 | 8.8058 | 8.3283 | 7.7753 | 7.0627 | 5.7134 | 3.7932 | 2.5527 | 2.0512 | 11.0579 | 10.9183 | 10.732 | 10.5195 | 10.2934 | 10.0391 | 9.7427 | 9.3841 | 8.9291 | 8.1939 | 7.2828 | 6.6921 | 6.2832 | 10.1611 | 9.9586 | 9.7003 | 9.368 | 9.0185 | 8.6242 | 8.176 | 7.6526 | 6.978 | 5.7402 | 4.047 | 2.9877 | 2.5471
|  | EASTERTON | LW |  |  | 10.4444 | 10.2296 | 9.959 | 9.6025 | 9.2283 | 8.8058 | 8.3283 | 7.7753 | 7.0627 | 5.7134 | 3.7932 | 2.5527 | 2.0512 | 11.0579 | 10.9183 | 10.732 | 10.5195 | 10.2934 | 10.0391 | 9.7427 | 9.3841 | 8.9291 | 8.1939 | 7.2828 | 6.6921 | 6.2832 | 10.1611 | 9.9586 | 9.7003 | 9.368 | 9.0185 | 8.6242 | 8.176 | 7.6526 | 6.978 | 5.7402 | 4.047 | 2.9877 | 2.5471
|  | EASTERTON | ST |  |  | 10.4444 | 10.2296 | 9.959 | 9.6025 | 9.2283 | 8.8058 | 8.3283 | 7.7753 | 7.0627 | 5.7134 | 3.7932 | 2.5527 | 2.0512 | 11.0579 | 10.9183 | 10.732 | 10.5195 | 10.2934 | 10.0391 | 9.7427 | 9.3841 | 8.9291 | 8.1939 | 7.2828 | 6.6921 | 6.2832 | 10.1611 | 9.9586 | 9.7003 | 9.368 | 9.0185 | 8.6242 | 8.176 | 7.6526 | 6.978 | 5.7402 | 4.047 | 2.9877 | 2.5471
|  | EASTERTON | FS |  |  | 10.4444 | 10.2296 | 9.959 | 9.6025 | 9.2283 | 8.8058 | 8.3283 | 7.7753 | 7.0627 | 5.7134 | 3.7932 | 2.5527 | 2.0512 | 11.0579 | 10.9183 | 10.732 | 10.5195 | 10.2934 | 10.0391 | 9.7427 | 9.3841 | 8.9291 | 8.1939 | 7.2828 | 6.6921 | 6.2832 | 10.1611 | 9.9586 | 9.7003 | 9.368 | 9.0185 | 8.6242 | 8.176 | 7.6526 | 6.978 | 5.7402 | 4.047 | 2.9877 | 2.5471
BRAMLEY (FLEE) | BRACKNELL RESERVE | EASTHAMPSTEAD | MINIMUM HEADROOM | SU 86148 67194 | YES | 18.7735 | 18.3175 | 17.7072 | 16.8907 | 15.9873 | 14.9263 | 13.7659 | 12.4728 | 10.4678 | 5.1143 | -2.8992 | -8.0791 | -10.6187 | 19.1171 | 18.7182 | 18.1717 | 17.5677 | 16.9008 | 16.1235 | 15.2548 | 14.2506 | 12.886 | 9.3184 | 4.3822 | 0.95597 | -2.1411 | 21.189 | 20.7602 | 20.1658 | 19.3953 | 18.5472 | 17.5624 | 16.4787 | 15.1719 | 13.2629 | 8.2198 | 0.90759 | -3.5902 | -5.6564
|  | EASTHAMPSTEAD | CT |  |  | 18.7735 | 18.3175 | 17.7072 | 16.8907 | 15.9873 | 14.9263 | 13.7659 | 12.4728 | 10.4678 | 5.1143 | -2.8992 | -8.0791 | -10.6187 | 19.1171 | 18.7182 | 18.1717 | 17.5677 | 16.9008 | 16.1235 | 15.2548 | 14.2506 | 12.886 | 9.3184 | 4.3822 | 0.95597 | -2.1411 | 21.189 | 20.7602 | 20.1658 | 19.3953 | 18.5472 | 17.5624 | 16.4787 | 15.1719 | 13.2629 | 8.2198 | 0.90759 | -3.5902 | -5.6564
|  | EASTHAMPSTEAD | LW |  |  | 18.7735 | 18.3175 | 17.7072 | 16.8907 | 15.9873 | 14.9263 | 13.7659 | 12.4728 | 10.4678 | 5.1143 | -2.8992 | -8.0791 | -10.6187 | 19.1171 | 18.7182 | 18.1717 | 17.5677 | 16.9008 | 16.1235 | 15.2548 | 14.2506 | 12.886 | 9.3184 | 4.3822 | 0.95597 | -2.1411 | 21.189 | 20.7602 | 20.1658 | 19.3953 | 18.5472 | 17.5624 | 16.4787 | 15.1719 | 13.2629 | 8.2198 | 0.90759 | -3.5902 | -5.6564
|  | EASTHAMPSTEAD | ST |  |  | 18.7735 | 18.3175 | 17.7072 | 16.8907 | 15.9873 | 14.9263 | 13.7659 | 12.4728 | 10.4678 | 5.1143 | -2.8992 | -8.0791 | -10.6187 | 19.1171 | 18.7182 | 18.1717 | 17.5677 | 16.9008 | 16.1235 | 15.2548 | 14.2506 | 12.886 | 9.3184 | 4.3822 | 0.95597 | -2.1411 | 21.189 | 20.7602 | 20.1658 | 19.3953 | 18.5472 | 17.5624 | 16.4787 | 15.1719 | 13.2629 | 8.2198 | 0.90759 | -3.5902 | -5.6564
|  | EASTHAMPSTEAD | FS |  |  | 18.7735 | 18.3175 | 17.7072 | 16.8907 | 15.9873 | 14.9263 | 13.7659 | 12.4728 | 10.4678 | 5.1143 | -2.8992 | -8.0791 | -10.6187 | 19.1171 | 18.7182 | 18.1717 | 17.5677 | 16.9008 | 16.1235 | 15.2548 | 14.2506 | 12.886 | 9.3184 | 4.3822 | 0.95597 | -2.1411 | 21.189 | 20.7602 | 20.1658 | 19.3953 | 18.5472 | 17.5624 | 16.4787 | 15.1719 | 13.2629 | 8.2198 | 0.90759 | -3.5902 | -5.6564
NURSLING GSP | VELMORE BSP | EASTLEIGH NORTH | MINIMUM HEADROOM | SU 45426 18958 | YES | 21.3125 | 20.0105 | 18.7351 | 17.2565 | 15.7806 | 14.2789 | 12.7954 | 11.1329 | 8.6763 | 2.6312 | -6.5099 | -12.5078 | -15.218 | 24.9416 | 23.9277 | 22.9422 | 21.9169 | 20.8892 | 19.8313 | 18.7378 | 17.4385 | 15.6944 | 11.5185 | 5.6903 | 0.8977 | -4.4236 | 21.8151 | 20.6601 | 19.3894 | 17.9805 | 16.5544 | 15.0945 | 13.6584 | 12.0115 | 9.6185 | 3.8759 | -4.1392 | -9.1073 | -11.4038
|  | EASTLEIGH NORTH | CT |  |  | 21.3125 | 20.0105 | 18.7351 | 17.2565 | 15.7806 | 14.2789 | 12.7954 | 11.1329 | 8.6763 | 2.6312 | -6.5099 | -12.5078 | -15.218 | 24.9416 | 23.9277 | 22.9422 | 21.9169 | 20.8892 | 19.8313 | 18.7378 | 17.4385 | 15.6944 | 11.5185 | 5.6903 | 0.8977 | -4.4236 | 21.8151 | 20.6601 | 19.3894 | 17.9805 | 16.5544 | 15.0945 | 13.6584 | 12.0115 | 9.6185 | 3.8759 | -4.1392 | -9.1073 | -11.4038
|  | EASTLEIGH NORTH | LW |  |  | 21.3125 | 20.0105 | 18.7351 | 17.2565 | 15.7806 | 14.2789 | 12.7954 | 11.1329 | 8.6763 | 2.6312 | -6.5099 | -12.5078 | -15.218 | 24.9416 | 23.9277 | 22.9422 | 21.9169 | 20.8892 | 19.8313 | 18.7378 | 17.4385 | 15.6944 | 11.5185 | 5.6903 | 0.8977 | -4.4236 | 21.8151 | 20.6601 | 19.3894 | 17.9805 | 16.5544 | 15.0945 | 13.6584 | 12.0115 | 9.6185 | 3.8759 | -4.1392 | -9.1073 | -11.4038
|  | EASTLEIGH NORTH | ST |  |  | 21.3125 | 20.0105 | 18.7351 | 17.2565 | 15.7806 | 14.2789 | 12.7954 | 11.1329 | 8.6763 | 2.6312 | -6.5099 | -12.5078 | -15.218 | 24.9416 | 23.9277 | 22.9422 | 21.9169 | 20.8892 | 19.8313 | 18.7378 | 17.4385 | 15.6944 | 11.5185 | 5.6903 | 0.8977 | -4.4236 | 21.8151 | 20.6601 | 19.3894 | 17.9805 | 16.5544 | 15.0945 | 13.6584 | 12.0115 | 9.6185 | 3.8759 | -4.1392 | -9.1073 | -11.4038
|  | EASTLEIGH NORTH | FS |  |  | 21.3125 | 20.0105 | 18.7351 | 17.2565 | 15.7806 | 14.2789 | 12.7954 | 11.1329 | 8.6763 | 2.6312 | -6.5099 | -12.5078 | -15.218 | 24.9416 | 23.9277 | 22.9422 | 21.9169 | 20.8892 | 19.8313 | 18.7378 | 17.4385 | 15.6944 | 11.5185 | 5.6903 | 0.8977 | -4.4236 | 21.8151 | 20.6601 | 19.3894 | 17.9805 | 16.5544 | 15.0945 | 13.6584 | 12.0115 | 9.6185 | 3.8759 | -4.1392 | -9.1073 | -11.4038
LOVEDEAN GSP | PORTSMOUTH BSP | EASTNEY | MINIMUM HEADROOM | SZ 66357 99040 | YES | 11.2869 | 11.1181 | 10.8827 | 10.5508 | 10.1942 | 9.8234 | 9.3873 | 8.8955 | 8.139 | 5.771 | 1.2706 | -2.2263 | -4.4867 | 13.9485 | 13.7952 | 13.5958 | 13.3383 | 13.0591 | 12.7565 | 12.3908 | 11.9735 | 11.4234 | 9.6625 | 5.8696 | 1.4949 | -4.487 | 12.1456 | 11.9908 | 11.7703 | 11.4654 | 11.1368 | 10.7926 | 10.3871 | 9.9267 | 9.2261 | 7.0355 | 3.0234 | 0.037593 | -1.8513
|  | EASTNEY | CT |  |  | 11.2869 | 11.1181 | 10.8827 | 10.5508 | 10.1942 | 9.8234 | 9.3873 | 8.8955 | 8.139 | 5.771 | 1.2706 | -2.2263 | -4.4867 | 13.9485 | 13.7952 | 13.5958 | 13.3383 | 13.0591 | 12.7565 | 12.3908 | 11.9735 | 11.4234 | 9.6625 | 5.8696 | 1.4949 | -4.487 | 12.1456 | 11.9908 | 11.7703 | 11.4654 | 11.1368 | 10.7926 | 10.3871 | 9.9267 | 9.2261 | 7.0355 | 3.0234 | 0.037593 | -1.8513
|  | EASTNEY | LW |  |  | 11.2869 | 11.1181 | 10.8827 | 10.5508 | 10.1942 | 9.8234 | 9.3873 | 8.8955 | 8.139 | 5.771 | 1.2706 | -2.2263 | -4.4867 | 13.9485 | 13.7952 | 13.5958 | 13.3383 | 13.0591 | 12.7565 | 12.3908 | 11.9735 | 11.4234 | 9.6625 | 5.8696 | 1.4949 | -4.487 | 12.1456 | 11.9908 | 11.7703 | 11.4654 | 11.1368 | 10.7926 | 10.3871 | 9.9267 | 9.2261 | 7.0355 | 3.0234 | 0.037593 | -1.8513
|  | EASTNEY | ST |  |  | 11.2869 | 11.1181 | 10.8827 | 10.5508 | 10.1942 | 9.8234 | 9.3873 | 8.8955 | 8.139 | 5.771 | 1.2706 | -2.2263 | -4.4867 | 13.9485 | 13.7952 | 13.5958 | 13.3383 | 13.0591 | 12.7565 | 12.3908 | 11.9735 | 11.4234 | 9.6625 | 5.8696 | 1.4949 | -4.487 | 12.1456 | 11.9908 | 11.7703 | 11.4654 | 11.1368 | 10.7926 | 10.3871 | 9.9267 | 9.2261 | 7.0355 | 3.0234 | 0.037593 | -1.8513
|  | EASTNEY | FS |  |  | 11.2869 | 11.1181 | 10.8827 | 10.5508 | 10.1942 | 9.8234 | 9.3873 | 8.8955 | 8.139 | 5.771 | 1.2706 | -2.2263 | -4.4867 | 13.9485 | 13.7952 | 13.5958 | 13.3383 | 13.0591 | 12.7565 | 12.3908 | 11.9735 | 11.4234 | 9.6625 | 5.8696 | 1.4949 | -4.487 | 12.1456 | 11.9908 | 11.7703 | 11.4654 | 11.1368 | 10.7926 | 10.3871 | 9.9267 | 9.2261 | 7.0355 | 3.0234 | 0.037593 | -1.8513
LALEHAM | STAINES | EGHAM | MINIMUM HEADROOM | TQ 01030 71404 | YES | 11.7046 | 10.7024 | 9.6975 | 8.4584 | 7.1609 | 5.855 | 4.7795 | 3.562 | 1.8616 | -2.6126 | -9.4853 | -13.6862 | -15.252 | 16.5519 | 15.9126 | 15.2228 | 14.4389 | 13.6156 | 12.7589 | 11.9923 | 11.0932 | 9.9384 | 6.906 | 2.2784 | -1.3084 | -5.1945 | 11.2084 | 10.3404 | 9.4496 | 8.3554 | 7.2062 | 6.0401 | 5.0456 | 3.9052 | 2.3124 | -1.849 | -8.0852 | -11.6396 | -12.9177
|  | EGHAM | CT |  |  | 11.7046 | 10.7024 | 9.6975 | 8.4584 | 7.1609 | 5.855 | 4.7795 | 3.562 | 1.8616 | -2.6126 | -9.4853 | -13.6862 | -15.252 | 16.5519 | 15.9126 | 15.2228 | 14.4389 | 13.6156 | 12.7589 | 11.9923 | 11.0932 | 9.9384 | 6.906 | 2.2784 | -1.3084 | -5.1945 | 11.2084 | 10.3404 | 9.4496 | 8.3554 | 7.2062 | 6.0401 | 5.0456 | 3.9052 | 2.3124 | -1.849 | -8.0852 | -11.6396 | -12.9177
|  | EGHAM | LW |  |  | 11.7046 | 10.7024 | 9.6975 | 8.4584 | 7.1609 | 5.855 | 4.7795 | 3.562 | 1.8616 | -2.6126 | -9.4853 | -13.6862 | -15.252 | 16.5519 | 15.9126 | 15.2228 | 14.4389 | 13.6156 | 12.7589 | 11.9923 | 11.0932 | 9.9384 | 6.906 | 2.2784 | -1.3084 | -5.1945 | 11.2084 | 10.3404 | 9.4496 | 8.3554 | 7.2062 | 6.0401 | 5.0456 | 3.9052 | 2.3124 | -1.849 | -8.0852 | -11.6396 | -12.9177
|  | EGHAM | ST |  |  | 11.7046 | 10.7024 | 9.6975 | 8.4584 | 7.1609 | 5.855 | 4.7795 | 3.562 | 1.8616 | -2.6126 | -9.4853 | -13.6862 | -15.252 | 16.5519 | 15.9126 | 15.2228 | 14.4389 | 13.6156 | 12.7589 | 11.9923 | 11.0932 | 9.9384 | 6.906 | 2.2784 | -1.3084 | -5.1945 | 11.2084 | 10.3404 | 9.4496 | 8.3554 | 7.2062 | 6.0401 | 5.0456 | 3.9052 | 2.3124 | -1.849 | -8.0852 | -11.6396 | -12.9177
|  | EGHAM | FS |  |  | 11.7046 | 10.7024 | 9.6975 | 8.4584 | 7.1609 | 5.855 | 4.7795 | 3.562 | 1.8616 | -2.6126 | -9.4853 | -13.6862 | -15.252 | 16.5519 | 15.9126 | 15.2228 | 14.4389 | 13.6156 | 12.7589 | 11.9923 | 11.0932 | 9.9384 | 6.906 | 2.2784 | -1.3084 | -5.1945 | 11.2084 | 10.3404 | 9.4496 | 8.3554 | 7.2062 | 6.0401 | 5.0456 | 3.9052 | 2.3124 | -1.849 | -8.0852 | -11.6396 | -12.9177
MANNINGTON GSP | BOURNEMOUTH | ELECTRIC HOUSE | MINIMUM HEADROOM | SZ 08757 91379 | YES | 18.4846 | 18.1625 | 17.7994 | 17.2086 | 16.7384 | 16.2941 | 15.8143 | 15.2471 | 14.5622 | 12.4228 | 8.0372 | 4.6666 | 2.4753 | 19.6527 | 19.49 | 19.308 | 19.0579 | 18.789 | 18.4423 | 18.0624 | 17.6242 | 17.145 | 15.569 | 12.1198 | 8.4191 | 3.6264 | 20.4673 | 20.2788 | 20.042 | 19.548 | 19.1422 | 18.7588 | 18.3452 | 17.8786 | 17.2976 | 15.4873 | 11.8262 | 9.1382 | 7.3286
|  | ELECTRIC HOUSE | CT |  |  | 18.4846 | 18.1625 | 17.7994 | 17.2086 | 16.7384 | 16.2941 | 15.8143 | 15.2471 | 14.5622 | 12.4228 | 8.0372 | 4.6666 | 2.4753 | 19.6527 | 19.49 | 19.308 | 19.0579 | 18.789 | 18.4423 | 18.0624 | 17.6242 | 17.145 | 15.569 | 12.1198 | 8.4191 | 3.6264 | 20.4673 | 20.2788 | 20.042 | 19.548 | 19.1422 | 18.7588 | 18.3452 | 17.8786 | 17.2976 | 15.4873 | 11.8262 | 9.1382 | 7.3286
|  | ELECTRIC HOUSE | LW |  |  | 18.4846 | 18.1625 | 17.7994 | 17.2086 | 16.7384 | 16.2941 | 15.8143 | 15.2471 | 14.5622 | 12.4228 | 8.0372 | 4.6666 | 2.4753 | 19.6527 | 19.49 | 19.308 | 19.0579 | 18.789 | 18.4423 | 18.0624 | 17.6242 | 17.145 | 15.569 | 12.1198 | 8.4191 | 3.6264 | 20.4673 | 20.2788 | 20.042 | 19.548 | 19.1422 | 18.7588 | 18.3452 | 17.8786 | 17.2976 | 15.4873 | 11.8262 | 9.1382 | 7.3286
|  | ELECTRIC HOUSE | ST |  |  | 18.4846 | 18.1625 | 17.7994 | 17.2086 | 16.7384 | 16.2941 | 15.8143 | 15.2471 | 14.5622 | 12.4228 | 8.0372 | 4.6666 | 2.4753 | 19.6527 | 19.49 | 19.308 | 19.0579 | 18.789 | 18.4423 | 18.0624 | 17.6242 | 17.145 | 15.569 | 12.1198 | 8.4191 | 3.6264 | 20.4673 | 20.2788 | 20.042 | 19.548 | 19.1422 | 18.7588 | 18.3452 | 17.8786 | 17.2976 | 15.4873 | 11.8262 | 9.1382 | 7.3286
|  | ELECTRIC HOUSE | FS |  |  | 18.4846 | 18.1625 | 17.7994 | 17.2086 | 16.7384 | 16.2941 | 15.8143 | 15.2471 | 14.5622 | 12.4228 | 8.0372 | 4.6666 | 2.4753 | 19.6527 | 19.49 | 19.308 | 19.0579 | 18.789 | 18.4423 | 18.0624 | 17.6242 | 17.145 | 15.569 | 12.1198 | 8.4191 | 3.6264 | 20.4673 | 20.2788 | 20.042 | 19.548 | 19.1422 | 18.7588 | 18.3452 | 17.8786 | 17.2976 | 15.4873 | 11.8262 | 9.1382 | 7.3286
BRAMLEY (FLEE) | WOKINGHAM BSP | ELMS ROAD | MINIMUM HEADROOM | SU 81057 68532 | YES | 11.5512 | 10.9241 | 10.185 | 8.9996 | 7.7855 | 6.6136 | 5.3481 | 3.7943 | 1.8232 | -2.9931 | -10.2472 | -14.8229 | -17.0231 | 14.6079 | 14.138 | 13.6019 | 12.864 | 12.0985 | 11.3237 | 10.4744 | 9.402 | 8.0946 | 4.9642 | 0.34399 | -3.1079 | -6.5696 | 10.8239 | 10.2424 | 9.5721 | 8.5713 | 7.5414 | 6.5269 | 5.4224 | 4.0369 | 2.2845 | -1.8202 | -7.7441 | -11.7616 | -13.6004
|  | ELMS ROAD | CT |  |  | 11.5512 | 10.9241 | 10.185 | 8.9996 | 7.7855 | 6.6136 | 5.3481 | 3.7943 | 1.8232 | -2.9931 | -10.2472 | -14.8229 | -17.0231 | 14.6079 | 14.138 | 13.6019 | 12.864 | 12.0985 | 11.3237 | 10.4744 | 9.402 | 8.0946 | 4.9642 | 0.34399 | -3.1079 | -6.5696 | 10.8239 | 10.2424 | 9.5721 | 8.5713 | 7.5414 | 6.5269 | 5.4224 | 4.0369 | 2.2845 | -1.8202 | -7.7441 | -11.7616 | -13.6004
|  | ELMS ROAD | LW |  |  | 11.5512 | 10.9241 | 10.185 | 8.9996 | 7.7855 | 6.6136 | 5.3481 | 3.7943 | 1.8232 | -2.9931 | -10.2472 | -14.8229 | -17.0231 | 14.6079 | 14.138 | 13.6019 | 12.864 | 12.0985 | 11.3237 | 10.4744 | 9.402 | 8.0946 | 4.9642 | 0.34399 | -3.1079 | -6.5696 | 10.8239 | 10.2424 | 9.5721 | 8.5713 | 7.5414 | 6.5269 | 5.4224 | 4.0369 | 2.2845 | -1.8202 | -7.7441 | -11.7616 | -13.6004
|  | ELMS ROAD | ST |  |  | 11.5512 | 10.9241 | 10.185 | 8.9996 | 7.7855 | 6.6136 | 5.3481 | 3.7943 | 1.8232 | -2.9931 | -10.2472 | -14.8229 | -17.0231 | 14.6079 | 14.138 | 13.6019 | 12.864 | 12.0985 | 11.3237 | 10.4744 | 9.402 | 8.0946 | 4.9642 | 0.34399 | -3.1079 | -6.5696 | 10.8239 | 10.2424 | 9.5721 | 8.5713 | 7.5414 | 6.5269 | 5.4224 | 4.0369 | 2.2845 | -1.8202 | -7.7441 | -11.7616 | -13.6004
|  | ELMS ROAD | FS |  |  | 11.5512 | 10.9241 | 10.185 | 8.9996 | 7.7855 | 6.6136 | 5.3481 | 3.7943 | 1.8232 | -2.9931 | -10.2472 | -14.8229 | -17.0231 | 14.6079 | 14.138 | 13.6019 | 12.864 | 12.0985 | 11.3237 | 10.4744 | 9.402 | 8.0946 | 4.9642 | 0.34399 | -3.1079 | -6.5696 | 10.8239 | 10.2424 | 9.5721 | 8.5713 | 7.5414 | 6.5269 | 5.4224 | 4.0369 | 2.2845 | -1.8202 | -7.7441 | -11.7616 | -13.6004
LOVEDEAN GSP | HAVANT | EMSWORTH | MINIMUM HEADROOM | SU 74861 05807 | YES | 0.99287 | 0.62451 | 0.12272 | -0.50375 | -1.1881 | -1.892 | -2.6384 | -3.5377 | -4.9208 | -8.7768 | -13.9293 | -17.0033 | -18.5955 | 5.2889 | 5.0443 | 4.7248 | 4.347 | 3.9353 | 3.5034 | 2.9809 | 2.3342 | 1.3613 | -1.34 | -4.5116 | -6.3283 | -7.9119 | 2.4178 | 2.1045 | 1.6963 | 1.1607 | 0.5779 | -0.021652 | -0.69546 | -1.5698 | -2.9084 | -6.6375 | -11.3701 | -13.9932 | -15.37
|  | EMSWORTH | CT |  |  | 0.99287 | 0.62451 | 0.12272 | -0.50375 | -1.1881 | -1.892 | -2.6384 | -3.5377 | -4.9208 | -8.7768 | -13.9293 | -17.0033 | -18.5955 | 5.2889 | 5.0443 | 4.7248 | 4.347 | 3.9353 | 3.5034 | 2.9809 | 2.3342 | 1.3613 | -1.34 | -4.5116 | -6.3283 | -7.9119 | 2.4178 | 2.1045 | 1.6963 | 1.1607 | 0.5779 | -0.021652 | -0.69546 | -1.5698 | -2.9084 | -6.6375 | -11.3701 | -13.9932 | -15.37
|  | EMSWORTH | LW |  |  | 0.99287 | 0.62451 | 0.12272 | -0.50375 | -1.1881 | -1.892 | -2.6384 | -3.5377 | -4.9208 | -8.7768 | -13.9293 | -17.0033 | -18.5955 | 5.2889 | 5.0443 | 4.7248 | 4.347 | 3.9353 | 3.5034 | 2.9809 | 2.3342 | 1.3613 | -1.34 | -4.5116 | -6.3283 | -7.9119 | 2.4178 | 2.1045 | 1.6963 | 1.1607 | 0.5779 | -0.021652 | -0.69546 | -1.5698 | -2.9084 | -6.6375 | -11.3701 | -13.9932 | -15.37
|  | EMSWORTH | ST |  |  | 0.99287 | 0.62451 | 0.12272 | -0.50375 | -1.1881 | -1.892 | -2.6384 | -3.5377 | -4.9208 | -8.7768 | -13.9293 | -17.0033 | -18.5955 | 5.2889 | 5.0443 | 4.7248 | 4.347 | 3.9353 | 3.5034 | 2.9809 | 2.3342 | 1.3613 | -1.34 | -4.5116 | -6.3283 | -7.9119 | 2.4178 | 2.1045 | 1.6963 | 1.1607 | 0.5779 | -0.021652 | -0.69546 | -1.5698 | -2.9084 | -6.6375 | -11.3701 | -13.9932 | -15.37
|  | EMSWORTH | FS |  |  | 0.99287 | 0.62451 | 0.12272 | -0.50375 | -1.1881 | -1.892 | -2.6384 | -3.5377 | -4.9208 | -8.7768 | -13.9293 | -17.0033 | -18.5955 | 5.2889 | 5.0443 | 4.7248 | 4.347 | 3.9353 | 3.5034 | 2.9809 | 2.3342 | 1.3613 | -1.34 | -4.5116 | -6.3283 | -7.9119 | 2.4178 | 2.1045 | 1.6963 | 1.1607 | 0.5779 | -0.021652 | -0.69546 | -1.5698 | -2.9084 | -6.6375 | -11.3701 | -13.9932 | -15.37
MELKSHAM GSP | AMESBURY | ENFORD | MINIMUM HEADROOM | SU 13728 51712 | YES | 7.2255 | 7.2154 | 7.1992 | 7.1837 | 7.1602 | 7.0175 | 6.8245 | 6.5971 | 6.2823 | 5.5524 | 4.959 | 4.754 | 4.6733 | 6.8376 | 6.7875 | 6.7166 | 6.6336 | 6.5449 | 6.4461 | 6.3425 | 6.2101 | 6.0302 | 5.6294 | 5.3023 | 5.1583 | 5.0316 | 7.0886 | 7.0113 | 6.907 | 6.7725 | 6.6301 | 6.4718 | 6.3074 | 6.1001 | 5.8047 | 5.1321 | 4.5947 | 4.4115 | 4.3362
|  | ENFORD | CT |  |  | 7.2255 | 7.2154 | 7.1992 | 7.1837 | 7.1602 | 7.0175 | 6.8245 | 6.5971 | 6.2823 | 5.5524 | 4.959 | 4.754 | 4.6733 | 6.8376 | 6.7875 | 6.7166 | 6.6336 | 6.5449 | 6.4461 | 6.3425 | 6.2101 | 6.0302 | 5.6294 | 5.3023 | 5.1583 | 5.0316 | 7.0886 | 7.0113 | 6.907 | 6.7725 | 6.6301 | 6.4718 | 6.3074 | 6.1001 | 5.8047 | 5.1321 | 4.5947 | 4.4115 | 4.3362
|  | ENFORD | LW |  |  | 7.2255 | 7.2154 | 7.1992 | 7.1837 | 7.1602 | 7.0175 | 6.8245 | 6.5971 | 6.2823 | 5.5524 | 4.959 | 4.754 | 4.6733 | 6.8376 | 6.7875 | 6.7166 | 6.6336 | 6.5449 | 6.4461 | 6.3425 | 6.2101 | 6.0302 | 5.6294 | 5.3023 | 5.1583 | 5.0316 | 7.0886 | 7.0113 | 6.907 | 6.7725 | 6.6301 | 6.4718 | 6.3074 | 6.1001 | 5.8047 | 5.1321 | 4.5947 | 4.4115 | 4.3362
|  | ENFORD | ST |  |  | 7.2255 | 7.2154 | 7.1992 | 7.1837 | 7.1602 | 7.0175 | 6.8245 | 6.5971 | 6.2823 | 5.5524 | 4.959 | 4.754 | 4.6733 | 6.8376 | 6.7875 | 6.7166 | 6.6336 | 6.5449 | 6.4461 | 6.3425 | 6.2101 | 6.0302 | 5.6294 | 5.3023 | 5.1583 | 5.0316 | 7.0886 | 7.0113 | 6.907 | 6.7725 | 6.6301 | 6.4718 | 6.3074 | 6.1001 | 5.8047 | 5.1321 | 4.5947 | 4.4115 | 4.3362
|  | ENFORD | FS |  |  | 7.2255 | 7.2154 | 7.1992 | 7.1837 | 7.1602 | 7.0175 | 6.8245 | 6.5971 | 6.2823 | 5.5524 | 4.959 | 4.754 | 4.6733 | 6.8376 | 6.7875 | 6.7166 | 6.6336 | 6.5449 | 6.4461 | 6.3425 | 6.2101 | 6.0302 | 5.6294 | 5.3023 | 5.1583 | 5.0316 | 7.0886 | 7.0113 | 6.907 | 6.7725 | 6.6301 | 6.4718 | 6.3074 | 6.1001 | 5.8047 | 5.1321 | 4.5947 | 4.4115 | 4.3362
COWLEY GSP | YARNTON BSP | EYNSHAM | MINIMUM HEADROOM | SP 42236 10266 | NO | 18.7667 | 18.1462 | 17.2795 | 16.0131 | 14.5389 | 12.9681 | 11.3181 | 9.627 | 7.6013 | 3.188 | -1.3588 | -4.1459 | -4.4709 | 22.0209 | 21.6884 | 21.2828 | 20.7838 | 19.9852 | 19.0378 | 18.0447 | 16.9971 | 15.7843 | 13.2301 | 10.9557 | 9.5476 | 8.8985 | 19.9097 | 19.3656 | 18.6111 | 17.5319 | 16.282 | 14.9434 | 13.5327 | 12.0669 | 10.2966 | 6.4862 | 2.6647 | 0.37163 | 0.0952
|  | EYNSHAM | CT |  |  | 18.7667 | 18.1462 | 17.2795 | 16.0131 | 14.5389 | 12.9681 | 11.3181 | 9.627 | 7.6013 | 3.188 | -1.3588 | -4.1459 | -4.4709 | 22.0209 | 21.6884 | 21.2828 | 20.7838 | 19.9852 | 19.0378 | 18.0447 | 16.9971 | 15.7843 | 13.2301 | 10.9557 | 9.5476 | 8.8985 | 19.9097 | 19.3656 | 18.6111 | 17.5319 | 16.282 | 14.9434 | 13.5327 | 12.0669 | 10.2966 | 6.4862 | 2.6647 | 0.37163 | 0.0952
|  | EYNSHAM | LW |  |  | 18.7667 | 18.1462 | 17.2795 | 16.0131 | 14.5389 | 12.9681 | 11.3181 | 9.627 | 7.6013 | 3.188 | -1.3588 | -4.1459 | -4.4709 | 22.0209 | 21.6884 | 21.2828 | 20.7838 | 19.9852 | 19.0378 | 18.0447 | 16.9971 | 15.7843 | 13.2301 | 10.9557 | 9.5476 | 8.8985 | 19.9097 | 19.3656 | 18.6111 | 17.5319 | 16.282 | 14.9434 | 13.5327 | 12.0669 | 10.2966 | 6.4862 | 2.6647 | 0.37163 | 0.0952
|  | EYNSHAM | ST |  |  | 18.7667 | 18.1462 | 17.2795 | 16.0131 | 14.5389 | 12.9681 | 11.3181 | 9.627 | 7.6013 | 3.188 | -1.3588 | -4.1459 | -4.4709 | 22.0209 | 21.6884 | 21.2828 | 20.7838 | 19.9852 | 19.0378 | 18.0447 | 16.9971 | 15.7843 | 13.2301 | 10.9557 | 9.5476 | 8.8985 | 19.9097 | 19.3656 | 18.6111 | 17.5319 | 16.282 | 14.9434 | 13.5327 | 12.0669 | 10.2966 | 6.4862 | 2.6647 | 0.37163 | 0.0952
|  | EYNSHAM | FS |  |  | 18.7667 | 18.1462 | 17.2795 | 16.0131 | 14.5389 | 12.9681 | 11.3181 | 9.627 | 7.6013 | 3.188 | -1.3588 | -4.1459 | -4.4709 | 22.0209 | 21.6884 | 21.2828 | 20.7838 | 19.9852 | 19.0378 | 18.0447 | 16.9971 | 15.7843 | 13.2301 | 10.9557 | 9.5476 | 8.8985 | 19.9097 | 19.3656 | 18.6111 | 17.5319 | 16.282 | 14.9434 | 13.5327 | 12.0669 | 10.2966 | 6.4862 | 2.6647 | 0.37163 | 0.0952
MINETY GSP | CIRENCESTER BSP | FAIRFORD | MINIMUM HEADROOM | SP 14418 00559 | YES | 9.6085 | 9.3633 | 9.0666 | 8.649 | 8.2155 | 7.7416 | 7.212 | 6.6088 | 5.759 | 3.8754 | 0.7016 | -0.97256 | -1.3578 | 13.1247 | 12.9676 | 12.7676 | 12.5281 | 12.2764 | 11.9966 | 11.6752 | 11.2923 | 10.7859 | 9.806 | 8.3521 | 7.5172 | 7.0768 | 10.6216 | 10.3914 | 10.1097 | 9.7232 | 9.3212 | 8.8806 | 8.3858 | 7.8175 | 7.0232 | 5.3068 | 2.4838 | 1.0069 | 0.67791
|  | FAIRFORD | CT |  |  | 9.6085 | 9.3633 | 9.0666 | 8.649 | 8.2155 | 7.7416 | 7.212 | 6.6088 | 5.759 | 3.8754 | 0.7016 | -0.97256 | -1.3578 | 13.1247 | 12.9676 | 12.7676 | 12.5281 | 12.2764 | 11.9966 | 11.6752 | 11.2923 | 10.7859 | 9.806 | 8.3521 | 7.5172 | 7.0768 | 10.6216 | 10.3914 | 10.1097 | 9.7232 | 9.3212 | 8.8806 | 8.3858 | 7.8175 | 7.0232 | 5.3068 | 2.4838 | 1.0069 | 0.67791
|  | FAIRFORD | LW |  |  | 9.6085 | 9.3633 | 9.0666 | 8.649 | 8.2155 | 7.7416 | 7.212 | 6.6088 | 5.759 | 3.8754 | 0.7016 | -0.97256 | -1.3578 | 13.1247 | 12.9676 | 12.7676 | 12.5281 | 12.2764 | 11.9966 | 11.6752 | 11.2923 | 10.7859 | 9.806 | 8.3521 | 7.5172 | 7.0768 | 10.6216 | 10.3914 | 10.1097 | 9.7232 | 9.3212 | 8.8806 | 8.3858 | 7.8175 | 7.0232 | 5.3068 | 2.4838 | 1.0069 | 0.67791
|  | FAIRFORD | ST |  |  | 9.6085 | 9.3633 | 9.0666 | 8.649 | 8.2155 | 7.7416 | 7.212 | 6.6088 | 5.759 | 3.8754 | 0.7016 | -0.97256 | -1.3578 | 13.1247 | 12.9676 | 12.7676 | 12.5281 | 12.2764 | 11.9966 | 11.6752 | 11.2923 | 10.7859 | 9.806 | 8.3521 | 7.5172 | 7.0768 | 10.6216 | 10.3914 | 10.1097 | 9.7232 | 9.3212 | 8.8806 | 8.3858 | 7.8175 | 7.0232 | 5.3068 | 2.4838 | 1.0069 | 0.67791
|  | FAIRFORD | FS |  |  | 9.6085 | 9.3633 | 9.0666 | 8.649 | 8.2155 | 7.7416 | 7.212 | 6.6088 | 5.759 | 3.8754 | 0.7016 | -0.97256 | -1.3578 | 13.1247 | 12.9676 | 12.7676 | 12.5281 | 12.2764 | 11.9966 | 11.6752 | 11.2923 | 10.7859 | 9.806 | 8.3521 | 7.5172 | 7.0768 | 10.6216 | 10.3914 | 10.1097 | 9.7232 | 9.3212 | 8.8806 | 8.3858 | 7.8175 | 7.0232 | 5.3068 | 2.4838 | 1.0069 | 0.67791
MINETY GSP | STRATTON (2 X 60) | FARINGDON | MINIMUM HEADROOM | SU 28819 94924 | YES | 1.0468 | 0.56749 | 0.10553 | -0.50249 | -1.1527 | -1.8251 | -2.5751 | -3.3938 | -4.5536 | -7.2058 | -11.5053 | -14.5353 | -15.7948 | 6.0703 | 5.7519 | 5.432 | 5.062 | 4.6633 | 4.2383 | 3.7544 | 3.1961 | 2.4522 | 0.86807 | -1.5188 | -3.3015 | -4.8293 | 3.6845 | 3.2525 | 2.8261 | 2.2708 | 1.6775 | 1.0608 | 0.36931 | -0.40012 | -1.4892 | -3.9344 | -7.8027 | -10.4409 | -11.5533
|  | FARINGDON | CT |  |  | 1.0468 | 0.56749 | 0.10553 | -0.50249 | -1.1527 | -1.8251 | -2.5751 | -3.3938 | -4.5536 | -7.2058 | -11.5053 | -14.5353 | -15.7948 | 6.0703 | 5.7519 | 5.432 | 5.062 | 4.6633 | 4.2383 | 3.7544 | 3.1961 | 2.4522 | 0.86807 | -1.5188 | -3.3015 | -4.8293 | 3.6845 | 3.2525 | 2.8261 | 2.2708 | 1.6775 | 1.0608 | 0.36931 | -0.40012 | -1.4892 | -3.9344 | -7.8027 | -10.4409 | -11.5533
|  | FARINGDON | LW |  |  | 1.0468 | 0.56749 | 0.10553 | -0.50249 | -1.1527 | -1.8251 | -2.5751 | -3.3938 | -4.5536 | -7.2058 | -11.5053 | -14.5353 | -15.7948 | 6.0703 | 5.7519 | 5.432 | 5.062 | 4.6633 | 4.2383 | 3.7544 | 3.1961 | 2.4522 | 0.86807 | -1.5188 | -3.3015 | -4.8293 | 3.6845 | 3.2525 | 2.8261 | 2.2708 | 1.6775 | 1.0608 | 0.36931 | -0.40012 | -1.4892 | -3.9344 | -7.8027 | -10.4409 | -11.5533
|  | FARINGDON | ST |  |  | 1.0468 | 0.56749 | 0.10553 | -0.50249 | -1.1527 | -1.8251 | -2.5751 | -3.3938 | -4.5536 | -7.2058 | -11.5053 | -14.5353 | -15.7948 | 6.0703 | 5.7519 | 5.432 | 5.062 | 4.6633 | 4.2383 | 3.7544 | 3.1961 | 2.4522 | 0.86807 | -1.5188 | -3.3015 | -4.8293 | 3.6845 | 3.2525 | 2.8261 | 2.2708 | 1.6775 | 1.0608 | 0.36931 | -0.40012 | -1.4892 | -3.9344 | -7.8027 | -10.4409 | -11.5533
|  | FARINGDON | FS |  |  | 1.0468 | 0.56749 | 0.10553 | -0.50249 | -1.1527 | -1.8251 | -2.5751 | -3.3938 | -4.5536 | -7.2058 | -11.5053 | -14.5353 | -15.7948 | 6.0703 | 5.7519 | 5.432 | 5.062 | 4.6633 | 4.2383 | 3.7544 | 3.1961 | 2.4522 | 0.86807 | -1.5188 | -3.3015 | -4.8293 | 3.6845 | 3.2525 | 2.8261 | 2.2708 | 1.6775 | 1.0608 | 0.36931 | -0.40012 | -1.4892 | -3.9344 | -7.8027 | -10.4409 | -11.5533
LOVEDEAN GSP | WYMERING BSP | FARLINGTON | MINIMUM HEADROOM | SU 67400 04843 | YES | 14.4283 | 14.2978 | 14.0806 | 13.8646 | 13.6711 | 13.4823 | 13.2927 | 13.1256 | 12.9087 | 12.2405 | 10.4281 | 8.5164 | 7.2211 | 17.8356 | 17.725 | 17.5304 | 17.3332 | 17.1418 | 16.9513 | 16.7609 | 16.5869 | 16.3549 | 15.6393 | 14.3771 | 13.3091 | 11.754 | 16.8916 | 16.7589 | 16.5351 | 16.3202 | 16.1331 | 15.9501 | 15.7457 | 15.5317 | 15.2014 | 14.0852 | 12.1049 | 10.8223 | 9.8281
|  | FARLINGTON | CT |  |  | 14.4283 | 14.2978 | 14.0806 | 13.8646 | 13.6711 | 13.4823 | 13.2927 | 13.1256 | 12.9087 | 12.2405 | 10.4281 | 8.5164 | 7.2211 | 17.8356 | 17.725 | 17.5304 | 17.3332 | 17.1418 | 16.9513 | 16.7609 | 16.5869 | 16.3549 | 15.6393 | 14.3771 | 13.3091 | 11.754 | 16.8916 | 16.7589 | 16.5351 | 16.3202 | 16.1331 | 15.9501 | 15.7457 | 15.5317 | 15.2014 | 14.0852 | 12.1049 | 10.8223 | 9.8281
|  | FARLINGTON | LW |  |  | 14.4283 | 14.2978 | 14.0806 | 13.8646 | 13.6711 | 13.4823 | 13.2927 | 13.1256 | 12.9087 | 12.2405 | 10.4281 | 8.5164 | 7.2211 | 17.8356 | 17.725 | 17.5304 | 17.3332 | 17.1418 | 16.9513 | 16.7609 | 16.5869 | 16.3549 | 15.6393 | 14.3771 | 13.3091 | 11.754 | 16.8916 | 16.7589 | 16.5351 | 16.3202 | 16.1331 | 15.9501 | 15.7457 | 15.5317 | 15.2014 | 14.0852 | 12.1049 | 10.8223 | 9.8281
|  | FARLINGTON | ST |  |  | 14.4283 | 14.2978 | 14.0806 | 13.8646 | 13.6711 | 13.4823 | 13.2927 | 13.1256 | 12.9087 | 12.2405 | 10.4281 | 8.5164 | 7.2211 | 17.8356 | 17.725 | 17.5304 | 17.3332 | 17.1418 | 16.9513 | 16.7609 | 16.5869 | 16.3549 | 15.6393 | 14.3771 | 13.3091 | 11.754 | 16.8916 | 16.7589 | 16.5351 | 16.3202 | 16.1331 | 15.9501 | 15.7457 | 15.5317 | 15.2014 | 14.0852 | 12.1049 | 10.8223 | 9.8281
|  | FARLINGTON | FS |  |  | 14.4283 | 14.2978 | 14.0806 | 13.8646 | 13.6711 | 13.4823 | 13.2927 | 13.1256 | 12.9087 | 12.2405 | 10.4281 | 8.5164 | 7.2211 | 17.8356 | 17.725 | 17.5304 | 17.3332 | 17.1418 | 16.9513 | 16.7609 | 16.5869 | 16.3549 | 15.6393 | 14.3771 | 13.3091 | 11.754 | 16.8916 | 16.7589 | 16.5351 | 16.3202 | 16.1331 | 15.9501 | 15.7457 | 15.5317 | 15.2014 | 14.0852 | 12.1049 | 10.8223 | 9.8281
BRAMLEY (FLEE) | CAMBERLEY RESERVE | FARNBOROUGH | MINIMUM HEADROOM | SU 88404 53930 | YES | 19.7151 | 18.4954 | 16.9322 | 15.3937 | 13.7547 | 12.0246 | 10.1273 | 7.9055 | 5.0522 | -1.2011 | -8.7397 | -13.1526 | -15.2926 | 21.2937 | 20.5162 | 19.5351 | 18.6005 | 17.6015 | 16.5352 | 15.3644 | 13.9655 | 12.1928 | 8.2512 | 3.4731 | 0.30685 | -2.6379 | 20.1341 | 19.0955 | 17.754 | 16.4173 | 14.9873 | 13.4729 | 11.8077 | 9.8379 | 7.2763 | 1.6203 | -5.2008 | -9.0908 | -10.9535
|  | FARNBOROUGH | CT |  |  | 19.7151 | 18.4954 | 16.9322 | 15.3937 | 13.7547 | 12.0246 | 10.1273 | 7.9055 | 5.0522 | -1.2011 | -8.7397 | -13.1526 | -15.2926 | 21.2937 | 20.5162 | 19.5351 | 18.6005 | 17.6015 | 16.5352 | 15.3644 | 13.9655 | 12.1928 | 8.2512 | 3.4731 | 0.30685 | -2.6379 | 20.1341 | 19.0955 | 17.754 | 16.4173 | 14.9873 | 13.4729 | 11.8077 | 9.8379 | 7.2763 | 1.6203 | -5.2008 | -9.0908 | -10.9535
|  | FARNBOROUGH | LW |  |  | 19.7151 | 18.4954 | 16.9322 | 15.3937 | 13.7547 | 12.0246 | 10.1273 | 7.9055 | 5.0522 | -1.2011 | -8.7397 | -13.1526 | -15.2926 | 21.2937 | 20.5162 | 19.5351 | 18.6005 | 17.6015 | 16.5352 | 15.3644 | 13.9655 | 12.1928 | 8.2512 | 3.4731 | 0.30685 | -2.6379 | 20.1341 | 19.0955 | 17.754 | 16.4173 | 14.9873 | 13.4729 | 11.8077 | 9.8379 | 7.2763 | 1.6203 | -5.2008 | -9.0908 | -10.9535
|  | FARNBOROUGH | ST |  |  | 19.7151 | 18.4954 | 16.9322 | 15.3937 | 13.7547 | 12.0246 | 10.1273 | 7.9055 | 5.0522 | -1.2011 | -8.7397 | -13.1526 | -15.2926 | 21.2937 | 20.5162 | 19.5351 | 18.6005 | 17.6015 | 16.5352 | 15.3644 | 13.9655 | 12.1928 | 8.2512 | 3.4731 | 0.30685 | -2.6379 | 20.1341 | 19.0955 | 17.754 | 16.4173 | 14.9873 | 13.4729 | 11.8077 | 9.8379 | 7.2763 | 1.6203 | -5.2008 | -9.0908 | -10.9535
|  | FARNBOROUGH | FS |  |  | 19.7151 | 18.4954 | 16.9322 | 15.3937 | 13.7547 | 12.0246 | 10.1273 | 7.9055 | 5.0522 | -1.2011 | -8.7397 | -13.1526 | -15.2926 | 21.2937 | 20.5162 | 19.5351 | 18.6005 | 17.6015 | 16.5352 | 15.3644 | 13.9655 | 12.1928 | 8.2512 | 3.4731 | 0.30685 | -2.6379 | 20.1341 | 19.0955 | 17.754 | 16.4173 | 14.9873 | 13.4729 | 11.8077 | 9.8379 | 7.2763 | 1.6203 | -5.2008 | -9.0908 | -10.9535
BRAMLEY (FLEE) | ALDERSHOT BSP | FARNHAM | MINIMUM HEADROOM | SU 84517 47217 | YES | 10.2261 | 9.6479 | 9.0492 | 8.3114 | 7.512 | 6.6726 | 5.7249 | 4.6873 | 3.214 | -0.61251 | -6.6712 | -10.3452 | -12.0194 | 16.9652 | 16.5164 | 16.0693 | 15.5775 | 15.0394 | 14.4155 | 13.7382 | 12.9646 | 11.9675 | 9.4155 | 5.5633 | 2.9546 | 0.34287 | 12.558 | 11.9507 | 11.3327 | 10.6138 | 9.8405 | 9.0106 | 8.1159 | 7.1256 | 5.7371 | 2.163 | -3.2811 | -6.3166 | -7.6415
|  | FARNHAM | CT |  |  | 10.2261 | 9.6479 | 9.0492 | 8.3114 | 7.512 | 6.6726 | 5.7249 | 4.6873 | 3.214 | -0.61251 | -6.6712 | -10.3452 | -12.0194 | 16.9652 | 16.5164 | 16.0693 | 15.5775 | 15.0394 | 14.4155 | 13.7382 | 12.9646 | 11.9675 | 9.4155 | 5.5633 | 2.9546 | 0.34287 | 12.558 | 11.9507 | 11.3327 | 10.6138 | 9.8405 | 9.0106 | 8.1159 | 7.1256 | 5.7371 | 2.163 | -3.2811 | -6.3166 | -7.6415
|  | FARNHAM | LW |  |  | 10.2261 | 9.6479 | 9.0492 | 8.3114 | 7.512 | 6.6726 | 5.7249 | 4.6873 | 3.214 | -0.61251 | -6.6712 | -10.3452 | -12.0194 | 16.9652 | 16.5164 | 16.0693 | 15.5775 | 15.0394 | 14.4155 | 13.7382 | 12.9646 | 11.9675 | 9.4155 | 5.5633 | 2.9546 | 0.34287 | 12.558 | 11.9507 | 11.3327 | 10.6138 | 9.8405 | 9.0106 | 8.1159 | 7.1256 | 5.7371 | 2.163 | -3.2811 | -6.3166 | -7.6415
|  | FARNHAM | ST |  |  | 10.2261 | 9.6479 | 9.0492 | 8.3114 | 7.512 | 6.6726 | 5.7249 | 4.6873 | 3.214 | -0.61251 | -6.6712 | -10.3452 | -12.0194 | 16.9652 | 16.5164 | 16.0693 | 15.5775 | 15.0394 | 14.4155 | 13.7382 | 12.9646 | 11.9675 | 9.4155 | 5.5633 | 2.9546 | 0.34287 | 12.558 | 11.9507 | 11.3327 | 10.6138 | 9.8405 | 9.0106 | 8.1159 | 7.1256 | 5.7371 | 2.163 | -3.2811 | -6.3166 | -7.6415
|  | FARNHAM | FS |  |  | 10.2261 | 9.6479 | 9.0492 | 8.3114 | 7.512 | 6.6726 | 5.7249 | 4.6873 | 3.214 | -0.61251 | -6.6712 | -10.3452 | -12.0194 | 16.9652 | 16.5164 | 16.0693 | 15.5775 | 15.0394 | 14.4155 | 13.7382 | 12.9646 | 11.9675 | 9.4155 | 5.5633 | 2.9546 | 0.34287 | 12.558 | 11.9507 | 11.3327 | 10.6138 | 9.8405 | 9.0106 | 8.1159 | 7.1256 | 5.7371 | 2.163 | -3.2811 | -6.3166 | -7.6415
IVER 132KV | SLOUGH | FARNHAM ROYAL | MINIMUM HEADROOM | SU 95597 82844 | YES | 19.8934 | 19.2554 | 18.3043 | 8.9067 | -0.57715 | -14.1308 | -15.5853 | -17.2511 | -19.7917 | -26.6013 | -37.8238 | -45.6989 | -49.9618 | 30.3877 | 29.8769 | 29.1393 | 18.0895 | 6.9733 | -9.2788 | -10.3522 | -11.6039 | -13.3303 | -17.8786 | -25.0076 | -30.8498 | -36.7813 | 25.5304 | 25.0074 | 24.1082 | 12.7571 | 1.3234 | -15.2219 | -16.6087 | -18.2038 | -20.6038 | -26.9674 | -37.106 | -43.9826 | -47.6204
|  | FARNHAM ROYAL | CT |  |  | 19.8934 | 19.2554 | 18.3043 | 8.9067 | -0.57715 | -14.1308 | -15.5853 | -17.2511 | -19.7917 | -26.6013 | -37.8238 | -45.6989 | -49.9618 | 30.3877 | 29.8769 | 29.1393 | 18.0895 | 6.9733 | -9.2788 | -10.3522 | -11.6039 | -13.3303 | -17.8786 | -25.0076 | -30.8498 | -36.7813 | 25.5304 | 25.0074 | 24.1082 | 12.7571 | 1.3234 | -15.2219 | -16.6087 | -18.2038 | -20.6038 | -26.9674 | -37.106 | -43.9826 | -47.6204
|  | FARNHAM ROYAL | LW |  |  | 19.8934 | 19.2554 | 18.3043 | 8.9067 | -0.57715 | -14.1308 | -15.5853 | -17.2511 | -19.7917 | -26.6013 | -37.8238 | -45.6989 | -49.9618 | 30.3877 | 29.8769 | 29.1393 | 18.0895 | 6.9733 | -9.2788 | -10.3522 | -11.6039 | -13.3303 | -17.8786 | -25.0076 | -30.8498 | -36.7813 | 25.5304 | 25.0074 | 24.1082 | 12.7571 | 1.3234 | -15.2219 | -16.6087 | -18.2038 | -20.6038 | -26.9674 | -37.106 | -43.9826 | -47.6204
|  | FARNHAM ROYAL | ST |  |  | 19.8934 | 19.2554 | 18.3043 | 8.9067 | -0.57715 | -14.1308 | -15.5853 | -17.2511 | -19.7917 | -26.6013 | -37.8238 | -45.6989 | -49.9618 | 30.3877 | 29.8769 | 29.1393 | 18.0895 | 6.9733 | -9.2788 | -10.3522 | -11.6039 | -13.3303 | -17.8786 | -25.0076 | -30.8498 | -36.7813 | 25.5304 | 25.0074 | 24.1082 | 12.7571 | 1.3234 | -15.2219 | -16.6087 | -18.2038 | -20.6038 | -26.9674 | -37.106 | -43.9826 | -47.6204
|  | FARNHAM ROYAL | FS |  |  | 19.8934 | 19.2554 | 18.3043 | 8.9067 | -0.57715 | -14.1308 | -15.5853 | -17.2511 | -19.7917 | -26.6013 | -37.8238 | -45.6989 | -49.9618 | 30.3877 | 29.8769 | 29.1393 | 18.0895 | 6.9733 | -9.2788 | -10.3522 | -11.6039 | -13.3303 | -17.8786 | -25.0076 | -30.8498 | -36.7813 | 25.5304 | 25.0074 | 24.1082 | 12.7571 | 1.3234 | -15.2219 | -16.6087 | -18.2038 | -20.6038 | -26.9674 | -37.106 | -43.9826 | -47.6204
LALEHAM | EAST BEDFONT A | FELTHAM | MINIMUM HEADROOM | TQ 10628 72811 | YES | 20.9137 | 20.4221 | 19.6269 | 18.6833 | 17.6726 | 16.6557 | 15.5387 | 14.6994 | 13.8274 | 11.2589 | 6.9949 | 3.6093 | 1.3532 | 22.6933 | 22.3404 | 21.8111 | 21.2013 | 20.5405 | 19.8516 | 19.1108 | 18.5211 | 17.9168 | 16.0164 | 12.3484 | 8.1115 | 2.4269 | 21.5013 | 21.026 | 20.3209 | 19.5003 | 18.6153 | 17.717 | 16.736 | 15.9846 | 15.1882 | 12.8218 | 9.0709 | 6.2062 | 4.3344
|  | FELTHAM | CT |  |  | 20.9137 | 20.4221 | 19.6269 | 18.6833 | 17.6726 | 16.6557 | 15.5387 | 14.6994 | 13.8274 | 11.2589 | 6.9949 | 3.6093 | 1.3532 | 22.6933 | 22.3404 | 21.8111 | 21.2013 | 20.5405 | 19.8516 | 19.1108 | 18.5211 | 17.9168 | 16.0164 | 12.3484 | 8.1115 | 2.4269 | 21.5013 | 21.026 | 20.3209 | 19.5003 | 18.6153 | 17.717 | 16.736 | 15.9846 | 15.1882 | 12.8218 | 9.0709 | 6.2062 | 4.3344
|  | FELTHAM | LW |  |  | 20.9137 | 20.4221 | 19.6269 | 18.6833 | 17.6726 | 16.6557 | 15.5387 | 14.6994 | 13.8274 | 11.2589 | 6.9949 | 3.6093 | 1.3532 | 22.6933 | 22.3404 | 21.8111 | 21.2013 | 20.5405 | 19.8516 | 19.1108 | 18.5211 | 17.9168 | 16.0164 | 12.3484 | 8.1115 | 2.4269 | 21.5013 | 21.026 | 20.3209 | 19.5003 | 18.6153 | 17.717 | 16.736 | 15.9846 | 15.1882 | 12.8218 | 9.0709 | 6.2062 | 4.3344
|  | FELTHAM | ST |  |  | 20.9137 | 20.4221 | 19.6269 | 18.6833 | 17.6726 | 16.6557 | 15.5387 | 14.6994 | 13.8274 | 11.2589 | 6.9949 | 3.6093 | 1.3532 | 22.6933 | 22.3404 | 21.8111 | 21.2013 | 20.5405 | 19.8516 | 19.1108 | 18.5211 | 17.9168 | 16.0164 | 12.3484 | 8.1115 | 2.4269 | 21.5013 | 21.026 | 20.3209 | 19.5003 | 18.6153 | 17.717 | 16.736 | 15.9846 | 15.1882 | 12.8218 | 9.0709 | 6.2062 | 4.3344
|  | FELTHAM | FS |  |  | 20.9137 | 20.4221 | 19.6269 | 18.6833 | 17.6726 | 16.6557 | 15.5387 | 14.6994 | 13.8274 | 11.2589 | 6.9949 | 3.6093 | 1.3532 | 22.6933 | 22.3404 | 21.8111 | 21.2013 | 20.5405 | 19.8516 | 19.1108 | 18.5211 | 17.9168 | 16.0164 | 12.3484 | 8.1115 | 2.4269 | 21.5013 | 21.026 | 20.3209 | 19.5003 | 18.6153 | 17.717 | 16.736 | 15.9846 | 15.1882 | 12.8218 | 9.0709 | 6.2062 | 4.3344
MANNINGTON GSP | MANNINGTON BSP | FERNDOWN | MINIMUM HEADROOM | SU 06593 00685 | YES | 6.7147 | 6.3772 | 5.666 | 4.5924 | 3.4937 | 2.125 | 0.59612 | -1.2718 | -3.7505 | -10.349 | -19.0431 | -23.9792 | -26.2941 | 12.8215 | 12.5081 | 12.2001 | 11.6715 | 11.1514 | 10.5128 | 9.8683 | 8.6924 | 7.1202 | 2.9764 | -1.9577 | -4.9049 | -7.3282 | 8.9353 | 8.5682 | 8.1904 | 7.5129 | 6.4425 | 5.1347 | 3.6831 | 1.9064 | -0.42048 | -6.5199 | -14.2804 | -18.4831 | -20.3834
|  | FERNDOWN | CT |  |  | 6.7147 | 6.3772 | 5.666 | 4.5924 | 3.4937 | 2.125 | 0.59612 | -1.2718 | -3.7505 | -10.349 | -19.0431 | -23.9792 | -26.2941 | 12.8215 | 12.5081 | 12.2001 | 11.6715 | 11.1514 | 10.5128 | 9.8683 | 8.6924 | 7.1202 | 2.9764 | -1.9577 | -4.9049 | -7.3282 | 8.9353 | 8.5682 | 8.1904 | 7.5129 | 6.4425 | 5.1347 | 3.6831 | 1.9064 | -0.42048 | -6.5199 | -14.2804 | -18.4831 | -20.3834
|  | FERNDOWN | LW |  |  | 6.7147 | 6.3772 | 5.666 | 4.5924 | 3.4937 | 2.125 | 0.59612 | -1.2718 | -3.7505 | -10.349 | -19.0431 | -23.9792 | -26.2941 | 12.8215 | 12.5081 | 12.2001 | 11.6715 | 11.1514 | 10.5128 | 9.8683 | 8.6924 | 7.1202 | 2.9764 | -1.9577 | -4.9049 | -7.3282 | 8.9353 | 8.5682 | 8.1904 | 7.5129 | 6.4425 | 5.1347 | 3.6831 | 1.9064 | -0.42048 | -6.5199 | -14.2804 | -18.4831 | -20.3834
|  | FERNDOWN | ST |  |  | 6.7147 | 6.3772 | 5.666 | 4.5924 | 3.4937 | 2.125 | 0.59612 | -1.2718 | -3.7505 | -10.349 | -19.0431 | -23.9792 | -26.2941 | 12.8215 | 12.5081 | 12.2001 | 11.6715 | 11.1514 | 10.5128 | 9.8683 | 8.6924 | 7.1202 | 2.9764 | -1.9577 | -4.9049 | -7.3282 | 8.9353 | 8.5682 | 8.1904 | 7.5129 | 6.4425 | 5.1347 | 3.6831 | 1.9064 | -0.42048 | -6.5199 | -14.2804 | -18.4831 | -20.3834
|  | FERNDOWN | FS |  |  | 6.7147 | 6.3772 | 5.666 | 4.5924 | 3.4937 | 2.125 | 0.59612 | -1.2718 | -3.7505 | -10.349 | -19.0431 | -23.9792 | -26.2941 | 12.8215 | 12.5081 | 12.2001 | 11.6715 | 11.1514 | 10.5128 | 9.8683 | 8.6924 | 7.1202 | 2.9764 | -1.9577 | -4.9049 | -7.3282 | 8.9353 | 8.5682 | 8.1904 | 7.5129 | 6.4425 | 5.1347 | 3.6831 | 1.9064 | -0.42048 | -6.5199 | -14.2804 | -18.4831 | -20.3834
BRAMLEY (FLEE) | FERNHURST | FIVE OAKS | MINIMUM HEADROOM | TQ 10647 29057 | YES | 9.0436 | 8.4487 | 7.8221 | 6.9825 | 6.0977 | 5.55 | 4.9863 | 4.4664 | 3.8126 | 2.5092 | 1.1575 | 0.51706 | 0.25126 | 11.0816 | 10.7349 | 10.373 | 9.9445 | 9.4862 | 9.1737 | 8.8196 | 8.4648 | 8.0352 | 7.2647 | 6.441 | 6.0188 | 5.6791 | 9.7576 | 9.2628 | 8.7202 | 7.9924 | 7.2235 | 6.7269 | 6.2128 | 5.7303 | 5.1076 | 3.9388 | 2.7134 | 2.1442 | 1.9076
|  | FIVE OAKS | CT |  |  | 9.0436 | 8.4487 | 7.8221 | 6.9825 | 6.0977 | 5.55 | 4.9863 | 4.4664 | 3.8126 | 2.5092 | 1.1575 | 0.51706 | 0.25126 | 11.0816 | 10.7349 | 10.373 | 9.9445 | 9.4862 | 9.1737 | 8.8196 | 8.4648 | 8.0352 | 7.2647 | 6.441 | 6.0188 | 5.6791 | 9.7576 | 9.2628 | 8.7202 | 7.9924 | 7.2235 | 6.7269 | 6.2128 | 5.7303 | 5.1076 | 3.9388 | 2.7134 | 2.1442 | 1.9076
|  | FIVE OAKS | LW |  |  | 9.0436 | 8.4487 | 7.8221 | 6.9825 | 6.0977 | 5.55 | 4.9863 | 4.4664 | 3.8126 | 2.5092 | 1.1575 | 0.51706 | 0.25126 | 11.0816 | 10.7349 | 10.373 | 9.9445 | 9.4862 | 9.1737 | 8.8196 | 8.4648 | 8.0352 | 7.2647 | 6.441 | 6.0188 | 5.6791 | 9.7576 | 9.2628 | 8.7202 | 7.9924 | 7.2235 | 6.7269 | 6.2128 | 5.7303 | 5.1076 | 3.9388 | 2.7134 | 2.1442 | 1.9076
|  | FIVE OAKS | ST |  |  | 9.0436 | 8.4487 | 7.8221 | 6.9825 | 6.0977 | 5.55 | 4.9863 | 4.4664 | 3.8126 | 2.5092 | 1.1575 | 0.51706 | 0.25126 | 11.0816 | 10.7349 | 10.373 | 9.9445 | 9.4862 | 9.1737 | 8.8196 | 8.4648 | 8.0352 | 7.2647 | 6.441 | 6.0188 | 5.6791 | 9.7576 | 9.2628 | 8.7202 | 7.9924 | 7.2235 | 6.7269 | 6.2128 | 5.7303 | 5.1076 | 3.9388 | 2.7134 | 2.1442 | 1.9076
|  | FIVE OAKS | FS |  |  | 9.0436 | 8.4487 | 7.8221 | 6.9825 | 6.0977 | 5.55 | 4.9863 | 4.4664 | 3.8126 | 2.5092 | 1.1575 | 0.51706 | 0.25126 | 11.0816 | 10.7349 | 10.373 | 9.9445 | 9.4862 | 9.1737 | 8.8196 | 8.4648 | 8.0352 | 7.2647 | 6.441 | 6.0188 | 5.6791 | 9.7576 | 9.2628 | 8.7202 | 7.9924 | 7.2235 | 6.7269 | 6.2128 | 5.7303 | 5.1076 | 3.9388 | 2.7134 | 2.1442 | 1.9076
AMERSHAM | LOUDWATER BSP | FLACKWELL HEATH | MINIMUM HEADROOM | SU 90667 89318 | YES | 27.7087 | 27.3857 | 26.9948 | 26.4718 | 25.9142 | 25.3399 | 24.6883 | 23.8899 | 22.6481 | 19.906 | 15.5701 | 12.5845 | 11.0679 | 25.4308 | 25.2035 | 24.926 | 24.5981 | 24.2448 | 23.8693 | 23.4385 | 22.9009 | 22.1245 | 20.4662 | 17.9498 | 16.0566 | 14.4577 | 28.5259 | 28.2626 | 27.9482 | 27.4568 | 26.9294 | 26.3827 | 25.7601 | 24.9915 | 23.8097 | 21.2511 | 17.3301 | 14.6859 | 13.3623
|  | FLACKWELL HEATH | CT |  |  | 27.7087 | 27.3857 | 26.9948 | 26.4718 | 25.9142 | 25.3399 | 24.6883 | 23.8899 | 22.6481 | 19.906 | 15.5701 | 12.5845 | 11.0679 | 25.4308 | 25.2035 | 24.926 | 24.5981 | 24.2448 | 23.8693 | 23.4385 | 22.9009 | 22.1245 | 20.4662 | 17.9498 | 16.0566 | 14.4577 | 28.5259 | 28.2626 | 27.9482 | 27.4568 | 26.9294 | 26.3827 | 25.7601 | 24.9915 | 23.8097 | 21.2511 | 17.3301 | 14.6859 | 13.3623
|  | FLACKWELL HEATH | LW |  |  | 27.7087 | 27.3857 | 26.9948 | 26.4718 | 25.9142 | 25.3399 | 24.6883 | 23.8899 | 22.6481 | 19.906 | 15.5701 | 12.5845 | 11.0679 | 25.4308 | 25.2035 | 24.926 | 24.5981 | 24.2448 | 23.8693 | 23.4385 | 22.9009 | 22.1245 | 20.4662 | 17.9498 | 16.0566 | 14.4577 | 28.5259 | 28.2626 | 27.9482 | 27.4568 | 26.9294 | 26.3827 | 25.7601 | 24.9915 | 23.8097 | 21.2511 | 17.3301 | 14.6859 | 13.3623
|  | FLACKWELL HEATH | ST |  |  | 27.7087 | 27.3857 | 26.9948 | 26.4718 | 25.9142 | 25.3399 | 24.6883 | 23.8899 | 22.6481 | 19.906 | 15.5701 | 12.5845 | 11.0679 | 25.4308 | 25.2035 | 24.926 | 24.5981 | 24.2448 | 23.8693 | 23.4385 | 22.9009 | 22.1245 | 20.4662 | 17.9498 | 16.0566 | 14.4577 | 28.5259 | 28.2626 | 27.9482 | 27.4568 | 26.9294 | 26.3827 | 25.7601 | 24.9915 | 23.8097 | 21.2511 | 17.3301 | 14.6859 | 13.3623
|  | FLACKWELL HEATH | FS |  |  | 27.7087 | 27.3857 | 26.9948 | 26.4718 | 25.9142 | 25.3399 | 24.6883 | 23.8899 | 22.6481 | 19.906 | 15.5701 | 12.5845 | 11.0679 | 25.4308 | 25.2035 | 24.926 | 24.5981 | 24.2448 | 23.8693 | 23.4385 | 22.9009 | 22.1245 | 20.4662 | 17.9498 | 16.0566 | 14.4577 | 28.5259 | 28.2626 | 27.9482 | 27.4568 | 26.9294 | 26.3827 | 25.7601 | 24.9915 | 23.8097 | 21.2511 | 17.3301 | 14.6859 | 13.3623
NURSLING GSP | ROWNHAMS | FLETCHWOOD | MINIMUM HEADROOM | SU 33800 12142 | YES | 19.9774 | 19.453 | 18.7943 | 17.9398 | 16.8915 | 15.7264 | 14.4404 | 13.0103 | 10.9398 | 5.8973 | -0.90181 | -4.8818 | -6.5051 | 25.8505 | 25.4336 | 24.8746 | 24.2723 | 23.5324 | 22.6983 | 21.7642 | 20.7054 | 19.2649 | 16.2141 | 12.6294 | 10.4658 | 8.7817 | 21.8563 | 21.3358 | 20.6561 | 19.8495 | 18.8734 | 17.7812 | 16.5515 | 15.1661 | 13.1776 | 8.8012 | 3.3819 | 0.081699 | -1.3432
|  | FLETCHWOOD | CT |  |  | 19.9774 | 19.453 | 18.7943 | 17.9398 | 16.8915 | 15.7264 | 14.4404 | 13.0103 | 10.9398 | 5.8973 | -0.90181 | -4.8818 | -6.5051 | 25.8505 | 25.4336 | 24.8746 | 24.2723 | 23.5324 | 22.6983 | 21.7642 | 20.7054 | 19.2649 | 16.2141 | 12.6294 | 10.4658 | 8.7817 | 21.8563 | 21.3358 | 20.6561 | 19.8495 | 18.8734 | 17.7812 | 16.5515 | 15.1661 | 13.1776 | 8.8012 | 3.3819 | 0.081699 | -1.3432
|  | FLETCHWOOD | LW |  |  | 19.9774 | 19.453 | 18.7943 | 17.9398 | 16.8915 | 15.7264 | 14.4404 | 13.0103 | 10.9398 | 5.8973 | -0.90181 | -4.8818 | -6.5051 | 25.8505 | 25.4336 | 24.8746 | 24.2723 | 23.5324 | 22.6983 | 21.7642 | 20.7054 | 19.2649 | 16.2141 | 12.6294 | 10.4658 | 8.7817 | 21.8563 | 21.3358 | 20.6561 | 19.8495 | 18.8734 | 17.7812 | 16.5515 | 15.1661 | 13.1776 | 8.8012 | 3.3819 | 0.081699 | -1.3432
|  | FLETCHWOOD | ST |  |  | 19.9774 | 19.453 | 18.7943 | 17.9398 | 16.8915 | 15.7264 | 14.4404 | 13.0103 | 10.9398 | 5.8973 | -0.90181 | -4.8818 | -6.5051 | 25.8505 | 25.4336 | 24.8746 | 24.2723 | 23.5324 | 22.6983 | 21.7642 | 20.7054 | 19.2649 | 16.2141 | 12.6294 | 10.4658 | 8.7817 | 21.8563 | 21.3358 | 20.6561 | 19.8495 | 18.8734 | 17.7812 | 16.5515 | 15.1661 | 13.1776 | 8.8012 | 3.3819 | 0.081699 | -1.3432
|  | FLETCHWOOD | FS |  |  | 19.9774 | 19.453 | 18.7943 | 17.9398 | 16.8915 | 15.7264 | 14.4404 | 13.0103 | 10.9398 | 5.8973 | -0.90181 | -4.8818 | -6.5051 | 25.8505 | 25.4336 | 24.8746 | 24.2723 | 23.5324 | 22.6983 | 21.7642 | 20.7054 | 19.2649 | 16.2141 | 12.6294 | 10.4658 | 8.7817 | 21.8563 | 21.3358 | 20.6561 | 19.8495 | 18.8734 | 17.7812 | 16.5515 | 15.1661 | 13.1776 | 8.8012 | 3.3819 | 0.081699 | -1.3432
MANNINGTON GSP | MANNINGTON BSP | FORDINGBRIDGE | MINIMUM HEADROOM | SU 14069 15523 | YES | 12.0495 | 11.7213 | 11.3147 | 10.8617 | 10.3126 | 9.6509 | 8.8815 | 8.1005 | 7.0807 | 4.5657 | 1.2904 | -0.82799 | -1.7156 | 12.1834 | 12.0058 | 11.837 | 11.6319 | 11.4042 | 11.1431 | 10.8316 | 10.4812 | 9.8602 | 8.4224 | 6.7523 | 5.7413 | 5.0795 | 13.2483 | 12.9516 | 12.5855 | 12.1723 | 11.6807 | 11.0939 | 10.408 | 9.7036 | 8.7725 | 6.5143 | 3.6433 | 1.8843 | 1.1005
|  | FORDINGBRIDGE | CT |  |  | 12.0495 | 11.7213 | 11.3147 | 10.8617 | 10.3126 | 9.6509 | 8.8815 | 8.1005 | 7.0807 | 4.5657 | 1.2904 | -0.82799 | -1.7156 | 12.1834 | 12.0058 | 11.837 | 11.6319 | 11.4042 | 11.1431 | 10.8316 | 10.4812 | 9.8602 | 8.4224 | 6.7523 | 5.7413 | 5.0795 | 13.2483 | 12.9516 | 12.5855 | 12.1723 | 11.6807 | 11.0939 | 10.408 | 9.7036 | 8.7725 | 6.5143 | 3.6433 | 1.8843 | 1.1005
|  | FORDINGBRIDGE | LW |  |  | 12.0495 | 11.7213 | 11.3147 | 10.8617 | 10.3126 | 9.6509 | 8.8815 | 8.1005 | 7.0807 | 4.5657 | 1.2904 | -0.82799 | -1.7156 | 12.1834 | 12.0058 | 11.837 | 11.6319 | 11.4042 | 11.1431 | 10.8316 | 10.4812 | 9.8602 | 8.4224 | 6.7523 | 5.7413 | 5.0795 | 13.2483 | 12.9516 | 12.5855 | 12.1723 | 11.6807 | 11.0939 | 10.408 | 9.7036 | 8.7725 | 6.5143 | 3.6433 | 1.8843 | 1.1005
|  | FORDINGBRIDGE | ST |  |  | 12.0495 | 11.7213 | 11.3147 | 10.8617 | 10.3126 | 9.6509 | 8.8815 | 8.1005 | 7.0807 | 4.5657 | 1.2904 | -0.82799 | -1.7156 | 12.1834 | 12.0058 | 11.837 | 11.6319 | 11.4042 | 11.1431 | 10.8316 | 10.4812 | 9.8602 | 8.4224 | 6.7523 | 5.7413 | 5.0795 | 13.2483 | 12.9516 | 12.5855 | 12.1723 | 11.6807 | 11.0939 | 10.408 | 9.7036 | 8.7725 | 6.5143 | 3.6433 | 1.8843 | 1.1005
|  | FORDINGBRIDGE | FS |  |  | 12.0495 | 11.7213 | 11.3147 | 10.8617 | 10.3126 | 9.6509 | 8.8815 | 8.1005 | 7.0807 | 4.5657 | 1.2904 | -0.82799 | -1.7156 | 12.1834 | 12.0058 | 11.837 | 11.6319 | 11.4042 | 11.1431 | 10.8316 | 10.4812 | 9.8602 | 8.4224 | 6.7523 | 5.7413 | 5.0795 | 13.2483 | 12.9516 | 12.5855 | 12.1723 | 11.6807 | 11.0939 | 10.408 | 9.7036 | 8.7725 | 6.5143 | 3.6433 | 1.8843 | 1.1005
LOVEDEAN GSP | PORTSMOUTH BSP | FRATTON PARK | MINIMUM HEADROOM | SU 66139 00180 | YES | 10.2896 | 9.6635 | 8.8085 | 7.6946 | 6.4892 | 5.2585 | 3.957 | 2.4909 | 0.32704 | -6.818 | -17.9217 | -25.5009 | -29.8296 | 17.0007 | 16.4279 | 15.6763 | 14.7532 | 13.7479 | 12.6706 | 11.5004 | 10.1647 | 8.4498 | 2.49 | -8.4871 | -21.5072 | -40.1367 | 11.9837 | 11.4301 | 10.6496 | 9.641 | 8.5478 | 7.4215 | 6.2232 | 4.8644 | 2.8737 | -3.7085 | -13.7256 | -20.275 | -23.7897
|  | FRATTON PARK | CT |  |  | 10.2896 | 9.6635 | 8.8085 | 7.6946 | 6.4892 | 5.2585 | 3.957 | 2.4909 | 0.32704 | -6.818 | -17.9217 | -25.5009 | -29.8296 | 17.0007 | 16.4279 | 15.6763 | 14.7532 | 13.7479 | 12.6706 | 11.5004 | 10.1647 | 8.4498 | 2.49 | -8.4871 | -21.5072 | -40.1367 | 11.9837 | 11.4301 | 10.6496 | 9.641 | 8.5478 | 7.4215 | 6.2232 | 4.8644 | 2.8737 | -3.7085 | -13.7256 | -20.275 | -23.7897
|  | FRATTON PARK | LW |  |  | 10.2896 | 9.6635 | 8.8085 | 7.6946 | 6.4892 | 5.2585 | 3.957 | 2.4909 | 0.32704 | -6.818 | -17.9217 | -25.5009 | -29.8296 | 17.0007 | 16.4279 | 15.6763 | 14.7532 | 13.7479 | 12.6706 | 11.5004 | 10.1647 | 8.4498 | 2.49 | -8.4871 | -21.5072 | -40.1367 | 11.9837 | 11.4301 | 10.6496 | 9.641 | 8.5478 | 7.4215 | 6.2232 | 4.8644 | 2.8737 | -3.7085 | -13.7256 | -20.275 | -23.7897
|  | FRATTON PARK | ST |  |  | 10.2896 | 9.6635 | 8.8085 | 7.6946 | 6.4892 | 5.2585 | 3.957 | 2.4909 | 0.32704 | -6.818 | -17.9217 | -25.5009 | -29.8296 | 17.0007 | 16.4279 | 15.6763 | 14.7532 | 13.7479 | 12.6706 | 11.5004 | 10.1647 | 8.4498 | 2.49 | -8.4871 | -21.5072 | -40.1367 | 11.9837 | 11.4301 | 10.6496 | 9.641 | 8.5478 | 7.4215 | 6.2232 | 4.8644 | 2.8737 | -3.7085 | -13.7256 | -20.275 | -23.7897
|  | FRATTON PARK | FS |  |  | 10.2896 | 9.6635 | 8.8085 | 7.6946 | 6.4892 | 5.2585 | 3.957 | 2.4909 | 0.32704 | -6.818 | -17.9217 | -25.5009 | -29.8296 | 17.0007 | 16.4279 | 15.6763 | 14.7532 | 13.7479 | 12.6706 | 11.5004 | 10.1647 | 8.4498 | 2.49 | -8.4871 | -21.5072 | -40.1367 | 11.9837 | 11.4301 | 10.6496 | 9.641 | 8.5478 | 7.4215 | 6.2232 | 4.8644 | 2.8737 | -3.7085 | -13.7256 | -20.275 | -23.7897
COWLEY GSP | OXFORD BSP | FRENCHAY ROAD | MINIMUM HEADROOM | SP 50426 08256 | YES | 9.3393 | 8.9852 | 8.6521 | 8.2943 | 7.9327 | 7.5846 | 7.1981 | 6.6871 | 5.8885 | 3.5801 | -0.39876 | -3.4247 | -5.2375 | 11.7906 | 11.5199 | 11.2508 | 10.9759 | 10.6876 | 10.3841 | 10.0443 | 9.6159 | 9.0448 | 7.2505 | 3.8732 | 0.19748 | -4.6779 | 10.2214 | 9.9141 | 9.6184 | 9.2935 | 8.9617 | 8.6398 | 8.2827 | 7.8171 | 7.0925 | 4.965 | 1.4098 | -1.1171 | -2.5827
|  | FRENCHAY ROAD | CT |  |  | 9.3393 | 8.9852 | 8.6521 | 8.2943 | 7.9327 | 7.5846 | 7.1981 | 6.6871 | 5.8885 | 3.5801 | -0.39876 | -3.4247 | -5.2375 | 11.7906 | 11.5199 | 11.2508 | 10.9759 | 10.6876 | 10.3841 | 10.0443 | 9.6159 | 9.0448 | 7.2505 | 3.8732 | 0.19748 | -4.6779 | 10.2214 | 9.9141 | 9.6184 | 9.2935 | 8.9617 | 8.6398 | 8.2827 | 7.8171 | 7.0925 | 4.965 | 1.4098 | -1.1171 | -2.5827
|  | FRENCHAY ROAD | LW |  |  | 9.3393 | 8.9852 | 8.6521 | 8.2943 | 7.9327 | 7.5846 | 7.1981 | 6.6871 | 5.8885 | 3.5801 | -0.39876 | -3.4247 | -5.2375 | 11.7906 | 11.5199 | 11.2508 | 10.9759 | 10.6876 | 10.3841 | 10.0443 | 9.6159 | 9.0448 | 7.2505 | 3.8732 | 0.19748 | -4.6779 | 10.2214 | 9.9141 | 9.6184 | 9.2935 | 8.9617 | 8.6398 | 8.2827 | 7.8171 | 7.0925 | 4.965 | 1.4098 | -1.1171 | -2.5827
|  | FRENCHAY ROAD | ST |  |  | 9.3393 | 8.9852 | 8.6521 | 8.2943 | 7.9327 | 7.5846 | 7.1981 | 6.6871 | 5.8885 | 3.5801 | -0.39876 | -3.4247 | -5.2375 | 11.7906 | 11.5199 | 11.2508 | 10.9759 | 10.6876 | 10.3841 | 10.0443 | 9.6159 | 9.0448 | 7.2505 | 3.8732 | 0.19748 | -4.6779 | 10.2214 | 9.9141 | 9.6184 | 9.2935 | 8.9617 | 8.6398 | 8.2827 | 7.8171 | 7.0925 | 4.965 | 1.4098 | -1.1171 | -2.5827
|  | FRENCHAY ROAD | FS |  |  | 9.3393 | 8.9852 | 8.6521 | 8.2943 | 7.9327 | 7.5846 | 7.1981 | 6.6871 | 5.8885 | 3.5801 | -0.39876 | -3.4247 | -5.2375 | 11.7906 | 11.5199 | 11.2508 | 10.9759 | 10.6876 | 10.3841 | 10.0443 | 9.6159 | 9.0448 | 7.2505 | 3.8732 | 0.19748 | -4.6779 | 10.2214 | 9.9141 | 9.6184 | 9.2935 | 8.9617 | 8.6398 | 8.2827 | 7.8171 | 7.0925 | 4.965 | 1.4098 | -1.1171 | -2.5827
FAWLEY GSP | COWES & WOOTTON COMMON BSP | FRESHWATER | MINIMUM HEADROOM | SZ 34325 86965 | YES | 12.0507 | 11.8302 | 11.4924 | 11.0337 | 10.6118 | 10.1476 | 9.6471 | 9.0935 | 8.238 | 5.568 | 1.4853 | -1.4974 | -2.5287 | 12.5466 | 12.4185 | 12.1986 | 11.9414 | 11.7011 | 11.4328 | 11.1413 | 10.8081 | 10.3366 | 8.8411 | 7.0861 | 5.8489 | 5.1407 | 11.1047 | 10.9077 | 10.5948 | 10.1795 | 9.7918 | 9.3641 | 8.9031 | 8.3903 | 7.6058 | 5.1531 | 1.6945 | -0.75279 | -1.652
|  | FRESHWATER | CT |  |  | 12.0507 | 11.8302 | 11.4924 | 11.0337 | 10.6118 | 10.1476 | 9.6471 | 9.0935 | 8.238 | 5.568 | 1.4853 | -1.4974 | -2.5287 | 12.5466 | 12.4185 | 12.1986 | 11.9414 | 11.7011 | 11.4328 | 11.1413 | 10.8081 | 10.3366 | 8.8411 | 7.0861 | 5.8489 | 5.1407 | 11.1047 | 10.9077 | 10.5948 | 10.1795 | 9.7918 | 9.3641 | 8.9031 | 8.3903 | 7.6058 | 5.1531 | 1.6945 | -0.75279 | -1.652
|  | FRESHWATER | LW |  |  | 12.0507 | 11.8302 | 11.4924 | 11.0337 | 10.6118 | 10.1476 | 9.6471 | 9.0935 | 8.238 | 5.568 | 1.4853 | -1.4974 | -2.5287 | 12.5466 | 12.4185 | 12.1986 | 11.9414 | 11.7011 | 11.4328 | 11.1413 | 10.8081 | 10.3366 | 8.8411 | 7.0861 | 5.8489 | 5.1407 | 11.1047 | 10.9077 | 10.5948 | 10.1795 | 9.7918 | 9.3641 | 8.9031 | 8.3903 | 7.6058 | 5.1531 | 1.6945 | -0.75279 | -1.652
|  | FRESHWATER | ST |  |  | 12.0507 | 11.8302 | 11.4924 | 11.0337 | 10.6118 | 10.1476 | 9.6471 | 9.0935 | 8.238 | 5.568 | 1.4853 | -1.4974 | -2.5287 | 12.5466 | 12.4185 | 12.1986 | 11.9414 | 11.7011 | 11.4328 | 11.1413 | 10.8081 | 10.3366 | 8.8411 | 7.0861 | 5.8489 | 5.1407 | 11.1047 | 10.9077 | 10.5948 | 10.1795 | 9.7918 | 9.3641 | 8.9031 | 8.3903 | 7.6058 | 5.1531 | 1.6945 | -0.75279 | -1.652
|  | FRESHWATER | FS |  |  | 12.0507 | 11.8302 | 11.4924 | 11.0337 | 10.6118 | 10.1476 | 9.6471 | 9.0935 | 8.238 | 5.568 | 1.4853 | -1.4974 | -2.5287 | 12.5466 | 12.4185 | 12.1986 | 11.9414 | 11.7011 | 11.4328 | 11.1413 | 10.8081 | 10.3366 | 8.8411 | 7.0861 | 5.8489 | 5.1407 | 11.1047 | 10.9077 | 10.5948 | 10.1795 | 9.7918 | 9.3641 | 8.9031 | 8.3903 | 7.6058 | 5.1531 | 1.6945 | -0.75279 | -1.652
BRAMLEY (FLEE) | CAMBERLEY RESERVE | FRIMLEY | MINIMUM HEADROOM | SU 87745 57942 | YES | 17.8372 | 17.3816 | 16.772 | 16.0221 | 15.2172 | 14.3435 | 13.3553 | 12.1489 | 10.3269 | 6.3817 | -0.1185 | -4.5846 | -7.0947 | 18.3091 | 17.9379 | 17.4641 | 16.9246 | 16.3382 | 15.6817 | 14.9314 | 13.9981 | 12.7171 | 10.0856 | 5.9877 | 2.8625 | -0.18547 | 19.9414 | 19.4626 | 18.859 | 18.1474 | 17.3822 | 16.5462 | 15.5975 | 14.4321 | 12.6931 | 9.008 | 3.1366 | -0.75076 | -2.7915
|  | FRIMLEY | CT |  |  | 17.8372 | 17.3816 | 16.772 | 16.0221 | 15.2172 | 14.3435 | 13.3553 | 12.1489 | 10.3269 | 6.3817 | -0.1185 | -4.5846 | -7.0947 | 18.3091 | 17.9379 | 17.4641 | 16.9246 | 16.3382 | 15.6817 | 14.9314 | 13.9981 | 12.7171 | 10.0856 | 5.9877 | 2.8625 | -0.18547 | 19.9414 | 19.4626 | 18.859 | 18.1474 | 17.3822 | 16.5462 | 15.5975 | 14.4321 | 12.6931 | 9.008 | 3.1366 | -0.75076 | -2.7915
|  | FRIMLEY | LW |  |  | 17.8372 | 17.3816 | 16.772 | 16.0221 | 15.2172 | 14.3435 | 13.3553 | 12.1489 | 10.3269 | 6.3817 | -0.1185 | -4.5846 | -7.0947 | 18.3091 | 17.9379 | 17.4641 | 16.9246 | 16.3382 | 15.6817 | 14.9314 | 13.9981 | 12.7171 | 10.0856 | 5.9877 | 2.8625 | -0.18547 | 19.9414 | 19.4626 | 18.859 | 18.1474 | 17.3822 | 16.5462 | 15.5975 | 14.4321 | 12.6931 | 9.008 | 3.1366 | -0.75076 | -2.7915
|  | FRIMLEY | ST |  |  | 17.8372 | 17.3816 | 16.772 | 16.0221 | 15.2172 | 14.3435 | 13.3553 | 12.1489 | 10.3269 | 6.3817 | -0.1185 | -4.5846 | -7.0947 | 18.3091 | 17.9379 | 17.4641 | 16.9246 | 16.3382 | 15.6817 | 14.9314 | 13.9981 | 12.7171 | 10.0856 | 5.9877 | 2.8625 | -0.18547 | 19.9414 | 19.4626 | 18.859 | 18.1474 | 17.3822 | 16.5462 | 15.5975 | 14.4321 | 12.6931 | 9.008 | 3.1366 | -0.75076 | -2.7915
|  | FRIMLEY | FS |  |  | 17.8372 | 17.3816 | 16.772 | 16.0221 | 15.2172 | 14.3435 | 13.3553 | 12.1489 | 10.3269 | 6.3817 | -0.1185 | -4.5846 | -7.0947 | 18.3091 | 17.9379 | 17.4641 | 16.9246 | 16.3382 | 15.6817 | 14.9314 | 13.9981 | 12.7171 | 10.0856 | 5.9877 | 2.8625 | -0.18547 | 19.9414 | 19.4626 | 18.859 | 18.1474 | 17.3822 | 16.5462 | 15.5975 | 14.4321 | 12.6931 | 9.008 | 3.1366 | -0.75076 | -2.7915
MELKSHAM GSP | FROME BSP | FROME | MINIMUM HEADROOM | ST 78850 48051 | YES | 45.9299 | 44.6602 | 42.9558 | 41.0773 | 39.2583 | 37.5098 | 35.643 | 33.5662 | 30.5953 | 22.5537 | 11.9602 | 5.9369 | 3.3593 | 45.7547 | 44.906 | 43.7733 | 42.5924 | 41.4571 | 40.3166 | 39.0824 | 37.6735 | 35.746 | 30.6875 | 24.5944 | 20.6679 | 17.1496 | 44.4205 | 43.373 | 41.9988 | 40.4054 | 38.8709 | 37.3791 | 35.7338 | 33.7967 | 31.0172 | 23.5951 | 14.1045 | 8.603 | 6.0613
|  | FROME | CT |  |  | 45.9299 | 44.6602 | 42.9558 | 41.0773 | 39.2583 | 37.5098 | 35.643 | 33.5662 | 30.5953 | 22.5537 | 11.9602 | 5.9369 | 3.3593 | 45.7547 | 44.906 | 43.7733 | 42.5924 | 41.4571 | 40.3166 | 39.0824 | 37.6735 | 35.746 | 30.6875 | 24.5944 | 20.6679 | 17.1496 | 44.4205 | 43.373 | 41.9988 | 40.4054 | 38.8709 | 37.3791 | 35.7338 | 33.7967 | 31.0172 | 23.5951 | 14.1045 | 8.603 | 6.0613
|  | FROME | LW |  |  | 45.9299 | 44.6602 | 42.9558 | 41.0773 | 39.2583 | 37.5098 | 35.643 | 33.5662 | 30.5953 | 22.5537 | 11.9602 | 5.9369 | 3.3593 | 45.7547 | 44.906 | 43.7733 | 42.5924 | 41.4571 | 40.3166 | 39.0824 | 37.6735 | 35.746 | 30.6875 | 24.5944 | 20.6679 | 17.1496 | 44.4205 | 43.373 | 41.9988 | 40.4054 | 38.8709 | 37.3791 | 35.7338 | 33.7967 | 31.0172 | 23.5951 | 14.1045 | 8.603 | 6.0613
|  | FROME | ST |  |  | 45.9299 | 44.6602 | 42.9558 | 41.0773 | 39.2583 | 37.5098 | 35.643 | 33.5662 | 30.5953 | 22.5537 | 11.9602 | 5.9369 | 3.3593 | 45.7547 | 44.906 | 43.7733 | 42.5924 | 41.4571 | 40.3166 | 39.0824 | 37.6735 | 35.746 | 30.6875 | 24.5944 | 20.6679 | 17.1496 | 44.4205 | 43.373 | 41.9988 | 40.4054 | 38.8709 | 37.3791 | 35.7338 | 33.7967 | 31.0172 | 23.5951 | 14.1045 | 8.603 | 6.0613
|  | FROME | FS |  |  | 45.9299 | 44.6602 | 42.9558 | 41.0773 | 39.2583 | 37.5098 | 35.643 | 33.5662 | 30.5953 | 22.5537 | 11.9602 | 5.9369 | 3.3593 | 45.7547 | 44.906 | 43.7733 | 42.5924 | 41.4571 | 40.3166 | 39.0824 | 37.6735 | 35.746 | 30.6875 | 24.5944 | 20.6679 | 17.1496 | 44.4205 | 43.373 | 41.9988 | 40.4054 | 38.8709 | 37.3791 | 35.7338 | 33.7967 | 31.0172 | 23.5951 | 14.1045 | 8.603 | 6.0613
COWLEY GSP | HIGH WYCOMBE BSP | FRYERS LANE | MINIMUM HEADROOM | SU 84935 93873 | YES | 10.4312 | 9.9622 | 9.3609 | 8.6082 | 7.8529 | 7.0649 | 6.1897 | 5.1598 | 3.5149 | -0.62548 | -6.8629 | -10.8896 | -12.8119 | 15.1381 | 14.7597 | 14.2708 | 13.7188 | 13.1468 | 12.5268 | 11.8281 | 10.9894 | 9.7966 | 6.7678 | 2.0015 | -2.5837 | -8.3299 | 12.425 | 12.0154 | 11.49 | 10.8146 | 10.1329 | 9.4224 | 8.6353 | 7.7118 | 6.2264 | 2.4461 | -3.3609 | -7.139 | -8.8196
|  | FRYERS LANE | CT |  |  | 10.4312 | 9.9622 | 9.3609 | 8.6082 | 7.8529 | 7.0649 | 6.1897 | 5.1598 | 3.5149 | -0.62548 | -6.8629 | -10.8896 | -12.8119 | 15.1381 | 14.7597 | 14.2708 | 13.7188 | 13.1468 | 12.5268 | 11.8281 | 10.9894 | 9.7966 | 6.7678 | 2.0015 | -2.5837 | -8.3299 | 12.425 | 12.0154 | 11.49 | 10.8146 | 10.1329 | 9.4224 | 8.6353 | 7.7118 | 6.2264 | 2.4461 | -3.3609 | -7.139 | -8.8196
|  | FRYERS LANE | LW |  |  | 10.4312 | 9.9622 | 9.3609 | 8.6082 | 7.8529 | 7.0649 | 6.1897 | 5.1598 | 3.5149 | -0.62548 | -6.8629 | -10.8896 | -12.8119 | 15.1381 | 14.7597 | 14.2708 | 13.7188 | 13.1468 | 12.5268 | 11.8281 | 10.9894 | 9.7966 | 6.7678 | 2.0015 | -2.5837 | -8.3299 | 12.425 | 12.0154 | 11.49 | 10.8146 | 10.1329 | 9.4224 | 8.6353 | 7.7118 | 6.2264 | 2.4461 | -3.3609 | -7.139 | -8.8196
|  | FRYERS LANE | ST |  |  | 10.4312 | 9.9622 | 9.3609 | 8.6082 | 7.8529 | 7.0649 | 6.1897 | 5.1598 | 3.5149 | -0.62548 | -6.8629 | -10.8896 | -12.8119 | 15.1381 | 14.7597 | 14.2708 | 13.7188 | 13.1468 | 12.5268 | 11.8281 | 10.9894 | 9.7966 | 6.7678 | 2.0015 | -2.5837 | -8.3299 | 12.425 | 12.0154 | 11.49 | 10.8146 | 10.1329 | 9.4224 | 8.6353 | 7.7118 | 6.2264 | 2.4461 | -3.3609 | -7.139 | -8.8196
|  | FRYERS LANE | FS |  |  | 10.4312 | 9.9622 | 9.3609 | 8.6082 | 7.8529 | 7.0649 | 6.1897 | 5.1598 | 3.5149 | -0.62548 | -6.8629 | -10.8896 | -12.8119 | 15.1381 | 14.7597 | 14.2708 | 13.7188 | 13.1468 | 12.5268 | 11.8281 | 10.9894 | 9.7966 | 6.7678 | 2.0015 | -2.5837 | -8.3299 | 12.425 | 12.0154 | 11.49 | 10.8146 | 10.1329 | 9.4224 | 8.6353 | 7.7118 | 6.2264 | 2.4461 | -3.3609 | -7.139 | -8.8196
COWLEY GSP | DRAYTON BSP | FULSCOT | MINIMUM HEADROOM | SU 54413 89511 | NO | 5.5557 | 4.6561 | 3.6191 | 2.4942 | 1.1815 | -0.17102 | -1.5976 | -2.9969 | -4.7832 | -8.8887 | -13.9007 | -17.1109 | -18.6358 | 10.3913 | 9.8375 | 9.1949 | 8.5361 | 7.7751 | 6.9775 | 6.1258 | 5.2584 | 4.158 | 1.6314 | -1.2682 | -3.2792 | -5.0312 | 7.4181 | 6.6549 | 5.7615 | 4.7849 | 3.6509 | 2.4752 | 1.2256 | -0.020991 | -1.6412 | -5.3821 | -9.882 | -12.6644 | -13.9493
|  | FULSCOT | CT |  |  | 5.5557 | 4.6561 | 3.6191 | 2.4942 | 1.1815 | -0.17102 | -1.5976 | -2.9969 | -4.7832 | -8.8887 | -13.9007 | -17.1109 | -18.6358 | 10.3913 | 9.8375 | 9.1949 | 8.5361 | 7.7751 | 6.9775 | 6.1258 | 5.2584 | 4.158 | 1.6314 | -1.2682 | -3.2792 | -5.0312 | 7.4181 | 6.6549 | 5.7615 | 4.7849 | 3.6509 | 2.4752 | 1.2256 | -0.020991 | -1.6412 | -5.3821 | -9.882 | -12.6644 | -13.9493
|  | FULSCOT | LW |  |  | 5.5557 | 4.6561 | 3.6191 | 2.4942 | 1.1815 | -0.17102 | -1.5976 | -2.9969 | -4.7832 | -8.8887 | -13.9007 | -17.1109 | -18.6358 | 10.3913 | 9.8375 | 9.1949 | 8.5361 | 7.7751 | 6.9775 | 6.1258 | 5.2584 | 4.158 | 1.6314 | -1.2682 | -3.2792 | -5.0312 | 7.4181 | 6.6549 | 5.7615 | 4.7849 | 3.6509 | 2.4752 | 1.2256 | -0.020991 | -1.6412 | -5.3821 | -9.882 | -12.6644 | -13.9493
|  | FULSCOT | ST |  |  | 5.5557 | 4.6561 | 3.6191 | 2.4942 | 1.1815 | -0.17102 | -1.5976 | -2.9969 | -4.7832 | -8.8887 | -13.9007 | -17.1109 | -18.6358 | 10.3913 | 9.8375 | 9.1949 | 8.5361 | 7.7751 | 6.9775 | 6.1258 | 5.2584 | 4.158 | 1.6314 | -1.2682 | -3.2792 | -5.0312 | 7.4181 | 6.6549 | 5.7615 | 4.7849 | 3.6509 | 2.4752 | 1.2256 | -0.020991 | -1.6412 | -5.3821 | -9.882 | -12.6644 | -13.9493
|  | FULSCOT | FS |  |  | 5.5557 | 4.6561 | 3.6191 | 2.4942 | 1.1815 | -0.17102 | -1.5976 | -2.9969 | -4.7832 | -8.8887 | -13.9007 | -17.1109 | -18.6358 | 10.3913 | 9.8375 | 9.1949 | 8.5361 | 7.7751 | 6.9775 | 6.1258 | 5.2584 | 4.158 | 1.6314 | -1.2682 | -3.2792 | -5.0312 | 7.4181 | 6.6549 | 5.7615 | 4.7849 | 3.6509 | 2.4752 | 1.2256 | -0.020991 | -1.6412 | -5.3821 | -9.882 | -12.6644 | -13.9493
COWLEY GSP | WITNEY BSP | FYFIELD | MINIMUM HEADROOM | SU 42256 99551 | NO | 9.7971 | 9.4938 | 9.0713 | 8.5302 | 7.9662 | 7.3887 | 6.7228 | 6.0569 | 5.2806 | 3.7031 | 0.95903 | -0.91984 | -1.6251 | 10.9029 | 10.699 | 10.4267 | 10.1184 | 9.7949 | 9.4559 | 9.0535 | 8.6216 | 8.1302 | 7.3151 | 6.0574 | 5.1646 | 4.576 | 10.7838 | 10.511 | 10.1399 | 9.6656 | 9.1699 | 8.6593 | 8.0673 | 7.4626 | 6.7454 | 5.3264 | 2.8896 | 1.2385 | 0.64587
|  | FYFIELD | CT |  |  | 9.7971 | 9.4938 | 9.0713 | 8.5302 | 7.9662 | 7.3887 | 6.7228 | 6.0569 | 5.2806 | 3.7031 | 0.95903 | -0.91984 | -1.6251 | 10.9029 | 10.699 | 10.4267 | 10.1184 | 9.7949 | 9.4559 | 9.0535 | 8.6216 | 8.1302 | 7.3151 | 6.0574 | 5.1646 | 4.576 | 10.7838 | 10.511 | 10.1399 | 9.6656 | 9.1699 | 8.6593 | 8.0673 | 7.4626 | 6.7454 | 5.3264 | 2.8896 | 1.2385 | 0.64587
|  | FYFIELD | LW |  |  | 9.7971 | 9.4938 | 9.0713 | 8.5302 | 7.9662 | 7.3887 | 6.7228 | 6.0569 | 5.2806 | 3.7031 | 0.95903 | -0.91984 | -1.6251 | 10.9029 | 10.699 | 10.4267 | 10.1184 | 9.7949 | 9.4559 | 9.0535 | 8.6216 | 8.1302 | 7.3151 | 6.0574 | 5.1646 | 4.576 | 10.7838 | 10.511 | 10.1399 | 9.6656 | 9.1699 | 8.6593 | 8.0673 | 7.4626 | 6.7454 | 5.3264 | 2.8896 | 1.2385 | 0.64587
|  | FYFIELD | ST |  |  | 9.7971 | 9.4938 | 9.0713 | 8.5302 | 7.9662 | 7.3887 | 6.7228 | 6.0569 | 5.2806 | 3.7031 | 0.95903 | -0.91984 | -1.6251 | 10.9029 | 10.699 | 10.4267 | 10.1184 | 9.7949 | 9.4559 | 9.0535 | 8.6216 | 8.1302 | 7.3151 | 6.0574 | 5.1646 | 4.576 | 10.7838 | 10.511 | 10.1399 | 9.6656 | 9.1699 | 8.6593 | 8.0673 | 7.4626 | 6.7454 | 5.3264 | 2.8896 | 1.2385 | 0.64587
|  | FYFIELD | FS |  |  | 9.7971 | 9.4938 | 9.0713 | 8.5302 | 7.9662 | 7.3887 | 6.7228 | 6.0569 | 5.2806 | 3.7031 | 0.95903 | -0.91984 | -1.6251 | 10.9029 | 10.699 | 10.4267 | 10.1184 | 9.7949 | 9.4559 | 9.0535 | 8.6216 | 8.1302 | 7.3151 | 6.0574 | 5.1646 | 4.576 | 10.7838 | 10.511 | 10.1399 | 9.6656 | 9.1699 | 8.6593 | 8.0673 | 7.4626 | 6.7454 | 5.3264 | 2.8896 | 1.2385 | 0.64587
LOVEDEAN GSP | HAVANT | GABLE HEAD | MINIMUM HEADROOM | SZ 72204 99904 | YES | 25.1262 | 24.5769 | 23.8256 | 23.1724 | 22.4697 | 21.6023 | 20.6354 | 19.6393 | 18.1 | 14.5759 | 9.7737 | 6.3797 | 4.7195 | 24.9698 | 24.6161 | 24.1154 | 23.6949 | 23.2405 | 22.6861 | 22.0649 | 21.3973 | 20.4076 | 18.2391 | 15.6855 | 13.8385 | 12.4066 | 23.8274 | 23.3477 | 22.6739 | 22.0705 | 21.4214 | 20.629 | 19.7448 | 18.8181 | 17.3791 | 14.1093 | 9.8039 | 6.8268 | 5.3852
|  | GABLE HEAD | CT |  |  | 25.1262 | 24.5769 | 23.8256 | 23.1724 | 22.4697 | 21.6023 | 20.6354 | 19.6393 | 18.1 | 14.5759 | 9.7737 | 6.3797 | 4.7195 | 24.9698 | 24.6161 | 24.1154 | 23.6949 | 23.2405 | 22.6861 | 22.0649 | 21.3973 | 20.4076 | 18.2391 | 15.6855 | 13.8385 | 12.4066 | 23.8274 | 23.3477 | 22.6739 | 22.0705 | 21.4214 | 20.629 | 19.7448 | 18.8181 | 17.3791 | 14.1093 | 9.8039 | 6.8268 | 5.3852
|  | GABLE HEAD | LW |  |  | 25.1262 | 24.5769 | 23.8256 | 23.1724 | 22.4697 | 21.6023 | 20.6354 | 19.6393 | 18.1 | 14.5759 | 9.7737 | 6.3797 | 4.7195 | 24.9698 | 24.6161 | 24.1154 | 23.6949 | 23.2405 | 22.6861 | 22.0649 | 21.3973 | 20.4076 | 18.2391 | 15.6855 | 13.8385 | 12.4066 | 23.8274 | 23.3477 | 22.6739 | 22.0705 | 21.4214 | 20.629 | 19.7448 | 18.8181 | 17.3791 | 14.1093 | 9.8039 | 6.8268 | 5.3852
|  | GABLE HEAD | ST |  |  | 25.1262 | 24.5769 | 23.8256 | 23.1724 | 22.4697 | 21.6023 | 20.6354 | 19.6393 | 18.1 | 14.5759 | 9.7737 | 6.3797 | 4.7195 | 24.9698 | 24.6161 | 24.1154 | 23.6949 | 23.2405 | 22.6861 | 22.0649 | 21.3973 | 20.4076 | 18.2391 | 15.6855 | 13.8385 | 12.4066 | 23.8274 | 23.3477 | 22.6739 | 22.0705 | 21.4214 | 20.629 | 19.7448 | 18.8181 | 17.3791 | 14.1093 | 9.8039 | 6.8268 | 5.3852
|  | GABLE HEAD | FS |  |  | 25.1262 | 24.5769 | 23.8256 | 23.1724 | 22.4697 | 21.6023 | 20.6354 | 19.6393 | 18.1 | 14.5759 | 9.7737 | 6.3797 | 4.7195 | 24.9698 | 24.6161 | 24.1154 | 23.6949 | 23.2405 | 22.6861 | 22.0649 | 21.3973 | 20.4076 | 18.2391 | 15.6855 | 13.8385 | 12.4066 | 23.8274 | 23.3477 | 22.6739 | 22.0705 | 21.4214 | 20.629 | 19.7448 | 18.8181 | 17.3791 | 14.1093 | 9.8039 | 6.8268 | 5.3852
LOVEDEAN GSP | WYMERING BSP | GAMBLE ROAD | MINIMUM HEADROOM | SU 64771 01769 | YES | 19.4358 | 18.946 | 17.9971 | 16.8439 | 15.3269 | 13.7412 | 11.9961 | 10.0119 | 7.4568 | -1.0201 | -14.0326 | -21.214 | -24.8675 | 20.4324 | 19.9233 | 19.12 | 18.1595 | 16.9723 | 15.6962 | 14.2837 | 12.657 | 10.7739 | 4.3018 | -7.6995 | -20.3593 | -38.3573 | 22.3102 | 21.9147 | 21.198 | 20.2182 | 18.9105 | 17.5347 | 16.0187 | 14.2841 | 12.0173 | 4.5172 | -7.0998 | -13.3515 | -16.469
|  | GAMBLE ROAD | CT |  |  | 19.4358 | 18.946 | 17.9971 | 16.8439 | 15.3269 | 13.7412 | 11.9961 | 10.0119 | 7.4568 | -1.0201 | -14.0326 | -21.214 | -24.8675 | 20.4324 | 19.9233 | 19.12 | 18.1595 | 16.9723 | 15.6962 | 14.2837 | 12.657 | 10.7739 | 4.3018 | -7.6995 | -20.3593 | -38.3573 | 22.3102 | 21.9147 | 21.198 | 20.2182 | 18.9105 | 17.5347 | 16.0187 | 14.2841 | 12.0173 | 4.5172 | -7.0998 | -13.3515 | -16.469
|  | GAMBLE ROAD | LW |  |  | 19.4358 | 18.946 | 17.9971 | 16.8439 | 15.3269 | 13.7412 | 11.9961 | 10.0119 | 7.4568 | -1.0201 | -14.0326 | -21.214 | -24.8675 | 20.4324 | 19.9233 | 19.12 | 18.1595 | 16.9723 | 15.6962 | 14.2837 | 12.657 | 10.7739 | 4.3018 | -7.6995 | -20.3593 | -38.3573 | 22.3102 | 21.9147 | 21.198 | 20.2182 | 18.9105 | 17.5347 | 16.0187 | 14.2841 | 12.0173 | 4.5172 | -7.0998 | -13.3515 | -16.469
|  | GAMBLE ROAD | ST |  |  | 19.4358 | 18.946 | 17.9971 | 16.8439 | 15.3269 | 13.7412 | 11.9961 | 10.0119 | 7.4568 | -1.0201 | -14.0326 | -21.214 | -24.8675 | 20.4324 | 19.9233 | 19.12 | 18.1595 | 16.9723 | 15.6962 | 14.2837 | 12.657 | 10.7739 | 4.3018 | -7.6995 | -20.3593 | -38.3573 | 22.3102 | 21.9147 | 21.198 | 20.2182 | 18.9105 | 17.5347 | 16.0187 | 14.2841 | 12.0173 | 4.5172 | -7.0998 | -13.3515 | -16.469
|  | GAMBLE ROAD | FS |  |  | 19.4358 | 18.946 | 17.9971 | 16.8439 | 15.3269 | 13.7412 | 11.9961 | 10.0119 | 7.4568 | -1.0201 | -14.0326 | -21.214 | -24.8675 | 20.4324 | 19.9233 | 19.12 | 18.1595 | 16.9723 | 15.6962 | 14.2837 | 12.657 | 10.7739 | 4.3018 | -7.6995 | -20.3593 | -38.3573 | 22.3102 | 21.9147 | 21.198 | 20.2182 | 18.9105 | 17.5347 | 16.0187 | 14.2841 | 12.0173 | 4.5172 | -7.0998 | -13.3515 | -16.469
IVER 132KV | DENHAM | GERRARDS CROSS | MINIMUM HEADROOM | SU 99973 87964 | YES | 1.7179 | 1.3981 | 1.1123 | 0.74668 | 0.30987 | -0.20682 | -0.76344 | -1.4405 | -2.3884 | -4.2495 | -7.1305 | -8.9983 | -9.8791 | 4.6109 | 4.348 | 4.113 | 3.8645 | 3.5476 | 3.1474 | 2.7113 | 2.1563 | 1.4714 | 0.27217 | -1.3036 | -2.4561 | -3.5872 | 2.8349 | 2.5233 | 2.2457 | 1.9001 | 1.4715 | 0.958 | 0.40228 | -0.29605 | -1.2341 | -3.0547 | -5.6904 | -7.3264 | -8.0865
|  | GERRARDS CROSS | CT |  |  | 1.7179 | 1.3981 | 1.1123 | 0.74668 | 0.30987 | -0.20682 | -0.76344 | -1.4405 | -2.3884 | -4.2495 | -7.1305 | -8.9983 | -9.8791 | 4.6109 | 4.348 | 4.113 | 3.8645 | 3.5476 | 3.1474 | 2.7113 | 2.1563 | 1.4714 | 0.27217 | -1.3036 | -2.4561 | -3.5872 | 2.8349 | 2.5233 | 2.2457 | 1.9001 | 1.4715 | 0.958 | 0.40228 | -0.29605 | -1.2341 | -3.0547 | -5.6904 | -7.3264 | -8.0865
|  | GERRARDS CROSS | LW |  |  | 1.7179 | 1.3981 | 1.1123 | 0.74668 | 0.30987 | -0.20682 | -0.76344 | -1.4405 | -2.3884 | -4.2495 | -7.1305 | -8.9983 | -9.8791 | 4.6109 | 4.348 | 4.113 | 3.8645 | 3.5476 | 3.1474 | 2.7113 | 2.1563 | 1.4714 | 0.27217 | -1.3036 | -2.4561 | -3.5872 | 2.8349 | 2.5233 | 2.2457 | 1.9001 | 1.4715 | 0.958 | 0.40228 | -0.29605 | -1.2341 | -3.0547 | -5.6904 | -7.3264 | -8.0865
|  | GERRARDS CROSS | ST |  |  | 1.7179 | 1.3981 | 1.1123 | 0.74668 | 0.30987 | -0.20682 | -0.76344 | -1.4405 | -2.3884 | -4.2495 | -7.1305 | -8.9983 | -9.8791 | 4.6109 | 4.348 | 4.113 | 3.8645 | 3.5476 | 3.1474 | 2.7113 | 2.1563 | 1.4714 | 0.27217 | -1.3036 | -2.4561 | -3.5872 | 2.8349 | 2.5233 | 2.2457 | 1.9001 | 1.4715 | 0.958 | 0.40228 | -0.29605 | -1.2341 | -3.0547 | -5.6904 | -7.3264 | -8.0865
|  | GERRARDS CROSS | FS |  |  | 1.7179 | 1.3981 | 1.1123 | 0.74668 | 0.30987 | -0.20682 | -0.76344 | -1.4405 | -2.3884 | -4.2495 | -7.1305 | -8.9983 | -9.8791 | 4.6109 | 4.348 | 4.113 | 3.8645 | 3.5476 | 3.1474 | 2.7113 | 2.1563 | 1.4714 | 0.27217 | -1.3036 | -2.4561 | -3.5872 | 2.8349 | 2.5233 | 2.2457 | 1.9001 | 1.4715 | 0.958 | 0.40228 | -0.29605 | -1.2341 | -3.0547 | -5.6904 | -7.3264 | -8.0865
MANNINGTON GSP | SHAFTESBURY BSP | GILLINGHAM | MINIMUM HEADROOM | ST 80185 25765 | YES | 32.6857 | 32.1813 | 31.7069 | 31.0841 | 30.3543 | 28.9097 | 28.0384 | 27.0102 | 25.8474 | 22.4369 | 17.2632 | 15.0487 | 14.0329 | 32.7647 | 32.3209 | 31.9718 | 31.593 | 31.2161 | 29.8263 | 29.2126 | 28.5189 | 27.7944 | 25.6545 | 22.2519 | 20.8344 | 20.0059 | 33.0296 | 32.5836 | 32.2452 | 31.7171 | 31.0885 | 29.5581 | 28.7174 | 27.7334 | 26.6202 | 23.3832 | 18.5338 | 16.4939 | 15.5423
|  | GILLINGHAM | CT |  |  | 32.6857 | 32.1813 | 31.7069 | 31.0841 | 30.3543 | 28.9097 | 28.0384 | 27.0102 | 25.8474 | 22.4369 | 17.2632 | 15.0487 | 14.0329 | 32.7647 | 32.3209 | 31.9718 | 31.593 | 31.2161 | 29.8263 | 29.2126 | 28.5189 | 27.7944 | 25.6545 | 22.2519 | 20.8344 | 20.0059 | 33.0296 | 32.5836 | 32.2452 | 31.7171 | 31.0885 | 29.5581 | 28.7174 | 27.7334 | 26.6202 | 23.3832 | 18.5338 | 16.4939 | 15.5423
|  | GILLINGHAM | LW |  |  | 32.6857 | 32.1813 | 31.7069 | 31.0841 | 30.3543 | 28.9097 | 28.0384 | 27.0102 | 25.8474 | 22.4369 | 17.2632 | 15.0487 | 14.0329 | 32.7647 | 32.3209 | 31.9718 | 31.593 | 31.2161 | 29.8263 | 29.2126 | 28.5189 | 27.7944 | 25.6545 | 22.2519 | 20.8344 | 20.0059 | 33.0296 | 32.5836 | 32.2452 | 31.7171 | 31.0885 | 29.5581 | 28.7174 | 27.7334 | 26.6202 | 23.3832 | 18.5338 | 16.4939 | 15.5423
|  | GILLINGHAM | ST |  |  | 32.6857 | 32.1813 | 31.7069 | 31.0841 | 30.3543 | 28.9097 | 28.0384 | 27.0102 | 25.8474 | 22.4369 | 17.2632 | 15.0487 | 14.0329 | 32.7647 | 32.3209 | 31.9718 | 31.593 | 31.2161 | 29.8263 | 29.2126 | 28.5189 | 27.7944 | 25.6545 | 22.2519 | 20.8344 | 20.0059 | 33.0296 | 32.5836 | 32.2452 | 31.7171 | 31.0885 | 29.5581 | 28.7174 | 27.7334 | 26.6202 | 23.3832 | 18.5338 | 16.4939 | 15.5423
|  | GILLINGHAM | FS |  |  | 32.6857 | 32.1813 | 31.7069 | 31.0841 | 30.3543 | 28.9097 | 28.0384 | 27.0102 | 25.8474 | 22.4369 | 17.2632 | 15.0487 | 14.0329 | 32.7647 | 32.3209 | 31.9718 | 31.593 | 31.2161 | 29.8263 | 29.2126 | 28.5189 | 27.7944 | 25.6545 | 22.2519 | 20.8344 | 20.0059 | 33.0296 | 32.5836 | 32.2452 | 31.7171 | 31.0885 | 29.5581 | 28.7174 | 27.7334 | 26.6202 | 23.3832 | 18.5338 | 16.4939 | 15.5423
BRAMLEY (FLEE) | ALDERSHOT BSP | GODALMING | MINIMUM HEADROOM | SU 96743 44375 | YES | 19.0384 | 18.4451 | 17.8166 | 17.0484 | 16.2093 | 15.3306 | 14.3805 | 13.2534 | 11.4676 | 6.8506 | 0.02305 | -4.2135 | -6.1112 | 20.64 | 20.1962 | 19.7184 | 19.2052 | 18.6369 | 18.0191 | 17.3423 | 16.5175 | 15.3179 | 12.3008 | 8.1937 | 5.5897 | 3.3661 | 18.6314 | 18.0699 | 17.4723 | 16.7492 | 15.9583 | 15.1256 | 14.223 | 13.1452 | 11.4516 | 7.1178 | 0.89505 | -2.726 | -4.2758
|  | GODALMING | CT |  |  | 19.0384 | 18.4451 | 17.8166 | 17.0484 | 16.2093 | 15.3306 | 14.3805 | 13.2534 | 11.4676 | 6.8506 | 0.02305 | -4.2135 | -6.1112 | 20.64 | 20.1962 | 19.7184 | 19.2052 | 18.6369 | 18.0191 | 17.3423 | 16.5175 | 15.3179 | 12.3008 | 8.1937 | 5.5897 | 3.3661 | 18.6314 | 18.0699 | 17.4723 | 16.7492 | 15.9583 | 15.1256 | 14.223 | 13.1452 | 11.4516 | 7.1178 | 0.89505 | -2.726 | -4.2758
|  | GODALMING | LW |  |  | 19.0384 | 18.4451 | 17.8166 | 17.0484 | 16.2093 | 15.3306 | 14.3805 | 13.2534 | 11.4676 | 6.8506 | 0.02305 | -4.2135 | -6.1112 | 20.64 | 20.1962 | 19.7184 | 19.2052 | 18.6369 | 18.0191 | 17.3423 | 16.5175 | 15.3179 | 12.3008 | 8.1937 | 5.5897 | 3.3661 | 18.6314 | 18.0699 | 17.4723 | 16.7492 | 15.9583 | 15.1256 | 14.223 | 13.1452 | 11.4516 | 7.1178 | 0.89505 | -2.726 | -4.2758
|  | GODALMING | ST |  |  | 19.0384 | 18.4451 | 17.8166 | 17.0484 | 16.2093 | 15.3306 | 14.3805 | 13.2534 | 11.4676 | 6.8506 | 0.02305 | -4.2135 | -6.1112 | 20.64 | 20.1962 | 19.7184 | 19.2052 | 18.6369 | 18.0191 | 17.3423 | 16.5175 | 15.3179 | 12.3008 | 8.1937 | 5.5897 | 3.3661 | 18.6314 | 18.0699 | 17.4723 | 16.7492 | 15.9583 | 15.1256 | 14.223 | 13.1452 | 11.4516 | 7.1178 | 0.89505 | -2.726 | -4.2758
|  | GODALMING | FS |  |  | 19.0384 | 18.4451 | 17.8166 | 17.0484 | 16.2093 | 15.3306 | 14.3805 | 13.2534 | 11.4676 | 6.8506 | 0.02305 | -4.2135 | -6.1112 | 20.64 | 20.1962 | 19.7184 | 19.2052 | 18.6369 | 18.0191 | 17.3423 | 16.5175 | 15.3179 | 12.3008 | 8.1937 | 5.5897 | 3.3661 | 18.6314 | 18.0699 | 17.4723 | 16.7492 | 15.9583 | 15.1256 | 14.223 | 13.1452 | 11.4516 | 7.1178 | 0.89505 | -2.726 | -4.2758
WILLESDEN GSP | ACTON LANE | GOLDSMITHS | MINIMUM HEADROOM | TQ 21089 80758 | YES | 4.0964 | 3.916 | 3.6592 | 3.2978 | 2.9073 | 2.5282 | 2.1973 | 1.8733 | 1.3384 | -0.33954 | -3.7657 | -6.5446 | -8.1554 | 6.2442 | 5.9814 | 5.6448 | 5.2192 | 4.6693 | 4.0725 | 3.4265 | 2.7114 | 1.9036 | -0.9428 | -8.3594 | -19.9719 | -38.6519 | 5.0425 | 4.8789 | 4.6351 | 4.3264 | 3.984 | 3.6463 | 3.3413 | 3.0306 | 2.5565 | 1.0632 | -1.6919 | -3.757 | -5.0435
|  | GOLDSMITHS | CT |  |  | 4.0964 | 3.916 | 3.6592 | 3.2978 | 2.9073 | 2.5282 | 2.1973 | 1.8733 | 1.3384 | -0.33954 | -3.7657 | -6.5446 | -8.1554 | 6.2442 | 5.9814 | 5.6448 | 5.2192 | 4.6693 | 4.0725 | 3.4265 | 2.7114 | 1.9036 | -0.9428 | -8.3594 | -19.9719 | -38.6519 | 5.0425 | 4.8789 | 4.6351 | 4.3264 | 3.984 | 3.6463 | 3.3413 | 3.0306 | 2.5565 | 1.0632 | -1.6919 | -3.757 | -5.0435
|  | GOLDSMITHS | LW |  |  | 4.0964 | 3.916 | 3.6592 | 3.2978 | 2.9073 | 2.5282 | 2.1973 | 1.8733 | 1.3384 | -0.33954 | -3.7657 | -6.5446 | -8.1554 | 6.2442 | 5.9814 | 5.6448 | 5.2192 | 4.6693 | 4.0725 | 3.4265 | 2.7114 | 1.9036 | -0.9428 | -8.3594 | -19.9719 | -38.6519 | 5.0425 | 4.8789 | 4.6351 | 4.3264 | 3.984 | 3.6463 | 3.3413 | 3.0306 | 2.5565 | 1.0632 | -1.6919 | -3.757 | -5.0435
|  | GOLDSMITHS | ST |  |  | 4.0964 | 3.916 | 3.6592 | 3.2978 | 2.9073 | 2.5282 | 2.1973 | 1.8733 | 1.3384 | -0.33954 | -3.7657 | -6.5446 | -8.1554 | 6.2442 | 5.9814 | 5.6448 | 5.2192 | 4.6693 | 4.0725 | 3.4265 | 2.7114 | 1.9036 | -0.9428 | -8.3594 | -19.9719 | -38.6519 | 5.0425 | 4.8789 | 4.6351 | 4.3264 | 3.984 | 3.6463 | 3.3413 | 3.0306 | 2.5565 | 1.0632 | -1.6919 | -3.757 | -5.0435
|  | GOLDSMITHS | FS |  |  | 4.0964 | 3.916 | 3.6592 | 3.2978 | 2.9073 | 2.5282 | 2.1973 | 1.8733 | 1.3384 | -0.33954 | -3.7657 | -6.5446 | -8.1554 | 6.2442 | 5.9814 | 5.6448 | 5.2192 | 4.6693 | 4.0725 | 3.4265 | 2.7114 | 1.9036 | -0.9428 | -8.3594 | -19.9719 | -38.6519 | 5.0425 | 4.8789 | 4.6351 | 4.3264 | 3.984 | 3.6463 | 3.3413 | 3.0306 | 2.5565 | 1.0632 | -1.6919 | -3.757 | -5.0435
NURSLING GSP | WINCHESTER | GORDON ROAD | MINIMUM HEADROOM | SU 48217 29991 | YES | 13.0212 | 12.8142 | 12.5504 | 12.0662 | 11.5069 | 10.9114 | 10.3005 | 9.6803 | 8.8173 | 5.825 | 0.25302 | -3.2198 | -4.7339 | 19.6412 | 19.4642 | 19.2457 | 18.9218 | 18.5505 | 18.1441 | 17.7153 | 17.2495 | 16.4964 | 14.0617 | 9.5197 | 5.1448 | -0.58375 | 14.2948 | 14.1385 | 13.9375 | 13.6806 | 13.3499 | 12.9671 | 12.564 | 11.9614 | 11.1568 | 8.5053 | 3.851 | 0.78715 | -0.55143
|  | GORDON ROAD | CT |  |  | 13.0212 | 12.8142 | 12.5504 | 12.0662 | 11.5069 | 10.9114 | 10.3005 | 9.6803 | 8.8173 | 5.825 | 0.25302 | -3.2198 | -4.7339 | 19.6412 | 19.4642 | 19.2457 | 18.9218 | 18.5505 | 18.1441 | 17.7153 | 17.2495 | 16.4964 | 14.0617 | 9.5197 | 5.1448 | -0.58375 | 14.2948 | 14.1385 | 13.9375 | 13.6806 | 13.3499 | 12.9671 | 12.564 | 11.9614 | 11.1568 | 8.5053 | 3.851 | 0.78715 | -0.55143
|  | GORDON ROAD | LW |  |  | 13.0212 | 12.8142 | 12.5504 | 12.0662 | 11.5069 | 10.9114 | 10.3005 | 9.6803 | 8.8173 | 5.825 | 0.25302 | -3.2198 | -4.7339 | 19.6412 | 19.4642 | 19.2457 | 18.9218 | 18.5505 | 18.1441 | 17.7153 | 17.2495 | 16.4964 | 14.0617 | 9.5197 | 5.1448 | -0.58375 | 14.2948 | 14.1385 | 13.9375 | 13.6806 | 13.3499 | 12.9671 | 12.564 | 11.9614 | 11.1568 | 8.5053 | 3.851 | 0.78715 | -0.55143
|  | GORDON ROAD | ST |  |  | 13.0212 | 12.8142 | 12.5504 | 12.0662 | 11.5069 | 10.9114 | 10.3005 | 9.6803 | 8.8173 | 5.825 | 0.25302 | -3.2198 | -4.7339 | 19.6412 | 19.4642 | 19.2457 | 18.9218 | 18.5505 | 18.1441 | 17.7153 | 17.2495 | 16.4964 | 14.0617 | 9.5197 | 5.1448 | -0.58375 | 14.2948 | 14.1385 | 13.9375 | 13.6806 | 13.3499 | 12.9671 | 12.564 | 11.9614 | 11.1568 | 8.5053 | 3.851 | 0.78715 | -0.55143
|  | GORDON ROAD | FS |  |  | 13.0212 | 12.8142 | 12.5504 | 12.0662 | 11.5069 | 10.9114 | 10.3005 | 9.6803 | 8.8173 | 5.825 | 0.25302 | -3.2198 | -4.7339 | 19.6412 | 19.4642 | 19.2457 | 18.9218 | 18.5505 | 18.1441 | 17.7153 | 17.2495 | 16.4964 | 14.0617 | 9.5197 | 5.1448 | -0.58375 | 14.2948 | 14.1385 | 13.9375 | 13.6806 | 13.3499 | 12.9671 | 12.564 | 11.9614 | 11.1568 | 8.5053 | 3.851 | 0.78715 | -0.55143
BRAMLEY (FLEE) | BURGHFIELD RESERVE | GORING | MINIMUM HEADROOM | SU 60305 82895 | YES | 13.0913 | 12.9827 | 12.8605 | 12.6903 | 12.5067 | 12.3187 | 12.1052 | 11.8692 | 11.4648 | 10.5167 | 8.9497 | 7.6887 | 7.1344 | 14.7483 | 14.6711 | 14.5814 | 14.4821 | 14.3715 | 14.2555 | 14.1184 | 13.9607 | 13.7129 | 13.2035 | 12.5699 | 12.074 | 11.7146 | 13.9723 | 13.8707 | 13.7551 | 13.604 | 13.4394 | 13.27 | 13.0751 | 12.857 | 12.4882 | 11.6605 | 10.4211 | 9.4945 | 9.0878
|  | GORING | CT |  |  | 13.0913 | 12.9827 | 12.8605 | 12.6903 | 12.5067 | 12.3187 | 12.1052 | 11.8692 | 11.4648 | 10.5167 | 8.9497 | 7.6887 | 7.1344 | 14.7483 | 14.6711 | 14.5814 | 14.4821 | 14.3715 | 14.2555 | 14.1184 | 13.9607 | 13.7129 | 13.2035 | 12.5699 | 12.074 | 11.7146 | 13.9723 | 13.8707 | 13.7551 | 13.604 | 13.4394 | 13.27 | 13.0751 | 12.857 | 12.4882 | 11.6605 | 10.4211 | 9.4945 | 9.0878
|  | GORING | LW |  |  | 13.0913 | 12.9827 | 12.8605 | 12.6903 | 12.5067 | 12.3187 | 12.1052 | 11.8692 | 11.4648 | 10.5167 | 8.9497 | 7.6887 | 7.1344 | 14.7483 | 14.6711 | 14.5814 | 14.4821 | 14.3715 | 14.2555 | 14.1184 | 13.9607 | 13.7129 | 13.2035 | 12.5699 | 12.074 | 11.7146 | 13.9723 | 13.8707 | 13.7551 | 13.604 | 13.4394 | 13.27 | 13.0751 | 12.857 | 12.4882 | 11.6605 | 10.4211 | 9.4945 | 9.0878
|  | GORING | ST |  |  | 13.0913 | 12.9827 | 12.8605 | 12.6903 | 12.5067 | 12.3187 | 12.1052 | 11.8692 | 11.4648 | 10.5167 | 8.9497 | 7.6887 | 7.1344 | 14.7483 | 14.6711 | 14.5814 | 14.4821 | 14.3715 | 14.2555 | 14.1184 | 13.9607 | 13.7129 | 13.2035 | 12.5699 | 12.074 | 11.7146 | 13.9723 | 13.8707 | 13.7551 | 13.604 | 13.4394 | 13.27 | 13.0751 | 12.857 | 12.4882 | 11.6605 | 10.4211 | 9.4945 | 9.0878
|  | GORING | FS |  |  | 13.0913 | 12.9827 | 12.8605 | 12.6903 | 12.5067 | 12.3187 | 12.1052 | 11.8692 | 11.4648 | 10.5167 | 8.9497 | 7.6887 | 7.1344 | 14.7483 | 14.6711 | 14.5814 | 14.4821 | 14.3715 | 14.2555 | 14.1184 | 13.9607 | 13.7129 | 13.2035 | 12.5699 | 12.074 | 11.7146 | 13.9723 | 13.8707 | 13.7551 | 13.604 | 13.4394 | 13.27 | 13.0751 | 12.857 | 12.4882 | 11.6605 | 10.4211 | 9.4945 | 9.0878
IVER 132KV | DENHAM | GRASSINGHAM ROAD | MINIMUM HEADROOM | TQ 00165 90988 | YES | 21.2212 | 20.8826 | 20.537 | 20.0874 | 19.6077 | 19.0818 | 18.4799 | 17.7669 | 16.6452 | 14.6096 | 11.2291 | 8.807 | 7.6965 | 23.0768 | 22.8037 | 22.5225 | 22.2155 | 21.8834 | 21.5043 | 21.0621 | 20.5237 | 19.7629 | 18.5829 | 16.846 | 15.5298 | 14.3989 | 21.7575 | 21.4277 | 21.0909 | 20.6645 | 20.2086 | 19.7055 | 19.1274 | 18.4387 | 17.3687 | 15.4873 | 12.4507 | 10.3156 | 9.3428
|  | GRASSINGHAM ROAD | CT |  |  | 21.2212 | 20.8826 | 20.537 | 20.0874 | 19.6077 | 19.0818 | 18.4799 | 17.7669 | 16.6452 | 14.6096 | 11.2291 | 8.807 | 7.6965 | 23.0768 | 22.8037 | 22.5225 | 22.2155 | 21.8834 | 21.5043 | 21.0621 | 20.5237 | 19.7629 | 18.5829 | 16.846 | 15.5298 | 14.3989 | 21.7575 | 21.4277 | 21.0909 | 20.6645 | 20.2086 | 19.7055 | 19.1274 | 18.4387 | 17.3687 | 15.4873 | 12.4507 | 10.3156 | 9.3428
|  | GRASSINGHAM ROAD | LW |  |  | 21.2212 | 20.8826 | 20.537 | 20.0874 | 19.6077 | 19.0818 | 18.4799 | 17.7669 | 16.6452 | 14.6096 | 11.2291 | 8.807 | 7.6965 | 23.0768 | 22.8037 | 22.5225 | 22.2155 | 21.8834 | 21.5043 | 21.0621 | 20.5237 | 19.7629 | 18.5829 | 16.846 | 15.5298 | 14.3989 | 21.7575 | 21.4277 | 21.0909 | 20.6645 | 20.2086 | 19.7055 | 19.1274 | 18.4387 | 17.3687 | 15.4873 | 12.4507 | 10.3156 | 9.3428
|  | GRASSINGHAM ROAD | ST |  |  | 21.2212 | 20.8826 | 20.537 | 20.0874 | 19.6077 | 19.0818 | 18.4799 | 17.7669 | 16.6452 | 14.6096 | 11.2291 | 8.807 | 7.6965 | 23.0768 | 22.8037 | 22.5225 | 22.2155 | 21.8834 | 21.5043 | 21.0621 | 20.5237 | 19.7629 | 18.5829 | 16.846 | 15.5298 | 14.3989 | 21.7575 | 21.4277 | 21.0909 | 20.6645 | 20.2086 | 19.7055 | 19.1274 | 18.4387 | 17.3687 | 15.4873 | 12.4507 | 10.3156 | 9.3428
|  | GRASSINGHAM ROAD | FS |  |  | 21.2212 | 20.8826 | 20.537 | 20.0874 | 19.6077 | 19.0818 | 18.4799 | 17.7669 | 16.6452 | 14.6096 | 11.2291 | 8.807 | 7.6965 | 23.0768 | 22.8037 | 22.5225 | 22.2155 | 21.8834 | 21.5043 | 21.0621 | 20.5237 | 19.7629 | 18.5829 | 16.846 | 15.5298 | 14.3989 | 21.7575 | 21.4277 | 21.0909 | 20.6645 | 20.2086 | 19.7055 | 19.1274 | 18.4387 | 17.3687 | 15.4873 | 12.4507 | 10.3156 | 9.3428
BRAMLEY (FLEE) | BURGHFIELD MAIN | GREEN PARK | MINIMUM HEADROOM |  |  | 51.03 | 51.03 | 51.03 | 51.03 | 51.03 | 51.03 | 51.03 | 51.03 | 51.03 | 51.03 | 51.03 | 51.03 | 51.03 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
|  | GREEN PARK | CT |  |  | 51.03 | 51.03 | 51.03 | 51.03 | 51.03 | 51.03 | 51.03 | 51.03 | 51.03 | 51.03 | 51.03 | 51.03 | 51.03 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
|  | GREEN PARK | LW |  |  | 51.03 | 51.03 | 51.03 | 51.03 | 51.03 | 51.03 | 51.03 | 51.03 | 51.03 | 51.03 | 51.03 | 51.03 | 51.03 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
|  | GREEN PARK | ST |  |  | 51.03 | 51.03 | 51.03 | 51.03 | 51.03 | 51.03 | 51.03 | 51.03 | 51.03 | 51.03 | 51.03 | 51.03 | 51.03 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
|  | GREEN PARK | FS |  |  | 51.03 | 51.03 | 51.03 | 51.03 | 51.03 | 51.03 | 51.03 | 51.03 | 51.03 | 51.03 | 51.03 | 51.03 | 51.03 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
WILLESDEN GSP |  | GREENFORD | MINIMUM HEADROOM | TQ 14695 83785 |  | 2.8067 | 2.0775 | 1.0613 | -0.15245 | -1.451 | -2.8411 | -4.4228 | -6.189 | -8.4432 | -15.2571 | -24.9869 | -31.7422 | -35.4966 | 10.8143 | 10.3567 | 9.6644 | 8.8101 | 7.8911 | 6.8927 | 5.7661 | 4.4836 | 2.902 | -2.1515 | -9.9698 | -18.281 | -29.4456 | 6.0948 | 5.4919 | 4.637 | 3.5906 | 2.4693 | 1.2541 | -0.16335 | -1.7582 | -3.8219 | -10.1212 | -18.8497 | -24.7742 | -27.9716
|  | GREENFORD | CT |  |  | 2.8067 | 2.0775 | 1.0613 | -0.15245 | -1.451 | -2.8411 | -4.4228 | -6.189 | -8.4432 | -15.2571 | -24.9869 | -31.7422 | -35.4966 | 10.8143 | 10.3567 | 9.6644 | 8.8101 | 7.8911 | 6.8927 | 5.7661 | 4.4836 | 2.902 | -2.1515 | -9.9698 | -18.281 | -29.4456 | 6.0948 | 5.4919 | 4.637 | 3.5906 | 2.4693 | 1.2541 | -0.16335 | -1.7582 | -3.8219 | -10.1212 | -18.8497 | -24.7742 | -27.9716
|  | GREENFORD | LW |  |  | 2.8067 | 2.0775 | 1.0613 | -0.15245 | -1.451 | -2.8411 | -4.4228 | -6.189 | -8.4432 | -15.2571 | -24.9869 | -31.7422 | -35.4966 | 10.8143 | 10.3567 | 9.6644 | 8.8101 | 7.8911 | 6.8927 | 5.7661 | 4.4836 | 2.902 | -2.1515 | -9.9698 | -18.281 | -29.4456 | 6.0948 | 5.4919 | 4.637 | 3.5906 | 2.4693 | 1.2541 | -0.16335 | -1.7582 | -3.8219 | -10.1212 | -18.8497 | -24.7742 | -27.9716
|  | GREENFORD | ST |  |  | 2.8067 | 2.0775 | 1.0613 | -0.15245 | -1.451 | -2.8411 | -4.4228 | -6.189 | -8.4432 | -15.2571 | -24.9869 | -31.7422 | -35.4966 | 10.8143 | 10.3567 | 9.6644 | 8.8101 | 7.8911 | 6.8927 | 5.7661 | 4.4836 | 2.902 | -2.1515 | -9.9698 | -18.281 | -29.4456 | 6.0948 | 5.4919 | 4.637 | 3.5906 | 2.4693 | 1.2541 | -0.16335 | -1.7582 | -3.8219 | -10.1212 | -18.8497 | -24.7742 | -27.9716
|  | GREENFORD | FS |  |  | 2.8067 | 2.0775 | 1.0613 | -0.15245 | -1.451 | -2.8411 | -4.4228 | -6.189 | -8.4432 | -15.2571 | -24.9869 | -31.7422 | -35.4966 | 10.8143 | 10.3567 | 9.6644 | 8.8101 | 7.8911 | 6.8927 | 5.7661 | 4.4836 | 2.902 | -2.1515 | -9.9698 | -18.281 | -29.4456 | 6.0948 | 5.4919 | 4.637 | 3.5906 | 2.4693 | 1.2541 | -0.16335 | -1.7582 | -3.8219 | -10.1212 | -18.8497 | -24.7742 | -27.9716
LOVEDEAN GSP | PORTSMOUTH BSP | GREETHAM STREET | MINIMUM HEADROOM | SU 64445 00178 | YES | 25.0167 | 24.8901 | 24.717 | 24.5285 | 24.313 | 24.0971 | 23.8605 | 23.6046 | 23.0746 | 21.2101 | 17.2437 | 14.1183 | 12.0145 | 23.6704 | 23.5457 | 23.388 | 23.2086 | 23.0056 | 22.6904 | 22.2516 | 21.7847 | 21.2494 | 19.3915 | 14.8751 | 8.9788 | 0.10738 | 25.9914 | 25.8505 | 25.6547 | 25.3863 | 25.0838 | 24.7791 | 24.448 | 24.0884 | 23.5682 | 21.8769 | 18.3833 | 15.8092 | 14.1433
|  | GREETHAM STREET | CT |  |  | 25.0167 | 24.8901 | 24.717 | 24.5285 | 24.313 | 24.0971 | 23.8605 | 23.6046 | 23.0746 | 21.2101 | 17.2437 | 14.1183 | 12.0145 | 23.6704 | 23.5457 | 23.388 | 23.2086 | 23.0056 | 22.6904 | 22.2516 | 21.7847 | 21.2494 | 19.3915 | 14.8751 | 8.9788 | 0.10738 | 25.9914 | 25.8505 | 25.6547 | 25.3863 | 25.0838 | 24.7791 | 24.448 | 24.0884 | 23.5682 | 21.8769 | 18.3833 | 15.8092 | 14.1433
|  | GREETHAM STREET | LW |  |  | 25.0167 | 24.8901 | 24.717 | 24.5285 | 24.313 | 24.0971 | 23.8605 | 23.6046 | 23.0746 | 21.2101 | 17.2437 | 14.1183 | 12.0145 | 23.6704 | 23.5457 | 23.388 | 23.2086 | 23.0056 | 22.6904 | 22.2516 | 21.7847 | 21.2494 | 19.3915 | 14.8751 | 8.9788 | 0.10738 | 25.9914 | 25.8505 | 25.6547 | 25.3863 | 25.0838 | 24.7791 | 24.448 | 24.0884 | 23.5682 | 21.8769 | 18.3833 | 15.8092 | 14.1433
|  | GREETHAM STREET | ST |  |  | 25.0167 | 24.8901 | 24.717 | 24.5285 | 24.313 | 24.0971 | 23.8605 | 23.6046 | 23.0746 | 21.2101 | 17.2437 | 14.1183 | 12.0145 | 23.6704 | 23.5457 | 23.388 | 23.2086 | 23.0056 | 22.6904 | 22.2516 | 21.7847 | 21.2494 | 19.3915 | 14.8751 | 8.9788 | 0.10738 | 25.9914 | 25.8505 | 25.6547 | 25.3863 | 25.0838 | 24.7791 | 24.448 | 24.0884 | 23.5682 | 21.8769 | 18.3833 | 15.8092 | 14.1433
|  | GREETHAM STREET | FS |  |  | 25.0167 | 24.8901 | 24.717 | 24.5285 | 24.313 | 24.0971 | 23.8605 | 23.6046 | 23.0746 | 21.2101 | 17.2437 | 14.1183 | 12.0145 | 23.6704 | 23.5457 | 23.388 | 23.2086 | 23.0056 | 22.6904 | 22.2516 | 21.7847 | 21.2494 | 19.3915 | 14.8751 | 8.9788 | 0.10738 | 25.9914 | 25.8505 | 25.6547 | 25.3863 | 25.0838 | 24.7791 | 24.448 | 24.0884 | 23.5682 | 21.8769 | 18.3833 | 15.8092 | 14.1433
COWLEY GSP | DRAYTON BSP | GROVE | MINIMUM HEADROOM | SU 39515 89611 | NO | -0.53225 | -1.2235 | -2.0351 | -2.9083 | -3.8368 | -4.8608 | -6.0331 | -7.5297 | -9.1871 | -13.0565 | -18.9716 | -22.1231 | -23.3678 | 1.982 | 1.5665 | 1.076 | 0.57493 | 0.041094 | -0.55091 | -1.2335 | -2.0972 | -3.0587 | -5.2404 | -8.5272 | -10.5663 | -12.217 | -0.82729 | -1.4138 | -2.1139 | -2.8575 | -3.6494 | -4.5249 | -5.5348 | -6.817 | -8.2714 | -11.6137 | -16.9135 | -19.7876 | -20.8801
|  | GROVE | CT |  |  | -0.53225 | -1.2235 | -2.0351 | -2.9083 | -3.8368 | -4.8608 | -6.0331 | -7.5297 | -9.1871 | -13.0565 | -18.9716 | -22.1231 | -23.3678 | 1.982 | 1.5665 | 1.076 | 0.57493 | 0.041094 | -0.55091 | -1.2335 | -2.0972 | -3.0587 | -5.2404 | -8.5272 | -10.5663 | -12.217 | -0.82729 | -1.4138 | -2.1139 | -2.8575 | -3.6494 | -4.5249 | -5.5348 | -6.817 | -8.2714 | -11.6137 | -16.9135 | -19.7876 | -20.8801
|  | GROVE | LW |  |  | -0.53225 | -1.2235 | -2.0351 | -2.9083 | -3.8368 | -4.8608 | -6.0331 | -7.5297 | -9.1871 | -13.0565 | -18.9716 | -22.1231 | -23.3678 | 1.982 | 1.5665 | 1.076 | 0.57493 | 0.041094 | -0.55091 | -1.2335 | -2.0972 | -3.0587 | -5.2404 | -8.5272 | -10.5663 | -12.217 | -0.82729 | -1.4138 | -2.1139 | -2.8575 | -3.6494 | -4.5249 | -5.5348 | -6.817 | -8.2714 | -11.6137 | -16.9135 | -19.7876 | -20.8801
|  | GROVE | ST |  |  | -0.53225 | -1.2235 | -2.0351 | -2.9083 | -3.8368 | -4.8608 | -6.0331 | -7.5297 | -9.1871 | -13.0565 | -18.9716 | -22.1231 | -23.3678 | 1.982 | 1.5665 | 1.076 | 0.57493 | 0.041094 | -0.55091 | -1.2335 | -2.0972 | -3.0587 | -5.2404 | -8.5272 | -10.5663 | -12.217 | -0.82729 | -1.4138 | -2.1139 | -2.8575 | -3.6494 | -4.5249 | -5.5348 | -6.817 | -8.2714 | -11.6137 | -16.9135 | -19.7876 | -20.8801
|  | GROVE | FS |  |  | -0.53225 | -1.2235 | -2.0351 | -2.9083 | -3.8368 | -4.8608 | -6.0331 | -7.5297 | -9.1871 | -13.0565 | -18.9716 | -22.1231 | -23.3678 | 1.982 | 1.5665 | 1.076 | 0.57493 | 0.041094 | -0.55091 | -1.2335 | -2.0972 | -3.0587 | -5.2404 | -8.5272 | -10.5663 | -12.217 | -0.82729 | -1.4138 | -2.1139 | -2.8575 | -3.6494 | -4.5249 | -5.5348 | -6.817 | -8.2714 | -11.6137 | -16.9135 | -19.7876 | -20.8801
MANNINGTON GSP | SHAFTESBURY BSP | GUSSAGE ST MICHAEL | MINIMUM HEADROOM | ST 98638 11417 | YES | 1.3461 | 1.3257 | 1.2981 | 1.2649 | 1.2284 | 1.1846 | 1.1321 | 1.0723 | 1.0034 | 0.8722 | 0.64922 | 0.51608 | 0.45733 | 1.7621 | 1.751 | 1.7348 | 1.7178 | 1.6986 | 1.6766 | 1.6487 | 1.6157 | 1.5787 | 1.5229 | 1.4326 | 1.3818 | 1.3539 | 1.7418 | 1.7225 | 1.6961 | 1.665 | 1.6307 | 1.5898 | 1.5404 | 1.4837 | 1.4185 | 1.2988 | 1.0972 | 0.97725 | 0.922
|  | GUSSAGE ST MICHAEL | CT |  |  | 1.3461 | 1.3257 | 1.2981 | 1.2649 | 1.2284 | 1.1846 | 1.1321 | 1.0723 | 1.0034 | 0.8722 | 0.64922 | 0.51608 | 0.45733 | 1.7621 | 1.751 | 1.7348 | 1.7178 | 1.6986 | 1.6766 | 1.6487 | 1.6157 | 1.5787 | 1.5229 | 1.4326 | 1.3818 | 1.3539 | 1.7418 | 1.7225 | 1.6961 | 1.665 | 1.6307 | 1.5898 | 1.5404 | 1.4837 | 1.4185 | 1.2988 | 1.0972 | 0.97725 | 0.922
|  | GUSSAGE ST MICHAEL | LW |  |  | 1.3461 | 1.3257 | 1.2981 | 1.2649 | 1.2284 | 1.1846 | 1.1321 | 1.0723 | 1.0034 | 0.8722 | 0.64922 | 0.51608 | 0.45733 | 1.7621 | 1.751 | 1.7348 | 1.7178 | 1.6986 | 1.6766 | 1.6487 | 1.6157 | 1.5787 | 1.5229 | 1.4326 | 1.3818 | 1.3539 | 1.7418 | 1.7225 | 1.6961 | 1.665 | 1.6307 | 1.5898 | 1.5404 | 1.4837 | 1.4185 | 1.2988 | 1.0972 | 0.97725 | 0.922
|  | GUSSAGE ST MICHAEL | ST |  |  | 1.3461 | 1.3257 | 1.2981 | 1.2649 | 1.2284 | 1.1846 | 1.1321 | 1.0723 | 1.0034 | 0.8722 | 0.64922 | 0.51608 | 0.45733 | 1.7621 | 1.751 | 1.7348 | 1.7178 | 1.6986 | 1.6766 | 1.6487 | 1.6157 | 1.5787 | 1.5229 | 1.4326 | 1.3818 | 1.3539 | 1.7418 | 1.7225 | 1.6961 | 1.665 | 1.6307 | 1.5898 | 1.5404 | 1.4837 | 1.4185 | 1.2988 | 1.0972 | 0.97725 | 0.922
|  | GUSSAGE ST MICHAEL | FS |  |  | 1.3461 | 1.3257 | 1.2981 | 1.2649 | 1.2284 | 1.1846 | 1.1321 | 1.0723 | 1.0034 | 0.8722 | 0.64922 | 0.51608 | 0.45733 | 1.7621 | 1.751 | 1.7348 | 1.7178 | 1.6986 | 1.6766 | 1.6487 | 1.6157 | 1.5787 | 1.5229 | 1.4326 | 1.3818 | 1.3539 | 1.7418 | 1.7225 | 1.6961 | 1.665 | 1.6307 | 1.5898 | 1.5404 | 1.4837 | 1.4185 | 1.2988 | 1.0972 | 0.97725 | 0.922
BOTLEY WOOD GSP | NETLEY COMMON BSP | HAMBLE | MINIMUM HEADROOM | SU 47370 08794 | YES | 21.0706 | 20.8696 | 20.6127 | 20.2675 | 19.9019 | 19.519 | 19.1071 | 18.5804 | 17.7128 | 15.5709 | 12.3451 | 10.0761 | 8.9238 | 21.0135 | 20.931 | 20.8308 | 20.726 | 20.6126 | 20.4672 | 20.1409 | 19.7319 | 19.1261 | 17.6716 | 15.617 | 14.0063 | 12.3697 | 20.505 | 20.2979 | 20.0262 | 19.6939 | 19.3399 | 18.961 | 18.5514 | 18.0414 | 17.2304 | 15.2876 | 12.5677 | 10.764 | 9.8266
|  | HAMBLE | CT |  |  | 21.0706 | 20.8696 | 20.6127 | 20.2675 | 19.9019 | 19.519 | 19.1071 | 18.5804 | 17.7128 | 15.5709 | 12.3451 | 10.0761 | 8.9238 | 21.0135 | 20.931 | 20.8308 | 20.726 | 20.6126 | 20.4672 | 20.1409 | 19.7319 | 19.1261 | 17.6716 | 15.617 | 14.0063 | 12.3697 | 20.505 | 20.2979 | 20.0262 | 19.6939 | 19.3399 | 18.961 | 18.5514 | 18.0414 | 17.2304 | 15.2876 | 12.5677 | 10.764 | 9.8266
|  | HAMBLE | LW |  |  | 21.0706 | 20.8696 | 20.6127 | 20.2675 | 19.9019 | 19.519 | 19.1071 | 18.5804 | 17.7128 | 15.5709 | 12.3451 | 10.0761 | 8.9238 | 21.0135 | 20.931 | 20.8308 | 20.726 | 20.6126 | 20.4672 | 20.1409 | 19.7319 | 19.1261 | 17.6716 | 15.617 | 14.0063 | 12.3697 | 20.505 | 20.2979 | 20.0262 | 19.6939 | 19.3399 | 18.961 | 18.5514 | 18.0414 | 17.2304 | 15.2876 | 12.5677 | 10.764 | 9.8266
|  | HAMBLE | ST |  |  | 21.0706 | 20.8696 | 20.6127 | 20.2675 | 19.9019 | 19.519 | 19.1071 | 18.5804 | 17.7128 | 15.5709 | 12.3451 | 10.0761 | 8.9238 | 21.0135 | 20.931 | 20.8308 | 20.726 | 20.6126 | 20.4672 | 20.1409 | 19.7319 | 19.1261 | 17.6716 | 15.617 | 14.0063 | 12.3697 | 20.505 | 20.2979 | 20.0262 | 19.6939 | 19.3399 | 18.961 | 18.5514 | 18.0414 | 17.2304 | 15.2876 | 12.5677 | 10.764 | 9.8266
|  | HAMBLE | FS |  |  | 21.0706 | 20.8696 | 20.6127 | 20.2675 | 19.9019 | 19.519 | 19.1071 | 18.5804 | 17.7128 | 15.5709 | 12.3451 | 10.0761 | 8.9238 | 21.0135 | 20.931 | 20.8308 | 20.726 | 20.6126 | 20.4672 | 20.1409 | 19.7319 | 19.1261 | 17.6716 | 15.617 | 14.0063 | 12.3697 | 20.505 | 20.2979 | 20.0262 | 19.6939 | 19.3399 | 18.961 | 18.5514 | 18.0414 | 17.2304 | 15.2876 | 12.5677 | 10.764 | 9.8266
MANNINGTON GSP | POOLE PS (HAMWORTHY) | HAMWORTHY | MINIMUM HEADROOM | SZ 00104 90800 | YES | 5.7296 | 4.7809 | 3.9365 | 2.5481 | 1.021 | -0.52223 | -2.1307 | -3.9227 | -6.3029 | -12.4053 | -20.0036 | -24.8828 | -27.4212 | 11.5586 | 10.9705 | 10.3948 | 9.5462 | 8.6118 | 7.6514 | 6.641 | 5.4957 | 3.9901 | 0.02346 | -4.8915 | -8.7283 | -12.9206 | 6.5903 | 5.8134 | 5.089 | 3.905 | 2.5993 | 1.2699 | -0.12259 | -1.7246 | -3.8727 | -9.4221 | -16.2414 | -20.6656 | -22.9498
|  | HAMWORTHY | CT |  |  | 5.7296 | 4.7809 | 3.9365 | 2.5481 | 1.021 | -0.52223 | -2.1307 | -3.9227 | -6.3029 | -12.4053 | -20.0036 | -24.8828 | -27.4212 | 11.5586 | 10.9705 | 10.3948 | 9.5462 | 8.6118 | 7.6514 | 6.641 | 5.4957 | 3.9901 | 0.02346 | -4.8915 | -8.7283 | -12.9206 | 6.5903 | 5.8134 | 5.089 | 3.905 | 2.5993 | 1.2699 | -0.12259 | -1.7246 | -3.8727 | -9.4221 | -16.2414 | -20.6656 | -22.9498
|  | HAMWORTHY | LW |  |  | 5.7296 | 4.7809 | 3.9365 | 2.5481 | 1.021 | -0.52223 | -2.1307 | -3.9227 | -6.3029 | -12.4053 | -20.0036 | -24.8828 | -27.4212 | 11.5586 | 10.9705 | 10.3948 | 9.5462 | 8.6118 | 7.6514 | 6.641 | 5.4957 | 3.9901 | 0.02346 | -4.8915 | -8.7283 | -12.9206 | 6.5903 | 5.8134 | 5.089 | 3.905 | 2.5993 | 1.2699 | -0.12259 | -1.7246 | -3.8727 | -9.4221 | -16.2414 | -20.6656 | -22.9498
|  | HAMWORTHY | ST |  |  | 5.7296 | 4.7809 | 3.9365 | 2.5481 | 1.021 | -0.52223 | -2.1307 | -3.9227 | -6.3029 | -12.4053 | -20.0036 | -24.8828 | -27.4212 | 11.5586 | 10.9705 | 10.3948 | 9.5462 | 8.6118 | 7.6514 | 6.641 | 5.4957 | 3.9901 | 0.02346 | -4.8915 | -8.7283 | -12.9206 | 6.5903 | 5.8134 | 5.089 | 3.905 | 2.5993 | 1.2699 | -0.12259 | -1.7246 | -3.8727 | -9.4221 | -16.2414 | -20.6656 | -22.9498
|  | HAMWORTHY | FS |  |  | 5.7296 | 4.7809 | 3.9365 | 2.5481 | 1.021 | -0.52223 | -2.1307 | -3.9227 | -6.3029 | -12.4053 | -20.0036 | -24.8828 | -27.4212 | 11.5586 | 10.9705 | 10.3948 | 9.5462 | 8.6118 | 7.6514 | 6.641 | 5.4957 | 3.9901 | 0.02346 | -4.8915 | -8.7283 | -12.9206 | 6.5903 | 5.8134 | 5.089 | 3.905 | 2.5993 | 1.2699 | -0.12259 | -1.7246 | -3.8727 | -9.4221 | -16.2414 | -20.6656 | -22.9498
IVER 132KV | DENHAM | HAREFIELD | MINIMUM HEADROOM | TQ 04001 91227 | YES | 9.2414 | 9.1619 | 9.0422 | 8.8867 | 8.7242 | 8.5444 | 8.3519 | 8.1321 | 7.7674 | 6.8173 | 5.4379 | 4.519 | 4.0713 | 10.811 | 10.7846 | 10.7478 | 10.7102 | 10.6691 | 10.6192 | 10.4778 | 10.312 | 10.0635 | 9.4313 | 8.5692 | 7.8718 | 7.1579 | 9.9983 | 9.9271 | 9.8209 | 9.6804 | 9.5335 | 9.3717 | 9.1985 | 9.0017 | 8.6724 | 7.7864 | 6.5312 | 5.6811 | 5.2737
|  | HAREFIELD | CT |  |  | 9.2414 | 9.1619 | 9.0422 | 8.8867 | 8.7242 | 8.5444 | 8.3519 | 8.1321 | 7.7674 | 6.8173 | 5.4379 | 4.519 | 4.0713 | 10.811 | 10.7846 | 10.7478 | 10.7102 | 10.6691 | 10.6192 | 10.4778 | 10.312 | 10.0635 | 9.4313 | 8.5692 | 7.8718 | 7.1579 | 9.9983 | 9.9271 | 9.8209 | 9.6804 | 9.5335 | 9.3717 | 9.1985 | 9.0017 | 8.6724 | 7.7864 | 6.5312 | 5.6811 | 5.2737
|  | HAREFIELD | LW |  |  | 9.2414 | 9.1619 | 9.0422 | 8.8867 | 8.7242 | 8.5444 | 8.3519 | 8.1321 | 7.7674 | 6.8173 | 5.4379 | 4.519 | 4.0713 | 10.811 | 10.7846 | 10.7478 | 10.7102 | 10.6691 | 10.6192 | 10.4778 | 10.312 | 10.0635 | 9.4313 | 8.5692 | 7.8718 | 7.1579 | 9.9983 | 9.9271 | 9.8209 | 9.6804 | 9.5335 | 9.3717 | 9.1985 | 9.0017 | 8.6724 | 7.7864 | 6.5312 | 5.6811 | 5.2737
|  | HAREFIELD | ST |  |  | 9.2414 | 9.1619 | 9.0422 | 8.8867 | 8.7242 | 8.5444 | 8.3519 | 8.1321 | 7.7674 | 6.8173 | 5.4379 | 4.519 | 4.0713 | 10.811 | 10.7846 | 10.7478 | 10.7102 | 10.6691 | 10.6192 | 10.4778 | 10.312 | 10.0635 | 9.4313 | 8.5692 | 7.8718 | 7.1579 | 9.9983 | 9.9271 | 9.8209 | 9.6804 | 9.5335 | 9.3717 | 9.1985 | 9.0017 | 8.6724 | 7.7864 | 6.5312 | 5.6811 | 5.2737
|  | HAREFIELD | FS |  |  | 9.2414 | 9.1619 | 9.0422 | 8.8867 | 8.7242 | 8.5444 | 8.3519 | 8.1321 | 7.7674 | 6.8173 | 5.4379 | 4.519 | 4.0713 | 10.811 | 10.7846 | 10.7478 | 10.7102 | 10.6691 | 10.6192 | 10.4778 | 10.312 | 10.0635 | 9.4313 | 8.5692 | 7.8718 | 7.1579 | 9.9983 | 9.9271 | 9.8209 | 9.6804 | 9.5335 | 9.3717 | 9.1985 | 9.0017 | 8.6724 | 7.7864 | 6.5312 | 5.6811 | 5.2737
NURSLING GSP | WINCHESTER | HARESTOCK | MINIMUM HEADROOM | SU 45908 31300 | YES | 5.9009 | 5.2619 | 4.5554 | 3.6576 | 2.6917 | 1.7081 | 0.60559 | -0.65301 | -2.5614 | -7.4128 | -13.7273 | -17.2971 | -18.7485 | 12.4919 | 12.039 | 11.5381 | 10.9796 | 10.3751 | 9.7421 | 9.0241 | 8.1817 | 6.9607 | 4.1344 | 0.8611 | -1.005 | -2.43 | 8.0511 | 7.4551 | 6.794 | 6.0004 | 5.144 | 4.2601 | 3.2617 | 2.1022 | 0.35263 | -3.9614 | -9.3705 | -12.3045 | -13.4822
|  | HARESTOCK | CT |  |  | 5.9009 | 5.2619 | 4.5554 | 3.6576 | 2.6917 | 1.7081 | 0.60559 | -0.65301 | -2.5614 | -7.4128 | -13.7273 | -17.2971 | -18.7485 | 12.4919 | 12.039 | 11.5381 | 10.9796 | 10.3751 | 9.7421 | 9.0241 | 8.1817 | 6.9607 | 4.1344 | 0.8611 | -1.005 | -2.43 | 8.0511 | 7.4551 | 6.794 | 6.0004 | 5.144 | 4.2601 | 3.2617 | 2.1022 | 0.35263 | -3.9614 | -9.3705 | -12.3045 | -13.4822
|  | HARESTOCK | LW |  |  | 5.9009 | 5.2619 | 4.5554 | 3.6576 | 2.6917 | 1.7081 | 0.60559 | -0.65301 | -2.5614 | -7.4128 | -13.7273 | -17.2971 | -18.7485 | 12.4919 | 12.039 | 11.5381 | 10.9796 | 10.3751 | 9.7421 | 9.0241 | 8.1817 | 6.9607 | 4.1344 | 0.8611 | -1.005 | -2.43 | 8.0511 | 7.4551 | 6.794 | 6.0004 | 5.144 | 4.2601 | 3.2617 | 2.1022 | 0.35263 | -3.9614 | -9.3705 | -12.3045 | -13.4822
|  | HARESTOCK | ST |  |  | 5.9009 | 5.2619 | 4.5554 | 3.6576 | 2.6917 | 1.7081 | 0.60559 | -0.65301 | -2.5614 | -7.4128 | -13.7273 | -17.2971 | -18.7485 | 12.4919 | 12.039 | 11.5381 | 10.9796 | 10.3751 | 9.7421 | 9.0241 | 8.1817 | 6.9607 | 4.1344 | 0.8611 | -1.005 | -2.43 | 8.0511 | 7.4551 | 6.794 | 6.0004 | 5.144 | 4.2601 | 3.2617 | 2.1022 | 0.35263 | -3.9614 | -9.3705 | -12.3045 | -13.4822
|  | HARESTOCK | FS |  |  | 5.9009 | 5.2619 | 4.5554 | 3.6576 | 2.6917 | 1.7081 | 0.60559 | -0.65301 | -2.5614 | -7.4128 | -13.7273 | -17.2971 | -18.7485 | 12.4919 | 12.039 | 11.5381 | 10.9796 | 10.3751 | 9.7421 | 9.0241 | 8.1817 | 6.9607 | 4.1344 | 0.8611 | -1.005 | -2.43 | 8.0511 | 7.4551 | 6.794 | 6.0004 | 5.144 | 4.2601 | 3.2617 | 2.1022 | 0.35263 | -3.9614 | -9.3705 | -12.3045 | -13.4822
EALING GSP | EALING 22kV | HARVARD LANE | MINIMUM HEADROOM | TQ 20021 78030 | YES | -0.15589 | -0.65547 | -1.2005 | -1.9255 | -2.7065 | -3.4759 | -4.3143 | -5.1993 | -6.5383 | -10.833 | -19.0199 | -25.1737 | -28.9664 | 5.7967 | 5.4963 | 5.1679 | 4.743 | 4.0604 | 3.2293 | 2.3099 | 1.2974 | 0.067959 | -4.1338 | -13.4563 | -25.6082 | -43.3763 | 1.3365 | 0.88317 | 0.38351 | -0.26484 | -0.97507 | -1.6803 | -2.4494 | -3.2536 | -4.444 | -8.2723 | -15.3299 | -20.599 | -23.772
|  | HARVARD LANE | CT |  |  | -0.15589 | -0.65547 | -1.2005 | -1.9255 | -2.7065 | -3.4759 | -4.3143 | -5.1993 | -6.5383 | -10.833 | -19.0199 | -25.1737 | -28.9664 | 5.7967 | 5.4963 | 5.1679 | 4.743 | 4.0604 | 3.2293 | 2.3099 | 1.2974 | 0.067959 | -4.1338 | -13.4563 | -25.6082 | -43.3763 | 1.3365 | 0.88317 | 0.38351 | -0.26484 | -0.97507 | -1.6803 | -2.4494 | -3.2536 | -4.444 | -8.2723 | -15.3299 | -20.599 | -23.772
|  | HARVARD LANE | LW |  |  | -0.15589 | -0.65547 | -1.2005 | -1.9255 | -2.7065 | -3.4759 | -4.3143 | -5.1993 | -6.5383 | -10.833 | -19.0199 | -25.1737 | -28.9664 | 5.7967 | 5.4963 | 5.1679 | 4.743 | 4.0604 | 3.2293 | 2.3099 | 1.2974 | 0.067959 | -4.1338 | -13.4563 | -25.6082 | -43.3763 | 1.3365 | 0.88317 | 0.38351 | -0.26484 | -0.97507 | -1.6803 | -2.4494 | -3.2536 | -4.444 | -8.2723 | -15.3299 | -20.599 | -23.772
|  | HARVARD LANE | ST |  |  | -0.15589 | -0.65547 | -1.2005 | -1.9255 | -2.7065 | -3.4759 | -4.3143 | -5.1993 | -6.5383 | -10.833 | -19.0199 | -25.1737 | -28.9664 | 5.7967 | 5.4963 | 5.1679 | 4.743 | 4.0604 | 3.2293 | 2.3099 | 1.2974 | 0.067959 | -4.1338 | -13.4563 | -25.6082 | -43.3763 | 1.3365 | 0.88317 | 0.38351 | -0.26484 | -0.97507 | -1.6803 | -2.4494 | -3.2536 | -4.444 | -8.2723 | -15.3299 | -20.599 | -23.772
|  | HARVARD LANE | FS |  |  | -0.15589 | -0.65547 | -1.2005 | -1.9255 | -2.7065 | -3.4759 | -4.3143 | -5.1993 | -6.5383 | -10.833 | -19.0199 | -25.1737 | -28.9664 | 5.7967 | 5.4963 | 5.1679 | 4.743 | 4.0604 | 3.2293 | 2.3099 | 1.2974 | 0.067959 | -4.1338 | -13.4563 | -25.6082 | -43.3763 | 1.3365 | 0.88317 | 0.38351 | -0.26484 | -0.97507 | -1.6803 | -2.4494 | -3.2536 | -4.444 | -8.2723 | -15.3299 | -20.599 | -23.772
BRAMLEY (FLEE) | FERNHURST | HASLEMERE | MINIMUM HEADROOM | SU 89300 31710 | YES | 15.723 | 15.2803 | 14.7341 | 14.068 | 13.365 | 12.6056 | 11.7562 | 10.768 | 9.3036 | 6.1224 | 0.98801 | -2.8927 | -4.687 | 19.5956 | 19.2552 | 18.8422 | 18.4111 | 17.9507 | 17.4352 | 16.8486 | 16.1444 | 15.1919 | 13.286 | 10.4757 | 8.28 | 6.3883 | 17.7252 | 17.3118 | 16.8158 | 16.2104 | 15.5726 | 14.8866 | 14.1214 | 13.2353 | 11.8857 | 8.9462 | 4.1978 | 0.78343 | -0.78601
|  | HASLEMERE | CT |  |  | 15.723 | 15.2803 | 14.7341 | 14.068 | 13.365 | 12.6056 | 11.7562 | 10.768 | 9.3036 | 6.1224 | 0.98801 | -2.8927 | -4.687 | 19.5956 | 19.2552 | 18.8422 | 18.4111 | 17.9507 | 17.4352 | 16.8486 | 16.1444 | 15.1919 | 13.286 | 10.4757 | 8.28 | 6.3883 | 17.7252 | 17.3118 | 16.8158 | 16.2104 | 15.5726 | 14.8866 | 14.1214 | 13.2353 | 11.8857 | 8.9462 | 4.1978 | 0.78343 | -0.78601
|  | HASLEMERE | LW |  |  | 15.723 | 15.2803 | 14.7341 | 14.068 | 13.365 | 12.6056 | 11.7562 | 10.768 | 9.3036 | 6.1224 | 0.98801 | -2.8927 | -4.687 | 19.5956 | 19.2552 | 18.8422 | 18.4111 | 17.9507 | 17.4352 | 16.8486 | 16.1444 | 15.1919 | 13.286 | 10.4757 | 8.28 | 6.3883 | 17.7252 | 17.3118 | 16.8158 | 16.2104 | 15.5726 | 14.8866 | 14.1214 | 13.2353 | 11.8857 | 8.9462 | 4.1978 | 0.78343 | -0.78601
|  | HASLEMERE | ST |  |  | 15.723 | 15.2803 | 14.7341 | 14.068 | 13.365 | 12.6056 | 11.7562 | 10.768 | 9.3036 | 6.1224 | 0.98801 | -2.8927 | -4.687 | 19.5956 | 19.2552 | 18.8422 | 18.4111 | 17.9507 | 17.4352 | 16.8486 | 16.1444 | 15.1919 | 13.286 | 10.4757 | 8.28 | 6.3883 | 17.7252 | 17.3118 | 16.8158 | 16.2104 | 15.5726 | 14.8866 | 14.1214 | 13.2353 | 11.8857 | 8.9462 | 4.1978 | 0.78343 | -0.78601
|  | HASLEMERE | FS |  |  | 15.723 | 15.2803 | 14.7341 | 14.068 | 13.365 | 12.6056 | 11.7562 | 10.768 | 9.3036 | 6.1224 | 0.98801 | -2.8927 | -4.687 | 19.5956 | 19.2552 | 18.8422 | 18.4111 | 17.9507 | 17.4352 | 16.8486 | 16.1444 | 15.1919 | 13.286 | 10.4757 | 8.28 | 6.3883 | 17.7252 | 17.3118 | 16.8158 | 16.2104 | 15.5726 | 14.8866 | 14.1214 | 13.2353 | 11.8857 | 8.9462 | 4.1978 | 0.78343 | -0.78601
BRAMLEY (FLEE) | FERNHURST | HASLINGBOURNE | MINIMUM HEADROOM | SU 98188 20276 | YES | 9.2354 | 9.0361 | 8.7874 | 8.4312 | 8.0578 | 7.6534 | 7.1877 | 6.6827 | 6.0127 | 4.7751 | 3.149 | 2.0331 | 1.5314 | 12.4275 | 12.3061 | 12.1425 | 11.9478 | 11.7399 | 11.5131 | 11.2386 | 10.9289 | 10.5305 | 9.8508 | 9.0493 | 8.49 | 8.0226 | 10.7514 | 10.5721 | 10.3419 | 10.0301 | 9.7016 | 9.3452 | 8.928 | 8.4568 | 7.8292 | 6.6876 | 5.2233 | 4.2705 | 3.8599
|  | HASLINGBOURNE | CT |  |  | 9.2354 | 9.0361 | 8.7874 | 8.4312 | 8.0578 | 7.6534 | 7.1877 | 6.6827 | 6.0127 | 4.7751 | 3.149 | 2.0331 | 1.5314 | 12.4275 | 12.3061 | 12.1425 | 11.9478 | 11.7399 | 11.5131 | 11.2386 | 10.9289 | 10.5305 | 9.8508 | 9.0493 | 8.49 | 8.0226 | 10.7514 | 10.5721 | 10.3419 | 10.0301 | 9.7016 | 9.3452 | 8.928 | 8.4568 | 7.8292 | 6.6876 | 5.2233 | 4.2705 | 3.8599
|  | HASLINGBOURNE | LW |  |  | 9.2354 | 9.0361 | 8.7874 | 8.4312 | 8.0578 | 7.6534 | 7.1877 | 6.6827 | 6.0127 | 4.7751 | 3.149 | 2.0331 | 1.5314 | 12.4275 | 12.3061 | 12.1425 | 11.9478 | 11.7399 | 11.5131 | 11.2386 | 10.9289 | 10.5305 | 9.8508 | 9.0493 | 8.49 | 8.0226 | 10.7514 | 10.5721 | 10.3419 | 10.0301 | 9.7016 | 9.3452 | 8.928 | 8.4568 | 7.8292 | 6.6876 | 5.2233 | 4.2705 | 3.8599
|  | HASLINGBOURNE | ST |  |  | 9.2354 | 9.0361 | 8.7874 | 8.4312 | 8.0578 | 7.6534 | 7.1877 | 6.6827 | 6.0127 | 4.7751 | 3.149 | 2.0331 | 1.5314 | 12.4275 | 12.3061 | 12.1425 | 11.9478 | 11.7399 | 11.5131 | 11.2386 | 10.9289 | 10.5305 | 9.8508 | 9.0493 | 8.49 | 8.0226 | 10.7514 | 10.5721 | 10.3419 | 10.0301 | 9.7016 | 9.3452 | 8.928 | 8.4568 | 7.8292 | 6.6876 | 5.2233 | 4.2705 | 3.8599
|  | HASLINGBOURNE | FS |  |  | 9.2354 | 9.0361 | 8.7874 | 8.4312 | 8.0578 | 7.6534 | 7.1877 | 6.6827 | 6.0127 | 4.7751 | 3.149 | 2.0331 | 1.5314 | 12.4275 | 12.3061 | 12.1425 | 11.9478 | 11.7399 | 11.5131 | 11.2386 | 10.9289 | 10.5305 | 9.8508 | 9.0493 | 8.49 | 8.0226 | 10.7514 | 10.5721 | 10.3419 | 10.0301 | 9.7016 | 9.3452 | 8.928 | 8.4568 | 7.8292 | 6.6876 | 5.2233 | 4.2705 | 3.8599
MELKSHAM GSP | FROME BSP | HAWKERIDGE | MINIMUM HEADROOM | ST 86422 53026 | YES | 6.7046 | 6.6681 | 6.6233 | 6.5655 | 6.4996 | 6.4224 | 6.3337 | 6.2377 | 6.1044 | 5.6452 | 4.72 | 4.1783 | 3.8577 | 6.2509 | 6.2351 | 6.2163 | 6.1906 | 6.162 | 6.1308 | 6.0952 | 6.0548 | 6 | 5.8167 | 5.4331 | 5.1659 | 4.9978 | 7.0775 | 7.0378 | 6.992 | 6.931 | 6.8629 | 6.7881 | 6.704 | 6.6129 | 6.4865 | 6.0505 | 5.173 | 4.6617 | 4.3571
|  | HAWKERIDGE | CT |  |  | 6.7046 | 6.6681 | 6.6233 | 6.5655 | 6.4996 | 6.4224 | 6.3337 | 6.2377 | 6.1044 | 5.6452 | 4.72 | 4.1783 | 3.8577 | 6.2509 | 6.2351 | 6.2163 | 6.1906 | 6.162 | 6.1308 | 6.0952 | 6.0548 | 6 | 5.8167 | 5.4331 | 5.1659 | 4.9978 | 7.0775 | 7.0378 | 6.992 | 6.931 | 6.8629 | 6.7881 | 6.704 | 6.6129 | 6.4865 | 6.0505 | 5.173 | 4.6617 | 4.3571
|  | HAWKERIDGE | LW |  |  | 6.7046 | 6.6681 | 6.6233 | 6.5655 | 6.4996 | 6.4224 | 6.3337 | 6.2377 | 6.1044 | 5.6452 | 4.72 | 4.1783 | 3.8577 | 6.2509 | 6.2351 | 6.2163 | 6.1906 | 6.162 | 6.1308 | 6.0952 | 6.0548 | 6 | 5.8167 | 5.4331 | 5.1659 | 4.9978 | 7.0775 | 7.0378 | 6.992 | 6.931 | 6.8629 | 6.7881 | 6.704 | 6.6129 | 6.4865 | 6.0505 | 5.173 | 4.6617 | 4.3571
|  | HAWKERIDGE | ST |  |  | 6.7046 | 6.6681 | 6.6233 | 6.5655 | 6.4996 | 6.4224 | 6.3337 | 6.2377 | 6.1044 | 5.6452 | 4.72 | 4.1783 | 3.8577 | 6.2509 | 6.2351 | 6.2163 | 6.1906 | 6.162 | 6.1308 | 6.0952 | 6.0548 | 6 | 5.8167 | 5.4331 | 5.1659 | 4.9978 | 7.0775 | 7.0378 | 6.992 | 6.931 | 6.8629 | 6.7881 | 6.704 | 6.6129 | 6.4865 | 6.0505 | 5.173 | 4.6617 | 4.3571
|  | HAWKERIDGE | FS |  |  | 6.7046 | 6.6681 | 6.6233 | 6.5655 | 6.4996 | 6.4224 | 6.3337 | 6.2377 | 6.1044 | 5.6452 | 4.72 | 4.1783 | 3.8577 | 6.2509 | 6.2351 | 6.2163 | 6.1906 | 6.162 | 6.1308 | 6.0952 | 6.0548 | 6 | 5.8167 | 5.4331 | 5.1659 | 4.9978 | 7.0775 | 7.0378 | 6.992 | 6.931 | 6.8629 | 6.7881 | 6.704 | 6.6129 | 6.4865 | 6.0505 | 5.173 | 4.6617 | 4.3571
BRAMLEY (FLEE) | COXMOOR WOOD BSP | HAWLEY | MINIMUM HEADROOM | SU 85973 57691 | YES | 10.6611 | 10.2527 | 9.7638 | 9.1701 | 8.5656 | 7.9059 | 7.1867 | 6.328 | 5.0363 | 1.7743 | -3.6228 | -7.7333 | -10.1899 | 14.5471 | 14.2186 | 13.8257 | 13.3964 | 12.9628 | 12.4851 | 11.9588 | 11.3156 | 10.4332 | 8.278 | 4.9831 | 2.1698 | -0.66132 | 11.6952 | 11.3216 | 10.8474 | 10.3041 | 9.7451 | 9.1302 | 8.4562 | 7.6397 | 6.4385 | 3.4953 | -1.1241 | -4.6619 | -6.7218
|  | HAWLEY | CT |  |  | 10.6611 | 10.2527 | 9.7638 | 9.1701 | 8.5656 | 7.9059 | 7.1867 | 6.328 | 5.0363 | 1.7743 | -3.6228 | -7.7333 | -10.1899 | 14.5471 | 14.2186 | 13.8257 | 13.3964 | 12.9628 | 12.4851 | 11.9588 | 11.3156 | 10.4332 | 8.278 | 4.9831 | 2.1698 | -0.66132 | 11.6952 | 11.3216 | 10.8474 | 10.3041 | 9.7451 | 9.1302 | 8.4562 | 7.6397 | 6.4385 | 3.4953 | -1.1241 | -4.6619 | -6.7218
|  | HAWLEY | LW |  |  | 10.6611 | 10.2527 | 9.7638 | 9.1701 | 8.5656 | 7.9059 | 7.1867 | 6.328 | 5.0363 | 1.7743 | -3.6228 | -7.7333 | -10.1899 | 14.5471 | 14.2186 | 13.8257 | 13.3964 | 12.9628 | 12.4851 | 11.9588 | 11.3156 | 10.4332 | 8.278 | 4.9831 | 2.1698 | -0.66132 | 11.6952 | 11.3216 | 10.8474 | 10.3041 | 9.7451 | 9.1302 | 8.4562 | 7.6397 | 6.4385 | 3.4953 | -1.1241 | -4.6619 | -6.7218
|  | HAWLEY | ST |  |  | 10.6611 | 10.2527 | 9.7638 | 9.1701 | 8.5656 | 7.9059 | 7.1867 | 6.328 | 5.0363 | 1.7743 | -3.6228 | -7.7333 | -10.1899 | 14.5471 | 14.2186 | 13.8257 | 13.3964 | 12.9628 | 12.4851 | 11.9588 | 11.3156 | 10.4332 | 8.278 | 4.9831 | 2.1698 | -0.66132 | 11.6952 | 11.3216 | 10.8474 | 10.3041 | 9.7451 | 9.1302 | 8.4562 | 7.6397 | 6.4385 | 3.4953 | -1.1241 | -4.6619 | -6.7218
|  | HAWLEY | FS |  |  | 10.6611 | 10.2527 | 9.7638 | 9.1701 | 8.5656 | 7.9059 | 7.1867 | 6.328 | 5.0363 | 1.7743 | -3.6228 | -7.7333 | -10.1899 | 14.5471 | 14.2186 | 13.8257 | 13.3964 | 12.9628 | 12.4851 | 11.9588 | 11.3156 | 10.4332 | 8.278 | 4.9831 | 2.1698 | -0.66132 | 11.6952 | 11.3216 | 10.8474 | 10.3041 | 9.7451 | 9.1302 | 8.4562 | 7.6397 | 6.4385 | 3.4953 | -1.1241 | -4.6619 | -6.7218
NORTH HYDE GSP |  | HAYES | MINIMUM HEADROOM | TQ 09519 79541 |  | 1.1291 | 0.77213 | 0.3266 | -0.59206 | -1.6205 | -2.7092 | -3.8473 | -5.1188 | -7.0809 | -13.4246 | -23.5249 | -30.4938 | -34.1796 | 8.0109 | 7.6471 | 7.2859 | 6.801 | 6.2731 | 5.7072 | 5.1051 | 4.4257 | 3.2891 | -1.2347 | -8.9306 | -16.6663 | -26.4785 | 3.2149 | 2.6602 | 1.9826 | 1.1405 | 0.18483 | -0.85345 | -1.9465 | -3.1831 | -5.014 | -10.9389 | -19.923 | -25.6909 | -28.7091
|  | HAYES | CT |  |  | 1.1291 | 0.77213 | 0.3266 | -0.59206 | -1.6205 | -2.7092 | -3.8473 | -5.1188 | -7.0809 | -13.4246 | -23.5249 | -30.4938 | -34.1796 | 8.0109 | 7.6471 | 7.2859 | 6.801 | 6.2731 | 5.7072 | 5.1051 | 4.4257 | 3.2891 | -1.2347 | -8.9306 | -16.6663 | -26.4785 | 3.2149 | 2.6602 | 1.9826 | 1.1405 | 0.18483 | -0.85345 | -1.9465 | -3.1831 | -5.014 | -10.9389 | -19.923 | -25.6909 | -28.7091
|  | HAYES | LW |  |  | 1.1291 | 0.77213 | 0.3266 | -0.59206 | -1.6205 | -2.7092 | -3.8473 | -5.1188 | -7.0809 | -13.4246 | -23.5249 | -30.4938 | -34.1796 | 8.0109 | 7.6471 | 7.2859 | 6.801 | 6.2731 | 5.7072 | 5.1051 | 4.4257 | 3.2891 | -1.2347 | -8.9306 | -16.6663 | -26.4785 | 3.2149 | 2.6602 | 1.9826 | 1.1405 | 0.18483 | -0.85345 | -1.9465 | -3.1831 | -5.014 | -10.9389 | -19.923 | -25.6909 | -28.7091
|  | HAYES | ST |  |  | 1.1291 | 0.77213 | 0.3266 | -0.59206 | -1.6205 | -2.7092 | -3.8473 | -5.1188 | -7.0809 | -13.4246 | -23.5249 | -30.4938 | -34.1796 | 8.0109 | 7.6471 | 7.2859 | 6.801 | 6.2731 | 5.7072 | 5.1051 | 4.4257 | 3.2891 | -1.2347 | -8.9306 | -16.6663 | -26.4785 | 3.2149 | 2.6602 | 1.9826 | 1.1405 | 0.18483 | -0.85345 | -1.9465 | -3.1831 | -5.014 | -10.9389 | -19.923 | -25.6909 | -28.7091
|  | HAYES | FS |  |  | 1.1291 | 0.77213 | 0.3266 | -0.59206 | -1.6205 | -2.7092 | -3.8473 | -5.1188 | -7.0809 | -13.4246 | -23.5249 | -30.4938 | -34.1796 | 8.0109 | 7.6471 | 7.2859 | 6.801 | 6.2731 | 5.7072 | 5.1051 | 4.4257 | 3.2891 | -1.2347 | -8.9306 | -16.6663 | -26.4785 | 3.2149 | 2.6602 | 1.9826 | 1.1405 | 0.18483 | -0.85345 | -1.9465 | -3.1831 | -5.014 | -10.9389 | -19.923 | -25.6909 | -28.7091
COWLEY GSP | HEADINGTON BSP | HEADINGTON | MINIMUM HEADROOM | SP 54440 08085 | NO | 33.0517 | 32.8319 | 32.5195 | 32.0904 | 31.6644 | 31.2882 | 30.6297 | 29.4071 | 27.7218 | 23.27 | 17.0333 | 12.3311 | 9.7519 | 29.5772 | 29.2685 | 28.7879 | 28.0992 | 27.4 | 26.7552 | 26.056 | 25.268 | 24.2428 | 21.3929 | 17.382 | 13.7655 | 9.6408 | 29.8964 | 29.5498 | 28.9835 | 28.0348 | 27.0732 | 26.2169 | 25.2956 | 24.2686 | 22.8232 | 18.9564 | 13.315 | 9.2799 | 7.1069
|  | HEADINGTON | CT |  |  | 33.0517 | 32.8319 | 32.5195 | 32.0904 | 31.6644 | 31.2882 | 30.6297 | 29.4071 | 27.7218 | 23.27 | 17.0333 | 12.3311 | 9.7519 | 29.5772 | 29.2685 | 28.7879 | 28.0992 | 27.4 | 26.7552 | 26.056 | 25.268 | 24.2428 | 21.3929 | 17.382 | 13.7655 | 9.6408 | 29.8964 | 29.5498 | 28.9835 | 28.0348 | 27.0732 | 26.2169 | 25.2956 | 24.2686 | 22.8232 | 18.9564 | 13.315 | 9.2799 | 7.1069
|  | HEADINGTON | LW |  |  | 33.0517 | 32.8319 | 32.5195 | 32.0904 | 31.6644 | 31.2882 | 30.6297 | 29.4071 | 27.7218 | 23.27 | 17.0333 | 12.3311 | 9.7519 | 29.5772 | 29.2685 | 28.7879 | 28.0992 | 27.4 | 26.7552 | 26.056 | 25.268 | 24.2428 | 21.3929 | 17.382 | 13.7655 | 9.6408 | 29.8964 | 29.5498 | 28.9835 | 28.0348 | 27.0732 | 26.2169 | 25.2956 | 24.2686 | 22.8232 | 18.9564 | 13.315 | 9.2799 | 7.1069
|  | HEADINGTON | ST |  |  | 33.0517 | 32.8319 | 32.5195 | 32.0904 | 31.6644 | 31.2882 | 30.6297 | 29.4071 | 27.7218 | 23.27 | 17.0333 | 12.3311 | 9.7519 | 29.5772 | 29.2685 | 28.7879 | 28.0992 | 27.4 | 26.7552 | 26.056 | 25.268 | 24.2428 | 21.3929 | 17.382 | 13.7655 | 9.6408 | 29.8964 | 29.5498 | 28.9835 | 28.0348 | 27.0732 | 26.2169 | 25.2956 | 24.2686 | 22.8232 | 18.9564 | 13.315 | 9.2799 | 7.1069
|  | HEADINGTON | FS |  |  | 33.0517 | 32.8319 | 32.5195 | 32.0904 | 31.6644 | 31.2882 | 30.6297 | 29.4071 | 27.7218 | 23.27 | 17.0333 | 12.3311 | 9.7519 | 29.5772 | 29.2685 | 28.7879 | 28.0992 | 27.4 | 26.7552 | 26.056 | 25.268 | 24.2428 | 21.3929 | 17.382 | 13.7655 | 9.6408 | 29.8964 | 29.5498 | 28.9835 | 28.0348 | 27.0732 | 26.2169 | 25.2956 | 24.2686 | 22.8232 | 18.9564 | 13.315 | 9.2799 | 7.1069
NURSLING GSP | VELMORE BSP | HEDGE END | MINIMUM HEADROOM | SU 49035 15685 | YES | 4.5244 | 3.9156 | 3.233 | 2.4532 | 1.6592 | 1.0005 | 0.31923 | -0.20689 | -0.84411 | -2.2985 | -4.8145 | -6.5764 | -7.4534 | 7.1647 | 6.6596 | 6.1209 | 5.557 | 4.9846 | 4.4803 | 3.9346 | 3.4458 | 2.8591 | 1.7453 | 0.055876 | -1.2436 | -2.5529 | 5.6356 | 4.9779 | 4.2513 | 3.4485 | 2.6287 | 1.928 | 1.1825 | 0.55848 | -0.21142 | -1.7484 | -4.1307 | -5.6769 | -6.441
|  | HEDGE END | CT |  |  | 4.5244 | 3.9156 | 3.233 | 2.4532 | 1.6592 | 1.0005 | 0.31923 | -0.20689 | -0.84411 | -2.2985 | -4.8145 | -6.5764 | -7.4534 | 7.1647 | 6.6596 | 6.1209 | 5.557 | 4.9846 | 4.4803 | 3.9346 | 3.4458 | 2.8591 | 1.7453 | 0.055876 | -1.2436 | -2.5529 | 5.6356 | 4.9779 | 4.2513 | 3.4485 | 2.6287 | 1.928 | 1.1825 | 0.55848 | -0.21142 | -1.7484 | -4.1307 | -5.6769 | -6.441
|  | HEDGE END | LW |  |  | 4.5244 | 3.9156 | 3.233 | 2.4532 | 1.6592 | 1.0005 | 0.31923 | -0.20689 | -0.84411 | -2.2985 | -4.8145 | -6.5764 | -7.4534 | 7.1647 | 6.6596 | 6.1209 | 5.557 | 4.9846 | 4.4803 | 3.9346 | 3.4458 | 2.8591 | 1.7453 | 0.055876 | -1.2436 | -2.5529 | 5.6356 | 4.9779 | 4.2513 | 3.4485 | 2.6287 | 1.928 | 1.1825 | 0.55848 | -0.21142 | -1.7484 | -4.1307 | -5.6769 | -6.441
|  | HEDGE END | ST |  |  | 4.5244 | 3.9156 | 3.233 | 2.4532 | 1.6592 | 1.0005 | 0.31923 | -0.20689 | -0.84411 | -2.2985 | -4.8145 | -6.5764 | -7.4534 | 7.1647 | 6.6596 | 6.1209 | 5.557 | 4.9846 | 4.4803 | 3.9346 | 3.4458 | 2.8591 | 1.7453 | 0.055876 | -1.2436 | -2.5529 | 5.6356 | 4.9779 | 4.2513 | 3.4485 | 2.6287 | 1.928 | 1.1825 | 0.55848 | -0.21142 | -1.7484 | -4.1307 | -5.6769 | -6.441
|  | HEDGE END | FS |  |  | 4.5244 | 3.9156 | 3.233 | 2.4532 | 1.6592 | 1.0005 | 0.31923 | -0.20689 | -0.84411 | -2.2985 | -4.8145 | -6.5764 | -7.4534 | 7.1647 | 6.6596 | 6.1209 | 5.557 | 4.9846 | 4.4803 | 3.9346 | 3.4458 | 2.8591 | 1.7453 | 0.055876 | -1.2436 | -2.5529 | 5.6356 | 4.9779 | 4.2513 | 3.4485 | 2.6287 | 1.928 | 1.1825 | 0.55848 | -0.21142 | -1.7484 | -4.1307 | -5.6769 | -6.441
BRAMLEY (FLEE) | READING BSP | HENLEY | MINIMUM HEADROOM | SU 76070 82422 | YES | 2.8686 | 2.5084 | 1.997 | 1.1094 | 0.077689 | -1.0002 | -2.1734 | -3.5109 | -5.3025 | -10.523 | -16.2915 | -19.9149 | -21.4642 | 3.5636 | 3.2821 | 2.9021 | 2.3676 | 1.7525 | 1.0858 | 0.35673 | -0.49221 | -1.5577 | -4.5456 | -7.8332 | -10.5234 | -13.2277 | 0.027028 | -0.31909 | -0.80037 | -1.5903 | -2.5018 | -3.4639 | -4.5121 | -5.7138 | -7.3285 | -11.9586 | -17.1248 | -20.3923 | -21.8471
|  | HENLEY | CT |  |  | 2.8686 | 2.5084 | 1.997 | 1.1094 | 0.077689 | -1.0002 | -2.1734 | -3.5109 | -5.3025 | -10.523 | -16.2915 | -19.9149 | -21.4642 | 3.5636 | 3.2821 | 2.9021 | 2.3676 | 1.7525 | 1.0858 | 0.35673 | -0.49221 | -1.5577 | -4.5456 | -7.8332 | -10.5234 | -13.2277 | 0.027028 | -0.31909 | -0.80037 | -1.5903 | -2.5018 | -3.4639 | -4.5121 | -5.7138 | -7.3285 | -11.9586 | -17.1248 | -20.3923 | -21.8471
|  | HENLEY | LW |  |  | 2.8686 | 2.5084 | 1.997 | 1.1094 | 0.077689 | -1.0002 | -2.1734 | -3.5109 | -5.3025 | -10.523 | -16.2915 | -19.9149 | -21.4642 | 3.5636 | 3.2821 | 2.9021 | 2.3676 | 1.7525 | 1.0858 | 0.35673 | -0.49221 | -1.5577 | -4.5456 | -7.8332 | -10.5234 | -13.2277 | 0.027028 | -0.31909 | -0.80037 | -1.5903 | -2.5018 | -3.4639 | -4.5121 | -5.7138 | -7.3285 | -11.9586 | -17.1248 | -20.3923 | -21.8471
|  | HENLEY | ST |  |  | 2.8686 | 2.5084 | 1.997 | 1.1094 | 0.077689 | -1.0002 | -2.1734 | -3.5109 | -5.3025 | -10.523 | -16.2915 | -19.9149 | -21.4642 | 3.5636 | 3.2821 | 2.9021 | 2.3676 | 1.7525 | 1.0858 | 0.35673 | -0.49221 | -1.5577 | -4.5456 | -7.8332 | -10.5234 | -13.2277 | 0.027028 | -0.31909 | -0.80037 | -1.5903 | -2.5018 | -3.4639 | -4.5121 | -5.7138 | -7.3285 | -11.9586 | -17.1248 | -20.3923 | -21.8471
|  | HENLEY | FS |  |  | 2.8686 | 2.5084 | 1.997 | 1.1094 | 0.077689 | -1.0002 | -2.1734 | -3.5109 | -5.3025 | -10.523 | -16.2915 | -19.9149 | -21.4642 | 3.5636 | 3.2821 | 2.9021 | 2.3676 | 1.7525 | 1.0858 | 0.35673 | -0.49221 | -1.5577 | -4.5456 | -7.8332 | -10.5234 | -13.2277 | 0.027028 | -0.31909 | -0.80037 | -1.5903 | -2.5018 | -3.4639 | -4.5121 | -5.7138 | -7.3285 | -11.9586 | -17.1248 | -20.3923 | -21.8471
AXMINSTER | YEOVIL BSP | HENSTRIDGE | MINIMUM HEADROOM | ST 72676 19263 | YES | 20.4198 | 20.044 | 19.6598 | 19.1455 | 18.5956 | 18.0129 | 17.3828 | 16.7349 | 15.8317 | 13.7651 | 10.8818 | 9.3692 | 8.7448 | 22.7881 | 22.6351 | 22.4814 | 22.2803 | 22.0649 | 21.8364 | 21.5635 | 21.304 | 20.9532 | 20.0949 | 18.8246 | 18.1572 | 17.7978 | 22.113 | 21.7964 | 21.4646 | 21.0231 | 20.5511 | 20.0492 | 19.4935 | 18.9299 | 18.1346 | 16.2537 | 13.6477 | 12.3109 | 11.7617
|  | HENSTRIDGE | CT |  |  | 20.4198 | 20.044 | 19.6598 | 19.1455 | 18.5956 | 18.0129 | 17.3828 | 16.7349 | 15.8317 | 13.7651 | 10.8818 | 9.3692 | 8.7448 | 22.7881 | 22.6351 | 22.4814 | 22.2803 | 22.0649 | 21.8364 | 21.5635 | 21.304 | 20.9532 | 20.0949 | 18.8246 | 18.1572 | 17.7978 | 22.113 | 21.7964 | 21.4646 | 21.0231 | 20.5511 | 20.0492 | 19.4935 | 18.9299 | 18.1346 | 16.2537 | 13.6477 | 12.3109 | 11.7617
|  | HENSTRIDGE | LW |  |  | 20.4198 | 20.044 | 19.6598 | 19.1455 | 18.5956 | 18.0129 | 17.3828 | 16.7349 | 15.8317 | 13.7651 | 10.8818 | 9.3692 | 8.7448 | 22.7881 | 22.6351 | 22.4814 | 22.2803 | 22.0649 | 21.8364 | 21.5635 | 21.304 | 20.9532 | 20.0949 | 18.8246 | 18.1572 | 17.7978 | 22.113 | 21.7964 | 21.4646 | 21.0231 | 20.5511 | 20.0492 | 19.4935 | 18.9299 | 18.1346 | 16.2537 | 13.6477 | 12.3109 | 11.7617
|  | HENSTRIDGE | ST |  |  | 20.4198 | 20.044 | 19.6598 | 19.1455 | 18.5956 | 18.0129 | 17.3828 | 16.7349 | 15.8317 | 13.7651 | 10.8818 | 9.3692 | 8.7448 | 22.7881 | 22.6351 | 22.4814 | 22.2803 | 22.0649 | 21.8364 | 21.5635 | 21.304 | 20.9532 | 20.0949 | 18.8246 | 18.1572 | 17.7978 | 22.113 | 21.7964 | 21.4646 | 21.0231 | 20.5511 | 20.0492 | 19.4935 | 18.9299 | 18.1346 | 16.2537 | 13.6477 | 12.3109 | 11.7617
|  | HENSTRIDGE | FS |  |  | 20.4198 | 20.044 | 19.6598 | 19.1455 | 18.5956 | 18.0129 | 17.3828 | 16.7349 | 15.8317 | 13.7651 | 10.8818 | 9.3692 | 8.7448 | 22.7881 | 22.6351 | 22.4814 | 22.2803 | 22.0649 | 21.8364 | 21.5635 | 21.304 | 20.9532 | 20.0949 | 18.8246 | 18.1572 | 17.7978 | 22.113 | 21.7964 | 21.4646 | 21.0231 | 20.5511 | 20.0492 | 19.4935 | 18.9299 | 18.1346 | 16.2537 | 13.6477 | 12.3109 | 11.7617
BRAMLEY (FLEE) | ALTON | HERRIARD | MINIMUM HEADROOM | SU 66770 44972 | YES | 5.8497 | 5.8037 | 5.7593 | 5.6947 | 5.6296 | 5.555 | 5.4702 | 5.3852 | 5.2722 | 5.0412 | 4.6122 | 4.3392 | 4.2382 | 6.0504 | 6.0332 | 6.0164 | 5.9964 | 5.9744 | 5.9422 | 5.906 | 5.8693 | 5.8214 | 5.7138 | 5.5131 | 5.3869 | 5.3165 | 5.3705 | 5.3228 | 5.2772 | 5.2174 | 5.1556 | 5.0838 | 4.9988 | 4.9141 | 4.8008 | 4.6126 | 4.254 | 4.0162 | 3.9271
|  | HERRIARD | CT |  |  | 5.8497 | 5.8037 | 5.7593 | 5.6947 | 5.6296 | 5.555 | 5.4702 | 5.3852 | 5.2722 | 5.0412 | 4.6122 | 4.3392 | 4.2382 | 6.0504 | 6.0332 | 6.0164 | 5.9964 | 5.9744 | 5.9422 | 5.906 | 5.8693 | 5.8214 | 5.7138 | 5.5131 | 5.3869 | 5.3165 | 5.3705 | 5.3228 | 5.2772 | 5.2174 | 5.1556 | 5.0838 | 4.9988 | 4.9141 | 4.8008 | 4.6126 | 4.254 | 4.0162 | 3.9271
|  | HERRIARD | LW |  |  | 5.8497 | 5.8037 | 5.7593 | 5.6947 | 5.6296 | 5.555 | 5.4702 | 5.3852 | 5.2722 | 5.0412 | 4.6122 | 4.3392 | 4.2382 | 6.0504 | 6.0332 | 6.0164 | 5.9964 | 5.9744 | 5.9422 | 5.906 | 5.8693 | 5.8214 | 5.7138 | 5.5131 | 5.3869 | 5.3165 | 5.3705 | 5.3228 | 5.2772 | 5.2174 | 5.1556 | 5.0838 | 4.9988 | 4.9141 | 4.8008 | 4.6126 | 4.254 | 4.0162 | 3.9271
|  | HERRIARD | ST |  |  | 5.8497 | 5.8037 | 5.7593 | 5.6947 | 5.6296 | 5.555 | 5.4702 | 5.3852 | 5.2722 | 5.0412 | 4.6122 | 4.3392 | 4.2382 | 6.0504 | 6.0332 | 6.0164 | 5.9964 | 5.9744 | 5.9422 | 5.906 | 5.8693 | 5.8214 | 5.7138 | 5.5131 | 5.3869 | 5.3165 | 5.3705 | 5.3228 | 5.2772 | 5.2174 | 5.1556 | 5.0838 | 4.9988 | 4.9141 | 4.8008 | 4.6126 | 4.254 | 4.0162 | 3.9271
|  | HERRIARD | FS |  |  | 5.8497 | 5.8037 | 5.7593 | 5.6947 | 5.6296 | 5.555 | 5.4702 | 5.3852 | 5.2722 | 5.0412 | 4.6122 | 4.3392 | 4.2382 | 6.0504 | 6.0332 | 6.0164 | 5.9964 | 5.9744 | 5.9422 | 5.906 | 5.8693 | 5.8214 | 5.7138 | 5.5131 | 5.3869 | 5.3165 | 5.3705 | 5.3228 | 5.2772 | 5.2174 | 5.1556 | 5.0838 | 4.9988 | 4.9141 | 4.8008 | 4.6126 | 4.254 | 4.0162 | 3.9271
COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE | MINIMUM HEADROOM | SU 84733 92200 | YES | 18.7315 | 18.5524 | 18.3333 | 18.1005 | 17.8388 | 17.5449 | 17.2181 | 16.8525 | 16.3529 | 14.4762 | 10.2152 | 8.181 | 7.0742 | 16.8119 | 16.6851 | 16.5271 | 16.3334 | 16.1224 | 15.8956 | 15.6462 | 15.3658 | 14.9259 | 13.6666 | 11.507 | 9.9897 | 8.8002 | 19.8925 | 19.7253 | 19.5127 | 19.2878 | 19.0348 | 18.7506 | 18.4346 | 18.052 | 17.4738 | 15.517 | 11.5122 | 9.6669 | 8.7342
|  | HIGH WYCOMBE | CT |  |  | 18.7315 | 18.5524 | 18.3333 | 18.1005 | 17.8388 | 17.5449 | 17.2181 | 16.8525 | 16.3529 | 14.4762 | 10.2152 | 8.181 | 7.0742 | 16.8119 | 16.6851 | 16.5271 | 16.3334 | 16.1224 | 15.8956 | 15.6462 | 15.3658 | 14.9259 | 13.6666 | 11.507 | 9.9897 | 8.8002 | 19.8925 | 19.7253 | 19.5127 | 19.2878 | 19.0348 | 18.7506 | 18.4346 | 18.052 | 17.4738 | 15.517 | 11.5122 | 9.6669 | 8.7342
|  | HIGH WYCOMBE | LW |  |  | 18.7315 | 18.5524 | 18.3333 | 18.1005 | 17.8388 | 17.5449 | 17.2181 | 16.8525 | 16.3529 | 14.4762 | 10.2152 | 8.181 | 7.0742 | 16.8119 | 16.6851 | 16.5271 | 16.3334 | 16.1224 | 15.8956 | 15.6462 | 15.3658 | 14.9259 | 13.6666 | 11.507 | 9.9897 | 8.8002 | 19.8925 | 19.7253 | 19.5127 | 19.2878 | 19.0348 | 18.7506 | 18.4346 | 18.052 | 17.4738 | 15.517 | 11.5122 | 9.6669 | 8.7342
|  | HIGH WYCOMBE | ST |  |  | 18.7315 | 18.5524 | 18.3333 | 18.1005 | 17.8388 | 17.5449 | 17.2181 | 16.8525 | 16.3529 | 14.4762 | 10.2152 | 8.181 | 7.0742 | 16.8119 | 16.6851 | 16.5271 | 16.3334 | 16.1224 | 15.8956 | 15.6462 | 15.3658 | 14.9259 | 13.6666 | 11.507 | 9.9897 | 8.8002 | 19.8925 | 19.7253 | 19.5127 | 19.2878 | 19.0348 | 18.7506 | 18.4346 | 18.052 | 17.4738 | 15.517 | 11.5122 | 9.6669 | 8.7342
|  | HIGH WYCOMBE | FS |  |  | 18.7315 | 18.5524 | 18.3333 | 18.1005 | 17.8388 | 17.5449 | 17.2181 | 16.8525 | 16.3529 | 14.4762 | 10.2152 | 8.181 | 7.0742 | 16.8119 | 16.6851 | 16.5271 | 16.3334 | 16.1224 | 15.8956 | 15.6462 | 15.3658 | 14.9259 | 13.6666 | 11.507 | 9.9897 | 8.8002 | 19.8925 | 19.7253 | 19.5127 | 19.2878 | 19.0348 | 18.7506 | 18.4346 | 18.052 | 17.4738 | 15.517 | 11.5122 | 9.6669 | 8.7342
COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE TOWN | MINIMUM HEADROOM | SU 86304 92972 | YES | 55.3692 | 55.1196 | 54.8183 | 54.3598 | 53.8709 | 53.3877 | 52.8646 | 52.2727 | 51.3438 | 48.6086 | 43.5353 | 39.7599 | 37.536 | 50.513 | 50.3946 | 50.2545 | 50.0704 | 49.8016 | 49.5243 | 49.223 | 48.8482 | 48.2675 | 46.5212 | 43.2083 | 40.1384 | 36.6851 | 52.5003 | 52.3651 | 52.2043 | 51.8848 | 51.4268 | 50.9678 | 50.4644 | 49.8747 | 48.9721 | 46.4023 | 41.9872 | 38.8056 | 36.9531
|  | HIGH WYCOMBE TOWN | CT |  |  | 55.3692 | 55.1196 | 54.8183 | 54.3598 | 53.8709 | 53.3877 | 52.8646 | 52.2727 | 51.3438 | 48.6086 | 43.5353 | 39.7599 | 37.536 | 50.513 | 50.3946 | 50.2545 | 50.0704 | 49.8016 | 49.5243 | 49.223 | 48.8482 | 48.2675 | 46.5212 | 43.2083 | 40.1384 | 36.6851 | 52.5003 | 52.3651 | 52.2043 | 51.8848 | 51.4268 | 50.9678 | 50.4644 | 49.8747 | 48.9721 | 46.4023 | 41.9872 | 38.8056 | 36.9531
|  | HIGH WYCOMBE TOWN | LW |  |  | 55.3692 | 55.1196 | 54.8183 | 54.3598 | 53.8709 | 53.3877 | 52.8646 | 52.2727 | 51.3438 | 48.6086 | 43.5353 | 39.7599 | 37.536 | 50.513 | 50.3946 | 50.2545 | 50.0704 | 49.8016 | 49.5243 | 49.223 | 48.8482 | 48.2675 | 46.5212 | 43.2083 | 40.1384 | 36.6851 | 52.5003 | 52.3651 | 52.2043 | 51.8848 | 51.4268 | 50.9678 | 50.4644 | 49.8747 | 48.9721 | 46.4023 | 41.9872 | 38.8056 | 36.9531
|  | HIGH WYCOMBE TOWN | ST |  |  | 55.3692 | 55.1196 | 54.8183 | 54.3598 | 53.8709 | 53.3877 | 52.8646 | 52.2727 | 51.3438 | 48.6086 | 43.5353 | 39.7599 | 37.536 | 50.513 | 50.3946 | 50.2545 | 50.0704 | 49.8016 | 49.5243 | 49.223 | 48.8482 | 48.2675 | 46.5212 | 43.2083 | 40.1384 | 36.6851 | 52.5003 | 52.3651 | 52.2043 | 51.8848 | 51.4268 | 50.9678 | 50.4644 | 49.8747 | 48.9721 | 46.4023 | 41.9872 | 38.8056 | 36.9531
|  | HIGH WYCOMBE TOWN | FS |  |  | 55.3692 | 55.1196 | 54.8183 | 54.3598 | 53.8709 | 53.3877 | 52.8646 | 52.2727 | 51.3438 | 48.6086 | 43.5353 | 39.7599 | 37.536 | 50.513 | 50.3946 | 50.2545 | 50.0704 | 49.8016 | 49.5243 | 49.223 | 48.8482 | 48.2675 | 46.5212 | 43.2083 | 40.1384 | 36.6851 | 52.5003 | 52.3651 | 52.2043 | 51.8848 | 51.4268 | 50.9678 | 50.4644 | 49.8747 | 48.9721 | 46.4023 | 41.9872 | 38.8056 | 36.9531
LOVEDEAN GSP | WYMERING BSP | HILSEA | MINIMUM HEADROOM | SU 66394 03806 | YES | 26.3831 | 26.3 | 26.2204 | 26.128 | 26.0276 | 25.9224 | 25.8068 | 25.6691 | 25.4902 | 24.9029 | 23.8608 | 23.2539 | 22.8794 | 28.8651 | 28.7891 | 28.7219 | 28.6452 | 28.5289 | 28.4028 | 28.2619 | 28.0933 | 27.8865 | 27.1022 | 25.7551 | 25.3507 | 25.1235 | 26.2155 | 26.1336 | 26.0574 | 25.9718 | 25.8781 | 25.7493 | 25.544 | 25.3028 | 24.9905 | 23.9555 | 22.2015 | 21.6359 | 21.3339
|  | HILSEA | CT |  |  | 26.3831 | 26.3 | 26.2204 | 26.128 | 26.0276 | 25.9224 | 25.8068 | 25.6691 | 25.4902 | 24.9029 | 23.8608 | 23.2539 | 22.8794 | 28.8651 | 28.7891 | 28.7219 | 28.6452 | 28.5289 | 28.4028 | 28.2619 | 28.0933 | 27.8865 | 27.1022 | 25.7551 | 25.3507 | 25.1235 | 26.2155 | 26.1336 | 26.0574 | 25.9718 | 25.8781 | 25.7493 | 25.544 | 25.3028 | 24.9905 | 23.9555 | 22.2015 | 21.6359 | 21.3339
|  | HILSEA | LW |  |  | 26.3831 | 26.3 | 26.2204 | 26.128 | 26.0276 | 25.9224 | 25.8068 | 25.6691 | 25.4902 | 24.9029 | 23.8608 | 23.2539 | 22.8794 | 28.8651 | 28.7891 | 28.7219 | 28.6452 | 28.5289 | 28.4028 | 28.2619 | 28.0933 | 27.8865 | 27.1022 | 25.7551 | 25.3507 | 25.1235 | 26.2155 | 26.1336 | 26.0574 | 25.9718 | 25.8781 | 25.7493 | 25.544 | 25.3028 | 24.9905 | 23.9555 | 22.2015 | 21.6359 | 21.3339
|  | HILSEA | ST |  |  | 26.3831 | 26.3 | 26.2204 | 26.128 | 26.0276 | 25.9224 | 25.8068 | 25.6691 | 25.4902 | 24.9029 | 23.8608 | 23.2539 | 22.8794 | 28.8651 | 28.7891 | 28.7219 | 28.6452 | 28.5289 | 28.4028 | 28.2619 | 28.0933 | 27.8865 | 27.1022 | 25.7551 | 25.3507 | 25.1235 | 26.2155 | 26.1336 | 26.0574 | 25.9718 | 25.8781 | 25.7493 | 25.544 | 25.3028 | 24.9905 | 23.9555 | 22.2015 | 21.6359 | 21.3339
|  | HILSEA | FS |  |  | 26.3831 | 26.3 | 26.2204 | 26.128 | 26.0276 | 25.9224 | 25.8068 | 25.6691 | 25.4902 | 24.9029 | 23.8608 | 23.2539 | 22.8794 | 28.8651 | 28.7891 | 28.7219 | 28.6452 | 28.5289 | 28.4028 | 28.2619 | 28.0933 | 27.8865 | 27.1022 | 25.7551 | 25.3507 | 25.1235 | 26.2155 | 26.1336 | 26.0574 | 25.9718 | 25.8781 | 25.7493 | 25.544 | 25.3028 | 24.9905 | 23.9555 | 22.2015 | 21.6359 | 21.3339
MANNINGTON GSP | ARNEWOOD | HINCHESLEA | MINIMUM HEADROOM | SU 27805 00447 | YES | 11.9864 | 11.8589 | 11.7008 | 11.4915 | 11.2632 | 11.0124 | 10.7251 | 10.3946 | 9.8387 | 8.7889 | 7.0709 | 5.743 | 5.1666 | 11.6503 | 11.5441 | 11.4071 | 11.2679 | 11.1167 | 10.9457 | 10.744 | 10.5041 | 10.1374 | 9.5607 | 8.7898 | 8.1965 | 7.7183 | 11.5391 | 11.4063 | 11.2386 | 11.0365 | 10.8203 | 10.5819 | 10.3074 | 9.99 | 9.4615 | 8.4942 | 6.9945 | 5.9096 | 5.4415
|  | HINCHESLEA | CT |  |  | 11.9864 | 11.8589 | 11.7008 | 11.4915 | 11.2632 | 11.0124 | 10.7251 | 10.3946 | 9.8387 | 8.7889 | 7.0709 | 5.743 | 5.1666 | 11.6503 | 11.5441 | 11.4071 | 11.2679 | 11.1167 | 10.9457 | 10.744 | 10.5041 | 10.1374 | 9.5607 | 8.7898 | 8.1965 | 7.7183 | 11.5391 | 11.4063 | 11.2386 | 11.0365 | 10.8203 | 10.5819 | 10.3074 | 9.99 | 9.4615 | 8.4942 | 6.9945 | 5.9096 | 5.4415
|  | HINCHESLEA | LW |  |  | 11.9864 | 11.8589 | 11.7008 | 11.4915 | 11.2632 | 11.0124 | 10.7251 | 10.3946 | 9.8387 | 8.7889 | 7.0709 | 5.743 | 5.1666 | 11.6503 | 11.5441 | 11.4071 | 11.2679 | 11.1167 | 10.9457 | 10.744 | 10.5041 | 10.1374 | 9.5607 | 8.7898 | 8.1965 | 7.7183 | 11.5391 | 11.4063 | 11.2386 | 11.0365 | 10.8203 | 10.5819 | 10.3074 | 9.99 | 9.4615 | 8.4942 | 6.9945 | 5.9096 | 5.4415
|  | HINCHESLEA | ST |  |  | 11.9864 | 11.8589 | 11.7008 | 11.4915 | 11.2632 | 11.0124 | 10.7251 | 10.3946 | 9.8387 | 8.7889 | 7.0709 | 5.743 | 5.1666 | 11.6503 | 11.5441 | 11.4071 | 11.2679 | 11.1167 | 10.9457 | 10.744 | 10.5041 | 10.1374 | 9.5607 | 8.7898 | 8.1965 | 7.7183 | 11.5391 | 11.4063 | 11.2386 | 11.0365 | 10.8203 | 10.5819 | 10.3074 | 9.99 | 9.4615 | 8.4942 | 6.9945 | 5.9096 | 5.4415
|  | HINCHESLEA | FS |  |  | 11.9864 | 11.8589 | 11.7008 | 11.4915 | 11.2632 | 11.0124 | 10.7251 | 10.3946 | 9.8387 | 8.7889 | 7.0709 | 5.743 | 5.1666 | 11.6503 | 11.5441 | 11.4071 | 11.2679 | 11.1167 | 10.9457 | 10.744 | 10.5041 | 10.1374 | 9.5607 | 8.7898 | 8.1965 | 7.7183 | 11.5391 | 11.4063 | 11.2386 | 11.0365 | 10.8203 | 10.5819 | 10.3074 | 9.99 | 9.4615 | 8.4942 | 6.9945 | 5.9096 | 5.4415
BRAMLEY (FLEE) | ALDERSHOT BSP | HINDHEAD | MINIMUM HEADROOM | SU 88631 36479 | YES | 8.2889 | 7.9807 | 7.6342 | 7.1611 | 6.6609 | 6.1203 | 5.5097 | 4.8284 | 3.8056 | 1.61 | -2.0068 | -4.5681 | -5.7234 | 11.2738 | 11.0429 | 10.7779 | 10.4816 | 10.1629 | 9.7988 | 9.3776 | 8.8928 | 8.2381 | 7.0317 | 5.3416 | 4.1149 | 3.2188 | 9.7821 | 9.507 | 9.1985 | 8.7691 | 8.3156 | 7.8282 | 7.2793 | 6.6693 | 5.7453 | 3.7232 | 0.33469 | -2.0749 | -3.1585
|  | HINDHEAD | CT |  |  | 8.2889 | 7.9807 | 7.6342 | 7.1611 | 6.6609 | 6.1203 | 5.5097 | 4.8284 | 3.8056 | 1.61 | -2.0068 | -4.5681 | -5.7234 | 11.2738 | 11.0429 | 10.7779 | 10.4816 | 10.1629 | 9.7988 | 9.3776 | 8.8928 | 8.2381 | 7.0317 | 5.3416 | 4.1149 | 3.2188 | 9.7821 | 9.507 | 9.1985 | 8.7691 | 8.3156 | 7.8282 | 7.2793 | 6.6693 | 5.7453 | 3.7232 | 0.33469 | -2.0749 | -3.1585
|  | HINDHEAD | LW |  |  | 8.2889 | 7.9807 | 7.6342 | 7.1611 | 6.6609 | 6.1203 | 5.5097 | 4.8284 | 3.8056 | 1.61 | -2.0068 | -4.5681 | -5.7234 | 11.2738 | 11.0429 | 10.7779 | 10.4816 | 10.1629 | 9.7988 | 9.3776 | 8.8928 | 8.2381 | 7.0317 | 5.3416 | 4.1149 | 3.2188 | 9.7821 | 9.507 | 9.1985 | 8.7691 | 8.3156 | 7.8282 | 7.2793 | 6.6693 | 5.7453 | 3.7232 | 0.33469 | -2.0749 | -3.1585
|  | HINDHEAD | ST |  |  | 8.2889 | 7.9807 | 7.6342 | 7.1611 | 6.6609 | 6.1203 | 5.5097 | 4.8284 | 3.8056 | 1.61 | -2.0068 | -4.5681 | -5.7234 | 11.2738 | 11.0429 | 10.7779 | 10.4816 | 10.1629 | 9.7988 | 9.3776 | 8.8928 | 8.2381 | 7.0317 | 5.3416 | 4.1149 | 3.2188 | 9.7821 | 9.507 | 9.1985 | 8.7691 | 8.3156 | 7.8282 | 7.2793 | 6.6693 | 5.7453 | 3.7232 | 0.33469 | -2.0749 | -3.1585
|  | HINDHEAD | FS |  |  | 8.2889 | 7.9807 | 7.6342 | 7.1611 | 6.6609 | 6.1203 | 5.5097 | 4.8284 | 3.8056 | 1.61 | -2.0068 | -4.5681 | -5.7234 | 11.2738 | 11.0429 | 10.7779 | 10.4816 | 10.1629 | 9.7988 | 9.3776 | 8.8928 | 8.2381 | 7.0317 | 5.3416 | 4.1149 | 3.2188 | 9.7821 | 9.507 | 9.1985 | 8.7691 | 8.3156 | 7.8282 | 7.2793 | 6.6693 | 5.7453 | 3.7232 | 0.33469 | -2.0749 | -3.1585
MANNINGTON GSP | MANNINGTON BSP | HINTON MARTELL | MINIMUM HEADROOM | SU 00702 06030 | YES | 1.868 | 1.8052 | 1.7396 | 1.6492 | 1.5554 | 1.4462 | 1.3266 | 1.2077 | 1.0682 | 0.79762 | 0.33031 | 0.066541 | -0.045602 | 2.8323 | 2.7886 | 2.7413 | 2.6871 | 2.63 | 2.5593 | 2.4786 | 2.3973 | 2.3064 | 2.1635 | 1.9129 | 1.7735 | 1.6724 | 2.4524 | 2.3919 | 2.3276 | 2.2467 | 2.162 | 2.06 | 1.9457 | 1.8314 | 1.6999 | 1.4765 | 1.0952 | 0.87671 | 0.77893
|  | HINTON MARTELL | CT |  |  | 1.868 | 1.8052 | 1.7396 | 1.6492 | 1.5554 | 1.4462 | 1.3266 | 1.2077 | 1.0682 | 0.79762 | 0.33031 | 0.066541 | -0.045602 | 2.8323 | 2.7886 | 2.7413 | 2.6871 | 2.63 | 2.5593 | 2.4786 | 2.3973 | 2.3064 | 2.1635 | 1.9129 | 1.7735 | 1.6724 | 2.4524 | 2.3919 | 2.3276 | 2.2467 | 2.162 | 2.06 | 1.9457 | 1.8314 | 1.6999 | 1.4765 | 1.0952 | 0.87671 | 0.77893
|  | HINTON MARTELL | LW |  |  | 1.868 | 1.8052 | 1.7396 | 1.6492 | 1.5554 | 1.4462 | 1.3266 | 1.2077 | 1.0682 | 0.79762 | 0.33031 | 0.066541 | -0.045602 | 2.8323 | 2.7886 | 2.7413 | 2.6871 | 2.63 | 2.5593 | 2.4786 | 2.3973 | 2.3064 | 2.1635 | 1.9129 | 1.7735 | 1.6724 | 2.4524 | 2.3919 | 2.3276 | 2.2467 | 2.162 | 2.06 | 1.9457 | 1.8314 | 1.6999 | 1.4765 | 1.0952 | 0.87671 | 0.77893
|  | HINTON MARTELL | ST |  |  | 1.868 | 1.8052 | 1.7396 | 1.6492 | 1.5554 | 1.4462 | 1.3266 | 1.2077 | 1.0682 | 0.79762 | 0.33031 | 0.066541 | -0.045602 | 2.8323 | 2.7886 | 2.7413 | 2.6871 | 2.63 | 2.5593 | 2.4786 | 2.3973 | 2.3064 | 2.1635 | 1.9129 | 1.7735 | 1.6724 | 2.4524 | 2.3919 | 2.3276 | 2.2467 | 2.162 | 2.06 | 1.9457 | 1.8314 | 1.6999 | 1.4765 | 1.0952 | 0.87671 | 0.77893
|  | HINTON MARTELL | FS |  |  | 1.868 | 1.8052 | 1.7396 | 1.6492 | 1.5554 | 1.4462 | 1.3266 | 1.2077 | 1.0682 | 0.79762 | 0.33031 | 0.066541 | -0.045602 | 2.8323 | 2.7886 | 2.7413 | 2.6871 | 2.63 | 2.5593 | 2.4786 | 2.3973 | 2.3064 | 2.1635 | 1.9129 | 1.7735 | 1.6724 | 2.4524 | 2.3919 | 2.3276 | 2.2467 | 2.162 | 2.06 | 1.9457 | 1.8314 | 1.6999 | 1.4765 | 1.0952 | 0.87671 | 0.77893
BRAMLEY (FLEE) | COXMOOR WOOD BSP | HITCHES LANE | MINIMUM HEADROOM | SU 79461 54769 | YES | 1.4744 | 0.70974 | -0.092794 | -1.143 | -2.285 | -3.4092 | -4.759 | -6.2526 | -8.4499 | -13.3862 | -20.2412 | -24.33 | -26.0498 | 5.5587 | 5.0089 | 4.4279 | 3.7664 | 3.045 | 2.2988 | 1.3895 | 0.37087 | -1.0475 | -4.0296 | -7.9777 | -10.3601 | -12.1809 | 4.052 | 3.3447 | 2.6011 | 1.6445 | 0.60541 | -0.42934 | -1.6772 | -3.062 | -5.1055 | -9.611 | -15.8346 | -19.4551 | -20.9653
|  | HITCHES LANE | CT |  |  | 1.4744 | 0.70974 | -0.092794 | -1.143 | -2.285 | -3.4092 | -4.759 | -6.2526 | -8.4499 | -13.3862 | -20.2412 | -24.33 | -26.0498 | 5.5587 | 5.0089 | 4.4279 | 3.7664 | 3.045 | 2.2988 | 1.3895 | 0.37087 | -1.0475 | -4.0296 | -7.9777 | -10.3601 | -12.1809 | 4.052 | 3.3447 | 2.6011 | 1.6445 | 0.60541 | -0.42934 | -1.6772 | -3.062 | -5.1055 | -9.611 | -15.8346 | -19.4551 | -20.9653
|  | HITCHES LANE | LW |  |  | 1.4744 | 0.70974 | -0.092794 | -1.143 | -2.285 | -3.4092 | -4.759 | -6.2526 | -8.4499 | -13.3862 | -20.2412 | -24.33 | -26.0498 | 5.5587 | 5.0089 | 4.4279 | 3.7664 | 3.045 | 2.2988 | 1.3895 | 0.37087 | -1.0475 | -4.0296 | -7.9777 | -10.3601 | -12.1809 | 4.052 | 3.3447 | 2.6011 | 1.6445 | 0.60541 | -0.42934 | -1.6772 | -3.062 | -5.1055 | -9.611 | -15.8346 | -19.4551 | -20.9653
|  | HITCHES LANE | ST |  |  | 1.4744 | 0.70974 | -0.092794 | -1.143 | -2.285 | -3.4092 | -4.759 | -6.2526 | -8.4499 | -13.3862 | -20.2412 | -24.33 | -26.0498 | 5.5587 | 5.0089 | 4.4279 | 3.7664 | 3.045 | 2.2988 | 1.3895 | 0.37087 | -1.0475 | -4.0296 | -7.9777 | -10.3601 | -12.1809 | 4.052 | 3.3447 | 2.6011 | 1.6445 | 0.60541 | -0.42934 | -1.6772 | -3.062 | -5.1055 | -9.611 | -15.8346 | -19.4551 | -20.9653
|  | HITCHES LANE | FS |  |  | 1.4744 | 0.70974 | -0.092794 | -1.143 | -2.285 | -3.4092 | -4.759 | -6.2526 | -8.4499 | -13.3862 | -20.2412 | -24.33 | -26.0498 | 5.5587 | 5.0089 | 4.4279 | 3.7664 | 3.045 | 2.2988 | 1.3895 | 0.37087 | -1.0475 | -4.0296 | -7.9777 | -10.3601 | -12.1809 | 4.052 | 3.3447 | 2.6011 | 1.6445 | 0.60541 | -0.42934 | -1.6772 | -3.062 | -5.1055 | -9.611 | -15.8346 | -19.4551 | -20.9653
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | HOEFORD | MINIMUM HEADROOM | SU 57855 04433 | YES | 6.9579 | 6.5692 | 6.1112 | 5.5962 | 5.0821 | 4.5108 | 3.9123 | 3.2643 | 2.2739 | -0.98857 | -6.4573 | -10.8675 | -13.6863 | 10.3928 | 10.2438 | 10.0404 | 9.8227 | 9.6202 | 9.3192 | 8.8802 | 8.3891 | 7.7077 | 5.4982 | 2.3444 | -0.29231 | -2.8233 | 9.1092 | 8.8787 | 8.5224 | 8.0959 | 7.6459 | 7.0976 | 6.5202 | 5.8867 | 4.9378 | 1.8262 | -2.9464 | -6.6695 | -9.0198
|  | HOEFORD | CT |  |  | 6.9579 | 6.5692 | 6.1112 | 5.5962 | 5.0821 | 4.5108 | 3.9123 | 3.2643 | 2.2739 | -0.98857 | -6.4573 | -10.8675 | -13.6863 | 10.3928 | 10.2438 | 10.0404 | 9.8227 | 9.6202 | 9.3192 | 8.8802 | 8.3891 | 7.7077 | 5.4982 | 2.3444 | -0.29231 | -2.8233 | 9.1092 | 8.8787 | 8.5224 | 8.0959 | 7.6459 | 7.0976 | 6.5202 | 5.8867 | 4.9378 | 1.8262 | -2.9464 | -6.6695 | -9.0198
|  | HOEFORD | LW |  |  | 6.9579 | 6.5692 | 6.1112 | 5.5962 | 5.0821 | 4.5108 | 3.9123 | 3.2643 | 2.2739 | -0.98857 | -6.4573 | -10.8675 | -13.6863 | 10.3928 | 10.2438 | 10.0404 | 9.8227 | 9.6202 | 9.3192 | 8.8802 | 8.3891 | 7.7077 | 5.4982 | 2.3444 | -0.29231 | -2.8233 | 9.1092 | 8.8787 | 8.5224 | 8.0959 | 7.6459 | 7.0976 | 6.5202 | 5.8867 | 4.9378 | 1.8262 | -2.9464 | -6.6695 | -9.0198
|  | HOEFORD | ST |  |  | 6.9579 | 6.5692 | 6.1112 | 5.5962 | 5.0821 | 4.5108 | 3.9123 | 3.2643 | 2.2739 | -0.98857 | -6.4573 | -10.8675 | -13.6863 | 10.3928 | 10.2438 | 10.0404 | 9.8227 | 9.6202 | 9.3192 | 8.8802 | 8.3891 | 7.7077 | 5.4982 | 2.3444 | -0.29231 | -2.8233 | 9.1092 | 8.8787 | 8.5224 | 8.0959 | 7.6459 | 7.0976 | 6.5202 | 5.8867 | 4.9378 | 1.8262 | -2.9464 | -6.6695 | -9.0198
|  | HOEFORD | FS |  |  | 6.9579 | 6.5692 | 6.1112 | 5.5962 | 5.0821 | 4.5108 | 3.9123 | 3.2643 | 2.2739 | -0.98857 | -6.4573 | -10.8675 | -13.6863 | 10.3928 | 10.2438 | 10.0404 | 9.8227 | 9.6202 | 9.3192 | 8.8802 | 8.3891 | 7.7077 | 5.4982 | 2.3444 | -0.29231 | -2.8233 | 9.1092 | 8.8787 | 8.5224 | 8.0959 | 7.6459 | 7.0976 | 6.5202 | 5.8867 | 4.9378 | 1.8262 | -2.9464 | -6.6695 | -9.0198
MANNINGTON GSP | LYTCHETT | HOLES BAY | MINIMUM HEADROOM | SZ 00725 91955 | YES | 11.5298 | 11.3775 | 11.2072 | 11.0227 | 10.8269 | 10.6194 | 10.3993 | 10.1478 | 9.7971 | 8.722 | 6.7879 | 5.6003 | 4.9134 | 13.0916 | 12.952 | 12.7993 | 12.6653 | 12.5236 | 12.3733 | 12.2156 | 12.0342 | 11.8177 | 11.1511 | 10.1068 | 9.6232 | 9.2467 | 13.3469 | 13.1992 | 13.0347 | 12.8788 | 12.7124 | 12.5346 | 12.3459 | 12.1256 | 11.8511 | 11.0008 | 9.6185 | 8.9794 | 8.5979
|  | HOLES BAY | CT |  |  | 11.5298 | 11.3775 | 11.2072 | 11.0227 | 10.8269 | 10.6194 | 10.3993 | 10.1478 | 9.7971 | 8.722 | 6.7879 | 5.6003 | 4.9134 | 13.0916 | 12.952 | 12.7993 | 12.6653 | 12.5236 | 12.3733 | 12.2156 | 12.0342 | 11.8177 | 11.1511 | 10.1068 | 9.6232 | 9.2467 | 13.3469 | 13.1992 | 13.0347 | 12.8788 | 12.7124 | 12.5346 | 12.3459 | 12.1256 | 11.8511 | 11.0008 | 9.6185 | 8.9794 | 8.5979
|  | HOLES BAY | LW |  |  | 11.5298 | 11.3775 | 11.2072 | 11.0227 | 10.8269 | 10.6194 | 10.3993 | 10.1478 | 9.7971 | 8.722 | 6.7879 | 5.6003 | 4.9134 | 13.0916 | 12.952 | 12.7993 | 12.6653 | 12.5236 | 12.3733 | 12.2156 | 12.0342 | 11.8177 | 11.1511 | 10.1068 | 9.6232 | 9.2467 | 13.3469 | 13.1992 | 13.0347 | 12.8788 | 12.7124 | 12.5346 | 12.3459 | 12.1256 | 11.8511 | 11.0008 | 9.6185 | 8.9794 | 8.5979
|  | HOLES BAY | ST |  |  | 11.5298 | 11.3775 | 11.2072 | 11.0227 | 10.8269 | 10.6194 | 10.3993 | 10.1478 | 9.7971 | 8.722 | 6.7879 | 5.6003 | 4.9134 | 13.0916 | 12.952 | 12.7993 | 12.6653 | 12.5236 | 12.3733 | 12.2156 | 12.0342 | 11.8177 | 11.1511 | 10.1068 | 9.6232 | 9.2467 | 13.3469 | 13.1992 | 13.0347 | 12.8788 | 12.7124 | 12.5346 | 12.3459 | 12.1256 | 11.8511 | 11.0008 | 9.6185 | 8.9794 | 8.5979
|  | HOLES BAY | FS |  |  | 11.5298 | 11.3775 | 11.2072 | 11.0227 | 10.8269 | 10.6194 | 10.3993 | 10.1478 | 9.7971 | 8.722 | 6.7879 | 5.6003 | 4.9134 | 13.0916 | 12.952 | 12.7993 | 12.6653 | 12.5236 | 12.3733 | 12.2156 | 12.0342 | 11.8177 | 11.1511 | 10.1068 | 9.6232 | 9.2467 | 13.3469 | 13.1992 | 13.0347 | 12.8788 | 12.7124 | 12.5346 | 12.3459 | 12.1256 | 11.8511 | 11.0008 | 9.6185 | 8.9794 | 8.5979
MELKSHAM GSP | FROME BSP | HOLWELL | MINIMUM HEADROOM | ST 72191 44633 | YES | 8.0645 | 7.9767 | 7.9134 | 7.8327 | 7.7513 | 7.6618 | 7.5087 | 7.3846 | 7.2283 | 6.8753 | 6.4179 | 6.1557 | 6.0401 | 8.0336 | 8.0034 | 7.9795 | 7.9483 | 7.9182 | 7.8819 | 7.7922 | 7.74 | 7.6709 | 7.4813 | 7.2205 | 7.1314 | 7.0498 | 7.421 | 7.3411 | 7.2816 | 7.2069 | 7.1313 | 7.0482 | 6.9051 | 6.7885 | 6.6396 | 6.3048 | 5.9013 | 5.6713 | 5.5695
|  | HOLWELL | CT |  |  | 8.0645 | 7.9767 | 7.9134 | 7.8327 | 7.7513 | 7.6618 | 7.5087 | 7.3846 | 7.2283 | 6.8753 | 6.4179 | 6.1557 | 6.0401 | 8.0336 | 8.0034 | 7.9795 | 7.9483 | 7.9182 | 7.8819 | 7.7922 | 7.74 | 7.6709 | 7.4813 | 7.2205 | 7.1314 | 7.0498 | 7.421 | 7.3411 | 7.2816 | 7.2069 | 7.1313 | 7.0482 | 6.9051 | 6.7885 | 6.6396 | 6.3048 | 5.9013 | 5.6713 | 5.5695
|  | HOLWELL | LW |  |  | 8.0645 | 7.9767 | 7.9134 | 7.8327 | 7.7513 | 7.6618 | 7.5087 | 7.3846 | 7.2283 | 6.8753 | 6.4179 | 6.1557 | 6.0401 | 8.0336 | 8.0034 | 7.9795 | 7.9483 | 7.9182 | 7.8819 | 7.7922 | 7.74 | 7.6709 | 7.4813 | 7.2205 | 7.1314 | 7.0498 | 7.421 | 7.3411 | 7.2816 | 7.2069 | 7.1313 | 7.0482 | 6.9051 | 6.7885 | 6.6396 | 6.3048 | 5.9013 | 5.6713 | 5.5695
|  | HOLWELL | ST |  |  | 8.0645 | 7.9767 | 7.9134 | 7.8327 | 7.7513 | 7.6618 | 7.5087 | 7.3846 | 7.2283 | 6.8753 | 6.4179 | 6.1557 | 6.0401 | 8.0336 | 8.0034 | 7.9795 | 7.9483 | 7.9182 | 7.8819 | 7.7922 | 7.74 | 7.6709 | 7.4813 | 7.2205 | 7.1314 | 7.0498 | 7.421 | 7.3411 | 7.2816 | 7.2069 | 7.1313 | 7.0482 | 6.9051 | 6.7885 | 6.6396 | 6.3048 | 5.9013 | 5.6713 | 5.5695
|  | HOLWELL | FS |  |  | 8.0645 | 7.9767 | 7.9134 | 7.8327 | 7.7513 | 7.6618 | 7.5087 | 7.3846 | 7.2283 | 6.8753 | 6.4179 | 6.1557 | 6.0401 | 8.0336 | 8.0034 | 7.9795 | 7.9483 | 7.9182 | 7.8819 | 7.7922 | 7.74 | 7.6709 | 7.4813 | 7.2205 | 7.1314 | 7.0498 | 7.421 | 7.3411 | 7.2816 | 7.2069 | 7.1313 | 7.0482 | 6.9051 | 6.7885 | 6.6396 | 6.3048 | 5.9013 | 5.6713 | 5.5695
MANNINGTON GSP | SALISBURY | HOMINGTON | MINIMUM HEADROOM | SU 11742 26037 | YES | 13.3966 | 13.3075 | 13.201 | 13.0789 | 12.9444 | 12.7493 | 12.474 | 12.1496 | 11.74 | 10.9012 | 9.5836 | 8.8567 | 8.5547 | 12.7991 | 12.7402 | 12.669 | 12.5911 | 12.5049 | 12.4087 | 12.3004 | 12.1581 | 11.9909 | 11.4841 | 10.7227 | 10.5656 | 10.4611 | 14.3447 | 14.2278 | 14.0934 | 13.911 | 13.7189 | 13.5053 | 13.2623 | 12.9791 | 12.6218 | 11.8285 | 10.5698 | 9.9052 | 9.6382
|  | HOMINGTON | CT |  |  | 13.3966 | 13.3075 | 13.201 | 13.0789 | 12.9444 | 12.7493 | 12.474 | 12.1496 | 11.74 | 10.9012 | 9.5836 | 8.8567 | 8.5547 | 12.7991 | 12.7402 | 12.669 | 12.5911 | 12.5049 | 12.4087 | 12.3004 | 12.1581 | 11.9909 | 11.4841 | 10.7227 | 10.5656 | 10.4611 | 14.3447 | 14.2278 | 14.0934 | 13.911 | 13.7189 | 13.5053 | 13.2623 | 12.9791 | 12.6218 | 11.8285 | 10.5698 | 9.9052 | 9.6382
|  | HOMINGTON | LW |  |  | 13.3966 | 13.3075 | 13.201 | 13.0789 | 12.9444 | 12.7493 | 12.474 | 12.1496 | 11.74 | 10.9012 | 9.5836 | 8.8567 | 8.5547 | 12.7991 | 12.7402 | 12.669 | 12.5911 | 12.5049 | 12.4087 | 12.3004 | 12.1581 | 11.9909 | 11.4841 | 10.7227 | 10.5656 | 10.4611 | 14.3447 | 14.2278 | 14.0934 | 13.911 | 13.7189 | 13.5053 | 13.2623 | 12.9791 | 12.6218 | 11.8285 | 10.5698 | 9.9052 | 9.6382
|  | HOMINGTON | ST |  |  | 13.3966 | 13.3075 | 13.201 | 13.0789 | 12.9444 | 12.7493 | 12.474 | 12.1496 | 11.74 | 10.9012 | 9.5836 | 8.8567 | 8.5547 | 12.7991 | 12.7402 | 12.669 | 12.5911 | 12.5049 | 12.4087 | 12.3004 | 12.1581 | 11.9909 | 11.4841 | 10.7227 | 10.5656 | 10.4611 | 14.3447 | 14.2278 | 14.0934 | 13.911 | 13.7189 | 13.5053 | 13.2623 | 12.9791 | 12.6218 | 11.8285 | 10.5698 | 9.9052 | 9.6382
|  | HOMINGTON | FS |  |  | 13.3966 | 13.3075 | 13.201 | 13.0789 | 12.9444 | 12.7493 | 12.474 | 12.1496 | 11.74 | 10.9012 | 9.5836 | 8.8567 | 8.5547 | 12.7991 | 12.7402 | 12.669 | 12.5911 | 12.5049 | 12.4087 | 12.3004 | 12.1581 | 11.9909 | 11.4841 | 10.7227 | 10.5656 | 10.4611 | 14.3447 | 14.2278 | 14.0934 | 13.911 | 13.7189 | 13.5053 | 13.2623 | 12.9791 | 12.6218 | 11.8285 | 10.5698 | 9.9052 | 9.6382
BRAMLEY (FLEE) | COXMOOR WOOD BSP | HOOK | MINIMUM HEADROOM | SU 72602 53780 | YES | 23.8879 | 23.4667 | 23.027 | 22.4322 | 21.8111 | 21.1563 | 20.3889 | 19.4998 | 18.2093 | 15.3236 | 10.4194 | 7.3373 | 5.9771 | 23.5764 | 23.2443 | 22.8946 | 22.4829 | 22.0564 | 21.5913 | 21.0352 | 20.3779 | 19.5059 | 17.6861 | 14.7579 | 12.7892 | 11.1596 | 21.4314 | 21.017 | 20.584 | 20.0139 | 19.4242 | 18.7988 | 18.0626 | 17.2067 | 15.9787 | 13.2915 | 8.8204 | 6.0103 | 4.7256
|  | HOOK | CT |  |  | 23.8879 | 23.4667 | 23.027 | 22.4322 | 21.8111 | 21.1563 | 20.3889 | 19.4998 | 18.2093 | 15.3236 | 10.4194 | 7.3373 | 5.9771 | 23.5764 | 23.2443 | 22.8946 | 22.4829 | 22.0564 | 21.5913 | 21.0352 | 20.3779 | 19.5059 | 17.6861 | 14.7579 | 12.7892 | 11.1596 | 21.4314 | 21.017 | 20.584 | 20.0139 | 19.4242 | 18.7988 | 18.0626 | 17.2067 | 15.9787 | 13.2915 | 8.8204 | 6.0103 | 4.7256
|  | HOOK | LW |  |  | 23.8879 | 23.4667 | 23.027 | 22.4322 | 21.8111 | 21.1563 | 20.3889 | 19.4998 | 18.2093 | 15.3236 | 10.4194 | 7.3373 | 5.9771 | 23.5764 | 23.2443 | 22.8946 | 22.4829 | 22.0564 | 21.5913 | 21.0352 | 20.3779 | 19.5059 | 17.6861 | 14.7579 | 12.7892 | 11.1596 | 21.4314 | 21.017 | 20.584 | 20.0139 | 19.4242 | 18.7988 | 18.0626 | 17.2067 | 15.9787 | 13.2915 | 8.8204 | 6.0103 | 4.7256
|  | HOOK | ST |  |  | 23.8879 | 23.4667 | 23.027 | 22.4322 | 21.8111 | 21.1563 | 20.3889 | 19.4998 | 18.2093 | 15.3236 | 10.4194 | 7.3373 | 5.9771 | 23.5764 | 23.2443 | 22.8946 | 22.4829 | 22.0564 | 21.5913 | 21.0352 | 20.3779 | 19.5059 | 17.6861 | 14.7579 | 12.7892 | 11.1596 | 21.4314 | 21.017 | 20.584 | 20.0139 | 19.4242 | 18.7988 | 18.0626 | 17.2067 | 15.9787 | 13.2915 | 8.8204 | 6.0103 | 4.7256
|  | HOOK | FS |  |  | 23.8879 | 23.4667 | 23.027 | 22.4322 | 21.8111 | 21.1563 | 20.3889 | 19.4998 | 18.2093 | 15.3236 | 10.4194 | 7.3373 | 5.9771 | 23.5764 | 23.2443 | 22.8946 | 22.4829 | 22.0564 | 21.5913 | 21.0352 | 20.3779 | 19.5059 | 17.6861 | 14.7579 | 12.7892 | 11.1596 | 21.4314 | 21.017 | 20.584 | 20.0139 | 19.4242 | 18.7988 | 18.0626 | 17.2067 | 15.9787 | 13.2915 | 8.8204 | 6.0103 | 4.7256
LALEHAM | EAST BEDFONT A | HOPE AND ANCHOR | MINIMUM HEADROOM | TQ 12710 72057 | YES | -1.671 | -1.7777 | -1.9167 | -2.0854 | -2.2681 | -2.4578 | -2.6597 | -2.8759 | -3.1564 | -4.177 | -7.0653 | -10.2856 | -13.0226 | -0.2494 | -0.31547 | -0.40751 | -0.50952 | -0.62096 | -0.73983 | -0.86715 | -1.007 | -1.1814 | -1.8149 | -3.4408 | -5.3495 | -7.3262 | -1.1985 | -1.2867 | -1.406 | -1.5513 | -1.709 | -1.8741 | -2.0503 | -2.2406 | -2.49 | -3.3884 | -5.8135 | -8.4572 | -10.683
|  | HOPE AND ANCHOR | CT |  |  | -1.671 | -1.7777 | -1.9167 | -2.0854 | -2.2681 | -2.4578 | -2.6597 | -2.8759 | -3.1564 | -4.177 | -7.0653 | -10.2856 | -13.0226 | -0.2494 | -0.31547 | -0.40751 | -0.50952 | -0.62096 | -0.73983 | -0.86715 | -1.007 | -1.1814 | -1.8149 | -3.4408 | -5.3495 | -7.3262 | -1.1985 | -1.2867 | -1.406 | -1.5513 | -1.709 | -1.8741 | -2.0503 | -2.2406 | -2.49 | -3.3884 | -5.8135 | -8.4572 | -10.683
|  | HOPE AND ANCHOR | LW |  |  | -1.671 | -1.7777 | -1.9167 | -2.0854 | -2.2681 | -2.4578 | -2.6597 | -2.8759 | -3.1564 | -4.177 | -7.0653 | -10.2856 | -13.0226 | -0.2494 | -0.31547 | -0.40751 | -0.50952 | -0.62096 | -0.73983 | -0.86715 | -1.007 | -1.1814 | -1.8149 | -3.4408 | -5.3495 | -7.3262 | -1.1985 | -1.2867 | -1.406 | -1.5513 | -1.709 | -1.8741 | -2.0503 | -2.2406 | -2.49 | -3.3884 | -5.8135 | -8.4572 | -10.683
|  | HOPE AND ANCHOR | ST |  |  | -1.671 | -1.7777 | -1.9167 | -2.0854 | -2.2681 | -2.4578 | -2.6597 | -2.8759 | -3.1564 | -4.177 | -7.0653 | -10.2856 | -13.0226 | -0.2494 | -0.31547 | -0.40751 | -0.50952 | -0.62096 | -0.73983 | -0.86715 | -1.007 | -1.1814 | -1.8149 | -3.4408 | -5.3495 | -7.3262 | -1.1985 | -1.2867 | -1.406 | -1.5513 | -1.709 | -1.8741 | -2.0503 | -2.2406 | -2.49 | -3.3884 | -5.8135 | -8.4572 | -10.683
|  | HOPE AND ANCHOR | FS |  |  | -1.671 | -1.7777 | -1.9167 | -2.0854 | -2.2681 | -2.4578 | -2.6597 | -2.8759 | -3.1564 | -4.177 | -7.0653 | -10.2856 | -13.0226 | -0.2494 | -0.31547 | -0.40751 | -0.50952 | -0.62096 | -0.73983 | -0.86715 | -1.007 | -1.1814 | -1.8149 | -3.4408 | -5.3495 | -7.3262 | -1.1985 | -1.2867 | -1.406 | -1.5513 | -1.709 | -1.8741 | -2.0503 | -2.2406 | -2.49 | -3.3884 | -5.8135 | -8.4572 | -10.683
LOVEDEAN GSP | HAVANT | HORNDEAN | MINIMUM HEADROOM | SU 70271 12802 | YES | 14.9588 | 14.0802 | 13.136 | 12.0061 | 10.8078 | 9.5288 | 8.0561 | 6.3777 | 3.7193 | -2.2146 | -11.2805 | -18.2636 | -22.0858 | 18.3998 | 17.7489 | 17.0021 | 16.2238 | 15.3929 | 14.4836 | 13.4121 | 12.1552 | 10.3931 | 6.7978 | 1.8012 | -2.266 | -6.0026 | 14.9611 | 14.1735 | 13.2979 | 12.2615 | 11.161 | 9.9805 | 8.614 | 7.0461 | 4.6784 | -0.64663 | -8.7987 | -14.8271 | -18.0677
|  | HORNDEAN | CT |  |  | 14.9588 | 14.0802 | 13.136 | 12.0061 | 10.8078 | 9.5288 | 8.0561 | 6.3777 | 3.7193 | -2.2146 | -11.2805 | -18.2636 | -22.0858 | 18.3998 | 17.7489 | 17.0021 | 16.2238 | 15.3929 | 14.4836 | 13.4121 | 12.1552 | 10.3931 | 6.7978 | 1.8012 | -2.266 | -6.0026 | 14.9611 | 14.1735 | 13.2979 | 12.2615 | 11.161 | 9.9805 | 8.614 | 7.0461 | 4.6784 | -0.64663 | -8.7987 | -14.8271 | -18.0677
|  | HORNDEAN | LW |  |  | 14.9588 | 14.0802 | 13.136 | 12.0061 | 10.8078 | 9.5288 | 8.0561 | 6.3777 | 3.7193 | -2.2146 | -11.2805 | -18.2636 | -22.0858 | 18.3998 | 17.7489 | 17.0021 | 16.2238 | 15.3929 | 14.4836 | 13.4121 | 12.1552 | 10.3931 | 6.7978 | 1.8012 | -2.266 | -6.0026 | 14.9611 | 14.1735 | 13.2979 | 12.2615 | 11.161 | 9.9805 | 8.614 | 7.0461 | 4.6784 | -0.64663 | -8.7987 | -14.8271 | -18.0677
|  | HORNDEAN | ST |  |  | 14.9588 | 14.0802 | 13.136 | 12.0061 | 10.8078 | 9.5288 | 8.0561 | 6.3777 | 3.7193 | -2.2146 | -11.2805 | -18.2636 | -22.0858 | 18.3998 | 17.7489 | 17.0021 | 16.2238 | 15.3929 | 14.4836 | 13.4121 | 12.1552 | 10.3931 | 6.7978 | 1.8012 | -2.266 | -6.0026 | 14.9611 | 14.1735 | 13.2979 | 12.2615 | 11.161 | 9.9805 | 8.614 | 7.0461 | 4.6784 | -0.64663 | -8.7987 | -14.8271 | -18.0677
|  | HORNDEAN | FS |  |  | 14.9588 | 14.0802 | 13.136 | 12.0061 | 10.8078 | 9.5288 | 8.0561 | 6.3777 | 3.7193 | -2.2146 | -11.2805 | -18.2636 | -22.0858 | 18.3998 | 17.7489 | 17.0021 | 16.2238 | 15.3929 | 14.4836 | 13.4121 | 12.1552 | 10.3931 | 6.7978 | 1.8012 | -2.266 | -6.0026 | 14.9611 | 14.1735 | 13.2979 | 12.2615 | 11.161 | 9.9805 | 8.614 | 7.0461 | 4.6784 | -0.64663 | -8.7987 | -14.8271 | -18.0677
NURSLING GSP | WINCHESTER | HOUGHTON | MINIMUM HEADROOM | SU 33784 31741 | YES | 11.9575 | 11.7621 | 11.5632 | 11.2702 | 10.965 | 10.6389 | 10.28 | 9.9083 | 9.3725 | 8.126 | 6.3057 | 5.9163 | 5.8115 | 14.5896 | 14.5317 | 14.4721 | 14.4077 | 14.3364 | 14.2599 | 14.174 | 14.0856 | 13.8819 | 13.2619 | 12.4333 | 12.1697 | 11.973 | 13.7369 | 13.6413 | 13.4979 | 13.2657 | 13.026 | 12.7764 | 12.5096 | 12.2346 | 11.7715 | 10.6705 | 9.0612 | 8.7112 | 8.6159
|  | HOUGHTON | CT |  |  | 11.9575 | 11.7621 | 11.5632 | 11.2702 | 10.965 | 10.6389 | 10.28 | 9.9083 | 9.3725 | 8.126 | 6.3057 | 5.9163 | 5.8115 | 14.5896 | 14.5317 | 14.4721 | 14.4077 | 14.3364 | 14.2599 | 14.174 | 14.0856 | 13.8819 | 13.2619 | 12.4333 | 12.1697 | 11.973 | 13.7369 | 13.6413 | 13.4979 | 13.2657 | 13.026 | 12.7764 | 12.5096 | 12.2346 | 11.7715 | 10.6705 | 9.0612 | 8.7112 | 8.6159
|  | HOUGHTON | LW |  |  | 11.9575 | 11.7621 | 11.5632 | 11.2702 | 10.965 | 10.6389 | 10.28 | 9.9083 | 9.3725 | 8.126 | 6.3057 | 5.9163 | 5.8115 | 14.5896 | 14.5317 | 14.4721 | 14.4077 | 14.3364 | 14.2599 | 14.174 | 14.0856 | 13.8819 | 13.2619 | 12.4333 | 12.1697 | 11.973 | 13.7369 | 13.6413 | 13.4979 | 13.2657 | 13.026 | 12.7764 | 12.5096 | 12.2346 | 11.7715 | 10.6705 | 9.0612 | 8.7112 | 8.6159
|  | HOUGHTON | ST |  |  | 11.9575 | 11.7621 | 11.5632 | 11.2702 | 10.965 | 10.6389 | 10.28 | 9.9083 | 9.3725 | 8.126 | 6.3057 | 5.9163 | 5.8115 | 14.5896 | 14.5317 | 14.4721 | 14.4077 | 14.3364 | 14.2599 | 14.174 | 14.0856 | 13.8819 | 13.2619 | 12.4333 | 12.1697 | 11.973 | 13.7369 | 13.6413 | 13.4979 | 13.2657 | 13.026 | 12.7764 | 12.5096 | 12.2346 | 11.7715 | 10.6705 | 9.0612 | 8.7112 | 8.6159
|  | HOUGHTON | FS |  |  | 11.9575 | 11.7621 | 11.5632 | 11.2702 | 10.965 | 10.6389 | 10.28 | 9.9083 | 9.3725 | 8.126 | 6.3057 | 5.9163 | 5.8115 | 14.5896 | 14.5317 | 14.4721 | 14.4077 | 14.3364 | 14.2599 | 14.174 | 14.0856 | 13.8819 | 13.2619 | 12.4333 | 12.1697 | 11.973 | 13.7369 | 13.6413 | 13.4979 | 13.2657 | 13.026 | 12.7764 | 12.5096 | 12.2346 | 11.7715 | 10.6705 | 9.0612 | 8.7112 | 8.6159
BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | HOUNDMILLS | MINIMUM HEADROOM | SU 62187 52886 | YES | 34.152 | 33.5809 | 32.7159 | 31.6158 | 30.7145 | 29.7911 | 28.7728 | 27.5999 | 26.1774 | 21.6308 | 18.1405 | 16.3512 | 15.5891 | 29.0826 | 28.7703 | 28.3578 | 27.8413 | 27.2865 | 26.7184 | 26.1018 | 25.389 | 24.5349 | 22.0967 | 19.9811 | 18.6127 | 17.3512 | 31.9588 | 31.5843 | 31.0627 | 30.0212 | 29.1572 | 28.2674 | 27.2816 | 26.1317 | 24.7212 | 20.7528 | 17.5634 | 15.8962 | 15.1838
|  | HOUNDMILLS | CT |  |  | 34.152 | 33.5809 | 32.7159 | 31.6158 | 30.7145 | 29.7911 | 28.7728 | 27.5999 | 26.1774 | 21.6308 | 18.1405 | 16.3512 | 15.5891 | 29.0826 | 28.7703 | 28.3578 | 27.8413 | 27.2865 | 26.7184 | 26.1018 | 25.389 | 24.5349 | 22.0967 | 19.9811 | 18.6127 | 17.3512 | 31.9588 | 31.5843 | 31.0627 | 30.0212 | 29.1572 | 28.2674 | 27.2816 | 26.1317 | 24.7212 | 20.7528 | 17.5634 | 15.8962 | 15.1838
|  | HOUNDMILLS | LW |  |  | 34.152 | 33.5809 | 32.7159 | 31.6158 | 30.7145 | 29.7911 | 28.7728 | 27.5999 | 26.1774 | 21.6308 | 18.1405 | 16.3512 | 15.5891 | 29.0826 | 28.7703 | 28.3578 | 27.8413 | 27.2865 | 26.7184 | 26.1018 | 25.389 | 24.5349 | 22.0967 | 19.9811 | 18.6127 | 17.3512 | 31.9588 | 31.5843 | 31.0627 | 30.0212 | 29.1572 | 28.2674 | 27.2816 | 26.1317 | 24.7212 | 20.7528 | 17.5634 | 15.8962 | 15.1838
|  | HOUNDMILLS | ST |  |  | 34.152 | 33.5809 | 32.7159 | 31.6158 | 30.7145 | 29.7911 | 28.7728 | 27.5999 | 26.1774 | 21.6308 | 18.1405 | 16.3512 | 15.5891 | 29.0826 | 28.7703 | 28.3578 | 27.8413 | 27.2865 | 26.7184 | 26.1018 | 25.389 | 24.5349 | 22.0967 | 19.9811 | 18.6127 | 17.3512 | 31.9588 | 31.5843 | 31.0627 | 30.0212 | 29.1572 | 28.2674 | 27.2816 | 26.1317 | 24.7212 | 20.7528 | 17.5634 | 15.8962 | 15.1838
|  | HOUNDMILLS | FS |  |  | 34.152 | 33.5809 | 32.7159 | 31.6158 | 30.7145 | 29.7911 | 28.7728 | 27.5999 | 26.1774 | 21.6308 | 18.1405 | 16.3512 | 15.5891 | 29.0826 | 28.7703 | 28.3578 | 27.8413 | 27.2865 | 26.7184 | 26.1018 | 25.389 | 24.5349 | 22.0967 | 19.9811 | 18.6127 | 17.3512 | 31.9588 | 31.5843 | 31.0627 | 30.0212 | 29.1572 | 28.2674 | 27.2816 | 26.1317 | 24.7212 | 20.7528 | 17.5634 | 15.8962 | 15.1838
BRAMLEY (ANDO-THAT) | THATCHAM BSP | HUNGERFORD | MINIMUM HEADROOM | SU 34066 68957 | YES | 6.4928 | 6.3974 | 6.2898 | 6.112 | 5.9248 | 5.7311 | 5.4143 | 5.0182 | 4.3599 | 2.4884 | -0.92227 | -2.9742 | -3.1833 | 9.8209 | 9.7251 | 9.6065 | 9.4375 | 9.2481 | 9.0475 | 8.8265 | 8.5828 | 8.2064 | 7.2278 | 5.6493 | 4.6398 | 4.2003 | 8.4048 | 8.2665 | 8.1102 | 7.8374 | 7.5523 | 7.2567 | 6.9348 | 6.5954 | 6.0241 | 4.2865 | 1.297 | -0.51042 | -0.69543
|  | HUNGERFORD | CT |  |  | 6.4928 | 6.3974 | 6.2898 | 6.112 | 5.9248 | 5.7311 | 5.4143 | 5.0182 | 4.3599 | 2.4884 | -0.92227 | -2.9742 | -3.1833 | 9.8209 | 9.7251 | 9.6065 | 9.4375 | 9.2481 | 9.0475 | 8.8265 | 8.5828 | 8.2064 | 7.2278 | 5.6493 | 4.6398 | 4.2003 | 8.4048 | 8.2665 | 8.1102 | 7.8374 | 7.5523 | 7.2567 | 6.9348 | 6.5954 | 6.0241 | 4.2865 | 1.297 | -0.51042 | -0.69543
|  | HUNGERFORD | LW |  |  | 6.4928 | 6.3974 | 6.2898 | 6.112 | 5.9248 | 5.7311 | 5.4143 | 5.0182 | 4.3599 | 2.4884 | -0.92227 | -2.9742 | -3.1833 | 9.8209 | 9.7251 | 9.6065 | 9.4375 | 9.2481 | 9.0475 | 8.8265 | 8.5828 | 8.2064 | 7.2278 | 5.6493 | 4.6398 | 4.2003 | 8.4048 | 8.2665 | 8.1102 | 7.8374 | 7.5523 | 7.2567 | 6.9348 | 6.5954 | 6.0241 | 4.2865 | 1.297 | -0.51042 | -0.69543
|  | HUNGERFORD | ST |  |  | 6.4928 | 6.3974 | 6.2898 | 6.112 | 5.9248 | 5.7311 | 5.4143 | 5.0182 | 4.3599 | 2.4884 | -0.92227 | -2.9742 | -3.1833 | 9.8209 | 9.7251 | 9.6065 | 9.4375 | 9.2481 | 9.0475 | 8.8265 | 8.5828 | 8.2064 | 7.2278 | 5.6493 | 4.6398 | 4.2003 | 8.4048 | 8.2665 | 8.1102 | 7.8374 | 7.5523 | 7.2567 | 6.9348 | 6.5954 | 6.0241 | 4.2865 | 1.297 | -0.51042 | -0.69543
|  | HUNGERFORD | FS |  |  | 6.4928 | 6.3974 | 6.2898 | 6.112 | 5.9248 | 5.7311 | 5.4143 | 5.0182 | 4.3599 | 2.4884 | -0.92227 | -2.9742 | -3.1833 | 9.8209 | 9.7251 | 9.6065 | 9.4375 | 9.2481 | 9.0475 | 8.8265 | 8.5828 | 8.2064 | 7.2278 | 5.6493 | 4.6398 | 4.2003 | 8.4048 | 8.2665 | 8.1102 | 7.8374 | 7.5523 | 7.2567 | 6.9348 | 6.5954 | 6.0241 | 4.2865 | 1.297 | -0.51042 | -0.69543
LOVEDEAN GSP | CHICHESTER & HUNSTON | HUNSTON | MINIMUM HEADROOM | SU 86949 02632 | YES | 18.5661 | 18.3636 | 18.1586 | 17.958 | 17.742 | 17.5103 | 17.2175 | 16.7897 | 16.2656 | 14.0907 | 10.8354 | 9.0613 | 8.247 | 25.5002 | 25.3445 | 25.191 | 25.0496 | 24.8875 | 24.6706 | 24.4134 | 24.0854 | 23.6591 | 22.1705 | 20.2708 | 19.0944 | 17.9973 | 19.5811 | 19.3996 | 19.2169 | 19.0435 | 18.8581 | 18.6596 | 18.4443 | 18.0279 | 17.2458 | 14.8702 | 11.9712 | 10.4073 | 9.6948
|  | HUNSTON | CT |  |  | 18.5661 | 18.3636 | 18.1586 | 17.958 | 17.742 | 17.5103 | 17.2175 | 16.7897 | 16.2656 | 14.0907 | 10.8354 | 9.0613 | 8.247 | 25.5002 | 25.3445 | 25.191 | 25.0496 | 24.8875 | 24.6706 | 24.4134 | 24.0854 | 23.6591 | 22.1705 | 20.2708 | 19.0944 | 17.9973 | 19.5811 | 19.3996 | 19.2169 | 19.0435 | 18.8581 | 18.6596 | 18.4443 | 18.0279 | 17.2458 | 14.8702 | 11.9712 | 10.4073 | 9.6948
|  | HUNSTON | LW |  |  | 18.5661 | 18.3636 | 18.1586 | 17.958 | 17.742 | 17.5103 | 17.2175 | 16.7897 | 16.2656 | 14.0907 | 10.8354 | 9.0613 | 8.247 | 25.5002 | 25.3445 | 25.191 | 25.0496 | 24.8875 | 24.6706 | 24.4134 | 24.0854 | 23.6591 | 22.1705 | 20.2708 | 19.0944 | 17.9973 | 19.5811 | 19.3996 | 19.2169 | 19.0435 | 18.8581 | 18.6596 | 18.4443 | 18.0279 | 17.2458 | 14.8702 | 11.9712 | 10.4073 | 9.6948
|  | HUNSTON | ST |  |  | 18.5661 | 18.3636 | 18.1586 | 17.958 | 17.742 | 17.5103 | 17.2175 | 16.7897 | 16.2656 | 14.0907 | 10.8354 | 9.0613 | 8.247 | 25.5002 | 25.3445 | 25.191 | 25.0496 | 24.8875 | 24.6706 | 24.4134 | 24.0854 | 23.6591 | 22.1705 | 20.2708 | 19.0944 | 17.9973 | 19.5811 | 19.3996 | 19.2169 | 19.0435 | 18.8581 | 18.6596 | 18.4443 | 18.0279 | 17.2458 | 14.8702 | 11.9712 | 10.4073 | 9.6948
|  | HUNSTON | FS |  |  | 18.5661 | 18.3636 | 18.1586 | 17.958 | 17.742 | 17.5103 | 17.2175 | 16.7897 | 16.2656 | 14.0907 | 10.8354 | 9.0613 | 8.247 | 25.5002 | 25.3445 | 25.191 | 25.0496 | 24.8875 | 24.6706 | 24.4134 | 24.0854 | 23.6591 | 22.1705 | 20.2708 | 19.0944 | 17.9973 | 19.5811 | 19.3996 | 19.2169 | 19.0435 | 18.8581 | 18.6596 | 18.4443 | 18.0279 | 17.2458 | 14.8702 | 11.9712 | 10.4073 | 9.6948
BRAMLEY (ANDO-THAT) | ANDOVER BSP | HURSTBOURNE TARRANT | MINIMUM HEADROOM | SU 39384 52476 | YES | 3.5672 | 3.443 | 3.3111 | 3.1206 | 2.9251 | 2.7144 | 2.4635 | 2.1883 | 1.8294 | 1.1726 | 0.031835 | -0.71159 | -0.87224 | 4.3643 | 4.2885 | 4.2067 | 4.101 | 3.9921 | 3.8739 | 3.7282 | 3.5641 | 3.3548 | 3.018 | 2.4839 | 2.1262 | 1.9357 | 4.0601 | 3.9431 | 3.8184 | 3.642 | 3.4609 | 3.2656 | 3.0307 | 2.7715 | 2.4332 | 1.8379 | 0.86982 | 0.27522 | 0.1496
|  | HURSTBOURNE TARRANT | CT |  |  | 3.5672 | 3.443 | 3.3111 | 3.1206 | 2.9251 | 2.7144 | 2.4635 | 2.1883 | 1.8294 | 1.1726 | 0.031835 | -0.71159 | -0.87224 | 4.3643 | 4.2885 | 4.2067 | 4.101 | 3.9921 | 3.8739 | 3.7282 | 3.5641 | 3.3548 | 3.018 | 2.4839 | 2.1262 | 1.9357 | 4.0601 | 3.9431 | 3.8184 | 3.642 | 3.4609 | 3.2656 | 3.0307 | 2.7715 | 2.4332 | 1.8379 | 0.86982 | 0.27522 | 0.1496
|  | HURSTBOURNE TARRANT | LW |  |  | 3.5672 | 3.443 | 3.3111 | 3.1206 | 2.9251 | 2.7144 | 2.4635 | 2.1883 | 1.8294 | 1.1726 | 0.031835 | -0.71159 | -0.87224 | 4.3643 | 4.2885 | 4.2067 | 4.101 | 3.9921 | 3.8739 | 3.7282 | 3.5641 | 3.3548 | 3.018 | 2.4839 | 2.1262 | 1.9357 | 4.0601 | 3.9431 | 3.8184 | 3.642 | 3.4609 | 3.2656 | 3.0307 | 2.7715 | 2.4332 | 1.8379 | 0.86982 | 0.27522 | 0.1496
|  | HURSTBOURNE TARRANT | ST |  |  | 3.5672 | 3.443 | 3.3111 | 3.1206 | 2.9251 | 2.7144 | 2.4635 | 2.1883 | 1.8294 | 1.1726 | 0.031835 | -0.71159 | -0.87224 | 4.3643 | 4.2885 | 4.2067 | 4.101 | 3.9921 | 3.8739 | 3.7282 | 3.5641 | 3.3548 | 3.018 | 2.4839 | 2.1262 | 1.9357 | 4.0601 | 3.9431 | 3.8184 | 3.642 | 3.4609 | 3.2656 | 3.0307 | 2.7715 | 2.4332 | 1.8379 | 0.86982 | 0.27522 | 0.1496
|  | HURSTBOURNE TARRANT | FS |  |  | 3.5672 | 3.443 | 3.3111 | 3.1206 | 2.9251 | 2.7144 | 2.4635 | 2.1883 | 1.8294 | 1.1726 | 0.031835 | -0.71159 | -0.87224 | 4.3643 | 4.2885 | 4.2067 | 4.101 | 3.9921 | 3.8739 | 3.7282 | 3.5641 | 3.3548 | 3.018 | 2.4839 | 2.1262 | 1.9357 | 4.0601 | 3.9431 | 3.8184 | 3.642 | 3.4609 | 3.2656 | 3.0307 | 2.7715 | 2.4332 | 1.8379 | 0.86982 | 0.27522 | 0.1496
EALING GSP |  | IRONBRIDGE | MINIMUM HEADROOM | TQ 14226 80171 |  | -0.56647 | -1.2201 | -2.1793 | -3.3739 | -4.659 | -6.0181 | -7.4587 | -8.7532 | -10.522 | -15.8018 | -24.2309 | -30.3763 | -33.7784 | 6.1225 | 5.6715 | 5.0359 | 4.286 | 3.2079 | 2.0232 | 0.76344 | -0.43431 | -1.8609 | -6.3303 | -14.2589 | -23.6213 | -36.7123 | 1.9527 | 1.3597 | 0.47731 | -0.61415 | -1.792 | -3.0451 | -4.3717 | -5.5802 | -7.2264 | -12.1356 | -19.6679 | -24.7232 | -27.4867
|  | IRONBRIDGE | CT |  |  | -0.56647 | -1.2201 | -2.1793 | -3.3739 | -4.659 | -6.0181 | -7.4587 | -8.7532 | -10.522 | -15.8018 | -24.2309 | -30.3763 | -33.7784 | 6.1225 | 5.6715 | 5.0359 | 4.286 | 3.2079 | 2.0232 | 0.76344 | -0.43431 | -1.8609 | -6.3303 | -14.2589 | -23.6213 | -36.7123 | 1.9527 | 1.3597 | 0.47731 | -0.61415 | -1.792 | -3.0451 | -4.3717 | -5.5802 | -7.2264 | -12.1356 | -19.6679 | -24.7232 | -27.4867
|  | IRONBRIDGE | LW |  |  | -0.56647 | -1.2201 | -2.1793 | -3.3739 | -4.659 | -6.0181 | -7.4587 | -8.7532 | -10.522 | -15.8018 | -24.2309 | -30.3763 | -33.7784 | 6.1225 | 5.6715 | 5.0359 | 4.286 | 3.2079 | 2.0232 | 0.76344 | -0.43431 | -1.8609 | -6.3303 | -14.2589 | -23.6213 | -36.7123 | 1.9527 | 1.3597 | 0.47731 | -0.61415 | -1.792 | -3.0451 | -4.3717 | -5.5802 | -7.2264 | -12.1356 | -19.6679 | -24.7232 | -27.4867
|  | IRONBRIDGE | ST |  |  | -0.56647 | -1.2201 | -2.1793 | -3.3739 | -4.659 | -6.0181 | -7.4587 | -8.7532 | -10.522 | -15.8018 | -24.2309 | -30.3763 | -33.7784 | 6.1225 | 5.6715 | 5.0359 | 4.286 | 3.2079 | 2.0232 | 0.76344 | -0.43431 | -1.8609 | -6.3303 | -14.2589 | -23.6213 | -36.7123 | 1.9527 | 1.3597 | 0.47731 | -0.61415 | -1.792 | -3.0451 | -4.3717 | -5.5802 | -7.2264 | -12.1356 | -19.6679 | -24.7232 | -27.4867
|  | IRONBRIDGE | FS |  |  | -0.56647 | -1.2201 | -2.1793 | -3.3739 | -4.659 | -6.0181 | -7.4587 | -8.7532 | -10.522 | -15.8018 | -24.2309 | -30.3763 | -33.7784 | 6.1225 | 5.6715 | 5.0359 | 4.286 | 3.2079 | 2.0232 | 0.76344 | -0.43431 | -1.8609 | -6.3303 | -14.2589 | -23.6213 | -36.7123 | 1.9527 | 1.3597 | 0.47731 | -0.61415 | -1.792 | -3.0451 | -4.3717 | -5.5802 | -7.2264 | -12.1356 | -19.6679 | -24.7232 | -27.4867
BRAMLEY (BASI) | BASINGSTOKE T1A & T2A | JAYS CLOSE | MINIMUM HEADROOM | SU 63055 50105 | YES | 30.1198 | 29.7674 | 29.3169 | 28.7161 | 28.1523 | 27.5686 | 26.9572 | 26.2698 | 25.1215 | 21.912 | 17.265 | 14.3088 | 12.9873 | 26.8675 | 26.5975 | 26.2776 | 25.8828 | 25.5429 | 25.1924 | 24.8292 | 24.4319 | 23.8508 | 22.1624 | 19.5712 | 17.8346 | 16.4619 | 32.1858 | 31.8607 | 31.4516 | 30.9015 | 30.3904 | 29.8501 | 29.2459 | 28.5585 | 27.4701 | 24.4464 | 20.2198 | 17.747 | 16.5993
|  | JAYS CLOSE | CT |  |  | 30.1198 | 29.7674 | 29.3169 | 28.7161 | 28.1523 | 27.5686 | 26.9572 | 26.2698 | 25.1215 | 21.912 | 17.265 | 14.3088 | 12.9873 | 26.8675 | 26.5975 | 26.2776 | 25.8828 | 25.5429 | 25.1924 | 24.8292 | 24.4319 | 23.8508 | 22.1624 | 19.5712 | 17.8346 | 16.4619 | 32.1858 | 31.8607 | 31.4516 | 30.9015 | 30.3904 | 29.8501 | 29.2459 | 28.5585 | 27.4701 | 24.4464 | 20.2198 | 17.747 | 16.5993
|  | JAYS CLOSE | LW |  |  | 30.1198 | 29.7674 | 29.3169 | 28.7161 | 28.1523 | 27.5686 | 26.9572 | 26.2698 | 25.1215 | 21.912 | 17.265 | 14.3088 | 12.9873 | 26.8675 | 26.5975 | 26.2776 | 25.8828 | 25.5429 | 25.1924 | 24.8292 | 24.4319 | 23.8508 | 22.1624 | 19.5712 | 17.8346 | 16.4619 | 32.1858 | 31.8607 | 31.4516 | 30.9015 | 30.3904 | 29.8501 | 29.2459 | 28.5585 | 27.4701 | 24.4464 | 20.2198 | 17.747 | 16.5993
|  | JAYS CLOSE | ST |  |  | 30.1198 | 29.7674 | 29.3169 | 28.7161 | 28.1523 | 27.5686 | 26.9572 | 26.2698 | 25.1215 | 21.912 | 17.265 | 14.3088 | 12.9873 | 26.8675 | 26.5975 | 26.2776 | 25.8828 | 25.5429 | 25.1924 | 24.8292 | 24.4319 | 23.8508 | 22.1624 | 19.5712 | 17.8346 | 16.4619 | 32.1858 | 31.8607 | 31.4516 | 30.9015 | 30.3904 | 29.8501 | 29.2459 | 28.5585 | 27.4701 | 24.4464 | 20.2198 | 17.747 | 16.5993
|  | JAYS CLOSE | FS |  |  | 30.1198 | 29.7674 | 29.3169 | 28.7161 | 28.1523 | 27.5686 | 26.9572 | 26.2698 | 25.1215 | 21.912 | 17.265 | 14.3088 | 12.9873 | 26.8675 | 26.5975 | 26.2776 | 25.8828 | 25.5429 | 25.1924 | 24.8292 | 24.4319 | 23.8508 | 22.1624 | 19.5712 | 17.8346 | 16.4619 | 32.1858 | 31.8607 | 31.4516 | 30.9015 | 30.3904 | 29.8501 | 29.2459 | 28.5585 | 27.4701 | 24.4464 | 20.2198 | 17.747 | 16.5993
MINETY GSP | CIRENCESTER BSP | KEMBLE RAF | MINIMUM HEADROOM |  |  | 0.22654 | 0.21011 | 0.19084 | 0.16782 | 0.1407 | 0.10857 | 0.072384 | 0.032384 | -0.020594 | -0.21472 | -0.60712 | -0.8273 | -0.97034 | 1.2553 | 1.2464 | 1.236 | 1.2235 | 1.2086 | 1.1907 | 1.1702 | 1.1473 | 1.1173 | 1.0052 | 0.77193 | 0.61617 | 0.50649 | 0.85117 | 0.83461 | 0.81533 | 0.79195 | 0.76476 | 0.73305 | 0.69764 | 0.6589 | 0.60723 | 0.42071 | 0.050426 | -0.16231 | -0.30062
|  | KEMBLE RAF | CT |  |  | 0.22654 | 0.21011 | 0.19084 | 0.16782 | 0.1407 | 0.10857 | 0.072384 | 0.032384 | -0.020594 | -0.21472 | -0.60712 | -0.8273 | -0.97034 | 1.2553 | 1.2464 | 1.236 | 1.2235 | 1.2086 | 1.1907 | 1.1702 | 1.1473 | 1.1173 | 1.0052 | 0.77193 | 0.61617 | 0.50649 | 0.85117 | 0.83461 | 0.81533 | 0.79195 | 0.76476 | 0.73305 | 0.69764 | 0.6589 | 0.60723 | 0.42071 | 0.050426 | -0.16231 | -0.30062
|  | KEMBLE RAF | LW |  |  | 0.22654 | 0.21011 | 0.19084 | 0.16782 | 0.1407 | 0.10857 | 0.072384 | 0.032384 | -0.020594 | -0.21472 | -0.60712 | -0.8273 | -0.97034 | 1.2553 | 1.2464 | 1.236 | 1.2235 | 1.2086 | 1.1907 | 1.1702 | 1.1473 | 1.1173 | 1.0052 | 0.77193 | 0.61617 | 0.50649 | 0.85117 | 0.83461 | 0.81533 | 0.79195 | 0.76476 | 0.73305 | 0.69764 | 0.6589 | 0.60723 | 0.42071 | 0.050426 | -0.16231 | -0.30062
|  | KEMBLE RAF | ST |  |  | 0.22654 | 0.21011 | 0.19084 | 0.16782 | 0.1407 | 0.10857 | 0.072384 | 0.032384 | -0.020594 | -0.21472 | -0.60712 | -0.8273 | -0.97034 | 1.2553 | 1.2464 | 1.236 | 1.2235 | 1.2086 | 1.1907 | 1.1702 | 1.1473 | 1.1173 | 1.0052 | 0.77193 | 0.61617 | 0.50649 | 0.85117 | 0.83461 | 0.81533 | 0.79195 | 0.76476 | 0.73305 | 0.69764 | 0.6589 | 0.60723 | 0.42071 | 0.050426 | -0.16231 | -0.30062
|  | KEMBLE RAF | FS |  |  | 0.22654 | 0.21011 | 0.19084 | 0.16782 | 0.1407 | 0.10857 | 0.072384 | 0.032384 | -0.020594 | -0.21472 | -0.60712 | -0.8273 | -0.97034 | 1.2553 | 1.2464 | 1.236 | 1.2235 | 1.2086 | 1.1907 | 1.1702 | 1.1473 | 1.1173 | 1.0052 | 0.77193 | 0.61617 | 0.50649 | 0.85117 | 0.83461 | 0.81533 | 0.79195 | 0.76476 | 0.73305 | 0.69764 | 0.6589 | 0.60723 | 0.42071 | 0.050426 | -0.16231 | -0.30062
COWLEY GSP | COWLEY LOCAL (2 X 45) | KENNINGTON | MINIMUM HEADROOM | SP 52881 01094 | NO | -2.4845 | -2.7468 | -3.0361 | -3.2556 | -3.4692 | -3.7027 | -3.9562 | -4.2333 | -4.7141 | -5.9147 | -7.4165 | -8.4987 | -9.0352 | 0.085313 | -0.080352 | -0.27041 | -0.4128 | -0.5555 | -0.71387 | -0.8872 | -1.0817 | -1.4002 | -2.1684 | -2.974 | -3.6078 | -4.1548 | -1.3199 | -1.5439 | -1.7992 | -1.9971 | -2.1943 | -2.4129 | -2.6502 | -2.9117 | -3.3664 | -4.4904 | -5.8268 | -6.7726 | -7.2183
|  | KENNINGTON | CT |  |  | -2.4845 | -2.7468 | -3.0361 | -3.2556 | -3.4692 | -3.7027 | -3.9562 | -4.2333 | -4.7141 | -5.9147 | -7.4165 | -8.4987 | -9.0352 | 0.085313 | -0.080352 | -0.27041 | -0.4128 | -0.5555 | -0.71387 | -0.8872 | -1.0817 | -1.4002 | -2.1684 | -2.974 | -3.6078 | -4.1548 | -1.3199 | -1.5439 | -1.7992 | -1.9971 | -2.1943 | -2.4129 | -2.6502 | -2.9117 | -3.3664 | -4.4904 | -5.8268 | -6.7726 | -7.2183
|  | KENNINGTON | LW |  |  | -2.4845 | -2.7468 | -3.0361 | -3.2556 | -3.4692 | -3.7027 | -3.9562 | -4.2333 | -4.7141 | -5.9147 | -7.4165 | -8.4987 | -9.0352 | 0.085313 | -0.080352 | -0.27041 | -0.4128 | -0.5555 | -0.71387 | -0.8872 | -1.0817 | -1.4002 | -2.1684 | -2.974 | -3.6078 | -4.1548 | -1.3199 | -1.5439 | -1.7992 | -1.9971 | -2.1943 | -2.4129 | -2.6502 | -2.9117 | -3.3664 | -4.4904 | -5.8268 | -6.7726 | -7.2183
|  | KENNINGTON | ST |  |  | -2.4845 | -2.7468 | -3.0361 | -3.2556 | -3.4692 | -3.7027 | -3.9562 | -4.2333 | -4.7141 | -5.9147 | -7.4165 | -8.4987 | -9.0352 | 0.085313 | -0.080352 | -0.27041 | -0.4128 | -0.5555 | -0.71387 | -0.8872 | -1.0817 | -1.4002 | -2.1684 | -2.974 | -3.6078 | -4.1548 | -1.3199 | -1.5439 | -1.7992 | -1.9971 | -2.1943 | -2.4129 | -2.6502 | -2.9117 | -3.3664 | -4.4904 | -5.8268 | -6.7726 | -7.2183
|  | KENNINGTON | FS |  |  | -2.4845 | -2.7468 | -3.0361 | -3.2556 | -3.4692 | -3.7027 | -3.9562 | -4.2333 | -4.7141 | -5.9147 | -7.4165 | -8.4987 | -9.0352 | 0.085313 | -0.080352 | -0.27041 | -0.4128 | -0.5555 | -0.71387 | -0.8872 | -1.0817 | -1.4002 | -2.1684 | -2.974 | -3.6078 | -4.1548 | -1.3199 | -1.5439 | -1.7992 | -1.9971 | -2.1943 | -2.4129 | -2.6502 | -2.9117 | -3.3664 | -4.4904 | -5.8268 | -6.7726 | -7.2183
BRAMLEY (FLEE) | BURGHFIELD MAIN | KENTWOOD HILL | MINIMUM HEADROOM | SU 67102 74048 | YES | 0.8628 | 0.31591 | -0.39974 | -1.3286 | -2.3232 | -3.3907 | -4.5607 | -5.9237 | -8.2062 | -13.8926 | -23.4165 | -31.1436 | -35.4702 | 6.9926 | 6.5962 | 6.0485 | 5.4371 | 4.7758 | 4.0542 | 3.2514 | 2.2861 | 0.69195 | -2.9689 | -8.0688 | -12.5695 | -16.914 | 2.6859 | 2.1817 | 1.4987 | 0.63072 | -0.2997 | -1.3019 | -2.404 | -3.6987 | -5.8434 | -11.0908 | -19.4968 | -26.1601 | -29.8276
|  | KENTWOOD HILL | CT |  |  | 0.8628 | 0.31591 | -0.39974 | -1.3286 | -2.3232 | -3.3907 | -4.5607 | -5.9237 | -8.2062 | -13.8926 | -23.4165 | -31.1436 | -35.4702 | 6.9926 | 6.5962 | 6.0485 | 5.4371 | 4.7758 | 4.0542 | 3.2514 | 2.2861 | 0.69195 | -2.9689 | -8.0688 | -12.5695 | -16.914 | 2.6859 | 2.1817 | 1.4987 | 0.63072 | -0.2997 | -1.3019 | -2.404 | -3.6987 | -5.8434 | -11.0908 | -19.4968 | -26.1601 | -29.8276
|  | KENTWOOD HILL | LW |  |  | 0.8628 | 0.31591 | -0.39974 | -1.3286 | -2.3232 | -3.3907 | -4.5607 | -5.9237 | -8.2062 | -13.8926 | -23.4165 | -31.1436 | -35.4702 | 6.9926 | 6.5962 | 6.0485 | 5.4371 | 4.7758 | 4.0542 | 3.2514 | 2.2861 | 0.69195 | -2.9689 | -8.0688 | -12.5695 | -16.914 | 2.6859 | 2.1817 | 1.4987 | 0.63072 | -0.2997 | -1.3019 | -2.404 | -3.6987 | -5.8434 | -11.0908 | -19.4968 | -26.1601 | -29.8276
|  | KENTWOOD HILL | ST |  |  | 0.8628 | 0.31591 | -0.39974 | -1.3286 | -2.3232 | -3.3907 | -4.5607 | -5.9237 | -8.2062 | -13.8926 | -23.4165 | -31.1436 | -35.4702 | 6.9926 | 6.5962 | 6.0485 | 5.4371 | 4.7758 | 4.0542 | 3.2514 | 2.2861 | 0.69195 | -2.9689 | -8.0688 | -12.5695 | -16.914 | 2.6859 | 2.1817 | 1.4987 | 0.63072 | -0.2997 | -1.3019 | -2.404 | -3.6987 | -5.8434 | -11.0908 | -19.4968 | -26.1601 | -29.8276
|  | KENTWOOD HILL | FS |  |  | 0.8628 | 0.31591 | -0.39974 | -1.3286 | -2.3232 | -3.3907 | -4.5607 | -5.9237 | -8.2062 | -13.8926 | -23.4165 | -31.1436 | -35.4702 | 6.9926 | 6.5962 | 6.0485 | 5.4371 | 4.7758 | 4.0542 | 3.2514 | 2.2861 | 0.69195 | -2.9689 | -8.0688 | -12.5695 | -16.914 | 2.6859 | 2.1817 | 1.4987 | 0.63072 | -0.2997 | -1.3019 | -2.404 | -3.6987 | -5.8434 | -11.0908 | -19.4968 | -26.1601 | -29.8276
COWLEY GSP | YARNTON BSP | KIDDINGTON | MINIMUM HEADROOM | SP 43362 24301 | NO | 20.2761 | 20.1788 | 20.0754 | 19.9098 | 19.7381 | 19.5571 | 19.3622 | 19.17 | 18.6607 | 17.5054 | 15.7934 | 15.0592 | 14.8486 | 22.3425 | 22.2576 | 22.1528 | 22.0266 | 21.8919 | 21.7451 | 21.573 | 21.3872 | 21.1069 | 20.6128 | 19.9719 | 19.6868 | 19.5492 | 20.5352 | 20.3932 | 20.2221 | 19.999 | 19.7631 | 19.5085 | 19.215 | 18.9031 | 18.4244 | 17.5034 | 16.0244 | 15.3935 | 15.224
|  | KIDDINGTON | CT |  |  | 20.2761 | 20.1788 | 20.0754 | 19.9098 | 19.7381 | 19.5571 | 19.3622 | 19.17 | 18.6607 | 17.5054 | 15.7934 | 15.0592 | 14.8486 | 22.3425 | 22.2576 | 22.1528 | 22.0266 | 21.8919 | 21.7451 | 21.573 | 21.3872 | 21.1069 | 20.6128 | 19.9719 | 19.6868 | 19.5492 | 20.5352 | 20.3932 | 20.2221 | 19.999 | 19.7631 | 19.5085 | 19.215 | 18.9031 | 18.4244 | 17.5034 | 16.0244 | 15.3935 | 15.224
|  | KIDDINGTON | LW |  |  | 20.2761 | 20.1788 | 20.0754 | 19.9098 | 19.7381 | 19.5571 | 19.3622 | 19.17 | 18.6607 | 17.5054 | 15.7934 | 15.0592 | 14.8486 | 22.3425 | 22.2576 | 22.1528 | 22.0266 | 21.8919 | 21.7451 | 21.573 | 21.3872 | 21.1069 | 20.6128 | 19.9719 | 19.6868 | 19.5492 | 20.5352 | 20.3932 | 20.2221 | 19.999 | 19.7631 | 19.5085 | 19.215 | 18.9031 | 18.4244 | 17.5034 | 16.0244 | 15.3935 | 15.224
|  | KIDDINGTON | ST |  |  | 20.2761 | 20.1788 | 20.0754 | 19.9098 | 19.7381 | 19.5571 | 19.3622 | 19.17 | 18.6607 | 17.5054 | 15.7934 | 15.0592 | 14.8486 | 22.3425 | 22.2576 | 22.1528 | 22.0266 | 21.8919 | 21.7451 | 21.573 | 21.3872 | 21.1069 | 20.6128 | 19.9719 | 19.6868 | 19.5492 | 20.5352 | 20.3932 | 20.2221 | 19.999 | 19.7631 | 19.5085 | 19.215 | 18.9031 | 18.4244 | 17.5034 | 16.0244 | 15.3935 | 15.224
|  | KIDDINGTON | FS |  |  | 20.2761 | 20.1788 | 20.0754 | 19.9098 | 19.7381 | 19.5571 | 19.3622 | 19.17 | 18.6607 | 17.5054 | 15.7934 | 15.0592 | 14.8486 | 22.3425 | 22.2576 | 22.1528 | 22.0266 | 21.8919 | 21.7451 | 21.573 | 21.3872 | 21.1069 | 20.6128 | 19.9719 | 19.6868 | 19.5492 | 20.5352 | 20.3932 | 20.2221 | 19.999 | 19.7631 | 19.5085 | 19.215 | 18.9031 | 18.4244 | 17.5034 | 16.0244 | 15.3935 | 15.224
BRAMLEY (FLEE) | READING BSP | KIDMORE END | MINIMUM HEADROOM | SU 69953 78205 | YES | 5.507 | 5.2437 | 4.9637 | 4.616 | 4.2476 | 3.8433 | 3.3816 | 2.8534 | 2.0456 | 0.52947 | -2.3306 | -4.8512 | -6.4469 | 8.5533 | 8.4928 | 8.4269 | 8.363 | 8.2935 | 8.2139 | 7.9628 | 7.582 | 7.0432 | 6.1764 | 4.6822 | 3.276 | 2.0421 | 6.6419 | 6.4124 | 6.168 | 5.858 | 5.5298 | 5.1703 | 4.7606 | 4.2933 | 3.5718 | 2.1901 | -0.40923 | -2.6597 | -4.0417
|  | KIDMORE END | CT |  |  | 5.507 | 5.2437 | 4.9637 | 4.616 | 4.2476 | 3.8433 | 3.3816 | 2.8534 | 2.0456 | 0.52947 | -2.3306 | -4.8512 | -6.4469 | 8.5533 | 8.4928 | 8.4269 | 8.363 | 8.2935 | 8.2139 | 7.9628 | 7.582 | 7.0432 | 6.1764 | 4.6822 | 3.276 | 2.0421 | 6.6419 | 6.4124 | 6.168 | 5.858 | 5.5298 | 5.1703 | 4.7606 | 4.2933 | 3.5718 | 2.1901 | -0.40923 | -2.6597 | -4.0417
|  | KIDMORE END | LW |  |  | 5.507 | 5.2437 | 4.9637 | 4.616 | 4.2476 | 3.8433 | 3.3816 | 2.8534 | 2.0456 | 0.52947 | -2.3306 | -4.8512 | -6.4469 | 8.5533 | 8.4928 | 8.4269 | 8.363 | 8.2935 | 8.2139 | 7.9628 | 7.582 | 7.0432 | 6.1764 | 4.6822 | 3.276 | 2.0421 | 6.6419 | 6.4124 | 6.168 | 5.858 | 5.5298 | 5.1703 | 4.7606 | 4.2933 | 3.5718 | 2.1901 | -0.40923 | -2.6597 | -4.0417
|  | KIDMORE END | ST |  |  | 5.507 | 5.2437 | 4.9637 | 4.616 | 4.2476 | 3.8433 | 3.3816 | 2.8534 | 2.0456 | 0.52947 | -2.3306 | -4.8512 | -6.4469 | 8.5533 | 8.4928 | 8.4269 | 8.363 | 8.2935 | 8.2139 | 7.9628 | 7.582 | 7.0432 | 6.1764 | 4.6822 | 3.276 | 2.0421 | 6.6419 | 6.4124 | 6.168 | 5.858 | 5.5298 | 5.1703 | 4.7606 | 4.2933 | 3.5718 | 2.1901 | -0.40923 | -2.6597 | -4.0417
|  | KIDMORE END | FS |  |  | 5.507 | 5.2437 | 4.9637 | 4.616 | 4.2476 | 3.8433 | 3.3816 | 2.8534 | 2.0456 | 0.52947 | -2.3306 | -4.8512 | -6.4469 | 8.5533 | 8.4928 | 8.4269 | 8.363 | 8.2935 | 8.2139 | 7.9628 | 7.582 | 7.0432 | 6.1764 | 4.6822 | 3.276 | 2.0421 | 6.6419 | 6.4124 | 6.168 | 5.858 | 5.5298 | 5.1703 | 4.7606 | 4.2933 | 3.5718 | 2.1901 | -0.40923 | -2.6597 | -4.0417
BRAMLEY (FLEE) | CAMBERLEY MAIN | KINGS RIDE | MINIMUM HEADROOM | SU 87551 61530 | YES | 10.6109 | 10.3459 | 10.0484 | 9.4537 | 8.8222 | 8.1702 | 7.4333 | 6.6319 | 5.5638 | 2.9346 | -0.84692 | -3.3197 | -4.5411 | 15.2865 | 15.0816 | 14.8486 | 14.4822 | 14.0899 | 13.667 | 13.1827 | 12.6525 | 11.9857 | 10.4118 | 8.1791 | 6.5715 | 5.0876 | 11.6938 | 11.4185 | 11.107 | 10.5611 | 9.9785 | 9.3633 | 8.6608 | 7.8955 | 6.8853 | 4.4897 | 1.1558 | -0.88768 | -1.8795
|  | KINGS RIDE | CT |  |  | 10.6109 | 10.3459 | 10.0484 | 9.4537 | 8.8222 | 8.1702 | 7.4333 | 6.6319 | 5.5638 | 2.9346 | -0.84692 | -3.3197 | -4.5411 | 15.2865 | 15.0816 | 14.8486 | 14.4822 | 14.0899 | 13.667 | 13.1827 | 12.6525 | 11.9857 | 10.4118 | 8.1791 | 6.5715 | 5.0876 | 11.6938 | 11.4185 | 11.107 | 10.5611 | 9.9785 | 9.3633 | 8.6608 | 7.8955 | 6.8853 | 4.4897 | 1.1558 | -0.88768 | -1.8795
|  | KINGS RIDE | LW |  |  | 10.6109 | 10.3459 | 10.0484 | 9.4537 | 8.8222 | 8.1702 | 7.4333 | 6.6319 | 5.5638 | 2.9346 | -0.84692 | -3.3197 | -4.5411 | 15.2865 | 15.0816 | 14.8486 | 14.4822 | 14.0899 | 13.667 | 13.1827 | 12.6525 | 11.9857 | 10.4118 | 8.1791 | 6.5715 | 5.0876 | 11.6938 | 11.4185 | 11.107 | 10.5611 | 9.9785 | 9.3633 | 8.6608 | 7.8955 | 6.8853 | 4.4897 | 1.1558 | -0.88768 | -1.8795
|  | KINGS RIDE | ST |  |  | 10.6109 | 10.3459 | 10.0484 | 9.4537 | 8.8222 | 8.1702 | 7.4333 | 6.6319 | 5.5638 | 2.9346 | -0.84692 | -3.3197 | -4.5411 | 15.2865 | 15.0816 | 14.8486 | 14.4822 | 14.0899 | 13.667 | 13.1827 | 12.6525 | 11.9857 | 10.4118 | 8.1791 | 6.5715 | 5.0876 | 11.6938 | 11.4185 | 11.107 | 10.5611 | 9.9785 | 9.3633 | 8.6608 | 7.8955 | 6.8853 | 4.4897 | 1.1558 | -0.88768 | -1.8795
|  | KINGS RIDE | FS |  |  | 10.6109 | 10.3459 | 10.0484 | 9.4537 | 8.8222 | 8.1702 | 7.4333 | 6.6319 | 5.5638 | 2.9346 | -0.84692 | -3.3197 | -4.5411 | 15.2865 | 15.0816 | 14.8486 | 14.4822 | 14.0899 | 13.667 | 13.1827 | 12.6525 | 11.9857 | 10.4118 | 8.1791 | 6.5715 | 5.0876 | 11.6938 | 11.4185 | 11.107 | 10.5611 | 9.9785 | 9.3633 | 8.6608 | 7.8955 | 6.8853 | 4.4897 | 1.1558 | -0.88768 | -1.8795
BRAMLEY (ANDO-THAT) | THATCHAM BSP | KINGSCLERE | MINIMUM HEADROOM | SU 51982 59358 | YES | 6.5968 | 6.3469 | 6.0933 | 5.6974 | 5.2914 | 4.8837 | 4.4477 | 4.0368 | 3.4438 | 2.5869 | 1.8322 | 1.4801 | 1.3413 | 8.0896 | 7.9465 | 7.7981 | 7.6117 | 7.4179 | 7.2079 | 6.9657 | 6.7213 | 6.3856 | 5.9047 | 5.4219 | 5.157 | 4.877 | 7.2744 | 7.0457 | 6.8137 | 6.4464 | 6.07 | 5.6937 | 5.2941 | 4.9194 | 4.3773 | 3.5859 | 2.8827 | 2.5527 | 2.4223
|  | KINGSCLERE | CT |  |  | 6.5968 | 6.3469 | 6.0933 | 5.6974 | 5.2914 | 4.8837 | 4.4477 | 4.0368 | 3.4438 | 2.5869 | 1.8322 | 1.4801 | 1.3413 | 8.0896 | 7.9465 | 7.7981 | 7.6117 | 7.4179 | 7.2079 | 6.9657 | 6.7213 | 6.3856 | 5.9047 | 5.4219 | 5.157 | 4.877 | 7.2744 | 7.0457 | 6.8137 | 6.4464 | 6.07 | 5.6937 | 5.2941 | 4.9194 | 4.3773 | 3.5859 | 2.8827 | 2.5527 | 2.4223
|  | KINGSCLERE | LW |  |  | 6.5968 | 6.3469 | 6.0933 | 5.6974 | 5.2914 | 4.8837 | 4.4477 | 4.0368 | 3.4438 | 2.5869 | 1.8322 | 1.4801 | 1.3413 | 8.0896 | 7.9465 | 7.7981 | 7.6117 | 7.4179 | 7.2079 | 6.9657 | 6.7213 | 6.3856 | 5.9047 | 5.4219 | 5.157 | 4.877 | 7.2744 | 7.0457 | 6.8137 | 6.4464 | 6.07 | 5.6937 | 5.2941 | 4.9194 | 4.3773 | 3.5859 | 2.8827 | 2.5527 | 2.4223
|  | KINGSCLERE | ST |  |  | 6.5968 | 6.3469 | 6.0933 | 5.6974 | 5.2914 | 4.8837 | 4.4477 | 4.0368 | 3.4438 | 2.5869 | 1.8322 | 1.4801 | 1.3413 | 8.0896 | 7.9465 | 7.7981 | 7.6117 | 7.4179 | 7.2079 | 6.9657 | 6.7213 | 6.3856 | 5.9047 | 5.4219 | 5.157 | 4.877 | 7.2744 | 7.0457 | 6.8137 | 6.4464 | 6.07 | 5.6937 | 5.2941 | 4.9194 | 4.3773 | 3.5859 | 2.8827 | 2.5527 | 2.4223
|  | KINGSCLERE | FS |  |  | 6.5968 | 6.3469 | 6.0933 | 5.6974 | 5.2914 | 4.8837 | 4.4477 | 4.0368 | 3.4438 | 2.5869 | 1.8322 | 1.4801 | 1.3413 | 8.0896 | 7.9465 | 7.7981 | 7.6117 | 7.4179 | 7.2079 | 6.9657 | 6.7213 | 6.3856 | 5.9047 | 5.4219 | 5.157 | 4.877 | 7.2744 | 7.0457 | 6.8137 | 6.4464 | 6.07 | 5.6937 | 5.2941 | 4.9194 | 4.3773 | 3.5859 | 2.8827 | 2.5527 | 2.4223
BRAMLEY (ANDO-THAT) | THATCHAM BSP | KINTBURY | MINIMUM HEADROOM | SU 37657 67143 | YES | 7.2366 | 7.0986 | 6.9433 | 6.722 | 6.4919 | 6.2408 | 5.9643 | 5.6625 | 5.2572 | 4.4277 | 3.1535 | 2.8551 | 2.7697 | 9.0345 | 8.954 | 8.8602 | 8.742 | 8.6178 | 8.4799 | 8.325 | 8.1503 | 7.9209 | 7.4945 | 6.9127 | 6.7076 | 6.5327 | 8.1785 | 8.0497 | 7.9035 | 7.7 | 7.488 | 7.2558 | 6.999 | 6.7163 | 6.3369 | 5.5823 | 4.5191 | 4.2728 | 4.2036
|  | KINTBURY | CT |  |  | 7.2366 | 7.0986 | 6.9433 | 6.722 | 6.4919 | 6.2408 | 5.9643 | 5.6625 | 5.2572 | 4.4277 | 3.1535 | 2.8551 | 2.7697 | 9.0345 | 8.954 | 8.8602 | 8.742 | 8.6178 | 8.4799 | 8.325 | 8.1503 | 7.9209 | 7.4945 | 6.9127 | 6.7076 | 6.5327 | 8.1785 | 8.0497 | 7.9035 | 7.7 | 7.488 | 7.2558 | 6.999 | 6.7163 | 6.3369 | 5.5823 | 4.5191 | 4.2728 | 4.2036
|  | KINTBURY | LW |  |  | 7.2366 | 7.0986 | 6.9433 | 6.722 | 6.4919 | 6.2408 | 5.9643 | 5.6625 | 5.2572 | 4.4277 | 3.1535 | 2.8551 | 2.7697 | 9.0345 | 8.954 | 8.8602 | 8.742 | 8.6178 | 8.4799 | 8.325 | 8.1503 | 7.9209 | 7.4945 | 6.9127 | 6.7076 | 6.5327 | 8.1785 | 8.0497 | 7.9035 | 7.7 | 7.488 | 7.2558 | 6.999 | 6.7163 | 6.3369 | 5.5823 | 4.5191 | 4.2728 | 4.2036
|  | KINTBURY | ST |  |  | 7.2366 | 7.0986 | 6.9433 | 6.722 | 6.4919 | 6.2408 | 5.9643 | 5.6625 | 5.2572 | 4.4277 | 3.1535 | 2.8551 | 2.7697 | 9.0345 | 8.954 | 8.8602 | 8.742 | 8.6178 | 8.4799 | 8.325 | 8.1503 | 7.9209 | 7.4945 | 6.9127 | 6.7076 | 6.5327 | 8.1785 | 8.0497 | 7.9035 | 7.7 | 7.488 | 7.2558 | 6.999 | 6.7163 | 6.3369 | 5.5823 | 4.5191 | 4.2728 | 4.2036
|  | KINTBURY | FS |  |  | 7.2366 | 7.0986 | 6.9433 | 6.722 | 6.4919 | 6.2408 | 5.9643 | 5.6625 | 5.2572 | 4.4277 | 3.1535 | 2.8551 | 2.7697 | 9.0345 | 8.954 | 8.8602 | 8.742 | 8.6178 | 8.4799 | 8.325 | 8.1503 | 7.9209 | 7.4945 | 6.9127 | 6.7076 | 6.5327 | 8.1785 | 8.0497 | 7.9035 | 7.7 | 7.488 | 7.2558 | 6.999 | 6.7163 | 6.3369 | 5.5823 | 4.5191 | 4.2728 | 4.2036
BRAMLEY (FLEE) | MAIDENHEAD BSP | KNOWL HILL | MINIMUM HEADROOM | SU 82849 79105 | YES | 4.0277 | 3.9512 | 3.8606 | 3.7496 | 3.6345 | 3.4962 | 3.3347 | 3.1678 | 2.9562 | 2.5829 | 1.8809 | 1.4106 | 1.179 | 5.1517 | 5.0959 | 5.0283 | 4.9555 | 4.8795 | 4.7852 | 4.6726 | 4.5553 | 4.4123 | 4.1961 | 3.8134 | 3.5481 | 3.3491 | 4.8694 | 4.8022 | 4.7243 | 4.6221 | 4.5161 | 4.392 | 4.2501 | 4.1039 | 3.915 | 3.5255 | 2.8166 | 2.3594 | 2.1361
|  | KNOWL HILL | CT |  |  | 4.0277 | 3.9512 | 3.8606 | 3.7496 | 3.6345 | 3.4962 | 3.3347 | 3.1678 | 2.9562 | 2.5829 | 1.8809 | 1.4106 | 1.179 | 5.1517 | 5.0959 | 5.0283 | 4.9555 | 4.8795 | 4.7852 | 4.6726 | 4.5553 | 4.4123 | 4.1961 | 3.8134 | 3.5481 | 3.3491 | 4.8694 | 4.8022 | 4.7243 | 4.6221 | 4.5161 | 4.392 | 4.2501 | 4.1039 | 3.915 | 3.5255 | 2.8166 | 2.3594 | 2.1361
|  | KNOWL HILL | LW |  |  | 4.0277 | 3.9512 | 3.8606 | 3.7496 | 3.6345 | 3.4962 | 3.3347 | 3.1678 | 2.9562 | 2.5829 | 1.8809 | 1.4106 | 1.179 | 5.1517 | 5.0959 | 5.0283 | 4.9555 | 4.8795 | 4.7852 | 4.6726 | 4.5553 | 4.4123 | 4.1961 | 3.8134 | 3.5481 | 3.3491 | 4.8694 | 4.8022 | 4.7243 | 4.6221 | 4.5161 | 4.392 | 4.2501 | 4.1039 | 3.915 | 3.5255 | 2.8166 | 2.3594 | 2.1361
|  | KNOWL HILL | ST |  |  | 4.0277 | 3.9512 | 3.8606 | 3.7496 | 3.6345 | 3.4962 | 3.3347 | 3.1678 | 2.9562 | 2.5829 | 1.8809 | 1.4106 | 1.179 | 5.1517 | 5.0959 | 5.0283 | 4.9555 | 4.8795 | 4.7852 | 4.6726 | 4.5553 | 4.4123 | 4.1961 | 3.8134 | 3.5481 | 3.3491 | 4.8694 | 4.8022 | 4.7243 | 4.6221 | 4.5161 | 4.392 | 4.2501 | 4.1039 | 3.915 | 3.5255 | 2.8166 | 2.3594 | 2.1361
|  | KNOWL HILL | FS |  |  | 4.0277 | 3.9512 | 3.8606 | 3.7496 | 3.6345 | 3.4962 | 3.3347 | 3.1678 | 2.9562 | 2.5829 | 1.8809 | 1.4106 | 1.179 | 5.1517 | 5.0959 | 5.0283 | 4.9555 | 4.8795 | 4.7852 | 4.6726 | 4.5553 | 4.4123 | 4.1961 | 3.8134 | 3.5481 | 3.3491 | 4.8694 | 4.8022 | 4.7243 | 4.6221 | 4.5161 | 4.392 | 4.2501 | 4.1039 | 3.915 | 3.5255 | 2.8166 | 2.3594 | 2.1361
BRAMLEY (FLEE) | ALDERSHOT BSP | LABURNUM ROAD | MINIMUM HEADROOM | SU 86017 50475 | YES | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3
|  | LABURNUM ROAD | CT |  |  | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3
|  | LABURNUM ROAD | LW |  |  | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3
|  | LABURNUM ROAD | ST |  |  | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3
|  | LABURNUM ROAD | FS |  |  | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3
BRAMLEY (ANDO-THAT) | THATCHAM BSP | LAMBOURN | MINIMUM HEADROOM | SU 33280 78217 | YES | 5.1048 | 4.9178 | 4.7079 | 4.4028 | 4.0871 | 3.7644 | 3.4019 | 3.008 | 2.4061 | 1.011 | -1.1763 | -2.3808 | -2.5758 | 7.6079 | 7.4859 | 7.3458 | 7.174 | 6.9951 | 6.8073 | 6.589 | 6.3429 | 5.9835 | 5.2383 | 4.2161 | 3.6367 | 3.3501 | 5.4739 | 5.3004 | 5.1087 | 4.8262 | 4.5349 | 4.2378 | 3.9056 | 3.5465 | 2.9978 | 1.7034 | -0.36186 | -1.4407 | -1.6137
|  | LAMBOURN | CT |  |  | 5.1048 | 4.9178 | 4.7079 | 4.4028 | 4.0871 | 3.7644 | 3.4019 | 3.008 | 2.4061 | 1.011 | -1.1763 | -2.3808 | -2.5758 | 7.6079 | 7.4859 | 7.3458 | 7.174 | 6.9951 | 6.8073 | 6.589 | 6.3429 | 5.9835 | 5.2383 | 4.2161 | 3.6367 | 3.3501 | 5.4739 | 5.3004 | 5.1087 | 4.8262 | 4.5349 | 4.2378 | 3.9056 | 3.5465 | 2.9978 | 1.7034 | -0.36186 | -1.4407 | -1.6137
|  | LAMBOURN | LW |  |  | 5.1048 | 4.9178 | 4.7079 | 4.4028 | 4.0871 | 3.7644 | 3.4019 | 3.008 | 2.4061 | 1.011 | -1.1763 | -2.3808 | -2.5758 | 7.6079 | 7.4859 | 7.3458 | 7.174 | 6.9951 | 6.8073 | 6.589 | 6.3429 | 5.9835 | 5.2383 | 4.2161 | 3.6367 | 3.3501 | 5.4739 | 5.3004 | 5.1087 | 4.8262 | 4.5349 | 4.2378 | 3.9056 | 3.5465 | 2.9978 | 1.7034 | -0.36186 | -1.4407 | -1.6137
|  | LAMBOURN | ST |  |  | 5.1048 | 4.9178 | 4.7079 | 4.4028 | 4.0871 | 3.7644 | 3.4019 | 3.008 | 2.4061 | 1.011 | -1.1763 | -2.3808 | -2.5758 | 7.6079 | 7.4859 | 7.3458 | 7.174 | 6.9951 | 6.8073 | 6.589 | 6.3429 | 5.9835 | 5.2383 | 4.2161 | 3.6367 | 3.3501 | 5.4739 | 5.3004 | 5.1087 | 4.8262 | 4.5349 | 4.2378 | 3.9056 | 3.5465 | 2.9978 | 1.7034 | -0.36186 | -1.4407 | -1.6137
|  | LAMBOURN | FS |  |  | 5.1048 | 4.9178 | 4.7079 | 4.4028 | 4.0871 | 3.7644 | 3.4019 | 3.008 | 2.4061 | 1.011 | -1.1763 | -2.3808 | -2.5758 | 7.6079 | 7.4859 | 7.3458 | 7.174 | 6.9951 | 6.8073 | 6.589 | 6.3429 | 5.9835 | 5.2383 | 4.2161 | 3.6367 | 3.3501 | 5.4739 | 5.3004 | 5.1087 | 4.8262 | 4.5349 | 4.2378 | 3.9056 | 3.5465 | 2.9978 | 1.7034 | -0.36186 | -1.4407 | -1.6137
FAWLEY GSP | LANGLEY BSP | LANGLEY | MINIMUM HEADROOM | SU 45158 01418 | YES | 9.6405 | 9.5775 | 9.4365 | 9.1814 | 8.8487 | 8.5448 | 8.0237 | 6.9993 | 5.5902 | 1.7026 | -2.4479 | -4.3691 | -5.189 | 4.5286 | 4.4765 | 4.3409 | 4.0918 | 3.7794 | 3.5055 | 3.1547 | 2.7475 | 2.1609 | 0.20176 | -1.7716 | -2.5647 | -3.0773 | 7.9775 | 7.9089 | 7.7596 | 7.4714 | 7.1013 | 6.7595 | 6.3355 | 5.7809 | 4.8992 | 2.0211 | -1.6429 | -3.4014 | -4.1567
|  | LANGLEY | CT |  |  | 9.6405 | 9.5775 | 9.4365 | 9.1814 | 8.8487 | 8.5448 | 8.0237 | 6.9993 | 5.5902 | 1.7026 | -2.4479 | -4.3691 | -5.189 | 4.5286 | 4.4765 | 4.3409 | 4.0918 | 3.7794 | 3.5055 | 3.1547 | 2.7475 | 2.1609 | 0.20176 | -1.7716 | -2.5647 | -3.0773 | 7.9775 | 7.9089 | 7.7596 | 7.4714 | 7.1013 | 6.7595 | 6.3355 | 5.7809 | 4.8992 | 2.0211 | -1.6429 | -3.4014 | -4.1567
|  | LANGLEY | LW |  |  | 9.6405 | 9.5775 | 9.4365 | 9.1814 | 8.8487 | 8.5448 | 8.0237 | 6.9993 | 5.5902 | 1.7026 | -2.4479 | -4.3691 | -5.189 | 4.5286 | 4.4765 | 4.3409 | 4.0918 | 3.7794 | 3.5055 | 3.1547 | 2.7475 | 2.1609 | 0.20176 | -1.7716 | -2.5647 | -3.0773 | 7.9775 | 7.9089 | 7.7596 | 7.4714 | 7.1013 | 6.7595 | 6.3355 | 5.7809 | 4.8992 | 2.0211 | -1.6429 | -3.4014 | -4.1567
|  | LANGLEY | ST |  |  | 9.6405 | 9.5775 | 9.4365 | 9.1814 | 8.8487 | 8.5448 | 8.0237 | 6.9993 | 5.5902 | 1.7026 | -2.4479 | -4.3691 | -5.189 | 4.5286 | 4.4765 | 4.3409 | 4.0918 | 3.7794 | 3.5055 | 3.1547 | 2.7475 | 2.1609 | 0.20176 | -1.7716 | -2.5647 | -3.0773 | 7.9775 | 7.9089 | 7.7596 | 7.4714 | 7.1013 | 6.7595 | 6.3355 | 5.7809 | 4.8992 | 2.0211 | -1.6429 | -3.4014 | -4.1567
|  | LANGLEY | FS |  |  | 9.6405 | 9.5775 | 9.4365 | 9.1814 | 8.8487 | 8.5448 | 8.0237 | 6.9993 | 5.5902 | 1.7026 | -2.4479 | -4.3691 | -5.189 | 4.5286 | 4.4765 | 4.3409 | 4.0918 | 3.7794 | 3.5055 | 3.1547 | 2.7475 | 2.1609 | 0.20176 | -1.7716 | -2.5647 | -3.0773 | 7.9775 | 7.9089 | 7.7596 | 7.4714 | 7.1013 | 6.7595 | 6.3355 | 5.7809 | 4.8992 | 2.0211 | -1.6429 | -3.4014 | -4.1567
BRAMLEY (FLEE) | FERNHURST | LANGLEY COURT | MINIMUM HEADROOM | SU 80847 29056 | YES | 20.634 | 20.3087 | 19.9744 | 19.6086 | 19.2181 | 18.7982 | 18.2782 | 17.7386 | 16.9658 | 15.434 | 12.683 | 10.874 | 10.0897 | 19.7367 | 19.5196 | 19.2855 | 19.0567 | 18.8093 | 18.5377 | 18.1828 | 17.8084 | 17.3002 | 16.4527 | 15.0318 | 14.062 | 13.3435 | 20.4045 | 20.1141 | 19.8136 | 19.4643 | 19.093 | 18.6964 | 18.2151 | 17.7169 | 16.9957 | 15.5025 | 12.9139 | 11.2082 | 10.47
|  | LANGLEY COURT | CT |  |  | 20.634 | 20.3087 | 19.9744 | 19.6086 | 19.2181 | 18.7982 | 18.2782 | 17.7386 | 16.9658 | 15.434 | 12.683 | 10.874 | 10.0897 | 19.7367 | 19.5196 | 19.2855 | 19.0567 | 18.8093 | 18.5377 | 18.1828 | 17.8084 | 17.3002 | 16.4527 | 15.0318 | 14.062 | 13.3435 | 20.4045 | 20.1141 | 19.8136 | 19.4643 | 19.093 | 18.6964 | 18.2151 | 17.7169 | 16.9957 | 15.5025 | 12.9139 | 11.2082 | 10.47
|  | LANGLEY COURT | LW |  |  | 20.634 | 20.3087 | 19.9744 | 19.6086 | 19.2181 | 18.7982 | 18.2782 | 17.7386 | 16.9658 | 15.434 | 12.683 | 10.874 | 10.0897 | 19.7367 | 19.5196 | 19.2855 | 19.0567 | 18.8093 | 18.5377 | 18.1828 | 17.8084 | 17.3002 | 16.4527 | 15.0318 | 14.062 | 13.3435 | 20.4045 | 20.1141 | 19.8136 | 19.4643 | 19.093 | 18.6964 | 18.2151 | 17.7169 | 16.9957 | 15.5025 | 12.9139 | 11.2082 | 10.47
|  | LANGLEY COURT | ST |  |  | 20.634 | 20.3087 | 19.9744 | 19.6086 | 19.2181 | 18.7982 | 18.2782 | 17.7386 | 16.9658 | 15.434 | 12.683 | 10.874 | 10.0897 | 19.7367 | 19.5196 | 19.2855 | 19.0567 | 18.8093 | 18.5377 | 18.1828 | 17.8084 | 17.3002 | 16.4527 | 15.0318 | 14.062 | 13.3435 | 20.4045 | 20.1141 | 19.8136 | 19.4643 | 19.093 | 18.6964 | 18.2151 | 17.7169 | 16.9957 | 15.5025 | 12.9139 | 11.2082 | 10.47
|  | LANGLEY COURT | FS |  |  | 20.634 | 20.3087 | 19.9744 | 19.6086 | 19.2181 | 18.7982 | 18.2782 | 17.7386 | 16.9658 | 15.434 | 12.683 | 10.874 | 10.0897 | 19.7367 | 19.5196 | 19.2855 | 19.0567 | 18.8093 | 18.5377 | 18.1828 | 17.8084 | 17.3002 | 16.4527 | 15.0318 | 14.062 | 13.3435 | 20.4045 | 20.1141 | 19.8136 | 19.4643 | 19.093 | 18.6964 | 18.2151 | 17.7169 | 16.9957 | 15.5025 | 12.9139 | 11.2082 | 10.47
AXMINSTER | YEOVIL BSP | LARKHILL | MINIMUM HEADROOM | ST 53677 16914 | YES | 12.3112 | 12.08 | 11.7575 | 11.346 | 10.919 | 10.4688 | 9.989 | 9.461 | 8.5509 | 5.9537 | 1.6016 | -2.0449 | -4.1907 | 15.4356 | 15.2522 | 14.9855 | 14.6937 | 14.3883 | 14.0577 | 13.7013 | 13.2962 | 12.671 | 10.9254 | 8.4317 | 6.0175 | 3.4557 | 13.2369 | 13.0227 | 12.717 | 12.3357 | 11.9394 | 11.5195 | 11.0714 | 10.5753 | 9.7269 | 7.3282 | 3.5005 | 0.37416 | -1.4329
|  | LARKHILL | CT |  |  | 12.3112 | 12.08 | 11.7575 | 11.346 | 10.919 | 10.4688 | 9.989 | 9.461 | 8.5509 | 5.9537 | 1.6016 | -2.0449 | -4.1907 | 15.4356 | 15.2522 | 14.9855 | 14.6937 | 14.3883 | 14.0577 | 13.7013 | 13.2962 | 12.671 | 10.9254 | 8.4317 | 6.0175 | 3.4557 | 13.2369 | 13.0227 | 12.717 | 12.3357 | 11.9394 | 11.5195 | 11.0714 | 10.5753 | 9.7269 | 7.3282 | 3.5005 | 0.37416 | -1.4329
|  | LARKHILL | LW |  |  | 12.3112 | 12.08 | 11.7575 | 11.346 | 10.919 | 10.4688 | 9.989 | 9.461 | 8.5509 | 5.9537 | 1.6016 | -2.0449 | -4.1907 | 15.4356 | 15.2522 | 14.9855 | 14.6937 | 14.3883 | 14.0577 | 13.7013 | 13.2962 | 12.671 | 10.9254 | 8.4317 | 6.0175 | 3.4557 | 13.2369 | 13.0227 | 12.717 | 12.3357 | 11.9394 | 11.5195 | 11.0714 | 10.5753 | 9.7269 | 7.3282 | 3.5005 | 0.37416 | -1.4329
|  | LARKHILL | ST |  |  | 12.3112 | 12.08 | 11.7575 | 11.346 | 10.919 | 10.4688 | 9.989 | 9.461 | 8.5509 | 5.9537 | 1.6016 | -2.0449 | -4.1907 | 15.4356 | 15.2522 | 14.9855 | 14.6937 | 14.3883 | 14.0577 | 13.7013 | 13.2962 | 12.671 | 10.9254 | 8.4317 | 6.0175 | 3.4557 | 13.2369 | 13.0227 | 12.717 | 12.3357 | 11.9394 | 11.5195 | 11.0714 | 10.5753 | 9.7269 | 7.3282 | 3.5005 | 0.37416 | -1.4329
|  | LARKHILL | FS |  |  | 12.3112 | 12.08 | 11.7575 | 11.346 | 10.919 | 10.4688 | 9.989 | 9.461 | 8.5509 | 5.9537 | 1.6016 | -2.0449 | -4.1907 | 15.4356 | 15.2522 | 14.9855 | 14.6937 | 14.3883 | 14.0577 | 13.7013 | 13.2962 | 12.671 | 10.9254 | 8.4317 | 6.0175 | 3.4557 | 13.2369 | 13.0227 | 12.717 | 12.3357 | 11.9394 | 11.5195 | 11.0714 | 10.5753 | 9.7269 | 7.3282 | 3.5005 | 0.37416 | -1.4329
COWLEY GSP | WITNEY BSP | LEAFIELD | MINIMUM HEADROOM | SP 30282 15270 | NO | 1.9963 | 1.8551 | 1.6911 | 1.4513 | 1.1979 | 0.93923 | 0.64151 | 0.3039 | -0.20676 | -1.2602 | -2.9572 | -3.8155 | -3.9251 | 2.8044 | 2.7128 | 2.6017 | 2.4644 | 2.3175 | 2.1644 | 1.9813 | 1.7637 | 1.4572 | 0.90957 | 0.1151 | -0.32182 | -0.5264 | 2.48 | 2.347 | 2.1912 | 1.9695 | 1.7352 | 1.4951 | 1.2166 | 0.89791 | 0.41994 | -0.53945 | -2.0907 | -2.901 | -3.0036
|  | LEAFIELD | CT |  |  | 1.9963 | 1.8551 | 1.6911 | 1.4513 | 1.1979 | 0.93923 | 0.64151 | 0.3039 | -0.20676 | -1.2602 | -2.9572 | -3.8155 | -3.9251 | 2.8044 | 2.7128 | 2.6017 | 2.4644 | 2.3175 | 2.1644 | 1.9813 | 1.7637 | 1.4572 | 0.90957 | 0.1151 | -0.32182 | -0.5264 | 2.48 | 2.347 | 2.1912 | 1.9695 | 1.7352 | 1.4951 | 1.2166 | 0.89791 | 0.41994 | -0.53945 | -2.0907 | -2.901 | -3.0036
|  | LEAFIELD | LW |  |  | 1.9963 | 1.8551 | 1.6911 | 1.4513 | 1.1979 | 0.93923 | 0.64151 | 0.3039 | -0.20676 | -1.2602 | -2.9572 | -3.8155 | -3.9251 | 2.8044 | 2.7128 | 2.6017 | 2.4644 | 2.3175 | 2.1644 | 1.9813 | 1.7637 | 1.4572 | 0.90957 | 0.1151 | -0.32182 | -0.5264 | 2.48 | 2.347 | 2.1912 | 1.9695 | 1.7352 | 1.4951 | 1.2166 | 0.89791 | 0.41994 | -0.53945 | -2.0907 | -2.901 | -3.0036
|  | LEAFIELD | ST |  |  | 1.9963 | 1.8551 | 1.6911 | 1.4513 | 1.1979 | 0.93923 | 0.64151 | 0.3039 | -0.20676 | -1.2602 | -2.9572 | -3.8155 | -3.9251 | 2.8044 | 2.7128 | 2.6017 | 2.4644 | 2.3175 | 2.1644 | 1.9813 | 1.7637 | 1.4572 | 0.90957 | 0.1151 | -0.32182 | -0.5264 | 2.48 | 2.347 | 2.1912 | 1.9695 | 1.7352 | 1.4951 | 1.2166 | 0.89791 | 0.41994 | -0.53945 | -2.0907 | -2.901 | -3.0036
|  | LEAFIELD | FS |  |  | 1.9963 | 1.8551 | 1.6911 | 1.4513 | 1.1979 | 0.93923 | 0.64151 | 0.3039 | -0.20676 | -1.2602 | -2.9572 | -3.8155 | -3.9251 | 2.8044 | 2.7128 | 2.6017 | 2.4644 | 2.3175 | 2.1644 | 1.9813 | 1.7637 | 1.4572 | 0.90957 | 0.1151 | -0.32182 | -0.5264 | 2.48 | 2.347 | 2.1912 | 1.9695 | 1.7352 | 1.4951 | 1.2166 | 0.89791 | 0.41994 | -0.53945 | -2.0907 | -2.901 | -3.0036
WILLESDEN GSP | ACTON LANE | LEAMINGTON PARK | MINIMUM HEADROOM | TQ 20539 81536 | YES | 29.2969 | 29.1984 | 29.0798 | 28.9512 | 28.8084 | 28.5684 | 28.2562 | 27.8943 | 27.3844 | 25.6444 | 22.029 | 19.1782 | 17.2021 | 31.4512 | 31.4305 | 31.4026 | 31.3735 | 31.3421 | 31.308 | 31.271 | 31.2264 | 31.0873 | 29.9812 | 27.8193 | 25.8789 | 23.5326 | 30.1046 | 30.0032 | 29.8298 | 29.6325 | 29.3948 | 29.1384 | 28.862 | 28.5368 | 28.093 | 26.5 | 23.3008 | 20.8839 | 19.2421
|  | LEAMINGTON PARK | CT |  |  | 29.2969 | 29.1984 | 29.0798 | 28.9512 | 28.8084 | 28.5684 | 28.2562 | 27.8943 | 27.3844 | 25.6444 | 22.029 | 19.1782 | 17.2021 | 31.4512 | 31.4305 | 31.4026 | 31.3735 | 31.3421 | 31.308 | 31.271 | 31.2264 | 31.0873 | 29.9812 | 27.8193 | 25.8789 | 23.5326 | 30.1046 | 30.0032 | 29.8298 | 29.6325 | 29.3948 | 29.1384 | 28.862 | 28.5368 | 28.093 | 26.5 | 23.3008 | 20.8839 | 19.2421
|  | LEAMINGTON PARK | LW |  |  | 29.2969 | 29.1984 | 29.0798 | 28.9512 | 28.8084 | 28.5684 | 28.2562 | 27.8943 | 27.3844 | 25.6444 | 22.029 | 19.1782 | 17.2021 | 31.4512 | 31.4305 | 31.4026 | 31.3735 | 31.3421 | 31.308 | 31.271 | 31.2264 | 31.0873 | 29.9812 | 27.8193 | 25.8789 | 23.5326 | 30.1046 | 30.0032 | 29.8298 | 29.6325 | 29.3948 | 29.1384 | 28.862 | 28.5368 | 28.093 | 26.5 | 23.3008 | 20.8839 | 19.2421
|  | LEAMINGTON PARK | ST |  |  | 29.2969 | 29.1984 | 29.0798 | 28.9512 | 28.8084 | 28.5684 | 28.2562 | 27.8943 | 27.3844 | 25.6444 | 22.029 | 19.1782 | 17.2021 | 31.4512 | 31.4305 | 31.4026 | 31.3735 | 31.3421 | 31.308 | 31.271 | 31.2264 | 31.0873 | 29.9812 | 27.8193 | 25.8789 | 23.5326 | 30.1046 | 30.0032 | 29.8298 | 29.6325 | 29.3948 | 29.1384 | 28.862 | 28.5368 | 28.093 | 26.5 | 23.3008 | 20.8839 | 19.2421
|  | LEAMINGTON PARK | FS |  |  | 29.2969 | 29.1984 | 29.0798 | 28.9512 | 28.8084 | 28.5684 | 28.2562 | 27.8943 | 27.3844 | 25.6444 | 22.029 | 19.1782 | 17.2021 | 31.4512 | 31.4305 | 31.4026 | 31.3735 | 31.3421 | 31.308 | 31.271 | 31.2264 | 31.0873 | 29.9812 | 27.8193 | 25.8789 | 23.5326 | 30.1046 | 30.0032 | 29.8298 | 29.6325 | 29.3948 | 29.1384 | 28.862 | 28.5368 | 28.093 | 26.5 | 23.3008 | 20.8839 | 19.2421
MINETY GSP | STRATTON (2 X 60) | LECHLADE | MINIMUM HEADROOM | SP 22074 00496 | YES | 3.9112 | 3.7606 | 3.5814 | 3.3264 | 3.0612 | 2.7809 | 2.4598 | 2.0877 | 1.5527 | 0.37354 | -1.6578 | -3.0156 | -3.3126 | 4.881 | 4.7957 | 4.6925 | 4.5592 | 4.4191 | 4.2695 | 4.0956 | 3.8907 | 3.6113 | 3.02 | 2.0458 | 1.4028 | 1.1181 | 4.6784 | 4.5418 | 4.3805 | 4.1467 | 3.904 | 3.6478 | 3.3556 | 3.0196 | 2.5325 | 1.4382 | -0.44854 | -1.6516 | -1.9213
|  | LECHLADE | CT |  |  | 3.9112 | 3.7606 | 3.5814 | 3.3264 | 3.0612 | 2.7809 | 2.4598 | 2.0877 | 1.5527 | 0.37354 | -1.6578 | -3.0156 | -3.3126 | 4.881 | 4.7957 | 4.6925 | 4.5592 | 4.4191 | 4.2695 | 4.0956 | 3.8907 | 3.6113 | 3.02 | 2.0458 | 1.4028 | 1.1181 | 4.6784 | 4.5418 | 4.3805 | 4.1467 | 3.904 | 3.6478 | 3.3556 | 3.0196 | 2.5325 | 1.4382 | -0.44854 | -1.6516 | -1.9213
|  | LECHLADE | LW |  |  | 3.9112 | 3.7606 | 3.5814 | 3.3264 | 3.0612 | 2.7809 | 2.4598 | 2.0877 | 1.5527 | 0.37354 | -1.6578 | -3.0156 | -3.3126 | 4.881 | 4.7957 | 4.6925 | 4.5592 | 4.4191 | 4.2695 | 4.0956 | 3.8907 | 3.6113 | 3.02 | 2.0458 | 1.4028 | 1.1181 | 4.6784 | 4.5418 | 4.3805 | 4.1467 | 3.904 | 3.6478 | 3.3556 | 3.0196 | 2.5325 | 1.4382 | -0.44854 | -1.6516 | -1.9213
|  | LECHLADE | ST |  |  | 3.9112 | 3.7606 | 3.5814 | 3.3264 | 3.0612 | 2.7809 | 2.4598 | 2.0877 | 1.5527 | 0.37354 | -1.6578 | -3.0156 | -3.3126 | 4.881 | 4.7957 | 4.6925 | 4.5592 | 4.4191 | 4.2695 | 4.0956 | 3.8907 | 3.6113 | 3.02 | 2.0458 | 1.4028 | 1.1181 | 4.6784 | 4.5418 | 4.3805 | 4.1467 | 3.904 | 3.6478 | 3.3556 | 3.0196 | 2.5325 | 1.4382 | -0.44854 | -1.6516 | -1.9213
|  | LECHLADE | FS |  |  | 3.9112 | 3.7606 | 3.5814 | 3.3264 | 3.0612 | 2.7809 | 2.4598 | 2.0877 | 1.5527 | 0.37354 | -1.6578 | -3.0156 | -3.3126 | 4.881 | 4.7957 | 4.6925 | 4.5592 | 4.4191 | 4.2695 | 4.0956 | 3.8907 | 3.6113 | 3.02 | 2.0458 | 1.4028 | 1.1181 | 4.6784 | 4.5418 | 4.3805 | 4.1467 | 3.904 | 3.6478 | 3.3556 | 3.0196 | 2.5325 | 1.4382 | -0.44854 | -1.6516 | -1.9213
BRAMLEY (ANDO-THAT) | THATCHAM BSP | LECKHAMPSTEAD | MINIMUM HEADROOM | SU 43962 77635 | YES | 2.9802 | 2.7913 | 2.6083 | 2.3188 | 2.0175 | 1.716 | 1.3834 | 1.116 | 0.85183 | 0.54725 | 0.12171 | -0.016341 | -0.069392 | 4.3013 | 4.1918 | 4.0863 | 3.9507 | 3.8079 | 3.6585 | 3.4768 | 3.3051 | 3.1029 | 2.9 | 2.6279 | 2.4862 | 2.3274 | 3.6003 | 3.4246 | 3.2548 | 2.9964 | 2.7238 | 2.4498 | 2.1446 | 1.8949 | 1.6276 | 1.3411 | 0.957 | 0.83914 | 0.79551
|  | LECKHAMPSTEAD | CT |  |  | 2.9802 | 2.7913 | 2.6083 | 2.3188 | 2.0175 | 1.716 | 1.3834 | 1.116 | 0.85183 | 0.54725 | 0.12171 | -0.016341 | -0.069392 | 4.3013 | 4.1918 | 4.0863 | 3.9507 | 3.8079 | 3.6585 | 3.4768 | 3.3051 | 3.1029 | 2.9 | 2.6279 | 2.4862 | 2.3274 | 3.6003 | 3.4246 | 3.2548 | 2.9964 | 2.7238 | 2.4498 | 2.1446 | 1.8949 | 1.6276 | 1.3411 | 0.957 | 0.83914 | 0.79551
|  | LECKHAMPSTEAD | LW |  |  | 2.9802 | 2.7913 | 2.6083 | 2.3188 | 2.0175 | 1.716 | 1.3834 | 1.116 | 0.85183 | 0.54725 | 0.12171 | -0.016341 | -0.069392 | 4.3013 | 4.1918 | 4.0863 | 3.9507 | 3.8079 | 3.6585 | 3.4768 | 3.3051 | 3.1029 | 2.9 | 2.6279 | 2.4862 | 2.3274 | 3.6003 | 3.4246 | 3.2548 | 2.9964 | 2.7238 | 2.4498 | 2.1446 | 1.8949 | 1.6276 | 1.3411 | 0.957 | 0.83914 | 0.79551
|  | LECKHAMPSTEAD | ST |  |  | 2.9802 | 2.7913 | 2.6083 | 2.3188 | 2.0175 | 1.716 | 1.3834 | 1.116 | 0.85183 | 0.54725 | 0.12171 | -0.016341 | -0.069392 | 4.3013 | 4.1918 | 4.0863 | 3.9507 | 3.8079 | 3.6585 | 3.4768 | 3.3051 | 3.1029 | 2.9 | 2.6279 | 2.4862 | 2.3274 | 3.6003 | 3.4246 | 3.2548 | 2.9964 | 2.7238 | 2.4498 | 2.1446 | 1.8949 | 1.6276 | 1.3411 | 0.957 | 0.83914 | 0.79551
|  | LECKHAMPSTEAD | FS |  |  | 2.9802 | 2.7913 | 2.6083 | 2.3188 | 2.0175 | 1.716 | 1.3834 | 1.116 | 0.85183 | 0.54725 | 0.12171 | -0.016341 | -0.069392 | 4.3013 | 4.1918 | 4.0863 | 3.9507 | 3.8079 | 3.6585 | 3.4768 | 3.3051 | 3.1029 | 2.9 | 2.6279 | 2.4862 | 2.3274 | 3.6003 | 3.4246 | 3.2548 | 2.9964 | 2.7238 | 2.4498 | 2.1446 | 1.8949 | 1.6276 | 1.3411 | 0.957 | 0.83914 | 0.79551
LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | LEE-ON-SOLENT | MINIMUM HEADROOM | SU 56858 00293 | YES | 17.4774 | 17.1659 | 16.7199 | 16.1413 | 15.511 | 14.8567 | 14.151 | 13.2771 | 11.9115 | 8.4339 | 2.9654 | -1.4942 | -4.1997 | 17.8345 | 17.6051 | 17.2766 | 16.9074 | 16.4954 | 16.0299 | 15.5242 | 14.8741 | 13.9413 | 11.7166 | 8.7054 | 6.0772 | 3.5828 | 16.9285 | 16.6639 | 16.2879 | 15.7866 | 15.2418 | 14.6775 | 14.0373 | 13.222 | 11.955 | 8.7777 | 3.9608 | 0.13717 | -2.1401
|  | LEE-ON-SOLENT | CT |  |  | 17.4774 | 17.1659 | 16.7199 | 16.1413 | 15.511 | 14.8567 | 14.151 | 13.2771 | 11.9115 | 8.4339 | 2.9654 | -1.4942 | -4.1997 | 17.8345 | 17.6051 | 17.2766 | 16.9074 | 16.4954 | 16.0299 | 15.5242 | 14.8741 | 13.9413 | 11.7166 | 8.7054 | 6.0772 | 3.5828 | 16.9285 | 16.6639 | 16.2879 | 15.7866 | 15.2418 | 14.6775 | 14.0373 | 13.222 | 11.955 | 8.7777 | 3.9608 | 0.13717 | -2.1401
|  | LEE-ON-SOLENT | LW |  |  | 17.4774 | 17.1659 | 16.7199 | 16.1413 | 15.511 | 14.8567 | 14.151 | 13.2771 | 11.9115 | 8.4339 | 2.9654 | -1.4942 | -4.1997 | 17.8345 | 17.6051 | 17.2766 | 16.9074 | 16.4954 | 16.0299 | 15.5242 | 14.8741 | 13.9413 | 11.7166 | 8.7054 | 6.0772 | 3.5828 | 16.9285 | 16.6639 | 16.2879 | 15.7866 | 15.2418 | 14.6775 | 14.0373 | 13.222 | 11.955 | 8.7777 | 3.9608 | 0.13717 | -2.1401
|  | LEE-ON-SOLENT | ST |  |  | 17.4774 | 17.1659 | 16.7199 | 16.1413 | 15.511 | 14.8567 | 14.151 | 13.2771 | 11.9115 | 8.4339 | 2.9654 | -1.4942 | -4.1997 | 17.8345 | 17.6051 | 17.2766 | 16.9074 | 16.4954 | 16.0299 | 15.5242 | 14.8741 | 13.9413 | 11.7166 | 8.7054 | 6.0772 | 3.5828 | 16.9285 | 16.6639 | 16.2879 | 15.7866 | 15.2418 | 14.6775 | 14.0373 | 13.222 | 11.955 | 8.7777 | 3.9608 | 0.13717 | -2.1401
|  | LEE-ON-SOLENT | FS |  |  | 17.4774 | 17.1659 | 16.7199 | 16.1413 | 15.511 | 14.8567 | 14.151 | 13.2771 | 11.9115 | 8.4339 | 2.9654 | -1.4942 | -4.1997 | 17.8345 | 17.6051 | 17.2766 | 16.9074 | 16.4954 | 16.0299 | 15.5242 | 14.8741 | 13.9413 | 11.7166 | 8.7054 | 6.0772 | 3.5828 | 16.9285 | 16.6639 | 16.2879 | 15.7866 | 15.2418 | 14.6775 | 14.0373 | 13.222 | 11.955 | 8.7777 | 3.9608 | 0.13717 | -2.1401
LOVEDEAN GSP | HAVANT | LEIGH PARK | MINIMUM HEADROOM | SU 72144 07875 | YES | 13.8636 | 13.5756 | 13.2013 | 12.859 | 12.3933 | 11.8981 | 11.3716 | 10.7054 | 9.7696 | 6.7837 | 1.8007 | -1.6451 | -3.7564 | 17.7406 | 17.5409 | 17.2742 | 17.0196 | 16.6452 | 16.2451 | 15.8271 | 15.2833 | 14.5923 | 12.345 | 8.7252 | 5.6139 | 1.9893 | 16.2569 | 16.0522 | 15.7365 | 15.409 | 14.9578 | 14.4743 | 13.968 | 13.326 | 12.4461 | 9.6614 | 5.2959 | 2.455 | 0.73097
|  | LEIGH PARK | CT |  |  | 13.8636 | 13.5756 | 13.2013 | 12.859 | 12.3933 | 11.8981 | 11.3716 | 10.7054 | 9.7696 | 6.7837 | 1.8007 | -1.6451 | -3.7564 | 17.7406 | 17.5409 | 17.2742 | 17.0196 | 16.6452 | 16.2451 | 15.8271 | 15.2833 | 14.5923 | 12.345 | 8.7252 | 5.6139 | 1.9893 | 16.2569 | 16.0522 | 15.7365 | 15.409 | 14.9578 | 14.4743 | 13.968 | 13.326 | 12.4461 | 9.6614 | 5.2959 | 2.455 | 0.73097
|  | LEIGH PARK | LW |  |  | 13.8636 | 13.5756 | 13.2013 | 12.859 | 12.3933 | 11.8981 | 11.3716 | 10.7054 | 9.7696 | 6.7837 | 1.8007 | -1.6451 | -3.7564 | 17.7406 | 17.5409 | 17.2742 | 17.0196 | 16.6452 | 16.2451 | 15.8271 | 15.2833 | 14.5923 | 12.345 | 8.7252 | 5.6139 | 1.9893 | 16.2569 | 16.0522 | 15.7365 | 15.409 | 14.9578 | 14.4743 | 13.968 | 13.326 | 12.4461 | 9.6614 | 5.2959 | 2.455 | 0.73097
|  | LEIGH PARK | ST |  |  | 13.8636 | 13.5756 | 13.2013 | 12.859 | 12.3933 | 11.8981 | 11.3716 | 10.7054 | 9.7696 | 6.7837 | 1.8007 | -1.6451 | -3.7564 | 17.7406 | 17.5409 | 17.2742 | 17.0196 | 16.6452 | 16.2451 | 15.8271 | 15.2833 | 14.5923 | 12.345 | 8.7252 | 5.6139 | 1.9893 | 16.2569 | 16.0522 | 15.7365 | 15.409 | 14.9578 | 14.4743 | 13.968 | 13.326 | 12.4461 | 9.6614 | 5.2959 | 2.455 | 0.73097
|  | LEIGH PARK | FS |  |  | 13.8636 | 13.5756 | 13.2013 | 12.859 | 12.3933 | 11.8981 | 11.3716 | 10.7054 | 9.7696 | 6.7837 | 1.8007 | -1.6451 | -3.7564 | 17.7406 | 17.5409 | 17.2742 | 17.0196 | 16.6452 | 16.2451 | 15.8271 | 15.2833 | 14.5923 | 12.345 | 8.7252 | 5.6139 | 1.9893 | 16.2569 | 16.0522 | 15.7365 | 15.409 | 14.9578 | 14.4743 | 13.968 | 13.326 | 12.4461 | 9.6614 | 5.2959 | 2.455 | 0.73097
BRAMLEY (FLEE) | READING BSP | LITTLE HUNGERFORD | MINIMUM HEADROOM | SU 75372 72019 | YES | 15.0346 | 14.337 | 13.5731 | 12.5781 | 11.5033 | 10.3815 | 9.1445 | 7.6153 | 4.9943 | -0.56699 | -8.7318 | -14.1726 | -16.6589 | 21.3517 | 20.7764 | 20.1416 | 19.433 | 18.6597 | 17.8172 | 16.8774 | 15.6917 | 13.8387 | 10.1009 | 4.9553 | 0.90485 | -3.1414 | 17.6536 | 16.9728 | 16.2263 | 15.2807 | 14.2581 | 13.1822 | 11.9928 | 10.5128 | 8.0031 | 2.7826 | -4.6097 | -9.3954 | -11.5523
|  | LITTLE HUNGERFORD | CT |  |  | 15.0346 | 14.337 | 13.5731 | 12.5781 | 11.5033 | 10.3815 | 9.1445 | 7.6153 | 4.9943 | -0.56699 | -8.7318 | -14.1726 | -16.6589 | 21.3517 | 20.7764 | 20.1416 | 19.433 | 18.6597 | 17.8172 | 16.8774 | 15.6917 | 13.8387 | 10.1009 | 4.9553 | 0.90485 | -3.1414 | 17.6536 | 16.9728 | 16.2263 | 15.2807 | 14.2581 | 13.1822 | 11.9928 | 10.5128 | 8.0031 | 2.7826 | -4.6097 | -9.3954 | -11.5523
|  | LITTLE HUNGERFORD | LW |  |  | 15.0346 | 14.337 | 13.5731 | 12.5781 | 11.5033 | 10.3815 | 9.1445 | 7.6153 | 4.9943 | -0.56699 | -8.7318 | -14.1726 | -16.6589 | 21.3517 | 20.7764 | 20.1416 | 19.433 | 18.6597 | 17.8172 | 16.8774 | 15.6917 | 13.8387 | 10.1009 | 4.9553 | 0.90485 | -3.1414 | 17.6536 | 16.9728 | 16.2263 | 15.2807 | 14.2581 | 13.1822 | 11.9928 | 10.5128 | 8.0031 | 2.7826 | -4.6097 | -9.3954 | -11.5523
|  | LITTLE HUNGERFORD | ST |  |  | 15.0346 | 14.337 | 13.5731 | 12.5781 | 11.5033 | 10.3815 | 9.1445 | 7.6153 | 4.9943 | -0.56699 | -8.7318 | -14.1726 | -16.6589 | 21.3517 | 20.7764 | 20.1416 | 19.433 | 18.6597 | 17.8172 | 16.8774 | 15.6917 | 13.8387 | 10.1009 | 4.9553 | 0.90485 | -3.1414 | 17.6536 | 16.9728 | 16.2263 | 15.2807 | 14.2581 | 13.1822 | 11.9928 | 10.5128 | 8.0031 | 2.7826 | -4.6097 | -9.3954 | -11.5523
|  | LITTLE HUNGERFORD | FS |  |  | 15.0346 | 14.337 | 13.5731 | 12.5781 | 11.5033 | 10.3815 | 9.1445 | 7.6153 | 4.9943 | -0.56699 | -8.7318 | -14.1726 | -16.6589 | 21.3517 | 20.7764 | 20.1416 | 19.433 | 18.6597 | 17.8172 | 16.8774 | 15.6917 | 13.8387 | 10.1009 | 4.9553 | 0.90485 | -3.1414 | 17.6536 | 16.9728 | 16.2263 | 15.2807 | 14.2581 | 13.1822 | 11.9928 | 10.5128 | 8.0031 | 2.7826 | -4.6097 | -9.3954 | -11.5523
COWLEY GSP | HIGH WYCOMBE BSP | LITTLE MARLOW | MINIMUM HEADROOM | SU 86037 87794 | YES | 19.8215 | 19.4285 | 19.0094 | 18.4483 | 17.8454 | 17.209 | 16.4745 | 15.6344 | 14.2195 | 11.1226 | 6.1795 | 2.8156 | 1.178 | 21.0403 | 20.7364 | 20.4082 | 20.0199 | 19.598 | 19.1395 | 18.6011 | 17.9348 | 16.9343 | 14.8223 | 11.4928 | 8.5498 | 5.1401 | 22.5189 | 22.1383 | 21.732 | 21.2021 | 20.6314 | 20.0258 | 19.3235 | 18.5163 | 17.1701 | 14.2847 | 9.8266 | 6.8774 | 5.5084
|  | LITTLE MARLOW | CT |  |  | 19.8215 | 19.4285 | 19.0094 | 18.4483 | 17.8454 | 17.209 | 16.4745 | 15.6344 | 14.2195 | 11.1226 | 6.1795 | 2.8156 | 1.178 | 21.0403 | 20.7364 | 20.4082 | 20.0199 | 19.598 | 19.1395 | 18.6011 | 17.9348 | 16.9343 | 14.8223 | 11.4928 | 8.5498 | 5.1401 | 22.5189 | 22.1383 | 21.732 | 21.2021 | 20.6314 | 20.0258 | 19.3235 | 18.5163 | 17.1701 | 14.2847 | 9.8266 | 6.8774 | 5.5084
|  | LITTLE MARLOW | LW |  |  | 19.8215 | 19.4285 | 19.0094 | 18.4483 | 17.8454 | 17.209 | 16.4745 | 15.6344 | 14.2195 | 11.1226 | 6.1795 | 2.8156 | 1.178 | 21.0403 | 20.7364 | 20.4082 | 20.0199 | 19.598 | 19.1395 | 18.6011 | 17.9348 | 16.9343 | 14.8223 | 11.4928 | 8.5498 | 5.1401 | 22.5189 | 22.1383 | 21.732 | 21.2021 | 20.6314 | 20.0258 | 19.3235 | 18.5163 | 17.1701 | 14.2847 | 9.8266 | 6.8774 | 5.5084
|  | LITTLE MARLOW | ST |  |  | 19.8215 | 19.4285 | 19.0094 | 18.4483 | 17.8454 | 17.209 | 16.4745 | 15.6344 | 14.2195 | 11.1226 | 6.1795 | 2.8156 | 1.178 | 21.0403 | 20.7364 | 20.4082 | 20.0199 | 19.598 | 19.1395 | 18.6011 | 17.9348 | 16.9343 | 14.8223 | 11.4928 | 8.5498 | 5.1401 | 22.5189 | 22.1383 | 21.732 | 21.2021 | 20.6314 | 20.0258 | 19.3235 | 18.5163 | 17.1701 | 14.2847 | 9.8266 | 6.8774 | 5.5084
|  | LITTLE MARLOW | FS |  |  | 19.8215 | 19.4285 | 19.0094 | 18.4483 | 17.8454 | 17.209 | 16.4745 | 15.6344 | 14.2195 | 11.1226 | 6.1795 | 2.8156 | 1.178 | 21.0403 | 20.7364 | 20.4082 | 20.0199 | 19.598 | 19.1395 | 18.6011 | 17.9348 | 16.9343 | 14.8223 | 11.4928 | 8.5498 | 5.1401 | 22.5189 | 22.1383 | 21.732 | 21.2021 | 20.6314 | 20.0258 | 19.3235 | 18.5163 | 17.1701 | 14.2847 | 9.8266 | 6.8774 | 5.5084
NURSLING GSP | ROWNHAMS | LORDSHILL | MINIMUM HEADROOM | SU 38746 16055 | YES | 25.9967 | 25.8928 | 25.7613 | 25.58 | 25.3829 | 25.169 | 24.9382 | 24.683 | 24.2684 | 22.1098 | 17.6735 | 13.9328 | 11.5022 | 23.6648 | 23.5442 | 23.3777 | 23.1615 | 22.9248 | 22.6653 | 22.3792 | 22.0475 | 21.5474 | 20.1147 | 17.6426 | 15.448 | 13.3787 | 25.692 | 25.5968 | 25.4747 | 25.309 | 25.1284 | 24.9318 | 24.719 | 24.4821 | 24.0997 | 22.0463 | 18.1746 | 14.9889 | 12.9602
|  | LORDSHILL | CT |  |  | 25.9967 | 25.8928 | 25.7613 | 25.58 | 25.3829 | 25.169 | 24.9382 | 24.683 | 24.2684 | 22.1098 | 17.6735 | 13.9328 | 11.5022 | 23.6648 | 23.5442 | 23.3777 | 23.1615 | 22.9248 | 22.6653 | 22.3792 | 22.0475 | 21.5474 | 20.1147 | 17.6426 | 15.448 | 13.3787 | 25.692 | 25.5968 | 25.4747 | 25.309 | 25.1284 | 24.9318 | 24.719 | 24.4821 | 24.0997 | 22.0463 | 18.1746 | 14.9889 | 12.9602
|  | LORDSHILL | LW |  |  | 25.9967 | 25.8928 | 25.7613 | 25.58 | 25.3829 | 25.169 | 24.9382 | 24.683 | 24.2684 | 22.1098 | 17.6735 | 13.9328 | 11.5022 | 23.6648 | 23.5442 | 23.3777 | 23.1615 | 22.9248 | 22.6653 | 22.3792 | 22.0475 | 21.5474 | 20.1147 | 17.6426 | 15.448 | 13.3787 | 25.692 | 25.5968 | 25.4747 | 25.309 | 25.1284 | 24.9318 | 24.719 | 24.4821 | 24.0997 | 22.0463 | 18.1746 | 14.9889 | 12.9602
|  | LORDSHILL | ST |  |  | 25.9967 | 25.8928 | 25.7613 | 25.58 | 25.3829 | 25.169 | 24.9382 | 24.683 | 24.2684 | 22.1098 | 17.6735 | 13.9328 | 11.5022 | 23.6648 | 23.5442 | 23.3777 | 23.1615 | 22.9248 | 22.6653 | 22.3792 | 22.0475 | 21.5474 | 20.1147 | 17.6426 | 15.448 | 13.3787 | 25.692 | 25.5968 | 25.4747 | 25.309 | 25.1284 | 24.9318 | 24.719 | 24.4821 | 24.0997 | 22.0463 | 18.1746 | 14.9889 | 12.9602
|  | LORDSHILL | FS |  |  | 25.9967 | 25.8928 | 25.7613 | 25.58 | 25.3829 | 25.169 | 24.9382 | 24.683 | 24.2684 | 22.1098 | 17.6735 | 13.9328 | 11.5022 | 23.6648 | 23.5442 | 23.3777 | 23.1615 | 22.9248 | 22.6653 | 22.3792 | 22.0475 | 21.5474 | 20.1147 | 17.6426 | 15.448 | 13.3787 | 25.692 | 25.5968 | 25.4747 | 25.309 | 25.1284 | 24.9318 | 24.719 | 24.4821 | 24.0997 | 22.0463 | 18.1746 | 14.9889 | 12.9602
BRAMLEY (ANDO-THAT) | THATCHAM BSP | LOVE LANE | MINIMUM HEADROOM | SU 47334 68495 | YES | 30.2179 | 29.7061 | 29.146 | 28.3153 | 27.3553 | 26.4824 | 25.4731 | 24.5536 | 23.249 | 19.9105 | 15.068 | 12.335 | 11.1664 | 29.1541 | 28.7785 | 28.3799 | 27.8737 | 27.3017 | 26.755 | 26.1146 | 25.4983 | 24.6928 | 22.4244 | 18.671 | 15.3363 | 11.1162 | 32.1419 | 31.7453 | 31.2241 | 30.4773 | 29.6224 | 28.833 | 27.9162 | 27.0634 | 25.847 | 22.7185 | 18.3742 | 15.9589 | 14.9341
|  | LOVE LANE | CT |  |  | 30.2179 | 29.7061 | 29.146 | 28.3153 | 27.3553 | 26.4824 | 25.4731 | 24.5536 | 23.249 | 19.9105 | 15.068 | 12.335 | 11.1664 | 29.1541 | 28.7785 | 28.3799 | 27.8737 | 27.3017 | 26.755 | 26.1146 | 25.4983 | 24.6928 | 22.4244 | 18.671 | 15.3363 | 11.1162 | 32.1419 | 31.7453 | 31.2241 | 30.4773 | 29.6224 | 28.833 | 27.9162 | 27.0634 | 25.847 | 22.7185 | 18.3742 | 15.9589 | 14.9341
|  | LOVE LANE | LW |  |  | 30.2179 | 29.7061 | 29.146 | 28.3153 | 27.3553 | 26.4824 | 25.4731 | 24.5536 | 23.249 | 19.9105 | 15.068 | 12.335 | 11.1664 | 29.1541 | 28.7785 | 28.3799 | 27.8737 | 27.3017 | 26.755 | 26.1146 | 25.4983 | 24.6928 | 22.4244 | 18.671 | 15.3363 | 11.1162 | 32.1419 | 31.7453 | 31.2241 | 30.4773 | 29.6224 | 28.833 | 27.9162 | 27.0634 | 25.847 | 22.7185 | 18.3742 | 15.9589 | 14.9341
|  | LOVE LANE | ST |  |  | 30.2179 | 29.7061 | 29.146 | 28.3153 | 27.3553 | 26.4824 | 25.4731 | 24.5536 | 23.249 | 19.9105 | 15.068 | 12.335 | 11.1664 | 29.1541 | 28.7785 | 28.3799 | 27.8737 | 27.3017 | 26.755 | 26.1146 | 25.4983 | 24.6928 | 22.4244 | 18.671 | 15.3363 | 11.1162 | 32.1419 | 31.7453 | 31.2241 | 30.4773 | 29.6224 | 28.833 | 27.9162 | 27.0634 | 25.847 | 22.7185 | 18.3742 | 15.9589 | 14.9341
|  | LOVE LANE | FS |  |  | 30.2179 | 29.7061 | 29.146 | 28.3153 | 27.3553 | 26.4824 | 25.4731 | 24.5536 | 23.249 | 19.9105 | 15.068 | 12.335 | 11.1664 | 29.1541 | 28.7785 | 28.3799 | 27.8737 | 27.3017 | 26.755 | 26.1146 | 25.4983 | 24.6928 | 22.4244 | 18.671 | 15.3363 | 11.1162 | 32.1419 | 31.7453 | 31.2241 | 30.4773 | 29.6224 | 28.833 | 27.9162 | 27.0634 | 25.847 | 22.7185 | 18.3742 | 15.9589 | 14.9341
COWLEY GSP | YARNTON BSP | LOVELACE ROAD | MINIMUM HEADROOM | SP 50395 10376 | NO | 13.8561 | 13.6465 | 13.3945 | 12.9594 | 12.5978 | 12.3224 | 12.03 | 11.6985 | 11.1266 | 9.1707 | 6.2726 | 4.1945 | 3.0001 | 15.0724 | 14.9185 | 14.7362 | 14.4724 | 14.2416 | 14.0439 | 13.8288 | 13.5806 | 13.21 | 11.9396 | 10.18 | 8.6687 | 7.0952 | 14.4284 | 14.2369 | 14.007 | 13.6225 | 13.2964 | 13.0396 | 12.7651 | 12.4529 | 11.9218 | 10.1204 | 7.5876 | 5.7983 | 4.7898
|  | LOVELACE ROAD | CT |  |  | 13.8561 | 13.6465 | 13.3945 | 12.9594 | 12.5978 | 12.3224 | 12.03 | 11.6985 | 11.1266 | 9.1707 | 6.2726 | 4.1945 | 3.0001 | 15.0724 | 14.9185 | 14.7362 | 14.4724 | 14.2416 | 14.0439 | 13.8288 | 13.5806 | 13.21 | 11.9396 | 10.18 | 8.6687 | 7.0952 | 14.4284 | 14.2369 | 14.007 | 13.6225 | 13.2964 | 13.0396 | 12.7651 | 12.4529 | 11.9218 | 10.1204 | 7.5876 | 5.7983 | 4.7898
|  | LOVELACE ROAD | LW |  |  | 13.8561 | 13.6465 | 13.3945 | 12.9594 | 12.5978 | 12.3224 | 12.03 | 11.6985 | 11.1266 | 9.1707 | 6.2726 | 4.1945 | 3.0001 | 15.0724 | 14.9185 | 14.7362 | 14.4724 | 14.2416 | 14.0439 | 13.8288 | 13.5806 | 13.21 | 11.9396 | 10.18 | 8.6687 | 7.0952 | 14.4284 | 14.2369 | 14.007 | 13.6225 | 13.2964 | 13.0396 | 12.7651 | 12.4529 | 11.9218 | 10.1204 | 7.5876 | 5.7983 | 4.7898
|  | LOVELACE ROAD | ST |  |  | 13.8561 | 13.6465 | 13.3945 | 12.9594 | 12.5978 | 12.3224 | 12.03 | 11.6985 | 11.1266 | 9.1707 | 6.2726 | 4.1945 | 3.0001 | 15.0724 | 14.9185 | 14.7362 | 14.4724 | 14.2416 | 14.0439 | 13.8288 | 13.5806 | 13.21 | 11.9396 | 10.18 | 8.6687 | 7.0952 | 14.4284 | 14.2369 | 14.007 | 13.6225 | 13.2964 | 13.0396 | 12.7651 | 12.4529 | 11.9218 | 10.1204 | 7.5876 | 5.7983 | 4.7898
|  | LOVELACE ROAD | FS |  |  | 13.8561 | 13.6465 | 13.3945 | 12.9594 | 12.5978 | 12.3224 | 12.03 | 11.6985 | 11.1266 | 9.1707 | 6.2726 | 4.1945 | 3.0001 | 15.0724 | 14.9185 | 14.7362 | 14.4724 | 14.2416 | 14.0439 | 13.8288 | 13.5806 | 13.21 | 11.9396 | 10.18 | 8.6687 | 7.0952 | 14.4284 | 14.2369 | 14.007 | 13.6225 | 13.2964 | 13.0396 | 12.7651 | 12.4529 | 11.9218 | 10.1204 | 7.5876 | 5.7983 | 4.7898
MANNINGTON GSP | ARNEWOOD | LYMINGTON | MINIMUM HEADROOM | SZ 31720 96856 | YES | 19.4604 | 18.9832 | 18.3879 | 17.586 | 16.7177 | 15.753 | 14.6907 | 13.6625 | 11.9962 | 7.8996 | 2.0801 | -2.0124 | -3.7826 | 20.9557 | 20.5803 | 20.0957 | 19.5764 | 19.0139 | 18.3947 | 17.7004 | 16.9856 | 15.9081 | 13.4454 | 10.5324 | 8.3607 | 6.459 | 22.4792 | 22.0117 | 21.4088 | 20.6499 | 19.8337 | 18.9414 | 17.9546 | 16.9789 | 15.4056 | 11.5822 | 6.3745 | 2.9969 | 1.5455
|  | LYMINGTON | CT |  |  | 19.4604 | 18.9832 | 18.3879 | 17.586 | 16.7177 | 15.753 | 14.6907 | 13.6625 | 11.9962 | 7.8996 | 2.0801 | -2.0124 | -3.7826 | 20.9557 | 20.5803 | 20.0957 | 19.5764 | 19.0139 | 18.3947 | 17.7004 | 16.9856 | 15.9081 | 13.4454 | 10.5324 | 8.3607 | 6.459 | 22.4792 | 22.0117 | 21.4088 | 20.6499 | 19.8337 | 18.9414 | 17.9546 | 16.9789 | 15.4056 | 11.5822 | 6.3745 | 2.9969 | 1.5455
|  | LYMINGTON | LW |  |  | 19.4604 | 18.9832 | 18.3879 | 17.586 | 16.7177 | 15.753 | 14.6907 | 13.6625 | 11.9962 | 7.8996 | 2.0801 | -2.0124 | -3.7826 | 20.9557 | 20.5803 | 20.0957 | 19.5764 | 19.0139 | 18.3947 | 17.7004 | 16.9856 | 15.9081 | 13.4454 | 10.5324 | 8.3607 | 6.459 | 22.4792 | 22.0117 | 21.4088 | 20.6499 | 19.8337 | 18.9414 | 17.9546 | 16.9789 | 15.4056 | 11.5822 | 6.3745 | 2.9969 | 1.5455
|  | LYMINGTON | ST |  |  | 19.4604 | 18.9832 | 18.3879 | 17.586 | 16.7177 | 15.753 | 14.6907 | 13.6625 | 11.9962 | 7.8996 | 2.0801 | -2.0124 | -3.7826 | 20.9557 | 20.5803 | 20.0957 | 19.5764 | 19.0139 | 18.3947 | 17.7004 | 16.9856 | 15.9081 | 13.4454 | 10.5324 | 8.3607 | 6.459 | 22.4792 | 22.0117 | 21.4088 | 20.6499 | 19.8337 | 18.9414 | 17.9546 | 16.9789 | 15.4056 | 11.5822 | 6.3745 | 2.9969 | 1.5455
|  | LYMINGTON | FS |  |  | 19.4604 | 18.9832 | 18.3879 | 17.586 | 16.7177 | 15.753 | 14.6907 | 13.6625 | 11.9962 | 7.8996 | 2.0801 | -2.0124 | -3.7826 | 20.9557 | 20.5803 | 20.0957 | 19.5764 | 19.0139 | 18.3947 | 17.7004 | 16.9856 | 15.9081 | 13.4454 | 10.5324 | 8.3607 | 6.459 | 22.4792 | 22.0117 | 21.4088 | 20.6499 | 19.8337 | 18.9414 | 17.9546 | 16.9789 | 15.4056 | 11.5822 | 6.3745 | 2.9969 | 1.5455
MELKSHAM GSP | CHIPPENHAM | LYNEHAM | MINIMUM HEADROOM | ST 99348 80481 | YES | 2.0902 | 1.9126 | 1.6991 | 1.3917 | 1.0728 | 0.72282 | 0.32444 | -0.11597 | -0.7444 | -2.0302 | -4.1238 | -5.5177 | -6.0989 | 5.3912 | 5.2653 | 5.1046 | 4.916 | 4.718 | 4.4951 | 4.2294 | 3.9289 | 3.5123 | 2.804 | 1.8194 | 1.1375 | 0.66885 | 3.4754 | 3.3086 | 3.1061 | 2.8221 | 2.5272 | 2.2024 | 1.8304 | 1.3972 | 0.79352 | -0.37007 | -2.2158 | -3.438 | -3.9492
|  | LYNEHAM | CT |  |  | 2.0902 | 1.9126 | 1.6991 | 1.3917 | 1.0728 | 0.72282 | 0.32444 | -0.11597 | -0.7444 | -2.0302 | -4.1238 | -5.5177 | -6.0989 | 5.3912 | 5.2653 | 5.1046 | 4.916 | 4.718 | 4.4951 | 4.2294 | 3.9289 | 3.5123 | 2.804 | 1.8194 | 1.1375 | 0.66885 | 3.4754 | 3.3086 | 3.1061 | 2.8221 | 2.5272 | 2.2024 | 1.8304 | 1.3972 | 0.79352 | -0.37007 | -2.2158 | -3.438 | -3.9492
|  | LYNEHAM | LW |  |  | 2.0902 | 1.9126 | 1.6991 | 1.3917 | 1.0728 | 0.72282 | 0.32444 | -0.11597 | -0.7444 | -2.0302 | -4.1238 | -5.5177 | -6.0989 | 5.3912 | 5.2653 | 5.1046 | 4.916 | 4.718 | 4.4951 | 4.2294 | 3.9289 | 3.5123 | 2.804 | 1.8194 | 1.1375 | 0.66885 | 3.4754 | 3.3086 | 3.1061 | 2.8221 | 2.5272 | 2.2024 | 1.8304 | 1.3972 | 0.79352 | -0.37007 | -2.2158 | -3.438 | -3.9492
|  | LYNEHAM | ST |  |  | 2.0902 | 1.9126 | 1.6991 | 1.3917 | 1.0728 | 0.72282 | 0.32444 | -0.11597 | -0.7444 | -2.0302 | -4.1238 | -5.5177 | -6.0989 | 5.3912 | 5.2653 | 5.1046 | 4.916 | 4.718 | 4.4951 | 4.2294 | 3.9289 | 3.5123 | 2.804 | 1.8194 | 1.1375 | 0.66885 | 3.4754 | 3.3086 | 3.1061 | 2.8221 | 2.5272 | 2.2024 | 1.8304 | 1.3972 | 0.79352 | -0.37007 | -2.2158 | -3.438 | -3.9492
|  | LYNEHAM | FS |  |  | 2.0902 | 1.9126 | 1.6991 | 1.3917 | 1.0728 | 0.72282 | 0.32444 | -0.11597 | -0.7444 | -2.0302 | -4.1238 | -5.5177 | -6.0989 | 5.3912 | 5.2653 | 5.1046 | 4.916 | 4.718 | 4.4951 | 4.2294 | 3.9289 | 3.5123 | 2.804 | 1.8194 | 1.1375 | 0.66885 | 3.4754 | 3.3086 | 3.1061 | 2.8221 | 2.5272 | 2.2024 | 1.8304 | 1.3972 | 0.79352 | -0.37007 | -2.2158 | -3.438 | -3.9492
BRAMLEY (FLEE) | BRACKNELL RESERVE | M V E E | MINIMUM HEADROOM | SU 98120 65945 | YES | 23.4328 | 23.3184 | 23.0653 | 22.6618 | 22.4541 | 22.2464 | 22.0457 | 21.8871 | 21.7435 | 21.3907 | 21.06 | 20.9662 | 20.9389 | 24.7169 | 24.619 | 24.3761 | 23.957 | 23.7439 | 23.5338 | 23.3336 | 23.1781 | 23.037 | 22.6632 | 22.2676 | 22.0745 | 22.0248 | 25.082 | 24.8896 | 24.5629 | 24.0922 | 23.7692 | 23.4465 | 23.1083 | 22.8059 | 22.5352 | 21.9915 | 21.2618 | 20.8104 | 20.6919
|  | M V E E | CT |  |  | 23.4328 | 23.3184 | 23.0653 | 22.6618 | 22.4541 | 22.2464 | 22.0457 | 21.8871 | 21.7435 | 21.3907 | 21.06 | 20.9662 | 20.9389 | 24.7169 | 24.619 | 24.3761 | 23.957 | 23.7439 | 23.5338 | 23.3336 | 23.1781 | 23.037 | 22.6632 | 22.2676 | 22.0745 | 22.0248 | 25.082 | 24.8896 | 24.5629 | 24.0922 | 23.7692 | 23.4465 | 23.1083 | 22.8059 | 22.5352 | 21.9915 | 21.2618 | 20.8104 | 20.6919
|  | M V E E | LW |  |  | 23.4328 | 23.3184 | 23.0653 | 22.6618 | 22.4541 | 22.2464 | 22.0457 | 21.8871 | 21.7435 | 21.3907 | 21.06 | 20.9662 | 20.9389 | 24.7169 | 24.619 | 24.3761 | 23.957 | 23.7439 | 23.5338 | 23.3336 | 23.1781 | 23.037 | 22.6632 | 22.2676 | 22.0745 | 22.0248 | 25.082 | 24.8896 | 24.5629 | 24.0922 | 23.7692 | 23.4465 | 23.1083 | 22.8059 | 22.5352 | 21.9915 | 21.2618 | 20.8104 | 20.6919
|  | M V E E | ST |  |  | 23.4328 | 23.3184 | 23.0653 | 22.6618 | 22.4541 | 22.2464 | 22.0457 | 21.8871 | 21.7435 | 21.3907 | 21.06 | 20.9662 | 20.9389 | 24.7169 | 24.619 | 24.3761 | 23.957 | 23.7439 | 23.5338 | 23.3336 | 23.1781 | 23.037 | 22.6632 | 22.2676 | 22.0745 | 22.0248 | 25.082 | 24.8896 | 24.5629 | 24.0922 | 23.7692 | 23.4465 | 23.1083 | 22.8059 | 22.5352 | 21.9915 | 21.2618 | 20.8104 | 20.6919
|  | M V E E | FS |  |  | 23.4328 | 23.3184 | 23.0653 | 22.6618 | 22.4541 | 22.2464 | 22.0457 | 21.8871 | 21.7435 | 21.3907 | 21.06 | 20.9662 | 20.9389 | 24.7169 | 24.619 | 24.3761 | 23.957 | 23.7439 | 23.5338 | 23.3336 | 23.1781 | 23.037 | 22.6632 | 22.2676 | 22.0745 | 22.0248 | 25.082 | 24.8896 | 24.5629 | 24.0922 | 23.7692 | 23.4465 | 23.1083 | 22.8059 | 22.5352 | 21.9915 | 21.2618 | 20.8104 | 20.6919
CHICKERELL GSP | CHICKERELL BSP | MAIDEN NEWTON | MINIMUM HEADROOM | SY 59138 97747 | YES | 2.3355 | 2.1783 | 1.9753 | 1.6955 | 1.3977 | 1.0756 | 0.72755 | 0.33138 | -0.22129 | -1.4516 | -3.2233 | -3.634 | -3.7173 | 5.9058 | 5.8507 | 5.7672 | 5.679 | 5.5809 | 5.4423 | 5.276 | 5.0608 | 4.7517 | 4.174 | 3.4879 | 3.2927 | 3.1847 | 3.3513 | 3.207 | 3.023 | 2.7649 | 2.491 | 2.1945 | 1.8749 | 1.5142 | 1.0112 | -0.12986 | -1.8018 | -2.1884 | -2.2666
|  | MAIDEN NEWTON | CT |  |  | 2.3355 | 2.1783 | 1.9753 | 1.6955 | 1.3977 | 1.0756 | 0.72755 | 0.33138 | -0.22129 | -1.4516 | -3.2233 | -3.634 | -3.7173 | 5.9058 | 5.8507 | 5.7672 | 5.679 | 5.5809 | 5.4423 | 5.276 | 5.0608 | 4.7517 | 4.174 | 3.4879 | 3.2927 | 3.1847 | 3.3513 | 3.207 | 3.023 | 2.7649 | 2.491 | 2.1945 | 1.8749 | 1.5142 | 1.0112 | -0.12986 | -1.8018 | -2.1884 | -2.2666
|  | MAIDEN NEWTON | LW |  |  | 2.3355 | 2.1783 | 1.9753 | 1.6955 | 1.3977 | 1.0756 | 0.72755 | 0.33138 | -0.22129 | -1.4516 | -3.2233 | -3.634 | -3.7173 | 5.9058 | 5.8507 | 5.7672 | 5.679 | 5.5809 | 5.4423 | 5.276 | 5.0608 | 4.7517 | 4.174 | 3.4879 | 3.2927 | 3.1847 | 3.3513 | 3.207 | 3.023 | 2.7649 | 2.491 | 2.1945 | 1.8749 | 1.5142 | 1.0112 | -0.12986 | -1.8018 | -2.1884 | -2.2666
|  | MAIDEN NEWTON | ST |  |  | 2.3355 | 2.1783 | 1.9753 | 1.6955 | 1.3977 | 1.0756 | 0.72755 | 0.33138 | -0.22129 | -1.4516 | -3.2233 | -3.634 | -3.7173 | 5.9058 | 5.8507 | 5.7672 | 5.679 | 5.5809 | 5.4423 | 5.276 | 5.0608 | 4.7517 | 4.174 | 3.4879 | 3.2927 | 3.1847 | 3.3513 | 3.207 | 3.023 | 2.7649 | 2.491 | 2.1945 | 1.8749 | 1.5142 | 1.0112 | -0.12986 | -1.8018 | -2.1884 | -2.2666
|  | MAIDEN NEWTON | FS |  |  | 2.3355 | 2.1783 | 1.9753 | 1.6955 | 1.3977 | 1.0756 | 0.72755 | 0.33138 | -0.22129 | -1.4516 | -3.2233 | -3.634 | -3.7173 | 5.9058 | 5.8507 | 5.7672 | 5.679 | 5.5809 | 5.4423 | 5.276 | 5.0608 | 4.7517 | 4.174 | 3.4879 | 3.2927 | 3.1847 | 3.3513 | 3.207 | 3.023 | 2.7649 | 2.491 | 2.1945 | 1.8749 | 1.5142 | 1.0112 | -0.12986 | -1.8018 | -2.1884 | -2.2666
BRAMLEY (FLEE) | MAIDENHEAD BSP | MAIDENHEAD | MINIMUM HEADROOM | SU 86485 79800 | YES | 23.6391 | 23.1092 | 22.4948 | 21.7028 | 20.7083 | 19.6402 | 18.306 | 16.7129 | 14.3967 | 9.6558 | 3.439 | -0.57587 | -2.3099 | 31.887 | 31.4769 | 30.9975 | 30.4606 | 29.8056 | 29.0835 | 28.1933 | 27.1209 | 25.6268 | 22.7157 | 19.1122 | 16.5264 | 14.2337 | 26.4295 | 25.9655 | 25.4274 | 24.7193 | 23.8095 | 22.8231 | 21.6012 | 20.1392 | 17.999 | 13.6687 | 8.0647 | 4.5059 | 2.88
|  | MAIDENHEAD | CT |  |  | 23.6391 | 23.1092 | 22.4948 | 21.7028 | 20.7083 | 19.6402 | 18.306 | 16.7129 | 14.3967 | 9.6558 | 3.439 | -0.57587 | -2.3099 | 31.887 | 31.4769 | 30.9975 | 30.4606 | 29.8056 | 29.0835 | 28.1933 | 27.1209 | 25.6268 | 22.7157 | 19.1122 | 16.5264 | 14.2337 | 26.4295 | 25.9655 | 25.4274 | 24.7193 | 23.8095 | 22.8231 | 21.6012 | 20.1392 | 17.999 | 13.6687 | 8.0647 | 4.5059 | 2.88
|  | MAIDENHEAD | LW |  |  | 23.6391 | 23.1092 | 22.4948 | 21.7028 | 20.7083 | 19.6402 | 18.306 | 16.7129 | 14.3967 | 9.6558 | 3.439 | -0.57587 | -2.3099 | 31.887 | 31.4769 | 30.9975 | 30.4606 | 29.8056 | 29.0835 | 28.1933 | 27.1209 | 25.6268 | 22.7157 | 19.1122 | 16.5264 | 14.2337 | 26.4295 | 25.9655 | 25.4274 | 24.7193 | 23.8095 | 22.8231 | 21.6012 | 20.1392 | 17.999 | 13.6687 | 8.0647 | 4.5059 | 2.88
|  | MAIDENHEAD | ST |  |  | 23.6391 | 23.1092 | 22.4948 | 21.7028 | 20.7083 | 19.6402 | 18.306 | 16.7129 | 14.3967 | 9.6558 | 3.439 | -0.57587 | -2.3099 | 31.887 | 31.4769 | 30.9975 | 30.4606 | 29.8056 | 29.0835 | 28.1933 | 27.1209 | 25.6268 | 22.7157 | 19.1122 | 16.5264 | 14.2337 | 26.4295 | 25.9655 | 25.4274 | 24.7193 | 23.8095 | 22.8231 | 21.6012 | 20.1392 | 17.999 | 13.6687 | 8.0647 | 4.5059 | 2.88
|  | MAIDENHEAD | FS |  |  | 23.6391 | 23.1092 | 22.4948 | 21.7028 | 20.7083 | 19.6402 | 18.306 | 16.7129 | 14.3967 | 9.6558 | 3.439 | -0.57587 | -2.3099 | 31.887 | 31.4769 | 30.9975 | 30.4606 | 29.8056 | 29.0835 | 28.1933 | 27.1209 | 25.6268 | 22.7157 | 19.1122 | 16.5264 | 14.2337 | 26.4295 | 25.9655 | 25.4274 | 24.7193 | 23.8095 | 22.8231 | 21.6012 | 20.1392 | 17.999 | 13.6687 | 8.0647 | 4.5059 | 2.88
MELKSHAM GSP | CHIPPENHAM | MALMESBURY | MINIMUM HEADROOM | ST 92288 87493 | YES | 1.8718 | 1.4698 | 1.13 | 0.6728 | 0.18718 | -0.30989 | -0.88127 | -1.4872 | -2.4174 | -4.5823 | -8.1162 | -10.5482 | -11.465 | 4.0317 | 3.846 | 3.6852 | 3.4756 | 3.2522 | 3.0212 | 2.6992 | 2.3001 | 1.7206 | 0.47652 | -1.3192 | -2.5266 | -3.3812 | 2.6394 | 2.2745 | 1.9556 | 1.5324 | 1.0827 | 0.62003 | 0.084299 | -0.48731 | -1.361 | -3.3579 | -6.5065 | -8.5067 | -9.252
|  | MALMESBURY | CT |  |  | 1.8718 | 1.4698 | 1.13 | 0.6728 | 0.18718 | -0.30989 | -0.88127 | -1.4872 | -2.4174 | -4.5823 | -8.1162 | -10.5482 | -11.465 | 4.0317 | 3.846 | 3.6852 | 3.4756 | 3.2522 | 3.0212 | 2.6992 | 2.3001 | 1.7206 | 0.47652 | -1.3192 | -2.5266 | -3.3812 | 2.6394 | 2.2745 | 1.9556 | 1.5324 | 1.0827 | 0.62003 | 0.084299 | -0.48731 | -1.361 | -3.3579 | -6.5065 | -8.5067 | -9.252
|  | MALMESBURY | LW |  |  | 1.8718 | 1.4698 | 1.13 | 0.6728 | 0.18718 | -0.30989 | -0.88127 | -1.4872 | -2.4174 | -4.5823 | -8.1162 | -10.5482 | -11.465 | 4.0317 | 3.846 | 3.6852 | 3.4756 | 3.2522 | 3.0212 | 2.6992 | 2.3001 | 1.7206 | 0.47652 | -1.3192 | -2.5266 | -3.3812 | 2.6394 | 2.2745 | 1.9556 | 1.5324 | 1.0827 | 0.62003 | 0.084299 | -0.48731 | -1.361 | -3.3579 | -6.5065 | -8.5067 | -9.252
|  | MALMESBURY | ST |  |  | 1.8718 | 1.4698 | 1.13 | 0.6728 | 0.18718 | -0.30989 | -0.88127 | -1.4872 | -2.4174 | -4.5823 | -8.1162 | -10.5482 | -11.465 | 4.0317 | 3.846 | 3.6852 | 3.4756 | 3.2522 | 3.0212 | 2.6992 | 2.3001 | 1.7206 | 0.47652 | -1.3192 | -2.5266 | -3.3812 | 2.6394 | 2.2745 | 1.9556 | 1.5324 | 1.0827 | 0.62003 | 0.084299 | -0.48731 | -1.361 | -3.3579 | -6.5065 | -8.5067 | -9.252
|  | MALMESBURY | FS |  |  | 1.8718 | 1.4698 | 1.13 | 0.6728 | 0.18718 | -0.30989 | -0.88127 | -1.4872 | -2.4174 | -4.5823 | -8.1162 | -10.5482 | -11.465 | 4.0317 | 3.846 | 3.6852 | 3.4756 | 3.2522 | 3.0212 | 2.6992 | 2.3001 | 1.7206 | 0.47652 | -1.3192 | -2.5266 | -3.3812 | 2.6394 | 2.2745 | 1.9556 | 1.5324 | 1.0827 | 0.62003 | 0.084299 | -0.48731 | -1.361 | -3.3579 | -6.5065 | -8.5067 | -9.252
MINETY GSP | SWINDON BSP | MANCHESTER ROAD | MINIMUM HEADROOM | SU 15254 85130 | YES | 11.3001 | 10.4869 | 9.6408 | 8.737 | 7.8027 | 6.8391 | 5.8021 | 4.6769 | 2.9387 | -2.3629 | -11.2449 | -17.179 | -20.4106 | 17.2827 | 16.7128 | 16.0222 | 15.3283 | 14.599 | 13.8111 | 12.9526 | 11.987 | 10.7278 | 6.6924 | -0.72038 | -8.4272 | -18.757 | 12.0841 | 11.3935 | 10.5884 | 9.7449 | 8.877 | 7.9757 | 7.0047 | 5.9386 | 4.344 | -0.54371 | -8.4242 | -13.4411 | -16.1409
|  | MANCHESTER ROAD | CT |  |  | 11.3001 | 10.4869 | 9.6408 | 8.737 | 7.8027 | 6.8391 | 5.8021 | 4.6769 | 2.9387 | -2.3629 | -11.2449 | -17.179 | -20.4106 | 17.2827 | 16.7128 | 16.0222 | 15.3283 | 14.599 | 13.8111 | 12.9526 | 11.987 | 10.7278 | 6.6924 | -0.72038 | -8.4272 | -18.757 | 12.0841 | 11.3935 | 10.5884 | 9.7449 | 8.877 | 7.9757 | 7.0047 | 5.9386 | 4.344 | -0.54371 | -8.4242 | -13.4411 | -16.1409
|  | MANCHESTER ROAD | LW |  |  | 11.3001 | 10.4869 | 9.6408 | 8.737 | 7.8027 | 6.8391 | 5.8021 | 4.6769 | 2.9387 | -2.3629 | -11.2449 | -17.179 | -20.4106 | 17.2827 | 16.7128 | 16.0222 | 15.3283 | 14.599 | 13.8111 | 12.9526 | 11.987 | 10.7278 | 6.6924 | -0.72038 | -8.4272 | -18.757 | 12.0841 | 11.3935 | 10.5884 | 9.7449 | 8.877 | 7.9757 | 7.0047 | 5.9386 | 4.344 | -0.54371 | -8.4242 | -13.4411 | -16.1409
|  | MANCHESTER ROAD | ST |  |  | 11.3001 | 10.4869 | 9.6408 | 8.737 | 7.8027 | 6.8391 | 5.8021 | 4.6769 | 2.9387 | -2.3629 | -11.2449 | -17.179 | -20.4106 | 17.2827 | 16.7128 | 16.0222 | 15.3283 | 14.599 | 13.8111 | 12.9526 | 11.987 | 10.7278 | 6.6924 | -0.72038 | -8.4272 | -18.757 | 12.0841 | 11.3935 | 10.5884 | 9.7449 | 8.877 | 7.9757 | 7.0047 | 5.9386 | 4.344 | -0.54371 | -8.4242 | -13.4411 | -16.1409
|  | MANCHESTER ROAD | FS |  |  | 11.3001 | 10.4869 | 9.6408 | 8.737 | 7.8027 | 6.8391 | 5.8021 | 4.6769 | 2.9387 | -2.3629 | -11.2449 | -17.179 | -20.4106 | 17.2827 | 16.7128 | 16.0222 | 15.3283 | 14.599 | 13.8111 | 12.9526 | 11.987 | 10.7278 | 6.6924 | -0.72038 | -8.4272 | -18.757 | 12.0841 | 11.3935 | 10.5884 | 9.7449 | 8.877 | 7.9757 | 7.0047 | 5.9386 | 4.344 | -0.54371 | -8.4242 | -13.4411 | -16.1409
MANNINGTON GSP | MANNINGTON BSP | MANNINGTON | MINIMUM HEADROOM | SU 07592 05256 | YES | 11.4754 | 11.3627 | 11.1672 | 10.9262 | 10.7609 | 10.5566 | 10.2761 | 10.0733 | 9.8153 | 9.1941 | 8.3067 | 7.7053 | 7.405 | 12.0434 | 11.9642 | 11.7804 | 11.5939 | 11.4808 | 11.3285 | 11.1054 | 10.9691 | 10.8223 | 10.3828 | 9.8715 | 9.6279 | 9.4709 | 13.4015 | 13.3023 | 13.1333 | 12.9312 | 12.7901 | 12.6144 | 12.3704 | 12.1885 | 11.9566 | 11.4542 | 10.7863 | 10.355 | 10.1369
|  | MANNINGTON | CT |  |  | 11.4754 | 11.3627 | 11.1672 | 10.9262 | 10.7609 | 10.5566 | 10.2761 | 10.0733 | 9.8153 | 9.1941 | 8.3067 | 7.7053 | 7.405 | 12.0434 | 11.9642 | 11.7804 | 11.5939 | 11.4808 | 11.3285 | 11.1054 | 10.9691 | 10.8223 | 10.3828 | 9.8715 | 9.6279 | 9.4709 | 13.4015 | 13.3023 | 13.1333 | 12.9312 | 12.7901 | 12.6144 | 12.3704 | 12.1885 | 11.9566 | 11.4542 | 10.7863 | 10.355 | 10.1369
|  | MANNINGTON | LW |  |  | 11.4754 | 11.3627 | 11.1672 | 10.9262 | 10.7609 | 10.5566 | 10.2761 | 10.0733 | 9.8153 | 9.1941 | 8.3067 | 7.7053 | 7.405 | 12.0434 | 11.9642 | 11.7804 | 11.5939 | 11.4808 | 11.3285 | 11.1054 | 10.9691 | 10.8223 | 10.3828 | 9.8715 | 9.6279 | 9.4709 | 13.4015 | 13.3023 | 13.1333 | 12.9312 | 12.7901 | 12.6144 | 12.3704 | 12.1885 | 11.9566 | 11.4542 | 10.7863 | 10.355 | 10.1369
|  | MANNINGTON | ST |  |  | 11.4754 | 11.3627 | 11.1672 | 10.9262 | 10.7609 | 10.5566 | 10.2761 | 10.0733 | 9.8153 | 9.1941 | 8.3067 | 7.7053 | 7.405 | 12.0434 | 11.9642 | 11.7804 | 11.5939 | 11.4808 | 11.3285 | 11.1054 | 10.9691 | 10.8223 | 10.3828 | 9.8715 | 9.6279 | 9.4709 | 13.4015 | 13.3023 | 13.1333 | 12.9312 | 12.7901 | 12.6144 | 12.3704 | 12.1885 | 11.9566 | 11.4542 | 10.7863 | 10.355 | 10.1369
|  | MANNINGTON | FS |  |  | 11.4754 | 11.3627 | 11.1672 | 10.9262 | 10.7609 | 10.5566 | 10.2761 | 10.0733 | 9.8153 | 9.1941 | 8.3067 | 7.7053 | 7.405 | 12.0434 | 11.9642 | 11.7804 | 11.5939 | 11.4808 | 11.3285 | 11.1054 | 10.9691 | 10.8223 | 10.3828 | 9.8715 | 9.6279 | 9.4709 | 13.4015 | 13.3023 | 13.1333 | 12.9312 | 12.7901 | 12.6144 | 12.3704 | 12.1885 | 11.9566 | 11.4542 | 10.7863 | 10.355 | 10.1369
LOVEDEAN GSP | CHICHESTER & HUNSTON | MARKET | MINIMUM HEADROOM | SU 86479 04732 | YES | 20.7458 | 20.5993 | 20.4013 | 20.2115 | 20.0214 | 19.8194 | 19.2129 | 18.5067 | 17.4927 | 14.2377 | 8.9618 | 5.114 | 2.7968 | 20.6156 | 20.5067 | 20.3623 | 20.2171 | 20.067 | 19.9055 | 19.7272 | 19.5011 | 19.0433 | 17.2838 | 14.2634 | 11.8466 | 9.5941 | 23.0225 | 22.8078 | 22.5251 | 22.1003 | 21.5909 | 21.1127 | 20.5922 | 20.0035 | 19.1418 | 16.3858 | 11.7769 | 8.4558 | 6.5246
|  | MARKET | CT |  |  | 20.7458 | 20.5993 | 20.4013 | 20.2115 | 20.0214 | 19.8194 | 19.2129 | 18.5067 | 17.4927 | 14.2377 | 8.9618 | 5.114 | 2.7968 | 20.6156 | 20.5067 | 20.3623 | 20.2171 | 20.067 | 19.9055 | 19.7272 | 19.5011 | 19.0433 | 17.2838 | 14.2634 | 11.8466 | 9.5941 | 23.0225 | 22.8078 | 22.5251 | 22.1003 | 21.5909 | 21.1127 | 20.5922 | 20.0035 | 19.1418 | 16.3858 | 11.7769 | 8.4558 | 6.5246
|  | MARKET | LW |  |  | 20.7458 | 20.5993 | 20.4013 | 20.2115 | 20.0214 | 19.8194 | 19.2129 | 18.5067 | 17.4927 | 14.2377 | 8.9618 | 5.114 | 2.7968 | 20.6156 | 20.5067 | 20.3623 | 20.2171 | 20.067 | 19.9055 | 19.7272 | 19.5011 | 19.0433 | 17.2838 | 14.2634 | 11.8466 | 9.5941 | 23.0225 | 22.8078 | 22.5251 | 22.1003 | 21.5909 | 21.1127 | 20.5922 | 20.0035 | 19.1418 | 16.3858 | 11.7769 | 8.4558 | 6.5246
|  | MARKET | ST |  |  | 20.7458 | 20.5993 | 20.4013 | 20.2115 | 20.0214 | 19.8194 | 19.2129 | 18.5067 | 17.4927 | 14.2377 | 8.9618 | 5.114 | 2.7968 | 20.6156 | 20.5067 | 20.3623 | 20.2171 | 20.067 | 19.9055 | 19.7272 | 19.5011 | 19.0433 | 17.2838 | 14.2634 | 11.8466 | 9.5941 | 23.0225 | 22.8078 | 22.5251 | 22.1003 | 21.5909 | 21.1127 | 20.5922 | 20.0035 | 19.1418 | 16.3858 | 11.7769 | 8.4558 | 6.5246
|  | MARKET | FS |  |  | 20.7458 | 20.5993 | 20.4013 | 20.2115 | 20.0214 | 19.8194 | 19.2129 | 18.5067 | 17.4927 | 14.2377 | 8.9618 | 5.114 | 2.7968 | 20.6156 | 20.5067 | 20.3623 | 20.2171 | 20.067 | 19.9055 | 19.7272 | 19.5011 | 19.0433 | 17.2838 | 14.2634 | 11.8466 | 9.5941 | 23.0225 | 22.8078 | 22.5251 | 22.1003 | 21.5909 | 21.1127 | 20.5922 | 20.0035 | 19.1418 | 16.3858 | 11.7769 | 8.4558 | 6.5246
MELKSHAM GSP | WEST GRAFTON | MARLBOROUGH SOUTH | MINIMUM HEADROOM | SU 19293 68264 | YES | 6.3593 | 6.1298 | 5.8642 | 5.4812 | 5.0774 | 4.6527 | 4.1931 | 3.6715 | 2.8247 | 0.74889 | -2.5237 | -4.7166 | -5.6194 | 8.0808 | 7.9257 | 7.7429 | 7.5139 | 7.2696 | 7.0062 | 6.717 | 6.3804 | 5.8512 | 4.6061 | 2.803 | 1.3362 | 0.022805 | 7.9867 | 7.7951 | 7.5414 | 7.1858 | 6.8104 | 6.4137 | 5.9831 | 5.4905 | 4.6955 | 2.7775 | -0.15836 | -2.1115 | -2.9873
|  | MARLBOROUGH SOUTH | CT |  |  | 6.3593 | 6.1298 | 5.8642 | 5.4812 | 5.0774 | 4.6527 | 4.1931 | 3.6715 | 2.8247 | 0.74889 | -2.5237 | -4.7166 | -5.6194 | 8.0808 | 7.9257 | 7.7429 | 7.5139 | 7.2696 | 7.0062 | 6.717 | 6.3804 | 5.8512 | 4.6061 | 2.803 | 1.3362 | 0.022805 | 7.9867 | 7.7951 | 7.5414 | 7.1858 | 6.8104 | 6.4137 | 5.9831 | 5.4905 | 4.6955 | 2.7775 | -0.15836 | -2.1115 | -2.9873
|  | MARLBOROUGH SOUTH | LW |  |  | 6.3593 | 6.1298 | 5.8642 | 5.4812 | 5.0774 | 4.6527 | 4.1931 | 3.6715 | 2.8247 | 0.74889 | -2.5237 | -4.7166 | -5.6194 | 8.0808 | 7.9257 | 7.7429 | 7.5139 | 7.2696 | 7.0062 | 6.717 | 6.3804 | 5.8512 | 4.6061 | 2.803 | 1.3362 | 0.022805 | 7.9867 | 7.7951 | 7.5414 | 7.1858 | 6.8104 | 6.4137 | 5.9831 | 5.4905 | 4.6955 | 2.7775 | -0.15836 | -2.1115 | -2.9873
|  | MARLBOROUGH SOUTH | ST |  |  | 6.3593 | 6.1298 | 5.8642 | 5.4812 | 5.0774 | 4.6527 | 4.1931 | 3.6715 | 2.8247 | 0.74889 | -2.5237 | -4.7166 | -5.6194 | 8.0808 | 7.9257 | 7.7429 | 7.5139 | 7.2696 | 7.0062 | 6.717 | 6.3804 | 5.8512 | 4.6061 | 2.803 | 1.3362 | 0.022805 | 7.9867 | 7.7951 | 7.5414 | 7.1858 | 6.8104 | 6.4137 | 5.9831 | 5.4905 | 4.6955 | 2.7775 | -0.15836 | -2.1115 | -2.9873
|  | MARLBOROUGH SOUTH | FS |  |  | 6.3593 | 6.1298 | 5.8642 | 5.4812 | 5.0774 | 4.6527 | 4.1931 | 3.6715 | 2.8247 | 0.74889 | -2.5237 | -4.7166 | -5.6194 | 8.0808 | 7.9257 | 7.7429 | 7.5139 | 7.2696 | 7.0062 | 6.717 | 6.3804 | 5.8512 | 4.6061 | 2.803 | 1.3362 | 0.022805 | 7.9867 | 7.7951 | 7.5414 | 7.1858 | 6.8104 | 6.4137 | 5.9831 | 5.4905 | 4.6955 | 2.7775 | -0.15836 | -2.1115 | -2.9873
NURSLING GSP | ROWNHAMS | MAYBUSH | MINIMUM HEADROOM | SU 38426 14930 | YES | 12.4615 | 12.1263 | 11.742 | 11.1603 | 10.5613 | 9.8558 | 9.1895 | 8.4933 | 7.4423 | 4.0991 | -2.5073 | -7.5825 | -10.4828 | 12.271 | 11.9558 | 11.5936 | 11.1468 | 10.6848 | 10.1361 | 9.6044 | 9.0245 | 8.2642 | 5.7912 | 1.3486 | -3.3053 | -9.1036 | 14.6677 | 14.3327 | 13.9184 | 13.335 | 12.7325 | 12.0188 | 11.3394 | 10.6172 | 9.5763 | 6.2809 | 0.5151 | -3.7867 | -6.1781
|  | MAYBUSH | CT |  |  | 12.4615 | 12.1263 | 11.742 | 11.1603 | 10.5613 | 9.8558 | 9.1895 | 8.4933 | 7.4423 | 4.0991 | -2.5073 | -7.5825 | -10.4828 | 12.271 | 11.9558 | 11.5936 | 11.1468 | 10.6848 | 10.1361 | 9.6044 | 9.0245 | 8.2642 | 5.7912 | 1.3486 | -3.3053 | -9.1036 | 14.6677 | 14.3327 | 13.9184 | 13.335 | 12.7325 | 12.0188 | 11.3394 | 10.6172 | 9.5763 | 6.2809 | 0.5151 | -3.7867 | -6.1781
|  | MAYBUSH | LW |  |  | 12.4615 | 12.1263 | 11.742 | 11.1603 | 10.5613 | 9.8558 | 9.1895 | 8.4933 | 7.4423 | 4.0991 | -2.5073 | -7.5825 | -10.4828 | 12.271 | 11.9558 | 11.5936 | 11.1468 | 10.6848 | 10.1361 | 9.6044 | 9.0245 | 8.2642 | 5.7912 | 1.3486 | -3.3053 | -9.1036 | 14.6677 | 14.3327 | 13.9184 | 13.335 | 12.7325 | 12.0188 | 11.3394 | 10.6172 | 9.5763 | 6.2809 | 0.5151 | -3.7867 | -6.1781
|  | MAYBUSH | ST |  |  | 12.4615 | 12.1263 | 11.742 | 11.1603 | 10.5613 | 9.8558 | 9.1895 | 8.4933 | 7.4423 | 4.0991 | -2.5073 | -7.5825 | -10.4828 | 12.271 | 11.9558 | 11.5936 | 11.1468 | 10.6848 | 10.1361 | 9.6044 | 9.0245 | 8.2642 | 5.7912 | 1.3486 | -3.3053 | -9.1036 | 14.6677 | 14.3327 | 13.9184 | 13.335 | 12.7325 | 12.0188 | 11.3394 | 10.6172 | 9.5763 | 6.2809 | 0.5151 | -3.7867 | -6.1781
|  | MAYBUSH | FS |  |  | 12.4615 | 12.1263 | 11.742 | 11.1603 | 10.5613 | 9.8558 | 9.1895 | 8.4933 | 7.4423 | 4.0991 | -2.5073 | -7.5825 | -10.4828 | 12.271 | 11.9558 | 11.5936 | 11.1468 | 10.6848 | 10.1361 | 9.6044 | 9.0245 | 8.2642 | 5.7912 | 1.3486 | -3.3053 | -9.1036 | 14.6677 | 14.3327 | 13.9184 | 13.335 | 12.7325 | 12.0188 | 11.3394 | 10.6172 | 9.5763 | 6.2809 | 0.5151 | -3.7867 | -6.1781
MELKSHAM GSP | NORRINGTON | MELKSHAM TOWN | MINIMUM HEADROOM | ST 90170 64096 | YES | 2.9056 | 2.5674 | 2.2337 | 1.8115 | 1.3554 | 0.85841 | 0.31724 | -0.30633 | -1.4439 | -5.1936 | -12.024 | -16.471 | -18.4954 | 6.1243 | 5.7163 | 5.2233 | 4.6954 | 4.1085 | 3.431 | 2.6728 | 1.7439 | 0.38053 | -2.6509 | -6.4198 | -8.965 | -10.9951 | 3.0983 | 2.5203 | 1.8271 | 1.0255 | 0.16119 | -0.78729 | -1.8373 | -3.0925 | -5.0397 | -9.5573 | -15.7338 | -19.6128 | -21.2761
|  | MELKSHAM TOWN | CT |  |  | 2.9056 | 2.5674 | 2.2337 | 1.8115 | 1.3554 | 0.85841 | 0.31724 | -0.30633 | -1.4439 | -5.1936 | -12.024 | -16.471 | -18.4954 | 6.1243 | 5.7163 | 5.2233 | 4.6954 | 4.1085 | 3.431 | 2.6728 | 1.7439 | 0.38053 | -2.6509 | -6.4198 | -8.965 | -10.9951 | 3.0983 | 2.5203 | 1.8271 | 1.0255 | 0.16119 | -0.78729 | -1.8373 | -3.0925 | -5.0397 | -9.5573 | -15.7338 | -19.6128 | -21.2761
|  | MELKSHAM TOWN | LW |  |  | 2.9056 | 2.5674 | 2.2337 | 1.8115 | 1.3554 | 0.85841 | 0.31724 | -0.30633 | -1.4439 | -5.1936 | -12.024 | -16.471 | -18.4954 | 6.1243 | 5.7163 | 5.2233 | 4.6954 | 4.1085 | 3.431 | 2.6728 | 1.7439 | 0.38053 | -2.6509 | -6.4198 | -8.965 | -10.9951 | 3.0983 | 2.5203 | 1.8271 | 1.0255 | 0.16119 | -0.78729 | -1.8373 | -3.0925 | -5.0397 | -9.5573 | -15.7338 | -19.6128 | -21.2761
|  | MELKSHAM TOWN | ST |  |  | 2.9056 | 2.5674 | 2.2337 | 1.8115 | 1.3554 | 0.85841 | 0.31724 | -0.30633 | -1.4439 | -5.1936 | -12.024 | -16.471 | -18.4954 | 6.1243 | 5.7163 | 5.2233 | 4.6954 | 4.1085 | 3.431 | 2.6728 | 1.7439 | 0.38053 | -2.6509 | -6.4198 | -8.965 | -10.9951 | 3.0983 | 2.5203 | 1.8271 | 1.0255 | 0.16119 | -0.78729 | -1.8373 | -3.0925 | -5.0397 | -9.5573 | -15.7338 | -19.6128 | -21.2761
|  | MELKSHAM TOWN | FS |  |  | 2.9056 | 2.5674 | 2.2337 | 1.8115 | 1.3554 | 0.85841 | 0.31724 | -0.30633 | -1.4439 | -5.1936 | -12.024 | -16.471 | -18.4954 | 6.1243 | 5.7163 | 5.2233 | 4.6954 | 4.1085 | 3.431 | 2.6728 | 1.7439 | 0.38053 | -2.6509 | -6.4198 | -8.965 | -10.9951 | 3.0983 | 2.5203 | 1.8271 | 1.0255 | 0.16119 | -0.78729 | -1.8373 | -3.0925 | -5.0397 | -9.5573 | -15.7338 | -19.6128 | -21.2761
LOVEDEAN GSP | HAVANT | MEYRICK ROAD | MINIMUM HEADROOM | SU 70849 06469 | YES | 2.9031 | 2.3806 | 1.6093 | 0.49497 | -0.80591 | -2.0997 | -3.4079 | -4.9291 | -7.0993 | -12.9323 | -20.9522 | -26.932 | -30.5465 | 9.5454 | 9.1999 | 8.6864 | 8.0177 | 7.2483 | 6.4707 | 5.6737 | 4.7327 | 3.4101 | -0.13672 | -4.5792 | -7.9661 | -10.9241 | 5.0045 | 4.5327 | 3.8249 | 2.8328 | 1.6823 | 0.52529 | -0.65619 | -2.0426 | -4.032 | -9.3253 | -16.4231 | -21.5703 | -24.6269
|  | MEYRICK ROAD | CT |  |  | 2.9031 | 2.3806 | 1.6093 | 0.49497 | -0.80591 | -2.0997 | -3.4079 | -4.9291 | -7.0993 | -12.9323 | -20.9522 | -26.932 | -30.5465 | 9.5454 | 9.1999 | 8.6864 | 8.0177 | 7.2483 | 6.4707 | 5.6737 | 4.7327 | 3.4101 | -0.13672 | -4.5792 | -7.9661 | -10.9241 | 5.0045 | 4.5327 | 3.8249 | 2.8328 | 1.6823 | 0.52529 | -0.65619 | -2.0426 | -4.032 | -9.3253 | -16.4231 | -21.5703 | -24.6269
|  | MEYRICK ROAD | LW |  |  | 2.9031 | 2.3806 | 1.6093 | 0.49497 | -0.80591 | -2.0997 | -3.4079 | -4.9291 | -7.0993 | -12.9323 | -20.9522 | -26.932 | -30.5465 | 9.5454 | 9.1999 | 8.6864 | 8.0177 | 7.2483 | 6.4707 | 5.6737 | 4.7327 | 3.4101 | -0.13672 | -4.5792 | -7.9661 | -10.9241 | 5.0045 | 4.5327 | 3.8249 | 2.8328 | 1.6823 | 0.52529 | -0.65619 | -2.0426 | -4.032 | -9.3253 | -16.4231 | -21.5703 | -24.6269
|  | MEYRICK ROAD | ST |  |  | 2.9031 | 2.3806 | 1.6093 | 0.49497 | -0.80591 | -2.0997 | -3.4079 | -4.9291 | -7.0993 | -12.9323 | -20.9522 | -26.932 | -30.5465 | 9.5454 | 9.1999 | 8.6864 | 8.0177 | 7.2483 | 6.4707 | 5.6737 | 4.7327 | 3.4101 | -0.13672 | -4.5792 | -7.9661 | -10.9241 | 5.0045 | 4.5327 | 3.8249 | 2.8328 | 1.6823 | 0.52529 | -0.65619 | -2.0426 | -4.032 | -9.3253 | -16.4231 | -21.5703 | -24.6269
|  | MEYRICK ROAD | FS |  |  | 2.9031 | 2.3806 | 1.6093 | 0.49497 | -0.80591 | -2.0997 | -3.4079 | -4.9291 | -7.0993 | -12.9323 | -20.9522 | -26.932 | -30.5465 | 9.5454 | 9.1999 | 8.6864 | 8.0177 | 7.2483 | 6.4707 | 5.6737 | 4.7327 | 3.4101 | -0.13672 | -4.5792 | -7.9661 | -10.9241 | 5.0045 | 4.5327 | 3.8249 | 2.8328 | 1.6823 | 0.52529 | -0.65619 | -2.0426 | -4.032 | -9.3253 | -16.4231 | -21.5703 | -24.6269
BRAMLEY (ANDO-THAT) | ANDOVER BSP | MIDDLE WALLOP | MINIMUM HEADROOM | SU 30984 40155 | YES | 1.9763 | 1.8699 | 1.7539 | 1.5753 | 1.3963 | 1.2141 | 1.011 | 0.78157 | 0.44702 | -0.25426 | -1.3422 | -1.8085 | -1.9163 | 4.4691 | 4.4042 | 4.331 | 4.2351 | 4.1379 | 4.035 | 3.9163 | 3.7759 | 3.5794 | 3.2302 | 2.7246 | 2.4623 | 2.2952 | 2.6732 | 2.5715 | 2.4589 | 2.2958 | 2.132 | 1.9628 | 1.7712 | 1.5494 | 1.2287 | 0.61543 | -0.28717 | -0.67318 | -0.76461
|  | MIDDLE WALLOP | CT |  |  | 1.9763 | 1.8699 | 1.7539 | 1.5753 | 1.3963 | 1.2141 | 1.011 | 0.78157 | 0.44702 | -0.25426 | -1.3422 | -1.8085 | -1.9163 | 4.4691 | 4.4042 | 4.331 | 4.2351 | 4.1379 | 4.035 | 3.9163 | 3.7759 | 3.5794 | 3.2302 | 2.7246 | 2.4623 | 2.2952 | 2.6732 | 2.5715 | 2.4589 | 2.2958 | 2.132 | 1.9628 | 1.7712 | 1.5494 | 1.2287 | 0.61543 | -0.28717 | -0.67318 | -0.76461
|  | MIDDLE WALLOP | LW |  |  | 1.9763 | 1.8699 | 1.7539 | 1.5753 | 1.3963 | 1.2141 | 1.011 | 0.78157 | 0.44702 | -0.25426 | -1.3422 | -1.8085 | -1.9163 | 4.4691 | 4.4042 | 4.331 | 4.2351 | 4.1379 | 4.035 | 3.9163 | 3.7759 | 3.5794 | 3.2302 | 2.7246 | 2.4623 | 2.2952 | 2.6732 | 2.5715 | 2.4589 | 2.2958 | 2.132 | 1.9628 | 1.7712 | 1.5494 | 1.2287 | 0.61543 | -0.28717 | -0.67318 | -0.76461
|  | MIDDLE WALLOP | ST |  |  | 1.9763 | 1.8699 | 1.7539 | 1.5753 | 1.3963 | 1.2141 | 1.011 | 0.78157 | 0.44702 | -0.25426 | -1.3422 | -1.8085 | -1.9163 | 4.4691 | 4.4042 | 4.331 | 4.2351 | 4.1379 | 4.035 | 3.9163 | 3.7759 | 3.5794 | 3.2302 | 2.7246 | 2.4623 | 2.2952 | 2.6732 | 2.5715 | 2.4589 | 2.2958 | 2.132 | 1.9628 | 1.7712 | 1.5494 | 1.2287 | 0.61543 | -0.28717 | -0.67318 | -0.76461
|  | MIDDLE WALLOP | FS |  |  | 1.9763 | 1.8699 | 1.7539 | 1.5753 | 1.3963 | 1.2141 | 1.011 | 0.78157 | 0.44702 | -0.25426 | -1.3422 | -1.8085 | -1.9163 | 4.4691 | 4.4042 | 4.331 | 4.2351 | 4.1379 | 4.035 | 3.9163 | 3.7759 | 3.5794 | 3.2302 | 2.7246 | 2.4623 | 2.2952 | 2.6732 | 2.5715 | 2.4589 | 2.2958 | 2.132 | 1.9628 | 1.7712 | 1.5494 | 1.2287 | 0.61543 | -0.28717 | -0.67318 | -0.76461
BRAMLEY (FLEE) | FERNHURST | MIDHURST | MINIMUM HEADROOM | SU 88127 19555 | YES | 24.9107 | 24.6189 | 24.2354 | 23.7135 | 23.1688 | 22.5638 | 21.8637 | 21.1206 | 20.0239 | 17.5538 | 13.7655 | 11.0549 | 9.8747 | 24.0705 | 23.8734 | 23.6008 | 23.2805 | 22.941 | 22.5624 | 22.1071 | 21.6134 | 20.919 | 19.498 | 17.6032 | 16.3196 | 15.4149 | 26.7277 | 26.4576 | 26.0931 | 25.6228 | 25.1295 | 24.5809 | 23.9356 | 23.2454 | 22.2387 | 20.0728 | 16.7716 | 14.5409 | 13.5782
|  | MIDHURST | CT |  |  | 24.9107 | 24.6189 | 24.2354 | 23.7135 | 23.1688 | 22.5638 | 21.8637 | 21.1206 | 20.0239 | 17.5538 | 13.7655 | 11.0549 | 9.8747 | 24.0705 | 23.8734 | 23.6008 | 23.2805 | 22.941 | 22.5624 | 22.1071 | 21.6134 | 20.919 | 19.498 | 17.6032 | 16.3196 | 15.4149 | 26.7277 | 26.4576 | 26.0931 | 25.6228 | 25.1295 | 24.5809 | 23.9356 | 23.2454 | 22.2387 | 20.0728 | 16.7716 | 14.5409 | 13.5782
|  | MIDHURST | LW |  |  | 24.9107 | 24.6189 | 24.2354 | 23.7135 | 23.1688 | 22.5638 | 21.8637 | 21.1206 | 20.0239 | 17.5538 | 13.7655 | 11.0549 | 9.8747 | 24.0705 | 23.8734 | 23.6008 | 23.2805 | 22.941 | 22.5624 | 22.1071 | 21.6134 | 20.919 | 19.498 | 17.6032 | 16.3196 | 15.4149 | 26.7277 | 26.4576 | 26.0931 | 25.6228 | 25.1295 | 24.5809 | 23.9356 | 23.2454 | 22.2387 | 20.0728 | 16.7716 | 14.5409 | 13.5782
|  | MIDHURST | ST |  |  | 24.9107 | 24.6189 | 24.2354 | 23.7135 | 23.1688 | 22.5638 | 21.8637 | 21.1206 | 20.0239 | 17.5538 | 13.7655 | 11.0549 | 9.8747 | 24.0705 | 23.8734 | 23.6008 | 23.2805 | 22.941 | 22.5624 | 22.1071 | 21.6134 | 20.919 | 19.498 | 17.6032 | 16.3196 | 15.4149 | 26.7277 | 26.4576 | 26.0931 | 25.6228 | 25.1295 | 24.5809 | 23.9356 | 23.2454 | 22.2387 | 20.0728 | 16.7716 | 14.5409 | 13.5782
|  | MIDHURST | FS |  |  | 24.9107 | 24.6189 | 24.2354 | 23.7135 | 23.1688 | 22.5638 | 21.8637 | 21.1206 | 20.0239 | 17.5538 | 13.7655 | 11.0549 | 9.8747 | 24.0705 | 23.8734 | 23.6008 | 23.2805 | 22.941 | 22.5624 | 22.1071 | 21.6134 | 20.919 | 19.498 | 17.6032 | 16.3196 | 15.4149 | 26.7277 | 26.4576 | 26.0931 | 25.6228 | 25.1295 | 24.5809 | 23.9356 | 23.2454 | 22.2387 | 20.0728 | 16.7716 | 14.5409 | 13.5782
AXMINSTER | YEOVIL BSP | MILBORNE PORT | MINIMUM HEADROOM | ST 67929 19741 | YES | 0.025484 | -0.060208 | -0.17958 | -0.34012 | -0.51259 | -0.69359 | -0.8916 | -1.1274 | -1.4969 | -2.3187 | -3.6452 | -4.6798 | -5.1194 | 1.3553 | 1.2993 | 1.215 | 1.1216 | 1.0186 | 0.90934 | 0.78697 | 0.63244 | 0.4049 | -0.036456 | -0.58408 | -0.98369 | -1.2373 | 0.58474 | 0.5038 | 0.38931 | 0.2397 | 0.078362 | -0.09118 | -0.27732 | -0.50117 | -0.84932 | -1.6069 | -2.766 | -3.6729 | -4.0561
|  | MILBORNE PORT | CT |  |  | 0.025484 | -0.060208 | -0.17958 | -0.34012 | -0.51259 | -0.69359 | -0.8916 | -1.1274 | -1.4969 | -2.3187 | -3.6452 | -4.6798 | -5.1194 | 1.3553 | 1.2993 | 1.215 | 1.1216 | 1.0186 | 0.90934 | 0.78697 | 0.63244 | 0.4049 | -0.036456 | -0.58408 | -0.98369 | -1.2373 | 0.58474 | 0.5038 | 0.38931 | 0.2397 | 0.078362 | -0.09118 | -0.27732 | -0.50117 | -0.84932 | -1.6069 | -2.766 | -3.6729 | -4.0561
|  | MILBORNE PORT | LW |  |  | 0.025484 | -0.060208 | -0.17958 | -0.34012 | -0.51259 | -0.69359 | -0.8916 | -1.1274 | -1.4969 | -2.3187 | -3.6452 | -4.6798 | -5.1194 | 1.3553 | 1.2993 | 1.215 | 1.1216 | 1.0186 | 0.90934 | 0.78697 | 0.63244 | 0.4049 | -0.036456 | -0.58408 | -0.98369 | -1.2373 | 0.58474 | 0.5038 | 0.38931 | 0.2397 | 0.078362 | -0.09118 | -0.27732 | -0.50117 | -0.84932 | -1.6069 | -2.766 | -3.6729 | -4.0561
|  | MILBORNE PORT | ST |  |  | 0.025484 | -0.060208 | -0.17958 | -0.34012 | -0.51259 | -0.69359 | -0.8916 | -1.1274 | -1.4969 | -2.3187 | -3.6452 | -4.6798 | -5.1194 | 1.3553 | 1.2993 | 1.215 | 1.1216 | 1.0186 | 0.90934 | 0.78697 | 0.63244 | 0.4049 | -0.036456 | -0.58408 | -0.98369 | -1.2373 | 0.58474 | 0.5038 | 0.38931 | 0.2397 | 0.078362 | -0.09118 | -0.27732 | -0.50117 | -0.84932 | -1.6069 | -2.766 | -3.6729 | -4.0561
|  | MILBORNE PORT | FS |  |  | 0.025484 | -0.060208 | -0.17958 | -0.34012 | -0.51259 | -0.69359 | -0.8916 | -1.1274 | -1.4969 | -2.3187 | -3.6452 | -4.6798 | -5.1194 | 1.3553 | 1.2993 | 1.215 | 1.1216 | 1.0186 | 0.90934 | 0.78697 | 0.63244 | 0.4049 | -0.036456 | -0.58408 | -0.98369 | -1.2373 | 0.58474 | 0.5038 | 0.38931 | 0.2397 | 0.078362 | -0.09118 | -0.27732 | -0.50117 | -0.84932 | -1.6069 | -2.766 | -3.6729 | -4.0561
BRAMLEY (FLEE) | ALDERSHOT BSP | MILFORD | MINIMUM HEADROOM | SU 94719 43018 | YES | 18.6028 | 18.1105 | 17.5451 | 16.9856 | 16.4513 | 15.8639 | 15.1914 | 14.425 | 13.234 | 10.6793 | 6.4414 | 3.3899 | 2.012 | 21.8541 | 21.5311 | 21.151 | 20.8065 | 20.4662 | 20.0802 | 19.6274 | 19.0914 | 18.3354 | 16.9426 | 15.0486 | 13.7318 | 12.7901 | 20.1282 | 19.6883 | 19.1761 | 18.6584 | 18.1565 | 17.6032 | 16.9678 | 16.2389 | 15.1149 | 12.7581 | 8.9585 | 6.2023 | 4.9048
|  | MILFORD | CT |  |  | 18.6028 | 18.1105 | 17.5451 | 16.9856 | 16.4513 | 15.8639 | 15.1914 | 14.425 | 13.234 | 10.6793 | 6.4414 | 3.3899 | 2.012 | 21.8541 | 21.5311 | 21.151 | 20.8065 | 20.4662 | 20.0802 | 19.6274 | 19.0914 | 18.3354 | 16.9426 | 15.0486 | 13.7318 | 12.7901 | 20.1282 | 19.6883 | 19.1761 | 18.6584 | 18.1565 | 17.6032 | 16.9678 | 16.2389 | 15.1149 | 12.7581 | 8.9585 | 6.2023 | 4.9048
|  | MILFORD | LW |  |  | 18.6028 | 18.1105 | 17.5451 | 16.9856 | 16.4513 | 15.8639 | 15.1914 | 14.425 | 13.234 | 10.6793 | 6.4414 | 3.3899 | 2.012 | 21.8541 | 21.5311 | 21.151 | 20.8065 | 20.4662 | 20.0802 | 19.6274 | 19.0914 | 18.3354 | 16.9426 | 15.0486 | 13.7318 | 12.7901 | 20.1282 | 19.6883 | 19.1761 | 18.6584 | 18.1565 | 17.6032 | 16.9678 | 16.2389 | 15.1149 | 12.7581 | 8.9585 | 6.2023 | 4.9048
|  | MILFORD | ST |  |  | 18.6028 | 18.1105 | 17.5451 | 16.9856 | 16.4513 | 15.8639 | 15.1914 | 14.425 | 13.234 | 10.6793 | 6.4414 | 3.3899 | 2.012 | 21.8541 | 21.5311 | 21.151 | 20.8065 | 20.4662 | 20.0802 | 19.6274 | 19.0914 | 18.3354 | 16.9426 | 15.0486 | 13.7318 | 12.7901 | 20.1282 | 19.6883 | 19.1761 | 18.6584 | 18.1565 | 17.6032 | 16.9678 | 16.2389 | 15.1149 | 12.7581 | 8.9585 | 6.2023 | 4.9048
|  | MILFORD | FS |  |  | 18.6028 | 18.1105 | 17.5451 | 16.9856 | 16.4513 | 15.8639 | 15.1914 | 14.425 | 13.234 | 10.6793 | 6.4414 | 3.3899 | 2.012 | 21.8541 | 21.5311 | 21.151 | 20.8065 | 20.4662 | 20.0802 | 19.6274 | 19.0914 | 18.3354 | 16.9426 | 15.0486 | 13.7318 | 12.7901 | 20.1282 | 19.6883 | 19.1761 | 18.6584 | 18.1565 | 17.6032 | 16.9678 | 16.2389 | 15.1149 | 12.7581 | 8.9585 | 6.2023 | 4.9048
MANNINGTON GSP | ARNEWOOD | MILFORD-ON-SEA | MINIMUM HEADROOM | SZ 28252 93347 | YES | 6.5856 | 6.3475 | 5.8998 | 5.1717 | 4.4557 | 3.7208 | 3.0139 | 2.1949 | 1.0073 | -1.7942 | -5.5894 | -8.2319 | -9.4128 | 9.8039 | 9.6232 | 9.293 | 8.855 | 8.4121 | 7.9478 | 7.4807 | 6.925 | 6.159 | 4.4611 | 2.6036 | 1.3011 | 0.30093 | 7.994 | 7.7805 | 7.3929 | 6.7661 | 6.1449 | 5.5029 | 4.8789 | 4.1571 | 3.0764 | 0.46283 | -2.9988 | -5.4826 | -6.591
|  | MILFORD-ON-SEA | CT |  |  | 6.5856 | 6.3475 | 5.8998 | 5.1717 | 4.4557 | 3.7208 | 3.0139 | 2.1949 | 1.0073 | -1.7942 | -5.5894 | -8.2319 | -9.4128 | 9.8039 | 9.6232 | 9.293 | 8.855 | 8.4121 | 7.9478 | 7.4807 | 6.925 | 6.159 | 4.4611 | 2.6036 | 1.3011 | 0.30093 | 7.994 | 7.7805 | 7.3929 | 6.7661 | 6.1449 | 5.5029 | 4.8789 | 4.1571 | 3.0764 | 0.46283 | -2.9988 | -5.4826 | -6.591
|  | MILFORD-ON-SEA | LW |  |  | 6.5856 | 6.3475 | 5.8998 | 5.1717 | 4.4557 | 3.7208 | 3.0139 | 2.1949 | 1.0073 | -1.7942 | -5.5894 | -8.2319 | -9.4128 | 9.8039 | 9.6232 | 9.293 | 8.855 | 8.4121 | 7.9478 | 7.4807 | 6.925 | 6.159 | 4.4611 | 2.6036 | 1.3011 | 0.30093 | 7.994 | 7.7805 | 7.3929 | 6.7661 | 6.1449 | 5.5029 | 4.8789 | 4.1571 | 3.0764 | 0.46283 | -2.9988 | -5.4826 | -6.591
|  | MILFORD-ON-SEA | ST |  |  | 6.5856 | 6.3475 | 5.8998 | 5.1717 | 4.4557 | 3.7208 | 3.0139 | 2.1949 | 1.0073 | -1.7942 | -5.5894 | -8.2319 | -9.4128 | 9.8039 | 9.6232 | 9.293 | 8.855 | 8.4121 | 7.9478 | 7.4807 | 6.925 | 6.159 | 4.4611 | 2.6036 | 1.3011 | 0.30093 | 7.994 | 7.7805 | 7.3929 | 6.7661 | 6.1449 | 5.5029 | 4.8789 | 4.1571 | 3.0764 | 0.46283 | -2.9988 | -5.4826 | -6.591
|  | MILFORD-ON-SEA | FS |  |  | 6.5856 | 6.3475 | 5.8998 | 5.1717 | 4.4557 | 3.7208 | 3.0139 | 2.1949 | 1.0073 | -1.7942 | -5.5894 | -8.2319 | -9.4128 | 9.8039 | 9.6232 | 9.293 | 8.855 | 8.4121 | 7.9478 | 7.4807 | 6.925 | 6.159 | 4.4611 | 2.6036 | 1.3011 | 0.30093 | 7.994 | 7.7805 | 7.3929 | 6.7661 | 6.1449 | 5.5029 | 4.8789 | 4.1571 | 3.0764 | 0.46283 | -2.9988 | -5.4826 | -6.591
MANNINGTON GSP | MANNINGTON BSP | MILL LANE | MINIMUM HEADROOM | SU 14691 05633 | YES | 17.4242 | 16.9166 | 16.3807 | 15.573 | 14.6 | 13.4046 | 12.0074 | 10.4419 | 8.314 | 2.7366 | -5.0858 | -9.9108 | -12.1232 | 21.0039 | 20.7019 | 20.4499 | 20.1187 | 19.7744 | 19.1033 | 18.1801 | 17.0531 | 15.647 | 12.1797 | 7.757 | 4.9875 | 2.7374 | 22.8507 | 22.3692 | 21.8562 | 21.1016 | 20.23 | 19.1712 | 17.8604 | 16.37 | 14.3685 | 9.3118 | 2.3848 | -1.9193 | -3.8722
|  | MILL LANE | CT |  |  | 17.4242 | 16.9166 | 16.3807 | 15.573 | 14.6 | 13.4046 | 12.0074 | 10.4419 | 8.314 | 2.7366 | -5.0858 | -9.9108 | -12.1232 | 21.0039 | 20.7019 | 20.4499 | 20.1187 | 19.7744 | 19.1033 | 18.1801 | 17.0531 | 15.647 | 12.1797 | 7.757 | 4.9875 | 2.7374 | 22.8507 | 22.3692 | 21.8562 | 21.1016 | 20.23 | 19.1712 | 17.8604 | 16.37 | 14.3685 | 9.3118 | 2.3848 | -1.9193 | -3.8722
|  | MILL LANE | LW |  |  | 17.4242 | 16.9166 | 16.3807 | 15.573 | 14.6 | 13.4046 | 12.0074 | 10.4419 | 8.314 | 2.7366 | -5.0858 | -9.9108 | -12.1232 | 21.0039 | 20.7019 | 20.4499 | 20.1187 | 19.7744 | 19.1033 | 18.1801 | 17.0531 | 15.647 | 12.1797 | 7.757 | 4.9875 | 2.7374 | 22.8507 | 22.3692 | 21.8562 | 21.1016 | 20.23 | 19.1712 | 17.8604 | 16.37 | 14.3685 | 9.3118 | 2.3848 | -1.9193 | -3.8722
|  | MILL LANE | ST |  |  | 17.4242 | 16.9166 | 16.3807 | 15.573 | 14.6 | 13.4046 | 12.0074 | 10.4419 | 8.314 | 2.7366 | -5.0858 | -9.9108 | -12.1232 | 21.0039 | 20.7019 | 20.4499 | 20.1187 | 19.7744 | 19.1033 | 18.1801 | 17.0531 | 15.647 | 12.1797 | 7.757 | 4.9875 | 2.7374 | 22.8507 | 22.3692 | 21.8562 | 21.1016 | 20.23 | 19.1712 | 17.8604 | 16.37 | 14.3685 | 9.3118 | 2.3848 | -1.9193 | -3.8722
|  | MILL LANE | FS |  |  | 17.4242 | 16.9166 | 16.3807 | 15.573 | 14.6 | 13.4046 | 12.0074 | 10.4419 | 8.314 | 2.7366 | -5.0858 | -9.9108 | -12.1232 | 21.0039 | 20.7019 | 20.4499 | 20.1187 | 19.7744 | 19.1033 | 18.1801 | 17.0531 | 15.647 | 12.1797 | 7.757 | 4.9875 | 2.7374 | 22.8507 | 22.3692 | 21.8562 | 21.1016 | 20.23 | 19.1712 | 17.8604 | 16.37 | 14.3685 | 9.3118 | 2.3848 | -1.9193 | -3.8722
COWLEY GSP | DRAYTON BSP | MILTON | MINIMUM HEADROOM | SU 49992 92060 | NO | 7.9479 | 2.0142 | -4.2292 | -6.7448 | -9.655 | -12.6639 | -15.8316 | -19.2116 | -22.8476 | -30.028 | -37.3762 | -41.4989 | -43.3359 | 9.8614 | 3.3711 | -3.2334 | -4.9148 | -6.7745 | -8.6641 | -10.5516 | -12.518 | -14.6099 | -18.9922 | -23.1641 | -25.376 | -26.8748 | 8.9698 | 2.2252 | -4.7704 | -6.9798 | -9.5 | -12.1101 | -14.8494 | -17.78 | -20.9833 | -27.4066 | -34.0053 | -37.6343 | -39.2419
|  | MILTON | CT |  |  | 7.9479 | 2.0142 | -4.2292 | -6.7448 | -9.655 | -12.6639 | -15.8316 | -19.2116 | -22.8476 | -30.028 | -37.3762 | -41.4989 | -43.3359 | 9.8614 | 3.3711 | -3.2334 | -4.9148 | -6.7745 | -8.6641 | -10.5516 | -12.518 | -14.6099 | -18.9922 | -23.1641 | -25.376 | -26.8748 | 8.9698 | 2.2252 | -4.7704 | -6.9798 | -9.5 | -12.1101 | -14.8494 | -17.78 | -20.9833 | -27.4066 | -34.0053 | -37.6343 | -39.2419
|  | MILTON | LW |  |  | 7.9479 | 2.0142 | -4.2292 | -6.7448 | -9.655 | -12.6639 | -15.8316 | -19.2116 | -22.8476 | -30.028 | -37.3762 | -41.4989 | -43.3359 | 9.8614 | 3.3711 | -3.2334 | -4.9148 | -6.7745 | -8.6641 | -10.5516 | -12.518 | -14.6099 | -18.9922 | -23.1641 | -25.376 | -26.8748 | 8.9698 | 2.2252 | -4.7704 | -6.9798 | -9.5 | -12.1101 | -14.8494 | -17.78 | -20.9833 | -27.4066 | -34.0053 | -37.6343 | -39.2419
|  | MILTON | ST |  |  | 7.9479 | 2.0142 | -4.2292 | -6.7448 | -9.655 | -12.6639 | -15.8316 | -19.2116 | -22.8476 | -30.028 | -37.3762 | -41.4989 | -43.3359 | 9.8614 | 3.3711 | -3.2334 | -4.9148 | -6.7745 | -8.6641 | -10.5516 | -12.518 | -14.6099 | -18.9922 | -23.1641 | -25.376 | -26.8748 | 8.9698 | 2.2252 | -4.7704 | -6.9798 | -9.5 | -12.1101 | -14.8494 | -17.78 | -20.9833 | -27.4066 | -34.0053 | -37.6343 | -39.2419
|  | MILTON | FS |  |  | 7.9479 | 2.0142 | -4.2292 | -6.7448 | -9.655 | -12.6639 | -15.8316 | -19.2116 | -22.8476 | -30.028 | -37.3762 | -41.4989 | -43.3359 | 9.8614 | 3.3711 | -3.2334 | -4.9148 | -6.7745 | -8.6641 | -10.5516 | -12.518 | -14.6099 | -18.9922 | -23.1641 | -25.376 | -26.8748 | 8.9698 | 2.2252 | -4.7704 | -6.9798 | -9.5 | -12.1101 | -14.8494 | -17.78 | -20.9833 | -27.4066 | -34.0053 | -37.6343 | -39.2419
MANNINGTON GSP | SHAFTESBURY BSP | MINCHINGTON | MINIMUM HEADROOM | ST 96164 14520 | YES | 2.2049 | 2.1362 | 2.0482 | 1.9312 | 1.8096 | 1.6707 | 1.5151 | 1.3407 | 1.1067 | 0.67898 | 0.057118 | -0.33742 | -0.50281 | 3.339 | 3.2958 | 3.2367 | 3.1689 | 3.0975 | 3.0162 | 2.9224 | 2.813 | 2.6675 | 2.4408 | 2.1509 | 1.9636 | 1.8452 | 2.7673 | 2.7047 | 2.6253 | 2.5181 | 2.4068 | 2.2797 | 2.1378 | 1.9796 | 1.7675 | 1.3698 | 0.78168 | 0.40942 | 0.25386
|  | MINCHINGTON | CT |  |  | 2.2049 | 2.1362 | 2.0482 | 1.9312 | 1.8096 | 1.6707 | 1.5151 | 1.3407 | 1.1067 | 0.67898 | 0.057118 | -0.33742 | -0.50281 | 3.339 | 3.2958 | 3.2367 | 3.1689 | 3.0975 | 3.0162 | 2.9224 | 2.813 | 2.6675 | 2.4408 | 2.1509 | 1.9636 | 1.8452 | 2.7673 | 2.7047 | 2.6253 | 2.5181 | 2.4068 | 2.2797 | 2.1378 | 1.9796 | 1.7675 | 1.3698 | 0.78168 | 0.40942 | 0.25386
|  | MINCHINGTON | LW |  |  | 2.2049 | 2.1362 | 2.0482 | 1.9312 | 1.8096 | 1.6707 | 1.5151 | 1.3407 | 1.1067 | 0.67898 | 0.057118 | -0.33742 | -0.50281 | 3.339 | 3.2958 | 3.2367 | 3.1689 | 3.0975 | 3.0162 | 2.9224 | 2.813 | 2.6675 | 2.4408 | 2.1509 | 1.9636 | 1.8452 | 2.7673 | 2.7047 | 2.6253 | 2.5181 | 2.4068 | 2.2797 | 2.1378 | 1.9796 | 1.7675 | 1.3698 | 0.78168 | 0.40942 | 0.25386
|  | MINCHINGTON | ST |  |  | 2.2049 | 2.1362 | 2.0482 | 1.9312 | 1.8096 | 1.6707 | 1.5151 | 1.3407 | 1.1067 | 0.67898 | 0.057118 | -0.33742 | -0.50281 | 3.339 | 3.2958 | 3.2367 | 3.1689 | 3.0975 | 3.0162 | 2.9224 | 2.813 | 2.6675 | 2.4408 | 2.1509 | 1.9636 | 1.8452 | 2.7673 | 2.7047 | 2.6253 | 2.5181 | 2.4068 | 2.2797 | 2.1378 | 1.9796 | 1.7675 | 1.3698 | 0.78168 | 0.40942 | 0.25386
|  | MINCHINGTON | FS |  |  | 2.2049 | 2.1362 | 2.0482 | 1.9312 | 1.8096 | 1.6707 | 1.5151 | 1.3407 | 1.1067 | 0.67898 | 0.057118 | -0.33742 | -0.50281 | 3.339 | 3.2958 | 3.2367 | 3.1689 | 3.0975 | 3.0162 | 2.9224 | 2.813 | 2.6675 | 2.4408 | 2.1509 | 1.9636 | 1.8452 | 2.7673 | 2.7047 | 2.6253 | 2.5181 | 2.4068 | 2.2797 | 2.1378 | 1.9796 | 1.7675 | 1.3698 | 0.78168 | 0.40942 | 0.25386
MINETY GSP | CIRENCESTER BSP | MINETY VILLAGE | MINIMUM HEADROOM | SU 01647 91932 | YES | 13.7856 | 13.4269 | 12.9689 | 12.3735 | 11.705 | 11.0092 | 10.1956 | 9.3013 | 8.2961 | 5.7194 | 3.6661 | 3.0351 | 2.867 | 15.0698 | 14.8382 | 14.5675 | 14.2427 | 13.8846 | 13.5062 | 13.0628 | 12.5805 | 12.0437 | 10.7407 | 9.6894 | 9.3437 | 9.1362 | 14.6898 | 14.519 | 14.1559 | 13.6482 | 13.081 | 12.4866 | 11.7891 | 11.0254 | 10.1609 | 8.005 | 6.2566 | 5.7348 | 5.5898
|  | MINETY VILLAGE | CT |  |  | 13.7856 | 13.4269 | 12.9689 | 12.3735 | 11.705 | 11.0092 | 10.1956 | 9.3013 | 8.2961 | 5.7194 | 3.6661 | 3.0351 | 2.867 | 15.0698 | 14.8382 | 14.5675 | 14.2427 | 13.8846 | 13.5062 | 13.0628 | 12.5805 | 12.0437 | 10.7407 | 9.6894 | 9.3437 | 9.1362 | 14.6898 | 14.519 | 14.1559 | 13.6482 | 13.081 | 12.4866 | 11.7891 | 11.0254 | 10.1609 | 8.005 | 6.2566 | 5.7348 | 5.5898
|  | MINETY VILLAGE | LW |  |  | 13.7856 | 13.4269 | 12.9689 | 12.3735 | 11.705 | 11.0092 | 10.1956 | 9.3013 | 8.2961 | 5.7194 | 3.6661 | 3.0351 | 2.867 | 15.0698 | 14.8382 | 14.5675 | 14.2427 | 13.8846 | 13.5062 | 13.0628 | 12.5805 | 12.0437 | 10.7407 | 9.6894 | 9.3437 | 9.1362 | 14.6898 | 14.519 | 14.1559 | 13.6482 | 13.081 | 12.4866 | 11.7891 | 11.0254 | 10.1609 | 8.005 | 6.2566 | 5.7348 | 5.5898
|  | MINETY VILLAGE | ST |  |  | 13.7856 | 13.4269 | 12.9689 | 12.3735 | 11.705 | 11.0092 | 10.1956 | 9.3013 | 8.2961 | 5.7194 | 3.6661 | 3.0351 | 2.867 | 15.0698 | 14.8382 | 14.5675 | 14.2427 | 13.8846 | 13.5062 | 13.0628 | 12.5805 | 12.0437 | 10.7407 | 9.6894 | 9.3437 | 9.1362 | 14.6898 | 14.519 | 14.1559 | 13.6482 | 13.081 | 12.4866 | 11.7891 | 11.0254 | 10.1609 | 8.005 | 6.2566 | 5.7348 | 5.5898
|  | MINETY VILLAGE | FS |  |  | 13.7856 | 13.4269 | 12.9689 | 12.3735 | 11.705 | 11.0092 | 10.1956 | 9.3013 | 8.2961 | 5.7194 | 3.6661 | 3.0351 | 2.867 | 15.0698 | 14.8382 | 14.5675 | 14.2427 | 13.8846 | 13.5062 | 13.0628 | 12.5805 | 12.0437 | 10.7407 | 9.6894 | 9.3437 | 9.1362 | 14.6898 | 14.519 | 14.1559 | 13.6482 | 13.081 | 12.4866 | 11.7891 | 11.0254 | 10.1609 | 8.005 | 6.2566 | 5.7348 | 5.5898
BRAMLEY (FLEE) | BURGHFIELD RESERVE | MORTIMER | MINIMUM HEADROOM | SU 62236 64103 | YES | 9.4502 | 9.0557 | 8.7355 | 8.3058 | 7.8547 | 7.371 | 6.8246 | 6.2177 | 5.3122 | 3.42 | 0.15123 | -2.1446 | -2.9548 | 10.4176 | 10.1297 | 9.8902 | 9.6195 | 9.3392 | 9.0355 | 8.6873 | 8.2798 | 7.6971 | 6.6148 | 4.9909 | 3.7262 | 2.7985 | 11.2991 | 10.9236 | 10.6 | 10.1918 | 9.7678 | 9.3133 | 8.797 | 8.2196 | 7.3653 | 5.6275 | 2.7988 | 0.78728 | 0.077386
|  | MORTIMER | CT |  |  | 9.4502 | 9.0557 | 8.7355 | 8.3058 | 7.8547 | 7.371 | 6.8246 | 6.2177 | 5.3122 | 3.42 | 0.15123 | -2.1446 | -2.9548 | 10.4176 | 10.1297 | 9.8902 | 9.6195 | 9.3392 | 9.0355 | 8.6873 | 8.2798 | 7.6971 | 6.6148 | 4.9909 | 3.7262 | 2.7985 | 11.2991 | 10.9236 | 10.6 | 10.1918 | 9.7678 | 9.3133 | 8.797 | 8.2196 | 7.3653 | 5.6275 | 2.7988 | 0.78728 | 0.077386
|  | MORTIMER | LW |  |  | 9.4502 | 9.0557 | 8.7355 | 8.3058 | 7.8547 | 7.371 | 6.8246 | 6.2177 | 5.3122 | 3.42 | 0.15123 | -2.1446 | -2.9548 | 10.4176 | 10.1297 | 9.8902 | 9.6195 | 9.3392 | 9.0355 | 8.6873 | 8.2798 | 7.6971 | 6.6148 | 4.9909 | 3.7262 | 2.7985 | 11.2991 | 10.9236 | 10.6 | 10.1918 | 9.7678 | 9.3133 | 8.797 | 8.2196 | 7.3653 | 5.6275 | 2.7988 | 0.78728 | 0.077386
|  | MORTIMER | ST |  |  | 9.4502 | 9.0557 | 8.7355 | 8.3058 | 7.8547 | 7.371 | 6.8246 | 6.2177 | 5.3122 | 3.42 | 0.15123 | -2.1446 | -2.9548 | 10.4176 | 10.1297 | 9.8902 | 9.6195 | 9.3392 | 9.0355 | 8.6873 | 8.2798 | 7.6971 | 6.6148 | 4.9909 | 3.7262 | 2.7985 | 11.2991 | 10.9236 | 10.6 | 10.1918 | 9.7678 | 9.3133 | 8.797 | 8.2196 | 7.3653 | 5.6275 | 2.7988 | 0.78728 | 0.077386
|  | MORTIMER | FS |  |  | 9.4502 | 9.0557 | 8.7355 | 8.3058 | 7.8547 | 7.371 | 6.8246 | 6.2177 | 5.3122 | 3.42 | 0.15123 | -2.1446 | -2.9548 | 10.4176 | 10.1297 | 9.8902 | 9.6195 | 9.3392 | 9.0355 | 8.6873 | 8.2798 | 7.6971 | 6.6148 | 4.9909 | 3.7262 | 2.7985 | 11.2991 | 10.9236 | 10.6 | 10.1918 | 9.7678 | 9.3133 | 8.797 | 8.2196 | 7.3653 | 5.6275 | 2.7988 | 0.78728 | 0.077386
MANNINGTON GSP | SALISBURY | NETHERHAMPTON | MINIMUM HEADROOM | SU 12478 29102 | YES | 8.867 | 8.729 | 8.5207 | 8.2365 | 7.8804 | 7.5015 | 7.0151 | 6.4391 | 5.756 | 4.3951 | 2.8398 | 1.7632 | 1.2551 | 9.5742 | 9.5394 | 9.4901 | 9.4318 | 9.3353 | 9.0956 | 8.7972 | 8.4449 | 8.0203 | 7.1165 | 6.0523 | 5.0467 | 3.8979 | 9.2762 | 9.1597 | 8.9844 | 8.7416 | 8.4395 | 8.1174 | 7.706 | 7.2184 | 6.6269 | 5.4187 | 3.9809 | 2.9752 | 2.503
|  | NETHERHAMPTON | CT |  |  | 8.867 | 8.729 | 8.5207 | 8.2365 | 7.8804 | 7.5015 | 7.0151 | 6.4391 | 5.756 | 4.3951 | 2.8398 | 1.7632 | 1.2551 | 9.5742 | 9.5394 | 9.4901 | 9.4318 | 9.3353 | 9.0956 | 8.7972 | 8.4449 | 8.0203 | 7.1165 | 6.0523 | 5.0467 | 3.8979 | 9.2762 | 9.1597 | 8.9844 | 8.7416 | 8.4395 | 8.1174 | 7.706 | 7.2184 | 6.6269 | 5.4187 | 3.9809 | 2.9752 | 2.503
|  | NETHERHAMPTON | LW |  |  | 8.867 | 8.729 | 8.5207 | 8.2365 | 7.8804 | 7.5015 | 7.0151 | 6.4391 | 5.756 | 4.3951 | 2.8398 | 1.7632 | 1.2551 | 9.5742 | 9.5394 | 9.4901 | 9.4318 | 9.3353 | 9.0956 | 8.7972 | 8.4449 | 8.0203 | 7.1165 | 6.0523 | 5.0467 | 3.8979 | 9.2762 | 9.1597 | 8.9844 | 8.7416 | 8.4395 | 8.1174 | 7.706 | 7.2184 | 6.6269 | 5.4187 | 3.9809 | 2.9752 | 2.503
|  | NETHERHAMPTON | ST |  |  | 8.867 | 8.729 | 8.5207 | 8.2365 | 7.8804 | 7.5015 | 7.0151 | 6.4391 | 5.756 | 4.3951 | 2.8398 | 1.7632 | 1.2551 | 9.5742 | 9.5394 | 9.4901 | 9.4318 | 9.3353 | 9.0956 | 8.7972 | 8.4449 | 8.0203 | 7.1165 | 6.0523 | 5.0467 | 3.8979 | 9.2762 | 9.1597 | 8.9844 | 8.7416 | 8.4395 | 8.1174 | 7.706 | 7.2184 | 6.6269 | 5.4187 | 3.9809 | 2.9752 | 2.503
|  | NETHERHAMPTON | FS |  |  | 8.867 | 8.729 | 8.5207 | 8.2365 | 7.8804 | 7.5015 | 7.0151 | 6.4391 | 5.756 | 4.3951 | 2.8398 | 1.7632 | 1.2551 | 9.5742 | 9.5394 | 9.4901 | 9.4318 | 9.3353 | 9.0956 | 8.7972 | 8.4449 | 8.0203 | 7.1165 | 6.0523 | 5.0467 | 3.8979 | 9.2762 | 9.1597 | 8.9844 | 8.7416 | 8.4395 | 8.1174 | 7.706 | 7.2184 | 6.6269 | 5.4187 | 3.9809 | 2.9752 | 2.503
BOTLEY WOOD GSP | NETLEY COMMON BSP | NETLEY COMMON | MINIMUM HEADROOM | SU 47615 12025 | YES | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
|  | NETLEY COMMON | CT |  |  | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
|  | NETLEY COMMON | LW |  |  | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
|  | NETLEY COMMON | ST |  |  | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
|  | NETLEY COMMON | FS |  |  | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 38.2725 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 33.375 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
MANNINGTON GSP | ARNEWOOD | NEW MILTON | MINIMUM HEADROOM | SZ 23049 94942 | YES | 18.3649 | 18.1756 | 17.9146 | 17.6212 | 16.8215 | 15.8584 | 14.802 | 13.6024 | 11.7694 | 6.9466 | 0.23395 | -4.8237 | -7.4487 | 18.9031 | 18.6412 | 18.1735 | 17.6409 | 17.0601 | 16.3933 | 15.6557 | 14.8036 | 13.5698 | 10.3564 | 6.4072 | 3.4275 | 0.8041 | 20.3574 | 20.1485 | 19.8665 | 19.4086 | 18.5976 | 17.669 | 16.6502 | 15.4919 | 13.7109 | 9.0068 | 2.6665 | -1.6632 | -3.8016
|  | NEW MILTON | CT |  |  | 18.3649 | 18.1756 | 17.9146 | 17.6212 | 16.8215 | 15.8584 | 14.802 | 13.6024 | 11.7694 | 6.9466 | 0.23395 | -4.8237 | -7.4487 | 18.9031 | 18.6412 | 18.1735 | 17.6409 | 17.0601 | 16.3933 | 15.6557 | 14.8036 | 13.5698 | 10.3564 | 6.4072 | 3.4275 | 0.8041 | 20.3574 | 20.1485 | 19.8665 | 19.4086 | 18.5976 | 17.669 | 16.6502 | 15.4919 | 13.7109 | 9.0068 | 2.6665 | -1.6632 | -3.8016
|  | NEW MILTON | LW |  |  | 18.3649 | 18.1756 | 17.9146 | 17.6212 | 16.8215 | 15.8584 | 14.802 | 13.6024 | 11.7694 | 6.9466 | 0.23395 | -4.8237 | -7.4487 | 18.9031 | 18.6412 | 18.1735 | 17.6409 | 17.0601 | 16.3933 | 15.6557 | 14.8036 | 13.5698 | 10.3564 | 6.4072 | 3.4275 | 0.8041 | 20.3574 | 20.1485 | 19.8665 | 19.4086 | 18.5976 | 17.669 | 16.6502 | 15.4919 | 13.7109 | 9.0068 | 2.6665 | -1.6632 | -3.8016
|  | NEW MILTON | ST |  |  | 18.3649 | 18.1756 | 17.9146 | 17.6212 | 16.8215 | 15.8584 | 14.802 | 13.6024 | 11.7694 | 6.9466 | 0.23395 | -4.8237 | -7.4487 | 18.9031 | 18.6412 | 18.1735 | 17.6409 | 17.0601 | 16.3933 | 15.6557 | 14.8036 | 13.5698 | 10.3564 | 6.4072 | 3.4275 | 0.8041 | 20.3574 | 20.1485 | 19.8665 | 19.4086 | 18.5976 | 17.669 | 16.6502 | 15.4919 | 13.7109 | 9.0068 | 2.6665 | -1.6632 | -3.8016
|  | NEW MILTON | FS |  |  | 18.3649 | 18.1756 | 17.9146 | 17.6212 | 16.8215 | 15.8584 | 14.802 | 13.6024 | 11.7694 | 6.9466 | 0.23395 | -4.8237 | -7.4487 | 18.9031 | 18.6412 | 18.1735 | 17.6409 | 17.0601 | 16.3933 | 15.6557 | 14.8036 | 13.5698 | 10.3564 | 6.4072 | 3.4275 | 0.8041 | 20.3574 | 20.1485 | 19.8665 | 19.4086 | 18.5976 | 17.669 | 16.6502 | 15.4919 | 13.7109 | 9.0068 | 2.6665 | -1.6632 | -3.8016
FAWLEY GSP | COWES & WOOTTON COMMON BSP | NEWPORT | MINIMUM HEADROOM | SZ 50076 89544 | YES | 10.014 | 9.4432 | 8.6689 | 7.5593 | 6.4073 | 5.2454 | 4.0918 | 2.8146 | 0.86044 | -5.0224 | -15.1783 | -21.8955 | -24.7786 | 17.7641 | 17.5445 | 17.2493 | 16.9371 | 16.544 | 15.8076 | 15.0568 | 14.1896 | 12.981 | 9.1899 | 3.4924 | -0.91945 | -5.1304 | 13.0795 | 12.81 | 12.3865 | 11.5433 | 10.5616 | 9.4701 | 8.3695 | 7.1353 | 5.2693 | -0.27138 | -9.4032 | -15.3299 | -17.8681
|  | NEWPORT | CT |  |  | 10.014 | 9.4432 | 8.6689 | 7.5593 | 6.4073 | 5.2454 | 4.0918 | 2.8146 | 0.86044 | -5.0224 | -15.1783 | -21.8955 | -24.7786 | 17.7641 | 17.5445 | 17.2493 | 16.9371 | 16.544 | 15.8076 | 15.0568 | 14.1896 | 12.981 | 9.1899 | 3.4924 | -0.91945 | -5.1304 | 13.0795 | 12.81 | 12.3865 | 11.5433 | 10.5616 | 9.4701 | 8.3695 | 7.1353 | 5.2693 | -0.27138 | -9.4032 | -15.3299 | -17.8681
|  | NEWPORT | LW |  |  | 10.014 | 9.4432 | 8.6689 | 7.5593 | 6.4073 | 5.2454 | 4.0918 | 2.8146 | 0.86044 | -5.0224 | -15.1783 | -21.8955 | -24.7786 | 17.7641 | 17.5445 | 17.2493 | 16.9371 | 16.544 | 15.8076 | 15.0568 | 14.1896 | 12.981 | 9.1899 | 3.4924 | -0.91945 | -5.1304 | 13.0795 | 12.81 | 12.3865 | 11.5433 | 10.5616 | 9.4701 | 8.3695 | 7.1353 | 5.2693 | -0.27138 | -9.4032 | -15.3299 | -17.8681
|  | NEWPORT | ST |  |  | 10.014 | 9.4432 | 8.6689 | 7.5593 | 6.4073 | 5.2454 | 4.0918 | 2.8146 | 0.86044 | -5.0224 | -15.1783 | -21.8955 | -24.7786 | 17.7641 | 17.5445 | 17.2493 | 16.9371 | 16.544 | 15.8076 | 15.0568 | 14.1896 | 12.981 | 9.1899 | 3.4924 | -0.91945 | -5.1304 | 13.0795 | 12.81 | 12.3865 | 11.5433 | 10.5616 | 9.4701 | 8.3695 | 7.1353 | 5.2693 | -0.27138 | -9.4032 | -15.3299 | -17.8681
|  | NEWPORT | FS |  |  | 10.014 | 9.4432 | 8.6689 | 7.5593 | 6.4073 | 5.2454 | 4.0918 | 2.8146 | 0.86044 | -5.0224 | -15.1783 | -21.8955 | -24.7786 | 17.7641 | 17.5445 | 17.2493 | 16.9371 | 16.544 | 15.8076 | 15.0568 | 14.1896 | 12.981 | 9.1899 | 3.4924 | -0.91945 | -5.1304 | 13.0795 | 12.81 | 12.3865 | 11.5433 | 10.5616 | 9.4701 | 8.3695 | 7.1353 | 5.2693 | -0.27138 | -9.4032 | -15.3299 | -17.8681
BRAMLEY (FLEE) | ALDERSHOT BSP | NORMANDY | MINIMUM HEADROOM | SU 93221 52894 | YES | -1.5524 | -1.6957 | -1.8894 | -2.1097 | -2.3411 | -2.5786 | -2.8551 | -3.1731 | -3.5513 | -4.4568 | -5.2989 | -5.8432 | -6.0713 | -0.80022 | -0.88607 | -0.99863 | -1.1189 | -1.2454 | -1.3767 | -1.5314 | -1.7121 | -1.9208 | -2.3704 | -2.7849 | -3.0692 | -3.2528 | -1.0105 | -1.1321 | -1.296 | -1.4831 | -1.6803 | -1.8841 | -2.1226 | -2.3988 | -2.7296 | -3.5011 | -4.2416 | -4.7218 | -4.9236
|  | NORMANDY | CT |  |  | -1.5524 | -1.6957 | -1.8894 | -2.1097 | -2.3411 | -2.5786 | -2.8551 | -3.1731 | -3.5513 | -4.4568 | -5.2989 | -5.8432 | -6.0713 | -0.80022 | -0.88607 | -0.99863 | -1.1189 | -1.2454 | -1.3767 | -1.5314 | -1.7121 | -1.9208 | -2.3704 | -2.7849 | -3.0692 | -3.2528 | -1.0105 | -1.1321 | -1.296 | -1.4831 | -1.6803 | -1.8841 | -2.1226 | -2.3988 | -2.7296 | -3.5011 | -4.2416 | -4.7218 | -4.9236
|  | NORMANDY | LW |  |  | -1.5524 | -1.6957 | -1.8894 | -2.1097 | -2.3411 | -2.5786 | -2.8551 | -3.1731 | -3.5513 | -4.4568 | -5.2989 | -5.8432 | -6.0713 | -0.80022 | -0.88607 | -0.99863 | -1.1189 | -1.2454 | -1.3767 | -1.5314 | -1.7121 | -1.9208 | -2.3704 | -2.7849 | -3.0692 | -3.2528 | -1.0105 | -1.1321 | -1.296 | -1.4831 | -1.6803 | -1.8841 | -2.1226 | -2.3988 | -2.7296 | -3.5011 | -4.2416 | -4.7218 | -4.9236
|  | NORMANDY | ST |  |  | -1.5524 | -1.6957 | -1.8894 | -2.1097 | -2.3411 | -2.5786 | -2.8551 | -3.1731 | -3.5513 | -4.4568 | -5.2989 | -5.8432 | -6.0713 | -0.80022 | -0.88607 | -0.99863 | -1.1189 | -1.2454 | -1.3767 | -1.5314 | -1.7121 | -1.9208 | -2.3704 | -2.7849 | -3.0692 | -3.2528 | -1.0105 | -1.1321 | -1.296 | -1.4831 | -1.6803 | -1.8841 | -2.1226 | -2.3988 | -2.7296 | -3.5011 | -4.2416 | -4.7218 | -4.9236
|  | NORMANDY | FS |  |  | -1.5524 | -1.6957 | -1.8894 | -2.1097 | -2.3411 | -2.5786 | -2.8551 | -3.1731 | -3.5513 | -4.4568 | -5.2989 | -5.8432 | -6.0713 | -0.80022 | -0.88607 | -0.99863 | -1.1189 | -1.2454 | -1.3767 | -1.5314 | -1.7121 | -1.9208 | -2.3704 | -2.7849 | -3.0692 | -3.2528 | -1.0105 | -1.1321 | -1.296 | -1.4831 | -1.6803 | -1.8841 | -2.1226 | -2.3988 | -2.7296 | -3.5011 | -4.2416 | -4.7218 | -4.9236
NURSLING GSP | ROWNHAMS | NORTH BADDESLEY | MINIMUM HEADROOM | SU 38080 20568 | YES | 3.9853 | 3.5236 | 3.1859 | 2.7557 | 2.2809 | 1.7716 | 1.2129 | 0.59862 | -0.45273 | -2.5631 | -5.6987 | -7.8643 | -8.8353 | 8.14 | 7.8267 | 7.5993 | 7.31 | 6.9882 | 6.6368 | 6.2443 | 5.8006 | 5.088 | 3.7885 | 2.0779 | 0.83417 | -0.21444 | 5.8665 | 5.4472 | 5.1419 | 4.7492 | 4.3192 | 3.8618 | 3.331 | 2.7417 | 1.7391 | -0.22398 | -3.0378 | -4.9763 | -5.8239
|  | NORTH BADDESLEY | CT |  |  | 3.9853 | 3.5236 | 3.1859 | 2.7557 | 2.2809 | 1.7716 | 1.2129 | 0.59862 | -0.45273 | -2.5631 | -5.6987 | -7.8643 | -8.8353 | 8.14 | 7.8267 | 7.5993 | 7.31 | 6.9882 | 6.6368 | 6.2443 | 5.8006 | 5.088 | 3.7885 | 2.0779 | 0.83417 | -0.21444 | 5.8665 | 5.4472 | 5.1419 | 4.7492 | 4.3192 | 3.8618 | 3.331 | 2.7417 | 1.7391 | -0.22398 | -3.0378 | -4.9763 | -5.8239
|  | NORTH BADDESLEY | LW |  |  | 3.9853 | 3.5236 | 3.1859 | 2.7557 | 2.2809 | 1.7716 | 1.2129 | 0.59862 | -0.45273 | -2.5631 | -5.6987 | -7.8643 | -8.8353 | 8.14 | 7.8267 | 7.5993 | 7.31 | 6.9882 | 6.6368 | 6.2443 | 5.8006 | 5.088 | 3.7885 | 2.0779 | 0.83417 | -0.21444 | 5.8665 | 5.4472 | 5.1419 | 4.7492 | 4.3192 | 3.8618 | 3.331 | 2.7417 | 1.7391 | -0.22398 | -3.0378 | -4.9763 | -5.8239
|  | NORTH BADDESLEY | ST |  |  | 3.9853 | 3.5236 | 3.1859 | 2.7557 | 2.2809 | 1.7716 | 1.2129 | 0.59862 | -0.45273 | -2.5631 | -5.6987 | -7.8643 | -8.8353 | 8.14 | 7.8267 | 7.5993 | 7.31 | 6.9882 | 6.6368 | 6.2443 | 5.8006 | 5.088 | 3.7885 | 2.0779 | 0.83417 | -0.21444 | 5.8665 | 5.4472 | 5.1419 | 4.7492 | 4.3192 | 3.8618 | 3.331 | 2.7417 | 1.7391 | -0.22398 | -3.0378 | -4.9763 | -5.8239
|  | NORTH BADDESLEY | FS |  |  | 3.9853 | 3.5236 | 3.1859 | 2.7557 | 2.2809 | 1.7716 | 1.2129 | 0.59862 | -0.45273 | -2.5631 | -5.6987 | -7.8643 | -8.8353 | 8.14 | 7.8267 | 7.5993 | 7.31 | 6.9882 | 6.6368 | 6.2443 | 5.8006 | 5.088 | 3.7885 | 2.0779 | 0.83417 | -0.21444 | 5.8665 | 5.4472 | 5.1419 | 4.7492 | 4.3192 | 3.8618 | 3.331 | 2.7417 | 1.7391 | -0.22398 | -3.0378 | -4.9763 | -5.8239
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | NORTH FAREHAM | MINIMUM HEADROOM | SU 56427 07430 | YES | 1.4641 | 1.1989 | 0.82377 | 0.3154 | -0.25401 | -0.89024 | -1.6029 | -2.418 | -3.7325 | -7.0217 | -11.6809 | -15.1576 | -16.9181 | 5.6503 | 5.5552 | 5.4283 | 5.2909 | 4.8909 | 4.4305 | 3.9075 | 3.2955 | 2.3872 | 0.17673 | -2.6708 | -5.0306 | -7.3918 | 2.8602 | 2.5932 | 2.1982 | 1.7149 | 1.19 | 0.60146 | -0.061514 | -0.82771 | -2.0425 | -5.1149 | -9.305 | -12.203 | -13.6478
|  | NORTH FAREHAM | CT |  |  | 1.4641 | 1.1989 | 0.82377 | 0.3154 | -0.25401 | -0.89024 | -1.6029 | -2.418 | -3.7325 | -7.0217 | -11.6809 | -15.1576 | -16.9181 | 5.6503 | 5.5552 | 5.4283 | 5.2909 | 4.8909 | 4.4305 | 3.9075 | 3.2955 | 2.3872 | 0.17673 | -2.6708 | -5.0306 | -7.3918 | 2.8602 | 2.5932 | 2.1982 | 1.7149 | 1.19 | 0.60146 | -0.061514 | -0.82771 | -2.0425 | -5.1149 | -9.305 | -12.203 | -13.6478
|  | NORTH FAREHAM | LW |  |  | 1.4641 | 1.1989 | 0.82377 | 0.3154 | -0.25401 | -0.89024 | -1.6029 | -2.418 | -3.7325 | -7.0217 | -11.6809 | -15.1576 | -16.9181 | 5.6503 | 5.5552 | 5.4283 | 5.2909 | 4.8909 | 4.4305 | 3.9075 | 3.2955 | 2.3872 | 0.17673 | -2.6708 | -5.0306 | -7.3918 | 2.8602 | 2.5932 | 2.1982 | 1.7149 | 1.19 | 0.60146 | -0.061514 | -0.82771 | -2.0425 | -5.1149 | -9.305 | -12.203 | -13.6478
|  | NORTH FAREHAM | ST |  |  | 1.4641 | 1.1989 | 0.82377 | 0.3154 | -0.25401 | -0.89024 | -1.6029 | -2.418 | -3.7325 | -7.0217 | -11.6809 | -15.1576 | -16.9181 | 5.6503 | 5.5552 | 5.4283 | 5.2909 | 4.8909 | 4.4305 | 3.9075 | 3.2955 | 2.3872 | 0.17673 | -2.6708 | -5.0306 | -7.3918 | 2.8602 | 2.5932 | 2.1982 | 1.7149 | 1.19 | 0.60146 | -0.061514 | -0.82771 | -2.0425 | -5.1149 | -9.305 | -12.203 | -13.6478
|  | NORTH FAREHAM | FS |  |  | 1.4641 | 1.1989 | 0.82377 | 0.3154 | -0.25401 | -0.89024 | -1.6029 | -2.418 | -3.7325 | -7.0217 | -11.6809 | -15.1576 | -16.9181 | 5.6503 | 5.5552 | 5.4283 | 5.2909 | 4.8909 | 4.4305 | 3.9075 | 3.2955 | 2.3872 | 0.17673 | -2.6708 | -5.0306 | -7.3918 | 2.8602 | 2.5932 | 2.1982 | 1.7149 | 1.19 | 0.60146 | -0.061514 | -0.82771 | -2.0425 | -5.1149 | -9.305 | -12.203 | -13.6478
LALEHAM | EAST BEDFONT A | NORTH FELTHAM | MINIMUM HEADROOM | TQ 10987 74875 | YES | 6.1766 | 5.688 | 5.1733 | 4.6248 | 4.0166 | 3.3568 | 2.6151 | 1.7336 | 0.70929 | -2.6159 | -7.5109 | -10.039 | -11.5516 | 7.7617 | 7.313 | 6.8463 | 6.3524 | 5.8014 | 5.2079 | 4.5554 | 3.8258 | 3.2078 | 0.84203 | -2.4032 | -5.5833 | -9.579 | 6.8208 | 6.3257 | 5.8058 | 5.213 | 4.5133 | 3.7544 | 2.9157 | 1.9513 | 1.0313 | -2.0845 | -6.7696 | -8.6505 | -9.603
|  | NORTH FELTHAM | CT |  |  | 6.1766 | 5.688 | 5.1733 | 4.6248 | 4.0166 | 3.3568 | 2.6151 | 1.7336 | 0.70929 | -2.6159 | -7.5109 | -10.039 | -11.5516 | 7.7617 | 7.313 | 6.8463 | 6.3524 | 5.8014 | 5.2079 | 4.5554 | 3.8258 | 3.2078 | 0.84203 | -2.4032 | -5.5833 | -9.579 | 6.8208 | 6.3257 | 5.8058 | 5.213 | 4.5133 | 3.7544 | 2.9157 | 1.9513 | 1.0313 | -2.0845 | -6.7696 | -8.6505 | -9.603
|  | NORTH FELTHAM | LW |  |  | 6.1766 | 5.688 | 5.1733 | 4.6248 | 4.0166 | 3.3568 | 2.6151 | 1.7336 | 0.70929 | -2.6159 | -7.5109 | -10.039 | -11.5516 | 7.7617 | 7.313 | 6.8463 | 6.3524 | 5.8014 | 5.2079 | 4.5554 | 3.8258 | 3.2078 | 0.84203 | -2.4032 | -5.5833 | -9.579 | 6.8208 | 6.3257 | 5.8058 | 5.213 | 4.5133 | 3.7544 | 2.9157 | 1.9513 | 1.0313 | -2.0845 | -6.7696 | -8.6505 | -9.603
|  | NORTH FELTHAM | ST |  |  | 6.1766 | 5.688 | 5.1733 | 4.6248 | 4.0166 | 3.3568 | 2.6151 | 1.7336 | 0.70929 | -2.6159 | -7.5109 | -10.039 | -11.5516 | 7.7617 | 7.313 | 6.8463 | 6.3524 | 5.8014 | 5.2079 | 4.5554 | 3.8258 | 3.2078 | 0.84203 | -2.4032 | -5.5833 | -9.579 | 6.8208 | 6.3257 | 5.8058 | 5.213 | 4.5133 | 3.7544 | 2.9157 | 1.9513 | 1.0313 | -2.0845 | -6.7696 | -8.6505 | -9.603
|  | NORTH FELTHAM | FS |  |  | 6.1766 | 5.688 | 5.1733 | 4.6248 | 4.0166 | 3.3568 | 2.6151 | 1.7336 | 0.70929 | -2.6159 | -7.5109 | -10.039 | -11.5516 | 7.7617 | 7.313 | 6.8463 | 6.3524 | 5.8014 | 5.2079 | 4.5554 | 3.8258 | 3.2078 | 0.84203 | -2.4032 | -5.5833 | -9.579 | 6.8208 | 6.3257 | 5.8058 | 5.213 | 4.5133 | 3.7544 | 2.9157 | 1.9513 | 1.0313 | -2.0845 | -6.7696 | -8.6505 | -9.603
COWLEY GSP | OXFORD BSP | NORTH HINKSEY | MINIMUM HEADROOM | SP 48645 04403 | YES | 2.1312 | 1.9473 | 1.736 | 1.4633 | 1.1743 | 0.87022 | 0.52069 | 0.11964 | -0.572 | -2.1893 | -4.4671 | -6.1365 | -6.8934 | 4.528 | 4.3835 | 4.216 | 4.0284 | 3.8275 | 3.6095 | 3.3555 | 3.0587 | 2.5963 | 1.5925 | 0.3834 | -0.54791 | -1.2951 | 3.0392 | 2.861 | 2.6555 | 2.3907 | 2.1093 | 1.8134 | 1.4735 | 1.084 | 0.41923 | -1.0911 | -3.1313 | -4.5986 | -5.2592
|  | NORTH HINKSEY | CT |  |  | 2.1312 | 1.9473 | 1.736 | 1.4633 | 1.1743 | 0.87022 | 0.52069 | 0.11964 | -0.572 | -2.1893 | -4.4671 | -6.1365 | -6.8934 | 4.528 | 4.3835 | 4.216 | 4.0284 | 3.8275 | 3.6095 | 3.3555 | 3.0587 | 2.5963 | 1.5925 | 0.3834 | -0.54791 | -1.2951 | 3.0392 | 2.861 | 2.6555 | 2.3907 | 2.1093 | 1.8134 | 1.4735 | 1.084 | 0.41923 | -1.0911 | -3.1313 | -4.5986 | -5.2592
|  | NORTH HINKSEY | LW |  |  | 2.1312 | 1.9473 | 1.736 | 1.4633 | 1.1743 | 0.87022 | 0.52069 | 0.11964 | -0.572 | -2.1893 | -4.4671 | -6.1365 | -6.8934 | 4.528 | 4.3835 | 4.216 | 4.0284 | 3.8275 | 3.6095 | 3.3555 | 3.0587 | 2.5963 | 1.5925 | 0.3834 | -0.54791 | -1.2951 | 3.0392 | 2.861 | 2.6555 | 2.3907 | 2.1093 | 1.8134 | 1.4735 | 1.084 | 0.41923 | -1.0911 | -3.1313 | -4.5986 | -5.2592
|  | NORTH HINKSEY | ST |  |  | 2.1312 | 1.9473 | 1.736 | 1.4633 | 1.1743 | 0.87022 | 0.52069 | 0.11964 | -0.572 | -2.1893 | -4.4671 | -6.1365 | -6.8934 | 4.528 | 4.3835 | 4.216 | 4.0284 | 3.8275 | 3.6095 | 3.3555 | 3.0587 | 2.5963 | 1.5925 | 0.3834 | -0.54791 | -1.2951 | 3.0392 | 2.861 | 2.6555 | 2.3907 | 2.1093 | 1.8134 | 1.4735 | 1.084 | 0.41923 | -1.0911 | -3.1313 | -4.5986 | -5.2592
|  | NORTH HINKSEY | FS |  |  | 2.1312 | 1.9473 | 1.736 | 1.4633 | 1.1743 | 0.87022 | 0.52069 | 0.11964 | -0.572 | -2.1893 | -4.4671 | -6.1365 | -6.8934 | 4.528 | 4.3835 | 4.216 | 4.0284 | 3.8275 | 3.6095 | 3.3555 | 3.0587 | 2.5963 | 1.5925 | 0.3834 | -0.54791 | -1.2951 | 3.0392 | 2.861 | 2.6555 | 2.3907 | 2.1093 | 1.8134 | 1.4735 | 1.084 | 0.41923 | -1.0911 | -3.1313 | -4.5986 | -5.2592
NORTH HYDE GSP |  | NORTH HYDE 11kV | MINIMUM HEADROOM | TQ 10367 79001 |  | 8.9987 | -17.3161 | -37.5872 | -48.9158 | -50.0478 | -51.2631 | -52.5532 | -54.0256 | -56.1988 | -62.912 | -74.9642 | -84.4466 | -90.4713 | 15.9665 | -16.6343 | -41.7796 | -54.9645 | -55.4125 | -56.1772 | -57.1998 | -58.36 | -59.884 | -65.0723 | -75.0168 | -86.1799 | -101.0369 | 11.1569 | -21.8188 | -47.3377 | -61.1164 | -62.1758 | -63.3245 | -64.5464 | -65.9211 | -67.9416 | -74.1561 | -84.8005 | -92.7731 | -97.8193
|  | NORTH HYDE 11kV | CT |  |  | 8.9987 | -17.3161 | -37.5872 | -48.9158 | -50.0478 | -51.2631 | -52.5532 | -54.0256 | -56.1988 | -62.912 | -74.9642 | -84.4466 | -90.4713 | 15.9665 | -16.6343 | -41.7796 | -54.9645 | -55.4125 | -56.1772 | -57.1998 | -58.36 | -59.884 | -65.0723 | -75.0168 | -86.1799 | -101.0369 | 11.1569 | -21.8188 | -47.3377 | -61.1164 | -62.1758 | -63.3245 | -64.5464 | -65.9211 | -67.9416 | -74.1561 | -84.8005 | -92.7731 | -97.8193
|  | NORTH HYDE 11kV | LW |  |  | 8.9987 | -17.3161 | -37.5872 | -48.9158 | -50.0478 | -51.2631 | -52.5532 | -54.0256 | -56.1988 | -62.912 | -74.9642 | -84.4466 | -90.4713 | 15.9665 | -16.6343 | -41.7796 | -54.9645 | -55.4125 | -56.1772 | -57.1998 | -58.36 | -59.884 | -65.0723 | -75.0168 | -86.1799 | -101.0369 | 11.1569 | -21.8188 | -47.3377 | -61.1164 | -62.1758 | -63.3245 | -64.5464 | -65.9211 | -67.9416 | -74.1561 | -84.8005 | -92.7731 | -97.8193
|  | NORTH HYDE 11kV | ST |  |  | 8.9987 | -17.3161 | -37.5872 | -48.9158 | -50.0478 | -51.2631 | -52.5532 | -54.0256 | -56.1988 | -62.912 | -74.9642 | -84.4466 | -90.4713 | 15.9665 | -16.6343 | -41.7796 | -54.9645 | -55.4125 | -56.1772 | -57.1998 | -58.36 | -59.884 | -65.0723 | -75.0168 | -86.1799 | -101.0369 | 11.1569 | -21.8188 | -47.3377 | -61.1164 | -62.1758 | -63.3245 | -64.5464 | -65.9211 | -67.9416 | -74.1561 | -84.8005 | -92.7731 | -97.8193
|  | NORTH HYDE 11kV | FS |  |  | 8.9987 | -17.3161 | -37.5872 | -48.9158 | -50.0478 | -51.2631 | -52.5532 | -54.0256 | -56.1988 | -62.912 | -74.9642 | -84.4466 | -90.4713 | 15.9665 | -16.6343 | -41.7796 | -54.9645 | -55.4125 | -56.1772 | -57.1998 | -58.36 | -59.884 | -65.0723 | -75.0168 | -86.1799 | -101.0369 | 11.1569 | -21.8188 | -47.3377 | -61.1164 | -62.1758 | -63.3245 | -64.5464 | -65.9211 | -67.9416 | -74.1561 | -84.8005 | -92.7731 | -97.8193
MINETY GSP | CIRENCESTER BSP | NORTHLEACH | MINIMUM HEADROOM | SP 10557 14251 | YES | 6.3496 | 6.1705 | 5.9554 | 5.6529 | 5.3372 | 4.9968 | 4.6176 | 4.1831 | 3.5882 | 2.2777 | 0.86456 | 0.63586 | 0.52661 | 8.3519 | 8.2457 | 8.1088 | 7.9468 | 7.7742 | 7.5867 | 7.3689 | 7.1036 | 6.7576 | 6.1824 | 5.5787 | 5.3687 | 5.1508 | 7.4006 | 7.2274 | 7.0241 | 6.7257 | 6.4156 | 6.0818 | 5.714 | 5.3003 | 4.7418 | 3.5474 | 2.2869 | 2.0805 | 1.9825
|  | NORTHLEACH | CT |  |  | 6.3496 | 6.1705 | 5.9554 | 5.6529 | 5.3372 | 4.9968 | 4.6176 | 4.1831 | 3.5882 | 2.2777 | 0.86456 | 0.63586 | 0.52661 | 8.3519 | 8.2457 | 8.1088 | 7.9468 | 7.7742 | 7.5867 | 7.3689 | 7.1036 | 6.7576 | 6.1824 | 5.5787 | 5.3687 | 5.1508 | 7.4006 | 7.2274 | 7.0241 | 6.7257 | 6.4156 | 6.0818 | 5.714 | 5.3003 | 4.7418 | 3.5474 | 2.2869 | 2.0805 | 1.9825
|  | NORTHLEACH | LW |  |  | 6.3496 | 6.1705 | 5.9554 | 5.6529 | 5.3372 | 4.9968 | 4.6176 | 4.1831 | 3.5882 | 2.2777 | 0.86456 | 0.63586 | 0.52661 | 8.3519 | 8.2457 | 8.1088 | 7.9468 | 7.7742 | 7.5867 | 7.3689 | 7.1036 | 6.7576 | 6.1824 | 5.5787 | 5.3687 | 5.1508 | 7.4006 | 7.2274 | 7.0241 | 6.7257 | 6.4156 | 6.0818 | 5.714 | 5.3003 | 4.7418 | 3.5474 | 2.2869 | 2.0805 | 1.9825
|  | NORTHLEACH | ST |  |  | 6.3496 | 6.1705 | 5.9554 | 5.6529 | 5.3372 | 4.9968 | 4.6176 | 4.1831 | 3.5882 | 2.2777 | 0.86456 | 0.63586 | 0.52661 | 8.3519 | 8.2457 | 8.1088 | 7.9468 | 7.7742 | 7.5867 | 7.3689 | 7.1036 | 6.7576 | 6.1824 | 5.5787 | 5.3687 | 5.1508 | 7.4006 | 7.2274 | 7.0241 | 6.7257 | 6.4156 | 6.0818 | 5.714 | 5.3003 | 4.7418 | 3.5474 | 2.2869 | 2.0805 | 1.9825
|  | NORTHLEACH | FS |  |  | 6.3496 | 6.1705 | 5.9554 | 5.6529 | 5.3372 | 4.9968 | 4.6176 | 4.1831 | 3.5882 | 2.2777 | 0.86456 | 0.63586 | 0.52661 | 8.3519 | 8.2457 | 8.1088 | 7.9468 | 7.7742 | 7.5867 | 7.3689 | 7.1036 | 6.7576 | 6.1824 | 5.5787 | 5.3687 | 5.1508 | 7.4006 | 7.2274 | 7.0241 | 6.7257 | 6.4156 | 6.0818 | 5.714 | 5.3003 | 4.7418 | 3.5474 | 2.2869 | 2.0805 | 1.9825
IVER 66KV |  | NORTHOLT | MINIMUM HEADROOM | TQ 11550 83230 | YES | 9.0828 | 8.5929 | 7.7875 | 6.696 | 5.5281 | 4.274 | 2.9196 | 1.3971 | -1.0661 | -8.9429 | -22.5093 | -32.5865 | -38.7159 | 20.129 | 19.7572 | 19.131 | 18.4022 | 17.6128 | 16.744 | 15.7915 | 14.6988 | 13.1152 | 7.5307 | -2.0742 | -11.4705 | -22.9444 | 13.8205 | 13.4211 | 12.7859 | 11.8445 | 10.7997 | 9.6778 | 8.413 | 6.9743 | 4.6775 | -2.6504 | -14.7786 | -23.6778 | -28.8968
|  | NORTHOLT | CT |  |  | 9.0828 | 8.5929 | 7.7875 | 6.696 | 5.5281 | 4.274 | 2.9196 | 1.3971 | -1.0661 | -8.9429 | -22.5093 | -32.5865 | -38.7159 | 20.129 | 19.7572 | 19.131 | 18.4022 | 17.6128 | 16.744 | 15.7915 | 14.6988 | 13.1152 | 7.5307 | -2.0742 | -11.4705 | -22.9444 | 13.8205 | 13.4211 | 12.7859 | 11.8445 | 10.7997 | 9.6778 | 8.413 | 6.9743 | 4.6775 | -2.6504 | -14.7786 | -23.6778 | -28.8968
|  | NORTHOLT | LW |  |  | 9.0828 | 8.5929 | 7.7875 | 6.696 | 5.5281 | 4.274 | 2.9196 | 1.3971 | -1.0661 | -8.9429 | -22.5093 | -32.5865 | -38.7159 | 20.129 | 19.7572 | 19.131 | 18.4022 | 17.6128 | 16.744 | 15.7915 | 14.6988 | 13.1152 | 7.5307 | -2.0742 | -11.4705 | -22.9444 | 13.8205 | 13.4211 | 12.7859 | 11.8445 | 10.7997 | 9.6778 | 8.413 | 6.9743 | 4.6775 | -2.6504 | -14.7786 | -23.6778 | -28.8968
|  | NORTHOLT | ST |  |  | 9.0828 | 8.5929 | 7.7875 | 6.696 | 5.5281 | 4.274 | 2.9196 | 1.3971 | -1.0661 | -8.9429 | -22.5093 | -32.5865 | -38.7159 | 20.129 | 19.7572 | 19.131 | 18.4022 | 17.6128 | 16.744 | 15.7915 | 14.6988 | 13.1152 | 7.5307 | -2.0742 | -11.4705 | -22.9444 | 13.8205 | 13.4211 | 12.7859 | 11.8445 | 10.7997 | 9.6778 | 8.413 | 6.9743 | 4.6775 | -2.6504 | -14.7786 | -23.6778 | -28.8968
|  | NORTHOLT | FS |  |  | 9.0828 | 8.5929 | 7.7875 | 6.696 | 5.5281 | 4.274 | 2.9196 | 1.3971 | -1.0661 | -8.9429 | -22.5093 | -32.5865 | -38.7159 | 20.129 | 19.7572 | 19.131 | 18.4022 | 17.6128 | 16.744 | 15.7915 | 14.6988 | 13.1152 | 7.5307 | -2.0742 | -11.4705 | -22.9444 | 13.8205 | 13.4211 | 12.7859 | 11.8445 | 10.7997 | 9.6778 | 8.413 | 6.9743 | 4.6775 | -2.6504 | -14.7786 | -23.6778 | -28.8968
BRAMLEY (FLEE) | READING BSP | NORTHUMBERLAND AVENUE | MINIMUM HEADROOM | SU 72207 71092 | YES | 5.1125 | 4.9399 | 4.7101 | 4.395 | 4.0369 | 3.6576 | 3.2364 | 2.5032 | 1.4078 | -2.2505 | -7.4944 | -11.2418 | -13.5579 | 0.86209 | 0.70356 | 0.51683 | 0.329 | 0.1164 | -0.10806 | -0.35906 | -0.747 | -1.3604 | -3.411 | -6.578 | -9.3213 | -12.2795 | 3.601 | 3.3565 | 3.0057 | 2.5164 | 1.9628 | 1.3757 | 0.73443 | -0.0036952 | -0.98493 | -4.2491 | -8.7986 | -12.0012 | -13.9439
|  | NORTHUMBERLAND AVENUE | CT |  |  | 5.1125 | 4.9399 | 4.7101 | 4.395 | 4.0369 | 3.6576 | 3.2364 | 2.5032 | 1.4078 | -2.2505 | -7.4944 | -11.2418 | -13.5579 | 0.86209 | 0.70356 | 0.51683 | 0.329 | 0.1164 | -0.10806 | -0.35906 | -0.747 | -1.3604 | -3.411 | -6.578 | -9.3213 | -12.2795 | 3.601 | 3.3565 | 3.0057 | 2.5164 | 1.9628 | 1.3757 | 0.73443 | -0.0036952 | -0.98493 | -4.2491 | -8.7986 | -12.0012 | -13.9439
|  | NORTHUMBERLAND AVENUE | LW |  |  | 5.1125 | 4.9399 | 4.7101 | 4.395 | 4.0369 | 3.6576 | 3.2364 | 2.5032 | 1.4078 | -2.2505 | -7.4944 | -11.2418 | -13.5579 | 0.86209 | 0.70356 | 0.51683 | 0.329 | 0.1164 | -0.10806 | -0.35906 | -0.747 | -1.3604 | -3.411 | -6.578 | -9.3213 | -12.2795 | 3.601 | 3.3565 | 3.0057 | 2.5164 | 1.9628 | 1.3757 | 0.73443 | -0.0036952 | -0.98493 | -4.2491 | -8.7986 | -12.0012 | -13.9439
|  | NORTHUMBERLAND AVENUE | ST |  |  | 5.1125 | 4.9399 | 4.7101 | 4.395 | 4.0369 | 3.6576 | 3.2364 | 2.5032 | 1.4078 | -2.2505 | -7.4944 | -11.2418 | -13.5579 | 0.86209 | 0.70356 | 0.51683 | 0.329 | 0.1164 | -0.10806 | -0.35906 | -0.747 | -1.3604 | -3.411 | -6.578 | -9.3213 | -12.2795 | 3.601 | 3.3565 | 3.0057 | 2.5164 | 1.9628 | 1.3757 | 0.73443 | -0.0036952 | -0.98493 | -4.2491 | -8.7986 | -12.0012 | -13.9439
|  | NORTHUMBERLAND AVENUE | FS |  |  | 5.1125 | 4.9399 | 4.7101 | 4.395 | 4.0369 | 3.6576 | 3.2364 | 2.5032 | 1.4078 | -2.2505 | -7.4944 | -11.2418 | -13.5579 | 0.86209 | 0.70356 | 0.51683 | 0.329 | 0.1164 | -0.10806 | -0.35906 | -0.747 | -1.3604 | -3.411 | -6.578 | -9.3213 | -12.2795 | 3.601 | 3.3565 | 3.0057 | 2.5164 | 1.9628 | 1.3757 | 0.73443 | -0.0036952 | -0.98493 | -4.2491 | -8.7986 | -12.0012 | -13.9439
COWLEY GSP | HIGH WYCOMBE BSP | NUFFIELD | MINIMUM HEADROOM | SU 68329 86784 | YES | 1.8235 | 1.7191 | 1.6003 | 1.4417 | 1.2763 | 1.0869 | 0.86872 | 0.64041 | 0.35651 | -0.15575 | -1.0323 | -1.577 | -1.803 | 4.2871 | 4.217 | 4.1347 | 4.0397 | 3.9394 | 3.8214 | 3.6801 | 3.5293 | 3.3473 | 3.077 | 2.6227 | 2.3151 | 2.0944 | 3.1508 | 3.0521 | 2.9388 | 2.7912 | 2.637 | 2.4595 | 2.2535 | 2.0373 | 1.7689 | 1.3036 | 0.51626 | 0.031516 | -0.17027
|  | NUFFIELD | CT |  |  | 1.8235 | 1.7191 | 1.6003 | 1.4417 | 1.2763 | 1.0869 | 0.86872 | 0.64041 | 0.35651 | -0.15575 | -1.0323 | -1.577 | -1.803 | 4.2871 | 4.217 | 4.1347 | 4.0397 | 3.9394 | 3.8214 | 3.6801 | 3.5293 | 3.3473 | 3.077 | 2.6227 | 2.3151 | 2.0944 | 3.1508 | 3.0521 | 2.9388 | 2.7912 | 2.637 | 2.4595 | 2.2535 | 2.0373 | 1.7689 | 1.3036 | 0.51626 | 0.031516 | -0.17027
|  | NUFFIELD | LW |  |  | 1.8235 | 1.7191 | 1.6003 | 1.4417 | 1.2763 | 1.0869 | 0.86872 | 0.64041 | 0.35651 | -0.15575 | -1.0323 | -1.577 | -1.803 | 4.2871 | 4.217 | 4.1347 | 4.0397 | 3.9394 | 3.8214 | 3.6801 | 3.5293 | 3.3473 | 3.077 | 2.6227 | 2.3151 | 2.0944 | 3.1508 | 3.0521 | 2.9388 | 2.7912 | 2.637 | 2.4595 | 2.2535 | 2.0373 | 1.7689 | 1.3036 | 0.51626 | 0.031516 | -0.17027
|  | NUFFIELD | ST |  |  | 1.8235 | 1.7191 | 1.6003 | 1.4417 | 1.2763 | 1.0869 | 0.86872 | 0.64041 | 0.35651 | -0.15575 | -1.0323 | -1.577 | -1.803 | 4.2871 | 4.217 | 4.1347 | 4.0397 | 3.9394 | 3.8214 | 3.6801 | 3.5293 | 3.3473 | 3.077 | 2.6227 | 2.3151 | 2.0944 | 3.1508 | 3.0521 | 2.9388 | 2.7912 | 2.637 | 2.4595 | 2.2535 | 2.0373 | 1.7689 | 1.3036 | 0.51626 | 0.031516 | -0.17027
|  | NUFFIELD | FS |  |  | 1.8235 | 1.7191 | 1.6003 | 1.4417 | 1.2763 | 1.0869 | 0.86872 | 0.64041 | 0.35651 | -0.15575 | -1.0323 | -1.577 | -1.803 | 4.2871 | 4.217 | 4.1347 | 4.0397 | 3.9394 | 3.8214 | 3.6801 | 3.5293 | 3.3473 | 3.077 | 2.6227 | 2.3151 | 2.0944 | 3.1508 | 3.0521 | 2.9388 | 2.7912 | 2.637 | 2.4595 | 2.2535 | 2.0373 | 1.7689 | 1.3036 | 0.51626 | 0.031516 | -0.17027
BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | OAKRIDGE | MINIMUM HEADROOM | SU 63496 53664 | YES | 27.0266 | 26.6821 | 26.2193 | 25.6422 | 25.076 | 24.4907 | 23.9223 | 23.2736 | 22.254 | 19.2019 | 14.6304 | 11.7419 | 10.4651 | 25.0731 | 24.8316 | 24.4999 | 24.1338 | 23.7644 | 23.3722 | 22.9761 | 22.5115 | 21.8546 | 19.8771 | 17.1681 | 15.3178 | 13.7044 | 28.6336 | 28.3537 | 27.9847 | 27.501 | 27.0242 | 26.5347 | 26.0577 | 25.5217 | 24.6144 | 21.7519 | 17.5884 | 14.8944 | 13.6986
|  | OAKRIDGE | CT |  |  | 27.0266 | 26.6821 | 26.2193 | 25.6422 | 25.076 | 24.4907 | 23.9223 | 23.2736 | 22.254 | 19.2019 | 14.6304 | 11.7419 | 10.4651 | 25.0731 | 24.8316 | 24.4999 | 24.1338 | 23.7644 | 23.3722 | 22.9761 | 22.5115 | 21.8546 | 19.8771 | 17.1681 | 15.3178 | 13.7044 | 28.6336 | 28.3537 | 27.9847 | 27.501 | 27.0242 | 26.5347 | 26.0577 | 25.5217 | 24.6144 | 21.7519 | 17.5884 | 14.8944 | 13.6986
|  | OAKRIDGE | LW |  |  | 27.0266 | 26.6821 | 26.2193 | 25.6422 | 25.076 | 24.4907 | 23.9223 | 23.2736 | 22.254 | 19.2019 | 14.6304 | 11.7419 | 10.4651 | 25.0731 | 24.8316 | 24.4999 | 24.1338 | 23.7644 | 23.3722 | 22.9761 | 22.5115 | 21.8546 | 19.8771 | 17.1681 | 15.3178 | 13.7044 | 28.6336 | 28.3537 | 27.9847 | 27.501 | 27.0242 | 26.5347 | 26.0577 | 25.5217 | 24.6144 | 21.7519 | 17.5884 | 14.8944 | 13.6986
|  | OAKRIDGE | ST |  |  | 27.0266 | 26.6821 | 26.2193 | 25.6422 | 25.076 | 24.4907 | 23.9223 | 23.2736 | 22.254 | 19.2019 | 14.6304 | 11.7419 | 10.4651 | 25.0731 | 24.8316 | 24.4999 | 24.1338 | 23.7644 | 23.3722 | 22.9761 | 22.5115 | 21.8546 | 19.8771 | 17.1681 | 15.3178 | 13.7044 | 28.6336 | 28.3537 | 27.9847 | 27.501 | 27.0242 | 26.5347 | 26.0577 | 25.5217 | 24.6144 | 21.7519 | 17.5884 | 14.8944 | 13.6986
|  | OAKRIDGE | FS |  |  | 27.0266 | 26.6821 | 26.2193 | 25.6422 | 25.076 | 24.4907 | 23.9223 | 23.2736 | 22.254 | 19.2019 | 14.6304 | 11.7419 | 10.4651 | 25.0731 | 24.8316 | 24.4999 | 24.1338 | 23.7644 | 23.3722 | 22.9761 | 22.5115 | 21.8546 | 19.8771 | 17.1681 | 15.3178 | 13.7044 | 28.6336 | 28.3537 | 27.9847 | 27.501 | 27.0242 | 26.5347 | 26.0577 | 25.5217 | 24.6144 | 21.7519 | 17.5884 | 14.8944 | 13.6986
COWLEY GSP | HEADINGTON BSP | OLD ROAD | MINIMUM HEADROOM | SP 55274 06426 | NO | 20.2333 | 19.7377 | 19.155 | 18.479 | 17.8771 | 17.3891 | 16.8731 | 16.2872 | 15.3351 | 12.6048 | 7.818 | 3.8108 | 1.2594 | 18.4477 | 18.079 | 17.6441 | 17.1956 | 16.759 | 16.3971 | 16.0148 | 15.5678 | 14.9184 | 13.037 | 10.1068 | 7.2316 | 4.1064 | 22.6336 | 22.2823 | 21.8779 | 21.4234 | 20.9824 | 20.6572 | 20.3241 | 19.9174 | 19.0361 | 16.4815 | 12.3901 | 9.0065 | 6.8772
|  | OLD ROAD | CT |  |  | 20.2333 | 19.7377 | 19.155 | 18.479 | 17.8771 | 17.3891 | 16.8731 | 16.2872 | 15.3351 | 12.6048 | 7.818 | 3.8108 | 1.2594 | 18.4477 | 18.079 | 17.6441 | 17.1956 | 16.759 | 16.3971 | 16.0148 | 15.5678 | 14.9184 | 13.037 | 10.1068 | 7.2316 | 4.1064 | 22.6336 | 22.2823 | 21.8779 | 21.4234 | 20.9824 | 20.6572 | 20.3241 | 19.9174 | 19.0361 | 16.4815 | 12.3901 | 9.0065 | 6.8772
|  | OLD ROAD | LW |  |  | 20.2333 | 19.7377 | 19.155 | 18.479 | 17.8771 | 17.3891 | 16.8731 | 16.2872 | 15.3351 | 12.6048 | 7.818 | 3.8108 | 1.2594 | 18.4477 | 18.079 | 17.6441 | 17.1956 | 16.759 | 16.3971 | 16.0148 | 15.5678 | 14.9184 | 13.037 | 10.1068 | 7.2316 | 4.1064 | 22.6336 | 22.2823 | 21.8779 | 21.4234 | 20.9824 | 20.6572 | 20.3241 | 19.9174 | 19.0361 | 16.4815 | 12.3901 | 9.0065 | 6.8772
|  | OLD ROAD | ST |  |  | 20.2333 | 19.7377 | 19.155 | 18.479 | 17.8771 | 17.3891 | 16.8731 | 16.2872 | 15.3351 | 12.6048 | 7.818 | 3.8108 | 1.2594 | 18.4477 | 18.079 | 17.6441 | 17.1956 | 16.759 | 16.3971 | 16.0148 | 15.5678 | 14.9184 | 13.037 | 10.1068 | 7.2316 | 4.1064 | 22.6336 | 22.2823 | 21.8779 | 21.4234 | 20.9824 | 20.6572 | 20.3241 | 19.9174 | 19.0361 | 16.4815 | 12.3901 | 9.0065 | 6.8772
|  | OLD ROAD | FS |  |  | 20.2333 | 19.7377 | 19.155 | 18.479 | 17.8771 | 17.3891 | 16.8731 | 16.2872 | 15.3351 | 12.6048 | 7.818 | 3.8108 | 1.2594 | 18.4477 | 18.079 | 17.6441 | 17.1956 | 16.759 | 16.3971 | 16.0148 | 15.5678 | 14.9184 | 13.037 | 10.1068 | 7.2316 | 4.1064 | 22.6336 | 22.2823 | 21.8779 | 21.4234 | 20.9824 | 20.6572 | 20.3241 | 19.9174 | 19.0361 | 16.4815 | 12.3901 | 9.0065 | 6.8772
COWLEY GSP | OXFORD BSP | OXFORD | MINIMUM HEADROOM | SP 50148 05901 | YES | 15.8242 | 15.6761 | 15.5012 | 15.2394 | 14.9006 | 14.5372 | 14.1339 | 13.4307 | 12.6204 | 10.218 | 5.8606 | 3.0382 | 1.4715 | 22.9285 | 22.7701 | 22.5872 | 22.2826 | 21.9043 | 21.5022 | 21.0523 | 20.5353 | 20.0005 | 18.023 | 14.058 | 9.9877 | 4.4528 | 17.09 | 16.9492 | 16.7826 | 16.5403 | 16.2305 | 15.8967 | 15.5266 | 15.0753 | 14.4872 | 12.2874 | 8.3392 | 5.8575 | 4.4957
|  | OXFORD | CT |  |  | 15.8242 | 15.6761 | 15.5012 | 15.2394 | 14.9006 | 14.5372 | 14.1339 | 13.4307 | 12.6204 | 10.218 | 5.8606 | 3.0382 | 1.4715 | 22.9285 | 22.7701 | 22.5872 | 22.2826 | 21.9043 | 21.5022 | 21.0523 | 20.5353 | 20.0005 | 18.023 | 14.058 | 9.9877 | 4.4528 | 17.09 | 16.9492 | 16.7826 | 16.5403 | 16.2305 | 15.8967 | 15.5266 | 15.0753 | 14.4872 | 12.2874 | 8.3392 | 5.8575 | 4.4957
|  | OXFORD | LW |  |  | 15.8242 | 15.6761 | 15.5012 | 15.2394 | 14.9006 | 14.5372 | 14.1339 | 13.4307 | 12.6204 | 10.218 | 5.8606 | 3.0382 | 1.4715 | 22.9285 | 22.7701 | 22.5872 | 22.2826 | 21.9043 | 21.5022 | 21.0523 | 20.5353 | 20.0005 | 18.023 | 14.058 | 9.9877 | 4.4528 | 17.09 | 16.9492 | 16.7826 | 16.5403 | 16.2305 | 15.8967 | 15.5266 | 15.0753 | 14.4872 | 12.2874 | 8.3392 | 5.8575 | 4.4957
|  | OXFORD | ST |  |  | 15.8242 | 15.6761 | 15.5012 | 15.2394 | 14.9006 | 14.5372 | 14.1339 | 13.4307 | 12.6204 | 10.218 | 5.8606 | 3.0382 | 1.4715 | 22.9285 | 22.7701 | 22.5872 | 22.2826 | 21.9043 | 21.5022 | 21.0523 | 20.5353 | 20.0005 | 18.023 | 14.058 | 9.9877 | 4.4528 | 17.09 | 16.9492 | 16.7826 | 16.5403 | 16.2305 | 15.8967 | 15.5266 | 15.0753 | 14.4872 | 12.2874 | 8.3392 | 5.8575 | 4.4957
|  | OXFORD | FS |  |  | 15.8242 | 15.6761 | 15.5012 | 15.2394 | 14.9006 | 14.5372 | 14.1339 | 13.4307 | 12.6204 | 10.218 | 5.8606 | 3.0382 | 1.4715 | 22.9285 | 22.7701 | 22.5872 | 22.2826 | 21.9043 | 21.5022 | 21.0523 | 20.5353 | 20.0005 | 18.023 | 14.058 | 9.9877 | 4.4528 | 17.09 | 16.9492 | 16.7826 | 16.5403 | 16.2305 | 15.8967 | 15.5266 | 15.0753 | 14.4872 | 12.2874 | 8.3392 | 5.8575 | 4.4957
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | OVERTON | MINIMUM HEADROOM | SU 52061 50913 | YES | 18.5209 | 18.3783 | 18.2264 | 17.9894 | 17.743 | 17.4887 | 17.2037 | 16.8883 | 16.3816 | 15.1261 | 12.9041 | 11.3309 | 10.7024 | 24.2241 | 24.187 | 24.1473 | 24.1056 | 24.0602 | 24.01 | 23.9522 | 23.8872 | 23.7964 | 23.5834 | 23.2965 | 23.1976 | 23.1197 | 19.219 | 19.0801 | 18.9293 | 18.7231 | 18.5074 | 18.2801 | 18.017 | 17.715 | 17.2517 | 16.2186 | 14.6185 | 13.3827 | 12.8922
|  | OVERTON | CT |  |  | 18.5209 | 18.3783 | 18.2264 | 17.9894 | 17.743 | 17.4887 | 17.2037 | 16.8883 | 16.3816 | 15.1261 | 12.9041 | 11.3309 | 10.7024 | 24.2241 | 24.187 | 24.1473 | 24.1056 | 24.0602 | 24.01 | 23.9522 | 23.8872 | 23.7964 | 23.5834 | 23.2965 | 23.1976 | 23.1197 | 19.219 | 19.0801 | 18.9293 | 18.7231 | 18.5074 | 18.2801 | 18.017 | 17.715 | 17.2517 | 16.2186 | 14.6185 | 13.3827 | 12.8922
|  | OVERTON | LW |  |  | 18.5209 | 18.3783 | 18.2264 | 17.9894 | 17.743 | 17.4887 | 17.2037 | 16.8883 | 16.3816 | 15.1261 | 12.9041 | 11.3309 | 10.7024 | 24.2241 | 24.187 | 24.1473 | 24.1056 | 24.0602 | 24.01 | 23.9522 | 23.8872 | 23.7964 | 23.5834 | 23.2965 | 23.1976 | 23.1197 | 19.219 | 19.0801 | 18.9293 | 18.7231 | 18.5074 | 18.2801 | 18.017 | 17.715 | 17.2517 | 16.2186 | 14.6185 | 13.3827 | 12.8922
|  | OVERTON | ST |  |  | 18.5209 | 18.3783 | 18.2264 | 17.9894 | 17.743 | 17.4887 | 17.2037 | 16.8883 | 16.3816 | 15.1261 | 12.9041 | 11.3309 | 10.7024 | 24.2241 | 24.187 | 24.1473 | 24.1056 | 24.0602 | 24.01 | 23.9522 | 23.8872 | 23.7964 | 23.5834 | 23.2965 | 23.1976 | 23.1197 | 19.219 | 19.0801 | 18.9293 | 18.7231 | 18.5074 | 18.2801 | 18.017 | 17.715 | 17.2517 | 16.2186 | 14.6185 | 13.3827 | 12.8922
|  | OVERTON | FS |  |  | 18.5209 | 18.3783 | 18.2264 | 17.9894 | 17.743 | 17.4887 | 17.2037 | 16.8883 | 16.3816 | 15.1261 | 12.9041 | 11.3309 | 10.7024 | 24.2241 | 24.187 | 24.1473 | 24.1056 | 24.0602 | 24.01 | 23.9522 | 23.8872 | 23.7964 | 23.5834 | 23.2965 | 23.1976 | 23.1197 | 19.219 | 19.0801 | 18.9293 | 18.7231 | 18.5074 | 18.2801 | 18.017 | 17.715 | 17.2517 | 16.2186 | 14.6185 | 13.3827 | 12.8922
BRAMLEY (FLEE) | BURGHFIELD RESERVE | PADWORTH | MINIMUM HEADROOM | SU 62243 66052 | YES | 1.4824 | 1.429 | 1.3727 | 1.2872 | 1.1989 | 1.109 | 1.0072 | 0.89874 | 0.73675 | 0.36474 | -0.25901 | -0.54554 | -0.61675 | 2.8441 | 2.8085 | 2.7699 | 2.7217 | 2.6714 | 2.6173 | 2.5532 | 2.4824 | 2.3806 | 2.1838 | 1.8847 | 1.7341 | 1.6423 | 2.0456 | 1.9961 | 1.9431 | 1.8695 | 1.7931 | 1.7135 | 1.6209 | 1.5203 | 1.3706 | 1.0612 | 0.55886 | 0.30066 | 0.23688
|  | PADWORTH | CT |  |  | 1.4824 | 1.429 | 1.3727 | 1.2872 | 1.1989 | 1.109 | 1.0072 | 0.89874 | 0.73675 | 0.36474 | -0.25901 | -0.54554 | -0.61675 | 2.8441 | 2.8085 | 2.7699 | 2.7217 | 2.6714 | 2.6173 | 2.5532 | 2.4824 | 2.3806 | 2.1838 | 1.8847 | 1.7341 | 1.6423 | 2.0456 | 1.9961 | 1.9431 | 1.8695 | 1.7931 | 1.7135 | 1.6209 | 1.5203 | 1.3706 | 1.0612 | 0.55886 | 0.30066 | 0.23688
|  | PADWORTH | LW |  |  | 1.4824 | 1.429 | 1.3727 | 1.2872 | 1.1989 | 1.109 | 1.0072 | 0.89874 | 0.73675 | 0.36474 | -0.25901 | -0.54554 | -0.61675 | 2.8441 | 2.8085 | 2.7699 | 2.7217 | 2.6714 | 2.6173 | 2.5532 | 2.4824 | 2.3806 | 2.1838 | 1.8847 | 1.7341 | 1.6423 | 2.0456 | 1.9961 | 1.9431 | 1.8695 | 1.7931 | 1.7135 | 1.6209 | 1.5203 | 1.3706 | 1.0612 | 0.55886 | 0.30066 | 0.23688
|  | PADWORTH | ST |  |  | 1.4824 | 1.429 | 1.3727 | 1.2872 | 1.1989 | 1.109 | 1.0072 | 0.89874 | 0.73675 | 0.36474 | -0.25901 | -0.54554 | -0.61675 | 2.8441 | 2.8085 | 2.7699 | 2.7217 | 2.6714 | 2.6173 | 2.5532 | 2.4824 | 2.3806 | 2.1838 | 1.8847 | 1.7341 | 1.6423 | 2.0456 | 1.9961 | 1.9431 | 1.8695 | 1.7931 | 1.7135 | 1.6209 | 1.5203 | 1.3706 | 1.0612 | 0.55886 | 0.30066 | 0.23688
|  | PADWORTH | FS |  |  | 1.4824 | 1.429 | 1.3727 | 1.2872 | 1.1989 | 1.109 | 1.0072 | 0.89874 | 0.73675 | 0.36474 | -0.25901 | -0.54554 | -0.61675 | 2.8441 | 2.8085 | 2.7699 | 2.7217 | 2.6714 | 2.6173 | 2.5532 | 2.4824 | 2.3806 | 2.1838 | 1.8847 | 1.7341 | 1.6423 | 2.0456 | 1.9961 | 1.9431 | 1.8695 | 1.7931 | 1.7135 | 1.6209 | 1.5203 | 1.3706 | 1.0612 | 0.55886 | 0.30066 | 0.23688
BRAMLEY (FLEE) | BURGHFIELD RESERVE | PANGBOURNE | MINIMUM HEADROOM | SU 62960 76144 | YES | 26.3748 | 26.1401 | 25.9024 | 25.5747 | 25.228 | 24.8478 | 24.4085 | 23.9313 | 23.234 | 21.6523 | 18.8801 | 16.9516 | 16.2277 | 27.1099 | 26.9426 | 26.7712 | 26.5663 | 26.3465 | 26.0963 | 25.8131 | 25.4967 | 25.0681 | 24.197 | 22.8083 | 21.8493 | 21.2211 | 28.5059 | 28.2772 | 28.0454 | 27.7244 | 27.3849 | 27.0131 | 26.5999 | 26.1492 | 25.4955 | 24.047 | 21.5657 | 19.9566 | 19.3792
|  | PANGBOURNE | CT |  |  | 26.3748 | 26.1401 | 25.9024 | 25.5747 | 25.228 | 24.8478 | 24.4085 | 23.9313 | 23.234 | 21.6523 | 18.8801 | 16.9516 | 16.2277 | 27.1099 | 26.9426 | 26.7712 | 26.5663 | 26.3465 | 26.0963 | 25.8131 | 25.4967 | 25.0681 | 24.197 | 22.8083 | 21.8493 | 21.2211 | 28.5059 | 28.2772 | 28.0454 | 27.7244 | 27.3849 | 27.0131 | 26.5999 | 26.1492 | 25.4955 | 24.047 | 21.5657 | 19.9566 | 19.3792
|  | PANGBOURNE | LW |  |  | 26.3748 | 26.1401 | 25.9024 | 25.5747 | 25.228 | 24.8478 | 24.4085 | 23.9313 | 23.234 | 21.6523 | 18.8801 | 16.9516 | 16.2277 | 27.1099 | 26.9426 | 26.7712 | 26.5663 | 26.3465 | 26.0963 | 25.8131 | 25.4967 | 25.0681 | 24.197 | 22.8083 | 21.8493 | 21.2211 | 28.5059 | 28.2772 | 28.0454 | 27.7244 | 27.3849 | 27.0131 | 26.5999 | 26.1492 | 25.4955 | 24.047 | 21.5657 | 19.9566 | 19.3792
|  | PANGBOURNE | ST |  |  | 26.3748 | 26.1401 | 25.9024 | 25.5747 | 25.228 | 24.8478 | 24.4085 | 23.9313 | 23.234 | 21.6523 | 18.8801 | 16.9516 | 16.2277 | 27.1099 | 26.9426 | 26.7712 | 26.5663 | 26.3465 | 26.0963 | 25.8131 | 25.4967 | 25.0681 | 24.197 | 22.8083 | 21.8493 | 21.2211 | 28.5059 | 28.2772 | 28.0454 | 27.7244 | 27.3849 | 27.0131 | 26.5999 | 26.1492 | 25.4955 | 24.047 | 21.5657 | 19.9566 | 19.3792
|  | PANGBOURNE | FS |  |  | 26.3748 | 26.1401 | 25.9024 | 25.5747 | 25.228 | 24.8478 | 24.4085 | 23.9313 | 23.234 | 21.6523 | 18.8801 | 16.9516 | 16.2277 | 27.1099 | 26.9426 | 26.7712 | 26.5663 | 26.3465 | 26.0963 | 25.8131 | 25.4967 | 25.0681 | 24.197 | 22.8083 | 21.8493 | 21.2211 | 28.5059 | 28.2772 | 28.0454 | 27.7244 | 27.3849 | 27.0131 | 26.5999 | 26.1492 | 25.4955 | 24.047 | 21.5657 | 19.9566 | 19.3792
BOTLEY WOOD GSP | BOTLEY WOOD BSP | PARK GATE | MINIMUM HEADROOM | SU 51369 08259 | NO | 22.9311 | 22.6003 | 22.1986 | 21.6716 | 21.1077 | 20.4542 | 19.6874 | 18.7855 | 17.374 | 14.2131 | 9.733 | 6.642 | 5.0319 | 22.2004 | 21.9538 | 21.6355 | 21.2781 | 20.8922 | 20.441 | 19.9074 | 19.2656 | 18.3216 | 16.376 | 13.8201 | 11.8643 | 10.0772 | 25.5383 | 25.2473 | 24.8919 | 24.394 | 23.8608 | 23.2491 | 22.5307 | 21.6796 | 20.3514 | 17.4613 | 13.4679 | 10.7742 | 9.4103
|  | PARK GATE | CT |  |  | 22.9311 | 22.6003 | 22.1986 | 21.6716 | 21.1077 | 20.4542 | 19.6874 | 18.7855 | 17.374 | 14.2131 | 9.733 | 6.642 | 5.0319 | 22.2004 | 21.9538 | 21.6355 | 21.2781 | 20.8922 | 20.441 | 19.9074 | 19.2656 | 18.3216 | 16.376 | 13.8201 | 11.8643 | 10.0772 | 25.5383 | 25.2473 | 24.8919 | 24.394 | 23.8608 | 23.2491 | 22.5307 | 21.6796 | 20.3514 | 17.4613 | 13.4679 | 10.7742 | 9.4103
|  | PARK GATE | LW |  |  | 22.9311 | 22.6003 | 22.1986 | 21.6716 | 21.1077 | 20.4542 | 19.6874 | 18.7855 | 17.374 | 14.2131 | 9.733 | 6.642 | 5.0319 | 22.2004 | 21.9538 | 21.6355 | 21.2781 | 20.8922 | 20.441 | 19.9074 | 19.2656 | 18.3216 | 16.376 | 13.8201 | 11.8643 | 10.0772 | 25.5383 | 25.2473 | 24.8919 | 24.394 | 23.8608 | 23.2491 | 22.5307 | 21.6796 | 20.3514 | 17.4613 | 13.4679 | 10.7742 | 9.4103
|  | PARK GATE | ST |  |  | 22.9311 | 22.6003 | 22.1986 | 21.6716 | 21.1077 | 20.4542 | 19.6874 | 18.7855 | 17.374 | 14.2131 | 9.733 | 6.642 | 5.0319 | 22.2004 | 21.9538 | 21.6355 | 21.2781 | 20.8922 | 20.441 | 19.9074 | 19.2656 | 18.3216 | 16.376 | 13.8201 | 11.8643 | 10.0772 | 25.5383 | 25.2473 | 24.8919 | 24.394 | 23.8608 | 23.2491 | 22.5307 | 21.6796 | 20.3514 | 17.4613 | 13.4679 | 10.7742 | 9.4103
|  | PARK GATE | FS |  |  | 22.9311 | 22.6003 | 22.1986 | 21.6716 | 21.1077 | 20.4542 | 19.6874 | 18.7855 | 17.374 | 14.2131 | 9.733 | 6.642 | 5.0319 | 22.2004 | 21.9538 | 21.6355 | 21.2781 | 20.8922 | 20.441 | 19.9074 | 19.2656 | 18.3216 | 16.376 | 13.8201 | 11.8643 | 10.0772 | 25.5383 | 25.2473 | 24.8919 | 24.394 | 23.8608 | 23.2491 | 22.5307 | 21.6796 | 20.3514 | 17.4613 | 13.4679 | 10.7742 | 9.4103
MELKSHAM GSP | AMESBURY | PARK HOUSE | MINIMUM HEADROOM | SU 23138 43780 | YES | 1.6938 | 1.6381 | 1.5696 | 1.4798 | 1.3851 | 1.2862 | 1.1742 | 1.0356 | 0.86805 | 0.54256 | 0.11644 | -0.10564 | -0.19722 | 3.644 | 3.6097 | 3.5661 | 3.5149 | 3.4602 | 3.4026 | 3.336 | 3.2494 | 3.1371 | 2.9434 | 2.7118 | 2.5825 | 2.4848 | 3.4075 | 3.3548 | 3.2895 | 3.2057 | 3.1171 | 3.0245 | 2.919 | 2.7871 | 2.6271 | 2.3246 | 1.9394 | 1.7439 | 1.6647
|  | PARK HOUSE | CT |  |  | 1.6938 | 1.6381 | 1.5696 | 1.4798 | 1.3851 | 1.2862 | 1.1742 | 1.0356 | 0.86805 | 0.54256 | 0.11644 | -0.10564 | -0.19722 | 3.644 | 3.6097 | 3.5661 | 3.5149 | 3.4602 | 3.4026 | 3.336 | 3.2494 | 3.1371 | 2.9434 | 2.7118 | 2.5825 | 2.4848 | 3.4075 | 3.3548 | 3.2895 | 3.2057 | 3.1171 | 3.0245 | 2.919 | 2.7871 | 2.6271 | 2.3246 | 1.9394 | 1.7439 | 1.6647
|  | PARK HOUSE | LW |  |  | 1.6938 | 1.6381 | 1.5696 | 1.4798 | 1.3851 | 1.2862 | 1.1742 | 1.0356 | 0.86805 | 0.54256 | 0.11644 | -0.10564 | -0.19722 | 3.644 | 3.6097 | 3.5661 | 3.5149 | 3.4602 | 3.4026 | 3.336 | 3.2494 | 3.1371 | 2.9434 | 2.7118 | 2.5825 | 2.4848 | 3.4075 | 3.3548 | 3.2895 | 3.2057 | 3.1171 | 3.0245 | 2.919 | 2.7871 | 2.6271 | 2.3246 | 1.9394 | 1.7439 | 1.6647
|  | PARK HOUSE | ST |  |  | 1.6938 | 1.6381 | 1.5696 | 1.4798 | 1.3851 | 1.2862 | 1.1742 | 1.0356 | 0.86805 | 0.54256 | 0.11644 | -0.10564 | -0.19722 | 3.644 | 3.6097 | 3.5661 | 3.5149 | 3.4602 | 3.4026 | 3.336 | 3.2494 | 3.1371 | 2.9434 | 2.7118 | 2.5825 | 2.4848 | 3.4075 | 3.3548 | 3.2895 | 3.2057 | 3.1171 | 3.0245 | 2.919 | 2.7871 | 2.6271 | 2.3246 | 1.9394 | 1.7439 | 1.6647
|  | PARK HOUSE | FS |  |  | 1.6938 | 1.6381 | 1.5696 | 1.4798 | 1.3851 | 1.2862 | 1.1742 | 1.0356 | 0.86805 | 0.54256 | 0.11644 | -0.10564 | -0.19722 | 3.644 | 3.6097 | 3.5661 | 3.5149 | 3.4602 | 3.4026 | 3.336 | 3.2494 | 3.1371 | 2.9434 | 2.7118 | 2.5825 | 2.4848 | 3.4075 | 3.3548 | 3.2895 | 3.2057 | 3.1171 | 3.0245 | 2.919 | 2.7871 | 2.6271 | 2.3246 | 1.9394 | 1.7439 | 1.6647
MINETY GSP | STRATTON (2 X 90) | PARK NORTH | MINIMUM HEADROOM | SU 18052 84542 | YES | 19.9473 | 19.6737 | 19.2459 | 18.6484 | 17.9905 | 17.2819 | 16.5149 | 15.638 | 14.204 | 9.9412 | 2.6566 | -2.4715 | -5.2253 | 19.4347 | 19.2158 | 18.8523 | 18.4297 | 17.9639 | 17.4568 | 16.8978 | 16.2386 | 15.2431 | 12.4117 | 8.2288 | 4.9565 | 1.7802 | 21.4219 | 21.1666 | 20.7586 | 20.2042 | 19.5961 | 18.9371 | 18.221 | 17.3961 | 16.0633 | 11.9512 | 5.6332 | 1.2133 | -1.1099
|  | PARK NORTH | CT |  |  | 19.9473 | 19.6737 | 19.2459 | 18.6484 | 17.9905 | 17.2819 | 16.5149 | 15.638 | 14.204 | 9.9412 | 2.6566 | -2.4715 | -5.2253 | 19.4347 | 19.2158 | 18.8523 | 18.4297 | 17.9639 | 17.4568 | 16.8978 | 16.2386 | 15.2431 | 12.4117 | 8.2288 | 4.9565 | 1.7802 | 21.4219 | 21.1666 | 20.7586 | 20.2042 | 19.5961 | 18.9371 | 18.221 | 17.3961 | 16.0633 | 11.9512 | 5.6332 | 1.2133 | -1.1099
|  | PARK NORTH | LW |  |  | 19.9473 | 19.6737 | 19.2459 | 18.6484 | 17.9905 | 17.2819 | 16.5149 | 15.638 | 14.204 | 9.9412 | 2.6566 | -2.4715 | -5.2253 | 19.4347 | 19.2158 | 18.8523 | 18.4297 | 17.9639 | 17.4568 | 16.8978 | 16.2386 | 15.2431 | 12.4117 | 8.2288 | 4.9565 | 1.7802 | 21.4219 | 21.1666 | 20.7586 | 20.2042 | 19.5961 | 18.9371 | 18.221 | 17.3961 | 16.0633 | 11.9512 | 5.6332 | 1.2133 | -1.1099
|  | PARK NORTH | ST |  |  | 19.9473 | 19.6737 | 19.2459 | 18.6484 | 17.9905 | 17.2819 | 16.5149 | 15.638 | 14.204 | 9.9412 | 2.6566 | -2.4715 | -5.2253 | 19.4347 | 19.2158 | 18.8523 | 18.4297 | 17.9639 | 17.4568 | 16.8978 | 16.2386 | 15.2431 | 12.4117 | 8.2288 | 4.9565 | 1.7802 | 21.4219 | 21.1666 | 20.7586 | 20.2042 | 19.5961 | 18.9371 | 18.221 | 17.3961 | 16.0633 | 11.9512 | 5.6332 | 1.2133 | -1.1099
|  | PARK NORTH | FS |  |  | 19.9473 | 19.6737 | 19.2459 | 18.6484 | 17.9905 | 17.2819 | 16.5149 | 15.638 | 14.204 | 9.9412 | 2.6566 | -2.4715 | -5.2253 | 19.4347 | 19.2158 | 18.8523 | 18.4297 | 17.9639 | 17.4568 | 16.8978 | 16.2386 | 15.2431 | 12.4117 | 8.2288 | 4.9565 | 1.7802 | 21.4219 | 21.1666 | 20.7586 | 20.2042 | 19.5961 | 18.9371 | 18.221 | 17.3961 | 16.0633 | 11.9512 | 5.6332 | 1.2133 | -1.1099
WILLESDEN GSP | ACTON LANE | PARK ROYAL | MINIMUM HEADROOM | TQ 20137 82215 | YES | 6.503 | 6.475 | 6.4427 | 6.4063 | 6.3644 | 6.3177 | 6.2654 | 6.2095 | 6.1353 | 5.8691 | 5.3043 | 4.7232 | 4.2254 | 7.415 | 7.3968 | 7.3756 | 7.3495 | 7.32 | 7.2876 | 7.2516 | 7.2131 | 7.1605 | 6.9757 | 6.5747 | 6.2612 | 5.9908 | 7.8834 | 7.8611 | 7.8353 | 7.8065 | 7.7734 | 7.7366 | 7.6952 | 7.6508 | 7.5926 | 7.2714 | 6.601 | 6.1111 | 5.6811
|  | PARK ROYAL | CT |  |  | 6.503 | 6.475 | 6.4427 | 6.4063 | 6.3644 | 6.3177 | 6.2654 | 6.2095 | 6.1353 | 5.8691 | 5.3043 | 4.7232 | 4.2254 | 7.415 | 7.3968 | 7.3756 | 7.3495 | 7.32 | 7.2876 | 7.2516 | 7.2131 | 7.1605 | 6.9757 | 6.5747 | 6.2612 | 5.9908 | 7.8834 | 7.8611 | 7.8353 | 7.8065 | 7.7734 | 7.7366 | 7.6952 | 7.6508 | 7.5926 | 7.2714 | 6.601 | 6.1111 | 5.6811
|  | PARK ROYAL | LW |  |  | 6.503 | 6.475 | 6.4427 | 6.4063 | 6.3644 | 6.3177 | 6.2654 | 6.2095 | 6.1353 | 5.8691 | 5.3043 | 4.7232 | 4.2254 | 7.415 | 7.3968 | 7.3756 | 7.3495 | 7.32 | 7.2876 | 7.2516 | 7.2131 | 7.1605 | 6.9757 | 6.5747 | 6.2612 | 5.9908 | 7.8834 | 7.8611 | 7.8353 | 7.8065 | 7.7734 | 7.7366 | 7.6952 | 7.6508 | 7.5926 | 7.2714 | 6.601 | 6.1111 | 5.6811
|  | PARK ROYAL | ST |  |  | 6.503 | 6.475 | 6.4427 | 6.4063 | 6.3644 | 6.3177 | 6.2654 | 6.2095 | 6.1353 | 5.8691 | 5.3043 | 4.7232 | 4.2254 | 7.415 | 7.3968 | 7.3756 | 7.3495 | 7.32 | 7.2876 | 7.2516 | 7.2131 | 7.1605 | 6.9757 | 6.5747 | 6.2612 | 5.9908 | 7.8834 | 7.8611 | 7.8353 | 7.8065 | 7.7734 | 7.7366 | 7.6952 | 7.6508 | 7.5926 | 7.2714 | 6.601 | 6.1111 | 5.6811
|  | PARK ROYAL | FS |  |  | 6.503 | 6.475 | 6.4427 | 6.4063 | 6.3644 | 6.3177 | 6.2654 | 6.2095 | 6.1353 | 5.8691 | 5.3043 | 4.7232 | 4.2254 | 7.415 | 7.3968 | 7.3756 | 7.3495 | 7.32 | 7.2876 | 7.2516 | 7.2131 | 7.1605 | 6.9757 | 6.5747 | 6.2612 | 5.9908 | 7.8834 | 7.8611 | 7.8353 | 7.8065 | 7.7734 | 7.7366 | 7.6952 | 7.6508 | 7.5926 | 7.2714 | 6.601 | 6.1111 | 5.6811
MANNINGTON GSP | BOURNEMOUTH | PARKSTONE NORTH | MINIMUM HEADROOM | SZ 03222 92233 | YES | -2.0332 | -2.6996 | -3.322 | -4.5638 | -5.8886 | -7.3124 | -8.8826 | -10.6505 | -13.3743 | -20.7791 | -31.4174 | -39.1436 | -43.2345 | 6.8501 | 6.3372 | 5.7757 | 4.9297 | 3.9992 | 2.9791 | 1.8662 | 0.58801 | -1.1878 | -6.1357 | -13.0483 | -18.9931 | -25.6036 | 1.1887 | 0.56078 | -0.092351 | -1.2487 | -2.485 | -3.7955 | -5.2172 | -6.8218 | -9.2533 | -16.0187 | -25.6115 | -32.3246 | -35.8187
|  | PARKSTONE NORTH | CT |  |  | -2.0332 | -2.6996 | -3.322 | -4.5638 | -5.8886 | -7.3124 | -8.8826 | -10.6505 | -13.3743 | -20.7791 | -31.4174 | -39.1436 | -43.2345 | 6.8501 | 6.3372 | 5.7757 | 4.9297 | 3.9992 | 2.9791 | 1.8662 | 0.58801 | -1.1878 | -6.1357 | -13.0483 | -18.9931 | -25.6036 | 1.1887 | 0.56078 | -0.092351 | -1.2487 | -2.485 | -3.7955 | -5.2172 | -6.8218 | -9.2533 | -16.0187 | -25.6115 | -32.3246 | -35.8187
|  | PARKSTONE NORTH | LW |  |  | -2.0332 | -2.6996 | -3.322 | -4.5638 | -5.8886 | -7.3124 | -8.8826 | -10.6505 | -13.3743 | -20.7791 | -31.4174 | -39.1436 | -43.2345 | 6.8501 | 6.3372 | 5.7757 | 4.9297 | 3.9992 | 2.9791 | 1.8662 | 0.58801 | -1.1878 | -6.1357 | -13.0483 | -18.9931 | -25.6036 | 1.1887 | 0.56078 | -0.092351 | -1.2487 | -2.485 | -3.7955 | -5.2172 | -6.8218 | -9.2533 | -16.0187 | -25.6115 | -32.3246 | -35.8187
|  | PARKSTONE NORTH | ST |  |  | -2.0332 | -2.6996 | -3.322 | -4.5638 | -5.8886 | -7.3124 | -8.8826 | -10.6505 | -13.3743 | -20.7791 | -31.4174 | -39.1436 | -43.2345 | 6.8501 | 6.3372 | 5.7757 | 4.9297 | 3.9992 | 2.9791 | 1.8662 | 0.58801 | -1.1878 | -6.1357 | -13.0483 | -18.9931 | -25.6036 | 1.1887 | 0.56078 | -0.092351 | -1.2487 | -2.485 | -3.7955 | -5.2172 | -6.8218 | -9.2533 | -16.0187 | -25.6115 | -32.3246 | -35.8187
|  | PARKSTONE NORTH | FS |  |  | -2.0332 | -2.6996 | -3.322 | -4.5638 | -5.8886 | -7.3124 | -8.8826 | -10.6505 | -13.3743 | -20.7791 | -31.4174 | -39.1436 | -43.2345 | 6.8501 | 6.3372 | 5.7757 | 4.9297 | 3.9992 | 2.9791 | 1.8662 | 0.58801 | -1.1878 | -6.1357 | -13.0483 | -18.9931 | -25.6036 | 1.1887 | 0.56078 | -0.092351 | -1.2487 | -2.485 | -3.7955 | -5.2172 | -6.8218 | -9.2533 | -16.0187 | -25.6115 | -32.3246 | -35.8187
MANNINGTON GSP | BOURNEMOUTH | PARKSTONE SOUTH | MINIMUM HEADROOM | SZ 04762 89848 | YES | 27.9757 | 27.6053 | 27.1905 | 26.5073 | 25.7951 | 25.0787 | 24.2976 | 23.3513 | 21.9119 | 18.2902 | 12.4323 | 8.5667 | 6.6773 | 25.0603 | 24.7839 | 24.4677 | 24.0549 | 23.6069 | 23.1312 | 22.6078 | 21.952 | 21.0379 | 18.8258 | 15.5946 | 13.6084 | 12.2448 | 29.9887 | 29.6355 | 29.2366 | 28.6278 | 27.9886 | 27.3327 | 26.615 | 25.7314 | 24.4145 | 21.1685 | 16.1824 | 12.8603 | 11.2367
|  | PARKSTONE SOUTH | CT |  |  | 27.9757 | 27.6053 | 27.1905 | 26.5073 | 25.7951 | 25.0787 | 24.2976 | 23.3513 | 21.9119 | 18.2902 | 12.4323 | 8.5667 | 6.6773 | 25.0603 | 24.7839 | 24.4677 | 24.0549 | 23.6069 | 23.1312 | 22.6078 | 21.952 | 21.0379 | 18.8258 | 15.5946 | 13.6084 | 12.2448 | 29.9887 | 29.6355 | 29.2366 | 28.6278 | 27.9886 | 27.3327 | 26.615 | 25.7314 | 24.4145 | 21.1685 | 16.1824 | 12.8603 | 11.2367
|  | PARKSTONE SOUTH | LW |  |  | 27.9757 | 27.6053 | 27.1905 | 26.5073 | 25.7951 | 25.0787 | 24.2976 | 23.3513 | 21.9119 | 18.2902 | 12.4323 | 8.5667 | 6.6773 | 25.0603 | 24.7839 | 24.4677 | 24.0549 | 23.6069 | 23.1312 | 22.6078 | 21.952 | 21.0379 | 18.8258 | 15.5946 | 13.6084 | 12.2448 | 29.9887 | 29.6355 | 29.2366 | 28.6278 | 27.9886 | 27.3327 | 26.615 | 25.7314 | 24.4145 | 21.1685 | 16.1824 | 12.8603 | 11.2367
|  | PARKSTONE SOUTH | ST |  |  | 27.9757 | 27.6053 | 27.1905 | 26.5073 | 25.7951 | 25.0787 | 24.2976 | 23.3513 | 21.9119 | 18.2902 | 12.4323 | 8.5667 | 6.6773 | 25.0603 | 24.7839 | 24.4677 | 24.0549 | 23.6069 | 23.1312 | 22.6078 | 21.952 | 21.0379 | 18.8258 | 15.5946 | 13.6084 | 12.2448 | 29.9887 | 29.6355 | 29.2366 | 28.6278 | 27.9886 | 27.3327 | 26.615 | 25.7314 | 24.4145 | 21.1685 | 16.1824 | 12.8603 | 11.2367
|  | PARKSTONE SOUTH | FS |  |  | 27.9757 | 27.6053 | 27.1905 | 26.5073 | 25.7951 | 25.0787 | 24.2976 | 23.3513 | 21.9119 | 18.2902 | 12.4323 | 8.5667 | 6.6773 | 25.0603 | 24.7839 | 24.4677 | 24.0549 | 23.6069 | 23.1312 | 22.6078 | 21.952 | 21.0379 | 18.8258 | 15.5946 | 13.6084 | 12.2448 | 29.9887 | 29.6355 | 29.2366 | 28.6278 | 27.9886 | 27.3327 | 26.615 | 25.7314 | 24.4145 | 21.1685 | 16.1824 | 12.8603 | 11.2367
BRAMLEY (FLEE) | WOKINGHAM BSP | PEACOCK FARM | MINIMUM HEADROOM | SU 84770 68709 | YES | 13.8069 | 12.838 | 10.924 | 10.7828 | 10.6449 | 10.5144 | 10.3966 | 10.2639 | 10.065 | 9.602 | 8.8337 | 8.2621 | 7.9169 | 14.1755 | 13.0235 | 10.6799 | 10.5819 | 10.4883 | 10.3973 | 10.3103 | 10.2106 | 10.074 | 9.7768 | 9.3371 | 9.0153 | 8.7452 | 13.9458 | 12.7747 | 10.4207 | 10.3124 | 10.2095 | 10.1072 | 10.0069 | 9.8866 | 9.6888 | 9.2483 | 8.5795 | 8.0964 | 7.8083
|  | PEACOCK FARM | CT |  |  | 13.8069 | 12.838 | 10.924 | 10.7828 | 10.6449 | 10.5144 | 10.3966 | 10.2639 | 10.065 | 9.602 | 8.8337 | 8.2621 | 7.9169 | 14.1755 | 13.0235 | 10.6799 | 10.5819 | 10.4883 | 10.3973 | 10.3103 | 10.2106 | 10.074 | 9.7768 | 9.3371 | 9.0153 | 8.7452 | 13.9458 | 12.7747 | 10.4207 | 10.3124 | 10.2095 | 10.1072 | 10.0069 | 9.8866 | 9.6888 | 9.2483 | 8.5795 | 8.0964 | 7.8083
|  | PEACOCK FARM | LW |  |  | 13.8069 | 12.838 | 10.924 | 10.7828 | 10.6449 | 10.5144 | 10.3966 | 10.2639 | 10.065 | 9.602 | 8.8337 | 8.2621 | 7.9169 | 14.1755 | 13.0235 | 10.6799 | 10.5819 | 10.4883 | 10.3973 | 10.3103 | 10.2106 | 10.074 | 9.7768 | 9.3371 | 9.0153 | 8.7452 | 13.9458 | 12.7747 | 10.4207 | 10.3124 | 10.2095 | 10.1072 | 10.0069 | 9.8866 | 9.6888 | 9.2483 | 8.5795 | 8.0964 | 7.8083
|  | PEACOCK FARM | ST |  |  | 13.8069 | 12.838 | 10.924 | 10.7828 | 10.6449 | 10.5144 | 10.3966 | 10.2639 | 10.065 | 9.602 | 8.8337 | 8.2621 | 7.9169 | 14.1755 | 13.0235 | 10.6799 | 10.5819 | 10.4883 | 10.3973 | 10.3103 | 10.2106 | 10.074 | 9.7768 | 9.3371 | 9.0153 | 8.7452 | 13.9458 | 12.7747 | 10.4207 | 10.3124 | 10.2095 | 10.1072 | 10.0069 | 9.8866 | 9.6888 | 9.2483 | 8.5795 | 8.0964 | 7.8083
|  | PEACOCK FARM | FS |  |  | 13.8069 | 12.838 | 10.924 | 10.7828 | 10.6449 | 10.5144 | 10.3966 | 10.2639 | 10.065 | 9.602 | 8.8337 | 8.2621 | 7.9169 | 14.1755 | 13.0235 | 10.6799 | 10.5819 | 10.4883 | 10.3973 | 10.3103 | 10.2106 | 10.074 | 9.7768 | 9.3371 | 9.0153 | 8.7452 | 13.9458 | 12.7747 | 10.4207 | 10.3124 | 10.2095 | 10.1072 | 10.0069 | 9.8866 | 9.6888 | 9.2483 | 8.5795 | 8.0964 | 7.8083
WILLESDEN GSP |  | PERIVALE | MINIMUM HEADROOM | TQ 17544 82947 |  | 58.9852 | 58.7892 | 58.5267 | 58.1348 | 57.7177 | 57.2758 | 56.801 | 56.2509 | 55.3706 | 52.3787 | 46.8006 | 42.6756 | 40.2306 | 63.5988 | 63.4433 | 63.2402 | 62.976 | 62.6912 | 62.3815 | 62.0436 | 61.6418 | 61.0935 | 59.2068 | 55.2515 | 51.3774 | 46.7312 | 61.3159 | 61.1246 | 60.8575 | 60.4778 | 60.0724 | 59.6403 | 59.174 | 58.6299 | 57.7815 | 54.9342 | 49.9688 | 46.4395 | 44.3972
|  | PERIVALE | CT |  |  | 58.9852 | 58.7892 | 58.5267 | 58.1348 | 57.7177 | 57.2758 | 56.801 | 56.2509 | 55.3706 | 52.3787 | 46.8006 | 42.6756 | 40.2306 | 63.5988 | 63.4433 | 63.2402 | 62.976 | 62.6912 | 62.3815 | 62.0436 | 61.6418 | 61.0935 | 59.2068 | 55.2515 | 51.3774 | 46.7312 | 61.3159 | 61.1246 | 60.8575 | 60.4778 | 60.0724 | 59.6403 | 59.174 | 58.6299 | 57.7815 | 54.9342 | 49.9688 | 46.4395 | 44.3972
|  | PERIVALE | LW |  |  | 58.9852 | 58.7892 | 58.5267 | 58.1348 | 57.7177 | 57.2758 | 56.801 | 56.2509 | 55.3706 | 52.3787 | 46.8006 | 42.6756 | 40.2306 | 63.5988 | 63.4433 | 63.2402 | 62.976 | 62.6912 | 62.3815 | 62.0436 | 61.6418 | 61.0935 | 59.2068 | 55.2515 | 51.3774 | 46.7312 | 61.3159 | 61.1246 | 60.8575 | 60.4778 | 60.0724 | 59.6403 | 59.174 | 58.6299 | 57.7815 | 54.9342 | 49.9688 | 46.4395 | 44.3972
|  | PERIVALE | ST |  |  | 58.9852 | 58.7892 | 58.5267 | 58.1348 | 57.7177 | 57.2758 | 56.801 | 56.2509 | 55.3706 | 52.3787 | 46.8006 | 42.6756 | 40.2306 | 63.5988 | 63.4433 | 63.2402 | 62.976 | 62.6912 | 62.3815 | 62.0436 | 61.6418 | 61.0935 | 59.2068 | 55.2515 | 51.3774 | 46.7312 | 61.3159 | 61.1246 | 60.8575 | 60.4778 | 60.0724 | 59.6403 | 59.174 | 58.6299 | 57.7815 | 54.9342 | 49.9688 | 46.4395 | 44.3972
|  | PERIVALE | FS |  |  | 58.9852 | 58.7892 | 58.5267 | 58.1348 | 57.7177 | 57.2758 | 56.801 | 56.2509 | 55.3706 | 52.3787 | 46.8006 | 42.6756 | 40.2306 | 63.5988 | 63.4433 | 63.2402 | 62.976 | 62.6912 | 62.3815 | 62.0436 | 61.6418 | 61.0935 | 59.2068 | 55.2515 | 51.3774 | 46.7312 | 61.3159 | 61.1246 | 60.8575 | 60.4778 | 60.0724 | 59.6403 | 59.174 | 58.6299 | 57.7815 | 54.9342 | 49.9688 | 46.4395 | 44.3972
BRAMLEY (FLEE) | FERNHURST | PETERSFIELD | MINIMUM HEADROOM | SU 74173 23420 | YES | 16.7619 | 16.2669 | 15.6856 | 14.8668 | 13.9959 | 13.0685 | 12.0224 | 10.8443 | 9.0336 | 4.5325 | -2.4596 | -7.2259 | -9.3189 | 19.6121 | 19.2372 | 18.7894 | 18.2564 | 17.6858 | 17.0595 | 16.3378 | 15.5014 | 14.3139 | 11.4735 | 7.3284 | 4.1777 | 1.1549 | 19.9737 | 19.5146 | 18.9817 | 18.2243 | 17.4266 | 16.5551 | 15.5665 | 14.447 | 12.7396 | 8.553 | 2.1822 | -2.0924 | -3.9322
|  | PETERSFIELD | CT |  |  | 16.7619 | 16.2669 | 15.6856 | 14.8668 | 13.9959 | 13.0685 | 12.0224 | 10.8443 | 9.0336 | 4.5325 | -2.4596 | -7.2259 | -9.3189 | 19.6121 | 19.2372 | 18.7894 | 18.2564 | 17.6858 | 17.0595 | 16.3378 | 15.5014 | 14.3139 | 11.4735 | 7.3284 | 4.1777 | 1.1549 | 19.9737 | 19.5146 | 18.9817 | 18.2243 | 17.4266 | 16.5551 | 15.5665 | 14.447 | 12.7396 | 8.553 | 2.1822 | -2.0924 | -3.9322
|  | PETERSFIELD | LW |  |  | 16.7619 | 16.2669 | 15.6856 | 14.8668 | 13.9959 | 13.0685 | 12.0224 | 10.8443 | 9.0336 | 4.5325 | -2.4596 | -7.2259 | -9.3189 | 19.6121 | 19.2372 | 18.7894 | 18.2564 | 17.6858 | 17.0595 | 16.3378 | 15.5014 | 14.3139 | 11.4735 | 7.3284 | 4.1777 | 1.1549 | 19.9737 | 19.5146 | 18.9817 | 18.2243 | 17.4266 | 16.5551 | 15.5665 | 14.447 | 12.7396 | 8.553 | 2.1822 | -2.0924 | -3.9322
|  | PETERSFIELD | ST |  |  | 16.7619 | 16.2669 | 15.6856 | 14.8668 | 13.9959 | 13.0685 | 12.0224 | 10.8443 | 9.0336 | 4.5325 | -2.4596 | -7.2259 | -9.3189 | 19.6121 | 19.2372 | 18.7894 | 18.2564 | 17.6858 | 17.0595 | 16.3378 | 15.5014 | 14.3139 | 11.4735 | 7.3284 | 4.1777 | 1.1549 | 19.9737 | 19.5146 | 18.9817 | 18.2243 | 17.4266 | 16.5551 | 15.5665 | 14.447 | 12.7396 | 8.553 | 2.1822 | -2.0924 | -3.9322
|  | PETERSFIELD | FS |  |  | 16.7619 | 16.2669 | 15.6856 | 14.8668 | 13.9959 | 13.0685 | 12.0224 | 10.8443 | 9.0336 | 4.5325 | -2.4596 | -7.2259 | -9.3189 | 19.6121 | 19.2372 | 18.7894 | 18.2564 | 17.6858 | 17.0595 | 16.3378 | 15.5014 | 14.3139 | 11.4735 | 7.3284 | 4.1777 | 1.1549 | 19.9737 | 19.5146 | 18.9817 | 18.2243 | 17.4266 | 16.5551 | 15.5665 | 14.447 | 12.7396 | 8.553 | 2.1822 | -2.0924 | -3.9322
IVER 132KV | CHALVEY BSP | PETERSFIELD AVENUE | MINIMUM HEADROOM | SU 98108 80286 | YES | 18.2503 | 17.1785 | 15.8918 | 14.2961 | 12.6542 | 10.9365 | 9.0562 | 7.0779 | 5.03 | 0.041603 | -7.4808 | -12.543 | -15.4743 | 25.6572 | 25.3033 | 24.8507 | 24.3113 | 23.753 | 23.1618 | 22.3732 | 21.2354 | 19.9773 | 16.5999 | 11.3194 | 6.6777 | 1.3195 | 21.5622 | 21.0912 | 20.5692 | 19.9946 | 19.4063 | 17.9578 | 16.3629 | 14.6623 | 12.8702 | 8.4402 | 1.9343 | -2.2613 | -4.6576
|  | PETERSFIELD AVENUE | CT |  |  | 18.2503 | 17.1785 | 15.8918 | 14.2961 | 12.6542 | 10.9365 | 9.0562 | 7.0779 | 5.03 | 0.041603 | -7.4808 | -12.543 | -15.4743 | 25.6572 | 25.3033 | 24.8507 | 24.3113 | 23.753 | 23.1618 | 22.3732 | 21.2354 | 19.9773 | 16.5999 | 11.3194 | 6.6777 | 1.3195 | 21.5622 | 21.0912 | 20.5692 | 19.9946 | 19.4063 | 17.9578 | 16.3629 | 14.6623 | 12.8702 | 8.4402 | 1.9343 | -2.2613 | -4.6576
|  | PETERSFIELD AVENUE | LW |  |  | 18.2503 | 17.1785 | 15.8918 | 14.2961 | 12.6542 | 10.9365 | 9.0562 | 7.0779 | 5.03 | 0.041603 | -7.4808 | -12.543 | -15.4743 | 25.6572 | 25.3033 | 24.8507 | 24.3113 | 23.753 | 23.1618 | 22.3732 | 21.2354 | 19.9773 | 16.5999 | 11.3194 | 6.6777 | 1.3195 | 21.5622 | 21.0912 | 20.5692 | 19.9946 | 19.4063 | 17.9578 | 16.3629 | 14.6623 | 12.8702 | 8.4402 | 1.9343 | -2.2613 | -4.6576
|  | PETERSFIELD AVENUE | ST |  |  | 18.2503 | 17.1785 | 15.8918 | 14.2961 | 12.6542 | 10.9365 | 9.0562 | 7.0779 | 5.03 | 0.041603 | -7.4808 | -12.543 | -15.4743 | 25.6572 | 25.3033 | 24.8507 | 24.3113 | 23.753 | 23.1618 | 22.3732 | 21.2354 | 19.9773 | 16.5999 | 11.3194 | 6.6777 | 1.3195 | 21.5622 | 21.0912 | 20.5692 | 19.9946 | 19.4063 | 17.9578 | 16.3629 | 14.6623 | 12.8702 | 8.4402 | 1.9343 | -2.2613 | -4.6576
|  | PETERSFIELD AVENUE | FS |  |  | 18.2503 | 17.1785 | 15.8918 | 14.2961 | 12.6542 | 10.9365 | 9.0562 | 7.0779 | 5.03 | 0.041603 | -7.4808 | -12.543 | -15.4743 | 25.6572 | 25.3033 | 24.8507 | 24.3113 | 23.753 | 23.1618 | 22.3732 | 21.2354 | 19.9773 | 16.5999 | 11.3194 | 6.6777 | 1.3195 | 21.5622 | 21.0912 | 20.5692 | 19.9946 | 19.4063 | 17.9578 | 16.3629 | 14.6623 | 12.8702 | 8.4402 | 1.9343 | -2.2613 | -4.6576
MANNINGTON GSP | SALISBURY | PETERSFINGER | MINIMUM HEADROOM | SU 15608 29334 | YES | 9.1115 | 8.848 | 8.5178 | 8.0541 | 7.5631 | 7.0375 | 6.3913 | 5.6496 | 4.5865 | 2.12 | -1.6036 | -4.0362 | -5.0547 | 14.5479 | 14.3385 | 14.0636 | 13.748 | 13.4069 | 13.0305 | 12.5705 | 12.0307 | 11.2934 | 9.682 | 7.4404 | 5.5252 | 3.4153 | 10.8062 | 10.5564 | 10.24 | 9.8084 | 9.3502 | 8.858 | 8.2597 | 7.5726 | 6.5795 | 4.3043 | 0.96348 | -1.1785 | -2.071
|  | PETERSFINGER | CT |  |  | 9.1115 | 8.848 | 8.5178 | 8.0541 | 7.5631 | 7.0375 | 6.3913 | 5.6496 | 4.5865 | 2.12 | -1.6036 | -4.0362 | -5.0547 | 14.5479 | 14.3385 | 14.0636 | 13.748 | 13.4069 | 13.0305 | 12.5705 | 12.0307 | 11.2934 | 9.682 | 7.4404 | 5.5252 | 3.4153 | 10.8062 | 10.5564 | 10.24 | 9.8084 | 9.3502 | 8.858 | 8.2597 | 7.5726 | 6.5795 | 4.3043 | 0.96348 | -1.1785 | -2.071
|  | PETERSFINGER | LW |  |  | 9.1115 | 8.848 | 8.5178 | 8.0541 | 7.5631 | 7.0375 | 6.3913 | 5.6496 | 4.5865 | 2.12 | -1.6036 | -4.0362 | -5.0547 | 14.5479 | 14.3385 | 14.0636 | 13.748 | 13.4069 | 13.0305 | 12.5705 | 12.0307 | 11.2934 | 9.682 | 7.4404 | 5.5252 | 3.4153 | 10.8062 | 10.5564 | 10.24 | 9.8084 | 9.3502 | 8.858 | 8.2597 | 7.5726 | 6.5795 | 4.3043 | 0.96348 | -1.1785 | -2.071
|  | PETERSFINGER | ST |  |  | 9.1115 | 8.848 | 8.5178 | 8.0541 | 7.5631 | 7.0375 | 6.3913 | 5.6496 | 4.5865 | 2.12 | -1.6036 | -4.0362 | -5.0547 | 14.5479 | 14.3385 | 14.0636 | 13.748 | 13.4069 | 13.0305 | 12.5705 | 12.0307 | 11.2934 | 9.682 | 7.4404 | 5.5252 | 3.4153 | 10.8062 | 10.5564 | 10.24 | 9.8084 | 9.3502 | 8.858 | 8.2597 | 7.5726 | 6.5795 | 4.3043 | 0.96348 | -1.1785 | -2.071
|  | PETERSFINGER | FS |  |  | 9.1115 | 8.848 | 8.5178 | 8.0541 | 7.5631 | 7.0375 | 6.3913 | 5.6496 | 4.5865 | 2.12 | -1.6036 | -4.0362 | -5.0547 | 14.5479 | 14.3385 | 14.0636 | 13.748 | 13.4069 | 13.0305 | 12.5705 | 12.0307 | 11.2934 | 9.682 | 7.4404 | 5.5252 | 3.4153 | 10.8062 | 10.5564 | 10.24 | 9.8084 | 9.3502 | 8.858 | 8.2597 | 7.5726 | 6.5795 | 4.3043 | 0.96348 | -1.1785 | -2.071
MELKSHAM GSP | AMESBURY | PEWSEY | MINIMUM HEADROOM | SU 14710 59252 | YES | 8.0484 | 8.015 | 7.8068 | 7.3232 | 6.8224 | 6.2955 | 5.725 | 5.09 | 4.1841 | 2.1089 | 0.86385 | 0.50403 | 0.34568 | 10.7969 | 10.651 | 10.476 | 10.2358 | 9.9849 | 9.7187 | 9.4261 | 9.0575 | 8.5373 | 7.4664 | 6.7367 | 6.4129 | 6.0874 | 9.7234 | 9.6902 | 9.6424 | 9.5973 | 9.311 | 8.8275 | 8.3019 | 7.7121 | 6.87 | 4.9784 | 3.8449 | 3.5213 | 3.3804
|  | PEWSEY | CT |  |  | 8.0484 | 8.015 | 7.8068 | 7.3232 | 6.8224 | 6.2955 | 5.725 | 5.09 | 4.1841 | 2.1089 | 0.86385 | 0.50403 | 0.34568 | 10.7969 | 10.651 | 10.476 | 10.2358 | 9.9849 | 9.7187 | 9.4261 | 9.0575 | 8.5373 | 7.4664 | 6.7367 | 6.4129 | 6.0874 | 9.7234 | 9.6902 | 9.6424 | 9.5973 | 9.311 | 8.8275 | 8.3019 | 7.7121 | 6.87 | 4.9784 | 3.8449 | 3.5213 | 3.3804
|  | PEWSEY | LW |  |  | 8.0484 | 8.015 | 7.8068 | 7.3232 | 6.8224 | 6.2955 | 5.725 | 5.09 | 4.1841 | 2.1089 | 0.86385 | 0.50403 | 0.34568 | 10.7969 | 10.651 | 10.476 | 10.2358 | 9.9849 | 9.7187 | 9.4261 | 9.0575 | 8.5373 | 7.4664 | 6.7367 | 6.4129 | 6.0874 | 9.7234 | 9.6902 | 9.6424 | 9.5973 | 9.311 | 8.8275 | 8.3019 | 7.7121 | 6.87 | 4.9784 | 3.8449 | 3.5213 | 3.3804
|  | PEWSEY | ST |  |  | 8.0484 | 8.015 | 7.8068 | 7.3232 | 6.8224 | 6.2955 | 5.725 | 5.09 | 4.1841 | 2.1089 | 0.86385 | 0.50403 | 0.34568 | 10.7969 | 10.651 | 10.476 | 10.2358 | 9.9849 | 9.7187 | 9.4261 | 9.0575 | 8.5373 | 7.4664 | 6.7367 | 6.4129 | 6.0874 | 9.7234 | 9.6902 | 9.6424 | 9.5973 | 9.311 | 8.8275 | 8.3019 | 7.7121 | 6.87 | 4.9784 | 3.8449 | 3.5213 | 3.3804
|  | PEWSEY | FS |  |  | 8.0484 | 8.015 | 7.8068 | 7.3232 | 6.8224 | 6.2955 | 5.725 | 5.09 | 4.1841 | 2.1089 | 0.86385 | 0.50403 | 0.34568 | 10.7969 | 10.651 | 10.476 | 10.2358 | 9.9849 | 9.7187 | 9.4261 | 9.0575 | 8.5373 | 7.4664 | 6.7367 | 6.4129 | 6.0874 | 9.7234 | 9.6902 | 9.6424 | 9.5973 | 9.311 | 8.8275 | 8.3019 | 7.7121 | 6.87 | 4.9784 | 3.8449 | 3.5213 | 3.3804
CHICKERELL GSP | CHICKERELL BSP | PIDDLETRENTHIDE | MINIMUM HEADROOM | SY 70169 99809 | YES | 4.8418 | 4.7671 | 4.6867 | 4.5568 | 4.4226 | 4.2831 | 4.1354 | 3.9757 | 3.737 | 3.2232 | 2.4238 | 2.2331 | 2.1771 | 6.8266 | 6.786 | 6.7404 | 6.677 | 6.6105 | 6.5404 | 6.4623 | 6.3772 | 6.2603 | 6.0239 | 5.6623 | 5.5474 | 5.4682 | 5.8851 | 5.8114 | 5.7285 | 5.6125 | 5.4909 | 5.3632 | 5.2192 | 5.0615 | 4.8404 | 4.4223 | 3.8204 | 3.6759 | 3.6329
|  | PIDDLETRENTHIDE | CT |  |  | 4.8418 | 4.7671 | 4.6867 | 4.5568 | 4.4226 | 4.2831 | 4.1354 | 3.9757 | 3.737 | 3.2232 | 2.4238 | 2.2331 | 2.1771 | 6.8266 | 6.786 | 6.7404 | 6.677 | 6.6105 | 6.5404 | 6.4623 | 6.3772 | 6.2603 | 6.0239 | 5.6623 | 5.5474 | 5.4682 | 5.8851 | 5.8114 | 5.7285 | 5.6125 | 5.4909 | 5.3632 | 5.2192 | 5.0615 | 4.8404 | 4.4223 | 3.8204 | 3.6759 | 3.6329
|  | PIDDLETRENTHIDE | LW |  |  | 4.8418 | 4.7671 | 4.6867 | 4.5568 | 4.4226 | 4.2831 | 4.1354 | 3.9757 | 3.737 | 3.2232 | 2.4238 | 2.2331 | 2.1771 | 6.8266 | 6.786 | 6.7404 | 6.677 | 6.6105 | 6.5404 | 6.4623 | 6.3772 | 6.2603 | 6.0239 | 5.6623 | 5.5474 | 5.4682 | 5.8851 | 5.8114 | 5.7285 | 5.6125 | 5.4909 | 5.3632 | 5.2192 | 5.0615 | 4.8404 | 4.4223 | 3.8204 | 3.6759 | 3.6329
|  | PIDDLETRENTHIDE | ST |  |  | 4.8418 | 4.7671 | 4.6867 | 4.5568 | 4.4226 | 4.2831 | 4.1354 | 3.9757 | 3.737 | 3.2232 | 2.4238 | 2.2331 | 2.1771 | 6.8266 | 6.786 | 6.7404 | 6.677 | 6.6105 | 6.5404 | 6.4623 | 6.3772 | 6.2603 | 6.0239 | 5.6623 | 5.5474 | 5.4682 | 5.8851 | 5.8114 | 5.7285 | 5.6125 | 5.4909 | 5.3632 | 5.2192 | 5.0615 | 4.8404 | 4.4223 | 3.8204 | 3.6759 | 3.6329
|  | PIDDLETRENTHIDE | FS |  |  | 4.8418 | 4.7671 | 4.6867 | 4.5568 | 4.4226 | 4.2831 | 4.1354 | 3.9757 | 3.737 | 3.2232 | 2.4238 | 2.2331 | 2.1771 | 6.8266 | 6.786 | 6.7404 | 6.677 | 6.6105 | 6.5404 | 6.4623 | 6.3772 | 6.2603 | 6.0239 | 5.6623 | 5.5474 | 5.4682 | 5.8851 | 5.8114 | 5.7285 | 5.6125 | 5.4909 | 5.3632 | 5.2192 | 5.0615 | 4.8404 | 4.4223 | 3.8204 | 3.6759 | 3.6329
BRAMLEY (FLEE) | FERNHURST | PLAISTOW | MINIMUM HEADROOM | TQ 02071 29626 | YES | 14.1278 | 13.951 | 13.7767 | 13.5445 | 13.3022 | 13.0151 | 12.7093 | 12.3986 | 12.0202 | 11.3557 | 10.2519 | 9.5597 | 9.2618 | 14.8109 | 14.6915 | 14.5733 | 14.4412 | 14.3015 | 14.1214 | 13.9274 | 13.7283 | 13.4981 | 13.1755 | 12.6386 | 12.2948 | 12.0257 | 14.8617 | 14.6936 | 14.5281 | 14.3129 | 14.0879 | 13.8178 | 13.5296 | 13.2366 | 12.8813 | 12.2801 | 11.2929 | 10.7196 | 10.4749
|  | PLAISTOW | CT |  |  | 14.1278 | 13.951 | 13.7767 | 13.5445 | 13.3022 | 13.0151 | 12.7093 | 12.3986 | 12.0202 | 11.3557 | 10.2519 | 9.5597 | 9.2618 | 14.8109 | 14.6915 | 14.5733 | 14.4412 | 14.3015 | 14.1214 | 13.9274 | 13.7283 | 13.4981 | 13.1755 | 12.6386 | 12.2948 | 12.0257 | 14.8617 | 14.6936 | 14.5281 | 14.3129 | 14.0879 | 13.8178 | 13.5296 | 13.2366 | 12.8813 | 12.2801 | 11.2929 | 10.7196 | 10.4749
|  | PLAISTOW | LW |  |  | 14.1278 | 13.951 | 13.7767 | 13.5445 | 13.3022 | 13.0151 | 12.7093 | 12.3986 | 12.0202 | 11.3557 | 10.2519 | 9.5597 | 9.2618 | 14.8109 | 14.6915 | 14.5733 | 14.4412 | 14.3015 | 14.1214 | 13.9274 | 13.7283 | 13.4981 | 13.1755 | 12.6386 | 12.2948 | 12.0257 | 14.8617 | 14.6936 | 14.5281 | 14.3129 | 14.0879 | 13.8178 | 13.5296 | 13.2366 | 12.8813 | 12.2801 | 11.2929 | 10.7196 | 10.4749
|  | PLAISTOW | ST |  |  | 14.1278 | 13.951 | 13.7767 | 13.5445 | 13.3022 | 13.0151 | 12.7093 | 12.3986 | 12.0202 | 11.3557 | 10.2519 | 9.5597 | 9.2618 | 14.8109 | 14.6915 | 14.5733 | 14.4412 | 14.3015 | 14.1214 | 13.9274 | 13.7283 | 13.4981 | 13.1755 | 12.6386 | 12.2948 | 12.0257 | 14.8617 | 14.6936 | 14.5281 | 14.3129 | 14.0879 | 13.8178 | 13.5296 | 13.2366 | 12.8813 | 12.2801 | 11.2929 | 10.7196 | 10.4749
|  | PLAISTOW | FS |  |  | 14.1278 | 13.951 | 13.7767 | 13.5445 | 13.3022 | 13.0151 | 12.7093 | 12.3986 | 12.0202 | 11.3557 | 10.2519 | 9.5597 | 9.2618 | 14.8109 | 14.6915 | 14.5733 | 14.4412 | 14.3015 | 14.1214 | 13.9274 | 13.7283 | 13.4981 | 13.1755 | 12.6386 | 12.2948 | 12.0257 | 14.8617 | 14.6936 | 14.5281 | 14.3129 | 14.0879 | 13.8178 | 13.5296 | 13.2366 | 12.8813 | 12.2801 | 11.2929 | 10.7196 | 10.4749
MINETY GSP | STRATTON (2 X 90) | PLESSEY | MINIMUM HEADROOM | SU 16381 86720 | YES | 8.3891 | 8.3029 | 8.1853 | 8.0397 | 7.8796 | 7.5546 | 7.149 | 6.7066 | 5.9884 | 3.7473 | -0.43424 | -3.9297 | -6.0998 | 10.5372 | 10.4441 | 10.2931 | 10.1091 | 9.91 | 9.6885 | 9.4433 | 9.1724 | 8.7532 | 7.4195 | 4.9401 | 2.6434 | 0.44801 | 8.8597 | 8.7427 | 8.5642 | 8.3095 | 8.0367 | 7.7316 | 7.399 | 7.0392 | 6.429 | 4.5005 | 0.72616 | -2.3214 | -4.1371
|  | PLESSEY | CT |  |  | 8.3891 | 8.3029 | 8.1853 | 8.0397 | 7.8796 | 7.5546 | 7.149 | 6.7066 | 5.9884 | 3.7473 | -0.43424 | -3.9297 | -6.0998 | 10.5372 | 10.4441 | 10.2931 | 10.1091 | 9.91 | 9.6885 | 9.4433 | 9.1724 | 8.7532 | 7.4195 | 4.9401 | 2.6434 | 0.44801 | 8.8597 | 8.7427 | 8.5642 | 8.3095 | 8.0367 | 7.7316 | 7.399 | 7.0392 | 6.429 | 4.5005 | 0.72616 | -2.3214 | -4.1371
|  | PLESSEY | LW |  |  | 8.3891 | 8.3029 | 8.1853 | 8.0397 | 7.8796 | 7.5546 | 7.149 | 6.7066 | 5.9884 | 3.7473 | -0.43424 | -3.9297 | -6.0998 | 10.5372 | 10.4441 | 10.2931 | 10.1091 | 9.91 | 9.6885 | 9.4433 | 9.1724 | 8.7532 | 7.4195 | 4.9401 | 2.6434 | 0.44801 | 8.8597 | 8.7427 | 8.5642 | 8.3095 | 8.0367 | 7.7316 | 7.399 | 7.0392 | 6.429 | 4.5005 | 0.72616 | -2.3214 | -4.1371
|  | PLESSEY | ST |  |  | 8.3891 | 8.3029 | 8.1853 | 8.0397 | 7.8796 | 7.5546 | 7.149 | 6.7066 | 5.9884 | 3.7473 | -0.43424 | -3.9297 | -6.0998 | 10.5372 | 10.4441 | 10.2931 | 10.1091 | 9.91 | 9.6885 | 9.4433 | 9.1724 | 8.7532 | 7.4195 | 4.9401 | 2.6434 | 0.44801 | 8.8597 | 8.7427 | 8.5642 | 8.3095 | 8.0367 | 7.7316 | 7.399 | 7.0392 | 6.429 | 4.5005 | 0.72616 | -2.3214 | -4.1371
|  | PLESSEY | FS |  |  | 8.3891 | 8.3029 | 8.1853 | 8.0397 | 7.8796 | 7.5546 | 7.149 | 6.7066 | 5.9884 | 3.7473 | -0.43424 | -3.9297 | -6.0998 | 10.5372 | 10.4441 | 10.2931 | 10.1091 | 9.91 | 9.6885 | 9.4433 | 9.1724 | 8.7532 | 7.4195 | 4.9401 | 2.6434 | 0.44801 | 8.8597 | 8.7427 | 8.5642 | 8.3095 | 8.0367 | 7.7316 | 7.399 | 7.0392 | 6.429 | 4.5005 | 0.72616 | -2.3214 | -4.1371
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | PLESSEY TITCHFIELD | MINIMUM HEADROOM | SU 53390 06922 | YES | 25.1296 | 24.7524 | 24.3384 | 23.8868 | 23.4123 | 22.935 | 22.384 | 21.7331 | 20.7248 | 18.4021 | 14.2343 | 11.1067 | 9.2081 | 24.1284 | 23.9789 | 23.7713 | 23.5165 | 23.2457 | 22.9644 | 22.6288 | 22.1207 | 21.3916 | 19.8878 | 17.5334 | 15.8265 | 14.4204 | 25.7667 | 25.4513 | 25.0454 | 24.6214 | 24.1711 | 23.7073 | 23.1612 | 22.4984 | 21.4891 | 19.3058 | 15.6763 | 13.0881 | 11.537
|  | PLESSEY TITCHFIELD | CT |  |  | 25.1296 | 24.7524 | 24.3384 | 23.8868 | 23.4123 | 22.935 | 22.384 | 21.7331 | 20.7248 | 18.4021 | 14.2343 | 11.1067 | 9.2081 | 24.1284 | 23.9789 | 23.7713 | 23.5165 | 23.2457 | 22.9644 | 22.6288 | 22.1207 | 21.3916 | 19.8878 | 17.5334 | 15.8265 | 14.4204 | 25.7667 | 25.4513 | 25.0454 | 24.6214 | 24.1711 | 23.7073 | 23.1612 | 22.4984 | 21.4891 | 19.3058 | 15.6763 | 13.0881 | 11.537
|  | PLESSEY TITCHFIELD | LW |  |  | 25.1296 | 24.7524 | 24.3384 | 23.8868 | 23.4123 | 22.935 | 22.384 | 21.7331 | 20.7248 | 18.4021 | 14.2343 | 11.1067 | 9.2081 | 24.1284 | 23.9789 | 23.7713 | 23.5165 | 23.2457 | 22.9644 | 22.6288 | 22.1207 | 21.3916 | 19.8878 | 17.5334 | 15.8265 | 14.4204 | 25.7667 | 25.4513 | 25.0454 | 24.6214 | 24.1711 | 23.7073 | 23.1612 | 22.4984 | 21.4891 | 19.3058 | 15.6763 | 13.0881 | 11.537
|  | PLESSEY TITCHFIELD | ST |  |  | 25.1296 | 24.7524 | 24.3384 | 23.8868 | 23.4123 | 22.935 | 22.384 | 21.7331 | 20.7248 | 18.4021 | 14.2343 | 11.1067 | 9.2081 | 24.1284 | 23.9789 | 23.7713 | 23.5165 | 23.2457 | 22.9644 | 22.6288 | 22.1207 | 21.3916 | 19.8878 | 17.5334 | 15.8265 | 14.4204 | 25.7667 | 25.4513 | 25.0454 | 24.6214 | 24.1711 | 23.7073 | 23.1612 | 22.4984 | 21.4891 | 19.3058 | 15.6763 | 13.0881 | 11.537
|  | PLESSEY TITCHFIELD | FS |  |  | 25.1296 | 24.7524 | 24.3384 | 23.8868 | 23.4123 | 22.935 | 22.384 | 21.7331 | 20.7248 | 18.4021 | 14.2343 | 11.1067 | 9.2081 | 24.1284 | 23.9789 | 23.7713 | 23.5165 | 23.2457 | 22.9644 | 22.6288 | 22.1207 | 21.3916 | 19.8878 | 17.5334 | 15.8265 | 14.4204 | 25.7667 | 25.4513 | 25.0454 | 24.6214 | 24.1711 | 23.7073 | 23.1612 | 22.4984 | 21.4891 | 19.3058 | 15.6763 | 13.0881 | 11.537
MANNINGTON GSP | POOLE PS (HAMWORTHY) | POOLE | MINIMUM HEADROOM | SZ 01091 90595 |  | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48
|  | POOLE | CT |  |  | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48
|  | POOLE | LW |  |  | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48
|  | POOLE | ST |  |  | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48
|  | POOLE | FS |  |  | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48
LOVEDEAN GSP | WYMERING BSP | PORTCHESTER | MINIMUM HEADROOM | SU 62043 05575 | YES | 14.4034 | 14.0512 | 13.6298 | 13.0435 | 12.3963 | 11.7046 | 10.9711 | 10.1341 | 8.6824 | 4.6776 | -1.6977 | -6.9339 | -10.1234 | 18.9336 | 18.6892 | 18.3736 | 17.9944 | 17.5167 | 16.9949 | 16.4304 | 15.7691 | 14.7606 | 12.1749 | 8.6099 | 5.5444 | 2.6382 | 16.097 | 15.7544 | 15.3099 | 14.7346 | 14.1006 | 13.4175 | 12.6874 | 11.848 | 10.4172 | 6.6785 | 1.1333 | -3.302 | -5.9781
|  | PORTCHESTER | CT |  |  | 14.4034 | 14.0512 | 13.6298 | 13.0435 | 12.3963 | 11.7046 | 10.9711 | 10.1341 | 8.6824 | 4.6776 | -1.6977 | -6.9339 | -10.1234 | 18.9336 | 18.6892 | 18.3736 | 17.9944 | 17.5167 | 16.9949 | 16.4304 | 15.7691 | 14.7606 | 12.1749 | 8.6099 | 5.5444 | 2.6382 | 16.097 | 15.7544 | 15.3099 | 14.7346 | 14.1006 | 13.4175 | 12.6874 | 11.848 | 10.4172 | 6.6785 | 1.1333 | -3.302 | -5.9781
|  | PORTCHESTER | LW |  |  | 14.4034 | 14.0512 | 13.6298 | 13.0435 | 12.3963 | 11.7046 | 10.9711 | 10.1341 | 8.6824 | 4.6776 | -1.6977 | -6.9339 | -10.1234 | 18.9336 | 18.6892 | 18.3736 | 17.9944 | 17.5167 | 16.9949 | 16.4304 | 15.7691 | 14.7606 | 12.1749 | 8.6099 | 5.5444 | 2.6382 | 16.097 | 15.7544 | 15.3099 | 14.7346 | 14.1006 | 13.4175 | 12.6874 | 11.848 | 10.4172 | 6.6785 | 1.1333 | -3.302 | -5.9781
|  | PORTCHESTER | ST |  |  | 14.4034 | 14.0512 | 13.6298 | 13.0435 | 12.3963 | 11.7046 | 10.9711 | 10.1341 | 8.6824 | 4.6776 | -1.6977 | -6.9339 | -10.1234 | 18.9336 | 18.6892 | 18.3736 | 17.9944 | 17.5167 | 16.9949 | 16.4304 | 15.7691 | 14.7606 | 12.1749 | 8.6099 | 5.5444 | 2.6382 | 16.097 | 15.7544 | 15.3099 | 14.7346 | 14.1006 | 13.4175 | 12.6874 | 11.848 | 10.4172 | 6.6785 | 1.1333 | -3.302 | -5.9781
|  | PORTCHESTER | FS |  |  | 14.4034 | 14.0512 | 13.6298 | 13.0435 | 12.3963 | 11.7046 | 10.9711 | 10.1341 | 8.6824 | 4.6776 | -1.6977 | -6.9339 | -10.1234 | 18.9336 | 18.6892 | 18.3736 | 17.9944 | 17.5167 | 16.9949 | 16.4304 | 15.7691 | 14.7606 | 12.1749 | 8.6099 | 5.5444 | 2.6382 | 16.097 | 15.7544 | 15.3099 | 14.7346 | 14.1006 | 13.4175 | 12.6874 | 11.848 | 10.4172 | 6.6785 | 1.1333 | -3.302 | -5.9781
CHICKERELL GSP | CHICKERELL BSP | PORTLAND | MINIMUM HEADROOM | SY 68307 73941 | YES | 6.507 | 6.2093 | 5.8932 | 5.5038 | 5.0674 | 4.5911 | 4.0759 | 3.5139 | 2.6031 | -0.26784 | -4.694 | -7.8158 | -9.4275 | 9.8882 | 9.7653 | 9.6435 | 9.519 | 9.3766 | 9.2145 | 9.0384 | 8.8327 | 8.5678 | 6.9253 | 4.4403 | 2.6971 | 1.2696 | 7.8435 | 7.5837 | 7.2833 | 6.9176 | 6.5087 | 6.0625 | 5.578 | 5.0458 | 4.1943 | 1.5085 | -2.4935 | -5.1691 | -6.5708
|  | PORTLAND | CT |  |  | 6.507 | 6.2093 | 5.8932 | 5.5038 | 5.0674 | 4.5911 | 4.0759 | 3.5139 | 2.6031 | -0.26784 | -4.694 | -7.8158 | -9.4275 | 9.8882 | 9.7653 | 9.6435 | 9.519 | 9.3766 | 9.2145 | 9.0384 | 8.8327 | 8.5678 | 6.9253 | 4.4403 | 2.6971 | 1.2696 | 7.8435 | 7.5837 | 7.2833 | 6.9176 | 6.5087 | 6.0625 | 5.578 | 5.0458 | 4.1943 | 1.5085 | -2.4935 | -5.1691 | -6.5708
|  | PORTLAND | LW |  |  | 6.507 | 6.2093 | 5.8932 | 5.5038 | 5.0674 | 4.5911 | 4.0759 | 3.5139 | 2.6031 | -0.26784 | -4.694 | -7.8158 | -9.4275 | 9.8882 | 9.7653 | 9.6435 | 9.519 | 9.3766 | 9.2145 | 9.0384 | 8.8327 | 8.5678 | 6.9253 | 4.4403 | 2.6971 | 1.2696 | 7.8435 | 7.5837 | 7.2833 | 6.9176 | 6.5087 | 6.0625 | 5.578 | 5.0458 | 4.1943 | 1.5085 | -2.4935 | -5.1691 | -6.5708
|  | PORTLAND | ST |  |  | 6.507 | 6.2093 | 5.8932 | 5.5038 | 5.0674 | 4.5911 | 4.0759 | 3.5139 | 2.6031 | -0.26784 | -4.694 | -7.8158 | -9.4275 | 9.8882 | 9.7653 | 9.6435 | 9.519 | 9.3766 | 9.2145 | 9.0384 | 8.8327 | 8.5678 | 6.9253 | 4.4403 | 2.6971 | 1.2696 | 7.8435 | 7.5837 | 7.2833 | 6.9176 | 6.5087 | 6.0625 | 5.578 | 5.0458 | 4.1943 | 1.5085 | -2.4935 | -5.1691 | -6.5708
|  | PORTLAND | FS |  |  | 6.507 | 6.2093 | 5.8932 | 5.5038 | 5.0674 | 4.5911 | 4.0759 | 3.5139 | 2.6031 | -0.26784 | -4.694 | -7.8158 | -9.4275 | 9.8882 | 9.7653 | 9.6435 | 9.519 | 9.3766 | 9.2145 | 9.0384 | 8.8327 | 8.5678 | 6.9253 | 4.4403 | 2.6971 | 1.2696 | 7.8435 | 7.5837 | 7.2833 | 6.9176 | 6.5087 | 6.0625 | 5.578 | 5.0458 | 4.1943 | 1.5085 | -2.4935 | -5.1691 | -6.5708
LOVEDEAN GSP | PORTSMOUTH BSP | PORTSMOUTH | MINIMUM HEADROOM | SZ 63405 99685 | YES | 39.1258 | 38.6161 | 37.9055 | 36.7462 | 35.493 | 34.5696 | 33.5769 | 32.1508 | 30.4949 | 24.9343 | 16.2779 | 12.8451 | 10.8871 | 41.7321 | 41.3916 | 40.9341 | 40.2448 | 39.5017 | 38.9076 | 38.2652 | 37.3843 | 36.406 | 33.0639 | 27.233 | 23.0513 | 17.651 | 39.7083 | 39.2908 | 38.7036 | 37.7469 | 36.7097 | 35.9342 | 35.0979 | 33.9037 | 32.5074 | 27.8289 | 20.5527 | 17.648 | 16.0137
|  | PORTSMOUTH | CT |  |  | 39.1258 | 38.6161 | 37.9055 | 36.7462 | 35.493 | 34.5696 | 33.5769 | 32.1508 | 30.4949 | 24.9343 | 16.2779 | 12.8451 | 10.8871 | 41.7321 | 41.3916 | 40.9341 | 40.2448 | 39.5017 | 38.9076 | 38.2652 | 37.3843 | 36.406 | 33.0639 | 27.233 | 23.0513 | 17.651 | 39.7083 | 39.2908 | 38.7036 | 37.7469 | 36.7097 | 35.9342 | 35.0979 | 33.9037 | 32.5074 | 27.8289 | 20.5527 | 17.648 | 16.0137
|  | PORTSMOUTH | LW |  |  | 39.1258 | 38.6161 | 37.9055 | 36.7462 | 35.493 | 34.5696 | 33.5769 | 32.1508 | 30.4949 | 24.9343 | 16.2779 | 12.8451 | 10.8871 | 41.7321 | 41.3916 | 40.9341 | 40.2448 | 39.5017 | 38.9076 | 38.2652 | 37.3843 | 36.406 | 33.0639 | 27.233 | 23.0513 | 17.651 | 39.7083 | 39.2908 | 38.7036 | 37.7469 | 36.7097 | 35.9342 | 35.0979 | 33.9037 | 32.5074 | 27.8289 | 20.5527 | 17.648 | 16.0137
|  | PORTSMOUTH | ST |  |  | 39.1258 | 38.6161 | 37.9055 | 36.7462 | 35.493 | 34.5696 | 33.5769 | 32.1508 | 30.4949 | 24.9343 | 16.2779 | 12.8451 | 10.8871 | 41.7321 | 41.3916 | 40.9341 | 40.2448 | 39.5017 | 38.9076 | 38.2652 | 37.3843 | 36.406 | 33.0639 | 27.233 | 23.0513 | 17.651 | 39.7083 | 39.2908 | 38.7036 | 37.7469 | 36.7097 | 35.9342 | 35.0979 | 33.9037 | 32.5074 | 27.8289 | 20.5527 | 17.648 | 16.0137
|  | PORTSMOUTH | FS |  |  | 39.1258 | 38.6161 | 37.9055 | 36.7462 | 35.493 | 34.5696 | 33.5769 | 32.1508 | 30.4949 | 24.9343 | 16.2779 | 12.8451 | 10.8871 | 41.7321 | 41.3916 | 40.9341 | 40.2448 | 39.5017 | 38.9076 | 38.2652 | 37.3843 | 36.406 | 33.0639 | 27.233 | 23.0513 | 17.651 | 39.7083 | 39.2908 | 38.7036 | 37.7469 | 36.7097 | 35.9342 | 35.0979 | 33.9037 | 32.5074 | 27.8289 | 20.5527 | 17.648 | 16.0137
BRAMLEY (ANDO-THAT) | ANDOVER BSP | PORTWAY | MINIMUM HEADROOM | SU 34402 46001 | YES | 11.0203 | 10.7276 | 10.3719 | 9.9689 | 9.5101 | 9.0087 | 8.4485 | 7.7062 | 6.8263 | 3.9233 | 0.26806 | -1.2307 | -1.8481 | 15.3815 | 15.1195 | 14.7988 | 14.4338 | 14.0162 | 13.5614 | 13.0686 | 12.4791 | 11.6907 | 8.9913 | 6.0839 | 5.4073 | 5.1263 | 13.1316 | 12.8411 | 12.4909 | 12.0363 | 11.5326 | 10.9999 | 10.4251 | 9.7648 | 8.8924 | 5.6984 | 1.6554 | 0.2947 | -0.25721
|  | PORTWAY | CT |  |  | 11.0203 | 10.7276 | 10.3719 | 9.9689 | 9.5101 | 9.0087 | 8.4485 | 7.7062 | 6.8263 | 3.9233 | 0.26806 | -1.2307 | -1.8481 | 15.3815 | 15.1195 | 14.7988 | 14.4338 | 14.0162 | 13.5614 | 13.0686 | 12.4791 | 11.6907 | 8.9913 | 6.0839 | 5.4073 | 5.1263 | 13.1316 | 12.8411 | 12.4909 | 12.0363 | 11.5326 | 10.9999 | 10.4251 | 9.7648 | 8.8924 | 5.6984 | 1.6554 | 0.2947 | -0.25721
|  | PORTWAY | LW |  |  | 11.0203 | 10.7276 | 10.3719 | 9.9689 | 9.5101 | 9.0087 | 8.4485 | 7.7062 | 6.8263 | 3.9233 | 0.26806 | -1.2307 | -1.8481 | 15.3815 | 15.1195 | 14.7988 | 14.4338 | 14.0162 | 13.5614 | 13.0686 | 12.4791 | 11.6907 | 8.9913 | 6.0839 | 5.4073 | 5.1263 | 13.1316 | 12.8411 | 12.4909 | 12.0363 | 11.5326 | 10.9999 | 10.4251 | 9.7648 | 8.8924 | 5.6984 | 1.6554 | 0.2947 | -0.25721
|  | PORTWAY | ST |  |  | 11.0203 | 10.7276 | 10.3719 | 9.9689 | 9.5101 | 9.0087 | 8.4485 | 7.7062 | 6.8263 | 3.9233 | 0.26806 | -1.2307 | -1.8481 | 15.3815 | 15.1195 | 14.7988 | 14.4338 | 14.0162 | 13.5614 | 13.0686 | 12.4791 | 11.6907 | 8.9913 | 6.0839 | 5.4073 | 5.1263 | 13.1316 | 12.8411 | 12.4909 | 12.0363 | 11.5326 | 10.9999 | 10.4251 | 9.7648 | 8.8924 | 5.6984 | 1.6554 | 0.2947 | -0.25721
|  | PORTWAY | FS |  |  | 11.0203 | 10.7276 | 10.3719 | 9.9689 | 9.5101 | 9.0087 | 8.4485 | 7.7062 | 6.8263 | 3.9233 | 0.26806 | -1.2307 | -1.8481 | 15.3815 | 15.1195 | 14.7988 | 14.4338 | 14.0162 | 13.5614 | 13.0686 | 12.4791 | 11.6907 | 8.9913 | 6.0839 | 5.4073 | 5.1263 | 13.1316 | 12.8411 | 12.4909 | 12.0363 | 11.5326 | 10.9999 | 10.4251 | 9.7648 | 8.8924 | 5.6984 | 1.6554 | 0.2947 | -0.25721
IVER 132KV | LONGFORD | POYLE | MINIMUM HEADROOM | TQ 03425 75555 | YES | 7.7222 | 7.4933 | 7.2178 | 6.9071 | 6.5544 | 6.0655 | 5.4326 | 4.7131 | 3.7461 | 0.40834 | -5.4138 | -7.8879 | -9.19 | 11.7926 | 11.6561 | 11.4886 | 11.303 | 11.0215 | 10.6617 | 10.2578 | 9.7846 | 9.1369 | 6.73 | 2.545 | 1.0832 | 0.23289 | 8.7375 | 8.4786 | 8.1055 | 7.6391 | 7.1197 | 6.5492 | 5.9196 | 5.2151 | 4.2409 | 0.90356 | -4.9265 | -7.2215 | -8.4286
|  | POYLE | CT |  |  | 7.7222 | 7.4933 | 7.2178 | 6.9071 | 6.5544 | 6.0655 | 5.4326 | 4.7131 | 3.7461 | 0.40834 | -5.4138 | -7.8879 | -9.19 | 11.7926 | 11.6561 | 11.4886 | 11.303 | 11.0215 | 10.6617 | 10.2578 | 9.7846 | 9.1369 | 6.73 | 2.545 | 1.0832 | 0.23289 | 8.7375 | 8.4786 | 8.1055 | 7.6391 | 7.1197 | 6.5492 | 5.9196 | 5.2151 | 4.2409 | 0.90356 | -4.9265 | -7.2215 | -8.4286
|  | POYLE | LW |  |  | 7.7222 | 7.4933 | 7.2178 | 6.9071 | 6.5544 | 6.0655 | 5.4326 | 4.7131 | 3.7461 | 0.40834 | -5.4138 | -7.8879 | -9.19 | 11.7926 | 11.6561 | 11.4886 | 11.303 | 11.0215 | 10.6617 | 10.2578 | 9.7846 | 9.1369 | 6.73 | 2.545 | 1.0832 | 0.23289 | 8.7375 | 8.4786 | 8.1055 | 7.6391 | 7.1197 | 6.5492 | 5.9196 | 5.2151 | 4.2409 | 0.90356 | -4.9265 | -7.2215 | -8.4286
|  | POYLE | ST |  |  | 7.7222 | 7.4933 | 7.2178 | 6.9071 | 6.5544 | 6.0655 | 5.4326 | 4.7131 | 3.7461 | 0.40834 | -5.4138 | -7.8879 | -9.19 | 11.7926 | 11.6561 | 11.4886 | 11.303 | 11.0215 | 10.6617 | 10.2578 | 9.7846 | 9.1369 | 6.73 | 2.545 | 1.0832 | 0.23289 | 8.7375 | 8.4786 | 8.1055 | 7.6391 | 7.1197 | 6.5492 | 5.9196 | 5.2151 | 4.2409 | 0.90356 | -4.9265 | -7.2215 | -8.4286
|  | POYLE | FS |  |  | 7.7222 | 7.4933 | 7.2178 | 6.9071 | 6.5544 | 6.0655 | 5.4326 | 4.7131 | 3.7461 | 0.40834 | -5.4138 | -7.8879 | -9.19 | 11.7926 | 11.6561 | 11.4886 | 11.303 | 11.0215 | 10.6617 | 10.2578 | 9.7846 | 9.1369 | 6.73 | 2.545 | 1.0832 | 0.23289 | 8.7375 | 8.4786 | 8.1055 | 7.6391 | 7.1197 | 6.5492 | 5.9196 | 5.2151 | 4.2409 | 0.90356 | -4.9265 | -7.2215 | -8.4286
MINETY GSP | STRATTON (2 X 90) | PRESSED STEEL SWINDON | MINIMUM HEADROOM | SU 16963 86368 | YES | 15.0362 | 14.6654 | 14.3269 | 13.864 | 13.3765 | 12.8473 | 12.3575 | 11.7735 | 11.2021 | 8.8122 | 5.1543 | 2.3371 | 0.58719 | 17.7371 | 17.4177 | 17.1126 | 16.6615 | 16.162 | 15.6412 | 15.1305 | 14.5534 | 13.9042 | 11.664 | 9.6041 | 8.1356 | 6.872 | 15.7027 | 15.3328 | 14.941 | 14.3683 | 13.7454 | 13.0934 | 12.4542 | 11.7226 | 10.7756 | 7.7263 | 4.3618 | 1.9044 | 0.42113
|  | PRESSED STEEL SWINDON | CT |  |  | 15.0362 | 14.6654 | 14.3269 | 13.864 | 13.3765 | 12.8473 | 12.3575 | 11.7735 | 11.2021 | 8.8122 | 5.1543 | 2.3371 | 0.58719 | 17.7371 | 17.4177 | 17.1126 | 16.6615 | 16.162 | 15.6412 | 15.1305 | 14.5534 | 13.9042 | 11.664 | 9.6041 | 8.1356 | 6.872 | 15.7027 | 15.3328 | 14.941 | 14.3683 | 13.7454 | 13.0934 | 12.4542 | 11.7226 | 10.7756 | 7.7263 | 4.3618 | 1.9044 | 0.42113
|  | PRESSED STEEL SWINDON | LW |  |  | 15.0362 | 14.6654 | 14.3269 | 13.864 | 13.3765 | 12.8473 | 12.3575 | 11.7735 | 11.2021 | 8.8122 | 5.1543 | 2.3371 | 0.58719 | 17.7371 | 17.4177 | 17.1126 | 16.6615 | 16.162 | 15.6412 | 15.1305 | 14.5534 | 13.9042 | 11.664 | 9.6041 | 8.1356 | 6.872 | 15.7027 | 15.3328 | 14.941 | 14.3683 | 13.7454 | 13.0934 | 12.4542 | 11.7226 | 10.7756 | 7.7263 | 4.3618 | 1.9044 | 0.42113
|  | PRESSED STEEL SWINDON | ST |  |  | 15.0362 | 14.6654 | 14.3269 | 13.864 | 13.3765 | 12.8473 | 12.3575 | 11.7735 | 11.2021 | 8.8122 | 5.1543 | 2.3371 | 0.58719 | 17.7371 | 17.4177 | 17.1126 | 16.6615 | 16.162 | 15.6412 | 15.1305 | 14.5534 | 13.9042 | 11.664 | 9.6041 | 8.1356 | 6.872 | 15.7027 | 15.3328 | 14.941 | 14.3683 | 13.7454 | 13.0934 | 12.4542 | 11.7226 | 10.7756 | 7.7263 | 4.3618 | 1.9044 | 0.42113
|  | PRESSED STEEL SWINDON | FS |  |  | 15.0362 | 14.6654 | 14.3269 | 13.864 | 13.3765 | 12.8473 | 12.3575 | 11.7735 | 11.2021 | 8.8122 | 5.1543 | 2.3371 | 0.58719 | 17.7371 | 17.4177 | 17.1126 | 16.6615 | 16.162 | 15.6412 | 15.1305 | 14.5534 | 13.9042 | 11.664 | 9.6041 | 8.1356 | 6.872 | 15.7027 | 15.3328 | 14.941 | 14.3683 | 13.7454 | 13.0934 | 12.4542 | 11.7226 | 10.7756 | 7.7263 | 4.3618 | 1.9044 | 0.42113
BRAMLEY (FLEE) | FERNHURST | PRESTON CANDOVER | MINIMUM HEADROOM | SU 60879 41131 | YES | 13.517 | 13.0069 | 12.451 | 11.782 | 11.1306 | 10.6106 | 10.0303 | 9.4 | 8.6095 | 6.6655 | 4.8091 | 4.0414 | 3.8663 | 15.9277 | 15.6642 | 15.3608 | 15.0131 | 14.6442 | 14.2959 | 13.8988 | 13.4347 | 12.8594 | 11.462 | 10.3665 | 9.9082 | 9.6418 | 13.8358 | 13.3873 | 12.8978 | 12.3106 | 11.7318 | 11.2531 | 10.7176 | 10.1363 | 9.4031 | 7.631 | 5.9663 | 5.2563 | 5.0926
|  | PRESTON CANDOVER | CT |  |  | 13.517 | 13.0069 | 12.451 | 11.782 | 11.1306 | 10.6106 | 10.0303 | 9.4 | 8.6095 | 6.6655 | 4.8091 | 4.0414 | 3.8663 | 15.9277 | 15.6642 | 15.3608 | 15.0131 | 14.6442 | 14.2959 | 13.8988 | 13.4347 | 12.8594 | 11.462 | 10.3665 | 9.9082 | 9.6418 | 13.8358 | 13.3873 | 12.8978 | 12.3106 | 11.7318 | 11.2531 | 10.7176 | 10.1363 | 9.4031 | 7.631 | 5.9663 | 5.2563 | 5.0926
|  | PRESTON CANDOVER | LW |  |  | 13.517 | 13.0069 | 12.451 | 11.782 | 11.1306 | 10.6106 | 10.0303 | 9.4 | 8.6095 | 6.6655 | 4.8091 | 4.0414 | 3.8663 | 15.9277 | 15.6642 | 15.3608 | 15.0131 | 14.6442 | 14.2959 | 13.8988 | 13.4347 | 12.8594 | 11.462 | 10.3665 | 9.9082 | 9.6418 | 13.8358 | 13.3873 | 12.8978 | 12.3106 | 11.7318 | 11.2531 | 10.7176 | 10.1363 | 9.4031 | 7.631 | 5.9663 | 5.2563 | 5.0926
|  | PRESTON CANDOVER | ST |  |  | 13.517 | 13.0069 | 12.451 | 11.782 | 11.1306 | 10.6106 | 10.0303 | 9.4 | 8.6095 | 6.6655 | 4.8091 | 4.0414 | 3.8663 | 15.9277 | 15.6642 | 15.3608 | 15.0131 | 14.6442 | 14.2959 | 13.8988 | 13.4347 | 12.8594 | 11.462 | 10.3665 | 9.9082 | 9.6418 | 13.8358 | 13.3873 | 12.8978 | 12.3106 | 11.7318 | 11.2531 | 10.7176 | 10.1363 | 9.4031 | 7.631 | 5.9663 | 5.2563 | 5.0926
|  | PRESTON CANDOVER | FS |  |  | 13.517 | 13.0069 | 12.451 | 11.782 | 11.1306 | 10.6106 | 10.0303 | 9.4 | 8.6095 | 6.6655 | 4.8091 | 4.0414 | 3.8663 | 15.9277 | 15.6642 | 15.3608 | 15.0131 | 14.6442 | 14.2959 | 13.8988 | 13.4347 | 12.8594 | 11.462 | 10.3665 | 9.9082 | 9.6418 | 13.8358 | 13.3873 | 12.8978 | 12.3106 | 11.7318 | 11.2531 | 10.7176 | 10.1363 | 9.4031 | 7.631 | 5.9663 | 5.2563 | 5.0926
CHICKERELL GSP | CHICKERELL BSP | PUDDLETOWN | MINIMUM HEADROOM | SY 74226 95039 | YES | 5.3236 | 5.2386 | 5.1459 | 5.0049 | 4.8611 | 4.71 | 4.5453 | 4.3596 | 4.0849 | 3.4524 | 2.4164 | 1.9402 | 1.8754 | 5.6503 | 5.5996 | 5.5425 | 5.4696 | 5.3929 | 5.3101 | 5.2178 | 5.1079 | 4.9516 | 4.6367 | 4.1714 | 3.9389 | 3.8378 | 5.31 | 5.2341 | 5.1517 | 5.0244 | 4.8949 | 4.7589 | 4.6113 | 4.4459 | 4.2007 | 3.6257 | 2.6731 | 2.236 | 2.1772
|  | PUDDLETOWN | CT |  |  | 5.3236 | 5.2386 | 5.1459 | 5.0049 | 4.8611 | 4.71 | 4.5453 | 4.3596 | 4.0849 | 3.4524 | 2.4164 | 1.9402 | 1.8754 | 5.6503 | 5.5996 | 5.5425 | 5.4696 | 5.3929 | 5.3101 | 5.2178 | 5.1079 | 4.9516 | 4.6367 | 4.1714 | 3.9389 | 3.8378 | 5.31 | 5.2341 | 5.1517 | 5.0244 | 4.8949 | 4.7589 | 4.6113 | 4.4459 | 4.2007 | 3.6257 | 2.6731 | 2.236 | 2.1772
|  | PUDDLETOWN | LW |  |  | 5.3236 | 5.2386 | 5.1459 | 5.0049 | 4.8611 | 4.71 | 4.5453 | 4.3596 | 4.0849 | 3.4524 | 2.4164 | 1.9402 | 1.8754 | 5.6503 | 5.5996 | 5.5425 | 5.4696 | 5.3929 | 5.3101 | 5.2178 | 5.1079 | 4.9516 | 4.6367 | 4.1714 | 3.9389 | 3.8378 | 5.31 | 5.2341 | 5.1517 | 5.0244 | 4.8949 | 4.7589 | 4.6113 | 4.4459 | 4.2007 | 3.6257 | 2.6731 | 2.236 | 2.1772
|  | PUDDLETOWN | ST |  |  | 5.3236 | 5.2386 | 5.1459 | 5.0049 | 4.8611 | 4.71 | 4.5453 | 4.3596 | 4.0849 | 3.4524 | 2.4164 | 1.9402 | 1.8754 | 5.6503 | 5.5996 | 5.5425 | 5.4696 | 5.3929 | 5.3101 | 5.2178 | 5.1079 | 4.9516 | 4.6367 | 4.1714 | 3.9389 | 3.8378 | 5.31 | 5.2341 | 5.1517 | 5.0244 | 4.8949 | 4.7589 | 4.6113 | 4.4459 | 4.2007 | 3.6257 | 2.6731 | 2.236 | 2.1772
|  | PUDDLETOWN | FS |  |  | 5.3236 | 5.2386 | 5.1459 | 5.0049 | 4.8611 | 4.71 | 4.5453 | 4.3596 | 4.0849 | 3.4524 | 2.4164 | 1.9402 | 1.8754 | 5.6503 | 5.5996 | 5.5425 | 5.4696 | 5.3929 | 5.3101 | 5.2178 | 5.1079 | 4.9516 | 4.6367 | 4.1714 | 3.9389 | 3.8378 | 5.31 | 5.2341 | 5.1517 | 5.0244 | 4.8949 | 4.7589 | 4.6113 | 4.4459 | 4.2007 | 3.6257 | 2.6731 | 2.236 | 2.1772
AXMINSTER | YEOVIL BSP | PULHAM | MINIMUM HEADROOM | ST 71579 09451 | YES | 4.7895 | 4.687 | 4.5963 | 4.4404 | 4.282 | 4.0337 | 3.7468 | 3.4066 | 2.99 | 2.2384 | 0.95493 | 0.22579 | -0.034258 | 6.5458 | 6.4402 | 6.334 | 6.2083 | 6.081 | 5.9461 | 5.7885 | 5.5986 | 5.3748 | 4.9968 | 4.3563 | 3.9699 | 3.7583 | 6.0542 | 5.9062 | 5.7497 | 5.5413 | 5.3262 | 5.0979 | 4.8357 | 4.5273 | 4.1492 | 3.4434 | 2.2261 | 1.5365 | 1.2913
|  | PULHAM | CT |  |  | 4.7895 | 4.687 | 4.5963 | 4.4404 | 4.282 | 4.0337 | 3.7468 | 3.4066 | 2.99 | 2.2384 | 0.95493 | 0.22579 | -0.034258 | 6.5458 | 6.4402 | 6.334 | 6.2083 | 6.081 | 5.9461 | 5.7885 | 5.5986 | 5.3748 | 4.9968 | 4.3563 | 3.9699 | 3.7583 | 6.0542 | 5.9062 | 5.7497 | 5.5413 | 5.3262 | 5.0979 | 4.8357 | 4.5273 | 4.1492 | 3.4434 | 2.2261 | 1.5365 | 1.2913
|  | PULHAM | LW |  |  | 4.7895 | 4.687 | 4.5963 | 4.4404 | 4.282 | 4.0337 | 3.7468 | 3.4066 | 2.99 | 2.2384 | 0.95493 | 0.22579 | -0.034258 | 6.5458 | 6.4402 | 6.334 | 6.2083 | 6.081 | 5.9461 | 5.7885 | 5.5986 | 5.3748 | 4.9968 | 4.3563 | 3.9699 | 3.7583 | 6.0542 | 5.9062 | 5.7497 | 5.5413 | 5.3262 | 5.0979 | 4.8357 | 4.5273 | 4.1492 | 3.4434 | 2.2261 | 1.5365 | 1.2913
|  | PULHAM | ST |  |  | 4.7895 | 4.687 | 4.5963 | 4.4404 | 4.282 | 4.0337 | 3.7468 | 3.4066 | 2.99 | 2.2384 | 0.95493 | 0.22579 | -0.034258 | 6.5458 | 6.4402 | 6.334 | 6.2083 | 6.081 | 5.9461 | 5.7885 | 5.5986 | 5.3748 | 4.9968 | 4.3563 | 3.9699 | 3.7583 | 6.0542 | 5.9062 | 5.7497 | 5.5413 | 5.3262 | 5.0979 | 4.8357 | 4.5273 | 4.1492 | 3.4434 | 2.2261 | 1.5365 | 1.2913
|  | PULHAM | FS |  |  | 4.7895 | 4.687 | 4.5963 | 4.4404 | 4.282 | 4.0337 | 3.7468 | 3.4066 | 2.99 | 2.2384 | 0.95493 | 0.22579 | -0.034258 | 6.5458 | 6.4402 | 6.334 | 6.2083 | 6.081 | 5.9461 | 5.7885 | 5.5986 | 5.3748 | 4.9968 | 4.3563 | 3.9699 | 3.7583 | 6.0542 | 5.9062 | 5.7497 | 5.5413 | 5.3262 | 5.0979 | 4.8357 | 4.5273 | 4.1492 | 3.4434 | 2.2261 | 1.5365 | 1.2913
LOVEDEAN GSP | FORT WIDLEY | PURBROOK | MINIMUM HEADROOM | SU 67047 07819 | YES | 17.5239 | 17.2534 | 16.8862 | 16.4436 | 15.8927 | 15.3136 | 14.6774 | 14.0133 | 13.0309 | 10.5613 | 6.7911 | 3.6888 | 1.672 | 13.3161 | 13.1575 | 12.9425 | 12.6969 | 12.3939 | 12.0733 | 11.7112 | 11.3044 | 10.718 | 9.2918 | 7.2205 | 5.3504 | 3.6069 | 9.7323 | 9.6269 | 9.5014 | 9.3428 | 9.1421 | 8.8372 | 8.5028 | 8.1734 | 7.6661 | 5.488 | 2.2082 | -0.39174 | -2.0216
|  | PURBROOK | CT |  |  | 17.5239 | 17.2534 | 16.8862 | 16.4436 | 15.8927 | 15.3136 | 14.6774 | 14.0133 | 13.0309 | 10.5613 | 6.7911 | 3.6888 | 1.672 | 13.3161 | 13.1575 | 12.9425 | 12.6969 | 12.3939 | 12.0733 | 11.7112 | 11.3044 | 10.718 | 9.2918 | 7.2205 | 5.3504 | 3.6069 | 9.7323 | 9.6269 | 9.5014 | 9.3428 | 9.1421 | 8.8372 | 8.5028 | 8.1734 | 7.6661 | 5.488 | 2.2082 | -0.39174 | -2.0216
|  | PURBROOK | LW |  |  | 17.5239 | 17.2534 | 16.8862 | 16.4436 | 15.8927 | 15.3136 | 14.6774 | 14.0133 | 13.0309 | 10.5613 | 6.7911 | 3.6888 | 1.672 | 13.3161 | 13.1575 | 12.9425 | 12.6969 | 12.3939 | 12.0733 | 11.7112 | 11.3044 | 10.718 | 9.2918 | 7.2205 | 5.3504 | 3.6069 | 9.7323 | 9.6269 | 9.5014 | 9.3428 | 9.1421 | 8.8372 | 8.5028 | 8.1734 | 7.6661 | 5.488 | 2.2082 | -0.39174 | -2.0216
|  | PURBROOK | ST |  |  | 17.5239 | 17.2534 | 16.8862 | 16.4436 | 15.8927 | 15.3136 | 14.6774 | 14.0133 | 13.0309 | 10.5613 | 6.7911 | 3.6888 | 1.672 | 13.3161 | 13.1575 | 12.9425 | 12.6969 | 12.3939 | 12.0733 | 11.7112 | 11.3044 | 10.718 | 9.2918 | 7.2205 | 5.3504 | 3.6069 | 9.7323 | 9.6269 | 9.5014 | 9.3428 | 9.1421 | 8.8372 | 8.5028 | 8.1734 | 7.6661 | 5.488 | 2.2082 | -0.39174 | -2.0216
|  | PURBROOK | FS |  |  | 17.5239 | 17.2534 | 16.8862 | 16.4436 | 15.8927 | 15.3136 | 14.6774 | 14.0133 | 13.0309 | 10.5613 | 6.7911 | 3.6888 | 1.672 | 13.3161 | 13.1575 | 12.9425 | 12.6969 | 12.3939 | 12.0733 | 11.7112 | 11.3044 | 10.718 | 9.2918 | 7.2205 | 5.3504 | 3.6069 | 9.7323 | 9.6269 | 9.5014 | 9.3428 | 9.1421 | 8.8372 | 8.5028 | 8.1734 | 7.6661 | 5.488 | 2.2082 | -0.39174 | -2.0216
BRAMLEY (FLEE) | PYESTOCK BSP | PYESTOCK | MINIMUM HEADROOM | SU 82940 54553 |  | 30.618 | 30.618 | 30.618 | 30.618 | 30.618 | 30.618 | 30.618 | 30.618 | 30.618 | 30.618 | 30.618 | 30.618 | 30.618 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2
|  | PYESTOCK | CT |  |  | 30.618 | 30.618 | 30.618 | 30.618 | 30.618 | 30.618 | 30.618 | 30.618 | 30.618 | 30.618 | 30.618 | 30.618 | 30.618 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2
|  | PYESTOCK | LW |  |  | 30.618 | 30.618 | 30.618 | 30.618 | 30.618 | 30.618 | 30.618 | 30.618 | 30.618 | 30.618 | 30.618 | 30.618 | 30.618 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2
|  | PYESTOCK | ST |  |  | 30.618 | 30.618 | 30.618 | 30.618 | 30.618 | 30.618 | 30.618 | 30.618 | 30.618 | 30.618 | 30.618 | 30.618 | 30.618 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2
|  | PYESTOCK | FS |  |  | 30.618 | 30.618 | 30.618 | 30.618 | 30.618 | 30.618 | 30.618 | 30.618 | 30.618 | 30.618 | 30.618 | 30.618 | 30.618 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2
MINETY GSP | TOOTHILL BSP | QUARRY ROAD | MINIMUM HEADROOM | SU 15334 83380 | YES | 11.2242 | 10.7171 | 10.0903 | 9.308 | 8.4915 | 7.6489 | 6.7271 | 5.7061 | 4.4102 | 0.53947 | -5.4956 | -9.6901 | -12.2095 | 15.4627 | 15.0803 | 14.6282 | 14.0818 | 13.5215 | 12.9231 | 12.2755 | 11.5581 | 10.6914 | 8.0396 | 3.8984 | 0.34798 | -3.5624 | 12.3108 | 11.8347 | 11.2592 | 10.532 | 9.7798 | 8.9918 | 8.1409 | 7.1926 | 5.9835 | 2.3677 | -3.05 | -6.6604 | -8.7814
|  | QUARRY ROAD | CT |  |  | 11.2242 | 10.7171 | 10.0903 | 9.308 | 8.4915 | 7.6489 | 6.7271 | 5.7061 | 4.4102 | 0.53947 | -5.4956 | -9.6901 | -12.2095 | 15.4627 | 15.0803 | 14.6282 | 14.0818 | 13.5215 | 12.9231 | 12.2755 | 11.5581 | 10.6914 | 8.0396 | 3.8984 | 0.34798 | -3.5624 | 12.3108 | 11.8347 | 11.2592 | 10.532 | 9.7798 | 8.9918 | 8.1409 | 7.1926 | 5.9835 | 2.3677 | -3.05 | -6.6604 | -8.7814
|  | QUARRY ROAD | LW |  |  | 11.2242 | 10.7171 | 10.0903 | 9.308 | 8.4915 | 7.6489 | 6.7271 | 5.7061 | 4.4102 | 0.53947 | -5.4956 | -9.6901 | -12.2095 | 15.4627 | 15.0803 | 14.6282 | 14.0818 | 13.5215 | 12.9231 | 12.2755 | 11.5581 | 10.6914 | 8.0396 | 3.8984 | 0.34798 | -3.5624 | 12.3108 | 11.8347 | 11.2592 | 10.532 | 9.7798 | 8.9918 | 8.1409 | 7.1926 | 5.9835 | 2.3677 | -3.05 | -6.6604 | -8.7814
|  | QUARRY ROAD | ST |  |  | 11.2242 | 10.7171 | 10.0903 | 9.308 | 8.4915 | 7.6489 | 6.7271 | 5.7061 | 4.4102 | 0.53947 | -5.4956 | -9.6901 | -12.2095 | 15.4627 | 15.0803 | 14.6282 | 14.0818 | 13.5215 | 12.9231 | 12.2755 | 11.5581 | 10.6914 | 8.0396 | 3.8984 | 0.34798 | -3.5624 | 12.3108 | 11.8347 | 11.2592 | 10.532 | 9.7798 | 8.9918 | 8.1409 | 7.1926 | 5.9835 | 2.3677 | -3.05 | -6.6604 | -8.7814
|  | QUARRY ROAD | FS |  |  | 11.2242 | 10.7171 | 10.0903 | 9.308 | 8.4915 | 7.6489 | 6.7271 | 5.7061 | 4.4102 | 0.53947 | -5.4956 | -9.6901 | -12.2095 | 15.4627 | 15.0803 | 14.6282 | 14.0818 | 13.5215 | 12.9231 | 12.2755 | 11.5581 | 10.6914 | 8.0396 | 3.8984 | 0.34798 | -3.5624 | 12.3108 | 11.8347 | 11.2592 | 10.532 | 9.7798 | 8.9918 | 8.1409 | 7.1926 | 5.9835 | 2.3677 | -3.05 | -6.6604 | -8.7814
BRAMLEY (FLEE) | CAMBERLEY RESERVE | QUEENSMEAD | MINIMUM HEADROOM | SU 87062 55683 | YES | 9.2874 | 8.7548 | 8.4777 | 8.1191 | 7.2929 | 6.4336 | 5.5919 | 4.6833 | 3.6487 | 1.4086 | -2.0288 | -4.4306 | -5.943 | 10.7723 | 10.4127 | 10.1877 | 9.9397 | 9.4542 | 8.943 | 8.4234 | 7.8309 | 7.1627 | 5.687 | 3.5339 | 1.9762 | 0.46563 | 9.7322 | 9.2493 | 8.972 | 8.639 | 7.9349 | 7.1821 | 6.4346 | 5.6101 | 4.6622 | 2.5979 | -0.44978 | -2.4276 | -3.6523
|  | QUEENSMEAD | CT |  |  | 9.2874 | 8.7548 | 8.4777 | 8.1191 | 7.2929 | 6.4336 | 5.5919 | 4.6833 | 3.6487 | 1.4086 | -2.0288 | -4.4306 | -5.943 | 10.7723 | 10.4127 | 10.1877 | 9.9397 | 9.4542 | 8.943 | 8.4234 | 7.8309 | 7.1627 | 5.687 | 3.5339 | 1.9762 | 0.46563 | 9.7322 | 9.2493 | 8.972 | 8.639 | 7.9349 | 7.1821 | 6.4346 | 5.6101 | 4.6622 | 2.5979 | -0.44978 | -2.4276 | -3.6523
|  | QUEENSMEAD | LW |  |  | 9.2874 | 8.7548 | 8.4777 | 8.1191 | 7.2929 | 6.4336 | 5.5919 | 4.6833 | 3.6487 | 1.4086 | -2.0288 | -4.4306 | -5.943 | 10.7723 | 10.4127 | 10.1877 | 9.9397 | 9.4542 | 8.943 | 8.4234 | 7.8309 | 7.1627 | 5.687 | 3.5339 | 1.9762 | 0.46563 | 9.7322 | 9.2493 | 8.972 | 8.639 | 7.9349 | 7.1821 | 6.4346 | 5.6101 | 4.6622 | 2.5979 | -0.44978 | -2.4276 | -3.6523
|  | QUEENSMEAD | ST |  |  | 9.2874 | 8.7548 | 8.4777 | 8.1191 | 7.2929 | 6.4336 | 5.5919 | 4.6833 | 3.6487 | 1.4086 | -2.0288 | -4.4306 | -5.943 | 10.7723 | 10.4127 | 10.1877 | 9.9397 | 9.4542 | 8.943 | 8.4234 | 7.8309 | 7.1627 | 5.687 | 3.5339 | 1.9762 | 0.46563 | 9.7322 | 9.2493 | 8.972 | 8.639 | 7.9349 | 7.1821 | 6.4346 | 5.6101 | 4.6622 | 2.5979 | -0.44978 | -2.4276 | -3.6523
|  | QUEENSMEAD | FS |  |  | 9.2874 | 8.7548 | 8.4777 | 8.1191 | 7.2929 | 6.4336 | 5.5919 | 4.6833 | 3.6487 | 1.4086 | -2.0288 | -4.4306 | -5.943 | 10.7723 | 10.4127 | 10.1877 | 9.9397 | 9.4542 | 8.943 | 8.4234 | 7.8309 | 7.1627 | 5.687 | 3.5339 | 1.9762 | 0.46563 | 9.7322 | 9.2493 | 8.972 | 8.639 | 7.9349 | 7.1821 | 6.4346 | 5.6101 | 4.6622 | 2.5979 | -0.44978 | -2.4276 | -3.6523
MELKSHAM GSP | WEST GRAFTON | RAMSBURY | MINIMUM HEADROOM | SU 27380 72108 | YES | 5.5437 | 5.4375 | 5.3133 | 5.1444 | 4.9704 | 4.7803 | 4.5671 | 4.311 | 3.9181 | 3.0607 | 1.6906 | 0.74328 | 0.3784 | 7.1689 | 7.0987 | 7.0152 | 6.9154 | 6.8117 | 6.6966 | 6.5652 | 6.4027 | 6.1716 | 5.702 | 5.0184 | 4.5292 | 4.2183 | 6.4033 | 6.302 | 6.1826 | 6.0246 | 5.8617 | 5.6831 | 5.4818 | 5.2378 | 4.8672 | 4.0776 | 2.8556 | 2.0219 | 1.7021
|  | RAMSBURY | CT |  |  | 5.5437 | 5.4375 | 5.3133 | 5.1444 | 4.9704 | 4.7803 | 4.5671 | 4.311 | 3.9181 | 3.0607 | 1.6906 | 0.74328 | 0.3784 | 7.1689 | 7.0987 | 7.0152 | 6.9154 | 6.8117 | 6.6966 | 6.5652 | 6.4027 | 6.1716 | 5.702 | 5.0184 | 4.5292 | 4.2183 | 6.4033 | 6.302 | 6.1826 | 6.0246 | 5.8617 | 5.6831 | 5.4818 | 5.2378 | 4.8672 | 4.0776 | 2.8556 | 2.0219 | 1.7021
|  | RAMSBURY | LW |  |  | 5.5437 | 5.4375 | 5.3133 | 5.1444 | 4.9704 | 4.7803 | 4.5671 | 4.311 | 3.9181 | 3.0607 | 1.6906 | 0.74328 | 0.3784 | 7.1689 | 7.0987 | 7.0152 | 6.9154 | 6.8117 | 6.6966 | 6.5652 | 6.4027 | 6.1716 | 5.702 | 5.0184 | 4.5292 | 4.2183 | 6.4033 | 6.302 | 6.1826 | 6.0246 | 5.8617 | 5.6831 | 5.4818 | 5.2378 | 4.8672 | 4.0776 | 2.8556 | 2.0219 | 1.7021
|  | RAMSBURY | ST |  |  | 5.5437 | 5.4375 | 5.3133 | 5.1444 | 4.9704 | 4.7803 | 4.5671 | 4.311 | 3.9181 | 3.0607 | 1.6906 | 0.74328 | 0.3784 | 7.1689 | 7.0987 | 7.0152 | 6.9154 | 6.8117 | 6.6966 | 6.5652 | 6.4027 | 6.1716 | 5.702 | 5.0184 | 4.5292 | 4.2183 | 6.4033 | 6.302 | 6.1826 | 6.0246 | 5.8617 | 5.6831 | 5.4818 | 5.2378 | 4.8672 | 4.0776 | 2.8556 | 2.0219 | 1.7021
|  | RAMSBURY | FS |  |  | 5.5437 | 5.4375 | 5.3133 | 5.1444 | 4.9704 | 4.7803 | 4.5671 | 4.311 | 3.9181 | 3.0607 | 1.6906 | 0.74328 | 0.3784 | 7.1689 | 7.0987 | 7.0152 | 6.9154 | 6.8117 | 6.6966 | 6.5652 | 6.4027 | 6.1716 | 5.702 | 5.0184 | 4.5292 | 4.2183 | 6.4033 | 6.302 | 6.1826 | 6.0246 | 5.8617 | 5.6831 | 5.4818 | 5.2378 | 4.8672 | 4.0776 | 2.8556 | 2.0219 | 1.7021
MELKSHAM GSP | AMESBURY | RATFYN | MINIMUM HEADROOM |  |  | 20.161 | 19.9847 | 19.7025 | 19.2739 | 18.7722 | 18.2416 | 17.6645 | 17.0802 | 16.1596 | 13.8706 | 10.7505 | 8.5591 | 7.6112 | 19.2978 | 19.1829 | 18.9942 | 18.7479 | 18.4596 | 18.1509 | 17.7991 | 17.3775 | 16.7594 | 15.3454 | 13.7715 | 12.6621 | 11.8183 | 21.379 | 21.2226 | 20.9765 | 20.6015 | 20.1673 | 19.7081 | 19.2091 | 18.6995 | 17.8461 | 15.7589 | 12.9202 | 10.9738 | 10.1055
|  | RATFYN | CT |  |  | 20.161 | 19.9847 | 19.7025 | 19.2739 | 18.7722 | 18.2416 | 17.6645 | 17.0802 | 16.1596 | 13.8706 | 10.7505 | 8.5591 | 7.6112 | 19.2978 | 19.1829 | 18.9942 | 18.7479 | 18.4596 | 18.1509 | 17.7991 | 17.3775 | 16.7594 | 15.3454 | 13.7715 | 12.6621 | 11.8183 | 21.379 | 21.2226 | 20.9765 | 20.6015 | 20.1673 | 19.7081 | 19.2091 | 18.6995 | 17.8461 | 15.7589 | 12.9202 | 10.9738 | 10.1055
|  | RATFYN | LW |  |  | 20.161 | 19.9847 | 19.7025 | 19.2739 | 18.7722 | 18.2416 | 17.6645 | 17.0802 | 16.1596 | 13.8706 | 10.7505 | 8.5591 | 7.6112 | 19.2978 | 19.1829 | 18.9942 | 18.7479 | 18.4596 | 18.1509 | 17.7991 | 17.3775 | 16.7594 | 15.3454 | 13.7715 | 12.6621 | 11.8183 | 21.379 | 21.2226 | 20.9765 | 20.6015 | 20.1673 | 19.7081 | 19.2091 | 18.6995 | 17.8461 | 15.7589 | 12.9202 | 10.9738 | 10.1055
|  | RATFYN | ST |  |  | 20.161 | 19.9847 | 19.7025 | 19.2739 | 18.7722 | 18.2416 | 17.6645 | 17.0802 | 16.1596 | 13.8706 | 10.7505 | 8.5591 | 7.6112 | 19.2978 | 19.1829 | 18.9942 | 18.7479 | 18.4596 | 18.1509 | 17.7991 | 17.3775 | 16.7594 | 15.3454 | 13.7715 | 12.6621 | 11.8183 | 21.379 | 21.2226 | 20.9765 | 20.6015 | 20.1673 | 19.7081 | 19.2091 | 18.6995 | 17.8461 | 15.7589 | 12.9202 | 10.9738 | 10.1055
|  | RATFYN | FS |  |  | 20.161 | 19.9847 | 19.7025 | 19.2739 | 18.7722 | 18.2416 | 17.6645 | 17.0802 | 16.1596 | 13.8706 | 10.7505 | 8.5591 | 7.6112 | 19.2978 | 19.1829 | 18.9942 | 18.7479 | 18.4596 | 18.1509 | 17.7991 | 17.3775 | 16.7594 | 15.3454 | 13.7715 | 12.6621 | 11.8183 | 21.379 | 21.2226 | 20.9765 | 20.6015 | 20.1673 | 19.7081 | 19.2091 | 18.6995 | 17.8461 | 15.7589 | 12.9202 | 10.9738 | 10.1055
BRAMLEY (FLEE) | READING BSP | READING | MINIMUM HEADROOM | SU 74591 73788 | YES | 24.7592 | 24.1503 | 23.4097 | 22.4631 | 21.4432 | 20.3651 | 19.1571 | 17.7275 | 15.4125 | 9.978 | 1.0522 | -5.5782 | -9.384 | 25.1846 | 24.6752 | 24.0608 | 23.351 | 22.5783 | 21.734 | 20.7795 | 19.6437 | 18.0272 | 13.9786 | 7.0836 | -0.32187 | -9.5579 | 27.0922 | 26.5005 | 25.7725 | 24.9118 | 23.9495 | 22.9253 | 21.7737 | 20.4017 | 18.2029 | 13.1384 | 5.1417 | -0.61293 | -3.7727
|  | READING | CT |  |  | 24.7592 | 24.1503 | 23.4097 | 22.4631 | 21.4432 | 20.3651 | 19.1571 | 17.7275 | 15.4125 | 9.978 | 1.0522 | -5.5782 | -9.384 | 25.1846 | 24.6752 | 24.0608 | 23.351 | 22.5783 | 21.734 | 20.7795 | 19.6437 | 18.0272 | 13.9786 | 7.0836 | -0.32187 | -9.5579 | 27.0922 | 26.5005 | 25.7725 | 24.9118 | 23.9495 | 22.9253 | 21.7737 | 20.4017 | 18.2029 | 13.1384 | 5.1417 | -0.61293 | -3.7727
|  | READING | LW |  |  | 24.7592 | 24.1503 | 23.4097 | 22.4631 | 21.4432 | 20.3651 | 19.1571 | 17.7275 | 15.4125 | 9.978 | 1.0522 | -5.5782 | -9.384 | 25.1846 | 24.6752 | 24.0608 | 23.351 | 22.5783 | 21.734 | 20.7795 | 19.6437 | 18.0272 | 13.9786 | 7.0836 | -0.32187 | -9.5579 | 27.0922 | 26.5005 | 25.7725 | 24.9118 | 23.9495 | 22.9253 | 21.7737 | 20.4017 | 18.2029 | 13.1384 | 5.1417 | -0.61293 | -3.7727
|  | READING | ST |  |  | 24.7592 | 24.1503 | 23.4097 | 22.4631 | 21.4432 | 20.3651 | 19.1571 | 17.7275 | 15.4125 | 9.978 | 1.0522 | -5.5782 | -9.384 | 25.1846 | 24.6752 | 24.0608 | 23.351 | 22.5783 | 21.734 | 20.7795 | 19.6437 | 18.0272 | 13.9786 | 7.0836 | -0.32187 | -9.5579 | 27.0922 | 26.5005 | 25.7725 | 24.9118 | 23.9495 | 22.9253 | 21.7737 | 20.4017 | 18.2029 | 13.1384 | 5.1417 | -0.61293 | -3.7727
|  | READING | FS |  |  | 24.7592 | 24.1503 | 23.4097 | 22.4631 | 21.4432 | 20.3651 | 19.1571 | 17.7275 | 15.4125 | 9.978 | 1.0522 | -5.5782 | -9.384 | 25.1846 | 24.6752 | 24.0608 | 23.351 | 22.5783 | 21.734 | 20.7795 | 19.6437 | 18.0272 | 13.9786 | 7.0836 | -0.32187 | -9.5579 | 27.0922 | 26.5005 | 25.7725 | 24.9118 | 23.9495 | 22.9253 | 21.7737 | 20.4017 | 18.2029 | 13.1384 | 5.1417 | -0.61293 | -3.7727
BRAMLEY (FLEE) | READING TOWN BSP | READING TOWN | MINIMUM HEADROOM | SU 71540 74122 | YES | 64.6056 | 63.4698 | 62.3459 | 60.6558 | 58.7745 | 57.0459 | 55.2613 | 53.438 | 51.2924 | 44.5541 | 36.4189 | 31.6932 | 29.1015 | 67.7036 | 66.4599 | 65.1868 | 63.9656 | 62.7532 | 61.5285 | 60.2146 | 58.8894 | 57.3796 | 52.4395 | 45.6609 | 38.9718 | 29.8907 | 64.3851 | 63.2377 | 62.0852 | 61.0121 | 59.7766 | 58.3304 | 56.6954 | 55.0633 | 53.1339 | 47.0878 | 39.8563 | 35.792 | 33.6121
|  | READING TOWN | CT |  |  | 64.6056 | 63.4698 | 62.3459 | 60.6558 | 58.7745 | 57.0459 | 55.2613 | 53.438 | 51.2924 | 44.5541 | 36.4189 | 31.6932 | 29.1015 | 67.7036 | 66.4599 | 65.1868 | 63.9656 | 62.7532 | 61.5285 | 60.2146 | 58.8894 | 57.3796 | 52.4395 | 45.6609 | 38.9718 | 29.8907 | 64.3851 | 63.2377 | 62.0852 | 61.0121 | 59.7766 | 58.3304 | 56.6954 | 55.0633 | 53.1339 | 47.0878 | 39.8563 | 35.792 | 33.6121
|  | READING TOWN | LW |  |  | 64.6056 | 63.4698 | 62.3459 | 60.6558 | 58.7745 | 57.0459 | 55.2613 | 53.438 | 51.2924 | 44.5541 | 36.4189 | 31.6932 | 29.1015 | 67.7036 | 66.4599 | 65.1868 | 63.9656 | 62.7532 | 61.5285 | 60.2146 | 58.8894 | 57.3796 | 52.4395 | 45.6609 | 38.9718 | 29.8907 | 64.3851 | 63.2377 | 62.0852 | 61.0121 | 59.7766 | 58.3304 | 56.6954 | 55.0633 | 53.1339 | 47.0878 | 39.8563 | 35.792 | 33.6121
|  | READING TOWN | ST |  |  | 64.6056 | 63.4698 | 62.3459 | 60.6558 | 58.7745 | 57.0459 | 55.2613 | 53.438 | 51.2924 | 44.5541 | 36.4189 | 31.6932 | 29.1015 | 67.7036 | 66.4599 | 65.1868 | 63.9656 | 62.7532 | 61.5285 | 60.2146 | 58.8894 | 57.3796 | 52.4395 | 45.6609 | 38.9718 | 29.8907 | 64.3851 | 63.2377 | 62.0852 | 61.0121 | 59.7766 | 58.3304 | 56.6954 | 55.0633 | 53.1339 | 47.0878 | 39.8563 | 35.792 | 33.6121
|  | READING TOWN | FS |  |  | 64.6056 | 63.4698 | 62.3459 | 60.6558 | 58.7745 | 57.0459 | 55.2613 | 53.438 | 51.2924 | 44.5541 | 36.4189 | 31.6932 | 29.1015 | 67.7036 | 66.4599 | 65.1868 | 63.9656 | 62.7532 | 61.5285 | 60.2146 | 58.8894 | 57.3796 | 52.4395 | 45.6609 | 38.9718 | 29.8907 | 64.3851 | 63.2377 | 62.0852 | 61.0121 | 59.7766 | 58.3304 | 56.6954 | 55.0633 | 53.1339 | 47.0878 | 39.8563 | 35.792 | 33.6121
MANNINGTON GSP | REDHILL BSP | REDHILL | MINIMUM HEADROOM | SZ 08512 96149 | YES | 33.269 | 32.7363 | 31.9603 | 30.9718 | 29.9036 | 28.9625 | 28.0119 | 26.9504 | 25.2124 | 20.4955 | 13.3003 | 7.505 | 4.2209 | 38.4267 | 37.9942 | 37.3428 | 36.642 | 35.8906 | 35.1764 | 34.4561 | 33.6327 | 32.4198 | 29.2517 | 25.294 | 21.8479 | 18.6154 | 34.9893 | 34.5118 | 33.8085 | 32.9459 | 32.0246 | 31.1735 | 30.2785 | 29.2745 | 27.646 | 23.2695 | 16.897 | 11.8877 | 9.0943
|  | REDHILL | CT |  |  | 33.269 | 32.7363 | 31.9603 | 30.9718 | 29.9036 | 28.9625 | 28.0119 | 26.9504 | 25.2124 | 20.4955 | 13.3003 | 7.505 | 4.2209 | 38.4267 | 37.9942 | 37.3428 | 36.642 | 35.8906 | 35.1764 | 34.4561 | 33.6327 | 32.4198 | 29.2517 | 25.294 | 21.8479 | 18.6154 | 34.9893 | 34.5118 | 33.8085 | 32.9459 | 32.0246 | 31.1735 | 30.2785 | 29.2745 | 27.646 | 23.2695 | 16.897 | 11.8877 | 9.0943
|  | REDHILL | LW |  |  | 33.269 | 32.7363 | 31.9603 | 30.9718 | 29.9036 | 28.9625 | 28.0119 | 26.9504 | 25.2124 | 20.4955 | 13.3003 | 7.505 | 4.2209 | 38.4267 | 37.9942 | 37.3428 | 36.642 | 35.8906 | 35.1764 | 34.4561 | 33.6327 | 32.4198 | 29.2517 | 25.294 | 21.8479 | 18.6154 | 34.9893 | 34.5118 | 33.8085 | 32.9459 | 32.0246 | 31.1735 | 30.2785 | 29.2745 | 27.646 | 23.2695 | 16.897 | 11.8877 | 9.0943
|  | REDHILL | ST |  |  | 33.269 | 32.7363 | 31.9603 | 30.9718 | 29.9036 | 28.9625 | 28.0119 | 26.9504 | 25.2124 | 20.4955 | 13.3003 | 7.505 | 4.2209 | 38.4267 | 37.9942 | 37.3428 | 36.642 | 35.8906 | 35.1764 | 34.4561 | 33.6327 | 32.4198 | 29.2517 | 25.294 | 21.8479 | 18.6154 | 34.9893 | 34.5118 | 33.8085 | 32.9459 | 32.0246 | 31.1735 | 30.2785 | 29.2745 | 27.646 | 23.2695 | 16.897 | 11.8877 | 9.0943
|  | REDHILL | FS |  |  | 33.269 | 32.7363 | 31.9603 | 30.9718 | 29.9036 | 28.9625 | 28.0119 | 26.9504 | 25.2124 | 20.4955 | 13.3003 | 7.505 | 4.2209 | 38.4267 | 37.9942 | 37.3428 | 36.642 | 35.8906 | 35.1764 | 34.4561 | 33.6327 | 32.4198 | 29.2517 | 25.294 | 21.8479 | 18.6154 | 34.9893 | 34.5118 | 33.8085 | 32.9459 | 32.0246 | 31.1735 | 30.2785 | 29.2745 | 27.646 | 23.2695 | 16.897 | 11.8877 | 9.0943
CHICKERELL GSP | CHICKERELL BSP | REDLANDS | MINIMUM HEADROOM | SY 67131 82321 | YES | 4.6245 | 4.4982 | 3.8324 | 3.0975 | 2.2551 | 1.384 | 0.42245 | -0.6543 | -2.0592 | -5.3561 | -9.501 | -12.4996 | -14.0836 | 8.182 | 7.9654 | 7.5006 | 7.0522 | 6.5121 | 5.9541 | 5.361 | 4.6622 | 3.7544 | 1.6464 | -0.55259 | -2.2057 | -3.5903 | 4.9495 | 4.6429 | 4.0251 | 3.3699 | 2.6132 | 1.8262 | 0.96432 | -0.013231 | -1.3165 | -4.3719 | -8.064 | -10.6987 | -12.0623
|  | REDLANDS | CT |  |  | 4.6245 | 4.4982 | 3.8324 | 3.0975 | 2.2551 | 1.384 | 0.42245 | -0.6543 | -2.0592 | -5.3561 | -9.501 | -12.4996 | -14.0836 | 8.182 | 7.9654 | 7.5006 | 7.0522 | 6.5121 | 5.9541 | 5.361 | 4.6622 | 3.7544 | 1.6464 | -0.55259 | -2.2057 | -3.5903 | 4.9495 | 4.6429 | 4.0251 | 3.3699 | 2.6132 | 1.8262 | 0.96432 | -0.013231 | -1.3165 | -4.3719 | -8.064 | -10.6987 | -12.0623
|  | REDLANDS | LW |  |  | 4.6245 | 4.4982 | 3.8324 | 3.0975 | 2.2551 | 1.384 | 0.42245 | -0.6543 | -2.0592 | -5.3561 | -9.501 | -12.4996 | -14.0836 | 8.182 | 7.9654 | 7.5006 | 7.0522 | 6.5121 | 5.9541 | 5.361 | 4.6622 | 3.7544 | 1.6464 | -0.55259 | -2.2057 | -3.5903 | 4.9495 | 4.6429 | 4.0251 | 3.3699 | 2.6132 | 1.8262 | 0.96432 | -0.013231 | -1.3165 | -4.3719 | -8.064 | -10.6987 | -12.0623
|  | REDLANDS | ST |  |  | 4.6245 | 4.4982 | 3.8324 | 3.0975 | 2.2551 | 1.384 | 0.42245 | -0.6543 | -2.0592 | -5.3561 | -9.501 | -12.4996 | -14.0836 | 8.182 | 7.9654 | 7.5006 | 7.0522 | 6.5121 | 5.9541 | 5.361 | 4.6622 | 3.7544 | 1.6464 | -0.55259 | -2.2057 | -3.5903 | 4.9495 | 4.6429 | 4.0251 | 3.3699 | 2.6132 | 1.8262 | 0.96432 | -0.013231 | -1.3165 | -4.3719 | -8.064 | -10.6987 | -12.0623
|  | REDLANDS | FS |  |  | 4.6245 | 4.4982 | 3.8324 | 3.0975 | 2.2551 | 1.384 | 0.42245 | -0.6543 | -2.0592 | -5.3561 | -9.501 | -12.4996 | -14.0836 | 8.182 | 7.9654 | 7.5006 | 7.0522 | 6.5121 | 5.9541 | 5.361 | 4.6622 | 3.7544 | 1.6464 | -0.55259 | -2.2057 | -3.5903 | 4.9495 | 4.6429 | 4.0251 | 3.3699 | 2.6132 | 1.8262 | 0.96432 | -0.013231 | -1.3165 | -4.3719 | -8.064 | -10.6987 | -12.0623
MANNINGTON GSP | SALISBURY | REDLYNCH | MINIMUM HEADROOM | SU 19073 20576 | YES | 1.1875 | 1.0022 | 0.77646 | 0.44014 | 0.089948 | -0.29024 | -0.72214 | -1.2487 | -2.0455 | -3.6334 | -6.4229 | -8.5734 | -9.5267 | 3.9395 | 3.7997 | 3.6265 | 3.4194 | 3.1899 | 2.9337 | 2.6327 | 2.2688 | 1.7624 | 0.89522 | -0.35607 | -1.2983 | -1.9258 | 2.355 | 2.1797 | 1.9709 | 1.6717 | 1.3454 | 0.98882 | 0.58249 | 0.11055 | -0.62064 | -2.0799 | -4.5905 | -6.4682 | -7.3052
|  | REDLYNCH | CT |  |  | 1.1875 | 1.0022 | 0.77646 | 0.44014 | 0.089948 | -0.29024 | -0.72214 | -1.2487 | -2.0455 | -3.6334 | -6.4229 | -8.5734 | -9.5267 | 3.9395 | 3.7997 | 3.6265 | 3.4194 | 3.1899 | 2.9337 | 2.6327 | 2.2688 | 1.7624 | 0.89522 | -0.35607 | -1.2983 | -1.9258 | 2.355 | 2.1797 | 1.9709 | 1.6717 | 1.3454 | 0.98882 | 0.58249 | 0.11055 | -0.62064 | -2.0799 | -4.5905 | -6.4682 | -7.3052
|  | REDLYNCH | LW |  |  | 1.1875 | 1.0022 | 0.77646 | 0.44014 | 0.089948 | -0.29024 | -0.72214 | -1.2487 | -2.0455 | -3.6334 | -6.4229 | -8.5734 | -9.5267 | 3.9395 | 3.7997 | 3.6265 | 3.4194 | 3.1899 | 2.9337 | 2.6327 | 2.2688 | 1.7624 | 0.89522 | -0.35607 | -1.2983 | -1.9258 | 2.355 | 2.1797 | 1.9709 | 1.6717 | 1.3454 | 0.98882 | 0.58249 | 0.11055 | -0.62064 | -2.0799 | -4.5905 | -6.4682 | -7.3052
|  | REDLYNCH | ST |  |  | 1.1875 | 1.0022 | 0.77646 | 0.44014 | 0.089948 | -0.29024 | -0.72214 | -1.2487 | -2.0455 | -3.6334 | -6.4229 | -8.5734 | -9.5267 | 3.9395 | 3.7997 | 3.6265 | 3.4194 | 3.1899 | 2.9337 | 2.6327 | 2.2688 | 1.7624 | 0.89522 | -0.35607 | -1.2983 | -1.9258 | 2.355 | 2.1797 | 1.9709 | 1.6717 | 1.3454 | 0.98882 | 0.58249 | 0.11055 | -0.62064 | -2.0799 | -4.5905 | -6.4682 | -7.3052
|  | REDLYNCH | FS |  |  | 1.1875 | 1.0022 | 0.77646 | 0.44014 | 0.089948 | -0.29024 | -0.72214 | -1.2487 | -2.0455 | -3.6334 | -6.4229 | -8.5734 | -9.5267 | 3.9395 | 3.7997 | 3.6265 | 3.4194 | 3.1899 | 2.9337 | 2.6327 | 2.2688 | 1.7624 | 0.89522 | -0.35607 | -1.2983 | -1.9258 | 2.355 | 2.1797 | 1.9709 | 1.6717 | 1.3454 | 0.98882 | 0.58249 | 0.11055 | -0.62064 | -2.0799 | -4.5905 | -6.4682 | -7.3052
NURSLING GSP | SOUTHAMPTON (2 X 90) | REGENTS PARK | MINIMUM HEADROOM | SU 39267 13050 | YES | 24.8636 | 24.7321 | 24.5582 | 24.3014 | 24.0237 | 23.7141 | 23.3817 | 22.9474 | 22.2714 | 20.0195 | 16.1829 | 13.6495 | 12.2456 | 23.1667 | 23.0739 | 22.9534 | 22.8205 | 22.6707 | 22.5024 | 22.3164 | 22.0284 | 21.6706 | 20.0953 | 17.1559 | 14.5197 | 11.3063 | 27.1428 | 27.02 | 26.8556 | 26.618 | 26.3605 | 26.0728 | 25.7636 | 25.3559 | 24.7291 | 22.6428 | 19.1542 | 16.9172 | 15.6941
|  | REGENTS PARK | CT |  |  | 24.8636 | 24.7321 | 24.5582 | 24.3014 | 24.0237 | 23.7141 | 23.3817 | 22.9474 | 22.2714 | 20.0195 | 16.1829 | 13.6495 | 12.2456 | 23.1667 | 23.0739 | 22.9534 | 22.8205 | 22.6707 | 22.5024 | 22.3164 | 22.0284 | 21.6706 | 20.0953 | 17.1559 | 14.5197 | 11.3063 | 27.1428 | 27.02 | 26.8556 | 26.618 | 26.3605 | 26.0728 | 25.7636 | 25.3559 | 24.7291 | 22.6428 | 19.1542 | 16.9172 | 15.6941
|  | REGENTS PARK | LW |  |  | 24.8636 | 24.7321 | 24.5582 | 24.3014 | 24.0237 | 23.7141 | 23.3817 | 22.9474 | 22.2714 | 20.0195 | 16.1829 | 13.6495 | 12.2456 | 23.1667 | 23.0739 | 22.9534 | 22.8205 | 22.6707 | 22.5024 | 22.3164 | 22.0284 | 21.6706 | 20.0953 | 17.1559 | 14.5197 | 11.3063 | 27.1428 | 27.02 | 26.8556 | 26.618 | 26.3605 | 26.0728 | 25.7636 | 25.3559 | 24.7291 | 22.6428 | 19.1542 | 16.9172 | 15.6941
|  | REGENTS PARK | ST |  |  | 24.8636 | 24.7321 | 24.5582 | 24.3014 | 24.0237 | 23.7141 | 23.3817 | 22.9474 | 22.2714 | 20.0195 | 16.1829 | 13.6495 | 12.2456 | 23.1667 | 23.0739 | 22.9534 | 22.8205 | 22.6707 | 22.5024 | 22.3164 | 22.0284 | 21.6706 | 20.0953 | 17.1559 | 14.5197 | 11.3063 | 27.1428 | 27.02 | 26.8556 | 26.618 | 26.3605 | 26.0728 | 25.7636 | 25.3559 | 24.7291 | 22.6428 | 19.1542 | 16.9172 | 15.6941
|  | REGENTS PARK | FS |  |  | 24.8636 | 24.7321 | 24.5582 | 24.3014 | 24.0237 | 23.7141 | 23.3817 | 22.9474 | 22.2714 | 20.0195 | 16.1829 | 13.6495 | 12.2456 | 23.1667 | 23.0739 | 22.9534 | 22.8205 | 22.6707 | 22.5024 | 22.3164 | 22.0284 | 21.6706 | 20.0953 | 17.1559 | 14.5197 | 11.3063 | 27.1428 | 27.02 | 26.8556 | 26.618 | 26.3605 | 26.0728 | 25.7636 | 25.3559 | 24.7291 | 22.6428 | 19.1542 | 16.9172 | 15.6941
COWLEY GSP | WITNEY BSP | RISSINGTON | MINIMUM HEADROOM | SP 19225 19563 | NO | 3.67 | 3.486 | 3.2527 | 2.904 | 2.5432 | 2.1685 | 1.7725 | 1.3026 | 0.61383 | -1.1433 | -3.6352 | -4.5982 | -4.7524 | 6.0441 | 5.9414 | 5.8036 | 5.6219 | 5.4317 | 5.2301 | 5.0156 | 4.7447 | 4.3579 | 3.434 | 2.3346 | 1.8524 | 1.6207 | 4.4041 | 4.2335 | 4.0137 | 3.6936 | 3.3616 | 3.0155 | 2.6493 | 2.2093 | 1.5711 | -0.032447 | -2.1507 | -3.001 | -3.1368
|  | RISSINGTON | CT |  |  | 3.67 | 3.486 | 3.2527 | 2.904 | 2.5432 | 2.1685 | 1.7725 | 1.3026 | 0.61383 | -1.1433 | -3.6352 | -4.5982 | -4.7524 | 6.0441 | 5.9414 | 5.8036 | 5.6219 | 5.4317 | 5.2301 | 5.0156 | 4.7447 | 4.3579 | 3.434 | 2.3346 | 1.8524 | 1.6207 | 4.4041 | 4.2335 | 4.0137 | 3.6936 | 3.3616 | 3.0155 | 2.6493 | 2.2093 | 1.5711 | -0.032447 | -2.1507 | -3.001 | -3.1368
|  | RISSINGTON | LW |  |  | 3.67 | 3.486 | 3.2527 | 2.904 | 2.5432 | 2.1685 | 1.7725 | 1.3026 | 0.61383 | -1.1433 | -3.6352 | -4.5982 | -4.7524 | 6.0441 | 5.9414 | 5.8036 | 5.6219 | 5.4317 | 5.2301 | 5.0156 | 4.7447 | 4.3579 | 3.434 | 2.3346 | 1.8524 | 1.6207 | 4.4041 | 4.2335 | 4.0137 | 3.6936 | 3.3616 | 3.0155 | 2.6493 | 2.2093 | 1.5711 | -0.032447 | -2.1507 | -3.001 | -3.1368
|  | RISSINGTON | ST |  |  | 3.67 | 3.486 | 3.2527 | 2.904 | 2.5432 | 2.1685 | 1.7725 | 1.3026 | 0.61383 | -1.1433 | -3.6352 | -4.5982 | -4.7524 | 6.0441 | 5.9414 | 5.8036 | 5.6219 | 5.4317 | 5.2301 | 5.0156 | 4.7447 | 4.3579 | 3.434 | 2.3346 | 1.8524 | 1.6207 | 4.4041 | 4.2335 | 4.0137 | 3.6936 | 3.3616 | 3.0155 | 2.6493 | 2.2093 | 1.5711 | -0.032447 | -2.1507 | -3.001 | -3.1368
|  | RISSINGTON | FS |  |  | 3.67 | 3.486 | 3.2527 | 2.904 | 2.5432 | 2.1685 | 1.7725 | 1.3026 | 0.61383 | -1.1433 | -3.6352 | -4.5982 | -4.7524 | 6.0441 | 5.9414 | 5.8036 | 5.6219 | 5.4317 | 5.2301 | 5.0156 | 4.7447 | 4.3579 | 3.434 | 2.3346 | 1.8524 | 1.6207 | 4.4041 | 4.2335 | 4.0137 | 3.6936 | 3.3616 | 3.0155 | 2.6493 | 2.2093 | 1.5711 | -0.032447 | -2.1507 | -3.001 | -3.1368
BRAMLEY (ANDO-THAT) | THATCHAM BSP | RIVERSIDE | MINIMUM HEADROOM | SU 47846 67187 | YES | 9.2069 | 8.9858 | 8.693 | 8.3799 | 7.8838 | 7.4356 | 6.9504 | 6.4361 | 5.7615 | 3.3968 | -0.45716 | -2.2648 | -3.2748 | 11.6695 | 11.4696 | 11.3198 | 11.1627 | 10.928 | 10.706 | 10.4537 | 10.1889 | 9.8491 | 8.6677 | 6.6862 | 5.6007 | 4.4472 | 11.3966 | 11.0464 | 10.7915 | 10.5093 | 10.0809 | 9.6906 | 9.261 | 8.8045 | 8.1977 | 6.1154 | 2.7527 | 1.18 | 0.32029
|  | RIVERSIDE | CT |  |  | 9.2069 | 8.9858 | 8.693 | 8.3799 | 7.8838 | 7.4356 | 6.9504 | 6.4361 | 5.7615 | 3.3968 | -0.45716 | -2.2648 | -3.2748 | 11.6695 | 11.4696 | 11.3198 | 11.1627 | 10.928 | 10.706 | 10.4537 | 10.1889 | 9.8491 | 8.6677 | 6.6862 | 5.6007 | 4.4472 | 11.3966 | 11.0464 | 10.7915 | 10.5093 | 10.0809 | 9.6906 | 9.261 | 8.8045 | 8.1977 | 6.1154 | 2.7527 | 1.18 | 0.32029
|  | RIVERSIDE | LW |  |  | 9.2069 | 8.9858 | 8.693 | 8.3799 | 7.8838 | 7.4356 | 6.9504 | 6.4361 | 5.7615 | 3.3968 | -0.45716 | -2.2648 | -3.2748 | 11.6695 | 11.4696 | 11.3198 | 11.1627 | 10.928 | 10.706 | 10.4537 | 10.1889 | 9.8491 | 8.6677 | 6.6862 | 5.6007 | 4.4472 | 11.3966 | 11.0464 | 10.7915 | 10.5093 | 10.0809 | 9.6906 | 9.261 | 8.8045 | 8.1977 | 6.1154 | 2.7527 | 1.18 | 0.32029
|  | RIVERSIDE | ST |  |  | 9.2069 | 8.9858 | 8.693 | 8.3799 | 7.8838 | 7.4356 | 6.9504 | 6.4361 | 5.7615 | 3.3968 | -0.45716 | -2.2648 | -3.2748 | 11.6695 | 11.4696 | 11.3198 | 11.1627 | 10.928 | 10.706 | 10.4537 | 10.1889 | 9.8491 | 8.6677 | 6.6862 | 5.6007 | 4.4472 | 11.3966 | 11.0464 | 10.7915 | 10.5093 | 10.0809 | 9.6906 | 9.261 | 8.8045 | 8.1977 | 6.1154 | 2.7527 | 1.18 | 0.32029
|  | RIVERSIDE | FS |  |  | 9.2069 | 8.9858 | 8.693 | 8.3799 | 7.8838 | 7.4356 | 6.9504 | 6.4361 | 5.7615 | 3.3968 | -0.45716 | -2.2648 | -3.2748 | 11.6695 | 11.4696 | 11.3198 | 11.1627 | 10.928 | 10.706 | 10.4537 | 10.1889 | 9.8491 | 8.6677 | 6.6862 | 5.6007 | 4.4472 | 11.3966 | 11.0464 | 10.7915 | 10.5093 | 10.0809 | 9.6906 | 9.261 | 8.8045 | 8.1977 | 6.1154 | 2.7527 | 1.18 | 0.32029
MANNINGTON GSP | MANNINGTON BSP | ROCKBOURNE | MINIMUM HEADROOM | SU 11617 17810 | YES | -0.12498 | -0.16708 | -0.22348 | -0.2978 | -0.373 | -0.46285 | -0.56947 | -0.68374 | -0.83388 | -1.1058 | -1.5815 | -1.8949 | -2.0178 | 0.88576 | 0.85914 | 0.81866 | 0.77545 | 0.73057 | 0.67731 | 0.6092 | 0.53662 | 0.44361 | 0.31783 | 0.13432 | 0.0087323 | -0.069998 | 0.39195 | 0.35274 | 0.29927 | 0.23056 | 0.16082 | 0.07757 | -0.022134 | -0.12624 | -0.2623 | -0.51467 | -0.93638 | -1.2122 | -1.3203
|  | ROCKBOURNE | CT |  |  | -0.12498 | -0.16708 | -0.22348 | -0.2978 | -0.373 | -0.46285 | -0.56947 | -0.68374 | -0.83388 | -1.1058 | -1.5815 | -1.8949 | -2.0178 | 0.88576 | 0.85914 | 0.81866 | 0.77545 | 0.73057 | 0.67731 | 0.6092 | 0.53662 | 0.44361 | 0.31783 | 0.13432 | 0.0087323 | -0.069998 | 0.39195 | 0.35274 | 0.29927 | 0.23056 | 0.16082 | 0.07757 | -0.022134 | -0.12624 | -0.2623 | -0.51467 | -0.93638 | -1.2122 | -1.3203
|  | ROCKBOURNE | LW |  |  | -0.12498 | -0.16708 | -0.22348 | -0.2978 | -0.373 | -0.46285 | -0.56947 | -0.68374 | -0.83388 | -1.1058 | -1.5815 | -1.8949 | -2.0178 | 0.88576 | 0.85914 | 0.81866 | 0.77545 | 0.73057 | 0.67731 | 0.6092 | 0.53662 | 0.44361 | 0.31783 | 0.13432 | 0.0087323 | -0.069998 | 0.39195 | 0.35274 | 0.29927 | 0.23056 | 0.16082 | 0.07757 | -0.022134 | -0.12624 | -0.2623 | -0.51467 | -0.93638 | -1.2122 | -1.3203
|  | ROCKBOURNE | ST |  |  | -0.12498 | -0.16708 | -0.22348 | -0.2978 | -0.373 | -0.46285 | -0.56947 | -0.68374 | -0.83388 | -1.1058 | -1.5815 | -1.8949 | -2.0178 | 0.88576 | 0.85914 | 0.81866 | 0.77545 | 0.73057 | 0.67731 | 0.6092 | 0.53662 | 0.44361 | 0.31783 | 0.13432 | 0.0087323 | -0.069998 | 0.39195 | 0.35274 | 0.29927 | 0.23056 | 0.16082 | 0.07757 | -0.022134 | -0.12624 | -0.2623 | -0.51467 | -0.93638 | -1.2122 | -1.3203
|  | ROCKBOURNE | FS |  |  | -0.12498 | -0.16708 | -0.22348 | -0.2978 | -0.373 | -0.46285 | -0.56947 | -0.68374 | -0.83388 | -1.1058 | -1.5815 | -1.8949 | -2.0178 | 0.88576 | 0.85914 | 0.81866 | 0.77545 | 0.73057 | 0.67731 | 0.6092 | 0.53662 | 0.44361 | 0.31783 | 0.13432 | 0.0087323 | -0.069998 | 0.39195 | 0.35274 | 0.29927 | 0.23056 | 0.16082 | 0.07757 | -0.022134 | -0.12624 | -0.2623 | -0.51467 | -0.93638 | -1.2122 | -1.3203
NURSLING GSP | ROWNHAMS | ROMSEY | MINIMUM HEADROOM | SU 36092 21110 | YES | -4.0229 | -4.5528 | -5.2252 | -6.2487 | -7.3208 | -8.4175 | -9.6312 | -11.0094 | -12.9425 | -17.9137 | -24.2511 | -28.2575 | -30.0471 | 2.7194 | 2.3912 | 2.0271 | 1.3796 | 0.69748 | -0.01352 | -0.80741 | -1.7239 | -2.9372 | -5.9506 | -9.7181 | -12.4808 | -15.1147 | -1.1765 | -1.6667 | -2.2671 | -3.1708 | -4.1185 | -5.088 | -6.1594 | -7.3748 | -9.0985 | -13.5632 | -19.4713 | -23.1838 | -24.7553
|  | ROMSEY | CT |  |  | -4.0229 | -4.5528 | -5.2252 | -6.2487 | -7.3208 | -8.4175 | -9.6312 | -11.0094 | -12.9425 | -17.9137 | -24.2511 | -28.2575 | -30.0471 | 2.7194 | 2.3912 | 2.0271 | 1.3796 | 0.69748 | -0.01352 | -0.80741 | -1.7239 | -2.9372 | -5.9506 | -9.7181 | -12.4808 | -15.1147 | -1.1765 | -1.6667 | -2.2671 | -3.1708 | -4.1185 | -5.088 | -6.1594 | -7.3748 | -9.0985 | -13.5632 | -19.4713 | -23.1838 | -24.7553
|  | ROMSEY | LW |  |  | -4.0229 | -4.5528 | -5.2252 | -6.2487 | -7.3208 | -8.4175 | -9.6312 | -11.0094 | -12.9425 | -17.9137 | -24.2511 | -28.2575 | -30.0471 | 2.7194 | 2.3912 | 2.0271 | 1.3796 | 0.69748 | -0.01352 | -0.80741 | -1.7239 | -2.9372 | -5.9506 | -9.7181 | -12.4808 | -15.1147 | -1.1765 | -1.6667 | -2.2671 | -3.1708 | -4.1185 | -5.088 | -6.1594 | -7.3748 | -9.0985 | -13.5632 | -19.4713 | -23.1838 | -24.7553
|  | ROMSEY | ST |  |  | -4.0229 | -4.5528 | -5.2252 | -6.2487 | -7.3208 | -8.4175 | -9.6312 | -11.0094 | -12.9425 | -17.9137 | -24.2511 | -28.2575 | -30.0471 | 2.7194 | 2.3912 | 2.0271 | 1.3796 | 0.69748 | -0.01352 | -0.80741 | -1.7239 | -2.9372 | -5.9506 | -9.7181 | -12.4808 | -15.1147 | -1.1765 | -1.6667 | -2.2671 | -3.1708 | -4.1185 | -5.088 | -6.1594 | -7.3748 | -9.0985 | -13.5632 | -19.4713 | -23.1838 | -24.7553
|  | ROMSEY | FS |  |  | -4.0229 | -4.5528 | -5.2252 | -6.2487 | -7.3208 | -8.4175 | -9.6312 | -11.0094 | -12.9425 | -17.9137 | -24.2511 | -28.2575 | -30.0471 | 2.7194 | 2.3912 | 2.0271 | 1.3796 | 0.69748 | -0.01352 | -0.80741 | -1.7239 | -2.9372 | -5.9506 | -9.7181 | -12.4808 | -15.1147 | -1.1765 | -1.6667 | -2.2671 | -3.1708 | -4.1185 | -5.088 | -6.1594 | -7.3748 | -9.0985 | -13.5632 | -19.4713 | -23.1838 | -24.7553
LOVEDEAN GSP | CHICHESTER & HUNSTON | ROSE GREEN | MINIMUM HEADROOM | SZ 89974 99335 | YES | 12.4226 | 12.0771 | 11.6293 | 11.1545 | 10.6936 | 10.2213 | 9.744 | 9.2299 | 8.1779 | 5.2983 | 1.4326 | -1.4747 | -2.9217 | 16.2826 | 16.0005 | 15.5636 | 15.1604 | 14.7578 | 14.3379 | 13.8998 | 13.3887 | 12.6745 | 10.7974 | 8.9258 | 7.5253 | 6.456 | 13.7517 | 13.5778 | 13.3688 | 13.1107 | 12.8614 | 12.6037 | 12.0222 | 11.3224 | 10.2801 | 7.495 | 4.2114 | 1.8374 | 0.66333
|  | ROSE GREEN | CT |  |  | 12.4226 | 12.0771 | 11.6293 | 11.1545 | 10.6936 | 10.2213 | 9.744 | 9.2299 | 8.1779 | 5.2983 | 1.4326 | -1.4747 | -2.9217 | 16.2826 | 16.0005 | 15.5636 | 15.1604 | 14.7578 | 14.3379 | 13.8998 | 13.3887 | 12.6745 | 10.7974 | 8.9258 | 7.5253 | 6.456 | 13.7517 | 13.5778 | 13.3688 | 13.1107 | 12.8614 | 12.6037 | 12.0222 | 11.3224 | 10.2801 | 7.495 | 4.2114 | 1.8374 | 0.66333
|  | ROSE GREEN | LW |  |  | 12.4226 | 12.0771 | 11.6293 | 11.1545 | 10.6936 | 10.2213 | 9.744 | 9.2299 | 8.1779 | 5.2983 | 1.4326 | -1.4747 | -2.9217 | 16.2826 | 16.0005 | 15.5636 | 15.1604 | 14.7578 | 14.3379 | 13.8998 | 13.3887 | 12.6745 | 10.7974 | 8.9258 | 7.5253 | 6.456 | 13.7517 | 13.5778 | 13.3688 | 13.1107 | 12.8614 | 12.6037 | 12.0222 | 11.3224 | 10.2801 | 7.495 | 4.2114 | 1.8374 | 0.66333
|  | ROSE GREEN | ST |  |  | 12.4226 | 12.0771 | 11.6293 | 11.1545 | 10.6936 | 10.2213 | 9.744 | 9.2299 | 8.1779 | 5.2983 | 1.4326 | -1.4747 | -2.9217 | 16.2826 | 16.0005 | 15.5636 | 15.1604 | 14.7578 | 14.3379 | 13.8998 | 13.3887 | 12.6745 | 10.7974 | 8.9258 | 7.5253 | 6.456 | 13.7517 | 13.5778 | 13.3688 | 13.1107 | 12.8614 | 12.6037 | 12.0222 | 11.3224 | 10.2801 | 7.495 | 4.2114 | 1.8374 | 0.66333
|  | ROSE GREEN | FS |  |  | 12.4226 | 12.0771 | 11.6293 | 11.1545 | 10.6936 | 10.2213 | 9.744 | 9.2299 | 8.1779 | 5.2983 | 1.4326 | -1.4747 | -2.9217 | 16.2826 | 16.0005 | 15.5636 | 15.1604 | 14.7578 | 14.3379 | 13.8998 | 13.3887 | 12.6745 | 10.7974 | 8.9258 | 7.5253 | 6.456 | 13.7517 | 13.5778 | 13.3688 | 13.1107 | 12.8614 | 12.6037 | 12.0222 | 11.3224 | 10.2801 | 7.495 | 4.2114 | 1.8374 | 0.66333
COWLEY GSP | COWLEY LOCAL (2 X 90) | ROSE HILL | MINIMUM HEADROOM | SP 53637 03027 | YES | 10.7347 | 10.3431 | 9.9072 | 9.1601 | 8.2108 | 7.0395 | 5.8942 | 4.4339 | 2.6513 | -3.4632 | -10.6492 | -14.6851 | -17.2054 | 12.5597 | 12.2664 | 11.906 | 11.4047 | 10.8145 | 10.0919 | 9.347 | 8.4343 | 7.3766 | 3.7551 | -0.5519 | -3.519 | -6.7451 | 11.469 | 11.1244 | 10.7196 | 10.059 | 9.2377 | 8.2301 | 7.229 | 5.9644 | 4.406 | -0.90529 | -7.1207 | -10.5107 | -12.6141
|  | ROSE HILL | CT |  |  | 10.7347 | 10.3431 | 9.9072 | 9.1601 | 8.2108 | 7.0395 | 5.8942 | 4.4339 | 2.6513 | -3.4632 | -10.6492 | -14.6851 | -17.2054 | 12.5597 | 12.2664 | 11.906 | 11.4047 | 10.8145 | 10.0919 | 9.347 | 8.4343 | 7.3766 | 3.7551 | -0.5519 | -3.519 | -6.7451 | 11.469 | 11.1244 | 10.7196 | 10.059 | 9.2377 | 8.2301 | 7.229 | 5.9644 | 4.406 | -0.90529 | -7.1207 | -10.5107 | -12.6141
|  | ROSE HILL | LW |  |  | 10.7347 | 10.3431 | 9.9072 | 9.1601 | 8.2108 | 7.0395 | 5.8942 | 4.4339 | 2.6513 | -3.4632 | -10.6492 | -14.6851 | -17.2054 | 12.5597 | 12.2664 | 11.906 | 11.4047 | 10.8145 | 10.0919 | 9.347 | 8.4343 | 7.3766 | 3.7551 | -0.5519 | -3.519 | -6.7451 | 11.469 | 11.1244 | 10.7196 | 10.059 | 9.2377 | 8.2301 | 7.229 | 5.9644 | 4.406 | -0.90529 | -7.1207 | -10.5107 | -12.6141
|  | ROSE HILL | ST |  |  | 10.7347 | 10.3431 | 9.9072 | 9.1601 | 8.2108 | 7.0395 | 5.8942 | 4.4339 | 2.6513 | -3.4632 | -10.6492 | -14.6851 | -17.2054 | 12.5597 | 12.2664 | 11.906 | 11.4047 | 10.8145 | 10.0919 | 9.347 | 8.4343 | 7.3766 | 3.7551 | -0.5519 | -3.519 | -6.7451 | 11.469 | 11.1244 | 10.7196 | 10.059 | 9.2377 | 8.2301 | 7.229 | 5.9644 | 4.406 | -0.90529 | -7.1207 | -10.5107 | -12.6141
|  | ROSE HILL | FS |  |  | 10.7347 | 10.3431 | 9.9072 | 9.1601 | 8.2108 | 7.0395 | 5.8942 | 4.4339 | 2.6513 | -3.4632 | -10.6492 | -14.6851 | -17.2054 | 12.5597 | 12.2664 | 11.906 | 11.4047 | 10.8145 | 10.0919 | 9.347 | 8.4343 | 7.3766 | 3.7551 | -0.5519 | -3.519 | -6.7451 | 11.469 | 11.1244 | 10.7196 | 10.059 | 9.2377 | 8.2301 | 7.229 | 5.9644 | 4.406 | -0.90529 | -7.1207 | -10.5107 | -12.6141
MELKSHAM GSP | CHIPPENHAM | ROWDEN | MINIMUM HEADROOM | ST 90805 72608 | YES | 4.4865 | 3.7266 | 2.7489 | 1.8748 | 1.0805 | 0.24506 | -0.65153 | -1.6826 | -3.2901 | -7.4245 | -13.4822 | -17.6485 | -19.5053 | 9.9755 | 9.4555 | 8.7617 | 8.1635 | 7.6316 | 7.0666 | 6.4625 | 5.7606 | 4.7559 | 2.1716 | -1.3314 | -3.9227 | -6.1659 | 6.2826 | 5.6258 | 4.7653 | 3.9686 | 3.2438 | 2.4839 | 1.6404 | 0.66242 | -0.85233 | -4.7102 | -10.1842 | -13.9121 | -15.5382
|  | ROWDEN | CT |  |  | 4.4865 | 3.7266 | 2.7489 | 1.8748 | 1.0805 | 0.24506 | -0.65153 | -1.6826 | -3.2901 | -7.4245 | -13.4822 | -17.6485 | -19.5053 | 9.9755 | 9.4555 | 8.7617 | 8.1635 | 7.6316 | 7.0666 | 6.4625 | 5.7606 | 4.7559 | 2.1716 | -1.3314 | -3.9227 | -6.1659 | 6.2826 | 5.6258 | 4.7653 | 3.9686 | 3.2438 | 2.4839 | 1.6404 | 0.66242 | -0.85233 | -4.7102 | -10.1842 | -13.9121 | -15.5382
|  | ROWDEN | LW |  |  | 4.4865 | 3.7266 | 2.7489 | 1.8748 | 1.0805 | 0.24506 | -0.65153 | -1.6826 | -3.2901 | -7.4245 | -13.4822 | -17.6485 | -19.5053 | 9.9755 | 9.4555 | 8.7617 | 8.1635 | 7.6316 | 7.0666 | 6.4625 | 5.7606 | 4.7559 | 2.1716 | -1.3314 | -3.9227 | -6.1659 | 6.2826 | 5.6258 | 4.7653 | 3.9686 | 3.2438 | 2.4839 | 1.6404 | 0.66242 | -0.85233 | -4.7102 | -10.1842 | -13.9121 | -15.5382
|  | ROWDEN | ST |  |  | 4.4865 | 3.7266 | 2.7489 | 1.8748 | 1.0805 | 0.24506 | -0.65153 | -1.6826 | -3.2901 | -7.4245 | -13.4822 | -17.6485 | -19.5053 | 9.9755 | 9.4555 | 8.7617 | 8.1635 | 7.6316 | 7.0666 | 6.4625 | 5.7606 | 4.7559 | 2.1716 | -1.3314 | -3.9227 | -6.1659 | 6.2826 | 5.6258 | 4.7653 | 3.9686 | 3.2438 | 2.4839 | 1.6404 | 0.66242 | -0.85233 | -4.7102 | -10.1842 | -13.9121 | -15.5382
|  | ROWDEN | FS |  |  | 4.4865 | 3.7266 | 2.7489 | 1.8748 | 1.0805 | 0.24506 | -0.65153 | -1.6826 | -3.2901 | -7.4245 | -13.4822 | -17.6485 | -19.5053 | 9.9755 | 9.4555 | 8.7617 | 8.1635 | 7.6316 | 7.0666 | 6.4625 | 5.7606 | 4.7559 | 2.1716 | -1.3314 | -3.9227 | -6.1659 | 6.2826 | 5.6258 | 4.7653 | 3.9686 | 3.2438 | 2.4839 | 1.6404 | 0.66242 | -0.85233 | -4.7102 | -10.1842 | -13.9121 | -15.5382
LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | ROWNER PARK | MINIMUM HEADROOM | SU 58018 00782 | YES | 18.1844 | 17.9913 | 17.7435 | 17.3992 | 17.0317 | 16.6492 | 16.2349 | 15.7528 | 15.0246 | 12.7735 | 8.926 | 6.1189 | 4.4579 | 17.8577 | 17.7405 | 17.619 | 17.4647 | 17.2978 | 17.1243 | 16.9361 | 16.7036 | 16.402 | 15.4159 | 13.7188 | 12.0169 | 10.3692 | 19.0256 | 18.8957 | 18.7741 | 18.5604 | 18.335 | 18.1051 | 17.8597 | 17.5836 | 17.1323 | 15.5194 | 12.1097 | 9.6996 | 8.3037
|  | ROWNER PARK | CT |  |  | 18.1844 | 17.9913 | 17.7435 | 17.3992 | 17.0317 | 16.6492 | 16.2349 | 15.7528 | 15.0246 | 12.7735 | 8.926 | 6.1189 | 4.4579 | 17.8577 | 17.7405 | 17.619 | 17.4647 | 17.2978 | 17.1243 | 16.9361 | 16.7036 | 16.402 | 15.4159 | 13.7188 | 12.0169 | 10.3692 | 19.0256 | 18.8957 | 18.7741 | 18.5604 | 18.335 | 18.1051 | 17.8597 | 17.5836 | 17.1323 | 15.5194 | 12.1097 | 9.6996 | 8.3037
|  | ROWNER PARK | LW |  |  | 18.1844 | 17.9913 | 17.7435 | 17.3992 | 17.0317 | 16.6492 | 16.2349 | 15.7528 | 15.0246 | 12.7735 | 8.926 | 6.1189 | 4.4579 | 17.8577 | 17.7405 | 17.619 | 17.4647 | 17.2978 | 17.1243 | 16.9361 | 16.7036 | 16.402 | 15.4159 | 13.7188 | 12.0169 | 10.3692 | 19.0256 | 18.8957 | 18.7741 | 18.5604 | 18.335 | 18.1051 | 17.8597 | 17.5836 | 17.1323 | 15.5194 | 12.1097 | 9.6996 | 8.3037
|  | ROWNER PARK | ST |  |  | 18.1844 | 17.9913 | 17.7435 | 17.3992 | 17.0317 | 16.6492 | 16.2349 | 15.7528 | 15.0246 | 12.7735 | 8.926 | 6.1189 | 4.4579 | 17.8577 | 17.7405 | 17.619 | 17.4647 | 17.2978 | 17.1243 | 16.9361 | 16.7036 | 16.402 | 15.4159 | 13.7188 | 12.0169 | 10.3692 | 19.0256 | 18.8957 | 18.7741 | 18.5604 | 18.335 | 18.1051 | 17.8597 | 17.5836 | 17.1323 | 15.5194 | 12.1097 | 9.6996 | 8.3037
|  | ROWNER PARK | FS |  |  | 18.1844 | 17.9913 | 17.7435 | 17.3992 | 17.0317 | 16.6492 | 16.2349 | 15.7528 | 15.0246 | 12.7735 | 8.926 | 6.1189 | 4.4579 | 17.8577 | 17.7405 | 17.619 | 17.4647 | 17.2978 | 17.1243 | 16.9361 | 16.7036 | 16.402 | 15.4159 | 13.7188 | 12.0169 | 10.3692 | 19.0256 | 18.8957 | 18.7741 | 18.5604 | 18.335 | 18.1051 | 17.8597 | 17.5836 | 17.1323 | 15.5194 | 12.1097 | 9.6996 | 8.3037
FAWLEY GSP | COWES & WOOTTON COMMON BSP | RYDE | MINIMUM HEADROOM | SZ 59554 91973 | YES | 18.2181 | 17.653 | 16.863 | 15.9679 | 15.0125 | 13.9663 | 12.9725 | 11.9175 | 10.2484 | 5.161 | -2.0716 | -7.018 | -9.3638 | 21.0726 | 20.7027 | 20.1508 | 19.5768 | 18.9609 | 18.2814 | 17.6111 | 16.8727 | 15.8176 | 12.5457 | 8.3123 | 4.9588 | 1.6373 | 20.696 | 20.2053 | 19.4871 | 18.6732 | 17.8039 | 16.8478 | 15.9239 | 14.9313 | 13.3751 | 8.6257 | 2.1088 | -2.1511 | -4.0631
|  | RYDE | CT |  |  | 18.2181 | 17.653 | 16.863 | 15.9679 | 15.0125 | 13.9663 | 12.9725 | 11.9175 | 10.2484 | 5.161 | -2.0716 | -7.018 | -9.3638 | 21.0726 | 20.7027 | 20.1508 | 19.5768 | 18.9609 | 18.2814 | 17.6111 | 16.8727 | 15.8176 | 12.5457 | 8.3123 | 4.9588 | 1.6373 | 20.696 | 20.2053 | 19.4871 | 18.6732 | 17.8039 | 16.8478 | 15.9239 | 14.9313 | 13.3751 | 8.6257 | 2.1088 | -2.1511 | -4.0631
|  | RYDE | LW |  |  | 18.2181 | 17.653 | 16.863 | 15.9679 | 15.0125 | 13.9663 | 12.9725 | 11.9175 | 10.2484 | 5.161 | -2.0716 | -7.018 | -9.3638 | 21.0726 | 20.7027 | 20.1508 | 19.5768 | 18.9609 | 18.2814 | 17.6111 | 16.8727 | 15.8176 | 12.5457 | 8.3123 | 4.9588 | 1.6373 | 20.696 | 20.2053 | 19.4871 | 18.6732 | 17.8039 | 16.8478 | 15.9239 | 14.9313 | 13.3751 | 8.6257 | 2.1088 | -2.1511 | -4.0631
|  | RYDE | ST |  |  | 18.2181 | 17.653 | 16.863 | 15.9679 | 15.0125 | 13.9663 | 12.9725 | 11.9175 | 10.2484 | 5.161 | -2.0716 | -7.018 | -9.3638 | 21.0726 | 20.7027 | 20.1508 | 19.5768 | 18.9609 | 18.2814 | 17.6111 | 16.8727 | 15.8176 | 12.5457 | 8.3123 | 4.9588 | 1.6373 | 20.696 | 20.2053 | 19.4871 | 18.6732 | 17.8039 | 16.8478 | 15.9239 | 14.9313 | 13.3751 | 8.6257 | 2.1088 | -2.1511 | -4.0631
|  | RYDE | FS |  |  | 18.2181 | 17.653 | 16.863 | 15.9679 | 15.0125 | 13.9663 | 12.9725 | 11.9175 | 10.2484 | 5.161 | -2.0716 | -7.018 | -9.3638 | 21.0726 | 20.7027 | 20.1508 | 19.5768 | 18.9609 | 18.2814 | 17.6111 | 16.8727 | 15.8176 | 12.5457 | 8.3123 | 4.9588 | 1.6373 | 20.696 | 20.2053 | 19.4871 | 18.6732 | 17.8039 | 16.8478 | 15.9239 | 14.9313 | 13.3751 | 8.6257 | 2.1088 | -2.1511 | -4.0631
MANNINGTON GSP | SALISBURY | SALISBURY CENTRAL | MINIMUM HEADROOM | SU 14215 30481 | YES | 14.3598 | 13.9125 | 13.4306 | 12.6682 | 11.8013 | 10.9415 | 9.9701 | 8.8687 | 7.1932 | 2.3683 | -5.3784 | -10.4759 | -12.7496 | 22.0443 | 21.703 | 21.4616 | 21.1394 | 20.4442 | 19.8043 | 19.0616 | 18.2035 | 17.1121 | 13.8193 | 9.1361 | 5.4997 | 1.6826 | 16.6773 | 16.3113 | 15.9717 | 15.2217 | 14.3291 | 13.495 | 12.5539 | 11.4838 | 9.8743 | 5.2381 | -1.6771 | -6.0911 | -8.0792
|  | SALISBURY CENTRAL | CT |  |  | 14.3598 | 13.9125 | 13.4306 | 12.6682 | 11.8013 | 10.9415 | 9.9701 | 8.8687 | 7.1932 | 2.3683 | -5.3784 | -10.4759 | -12.7496 | 22.0443 | 21.703 | 21.4616 | 21.1394 | 20.4442 | 19.8043 | 19.0616 | 18.2035 | 17.1121 | 13.8193 | 9.1361 | 5.4997 | 1.6826 | 16.6773 | 16.3113 | 15.9717 | 15.2217 | 14.3291 | 13.495 | 12.5539 | 11.4838 | 9.8743 | 5.2381 | -1.6771 | -6.0911 | -8.0792
|  | SALISBURY CENTRAL | LW |  |  | 14.3598 | 13.9125 | 13.4306 | 12.6682 | 11.8013 | 10.9415 | 9.9701 | 8.8687 | 7.1932 | 2.3683 | -5.3784 | -10.4759 | -12.7496 | 22.0443 | 21.703 | 21.4616 | 21.1394 | 20.4442 | 19.8043 | 19.0616 | 18.2035 | 17.1121 | 13.8193 | 9.1361 | 5.4997 | 1.6826 | 16.6773 | 16.3113 | 15.9717 | 15.2217 | 14.3291 | 13.495 | 12.5539 | 11.4838 | 9.8743 | 5.2381 | -1.6771 | -6.0911 | -8.0792
|  | SALISBURY CENTRAL | ST |  |  | 14.3598 | 13.9125 | 13.4306 | 12.6682 | 11.8013 | 10.9415 | 9.9701 | 8.8687 | 7.1932 | 2.3683 | -5.3784 | -10.4759 | -12.7496 | 22.0443 | 21.703 | 21.4616 | 21.1394 | 20.4442 | 19.8043 | 19.0616 | 18.2035 | 17.1121 | 13.8193 | 9.1361 | 5.4997 | 1.6826 | 16.6773 | 16.3113 | 15.9717 | 15.2217 | 14.3291 | 13.495 | 12.5539 | 11.4838 | 9.8743 | 5.2381 | -1.6771 | -6.0911 | -8.0792
|  | SALISBURY CENTRAL | FS |  |  | 14.3598 | 13.9125 | 13.4306 | 12.6682 | 11.8013 | 10.9415 | 9.9701 | 8.8687 | 7.1932 | 2.3683 | -5.3784 | -10.4759 | -12.7496 | 22.0443 | 21.703 | 21.4616 | 21.1394 | 20.4442 | 19.8043 | 19.0616 | 18.2035 | 17.1121 | 13.8193 | 9.1361 | 5.4997 | 1.6826 | 16.6773 | 16.3113 | 15.9717 | 15.2217 | 14.3291 | 13.495 | 12.5539 | 11.4838 | 9.8743 | 5.2381 | -1.6771 | -6.0911 | -8.0792
BRAMLEY (FLEE) | CAMBERLEY MAIN | SANDHURST | MINIMUM HEADROOM | SU 83597 60930 | YES | 15.7493 | 15.1666 | 14.405 | 13.4019 | 12.3263 | 11.1789 | 9.821 | 8.2041 | 5.7504 | 0.73124 | -7.8227 | -13.7424 | -16.8391 | 15.4006 | 14.9503 | 14.339 | 13.6497 | 12.9008 | 12.0805 | 11.0917 | 9.8888 | 8.2183 | 5.0918 | 0.20144 | -3.2619 | -6.1072 | 17.1799 | 16.5657 | 15.7951 | 14.843 | 13.8187 | 12.7211 | 11.4159 | 9.8535 | 7.5129 | 2.8411 | -4.892 | -10.0813 | -12.6145
|  | SANDHURST | CT |  |  | 15.7493 | 15.1666 | 14.405 | 13.4019 | 12.3263 | 11.1789 | 9.821 | 8.2041 | 5.7504 | 0.73124 | -7.8227 | -13.7424 | -16.8391 | 15.4006 | 14.9503 | 14.339 | 13.6497 | 12.9008 | 12.0805 | 11.0917 | 9.8888 | 8.2183 | 5.0918 | 0.20144 | -3.2619 | -6.1072 | 17.1799 | 16.5657 | 15.7951 | 14.843 | 13.8187 | 12.7211 | 11.4159 | 9.8535 | 7.5129 | 2.8411 | -4.892 | -10.0813 | -12.6145
|  | SANDHURST | LW |  |  | 15.7493 | 15.1666 | 14.405 | 13.4019 | 12.3263 | 11.1789 | 9.821 | 8.2041 | 5.7504 | 0.73124 | -7.8227 | -13.7424 | -16.8391 | 15.4006 | 14.9503 | 14.339 | 13.6497 | 12.9008 | 12.0805 | 11.0917 | 9.8888 | 8.2183 | 5.0918 | 0.20144 | -3.2619 | -6.1072 | 17.1799 | 16.5657 | 15.7951 | 14.843 | 13.8187 | 12.7211 | 11.4159 | 9.8535 | 7.5129 | 2.8411 | -4.892 | -10.0813 | -12.6145
|  | SANDHURST | ST |  |  | 15.7493 | 15.1666 | 14.405 | 13.4019 | 12.3263 | 11.1789 | 9.821 | 8.2041 | 5.7504 | 0.73124 | -7.8227 | -13.7424 | -16.8391 | 15.4006 | 14.9503 | 14.339 | 13.6497 | 12.9008 | 12.0805 | 11.0917 | 9.8888 | 8.2183 | 5.0918 | 0.20144 | -3.2619 | -6.1072 | 17.1799 | 16.5657 | 15.7951 | 14.843 | 13.8187 | 12.7211 | 11.4159 | 9.8535 | 7.5129 | 2.8411 | -4.892 | -10.0813 | -12.6145
|  | SANDHURST | FS |  |  | 15.7493 | 15.1666 | 14.405 | 13.4019 | 12.3263 | 11.1789 | 9.821 | 8.2041 | 5.7504 | 0.73124 | -7.8227 | -13.7424 | -16.8391 | 15.4006 | 14.9503 | 14.339 | 13.6497 | 12.9008 | 12.0805 | 11.0917 | 9.8888 | 8.2183 | 5.0918 | 0.20144 | -3.2619 | -6.1072 | 17.1799 | 16.5657 | 15.7951 | 14.843 | 13.8187 | 12.7211 | 11.4159 | 9.8535 | 7.5129 | 2.8411 | -4.892 | -10.0813 | -12.6145
FAWLEY GSP | COWES & WOOTTON COMMON BSP | SANDOWN | MINIMUM HEADROOM | SZ 59877 85052 | YES | 5.4861 | 5.2425 | 4.8285 | 4.2854 | 3.7171 | 3.0968 | 2.4286 | 1.657 | 0.49062 | -3.0225 | -8.5988 | -12.3909 | -14.1015 | 6.7275 | 6.5403 | 6.1883 | 5.8258 | 5.4426 | 5.0197 | 4.558 | 4.003 | 3.2557 | 1.0443 | -1.6131 | -3.5177 | -5.0468 | 7.3543 | 7.106 | 6.6764 | 6.1517 | 5.6013 | 4.9982 | 4.3468 | 3.5867 | 2.4413 | -0.99147 | -5.8252 | -9.0285 | -10.4628
|  | SANDOWN | CT |  |  | 5.4861 | 5.2425 | 4.8285 | 4.2854 | 3.7171 | 3.0968 | 2.4286 | 1.657 | 0.49062 | -3.0225 | -8.5988 | -12.3909 | -14.1015 | 6.7275 | 6.5403 | 6.1883 | 5.8258 | 5.4426 | 5.0197 | 4.558 | 4.003 | 3.2557 | 1.0443 | -1.6131 | -3.5177 | -5.0468 | 7.3543 | 7.106 | 6.6764 | 6.1517 | 5.6013 | 4.9982 | 4.3468 | 3.5867 | 2.4413 | -0.99147 | -5.8252 | -9.0285 | -10.4628
|  | SANDOWN | LW |  |  | 5.4861 | 5.2425 | 4.8285 | 4.2854 | 3.7171 | 3.0968 | 2.4286 | 1.657 | 0.49062 | -3.0225 | -8.5988 | -12.3909 | -14.1015 | 6.7275 | 6.5403 | 6.1883 | 5.8258 | 5.4426 | 5.0197 | 4.558 | 4.003 | 3.2557 | 1.0443 | -1.6131 | -3.5177 | -5.0468 | 7.3543 | 7.106 | 6.6764 | 6.1517 | 5.6013 | 4.9982 | 4.3468 | 3.5867 | 2.4413 | -0.99147 | -5.8252 | -9.0285 | -10.4628
|  | SANDOWN | ST |  |  | 5.4861 | 5.2425 | 4.8285 | 4.2854 | 3.7171 | 3.0968 | 2.4286 | 1.657 | 0.49062 | -3.0225 | -8.5988 | -12.3909 | -14.1015 | 6.7275 | 6.5403 | 6.1883 | 5.8258 | 5.4426 | 5.0197 | 4.558 | 4.003 | 3.2557 | 1.0443 | -1.6131 | -3.5177 | -5.0468 | 7.3543 | 7.106 | 6.6764 | 6.1517 | 5.6013 | 4.9982 | 4.3468 | 3.5867 | 2.4413 | -0.99147 | -5.8252 | -9.0285 | -10.4628
|  | SANDOWN | FS |  |  | 5.4861 | 5.2425 | 4.8285 | 4.2854 | 3.7171 | 3.0968 | 2.4286 | 1.657 | 0.49062 | -3.0225 | -8.5988 | -12.3909 | -14.1015 | 6.7275 | 6.5403 | 6.1883 | 5.8258 | 5.4426 | 5.0197 | 4.558 | 4.003 | 3.2557 | 1.0443 | -1.6131 | -3.5177 | -5.0468 | 7.3543 | 7.106 | 6.6764 | 6.1517 | 5.6013 | 4.9982 | 4.3468 | 3.5867 | 2.4413 | -0.99147 | -5.8252 | -9.0285 | -10.4628
LOVEDEAN GSP | CHICHESTER & HUNSTON | SELSEY | MINIMUM HEADROOM | SZ 85667 94289 | YES | 9.3263 | 9.1108 | 8.8285 | 8.4306 | 7.9882 | 7.4955 | 6.9739 | 6.4071 | 5.4866 | 3.1036 | 0.028087 | -2.2907 | -3.4636 | 10.9962 | 10.853 | 10.6381 | 10.3878 | 10.1115 | 9.8021 | 9.4737 | 9.1103 | 8.5426 | 7.0909 | 5.5607 | 4.3784 | 3.4676 | 9.1451 | 8.9573 | 8.7059 | 8.3533 | 7.9634 | 7.5279 | 7.0665 | 6.5659 | 5.7425 | 3.5629 | 0.72054 | -1.422 | -2.4427
|  | SELSEY | CT |  |  | 9.3263 | 9.1108 | 8.8285 | 8.4306 | 7.9882 | 7.4955 | 6.9739 | 6.4071 | 5.4866 | 3.1036 | 0.028087 | -2.2907 | -3.4636 | 10.9962 | 10.853 | 10.6381 | 10.3878 | 10.1115 | 9.8021 | 9.4737 | 9.1103 | 8.5426 | 7.0909 | 5.5607 | 4.3784 | 3.4676 | 9.1451 | 8.9573 | 8.7059 | 8.3533 | 7.9634 | 7.5279 | 7.0665 | 6.5659 | 5.7425 | 3.5629 | 0.72054 | -1.422 | -2.4427
|  | SELSEY | LW |  |  | 9.3263 | 9.1108 | 8.8285 | 8.4306 | 7.9882 | 7.4955 | 6.9739 | 6.4071 | 5.4866 | 3.1036 | 0.028087 | -2.2907 | -3.4636 | 10.9962 | 10.853 | 10.6381 | 10.3878 | 10.1115 | 9.8021 | 9.4737 | 9.1103 | 8.5426 | 7.0909 | 5.5607 | 4.3784 | 3.4676 | 9.1451 | 8.9573 | 8.7059 | 8.3533 | 7.9634 | 7.5279 | 7.0665 | 6.5659 | 5.7425 | 3.5629 | 0.72054 | -1.422 | -2.4427
|  | SELSEY | ST |  |  | 9.3263 | 9.1108 | 8.8285 | 8.4306 | 7.9882 | 7.4955 | 6.9739 | 6.4071 | 5.4866 | 3.1036 | 0.028087 | -2.2907 | -3.4636 | 10.9962 | 10.853 | 10.6381 | 10.3878 | 10.1115 | 9.8021 | 9.4737 | 9.1103 | 8.5426 | 7.0909 | 5.5607 | 4.3784 | 3.4676 | 9.1451 | 8.9573 | 8.7059 | 8.3533 | 7.9634 | 7.5279 | 7.0665 | 6.5659 | 5.7425 | 3.5629 | 0.72054 | -1.422 | -2.4427
|  | SELSEY | FS |  |  | 9.3263 | 9.1108 | 8.8285 | 8.4306 | 7.9882 | 7.4955 | 6.9739 | 6.4071 | 5.4866 | 3.1036 | 0.028087 | -2.2907 | -3.4636 | 10.9962 | 10.853 | 10.6381 | 10.3878 | 10.1115 | 9.8021 | 9.4737 | 9.1103 | 8.5426 | 7.0909 | 5.5607 | 4.3784 | 3.4676 | 9.1451 | 8.9573 | 8.7059 | 8.3533 | 7.9634 | 7.5279 | 7.0665 | 6.5659 | 5.7425 | 3.5629 | 0.72054 | -1.422 | -2.4427
MANNINGTON GSP | SHAFTESBURY BSP | SHAFTESBURY | MINIMUM HEADROOM | ST 85605 23325 | YES | 2.8342 | 2.4583 | 1.8527 | 1.2605 | 0.62947 | -0.029912 | -0.71322 | -1.4874 | -2.7063 | -5.6987 | -10.605 | -14.0813 | -15.3868 | 5.4159 | 5.174 | 4.7306 | 4.3765 | 3.9936 | 3.5859 | 3.1595 | 2.6511 | 1.9101 | 0.20274 | -2.0696 | -3.7404 | -4.8906 | 4.7282 | 4.3928 | 3.836 | 3.315 | 2.7561 | 2.167 | 1.5489 | 0.83077 | -0.26952 | -3.0254 | -7.1824 | -10.2254 | -11.4152
|  | SHAFTESBURY | CT |  |  | 2.8342 | 2.4583 | 1.8527 | 1.2605 | 0.62947 | -0.029912 | -0.71322 | -1.4874 | -2.7063 | -5.6987 | -10.605 | -14.0813 | -15.3868 | 5.4159 | 5.174 | 4.7306 | 4.3765 | 3.9936 | 3.5859 | 3.1595 | 2.6511 | 1.9101 | 0.20274 | -2.0696 | -3.7404 | -4.8906 | 4.7282 | 4.3928 | 3.836 | 3.315 | 2.7561 | 2.167 | 1.5489 | 0.83077 | -0.26952 | -3.0254 | -7.1824 | -10.2254 | -11.4152
|  | SHAFTESBURY | LW |  |  | 2.8342 | 2.4583 | 1.8527 | 1.2605 | 0.62947 | -0.029912 | -0.71322 | -1.4874 | -2.7063 | -5.6987 | -10.605 | -14.0813 | -15.3868 | 5.4159 | 5.174 | 4.7306 | 4.3765 | 3.9936 | 3.5859 | 3.1595 | 2.6511 | 1.9101 | 0.20274 | -2.0696 | -3.7404 | -4.8906 | 4.7282 | 4.3928 | 3.836 | 3.315 | 2.7561 | 2.167 | 1.5489 | 0.83077 | -0.26952 | -3.0254 | -7.1824 | -10.2254 | -11.4152
|  | SHAFTESBURY | ST |  |  | 2.8342 | 2.4583 | 1.8527 | 1.2605 | 0.62947 | -0.029912 | -0.71322 | -1.4874 | -2.7063 | -5.6987 | -10.605 | -14.0813 | -15.3868 | 5.4159 | 5.174 | 4.7306 | 4.3765 | 3.9936 | 3.5859 | 3.1595 | 2.6511 | 1.9101 | 0.20274 | -2.0696 | -3.7404 | -4.8906 | 4.7282 | 4.3928 | 3.836 | 3.315 | 2.7561 | 2.167 | 1.5489 | 0.83077 | -0.26952 | -3.0254 | -7.1824 | -10.2254 | -11.4152
|  | SHAFTESBURY | FS |  |  | 2.8342 | 2.4583 | 1.8527 | 1.2605 | 0.62947 | -0.029912 | -0.71322 | -1.4874 | -2.7063 | -5.6987 | -10.605 | -14.0813 | -15.3868 | 5.4159 | 5.174 | 4.7306 | 4.3765 | 3.9936 | 3.5859 | 3.1595 | 2.6511 | 1.9101 | 0.20274 | -2.0696 | -3.7404 | -4.8906 | 4.7282 | 4.3928 | 3.836 | 3.315 | 2.7561 | 2.167 | 1.5489 | 0.83077 | -0.26952 | -3.0254 | -7.1824 | -10.2254 | -11.4152
FAWLEY GSP | COWES & WOOTTON COMMON BSP | SHALFLEET | MINIMUM HEADROOM | SZ 40828 88643 | YES | 11.7782 | 11.5972 | 11.3331 | 10.9933 | 10.6309 | 10.2364 | 9.8372 | 9.4008 | 8.7838 | 7.4442 | 5.5854 | 4.4694 | 4.0216 | 12.0675 | 11.9629 | 11.7952 | 11.6144 | 11.4167 | 11.2031 | 10.9786 | 10.7181 | 10.3455 | 9.673 | 8.9007 | 8.4059 | 8.1148 | 13.3583 | 13.1923 | 12.9481 | 12.6398 | 12.3097 | 11.9498 | 11.5808 | 11.1728 | 10.593 | 9.3636 | 7.6742 | 6.6878 | 6.2902
|  | SHALFLEET | CT |  |  | 11.7782 | 11.5972 | 11.3331 | 10.9933 | 10.6309 | 10.2364 | 9.8372 | 9.4008 | 8.7838 | 7.4442 | 5.5854 | 4.4694 | 4.0216 | 12.0675 | 11.9629 | 11.7952 | 11.6144 | 11.4167 | 11.2031 | 10.9786 | 10.7181 | 10.3455 | 9.673 | 8.9007 | 8.4059 | 8.1148 | 13.3583 | 13.1923 | 12.9481 | 12.6398 | 12.3097 | 11.9498 | 11.5808 | 11.1728 | 10.593 | 9.3636 | 7.6742 | 6.6878 | 6.2902
|  | SHALFLEET | LW |  |  | 11.7782 | 11.5972 | 11.3331 | 10.9933 | 10.6309 | 10.2364 | 9.8372 | 9.4008 | 8.7838 | 7.4442 | 5.5854 | 4.4694 | 4.0216 | 12.0675 | 11.9629 | 11.7952 | 11.6144 | 11.4167 | 11.2031 | 10.9786 | 10.7181 | 10.3455 | 9.673 | 8.9007 | 8.4059 | 8.1148 | 13.3583 | 13.1923 | 12.9481 | 12.6398 | 12.3097 | 11.9498 | 11.5808 | 11.1728 | 10.593 | 9.3636 | 7.6742 | 6.6878 | 6.2902
|  | SHALFLEET | ST |  |  | 11.7782 | 11.5972 | 11.3331 | 10.9933 | 10.6309 | 10.2364 | 9.8372 | 9.4008 | 8.7838 | 7.4442 | 5.5854 | 4.4694 | 4.0216 | 12.0675 | 11.9629 | 11.7952 | 11.6144 | 11.4167 | 11.2031 | 10.9786 | 10.7181 | 10.3455 | 9.673 | 8.9007 | 8.4059 | 8.1148 | 13.3583 | 13.1923 | 12.9481 | 12.6398 | 12.3097 | 11.9498 | 11.5808 | 11.1728 | 10.593 | 9.3636 | 7.6742 | 6.6878 | 6.2902
|  | SHALFLEET | FS |  |  | 11.7782 | 11.5972 | 11.3331 | 10.9933 | 10.6309 | 10.2364 | 9.8372 | 9.4008 | 8.7838 | 7.4442 | 5.5854 | 4.4694 | 4.0216 | 12.0675 | 11.9629 | 11.7952 | 11.6144 | 11.4167 | 11.2031 | 10.9786 | 10.7181 | 10.3455 | 9.673 | 8.9007 | 8.4059 | 8.1148 | 13.3583 | 13.1923 | 12.9481 | 12.6398 | 12.3097 | 11.9498 | 11.5808 | 11.1728 | 10.593 | 9.3636 | 7.6742 | 6.6878 | 6.2902
FAWLEY GSP | COWES & WOOTTON COMMON BSP | SHANKLIN | MINIMUM HEADROOM | SZ 57809 81912 | YES | 25.4122 | 25.1391 | 24.7167 | 24.2099 | 23.6787 | 23.084 | 22.4478 | 21.711 | 20.5549 | 17.1882 | 11.9744 | 8.0502 | 6.3153 | 24.557 | 24.3899 | 24.1319 | 23.8421 | 23.5354 | 23.1903 | 22.8179 | 22.3801 | 21.7424 | 19.8582 | 16.9567 | 14.4938 | 12.2953 | 27.3815 | 27.1414 | 26.7708 | 26.3099 | 25.8272 | 25.2877 | 24.7111 | 24.0469 | 22.992 | 19.9086 | 15.0783 | 11.625 | 10.1025
|  | SHANKLIN | CT |  |  | 25.4122 | 25.1391 | 24.7167 | 24.2099 | 23.6787 | 23.084 | 22.4478 | 21.711 | 20.5549 | 17.1882 | 11.9744 | 8.0502 | 6.3153 | 24.557 | 24.3899 | 24.1319 | 23.8421 | 23.5354 | 23.1903 | 22.8179 | 22.3801 | 21.7424 | 19.8582 | 16.9567 | 14.4938 | 12.2953 | 27.3815 | 27.1414 | 26.7708 | 26.3099 | 25.8272 | 25.2877 | 24.7111 | 24.0469 | 22.992 | 19.9086 | 15.0783 | 11.625 | 10.1025
|  | SHANKLIN | LW |  |  | 25.4122 | 25.1391 | 24.7167 | 24.2099 | 23.6787 | 23.084 | 22.4478 | 21.711 | 20.5549 | 17.1882 | 11.9744 | 8.0502 | 6.3153 | 24.557 | 24.3899 | 24.1319 | 23.8421 | 23.5354 | 23.1903 | 22.8179 | 22.3801 | 21.7424 | 19.8582 | 16.9567 | 14.4938 | 12.2953 | 27.3815 | 27.1414 | 26.7708 | 26.3099 | 25.8272 | 25.2877 | 24.7111 | 24.0469 | 22.992 | 19.9086 | 15.0783 | 11.625 | 10.1025
|  | SHANKLIN | ST |  |  | 25.4122 | 25.1391 | 24.7167 | 24.2099 | 23.6787 | 23.084 | 22.4478 | 21.711 | 20.5549 | 17.1882 | 11.9744 | 8.0502 | 6.3153 | 24.557 | 24.3899 | 24.1319 | 23.8421 | 23.5354 | 23.1903 | 22.8179 | 22.3801 | 21.7424 | 19.8582 | 16.9567 | 14.4938 | 12.2953 | 27.3815 | 27.1414 | 26.7708 | 26.3099 | 25.8272 | 25.2877 | 24.7111 | 24.0469 | 22.992 | 19.9086 | 15.0783 | 11.625 | 10.1025
|  | SHANKLIN | FS |  |  | 25.4122 | 25.1391 | 24.7167 | 24.2099 | 23.6787 | 23.084 | 22.4478 | 21.711 | 20.5549 | 17.1882 | 11.9744 | 8.0502 | 6.3153 | 24.557 | 24.3899 | 24.1319 | 23.8421 | 23.5354 | 23.1903 | 22.8179 | 22.3801 | 21.7424 | 19.8582 | 16.9567 | 14.4938 | 12.2953 | 27.3815 | 27.1414 | 26.7708 | 26.3099 | 25.8272 | 25.2877 | 24.7111 | 24.0469 | 22.992 | 19.9086 | 15.0783 | 11.625 | 10.1025
AXMINSTER | YEOVIL BSP | SHERBORNE | MINIMUM HEADROOM | ST 63978 18163 | YES | 1.0667 | 0.91228 | 0.70367 | 0.35957 | -0.039139 | -0.45549 | -0.89985 | -1.4933 | -2.3923 | -5.2037 | -10.001 | -13.0683 | -14.4378 | 2.8414 | 2.7398 | 2.5854 | 2.3843 | 2.1498 | 1.9003 | 1.6304 | 1.2748 | 0.7784 | -0.76658 | -3.1715 | -4.8238 | -6.2059 | 1.9139 | 1.765 | 1.5434 | 1.2199 | 0.84796 | 0.45635 | 0.036073 | -0.51043 | -1.3221 | -3.8278 | -7.9448 | -10.5529 | -11.7491
|  | SHERBORNE | CT |  |  | 1.0667 | 0.91228 | 0.70367 | 0.35957 | -0.039139 | -0.45549 | -0.89985 | -1.4933 | -2.3923 | -5.2037 | -10.001 | -13.0683 | -14.4378 | 2.8414 | 2.7398 | 2.5854 | 2.3843 | 2.1498 | 1.9003 | 1.6304 | 1.2748 | 0.7784 | -0.76658 | -3.1715 | -4.8238 | -6.2059 | 1.9139 | 1.765 | 1.5434 | 1.2199 | 0.84796 | 0.45635 | 0.036073 | -0.51043 | -1.3221 | -3.8278 | -7.9448 | -10.5529 | -11.7491
|  | SHERBORNE | LW |  |  | 1.0667 | 0.91228 | 0.70367 | 0.35957 | -0.039139 | -0.45549 | -0.89985 | -1.4933 | -2.3923 | -5.2037 | -10.001 | -13.0683 | -14.4378 | 2.8414 | 2.7398 | 2.5854 | 2.3843 | 2.1498 | 1.9003 | 1.6304 | 1.2748 | 0.7784 | -0.76658 | -3.1715 | -4.8238 | -6.2059 | 1.9139 | 1.765 | 1.5434 | 1.2199 | 0.84796 | 0.45635 | 0.036073 | -0.51043 | -1.3221 | -3.8278 | -7.9448 | -10.5529 | -11.7491
|  | SHERBORNE | ST |  |  | 1.0667 | 0.91228 | 0.70367 | 0.35957 | -0.039139 | -0.45549 | -0.89985 | -1.4933 | -2.3923 | -5.2037 | -10.001 | -13.0683 | -14.4378 | 2.8414 | 2.7398 | 2.5854 | 2.3843 | 2.1498 | 1.9003 | 1.6304 | 1.2748 | 0.7784 | -0.76658 | -3.1715 | -4.8238 | -6.2059 | 1.9139 | 1.765 | 1.5434 | 1.2199 | 0.84796 | 0.45635 | 0.036073 | -0.51043 | -1.3221 | -3.8278 | -7.9448 | -10.5529 | -11.7491
|  | SHERBORNE | FS |  |  | 1.0667 | 0.91228 | 0.70367 | 0.35957 | -0.039139 | -0.45549 | -0.89985 | -1.4933 | -2.3923 | -5.2037 | -10.001 | -13.0683 | -14.4378 | 2.8414 | 2.7398 | 2.5854 | 2.3843 | 2.1498 | 1.9003 | 1.6304 | 1.2748 | 0.7784 | -0.76658 | -3.1715 | -4.8238 | -6.2059 | 1.9139 | 1.765 | 1.5434 | 1.2199 | 0.84796 | 0.45635 | 0.036073 | -0.51043 | -1.3221 | -3.8278 | -7.9448 | -10.5529 | -11.7491
MINETY GSP | CIRENCESTER BSP | SHIPTON OLIFFE | MINIMUM HEADROOM | SP 03884 19102 | YES | 0.72038 | 0.70531 | 0.68877 | 0.60403 | 0.48033 | 0.35441 | 0.20536 | 0.0060896 | -0.26636 | -0.79525 | -1.3686 | -1.49 | -1.5501 | 2.1798 | 2.1475 | 2.1131 | 2.062 | 2.0069 | 1.9496 | 1.8864 | 1.8259 | 1.7111 | 1.4661 | 1.1866 | 1.0889 | 1.0001 | 2.2515 | 2.1593 | 2.0623 | 1.9242 | 1.7801 | 1.6246 | 1.4442 | 1.2572 | 1.0017 | 0.52446 | 0.013546 | -0.097309 | -0.15167
|  | SHIPTON OLIFFE | CT |  |  | 0.72038 | 0.70531 | 0.68877 | 0.60403 | 0.48033 | 0.35441 | 0.20536 | 0.0060896 | -0.26636 | -0.79525 | -1.3686 | -1.49 | -1.5501 | 2.1798 | 2.1475 | 2.1131 | 2.062 | 2.0069 | 1.9496 | 1.8864 | 1.8259 | 1.7111 | 1.4661 | 1.1866 | 1.0889 | 1.0001 | 2.2515 | 2.1593 | 2.0623 | 1.9242 | 1.7801 | 1.6246 | 1.4442 | 1.2572 | 1.0017 | 0.52446 | 0.013546 | -0.097309 | -0.15167
|  | SHIPTON OLIFFE | LW |  |  | 0.72038 | 0.70531 | 0.68877 | 0.60403 | 0.48033 | 0.35441 | 0.20536 | 0.0060896 | -0.26636 | -0.79525 | -1.3686 | -1.49 | -1.5501 | 2.1798 | 2.1475 | 2.1131 | 2.062 | 2.0069 | 1.9496 | 1.8864 | 1.8259 | 1.7111 | 1.4661 | 1.1866 | 1.0889 | 1.0001 | 2.2515 | 2.1593 | 2.0623 | 1.9242 | 1.7801 | 1.6246 | 1.4442 | 1.2572 | 1.0017 | 0.52446 | 0.013546 | -0.097309 | -0.15167
|  | SHIPTON OLIFFE | ST |  |  | 0.72038 | 0.70531 | 0.68877 | 0.60403 | 0.48033 | 0.35441 | 0.20536 | 0.0060896 | -0.26636 | -0.79525 | -1.3686 | -1.49 | -1.5501 | 2.1798 | 2.1475 | 2.1131 | 2.062 | 2.0069 | 1.9496 | 1.8864 | 1.8259 | 1.7111 | 1.4661 | 1.1866 | 1.0889 | 1.0001 | 2.2515 | 2.1593 | 2.0623 | 1.9242 | 1.7801 | 1.6246 | 1.4442 | 1.2572 | 1.0017 | 0.52446 | 0.013546 | -0.097309 | -0.15167
|  | SHIPTON OLIFFE | FS |  |  | 0.72038 | 0.70531 | 0.68877 | 0.60403 | 0.48033 | 0.35441 | 0.20536 | 0.0060896 | -0.26636 | -0.79525 | -1.3686 | -1.49 | -1.5501 | 2.1798 | 2.1475 | 2.1131 | 2.062 | 2.0069 | 1.9496 | 1.8864 | 1.8259 | 1.7111 | 1.4661 | 1.1866 | 1.0889 | 1.0001 | 2.2515 | 2.1593 | 2.0623 | 1.9242 | 1.7801 | 1.6246 | 1.4442 | 1.2572 | 1.0017 | 0.52446 | 0.013546 | -0.097309 | -0.15167
NURSLING GSP | SOUTHAMPTON (2 X 90) | SHIRLEY | MINIMUM HEADROOM | SU 39988 13808 | YES | 22.8003 | 22.463 | 21.9951 | 21.3595 | 20.6746 | 19.9545 | 19.1653 | 18.2846 | 16.8677 | 12.4542 | 5.3442 | 0.087362 | -3.0625 | 23.5829 | 23.4072 | 22.9864 | 22.4873 | 21.9419 | 21.3493 | 20.6852 | 19.9311 | 18.8828 | 15.5215 | 9.8304 | 3.7714 | -4.3181 | 25.3864 | 25.0707 | 24.6256 | 24.035 | 23.3967 | 22.7226 | 21.978 | 21.1456 | 19.8188 | 15.7007 | 9.3474 | 4.89 | 2.3447
|  | SHIRLEY | CT |  |  | 22.8003 | 22.463 | 21.9951 | 21.3595 | 20.6746 | 19.9545 | 19.1653 | 18.2846 | 16.8677 | 12.4542 | 5.3442 | 0.087362 | -3.0625 | 23.5829 | 23.4072 | 22.9864 | 22.4873 | 21.9419 | 21.3493 | 20.6852 | 19.9311 | 18.8828 | 15.5215 | 9.8304 | 3.7714 | -4.3181 | 25.3864 | 25.0707 | 24.6256 | 24.035 | 23.3967 | 22.7226 | 21.978 | 21.1456 | 19.8188 | 15.7007 | 9.3474 | 4.89 | 2.3447
|  | SHIRLEY | LW |  |  | 22.8003 | 22.463 | 21.9951 | 21.3595 | 20.6746 | 19.9545 | 19.1653 | 18.2846 | 16.8677 | 12.4542 | 5.3442 | 0.087362 | -3.0625 | 23.5829 | 23.4072 | 22.9864 | 22.4873 | 21.9419 | 21.3493 | 20.6852 | 19.9311 | 18.8828 | 15.5215 | 9.8304 | 3.7714 | -4.3181 | 25.3864 | 25.0707 | 24.6256 | 24.035 | 23.3967 | 22.7226 | 21.978 | 21.1456 | 19.8188 | 15.7007 | 9.3474 | 4.89 | 2.3447
|  | SHIRLEY | ST |  |  | 22.8003 | 22.463 | 21.9951 | 21.3595 | 20.6746 | 19.9545 | 19.1653 | 18.2846 | 16.8677 | 12.4542 | 5.3442 | 0.087362 | -3.0625 | 23.5829 | 23.4072 | 22.9864 | 22.4873 | 21.9419 | 21.3493 | 20.6852 | 19.9311 | 18.8828 | 15.5215 | 9.8304 | 3.7714 | -4.3181 | 25.3864 | 25.0707 | 24.6256 | 24.035 | 23.3967 | 22.7226 | 21.978 | 21.1456 | 19.8188 | 15.7007 | 9.3474 | 4.89 | 2.3447
|  | SHIRLEY | FS |  |  | 22.8003 | 22.463 | 21.9951 | 21.3595 | 20.6746 | 19.9545 | 19.1653 | 18.2846 | 16.8677 | 12.4542 | 5.3442 | 0.087362 | -3.0625 | 23.5829 | 23.4072 | 22.9864 | 22.4873 | 21.9419 | 21.3493 | 20.6852 | 19.9311 | 18.8828 | 15.5215 | 9.8304 | 3.7714 | -4.3181 | 25.3864 | 25.0707 | 24.6256 | 24.035 | 23.3967 | 22.7226 | 21.978 | 21.1456 | 19.8188 | 15.7007 | 9.3474 | 4.89 | 2.3447
MINETY GSP | STRATTON (2 X 60) | SHRIVENHAM | MINIMUM HEADROOM | SU 23782 87902 | YES | 12.1732 | 11.9405 | 11.6815 | 11.4911 | 11.2793 | 11.0544 | 10.8026 | 10.5138 | 10.0747 | 9.1939 | 7.8994 | 7.0637 | 6.7041 | 14.7063 | 14.6424 | 14.5729 | 14.5299 | 14.481 | 14.3726 | 14.205 | 14.0055 | 13.7151 | 13.193 | 12.5104 | 12.0436 | 11.6841 | 12.4998 | 12.2974 | 12.0709 | 11.8931 | 11.6969 | 11.4874 | 11.252 | 10.9792 | 10.5633 | 9.7506 | 8.5934 | 7.8569 | 7.5413
|  | SHRIVENHAM | CT |  |  | 12.1732 | 11.9405 | 11.6815 | 11.4911 | 11.2793 | 11.0544 | 10.8026 | 10.5138 | 10.0747 | 9.1939 | 7.8994 | 7.0637 | 6.7041 | 14.7063 | 14.6424 | 14.5729 | 14.5299 | 14.481 | 14.3726 | 14.205 | 14.0055 | 13.7151 | 13.193 | 12.5104 | 12.0436 | 11.6841 | 12.4998 | 12.2974 | 12.0709 | 11.8931 | 11.6969 | 11.4874 | 11.252 | 10.9792 | 10.5633 | 9.7506 | 8.5934 | 7.8569 | 7.5413
|  | SHRIVENHAM | LW |  |  | 12.1732 | 11.9405 | 11.6815 | 11.4911 | 11.2793 | 11.0544 | 10.8026 | 10.5138 | 10.0747 | 9.1939 | 7.8994 | 7.0637 | 6.7041 | 14.7063 | 14.6424 | 14.5729 | 14.5299 | 14.481 | 14.3726 | 14.205 | 14.0055 | 13.7151 | 13.193 | 12.5104 | 12.0436 | 11.6841 | 12.4998 | 12.2974 | 12.0709 | 11.8931 | 11.6969 | 11.4874 | 11.252 | 10.9792 | 10.5633 | 9.7506 | 8.5934 | 7.8569 | 7.5413
|  | SHRIVENHAM | ST |  |  | 12.1732 | 11.9405 | 11.6815 | 11.4911 | 11.2793 | 11.0544 | 10.8026 | 10.5138 | 10.0747 | 9.1939 | 7.8994 | 7.0637 | 6.7041 | 14.7063 | 14.6424 | 14.5729 | 14.5299 | 14.481 | 14.3726 | 14.205 | 14.0055 | 13.7151 | 13.193 | 12.5104 | 12.0436 | 11.6841 | 12.4998 | 12.2974 | 12.0709 | 11.8931 | 11.6969 | 11.4874 | 11.252 | 10.9792 | 10.5633 | 9.7506 | 8.5934 | 7.8569 | 7.5413
|  | SHRIVENHAM | FS |  |  | 12.1732 | 11.9405 | 11.6815 | 11.4911 | 11.2793 | 11.0544 | 10.8026 | 10.5138 | 10.0747 | 9.1939 | 7.8994 | 7.0637 | 6.7041 | 14.7063 | 14.6424 | 14.5729 | 14.5299 | 14.481 | 14.3726 | 14.205 | 14.0055 | 13.7151 | 13.193 | 12.5104 | 12.0436 | 11.6841 | 12.4998 | 12.2974 | 12.0709 | 11.8931 | 11.6969 | 11.4874 | 11.252 | 10.9792 | 10.5633 | 9.7506 | 8.5934 | 7.8569 | 7.5413
MANNINGTON GSP | SHAFTESBURY BSP | SHROTON | MINIMUM HEADROOM | ST 85356 13659 | YES | 18.9309 | 18.6881 | 18.3077 | 17.8045 | 17.278 | 16.7081 | 16.0725 | 15.3568 | 14.3216 | 12.0386 | 8.2647 | 5.467 | 4.3337 | 22.2304 | 22.1041 | 21.908 | 21.6437 | 21.3444 | 21.0189 | 20.6434 | 20.1863 | 19.5516 | 18.3094 | 16.6376 | 15.3665 | 14.5807 | 16.4166 | 16.1955 | 15.8581 | 15.4027 | 14.9264 | 14.4106 | 13.8368 | 13.1935 | 12.2549 | 10.1443 | 6.7107 | 4.244 | 3.2016
|  | SHROTON | CT |  |  | 18.9309 | 18.6881 | 18.3077 | 17.8045 | 17.278 | 16.7081 | 16.0725 | 15.3568 | 14.3216 | 12.0386 | 8.2647 | 5.467 | 4.3337 | 22.2304 | 22.1041 | 21.908 | 21.6437 | 21.3444 | 21.0189 | 20.6434 | 20.1863 | 19.5516 | 18.3094 | 16.6376 | 15.3665 | 14.5807 | 16.4166 | 16.1955 | 15.8581 | 15.4027 | 14.9264 | 14.4106 | 13.8368 | 13.1935 | 12.2549 | 10.1443 | 6.7107 | 4.244 | 3.2016
|  | SHROTON | LW |  |  | 18.9309 | 18.6881 | 18.3077 | 17.8045 | 17.278 | 16.7081 | 16.0725 | 15.3568 | 14.3216 | 12.0386 | 8.2647 | 5.467 | 4.3337 | 22.2304 | 22.1041 | 21.908 | 21.6437 | 21.3444 | 21.0189 | 20.6434 | 20.1863 | 19.5516 | 18.3094 | 16.6376 | 15.3665 | 14.5807 | 16.4166 | 16.1955 | 15.8581 | 15.4027 | 14.9264 | 14.4106 | 13.8368 | 13.1935 | 12.2549 | 10.1443 | 6.7107 | 4.244 | 3.2016
|  | SHROTON | ST |  |  | 18.9309 | 18.6881 | 18.3077 | 17.8045 | 17.278 | 16.7081 | 16.0725 | 15.3568 | 14.3216 | 12.0386 | 8.2647 | 5.467 | 4.3337 | 22.2304 | 22.1041 | 21.908 | 21.6437 | 21.3444 | 21.0189 | 20.6434 | 20.1863 | 19.5516 | 18.3094 | 16.6376 | 15.3665 | 14.5807 | 16.4166 | 16.1955 | 15.8581 | 15.4027 | 14.9264 | 14.4106 | 13.8368 | 13.1935 | 12.2549 | 10.1443 | 6.7107 | 4.244 | 3.2016
|  | SHROTON | FS |  |  | 18.9309 | 18.6881 | 18.3077 | 17.8045 | 17.278 | 16.7081 | 16.0725 | 15.3568 | 14.3216 | 12.0386 | 8.2647 | 5.467 | 4.3337 | 22.2304 | 22.1041 | 21.908 | 21.6437 | 21.3444 | 21.0189 | 20.6434 | 20.1863 | 19.5516 | 18.3094 | 16.6376 | 15.3665 | 14.5807 | 16.4166 | 16.1955 | 15.8581 | 15.4027 | 14.9264 | 14.4106 | 13.8368 | 13.1935 | 12.2549 | 10.1443 | 6.7107 | 4.244 | 3.2016
LALEHAM | STAINES | SIDNEY ROAD | MINIMUM HEADROOM | TQ 04100 71760 | YES | 23.7316 | 23.3934 | 22.9218 | 22.2968 | 21.5916 | 20.978 | 20.3762 | 19.4697 | 18.0482 | 13.2044 | 8.051 | 4.8256 | 3.1593 | 23.2039 | 22.9801 | 22.6729 | 22.302 | 21.8843 | 21.4722 | 21.0314 | 20.3816 | 19.3894 | 16.3228 | 13.1928 | 11.0693 | 9.0143 | 25.575 | 25.437 | 25.2556 | 24.7742 | 24.1278 | 23.5438 | 22.9576 | 22.0853 | 20.7015 | 16.2641 | 11.7104 | 9.0462 | 7.6931
|  | SIDNEY ROAD | CT |  |  | 23.7316 | 23.3934 | 22.9218 | 22.2968 | 21.5916 | 20.978 | 20.3762 | 19.4697 | 18.0482 | 13.2044 | 8.051 | 4.8256 | 3.1593 | 23.2039 | 22.9801 | 22.6729 | 22.302 | 21.8843 | 21.4722 | 21.0314 | 20.3816 | 19.3894 | 16.3228 | 13.1928 | 11.0693 | 9.0143 | 25.575 | 25.437 | 25.2556 | 24.7742 | 24.1278 | 23.5438 | 22.9576 | 22.0853 | 20.7015 | 16.2641 | 11.7104 | 9.0462 | 7.6931
|  | SIDNEY ROAD | LW |  |  | 23.7316 | 23.3934 | 22.9218 | 22.2968 | 21.5916 | 20.978 | 20.3762 | 19.4697 | 18.0482 | 13.2044 | 8.051 | 4.8256 | 3.1593 | 23.2039 | 22.9801 | 22.6729 | 22.302 | 21.8843 | 21.4722 | 21.0314 | 20.3816 | 19.3894 | 16.3228 | 13.1928 | 11.0693 | 9.0143 | 25.575 | 25.437 | 25.2556 | 24.7742 | 24.1278 | 23.5438 | 22.9576 | 22.0853 | 20.7015 | 16.2641 | 11.7104 | 9.0462 | 7.6931
|  | SIDNEY ROAD | ST |  |  | 23.7316 | 23.3934 | 22.9218 | 22.2968 | 21.5916 | 20.978 | 20.3762 | 19.4697 | 18.0482 | 13.2044 | 8.051 | 4.8256 | 3.1593 | 23.2039 | 22.9801 | 22.6729 | 22.302 | 21.8843 | 21.4722 | 21.0314 | 20.3816 | 19.3894 | 16.3228 | 13.1928 | 11.0693 | 9.0143 | 25.575 | 25.437 | 25.2556 | 24.7742 | 24.1278 | 23.5438 | 22.9576 | 22.0853 | 20.7015 | 16.2641 | 11.7104 | 9.0462 | 7.6931
|  | SIDNEY ROAD | FS |  |  | 23.7316 | 23.3934 | 22.9218 | 22.2968 | 21.5916 | 20.978 | 20.3762 | 19.4697 | 18.0482 | 13.2044 | 8.051 | 4.8256 | 3.1593 | 23.2039 | 22.9801 | 22.6729 | 22.302 | 21.8843 | 21.4722 | 21.0314 | 20.3816 | 19.3894 | 16.3228 | 13.1928 | 11.0693 | 9.0143 | 25.575 | 25.437 | 25.2556 | 24.7742 | 24.1278 | 23.5438 | 22.9576 | 22.0853 | 20.7015 | 16.2641 | 11.7104 | 9.0462 | 7.6931
NURSLING GSP | ROWNHAMS | SILKSTEAD | MINIMUM HEADROOM | SU 44578 24565 | YES | 4.251 | 3.9595 | 3.6613 | 3.2561 | 2.8207 | 2.3672 | 1.8598 | 1.2102 | 0.29014 | -2.0177 | -5.835 | -7.9616 | -8.8152 | 6.0536 | 5.8363 | 5.6126 | 5.3477 | 5.0595 | 4.7472 | 4.3922 | 3.9229 | 3.3094 | 1.8399 | -0.39446 | -1.4744 | -2.1588 | 5.6862 | 5.4204 | 5.1474 | 4.7724 | 4.3699 | 3.9515 | 3.4848 | 2.8882 | 2.0429 | -0.11848 | -3.729 | -5.6428 | -6.3916
|  | SILKSTEAD | CT |  |  | 4.251 | 3.9595 | 3.6613 | 3.2561 | 2.8207 | 2.3672 | 1.8598 | 1.2102 | 0.29014 | -2.0177 | -5.835 | -7.9616 | -8.8152 | 6.0536 | 5.8363 | 5.6126 | 5.3477 | 5.0595 | 4.7472 | 4.3922 | 3.9229 | 3.3094 | 1.8399 | -0.39446 | -1.4744 | -2.1588 | 5.6862 | 5.4204 | 5.1474 | 4.7724 | 4.3699 | 3.9515 | 3.4848 | 2.8882 | 2.0429 | -0.11848 | -3.729 | -5.6428 | -6.3916
|  | SILKSTEAD | LW |  |  | 4.251 | 3.9595 | 3.6613 | 3.2561 | 2.8207 | 2.3672 | 1.8598 | 1.2102 | 0.29014 | -2.0177 | -5.835 | -7.9616 | -8.8152 | 6.0536 | 5.8363 | 5.6126 | 5.3477 | 5.0595 | 4.7472 | 4.3922 | 3.9229 | 3.3094 | 1.8399 | -0.39446 | -1.4744 | -2.1588 | 5.6862 | 5.4204 | 5.1474 | 4.7724 | 4.3699 | 3.9515 | 3.4848 | 2.8882 | 2.0429 | -0.11848 | -3.729 | -5.6428 | -6.3916
|  | SILKSTEAD | ST |  |  | 4.251 | 3.9595 | 3.6613 | 3.2561 | 2.8207 | 2.3672 | 1.8598 | 1.2102 | 0.29014 | -2.0177 | -5.835 | -7.9616 | -8.8152 | 6.0536 | 5.8363 | 5.6126 | 5.3477 | 5.0595 | 4.7472 | 4.3922 | 3.9229 | 3.3094 | 1.8399 | -0.39446 | -1.4744 | -2.1588 | 5.6862 | 5.4204 | 5.1474 | 4.7724 | 4.3699 | 3.9515 | 3.4848 | 2.8882 | 2.0429 | -0.11848 | -3.729 | -5.6428 | -6.3916
|  | SILKSTEAD | FS |  |  | 4.251 | 3.9595 | 3.6613 | 3.2561 | 2.8207 | 2.3672 | 1.8598 | 1.2102 | 0.29014 | -2.0177 | -5.835 | -7.9616 | -8.8152 | 6.0536 | 5.8363 | 5.6126 | 5.3477 | 5.0595 | 4.7472 | 4.3922 | 3.9229 | 3.3094 | 1.8399 | -0.39446 | -1.4744 | -2.1588 | 5.6862 | 5.4204 | 5.1474 | 4.7724 | 4.3699 | 3.9515 | 3.4848 | 2.8882 | 2.0429 | -0.11848 | -3.729 | -5.6428 | -6.3916
BRAMLEY (FLEE) | READING BSP | SILVER STREET | MINIMUM HEADROOM | SU 71957 72821 | YES | 7.8929 | 7.5712 | 7.1867 | 6.5974 | 5.9665 | 5.3696 | 4.7228 | 3.9856 | 2.88 | -0.73162 | -7.6162 | -12.5135 | -15.4552 | 14.1985 | 13.9876 | 13.7435 | 13.3962 | 13.0218 | 12.6243 | 12.0749 | 11.4348 | 10.6206 | 7.8654 | 2.3049 | -3.2984 | -10.63 | 10.1412 | 10.0029 | 9.8392 | 9.6614 | 9.4629 | 9.2463 | 8.9482 | 8.3064 | 7.315 | 3.9716 | -2.2226 | -6.4947 | -8.9799
|  | SILVER STREET | CT |  |  | 7.8929 | 7.5712 | 7.1867 | 6.5974 | 5.9665 | 5.3696 | 4.7228 | 3.9856 | 2.88 | -0.73162 | -7.6162 | -12.5135 | -15.4552 | 14.1985 | 13.9876 | 13.7435 | 13.3962 | 13.0218 | 12.6243 | 12.0749 | 11.4348 | 10.6206 | 7.8654 | 2.3049 | -3.2984 | -10.63 | 10.1412 | 10.0029 | 9.8392 | 9.6614 | 9.4629 | 9.2463 | 8.9482 | 8.3064 | 7.315 | 3.9716 | -2.2226 | -6.4947 | -8.9799
|  | SILVER STREET | LW |  |  | 7.8929 | 7.5712 | 7.1867 | 6.5974 | 5.9665 | 5.3696 | 4.7228 | 3.9856 | 2.88 | -0.73162 | -7.6162 | -12.5135 | -15.4552 | 14.1985 | 13.9876 | 13.7435 | 13.3962 | 13.0218 | 12.6243 | 12.0749 | 11.4348 | 10.6206 | 7.8654 | 2.3049 | -3.2984 | -10.63 | 10.1412 | 10.0029 | 9.8392 | 9.6614 | 9.4629 | 9.2463 | 8.9482 | 8.3064 | 7.315 | 3.9716 | -2.2226 | -6.4947 | -8.9799
|  | SILVER STREET | ST |  |  | 7.8929 | 7.5712 | 7.1867 | 6.5974 | 5.9665 | 5.3696 | 4.7228 | 3.9856 | 2.88 | -0.73162 | -7.6162 | -12.5135 | -15.4552 | 14.1985 | 13.9876 | 13.7435 | 13.3962 | 13.0218 | 12.6243 | 12.0749 | 11.4348 | 10.6206 | 7.8654 | 2.3049 | -3.2984 | -10.63 | 10.1412 | 10.0029 | 9.8392 | 9.6614 | 9.4629 | 9.2463 | 8.9482 | 8.3064 | 7.315 | 3.9716 | -2.2226 | -6.4947 | -8.9799
|  | SILVER STREET | FS |  |  | 7.8929 | 7.5712 | 7.1867 | 6.5974 | 5.9665 | 5.3696 | 4.7228 | 3.9856 | 2.88 | -0.73162 | -7.6162 | -12.5135 | -15.4552 | 14.1985 | 13.9876 | 13.7435 | 13.3962 | 13.0218 | 12.6243 | 12.0749 | 11.4348 | 10.6206 | 7.8654 | 2.3049 | -3.2984 | -10.63 | 10.1412 | 10.0029 | 9.8392 | 9.6614 | 9.4629 | 9.2463 | 8.9482 | 8.3064 | 7.315 | 3.9716 | -2.2226 | -6.4947 | -8.9799
MANNINGTON GSP | CHRISTCHURCH BSP | SOMERFORD | MINIMUM HEADROOM | SZ 18262 93590 | YES | 1.0848 | 0.49152 | -0.37252 | -1.4439 | -2.5046 | -3.6546 | -4.9112 | -6.102 | -8.0522 | -13.4595 | -21.2867 | -27.1719 | -30.1124 | 7.3677 | 6.961 | 6.3333 | 5.6487 | 4.9532 | 4.1946 | 3.3651 | 2.5076 | 1.2527 | -2.1162 | -6.2001 | -9.1487 | -11.4158 | 2.5975 | 2.0775 | 1.2989 | 0.34141 | -0.61806 | -1.6623 | -2.8028 | -3.9406 | -5.7966 | -10.8452 | -17.7496 | -22.8758 | -25.4154
|  | SOMERFORD | CT |  |  | 1.0848 | 0.49152 | -0.37252 | -1.4439 | -2.5046 | -3.6546 | -4.9112 | -6.102 | -8.0522 | -13.4595 | -21.2867 | -27.1719 | -30.1124 | 7.3677 | 6.961 | 6.3333 | 5.6487 | 4.9532 | 4.1946 | 3.3651 | 2.5076 | 1.2527 | -2.1162 | -6.2001 | -9.1487 | -11.4158 | 2.5975 | 2.0775 | 1.2989 | 0.34141 | -0.61806 | -1.6623 | -2.8028 | -3.9406 | -5.7966 | -10.8452 | -17.7496 | -22.8758 | -25.4154
|  | SOMERFORD | LW |  |  | 1.0848 | 0.49152 | -0.37252 | -1.4439 | -2.5046 | -3.6546 | -4.9112 | -6.102 | -8.0522 | -13.4595 | -21.2867 | -27.1719 | -30.1124 | 7.3677 | 6.961 | 6.3333 | 5.6487 | 4.9532 | 4.1946 | 3.3651 | 2.5076 | 1.2527 | -2.1162 | -6.2001 | -9.1487 | -11.4158 | 2.5975 | 2.0775 | 1.2989 | 0.34141 | -0.61806 | -1.6623 | -2.8028 | -3.9406 | -5.7966 | -10.8452 | -17.7496 | -22.8758 | -25.4154
|  | SOMERFORD | ST |  |  | 1.0848 | 0.49152 | -0.37252 | -1.4439 | -2.5046 | -3.6546 | -4.9112 | -6.102 | -8.0522 | -13.4595 | -21.2867 | -27.1719 | -30.1124 | 7.3677 | 6.961 | 6.3333 | 5.6487 | 4.9532 | 4.1946 | 3.3651 | 2.5076 | 1.2527 | -2.1162 | -6.2001 | -9.1487 | -11.4158 | 2.5975 | 2.0775 | 1.2989 | 0.34141 | -0.61806 | -1.6623 | -2.8028 | -3.9406 | -5.7966 | -10.8452 | -17.7496 | -22.8758 | -25.4154
|  | SOMERFORD | FS |  |  | 1.0848 | 0.49152 | -0.37252 | -1.4439 | -2.5046 | -3.6546 | -4.9112 | -6.102 | -8.0522 | -13.4595 | -21.2867 | -27.1719 | -30.1124 | 7.3677 | 6.961 | 6.3333 | 5.6487 | 4.9532 | 4.1946 | 3.3651 | 2.5076 | 1.2527 | -2.1162 | -6.2001 | -9.1487 | -11.4158 | 2.5975 | 2.0775 | 1.2989 | 0.34141 | -0.61806 | -1.6623 | -2.8028 | -3.9406 | -5.7966 | -10.8452 | -17.7496 | -22.8758 | -25.4154
LOVEDEAN GSP | CHICHESTER & HUNSTON | SOUTH BERSTED | MINIMUM HEADROOM | SU 94025 00705 | YES | 6.6616 | 6.1217 | 5.4461 | 4.75 | 4.047 | 3.26 | 2.4169 | 1.4624 | -0.085886 | -4.3321 | -10.4582 | -14.9351 | -17.2199 | 11.3104 | 10.8696 | 10.4456 | 10.0485 | 9.554 | 9.001 | 8.4041 | 7.7146 | 6.7216 | 4.1031 | 0.60174 | -2.1454 | -4.6436 | 7.4097 | 6.9095 | 6.301 | 5.6772 | 5.0499 | 4.3482 | 3.5973 | 2.7488 | 1.3893 | -2.321 | -7.9869 | -12.0166 | -14.0356
|  | SOUTH BERSTED | CT |  |  | 6.6616 | 6.1217 | 5.4461 | 4.75 | 4.047 | 3.26 | 2.4169 | 1.4624 | -0.085886 | -4.3321 | -10.4582 | -14.9351 | -17.2199 | 11.3104 | 10.8696 | 10.4456 | 10.0485 | 9.554 | 9.001 | 8.4041 | 7.7146 | 6.7216 | 4.1031 | 0.60174 | -2.1454 | -4.6436 | 7.4097 | 6.9095 | 6.301 | 5.6772 | 5.0499 | 4.3482 | 3.5973 | 2.7488 | 1.3893 | -2.321 | -7.9869 | -12.0166 | -14.0356
|  | SOUTH BERSTED | LW |  |  | 6.6616 | 6.1217 | 5.4461 | 4.75 | 4.047 | 3.26 | 2.4169 | 1.4624 | -0.085886 | -4.3321 | -10.4582 | -14.9351 | -17.2199 | 11.3104 | 10.8696 | 10.4456 | 10.0485 | 9.554 | 9.001 | 8.4041 | 7.7146 | 6.7216 | 4.1031 | 0.60174 | -2.1454 | -4.6436 | 7.4097 | 6.9095 | 6.301 | 5.6772 | 5.0499 | 4.3482 | 3.5973 | 2.7488 | 1.3893 | -2.321 | -7.9869 | -12.0166 | -14.0356
|  | SOUTH BERSTED | ST |  |  | 6.6616 | 6.1217 | 5.4461 | 4.75 | 4.047 | 3.26 | 2.4169 | 1.4624 | -0.085886 | -4.3321 | -10.4582 | -14.9351 | -17.2199 | 11.3104 | 10.8696 | 10.4456 | 10.0485 | 9.554 | 9.001 | 8.4041 | 7.7146 | 6.7216 | 4.1031 | 0.60174 | -2.1454 | -4.6436 | 7.4097 | 6.9095 | 6.301 | 5.6772 | 5.0499 | 4.3482 | 3.5973 | 2.7488 | 1.3893 | -2.321 | -7.9869 | -12.0166 | -14.0356
|  | SOUTH BERSTED | FS |  |  | 6.6616 | 6.1217 | 5.4461 | 4.75 | 4.047 | 3.26 | 2.4169 | 1.4624 | -0.085886 | -4.3321 | -10.4582 | -14.9351 | -17.2199 | 11.3104 | 10.8696 | 10.4456 | 10.0485 | 9.554 | 9.001 | 8.4041 | 7.7146 | 6.7216 | 4.1031 | 0.60174 | -2.1454 | -4.6436 | 7.4097 | 6.9095 | 6.301 | 5.6772 | 5.0499 | 4.3482 | 3.5973 | 2.7488 | 1.3893 | -2.321 | -7.9869 | -12.0166 | -14.0356
MANNINGTON GSP | CHRISTCHURCH BSP | SOUTHBOURNE | MINIMUM HEADROOM | SZ 13563 92074 | YES | 12.43 | 12.0628 | 11.5614 | 10.8679 | 10.1292 | 9.3685 | 8.5468 | 7.623 | 6.1347 | 1.5465 | -6.3276 | -12.4834 | -16.3644 | 16.1404 | 15.8679 | 15.4858 | 15.0336 | 14.545 | 14.0205 | 13.4468 | 12.7854 | 11.8177 | 8.8274 | 4.1371 | 0.17995 | -3.6684 | 14.1744 | 13.8335 | 13.3599 | 12.7184 | 12.0336 | 11.3227 | 10.5527 | 9.6813 | 8.2883 | 4.0159 | -2.9916 | -8.2559 | -11.5012
|  | SOUTHBOURNE | CT |  |  | 12.43 | 12.0628 | 11.5614 | 10.8679 | 10.1292 | 9.3685 | 8.5468 | 7.623 | 6.1347 | 1.5465 | -6.3276 | -12.4834 | -16.3644 | 16.1404 | 15.8679 | 15.4858 | 15.0336 | 14.545 | 14.0205 | 13.4468 | 12.7854 | 11.8177 | 8.8274 | 4.1371 | 0.17995 | -3.6684 | 14.1744 | 13.8335 | 13.3599 | 12.7184 | 12.0336 | 11.3227 | 10.5527 | 9.6813 | 8.2883 | 4.0159 | -2.9916 | -8.2559 | -11.5012
|  | SOUTHBOURNE | LW |  |  | 12.43 | 12.0628 | 11.5614 | 10.8679 | 10.1292 | 9.3685 | 8.5468 | 7.623 | 6.1347 | 1.5465 | -6.3276 | -12.4834 | -16.3644 | 16.1404 | 15.8679 | 15.4858 | 15.0336 | 14.545 | 14.0205 | 13.4468 | 12.7854 | 11.8177 | 8.8274 | 4.1371 | 0.17995 | -3.6684 | 14.1744 | 13.8335 | 13.3599 | 12.7184 | 12.0336 | 11.3227 | 10.5527 | 9.6813 | 8.2883 | 4.0159 | -2.9916 | -8.2559 | -11.5012
|  | SOUTHBOURNE | ST |  |  | 12.43 | 12.0628 | 11.5614 | 10.8679 | 10.1292 | 9.3685 | 8.5468 | 7.623 | 6.1347 | 1.5465 | -6.3276 | -12.4834 | -16.3644 | 16.1404 | 15.8679 | 15.4858 | 15.0336 | 14.545 | 14.0205 | 13.4468 | 12.7854 | 11.8177 | 8.8274 | 4.1371 | 0.17995 | -3.6684 | 14.1744 | 13.8335 | 13.3599 | 12.7184 | 12.0336 | 11.3227 | 10.5527 | 9.6813 | 8.2883 | 4.0159 | -2.9916 | -8.2559 | -11.5012
|  | SOUTHBOURNE | FS |  |  | 12.43 | 12.0628 | 11.5614 | 10.8679 | 10.1292 | 9.3685 | 8.5468 | 7.623 | 6.1347 | 1.5465 | -6.3276 | -12.4834 | -16.3644 | 16.1404 | 15.8679 | 15.4858 | 15.0336 | 14.545 | 14.0205 | 13.4468 | 12.7854 | 11.8177 | 8.8274 | 4.1371 | 0.17995 | -3.6684 | 14.1744 | 13.8335 | 13.3599 | 12.7184 | 12.0336 | 11.3227 | 10.5527 | 9.6813 | 8.2883 | 4.0159 | -2.9916 | -8.2559 | -11.5012
BRAMLEY (FLEE) | BURGHFIELD RESERVE | SOUTHCOTE | MINIMUM HEADROOM | SU 68199 71325 | YES | 17.0313 | 16.761 | 16.3882 | 15.9277 | 15.4291 | 14.9071 | 14.3391 | 13.6688 | 12.6494 | 9.8313 | 4.2545 | -0.74065 | -4.342 | 18.9842 | 18.8131 | 18.5616 | 18.2559 | 17.9219 | 17.5648 | 17.1719 | 16.6953 | 16.0214 | 14.2292 | 11.0316 | 8.0526 | 5.1854 | 18.1861 | 17.9723 | 17.6804 | 17.2977 | 16.8843 | 16.4477 | 15.946 | 15.3305 | 14.3766 | 11.7882 | 6.9268 | 2.6167 | -0.42262
|  | SOUTHCOTE | CT |  |  | 17.0313 | 16.761 | 16.3882 | 15.9277 | 15.4291 | 14.9071 | 14.3391 | 13.6688 | 12.6494 | 9.8313 | 4.2545 | -0.74065 | -4.342 | 18.9842 | 18.8131 | 18.5616 | 18.2559 | 17.9219 | 17.5648 | 17.1719 | 16.6953 | 16.0214 | 14.2292 | 11.0316 | 8.0526 | 5.1854 | 18.1861 | 17.9723 | 17.6804 | 17.2977 | 16.8843 | 16.4477 | 15.946 | 15.3305 | 14.3766 | 11.7882 | 6.9268 | 2.6167 | -0.42262
|  | SOUTHCOTE | LW |  |  | 17.0313 | 16.761 | 16.3882 | 15.9277 | 15.4291 | 14.9071 | 14.3391 | 13.6688 | 12.6494 | 9.8313 | 4.2545 | -0.74065 | -4.342 | 18.9842 | 18.8131 | 18.5616 | 18.2559 | 17.9219 | 17.5648 | 17.1719 | 16.6953 | 16.0214 | 14.2292 | 11.0316 | 8.0526 | 5.1854 | 18.1861 | 17.9723 | 17.6804 | 17.2977 | 16.8843 | 16.4477 | 15.946 | 15.3305 | 14.3766 | 11.7882 | 6.9268 | 2.6167 | -0.42262
|  | SOUTHCOTE | ST |  |  | 17.0313 | 16.761 | 16.3882 | 15.9277 | 15.4291 | 14.9071 | 14.3391 | 13.6688 | 12.6494 | 9.8313 | 4.2545 | -0.74065 | -4.342 | 18.9842 | 18.8131 | 18.5616 | 18.2559 | 17.9219 | 17.5648 | 17.1719 | 16.6953 | 16.0214 | 14.2292 | 11.0316 | 8.0526 | 5.1854 | 18.1861 | 17.9723 | 17.6804 | 17.2977 | 16.8843 | 16.4477 | 15.946 | 15.3305 | 14.3766 | 11.7882 | 6.9268 | 2.6167 | -0.42262
|  | SOUTHCOTE | FS |  |  | 17.0313 | 16.761 | 16.3882 | 15.9277 | 15.4291 | 14.9071 | 14.3391 | 13.6688 | 12.6494 | 9.8313 | 4.2545 | -0.74065 | -4.342 | 18.9842 | 18.8131 | 18.5616 | 18.2559 | 17.9219 | 17.5648 | 17.1719 | 16.6953 | 16.0214 | 14.2292 | 11.0316 | 8.0526 | 5.1854 | 18.1861 | 17.9723 | 17.6804 | 17.2977 | 16.8843 | 16.4477 | 15.946 | 15.3305 | 14.3766 | 11.7882 | 6.9268 | 2.6167 | -0.42262
NURSLING GSP |  | SOUTHFIELD ROAD | MINIMUM HEADROOM | TQ 20533 79746 |  | 9.8104 | 9.7702 | 9.725 | 9.6654 | 9.6009 | 9.5393 | 9.4727 | 9.4016 | 9.303 | 8.9583 | 7.9738 | 6.8964 | 6.0124 | 18.8926 | 18.8681 | 18.8411 | 18.8103 | 18.7757 | 18.738 | 18.6965 | 18.6503 | 18.6036 | 18.3796 | 17.3592 | 15.447 | 12.6164 | 12.5422 | 12.506 | 12.4649 | 12.4101 | 12.3507 | 12.2938 | 12.2321 | 12.166 | 12.0729 | 11.7503 | 10.908 | 10.0558 | 9.3584
|  | SOUTHFIELD ROAD | CT |  |  | 9.8104 | 9.7702 | 9.725 | 9.6654 | 9.6009 | 9.5393 | 9.4727 | 9.4016 | 9.303 | 8.9583 | 7.9738 | 6.8964 | 6.0124 | 18.8926 | 18.8681 | 18.8411 | 18.8103 | 18.7757 | 18.738 | 18.6965 | 18.6503 | 18.6036 | 18.3796 | 17.3592 | 15.447 | 12.6164 | 12.5422 | 12.506 | 12.4649 | 12.4101 | 12.3507 | 12.2938 | 12.2321 | 12.166 | 12.0729 | 11.7503 | 10.908 | 10.0558 | 9.3584
|  | SOUTHFIELD ROAD | LW |  |  | 9.8104 | 9.7702 | 9.725 | 9.6654 | 9.6009 | 9.5393 | 9.4727 | 9.4016 | 9.303 | 8.9583 | 7.9738 | 6.8964 | 6.0124 | 18.8926 | 18.8681 | 18.8411 | 18.8103 | 18.7757 | 18.738 | 18.6965 | 18.6503 | 18.6036 | 18.3796 | 17.3592 | 15.447 | 12.6164 | 12.5422 | 12.506 | 12.4649 | 12.4101 | 12.3507 | 12.2938 | 12.2321 | 12.166 | 12.0729 | 11.7503 | 10.908 | 10.0558 | 9.3584
|  | SOUTHFIELD ROAD | ST |  |  | 9.8104 | 9.7702 | 9.725 | 9.6654 | 9.6009 | 9.5393 | 9.4727 | 9.4016 | 9.303 | 8.9583 | 7.9738 | 6.8964 | 6.0124 | 18.8926 | 18.8681 | 18.8411 | 18.8103 | 18.7757 | 18.738 | 18.6965 | 18.6503 | 18.6036 | 18.3796 | 17.3592 | 15.447 | 12.6164 | 12.5422 | 12.506 | 12.4649 | 12.4101 | 12.3507 | 12.2938 | 12.2321 | 12.166 | 12.0729 | 11.7503 | 10.908 | 10.0558 | 9.3584
|  | SOUTHFIELD ROAD | FS |  |  | 9.8104 | 9.7702 | 9.725 | 9.6654 | 9.6009 | 9.5393 | 9.4727 | 9.4016 | 9.303 | 8.9583 | 7.9738 | 6.8964 | 6.0124 | 18.8926 | 18.8681 | 18.8411 | 18.8103 | 18.7757 | 18.738 | 18.6965 | 18.6503 | 18.6036 | 18.3796 | 17.3592 | 15.447 | 12.6164 | 12.5422 | 12.506 | 12.4649 | 12.4101 | 12.3507 | 12.2938 | 12.2321 | 12.166 | 12.0729 | 11.7503 | 10.908 | 10.0558 | 9.3584
AXMINSTER | YEOVIL BSP | SPARKFORD | MINIMUM HEADROOM | ST 60767 25496 | YES | 2.4333 | 2.2678 | 2.0857 | 1.8168 | 1.5597 | 1.3307 | 1.1871 | 1.0394 | 0.86413 | 0.61268 | 0.33669 | 0.17968 | 0.090929 | 3.6846 | 3.5892 | 3.4839 | 3.3485 | 3.218 | 3.0948 | 2.9973 | 2.8808 | 2.745 | 2.5582 | 2.3659 | 2.2431 | 2.1313 | 2.6813 | 2.5259 | 2.3575 | 2.1063 | 1.8669 | 1.6546 | 1.524 | 1.3927 | 1.2373 | 1.0076 | 0.74509 | 0.59721 | 0.51388
|  | SPARKFORD | CT |  |  | 2.4333 | 2.2678 | 2.0857 | 1.8168 | 1.5597 | 1.3307 | 1.1871 | 1.0394 | 0.86413 | 0.61268 | 0.33669 | 0.17968 | 0.090929 | 3.6846 | 3.5892 | 3.4839 | 3.3485 | 3.218 | 3.0948 | 2.9973 | 2.8808 | 2.745 | 2.5582 | 2.3659 | 2.2431 | 2.1313 | 2.6813 | 2.5259 | 2.3575 | 2.1063 | 1.8669 | 1.6546 | 1.524 | 1.3927 | 1.2373 | 1.0076 | 0.74509 | 0.59721 | 0.51388
|  | SPARKFORD | LW |  |  | 2.4333 | 2.2678 | 2.0857 | 1.8168 | 1.5597 | 1.3307 | 1.1871 | 1.0394 | 0.86413 | 0.61268 | 0.33669 | 0.17968 | 0.090929 | 3.6846 | 3.5892 | 3.4839 | 3.3485 | 3.218 | 3.0948 | 2.9973 | 2.8808 | 2.745 | 2.5582 | 2.3659 | 2.2431 | 2.1313 | 2.6813 | 2.5259 | 2.3575 | 2.1063 | 1.8669 | 1.6546 | 1.524 | 1.3927 | 1.2373 | 1.0076 | 0.74509 | 0.59721 | 0.51388
|  | SPARKFORD | ST |  |  | 2.4333 | 2.2678 | 2.0857 | 1.8168 | 1.5597 | 1.3307 | 1.1871 | 1.0394 | 0.86413 | 0.61268 | 0.33669 | 0.17968 | 0.090929 | 3.6846 | 3.5892 | 3.4839 | 3.3485 | 3.218 | 3.0948 | 2.9973 | 2.8808 | 2.745 | 2.5582 | 2.3659 | 2.2431 | 2.1313 | 2.6813 | 2.5259 | 2.3575 | 2.1063 | 1.8669 | 1.6546 | 1.524 | 1.3927 | 1.2373 | 1.0076 | 0.74509 | 0.59721 | 0.51388
|  | SPARKFORD | FS |  |  | 2.4333 | 2.2678 | 2.0857 | 1.8168 | 1.5597 | 1.3307 | 1.1871 | 1.0394 | 0.86413 | 0.61268 | 0.33669 | 0.17968 | 0.090929 | 3.6846 | 3.5892 | 3.4839 | 3.3485 | 3.218 | 3.0948 | 2.9973 | 2.8808 | 2.745 | 2.5582 | 2.3659 | 2.2431 | 2.1313 | 2.6813 | 2.5259 | 2.3575 | 2.1063 | 1.8669 | 1.6546 | 1.524 | 1.3927 | 1.2373 | 1.0076 | 0.74509 | 0.59721 | 0.51388
MELKSHAM GSP | NORRINGTON | SPRING QUARRY WEST | MINIMUM HEADROOM | ST 84368 68717 | YES | 20.0438 | 15.8317 | 11.5866 | 3.2009 | 2.9642 | 2.7146 | 2.4408 | 2.1128 | 1.5896 | 0.40306 | -1.3701 | -2.5674 | -3.0804 | 17.1448 | 11.9359 | 6.6951 | -3.6637 | -3.8317 | -4.0133 | -4.2167 | -4.473 | -4.8439 | -5.6005 | -6.5722 | -7.3353 | -8.0638 | 19.6413 | 14.4057 | 9.1326 | -1.2873 | -1.5188 | -1.7646 | -2.0363 | -2.3705 | -2.8917 | -4.0065 | -5.5213 | -6.5049 | -6.9518
|  | SPRING QUARRY WEST | CT |  |  | 20.0438 | 15.8317 | 11.5866 | 3.2009 | 2.9642 | 2.7146 | 2.4408 | 2.1128 | 1.5896 | 0.40306 | -1.3701 | -2.5674 | -3.0804 | 17.1448 | 11.9359 | 6.6951 | -3.6637 | -3.8317 | -4.0133 | -4.2167 | -4.473 | -4.8439 | -5.6005 | -6.5722 | -7.3353 | -8.0638 | 19.6413 | 14.4057 | 9.1326 | -1.2873 | -1.5188 | -1.7646 | -2.0363 | -2.3705 | -2.8917 | -4.0065 | -5.5213 | -6.5049 | -6.9518
|  | SPRING QUARRY WEST | LW |  |  | 20.0438 | 15.8317 | 11.5866 | 3.2009 | 2.9642 | 2.7146 | 2.4408 | 2.1128 | 1.5896 | 0.40306 | -1.3701 | -2.5674 | -3.0804 | 17.1448 | 11.9359 | 6.6951 | -3.6637 | -3.8317 | -4.0133 | -4.2167 | -4.473 | -4.8439 | -5.6005 | -6.5722 | -7.3353 | -8.0638 | 19.6413 | 14.4057 | 9.1326 | -1.2873 | -1.5188 | -1.7646 | -2.0363 | -2.3705 | -2.8917 | -4.0065 | -5.5213 | -6.5049 | -6.9518
|  | SPRING QUARRY WEST | ST |  |  | 20.0438 | 15.8317 | 11.5866 | 3.2009 | 2.9642 | 2.7146 | 2.4408 | 2.1128 | 1.5896 | 0.40306 | -1.3701 | -2.5674 | -3.0804 | 17.1448 | 11.9359 | 6.6951 | -3.6637 | -3.8317 | -4.0133 | -4.2167 | -4.473 | -4.8439 | -5.6005 | -6.5722 | -7.3353 | -8.0638 | 19.6413 | 14.4057 | 9.1326 | -1.2873 | -1.5188 | -1.7646 | -2.0363 | -2.3705 | -2.8917 | -4.0065 | -5.5213 | -6.5049 | -6.9518
|  | SPRING QUARRY WEST | FS |  |  | 20.0438 | 15.8317 | 11.5866 | 3.2009 | 2.9642 | 2.7146 | 2.4408 | 2.1128 | 1.5896 | 0.40306 | -1.3701 | -2.5674 | -3.0804 | 17.1448 | 11.9359 | 6.6951 | -3.6637 | -3.8317 | -4.0133 | -4.2167 | -4.473 | -4.8439 | -5.6005 | -6.5722 | -7.3353 | -8.0638 | 19.6413 | 14.4057 | 9.1326 | -1.2873 | -1.5188 | -1.7646 | -2.0363 | -2.3705 | -2.8917 | -4.0065 | -5.5213 | -6.5049 | -6.9518
NORTH HYDE GSP | NORTH HYDE 22kV | SPRINGFIELD ROAD | MINIMUM HEADROOM | TQ 11409 80620 | YES | 6.773 | -1.5678 | -9.9958 | -18.5427 | -18.9615 | -19.4355 | -19.9448 | -20.501 | -21.4376 | -24.4787 | -30.5273 | -35.9147 | -39.6178 | 8.2752 | -2.0287 | -12.3615 | -22.7765 | -23.1243 | -23.5715 | -24.064 | -24.6175 | -25.3351 | -27.7278 | -32.461 | -38.3962 | -46.2007 | 5.991 | -4.399 | -14.9297 | -25.5257 | -25.9439 | -26.4134 | -26.9231 | -27.4862 | -28.3434 | -31.1166 | -36.2982 | -40.6863 | -43.6785
|  | SPRINGFIELD ROAD | CT |  |  | 6.773 | -1.5678 | -9.9958 | -18.5427 | -18.9615 | -19.4355 | -19.9448 | -20.501 | -21.4376 | -24.4787 | -30.5273 | -35.9147 | -39.6178 | 8.2752 | -2.0287 | -12.3615 | -22.7765 | -23.1243 | -23.5715 | -24.064 | -24.6175 | -25.3351 | -27.7278 | -32.461 | -38.3962 | -46.2007 | 5.991 | -4.399 | -14.9297 | -25.5257 | -25.9439 | -26.4134 | -26.9231 | -27.4862 | -28.3434 | -31.1166 | -36.2982 | -40.6863 | -43.6785
|  | SPRINGFIELD ROAD | LW |  |  | 6.773 | -1.5678 | -9.9958 | -18.5427 | -18.9615 | -19.4355 | -19.9448 | -20.501 | -21.4376 | -24.4787 | -30.5273 | -35.9147 | -39.6178 | 8.2752 | -2.0287 | -12.3615 | -22.7765 | -23.1243 | -23.5715 | -24.064 | -24.6175 | -25.3351 | -27.7278 | -32.461 | -38.3962 | -46.2007 | 5.991 | -4.399 | -14.9297 | -25.5257 | -25.9439 | -26.4134 | -26.9231 | -27.4862 | -28.3434 | -31.1166 | -36.2982 | -40.6863 | -43.6785
|  | SPRINGFIELD ROAD | ST |  |  | 6.773 | -1.5678 | -9.9958 | -18.5427 | -18.9615 | -19.4355 | -19.9448 | -20.501 | -21.4376 | -24.4787 | -30.5273 | -35.9147 | -39.6178 | 8.2752 | -2.0287 | -12.3615 | -22.7765 | -23.1243 | -23.5715 | -24.064 | -24.6175 | -25.3351 | -27.7278 | -32.461 | -38.3962 | -46.2007 | 5.991 | -4.399 | -14.9297 | -25.5257 | -25.9439 | -26.4134 | -26.9231 | -27.4862 | -28.3434 | -31.1166 | -36.2982 | -40.6863 | -43.6785
|  | SPRINGFIELD ROAD | FS |  |  | 6.773 | -1.5678 | -9.9958 | -18.5427 | -18.9615 | -19.4355 | -19.9448 | -20.501 | -21.4376 | -24.4787 | -30.5273 | -35.9147 | -39.6178 | 8.2752 | -2.0287 | -12.3615 | -22.7765 | -23.1243 | -23.5715 | -24.064 | -24.6175 | -25.3351 | -27.7278 | -32.461 | -38.3962 | -46.2007 | 5.991 | -4.399 | -14.9297 | -25.5257 | -25.9439 | -26.4134 | -26.9231 | -27.4862 | -28.3434 | -31.1166 | -36.2982 | -40.6863 | -43.6785
NURSLING GSP | WINCHESTER | ST CROSS | MINIMUM HEADROOM | SU 47287 28156 | YES | 2.1772 | 1.7857 | 1.1661 | 0.35017 | -0.49476 | -1.3424 | -2.1575 | -3.0556 | -4.5347 | -8.6744 | -14.3939 | -17.7717 | -19.2115 | 5.9373 | 5.6162 | 5.0961 | 4.495 | 3.8701 | 3.2215 | 2.6035 | 1.9129 | 0.9018 | -1.8934 | -5.4535 | -7.9403 | -10.3658 | 3.9652 | 3.5891 | 2.9976 | 2.2336 | 1.4414 | 0.6415 | -0.13119 | -0.9876 | -2.3866 | -6.279 | -11.4995 | -14.484 | -15.7324
|  | ST CROSS | CT |  |  | 2.1772 | 1.7857 | 1.1661 | 0.35017 | -0.49476 | -1.3424 | -2.1575 | -3.0556 | -4.5347 | -8.6744 | -14.3939 | -17.7717 | -19.2115 | 5.9373 | 5.6162 | 5.0961 | 4.495 | 3.8701 | 3.2215 | 2.6035 | 1.9129 | 0.9018 | -1.8934 | -5.4535 | -7.9403 | -10.3658 | 3.9652 | 3.5891 | 2.9976 | 2.2336 | 1.4414 | 0.6415 | -0.13119 | -0.9876 | -2.3866 | -6.279 | -11.4995 | -14.484 | -15.7324
|  | ST CROSS | LW |  |  | 2.1772 | 1.7857 | 1.1661 | 0.35017 | -0.49476 | -1.3424 | -2.1575 | -3.0556 | -4.5347 | -8.6744 | -14.3939 | -17.7717 | -19.2115 | 5.9373 | 5.6162 | 5.0961 | 4.495 | 3.8701 | 3.2215 | 2.6035 | 1.9129 | 0.9018 | -1.8934 | -5.4535 | -7.9403 | -10.3658 | 3.9652 | 3.5891 | 2.9976 | 2.2336 | 1.4414 | 0.6415 | -0.13119 | -0.9876 | -2.3866 | -6.279 | -11.4995 | -14.484 | -15.7324
|  | ST CROSS | ST |  |  | 2.1772 | 1.7857 | 1.1661 | 0.35017 | -0.49476 | -1.3424 | -2.1575 | -3.0556 | -4.5347 | -8.6744 | -14.3939 | -17.7717 | -19.2115 | 5.9373 | 5.6162 | 5.0961 | 4.495 | 3.8701 | 3.2215 | 2.6035 | 1.9129 | 0.9018 | -1.8934 | -5.4535 | -7.9403 | -10.3658 | 3.9652 | 3.5891 | 2.9976 | 2.2336 | 1.4414 | 0.6415 | -0.13119 | -0.9876 | -2.3866 | -6.279 | -11.4995 | -14.484 | -15.7324
|  | ST CROSS | FS |  |  | 2.1772 | 1.7857 | 1.1661 | 0.35017 | -0.49476 | -1.3424 | -2.1575 | -3.0556 | -4.5347 | -8.6744 | -14.3939 | -17.7717 | -19.2115 | 5.9373 | 5.6162 | 5.0961 | 4.495 | 3.8701 | 3.2215 | 2.6035 | 1.9129 | 0.9018 | -1.8934 | -5.4535 | -7.9403 | -10.3658 | 3.9652 | 3.5891 | 2.9976 | 2.2336 | 1.4414 | 0.6415 | -0.13119 | -0.9876 | -2.3866 | -6.279 | -11.4995 | -14.484 | -15.7324
COWLEY GSP | OXFORD BSP | ST EBBES | MINIMUM HEADROOM | SP 51259 05741 | YES | 19.3318 | 19.0943 | 18.761 | 18.4784 | 18.1546 | 17.8844 | 17.5627 | 17.2862 | 16.7849 | 15.0139 | 11.4029 | 8.5175 | 6.6713 | 20.4484 | 20.2333 | 19.9065 | 19.6681 | 19.3692 | 19.1178 | 18.7828 | 18.5009 | 18.1637 | 17.1195 | 14.9727 | 12.8611 | 10.58 | 20.384 | 20.1594 | 19.8311 | 19.565 | 19.2517 | 18.9917 | 18.6795 | 18.4169 | 18.0811 | 16.5667 | 13.487 | 11.1712 | 9.6906
|  | ST EBBES | CT |  |  | 19.3318 | 19.0943 | 18.761 | 18.4784 | 18.1546 | 17.8844 | 17.5627 | 17.2862 | 16.7849 | 15.0139 | 11.4029 | 8.5175 | 6.6713 | 20.4484 | 20.2333 | 19.9065 | 19.6681 | 19.3692 | 19.1178 | 18.7828 | 18.5009 | 18.1637 | 17.1195 | 14.9727 | 12.8611 | 10.58 | 20.384 | 20.1594 | 19.8311 | 19.565 | 19.2517 | 18.9917 | 18.6795 | 18.4169 | 18.0811 | 16.5667 | 13.487 | 11.1712 | 9.6906
|  | ST EBBES | LW |  |  | 19.3318 | 19.0943 | 18.761 | 18.4784 | 18.1546 | 17.8844 | 17.5627 | 17.2862 | 16.7849 | 15.0139 | 11.4029 | 8.5175 | 6.6713 | 20.4484 | 20.2333 | 19.9065 | 19.6681 | 19.3692 | 19.1178 | 18.7828 | 18.5009 | 18.1637 | 17.1195 | 14.9727 | 12.8611 | 10.58 | 20.384 | 20.1594 | 19.8311 | 19.565 | 19.2517 | 18.9917 | 18.6795 | 18.4169 | 18.0811 | 16.5667 | 13.487 | 11.1712 | 9.6906
|  | ST EBBES | ST |  |  | 19.3318 | 19.0943 | 18.761 | 18.4784 | 18.1546 | 17.8844 | 17.5627 | 17.2862 | 16.7849 | 15.0139 | 11.4029 | 8.5175 | 6.6713 | 20.4484 | 20.2333 | 19.9065 | 19.6681 | 19.3692 | 19.1178 | 18.7828 | 18.5009 | 18.1637 | 17.1195 | 14.9727 | 12.8611 | 10.58 | 20.384 | 20.1594 | 19.8311 | 19.565 | 19.2517 | 18.9917 | 18.6795 | 18.4169 | 18.0811 | 16.5667 | 13.487 | 11.1712 | 9.6906
|  | ST EBBES | FS |  |  | 19.3318 | 19.0943 | 18.761 | 18.4784 | 18.1546 | 17.8844 | 17.5627 | 17.2862 | 16.7849 | 15.0139 | 11.4029 | 8.5175 | 6.6713 | 20.4484 | 20.2333 | 19.9065 | 19.6681 | 19.3692 | 19.1178 | 18.7828 | 18.5009 | 18.1637 | 17.1195 | 14.9727 | 12.8611 | 10.58 | 20.384 | 20.1594 | 19.8311 | 19.565 | 19.2517 | 18.9917 | 18.6795 | 18.4169 | 18.0811 | 16.5667 | 13.487 | 11.1712 | 9.6906
BRAMLEY (ANDO-THAT) | THATCHAM BSP | ST JOHNS | MINIMUM HEADROOM | SU 47113 66363 | YES | 18.5098 | 18.4591 | 18.408 | 18.3536 | 18.092 | 17.7942 | 17.4644 | 17.0927 | 16.703 | 15.307 | 14.0798 | 13.5044 | 13.0389 | 23.1955 | 23.1419 | 23.0907 | 23.0421 | 22.8876 | 22.7137 | 22.5223 | 22.3062 | 22.0863 | 21.3074 | 20.5148 | 20.0367 | 19.493 | 19.3286 | 19.2739 | 19.2217 | 19.1686 | 18.9513 | 18.7045 | 18.4309 | 18.1211 | 17.7956 | 16.6416 | 15.6123 | 15.1427 | 14.7673
|  | ST JOHNS | CT |  |  | 18.5098 | 18.4591 | 18.408 | 18.3536 | 18.092 | 17.7942 | 17.4644 | 17.0927 | 16.703 | 15.307 | 14.0798 | 13.5044 | 13.0389 | 23.1955 | 23.1419 | 23.0907 | 23.0421 | 22.8876 | 22.7137 | 22.5223 | 22.3062 | 22.0863 | 21.3074 | 20.5148 | 20.0367 | 19.493 | 19.3286 | 19.2739 | 19.2217 | 19.1686 | 18.9513 | 18.7045 | 18.4309 | 18.1211 | 17.7956 | 16.6416 | 15.6123 | 15.1427 | 14.7673
|  | ST JOHNS | LW |  |  | 18.5098 | 18.4591 | 18.408 | 18.3536 | 18.092 | 17.7942 | 17.4644 | 17.0927 | 16.703 | 15.307 | 14.0798 | 13.5044 | 13.0389 | 23.1955 | 23.1419 | 23.0907 | 23.0421 | 22.8876 | 22.7137 | 22.5223 | 22.3062 | 22.0863 | 21.3074 | 20.5148 | 20.0367 | 19.493 | 19.3286 | 19.2739 | 19.2217 | 19.1686 | 18.9513 | 18.7045 | 18.4309 | 18.1211 | 17.7956 | 16.6416 | 15.6123 | 15.1427 | 14.7673
|  | ST JOHNS | ST |  |  | 18.5098 | 18.4591 | 18.408 | 18.3536 | 18.092 | 17.7942 | 17.4644 | 17.0927 | 16.703 | 15.307 | 14.0798 | 13.5044 | 13.0389 | 23.1955 | 23.1419 | 23.0907 | 23.0421 | 22.8876 | 22.7137 | 22.5223 | 22.3062 | 22.0863 | 21.3074 | 20.5148 | 20.0367 | 19.493 | 19.3286 | 19.2739 | 19.2217 | 19.1686 | 18.9513 | 18.7045 | 18.4309 | 18.1211 | 17.7956 | 16.6416 | 15.6123 | 15.1427 | 14.7673
|  | ST JOHNS | FS |  |  | 18.5098 | 18.4591 | 18.408 | 18.3536 | 18.092 | 17.7942 | 17.4644 | 17.0927 | 16.703 | 15.307 | 14.0798 | 13.5044 | 13.0389 | 23.1955 | 23.1419 | 23.0907 | 23.0421 | 22.8876 | 22.7137 | 22.5223 | 22.3062 | 22.0863 | 21.3074 | 20.5148 | 20.0367 | 19.493 | 19.3286 | 19.2739 | 19.2217 | 19.1686 | 18.9513 | 18.7045 | 18.4309 | 18.1211 | 17.7956 | 16.6416 | 15.6123 | 15.1427 | 14.7673
COWLEY GSP | WITNEY BSP | STANDLAKE | MINIMUM HEADROOM | SP 38923 02349 | NO | 0.15173 | 0.010287 | -0.13701 | -0.35011 | -0.57472 | -0.8076 | -1.0788 | -1.3749 | -1.7962 | -2.6586 | -3.7206 | -3.9525 | -4.0789 | 0.67025 | 0.62817 | 0.58037 | 0.51934 | 0.45303 | 0.38351 | 0.30436 | 0.21995 | 0.10228 | -0.22438 | -0.74519 | -0.91626 | -1.0193 | -1.4448 | -1.5548 | -1.6683 | -1.8587 | -2.0534 | -2.2416 | -2.4491 | -2.6652 | -2.9787 | -3.7594 | -4.798 | -5.0197 | -5.1411
|  | STANDLAKE | CT |  |  | 0.15173 | 0.010287 | -0.13701 | -0.35011 | -0.57472 | -0.8076 | -1.0788 | -1.3749 | -1.7962 | -2.6586 | -3.7206 | -3.9525 | -4.0789 | 0.67025 | 0.62817 | 0.58037 | 0.51934 | 0.45303 | 0.38351 | 0.30436 | 0.21995 | 0.10228 | -0.22438 | -0.74519 | -0.91626 | -1.0193 | -1.4448 | -1.5548 | -1.6683 | -1.8587 | -2.0534 | -2.2416 | -2.4491 | -2.6652 | -2.9787 | -3.7594 | -4.798 | -5.0197 | -5.1411
|  | STANDLAKE | LW |  |  | 0.15173 | 0.010287 | -0.13701 | -0.35011 | -0.57472 | -0.8076 | -1.0788 | -1.3749 | -1.7962 | -2.6586 | -3.7206 | -3.9525 | -4.0789 | 0.67025 | 0.62817 | 0.58037 | 0.51934 | 0.45303 | 0.38351 | 0.30436 | 0.21995 | 0.10228 | -0.22438 | -0.74519 | -0.91626 | -1.0193 | -1.4448 | -1.5548 | -1.6683 | -1.8587 | -2.0534 | -2.2416 | -2.4491 | -2.6652 | -2.9787 | -3.7594 | -4.798 | -5.0197 | -5.1411
|  | STANDLAKE | ST |  |  | 0.15173 | 0.010287 | -0.13701 | -0.35011 | -0.57472 | -0.8076 | -1.0788 | -1.3749 | -1.7962 | -2.6586 | -3.7206 | -3.9525 | -4.0789 | 0.67025 | 0.62817 | 0.58037 | 0.51934 | 0.45303 | 0.38351 | 0.30436 | 0.21995 | 0.10228 | -0.22438 | -0.74519 | -0.91626 | -1.0193 | -1.4448 | -1.5548 | -1.6683 | -1.8587 | -2.0534 | -2.2416 | -2.4491 | -2.6652 | -2.9787 | -3.7594 | -4.798 | -5.0197 | -5.1411
|  | STANDLAKE | FS |  |  | 0.15173 | 0.010287 | -0.13701 | -0.35011 | -0.57472 | -0.8076 | -1.0788 | -1.3749 | -1.7962 | -2.6586 | -3.7206 | -3.9525 | -4.0789 | 0.67025 | 0.62817 | 0.58037 | 0.51934 | 0.45303 | 0.38351 | 0.30436 | 0.21995 | 0.10228 | -0.22438 | -0.74519 | -0.91626 | -1.0193 | -1.4448 | -1.5548 | -1.6683 | -1.8587 | -2.0534 | -2.2416 | -2.4491 | -2.6652 | -2.9787 | -3.7594 | -4.798 | -5.0197 | -5.1411
MINETY GSP | STRATTON (2 X 60) | STANTON FITZWARREN | MINIMUM HEADROOM | SU 17585 90987 | YES | 16.6686 | 16.2376 | 15.7881 | 15.2885 | 14.8748 | 14.5108 | 14.1376 | 12.9856 | 11.4311 | 7.6963 | 3.7141 | 1.15 | 0.079528 | 16.8163 | 16.3005 | 15.7147 | 15.0261 | 14.4239 | 13.87 | 13.2862 | 12.6023 | 11.7632 | 9.7552 | 7.5641 | 6.0961 | 5.0403 | 19.5557 | 19.1861 | 18.6206 | 17.7648 | 17.0168 | 16.3352 | 15.6219 | 14.8191 | 13.7695 | 10.9952 | 7.4405 | 5.0994 | 4.1108
|  | STANTON FITZWARREN | CT |  |  | 16.6686 | 16.2376 | 15.7881 | 15.2885 | 14.8748 | 14.5108 | 14.1376 | 12.9856 | 11.4311 | 7.6963 | 3.7141 | 1.15 | 0.079528 | 16.8163 | 16.3005 | 15.7147 | 15.0261 | 14.4239 | 13.87 | 13.2862 | 12.6023 | 11.7632 | 9.7552 | 7.5641 | 6.0961 | 5.0403 | 19.5557 | 19.1861 | 18.6206 | 17.7648 | 17.0168 | 16.3352 | 15.6219 | 14.8191 | 13.7695 | 10.9952 | 7.4405 | 5.0994 | 4.1108
|  | STANTON FITZWARREN | LW |  |  | 16.6686 | 16.2376 | 15.7881 | 15.2885 | 14.8748 | 14.5108 | 14.1376 | 12.9856 | 11.4311 | 7.6963 | 3.7141 | 1.15 | 0.079528 | 16.8163 | 16.3005 | 15.7147 | 15.0261 | 14.4239 | 13.87 | 13.2862 | 12.6023 | 11.7632 | 9.7552 | 7.5641 | 6.0961 | 5.0403 | 19.5557 | 19.1861 | 18.6206 | 17.7648 | 17.0168 | 16.3352 | 15.6219 | 14.8191 | 13.7695 | 10.9952 | 7.4405 | 5.0994 | 4.1108
|  | STANTON FITZWARREN | ST |  |  | 16.6686 | 16.2376 | 15.7881 | 15.2885 | 14.8748 | 14.5108 | 14.1376 | 12.9856 | 11.4311 | 7.6963 | 3.7141 | 1.15 | 0.079528 | 16.8163 | 16.3005 | 15.7147 | 15.0261 | 14.4239 | 13.87 | 13.2862 | 12.6023 | 11.7632 | 9.7552 | 7.5641 | 6.0961 | 5.0403 | 19.5557 | 19.1861 | 18.6206 | 17.7648 | 17.0168 | 16.3352 | 15.6219 | 14.8191 | 13.7695 | 10.9952 | 7.4405 | 5.0994 | 4.1108
|  | STANTON FITZWARREN | FS |  |  | 16.6686 | 16.2376 | 15.7881 | 15.2885 | 14.8748 | 14.5108 | 14.1376 | 12.9856 | 11.4311 | 7.6963 | 3.7141 | 1.15 | 0.079528 | 16.8163 | 16.3005 | 15.7147 | 15.0261 | 14.4239 | 13.87 | 13.2862 | 12.6023 | 11.7632 | 9.7552 | 7.5641 | 6.0961 | 5.0403 | 19.5557 | 19.1861 | 18.6206 | 17.7648 | 17.0168 | 16.3352 | 15.6219 | 14.8191 | 13.7695 | 10.9952 | 7.4405 | 5.0994 | 4.1108
LALEHAM | STAINES | STANWELL | MINIMUM HEADROOM | TQ 06003 72766 | YES | 9.9287 | 9.2698 | 8.3748 | 7.3707 | 6.3011 | 5.2002 | 3.9781 | 2.7594 | 1.4288 | -2.835 | -7.7977 | -10.9313 | -12.9368 | 12.3795 | 12.1389 | 11.8496 | 11.4622 | 10.8894 | 10.2965 | 9.6094 | 8.9135 | 8.1564 | 5.7082 | 2.8065 | 0.99044 | -0.52377 | 10.2716 | 9.678 | 8.8877 | 8.0124 | 7.0785 | 6.111 | 5.0456 | 3.9739 | 2.788 | -1.0025 | -5.3499 | -7.9415 | -9.5737
|  | STANWELL | CT |  |  | 9.9287 | 9.2698 | 8.3748 | 7.3707 | 6.3011 | 5.2002 | 3.9781 | 2.7594 | 1.4288 | -2.835 | -7.7977 | -10.9313 | -12.9368 | 12.3795 | 12.1389 | 11.8496 | 11.4622 | 10.8894 | 10.2965 | 9.6094 | 8.9135 | 8.1564 | 5.7082 | 2.8065 | 0.99044 | -0.52377 | 10.2716 | 9.678 | 8.8877 | 8.0124 | 7.0785 | 6.111 | 5.0456 | 3.9739 | 2.788 | -1.0025 | -5.3499 | -7.9415 | -9.5737
|  | STANWELL | LW |  |  | 9.9287 | 9.2698 | 8.3748 | 7.3707 | 6.3011 | 5.2002 | 3.9781 | 2.7594 | 1.4288 | -2.835 | -7.7977 | -10.9313 | -12.9368 | 12.3795 | 12.1389 | 11.8496 | 11.4622 | 10.8894 | 10.2965 | 9.6094 | 8.9135 | 8.1564 | 5.7082 | 2.8065 | 0.99044 | -0.52377 | 10.2716 | 9.678 | 8.8877 | 8.0124 | 7.0785 | 6.111 | 5.0456 | 3.9739 | 2.788 | -1.0025 | -5.3499 | -7.9415 | -9.5737
|  | STANWELL | ST |  |  | 9.9287 | 9.2698 | 8.3748 | 7.3707 | 6.3011 | 5.2002 | 3.9781 | 2.7594 | 1.4288 | -2.835 | -7.7977 | -10.9313 | -12.9368 | 12.3795 | 12.1389 | 11.8496 | 11.4622 | 10.8894 | 10.2965 | 9.6094 | 8.9135 | 8.1564 | 5.7082 | 2.8065 | 0.99044 | -0.52377 | 10.2716 | 9.678 | 8.8877 | 8.0124 | 7.0785 | 6.111 | 5.0456 | 3.9739 | 2.788 | -1.0025 | -5.3499 | -7.9415 | -9.5737
|  | STANWELL | FS |  |  | 9.9287 | 9.2698 | 8.3748 | 7.3707 | 6.3011 | 5.2002 | 3.9781 | 2.7594 | 1.4288 | -2.835 | -7.7977 | -10.9313 | -12.9368 | 12.3795 | 12.1389 | 11.8496 | 11.4622 | 10.8894 | 10.2965 | 9.6094 | 8.9135 | 8.1564 | 5.7082 | 2.8065 | 0.99044 | -0.52377 | 10.2716 | 9.678 | 8.8877 | 8.0124 | 7.0785 | 6.111 | 5.0456 | 3.9739 | 2.788 | -1.0025 | -5.3499 | -7.9415 | -9.5737
MANNINGTON GSP | SALISBURY | STAPLEFORD | MINIMUM HEADROOM | SU 06871 37078 | YES | 11.576 | 11.3774 | 11.1455 | 10.8084 | 10.4568 | 10.0909 | 9.697 | 9.2295 | 8.5852 | 7.4413 | 6.6319 | 6.1874 | 6.0161 | 11.3078 | 11.2934 | 11.2733 | 11.1705 | 11.0445 | 10.9112 | 10.7708 | 10.6247 | 10.3577 | 9.781 | 9.3558 | 9.1501 | 8.9323 | 13.9115 | 13.8851 | 13.8478 | 13.7437 | 13.4196 | 13.0822 | 12.7172 | 12.2788 | 11.6771 | 10.6231 | 9.9042 | 9.5305 | 9.3873
|  | STAPLEFORD | CT |  |  | 11.576 | 11.3774 | 11.1455 | 10.8084 | 10.4568 | 10.0909 | 9.697 | 9.2295 | 8.5852 | 7.4413 | 6.6319 | 6.1874 | 6.0161 | 11.3078 | 11.2934 | 11.2733 | 11.1705 | 11.0445 | 10.9112 | 10.7708 | 10.6247 | 10.3577 | 9.781 | 9.3558 | 9.1501 | 8.9323 | 13.9115 | 13.8851 | 13.8478 | 13.7437 | 13.4196 | 13.0822 | 12.7172 | 12.2788 | 11.6771 | 10.6231 | 9.9042 | 9.5305 | 9.3873
|  | STAPLEFORD | LW |  |  | 11.576 | 11.3774 | 11.1455 | 10.8084 | 10.4568 | 10.0909 | 9.697 | 9.2295 | 8.5852 | 7.4413 | 6.6319 | 6.1874 | 6.0161 | 11.3078 | 11.2934 | 11.2733 | 11.1705 | 11.0445 | 10.9112 | 10.7708 | 10.6247 | 10.3577 | 9.781 | 9.3558 | 9.1501 | 8.9323 | 13.9115 | 13.8851 | 13.8478 | 13.7437 | 13.4196 | 13.0822 | 12.7172 | 12.2788 | 11.6771 | 10.6231 | 9.9042 | 9.5305 | 9.3873
|  | STAPLEFORD | ST |  |  | 11.576 | 11.3774 | 11.1455 | 10.8084 | 10.4568 | 10.0909 | 9.697 | 9.2295 | 8.5852 | 7.4413 | 6.6319 | 6.1874 | 6.0161 | 11.3078 | 11.2934 | 11.2733 | 11.1705 | 11.0445 | 10.9112 | 10.7708 | 10.6247 | 10.3577 | 9.781 | 9.3558 | 9.1501 | 8.9323 | 13.9115 | 13.8851 | 13.8478 | 13.7437 | 13.4196 | 13.0822 | 12.7172 | 12.2788 | 11.6771 | 10.6231 | 9.9042 | 9.5305 | 9.3873
|  | STAPLEFORD | FS |  |  | 11.576 | 11.3774 | 11.1455 | 10.8084 | 10.4568 | 10.0909 | 9.697 | 9.2295 | 8.5852 | 7.4413 | 6.6319 | 6.1874 | 6.0161 | 11.3078 | 11.2934 | 11.2733 | 11.1705 | 11.0445 | 10.9112 | 10.7708 | 10.6247 | 10.3577 | 9.781 | 9.3558 | 9.1501 | 8.9323 | 13.9115 | 13.8851 | 13.8478 | 13.7437 | 13.4196 | 13.0822 | 12.7172 | 12.2788 | 11.6771 | 10.6231 | 9.9042 | 9.5305 | 9.3873
COWLEY GSP | HIGH WYCOMBE BSP | STOKENCHURCH | MINIMUM HEADROOM | SU 77124 94355 | YES | -0.21156 | -0.47087 | -0.75422 | -1.1433 | -1.5414 | -1.9817 | -2.466 | -3.0374 | -3.8185 | -5.4761 | -8.4155 | -10.5046 | -11.382 | 3.1077 | 2.9258 | 2.721 | 2.4782 | 2.2271 | 1.938 | 1.6182 | 1.2323 | 0.74193 | -0.17482 | -1.5949 | -2.5505 | -3.1584 | 1.5417 | 1.2922 | 1.0101 | 0.65663 | 0.29195 | -0.1207 | -0.57227 | -1.1057 | -1.8212 | -3.2869 | -5.8488 | -7.574 | -8.3339
|  | STOKENCHURCH | CT |  |  | -0.21156 | -0.47087 | -0.75422 | -1.1433 | -1.5414 | -1.9817 | -2.466 | -3.0374 | -3.8185 | -5.4761 | -8.4155 | -10.5046 | -11.382 | 3.1077 | 2.9258 | 2.721 | 2.4782 | 2.2271 | 1.938 | 1.6182 | 1.2323 | 0.74193 | -0.17482 | -1.5949 | -2.5505 | -3.1584 | 1.5417 | 1.2922 | 1.0101 | 0.65663 | 0.29195 | -0.1207 | -0.57227 | -1.1057 | -1.8212 | -3.2869 | -5.8488 | -7.574 | -8.3339
|  | STOKENCHURCH | LW |  |  | -0.21156 | -0.47087 | -0.75422 | -1.1433 | -1.5414 | -1.9817 | -2.466 | -3.0374 | -3.8185 | -5.4761 | -8.4155 | -10.5046 | -11.382 | 3.1077 | 2.9258 | 2.721 | 2.4782 | 2.2271 | 1.938 | 1.6182 | 1.2323 | 0.74193 | -0.17482 | -1.5949 | -2.5505 | -3.1584 | 1.5417 | 1.2922 | 1.0101 | 0.65663 | 0.29195 | -0.1207 | -0.57227 | -1.1057 | -1.8212 | -3.2869 | -5.8488 | -7.574 | -8.3339
|  | STOKENCHURCH | ST |  |  | -0.21156 | -0.47087 | -0.75422 | -1.1433 | -1.5414 | -1.9817 | -2.466 | -3.0374 | -3.8185 | -5.4761 | -8.4155 | -10.5046 | -11.382 | 3.1077 | 2.9258 | 2.721 | 2.4782 | 2.2271 | 1.938 | 1.6182 | 1.2323 | 0.74193 | -0.17482 | -1.5949 | -2.5505 | -3.1584 | 1.5417 | 1.2922 | 1.0101 | 0.65663 | 0.29195 | -0.1207 | -0.57227 | -1.1057 | -1.8212 | -3.2869 | -5.8488 | -7.574 | -8.3339
|  | STOKENCHURCH | FS |  |  | -0.21156 | -0.47087 | -0.75422 | -1.1433 | -1.5414 | -1.9817 | -2.466 | -3.0374 | -3.8185 | -5.4761 | -8.4155 | -10.5046 | -11.382 | 3.1077 | 2.9258 | 2.721 | 2.4782 | 2.2271 | 1.938 | 1.6182 | 1.2323 | 0.74193 | -0.17482 | -1.5949 | -2.5505 | -3.1584 | 1.5417 | 1.2922 | 1.0101 | 0.65663 | 0.29195 | -0.1207 | -0.57227 | -1.1057 | -1.8212 | -3.2869 | -5.8488 | -7.574 | -8.3339
MINETY GSP | STRATTON (2 X 60) | STRATTON | MINIMUM HEADROOM | SU 16998 88837 | YES | 24.0262 | 23.4855 | 22.8207 | 22.0178 | 21.1489 | 20.2547 | 19.1818 | 17.8478 | 16.2179 | 12.0863 | 7.2081 | 3.8282 | 2.0958 | 27.8419 | 27.5118 | 27.094 | 26.6414 | 26.1526 | 25.6369 | 25.0311 | 24.2235 | 23.2366 | 20.7364 | 17.8762 | 15.8484 | 14.1441 | 25.1826 | 24.7481 | 24.2066 | 23.5381 | 22.8133 | 22.0372 | 21.0693 | 19.8674 | 18.3899 | 14.659 | 10.2933 | 7.4529 | 6.0054
|  | STRATTON | CT |  |  | 24.0262 | 23.4855 | 22.8207 | 22.0178 | 21.1489 | 20.2547 | 19.1818 | 17.8478 | 16.2179 | 12.0863 | 7.2081 | 3.8282 | 2.0958 | 27.8419 | 27.5118 | 27.094 | 26.6414 | 26.1526 | 25.6369 | 25.0311 | 24.2235 | 23.2366 | 20.7364 | 17.8762 | 15.8484 | 14.1441 | 25.1826 | 24.7481 | 24.2066 | 23.5381 | 22.8133 | 22.0372 | 21.0693 | 19.8674 | 18.3899 | 14.659 | 10.2933 | 7.4529 | 6.0054
|  | STRATTON | LW |  |  | 24.0262 | 23.4855 | 22.8207 | 22.0178 | 21.1489 | 20.2547 | 19.1818 | 17.8478 | 16.2179 | 12.0863 | 7.2081 | 3.8282 | 2.0958 | 27.8419 | 27.5118 | 27.094 | 26.6414 | 26.1526 | 25.6369 | 25.0311 | 24.2235 | 23.2366 | 20.7364 | 17.8762 | 15.8484 | 14.1441 | 25.1826 | 24.7481 | 24.2066 | 23.5381 | 22.8133 | 22.0372 | 21.0693 | 19.8674 | 18.3899 | 14.659 | 10.2933 | 7.4529 | 6.0054
|  | STRATTON | ST |  |  | 24.0262 | 23.4855 | 22.8207 | 22.0178 | 21.1489 | 20.2547 | 19.1818 | 17.8478 | 16.2179 | 12.0863 | 7.2081 | 3.8282 | 2.0958 | 27.8419 | 27.5118 | 27.094 | 26.6414 | 26.1526 | 25.6369 | 25.0311 | 24.2235 | 23.2366 | 20.7364 | 17.8762 | 15.8484 | 14.1441 | 25.1826 | 24.7481 | 24.2066 | 23.5381 | 22.8133 | 22.0372 | 21.0693 | 19.8674 | 18.3899 | 14.659 | 10.2933 | 7.4529 | 6.0054
|  | STRATTON | FS |  |  | 24.0262 | 23.4855 | 22.8207 | 22.0178 | 21.1489 | 20.2547 | 19.1818 | 17.8478 | 16.2179 | 12.0863 | 7.2081 | 3.8282 | 2.0958 | 27.8419 | 27.5118 | 27.094 | 26.6414 | 26.1526 | 25.6369 | 25.0311 | 24.2235 | 23.2366 | 20.7364 | 17.8762 | 15.8484 | 14.1441 | 25.1826 | 24.7481 | 24.2066 | 23.5381 | 22.8133 | 22.0372 | 21.0693 | 19.8674 | 18.3899 | 14.659 | 10.2933 | 7.4529 | 6.0054
LALEHAM | STAINES | SUNBURY CROSS | MINIMUM HEADROOM | TQ 10053 69996 | YES | 14.7485 | 13.5909 | 12.0885 | 10.2934 | 8.3746 | 6.3691 | 4.137 | 1.759 | -1.4685 | -10.2459 | -23.6686 | -31.5719 | -35.5639 | 28.957 | 28.1445 | 27.1648 | 26.0135 | 24.7813 | 23.4722 | 22.0137 | 20.3838 | 18.291 | 12.3364 | 3.6877 | -1.9072 | -7.3407 | 26.8131 | 25.7543 | 24.4247 | 22.8115 | 21.051 | 19.2001 | 17.1398 | 14.8906 | 11.846 | 3.6102 | -8.6381 | -15.5543 | -19.0623
|  | SUNBURY CROSS | CT |  |  | 14.7485 | 13.5909 | 12.0885 | 10.2934 | 8.3746 | 6.3691 | 4.137 | 1.759 | -1.4685 | -10.2459 | -23.6686 | -31.5719 | -35.5639 | 28.957 | 28.1445 | 27.1648 | 26.0135 | 24.7813 | 23.4722 | 22.0137 | 20.3838 | 18.291 | 12.3364 | 3.6877 | -1.9072 | -7.3407 | 26.8131 | 25.7543 | 24.4247 | 22.8115 | 21.051 | 19.2001 | 17.1398 | 14.8906 | 11.846 | 3.6102 | -8.6381 | -15.5543 | -19.0623
|  | SUNBURY CROSS | LW |  |  | 14.7485 | 13.5909 | 12.0885 | 10.2934 | 8.3746 | 6.3691 | 4.137 | 1.759 | -1.4685 | -10.2459 | -23.6686 | -31.5719 | -35.5639 | 28.957 | 28.1445 | 27.1648 | 26.0135 | 24.7813 | 23.4722 | 22.0137 | 20.3838 | 18.291 | 12.3364 | 3.6877 | -1.9072 | -7.3407 | 26.8131 | 25.7543 | 24.4247 | 22.8115 | 21.051 | 19.2001 | 17.1398 | 14.8906 | 11.846 | 3.6102 | -8.6381 | -15.5543 | -19.0623
|  | SUNBURY CROSS | ST |  |  | 14.7485 | 13.5909 | 12.0885 | 10.2934 | 8.3746 | 6.3691 | 4.137 | 1.759 | -1.4685 | -10.2459 | -23.6686 | -31.5719 | -35.5639 | 28.957 | 28.1445 | 27.1648 | 26.0135 | 24.7813 | 23.4722 | 22.0137 | 20.3838 | 18.291 | 12.3364 | 3.6877 | -1.9072 | -7.3407 | 26.8131 | 25.7543 | 24.4247 | 22.8115 | 21.051 | 19.2001 | 17.1398 | 14.8906 | 11.846 | 3.6102 | -8.6381 | -15.5543 | -19.0623
|  | SUNBURY CROSS | FS |  |  | 14.7485 | 13.5909 | 12.0885 | 10.2934 | 8.3746 | 6.3691 | 4.137 | 1.759 | -1.4685 | -10.2459 | -23.6686 | -31.5719 | -35.5639 | 28.957 | 28.1445 | 27.1648 | 26.0135 | 24.7813 | 23.4722 | 22.0137 | 20.3838 | 18.291 | 12.3364 | 3.6877 | -1.9072 | -7.3407 | 26.8131 | 25.7543 | 24.4247 | 22.8115 | 21.051 | 19.2001 | 17.1398 | 14.8906 | 11.846 | 3.6102 | -8.6381 | -15.5543 | -19.0623
BRAMLEY (FLEE) | BRACKNELL RESERVE | SUNNINGHILL | MINIMUM HEADROOM | SU 93757 67606 | YES | 19.0056 | 18.7572 | 18.5232 | 18.1945 | 17.8406 | 17.4746 | 17.081 | 16.6364 | 15.901 | 14.1611 | 11.3646 | 9.4784 | 8.6275 | 19.466 | 19.2836 | 19.1052 | 18.896 | 18.6688 | 18.4201 | 18.1484 | 17.8323 | 17.3532 | 16.2906 | 14.7523 | 13.6794 | 12.8314 | 21.1525 | 20.9188 | 20.6948 | 20.3993 | 20.0806 | 19.7444 | 19.3806 | 18.9636 | 18.2856 | 16.7083 | 14.1892 | 12.532 | 11.7937
|  | SUNNINGHILL | CT |  |  | 19.0056 | 18.7572 | 18.5232 | 18.1945 | 17.8406 | 17.4746 | 17.081 | 16.6364 | 15.901 | 14.1611 | 11.3646 | 9.4784 | 8.6275 | 19.466 | 19.2836 | 19.1052 | 18.896 | 18.6688 | 18.4201 | 18.1484 | 17.8323 | 17.3532 | 16.2906 | 14.7523 | 13.6794 | 12.8314 | 21.1525 | 20.9188 | 20.6948 | 20.3993 | 20.0806 | 19.7444 | 19.3806 | 18.9636 | 18.2856 | 16.7083 | 14.1892 | 12.532 | 11.7937
|  | SUNNINGHILL | LW |  |  | 19.0056 | 18.7572 | 18.5232 | 18.1945 | 17.8406 | 17.4746 | 17.081 | 16.6364 | 15.901 | 14.1611 | 11.3646 | 9.4784 | 8.6275 | 19.466 | 19.2836 | 19.1052 | 18.896 | 18.6688 | 18.4201 | 18.1484 | 17.8323 | 17.3532 | 16.2906 | 14.7523 | 13.6794 | 12.8314 | 21.1525 | 20.9188 | 20.6948 | 20.3993 | 20.0806 | 19.7444 | 19.3806 | 18.9636 | 18.2856 | 16.7083 | 14.1892 | 12.532 | 11.7937
|  | SUNNINGHILL | ST |  |  | 19.0056 | 18.7572 | 18.5232 | 18.1945 | 17.8406 | 17.4746 | 17.081 | 16.6364 | 15.901 | 14.1611 | 11.3646 | 9.4784 | 8.6275 | 19.466 | 19.2836 | 19.1052 | 18.896 | 18.6688 | 18.4201 | 18.1484 | 17.8323 | 17.3532 | 16.2906 | 14.7523 | 13.6794 | 12.8314 | 21.1525 | 20.9188 | 20.6948 | 20.3993 | 20.0806 | 19.7444 | 19.3806 | 18.9636 | 18.2856 | 16.7083 | 14.1892 | 12.532 | 11.7937
|  | SUNNINGHILL | FS |  |  | 19.0056 | 18.7572 | 18.5232 | 18.1945 | 17.8406 | 17.4746 | 17.081 | 16.6364 | 15.901 | 14.1611 | 11.3646 | 9.4784 | 8.6275 | 19.466 | 19.2836 | 19.1052 | 18.896 | 18.6688 | 18.4201 | 18.1484 | 17.8323 | 17.3532 | 16.2906 | 14.7523 | 13.6794 | 12.8314 | 21.1525 | 20.9188 | 20.6948 | 20.3993 | 20.0806 | 19.7444 | 19.3806 | 18.9636 | 18.2856 | 16.7083 | 14.1892 | 12.532 | 11.7937
MELKSHAM GSP | CHIPPENHAM | SUTTON BENGER | MINIMUM HEADROOM | ST 93394 80051 | YES | 3.2353 | 3.1391 | 3.041 | 2.9078 | 2.7665 | 2.6199 | 2.4389 | 2.2508 | 1.9902 | 1.56 | 0.88205 | 0.44072 | 0.24988 | 4.8455 | 4.7789 | 4.71 | 4.6299 | 4.5441 | 4.4517 | 4.3319 | 4.2057 | 4.0324 | 3.7965 | 3.4376 | 3.186 | 2.9781 | 3.7587 | 3.6672 | 3.5738 | 3.4501 | 3.319 | 3.1819 | 3.0108 | 2.8327 | 2.5847 | 2.1929 | 1.5868 | 1.2122 | 1.0443
|  | SUTTON BENGER | CT |  |  | 3.2353 | 3.1391 | 3.041 | 2.9078 | 2.7665 | 2.6199 | 2.4389 | 2.2508 | 1.9902 | 1.56 | 0.88205 | 0.44072 | 0.24988 | 4.8455 | 4.7789 | 4.71 | 4.6299 | 4.5441 | 4.4517 | 4.3319 | 4.2057 | 4.0324 | 3.7965 | 3.4376 | 3.186 | 2.9781 | 3.7587 | 3.6672 | 3.5738 | 3.4501 | 3.319 | 3.1819 | 3.0108 | 2.8327 | 2.5847 | 2.1929 | 1.5868 | 1.2122 | 1.0443
|  | SUTTON BENGER | LW |  |  | 3.2353 | 3.1391 | 3.041 | 2.9078 | 2.7665 | 2.6199 | 2.4389 | 2.2508 | 1.9902 | 1.56 | 0.88205 | 0.44072 | 0.24988 | 4.8455 | 4.7789 | 4.71 | 4.6299 | 4.5441 | 4.4517 | 4.3319 | 4.2057 | 4.0324 | 3.7965 | 3.4376 | 3.186 | 2.9781 | 3.7587 | 3.6672 | 3.5738 | 3.4501 | 3.319 | 3.1819 | 3.0108 | 2.8327 | 2.5847 | 2.1929 | 1.5868 | 1.2122 | 1.0443
|  | SUTTON BENGER | ST |  |  | 3.2353 | 3.1391 | 3.041 | 2.9078 | 2.7665 | 2.6199 | 2.4389 | 2.2508 | 1.9902 | 1.56 | 0.88205 | 0.44072 | 0.24988 | 4.8455 | 4.7789 | 4.71 | 4.6299 | 4.5441 | 4.4517 | 4.3319 | 4.2057 | 4.0324 | 3.7965 | 3.4376 | 3.186 | 2.9781 | 3.7587 | 3.6672 | 3.5738 | 3.4501 | 3.319 | 3.1819 | 3.0108 | 2.8327 | 2.5847 | 2.1929 | 1.5868 | 1.2122 | 1.0443
|  | SUTTON BENGER | FS |  |  | 3.2353 | 3.1391 | 3.041 | 2.9078 | 2.7665 | 2.6199 | 2.4389 | 2.2508 | 1.9902 | 1.56 | 0.88205 | 0.44072 | 0.24988 | 4.8455 | 4.7789 | 4.71 | 4.6299 | 4.5441 | 4.4517 | 4.3319 | 4.2057 | 4.0324 | 3.7965 | 3.4376 | 3.186 | 2.9781 | 3.7587 | 3.6672 | 3.5738 | 3.4501 | 3.319 | 3.1819 | 3.0108 | 2.8327 | 2.5847 | 2.1929 | 1.5868 | 1.2122 | 1.0443
IVER 132KV | UPTON BSP | SUTTON LANE | MINIMUM HEADROOM | TQ 02185 78595 | YES | 12.5334 | 12.3926 | 12.2394 | 12.0756 | 11.8914 | 11.6911 | 11.4731 | 11.1989 | 10.8749 | 8.9232 | 5.2387 | 2.5341 | 0.78074 | 14.8043 | 14.6376 | 14.4442 | 14.1905 | 13.9088 | 13.5947 | 13.2541 | 12.8493 | 12.3175 | 10.7961 | 8.0731 | 5.468 | 2.3065 | 14.3271 | 14.2129 | 14.0879 | 13.9574 | 13.8106 | 13.6501 | 13.4756 | 13.257 | 12.67 | 10.7456 | 7.4487 | 5.134 | 3.6958
|  | SUTTON LANE | CT |  |  | 12.5334 | 12.3926 | 12.2394 | 12.0756 | 11.8914 | 11.6911 | 11.4731 | 11.1989 | 10.8749 | 8.9232 | 5.2387 | 2.5341 | 0.78074 | 14.8043 | 14.6376 | 14.4442 | 14.1905 | 13.9088 | 13.5947 | 13.2541 | 12.8493 | 12.3175 | 10.7961 | 8.0731 | 5.468 | 2.3065 | 14.3271 | 14.2129 | 14.0879 | 13.9574 | 13.8106 | 13.6501 | 13.4756 | 13.257 | 12.67 | 10.7456 | 7.4487 | 5.134 | 3.6958
|  | SUTTON LANE | LW |  |  | 12.5334 | 12.3926 | 12.2394 | 12.0756 | 11.8914 | 11.6911 | 11.4731 | 11.1989 | 10.8749 | 8.9232 | 5.2387 | 2.5341 | 0.78074 | 14.8043 | 14.6376 | 14.4442 | 14.1905 | 13.9088 | 13.5947 | 13.2541 | 12.8493 | 12.3175 | 10.7961 | 8.0731 | 5.468 | 2.3065 | 14.3271 | 14.2129 | 14.0879 | 13.9574 | 13.8106 | 13.6501 | 13.4756 | 13.257 | 12.67 | 10.7456 | 7.4487 | 5.134 | 3.6958
|  | SUTTON LANE | ST |  |  | 12.5334 | 12.3926 | 12.2394 | 12.0756 | 11.8914 | 11.6911 | 11.4731 | 11.1989 | 10.8749 | 8.9232 | 5.2387 | 2.5341 | 0.78074 | 14.8043 | 14.6376 | 14.4442 | 14.1905 | 13.9088 | 13.5947 | 13.2541 | 12.8493 | 12.3175 | 10.7961 | 8.0731 | 5.468 | 2.3065 | 14.3271 | 14.2129 | 14.0879 | 13.9574 | 13.8106 | 13.6501 | 13.4756 | 13.257 | 12.67 | 10.7456 | 7.4487 | 5.134 | 3.6958
|  | SUTTON LANE | FS |  |  | 12.5334 | 12.3926 | 12.2394 | 12.0756 | 11.8914 | 11.6911 | 11.4731 | 11.1989 | 10.8749 | 8.9232 | 5.2387 | 2.5341 | 0.78074 | 14.8043 | 14.6376 | 14.4442 | 14.1905 | 13.9088 | 13.5947 | 13.2541 | 12.8493 | 12.3175 | 10.7961 | 8.0731 | 5.468 | 2.3065 | 14.3271 | 14.2129 | 14.0879 | 13.9574 | 13.8106 | 13.6501 | 13.4756 | 13.257 | 12.67 | 10.7456 | 7.4487 | 5.134 | 3.6958
MANNINGTON GSP | WAREHAM | SWANAGE | MINIMUM HEADROOM | SZ 02010 79296 | YES | 6.3602 | 6.1613 | 5.8271 | 5.3708 | 4.8921 | 4.3228 | 3.7094 | 3.0198 | 1.9084 | -1.2042 | -5.8714 | -9.1101 | -10.6533 | 9.5914 | 9.4488 | 9.195 | 8.9006 | 8.5876 | 8.2198 | 7.8186 | 7.3531 | 6.6655 | 4.7751 | 2.243 | 0.28855 | -1.4548 | 7.3695 | 7.1813 | 6.8581 | 6.4301 | 5.9801 | 5.4491 | 4.876 | 4.2274 | 3.1914 | 0.31272 | -3.867 | -6.8334 | -8.1873
|  | SWANAGE | CT |  |  | 6.3602 | 6.1613 | 5.8271 | 5.3708 | 4.8921 | 4.3228 | 3.7094 | 3.0198 | 1.9084 | -1.2042 | -5.8714 | -9.1101 | -10.6533 | 9.5914 | 9.4488 | 9.195 | 8.9006 | 8.5876 | 8.2198 | 7.8186 | 7.3531 | 6.6655 | 4.7751 | 2.243 | 0.28855 | -1.4548 | 7.3695 | 7.1813 | 6.8581 | 6.4301 | 5.9801 | 5.4491 | 4.876 | 4.2274 | 3.1914 | 0.31272 | -3.867 | -6.8334 | -8.1873
|  | SWANAGE | LW |  |  | 6.3602 | 6.1613 | 5.8271 | 5.3708 | 4.8921 | 4.3228 | 3.7094 | 3.0198 | 1.9084 | -1.2042 | -5.8714 | -9.1101 | -10.6533 | 9.5914 | 9.4488 | 9.195 | 8.9006 | 8.5876 | 8.2198 | 7.8186 | 7.3531 | 6.6655 | 4.7751 | 2.243 | 0.28855 | -1.4548 | 7.3695 | 7.1813 | 6.8581 | 6.4301 | 5.9801 | 5.4491 | 4.876 | 4.2274 | 3.1914 | 0.31272 | -3.867 | -6.8334 | -8.1873
|  | SWANAGE | ST |  |  | 6.3602 | 6.1613 | 5.8271 | 5.3708 | 4.8921 | 4.3228 | 3.7094 | 3.0198 | 1.9084 | -1.2042 | -5.8714 | -9.1101 | -10.6533 | 9.5914 | 9.4488 | 9.195 | 8.9006 | 8.5876 | 8.2198 | 7.8186 | 7.3531 | 6.6655 | 4.7751 | 2.243 | 0.28855 | -1.4548 | 7.3695 | 7.1813 | 6.8581 | 6.4301 | 5.9801 | 5.4491 | 4.876 | 4.2274 | 3.1914 | 0.31272 | -3.867 | -6.8334 | -8.1873
|  | SWANAGE | FS |  |  | 6.3602 | 6.1613 | 5.8271 | 5.3708 | 4.8921 | 4.3228 | 3.7094 | 3.0198 | 1.9084 | -1.2042 | -5.8714 | -9.1101 | -10.6533 | 9.5914 | 9.4488 | 9.195 | 8.9006 | 8.5876 | 8.2198 | 7.8186 | 7.3531 | 6.6655 | 4.7751 | 2.243 | 0.28855 | -1.4548 | 7.3695 | 7.1813 | 6.8581 | 6.4301 | 5.9801 | 5.4491 | 4.876 | 4.2274 | 3.1914 | 0.31272 | -3.867 | -6.8334 | -8.1873
MINETY GSP | SWINDON BSP | SWINDON | MINIMUM HEADROOM | SU 12449 86967 | YES | 45.3512 | 44.7136 | 43.723 | 42.4469 | 41.0757 | 39.6508 | 38.0761 | 36.1406 | 33.0324 | 25.3082 | 13.9823 | 6.263 | 2.2889 | 43.9773 | 43.4784 | 42.7626 | 41.9446 | 41.0572 | 40.1107 | 39.0231 | 37.5815 | 35.4635 | 30.3953 | 23.7209 | 18.8173 | 14.3825 | 48.7829 | 48.172 | 47.2986 | 46.1515 | 44.92 | 43.644 | 42.2358 | 40.5102 | 37.7147 | 30.695 | 20.2214 | 13.0949 | 9.6101
|  | SWINDON | CT |  |  | 45.3512 | 44.7136 | 43.723 | 42.4469 | 41.0757 | 39.6508 | 38.0761 | 36.1406 | 33.0324 | 25.3082 | 13.9823 | 6.263 | 2.2889 | 43.9773 | 43.4784 | 42.7626 | 41.9446 | 41.0572 | 40.1107 | 39.0231 | 37.5815 | 35.4635 | 30.3953 | 23.7209 | 18.8173 | 14.3825 | 48.7829 | 48.172 | 47.2986 | 46.1515 | 44.92 | 43.644 | 42.2358 | 40.5102 | 37.7147 | 30.695 | 20.2214 | 13.0949 | 9.6101
|  | SWINDON | LW |  |  | 45.3512 | 44.7136 | 43.723 | 42.4469 | 41.0757 | 39.6508 | 38.0761 | 36.1406 | 33.0324 | 25.3082 | 13.9823 | 6.263 | 2.2889 | 43.9773 | 43.4784 | 42.7626 | 41.9446 | 41.0572 | 40.1107 | 39.0231 | 37.5815 | 35.4635 | 30.3953 | 23.7209 | 18.8173 | 14.3825 | 48.7829 | 48.172 | 47.2986 | 46.1515 | 44.92 | 43.644 | 42.2358 | 40.5102 | 37.7147 | 30.695 | 20.2214 | 13.0949 | 9.6101
|  | SWINDON | ST |  |  | 45.3512 | 44.7136 | 43.723 | 42.4469 | 41.0757 | 39.6508 | 38.0761 | 36.1406 | 33.0324 | 25.3082 | 13.9823 | 6.263 | 2.2889 | 43.9773 | 43.4784 | 42.7626 | 41.9446 | 41.0572 | 40.1107 | 39.0231 | 37.5815 | 35.4635 | 30.3953 | 23.7209 | 18.8173 | 14.3825 | 48.7829 | 48.172 | 47.2986 | 46.1515 | 44.92 | 43.644 | 42.2358 | 40.5102 | 37.7147 | 30.695 | 20.2214 | 13.0949 | 9.6101
|  | SWINDON | FS |  |  | 45.3512 | 44.7136 | 43.723 | 42.4469 | 41.0757 | 39.6508 | 38.0761 | 36.1406 | 33.0324 | 25.3082 | 13.9823 | 6.263 | 2.2889 | 43.9773 | 43.4784 | 42.7626 | 41.9446 | 41.0572 | 40.1107 | 39.0231 | 37.5815 | 35.4635 | 30.3953 | 23.7209 | 18.8173 | 14.3825 | 48.7829 | 48.172 | 47.2986 | 46.1515 | 44.92 | 43.644 | 42.2358 | 40.5102 | 37.7147 | 30.695 | 20.2214 | 13.0949 | 9.6101
BRAMLEY (ANDO-THAT) | THATCHAM BSP | TADLEY | MINIMUM HEADROOM | SU 57753 62717 | YES | 13.91 | 13.6793 | 13.3839 | 12.9789 | 12.5504 | 12.1004 | 11.6028 | 11.0242 | 10.0669 | 7.8537 | 4.2872 | 2.023 | 1.0206 | 16.7111 | 16.5298 | 16.2876 | 16.0152 | 15.7226 | 15.4027 | 15.0414 | 14.6043 | 13.9393 | 12.5726 | 10.7384 | 9.5805 | 8.7361 | 14.6236 | 14.4033 | 14.1186 | 13.739 | 13.3365 | 12.9114 | 12.4398 | 11.8878 | 10.983 | 8.9314 | 5.7246 | 3.7324 | 2.8595
|  | TADLEY | CT |  |  | 13.91 | 13.6793 | 13.3839 | 12.9789 | 12.5504 | 12.1004 | 11.6028 | 11.0242 | 10.0669 | 7.8537 | 4.2872 | 2.023 | 1.0206 | 16.7111 | 16.5298 | 16.2876 | 16.0152 | 15.7226 | 15.4027 | 15.0414 | 14.6043 | 13.9393 | 12.5726 | 10.7384 | 9.5805 | 8.7361 | 14.6236 | 14.4033 | 14.1186 | 13.739 | 13.3365 | 12.9114 | 12.4398 | 11.8878 | 10.983 | 8.9314 | 5.7246 | 3.7324 | 2.8595
|  | TADLEY | LW |  |  | 13.91 | 13.6793 | 13.3839 | 12.9789 | 12.5504 | 12.1004 | 11.6028 | 11.0242 | 10.0669 | 7.8537 | 4.2872 | 2.023 | 1.0206 | 16.7111 | 16.5298 | 16.2876 | 16.0152 | 15.7226 | 15.4027 | 15.0414 | 14.6043 | 13.9393 | 12.5726 | 10.7384 | 9.5805 | 8.7361 | 14.6236 | 14.4033 | 14.1186 | 13.739 | 13.3365 | 12.9114 | 12.4398 | 11.8878 | 10.983 | 8.9314 | 5.7246 | 3.7324 | 2.8595
|  | TADLEY | ST |  |  | 13.91 | 13.6793 | 13.3839 | 12.9789 | 12.5504 | 12.1004 | 11.6028 | 11.0242 | 10.0669 | 7.8537 | 4.2872 | 2.023 | 1.0206 | 16.7111 | 16.5298 | 16.2876 | 16.0152 | 15.7226 | 15.4027 | 15.0414 | 14.6043 | 13.9393 | 12.5726 | 10.7384 | 9.5805 | 8.7361 | 14.6236 | 14.4033 | 14.1186 | 13.739 | 13.3365 | 12.9114 | 12.4398 | 11.8878 | 10.983 | 8.9314 | 5.7246 | 3.7324 | 2.8595
|  | TADLEY | FS |  |  | 13.91 | 13.6793 | 13.3839 | 12.9789 | 12.5504 | 12.1004 | 11.6028 | 11.0242 | 10.0669 | 7.8537 | 4.2872 | 2.023 | 1.0206 | 16.7111 | 16.5298 | 16.2876 | 16.0152 | 15.7226 | 15.4027 | 15.0414 | 14.6043 | 13.9393 | 12.5726 | 10.7384 | 9.5805 | 8.7361 | 14.6236 | 14.4033 | 14.1186 | 13.739 | 13.3365 | 12.9114 | 12.4398 | 11.8878 | 10.983 | 8.9314 | 5.7246 | 3.7324 | 2.8595
IVER 132KV | SLOUGH | TAPLOW | MINIMUM HEADROOM | SU 91721 81234 | YES | 23.1969 | 22.828 | 22.3588 | 21.7603 | 21.1143 | 20.4331 | 19.6664 | 18.7349 | 17.3605 | 13.6831 | 7.5038 | 3.4028 | 0.94998 | 23.2032 | 22.9466 | 22.6184 | 22.219 | 21.7788 | 21.3006 | 20.7549 | 20.0854 | 19.1637 | 16.7932 | 13.164 | 10.8021 | 8.8394 | 24.8746 | 24.5251 | 24.0766 | 23.515 | 22.9073 | 22.2624 | 21.5339 | 20.6485 | 19.3498 | 15.9272 | 10.3868 | 6.8594 | 4.8031
|  | TAPLOW | CT |  |  | 23.1969 | 22.828 | 22.3588 | 21.7603 | 21.1143 | 20.4331 | 19.6664 | 18.7349 | 17.3605 | 13.6831 | 7.5038 | 3.4028 | 0.94998 | 23.2032 | 22.9466 | 22.6184 | 22.219 | 21.7788 | 21.3006 | 20.7549 | 20.0854 | 19.1637 | 16.7932 | 13.164 | 10.8021 | 8.8394 | 24.8746 | 24.5251 | 24.0766 | 23.515 | 22.9073 | 22.2624 | 21.5339 | 20.6485 | 19.3498 | 15.9272 | 10.3868 | 6.8594 | 4.8031
|  | TAPLOW | LW |  |  | 23.1969 | 22.828 | 22.3588 | 21.7603 | 21.1143 | 20.4331 | 19.6664 | 18.7349 | 17.3605 | 13.6831 | 7.5038 | 3.4028 | 0.94998 | 23.2032 | 22.9466 | 22.6184 | 22.219 | 21.7788 | 21.3006 | 20.7549 | 20.0854 | 19.1637 | 16.7932 | 13.164 | 10.8021 | 8.8394 | 24.8746 | 24.5251 | 24.0766 | 23.515 | 22.9073 | 22.2624 | 21.5339 | 20.6485 | 19.3498 | 15.9272 | 10.3868 | 6.8594 | 4.8031
|  | TAPLOW | ST |  |  | 23.1969 | 22.828 | 22.3588 | 21.7603 | 21.1143 | 20.4331 | 19.6664 | 18.7349 | 17.3605 | 13.6831 | 7.5038 | 3.4028 | 0.94998 | 23.2032 | 22.9466 | 22.6184 | 22.219 | 21.7788 | 21.3006 | 20.7549 | 20.0854 | 19.1637 | 16.7932 | 13.164 | 10.8021 | 8.8394 | 24.8746 | 24.5251 | 24.0766 | 23.515 | 22.9073 | 22.2624 | 21.5339 | 20.6485 | 19.3498 | 15.9272 | 10.3868 | 6.8594 | 4.8031
|  | TAPLOW | FS |  |  | 23.1969 | 22.828 | 22.3588 | 21.7603 | 21.1143 | 20.4331 | 19.6664 | 18.7349 | 17.3605 | 13.6831 | 7.5038 | 3.4028 | 0.94998 | 23.2032 | 22.9466 | 22.6184 | 22.219 | 21.7788 | 21.3006 | 20.7549 | 20.0854 | 19.1637 | 16.7932 | 13.164 | 10.8021 | 8.8394 | 24.8746 | 24.5251 | 24.0766 | 23.515 | 22.9073 | 22.2624 | 21.5339 | 20.6485 | 19.3498 | 15.9272 | 10.3868 | 6.8594 | 4.8031
MANNINGTON GSP | SHAFTESBURY BSP | TARRANT RUSHTON | MINIMUM HEADROOM | ST 94510 07307 | YES | 3.9984 | 3.9623 | 3.9164 | 3.8431 | 3.7657 | 3.5989 | 3.4136 | 3.2109 | 2.956 | 2.0636 | 0.57341 | 0.04404 | -0.19118 | 5.0277 | 5.0022 | 4.9655 | 4.9193 | 4.8691 | 4.768 | 4.654 | 4.5268 | 4.3703 | 3.8651 | 3.0661 | 2.7758 | 2.555 | 4.4256 | 4.3952 | 4.3477 | 4.2878 | 4.2235 | 4.0914 | 3.9414 | 3.772 | 3.5621 | 2.8146 | 1.4821 | 1.0312 | 0.83196
|  | TARRANT RUSHTON | CT |  |  | 3.9984 | 3.9623 | 3.9164 | 3.8431 | 3.7657 | 3.5989 | 3.4136 | 3.2109 | 2.956 | 2.0636 | 0.57341 | 0.04404 | -0.19118 | 5.0277 | 5.0022 | 4.9655 | 4.9193 | 4.8691 | 4.768 | 4.654 | 4.5268 | 4.3703 | 3.8651 | 3.0661 | 2.7758 | 2.555 | 4.4256 | 4.3952 | 4.3477 | 4.2878 | 4.2235 | 4.0914 | 3.9414 | 3.772 | 3.5621 | 2.8146 | 1.4821 | 1.0312 | 0.83196
|  | TARRANT RUSHTON | LW |  |  | 3.9984 | 3.9623 | 3.9164 | 3.8431 | 3.7657 | 3.5989 | 3.4136 | 3.2109 | 2.956 | 2.0636 | 0.57341 | 0.04404 | -0.19118 | 5.0277 | 5.0022 | 4.9655 | 4.9193 | 4.8691 | 4.768 | 4.654 | 4.5268 | 4.3703 | 3.8651 | 3.0661 | 2.7758 | 2.555 | 4.4256 | 4.3952 | 4.3477 | 4.2878 | 4.2235 | 4.0914 | 3.9414 | 3.772 | 3.5621 | 2.8146 | 1.4821 | 1.0312 | 0.83196
|  | TARRANT RUSHTON | ST |  |  | 3.9984 | 3.9623 | 3.9164 | 3.8431 | 3.7657 | 3.5989 | 3.4136 | 3.2109 | 2.956 | 2.0636 | 0.57341 | 0.04404 | -0.19118 | 5.0277 | 5.0022 | 4.9655 | 4.9193 | 4.8691 | 4.768 | 4.654 | 4.5268 | 4.3703 | 3.8651 | 3.0661 | 2.7758 | 2.555 | 4.4256 | 4.3952 | 4.3477 | 4.2878 | 4.2235 | 4.0914 | 3.9414 | 3.772 | 3.5621 | 2.8146 | 1.4821 | 1.0312 | 0.83196
|  | TARRANT RUSHTON | FS |  |  | 3.9984 | 3.9623 | 3.9164 | 3.8431 | 3.7657 | 3.5989 | 3.4136 | 3.2109 | 2.956 | 2.0636 | 0.57341 | 0.04404 | -0.19118 | 5.0277 | 5.0022 | 4.9655 | 4.9193 | 4.8691 | 4.768 | 4.654 | 4.5268 | 4.3703 | 3.8651 | 3.0661 | 2.7758 | 2.555 | 4.4256 | 4.3952 | 4.3477 | 4.2878 | 4.2235 | 4.0914 | 3.9414 | 3.772 | 3.5621 | 2.8146 | 1.4821 | 1.0312 | 0.83196
MANNINGTON GSP | SALISBURY | TEFFONT | MINIMUM HEADROOM | ST 99837 30994 | YES | 3.155 | 3.047 | 2.9115 | 2.6959 | 2.4718 | 2.2316 | 1.9736 | 1.6716 | 1.2681 | 0.59494 | 0.40101 | 0.30923 | 0.26063 | 2.8789 | 2.815 | 2.729 | 2.6236 | 2.5117 | 2.3915 | 2.2577 | 2.0811 | 1.8636 | 1.5446 | 1.4049 | 1.3173 | 1.225 | 4.0625 | 3.9629 | 3.8528 | 3.673 | 3.4871 | 3.2879 | 3.0761 | 2.8397 | 2.506 | 1.8967 | 1.716 | 1.6324 | 1.5883
|  | TEFFONT | CT |  |  | 3.155 | 3.047 | 2.9115 | 2.6959 | 2.4718 | 2.2316 | 1.9736 | 1.6716 | 1.2681 | 0.59494 | 0.40101 | 0.30923 | 0.26063 | 2.8789 | 2.815 | 2.729 | 2.6236 | 2.5117 | 2.3915 | 2.2577 | 2.0811 | 1.8636 | 1.5446 | 1.4049 | 1.3173 | 1.225 | 4.0625 | 3.9629 | 3.8528 | 3.673 | 3.4871 | 3.2879 | 3.0761 | 2.8397 | 2.506 | 1.8967 | 1.716 | 1.6324 | 1.5883
|  | TEFFONT | LW |  |  | 3.155 | 3.047 | 2.9115 | 2.6959 | 2.4718 | 2.2316 | 1.9736 | 1.6716 | 1.2681 | 0.59494 | 0.40101 | 0.30923 | 0.26063 | 2.8789 | 2.815 | 2.729 | 2.6236 | 2.5117 | 2.3915 | 2.2577 | 2.0811 | 1.8636 | 1.5446 | 1.4049 | 1.3173 | 1.225 | 4.0625 | 3.9629 | 3.8528 | 3.673 | 3.4871 | 3.2879 | 3.0761 | 2.8397 | 2.506 | 1.8967 | 1.716 | 1.6324 | 1.5883
|  | TEFFONT | ST |  |  | 3.155 | 3.047 | 2.9115 | 2.6959 | 2.4718 | 2.2316 | 1.9736 | 1.6716 | 1.2681 | 0.59494 | 0.40101 | 0.30923 | 0.26063 | 2.8789 | 2.815 | 2.729 | 2.6236 | 2.5117 | 2.3915 | 2.2577 | 2.0811 | 1.8636 | 1.5446 | 1.4049 | 1.3173 | 1.225 | 4.0625 | 3.9629 | 3.8528 | 3.673 | 3.4871 | 3.2879 | 3.0761 | 2.8397 | 2.506 | 1.8967 | 1.716 | 1.6324 | 1.5883
|  | TEFFONT | FS |  |  | 3.155 | 3.047 | 2.9115 | 2.6959 | 2.4718 | 2.2316 | 1.9736 | 1.6716 | 1.2681 | 0.59494 | 0.40101 | 0.30923 | 0.26063 | 2.8789 | 2.815 | 2.729 | 2.6236 | 2.5117 | 2.3915 | 2.2577 | 2.0811 | 1.8636 | 1.5446 | 1.4049 | 1.3173 | 1.225 | 4.0625 | 3.9629 | 3.8528 | 3.673 | 3.4871 | 3.2879 | 3.0761 | 2.8397 | 2.506 | 1.8967 | 1.716 | 1.6324 | 1.5883
BRAMLEY (FLEE) | MAIDENHEAD BSP | TEMPLE FARM | MINIMUM HEADROOM | SU 84178 83872 | YES | 2.4052 | 2.3875 | 2.3665 | 2.3442 | 2.3189 | 2.2914 | 2.2313 | 2.1624 | 2.0669 | 1.9113 | 1.6596 | 1.5167 | 1.4414 | 2.1549 | 2.1322 | 2.1081 | 2.08 | 2.0498 | 2.0169 | 1.9707 | 1.9255 | 1.8642 | 1.7676 | 1.6046 | 1.5021 | 1.4164 | 2.4842 | 2.4617 | 2.4359 | 2.4027 | 2.3663 | 2.328 | 2.2845 | 2.2419 | 2.1838 | 2.0155 | 1.7304 | 1.6215 | 1.5724
|  | TEMPLE FARM | CT |  |  | 2.4052 | 2.3875 | 2.3665 | 2.3442 | 2.3189 | 2.2914 | 2.2313 | 2.1624 | 2.0669 | 1.9113 | 1.6596 | 1.5167 | 1.4414 | 2.1549 | 2.1322 | 2.1081 | 2.08 | 2.0498 | 2.0169 | 1.9707 | 1.9255 | 1.8642 | 1.7676 | 1.6046 | 1.5021 | 1.4164 | 2.4842 | 2.4617 | 2.4359 | 2.4027 | 2.3663 | 2.328 | 2.2845 | 2.2419 | 2.1838 | 2.0155 | 1.7304 | 1.6215 | 1.5724
|  | TEMPLE FARM | LW |  |  | 2.4052 | 2.3875 | 2.3665 | 2.3442 | 2.3189 | 2.2914 | 2.2313 | 2.1624 | 2.0669 | 1.9113 | 1.6596 | 1.5167 | 1.4414 | 2.1549 | 2.1322 | 2.1081 | 2.08 | 2.0498 | 2.0169 | 1.9707 | 1.9255 | 1.8642 | 1.7676 | 1.6046 | 1.5021 | 1.4164 | 2.4842 | 2.4617 | 2.4359 | 2.4027 | 2.3663 | 2.328 | 2.2845 | 2.2419 | 2.1838 | 2.0155 | 1.7304 | 1.6215 | 1.5724
|  | TEMPLE FARM | ST |  |  | 2.4052 | 2.3875 | 2.3665 | 2.3442 | 2.3189 | 2.2914 | 2.2313 | 2.1624 | 2.0669 | 1.9113 | 1.6596 | 1.5167 | 1.4414 | 2.1549 | 2.1322 | 2.1081 | 2.08 | 2.0498 | 2.0169 | 1.9707 | 1.9255 | 1.8642 | 1.7676 | 1.6046 | 1.5021 | 1.4164 | 2.4842 | 2.4617 | 2.4359 | 2.4027 | 2.3663 | 2.328 | 2.2845 | 2.2419 | 2.1838 | 2.0155 | 1.7304 | 1.6215 | 1.5724
|  | TEMPLE FARM | FS |  |  | 2.4052 | 2.3875 | 2.3665 | 2.3442 | 2.3189 | 2.2914 | 2.2313 | 2.1624 | 2.0669 | 1.9113 | 1.6596 | 1.5167 | 1.4414 | 2.1549 | 2.1322 | 2.1081 | 2.08 | 2.0498 | 2.0169 | 1.9707 | 1.9255 | 1.8642 | 1.7676 | 1.6046 | 1.5021 | 1.4164 | 2.4842 | 2.4617 | 2.4359 | 2.4027 | 2.3663 | 2.328 | 2.2845 | 2.2419 | 2.1838 | 2.0155 | 1.7304 | 1.6215 | 1.5724
MELKSHAM GSP | CHIPPENHAM | TETBURY | MINIMUM HEADROOM | ST 89708 93444 | YES | 2.9343 | 2.7766 | 2.5808 | 2.3059 | 2.0158 | 1.7025 | 1.3613 | 0.97881 | 0.34749 | -1.1775 | -3.6994 | -5.6558 | -6.541 | 4.9101 | 4.8001 | 4.6583 | 4.4911 | 4.3117 | 4.1129 | 3.8928 | 3.638 | 3.2451 | 2.364 | 1.1275 | 0.18901 | -0.48866 | 3.6233 | 3.4734 | 3.2855 | 3.0292 | 2.758 | 2.4639 | 2.1427 | 1.7805 | 1.1872 | -0.22193 | -2.4307 | -4.0267 | -4.7241
|  | TETBURY | CT |  |  | 2.9343 | 2.7766 | 2.5808 | 2.3059 | 2.0158 | 1.7025 | 1.3613 | 0.97881 | 0.34749 | -1.1775 | -3.6994 | -5.6558 | -6.541 | 4.9101 | 4.8001 | 4.6583 | 4.4911 | 4.3117 | 4.1129 | 3.8928 | 3.638 | 3.2451 | 2.364 | 1.1275 | 0.18901 | -0.48866 | 3.6233 | 3.4734 | 3.2855 | 3.0292 | 2.758 | 2.4639 | 2.1427 | 1.7805 | 1.1872 | -0.22193 | -2.4307 | -4.0267 | -4.7241
|  | TETBURY | LW |  |  | 2.9343 | 2.7766 | 2.5808 | 2.3059 | 2.0158 | 1.7025 | 1.3613 | 0.97881 | 0.34749 | -1.1775 | -3.6994 | -5.6558 | -6.541 | 4.9101 | 4.8001 | 4.6583 | 4.4911 | 4.3117 | 4.1129 | 3.8928 | 3.638 | 3.2451 | 2.364 | 1.1275 | 0.18901 | -0.48866 | 3.6233 | 3.4734 | 3.2855 | 3.0292 | 2.758 | 2.4639 | 2.1427 | 1.7805 | 1.1872 | -0.22193 | -2.4307 | -4.0267 | -4.7241
|  | TETBURY | ST |  |  | 2.9343 | 2.7766 | 2.5808 | 2.3059 | 2.0158 | 1.7025 | 1.3613 | 0.97881 | 0.34749 | -1.1775 | -3.6994 | -5.6558 | -6.541 | 4.9101 | 4.8001 | 4.6583 | 4.4911 | 4.3117 | 4.1129 | 3.8928 | 3.638 | 3.2451 | 2.364 | 1.1275 | 0.18901 | -0.48866 | 3.6233 | 3.4734 | 3.2855 | 3.0292 | 2.758 | 2.4639 | 2.1427 | 1.7805 | 1.1872 | -0.22193 | -2.4307 | -4.0267 | -4.7241
|  | TETBURY | FS |  |  | 2.9343 | 2.7766 | 2.5808 | 2.3059 | 2.0158 | 1.7025 | 1.3613 | 0.97881 | 0.34749 | -1.1775 | -3.6994 | -5.6558 | -6.541 | 4.9101 | 4.8001 | 4.6583 | 4.4911 | 4.3117 | 4.1129 | 3.8928 | 3.638 | 3.2451 | 2.364 | 1.1275 | 0.18901 | -0.48866 | 3.6233 | 3.4734 | 3.2855 | 3.0292 | 2.758 | 2.4639 | 2.1427 | 1.7805 | 1.1872 | -0.22193 | -2.4307 | -4.0267 | -4.7241
BRAMLEY (ANDO-THAT) | THATCHAM BSP | THATCHAM | MINIMUM HEADROOM | SU 52758 66466 | YES | 13.9173 | 13.0682 | 12.2711 | 11.1944 | 10.0637 | 8.9791 | 7.7717 | 6.4262 | 4.125 | -0.98278 | -8.8782 | -14.0367 | -16.2565 | 15.3096 | 14.661 | 14.0519 | 13.3557 | 12.6149 | 11.8696 | 11.0235 | 10.0591 | 8.5257 | 5.3336 | 0.8704 | -2.2278 | -4.7484 | 16.1637 | 15.3506 | 14.5871 | 13.5809 | 12.5216 | 11.4949 | 10.3464 | 9.0599 | 6.875 | 2.1087 | -5.0478 | -9.6126 | -11.5624
|  | THATCHAM | CT |  |  | 13.9173 | 13.0682 | 12.2711 | 11.1944 | 10.0637 | 8.9791 | 7.7717 | 6.4262 | 4.125 | -0.98278 | -8.8782 | -14.0367 | -16.2565 | 15.3096 | 14.661 | 14.0519 | 13.3557 | 12.6149 | 11.8696 | 11.0235 | 10.0591 | 8.5257 | 5.3336 | 0.8704 | -2.2278 | -4.7484 | 16.1637 | 15.3506 | 14.5871 | 13.5809 | 12.5216 | 11.4949 | 10.3464 | 9.0599 | 6.875 | 2.1087 | -5.0478 | -9.6126 | -11.5624
|  | THATCHAM | LW |  |  | 13.9173 | 13.0682 | 12.2711 | 11.1944 | 10.0637 | 8.9791 | 7.7717 | 6.4262 | 4.125 | -0.98278 | -8.8782 | -14.0367 | -16.2565 | 15.3096 | 14.661 | 14.0519 | 13.3557 | 12.6149 | 11.8696 | 11.0235 | 10.0591 | 8.5257 | 5.3336 | 0.8704 | -2.2278 | -4.7484 | 16.1637 | 15.3506 | 14.5871 | 13.5809 | 12.5216 | 11.4949 | 10.3464 | 9.0599 | 6.875 | 2.1087 | -5.0478 | -9.6126 | -11.5624
|  | THATCHAM | ST |  |  | 13.9173 | 13.0682 | 12.2711 | 11.1944 | 10.0637 | 8.9791 | 7.7717 | 6.4262 | 4.125 | -0.98278 | -8.8782 | -14.0367 | -16.2565 | 15.3096 | 14.661 | 14.0519 | 13.3557 | 12.6149 | 11.8696 | 11.0235 | 10.0591 | 8.5257 | 5.3336 | 0.8704 | -2.2278 | -4.7484 | 16.1637 | 15.3506 | 14.5871 | 13.5809 | 12.5216 | 11.4949 | 10.3464 | 9.0599 | 6.875 | 2.1087 | -5.0478 | -9.6126 | -11.5624
|  | THATCHAM | FS |  |  | 13.9173 | 13.0682 | 12.2711 | 11.1944 | 10.0637 | 8.9791 | 7.7717 | 6.4262 | 4.125 | -0.98278 | -8.8782 | -14.0367 | -16.2565 | 15.3096 | 14.661 | 14.0519 | 13.3557 | 12.6149 | 11.8696 | 11.0235 | 10.0591 | 8.5257 | 5.3336 | 0.8704 | -2.2278 | -4.7484 | 16.1637 | 15.3506 | 14.5871 | 13.5809 | 12.5216 | 11.4949 | 10.3464 | 9.0599 | 6.875 | 2.1087 | -5.0478 | -9.6126 | -11.5624
NORTH HYDE GSP | NORTH HYDE 22kV | THE GREEN | MINIMUM HEADROOM | TQ 12414 79503 | YES | 2.8225 | 2.5815 | 2.286 | 1.9133 | 1.4992 | 1.066 | 0.67297 | 0.33404 | -0.13595 | -1.5735 | -4.66 | -7.3494 | -9.115 | 5.4939 | 5.3947 | 5.2775 | 5.0681 | 4.8131 | 4.5443 | 4.2901 | 4.0451 | 3.7401 | 2.7608 | 0.69609 | -1.4683 | -4.0043 | 3.6566 | 3.4349 | 3.1457 | 2.7973 | 2.4109 | 2.0048 | 1.6274 | 1.289 | 0.83884 | -0.52682 | -3.2143 | -5.4647 | -6.932
|  | THE GREEN | CT |  |  | 2.8225 | 2.5815 | 2.286 | 1.9133 | 1.4992 | 1.066 | 0.67297 | 0.33404 | -0.13595 | -1.5735 | -4.66 | -7.3494 | -9.115 | 5.4939 | 5.3947 | 5.2775 | 5.0681 | 4.8131 | 4.5443 | 4.2901 | 4.0451 | 3.7401 | 2.7608 | 0.69609 | -1.4683 | -4.0043 | 3.6566 | 3.4349 | 3.1457 | 2.7973 | 2.4109 | 2.0048 | 1.6274 | 1.289 | 0.83884 | -0.52682 | -3.2143 | -5.4647 | -6.932
|  | THE GREEN | LW |  |  | 2.8225 | 2.5815 | 2.286 | 1.9133 | 1.4992 | 1.066 | 0.67297 | 0.33404 | -0.13595 | -1.5735 | -4.66 | -7.3494 | -9.115 | 5.4939 | 5.3947 | 5.2775 | 5.0681 | 4.8131 | 4.5443 | 4.2901 | 4.0451 | 3.7401 | 2.7608 | 0.69609 | -1.4683 | -4.0043 | 3.6566 | 3.4349 | 3.1457 | 2.7973 | 2.4109 | 2.0048 | 1.6274 | 1.289 | 0.83884 | -0.52682 | -3.2143 | -5.4647 | -6.932
|  | THE GREEN | ST |  |  | 2.8225 | 2.5815 | 2.286 | 1.9133 | 1.4992 | 1.066 | 0.67297 | 0.33404 | -0.13595 | -1.5735 | -4.66 | -7.3494 | -9.115 | 5.4939 | 5.3947 | 5.2775 | 5.0681 | 4.8131 | 4.5443 | 4.2901 | 4.0451 | 3.7401 | 2.7608 | 0.69609 | -1.4683 | -4.0043 | 3.6566 | 3.4349 | 3.1457 | 2.7973 | 2.4109 | 2.0048 | 1.6274 | 1.289 | 0.83884 | -0.52682 | -3.2143 | -5.4647 | -6.932
|  | THE GREEN | FS |  |  | 2.8225 | 2.5815 | 2.286 | 1.9133 | 1.4992 | 1.066 | 0.67297 | 0.33404 | -0.13595 | -1.5735 | -4.66 | -7.3494 | -9.115 | 5.4939 | 5.3947 | 5.2775 | 5.0681 | 4.8131 | 4.5443 | 4.2901 | 4.0451 | 3.7401 | 2.7608 | 0.69609 | -1.4683 | -4.0043 | 3.6566 | 3.4349 | 3.1457 | 2.7973 | 2.4109 | 2.0048 | 1.6274 | 1.289 | 0.83884 | -0.52682 | -3.2143 | -5.4647 | -6.932
BRAMLEY (FLEE) | READING TOWN BSP | THE MALL | MINIMUM HEADROOM | SU 71319 73293 | YES | 10.2888 | 9.994 | 9.6277 | 9.1051 | 8.5326 | 7.9543 | 7.3557 | 6.6859 | 5.7835 | 2.8048 | -2.0908 | -5.7023 | -8.0041 | 13.0742 | 12.9207 | 12.7468 | 12.5269 | 12.2689 | 11.9473 | 11.6113 | 11.2295 | 10.7288 | 9.0029 | 6.0243 | 3.6034 | 1.1702 | 11.5586 | 11.3379 | 11.0174 | 10.5631 | 10.056 | 9.5221 | 8.9886 | 8.3885 | 7.5788 | 4.9208 | 0.62258 | -2.4341 | -4.3349
|  | THE MALL | CT |  |  | 10.2888 | 9.994 | 9.6277 | 9.1051 | 8.5326 | 7.9543 | 7.3557 | 6.6859 | 5.7835 | 2.8048 | -2.0908 | -5.7023 | -8.0041 | 13.0742 | 12.9207 | 12.7468 | 12.5269 | 12.2689 | 11.9473 | 11.6113 | 11.2295 | 10.7288 | 9.0029 | 6.0243 | 3.6034 | 1.1702 | 11.5586 | 11.3379 | 11.0174 | 10.5631 | 10.056 | 9.5221 | 8.9886 | 8.3885 | 7.5788 | 4.9208 | 0.62258 | -2.4341 | -4.3349
|  | THE MALL | LW |  |  | 10.2888 | 9.994 | 9.6277 | 9.1051 | 8.5326 | 7.9543 | 7.3557 | 6.6859 | 5.7835 | 2.8048 | -2.0908 | -5.7023 | -8.0041 | 13.0742 | 12.9207 | 12.7468 | 12.5269 | 12.2689 | 11.9473 | 11.6113 | 11.2295 | 10.7288 | 9.0029 | 6.0243 | 3.6034 | 1.1702 | 11.5586 | 11.3379 | 11.0174 | 10.5631 | 10.056 | 9.5221 | 8.9886 | 8.3885 | 7.5788 | 4.9208 | 0.62258 | -2.4341 | -4.3349
|  | THE MALL | ST |  |  | 10.2888 | 9.994 | 9.6277 | 9.1051 | 8.5326 | 7.9543 | 7.3557 | 6.6859 | 5.7835 | 2.8048 | -2.0908 | -5.7023 | -8.0041 | 13.0742 | 12.9207 | 12.7468 | 12.5269 | 12.2689 | 11.9473 | 11.6113 | 11.2295 | 10.7288 | 9.0029 | 6.0243 | 3.6034 | 1.1702 | 11.5586 | 11.3379 | 11.0174 | 10.5631 | 10.056 | 9.5221 | 8.9886 | 8.3885 | 7.5788 | 4.9208 | 0.62258 | -2.4341 | -4.3349
|  | THE MALL | FS |  |  | 10.2888 | 9.994 | 9.6277 | 9.1051 | 8.5326 | 7.9543 | 7.3557 | 6.6859 | 5.7835 | 2.8048 | -2.0908 | -5.7023 | -8.0041 | 13.0742 | 12.9207 | 12.7468 | 12.5269 | 12.2689 | 11.9473 | 11.6113 | 11.2295 | 10.7288 | 9.0029 | 6.0243 | 3.6034 | 1.1702 | 11.5586 | 11.3379 | 11.0174 | 10.5631 | 10.056 | 9.5221 | 8.9886 | 8.3885 | 7.5788 | 4.9208 | 0.62258 | -2.4341 | -4.3349
BRAMLEY (FLEE) | BURGHFIELD RESERVE | THEALE | MINIMUM HEADROOM | SU 64755 71015 | YES | 22.5892 | 22.3763 | 22.1128 | 21.8694 | 21.6311 | 21.4215 | 21.1873 | 20.9423 | 20.5958 | 19.5246 | 17.6436 | 16.7112 | 16.3537 | 23.9477 | 23.824 | 23.6745 | 23.5486 | 23.4092 | 23.2975 | 23.1725 | 23.0356 | 22.845 | 22.2866 | 21.0833 | 20.4965 | 19.8805 | 22.8182 | 22.6439 | 22.4311 | 22.24 | 22.0505 | 21.8769 | 21.682 | 21.476 | 21.1942 | 20.3182 | 18.4659 | 17.5861 | 17.259
|  | THEALE | CT |  |  | 22.5892 | 22.3763 | 22.1128 | 21.8694 | 21.6311 | 21.4215 | 21.1873 | 20.9423 | 20.5958 | 19.5246 | 17.6436 | 16.7112 | 16.3537 | 23.9477 | 23.824 | 23.6745 | 23.5486 | 23.4092 | 23.2975 | 23.1725 | 23.0356 | 22.845 | 22.2866 | 21.0833 | 20.4965 | 19.8805 | 22.8182 | 22.6439 | 22.4311 | 22.24 | 22.0505 | 21.8769 | 21.682 | 21.476 | 21.1942 | 20.3182 | 18.4659 | 17.5861 | 17.259
|  | THEALE | LW |  |  | 22.5892 | 22.3763 | 22.1128 | 21.8694 | 21.6311 | 21.4215 | 21.1873 | 20.9423 | 20.5958 | 19.5246 | 17.6436 | 16.7112 | 16.3537 | 23.9477 | 23.824 | 23.6745 | 23.5486 | 23.4092 | 23.2975 | 23.1725 | 23.0356 | 22.845 | 22.2866 | 21.0833 | 20.4965 | 19.8805 | 22.8182 | 22.6439 | 22.4311 | 22.24 | 22.0505 | 21.8769 | 21.682 | 21.476 | 21.1942 | 20.3182 | 18.4659 | 17.5861 | 17.259
|  | THEALE | ST |  |  | 22.5892 | 22.3763 | 22.1128 | 21.8694 | 21.6311 | 21.4215 | 21.1873 | 20.9423 | 20.5958 | 19.5246 | 17.6436 | 16.7112 | 16.3537 | 23.9477 | 23.824 | 23.6745 | 23.5486 | 23.4092 | 23.2975 | 23.1725 | 23.0356 | 22.845 | 22.2866 | 21.0833 | 20.4965 | 19.8805 | 22.8182 | 22.6439 | 22.4311 | 22.24 | 22.0505 | 21.8769 | 21.682 | 21.476 | 21.1942 | 20.3182 | 18.4659 | 17.5861 | 17.259
|  | THEALE | FS |  |  | 22.5892 | 22.3763 | 22.1128 | 21.8694 | 21.6311 | 21.4215 | 21.1873 | 20.9423 | 20.5958 | 19.5246 | 17.6436 | 16.7112 | 16.3537 | 23.9477 | 23.824 | 23.6745 | 23.5486 | 23.4092 | 23.2975 | 23.1725 | 23.0356 | 22.845 | 22.2866 | 21.0833 | 20.4965 | 19.8805 | 22.8182 | 22.6439 | 22.4311 | 22.24 | 22.0505 | 21.8769 | 21.682 | 21.476 | 21.1942 | 20.3182 | 18.4659 | 17.5861 | 17.259
BRAMLEY (ANDO-THAT) | ANDOVER BSP | THRUXTON | MINIMUM HEADROOM | SU 29134 45674 | YES | 2.5573 | 2.417 | 2.2584 | 2.0534 | 1.8407 | 1.6115 | 1.344 | 1.0327 | 0.641 | -0.11934 | -1.4259 | -2.237 | -2.4322 | 3.4969 | 3.3987 | 3.2858 | 3.1584 | 3.0254 | 2.8809 | 2.7066 | 2.4966 | 2.2407 | 1.8402 | 1.2102 | 0.82686 | 0.62361 | 2.7715 | 2.638 | 2.4894 | 2.2894 | 2.0826 | 1.8601 | 1.6047 | 1.3117 | 0.94174 | 0.21763 | -1.0223 | -1.744 | -1.9161
|  | THRUXTON | CT |  |  | 2.5573 | 2.417 | 2.2584 | 2.0534 | 1.8407 | 1.6115 | 1.344 | 1.0327 | 0.641 | -0.11934 | -1.4259 | -2.237 | -2.4322 | 3.4969 | 3.3987 | 3.2858 | 3.1584 | 3.0254 | 2.8809 | 2.7066 | 2.4966 | 2.2407 | 1.8402 | 1.2102 | 0.82686 | 0.62361 | 2.7715 | 2.638 | 2.4894 | 2.2894 | 2.0826 | 1.8601 | 1.6047 | 1.3117 | 0.94174 | 0.21763 | -1.0223 | -1.744 | -1.9161
|  | THRUXTON | LW |  |  | 2.5573 | 2.417 | 2.2584 | 2.0534 | 1.8407 | 1.6115 | 1.344 | 1.0327 | 0.641 | -0.11934 | -1.4259 | -2.237 | -2.4322 | 3.4969 | 3.3987 | 3.2858 | 3.1584 | 3.0254 | 2.8809 | 2.7066 | 2.4966 | 2.2407 | 1.8402 | 1.2102 | 0.82686 | 0.62361 | 2.7715 | 2.638 | 2.4894 | 2.2894 | 2.0826 | 1.8601 | 1.6047 | 1.3117 | 0.94174 | 0.21763 | -1.0223 | -1.744 | -1.9161
|  | THRUXTON | ST |  |  | 2.5573 | 2.417 | 2.2584 | 2.0534 | 1.8407 | 1.6115 | 1.344 | 1.0327 | 0.641 | -0.11934 | -1.4259 | -2.237 | -2.4322 | 3.4969 | 3.3987 | 3.2858 | 3.1584 | 3.0254 | 2.8809 | 2.7066 | 2.4966 | 2.2407 | 1.8402 | 1.2102 | 0.82686 | 0.62361 | 2.7715 | 2.638 | 2.4894 | 2.2894 | 2.0826 | 1.8601 | 1.6047 | 1.3117 | 0.94174 | 0.21763 | -1.0223 | -1.744 | -1.9161
|  | THRUXTON | FS |  |  | 2.5573 | 2.417 | 2.2584 | 2.0534 | 1.8407 | 1.6115 | 1.344 | 1.0327 | 0.641 | -0.11934 | -1.4259 | -2.237 | -2.4322 | 3.4969 | 3.3987 | 3.2858 | 3.1584 | 3.0254 | 2.8809 | 2.7066 | 2.4966 | 2.2407 | 1.8402 | 1.2102 | 0.82686 | 0.62361 | 2.7715 | 2.638 | 2.4894 | 2.2894 | 2.0826 | 1.8601 | 1.6047 | 1.3117 | 0.94174 | 0.21763 | -1.0223 | -1.744 | -1.9161
MELKSHAM GSP | WEST GRAFTON | TIDWORTH | MINIMUM HEADROOM | SU 24088 49593 | YES | 7.5678 | 7.1724 | 6.6665 | 6.1435 | 5.634 | 5.1133 | 4.5542 | 3.935 | 3 | 0.38032 | -3.4179 | -5.9355 | -6.8457 | 9.8961 | 9.6663 | 9.3612 | 9.0666 | 8.7746 | 8.4658 | 8.1312 | 7.7518 | 7.2054 | 5.6841 | 3.6167 | 2.1634 | 1.0165 | 8.6257 | 8.2895 | 7.8555 | 7.3831 | 6.9198 | 6.4488 | 5.9437 | 5.3864 | 4.5382 | 2.149 | -1.3862 | -3.6011 | -4.3962
|  | TIDWORTH | CT |  |  | 7.5678 | 7.1724 | 6.6665 | 6.1435 | 5.634 | 5.1133 | 4.5542 | 3.935 | 3 | 0.38032 | -3.4179 | -5.9355 | -6.8457 | 9.8961 | 9.6663 | 9.3612 | 9.0666 | 8.7746 | 8.4658 | 8.1312 | 7.7518 | 7.2054 | 5.6841 | 3.6167 | 2.1634 | 1.0165 | 8.6257 | 8.2895 | 7.8555 | 7.3831 | 6.9198 | 6.4488 | 5.9437 | 5.3864 | 4.5382 | 2.149 | -1.3862 | -3.6011 | -4.3962
|  | TIDWORTH | LW |  |  | 7.5678 | 7.1724 | 6.6665 | 6.1435 | 5.634 | 5.1133 | 4.5542 | 3.935 | 3 | 0.38032 | -3.4179 | -5.9355 | -6.8457 | 9.8961 | 9.6663 | 9.3612 | 9.0666 | 8.7746 | 8.4658 | 8.1312 | 7.7518 | 7.2054 | 5.6841 | 3.6167 | 2.1634 | 1.0165 | 8.6257 | 8.2895 | 7.8555 | 7.3831 | 6.9198 | 6.4488 | 5.9437 | 5.3864 | 4.5382 | 2.149 | -1.3862 | -3.6011 | -4.3962
|  | TIDWORTH | ST |  |  | 7.5678 | 7.1724 | 6.6665 | 6.1435 | 5.634 | 5.1133 | 4.5542 | 3.935 | 3 | 0.38032 | -3.4179 | -5.9355 | -6.8457 | 9.8961 | 9.6663 | 9.3612 | 9.0666 | 8.7746 | 8.4658 | 8.1312 | 7.7518 | 7.2054 | 5.6841 | 3.6167 | 2.1634 | 1.0165 | 8.6257 | 8.2895 | 7.8555 | 7.3831 | 6.9198 | 6.4488 | 5.9437 | 5.3864 | 4.5382 | 2.149 | -1.3862 | -3.6011 | -4.3962
|  | TIDWORTH | FS |  |  | 7.5678 | 7.1724 | 6.6665 | 6.1435 | 5.634 | 5.1133 | 4.5542 | 3.935 | 3 | 0.38032 | -3.4179 | -5.9355 | -6.8457 | 9.8961 | 9.6663 | 9.3612 | 9.0666 | 8.7746 | 8.4658 | 8.1312 | 7.7518 | 7.2054 | 5.6841 | 3.6167 | 2.1634 | 1.0165 | 8.6257 | 8.2895 | 7.8555 | 7.3831 | 6.9198 | 6.4488 | 5.9437 | 5.3864 | 4.5382 | 2.149 | -1.3862 | -3.6011 | -4.3962
MANNINGTON GSP | SHAFTESBURY BSP | TISBURY | MINIMUM HEADROOM | ST 93438 29127 | YES | 4.5265 | 4.3635 | 4.1608 | 3.8623 | 3.5482 | 3.2188 | 2.8588 | 2.4492 | 1.8546 | 0.79577 | 0.41084 | 0.22916 | 0.16833 | 6.9395 | 6.8497 | 6.7271 | 6.5734 | 6.4083 | 6.2339 | 6.0456 | 5.8252 | 5.508 | 4.951 | 4.7122 | 4.5808 | 4.4565 | 5.478 | 5.318 | 5.1199 | 4.8267 | 4.5186 | 4.1953 | 3.8538 | 3.4756 | 2.9262 | 1.9517 | 1.5984 | 1.4379 | 1.3851
|  | TISBURY | CT |  |  | 4.5265 | 4.3635 | 4.1608 | 3.8623 | 3.5482 | 3.2188 | 2.8588 | 2.4492 | 1.8546 | 0.79577 | 0.41084 | 0.22916 | 0.16833 | 6.9395 | 6.8497 | 6.7271 | 6.5734 | 6.4083 | 6.2339 | 6.0456 | 5.8252 | 5.508 | 4.951 | 4.7122 | 4.5808 | 4.4565 | 5.478 | 5.318 | 5.1199 | 4.8267 | 4.5186 | 4.1953 | 3.8538 | 3.4756 | 2.9262 | 1.9517 | 1.5984 | 1.4379 | 1.3851
|  | TISBURY | LW |  |  | 4.5265 | 4.3635 | 4.1608 | 3.8623 | 3.5482 | 3.2188 | 2.8588 | 2.4492 | 1.8546 | 0.79577 | 0.41084 | 0.22916 | 0.16833 | 6.9395 | 6.8497 | 6.7271 | 6.5734 | 6.4083 | 6.2339 | 6.0456 | 5.8252 | 5.508 | 4.951 | 4.7122 | 4.5808 | 4.4565 | 5.478 | 5.318 | 5.1199 | 4.8267 | 4.5186 | 4.1953 | 3.8538 | 3.4756 | 2.9262 | 1.9517 | 1.5984 | 1.4379 | 1.3851
|  | TISBURY | ST |  |  | 4.5265 | 4.3635 | 4.1608 | 3.8623 | 3.5482 | 3.2188 | 2.8588 | 2.4492 | 1.8546 | 0.79577 | 0.41084 | 0.22916 | 0.16833 | 6.9395 | 6.8497 | 6.7271 | 6.5734 | 6.4083 | 6.2339 | 6.0456 | 5.8252 | 5.508 | 4.951 | 4.7122 | 4.5808 | 4.4565 | 5.478 | 5.318 | 5.1199 | 4.8267 | 4.5186 | 4.1953 | 3.8538 | 3.4756 | 2.9262 | 1.9517 | 1.5984 | 1.4379 | 1.3851
|  | TISBURY | FS |  |  | 4.5265 | 4.3635 | 4.1608 | 3.8623 | 3.5482 | 3.2188 | 2.8588 | 2.4492 | 1.8546 | 0.79577 | 0.41084 | 0.22916 | 0.16833 | 6.9395 | 6.8497 | 6.7271 | 6.5734 | 6.4083 | 6.2339 | 6.0456 | 5.8252 | 5.508 | 4.951 | 4.7122 | 4.5808 | 4.4565 | 5.478 | 5.318 | 5.1199 | 4.8267 | 4.5186 | 4.1953 | 3.8538 | 3.4756 | 2.9262 | 1.9517 | 1.5984 | 1.4379 | 1.3851
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | TITCHFIELD | MINIMUM HEADROOM | SU 54104 05695 | YES | 8.1971 | 7.468 | 6.6304 | 5.6911 | 4.6895 | 3.6674 | 2.5081 | 1.1574 | -0.58887 | -5.2578 | -10.1177 | -12.7321 | -13.9177 | 10.8675 | 10.4184 | 9.9017 | 9.3571 | 8.7756 | 8.1519 | 7.4389 | 6.6081 | 5.5511 | 2.9237 | 0.25528 | -1.2722 | -2.5497 | 9.3773 | 8.7392 | 7.9941 | 7.1697 | 6.2878 | 5.3795 | 4.3472 | 3.1546 | 1.592 | -2.4665 | -6.6829 | -8.8556 | -9.832
|  | TITCHFIELD | CT |  |  | 8.1971 | 7.468 | 6.6304 | 5.6911 | 4.6895 | 3.6674 | 2.5081 | 1.1574 | -0.58887 | -5.2578 | -10.1177 | -12.7321 | -13.9177 | 10.8675 | 10.4184 | 9.9017 | 9.3571 | 8.7756 | 8.1519 | 7.4389 | 6.6081 | 5.5511 | 2.9237 | 0.25528 | -1.2722 | -2.5497 | 9.3773 | 8.7392 | 7.9941 | 7.1697 | 6.2878 | 5.3795 | 4.3472 | 3.1546 | 1.592 | -2.4665 | -6.6829 | -8.8556 | -9.832
|  | TITCHFIELD | LW |  |  | 8.1971 | 7.468 | 6.6304 | 5.6911 | 4.6895 | 3.6674 | 2.5081 | 1.1574 | -0.58887 | -5.2578 | -10.1177 | -12.7321 | -13.9177 | 10.8675 | 10.4184 | 9.9017 | 9.3571 | 8.7756 | 8.1519 | 7.4389 | 6.6081 | 5.5511 | 2.9237 | 0.25528 | -1.2722 | -2.5497 | 9.3773 | 8.7392 | 7.9941 | 7.1697 | 6.2878 | 5.3795 | 4.3472 | 3.1546 | 1.592 | -2.4665 | -6.6829 | -8.8556 | -9.832
|  | TITCHFIELD | ST |  |  | 8.1971 | 7.468 | 6.6304 | 5.6911 | 4.6895 | 3.6674 | 2.5081 | 1.1574 | -0.58887 | -5.2578 | -10.1177 | -12.7321 | -13.9177 | 10.8675 | 10.4184 | 9.9017 | 9.3571 | 8.7756 | 8.1519 | 7.4389 | 6.6081 | 5.5511 | 2.9237 | 0.25528 | -1.2722 | -2.5497 | 9.3773 | 8.7392 | 7.9941 | 7.1697 | 6.2878 | 5.3795 | 4.3472 | 3.1546 | 1.592 | -2.4665 | -6.6829 | -8.8556 | -9.832
|  | TITCHFIELD | FS |  |  | 8.1971 | 7.468 | 6.6304 | 5.6911 | 4.6895 | 3.6674 | 2.5081 | 1.1574 | -0.58887 | -5.2578 | -10.1177 | -12.7321 | -13.9177 | 10.8675 | 10.4184 | 9.9017 | 9.3571 | 8.7756 | 8.1519 | 7.4389 | 6.6081 | 5.5511 | 2.9237 | 0.25528 | -1.2722 | -2.5497 | 9.3773 | 8.7392 | 7.9941 | 7.1697 | 6.2878 | 5.3795 | 4.3472 | 3.1546 | 1.592 | -2.4665 | -6.6829 | -8.8556 | -9.832
BRAMLEY (FLEE) | ALDERSHOT BSP | TONGHAM | MINIMUM HEADROOM | SU 88310 49487 | YES | 24.0995 | 23.5512 | 22.8588 | 22.0099 | 21.1286 | 20.198 | 19.2339 | 18.1219 | 16.4445 | 12.2282 | 5.0884 | -0.28091 | -3.4723 | 27.4501 | 27.0662 | 26.572 | 26.0258 | 25.4499 | 24.8312 | 24.1722 | 23.3859 | 22.282 | 19.6352 | 15.6043 | 12.5639 | 10.0974 | 24.7666 | 24.2671 | 23.6248 | 22.8473 | 22.0344 | 21.1705 | 20.2644 | 19.2077 | 17.6245 | 13.7033 | 7.2976 | 2.6345 | 0.011794
|  | TONGHAM | CT |  |  | 24.0995 | 23.5512 | 22.8588 | 22.0099 | 21.1286 | 20.198 | 19.2339 | 18.1219 | 16.4445 | 12.2282 | 5.0884 | -0.28091 | -3.4723 | 27.4501 | 27.0662 | 26.572 | 26.0258 | 25.4499 | 24.8312 | 24.1722 | 23.3859 | 22.282 | 19.6352 | 15.6043 | 12.5639 | 10.0974 | 24.7666 | 24.2671 | 23.6248 | 22.8473 | 22.0344 | 21.1705 | 20.2644 | 19.2077 | 17.6245 | 13.7033 | 7.2976 | 2.6345 | 0.011794
|  | TONGHAM | LW |  |  | 24.0995 | 23.5512 | 22.8588 | 22.0099 | 21.1286 | 20.198 | 19.2339 | 18.1219 | 16.4445 | 12.2282 | 5.0884 | -0.28091 | -3.4723 | 27.4501 | 27.0662 | 26.572 | 26.0258 | 25.4499 | 24.8312 | 24.1722 | 23.3859 | 22.282 | 19.6352 | 15.6043 | 12.5639 | 10.0974 | 24.7666 | 24.2671 | 23.6248 | 22.8473 | 22.0344 | 21.1705 | 20.2644 | 19.2077 | 17.6245 | 13.7033 | 7.2976 | 2.6345 | 0.011794
|  | TONGHAM | ST |  |  | 24.0995 | 23.5512 | 22.8588 | 22.0099 | 21.1286 | 20.198 | 19.2339 | 18.1219 | 16.4445 | 12.2282 | 5.0884 | -0.28091 | -3.4723 | 27.4501 | 27.0662 | 26.572 | 26.0258 | 25.4499 | 24.8312 | 24.1722 | 23.3859 | 22.282 | 19.6352 | 15.6043 | 12.5639 | 10.0974 | 24.7666 | 24.2671 | 23.6248 | 22.8473 | 22.0344 | 21.1705 | 20.2644 | 19.2077 | 17.6245 | 13.7033 | 7.2976 | 2.6345 | 0.011794
|  | TONGHAM | FS |  |  | 24.0995 | 23.5512 | 22.8588 | 22.0099 | 21.1286 | 20.198 | 19.2339 | 18.1219 | 16.4445 | 12.2282 | 5.0884 | -0.28091 | -3.4723 | 27.4501 | 27.0662 | 26.572 | 26.0258 | 25.4499 | 24.8312 | 24.1722 | 23.3859 | 22.282 | 19.6352 | 15.6043 | 12.5639 | 10.0974 | 24.7666 | 24.2671 | 23.6248 | 22.8473 | 22.0344 | 21.1705 | 20.2644 | 19.2077 | 17.6245 | 13.7033 | 7.2976 | 2.6345 | 0.011794
MINETY GSP | TOOTHILL BSP | TOOTHILL | MINIMUM HEADROOM | SU 13215 83986 | YES | 23.9773 | 23.5546 | 23.009 | 22.344 | 21.6203 | 20.8719 | 20.0532 | 19.0946 | 17.9263 | 14.6202 | 9.4366 | 6.0504 | 4.0356 | 23.2169 | 22.9399 | 22.5715 | 22.1577 | 21.7054 | 21.2276 | 20.7041 | 20.0777 | 19.326 | 17.1776 | 14.0888 | 12.1406 | 10.5636 | 25.4754 | 25.1039 | 24.6127 | 24.0172 | 23.3678 | 22.6919 | 21.9519 | 21.0784 | 19.9944 | 16.9139 | 12.2285 | 9.3098 | 7.6626
|  | TOOTHILL | CT |  |  | 23.9773 | 23.5546 | 23.009 | 22.344 | 21.6203 | 20.8719 | 20.0532 | 19.0946 | 17.9263 | 14.6202 | 9.4366 | 6.0504 | 4.0356 | 23.2169 | 22.9399 | 22.5715 | 22.1577 | 21.7054 | 21.2276 | 20.7041 | 20.0777 | 19.326 | 17.1776 | 14.0888 | 12.1406 | 10.5636 | 25.4754 | 25.1039 | 24.6127 | 24.0172 | 23.3678 | 22.6919 | 21.9519 | 21.0784 | 19.9944 | 16.9139 | 12.2285 | 9.3098 | 7.6626
|  | TOOTHILL | LW |  |  | 23.9773 | 23.5546 | 23.009 | 22.344 | 21.6203 | 20.8719 | 20.0532 | 19.0946 | 17.9263 | 14.6202 | 9.4366 | 6.0504 | 4.0356 | 23.2169 | 22.9399 | 22.5715 | 22.1577 | 21.7054 | 21.2276 | 20.7041 | 20.0777 | 19.326 | 17.1776 | 14.0888 | 12.1406 | 10.5636 | 25.4754 | 25.1039 | 24.6127 | 24.0172 | 23.3678 | 22.6919 | 21.9519 | 21.0784 | 19.9944 | 16.9139 | 12.2285 | 9.3098 | 7.6626
|  | TOOTHILL | ST |  |  | 23.9773 | 23.5546 | 23.009 | 22.344 | 21.6203 | 20.8719 | 20.0532 | 19.0946 | 17.9263 | 14.6202 | 9.4366 | 6.0504 | 4.0356 | 23.2169 | 22.9399 | 22.5715 | 22.1577 | 21.7054 | 21.2276 | 20.7041 | 20.0777 | 19.326 | 17.1776 | 14.0888 | 12.1406 | 10.5636 | 25.4754 | 25.1039 | 24.6127 | 24.0172 | 23.3678 | 22.6919 | 21.9519 | 21.0784 | 19.9944 | 16.9139 | 12.2285 | 9.3098 | 7.6626
|  | TOOTHILL | FS |  |  | 23.9773 | 23.5546 | 23.009 | 22.344 | 21.6203 | 20.8719 | 20.0532 | 19.0946 | 17.9263 | 14.6202 | 9.4366 | 6.0504 | 4.0356 | 23.2169 | 22.9399 | 22.5715 | 22.1577 | 21.7054 | 21.2276 | 20.7041 | 20.0777 | 19.326 | 17.1776 | 14.0888 | 12.1406 | 10.5636 | 25.4754 | 25.1039 | 24.6127 | 24.0172 | 23.3678 | 22.6919 | 21.9519 | 21.0784 | 19.9944 | 16.9139 | 12.2285 | 9.3098 | 7.6626
NURSLING GSP | ROWNHAMS | TOTTON | MINIMUM HEADROOM | SU 35835 13428 | YES | 10.9937 | 10.8318 | 10.6122 | 10.4264 | 10.0967 | 9.6865 | 9.0074 | 8.2087 | 6.8484 | 2.4596 | -3.4498 | -6.8803 | -8.6001 | 13.9074 | 13.6961 | 13.3661 | 13.0359 | 12.6616 | 12.2381 | 11.7786 | 11.25 | 10.396 | 7.7268 | 4.4809 | 2.5236 | 0.94975 | 11.5281 | 11.2857 | 10.9189 | 10.4869 | 9.9975 | 9.4412 | 8.8411 | 8.1651 | 6.9742 | 2.8404 | -2.3159 | -5.3556 | -6.8886
|  | TOTTON | CT |  |  | 10.9937 | 10.8318 | 10.6122 | 10.4264 | 10.0967 | 9.6865 | 9.0074 | 8.2087 | 6.8484 | 2.4596 | -3.4498 | -6.8803 | -8.6001 | 13.9074 | 13.6961 | 13.3661 | 13.0359 | 12.6616 | 12.2381 | 11.7786 | 11.25 | 10.396 | 7.7268 | 4.4809 | 2.5236 | 0.94975 | 11.5281 | 11.2857 | 10.9189 | 10.4869 | 9.9975 | 9.4412 | 8.8411 | 8.1651 | 6.9742 | 2.8404 | -2.3159 | -5.3556 | -6.8886
|  | TOTTON | LW |  |  | 10.9937 | 10.8318 | 10.6122 | 10.4264 | 10.0967 | 9.6865 | 9.0074 | 8.2087 | 6.8484 | 2.4596 | -3.4498 | -6.8803 | -8.6001 | 13.9074 | 13.6961 | 13.3661 | 13.0359 | 12.6616 | 12.2381 | 11.7786 | 11.25 | 10.396 | 7.7268 | 4.4809 | 2.5236 | 0.94975 | 11.5281 | 11.2857 | 10.9189 | 10.4869 | 9.9975 | 9.4412 | 8.8411 | 8.1651 | 6.9742 | 2.8404 | -2.3159 | -5.3556 | -6.8886
|  | TOTTON | ST |  |  | 10.9937 | 10.8318 | 10.6122 | 10.4264 | 10.0967 | 9.6865 | 9.0074 | 8.2087 | 6.8484 | 2.4596 | -3.4498 | -6.8803 | -8.6001 | 13.9074 | 13.6961 | 13.3661 | 13.0359 | 12.6616 | 12.2381 | 11.7786 | 11.25 | 10.396 | 7.7268 | 4.4809 | 2.5236 | 0.94975 | 11.5281 | 11.2857 | 10.9189 | 10.4869 | 9.9975 | 9.4412 | 8.8411 | 8.1651 | 6.9742 | 2.8404 | -2.3159 | -5.3556 | -6.8886
|  | TOTTON | FS |  |  | 10.9937 | 10.8318 | 10.6122 | 10.4264 | 10.0967 | 9.6865 | 9.0074 | 8.2087 | 6.8484 | 2.4596 | -3.4498 | -6.8803 | -8.6001 | 13.9074 | 13.6961 | 13.3661 | 13.0359 | 12.6616 | 12.2381 | 11.7786 | 11.25 | 10.396 | 7.7268 | 4.4809 | 2.5236 | 0.94975 | 11.5281 | 11.2857 | 10.9189 | 10.4869 | 9.9975 | 9.4412 | 8.8411 | 8.1651 | 6.9742 | 2.8404 | -2.3159 | -5.3556 | -6.8886
BOTLEY WOOD GSP | NETLEY COMMON BSP | TOWNHILL PARK | MINIMUM HEADROOM | SU 45156 14783 | YES | 17.8276 | 17.2781 | 16.4905 | 15.5895 | 14.6696 | 13.6857 | 12.6182 | 11.3794 | 9.4574 | 3.6429 | -5.2181 | -11.7656 | -15.6145 | 18.526 | 18.1428 | 17.5879 | 17.0069 | 16.4102 | 15.7645 | 15.0587 | 14.2234 | 12.9357 | 9.2767 | 4.7094 | 0.87831 | -3.1772 | 18.8609 | 18.3407 | 17.5832 | 16.7311 | 15.8577 | 14.9192 | 13.8989 | 12.708 | 10.8779 | 5.7677 | -1.0754 | -5.9841 | -9.1831
|  | TOWNHILL PARK | CT |  |  | 17.8276 | 17.2781 | 16.4905 | 15.5895 | 14.6696 | 13.6857 | 12.6182 | 11.3794 | 9.4574 | 3.6429 | -5.2181 | -11.7656 | -15.6145 | 18.526 | 18.1428 | 17.5879 | 17.0069 | 16.4102 | 15.7645 | 15.0587 | 14.2234 | 12.9357 | 9.2767 | 4.7094 | 0.87831 | -3.1772 | 18.8609 | 18.3407 | 17.5832 | 16.7311 | 15.8577 | 14.9192 | 13.8989 | 12.708 | 10.8779 | 5.7677 | -1.0754 | -5.9841 | -9.1831
|  | TOWNHILL PARK | LW |  |  | 17.8276 | 17.2781 | 16.4905 | 15.5895 | 14.6696 | 13.6857 | 12.6182 | 11.3794 | 9.4574 | 3.6429 | -5.2181 | -11.7656 | -15.6145 | 18.526 | 18.1428 | 17.5879 | 17.0069 | 16.4102 | 15.7645 | 15.0587 | 14.2234 | 12.9357 | 9.2767 | 4.7094 | 0.87831 | -3.1772 | 18.8609 | 18.3407 | 17.5832 | 16.7311 | 15.8577 | 14.9192 | 13.8989 | 12.708 | 10.8779 | 5.7677 | -1.0754 | -5.9841 | -9.1831
|  | TOWNHILL PARK | ST |  |  | 17.8276 | 17.2781 | 16.4905 | 15.5895 | 14.6696 | 13.6857 | 12.6182 | 11.3794 | 9.4574 | 3.6429 | -5.2181 | -11.7656 | -15.6145 | 18.526 | 18.1428 | 17.5879 | 17.0069 | 16.4102 | 15.7645 | 15.0587 | 14.2234 | 12.9357 | 9.2767 | 4.7094 | 0.87831 | -3.1772 | 18.8609 | 18.3407 | 17.5832 | 16.7311 | 15.8577 | 14.9192 | 13.8989 | 12.708 | 10.8779 | 5.7677 | -1.0754 | -5.9841 | -9.1831
|  | TOWNHILL PARK | FS |  |  | 17.8276 | 17.2781 | 16.4905 | 15.5895 | 14.6696 | 13.6857 | 12.6182 | 11.3794 | 9.4574 | 3.6429 | -5.2181 | -11.7656 | -15.6145 | 18.526 | 18.1428 | 17.5879 | 17.0069 | 16.4102 | 15.7645 | 15.0587 | 14.2234 | 12.9357 | 9.2767 | 4.7094 | 0.87831 | -3.1772 | 18.8609 | 18.3407 | 17.5832 | 16.7311 | 15.8577 | 14.9192 | 13.8989 | 12.708 | 10.8779 | 5.7677 | -1.0754 | -5.9841 | -9.1831
MINETY GSP | SWINDON BSP | TRADING ESTATE | MINIMUM HEADROOM | SU 13490 85868 | YES | 11.7392 | 11.5921 | 11.4084 | 11.2057 | 10.9741 | 10.7119 | 10.421 | 10.0188 | 9.5702 | 7.8058 | 3.4649 | 1.8114 | 0.85537 | 14.7674 | 14.6584 | 14.5213 | 14.3703 | 14.1976 | 14.0018 | 13.7844 | 13.4844 | 13.1533 | 11.9209 | 9.4833 | 8.2753 | 7.576 | 12.6784 | 12.5441 | 12.3757 | 12.1525 | 11.8753 | 11.4821 | 11.0462 | 10.4508 | 9.7788 | 7.3062 | 3.1388 | 1.5728 | 0.68174
|  | TRADING ESTATE | CT |  |  | 11.7392 | 11.5921 | 11.4084 | 11.2057 | 10.9741 | 10.7119 | 10.421 | 10.0188 | 9.5702 | 7.8058 | 3.4649 | 1.8114 | 0.85537 | 14.7674 | 14.6584 | 14.5213 | 14.3703 | 14.1976 | 14.0018 | 13.7844 | 13.4844 | 13.1533 | 11.9209 | 9.4833 | 8.2753 | 7.576 | 12.6784 | 12.5441 | 12.3757 | 12.1525 | 11.8753 | 11.4821 | 11.0462 | 10.4508 | 9.7788 | 7.3062 | 3.1388 | 1.5728 | 0.68174
|  | TRADING ESTATE | LW |  |  | 11.7392 | 11.5921 | 11.4084 | 11.2057 | 10.9741 | 10.7119 | 10.421 | 10.0188 | 9.5702 | 7.8058 | 3.4649 | 1.8114 | 0.85537 | 14.7674 | 14.6584 | 14.5213 | 14.3703 | 14.1976 | 14.0018 | 13.7844 | 13.4844 | 13.1533 | 11.9209 | 9.4833 | 8.2753 | 7.576 | 12.6784 | 12.5441 | 12.3757 | 12.1525 | 11.8753 | 11.4821 | 11.0462 | 10.4508 | 9.7788 | 7.3062 | 3.1388 | 1.5728 | 0.68174
|  | TRADING ESTATE | ST |  |  | 11.7392 | 11.5921 | 11.4084 | 11.2057 | 10.9741 | 10.7119 | 10.421 | 10.0188 | 9.5702 | 7.8058 | 3.4649 | 1.8114 | 0.85537 | 14.7674 | 14.6584 | 14.5213 | 14.3703 | 14.1976 | 14.0018 | 13.7844 | 13.4844 | 13.1533 | 11.9209 | 9.4833 | 8.2753 | 7.576 | 12.6784 | 12.5441 | 12.3757 | 12.1525 | 11.8753 | 11.4821 | 11.0462 | 10.4508 | 9.7788 | 7.3062 | 3.1388 | 1.5728 | 0.68174
|  | TRADING ESTATE | FS |  |  | 11.7392 | 11.5921 | 11.4084 | 11.2057 | 10.9741 | 10.7119 | 10.421 | 10.0188 | 9.5702 | 7.8058 | 3.4649 | 1.8114 | 0.85537 | 14.7674 | 14.6584 | 14.5213 | 14.3703 | 14.1976 | 14.0018 | 13.7844 | 13.4844 | 13.1533 | 11.9209 | 9.4833 | 8.2753 | 7.576 | 12.6784 | 12.5441 | 12.3757 | 12.1525 | 11.8753 | 11.4821 | 11.0462 | 10.4508 | 9.7788 | 7.3062 | 3.1388 | 1.5728 | 0.68174
BRAMLEY (FLEE) | BURGHFIELD RESERVE | TRASH GREEN | MINIMUM HEADROOM | SU 66254 68745 | YES | 9.333 | 8.9214 | 8.4882 | 7.8405 | 7.2427 | 6.8248 | 6.3519 | 5.8037 | 4.9576 | 3.2042 | 0.14652 | -1.8987 | -2.4489 | 10.483 | 10.2199 | 9.9451 | 9.5791 | 9.2351 | 8.9752 | 8.6695 | 8.3031 | 7.7742 | 6.8078 | 5.3259 | 4.3494 | 3.7755 | 10.6696 | 10.3085 | 9.9249 | 9.3618 | 8.8344 | 8.4484 | 8.0065 | 7.4907 | 6.6988 | 5.1 | 2.4264 | 0.74836 | 0.30004
|  | TRASH GREEN | CT |  |  | 9.333 | 8.9214 | 8.4882 | 7.8405 | 7.2427 | 6.8248 | 6.3519 | 5.8037 | 4.9576 | 3.2042 | 0.14652 | -1.8987 | -2.4489 | 10.483 | 10.2199 | 9.9451 | 9.5791 | 9.2351 | 8.9752 | 8.6695 | 8.3031 | 7.7742 | 6.8078 | 5.3259 | 4.3494 | 3.7755 | 10.6696 | 10.3085 | 9.9249 | 9.3618 | 8.8344 | 8.4484 | 8.0065 | 7.4907 | 6.6988 | 5.1 | 2.4264 | 0.74836 | 0.30004
|  | TRASH GREEN | LW |  |  | 9.333 | 8.9214 | 8.4882 | 7.8405 | 7.2427 | 6.8248 | 6.3519 | 5.8037 | 4.9576 | 3.2042 | 0.14652 | -1.8987 | -2.4489 | 10.483 | 10.2199 | 9.9451 | 9.5791 | 9.2351 | 8.9752 | 8.6695 | 8.3031 | 7.7742 | 6.8078 | 5.3259 | 4.3494 | 3.7755 | 10.6696 | 10.3085 | 9.9249 | 9.3618 | 8.8344 | 8.4484 | 8.0065 | 7.4907 | 6.6988 | 5.1 | 2.4264 | 0.74836 | 0.30004
|  | TRASH GREEN | ST |  |  | 9.333 | 8.9214 | 8.4882 | 7.8405 | 7.2427 | 6.8248 | 6.3519 | 5.8037 | 4.9576 | 3.2042 | 0.14652 | -1.8987 | -2.4489 | 10.483 | 10.2199 | 9.9451 | 9.5791 | 9.2351 | 8.9752 | 8.6695 | 8.3031 | 7.7742 | 6.8078 | 5.3259 | 4.3494 | 3.7755 | 10.6696 | 10.3085 | 9.9249 | 9.3618 | 8.8344 | 8.4484 | 8.0065 | 7.4907 | 6.6988 | 5.1 | 2.4264 | 0.74836 | 0.30004
|  | TRASH GREEN | FS |  |  | 9.333 | 8.9214 | 8.4882 | 7.8405 | 7.2427 | 6.8248 | 6.3519 | 5.8037 | 4.9576 | 3.2042 | 0.14652 | -1.8987 | -2.4489 | 10.483 | 10.2199 | 9.9451 | 9.5791 | 9.2351 | 8.9752 | 8.6695 | 8.3031 | 7.7742 | 6.8078 | 5.3259 | 4.3494 | 3.7755 | 10.6696 | 10.3085 | 9.9249 | 9.3618 | 8.8344 | 8.4484 | 8.0065 | 7.4907 | 6.6988 | 5.1 | 2.4264 | 0.74836 | 0.30004
MELKSHAM GSP | NORRINGTON | TROWBRIDGE TOWN | MINIMUM HEADROOM | ST 84668 58036 | YES | 11.5782 | 11.3396 | 10.9956 | 10.4785 | 9.93 | 9.3427 | 8.7092 | 7.993 | 6.7951 | 3.4203 | -2.1397 | -5.9367 | -7.6737 | 17.4974 | 17.3347 | 17.0654 | 16.7545 | 16.4173 | 16.0495 | 15.6442 | 15.1645 | 14.4518 | 12.5766 | 9.6336 | 7.4779 | 5.5362 | 14.2636 | 14.1445 | 13.9851 | 13.5535 | 13.0263 | 12.4522 | 11.8295 | 11.1153 | 9.9543 | 6.753 | 1.8475 | -1.3633 | -2.8521
|  | TROWBRIDGE TOWN | CT |  |  | 11.5782 | 11.3396 | 10.9956 | 10.4785 | 9.93 | 9.3427 | 8.7092 | 7.993 | 6.7951 | 3.4203 | -2.1397 | -5.9367 | -7.6737 | 17.4974 | 17.3347 | 17.0654 | 16.7545 | 16.4173 | 16.0495 | 15.6442 | 15.1645 | 14.4518 | 12.5766 | 9.6336 | 7.4779 | 5.5362 | 14.2636 | 14.1445 | 13.9851 | 13.5535 | 13.0263 | 12.4522 | 11.8295 | 11.1153 | 9.9543 | 6.753 | 1.8475 | -1.3633 | -2.8521
|  | TROWBRIDGE TOWN | LW |  |  | 11.5782 | 11.3396 | 10.9956 | 10.4785 | 9.93 | 9.3427 | 8.7092 | 7.993 | 6.7951 | 3.4203 | -2.1397 | -5.9367 | -7.6737 | 17.4974 | 17.3347 | 17.0654 | 16.7545 | 16.4173 | 16.0495 | 15.6442 | 15.1645 | 14.4518 | 12.5766 | 9.6336 | 7.4779 | 5.5362 | 14.2636 | 14.1445 | 13.9851 | 13.5535 | 13.0263 | 12.4522 | 11.8295 | 11.1153 | 9.9543 | 6.753 | 1.8475 | -1.3633 | -2.8521
|  | TROWBRIDGE TOWN | ST |  |  | 11.5782 | 11.3396 | 10.9956 | 10.4785 | 9.93 | 9.3427 | 8.7092 | 7.993 | 6.7951 | 3.4203 | -2.1397 | -5.9367 | -7.6737 | 17.4974 | 17.3347 | 17.0654 | 16.7545 | 16.4173 | 16.0495 | 15.6442 | 15.1645 | 14.4518 | 12.5766 | 9.6336 | 7.4779 | 5.5362 | 14.2636 | 14.1445 | 13.9851 | 13.5535 | 13.0263 | 12.4522 | 11.8295 | 11.1153 | 9.9543 | 6.753 | 1.8475 | -1.3633 | -2.8521
|  | TROWBRIDGE TOWN | FS |  |  | 11.5782 | 11.3396 | 10.9956 | 10.4785 | 9.93 | 9.3427 | 8.7092 | 7.993 | 6.7951 | 3.4203 | -2.1397 | -5.9367 | -7.6737 | 17.4974 | 17.3347 | 17.0654 | 16.7545 | 16.4173 | 16.0495 | 15.6442 | 15.1645 | 14.4518 | 12.5766 | 9.6336 | 7.4779 | 5.5362 | 14.2636 | 14.1445 | 13.9851 | 13.5535 | 13.0263 | 12.4522 | 11.8295 | 11.1153 | 9.9543 | 6.753 | 1.8475 | -1.3633 | -2.8521
BRAMLEY (FLEE) | READING BSP | TWYFORD | MINIMUM HEADROOM | SU 78430 76339 | YES | 6.1866 | 5.8379 | 5.4848 | 5.0011 | 4.4895 | 3.9622 | 3.3333 | 2.6239 | 1.4229 | -1.0415 | -4.9611 | -7.7296 | -9.0204 | 7.9485 | 7.6717 | 7.3885 | 7.0685 | 6.7244 | 6.3525 | 5.898 | 5.3738 | 4.566 | 3.0537 | 0.86682 | -0.79557 | -2.2186 | 7.5869 | 7.2482 | 6.9033 | 6.4511 | 5.9681 | 5.4674 | 4.8665 | 4.1854 | 3.0429 | 0.7559 | -2.7689 | -5.1719 | -6.2259
|  | TWYFORD | CT |  |  | 6.1866 | 5.8379 | 5.4848 | 5.0011 | 4.4895 | 3.9622 | 3.3333 | 2.6239 | 1.4229 | -1.0415 | -4.9611 | -7.7296 | -9.0204 | 7.9485 | 7.6717 | 7.3885 | 7.0685 | 6.7244 | 6.3525 | 5.898 | 5.3738 | 4.566 | 3.0537 | 0.86682 | -0.79557 | -2.2186 | 7.5869 | 7.2482 | 6.9033 | 6.4511 | 5.9681 | 5.4674 | 4.8665 | 4.1854 | 3.0429 | 0.7559 | -2.7689 | -5.1719 | -6.2259
|  | TWYFORD | LW |  |  | 6.1866 | 5.8379 | 5.4848 | 5.0011 | 4.4895 | 3.9622 | 3.3333 | 2.6239 | 1.4229 | -1.0415 | -4.9611 | -7.7296 | -9.0204 | 7.9485 | 7.6717 | 7.3885 | 7.0685 | 6.7244 | 6.3525 | 5.898 | 5.3738 | 4.566 | 3.0537 | 0.86682 | -0.79557 | -2.2186 | 7.5869 | 7.2482 | 6.9033 | 6.4511 | 5.9681 | 5.4674 | 4.8665 | 4.1854 | 3.0429 | 0.7559 | -2.7689 | -5.1719 | -6.2259
|  | TWYFORD | ST |  |  | 6.1866 | 5.8379 | 5.4848 | 5.0011 | 4.4895 | 3.9622 | 3.3333 | 2.6239 | 1.4229 | -1.0415 | -4.9611 | -7.7296 | -9.0204 | 7.9485 | 7.6717 | 7.3885 | 7.0685 | 6.7244 | 6.3525 | 5.898 | 5.3738 | 4.566 | 3.0537 | 0.86682 | -0.79557 | -2.2186 | 7.5869 | 7.2482 | 6.9033 | 6.4511 | 5.9681 | 5.4674 | 4.8665 | 4.1854 | 3.0429 | 0.7559 | -2.7689 | -5.1719 | -6.2259
|  | TWYFORD | FS |  |  | 6.1866 | 5.8379 | 5.4848 | 5.0011 | 4.4895 | 3.9622 | 3.3333 | 2.6239 | 1.4229 | -1.0415 | -4.9611 | -7.7296 | -9.0204 | 7.9485 | 7.6717 | 7.3885 | 7.0685 | 6.7244 | 6.3525 | 5.898 | 5.3738 | 4.566 | 3.0537 | 0.86682 | -0.79557 | -2.2186 | 7.5869 | 7.2482 | 6.9033 | 6.4511 | 5.9681 | 5.4674 | 4.8665 | 4.1854 | 3.0429 | 0.7559 | -2.7689 | -5.1719 | -6.2259
COWLEY GSP | COWLEY LOCAL (2 X 90) | UNION STREET | MINIMUM HEADROOM | SP 52865 05849 | NO | 10.2662 | 10.0423 | 9.443 | 8.9211 | 8.4831 | 8.0459 | 7.5688 | 7.0226 | 6.1614 | 3.3951 | -1.7969 | -6.183 | -8.7498 | 8.8513 | 8.6284 | 8.1883 | 7.7882 | 7.4024 | 6.9864 | 6.5269 | 5.9961 | 5.3167 | 2.984 | -1.7676 | -7.3663 | -15.0038 | 10.3173 | 10.1057 | 9.5634 | 9.0858 | 8.6776 | 8.2666 | 7.8182 | 7.3033 | 6.4998 | 3.8259 | -1.0901 | -4.6863 | -6.7677
|  | UNION STREET | CT |  |  | 10.2662 | 10.0423 | 9.443 | 8.9211 | 8.4831 | 8.0459 | 7.5688 | 7.0226 | 6.1614 | 3.3951 | -1.7969 | -6.183 | -8.7498 | 8.8513 | 8.6284 | 8.1883 | 7.7882 | 7.4024 | 6.9864 | 6.5269 | 5.9961 | 5.3167 | 2.984 | -1.7676 | -7.3663 | -15.0038 | 10.3173 | 10.1057 | 9.5634 | 9.0858 | 8.6776 | 8.2666 | 7.8182 | 7.3033 | 6.4998 | 3.8259 | -1.0901 | -4.6863 | -6.7677
|  | UNION STREET | LW |  |  | 10.2662 | 10.0423 | 9.443 | 8.9211 | 8.4831 | 8.0459 | 7.5688 | 7.0226 | 6.1614 | 3.3951 | -1.7969 | -6.183 | -8.7498 | 8.8513 | 8.6284 | 8.1883 | 7.7882 | 7.4024 | 6.9864 | 6.5269 | 5.9961 | 5.3167 | 2.984 | -1.7676 | -7.3663 | -15.0038 | 10.3173 | 10.1057 | 9.5634 | 9.0858 | 8.6776 | 8.2666 | 7.8182 | 7.3033 | 6.4998 | 3.8259 | -1.0901 | -4.6863 | -6.7677
|  | UNION STREET | ST |  |  | 10.2662 | 10.0423 | 9.443 | 8.9211 | 8.4831 | 8.0459 | 7.5688 | 7.0226 | 6.1614 | 3.3951 | -1.7969 | -6.183 | -8.7498 | 8.8513 | 8.6284 | 8.1883 | 7.7882 | 7.4024 | 6.9864 | 6.5269 | 5.9961 | 5.3167 | 2.984 | -1.7676 | -7.3663 | -15.0038 | 10.3173 | 10.1057 | 9.5634 | 9.0858 | 8.6776 | 8.2666 | 7.8182 | 7.3033 | 6.4998 | 3.8259 | -1.0901 | -4.6863 | -6.7677
|  | UNION STREET | FS |  |  | 10.2662 | 10.0423 | 9.443 | 8.9211 | 8.4831 | 8.0459 | 7.5688 | 7.0226 | 6.1614 | 3.3951 | -1.7969 | -6.183 | -8.7498 | 8.8513 | 8.6284 | 8.1883 | 7.7882 | 7.4024 | 6.9864 | 6.5269 | 5.9961 | 5.3167 | 2.984 | -1.7676 | -7.3663 | -15.0038 | 10.3173 | 10.1057 | 9.5634 | 9.0858 | 8.6776 | 8.2666 | 7.8182 | 7.3033 | 6.4998 | 3.8259 | -1.0901 | -4.6863 | -6.7677
COWLEY GSP | OXFORD BSP | UNIVERSITY PARKS | MINIMUM HEADROOM |  |  | 21.3068 | 21.2744 | 21.2344 | 21.1921 | 21.1443 | 21.0926 | 21.0361 | 20.9605 | 20.8752 | 20.5735 | 19.5229 | 18.7394 | 18.3063 | 25.0127 | 24.9821 | 24.9455 | 24.9007 | 24.8513 | 24.7979 | 24.7399 | 24.668 | 24.5816 | 24.2846 | 23.7122 | 23.211 | 22.7247 | 20.5717 | 20.5389 | 20.4984 | 20.4551 | 20.4062 | 20.3532 | 20.2952 | 20.2175 | 20.1294 | 19.8187 | 19.3363 | 18.9719 | 18.6127
|  | UNIVERSITY PARKS | CT |  |  | 21.3068 | 21.2744 | 21.2344 | 21.1921 | 21.1443 | 21.0926 | 21.0361 | 20.9605 | 20.8752 | 20.5735 | 19.5229 | 18.7394 | 18.3063 | 25.0127 | 24.9821 | 24.9455 | 24.9007 | 24.8513 | 24.7979 | 24.7399 | 24.668 | 24.5816 | 24.2846 | 23.7122 | 23.211 | 22.7247 | 20.5717 | 20.5389 | 20.4984 | 20.4551 | 20.4062 | 20.3532 | 20.2952 | 20.2175 | 20.1294 | 19.8187 | 19.3363 | 18.9719 | 18.6127
|  | UNIVERSITY PARKS | LW |  |  | 21.3068 | 21.2744 | 21.2344 | 21.1921 | 21.1443 | 21.0926 | 21.0361 | 20.9605 | 20.8752 | 20.5735 | 19.5229 | 18.7394 | 18.3063 | 25.0127 | 24.9821 | 24.9455 | 24.9007 | 24.8513 | 24.7979 | 24.7399 | 24.668 | 24.5816 | 24.2846 | 23.7122 | 23.211 | 22.7247 | 20.5717 | 20.5389 | 20.4984 | 20.4551 | 20.4062 | 20.3532 | 20.2952 | 20.2175 | 20.1294 | 19.8187 | 19.3363 | 18.9719 | 18.6127
|  | UNIVERSITY PARKS | ST |  |  | 21.3068 | 21.2744 | 21.2344 | 21.1921 | 21.1443 | 21.0926 | 21.0361 | 20.9605 | 20.8752 | 20.5735 | 19.5229 | 18.7394 | 18.3063 | 25.0127 | 24.9821 | 24.9455 | 24.9007 | 24.8513 | 24.7979 | 24.7399 | 24.668 | 24.5816 | 24.2846 | 23.7122 | 23.211 | 22.7247 | 20.5717 | 20.5389 | 20.4984 | 20.4551 | 20.4062 | 20.3532 | 20.2952 | 20.2175 | 20.1294 | 19.8187 | 19.3363 | 18.9719 | 18.6127
|  | UNIVERSITY PARKS | FS |  |  | 21.3068 | 21.2744 | 21.2344 | 21.1921 | 21.1443 | 21.0926 | 21.0361 | 20.9605 | 20.8752 | 20.5735 | 19.5229 | 18.7394 | 18.3063 | 25.0127 | 24.9821 | 24.9455 | 24.9007 | 24.8513 | 24.7979 | 24.7399 | 24.668 | 24.5816 | 24.2846 | 23.7122 | 23.211 | 22.7247 | 20.5717 | 20.5389 | 20.4984 | 20.4551 | 20.4062 | 20.3532 | 20.2952 | 20.2175 | 20.1294 | 19.8187 | 19.3363 | 18.9719 | 18.6127
EAST CLAYDON GSP | BICESTER NORTH BSP | UPPER HEYFORD | MINIMUM HEADROOM | SP 51750 25667 | NO | 8.826 | 8.53 | 8.1365 | 7.6671 | 7.1565 | 6.6386 | 6.059 | 5.4055 | 4.6671 | 3.6292 | 2.3111 | 1.7145 | 1.5245 | 10.6697 | 10.4557 | 10.2345 | 9.9927 | 9.7302 | 9.4605 | 9.1572 | 8.8055 | 8.4028 | 7.8831 | 7.2786 | 6.9664 | 6.7585 | 9.1189 | 8.806 | 8.4755 | 8.0949 | 7.6807 | 7.2575 | 6.7821 | 6.2373 | 5.6128 | 4.7674 | 3.7455 | 3.2894 | 3.1404
|  | UPPER HEYFORD | CT |  |  | 8.826 | 8.53 | 8.1365 | 7.6671 | 7.1565 | 6.6386 | 6.059 | 5.4055 | 4.6671 | 3.6292 | 2.3111 | 1.7145 | 1.5245 | 10.6697 | 10.4557 | 10.2345 | 9.9927 | 9.7302 | 9.4605 | 9.1572 | 8.8055 | 8.4028 | 7.8831 | 7.2786 | 6.9664 | 6.7585 | 9.1189 | 8.806 | 8.4755 | 8.0949 | 7.6807 | 7.2575 | 6.7821 | 6.2373 | 5.6128 | 4.7674 | 3.7455 | 3.2894 | 3.1404
|  | UPPER HEYFORD | LW |  |  | 8.826 | 8.53 | 8.1365 | 7.6671 | 7.1565 | 6.6386 | 6.059 | 5.4055 | 4.6671 | 3.6292 | 2.3111 | 1.7145 | 1.5245 | 10.6697 | 10.4557 | 10.2345 | 9.9927 | 9.7302 | 9.4605 | 9.1572 | 8.8055 | 8.4028 | 7.8831 | 7.2786 | 6.9664 | 6.7585 | 9.1189 | 8.806 | 8.4755 | 8.0949 | 7.6807 | 7.2575 | 6.7821 | 6.2373 | 5.6128 | 4.7674 | 3.7455 | 3.2894 | 3.1404
|  | UPPER HEYFORD | ST |  |  | 8.826 | 8.53 | 8.1365 | 7.6671 | 7.1565 | 6.6386 | 6.059 | 5.4055 | 4.6671 | 3.6292 | 2.3111 | 1.7145 | 1.5245 | 10.6697 | 10.4557 | 10.2345 | 9.9927 | 9.7302 | 9.4605 | 9.1572 | 8.8055 | 8.4028 | 7.8831 | 7.2786 | 6.9664 | 6.7585 | 9.1189 | 8.806 | 8.4755 | 8.0949 | 7.6807 | 7.2575 | 6.7821 | 6.2373 | 5.6128 | 4.7674 | 3.7455 | 3.2894 | 3.1404
|  | UPPER HEYFORD | FS |  |  | 8.826 | 8.53 | 8.1365 | 7.6671 | 7.1565 | 6.6386 | 6.059 | 5.4055 | 4.6671 | 3.6292 | 2.3111 | 1.7145 | 1.5245 | 10.6697 | 10.4557 | 10.2345 | 9.9927 | 9.7302 | 9.4605 | 9.1572 | 8.8055 | 8.4028 | 7.8831 | 7.2786 | 6.9664 | 6.7585 | 9.1189 | 8.806 | 8.4755 | 8.0949 | 7.6807 | 7.2575 | 6.7821 | 6.2373 | 5.6128 | 4.7674 | 3.7455 | 3.2894 | 3.1404
IVER 132KV | UPTON BSP | UPTON | MINIMUM HEADROOM | TQ 00800 79434 | YES | 10.3908 | 9.9663 | 9.357 | 8.5553 | 7.6886 | 6.7922 | 5.8021 | 4.5529 | 2.7353 | -1.9793 | -9.4504 | -14.4961 | -17.4027 | 17.073 | 16.8889 | 16.6457 | 16.2863 | 15.7332 | 15.1431 | 14.4856 | 13.6587 | 12.5277 | 9.5838 | 4.9436 | 1.3596 | -2.1048 | 13.4371 | 13.0389 | 12.4629 | 11.753 | 10.9823 | 10.1699 | 9.2511 | 8.0831 | 6.3909 | 2.0288 | -4.7121 | -9.0915 | -11.4873
|  | UPTON | CT |  |  | 10.3908 | 9.9663 | 9.357 | 8.5553 | 7.6886 | 6.7922 | 5.8021 | 4.5529 | 2.7353 | -1.9793 | -9.4504 | -14.4961 | -17.4027 | 17.073 | 16.8889 | 16.6457 | 16.2863 | 15.7332 | 15.1431 | 14.4856 | 13.6587 | 12.5277 | 9.5838 | 4.9436 | 1.3596 | -2.1048 | 13.4371 | 13.0389 | 12.4629 | 11.753 | 10.9823 | 10.1699 | 9.2511 | 8.0831 | 6.3909 | 2.0288 | -4.7121 | -9.0915 | -11.4873
|  | UPTON | LW |  |  | 10.3908 | 9.9663 | 9.357 | 8.5553 | 7.6886 | 6.7922 | 5.8021 | 4.5529 | 2.7353 | -1.9793 | -9.4504 | -14.4961 | -17.4027 | 17.073 | 16.8889 | 16.6457 | 16.2863 | 15.7332 | 15.1431 | 14.4856 | 13.6587 | 12.5277 | 9.5838 | 4.9436 | 1.3596 | -2.1048 | 13.4371 | 13.0389 | 12.4629 | 11.753 | 10.9823 | 10.1699 | 9.2511 | 8.0831 | 6.3909 | 2.0288 | -4.7121 | -9.0915 | -11.4873
|  | UPTON | ST |  |  | 10.3908 | 9.9663 | 9.357 | 8.5553 | 7.6886 | 6.7922 | 5.8021 | 4.5529 | 2.7353 | -1.9793 | -9.4504 | -14.4961 | -17.4027 | 17.073 | 16.8889 | 16.6457 | 16.2863 | 15.7332 | 15.1431 | 14.4856 | 13.6587 | 12.5277 | 9.5838 | 4.9436 | 1.3596 | -2.1048 | 13.4371 | 13.0389 | 12.4629 | 11.753 | 10.9823 | 10.1699 | 9.2511 | 8.0831 | 6.3909 | 2.0288 | -4.7121 | -9.0915 | -11.4873
|  | UPTON | FS |  |  | 10.3908 | 9.9663 | 9.357 | 8.5553 | 7.6886 | 6.7922 | 5.8021 | 4.5529 | 2.7353 | -1.9793 | -9.4504 | -14.4961 | -17.4027 | 17.073 | 16.8889 | 16.6457 | 16.2863 | 15.7332 | 15.1431 | 14.4856 | 13.6587 | 12.5277 | 9.5838 | 4.9436 | 1.3596 | -2.1048 | 13.4371 | 13.0389 | 12.4629 | 11.753 | 10.9823 | 10.1699 | 9.2511 | 8.0831 | 6.3909 | 2.0288 | -4.7121 | -9.0915 | -11.4873
IVER 132kV |  | UXBRIDGE | MINIMUM HEADROOM | TQ 04984 83484 |  | 36.455 | 36.0296 | 35.5094 | 34.6344 | 33.7578 | 32.7746 | 31.6607 | 30.3797 | 28.4403 | 23.4801 | 15.6109 | 10.6503 | 8.2689 | 39.9272 | 39.573 | 39.1186 | 38.5455 | 38.0081 | 37.4117 | 36.7988 | 36.1158 | 34.8884 | 31.453 | 25.6176 | 20.2859 | 13.8176 | 36.3034 | 35.9079 | 35.4166 | 34.8374 | 34.2104 | 33.4681 | 32.542 | 31.3726 | 29.5973 | 25.0406 | 17.8192 | 13.3283 | 11.2025
|  | UXBRIDGE | CT |  |  | 36.455 | 36.0296 | 35.5094 | 34.6344 | 33.7578 | 32.7746 | 31.6607 | 30.3797 | 28.4403 | 23.4801 | 15.6109 | 10.6503 | 8.2689 | 39.9272 | 39.573 | 39.1186 | 38.5455 | 38.0081 | 37.4117 | 36.7988 | 36.1158 | 34.8884 | 31.453 | 25.6176 | 20.2859 | 13.8176 | 36.3034 | 35.9079 | 35.4166 | 34.8374 | 34.2104 | 33.4681 | 32.542 | 31.3726 | 29.5973 | 25.0406 | 17.8192 | 13.3283 | 11.2025
|  | UXBRIDGE | LW |  |  | 36.455 | 36.0296 | 35.5094 | 34.6344 | 33.7578 | 32.7746 | 31.6607 | 30.3797 | 28.4403 | 23.4801 | 15.6109 | 10.6503 | 8.2689 | 39.9272 | 39.573 | 39.1186 | 38.5455 | 38.0081 | 37.4117 | 36.7988 | 36.1158 | 34.8884 | 31.453 | 25.6176 | 20.2859 | 13.8176 | 36.3034 | 35.9079 | 35.4166 | 34.8374 | 34.2104 | 33.4681 | 32.542 | 31.3726 | 29.5973 | 25.0406 | 17.8192 | 13.3283 | 11.2025
|  | UXBRIDGE | ST |  |  | 36.455 | 36.0296 | 35.5094 | 34.6344 | 33.7578 | 32.7746 | 31.6607 | 30.3797 | 28.4403 | 23.4801 | 15.6109 | 10.6503 | 8.2689 | 39.9272 | 39.573 | 39.1186 | 38.5455 | 38.0081 | 37.4117 | 36.7988 | 36.1158 | 34.8884 | 31.453 | 25.6176 | 20.2859 | 13.8176 | 36.3034 | 35.9079 | 35.4166 | 34.8374 | 34.2104 | 33.4681 | 32.542 | 31.3726 | 29.5973 | 25.0406 | 17.8192 | 13.3283 | 11.2025
|  | UXBRIDGE | FS |  |  | 36.455 | 36.0296 | 35.5094 | 34.6344 | 33.7578 | 32.7746 | 31.6607 | 30.3797 | 28.4403 | 23.4801 | 15.6109 | 10.6503 | 8.2689 | 39.9272 | 39.573 | 39.1186 | 38.5455 | 38.0081 | 37.4117 | 36.7988 | 36.1158 | 34.8884 | 31.453 | 25.6176 | 20.2859 | 13.8176 | 36.3034 | 35.9079 | 35.4166 | 34.8374 | 34.2104 | 33.4681 | 32.542 | 31.3726 | 29.5973 | 25.0406 | 17.8192 | 13.3283 | 11.2025
NURSLING GSP | VELMORE BSP | VELMORE | MINIMUM HEADROOM | SU 42935 19205 | YES | 16.6024 | 15.831 | 15.2983 | 14.6358 | 13.9162 | 13.1594 | 12.2993 | 11.3021 | 9.8079 | 6.3695 | 0.4614 | -3.6762 | -6.0773 | 16.3372 | 16.0202 | 15.7879 | 15.5459 | 15.2963 | 15.0194 | 14.5287 | 13.8252 | 12.8575 | 10.6637 | 6.9842 | 4.2064 | 1.6829 | 18.9701 | 18.5105 | 18.1261 | 17.6487 | 16.9707 | 16.2536 | 15.4355 | 14.479 | 13.0587 | 9.8558 | 4.5338 | 0.93657 | -1.1106
|  | VELMORE | CT |  |  | 16.6024 | 15.831 | 15.2983 | 14.6358 | 13.9162 | 13.1594 | 12.2993 | 11.3021 | 9.8079 | 6.3695 | 0.4614 | -3.6762 | -6.0773 | 16.3372 | 16.0202 | 15.7879 | 15.5459 | 15.2963 | 15.0194 | 14.5287 | 13.8252 | 12.8575 | 10.6637 | 6.9842 | 4.2064 | 1.6829 | 18.9701 | 18.5105 | 18.1261 | 17.6487 | 16.9707 | 16.2536 | 15.4355 | 14.479 | 13.0587 | 9.8558 | 4.5338 | 0.93657 | -1.1106
|  | VELMORE | LW |  |  | 16.6024 | 15.831 | 15.2983 | 14.6358 | 13.9162 | 13.1594 | 12.2993 | 11.3021 | 9.8079 | 6.3695 | 0.4614 | -3.6762 | -6.0773 | 16.3372 | 16.0202 | 15.7879 | 15.5459 | 15.2963 | 15.0194 | 14.5287 | 13.8252 | 12.8575 | 10.6637 | 6.9842 | 4.2064 | 1.6829 | 18.9701 | 18.5105 | 18.1261 | 17.6487 | 16.9707 | 16.2536 | 15.4355 | 14.479 | 13.0587 | 9.8558 | 4.5338 | 0.93657 | -1.1106
|  | VELMORE | ST |  |  | 16.6024 | 15.831 | 15.2983 | 14.6358 | 13.9162 | 13.1594 | 12.2993 | 11.3021 | 9.8079 | 6.3695 | 0.4614 | -3.6762 | -6.0773 | 16.3372 | 16.0202 | 15.7879 | 15.5459 | 15.2963 | 15.0194 | 14.5287 | 13.8252 | 12.8575 | 10.6637 | 6.9842 | 4.2064 | 1.6829 | 18.9701 | 18.5105 | 18.1261 | 17.6487 | 16.9707 | 16.2536 | 15.4355 | 14.479 | 13.0587 | 9.8558 | 4.5338 | 0.93657 | -1.1106
|  | VELMORE | FS |  |  | 16.6024 | 15.831 | 15.2983 | 14.6358 | 13.9162 | 13.1594 | 12.2993 | 11.3021 | 9.8079 | 6.3695 | 0.4614 | -3.6762 | -6.0773 | 16.3372 | 16.0202 | 15.7879 | 15.5459 | 15.2963 | 15.0194 | 14.5287 | 13.8252 | 12.8575 | 10.6637 | 6.9842 | 4.2064 | 1.6829 | 18.9701 | 18.5105 | 18.1261 | 17.6487 | 16.9707 | 16.2536 | 15.4355 | 14.479 | 13.0587 | 9.8558 | 4.5338 | 0.93657 | -1.1106
FAWLEY GSP | COWES & WOOTTON COMMON BSP | VENTNOR | MINIMUM HEADROOM | SZ 56148 77857 | YES | 27.4449 | 27.1819 | 26.8164 | 26.2677 | 25.693 | 25.0699 | 24.4054 | 23.6917 | 22.5526 | 19.317 | 13.9502 | 10.4326 | 9.4016 | 26.3987 | 26.2464 | 25.9968 | 25.6897 | 25.3604 | 24.9999 | 24.6083 | 24.1688 | 23.508 | 21.7068 | 19.3112 | 17.5877 | 16.4492 | 29.956 | 29.7259 | 29.3743 | 28.8979 | 28.3674 | 27.7907 | 27.1722 | 26.4984 | 25.436 | 22.4769 | 17.953 | 14.8626 | 13.9402
|  | VENTNOR | CT |  |  | 27.4449 | 27.1819 | 26.8164 | 26.2677 | 25.693 | 25.0699 | 24.4054 | 23.6917 | 22.5526 | 19.317 | 13.9502 | 10.4326 | 9.4016 | 26.3987 | 26.2464 | 25.9968 | 25.6897 | 25.3604 | 24.9999 | 24.6083 | 24.1688 | 23.508 | 21.7068 | 19.3112 | 17.5877 | 16.4492 | 29.956 | 29.7259 | 29.3743 | 28.8979 | 28.3674 | 27.7907 | 27.1722 | 26.4984 | 25.436 | 22.4769 | 17.953 | 14.8626 | 13.9402
|  | VENTNOR | LW |  |  | 27.4449 | 27.1819 | 26.8164 | 26.2677 | 25.693 | 25.0699 | 24.4054 | 23.6917 | 22.5526 | 19.317 | 13.9502 | 10.4326 | 9.4016 | 26.3987 | 26.2464 | 25.9968 | 25.6897 | 25.3604 | 24.9999 | 24.6083 | 24.1688 | 23.508 | 21.7068 | 19.3112 | 17.5877 | 16.4492 | 29.956 | 29.7259 | 29.3743 | 28.8979 | 28.3674 | 27.7907 | 27.1722 | 26.4984 | 25.436 | 22.4769 | 17.953 | 14.8626 | 13.9402
|  | VENTNOR | ST |  |  | 27.4449 | 27.1819 | 26.8164 | 26.2677 | 25.693 | 25.0699 | 24.4054 | 23.6917 | 22.5526 | 19.317 | 13.9502 | 10.4326 | 9.4016 | 26.3987 | 26.2464 | 25.9968 | 25.6897 | 25.3604 | 24.9999 | 24.6083 | 24.1688 | 23.508 | 21.7068 | 19.3112 | 17.5877 | 16.4492 | 29.956 | 29.7259 | 29.3743 | 28.8979 | 28.3674 | 27.7907 | 27.1722 | 26.4984 | 25.436 | 22.4769 | 17.953 | 14.8626 | 13.9402
|  | VENTNOR | FS |  |  | 27.4449 | 27.1819 | 26.8164 | 26.2677 | 25.693 | 25.0699 | 24.4054 | 23.6917 | 22.5526 | 19.317 | 13.9502 | 10.4326 | 9.4016 | 26.3987 | 26.2464 | 25.9968 | 25.6897 | 25.3604 | 24.9999 | 24.6083 | 24.1688 | 23.508 | 21.7068 | 19.3112 | 17.5877 | 16.4492 | 29.956 | 29.7259 | 29.3743 | 28.8979 | 28.3674 | 27.7907 | 27.1722 | 26.4984 | 25.436 | 22.4769 | 17.953 | 14.8626 | 13.9402
MANNINGTON GSP | MANNINGTON BSP | VERWOOD | MINIMUM HEADROOM | SU 07716 10226 | YES | 1.3231 | 0.94624 | 0.47028 | -0.048252 | -0.61701 | -1.229 | -1.9007 | -2.7581 | -4.0108 | -6.4859 | -10.1982 | -12.661 | -13.718 | 4.9686 | 4.7189 | 4.4014 | 4.0761 | 3.7189 | 3.3265 | 2.863 | 2.2466 | 1.4031 | -0.13321 | -2.229 | -3.6849 | -4.7593 | 2.8374 | 2.4811 | 2.0292 | 1.5247 | 0.97443 | 0.38049 | -0.27091 | -1.0995 | -2.3133 | -4.7174 | -8.3386 | -10.7514 | -11.7835
|  | VERWOOD | CT |  |  | 1.3231 | 0.94624 | 0.47028 | -0.048252 | -0.61701 | -1.229 | -1.9007 | -2.7581 | -4.0108 | -6.4859 | -10.1982 | -12.661 | -13.718 | 4.9686 | 4.7189 | 4.4014 | 4.0761 | 3.7189 | 3.3265 | 2.863 | 2.2466 | 1.4031 | -0.13321 | -2.229 | -3.6849 | -4.7593 | 2.8374 | 2.4811 | 2.0292 | 1.5247 | 0.97443 | 0.38049 | -0.27091 | -1.0995 | -2.3133 | -4.7174 | -8.3386 | -10.7514 | -11.7835
|  | VERWOOD | LW |  |  | 1.3231 | 0.94624 | 0.47028 | -0.048252 | -0.61701 | -1.229 | -1.9007 | -2.7581 | -4.0108 | -6.4859 | -10.1982 | -12.661 | -13.718 | 4.9686 | 4.7189 | 4.4014 | 4.0761 | 3.7189 | 3.3265 | 2.863 | 2.2466 | 1.4031 | -0.13321 | -2.229 | -3.6849 | -4.7593 | 2.8374 | 2.4811 | 2.0292 | 1.5247 | 0.97443 | 0.38049 | -0.27091 | -1.0995 | -2.3133 | -4.7174 | -8.3386 | -10.7514 | -11.7835
|  | VERWOOD | ST |  |  | 1.3231 | 0.94624 | 0.47028 | -0.048252 | -0.61701 | -1.229 | -1.9007 | -2.7581 | -4.0108 | -6.4859 | -10.1982 | -12.661 | -13.718 | 4.9686 | 4.7189 | 4.4014 | 4.0761 | 3.7189 | 3.3265 | 2.863 | 2.2466 | 1.4031 | -0.13321 | -2.229 | -3.6849 | -4.7593 | 2.8374 | 2.4811 | 2.0292 | 1.5247 | 0.97443 | 0.38049 | -0.27091 | -1.0995 | -2.3133 | -4.7174 | -8.3386 | -10.7514 | -11.7835
|  | VERWOOD | FS |  |  | 1.3231 | 0.94624 | 0.47028 | -0.048252 | -0.61701 | -1.229 | -1.9007 | -2.7581 | -4.0108 | -6.4859 | -10.1982 | -12.661 | -13.718 | 4.9686 | 4.7189 | 4.4014 | 4.0761 | 3.7189 | 3.3265 | 2.863 | 2.2466 | 1.4031 | -0.13321 | -2.229 | -3.6849 | -4.7593 | 2.8374 | 2.4811 | 2.0292 | 1.5247 | 0.97443 | 0.38049 | -0.27091 | -1.0995 | -2.3133 | -4.7174 | -8.3386 | -10.7514 | -11.7835
NURSLING GSP |  | VICARAGE FARM ROAD | MINIMUM HEADROOM | TQ 12358 76435 |  | 10.1844 | 9.474 | 8.6211 | 7.5551 | 6.4061 | 5.1935 | 3.8708 | 2.4891 | 0.48365 | -5.8071 | -15.8768 | -22.7835 | -26.7179 | 20.2087 | 19.9215 | 19.6157 | 18.8895 | 18.0987 | 17.2408 | 16.2849 | 15.2328 | 13.8769 | 9.5143 | 2.4873 | -4.1063 | -11.8458 | 14.5817 | 13.96 | 13.1789 | 12.2337 | 11.213 | 10.1145 | 8.8983 | 7.6051 | 5.7351 | -0.13531 | -9.2075 | -15.1173 | -18.3156
|  | VICARAGE FARM ROAD | CT |  |  | 10.1844 | 9.474 | 8.6211 | 7.5551 | 6.4061 | 5.1935 | 3.8708 | 2.4891 | 0.48365 | -5.8071 | -15.8768 | -22.7835 | -26.7179 | 20.2087 | 19.9215 | 19.6157 | 18.8895 | 18.0987 | 17.2408 | 16.2849 | 15.2328 | 13.8769 | 9.5143 | 2.4873 | -4.1063 | -11.8458 | 14.5817 | 13.96 | 13.1789 | 12.2337 | 11.213 | 10.1145 | 8.8983 | 7.6051 | 5.7351 | -0.13531 | -9.2075 | -15.1173 | -18.3156
|  | VICARAGE FARM ROAD | LW |  |  | 10.1844 | 9.474 | 8.6211 | 7.5551 | 6.4061 | 5.1935 | 3.8708 | 2.4891 | 0.48365 | -5.8071 | -15.8768 | -22.7835 | -26.7179 | 20.2087 | 19.9215 | 19.6157 | 18.8895 | 18.0987 | 17.2408 | 16.2849 | 15.2328 | 13.8769 | 9.5143 | 2.4873 | -4.1063 | -11.8458 | 14.5817 | 13.96 | 13.1789 | 12.2337 | 11.213 | 10.1145 | 8.8983 | 7.6051 | 5.7351 | -0.13531 | -9.2075 | -15.1173 | -18.3156
|  | VICARAGE FARM ROAD | ST |  |  | 10.1844 | 9.474 | 8.6211 | 7.5551 | 6.4061 | 5.1935 | 3.8708 | 2.4891 | 0.48365 | -5.8071 | -15.8768 | -22.7835 | -26.7179 | 20.2087 | 19.9215 | 19.6157 | 18.8895 | 18.0987 | 17.2408 | 16.2849 | 15.2328 | 13.8769 | 9.5143 | 2.4873 | -4.1063 | -11.8458 | 14.5817 | 13.96 | 13.1789 | 12.2337 | 11.213 | 10.1145 | 8.8983 | 7.6051 | 5.7351 | -0.13531 | -9.2075 | -15.1173 | -18.3156
|  | VICARAGE FARM ROAD | FS |  |  | 10.1844 | 9.474 | 8.6211 | 7.5551 | 6.4061 | 5.1935 | 3.8708 | 2.4891 | 0.48365 | -5.8071 | -15.8768 | -22.7835 | -26.7179 | 20.2087 | 19.9215 | 19.6157 | 18.8895 | 18.0987 | 17.2408 | 16.2849 | 15.2328 | 13.8769 | 9.5143 | 2.4873 | -4.1063 | -11.8458 | 14.5817 | 13.96 | 13.1789 | 12.2337 | 11.213 | 10.1145 | 8.8983 | 7.6051 | 5.7351 | -0.13531 | -9.2075 | -15.1173 | -18.3156
COWLEY GSP | COWLEY LOCAL (2 X 90) | WALLINGFORD | MINIMUM HEADROOM | SU 59847 89486 | NO | 0.55363 | 0.042784 | -0.5968 | -1.3769 | -2.1863 | -2.8796 | -3.6488 | -4.5078 | -5.8007 | -8.8694 | -13.4619 | -16.807 | -18.3 | 5.4831 | 5.1356 | 4.7141 | 4.2564 | 3.7796 | 3.3504 | 2.8696 | 2.3249 | 1.5354 | -0.32808 | -2.7911 | -4.7653 | -6.4244 | 1.7048 | 1.2371 | 0.66025 | -0.032159 | -0.75273 | -1.3873 | -2.094 | -2.8876 | -4.0831 | -6.908 | -10.9342 | -13.6975 | -14.9255
|  | WALLINGFORD | CT |  |  | 0.55363 | 0.042784 | -0.5968 | -1.3769 | -2.1863 | -2.8796 | -3.6488 | -4.5078 | -5.8007 | -8.8694 | -13.4619 | -16.807 | -18.3 | 5.4831 | 5.1356 | 4.7141 | 4.2564 | 3.7796 | 3.3504 | 2.8696 | 2.3249 | 1.5354 | -0.32808 | -2.7911 | -4.7653 | -6.4244 | 1.7048 | 1.2371 | 0.66025 | -0.032159 | -0.75273 | -1.3873 | -2.094 | -2.8876 | -4.0831 | -6.908 | -10.9342 | -13.6975 | -14.9255
|  | WALLINGFORD | LW |  |  | 0.55363 | 0.042784 | -0.5968 | -1.3769 | -2.1863 | -2.8796 | -3.6488 | -4.5078 | -5.8007 | -8.8694 | -13.4619 | -16.807 | -18.3 | 5.4831 | 5.1356 | 4.7141 | 4.2564 | 3.7796 | 3.3504 | 2.8696 | 2.3249 | 1.5354 | -0.32808 | -2.7911 | -4.7653 | -6.4244 | 1.7048 | 1.2371 | 0.66025 | -0.032159 | -0.75273 | -1.3873 | -2.094 | -2.8876 | -4.0831 | -6.908 | -10.9342 | -13.6975 | -14.9255
|  | WALLINGFORD | ST |  |  | 0.55363 | 0.042784 | -0.5968 | -1.3769 | -2.1863 | -2.8796 | -3.6488 | -4.5078 | -5.8007 | -8.8694 | -13.4619 | -16.807 | -18.3 | 5.4831 | 5.1356 | 4.7141 | 4.2564 | 3.7796 | 3.3504 | 2.8696 | 2.3249 | 1.5354 | -0.32808 | -2.7911 | -4.7653 | -6.4244 | 1.7048 | 1.2371 | 0.66025 | -0.032159 | -0.75273 | -1.3873 | -2.094 | -2.8876 | -4.0831 | -6.908 | -10.9342 | -13.6975 | -14.9255
|  | WALLINGFORD | FS |  |  | 0.55363 | 0.042784 | -0.5968 | -1.3769 | -2.1863 | -2.8796 | -3.6488 | -4.5078 | -5.8007 | -8.8694 | -13.4619 | -16.807 | -18.3 | 5.4831 | 5.1356 | 4.7141 | 4.2564 | 3.7796 | 3.3504 | 2.8696 | 2.3249 | 1.5354 | -0.32808 | -2.7911 | -4.7653 | -6.4244 | 1.7048 | 1.2371 | 0.66025 | -0.032159 | -0.75273 | -1.3873 | -2.094 | -2.8876 | -4.0831 | -6.908 | -10.9342 | -13.6975 | -14.9255
COWLEY GSP | DRAYTON BSP | WANTAGE | MINIMUM HEADROOM | SU 41290 88304 | NO | 3.9264 | 3.145 | 2.2459 | 1.1465 | -0.020093 | -1.0842 | -1.9547 | -2.8777 | -4.1455 | -7.0272 | -10.8925 | -13.597 | -14.814 | 6.053 | 5.4923 | 4.857 | 4.0981 | 3.293 | 2.5556 | 1.9331 | 1.2683 | 0.42629 | -1.4335 | -3.5222 | -5.0502 | -6.2854 | 4.2686 | 3.6016 | 2.835 | 1.8662 | 0.83812 | -0.10277 | -0.88368 | -1.7013 | -2.8418 | -5.5041 | -9.0228 | -11.4993 | -12.5858
|  | WANTAGE | CT |  |  | 3.9264 | 3.145 | 2.2459 | 1.1465 | -0.020093 | -1.0842 | -1.9547 | -2.8777 | -4.1455 | -7.0272 | -10.8925 | -13.597 | -14.814 | 6.053 | 5.4923 | 4.857 | 4.0981 | 3.293 | 2.5556 | 1.9331 | 1.2683 | 0.42629 | -1.4335 | -3.5222 | -5.0502 | -6.2854 | 4.2686 | 3.6016 | 2.835 | 1.8662 | 0.83812 | -0.10277 | -0.88368 | -1.7013 | -2.8418 | -5.5041 | -9.0228 | -11.4993 | -12.5858
|  | WANTAGE | LW |  |  | 3.9264 | 3.145 | 2.2459 | 1.1465 | -0.020093 | -1.0842 | -1.9547 | -2.8777 | -4.1455 | -7.0272 | -10.8925 | -13.597 | -14.814 | 6.053 | 5.4923 | 4.857 | 4.0981 | 3.293 | 2.5556 | 1.9331 | 1.2683 | 0.42629 | -1.4335 | -3.5222 | -5.0502 | -6.2854 | 4.2686 | 3.6016 | 2.835 | 1.8662 | 0.83812 | -0.10277 | -0.88368 | -1.7013 | -2.8418 | -5.5041 | -9.0228 | -11.4993 | -12.5858
|  | WANTAGE | ST |  |  | 3.9264 | 3.145 | 2.2459 | 1.1465 | -0.020093 | -1.0842 | -1.9547 | -2.8777 | -4.1455 | -7.0272 | -10.8925 | -13.597 | -14.814 | 6.053 | 5.4923 | 4.857 | 4.0981 | 3.293 | 2.5556 | 1.9331 | 1.2683 | 0.42629 | -1.4335 | -3.5222 | -5.0502 | -6.2854 | 4.2686 | 3.6016 | 2.835 | 1.8662 | 0.83812 | -0.10277 | -0.88368 | -1.7013 | -2.8418 | -5.5041 | -9.0228 | -11.4993 | -12.5858
|  | WANTAGE | FS |  |  | 3.9264 | 3.145 | 2.2459 | 1.1465 | -0.020093 | -1.0842 | -1.9547 | -2.8777 | -4.1455 | -7.0272 | -10.8925 | -13.597 | -14.814 | 6.053 | 5.4923 | 4.857 | 4.0981 | 3.293 | 2.5556 | 1.9331 | 1.2683 | 0.42629 | -1.4335 | -3.5222 | -5.0502 | -6.2854 | 4.2686 | 3.6016 | 2.835 | 1.8662 | 0.83812 | -0.10277 | -0.88368 | -1.7013 | -2.8418 | -5.5041 | -9.0228 | -11.4993 | -12.5858
MANNINGTON GSP | WAREHAM | WAREHAM TOWN | MINIMUM HEADROOM | SY 92036 87463 | YES | 2.8525 | 2.6293 | 2.3956 | 2.1246 | 1.8084 | 1.4764 | 0.91724 | 0.31003 | -0.56522 | -2.7974 | -6.138 | -8.5368 | -9.6239 | 4.8838 | 4.6366 | 4.3857 | 4.1197 | 3.8396 | 3.5426 | 3.2155 | 2.8932 | 2.5704 | 1.6175 | 0.24164 | -0.79984 | -1.7059 | 3.8224 | 3.5657 | 3.2991 | 3.0164 | 2.7124 | 2.3945 | 1.9031 | 1.4009 | 0.61484 | -1.4493 | -4.3018 | -6.4187 | -7.4198
|  | WAREHAM TOWN | CT |  |  | 2.8525 | 2.6293 | 2.3956 | 2.1246 | 1.8084 | 1.4764 | 0.91724 | 0.31003 | -0.56522 | -2.7974 | -6.138 | -8.5368 | -9.6239 | 4.8838 | 4.6366 | 4.3857 | 4.1197 | 3.8396 | 3.5426 | 3.2155 | 2.8932 | 2.5704 | 1.6175 | 0.24164 | -0.79984 | -1.7059 | 3.8224 | 3.5657 | 3.2991 | 3.0164 | 2.7124 | 2.3945 | 1.9031 | 1.4009 | 0.61484 | -1.4493 | -4.3018 | -6.4187 | -7.4198
|  | WAREHAM TOWN | LW |  |  | 2.8525 | 2.6293 | 2.3956 | 2.1246 | 1.8084 | 1.4764 | 0.91724 | 0.31003 | -0.56522 | -2.7974 | -6.138 | -8.5368 | -9.6239 | 4.8838 | 4.6366 | 4.3857 | 4.1197 | 3.8396 | 3.5426 | 3.2155 | 2.8932 | 2.5704 | 1.6175 | 0.24164 | -0.79984 | -1.7059 | 3.8224 | 3.5657 | 3.2991 | 3.0164 | 2.7124 | 2.3945 | 1.9031 | 1.4009 | 0.61484 | -1.4493 | -4.3018 | -6.4187 | -7.4198
|  | WAREHAM TOWN | ST |  |  | 2.8525 | 2.6293 | 2.3956 | 2.1246 | 1.8084 | 1.4764 | 0.91724 | 0.31003 | -0.56522 | -2.7974 | -6.138 | -8.5368 | -9.6239 | 4.8838 | 4.6366 | 4.3857 | 4.1197 | 3.8396 | 3.5426 | 3.2155 | 2.8932 | 2.5704 | 1.6175 | 0.24164 | -0.79984 | -1.7059 | 3.8224 | 3.5657 | 3.2991 | 3.0164 | 2.7124 | 2.3945 | 1.9031 | 1.4009 | 0.61484 | -1.4493 | -4.3018 | -6.4187 | -7.4198
|  | WAREHAM TOWN | FS |  |  | 2.8525 | 2.6293 | 2.3956 | 2.1246 | 1.8084 | 1.4764 | 0.91724 | 0.31003 | -0.56522 | -2.7974 | -6.138 | -8.5368 | -9.6239 | 4.8838 | 4.6366 | 4.3857 | 4.1197 | 3.8396 | 3.5426 | 3.2155 | 2.8932 | 2.5704 | 1.6175 | 0.24164 | -0.79984 | -1.7059 | 3.8224 | 3.5657 | 3.2991 | 3.0164 | 2.7124 | 2.3945 | 1.9031 | 1.4009 | 0.61484 | -1.4493 | -4.3018 | -6.4187 | -7.4198
BRAMLEY (FLEE) | BRACKNELL MAIN | WARFIELD | MINIMUM HEADROOM | SU 86960 71382 | YES | 0.23112 | -0.32705 | -0.96326 | -1.9619 | -3.3777 | -5.0962 | -7.1621 | -9.3215 | -12.0495 | -18.3824 | -25.4911 | -28.5842 | -29.882 | 5.9659 | 5.546 | 5.0736 | 4.451 | 3.6009 | 2.5729 | 1.3316 | 0.0025018 | -1.6525 | -5.2253 | -9.2008 | -11.1053 | -12.6661 | 2.8411 | 2.3172 | 1.7234 | 0.83086 | -0.40326 | -1.8937 | -3.6927 | -5.5963 | -8.0311 | -13.5394 | -19.7656 | -22.4907 | -23.6242
|  | WARFIELD | CT |  |  | 0.23112 | -0.32705 | -0.96326 | -1.9619 | -3.3777 | -5.0962 | -7.1621 | -9.3215 | -12.0495 | -18.3824 | -25.4911 | -28.5842 | -29.882 | 5.9659 | 5.546 | 5.0736 | 4.451 | 3.6009 | 2.5729 | 1.3316 | 0.0025018 | -1.6525 | -5.2253 | -9.2008 | -11.1053 | -12.6661 | 2.8411 | 2.3172 | 1.7234 | 0.83086 | -0.40326 | -1.8937 | -3.6927 | -5.5963 | -8.0311 | -13.5394 | -19.7656 | -22.4907 | -23.6242
|  | WARFIELD | LW |  |  | 0.23112 | -0.32705 | -0.96326 | -1.9619 | -3.3777 | -5.0962 | -7.1621 | -9.3215 | -12.0495 | -18.3824 | -25.4911 | -28.5842 | -29.882 | 5.9659 | 5.546 | 5.0736 | 4.451 | 3.6009 | 2.5729 | 1.3316 | 0.0025018 | -1.6525 | -5.2253 | -9.2008 | -11.1053 | -12.6661 | 2.8411 | 2.3172 | 1.7234 | 0.83086 | -0.40326 | -1.8937 | -3.6927 | -5.5963 | -8.0311 | -13.5394 | -19.7656 | -22.4907 | -23.6242
|  | WARFIELD | ST |  |  | 0.23112 | -0.32705 | -0.96326 | -1.9619 | -3.3777 | -5.0962 | -7.1621 | -9.3215 | -12.0495 | -18.3824 | -25.4911 | -28.5842 | -29.882 | 5.9659 | 5.546 | 5.0736 | 4.451 | 3.6009 | 2.5729 | 1.3316 | 0.0025018 | -1.6525 | -5.2253 | -9.2008 | -11.1053 | -12.6661 | 2.8411 | 2.3172 | 1.7234 | 0.83086 | -0.40326 | -1.8937 | -3.6927 | -5.5963 | -8.0311 | -13.5394 | -19.7656 | -22.4907 | -23.6242
|  | WARFIELD | FS |  |  | 0.23112 | -0.32705 | -0.96326 | -1.9619 | -3.3777 | -5.0962 | -7.1621 | -9.3215 | -12.0495 | -18.3824 | -25.4911 | -28.5842 | -29.882 | 5.9659 | 5.546 | 5.0736 | 4.451 | 3.6009 | 2.5729 | 1.3316 | 0.0025018 | -1.6525 | -5.2253 | -9.2008 | -11.1053 | -12.6661 | 2.8411 | 2.3172 | 1.7234 | 0.83086 | -0.40326 | -1.8937 | -3.6927 | -5.5963 | -8.0311 | -13.5394 | -19.7656 | -22.4907 | -23.6242
MELKSHAM GSP | FROME BSP | WARMINSTER | MINIMUM HEADROOM | ST 84936 44551 | YES | 10.6216 | 10.3583 | 10.104 | 9.7906 | 9.4672 | 9.1337 | 8.7814 | 8.3961 | 7.7544 | 6 | 3.0957 | 0.962 | 0.0552 | 10.571 | 10.3973 | 10.2809 | 10.1675 | 10.0531 | 9.9424 | 9.7783 | 9.5357 | 9.1591 | 8.1714 | 6.797 | 5.8038 | 5.1758 | 10.6611 | 10.4757 | 10.3252 | 10.1225 | 9.9166 | 9.7104 | 9.4934 | 9.2436 | 8.6566 | 7.1039 | 4.6124 | 2.6604 | 1.831
|  | WARMINSTER | CT |  |  | 10.6216 | 10.3583 | 10.104 | 9.7906 | 9.4672 | 9.1337 | 8.7814 | 8.3961 | 7.7544 | 6 | 3.0957 | 0.962 | 0.0552 | 10.571 | 10.3973 | 10.2809 | 10.1675 | 10.0531 | 9.9424 | 9.7783 | 9.5357 | 9.1591 | 8.1714 | 6.797 | 5.8038 | 5.1758 | 10.6611 | 10.4757 | 10.3252 | 10.1225 | 9.9166 | 9.7104 | 9.4934 | 9.2436 | 8.6566 | 7.1039 | 4.6124 | 2.6604 | 1.831
|  | WARMINSTER | LW |  |  | 10.6216 | 10.3583 | 10.104 | 9.7906 | 9.4672 | 9.1337 | 8.7814 | 8.3961 | 7.7544 | 6 | 3.0957 | 0.962 | 0.0552 | 10.571 | 10.3973 | 10.2809 | 10.1675 | 10.0531 | 9.9424 | 9.7783 | 9.5357 | 9.1591 | 8.1714 | 6.797 | 5.8038 | 5.1758 | 10.6611 | 10.4757 | 10.3252 | 10.1225 | 9.9166 | 9.7104 | 9.4934 | 9.2436 | 8.6566 | 7.1039 | 4.6124 | 2.6604 | 1.831
|  | WARMINSTER | ST |  |  | 10.6216 | 10.3583 | 10.104 | 9.7906 | 9.4672 | 9.1337 | 8.7814 | 8.3961 | 7.7544 | 6 | 3.0957 | 0.962 | 0.0552 | 10.571 | 10.3973 | 10.2809 | 10.1675 | 10.0531 | 9.9424 | 9.7783 | 9.5357 | 9.1591 | 8.1714 | 6.797 | 5.8038 | 5.1758 | 10.6611 | 10.4757 | 10.3252 | 10.1225 | 9.9166 | 9.7104 | 9.4934 | 9.2436 | 8.6566 | 7.1039 | 4.6124 | 2.6604 | 1.831
|  | WARMINSTER | FS |  |  | 10.6216 | 10.3583 | 10.104 | 9.7906 | 9.4672 | 9.1337 | 8.7814 | 8.3961 | 7.7544 | 6 | 3.0957 | 0.962 | 0.0552 | 10.571 | 10.3973 | 10.2809 | 10.1675 | 10.0531 | 9.9424 | 9.7783 | 9.5357 | 9.1591 | 8.1714 | 6.797 | 5.8038 | 5.1758 | 10.6611 | 10.4757 | 10.3252 | 10.1225 | 9.9166 | 9.7104 | 9.4934 | 9.2436 | 8.6566 | 7.1039 | 4.6124 | 2.6604 | 1.831
LOVEDEAN GSP | FORT WIDLEY | WATERLOOVILLE | MINIMUM HEADROOM | SU 67988 09282 | YES | 20.4981 | 19.591 | 18.4897 | 17.0334 | 15.4521 | 13.7411 | 11.8036 | 9.5753 | 6.7593 | 0.16704 | -8.1604 | -13.9081 | -17.0664 | 28.4499 | 27.7881 | 27.0018 | 26.0737 | 25.0727 | 23.9425 | 22.6882 | 21.191 | 19.4083 | 15.3808 | 10.812 | 7.5568 | 4.842 | 27.1351 | 26.3686 | 25.4701 | 24.234 | 22.8715 | 21.3474 | 19.6404 | 17.6694 | 15.1688 | 9.2384 | 1.5744 | -3.7022 | -6.4413
|  | WATERLOOVILLE | CT |  |  | 20.4981 | 19.591 | 18.4897 | 17.0334 | 15.4521 | 13.7411 | 11.8036 | 9.5753 | 6.7593 | 0.16704 | -8.1604 | -13.9081 | -17.0664 | 28.4499 | 27.7881 | 27.0018 | 26.0737 | 25.0727 | 23.9425 | 22.6882 | 21.191 | 19.4083 | 15.3808 | 10.812 | 7.5568 | 4.842 | 27.1351 | 26.3686 | 25.4701 | 24.234 | 22.8715 | 21.3474 | 19.6404 | 17.6694 | 15.1688 | 9.2384 | 1.5744 | -3.7022 | -6.4413
|  | WATERLOOVILLE | LW |  |  | 20.4981 | 19.591 | 18.4897 | 17.0334 | 15.4521 | 13.7411 | 11.8036 | 9.5753 | 6.7593 | 0.16704 | -8.1604 | -13.9081 | -17.0664 | 28.4499 | 27.7881 | 27.0018 | 26.0737 | 25.0727 | 23.9425 | 22.6882 | 21.191 | 19.4083 | 15.3808 | 10.812 | 7.5568 | 4.842 | 27.1351 | 26.3686 | 25.4701 | 24.234 | 22.8715 | 21.3474 | 19.6404 | 17.6694 | 15.1688 | 9.2384 | 1.5744 | -3.7022 | -6.4413
|  | WATERLOOVILLE | ST |  |  | 20.4981 | 19.591 | 18.4897 | 17.0334 | 15.4521 | 13.7411 | 11.8036 | 9.5753 | 6.7593 | 0.16704 | -8.1604 | -13.9081 | -17.0664 | 28.4499 | 27.7881 | 27.0018 | 26.0737 | 25.0727 | 23.9425 | 22.6882 | 21.191 | 19.4083 | 15.3808 | 10.812 | 7.5568 | 4.842 | 27.1351 | 26.3686 | 25.4701 | 24.234 | 22.8715 | 21.3474 | 19.6404 | 17.6694 | 15.1688 | 9.2384 | 1.5744 | -3.7022 | -6.4413
|  | WATERLOOVILLE | FS |  |  | 20.4981 | 19.591 | 18.4897 | 17.0334 | 15.4521 | 13.7411 | 11.8036 | 9.5753 | 6.7593 | 0.16704 | -8.1604 | -13.9081 | -17.0664 | 28.4499 | 27.7881 | 27.0018 | 26.0737 | 25.0727 | 23.9425 | 22.6882 | 21.191 | 19.4083 | 15.3808 | 10.812 | 7.5568 | 4.842 | 27.1351 | 26.3686 | 25.4701 | 24.234 | 22.8715 | 21.3474 | 19.6404 | 17.6694 | 15.1688 | 9.2384 | 1.5744 | -3.7022 | -6.4413
COWLEY GSP | HIGH WYCOMBE BSP | WATLINGTON | MINIMUM HEADROOM | SU 69106 94287 | YES | 2.4621 | 2.1931 | 1.9556 | 1.6129 | 1.2564 | 0.86385 | 0.44695 | 0.032454 | -0.48955 | -1.4704 | -2.8964 | -3.8291 | -4.2369 | 4.758 | 4.5906 | 4.434 | 4.2467 | 4.0471 | 3.8163 | 3.5629 | 3.29 | 2.9574 | 2.4036 | 1.6701 | 1.1579 | 0.72304 | 3.4981 | 3.2582 | 3.0395 | 2.7391 | 2.4104 | 2.0459 | 1.6567 | 1.2647 | 0.7718 | -0.13254 | -1.4156 | -2.2389 | -2.6239
|  | WATLINGTON | CT |  |  | 2.4621 | 2.1931 | 1.9556 | 1.6129 | 1.2564 | 0.86385 | 0.44695 | 0.032454 | -0.48955 | -1.4704 | -2.8964 | -3.8291 | -4.2369 | 4.758 | 4.5906 | 4.434 | 4.2467 | 4.0471 | 3.8163 | 3.5629 | 3.29 | 2.9574 | 2.4036 | 1.6701 | 1.1579 | 0.72304 | 3.4981 | 3.2582 | 3.0395 | 2.7391 | 2.4104 | 2.0459 | 1.6567 | 1.2647 | 0.7718 | -0.13254 | -1.4156 | -2.2389 | -2.6239
|  | WATLINGTON | LW |  |  | 2.4621 | 2.1931 | 1.9556 | 1.6129 | 1.2564 | 0.86385 | 0.44695 | 0.032454 | -0.48955 | -1.4704 | -2.8964 | -3.8291 | -4.2369 | 4.758 | 4.5906 | 4.434 | 4.2467 | 4.0471 | 3.8163 | 3.5629 | 3.29 | 2.9574 | 2.4036 | 1.6701 | 1.1579 | 0.72304 | 3.4981 | 3.2582 | 3.0395 | 2.7391 | 2.4104 | 2.0459 | 1.6567 | 1.2647 | 0.7718 | -0.13254 | -1.4156 | -2.2389 | -2.6239
|  | WATLINGTON | ST |  |  | 2.4621 | 2.1931 | 1.9556 | 1.6129 | 1.2564 | 0.86385 | 0.44695 | 0.032454 | -0.48955 | -1.4704 | -2.8964 | -3.8291 | -4.2369 | 4.758 | 4.5906 | 4.434 | 4.2467 | 4.0471 | 3.8163 | 3.5629 | 3.29 | 2.9574 | 2.4036 | 1.6701 | 1.1579 | 0.72304 | 3.4981 | 3.2582 | 3.0395 | 2.7391 | 2.4104 | 2.0459 | 1.6567 | 1.2647 | 0.7718 | -0.13254 | -1.4156 | -2.2389 | -2.6239
|  | WATLINGTON | FS |  |  | 2.4621 | 2.1931 | 1.9556 | 1.6129 | 1.2564 | 0.86385 | 0.44695 | 0.032454 | -0.48955 | -1.4704 | -2.8964 | -3.8291 | -4.2369 | 4.758 | 4.5906 | 4.434 | 4.2467 | 4.0471 | 3.8163 | 3.5629 | 3.29 | 2.9574 | 2.4036 | 1.6701 | 1.1579 | 0.72304 | 3.4981 | 3.2582 | 3.0395 | 2.7391 | 2.4104 | 2.0459 | 1.6567 | 1.2647 | 0.7718 | -0.13254 | -1.4156 | -2.2389 | -2.6239
AMERSHAM | LOUDWATER BSP | WELL END | MINIMUM HEADROOM | SU 88511 87957 | YES | 7.2983 | 6.8202 | 6.275 | 5.6527 | 5.0011 | 4.3073 | 3.536 | 2.7102 | 1.4943 | -1.2148 | -5.4945 | -8.3343 | -9.6489 | 13.2628 | 12.9139 | 12.5178 | 12.1127 | 11.6806 | 11.2041 | 10.6682 | 10.0649 | 9.2456 | 7.5352 | 5.0649 | 3.3535 | 1.8817 | 9.9992 | 9.5458 | 9.0292 | 8.467 | 7.872 | 7.2266 | 6.5043 | 5.7077 | 4.5755 | 2.173 | -1.5921 | -3.9571 | -5.0406
|  | WELL END | CT |  |  | 7.2983 | 6.8202 | 6.275 | 5.6527 | 5.0011 | 4.3073 | 3.536 | 2.7102 | 1.4943 | -1.2148 | -5.4945 | -8.3343 | -9.6489 | 13.2628 | 12.9139 | 12.5178 | 12.1127 | 11.6806 | 11.2041 | 10.6682 | 10.0649 | 9.2456 | 7.5352 | 5.0649 | 3.3535 | 1.8817 | 9.9992 | 9.5458 | 9.0292 | 8.467 | 7.872 | 7.2266 | 6.5043 | 5.7077 | 4.5755 | 2.173 | -1.5921 | -3.9571 | -5.0406
|  | WELL END | LW |  |  | 7.2983 | 6.8202 | 6.275 | 5.6527 | 5.0011 | 4.3073 | 3.536 | 2.7102 | 1.4943 | -1.2148 | -5.4945 | -8.3343 | -9.6489 | 13.2628 | 12.9139 | 12.5178 | 12.1127 | 11.6806 | 11.2041 | 10.6682 | 10.0649 | 9.2456 | 7.5352 | 5.0649 | 3.3535 | 1.8817 | 9.9992 | 9.5458 | 9.0292 | 8.467 | 7.872 | 7.2266 | 6.5043 | 5.7077 | 4.5755 | 2.173 | -1.5921 | -3.9571 | -5.0406
|  | WELL END | ST |  |  | 7.2983 | 6.8202 | 6.275 | 5.6527 | 5.0011 | 4.3073 | 3.536 | 2.7102 | 1.4943 | -1.2148 | -5.4945 | -8.3343 | -9.6489 | 13.2628 | 12.9139 | 12.5178 | 12.1127 | 11.6806 | 11.2041 | 10.6682 | 10.0649 | 9.2456 | 7.5352 | 5.0649 | 3.3535 | 1.8817 | 9.9992 | 9.5458 | 9.0292 | 8.467 | 7.872 | 7.2266 | 6.5043 | 5.7077 | 4.5755 | 2.173 | -1.5921 | -3.9571 | -5.0406
|  | WELL END | FS |  |  | 7.2983 | 6.8202 | 6.275 | 5.6527 | 5.0011 | 4.3073 | 3.536 | 2.7102 | 1.4943 | -1.2148 | -5.4945 | -8.3343 | -9.6489 | 13.2628 | 12.9139 | 12.5178 | 12.1127 | 11.6806 | 11.2041 | 10.6682 | 10.0649 | 9.2456 | 7.5352 | 5.0649 | 3.3535 | 1.8817 | 9.9992 | 9.5458 | 9.0292 | 8.467 | 7.872 | 7.2266 | 6.5043 | 5.7077 | 4.5755 | 2.173 | -1.5921 | -3.9571 | -5.0406
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | WEST END | MINIMUM HEADROOM | SU 57216 06147 | YES | 25.8486 | 25.5839 | 25.0621 | 24.4397 | 23.7263 | 22.9455 | 22.1614 | 21.2403 | 19.7952 | 15.9642 | 10.234 | 5.9507 | 3.4668 | 19.5232 | 19.3969 | 19.229 | 19.0558 | 18.768 | 18.2794 | 17.7787 | 17.1775 | 16.2288 | 13.735 | 10.3867 | 7.8318 | 5.4428 | 25.0561 | 24.731 | 24.2592 | 23.6992 | 23.0629 | 22.3664 | 21.6364 | 20.7727 | 19.4132 | 15.8157 | 10.6713 | 6.998 | 4.8957
|  | WEST END | CT |  |  | 25.8486 | 25.5839 | 25.0621 | 24.4397 | 23.7263 | 22.9455 | 22.1614 | 21.2403 | 19.7952 | 15.9642 | 10.234 | 5.9507 | 3.4668 | 19.5232 | 19.3969 | 19.229 | 19.0558 | 18.768 | 18.2794 | 17.7787 | 17.1775 | 16.2288 | 13.735 | 10.3867 | 7.8318 | 5.4428 | 25.0561 | 24.731 | 24.2592 | 23.6992 | 23.0629 | 22.3664 | 21.6364 | 20.7727 | 19.4132 | 15.8157 | 10.6713 | 6.998 | 4.8957
|  | WEST END | LW |  |  | 25.8486 | 25.5839 | 25.0621 | 24.4397 | 23.7263 | 22.9455 | 22.1614 | 21.2403 | 19.7952 | 15.9642 | 10.234 | 5.9507 | 3.4668 | 19.5232 | 19.3969 | 19.229 | 19.0558 | 18.768 | 18.2794 | 17.7787 | 17.1775 | 16.2288 | 13.735 | 10.3867 | 7.8318 | 5.4428 | 25.0561 | 24.731 | 24.2592 | 23.6992 | 23.0629 | 22.3664 | 21.6364 | 20.7727 | 19.4132 | 15.8157 | 10.6713 | 6.998 | 4.8957
|  | WEST END | ST |  |  | 25.8486 | 25.5839 | 25.0621 | 24.4397 | 23.7263 | 22.9455 | 22.1614 | 21.2403 | 19.7952 | 15.9642 | 10.234 | 5.9507 | 3.4668 | 19.5232 | 19.3969 | 19.229 | 19.0558 | 18.768 | 18.2794 | 17.7787 | 17.1775 | 16.2288 | 13.735 | 10.3867 | 7.8318 | 5.4428 | 25.0561 | 24.731 | 24.2592 | 23.6992 | 23.0629 | 22.3664 | 21.6364 | 20.7727 | 19.4132 | 15.8157 | 10.6713 | 6.998 | 4.8957
|  | WEST END | FS |  |  | 25.8486 | 25.5839 | 25.0621 | 24.4397 | 23.7263 | 22.9455 | 22.1614 | 21.2403 | 19.7952 | 15.9642 | 10.234 | 5.9507 | 3.4668 | 19.5232 | 19.3969 | 19.229 | 19.0558 | 18.768 | 18.2794 | 17.7787 | 17.1775 | 16.2288 | 13.735 | 10.3867 | 7.8318 | 5.4428 | 25.0561 | 24.731 | 24.2592 | 23.6992 | 23.0629 | 22.3664 | 21.6364 | 20.7727 | 19.4132 | 15.8157 | 10.6713 | 6.998 | 4.8957
MELKSHAM GSP | WEST GRAFTON | WEST GRAFTON VILLAGE | MINIMUM HEADROOM | SU 24639 60279 | YES | 6.0559 | 5.899 | 5.7217 | 5.4779 | 5.2218 | 4.9484 | 4.636 | 4.2729 | 3.8047 | 2.8768 | 1.5482 | 0.74532 | 0.44226 | 8.1672 | 8.0661 | 7.9471 | 7.8097 | 7.6629 | 7.505 | 7.3164 | 7.083 | 6.7906 | 6.2918 | 5.6442 | 5.2318 | 4.9502 | 7.063 | 6.9152 | 6.7469 | 6.5209 | 6.2832 | 6.0291 | 5.7368 | 5.3937 | 4.9518 | 4.0993 | 2.9125 | 2.2058 | 1.9406
|  | WEST GRAFTON VILLAGE | CT |  |  | 6.0559 | 5.899 | 5.7217 | 5.4779 | 5.2218 | 4.9484 | 4.636 | 4.2729 | 3.8047 | 2.8768 | 1.5482 | 0.74532 | 0.44226 | 8.1672 | 8.0661 | 7.9471 | 7.8097 | 7.6629 | 7.505 | 7.3164 | 7.083 | 6.7906 | 6.2918 | 5.6442 | 5.2318 | 4.9502 | 7.063 | 6.9152 | 6.7469 | 6.5209 | 6.2832 | 6.0291 | 5.7368 | 5.3937 | 4.9518 | 4.0993 | 2.9125 | 2.2058 | 1.9406
|  | WEST GRAFTON VILLAGE | LW |  |  | 6.0559 | 5.899 | 5.7217 | 5.4779 | 5.2218 | 4.9484 | 4.636 | 4.2729 | 3.8047 | 2.8768 | 1.5482 | 0.74532 | 0.44226 | 8.1672 | 8.0661 | 7.9471 | 7.8097 | 7.6629 | 7.505 | 7.3164 | 7.083 | 6.7906 | 6.2918 | 5.6442 | 5.2318 | 4.9502 | 7.063 | 6.9152 | 6.7469 | 6.5209 | 6.2832 | 6.0291 | 5.7368 | 5.3937 | 4.9518 | 4.0993 | 2.9125 | 2.2058 | 1.9406
|  | WEST GRAFTON VILLAGE | ST |  |  | 6.0559 | 5.899 | 5.7217 | 5.4779 | 5.2218 | 4.9484 | 4.636 | 4.2729 | 3.8047 | 2.8768 | 1.5482 | 0.74532 | 0.44226 | 8.1672 | 8.0661 | 7.9471 | 7.8097 | 7.6629 | 7.505 | 7.3164 | 7.083 | 6.7906 | 6.2918 | 5.6442 | 5.2318 | 4.9502 | 7.063 | 6.9152 | 6.7469 | 6.5209 | 6.2832 | 6.0291 | 5.7368 | 5.3937 | 4.9518 | 4.0993 | 2.9125 | 2.2058 | 1.9406
|  | WEST GRAFTON VILLAGE | FS |  |  | 6.0559 | 5.899 | 5.7217 | 5.4779 | 5.2218 | 4.9484 | 4.636 | 4.2729 | 3.8047 | 2.8768 | 1.5482 | 0.74532 | 0.44226 | 8.1672 | 8.0661 | 7.9471 | 7.8097 | 7.6629 | 7.505 | 7.3164 | 7.083 | 6.7906 | 6.2918 | 5.6442 | 5.2318 | 4.9502 | 7.063 | 6.9152 | 6.7469 | 6.5209 | 6.2832 | 6.0291 | 5.7368 | 5.3937 | 4.9518 | 4.0993 | 2.9125 | 2.2058 | 1.9406
AXMINSTER | YEOVIL BSP | WEST HENDFORD | MINIMUM HEADROOM | ST 55000 15442 | YES | 27.4798 | 27.3214 | 27.115 | 26.7991 | 26.3328 | 25.7483 | 25.1681 | 24.541 | 23.7228 | 21.1131 | 18.0818 | 16.296 | 15.3812 | 30.0228 | 29.8582 | 29.6405 | 29.3654 | 29.0739 | 28.7759 | 28.4703 | 28.1282 | 27.6978 | 26.2098 | 24.2403 | 22.7517 | 21.1074 | 27.9524 | 27.7699 | 27.5412 | 27.2944 | 27.0261 | 26.7418 | 26.386 | 25.9447 | 25.3739 | 23.1428 | 20.4433 | 18.8969 | 18.1199
|  | WEST HENDFORD | CT |  |  | 27.4798 | 27.3214 | 27.115 | 26.7991 | 26.3328 | 25.7483 | 25.1681 | 24.541 | 23.7228 | 21.1131 | 18.0818 | 16.296 | 15.3812 | 30.0228 | 29.8582 | 29.6405 | 29.3654 | 29.0739 | 28.7759 | 28.4703 | 28.1282 | 27.6978 | 26.2098 | 24.2403 | 22.7517 | 21.1074 | 27.9524 | 27.7699 | 27.5412 | 27.2944 | 27.0261 | 26.7418 | 26.386 | 25.9447 | 25.3739 | 23.1428 | 20.4433 | 18.8969 | 18.1199
|  | WEST HENDFORD | LW |  |  | 27.4798 | 27.3214 | 27.115 | 26.7991 | 26.3328 | 25.7483 | 25.1681 | 24.541 | 23.7228 | 21.1131 | 18.0818 | 16.296 | 15.3812 | 30.0228 | 29.8582 | 29.6405 | 29.3654 | 29.0739 | 28.7759 | 28.4703 | 28.1282 | 27.6978 | 26.2098 | 24.2403 | 22.7517 | 21.1074 | 27.9524 | 27.7699 | 27.5412 | 27.2944 | 27.0261 | 26.7418 | 26.386 | 25.9447 | 25.3739 | 23.1428 | 20.4433 | 18.8969 | 18.1199
|  | WEST HENDFORD | ST |  |  | 27.4798 | 27.3214 | 27.115 | 26.7991 | 26.3328 | 25.7483 | 25.1681 | 24.541 | 23.7228 | 21.1131 | 18.0818 | 16.296 | 15.3812 | 30.0228 | 29.8582 | 29.6405 | 29.3654 | 29.0739 | 28.7759 | 28.4703 | 28.1282 | 27.6978 | 26.2098 | 24.2403 | 22.7517 | 21.1074 | 27.9524 | 27.7699 | 27.5412 | 27.2944 | 27.0261 | 26.7418 | 26.386 | 25.9447 | 25.3739 | 23.1428 | 20.4433 | 18.8969 | 18.1199
|  | WEST HENDFORD | FS |  |  | 27.4798 | 27.3214 | 27.115 | 26.7991 | 26.3328 | 25.7483 | 25.1681 | 24.541 | 23.7228 | 21.1131 | 18.0818 | 16.296 | 15.3812 | 30.0228 | 29.8582 | 29.6405 | 29.3654 | 29.0739 | 28.7759 | 28.4703 | 28.1282 | 27.6978 | 26.2098 | 24.2403 | 22.7517 | 21.1074 | 27.9524 | 27.7699 | 27.5412 | 27.2944 | 27.0261 | 26.7418 | 26.386 | 25.9447 | 25.3739 | 23.1428 | 20.4433 | 18.8969 | 18.1199
MANNINGTON GSP | SHAFTESBURY BSP | WEST STOUR | MINIMUM HEADROOM | ST 77699 22040 | YES | 4.1066 | 3.9897 | 3.8212 | 3.6124 | 3.3894 | 3.1415 | 2.8523 | 2.5143 | 2.0731 | 1.3102 | -0.01359 | -0.91653 | -1.2705 | 6.045 | 5.9687 | 5.8514 | 5.7225 | 5.5826 | 5.4281 | 5.2426 | 5.0183 | 4.7325 | 4.3269 | 3.7485 | 3.3537 | 3.1408 | 4.8447 | 4.7384 | 4.5955 | 4.4016 | 4.1965 | 3.9676 | 3.7072 | 3.3974 | 2.9848 | 2.2275 | 0.94274 | 0.049737 | -0.29251
|  | WEST STOUR | CT |  |  | 4.1066 | 3.9897 | 3.8212 | 3.6124 | 3.3894 | 3.1415 | 2.8523 | 2.5143 | 2.0731 | 1.3102 | -0.01359 | -0.91653 | -1.2705 | 6.045 | 5.9687 | 5.8514 | 5.7225 | 5.5826 | 5.4281 | 5.2426 | 5.0183 | 4.7325 | 4.3269 | 3.7485 | 3.3537 | 3.1408 | 4.8447 | 4.7384 | 4.5955 | 4.4016 | 4.1965 | 3.9676 | 3.7072 | 3.3974 | 2.9848 | 2.2275 | 0.94274 | 0.049737 | -0.29251
|  | WEST STOUR | LW |  |  | 4.1066 | 3.9897 | 3.8212 | 3.6124 | 3.3894 | 3.1415 | 2.8523 | 2.5143 | 2.0731 | 1.3102 | -0.01359 | -0.91653 | -1.2705 | 6.045 | 5.9687 | 5.8514 | 5.7225 | 5.5826 | 5.4281 | 5.2426 | 5.0183 | 4.7325 | 4.3269 | 3.7485 | 3.3537 | 3.1408 | 4.8447 | 4.7384 | 4.5955 | 4.4016 | 4.1965 | 3.9676 | 3.7072 | 3.3974 | 2.9848 | 2.2275 | 0.94274 | 0.049737 | -0.29251
|  | WEST STOUR | ST |  |  | 4.1066 | 3.9897 | 3.8212 | 3.6124 | 3.3894 | 3.1415 | 2.8523 | 2.5143 | 2.0731 | 1.3102 | -0.01359 | -0.91653 | -1.2705 | 6.045 | 5.9687 | 5.8514 | 5.7225 | 5.5826 | 5.4281 | 5.2426 | 5.0183 | 4.7325 | 4.3269 | 3.7485 | 3.3537 | 3.1408 | 4.8447 | 4.7384 | 4.5955 | 4.4016 | 4.1965 | 3.9676 | 3.7072 | 3.3974 | 2.9848 | 2.2275 | 0.94274 | 0.049737 | -0.29251
|  | WEST STOUR | FS |  |  | 4.1066 | 3.9897 | 3.8212 | 3.6124 | 3.3894 | 3.1415 | 2.8523 | 2.5143 | 2.0731 | 1.3102 | -0.01359 | -0.91653 | -1.2705 | 6.045 | 5.9687 | 5.8514 | 5.7225 | 5.5826 | 5.4281 | 5.2426 | 5.0183 | 4.7325 | 4.3269 | 3.7485 | 3.3537 | 3.1408 | 4.8447 | 4.7384 | 4.5955 | 4.4016 | 4.1965 | 3.9676 | 3.7072 | 3.3974 | 2.9848 | 2.2275 | 0.94274 | 0.049737 | -0.29251
MANNINGTON GSP | BOURNEMOUTH | WESTBOURNE | MINIMUM HEADROOM | SZ 07642 91485 | YES | 22.2191 | 21.8529 | 21.4053 | 20.6476 | 19.8362 | 19.0482 | 18.1928 | 17.2148 | 15.8402 | 11.6101 | 3.2939 | -3.1778 | -7.4224 | 22.6969 | 22.4053 | 22.0449 | 21.5412 | 20.9938 | 20.4299 | 19.8099 | 19.0827 | 18.1718 | 15.2733 | 9.4831 | 3.9865 | -2.3206 | 24.9773 | 24.6506 | 24.2429 | 23.5919 | 22.8903 | 22.1994 | 21.4256 | 20.5297 | 19.275 | 15.4066 | 8.0025 | 2.4775 | -1.0672
|  | WESTBOURNE | CT |  |  | 22.2191 | 21.8529 | 21.4053 | 20.6476 | 19.8362 | 19.0482 | 18.1928 | 17.2148 | 15.8402 | 11.6101 | 3.2939 | -3.1778 | -7.4224 | 22.6969 | 22.4053 | 22.0449 | 21.5412 | 20.9938 | 20.4299 | 19.8099 | 19.0827 | 18.1718 | 15.2733 | 9.4831 | 3.9865 | -2.3206 | 24.9773 | 24.6506 | 24.2429 | 23.5919 | 22.8903 | 22.1994 | 21.4256 | 20.5297 | 19.275 | 15.4066 | 8.0025 | 2.4775 | -1.0672
|  | WESTBOURNE | LW |  |  | 22.2191 | 21.8529 | 21.4053 | 20.6476 | 19.8362 | 19.0482 | 18.1928 | 17.2148 | 15.8402 | 11.6101 | 3.2939 | -3.1778 | -7.4224 | 22.6969 | 22.4053 | 22.0449 | 21.5412 | 20.9938 | 20.4299 | 19.8099 | 19.0827 | 18.1718 | 15.2733 | 9.4831 | 3.9865 | -2.3206 | 24.9773 | 24.6506 | 24.2429 | 23.5919 | 22.8903 | 22.1994 | 21.4256 | 20.5297 | 19.275 | 15.4066 | 8.0025 | 2.4775 | -1.0672
|  | WESTBOURNE | ST |  |  | 22.2191 | 21.8529 | 21.4053 | 20.6476 | 19.8362 | 19.0482 | 18.1928 | 17.2148 | 15.8402 | 11.6101 | 3.2939 | -3.1778 | -7.4224 | 22.6969 | 22.4053 | 22.0449 | 21.5412 | 20.9938 | 20.4299 | 19.8099 | 19.0827 | 18.1718 | 15.2733 | 9.4831 | 3.9865 | -2.3206 | 24.9773 | 24.6506 | 24.2429 | 23.5919 | 22.8903 | 22.1994 | 21.4256 | 20.5297 | 19.275 | 15.4066 | 8.0025 | 2.4775 | -1.0672
|  | WESTBOURNE | FS |  |  | 22.2191 | 21.8529 | 21.4053 | 20.6476 | 19.8362 | 19.0482 | 18.1928 | 17.2148 | 15.8402 | 11.6101 | 3.2939 | -3.1778 | -7.4224 | 22.6969 | 22.4053 | 22.0449 | 21.5412 | 20.9938 | 20.4299 | 19.8099 | 19.0827 | 18.1718 | 15.2733 | 9.4831 | 3.9865 | -2.3206 | 24.9773 | 24.6506 | 24.2429 | 23.5919 | 22.8903 | 22.1994 | 21.4256 | 20.5297 | 19.275 | 15.4066 | 8.0025 | 2.4775 | -1.0672
MELKSHAM GSP | FROME BSP | WESTBURY | MINIMUM HEADROOM | ST 87654 51530 | YES | 10.1501 | 9.5795 | 8.8348 | 7.9733 | 7.0719 | 6.1697 | 5.2006 | 4.0813 | 2.3706 | -1.9064 | -8.5273 | -13.326 | -15.4255 | 14.7683 | 14.3661 | 13.8392 | 13.2952 | 12.7196 | 12.1535 | 11.5446 | 10.8267 | 9.759 | 7.1845 | 3.8317 | 1.3689 | -0.47512 | 11.7474 | 11.2168 | 10.5177 | 9.7158 | 8.874 | 8.0287 | 7.1178 | 6.0571 | 4.4482 | 0.47733 | -5.3843 | -9.6139 | -11.4591
|  | WESTBURY | CT |  |  | 10.1501 | 9.5795 | 8.8348 | 7.9733 | 7.0719 | 6.1697 | 5.2006 | 4.0813 | 2.3706 | -1.9064 | -8.5273 | -13.326 | -15.4255 | 14.7683 | 14.3661 | 13.8392 | 13.2952 | 12.7196 | 12.1535 | 11.5446 | 10.8267 | 9.759 | 7.1845 | 3.8317 | 1.3689 | -0.47512 | 11.7474 | 11.2168 | 10.5177 | 9.7158 | 8.874 | 8.0287 | 7.1178 | 6.0571 | 4.4482 | 0.47733 | -5.3843 | -9.6139 | -11.4591
|  | WESTBURY | LW |  |  | 10.1501 | 9.5795 | 8.8348 | 7.9733 | 7.0719 | 6.1697 | 5.2006 | 4.0813 | 2.3706 | -1.9064 | -8.5273 | -13.326 | -15.4255 | 14.7683 | 14.3661 | 13.8392 | 13.2952 | 12.7196 | 12.1535 | 11.5446 | 10.8267 | 9.759 | 7.1845 | 3.8317 | 1.3689 | -0.47512 | 11.7474 | 11.2168 | 10.5177 | 9.7158 | 8.874 | 8.0287 | 7.1178 | 6.0571 | 4.4482 | 0.47733 | -5.3843 | -9.6139 | -11.4591
|  | WESTBURY | ST |  |  | 10.1501 | 9.5795 | 8.8348 | 7.9733 | 7.0719 | 6.1697 | 5.2006 | 4.0813 | 2.3706 | -1.9064 | -8.5273 | -13.326 | -15.4255 | 14.7683 | 14.3661 | 13.8392 | 13.2952 | 12.7196 | 12.1535 | 11.5446 | 10.8267 | 9.759 | 7.1845 | 3.8317 | 1.3689 | -0.47512 | 11.7474 | 11.2168 | 10.5177 | 9.7158 | 8.874 | 8.0287 | 7.1178 | 6.0571 | 4.4482 | 0.47733 | -5.3843 | -9.6139 | -11.4591
|  | WESTBURY | FS |  |  | 10.1501 | 9.5795 | 8.8348 | 7.9733 | 7.0719 | 6.1697 | 5.2006 | 4.0813 | 2.3706 | -1.9064 | -8.5273 | -13.326 | -15.4255 | 14.7683 | 14.3661 | 13.8392 | 13.2952 | 12.7196 | 12.1535 | 11.5446 | 10.8267 | 9.759 | 7.1845 | 3.8317 | 1.3689 | -0.47512 | 11.7474 | 11.2168 | 10.5177 | 9.7158 | 8.874 | 8.0287 | 7.1178 | 6.0571 | 4.4482 | 0.47733 | -5.3843 | -9.6139 | -11.4591
NURSLING GSP | SOUTHAMPTON (2 X 90) | WESTERN ESPLANADE | MINIMUM HEADROOM | SU 41618 12009 | YES | 43.2368 | 42.6885 | 41.7482 | 40.819 | 39.5845 | 38.553 | 37.499 | 36.3348 | 34.8609 | 30.0994 | 23.1238 | 18.5806 | 15.9519 | 38.7917 | 38.4972 | 38.1038 | 37.6874 | 37.1546 | 36.6853 | 36.1976 | 35.6529 | 35.0332 | 32.9303 | 28.6565 | 25.4834 | 22.3405 | 46.7121 | 46.3263 | 45.5822 | 44.7347 | 43.6264 | 42.6969 | 41.7426 | 40.6889 | 39.3736 | 35.4089 | 29.4234 | 25.5335 | 23.334
|  | WESTERN ESPLANADE | CT |  |  | 43.2368 | 42.6885 | 41.7482 | 40.819 | 39.5845 | 38.553 | 37.499 | 36.3348 | 34.8609 | 30.0994 | 23.1238 | 18.5806 | 15.9519 | 38.7917 | 38.4972 | 38.1038 | 37.6874 | 37.1546 | 36.6853 | 36.1976 | 35.6529 | 35.0332 | 32.9303 | 28.6565 | 25.4834 | 22.3405 | 46.7121 | 46.3263 | 45.5822 | 44.7347 | 43.6264 | 42.6969 | 41.7426 | 40.6889 | 39.3736 | 35.4089 | 29.4234 | 25.5335 | 23.334
|  | WESTERN ESPLANADE | LW |  |  | 43.2368 | 42.6885 | 41.7482 | 40.819 | 39.5845 | 38.553 | 37.499 | 36.3348 | 34.8609 | 30.0994 | 23.1238 | 18.5806 | 15.9519 | 38.7917 | 38.4972 | 38.1038 | 37.6874 | 37.1546 | 36.6853 | 36.1976 | 35.6529 | 35.0332 | 32.9303 | 28.6565 | 25.4834 | 22.3405 | 46.7121 | 46.3263 | 45.5822 | 44.7347 | 43.6264 | 42.6969 | 41.7426 | 40.6889 | 39.3736 | 35.4089 | 29.4234 | 25.5335 | 23.334
|  | WESTERN ESPLANADE | ST |  |  | 43.2368 | 42.6885 | 41.7482 | 40.819 | 39.5845 | 38.553 | 37.499 | 36.3348 | 34.8609 | 30.0994 | 23.1238 | 18.5806 | 15.9519 | 38.7917 | 38.4972 | 38.1038 | 37.6874 | 37.1546 | 36.6853 | 36.1976 | 35.6529 | 35.0332 | 32.9303 | 28.6565 | 25.4834 | 22.3405 | 46.7121 | 46.3263 | 45.5822 | 44.7347 | 43.6264 | 42.6969 | 41.7426 | 40.6889 | 39.3736 | 35.4089 | 29.4234 | 25.5335 | 23.334
|  | WESTERN ESPLANADE | FS |  |  | 43.2368 | 42.6885 | 41.7482 | 40.819 | 39.5845 | 38.553 | 37.499 | 36.3348 | 34.8609 | 30.0994 | 23.1238 | 18.5806 | 15.9519 | 38.7917 | 38.4972 | 38.1038 | 37.6874 | 37.1546 | 36.6853 | 36.1976 | 35.6529 | 35.0332 | 32.9303 | 28.6565 | 25.4834 | 22.3405 | 46.7121 | 46.3263 | 45.5822 | 44.7347 | 43.6264 | 42.6969 | 41.7426 | 40.6889 | 39.3736 | 35.4089 | 29.4234 | 25.5335 | 23.334
BOTLEY WOOD GSP | NETLEY COMMON BSP | WESTON | MINIMUM HEADROOM | SU 45207 09912 | YES | 14.0711 | 13.908 | 13.6821 | 13.3268 | 12.9511 | 12.5451 | 12.0275 | 11.442 | 10.5071 | 7.5023 | 1.9576 | -2.7612 | -5.8089 | 17.6837 | 17.5319 | 17.2834 | 16.9913 | 16.6774 | 16.3321 | 15.9577 | 15.5338 | 14.9237 | 12.9658 | 9.784 | 6.8036 | 3.8254 | 15.3681 | 15.1723 | 14.8567 | 14.4388 | 13.9932 | 13.5063 | 12.983 | 12.402 | 11.4994 | 8.6427 | 3.776 | -0.17108 | -2.6878
|  | WESTON | CT |  |  | 14.0711 | 13.908 | 13.6821 | 13.3268 | 12.9511 | 12.5451 | 12.0275 | 11.442 | 10.5071 | 7.5023 | 1.9576 | -2.7612 | -5.8089 | 17.6837 | 17.5319 | 17.2834 | 16.9913 | 16.6774 | 16.3321 | 15.9577 | 15.5338 | 14.9237 | 12.9658 | 9.784 | 6.8036 | 3.8254 | 15.3681 | 15.1723 | 14.8567 | 14.4388 | 13.9932 | 13.5063 | 12.983 | 12.402 | 11.4994 | 8.6427 | 3.776 | -0.17108 | -2.6878
|  | WESTON | LW |  |  | 14.0711 | 13.908 | 13.6821 | 13.3268 | 12.9511 | 12.5451 | 12.0275 | 11.442 | 10.5071 | 7.5023 | 1.9576 | -2.7612 | -5.8089 | 17.6837 | 17.5319 | 17.2834 | 16.9913 | 16.6774 | 16.3321 | 15.9577 | 15.5338 | 14.9237 | 12.9658 | 9.784 | 6.8036 | 3.8254 | 15.3681 | 15.1723 | 14.8567 | 14.4388 | 13.9932 | 13.5063 | 12.983 | 12.402 | 11.4994 | 8.6427 | 3.776 | -0.17108 | -2.6878
|  | WESTON | ST |  |  | 14.0711 | 13.908 | 13.6821 | 13.3268 | 12.9511 | 12.5451 | 12.0275 | 11.442 | 10.5071 | 7.5023 | 1.9576 | -2.7612 | -5.8089 | 17.6837 | 17.5319 | 17.2834 | 16.9913 | 16.6774 | 16.3321 | 15.9577 | 15.5338 | 14.9237 | 12.9658 | 9.784 | 6.8036 | 3.8254 | 15.3681 | 15.1723 | 14.8567 | 14.4388 | 13.9932 | 13.5063 | 12.983 | 12.402 | 11.4994 | 8.6427 | 3.776 | -0.17108 | -2.6878
|  | WESTON | FS |  |  | 14.0711 | 13.908 | 13.6821 | 13.3268 | 12.9511 | 12.5451 | 12.0275 | 11.442 | 10.5071 | 7.5023 | 1.9576 | -2.7612 | -5.8089 | 17.6837 | 17.5319 | 17.2834 | 16.9913 | 16.6774 | 16.3321 | 15.9577 | 15.5338 | 14.9237 | 12.9658 | 9.784 | 6.8036 | 3.8254 | 15.3681 | 15.1723 | 14.8567 | 14.4388 | 13.9932 | 13.5063 | 12.983 | 12.402 | 11.4994 | 8.6427 | 3.776 | -0.17108 | -2.6878
CHICKERELL GSP | CHICKERELL BSP | WEYMOUTH | MINIMUM HEADROOM | SY 67443 79096 | YES | 2.88 | 2.3084 | 1.4835 | -0.15691 | -1.6297 | -3.0902 | -4.5111 | -6.0698 | -8.4392 | -15.428 | -26.6711 | -34.3414 | -38.1712 | 9.6741 | 9.2547 | 8.6312 | 7.6153 | 6.6528 | 5.6463 | 4.6287 | 3.4614 | 1.8834 | -2.8772 | -10.0047 | -16.0941 | -23.1538 | 4.9297 | 4.3974 | 3.5826 | 2.1207 | 0.77944 | -0.57566 | -1.9168 | -3.4181 | -5.6455 | -12.2126 | -21.9906 | -28.3304 | -31.6241
|  | WEYMOUTH | CT |  |  | 2.88 | 2.3084 | 1.4835 | -0.15691 | -1.6297 | -3.0902 | -4.5111 | -6.0698 | -8.4392 | -15.428 | -26.6711 | -34.3414 | -38.1712 | 9.6741 | 9.2547 | 8.6312 | 7.6153 | 6.6528 | 5.6463 | 4.6287 | 3.4614 | 1.8834 | -2.8772 | -10.0047 | -16.0941 | -23.1538 | 4.9297 | 4.3974 | 3.5826 | 2.1207 | 0.77944 | -0.57566 | -1.9168 | -3.4181 | -5.6455 | -12.2126 | -21.9906 | -28.3304 | -31.6241
|  | WEYMOUTH | LW |  |  | 2.88 | 2.3084 | 1.4835 | -0.15691 | -1.6297 | -3.0902 | -4.5111 | -6.0698 | -8.4392 | -15.428 | -26.6711 | -34.3414 | -38.1712 | 9.6741 | 9.2547 | 8.6312 | 7.6153 | 6.6528 | 5.6463 | 4.6287 | 3.4614 | 1.8834 | -2.8772 | -10.0047 | -16.0941 | -23.1538 | 4.9297 | 4.3974 | 3.5826 | 2.1207 | 0.77944 | -0.57566 | -1.9168 | -3.4181 | -5.6455 | -12.2126 | -21.9906 | -28.3304 | -31.6241
|  | WEYMOUTH | ST |  |  | 2.88 | 2.3084 | 1.4835 | -0.15691 | -1.6297 | -3.0902 | -4.5111 | -6.0698 | -8.4392 | -15.428 | -26.6711 | -34.3414 | -38.1712 | 9.6741 | 9.2547 | 8.6312 | 7.6153 | 6.6528 | 5.6463 | 4.6287 | 3.4614 | 1.8834 | -2.8772 | -10.0047 | -16.0941 | -23.1538 | 4.9297 | 4.3974 | 3.5826 | 2.1207 | 0.77944 | -0.57566 | -1.9168 | -3.4181 | -5.6455 | -12.2126 | -21.9906 | -28.3304 | -31.6241
|  | WEYMOUTH | FS |  |  | 2.88 | 2.3084 | 1.4835 | -0.15691 | -1.6297 | -3.0902 | -4.5111 | -6.0698 | -8.4392 | -15.428 | -26.6711 | -34.3414 | -38.1712 | 9.6741 | 9.2547 | 8.6312 | 7.6153 | 6.6528 | 5.6463 | 4.6287 | 3.4614 | 1.8834 | -2.8772 | -10.0047 | -16.0941 | -23.1538 | 4.9297 | 4.3974 | 3.5826 | 2.1207 | 0.77944 | -0.57566 | -1.9168 | -3.4181 | -5.6455 | -12.2126 | -21.9906 | -28.3304 | -31.6241
COWLEY GSP | HEADINGTON BSP | WHEATLEY | MINIMUM HEADROOM | SP 60777 05379 | NO | 9.1287 | 8.7204 | 8.2595 | 7.6619 | 7.0352 | 6.5533 | 6.0103 | 5.3718 | 4.4536 | 2.2217 | -1.264 | -3.2859 | -4.1265 | 10.1118 | 9.8385 | 9.5242 | 9.1772 | 8.8061 | 8.4936 | 8.1257 | 7.6618 | 7.0468 | 5.7403 | 3.8429 | 2.8722 | 2.2495 | 9.9155 | 9.524 | 9.076 | 8.5248 | 7.9415 | 7.4682 | 6.9247 | 6.2667 | 5.3528 | 3.2682 | 0.20521 | -1.4548 | -2.1629
|  | WHEATLEY | CT |  |  | 9.1287 | 8.7204 | 8.2595 | 7.6619 | 7.0352 | 6.5533 | 6.0103 | 5.3718 | 4.4536 | 2.2217 | -1.264 | -3.2859 | -4.1265 | 10.1118 | 9.8385 | 9.5242 | 9.1772 | 8.8061 | 8.4936 | 8.1257 | 7.6618 | 7.0468 | 5.7403 | 3.8429 | 2.8722 | 2.2495 | 9.9155 | 9.524 | 9.076 | 8.5248 | 7.9415 | 7.4682 | 6.9247 | 6.2667 | 5.3528 | 3.2682 | 0.20521 | -1.4548 | -2.1629
|  | WHEATLEY | LW |  |  | 9.1287 | 8.7204 | 8.2595 | 7.6619 | 7.0352 | 6.5533 | 6.0103 | 5.3718 | 4.4536 | 2.2217 | -1.264 | -3.2859 | -4.1265 | 10.1118 | 9.8385 | 9.5242 | 9.1772 | 8.8061 | 8.4936 | 8.1257 | 7.6618 | 7.0468 | 5.7403 | 3.8429 | 2.8722 | 2.2495 | 9.9155 | 9.524 | 9.076 | 8.5248 | 7.9415 | 7.4682 | 6.9247 | 6.2667 | 5.3528 | 3.2682 | 0.20521 | -1.4548 | -2.1629
|  | WHEATLEY | ST |  |  | 9.1287 | 8.7204 | 8.2595 | 7.6619 | 7.0352 | 6.5533 | 6.0103 | 5.3718 | 4.4536 | 2.2217 | -1.264 | -3.2859 | -4.1265 | 10.1118 | 9.8385 | 9.5242 | 9.1772 | 8.8061 | 8.4936 | 8.1257 | 7.6618 | 7.0468 | 5.7403 | 3.8429 | 2.8722 | 2.2495 | 9.9155 | 9.524 | 9.076 | 8.5248 | 7.9415 | 7.4682 | 6.9247 | 6.2667 | 5.3528 | 3.2682 | 0.20521 | -1.4548 | -2.1629
|  | WHEATLEY | FS |  |  | 9.1287 | 8.7204 | 8.2595 | 7.6619 | 7.0352 | 6.5533 | 6.0103 | 5.3718 | 4.4536 | 2.2217 | -1.264 | -3.2859 | -4.1265 | 10.1118 | 9.8385 | 9.5242 | 9.1772 | 8.8061 | 8.4936 | 8.1257 | 7.6618 | 7.0468 | 5.7403 | 3.8429 | 2.8722 | 2.2495 | 9.9155 | 9.524 | 9.076 | 8.5248 | 7.9415 | 7.4682 | 6.9247 | 6.2667 | 5.3528 | 3.2682 | 0.20521 | -1.4548 | -2.1629
BRAMLEY (ANDO-THAT) | ANDOVER BSP | WHITCHURCH | MINIMUM HEADROOM | SU 45924 48466 | YES | 3.3731 | 3.242 | 3.1013 | 2.9123 | 2.7164 | 2.5121 | 2.2828 | 2.0294 | 1.6041 | 0.5241 | -1.1935 | -2.404 | -2.9427 | 5.1254 | 5.0612 | 4.9996 | 4.9404 | 4.8804 | 4.7893 | 4.6257 | 4.4399 | 4.1603 | 3.4808 | 2.4882 | 1.6457 | 0.78199 | 4.4523 | 4.3275 | 4.1928 | 4.016 | 3.8324 | 3.6399 | 3.423 | 3.1821 | 2.7811 | 1.7752 | 0.22201 | -0.80556 | -1.2507
|  | WHITCHURCH | CT |  |  | 3.3731 | 3.242 | 3.1013 | 2.9123 | 2.7164 | 2.5121 | 2.2828 | 2.0294 | 1.6041 | 0.5241 | -1.1935 | -2.404 | -2.9427 | 5.1254 | 5.0612 | 4.9996 | 4.9404 | 4.8804 | 4.7893 | 4.6257 | 4.4399 | 4.1603 | 3.4808 | 2.4882 | 1.6457 | 0.78199 | 4.4523 | 4.3275 | 4.1928 | 4.016 | 3.8324 | 3.6399 | 3.423 | 3.1821 | 2.7811 | 1.7752 | 0.22201 | -0.80556 | -1.2507
|  | WHITCHURCH | LW |  |  | 3.3731 | 3.242 | 3.1013 | 2.9123 | 2.7164 | 2.5121 | 2.2828 | 2.0294 | 1.6041 | 0.5241 | -1.1935 | -2.404 | -2.9427 | 5.1254 | 5.0612 | 4.9996 | 4.9404 | 4.8804 | 4.7893 | 4.6257 | 4.4399 | 4.1603 | 3.4808 | 2.4882 | 1.6457 | 0.78199 | 4.4523 | 4.3275 | 4.1928 | 4.016 | 3.8324 | 3.6399 | 3.423 | 3.1821 | 2.7811 | 1.7752 | 0.22201 | -0.80556 | -1.2507
|  | WHITCHURCH | ST |  |  | 3.3731 | 3.242 | 3.1013 | 2.9123 | 2.7164 | 2.5121 | 2.2828 | 2.0294 | 1.6041 | 0.5241 | -1.1935 | -2.404 | -2.9427 | 5.1254 | 5.0612 | 4.9996 | 4.9404 | 4.8804 | 4.7893 | 4.6257 | 4.4399 | 4.1603 | 3.4808 | 2.4882 | 1.6457 | 0.78199 | 4.4523 | 4.3275 | 4.1928 | 4.016 | 3.8324 | 3.6399 | 3.423 | 3.1821 | 2.7811 | 1.7752 | 0.22201 | -0.80556 | -1.2507
|  | WHITCHURCH | FS |  |  | 3.3731 | 3.242 | 3.1013 | 2.9123 | 2.7164 | 2.5121 | 2.2828 | 2.0294 | 1.6041 | 0.5241 | -1.1935 | -2.404 | -2.9427 | 5.1254 | 5.0612 | 4.9996 | 4.9404 | 4.8804 | 4.7893 | 4.6257 | 4.4399 | 4.1603 | 3.4808 | 2.4882 | 1.6457 | 0.78199 | 4.4523 | 4.3275 | 4.1928 | 4.016 | 3.8324 | 3.6399 | 3.423 | 3.1821 | 2.7811 | 1.7752 | 0.22201 | -0.80556 | -1.2507
BOTLEY WOOD GSP | BOTLEY WOOD BSP | WHITELEY | MINIMUM HEADROOM | SU 52936 08794 | NO | 17.8721 | 17.2754 | 16.3866 | 15.4212 | 14.4083 | 13.3919 | 12.293 | 11.1352 | 9.7961 | 6.9755 | 3.1608 | 1.2595 | 0.36631 | 16.6874 | 16.2113 | 15.7763 | 15.3718 | 14.9475 | 14.5229 | 13.9843 | 13.3045 | 12.5281 | 10.8704 | 8.5536 | 7.3329 | 6.3838 | 18.6018 | 18.0877 | 17.404 | 16.5958 | 15.7305 | 14.8614 | 13.9177 | 12.9161 | 11.7359 | 9.208 | 5.704 | 3.9512 | 3.1386
|  | WHITELEY | CT |  |  | 17.8721 | 17.2754 | 16.3866 | 15.4212 | 14.4083 | 13.3919 | 12.293 | 11.1352 | 9.7961 | 6.9755 | 3.1608 | 1.2595 | 0.36631 | 16.6874 | 16.2113 | 15.7763 | 15.3718 | 14.9475 | 14.5229 | 13.9843 | 13.3045 | 12.5281 | 10.8704 | 8.5536 | 7.3329 | 6.3838 | 18.6018 | 18.0877 | 17.404 | 16.5958 | 15.7305 | 14.8614 | 13.9177 | 12.9161 | 11.7359 | 9.208 | 5.704 | 3.9512 | 3.1386
|  | WHITELEY | LW |  |  | 17.8721 | 17.2754 | 16.3866 | 15.4212 | 14.4083 | 13.3919 | 12.293 | 11.1352 | 9.7961 | 6.9755 | 3.1608 | 1.2595 | 0.36631 | 16.6874 | 16.2113 | 15.7763 | 15.3718 | 14.9475 | 14.5229 | 13.9843 | 13.3045 | 12.5281 | 10.8704 | 8.5536 | 7.3329 | 6.3838 | 18.6018 | 18.0877 | 17.404 | 16.5958 | 15.7305 | 14.8614 | 13.9177 | 12.9161 | 11.7359 | 9.208 | 5.704 | 3.9512 | 3.1386
|  | WHITELEY | ST |  |  | 17.8721 | 17.2754 | 16.3866 | 15.4212 | 14.4083 | 13.3919 | 12.293 | 11.1352 | 9.7961 | 6.9755 | 3.1608 | 1.2595 | 0.36631 | 16.6874 | 16.2113 | 15.7763 | 15.3718 | 14.9475 | 14.5229 | 13.9843 | 13.3045 | 12.5281 | 10.8704 | 8.5536 | 7.3329 | 6.3838 | 18.6018 | 18.0877 | 17.404 | 16.5958 | 15.7305 | 14.8614 | 13.9177 | 12.9161 | 11.7359 | 9.208 | 5.704 | 3.9512 | 3.1386
|  | WHITELEY | FS |  |  | 17.8721 | 17.2754 | 16.3866 | 15.4212 | 14.4083 | 13.3919 | 12.293 | 11.1352 | 9.7961 | 6.9755 | 3.1608 | 1.2595 | 0.36631 | 16.6874 | 16.2113 | 15.7763 | 15.3718 | 14.9475 | 14.5229 | 13.9843 | 13.3045 | 12.5281 | 10.8704 | 8.5536 | 7.3329 | 6.3838 | 18.6018 | 18.0877 | 17.404 | 16.5958 | 15.7305 | 14.8614 | 13.9177 | 12.9161 | 11.7359 | 9.208 | 5.704 | 3.9512 | 3.1386
BRAMLEY (FLEE) | BURGHFIELD MAIN | WHITLEY WOOD | MINIMUM HEADROOM | SU 72812 69667 | YES | 18.3949 | 18.0885 | 17.6309 | 16.9657 | 16.3554 | 15.7506 | 15.0833 | 14.313 | 13.0802 | 10.0575 | 4.4713 | 0.61038 | -0.20855 | 22.4302 | 22.2368 | 21.9509 | 21.5857 | 21.2452 | 20.8994 | 20.5122 | 20.0508 | 19.3589 | 17.7483 | 15.1328 | 13.3164 | 12.4443 | 20.0312 | 19.738 | 19.311 | 18.7078 | 18.1447 | 17.5808 | 16.9568 | 16.2314 | 15.0834 | 12.3157 | 7.566 | 4.2579 | 3.5718
|  | WHITLEY WOOD | CT |  |  | 18.3949 | 18.0885 | 17.6309 | 16.9657 | 16.3554 | 15.7506 | 15.0833 | 14.313 | 13.0802 | 10.0575 | 4.4713 | 0.61038 | -0.20855 | 22.4302 | 22.2368 | 21.9509 | 21.5857 | 21.2452 | 20.8994 | 20.5122 | 20.0508 | 19.3589 | 17.7483 | 15.1328 | 13.3164 | 12.4443 | 20.0312 | 19.738 | 19.311 | 18.7078 | 18.1447 | 17.5808 | 16.9568 | 16.2314 | 15.0834 | 12.3157 | 7.566 | 4.2579 | 3.5718
|  | WHITLEY WOOD | LW |  |  | 18.3949 | 18.0885 | 17.6309 | 16.9657 | 16.3554 | 15.7506 | 15.0833 | 14.313 | 13.0802 | 10.0575 | 4.4713 | 0.61038 | -0.20855 | 22.4302 | 22.2368 | 21.9509 | 21.5857 | 21.2452 | 20.8994 | 20.5122 | 20.0508 | 19.3589 | 17.7483 | 15.1328 | 13.3164 | 12.4443 | 20.0312 | 19.738 | 19.311 | 18.7078 | 18.1447 | 17.5808 | 16.9568 | 16.2314 | 15.0834 | 12.3157 | 7.566 | 4.2579 | 3.5718
|  | WHITLEY WOOD | ST |  |  | 18.3949 | 18.0885 | 17.6309 | 16.9657 | 16.3554 | 15.7506 | 15.0833 | 14.313 | 13.0802 | 10.0575 | 4.4713 | 0.61038 | -0.20855 | 22.4302 | 22.2368 | 21.9509 | 21.5857 | 21.2452 | 20.8994 | 20.5122 | 20.0508 | 19.3589 | 17.7483 | 15.1328 | 13.3164 | 12.4443 | 20.0312 | 19.738 | 19.311 | 18.7078 | 18.1447 | 17.5808 | 16.9568 | 16.2314 | 15.0834 | 12.3157 | 7.566 | 4.2579 | 3.5718
|  | WHITLEY WOOD | FS |  |  | 18.3949 | 18.0885 | 17.6309 | 16.9657 | 16.3554 | 15.7506 | 15.0833 | 14.313 | 13.0802 | 10.0575 | 4.4713 | 0.61038 | -0.20855 | 22.4302 | 22.2368 | 21.9509 | 21.5857 | 21.2452 | 20.8994 | 20.5122 | 20.0508 | 19.3589 | 17.7483 | 15.1328 | 13.3164 | 12.4443 | 20.0312 | 19.738 | 19.311 | 18.7078 | 18.1447 | 17.5808 | 16.9568 | 16.2314 | 15.0834 | 12.3157 | 7.566 | 4.2579 | 3.5718
MINETY GSP | CIRENCESTER BSP | WHITEWAY | MINIMUM HEADROOM | SP 02076 03059 | YES | 29.0176 | 28.6302 | 28.1669 | 27.5114 | 26.8047 | 26.0516 | 25.2372 | 24.3434 | 22.9389 | 19.5267 | 13.6928 | 9.11 | 6.3923 | 25.8268 | 25.4998 | 25.1082 | 24.6575 | 24.1679 | 23.6517 | 23.0896 | 22.451 | 21.5252 | 19.4021 | 16.1568 | 13.5642 | 11.3655 | 29.053 | 28.6389 | 28.1409 | 27.5025 | 26.8091 | 26.095 | 25.3344 | 24.4893 | 23.1654 | 20.0079 | 14.8336 | 10.9429 | 8.7693
|  | WHITEWAY | CT |  |  | 29.0176 | 28.6302 | 28.1669 | 27.5114 | 26.8047 | 26.0516 | 25.2372 | 24.3434 | 22.9389 | 19.5267 | 13.6928 | 9.11 | 6.3923 | 25.8268 | 25.4998 | 25.1082 | 24.6575 | 24.1679 | 23.6517 | 23.0896 | 22.451 | 21.5252 | 19.4021 | 16.1568 | 13.5642 | 11.3655 | 29.053 | 28.6389 | 28.1409 | 27.5025 | 26.8091 | 26.095 | 25.3344 | 24.4893 | 23.1654 | 20.0079 | 14.8336 | 10.9429 | 8.7693
|  | WHITEWAY | LW |  |  | 29.0176 | 28.6302 | 28.1669 | 27.5114 | 26.8047 | 26.0516 | 25.2372 | 24.3434 | 22.9389 | 19.5267 | 13.6928 | 9.11 | 6.3923 | 25.8268 | 25.4998 | 25.1082 | 24.6575 | 24.1679 | 23.6517 | 23.0896 | 22.451 | 21.5252 | 19.4021 | 16.1568 | 13.5642 | 11.3655 | 29.053 | 28.6389 | 28.1409 | 27.5025 | 26.8091 | 26.095 | 25.3344 | 24.4893 | 23.1654 | 20.0079 | 14.8336 | 10.9429 | 8.7693
|  | WHITEWAY | ST |  |  | 29.0176 | 28.6302 | 28.1669 | 27.5114 | 26.8047 | 26.0516 | 25.2372 | 24.3434 | 22.9389 | 19.5267 | 13.6928 | 9.11 | 6.3923 | 25.8268 | 25.4998 | 25.1082 | 24.6575 | 24.1679 | 23.6517 | 23.0896 | 22.451 | 21.5252 | 19.4021 | 16.1568 | 13.5642 | 11.3655 | 29.053 | 28.6389 | 28.1409 | 27.5025 | 26.8091 | 26.095 | 25.3344 | 24.4893 | 23.1654 | 20.0079 | 14.8336 | 10.9429 | 8.7693
|  | WHITEWAY | FS |  |  | 29.0176 | 28.6302 | 28.1669 | 27.5114 | 26.8047 | 26.0516 | 25.2372 | 24.3434 | 22.9389 | 19.5267 | 13.6928 | 9.11 | 6.3923 | 25.8268 | 25.4998 | 25.1082 | 24.6575 | 24.1679 | 23.6517 | 23.0896 | 22.451 | 21.5252 | 19.4021 | 16.1568 | 13.5642 | 11.3655 | 29.053 | 28.6389 | 28.1409 | 27.5025 | 26.8091 | 26.095 | 25.3344 | 24.4893 | 23.1654 | 20.0079 | 14.8336 | 10.9429 | 8.7693
BRAMLEY (FLEE) | BURGHFIELD MAIN | WILSON ROAD | MINIMUM HEADROOM | SU 69235 73304 | YES | 11.2753 | 10.9228 | 10.4563 | 9.8661 | 9.2505 | 8.6184 | 7.9372 | 7.173 | 6.0028 | 2.2367 | -4.4708 | -9.1792 | -11.959 | 17.1575 | 16.8986 | 16.5474 | 16.1503 | 15.7272 | 15.2742 | 14.7788 | 14.2072 | 13.4362 | 10.8918 | 6.4127 | 2.4951 | -1.8904 | 13.2494 | 12.9382 | 12.5126 | 11.991 | 11.4424 | 10.8726 | 10.2563 | 9.5556 | 8.511 | 5.1452 | -0.84006 | -4.9068 | -7.1631
|  | WILSON ROAD | CT |  |  | 11.2753 | 10.9228 | 10.4563 | 9.8661 | 9.2505 | 8.6184 | 7.9372 | 7.173 | 6.0028 | 2.2367 | -4.4708 | -9.1792 | -11.959 | 17.1575 | 16.8986 | 16.5474 | 16.1503 | 15.7272 | 15.2742 | 14.7788 | 14.2072 | 13.4362 | 10.8918 | 6.4127 | 2.4951 | -1.8904 | 13.2494 | 12.9382 | 12.5126 | 11.991 | 11.4424 | 10.8726 | 10.2563 | 9.5556 | 8.511 | 5.1452 | -0.84006 | -4.9068 | -7.1631
|  | WILSON ROAD | LW |  |  | 11.2753 | 10.9228 | 10.4563 | 9.8661 | 9.2505 | 8.6184 | 7.9372 | 7.173 | 6.0028 | 2.2367 | -4.4708 | -9.1792 | -11.959 | 17.1575 | 16.8986 | 16.5474 | 16.1503 | 15.7272 | 15.2742 | 14.7788 | 14.2072 | 13.4362 | 10.8918 | 6.4127 | 2.4951 | -1.8904 | 13.2494 | 12.9382 | 12.5126 | 11.991 | 11.4424 | 10.8726 | 10.2563 | 9.5556 | 8.511 | 5.1452 | -0.84006 | -4.9068 | -7.1631
|  | WILSON ROAD | ST |  |  | 11.2753 | 10.9228 | 10.4563 | 9.8661 | 9.2505 | 8.6184 | 7.9372 | 7.173 | 6.0028 | 2.2367 | -4.4708 | -9.1792 | -11.959 | 17.1575 | 16.8986 | 16.5474 | 16.1503 | 15.7272 | 15.2742 | 14.7788 | 14.2072 | 13.4362 | 10.8918 | 6.4127 | 2.4951 | -1.8904 | 13.2494 | 12.9382 | 12.5126 | 11.991 | 11.4424 | 10.8726 | 10.2563 | 9.5556 | 8.511 | 5.1452 | -0.84006 | -4.9068 | -7.1631
|  | WILSON ROAD | FS |  |  | 11.2753 | 10.9228 | 10.4563 | 9.8661 | 9.2505 | 8.6184 | 7.9372 | 7.173 | 6.0028 | 2.2367 | -4.4708 | -9.1792 | -11.959 | 17.1575 | 16.8986 | 16.5474 | 16.1503 | 15.7272 | 15.2742 | 14.7788 | 14.2072 | 13.4362 | 10.8918 | 6.4127 | 2.4951 | -1.8904 | 13.2494 | 12.9382 | 12.5126 | 11.991 | 11.4424 | 10.8726 | 10.2563 | 9.5556 | 8.511 | 5.1452 | -0.84006 | -4.9068 | -7.1631
MANNINGTON GSP | MANNINGTON BSP | WIMBORNE | MINIMUM HEADROOM | SZ 02014 99989 | YES | 7.0716 | 5.9588 | 4.77 | 3.6039 | 2.4108 | 1.1308 | -0.33966 | -2.0223 | -4.2803 | -9.7882 | -18.217 | -23.6512 | -26.0863 | 12.0567 | 11.3704 | 10.6219 | 9.9208 | 9.1668 | 8.3453 | 7.3883 | 6.2693 | 4.8271 | 1.5014 | -3.1313 | -5.9371 | -8.0228 | 8.7297 | 7.7925 | 6.7744 | 5.7415 | 4.6803 | 3.5425 | 2.2386 | 0.7442 | -1.2911 | -6.3227 | -14.1716 | -19.0059 | -21.1351
|  | WIMBORNE | CT |  |  | 7.0716 | 5.9588 | 4.77 | 3.6039 | 2.4108 | 1.1308 | -0.33966 | -2.0223 | -4.2803 | -9.7882 | -18.217 | -23.6512 | -26.0863 | 12.0567 | 11.3704 | 10.6219 | 9.9208 | 9.1668 | 8.3453 | 7.3883 | 6.2693 | 4.8271 | 1.5014 | -3.1313 | -5.9371 | -8.0228 | 8.7297 | 7.7925 | 6.7744 | 5.7415 | 4.6803 | 3.5425 | 2.2386 | 0.7442 | -1.2911 | -6.3227 | -14.1716 | -19.0059 | -21.1351
|  | WIMBORNE | LW |  |  | 7.0716 | 5.9588 | 4.77 | 3.6039 | 2.4108 | 1.1308 | -0.33966 | -2.0223 | -4.2803 | -9.7882 | -18.217 | -23.6512 | -26.0863 | 12.0567 | 11.3704 | 10.6219 | 9.9208 | 9.1668 | 8.3453 | 7.3883 | 6.2693 | 4.8271 | 1.5014 | -3.1313 | -5.9371 | -8.0228 | 8.7297 | 7.7925 | 6.7744 | 5.7415 | 4.6803 | 3.5425 | 2.2386 | 0.7442 | -1.2911 | -6.3227 | -14.1716 | -19.0059 | -21.1351
|  | WIMBORNE | ST |  |  | 7.0716 | 5.9588 | 4.77 | 3.6039 | 2.4108 | 1.1308 | -0.33966 | -2.0223 | -4.2803 | -9.7882 | -18.217 | -23.6512 | -26.0863 | 12.0567 | 11.3704 | 10.6219 | 9.9208 | 9.1668 | 8.3453 | 7.3883 | 6.2693 | 4.8271 | 1.5014 | -3.1313 | -5.9371 | -8.0228 | 8.7297 | 7.7925 | 6.7744 | 5.7415 | 4.6803 | 3.5425 | 2.2386 | 0.7442 | -1.2911 | -6.3227 | -14.1716 | -19.0059 | -21.1351
|  | WIMBORNE | FS |  |  | 7.0716 | 5.9588 | 4.77 | 3.6039 | 2.4108 | 1.1308 | -0.33966 | -2.0223 | -4.2803 | -9.7882 | -18.217 | -23.6512 | -26.0863 | 12.0567 | 11.3704 | 10.6219 | 9.9208 | 9.1668 | 8.3453 | 7.3883 | 6.2693 | 4.8271 | 1.5014 | -3.1313 | -5.9371 | -8.0228 | 8.7297 | 7.7925 | 6.7744 | 5.7415 | 4.6803 | 3.5425 | 2.2386 | 0.7442 | -1.2911 | -6.3227 | -14.1716 | -19.0059 | -21.1351
MANNINGTON GSP | MANNINGTON BSP | WIMBORNE ST GILES | MINIMUM HEADROOM | SU 03028 12678 | YES | 0.37452 | 0.36554 | 0.33275 | 0.28932 | 0.24413 | 0.18774 | 0.12376 | 0.051806 | -0.033518 | -0.23034 | -0.54392 | -0.70494 | -0.77145 | 0.64615 | 0.62865 | 0.60558 | 0.5791 | 0.55126 | 0.5175 | 0.47788 | 0.43141 | 0.37781 | 0.26682 | 0.10029 | 0.023053 | -0.025437 | 0.50937 | 0.48849 | 0.46364 | 0.42826 | 0.39161 | 0.34546 | 0.29409 | 0.23803 | 0.17062 | -0.00013922 | -0.28975 | -0.43996 | -0.5005
|  | WIMBORNE ST GILES | CT |  |  | 0.37452 | 0.36554 | 0.33275 | 0.28932 | 0.24413 | 0.18774 | 0.12376 | 0.051806 | -0.033518 | -0.23034 | -0.54392 | -0.70494 | -0.77145 | 0.64615 | 0.62865 | 0.60558 | 0.5791 | 0.55126 | 0.5175 | 0.47788 | 0.43141 | 0.37781 | 0.26682 | 0.10029 | 0.023053 | -0.025437 | 0.50937 | 0.48849 | 0.46364 | 0.42826 | 0.39161 | 0.34546 | 0.29409 | 0.23803 | 0.17062 | -0.00013922 | -0.28975 | -0.43996 | -0.5005
|  | WIMBORNE ST GILES | LW |  |  | 0.37452 | 0.36554 | 0.33275 | 0.28932 | 0.24413 | 0.18774 | 0.12376 | 0.051806 | -0.033518 | -0.23034 | -0.54392 | -0.70494 | -0.77145 | 0.64615 | 0.62865 | 0.60558 | 0.5791 | 0.55126 | 0.5175 | 0.47788 | 0.43141 | 0.37781 | 0.26682 | 0.10029 | 0.023053 | -0.025437 | 0.50937 | 0.48849 | 0.46364 | 0.42826 | 0.39161 | 0.34546 | 0.29409 | 0.23803 | 0.17062 | -0.00013922 | -0.28975 | -0.43996 | -0.5005
|  | WIMBORNE ST GILES | ST |  |  | 0.37452 | 0.36554 | 0.33275 | 0.28932 | 0.24413 | 0.18774 | 0.12376 | 0.051806 | -0.033518 | -0.23034 | -0.54392 | -0.70494 | -0.77145 | 0.64615 | 0.62865 | 0.60558 | 0.5791 | 0.55126 | 0.5175 | 0.47788 | 0.43141 | 0.37781 | 0.26682 | 0.10029 | 0.023053 | -0.025437 | 0.50937 | 0.48849 | 0.46364 | 0.42826 | 0.39161 | 0.34546 | 0.29409 | 0.23803 | 0.17062 | -0.00013922 | -0.28975 | -0.43996 | -0.5005
|  | WIMBORNE ST GILES | FS |  |  | 0.37452 | 0.36554 | 0.33275 | 0.28932 | 0.24413 | 0.18774 | 0.12376 | 0.051806 | -0.033518 | -0.23034 | -0.54392 | -0.70494 | -0.77145 | 0.64615 | 0.62865 | 0.60558 | 0.5791 | 0.55126 | 0.5175 | 0.47788 | 0.43141 | 0.37781 | 0.26682 | 0.10029 | 0.023053 | -0.025437 | 0.50937 | 0.48849 | 0.46364 | 0.42826 | 0.39161 | 0.34546 | 0.29409 | 0.23803 | 0.17062 | -0.00013922 | -0.28975 | -0.43996 | -0.5005
MANNINGTON GSP | SHAFTESBURY BSP | WINCANTON | MINIMUM HEADROOM | ST 71286 27802 | YES | 9.6132 | 9.2929 | 8.8962 | 8.4332 | 7.953 | 7.4483 | 6.9508 | 6.4047 | 5.6707 | 3.8157 | 1.1133 | -0.36697 | -0.98043 | 9.6936 | 9.5188 | 9.3495 | 9.202 | 9.0589 | 8.9062 | 8.7507 | 8.5633 | 8.2759 | 7.1776 | 5.6779 | 4.8434 | 4.2691 | 12.0746 | 11.7897 | 11.4526 | 11.0455 | 10.6267 | 10.1825 | 9.7196 | 9.205 | 8.5141 | 6.7861 | 4.3137 | 2.8912 | 2.2875
|  | WINCANTON | CT |  |  | 9.6132 | 9.2929 | 8.8962 | 8.4332 | 7.953 | 7.4483 | 6.9508 | 6.4047 | 5.6707 | 3.8157 | 1.1133 | -0.36697 | -0.98043 | 9.6936 | 9.5188 | 9.3495 | 9.202 | 9.0589 | 8.9062 | 8.7507 | 8.5633 | 8.2759 | 7.1776 | 5.6779 | 4.8434 | 4.2691 | 12.0746 | 11.7897 | 11.4526 | 11.0455 | 10.6267 | 10.1825 | 9.7196 | 9.205 | 8.5141 | 6.7861 | 4.3137 | 2.8912 | 2.2875
|  | WINCANTON | LW |  |  | 9.6132 | 9.2929 | 8.8962 | 8.4332 | 7.953 | 7.4483 | 6.9508 | 6.4047 | 5.6707 | 3.8157 | 1.1133 | -0.36697 | -0.98043 | 9.6936 | 9.5188 | 9.3495 | 9.202 | 9.0589 | 8.9062 | 8.7507 | 8.5633 | 8.2759 | 7.1776 | 5.6779 | 4.8434 | 4.2691 | 12.0746 | 11.7897 | 11.4526 | 11.0455 | 10.6267 | 10.1825 | 9.7196 | 9.205 | 8.5141 | 6.7861 | 4.3137 | 2.8912 | 2.2875
|  | WINCANTON | ST |  |  | 9.6132 | 9.2929 | 8.8962 | 8.4332 | 7.953 | 7.4483 | 6.9508 | 6.4047 | 5.6707 | 3.8157 | 1.1133 | -0.36697 | -0.98043 | 9.6936 | 9.5188 | 9.3495 | 9.202 | 9.0589 | 8.9062 | 8.7507 | 8.5633 | 8.2759 | 7.1776 | 5.6779 | 4.8434 | 4.2691 | 12.0746 | 11.7897 | 11.4526 | 11.0455 | 10.6267 | 10.1825 | 9.7196 | 9.205 | 8.5141 | 6.7861 | 4.3137 | 2.8912 | 2.2875
|  | WINCANTON | FS |  |  | 9.6132 | 9.2929 | 8.8962 | 8.4332 | 7.953 | 7.4483 | 6.9508 | 6.4047 | 5.6707 | 3.8157 | 1.1133 | -0.36697 | -0.98043 | 9.6936 | 9.5188 | 9.3495 | 9.202 | 9.0589 | 8.9062 | 8.7507 | 8.5633 | 8.2759 | 7.1776 | 5.6779 | 4.8434 | 4.2691 | 12.0746 | 11.7897 | 11.4526 | 11.0455 | 10.6267 | 10.1825 | 9.7196 | 9.205 | 8.5141 | 6.7861 | 4.3137 | 2.8912 | 2.2875
COWLEY GSP | WITNEY BSP | WINDRUSH PARK | MINIMUM HEADROOM | SP 33366 09758 | NO | 27.9132 | 27.7331 | 27.5082 | 27.2344 | 26.9148 | 26.6009 | 26.2727 | 25.9058 | 25.296 | 23.6729 | 21.1629 | 19.4976 | 18.6914 | 27.3039 | 27.1761 | 27.0242 | 26.8675 | 26.6869 | 26.5027 | 26.307 | 26.0846 | 25.6555 | 24.4583 | 22.6665 | 21.0224 | 19.0302 | 28.8253 | 28.6964 | 28.5471 | 28.4144 | 28.2031 | 27.9261 | 27.6356 | 27.3102 | 26.7685 | 25.2928 | 23.0295 | 21.5223 | 20.7999
|  | WINDRUSH PARK | CT |  |  | 27.9132 | 27.7331 | 27.5082 | 27.2344 | 26.9148 | 26.6009 | 26.2727 | 25.9058 | 25.296 | 23.6729 | 21.1629 | 19.4976 | 18.6914 | 27.3039 | 27.1761 | 27.0242 | 26.8675 | 26.6869 | 26.5027 | 26.307 | 26.0846 | 25.6555 | 24.4583 | 22.6665 | 21.0224 | 19.0302 | 28.8253 | 28.6964 | 28.5471 | 28.4144 | 28.2031 | 27.9261 | 27.6356 | 27.3102 | 26.7685 | 25.2928 | 23.0295 | 21.5223 | 20.7999
|  | WINDRUSH PARK | LW |  |  | 27.9132 | 27.7331 | 27.5082 | 27.2344 | 26.9148 | 26.6009 | 26.2727 | 25.9058 | 25.296 | 23.6729 | 21.1629 | 19.4976 | 18.6914 | 27.3039 | 27.1761 | 27.0242 | 26.8675 | 26.6869 | 26.5027 | 26.307 | 26.0846 | 25.6555 | 24.4583 | 22.6665 | 21.0224 | 19.0302 | 28.8253 | 28.6964 | 28.5471 | 28.4144 | 28.2031 | 27.9261 | 27.6356 | 27.3102 | 26.7685 | 25.2928 | 23.0295 | 21.5223 | 20.7999
|  | WINDRUSH PARK | ST |  |  | 27.9132 | 27.7331 | 27.5082 | 27.2344 | 26.9148 | 26.6009 | 26.2727 | 25.9058 | 25.296 | 23.6729 | 21.1629 | 19.4976 | 18.6914 | 27.3039 | 27.1761 | 27.0242 | 26.8675 | 26.6869 | 26.5027 | 26.307 | 26.0846 | 25.6555 | 24.4583 | 22.6665 | 21.0224 | 19.0302 | 28.8253 | 28.6964 | 28.5471 | 28.4144 | 28.2031 | 27.9261 | 27.6356 | 27.3102 | 26.7685 | 25.2928 | 23.0295 | 21.5223 | 20.7999
|  | WINDRUSH PARK | FS |  |  | 27.9132 | 27.7331 | 27.5082 | 27.2344 | 26.9148 | 26.6009 | 26.2727 | 25.9058 | 25.296 | 23.6729 | 21.1629 | 19.4976 | 18.6914 | 27.3039 | 27.1761 | 27.0242 | 26.8675 | 26.6869 | 26.5027 | 26.307 | 26.0846 | 25.6555 | 24.4583 | 22.6665 | 21.0224 | 19.0302 | 28.8253 | 28.6964 | 28.5471 | 28.4144 | 28.2031 | 27.9261 | 27.6356 | 27.3102 | 26.7685 | 25.2928 | 23.0295 | 21.5223 | 20.7999
COWLEY GSP | DRAYTON BSP | WINSMORE LANE | MINIMUM HEADROOM | SU 49513 96982 | NO | 8.9339 | 8.6357 | 8.2671 | 7.6725 | 7.0441 | 6.4467 | 5.8058 | 5.0669 | 3.8136 | 0.094783 | -5.745 | -9.804 | -11.6733 | 13.1587 | 12.9116 | 12.5945 | 12.1932 | 11.7601 | 11.3119 | 10.8228 | 10.1939 | 9.2757 | 6.7161 | 2.8983 | -0.12316 | -3.3968 | 10.7073 | 10.4051 | 10.0217 | 9.4508 | 8.8436 | 8.2526 | 7.6158 | 6.8663 | 5.6364 | 2.1933 | -3.2 | -6.662 | -8.2372
|  | WINSMORE LANE | CT |  |  | 8.9339 | 8.6357 | 8.2671 | 7.6725 | 7.0441 | 6.4467 | 5.8058 | 5.0669 | 3.8136 | 0.094783 | -5.745 | -9.804 | -11.6733 | 13.1587 | 12.9116 | 12.5945 | 12.1932 | 11.7601 | 11.3119 | 10.8228 | 10.1939 | 9.2757 | 6.7161 | 2.8983 | -0.12316 | -3.3968 | 10.7073 | 10.4051 | 10.0217 | 9.4508 | 8.8436 | 8.2526 | 7.6158 | 6.8663 | 5.6364 | 2.1933 | -3.2 | -6.662 | -8.2372
|  | WINSMORE LANE | LW |  |  | 8.9339 | 8.6357 | 8.2671 | 7.6725 | 7.0441 | 6.4467 | 5.8058 | 5.0669 | 3.8136 | 0.094783 | -5.745 | -9.804 | -11.6733 | 13.1587 | 12.9116 | 12.5945 | 12.1932 | 11.7601 | 11.3119 | 10.8228 | 10.1939 | 9.2757 | 6.7161 | 2.8983 | -0.12316 | -3.3968 | 10.7073 | 10.4051 | 10.0217 | 9.4508 | 8.8436 | 8.2526 | 7.6158 | 6.8663 | 5.6364 | 2.1933 | -3.2 | -6.662 | -8.2372
|  | WINSMORE LANE | ST |  |  | 8.9339 | 8.6357 | 8.2671 | 7.6725 | 7.0441 | 6.4467 | 5.8058 | 5.0669 | 3.8136 | 0.094783 | -5.745 | -9.804 | -11.6733 | 13.1587 | 12.9116 | 12.5945 | 12.1932 | 11.7601 | 11.3119 | 10.8228 | 10.1939 | 9.2757 | 6.7161 | 2.8983 | -0.12316 | -3.3968 | 10.7073 | 10.4051 | 10.0217 | 9.4508 | 8.8436 | 8.2526 | 7.6158 | 6.8663 | 5.6364 | 2.1933 | -3.2 | -6.662 | -8.2372
|  | WINSMORE LANE | FS |  |  | 8.9339 | 8.6357 | 8.2671 | 7.6725 | 7.0441 | 6.4467 | 5.8058 | 5.0669 | 3.8136 | 0.094783 | -5.745 | -9.804 | -11.6733 | 13.1587 | 12.9116 | 12.5945 | 12.1932 | 11.7601 | 11.3119 | 10.8228 | 10.1939 | 9.2757 | 6.7161 | 2.8983 | -0.12316 | -3.3968 | 10.7073 | 10.4051 | 10.0217 | 9.4508 | 8.8436 | 8.2526 | 7.6158 | 6.8663 | 5.6364 | 2.1933 | -3.2 | -6.662 | -8.2372
MANNINGTON GSP | LYTCHETT | WINTERBORNE KINGSTON | MINIMUM HEADROOM | SY 84631 98138 | YES | 5.4932 | 5.3036 | 5.0595 | 4.7334 | 4.3915 | 4.0234 | 3.6 | 3.0978 | 2.4043 | 1.03 | -1.2695 | -2.8856 | -3.5777 | 7.3486 | 7.2228 | 7.0519 | 6.8566 | 6.6462 | 6.4189 | 6.1493 | 5.8146 | 5.3754 | 4.6287 | 3.5373 | 2.7823 | 2.274 | 5.8297 | 5.6502 | 5.4165 | 5.1124 | 4.792 | 4.4472 | 4.0481 | 3.5704 | 2.9152 | 1.6556 | -0.36545 | -1.6988 | -2.2682
|  | WINTERBORNE KINGSTON | CT |  |  | 5.4932 | 5.3036 | 5.0595 | 4.7334 | 4.3915 | 4.0234 | 3.6 | 3.0978 | 2.4043 | 1.03 | -1.2695 | -2.8856 | -3.5777 | 7.3486 | 7.2228 | 7.0519 | 6.8566 | 6.6462 | 6.4189 | 6.1493 | 5.8146 | 5.3754 | 4.6287 | 3.5373 | 2.7823 | 2.274 | 5.8297 | 5.6502 | 5.4165 | 5.1124 | 4.792 | 4.4472 | 4.0481 | 3.5704 | 2.9152 | 1.6556 | -0.36545 | -1.6988 | -2.2682
|  | WINTERBORNE KINGSTON | LW |  |  | 5.4932 | 5.3036 | 5.0595 | 4.7334 | 4.3915 | 4.0234 | 3.6 | 3.0978 | 2.4043 | 1.03 | -1.2695 | -2.8856 | -3.5777 | 7.3486 | 7.2228 | 7.0519 | 6.8566 | 6.6462 | 6.4189 | 6.1493 | 5.8146 | 5.3754 | 4.6287 | 3.5373 | 2.7823 | 2.274 | 5.8297 | 5.6502 | 5.4165 | 5.1124 | 4.792 | 4.4472 | 4.0481 | 3.5704 | 2.9152 | 1.6556 | -0.36545 | -1.6988 | -2.2682
|  | WINTERBORNE KINGSTON | ST |  |  | 5.4932 | 5.3036 | 5.0595 | 4.7334 | 4.3915 | 4.0234 | 3.6 | 3.0978 | 2.4043 | 1.03 | -1.2695 | -2.8856 | -3.5777 | 7.3486 | 7.2228 | 7.0519 | 6.8566 | 6.6462 | 6.4189 | 6.1493 | 5.8146 | 5.3754 | 4.6287 | 3.5373 | 2.7823 | 2.274 | 5.8297 | 5.6502 | 5.4165 | 5.1124 | 4.792 | 4.4472 | 4.0481 | 3.5704 | 2.9152 | 1.6556 | -0.36545 | -1.6988 | -2.2682
|  | WINTERBORNE KINGSTON | FS |  |  | 5.4932 | 5.3036 | 5.0595 | 4.7334 | 4.3915 | 4.0234 | 3.6 | 3.0978 | 2.4043 | 1.03 | -1.2695 | -2.8856 | -3.5777 | 7.3486 | 7.2228 | 7.0519 | 6.8566 | 6.6462 | 6.4189 | 6.1493 | 5.8146 | 5.3754 | 4.6287 | 3.5373 | 2.7823 | 2.274 | 5.8297 | 5.6502 | 5.4165 | 5.1124 | 4.792 | 4.4472 | 4.0481 | 3.5704 | 2.9152 | 1.6556 | -0.36545 | -1.6988 | -2.2682
MANNINGTON GSP | REDHILL BSP | WINTON | MINIMUM HEADROOM | SZ 09349 93822 | YES | 10.5929 | 10.1367 | 9.4968 | 8.6728 | 7.8055 | 6.8909 | 5.8951 | 4.7409 | 2.8873 | -2.3873 | -10.7829 | -17.1227 | -20.9263 | 16.82 | 16.4552 | 15.9438 | 15.3694 | 14.7617 | 14.1049 | 13.3818 | 12.5239 | 11.291 | 7.8177 | 2.7732 | -1.469 | -5.6956 | 12.5088 | 12.1011 | 11.5373 | 10.7962 | 10.0184 | 9.1991 | 8.3078 | 7.2777 | 5.6052 | 0.74818 | -6.8376 | -12.5546 | -15.7668
|  | WINTON | CT |  |  | 10.5929 | 10.1367 | 9.4968 | 8.6728 | 7.8055 | 6.8909 | 5.8951 | 4.7409 | 2.8873 | -2.3873 | -10.7829 | -17.1227 | -20.9263 | 16.82 | 16.4552 | 15.9438 | 15.3694 | 14.7617 | 14.1049 | 13.3818 | 12.5239 | 11.291 | 7.8177 | 2.7732 | -1.469 | -5.6956 | 12.5088 | 12.1011 | 11.5373 | 10.7962 | 10.0184 | 9.1991 | 8.3078 | 7.2777 | 5.6052 | 0.74818 | -6.8376 | -12.5546 | -15.7668
|  | WINTON | LW |  |  | 10.5929 | 10.1367 | 9.4968 | 8.6728 | 7.8055 | 6.8909 | 5.8951 | 4.7409 | 2.8873 | -2.3873 | -10.7829 | -17.1227 | -20.9263 | 16.82 | 16.4552 | 15.9438 | 15.3694 | 14.7617 | 14.1049 | 13.3818 | 12.5239 | 11.291 | 7.8177 | 2.7732 | -1.469 | -5.6956 | 12.5088 | 12.1011 | 11.5373 | 10.7962 | 10.0184 | 9.1991 | 8.3078 | 7.2777 | 5.6052 | 0.74818 | -6.8376 | -12.5546 | -15.7668
|  | WINTON | ST |  |  | 10.5929 | 10.1367 | 9.4968 | 8.6728 | 7.8055 | 6.8909 | 5.8951 | 4.7409 | 2.8873 | -2.3873 | -10.7829 | -17.1227 | -20.9263 | 16.82 | 16.4552 | 15.9438 | 15.3694 | 14.7617 | 14.1049 | 13.3818 | 12.5239 | 11.291 | 7.8177 | 2.7732 | -1.469 | -5.6956 | 12.5088 | 12.1011 | 11.5373 | 10.7962 | 10.0184 | 9.1991 | 8.3078 | 7.2777 | 5.6052 | 0.74818 | -6.8376 | -12.5546 | -15.7668
|  | WINTON | FS |  |  | 10.5929 | 10.1367 | 9.4968 | 8.6728 | 7.8055 | 6.8909 | 5.8951 | 4.7409 | 2.8873 | -2.3873 | -10.7829 | -17.1227 | -20.9263 | 16.82 | 16.4552 | 15.9438 | 15.3694 | 14.7617 | 14.1049 | 13.3818 | 12.5239 | 11.291 | 7.8177 | 2.7732 | -1.469 | -5.6956 | 12.5088 | 12.1011 | 11.5373 | 10.7962 | 10.0184 | 9.1991 | 8.3078 | 7.2777 | 5.6052 | 0.74818 | -6.8376 | -12.5546 | -15.7668
COWLEY GSP | WITNEY BSP | WITNEY TOWN | MINIMUM HEADROOM | SP 35844 09625 | NO | 0.52259 | -0.29899 | -1.4063 | -2.7258 | -4.124 | -5.5159 | -7.0678 | -8.8719 | -11.3983 | -17.1632 | -25.2514 | -30.6199 | -32.5622 | 8.3433 | 7.8243 | 7.1123 | 6.3505 | 5.5337 | 4.6797 | 3.7199 | 2.5751 | 1.0273 | -2.4231 | -6.8103 | -9.6833 | -11.7384 | 2.6415 | 1.9829 | 1.1023 | -0.0080916 | -1.1848 | -2.4067 | -3.7701 | -5.3542 | -7.6036 | -12.8371 | -20.4003 | -25.1827 | -26.8975
|  | WITNEY TOWN | CT |  |  | 0.52259 | -0.29899 | -1.4063 | -2.7258 | -4.124 | -5.5159 | -7.0678 | -8.8719 | -11.3983 | -17.1632 | -25.2514 | -30.6199 | -32.5622 | 8.3433 | 7.8243 | 7.1123 | 6.3505 | 5.5337 | 4.6797 | 3.7199 | 2.5751 | 1.0273 | -2.4231 | -6.8103 | -9.6833 | -11.7384 | 2.6415 | 1.9829 | 1.1023 | -0.0080916 | -1.1848 | -2.4067 | -3.7701 | -5.3542 | -7.6036 | -12.8371 | -20.4003 | -25.1827 | -26.8975
|  | WITNEY TOWN | LW |  |  | 0.52259 | -0.29899 | -1.4063 | -2.7258 | -4.124 | -5.5159 | -7.0678 | -8.8719 | -11.3983 | -17.1632 | -25.2514 | -30.6199 | -32.5622 | 8.3433 | 7.8243 | 7.1123 | 6.3505 | 5.5337 | 4.6797 | 3.7199 | 2.5751 | 1.0273 | -2.4231 | -6.8103 | -9.6833 | -11.7384 | 2.6415 | 1.9829 | 1.1023 | -0.0080916 | -1.1848 | -2.4067 | -3.7701 | -5.3542 | -7.6036 | -12.8371 | -20.4003 | -25.1827 | -26.8975
|  | WITNEY TOWN | ST |  |  | 0.52259 | -0.29899 | -1.4063 | -2.7258 | -4.124 | -5.5159 | -7.0678 | -8.8719 | -11.3983 | -17.1632 | -25.2514 | -30.6199 | -32.5622 | 8.3433 | 7.8243 | 7.1123 | 6.3505 | 5.5337 | 4.6797 | 3.7199 | 2.5751 | 1.0273 | -2.4231 | -6.8103 | -9.6833 | -11.7384 | 2.6415 | 1.9829 | 1.1023 | -0.0080916 | -1.1848 | -2.4067 | -3.7701 | -5.3542 | -7.6036 | -12.8371 | -20.4003 | -25.1827 | -26.8975
|  | WITNEY TOWN | FS |  |  | 0.52259 | -0.29899 | -1.4063 | -2.7258 | -4.124 | -5.5159 | -7.0678 | -8.8719 | -11.3983 | -17.1632 | -25.2514 | -30.6199 | -32.5622 | 8.3433 | 7.8243 | 7.1123 | 6.3505 | 5.5337 | 4.6797 | 3.7199 | 2.5751 | 1.0273 | -2.4231 | -6.8103 | -9.6833 | -11.7384 | 2.6415 | 1.9829 | 1.1023 | -0.0080916 | -1.1848 | -2.4067 | -3.7701 | -5.3542 | -7.6036 | -12.8371 | -20.4003 | -25.1827 | -26.8975
BRAMLEY (FLEE) | WOKINGHAM BSP | WOKINGHAM | MINIMUM HEADROOM | SU 79589 67665 | YES | 27.8245 | 27.2716 | 26.6532 | 25.9126 | 25.1258 | 24.3186 | 23.3879 | 22.3059 | 20.8155 | 17.2929 | 12.86 | 10.1431 | 8.7864 | 25.8679 | 25.4764 | 25.0596 | 24.6037 | 24.1154 | 23.5937 | 22.9881 | 22.2733 | 21.3304 | 19.3235 | 16.8342 | 15.2021 | 13.863 | 29.6118 | 29.1051 | 28.5556 | 27.908 | 27.2082 | 26.4829 | 25.6438 | 24.6622 | 23.2994 | 20.2003 | 16.2782 | 13.8937 | 12.716
|  | WOKINGHAM | CT |  |  | 27.8245 | 27.2716 | 26.6532 | 25.9126 | 25.1258 | 24.3186 | 23.3879 | 22.3059 | 20.8155 | 17.2929 | 12.86 | 10.1431 | 8.7864 | 25.8679 | 25.4764 | 25.0596 | 24.6037 | 24.1154 | 23.5937 | 22.9881 | 22.2733 | 21.3304 | 19.3235 | 16.8342 | 15.2021 | 13.863 | 29.6118 | 29.1051 | 28.5556 | 27.908 | 27.2082 | 26.4829 | 25.6438 | 24.6622 | 23.2994 | 20.2003 | 16.2782 | 13.8937 | 12.716
|  | WOKINGHAM | LW |  |  | 27.8245 | 27.2716 | 26.6532 | 25.9126 | 25.1258 | 24.3186 | 23.3879 | 22.3059 | 20.8155 | 17.2929 | 12.86 | 10.1431 | 8.7864 | 25.8679 | 25.4764 | 25.0596 | 24.6037 | 24.1154 | 23.5937 | 22.9881 | 22.2733 | 21.3304 | 19.3235 | 16.8342 | 15.2021 | 13.863 | 29.6118 | 29.1051 | 28.5556 | 27.908 | 27.2082 | 26.4829 | 25.6438 | 24.6622 | 23.2994 | 20.2003 | 16.2782 | 13.8937 | 12.716
|  | WOKINGHAM | ST |  |  | 27.8245 | 27.2716 | 26.6532 | 25.9126 | 25.1258 | 24.3186 | 23.3879 | 22.3059 | 20.8155 | 17.2929 | 12.86 | 10.1431 | 8.7864 | 25.8679 | 25.4764 | 25.0596 | 24.6037 | 24.1154 | 23.5937 | 22.9881 | 22.2733 | 21.3304 | 19.3235 | 16.8342 | 15.2021 | 13.863 | 29.6118 | 29.1051 | 28.5556 | 27.908 | 27.2082 | 26.4829 | 25.6438 | 24.6622 | 23.2994 | 20.2003 | 16.2782 | 13.8937 | 12.716
|  | WOKINGHAM | FS |  |  | 27.8245 | 27.2716 | 26.6532 | 25.9126 | 25.1258 | 24.3186 | 23.3879 | 22.3059 | 20.8155 | 17.2929 | 12.86 | 10.1431 | 8.7864 | 25.8679 | 25.4764 | 25.0596 | 24.6037 | 24.1154 | 23.5937 | 22.9881 | 22.2733 | 21.3304 | 19.3235 | 16.8342 | 15.2021 | 13.863 | 29.6118 | 29.1051 | 28.5556 | 27.908 | 27.2082 | 26.4829 | 25.6438 | 24.6622 | 23.2994 | 20.2003 | 16.2782 | 13.8937 | 12.716
BRAMLEY (FLEE) | BURGHFIELD RESERVE | WOODCOTE | MINIMUM HEADROOM | SU 64425 81624 | YES | 1.0802 | 1.0016 | 0.90979 | 0.77753 | 0.64193 | 0.49233 | 0.32229 | 0.1429 | -0.14997 | -0.75927 | -1.9167 | -2.7847 | -3.1396 | 1.7534 | 1.6956 | 1.625 | 1.5426 | 1.4576 | 1.3582 | 1.241 | 1.1146 | 0.9255 | 0.61382 | 0.10488 | -0.28186 | -0.52922 | 0.9179 | 0.8389 | 0.74469 | 0.61878 | 0.48954 | 0.34388 | 0.17571 | -0.0030812 | -0.28786 | -0.82693 | -1.7938 | -2.5104 | -2.8212
|  | WOODCOTE | CT |  |  | 1.0802 | 1.0016 | 0.90979 | 0.77753 | 0.64193 | 0.49233 | 0.32229 | 0.1429 | -0.14997 | -0.75927 | -1.9167 | -2.7847 | -3.1396 | 1.7534 | 1.6956 | 1.625 | 1.5426 | 1.4576 | 1.3582 | 1.241 | 1.1146 | 0.9255 | 0.61382 | 0.10488 | -0.28186 | -0.52922 | 0.9179 | 0.8389 | 0.74469 | 0.61878 | 0.48954 | 0.34388 | 0.17571 | -0.0030812 | -0.28786 | -0.82693 | -1.7938 | -2.5104 | -2.8212
|  | WOODCOTE | LW |  |  | 1.0802 | 1.0016 | 0.90979 | 0.77753 | 0.64193 | 0.49233 | 0.32229 | 0.1429 | -0.14997 | -0.75927 | -1.9167 | -2.7847 | -3.1396 | 1.7534 | 1.6956 | 1.625 | 1.5426 | 1.4576 | 1.3582 | 1.241 | 1.1146 | 0.9255 | 0.61382 | 0.10488 | -0.28186 | -0.52922 | 0.9179 | 0.8389 | 0.74469 | 0.61878 | 0.48954 | 0.34388 | 0.17571 | -0.0030812 | -0.28786 | -0.82693 | -1.7938 | -2.5104 | -2.8212
|  | WOODCOTE | ST |  |  | 1.0802 | 1.0016 | 0.90979 | 0.77753 | 0.64193 | 0.49233 | 0.32229 | 0.1429 | -0.14997 | -0.75927 | -1.9167 | -2.7847 | -3.1396 | 1.7534 | 1.6956 | 1.625 | 1.5426 | 1.4576 | 1.3582 | 1.241 | 1.1146 | 0.9255 | 0.61382 | 0.10488 | -0.28186 | -0.52922 | 0.9179 | 0.8389 | 0.74469 | 0.61878 | 0.48954 | 0.34388 | 0.17571 | -0.0030812 | -0.28786 | -0.82693 | -1.7938 | -2.5104 | -2.8212
|  | WOODCOTE | FS |  |  | 1.0802 | 1.0016 | 0.90979 | 0.77753 | 0.64193 | 0.49233 | 0.32229 | 0.1429 | -0.14997 | -0.75927 | -1.9167 | -2.7847 | -3.1396 | 1.7534 | 1.6956 | 1.625 | 1.5426 | 1.4576 | 1.3582 | 1.241 | 1.1146 | 0.9255 | 0.61382 | 0.10488 | -0.28186 | -0.52922 | 0.9179 | 0.8389 | 0.74469 | 0.61878 | 0.48954 | 0.34388 | 0.17571 | -0.0030812 | -0.28786 | -0.82693 | -1.7938 | -2.5104 | -2.8212
NURSLING GSP | SOUTHAMPTON (2 X 90) | WOODMILL LANE | MINIMUM HEADROOM | SU 43733 15470 | YES | 13.3323 | 13.1329 | 12.8492 | 12.4638 | 12.0596 | 11.6487 | 11.2079 | 10.7114 | 9.9839 | 7.507 | 2.8621 | -0.8999 | -3.4166 | 16.866 | 16.7179 | 16.5049 | 16.2407 | 15.9666 | 15.6794 | 15.3685 | 15.012 | 14.5347 | 12.9224 | 10.2249 | 7.9166 | 5.6928 | 14.122 | 13.9383 | 13.6711 | 13.3094 | 12.9334 | 12.5487 | 12.1352 | 11.6673 | 10.9888 | 8.7297 | 4.6372 | 1.4445 | -0.64922
|  | WOODMILL LANE | CT |  |  | 13.3323 | 13.1329 | 12.8492 | 12.4638 | 12.0596 | 11.6487 | 11.2079 | 10.7114 | 9.9839 | 7.507 | 2.8621 | -0.8999 | -3.4166 | 16.866 | 16.7179 | 16.5049 | 16.2407 | 15.9666 | 15.6794 | 15.3685 | 15.012 | 14.5347 | 12.9224 | 10.2249 | 7.9166 | 5.6928 | 14.122 | 13.9383 | 13.6711 | 13.3094 | 12.9334 | 12.5487 | 12.1352 | 11.6673 | 10.9888 | 8.7297 | 4.6372 | 1.4445 | -0.64922
|  | WOODMILL LANE | LW |  |  | 13.3323 | 13.1329 | 12.8492 | 12.4638 | 12.0596 | 11.6487 | 11.2079 | 10.7114 | 9.9839 | 7.507 | 2.8621 | -0.8999 | -3.4166 | 16.866 | 16.7179 | 16.5049 | 16.2407 | 15.9666 | 15.6794 | 15.3685 | 15.012 | 14.5347 | 12.9224 | 10.2249 | 7.9166 | 5.6928 | 14.122 | 13.9383 | 13.6711 | 13.3094 | 12.9334 | 12.5487 | 12.1352 | 11.6673 | 10.9888 | 8.7297 | 4.6372 | 1.4445 | -0.64922
|  | WOODMILL LANE | ST |  |  | 13.3323 | 13.1329 | 12.8492 | 12.4638 | 12.0596 | 11.6487 | 11.2079 | 10.7114 | 9.9839 | 7.507 | 2.8621 | -0.8999 | -3.4166 | 16.866 | 16.7179 | 16.5049 | 16.2407 | 15.9666 | 15.6794 | 15.3685 | 15.012 | 14.5347 | 12.9224 | 10.2249 | 7.9166 | 5.6928 | 14.122 | 13.9383 | 13.6711 | 13.3094 | 12.9334 | 12.5487 | 12.1352 | 11.6673 | 10.9888 | 8.7297 | 4.6372 | 1.4445 | -0.64922
|  | WOODMILL LANE | FS |  |  | 13.3323 | 13.1329 | 12.8492 | 12.4638 | 12.0596 | 11.6487 | 11.2079 | 10.7114 | 9.9839 | 7.507 | 2.8621 | -0.8999 | -3.4166 | 16.866 | 16.7179 | 16.5049 | 16.2407 | 15.9666 | 15.6794 | 15.3685 | 15.012 | 14.5347 | 12.9224 | 10.2249 | 7.9166 | 5.6928 | 14.122 | 13.9383 | 13.6711 | 13.3094 | 12.9334 | 12.5487 | 12.1352 | 11.6673 | 10.9888 | 8.7297 | 4.6372 | 1.4445 | -0.64922
COWLEY GSP | YARNTON BSP | WOODSTOCK | MINIMUM HEADROOM | SP 44795 17462 | NO | 11.0608 | 10.6998 | 10.2965 | 9.856 | 9.3841 | 8.9723 | 8.5509 | 8.0867 | 7.3112 | 5.2996 | 1.8836 | -0.29008 | -0.60478 | 11.3183 | 11.0961 | 10.8443 | 10.5979 | 10.3298 | 10.084 | 9.8269 | 9.5287 | 9.0606 | 7.9373 | 6.3568 | 5.3309 | 4.826 | 11.5954 | 11.2837 | 10.9291 | 10.5549 | 10.1514 | 9.7892 | 9.4141 | 8.9889 | 8.2873 | 6.5136 | 3.5494 | 1.6404 | 1.3671
|  | WOODSTOCK | CT |  |  | 11.0608 | 10.6998 | 10.2965 | 9.856 | 9.3841 | 8.9723 | 8.5509 | 8.0867 | 7.3112 | 5.2996 | 1.8836 | -0.29008 | -0.60478 | 11.3183 | 11.0961 | 10.8443 | 10.5979 | 10.3298 | 10.084 | 9.8269 | 9.5287 | 9.0606 | 7.9373 | 6.3568 | 5.3309 | 4.826 | 11.5954 | 11.2837 | 10.9291 | 10.5549 | 10.1514 | 9.7892 | 9.4141 | 8.9889 | 8.2873 | 6.5136 | 3.5494 | 1.6404 | 1.3671
|  | WOODSTOCK | LW |  |  | 11.0608 | 10.6998 | 10.2965 | 9.856 | 9.3841 | 8.9723 | 8.5509 | 8.0867 | 7.3112 | 5.2996 | 1.8836 | -0.29008 | -0.60478 | 11.3183 | 11.0961 | 10.8443 | 10.5979 | 10.3298 | 10.084 | 9.8269 | 9.5287 | 9.0606 | 7.9373 | 6.3568 | 5.3309 | 4.826 | 11.5954 | 11.2837 | 10.9291 | 10.5549 | 10.1514 | 9.7892 | 9.4141 | 8.9889 | 8.2873 | 6.5136 | 3.5494 | 1.6404 | 1.3671
|  | WOODSTOCK | ST |  |  | 11.0608 | 10.6998 | 10.2965 | 9.856 | 9.3841 | 8.9723 | 8.5509 | 8.0867 | 7.3112 | 5.2996 | 1.8836 | -0.29008 | -0.60478 | 11.3183 | 11.0961 | 10.8443 | 10.5979 | 10.3298 | 10.084 | 9.8269 | 9.5287 | 9.0606 | 7.9373 | 6.3568 | 5.3309 | 4.826 | 11.5954 | 11.2837 | 10.9291 | 10.5549 | 10.1514 | 9.7892 | 9.4141 | 8.9889 | 8.2873 | 6.5136 | 3.5494 | 1.6404 | 1.3671
|  | WOODSTOCK | FS |  |  | 11.0608 | 10.6998 | 10.2965 | 9.856 | 9.3841 | 8.9723 | 8.5509 | 8.0867 | 7.3112 | 5.2996 | 1.8836 | -0.29008 | -0.60478 | 11.3183 | 11.0961 | 10.8443 | 10.5979 | 10.3298 | 10.084 | 9.8269 | 9.5287 | 9.0606 | 7.9373 | 6.3568 | 5.3309 | 4.826 | 11.5954 | 11.2837 | 10.9291 | 10.5549 | 10.1514 | 9.7892 | 9.4141 | 8.9889 | 8.2873 | 6.5136 | 3.5494 | 1.6404 | 1.3671
BOTLEY WOOD GSP | NETLEY COMMON BSP | WOOLSTON | MINIMUM HEADROOM | SU 44145 11242 | YES | 6.4847 | 6.0535 | 5.6636 | 5.153 | 4.5878 | 3.9075 | 3.1876 | 2.3767 | 1.2155 | -2.6128 | -8.3604 | -12.7412 | -15.4773 | 9.0365 | 8.7517 | 8.4458 | 8.0947 | 7.7056 | 7.2226 | 6.706 | 6.1016 | 5.3303 | 2.737 | -0.79079 | -3.9073 | -7.1721 | 7.2014 | 6.8283 | 6.4477 | 5.9861 | 5.4752 | 4.8516 | 4.1793 | 3.41 | 2.3248 | -1.2547 | -6.3653 | -10.1232 | -12.3447
|  | WOOLSTON | CT |  |  | 6.4847 | 6.0535 | 5.6636 | 5.153 | 4.5878 | 3.9075 | 3.1876 | 2.3767 | 1.2155 | -2.6128 | -8.3604 | -12.7412 | -15.4773 | 9.0365 | 8.7517 | 8.4458 | 8.0947 | 7.7056 | 7.2226 | 6.706 | 6.1016 | 5.3303 | 2.737 | -0.79079 | -3.9073 | -7.1721 | 7.2014 | 6.8283 | 6.4477 | 5.9861 | 5.4752 | 4.8516 | 4.1793 | 3.41 | 2.3248 | -1.2547 | -6.3653 | -10.1232 | -12.3447
|  | WOOLSTON | LW |  |  | 6.4847 | 6.0535 | 5.6636 | 5.153 | 4.5878 | 3.9075 | 3.1876 | 2.3767 | 1.2155 | -2.6128 | -8.3604 | -12.7412 | -15.4773 | 9.0365 | 8.7517 | 8.4458 | 8.0947 | 7.7056 | 7.2226 | 6.706 | 6.1016 | 5.3303 | 2.737 | -0.79079 | -3.9073 | -7.1721 | 7.2014 | 6.8283 | 6.4477 | 5.9861 | 5.4752 | 4.8516 | 4.1793 | 3.41 | 2.3248 | -1.2547 | -6.3653 | -10.1232 | -12.3447
|  | WOOLSTON | ST |  |  | 6.4847 | 6.0535 | 5.6636 | 5.153 | 4.5878 | 3.9075 | 3.1876 | 2.3767 | 1.2155 | -2.6128 | -8.3604 | -12.7412 | -15.4773 | 9.0365 | 8.7517 | 8.4458 | 8.0947 | 7.7056 | 7.2226 | 6.706 | 6.1016 | 5.3303 | 2.737 | -0.79079 | -3.9073 | -7.1721 | 7.2014 | 6.8283 | 6.4477 | 5.9861 | 5.4752 | 4.8516 | 4.1793 | 3.41 | 2.3248 | -1.2547 | -6.3653 | -10.1232 | -12.3447
|  | WOOLSTON | FS |  |  | 6.4847 | 6.0535 | 5.6636 | 5.153 | 4.5878 | 3.9075 | 3.1876 | 2.3767 | 1.2155 | -2.6128 | -8.3604 | -12.7412 | -15.4773 | 9.0365 | 8.7517 | 8.4458 | 8.0947 | 7.7056 | 7.2226 | 6.706 | 6.1016 | 5.3303 | 2.737 | -0.79079 | -3.9073 | -7.1721 | 7.2014 | 6.8283 | 6.4477 | 5.9861 | 5.4752 | 4.8516 | 4.1793 | 3.41 | 2.3248 | -1.2547 | -6.3653 | -10.1232 | -12.3447
MINETY GSP | SWINDON BSP | WOOTTON BASSETT | MINIMUM HEADROOM | SU 07587 81123 | YES | 18.3553 | 18.099 | 17.7615 | 17.2957 | 16.8043 | 16.2855 | 15.7116 | 15.0306 | 13.8897 | 11.3049 | 7.5361 | 4.9769 | 3.8788 | 22.5802 | 22.4044 | 22.17 | 21.8877 | 21.5862 | 21.2602 | 20.8951 | 20.4571 | 19.8022 | 18.3048 | 16.1112 | 14.4165 | 12.8873 | 19.844 | 19.5806 | 19.2245 | 18.7687 | 18.2851 | 17.7691 | 17.1931 | 16.5053 | 15.4201 | 13.0039 | 9.6608 | 7.546 | 6.6469
|  | WOOTTON BASSETT | CT |  |  | 18.3553 | 18.099 | 17.7615 | 17.2957 | 16.8043 | 16.2855 | 15.7116 | 15.0306 | 13.8897 | 11.3049 | 7.5361 | 4.9769 | 3.8788 | 22.5802 | 22.4044 | 22.17 | 21.8877 | 21.5862 | 21.2602 | 20.8951 | 20.4571 | 19.8022 | 18.3048 | 16.1112 | 14.4165 | 12.8873 | 19.844 | 19.5806 | 19.2245 | 18.7687 | 18.2851 | 17.7691 | 17.1931 | 16.5053 | 15.4201 | 13.0039 | 9.6608 | 7.546 | 6.6469
|  | WOOTTON BASSETT | LW |  |  | 18.3553 | 18.099 | 17.7615 | 17.2957 | 16.8043 | 16.2855 | 15.7116 | 15.0306 | 13.8897 | 11.3049 | 7.5361 | 4.9769 | 3.8788 | 22.5802 | 22.4044 | 22.17 | 21.8877 | 21.5862 | 21.2602 | 20.8951 | 20.4571 | 19.8022 | 18.3048 | 16.1112 | 14.4165 | 12.8873 | 19.844 | 19.5806 | 19.2245 | 18.7687 | 18.2851 | 17.7691 | 17.1931 | 16.5053 | 15.4201 | 13.0039 | 9.6608 | 7.546 | 6.6469
|  | WOOTTON BASSETT | ST |  |  | 18.3553 | 18.099 | 17.7615 | 17.2957 | 16.8043 | 16.2855 | 15.7116 | 15.0306 | 13.8897 | 11.3049 | 7.5361 | 4.9769 | 3.8788 | 22.5802 | 22.4044 | 22.17 | 21.8877 | 21.5862 | 21.2602 | 20.8951 | 20.4571 | 19.8022 | 18.3048 | 16.1112 | 14.4165 | 12.8873 | 19.844 | 19.5806 | 19.2245 | 18.7687 | 18.2851 | 17.7691 | 17.1931 | 16.5053 | 15.4201 | 13.0039 | 9.6608 | 7.546 | 6.6469
|  | WOOTTON BASSETT | FS |  |  | 18.3553 | 18.099 | 17.7615 | 17.2957 | 16.8043 | 16.2855 | 15.7116 | 15.0306 | 13.8897 | 11.3049 | 7.5361 | 4.9769 | 3.8788 | 22.5802 | 22.4044 | 22.17 | 21.8877 | 21.5862 | 21.2602 | 20.8951 | 20.4571 | 19.8022 | 18.3048 | 16.1112 | 14.4165 | 12.8873 | 19.844 | 19.5806 | 19.2245 | 18.7687 | 18.2851 | 17.7691 | 17.1931 | 16.5053 | 15.4201 | 13.0039 | 9.6608 | 7.546 | 6.6469
COWLEY GSP | OXFORD BSP | WOOTTON ROAD | MINIMUM HEADROOM | SU 49244 98269 | YES | 3.1444 | 2.4263 | 1.5449 | 0.34088 | -0.94947 | -2.275 | -3.7705 | -5.3432 | -7.1131 | -11.1221 | -16.7877 | -20.6927 | -22.6139 | 5.6274 | 5.1448 | 4.5502 | 3.8199 | 3.036 | 2.2163 | 1.2855 | 0.27419 | -0.87594 | -3.3907 | -6.6361 | -9.0623 | -11.2227 | 4.7963 | 4.1662 | 3.3835 | 2.3324 | 1.2033 | 0.035588 | -1.2871 | -2.6981 | -4.3446 | -8.0397 | -13.1146 | -16.4966 | -18.0714
|  | WOOTTON ROAD | CT |  |  | 3.1444 | 2.4263 | 1.5449 | 0.34088 | -0.94947 | -2.275 | -3.7705 | -5.3432 | -7.1131 | -11.1221 | -16.7877 | -20.6927 | -22.6139 | 5.6274 | 5.1448 | 4.5502 | 3.8199 | 3.036 | 2.2163 | 1.2855 | 0.27419 | -0.87594 | -3.3907 | -6.6361 | -9.0623 | -11.2227 | 4.7963 | 4.1662 | 3.3835 | 2.3324 | 1.2033 | 0.035588 | -1.2871 | -2.6981 | -4.3446 | -8.0397 | -13.1146 | -16.4966 | -18.0714
|  | WOOTTON ROAD | LW |  |  | 3.1444 | 2.4263 | 1.5449 | 0.34088 | -0.94947 | -2.275 | -3.7705 | -5.3432 | -7.1131 | -11.1221 | -16.7877 | -20.6927 | -22.6139 | 5.6274 | 5.1448 | 4.5502 | 3.8199 | 3.036 | 2.2163 | 1.2855 | 0.27419 | -0.87594 | -3.3907 | -6.6361 | -9.0623 | -11.2227 | 4.7963 | 4.1662 | 3.3835 | 2.3324 | 1.2033 | 0.035588 | -1.2871 | -2.6981 | -4.3446 | -8.0397 | -13.1146 | -16.4966 | -18.0714
|  | WOOTTON ROAD | ST |  |  | 3.1444 | 2.4263 | 1.5449 | 0.34088 | -0.94947 | -2.275 | -3.7705 | -5.3432 | -7.1131 | -11.1221 | -16.7877 | -20.6927 | -22.6139 | 5.6274 | 5.1448 | 4.5502 | 3.8199 | 3.036 | 2.2163 | 1.2855 | 0.27419 | -0.87594 | -3.3907 | -6.6361 | -9.0623 | -11.2227 | 4.7963 | 4.1662 | 3.3835 | 2.3324 | 1.2033 | 0.035588 | -1.2871 | -2.6981 | -4.3446 | -8.0397 | -13.1146 | -16.4966 | -18.0714
|  | WOOTTON ROAD | FS |  |  | 3.1444 | 2.4263 | 1.5449 | 0.34088 | -0.94947 | -2.275 | -3.7705 | -5.3432 | -7.1131 | -11.1221 | -16.7877 | -20.6927 | -22.6139 | 5.6274 | 5.1448 | 4.5502 | 3.8199 | 3.036 | 2.2163 | 1.2855 | 0.27419 | -0.87594 | -3.3907 | -6.6361 | -9.0623 | -11.2227 | 4.7963 | 4.1662 | 3.3835 | 2.3324 | 1.2033 | 0.035588 | -1.2871 | -2.6981 | -4.3446 | -8.0397 | -13.1146 | -16.4966 | -18.0714
BRAMLEY (FLEE) | COXMOOR WOOD BSP | WRECCLESHAM | MINIMUM HEADROOM | SU 82093 44312 | YES | 24.0315 | 23.6747 | 23.3011 | 22.7772 | 22.2474 | 21.6903 | 21.0442 | 20.2942 | 19.1223 | 16.8081 | 12.8164 | 9.9159 | 8.5839 | 29.2053 | 28.9275 | 28.6338 | 28.2965 | 27.9483 | 27.5642 | 27.1093 | 26.5669 | 25.7986 | 24.4591 | 22.379 | 20.8256 | 19.6474 | 26.8231 | 26.4761 | 26.113 | 25.6205 | 25.1214 | 24.5925 | 23.9759 | 23.2556 | 22.1438 | 20.0119 | 16.4326 | 13.8204 | 12.5903
|  | WRECCLESHAM | CT |  |  | 24.0315 | 23.6747 | 23.3011 | 22.7772 | 22.2474 | 21.6903 | 21.0442 | 20.2942 | 19.1223 | 16.8081 | 12.8164 | 9.9159 | 8.5839 | 29.2053 | 28.9275 | 28.6338 | 28.2965 | 27.9483 | 27.5642 | 27.1093 | 26.5669 | 25.7986 | 24.4591 | 22.379 | 20.8256 | 19.6474 | 26.8231 | 26.4761 | 26.113 | 25.6205 | 25.1214 | 24.5925 | 23.9759 | 23.2556 | 22.1438 | 20.0119 | 16.4326 | 13.8204 | 12.5903
|  | WRECCLESHAM | LW |  |  | 24.0315 | 23.6747 | 23.3011 | 22.7772 | 22.2474 | 21.6903 | 21.0442 | 20.2942 | 19.1223 | 16.8081 | 12.8164 | 9.9159 | 8.5839 | 29.2053 | 28.9275 | 28.6338 | 28.2965 | 27.9483 | 27.5642 | 27.1093 | 26.5669 | 25.7986 | 24.4591 | 22.379 | 20.8256 | 19.6474 | 26.8231 | 26.4761 | 26.113 | 25.6205 | 25.1214 | 24.5925 | 23.9759 | 23.2556 | 22.1438 | 20.0119 | 16.4326 | 13.8204 | 12.5903
|  | WRECCLESHAM | ST |  |  | 24.0315 | 23.6747 | 23.3011 | 22.7772 | 22.2474 | 21.6903 | 21.0442 | 20.2942 | 19.1223 | 16.8081 | 12.8164 | 9.9159 | 8.5839 | 29.2053 | 28.9275 | 28.6338 | 28.2965 | 27.9483 | 27.5642 | 27.1093 | 26.5669 | 25.7986 | 24.4591 | 22.379 | 20.8256 | 19.6474 | 26.8231 | 26.4761 | 26.113 | 25.6205 | 25.1214 | 24.5925 | 23.9759 | 23.2556 | 22.1438 | 20.0119 | 16.4326 | 13.8204 | 12.5903
|  | WRECCLESHAM | FS |  |  | 24.0315 | 23.6747 | 23.3011 | 22.7772 | 22.2474 | 21.6903 | 21.0442 | 20.2942 | 19.1223 | 16.8081 | 12.8164 | 9.9159 | 8.5839 | 29.2053 | 28.9275 | 28.6338 | 28.2965 | 27.9483 | 27.5642 | 27.1093 | 26.5669 | 25.7986 | 24.4591 | 22.379 | 20.8256 | 19.6474 | 26.8231 | 26.4761 | 26.113 | 25.6205 | 25.1214 | 24.5925 | 23.9759 | 23.2556 | 22.1438 | 20.0119 | 16.4326 | 13.8204 | 12.5903
MINETY GSP | TOOTHILL BSP | WROUGHTON | MINIMUM HEADROOM | SU 14446 81504 | YES | 15.9346 | 15.6321 | 15.2796 | 14.8227 | 14.333 | 13.8319 | 13.3177 | 12.7895 | 12.1444 | 10.6171 | 8.6579 | 7.2416 | 6.6049 | 17.6503 | 17.4635 | 17.2426 | 16.9819 | 16.7024 | 16.4131 | 16.1139 | 15.8182 | 15.4361 | 14.5358 | 13.4681 | 12.7139 | 12.1408 | 16.5903 | 16.3127 | 15.976 | 15.5614 | 15.115 | 14.6533 | 14.1741 | 13.6987 | 13.1002 | 11.687 | 9.9356 | 8.7899 | 8.2931
|  | WROUGHTON | CT |  |  | 15.9346 | 15.6321 | 15.2796 | 14.8227 | 14.333 | 13.8319 | 13.3177 | 12.7895 | 12.1444 | 10.6171 | 8.6579 | 7.2416 | 6.6049 | 17.6503 | 17.4635 | 17.2426 | 16.9819 | 16.7024 | 16.4131 | 16.1139 | 15.8182 | 15.4361 | 14.5358 | 13.4681 | 12.7139 | 12.1408 | 16.5903 | 16.3127 | 15.976 | 15.5614 | 15.115 | 14.6533 | 14.1741 | 13.6987 | 13.1002 | 11.687 | 9.9356 | 8.7899 | 8.2931
|  | WROUGHTON | LW |  |  | 15.9346 | 15.6321 | 15.2796 | 14.8227 | 14.333 | 13.8319 | 13.3177 | 12.7895 | 12.1444 | 10.6171 | 8.6579 | 7.2416 | 6.6049 | 17.6503 | 17.4635 | 17.2426 | 16.9819 | 16.7024 | 16.4131 | 16.1139 | 15.8182 | 15.4361 | 14.5358 | 13.4681 | 12.7139 | 12.1408 | 16.5903 | 16.3127 | 15.976 | 15.5614 | 15.115 | 14.6533 | 14.1741 | 13.6987 | 13.1002 | 11.687 | 9.9356 | 8.7899 | 8.2931
|  | WROUGHTON | ST |  |  | 15.9346 | 15.6321 | 15.2796 | 14.8227 | 14.333 | 13.8319 | 13.3177 | 12.7895 | 12.1444 | 10.6171 | 8.6579 | 7.2416 | 6.6049 | 17.6503 | 17.4635 | 17.2426 | 16.9819 | 16.7024 | 16.4131 | 16.1139 | 15.8182 | 15.4361 | 14.5358 | 13.4681 | 12.7139 | 12.1408 | 16.5903 | 16.3127 | 15.976 | 15.5614 | 15.115 | 14.6533 | 14.1741 | 13.6987 | 13.1002 | 11.687 | 9.9356 | 8.7899 | 8.2931
|  | WROUGHTON | FS |  |  | 15.9346 | 15.6321 | 15.2796 | 14.8227 | 14.333 | 13.8319 | 13.3177 | 12.7895 | 12.1444 | 10.6171 | 8.6579 | 7.2416 | 6.6049 | 17.6503 | 17.4635 | 17.2426 | 16.9819 | 16.7024 | 16.4131 | 16.1139 | 15.8182 | 15.4361 | 14.5358 | 13.4681 | 12.7139 | 12.1408 | 16.5903 | 16.3127 | 15.976 | 15.5614 | 15.115 | 14.6533 | 14.1741 | 13.6987 | 13.1002 | 11.687 | 9.9356 | 8.7899 | 8.2931
AMERSHAM | LOUDWATER BSP | WYCOMBE MARSH | MINIMUM HEADROOM | SU 88582 91845 | YES | 5.1554 | 4.7623 | 4.3037 | 3.7857 | 3.2948 | 2.8023 | 2.2695 | 1.65 | 0.69323 | -1.9877 | -5.9567 | -8.5023 | -9.7171 | 9.9151 | 9.6508 | 9.3307 | 9.0035 | 8.6853 | 8.3486 | 7.981 | 7.5403 | 6.9161 | 5.1817 | 2.8315 | 1.1871 | -0.27824 | 6.8505 | 6.4989 | 6.0808 | 5.606 | 5.1491 | 4.6855 | 4.1833 | 3.5945 | 2.6934 | 0.17935 | -3.4256 | -5.6691 | -6.6893
|  | WYCOMBE MARSH | CT |  |  | 5.1554 | 4.7623 | 4.3037 | 3.7857 | 3.2948 | 2.8023 | 2.2695 | 1.65 | 0.69323 | -1.9877 | -5.9567 | -8.5023 | -9.7171 | 9.9151 | 9.6508 | 9.3307 | 9.0035 | 8.6853 | 8.3486 | 7.981 | 7.5403 | 6.9161 | 5.1817 | 2.8315 | 1.1871 | -0.27824 | 6.8505 | 6.4989 | 6.0808 | 5.606 | 5.1491 | 4.6855 | 4.1833 | 3.5945 | 2.6934 | 0.17935 | -3.4256 | -5.6691 | -6.6893
|  | WYCOMBE MARSH | LW |  |  | 5.1554 | 4.7623 | 4.3037 | 3.7857 | 3.2948 | 2.8023 | 2.2695 | 1.65 | 0.69323 | -1.9877 | -5.9567 | -8.5023 | -9.7171 | 9.9151 | 9.6508 | 9.3307 | 9.0035 | 8.6853 | 8.3486 | 7.981 | 7.5403 | 6.9161 | 5.1817 | 2.8315 | 1.1871 | -0.27824 | 6.8505 | 6.4989 | 6.0808 | 5.606 | 5.1491 | 4.6855 | 4.1833 | 3.5945 | 2.6934 | 0.17935 | -3.4256 | -5.6691 | -6.6893
|  | WYCOMBE MARSH | ST |  |  | 5.1554 | 4.7623 | 4.3037 | 3.7857 | 3.2948 | 2.8023 | 2.2695 | 1.65 | 0.69323 | -1.9877 | -5.9567 | -8.5023 | -9.7171 | 9.9151 | 9.6508 | 9.3307 | 9.0035 | 8.6853 | 8.3486 | 7.981 | 7.5403 | 6.9161 | 5.1817 | 2.8315 | 1.1871 | -0.27824 | 6.8505 | 6.4989 | 6.0808 | 5.606 | 5.1491 | 4.6855 | 4.1833 | 3.5945 | 2.6934 | 0.17935 | -3.4256 | -5.6691 | -6.6893
|  | WYCOMBE MARSH | FS |  |  | 5.1554 | 4.7623 | 4.3037 | 3.7857 | 3.2948 | 2.8023 | 2.2695 | 1.65 | 0.69323 | -1.9877 | -5.9567 | -8.5023 | -9.7171 | 9.9151 | 9.6508 | 9.3307 | 9.0035 | 8.6853 | 8.3486 | 7.981 | 7.5403 | 6.9161 | 5.1817 | 2.8315 | 1.1871 | -0.27824 | 6.8505 | 6.4989 | 6.0808 | 5.606 | 5.1491 | 4.6855 | 4.1833 | 3.5945 | 2.6934 | 0.17935 | -3.4256 | -5.6691 | -6.6893
LOVEDEAN GSP | WYMERING BSP | WYMERING | MINIMUM HEADROOM | SU 64974 05375 | YES | 41.4354 | 41.0038 | 40.4457 | 39.7755 | 38.9814 | 38.0211 | 36.7059 | 35.3165 | 33.331 | 27.309 | 18.0658 | 12.0329 | 8.7249 | 39.5467 | 39.188 | 38.741 | 38.286 | 37.8088 | 37.2671 | 36.6872 | 36.0539 | 35.3341 | 31.9407 | 25.9594 | 21.4824 | 16.7011 | 44.6971 | 44.1924 | 43.4294 | 42.418 | 41.3628 | 40.2654 | 39.1121 | 37.8859 | 36.1186 | 30.7053 | 22.3765 | 17.0099 | 14.1371
|  | WYMERING | CT |  |  | 41.4354 | 41.0038 | 40.4457 | 39.7755 | 38.9814 | 38.0211 | 36.7059 | 35.3165 | 33.331 | 27.309 | 18.0658 | 12.0329 | 8.7249 | 39.5467 | 39.188 | 38.741 | 38.286 | 37.8088 | 37.2671 | 36.6872 | 36.0539 | 35.3341 | 31.9407 | 25.9594 | 21.4824 | 16.7011 | 44.6971 | 44.1924 | 43.4294 | 42.418 | 41.3628 | 40.2654 | 39.1121 | 37.8859 | 36.1186 | 30.7053 | 22.3765 | 17.0099 | 14.1371
|  | WYMERING | LW |  |  | 41.4354 | 41.0038 | 40.4457 | 39.7755 | 38.9814 | 38.0211 | 36.7059 | 35.3165 | 33.331 | 27.309 | 18.0658 | 12.0329 | 8.7249 | 39.5467 | 39.188 | 38.741 | 38.286 | 37.8088 | 37.2671 | 36.6872 | 36.0539 | 35.3341 | 31.9407 | 25.9594 | 21.4824 | 16.7011 | 44.6971 | 44.1924 | 43.4294 | 42.418 | 41.3628 | 40.2654 | 39.1121 | 37.8859 | 36.1186 | 30.7053 | 22.3765 | 17.0099 | 14.1371
|  | WYMERING | ST |  |  | 41.4354 | 41.0038 | 40.4457 | 39.7755 | 38.9814 | 38.0211 | 36.7059 | 35.3165 | 33.331 | 27.309 | 18.0658 | 12.0329 | 8.7249 | 39.5467 | 39.188 | 38.741 | 38.286 | 37.8088 | 37.2671 | 36.6872 | 36.0539 | 35.3341 | 31.9407 | 25.9594 | 21.4824 | 16.7011 | 44.6971 | 44.1924 | 43.4294 | 42.418 | 41.3628 | 40.2654 | 39.1121 | 37.8859 | 36.1186 | 30.7053 | 22.3765 | 17.0099 | 14.1371
|  | WYMERING | FS |  |  | 41.4354 | 41.0038 | 40.4457 | 39.7755 | 38.9814 | 38.0211 | 36.7059 | 35.3165 | 33.331 | 27.309 | 18.0658 | 12.0329 | 8.7249 | 39.5467 | 39.188 | 38.741 | 38.286 | 37.8088 | 37.2671 | 36.6872 | 36.0539 | 35.3341 | 31.9407 | 25.9594 | 21.4824 | 16.7011 | 44.6971 | 44.1924 | 43.4294 | 42.418 | 41.3628 | 40.2654 | 39.1121 | 37.8859 | 36.1186 | 30.7053 | 22.3765 | 17.0099 | 14.1371
COWLEY GSP | YARNTON BSP | YARNTON | MINIMUM HEADROOM | SP 48277 12108 | NO | 28.6924 | 27.1489 | 25.312 | 22.9605 | 20.4716 | 18.0639 | 15.5735 | 12.8949 | 9.5742 | 2.3302 | -8.171 | -14.9269 | -16.6701 | 28.717 | 28.1494 | 27.544 | 26.8597 | 26.0288 | 24.6793 | 23.2767 | 21.7352 | 19.8614 | 15.7398 | 10.3624 | 6.8758 | 4.8627 | 30.4915 | 29.5056 | 28.3826 | 26.9215 | 24.8921 | 22.8085 | 20.6409 | 18.2784 | 15.3014 | 8.7479 | -0.20345 | -5.8638 | -7.3334
|  | YARNTON | CT |  |  | 28.6924 | 27.1489 | 25.312 | 22.9605 | 20.4716 | 18.0639 | 15.5735 | 12.8949 | 9.5742 | 2.3302 | -8.171 | -14.9269 | -16.6701 | 28.717 | 28.1494 | 27.544 | 26.8597 | 26.0288 | 24.6793 | 23.2767 | 21.7352 | 19.8614 | 15.7398 | 10.3624 | 6.8758 | 4.8627 | 30.4915 | 29.5056 | 28.3826 | 26.9215 | 24.8921 | 22.8085 | 20.6409 | 18.2784 | 15.3014 | 8.7479 | -0.20345 | -5.8638 | -7.3334
|  | YARNTON | LW |  |  | 28.6924 | 27.1489 | 25.312 | 22.9605 | 20.4716 | 18.0639 | 15.5735 | 12.8949 | 9.5742 | 2.3302 | -8.171 | -14.9269 | -16.6701 | 28.717 | 28.1494 | 27.544 | 26.8597 | 26.0288 | 24.6793 | 23.2767 | 21.7352 | 19.8614 | 15.7398 | 10.3624 | 6.8758 | 4.8627 | 30.4915 | 29.5056 | 28.3826 | 26.9215 | 24.8921 | 22.8085 | 20.6409 | 18.2784 | 15.3014 | 8.7479 | -0.20345 | -5.8638 | -7.3334
|  | YARNTON | ST |  |  | 28.6924 | 27.1489 | 25.312 | 22.9605 | 20.4716 | 18.0639 | 15.5735 | 12.8949 | 9.5742 | 2.3302 | -8.171 | -14.9269 | -16.6701 | 28.717 | 28.1494 | 27.544 | 26.8597 | 26.0288 | 24.6793 | 23.2767 | 21.7352 | 19.8614 | 15.7398 | 10.3624 | 6.8758 | 4.8627 | 30.4915 | 29.5056 | 28.3826 | 26.9215 | 24.8921 | 22.8085 | 20.6409 | 18.2784 | 15.3014 | 8.7479 | -0.20345 | -5.8638 | -7.3334
|  | YARNTON | FS |  |  | 28.6924 | 27.1489 | 25.312 | 22.9605 | 20.4716 | 18.0639 | 15.5735 | 12.8949 | 9.5742 | 2.3302 | -8.171 | -14.9269 | -16.6701 | 28.717 | 28.1494 | 27.544 | 26.8597 | 26.0288 | 24.6793 | 23.2767 | 21.7352 | 19.8614 | 15.7398 | 10.3624 | 6.8758 | 4.8627 | 30.4915 | 29.5056 | 28.3826 | 26.9215 | 24.8921 | 22.8085 | 20.6409 | 18.2784 | 15.3014 | 8.7479 | -0.20345 | -5.8638 | -7.3334
BRAMLEY (ANDO-THAT) | THATCHAM BSP | YATTENDON | MINIMUM HEADROOM | SU 53699 74307 | YES | 1.8384 | 1.4776 | 1.1295 | 0.53849 | -0.061249 | -0.67464 | -1.2797 | -1.8565 | -2.5614 | -3.7569 | -5.6367 | -6.683 | -7.0662 | 6.0203 | 5.7724 | 5.5363 | 5.1995 | 4.8601 | 4.4973 | 4.1172 | 3.7258 | 3.2485 | 2.5416 | 1.4775 | 0.82232 | 0.30564 | 3.1997 | 2.9732 | 2.7536 | 2.3567 | 1.9536 | 1.4019 | 0.835 | 0.28746 | -0.3842 | -1.485 | -3.1845 | -4.1497 | -4.5115
|  | YATTENDON | CT |  |  | 1.8384 | 1.4776 | 1.1295 | 0.53849 | -0.061249 | -0.67464 | -1.2797 | -1.8565 | -2.5614 | -3.7569 | -5.6367 | -6.683 | -7.0662 | 6.0203 | 5.7724 | 5.5363 | 5.1995 | 4.8601 | 4.4973 | 4.1172 | 3.7258 | 3.2485 | 2.5416 | 1.4775 | 0.82232 | 0.30564 | 3.1997 | 2.9732 | 2.7536 | 2.3567 | 1.9536 | 1.4019 | 0.835 | 0.28746 | -0.3842 | -1.485 | -3.1845 | -4.1497 | -4.5115
|  | YATTENDON | LW |  |  | 1.8384 | 1.4776 | 1.1295 | 0.53849 | -0.061249 | -0.67464 | -1.2797 | -1.8565 | -2.5614 | -3.7569 | -5.6367 | -6.683 | -7.0662 | 6.0203 | 5.7724 | 5.5363 | 5.1995 | 4.8601 | 4.4973 | 4.1172 | 3.7258 | 3.2485 | 2.5416 | 1.4775 | 0.82232 | 0.30564 | 3.1997 | 2.9732 | 2.7536 | 2.3567 | 1.9536 | 1.4019 | 0.835 | 0.28746 | -0.3842 | -1.485 | -3.1845 | -4.1497 | -4.5115
|  | YATTENDON | ST |  |  | 1.8384 | 1.4776 | 1.1295 | 0.53849 | -0.061249 | -0.67464 | -1.2797 | -1.8565 | -2.5614 | -3.7569 | -5.6367 | -6.683 | -7.0662 | 6.0203 | 5.7724 | 5.5363 | 5.1995 | 4.8601 | 4.4973 | 4.1172 | 3.7258 | 3.2485 | 2.5416 | 1.4775 | 0.82232 | 0.30564 | 3.1997 | 2.9732 | 2.7536 | 2.3567 | 1.9536 | 1.4019 | 0.835 | 0.28746 | -0.3842 | -1.485 | -3.1845 | -4.1497 | -4.5115
|  | YATTENDON | FS |  |  | 1.8384 | 1.4776 | 1.1295 | 0.53849 | -0.061249 | -0.67464 | -1.2797 | -1.8565 | -2.5614 | -3.7569 | -5.6367 | -6.683 | -7.0662 | 6.0203 | 5.7724 | 5.5363 | 5.1995 | 4.8601 | 4.4973 | 4.1172 | 3.7258 | 3.2485 | 2.5416 | 1.4775 | 0.82232 | 0.30564 | 3.1997 | 2.9732 | 2.7536 | 2.3567 | 1.9536 | 1.4019 | 0.835 | 0.28746 | -0.3842 | -1.485 | -3.1845 | -4.1497 | -4.5115
MELKSHAM GSP | CHIPPENHAM | YATTON KEYNELL | MINIMUM HEADROOM | ST 87300 75782 | YES | 0.76254 | 0.63895 | 0.51898 | 0.3547 | 0.18426 | 0.0025769 | -0.21216 | -0.45309 | -0.80736 | -1.5181 | -2.6217 | -3.312 | -3.6218 | 2.0012 | 1.9117 | 1.8239 | 1.7207 | 1.6128 | 1.4936 | 1.3482 | 1.1808 | 0.944 | 0.5184 | -0.10113 | -0.51125 | -0.81803 | 1.2358 | 1.133 | 1.0328 | 0.88772 | 0.73733 | 0.57878 | 0.39453 | 0.19083 | -0.12148 | -0.78093 | -1.8213 | -2.495 | -2.7976
|  | YATTON KEYNELL | CT |  |  | 0.76254 | 0.63895 | 0.51898 | 0.3547 | 0.18426 | 0.0025769 | -0.21216 | -0.45309 | -0.80736 | -1.5181 | -2.6217 | -3.312 | -3.6218 | 2.0012 | 1.9117 | 1.8239 | 1.7207 | 1.6128 | 1.4936 | 1.3482 | 1.1808 | 0.944 | 0.5184 | -0.10113 | -0.51125 | -0.81803 | 1.2358 | 1.133 | 1.0328 | 0.88772 | 0.73733 | 0.57878 | 0.39453 | 0.19083 | -0.12148 | -0.78093 | -1.8213 | -2.495 | -2.7976
|  | YATTON KEYNELL | LW |  |  | 0.76254 | 0.63895 | 0.51898 | 0.3547 | 0.18426 | 0.0025769 | -0.21216 | -0.45309 | -0.80736 | -1.5181 | -2.6217 | -3.312 | -3.6218 | 2.0012 | 1.9117 | 1.8239 | 1.7207 | 1.6128 | 1.4936 | 1.3482 | 1.1808 | 0.944 | 0.5184 | -0.10113 | -0.51125 | -0.81803 | 1.2358 | 1.133 | 1.0328 | 0.88772 | 0.73733 | 0.57878 | 0.39453 | 0.19083 | -0.12148 | -0.78093 | -1.8213 | -2.495 | -2.7976
|  | YATTON KEYNELL | ST |  |  | 0.76254 | 0.63895 | 0.51898 | 0.3547 | 0.18426 | 0.0025769 | -0.21216 | -0.45309 | -0.80736 | -1.5181 | -2.6217 | -3.312 | -3.6218 | 2.0012 | 1.9117 | 1.8239 | 1.7207 | 1.6128 | 1.4936 | 1.3482 | 1.1808 | 0.944 | 0.5184 | -0.10113 | -0.51125 | -0.81803 | 1.2358 | 1.133 | 1.0328 | 0.88772 | 0.73733 | 0.57878 | 0.39453 | 0.19083 | -0.12148 | -0.78093 | -1.8213 | -2.495 | -2.7976
|  | YATTON KEYNELL | FS |  |  | 0.76254 | 0.63895 | 0.51898 | 0.3547 | 0.18426 | 0.0025769 | -0.21216 | -0.45309 | -0.80736 | -1.5181 | -2.6217 | -3.312 | -3.6218 | 2.0012 | 1.9117 | 1.8239 | 1.7207 | 1.6128 | 1.4936 | 1.3482 | 1.1808 | 0.944 | 0.5184 | -0.10113 | -0.51125 | -0.81803 | 1.2358 | 1.133 | 1.0328 | 0.88772 | 0.73733 | 0.57878 | 0.39453 | 0.19083 | -0.12148 | -0.78093 | -1.8213 | -2.495 | -2.7976
AXMINSTER | YEOVIL BSP | YEOVIL | MINIMUM HEADROOM | ST 57690 16833 | YES | 25.1919 | 24.8618 | 24.3673 | 23.7274 | 23.0576 | 22.3496 | 21.5159 | 20.5675 | 19.122 | 14.6003 | 8.1217 | 3.1639 | 0.38928 | 29.3634 | 29.1976 | 28.8307 | 28.4294 | 28.0057 | 27.5514 | 27.0244 | 26.4153 | 25.5489 | 22.8748 | 19.5625 | 16.9638 | 14.7341 | 26.9035 | 26.6031 | 26.1221 | 25.5296 | 24.9052 | 24.2406 | 23.467 | 22.5824 | 21.2496 | 17.128 | 11.5881 | 7.5364 | 5.2876
|  | YEOVIL | CT |  |  | 25.1919 | 24.8618 | 24.3673 | 23.7274 | 23.0576 | 22.3496 | 21.5159 | 20.5675 | 19.122 | 14.6003 | 8.1217 | 3.1639 | 0.38928 | 29.3634 | 29.1976 | 28.8307 | 28.4294 | 28.0057 | 27.5514 | 27.0244 | 26.4153 | 25.5489 | 22.8748 | 19.5625 | 16.9638 | 14.7341 | 26.9035 | 26.6031 | 26.1221 | 25.5296 | 24.9052 | 24.2406 | 23.467 | 22.5824 | 21.2496 | 17.128 | 11.5881 | 7.5364 | 5.2876
|  | YEOVIL | LW |  |  | 25.1919 | 24.8618 | 24.3673 | 23.7274 | 23.0576 | 22.3496 | 21.5159 | 20.5675 | 19.122 | 14.6003 | 8.1217 | 3.1639 | 0.38928 | 29.3634 | 29.1976 | 28.8307 | 28.4294 | 28.0057 | 27.5514 | 27.0244 | 26.4153 | 25.5489 | 22.8748 | 19.5625 | 16.9638 | 14.7341 | 26.9035 | 26.6031 | 26.1221 | 25.5296 | 24.9052 | 24.2406 | 23.467 | 22.5824 | 21.2496 | 17.128 | 11.5881 | 7.5364 | 5.2876
|  | YEOVIL | ST |  |  | 25.1919 | 24.8618 | 24.3673 | 23.7274 | 23.0576 | 22.3496 | 21.5159 | 20.5675 | 19.122 | 14.6003 | 8.1217 | 3.1639 | 0.38928 | 29.3634 | 29.1976 | 28.8307 | 28.4294 | 28.0057 | 27.5514 | 27.0244 | 26.4153 | 25.5489 | 22.8748 | 19.5625 | 16.9638 | 14.7341 | 26.9035 | 26.6031 | 26.1221 | 25.5296 | 24.9052 | 24.2406 | 23.467 | 22.5824 | 21.2496 | 17.128 | 11.5881 | 7.5364 | 5.2876
|  | YEOVIL | FS |  |  | 25.1919 | 24.8618 | 24.3673 | 23.7274 | 23.0576 | 22.3496 | 21.5159 | 20.5675 | 19.122 | 14.6003 | 8.1217 | 3.1639 | 0.38928 | 29.3634 | 29.1976 | 28.8307 | 28.4294 | 28.0057 | 27.5514 | 27.0244 | 26.4153 | 25.5489 | 22.8748 | 19.5625 | 16.9638 | 14.7341 | 26.9035 | 26.6031 | 26.1221 | 25.5296 | 24.9052 | 24.2406 | 23.467 | 22.5824 | 21.2496 | 17.128 | 11.5881 | 7.5364 | 5.2876
AXMINSTER | YEOVIL BSP | YETMINSTER | MINIMUM HEADROOM | ST 60294 10206 | YES | 7.4036 | 7.1771 | 6.8811 | 6.3599 | 5.8107 | 5.1719 | 4.5216 | 3.7673 | 2.8017 | 0.76783 | -1.8098 | -3.1827 | -3.6612 | 10.0532 | 9.9181 | 9.7246 | 9.439 | 9.1332 | 8.7625 | 8.3722 | 7.894 | 7.2796 | 6.165 | 5.035 | 4.4389 | 4.0981 | 8.6994 | 8.4886 | 8.2055 | 7.7402 | 7.2488 | 6.6748 | 6.0858 | 5.3939 | 4.5026 | 2.6933 | 0.44613 | -0.72717 | -1.1328
|  | YETMINSTER | CT |  |  | 7.4036 | 7.1771 | 6.8811 | 6.3599 | 5.8107 | 5.1719 | 4.5216 | 3.7673 | 2.8017 | 0.76783 | -1.8098 | -3.1827 | -3.6612 | 10.0532 | 9.9181 | 9.7246 | 9.439 | 9.1332 | 8.7625 | 8.3722 | 7.894 | 7.2796 | 6.165 | 5.035 | 4.4389 | 4.0981 | 8.6994 | 8.4886 | 8.2055 | 7.7402 | 7.2488 | 6.6748 | 6.0858 | 5.3939 | 4.5026 | 2.6933 | 0.44613 | -0.72717 | -1.1328
|  | YETMINSTER | LW |  |  | 7.4036 | 7.1771 | 6.8811 | 6.3599 | 5.8107 | 5.1719 | 4.5216 | 3.7673 | 2.8017 | 0.76783 | -1.8098 | -3.1827 | -3.6612 | 10.0532 | 9.9181 | 9.7246 | 9.439 | 9.1332 | 8.7625 | 8.3722 | 7.894 | 7.2796 | 6.165 | 5.035 | 4.4389 | 4.0981 | 8.6994 | 8.4886 | 8.2055 | 7.7402 | 7.2488 | 6.6748 | 6.0858 | 5.3939 | 4.5026 | 2.6933 | 0.44613 | -0.72717 | -1.1328
|  | YETMINSTER | ST |  |  | 7.4036 | 7.1771 | 6.8811 | 6.3599 | 5.8107 | 5.1719 | 4.5216 | 3.7673 | 2.8017 | 0.76783 | -1.8098 | -3.1827 | -3.6612 | 10.0532 | 9.9181 | 9.7246 | 9.439 | 9.1332 | 8.7625 | 8.3722 | 7.894 | 7.2796 | 6.165 | 5.035 | 4.4389 | 4.0981 | 8.6994 | 8.4886 | 8.2055 | 7.7402 | 7.2488 | 6.6748 | 6.0858 | 5.3939 | 4.5026 | 2.6933 | 0.44613 | -0.72717 | -1.1328
|  | YETMINSTER | FS |  |  | 7.4036 | 7.1771 | 6.8811 | 6.3599 | 5.8107 | 5.1719 | 4.5216 | 3.7673 | 2.8017 | 0.76783 | -1.8098 | -3.1827 | -3.6612 | 10.0532 | 9.9181 | 9.7246 | 9.439 | 9.1332 | 8.7625 | 8.3722 | 7.894 | 7.2796 | 6.165 | 5.035 | 4.4389 | 4.0981 | 8.6994 | 8.4886 | 8.2055 | 7.7402 | 7.2488 | 6.6748 | 6.0858 | 5.3939 | 4.5026 | 2.6933 | 0.44613 | -0.72717 | -1.1328
AXMINSTER |  | YIEWSLEY | MINIMUM HEADROOM | TQ 05643 80961 |  | 10.2419 | 9.7169 | 8.9334 | 7.8508 | 6.7188 | 5.6181 | 4.4202 | 3.0361 | 1.0274 | -5.0456 | -14.7051 | -21.1443 | -24.7812 | 18.7864 | 18.59 | 18.0264 | 17.3409 | 16.589 | 15.8221 | 14.9813 | 13.9766 | 12.6696 | 8.5734 | 2.3808 | -2.5005 | -7.5509 | 13.0414 | 12.5707 | 11.8446 | 10.8699 | 9.824 | 8.7864 | 7.6483 | 6.3227 | 4.4335 | -1.2657 | -10.0084 | -15.6248 | -18.6203
|  | YIEWSLEY | CT |  |  | 10.2419 | 9.7169 | 8.9334 | 7.8508 | 6.7188 | 5.6181 | 4.4202 | 3.0361 | 1.0274 | -5.0456 | -14.7051 | -21.1443 | -24.7812 | 18.7864 | 18.59 | 18.0264 | 17.3409 | 16.589 | 15.8221 | 14.9813 | 13.9766 | 12.6696 | 8.5734 | 2.3808 | -2.5005 | -7.5509 | 13.0414 | 12.5707 | 11.8446 | 10.8699 | 9.824 | 8.7864 | 7.6483 | 6.3227 | 4.4335 | -1.2657 | -10.0084 | -15.6248 | -18.6203
|  | YIEWSLEY | LW |  |  | 10.2419 | 9.7169 | 8.9334 | 7.8508 | 6.7188 | 5.6181 | 4.4202 | 3.0361 | 1.0274 | -5.0456 | -14.7051 | -21.1443 | -24.7812 | 18.7864 | 18.59 | 18.0264 | 17.3409 | 16.589 | 15.8221 | 14.9813 | 13.9766 | 12.6696 | 8.5734 | 2.3808 | -2.5005 | -7.5509 | 13.0414 | 12.5707 | 11.8446 | 10.8699 | 9.824 | 8.7864 | 7.6483 | 6.3227 | 4.4335 | -1.2657 | -10.0084 | -15.6248 | -18.6203
|  | YIEWSLEY | ST |  |  | 10.2419 | 9.7169 | 8.9334 | 7.8508 | 6.7188 | 5.6181 | 4.4202 | 3.0361 | 1.0274 | -5.0456 | -14.7051 | -21.1443 | -24.7812 | 18.7864 | 18.59 | 18.0264 | 17.3409 | 16.589 | 15.8221 | 14.9813 | 13.9766 | 12.6696 | 8.5734 | 2.3808 | -2.5005 | -7.5509 | 13.0414 | 12.5707 | 11.8446 | 10.8699 | 9.824 | 8.7864 | 7.6483 | 6.3227 | 4.4335 | -1.2657 | -10.0084 | -15.6248 | -18.6203
|  | YIEWSLEY | FS |  |  | 10.2419 | 9.7169 | 8.9334 | 7.8508 | 6.7188 | 5.6181 | 4.4202 | 3.0361 | 1.0274 | -5.0456 | -14.7051 | -21.1443 | -24.7812 | 18.7864 | 18.59 | 18.0264 | 17.3409 | 16.589 | 15.8221 | 14.9813 | 13.9766 | 12.6696 | 8.5734 | 2.3808 | -2.5005 | -7.5509 | 13.0414 | 12.5707 | 11.8446 | 10.8699 | 9.824 | 8.7864 | 7.6483 | 6.3227 | 4.4335 | -1.2657 | -10.0084 | -15.6248 | -18.6203
LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | ZETLAND ROAD | MINIMUM HEADROOM | SU 60592 00043 | YES | 7.7722 | 7.3629 | 6.5473 | 5.3563 | 4.0816 | 2.9268 | 1.7297 | 0.30388 | -1.6922 | -7.3283 | -16.3667 | -22.9543 | -26.6746 | 13.3734 | 13.0488 | 12.4347 | 11.6555 | 10.8214 | 10.025 | 9.1846 | 8.1751 | 6.8752 | 3.0639 | -2.838 | -8.0697 | -13.9723 | 9.5384 | 9.151 | 8.3822 | 7.3121 | 6.1647 | 5.0985 | 3.9843 | 2.651 | 0.8052 | -4.4389 | -12.3863 | -17.8178 | -20.8466
|  | ZETLAND ROAD | CT |  |  | 7.7722 | 7.3629 | 6.5473 | 5.3563 | 4.0816 | 2.9268 | 1.7297 | 0.30388 | -1.6922 | -7.3283 | -16.3667 | -22.9543 | -26.6746 | 13.3734 | 13.0488 | 12.4347 | 11.6555 | 10.8214 | 10.025 | 9.1846 | 8.1751 | 6.8752 | 3.0639 | -2.838 | -8.0697 | -13.9723 | 9.5384 | 9.151 | 8.3822 | 7.3121 | 6.1647 | 5.0985 | 3.9843 | 2.651 | 0.8052 | -4.4389 | -12.3863 | -17.8178 | -20.8466
|  | ZETLAND ROAD | LW |  |  | 7.7722 | 7.3629 | 6.5473 | 5.3563 | 4.0816 | 2.9268 | 1.7297 | 0.30388 | -1.6922 | -7.3283 | -16.3667 | -22.9543 | -26.6746 | 13.3734 | 13.0488 | 12.4347 | 11.6555 | 10.8214 | 10.025 | 9.1846 | 8.1751 | 6.8752 | 3.0639 | -2.838 | -8.0697 | -13.9723 | 9.5384 | 9.151 | 8.3822 | 7.3121 | 6.1647 | 5.0985 | 3.9843 | 2.651 | 0.8052 | -4.4389 | -12.3863 | -17.8178 | -20.8466
|  | ZETLAND ROAD | ST |  |  | 7.7722 | 7.3629 | 6.5473 | 5.3563 | 4.0816 | 2.9268 | 1.7297 | 0.30388 | -1.6922 | -7.3283 | -16.3667 | -22.9543 | -26.6746 | 13.3734 | 13.0488 | 12.4347 | 11.6555 | 10.8214 | 10.025 | 9.1846 | 8.1751 | 6.8752 | 3.0639 | -2.838 | -8.0697 | -13.9723 | 9.5384 | 9.151 | 8.3822 | 7.3121 | 6.1647 | 5.0985 | 3.9843 | 2.651 | 0.8052 | -4.4389 | -12.3863 | -17.8178 | -20.8466
|  | ZETLAND ROAD | FS |  |  | 7.7722 | 7.3629 | 6.5473 | 5.3563 | 4.0816 | 2.9268 | 1.7297 | 0.30388 | -1.6922 | -7.3283 | -16.3667 | -22.9543 | -26.6746 | 13.3734 | 13.0488 | 12.4347 | 11.6555 | 10.8214 | 10.025 | 9.1846 | 8.1751 | 6.8752 | 3.0639 | -2.838 | -8.0697 | -13.9723 | 9.5384 | 9.151 | 8.3822 | 7.3121 | 6.1647 | 5.0985 | 3.9843 | 2.651 | 0.8052 | -4.4389 | -12.3863 | -17.8178 | -20.8466

## Primary Headroom Gen
Grid Supply Point | Bulk Supply Point | Primary Substation | Scenario | Grid Reference | Upstream Constraint (YES / NO) | Generation Headroom Winter (MVA) | [12 empty] | Generation Headroom Summer (MVA) | [12 empty] | Generation Headroom Spring/Autumn (MVA)
[6 empty] | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2035 | 2040 | 2045 | 2050 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2035 | 2040 | 2045 | 2050 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2035 | 2040 | 2045 | 2050
MANNINGTON GSP | BOURNEMOUTH | ALDERNEY | MINIMUM HEADROOM | SZ 04270 95141 | YES | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 25.9143 | 25.8989 | 25.8687 | 25.8386 | 25.8077 | 25.7217 | 25.6357 | 25.5498 | 25.458 | 25.1735 | 24.5859 | 23.9051 | 26.0425 | 26.628 | 26.628 | 26.628 | 26.628 | 26.628 | 26.628 | 26.628 | 26.628 | 26.628 | 26.628 | 26.5904 | 26.5454 | 26.628
|  | ALDERNEY | CT |  |  | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 25.9143 | 25.8989 | 25.8687 | 25.8386 | 25.8077 | 25.7767 | 25.6907 | 25.6048 | 25.5131 | 25.2285 | 24.6409 | 23.9601 | 26.0425 | 26.628 | 26.628 | 26.628 | 26.628 | 26.628 | 26.628 | 26.628 | 26.628 | 26.628 | 26.628 | 26.594 | 26.549 | 26.628
|  | ALDERNEY | LW |  |  | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 25.9143 | 25.8989 | 25.8687 | 25.8386 | 25.8077 | 25.7217 | 25.6357 | 25.5498 | 25.458 | 25.1735 | 24.5859 | 23.9051 | 26.0425 | 26.628 | 26.628 | 26.628 | 26.628 | 26.628 | 26.628 | 26.628 | 26.628 | 26.628 | 26.628 | 26.5904 | 26.5454 | 26.628
|  | ALDERNEY | ST |  |  | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.04 | 25.9145 | 25.9002 | 25.8827 | 25.8615 | 25.811 | 25.7607 | 25.7022 | 25.6396 | 25.4463 | 25.0459 | 24.6011 | 26.0425 | 26.628 | 26.628 | 26.628 | 26.628 | 26.628 | 26.628 | 26.628 | 26.628 | 26.628 | 26.628 | 26.6207 | 26.5914 | 26.628
|  | ALDERNEY | FS |  |  | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.8643 | 26.052 | 25.9969 | 25.9947 | 25.9892 | 25.9828 | 25.9701 | 25.9574 | 25.9413 | 25.9171 | 25.8424 | 25.6834 | 25.495 | 26.0425 | 26.628 | 26.628 | 26.628 | 26.628 | 26.628 | 26.628 | 26.628 | 26.628 | 26.628 | 26.628 | 26.628 | 26.628 | 26.628
BRAMLEY (FLEE) | ALDERSHOT BSP | ALDERSHOT | MINIMUM HEADROOM | SU 85976 48834 | YES | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 29.1343 | 27.494 | 27.4891 | 27.4798 | 27.4707 | 27.4615 | 27.4523 | 27.4445 | 27.4366 | 27.4283 | 27.4025 | 27.349 | 26.5366 | 25.2813 | 28.6229 | 28.6229 | 28.6229 | 28.6229 | 28.6229 | 28.6229 | 28.6229 | 28.6229 | 28.6229 | 28.6229 | 28.6229 | 27.4849 | 26.1902
|  | ALDERSHOT | CT |  |  | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 29.1343 | 27.494 | 27.4891 | 27.4798 | 27.4707 | 27.4615 | 27.4523 | 27.4445 | 27.4366 | 27.4283 | 27.4025 | 27.349 | 26.5366 | 25.2813 | 28.6229 | 28.6229 | 28.6229 | 28.6229 | 28.6229 | 28.6229 | 28.6229 | 28.6229 | 28.6229 | 28.6229 | 28.6229 | 27.4849 | 26.1902
|  | ALDERSHOT | LW |  |  | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 29.229 | 27.4948 | 27.4904 | 27.482 | 27.4738 | 27.4655 | 27.4577 | 27.4498 | 27.442 | 27.4337 | 27.4079 | 27.3543 | 26.6456 | 25.3899 | 28.6229 | 28.6229 | 28.6229 | 28.6229 | 28.6229 | 28.6229 | 28.6229 | 28.6229 | 28.6229 | 28.6229 | 28.6229 | 27.5973 | 26.302
|  | ALDERSHOT | ST |  |  | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 27.4985 | 27.4964 | 27.4933 | 27.4895 | 27.4848 | 27.479 | 27.4732 | 27.4678 | 27.4622 | 27.4446 | 27.408 | 27.3676 | 27.3281 | 28.6229 | 28.6229 | 28.6229 | 28.6229 | 28.6229 | 28.6229 | 28.6229 | 28.6229 | 28.6229 | 28.6229 | 28.6229 | 28.6229 | 28.3425
|  | ALDERSHOT | FS |  |  | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 29.4251 | 27.5014 | 27.5009 | 27.5005 | 27.4993 | 27.4978 | 27.4958 | 27.4938 | 27.4913 | 27.4891 | 27.4823 | 27.4677 | 27.4504 | 27.4328 | 28.6229 | 28.6229 | 28.6229 | 28.6229 | 28.6229 | 28.6229 | 28.6229 | 28.6229 | 28.6229 | 28.6229 | 28.6229 | 28.6229 | 28.6229
MELKSHAM GSP | CHIPPENHAM | ALDERTON | MINIMUM HEADROOM | ST 84609 84059 | YES | 5.0163 | 5.0163 | 5.0163 | 5.0163 | 5.0163 | 5.0152 | 5.0024 | 4.9638 | 4.9264 | 4.8147 | 4.6034 | 4.3737 | 4.1786 | 4.2701 | 4.2431 | 4.1859 | 4.1305 | 4.0755 | 4.0211 | 3.9887 | 3.9534 | 3.9196 | 3.8185 | 3.6248 | 3.4131 | 3.2357 | 3.8423 | 3.8044 | 3.7244 | 3.6468 | 3.5698 | 3.4936 | 3.4489 | 3.4014 | 3.3544 | 3.2145 | 2.9567 | 2.6791 | 2.4368
|  | ALDERTON | CT |  |  | 5.0163 | 5.0163 | 5.0163 | 5.0163 | 5.0163 | 5.0163 | 5.0024 | 4.9638 | 4.9264 | 4.8147 | 4.6034 | 4.3737 | 4.1786 | 4.2701 | 4.2431 | 4.1859 | 4.1305 | 4.0755 | 4.0211 | 3.9887 | 3.9534 | 3.9196 | 3.8185 | 3.6248 | 3.4131 | 3.2357 | 3.8423 | 3.8044 | 3.7244 | 3.6468 | 3.5698 | 3.4936 | 3.4489 | 3.4014 | 3.3544 | 3.2145 | 2.9567 | 2.6791 | 2.4368
|  | ALDERTON | LW |  |  | 5.0163 | 5.0163 | 5.0163 | 5.0163 | 5.0163 | 5.0152 | 5.0129 | 5.007 | 4.9724 | 4.858 | 4.6648 | 4.4474 | 4.2647 | 4.2743 | 4.2496 | 4.1973 | 4.1467 | 4.0964 | 4.0643 | 4.0312 | 3.9948 | 3.9608 | 3.857 | 3.6813 | 3.482 | 3.317 | 3.8482 | 3.8136 | 3.7404 | 3.6694 | 3.5991 | 3.5545 | 3.5091 | 3.4606 | 3.4133 | 3.2707 | 3.031 | 2.7657 | 2.5358
|  | ALDERTON | ST |  |  | 5.0163 | 5.0163 | 5.0163 | 5.0163 | 5.0163 | 5.016 | 5.0154 | 5.0137 | 5.013 | 4.9966 | 4.8746 | 4.7418 | 4.6195 | 4.2808 | 4.2622 | 4.2304 | 4.1913 | 4.1441 | 4.1207 | 4.0974 | 4.0748 | 4.0517 | 3.983 | 3.8727 | 3.7514 | 3.6407 | 3.8573 | 3.8313 | 3.7867 | 3.7319 | 3.6659 | 3.6332 | 3.6008 | 3.5699 | 3.5377 | 3.4429 | 3.29 | 3.1262 | 2.9733
|  | ALDERTON | FS |  |  | 5.0163 | 5.0163 | 5.0163 | 5.0163 | 5.0163 | 5.0163 | 5.0163 | 5.0162 | 5.016 | 5.0146 | 5.0136 | 5.0101 | 5.0071 | 4.313 | 4.3112 | 4.3093 | 4.3009 | 4.2909 | 4.2828 | 4.2748 | 4.2645 | 4.2556 | 4.2289 | 4.1877 | 4.1458 | 4.1065 | 3.9024 | 3.8998 | 3.8972 | 3.8854 | 3.8714 | 3.8601 | 3.8489 | 3.8345 | 3.8221 | 3.7853 | 3.728 | 3.6707 | 3.617
BRAMLEY (FLEE) | ALTON | ALRESFORD | MINIMUM HEADROOM | SU 59684 32511 | YES | 21.3778 | 21.3778 | 21.3778 | 32.3728 | 32.3626 | 32.3465 | 32.3242 | 32.2794 | 32.2716 | 31.8448 | 30.9472 | 30.0225 | 29.1998 | 18.999 | 18.9926 | 18.9789 | 29.7925 | 29.5045 | 29.2155 | 28.9994 | 28.7693 | 28.5586 | 27.9643 | 26.9352 | 25.8765 | 24.9231 | 19.8395 | 19.8317 | 19.815 | 30.7968 | 30.7772 | 30.7563 | 30.722 | 30.6645 | 30.6445 | 30.1114 | 29.0714 | 28.0016 | 27.0373
|  | ALRESFORD | CT |  |  | 21.3778 | 21.3778 | 21.3778 | 32.3763 | 32.3735 | 32.3693 | 32.3631 | 32.3496 | 32.3472 | 31.8448 | 30.9472 | 30.0225 | 29.1998 | 18.999 | 18.9926 | 18.9789 | 29.7925 | 29.5045 | 29.2155 | 28.9994 | 28.7693 | 28.5586 | 27.9643 | 26.9352 | 25.8765 | 24.9231 | 19.8395 | 19.8317 | 19.815 | 30.7968 | 30.7772 | 30.7563 | 30.7378 | 30.7116 | 30.6827 | 30.1114 | 29.0714 | 28.0016 | 27.0373
|  | ALRESFORD | LW |  |  | 21.3778 | 21.3778 | 21.3778 | 32.3728 | 32.3626 | 32.3465 | 32.3242 | 32.2794 | 32.2716 | 32.0805 | 31.1937 | 30.2009 | 29.4013 | 19.0021 | 18.9973 | 18.9872 | 29.972 | 29.8079 | 29.5869 | 29.3544 | 29.0931 | 28.8772 | 28.2562 | 27.2379 | 26.1111 | 25.1807 | 19.8432 | 19.8374 | 19.8251 | 30.8076 | 30.7848 | 30.7566 | 30.722 | 30.6645 | 30.6445 | 30.3919 | 29.3788 | 28.2408 | 27.2995
|  | ALRESFORD | ST |  |  | 21.3778 | 21.3778 | 21.3778 | 32.3767 | 32.3747 | 32.3715 | 32.3668 | 32.3564 | 32.3514 | 32.3244 | 32.2891 | 31.6512 | 31.0943 | 19.0047 | 19.0018 | 18.9968 | 29.9895 | 29.9798 | 29.9699 | 29.8699 | 29.7122 | 29.5652 | 29.1452 | 28.4956 | 27.7667 | 27.1246 | 19.8464 | 19.8429 | 19.8368 | 30.8281 | 30.8168 | 30.8055 | 30.7924 | 30.7733 | 30.76 | 30.71 | 30.62 | 29.9134 | 29.2643
|  | ALRESFORD | FS |  |  | 21.3778 | 21.3778 | 21.3778 | 32.3778 | 32.3777 | 32.3776 | 32.3774 | 32.3769 | 32.3752 | 32.3655 | 32.3578 | 32.3208 | 32.2848 | 19.0091 | 19.0086 | 19.008 | 30.006 | 30.0038 | 30.0012 | 29.9986 | 29.9951 | 29.9907 | 29.9737 | 29.9547 | 29.7166 | 29.476 | 19.8517 | 19.8511 | 19.8504 | 30.848 | 30.8453 | 30.8422 | 30.8391 | 30.8349 | 30.8299 | 30.8113 | 30.7899 | 30.7401 | 30.692
BRAMLEY (FLEE) | ALTON | ALTON LOCAL | MINIMUM HEADROOM | SU 72434 39606 | YES | 50.6853 | 50.6666 | 49.5266 | 49.0534 | 48.7704 | 48.4497 | 48.09 | 47.5718 | 47.4727 | 47.1246 | 46.2747 | 43.9691 | 42.312 | 47.2121 | 47.1734 | 45.9962 | 45.4888 | 45.174 | 44.8253 | 44.4376 | 43.8914 | 43.7626 | 43.3276 | 41.2951 | 38.7888 | 36.8218 | 47.7458 | 47.712 | 46.5438 | 46.0447 | 45.7376 | 45.3956 | 45.0148 | 44.4754 | 44.3537 | 43.6653 | 41.334 | 38.6768 | 36.676
|  | ALTON LOCAL | CT |  |  | 50.7825 | 50.7713 | 50.0873 | 49.8012 | 49.7303 | 49.6522 | 49.5625 | 49.4454 | 49.4139 | 49.3072 | 47.3849 | 45.3534 | 43.6594 | 47.3002 | 47.264 | 46.5323 | 46.2017 | 46.0889 | 45.9689 | 45.8511 | 45.7061 | 45.6448 | 45.0338 | 42.3232 | 40.0596 | 38.0283 | 47.8361 | 47.806 | 47.0858 | 46.766 | 46.6634 | 46.5536 | 46.4426 | 46.3044 | 46.2503 | 45.1602 | 42.3004 | 39.9174 | 37.8798
|  | ALTON LOCAL | LW |  |  | 50.6853 | 50.6666 | 49.5266 | 49.0534 | 48.7704 | 48.4497 | 48.09 | 47.5718 | 47.4727 | 47.1246 | 46.2747 | 43.9691 | 42.312 | 47.2121 | 47.1734 | 45.9962 | 45.4888 | 45.174 | 44.8253 | 44.4376 | 43.8914 | 43.7626 | 43.3276 | 41.2951 | 38.7888 | 36.8218 | 47.7458 | 47.712 | 46.5438 | 46.0447 | 45.7376 | 45.3956 | 45.0148 | 44.4754 | 44.3537 | 43.6653 | 41.334 | 38.6768 | 36.676
|  | ALTON LOCAL | ST |  |  | 50.8311 | 50.8236 | 50.3676 | 50.3247 | 50.2764 | 50.2222 | 50.1597 | 50.0775 | 50.0447 | 49.9238 | 49.7636 | 49.4373 | 48.7799 | 47.3836 | 47.3462 | 46.8702 | 46.8049 | 46.7314 | 46.6565 | 46.5734 | 46.472 | 46.419 | 46.2395 | 45.9844 | 44.9818 | 43.7667 | 47.9111 | 47.8809 | 47.4098 | 47.35 | 47.2826 | 47.2127 | 47.1345 | 47.0378 | 46.9897 | 46.8244 | 46.5092 | 45.0913 | 43.7803
|  | ALTON LOCAL | FS |  |  | 50.8797 | 50.8759 | 50.6479 | 50.629 | 50.6099 | 50.5904 | 50.5705 | 50.5492 | 50.5314 | 50.4499 | 50.3657 | 50.1205 | 49.8624 | 47.4499 | 47.438 | 47.2071 | 47.1825 | 47.1575 | 47.131 | 47.104 | 47.0737 | 47.0481 | 46.944 | 46.8238 | 46.5451 | 46.2557 | 47.9731 | 47.9632 | 47.733 | 47.7098 | 47.6862 | 47.6614 | 47.6362 | 47.608 | 47.5843 | 47.4856 | 47.3742 | 47.1036 | 46.8218
BRAMLEY (ANDO-THAT) | ANDOVER BSP | ANDOVER | MINIMUM HEADROOM | SU 35240 46643 | YES | 42.3211 | 42.3211 | 42.3211 | 42.3204 | 42.319 | 42.3168 | 42.3138 | 42.3078 | 42.3067 | 42.3014 | 42.2884 | 42.2631 | 42.2396 | 39.9173 | 39.9144 | 39.9083 | 39.9016 | 39.8943 | 39.8856 | 39.8761 | 39.8636 | 39.8556 | 39.8 | 39.5602 | 38.8614 | 38.1944 | 41.2782 | 41.2782 | 41.2782 | 41.2775 | 41.2762 | 41.274 | 41.271 | 41.2649 | 41.2639 | 41.2585 | 41.2456 | 40.9403 | 40.2654
|  | ANDOVER | CT |  |  | 42.3211 | 42.3211 | 42.3211 | 42.3209 | 42.3205 | 42.3199 | 42.3191 | 42.3173 | 42.3169 | 42.3152 | 42.3008 | 42.2846 | 42.2665 | 39.9184 | 39.916 | 39.9111 | 39.9061 | 39.9009 | 39.8956 | 39.8883 | 39.88 | 39.8728 | 39.8503 | 39.6377 | 39.0045 | 38.3344 | 41.2782 | 41.2782 | 41.2782 | 41.278 | 41.2776 | 41.2771 | 41.2762 | 41.2744 | 41.2741 | 41.2723 | 41.2579 | 41.0849 | 40.4069
|  | ANDOVER | LW |  |  | 42.3211 | 42.3211 | 42.3211 | 42.3204 | 42.319 | 42.3168 | 42.3138 | 42.3078 | 42.3067 | 42.3014 | 42.2884 | 42.2631 | 42.2396 | 39.9173 | 39.9144 | 39.9083 | 39.9016 | 39.8943 | 39.8856 | 39.8761 | 39.8636 | 39.8556 | 39.8 | 39.5602 | 38.8614 | 38.1944 | 41.2782 | 41.2782 | 41.2782 | 41.2775 | 41.2762 | 41.274 | 41.271 | 41.2649 | 41.2639 | 41.2585 | 41.2456 | 40.9403 | 40.2654
|  | ANDOVER | ST |  |  | 42.3211 | 42.3211 | 42.3211 | 42.3209 | 42.3206 | 42.3202 | 42.3196 | 42.3182 | 42.3175 | 42.3139 | 42.3091 | 42.2923 | 42.2862 | 39.9179 | 39.9156 | 39.9117 | 39.9068 | 39.9008 | 39.8957 | 39.8904 | 39.8846 | 39.8792 | 39.8616 | 39.782 | 39.6272 | 39.2423 | 41.2782 | 41.2782 | 41.2782 | 41.2781 | 41.2778 | 41.2774 | 41.2767 | 41.2753 | 41.2746 | 41.271 | 41.2662 | 41.2495 | 41.2434
|  | ANDOVER | FS |  |  | 42.3211 | 42.3211 | 42.3211 | 42.3211 | 42.321 | 42.321 | 42.321 | 42.3209 | 42.3207 | 42.3194 | 42.3184 | 42.3134 | 42.3085 | 39.9218 | 39.9216 | 39.9214 | 39.9204 | 39.9191 | 39.9176 | 39.916 | 39.914 | 39.9119 | 39.9052 | 39.8949 | 39.8805 | 39.8664 | 41.2782 | 41.2782 | 41.2782 | 41.2782 | 41.2782 | 41.2782 | 41.2782 | 41.2781 | 41.2779 | 41.2766 | 41.2755 | 41.2705 | 41.2656
BRAMLEY (ANDO-THAT) | ANDOVER BSP | ANDOVER EAST | MINIMUM HEADROOM | SU 37953 46433 | YES | 44.9969 | 44.9829 | 44.1313 | 43.9144 | 43.6916 | 43.4606 | 43.2224 | 42.8943 | 42.8302 | 42.6194 | 42.2454 | 41.7233 | 41.2047 | 42.9682 | 42.9486 | 42.0856 | 41.8571 | 41.6223 | 41.3799 | 41.1306 | 40.7919 | 40.7166 | 40.4726 | 40.0791 | 38.8934 | 37.74 | 44.7986 | 44.7789 | 43.9159 | 43.6874 | 43.4525 | 43.2101 | 42.9608 | 42.622 | 42.5467 | 42.3026 | 41.909 | 41.0253 | 39.8716
|  | ANDOVER EAST | CT |  |  | 45.0695 | 45.0611 | 44.5501 | 44.5079 | 44.4653 | 44.4224 | 44.3791 | 44.3339 | 44.3166 | 44.2632 | 43.5948 | 43.2814 | 42.8206 | 43.0414 | 43.0276 | 42.5059 | 42.4527 | 42.3988 | 42.3446 | 42.2902 | 42.2344 | 42.2059 | 42.1193 | 41.4278 | 40.4999 | 39.3668 | 44.8718 | 44.858 | 44.3363 | 44.283 | 44.2291 | 44.1748 | 44.1204 | 44.0646 | 44.036 | 43.9494 | 43.2576 | 42.6318 | 41.4984
|  | ANDOVER EAST | LW |  |  | 44.9969 | 44.9829 | 44.1313 | 43.9144 | 43.6916 | 43.4606 | 43.2224 | 42.8943 | 42.8302 | 42.6194 | 42.2454 | 41.7233 | 41.2047 | 42.9682 | 42.9486 | 42.0856 | 41.8571 | 41.6223 | 41.3799 | 41.1306 | 40.7919 | 40.7166 | 40.4726 | 40.0791 | 38.8934 | 37.74 | 44.7986 | 44.7789 | 43.9159 | 43.6874 | 43.4525 | 43.2101 | 42.9608 | 42.622 | 42.5467 | 42.3026 | 41.909 | 41.0253 | 39.8716
|  | ANDOVER EAST | ST |  |  | 45.1058 | 45.1002 | 44.7595 | 44.7314 | 44.7029 | 44.6743 | 44.6452 | 44.6148 | 44.6024 | 44.5624 | 44.4981 | 44.4279 | 44.3115 | 43.0948 | 43.0689 | 42.7209 | 42.6833 | 42.6434 | 42.61 | 42.5764 | 42.5388 | 42.5187 | 42.4563 | 42.3552 | 42.256 | 42.1482 | 44.9252 | 44.8993 | 44.5512 | 44.5137 | 44.4737 | 44.4402 | 44.4067 | 44.369 | 44.3489 | 44.2864 | 44.1853 | 44.0859 | 43.978
|  | ANDOVER EAST | FS |  |  | 45.1421 | 45.1393 | 44.969 | 44.955 | 44.941 | 44.927 | 44.913 | 44.8989 | 44.8929 | 44.8739 | 44.8441 | 44.8184 | 44.779 | 43.1393 | 43.1269 | 42.9561 | 42.9401 | 42.9236 | 42.908 | 42.8925 | 42.8767 | 42.8677 | 42.8399 | 42.7961 | 42.7573 | 42.7054 | 44.9697 | 44.9574 | 44.7866 | 44.7705 | 44.754 | 44.7384 | 44.7229 | 44.7071 | 44.6981 | 44.6703 | 44.6265 | 44.5876 | 44.5357
BRAMLEY (ANDO-THAT) | ANDOVER BSP | ANDOVER TOWN | MINIMUM HEADROOM | SU 36207 45078 | YES | 22.4377 | 22.4377 | 22.4377 | 22.4371 | 22.4357 | 22.4336 | 22.4307 | 22.4249 | 22.4238 | 22.1303 | 21.4998 | 20.7951 | 20.1185 | 20.9076 | 20.9067 | 20.9048 | 20.9028 | 20.8997 | 20.8907 | 20.8809 | 20.8682 | 20.8599 | 20.8325 | 20.7789 | 20.0372 | 19.2484 | 21.2288 | 21.2132 | 21.1818 | 21.1505 | 21.1186 | 21.0062 | 20.8854 | 20.7623 | 20.6355 | 20.2502 | 19.5349 | 18.737 | 17.968
|  | ANDOVER TOWN | CT |  |  | 22.4377 | 22.4377 | 22.4377 | 22.4375 | 22.4371 | 22.4366 | 22.4358 | 22.434 | 22.4337 | 22.2115 | 21.5798 | 20.884 | 20.2047 | 20.9076 | 20.9067 | 20.9048 | 20.9028 | 20.9006 | 20.8982 | 20.8905 | 20.8819 | 20.8742 | 20.8503 | 20.7954 | 20.1375 | 19.346 | 21.2288 | 21.2132 | 21.1818 | 21.1505 | 21.1186 | 21.0866 | 20.9679 | 20.849 | 20.7228 | 20.3409 | 19.6243 | 18.8353 | 18.0635
|  | ANDOVER TOWN | LW |  |  | 22.4377 | 22.4377 | 22.4377 | 22.4371 | 22.4357 | 22.4336 | 22.4307 | 22.4249 | 22.4238 | 22.1303 | 21.4998 | 20.7951 | 20.1185 | 20.9077 | 20.9068 | 20.9051 | 20.9028 | 20.8997 | 20.8907 | 20.8809 | 20.8682 | 20.8599 | 20.8325 | 20.7789 | 20.0372 | 19.2484 | 21.2308 | 21.2162 | 21.187 | 21.1574 | 21.1268 | 21.0062 | 20.8854 | 20.7623 | 20.6355 | 20.2502 | 19.5349 | 18.737 | 17.968
|  | ANDOVER TOWN | ST |  |  | 22.4377 | 22.4377 | 22.4377 | 22.4376 | 22.4373 | 22.4369 | 22.4363 | 22.4349 | 22.4343 | 22.3522 | 21.9574 | 21.4995 | 21.0587 | 20.9077 | 20.907 | 20.9058 | 20.9041 | 20.9021 | 20.8964 | 20.8905 | 20.8845 | 20.8788 | 20.8602 | 20.828 | 20.7824 | 20.341 | 21.2311 | 21.2185 | 21.1977 | 21.172 | 21.141 | 21.0499 | 20.9596 | 20.8782 | 20.7915 | 20.5308 | 20.0526 | 19.5342 | 19.0337
|  | ANDOVER TOWN | FS |  |  | 22.4377 | 22.4377 | 22.4377 | 22.4377 | 22.4377 | 22.4377 | 22.4376 | 22.4376 | 22.4374 | 22.4361 | 22.4351 | 22.4166 | 22.2645 | 20.9089 | 20.9088 | 20.9087 | 20.9084 | 20.908 | 20.9063 | 20.9046 | 20.9024 | 20.9002 | 20.8932 | 20.8814 | 20.8649 | 20.8486 | 21.2516 | 21.2498 | 21.2481 | 21.243 | 21.237 | 21.2079 | 21.1792 | 21.1423 | 21.1087 | 21.0078 | 20.8223 | 20.6177 | 20.4145
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | ARBORFIELD | MINIMUM HEADROOM | SU 75949 65766 | YES | 21.4305 | 21.4172 | 20.6091 | 20.4666 | 20.3174 | 20.16 | 19.9949 | 19.7694 | 19.7196 | 19.5497 | 19.2518 | 18.8641 | 18.566 | 19.1489 | 19.1357 | 18.3276 | 18.185 | 18.0358 | 17.8785 | 17.6454 | 17.3242 | 17.1715 | 16.6963 | 15.8883 | 14.9725 | 14.2862 | 20.2265 | 20.2133 | 19.4052 | 19.2626 | 19.1134 | 18.9561 | 18.7909 | 18.5655 | 18.5157 | 18.3457 | 18.0479 | 17.6602 | 17.2206
|  | ARBORFIELD | CT |  |  | 21.4994 | 21.4914 | 21.0066 | 20.9656 | 20.9235 | 20.8804 | 20.8356 | 20.7849 | 20.767 | 20.7088 | 20.0421 | 19.7404 | 19.3534 | 19.2178 | 19.2099 | 18.725 | 18.684 | 18.642 | 18.5343 | 18.3927 | 18.2462 | 18.1253 | 17.7619 | 16.585 | 15.7554 | 15.0601 | 20.2954 | 20.2875 | 19.8026 | 19.7617 | 19.7196 | 19.6764 | 19.6317 | 19.5809 | 19.5631 | 19.5048 | 18.8381 | 18.5365 | 17.9916
|  | ARBORFIELD | LW |  |  | 21.4305 | 21.4172 | 20.6091 | 20.4666 | 20.3174 | 20.16 | 19.9949 | 19.7694 | 19.7196 | 19.5497 | 19.2518 | 18.8641 | 18.566 | 19.1489 | 19.1357 | 18.3276 | 18.185 | 18.0358 | 17.8785 | 17.6454 | 17.3242 | 17.1715 | 16.6963 | 15.8883 | 14.9725 | 14.2862 | 20.2265 | 20.2133 | 19.4052 | 19.2626 | 19.1134 | 18.9561 | 18.7909 | 18.5655 | 18.5157 | 18.3457 | 18.0479 | 17.6602 | 17.2206
|  | ARBORFIELD | ST |  |  | 21.5338 | 21.5285 | 21.2053 | 21.1779 | 21.1497 | 21.1207 | 21.0904 | 21.0553 | 21.0407 | 20.9869 | 20.9051 | 20.7723 | 20.6773 | 19.2522 | 19.247 | 18.9237 | 18.8964 | 18.8682 | 18.8391 | 18.8088 | 18.7738 | 18.7591 | 18.6302 | 18.2082 | 17.7349 | 17.3018 | 20.3299 | 20.3246 | 20.0013 | 19.974 | 19.9458 | 19.9167 | 19.8864 | 19.8514 | 19.8367 | 19.783 | 19.7012 | 19.5683 | 19.4733
|  | ARBORFIELD | FS |  |  | 21.5682 | 21.5656 | 21.404 | 21.3907 | 21.3774 | 21.364 | 21.3506 | 21.337 | 21.3303 | 21.3065 | 21.2737 | 21.2277 | 21.1691 | 19.2867 | 19.284 | 19.1224 | 19.1092 | 19.0958 | 19.0825 | 19.0691 | 19.0555 | 19.0488 | 19.025 | 18.9922 | 18.9461 | 18.8876 | 20.3643 | 20.3617 | 20.2 | 20.1868 | 20.1735 | 20.1601 | 20.1467 | 20.1331 | 20.1264 | 20.1026 | 20.0698 | 20.0238 | 19.9652
LOVEDEAN GSP | CHICHESTER & HUNSTON | ARGYLE ROAD | MINIMUM HEADROOM | SZ 93193 99152 | YES | 43.8004 | 43.8004 | 43.8004 | 43.8004 | 43.8004 | 43.8004 | 43.8004 | 43.8004 | 43.8004 | 43.8004 | 43.8004 | 42.9247 | 41.7705 | 40.0494 | 40.0494 | 40.0494 | 40.0494 | 40.0494 | 40.0494 | 40.0494 | 40.0494 | 40.0494 | 40.0494 | 39.3444 | 37.9517 | 36.5515 | 36.9635 | 36.937 | 36.8879 | 36.8375 | 36.7838 | 36.6416 | 36.4984 | 36.355 | 36.2029 | 35.7147 | 34.5688 | 33.1757 | 31.7751
|  | ARGYLE ROAD | CT |  |  | 43.8004 | 43.8004 | 43.8004 | 43.8004 | 43.8004 | 43.8004 | 43.8004 | 43.8004 | 43.8004 | 43.8004 | 43.8004 | 42.9951 | 41.8459 | 40.0494 | 40.0494 | 40.0494 | 40.0494 | 40.0494 | 40.0494 | 40.0494 | 40.0494 | 40.0494 | 40.0494 | 39.433 | 38.0405 | 36.6405 | 36.9636 | 36.937 | 36.888 | 36.8376 | 36.784 | 36.7302 | 36.5873 | 36.4439 | 36.2918 | 35.8036 | 34.6575 | 33.2646 | 31.8641
|  | ARGYLE ROAD | LW |  |  | 43.8004 | 43.8004 | 43.8004 | 43.8004 | 43.8004 | 43.8004 | 43.8004 | 43.8004 | 43.8004 | 43.8004 | 43.8004 | 42.9247 | 41.7705 | 40.0494 | 40.0494 | 40.0494 | 40.0494 | 40.0494 | 40.0494 | 40.0494 | 40.0494 | 40.0494 | 40.0494 | 39.3444 | 37.9517 | 36.5515 | 36.9635 | 36.937 | 36.8879 | 36.8375 | 36.7838 | 36.6416 | 36.4984 | 36.355 | 36.2029 | 35.7147 | 34.5688 | 33.1757 | 31.7751
|  | ARGYLE ROAD | ST |  |  | 43.8004 | 43.8004 | 43.8004 | 43.8004 | 43.8004 | 43.8004 | 43.8004 | 43.8004 | 43.8004 | 43.8004 | 43.8004 | 43.8004 | 43.2552 | 40.0494 | 40.0494 | 40.0494 | 40.0494 | 40.0494 | 40.0494 | 40.0494 | 40.0494 | 40.0494 | 40.0494 | 40.0494 | 39.261 | 38.3688 | 37.1524 | 36.9639 | 36.9397 | 36.9099 | 36.8732 | 36.8007 | 36.7276 | 36.63 | 36.5262 | 36.1926 | 35.4023 | 34.4855 | 33.5929
|  | ARGYLE ROAD | FS |  |  | 43.8004 | 43.8004 | 43.8004 | 43.8004 | 43.8004 | 43.8004 | 43.8004 | 43.8004 | 43.8004 | 43.8004 | 43.8004 | 43.8004 | 43.8004 | 40.0494 | 40.0494 | 40.0494 | 40.0494 | 40.0494 | 40.0494 | 40.0494 | 40.0494 | 40.0494 | 40.0494 | 40.0494 | 40.0494 | 40.0494 | 37.1724 | 36.9948 | 36.9897 | 36.9795 | 36.9674 | 36.9465 | 36.9255 | 36.8996 | 36.8593 | 36.7298 | 36.4092 | 35.9989 | 35.5679
COWLEY GSP | HEADINGTON BSP | ARNCOTT | MINIMUM HEADROOM | SP 60730 18095 | NO | 22.7609 | 22.7609 | 22.3398 | 22.2562 | 22.168 | 22.0725 | 21.9674 | 21.7105 | 21.5868 | 21.2753 | 20.7851 | 20.1399 | 19.8308 | 20.7706 | 20.7291 | 20.2785 | 20.0595 | 19.7194 | 19.4897 | 19.2653 | 18.9682 | 18.8018 | 18.4157 | 17.8388 | 17.1134 | 16.7405 | 20.5548 | 20.1194 | 19.5021 | 19.21 | 18.906 | 18.6955 | 18.4886 | 18.2109 | 18.0649 | 17.7215 | 17.2044 | 16.5344 | 16.2117
|  | ARNCOTT | CT |  |  | 22.7609 | 22.7609 | 22.3398 | 22.3392 | 22.3381 | 22.3364 | 22.3323 | 22.2543 | 22.1521 | 21.9233 | 21.5158 | 21.1151 | 20.8008 | 20.772 | 20.7324 | 20.2848 | 20.2118 | 19.9789 | 19.7957 | 19.6696 | 19.5245 | 19.3797 | 19.0725 | 18.5783 | 18.0973 | 17.717 | 20.5703 | 20.1433 | 19.5441 | 19.3524 | 19.1527 | 18.9955 | 18.8869 | 18.7611 | 18.6368 | 18.3722 | 17.9379 | 17.5122 | 17.1821
|  | ARNCOTT | LW |  |  | 22.7609 | 22.7609 | 22.3398 | 22.2562 | 22.168 | 22.0725 | 21.9674 | 21.7105 | 21.5868 | 21.2753 | 20.7851 | 20.1399 | 19.8308 | 20.7706 | 20.7291 | 20.2785 | 20.0595 | 19.7194 | 19.4897 | 19.2653 | 18.9682 | 18.8018 | 18.4157 | 17.8388 | 17.1134 | 16.7405 | 20.5548 | 20.1194 | 19.5021 | 19.21 | 18.906 | 18.6955 | 18.4886 | 18.2109 | 18.0649 | 17.7215 | 17.2044 | 16.5344 | 16.2117
|  | ARNCOTT | ST |  |  | 22.7609 | 22.7609 | 22.7609 | 22.7604 | 22.7596 | 22.7581 | 22.7556 | 22.7497 | 22.747 | 22.7331 | 22.7149 | 22.4975 | 22.312 | 20.7724 | 20.7666 | 20.7549 | 20.7403 | 20.7184 | 20.7037 | 20.6891 | 20.6656 | 20.565 | 20.3464 | 20.0461 | 19.7316 | 19.4801 | 20.5742 | 20.5114 | 20.3864 | 20.2333 | 20.0555 | 19.9666 | 19.8839 | 19.8 | 19.7134 | 19.5241 | 19.2642 | 18.9855 | 18.7668
|  | ARNCOTT | FS |  |  | 22.7609 | 22.7609 | 22.7609 | 22.7608 | 22.7608 | 22.7608 | 22.7607 | 22.7604 | 22.7595 | 22.7542 | 22.7501 | 22.732 | 22.7145 | 20.7799 | 20.7783 | 20.7751 | 20.7703 | 20.7651 | 20.7619 | 20.7591 | 20.7555 | 20.7515 | 20.7399 | 20.7271 | 20.7006 | 20.673 | 20.6546 | 20.6377 | 20.6034 | 20.5515 | 20.496 | 20.4627 | 20.4332 | 20.3968 | 20.3629 | 20.2891 | 20.1911 | 20.093 | 20.0082
BRAMLEY (FLEE) | BRACKNELL MAIN | ASCOT | MINIMUM HEADROOM | SU 91615 68855 | YES | 45.4924 | 45.4924 | 45.4924 | 45.4918 | 45.4906 | 45.4888 | 45.4862 | 45.481 | 45.4802 | 45.4756 | 45.4646 | 44.8243 | 44.0537 | 43.0961 | 43.0961 | 43.0961 | 43.0955 | 43.0943 | 43.0925 | 43.0899 | 43.0847 | 43.0838 | 42.8847 | 42.1111 | 41.216 | 40.323 | 44.5062 | 44.5062 | 44.5062 | 44.5057 | 44.5045 | 44.5026 | 44.5001 | 44.4949 | 44.494 | 44.2066 | 43.3512 | 42.4211 | 41.5126
|  | ASCOT | CT |  |  | 45.4924 | 45.4924 | 45.4924 | 45.4922 | 45.4919 | 45.4914 | 45.4907 | 45.4891 | 45.4889 | 45.4874 | 45.4751 | 44.8243 | 44.0537 | 43.0961 | 43.0961 | 43.0961 | 43.0959 | 43.0956 | 43.0951 | 43.0944 | 43.0928 | 43.0925 | 42.8847 | 42.1111 | 41.216 | 40.323 | 44.5062 | 44.5062 | 44.5062 | 44.5061 | 44.5057 | 44.5052 | 44.5045 | 44.503 | 44.5027 | 44.2066 | 43.3512 | 42.4211 | 41.5126
|  | ASCOT | LW |  |  | 45.4924 | 45.4924 | 45.4924 | 45.4918 | 45.4906 | 45.4888 | 45.4862 | 45.481 | 45.4802 | 45.4756 | 45.4646 | 44.9308 | 44.1629 | 43.0961 | 43.0961 | 43.0961 | 43.0955 | 43.0943 | 43.0925 | 43.0899 | 43.0847 | 43.0838 | 43.0061 | 42.2339 | 41.3424 | 40.4521 | 44.5062 | 44.5062 | 44.5062 | 44.5057 | 44.5045 | 44.5026 | 44.5001 | 44.4949 | 44.494 | 44.3423 | 43.4883 | 42.5501 | 41.6442
|  | ASCOT | ST |  |  | 45.4924 | 45.4924 | 45.4924 | 45.4923 | 45.492 | 45.4917 | 45.4911 | 45.4899 | 45.4893 | 45.4862 | 45.4822 | 45.4679 | 45.4627 | 43.0961 | 43.0961 | 43.0961 | 43.096 | 43.0957 | 43.0953 | 43.0948 | 43.0936 | 43.093 | 43.0899 | 43.0859 | 42.7986 | 42.2678 | 44.5062 | 44.5062 | 44.5062 | 44.5061 | 44.5059 | 44.5055 | 44.505 | 44.5038 | 44.5032 | 44.5001 | 44.496 | 44.1133 | 43.5261
|  | ASCOT | FS |  |  | 45.4924 | 45.4924 | 45.4924 | 45.4924 | 45.4924 | 45.4924 | 45.4923 | 45.4923 | 45.4921 | 45.491 | 45.4901 | 45.4858 | 45.4817 | 43.0961 | 43.0961 | 43.0961 | 43.0961 | 43.0961 | 43.096 | 43.096 | 43.096 | 43.0958 | 43.0947 | 43.0938 | 43.0895 | 43.0854 | 44.5062 | 44.5062 | 44.5062 | 44.5062 | 44.5062 | 44.5062 | 44.5062 | 44.5061 | 44.5059 | 44.5048 | 44.5039 | 44.4997 | 44.4955
LOVEDEAN GSP | CHICHESTER & HUNSTON | ASHLING ROAD | MINIMUM HEADROOM | SU 84085 06737 | YES | 32.4167 | 32.4038 | 31.6175 | 31.5067 | 36.4943 | 36.3799 | 36.2636 | 36.1204 | 36.0837 | 35.969 | 35.3783 | 33.6124 | 32.0935 | 30.5262 | 30.4895 | 29.685 | 29.5527 | 34.5187 | 34.3824 | 34.2433 | 34.0755 | 33.8288 | 31.69 | 28.872 | 26.767 | 25.0134 | 31.9544 | 31.9415 | 31.1552 | 31.0443 | 36.032 | 35.9175 | 35.8013 | 35.6581 | 35.3669 | 33.1642 | 30.2759 | 28.1201 | 26.3331
|  | ASHLING ROAD | CT |  |  | 32.4837 | 32.476 | 32.0042 | 31.8731 | 36.8405 | 36.7063 | 36.5679 | 36.3754 | 36.3404 | 36.2315 | 35.3783 | 33.6124 | 32.0935 | 30.5942 | 30.5632 | 30.0743 | 29.9228 | 34.8695 | 34.7155 | 34.5543 | 34.3372 | 34.232 | 32.0993 | 28.872 | 26.767 | 25.0134 | 32.0214 | 32.0137 | 31.5419 | 31.4108 | 36.3782 | 36.244 | 36.1055 | 35.9131 | 35.7748 | 33.5782 | 30.2759 | 28.1201 | 26.3331
|  | ASHLING ROAD | LW |  |  | 32.4167 | 32.4038 | 31.6175 | 31.5067 | 36.4943 | 36.3799 | 36.2636 | 36.1204 | 36.0837 | 35.969 | 35.7662 | 34.1735 | 32.7175 | 30.5262 | 30.4895 | 29.685 | 29.5527 | 34.5187 | 34.3824 | 34.2433 | 34.0755 | 33.8288 | 31.69 | 29.1313 | 27.307 | 25.6139 | 31.9544 | 31.9415 | 31.1552 | 31.0443 | 36.032 | 35.9175 | 35.8013 | 35.6581 | 35.3669 | 33.1642 | 30.5306 | 28.6554 | 26.931
|  | ASHLING ROAD | ST |  |  | 32.5172 | 32.5121 | 32.1976 | 32.1718 | 37.246 | 37.2202 | 37.1944 | 37.1687 | 37.1584 | 37.1274 | 37.0759 | 37.0449 | 36.9882 | 30.6645 | 30.622 | 30.2992 | 30.2617 | 35.3227 | 35.2814 | 35.2395 | 35.1971 | 35.1685 | 35.0728 | 33.5493 | 32.4822 | 31.4319 | 32.0549 | 32.0498 | 31.7352 | 31.7095 | 36.7837 | 36.7579 | 36.7321 | 36.7063 | 36.696 | 36.6651 | 35.0473 | 33.9475 | 32.8658
|  | ASHLING ROAD | FS |  |  | 32.5508 | 32.5482 | 32.3909 | 32.378 | 37.4651 | 37.4523 | 37.4394 | 37.4265 | 37.4213 | 37.4058 | 37.3801 | 37.3646 | 37.3362 | 30.7029 | 30.6788 | 30.5191 | 30.501 | 35.5827 | 35.564 | 35.5451 | 35.525 | 35.5127 | 35.4717 | 35.4164 | 35.3836 | 35.3398 | 32.0884 | 32.0859 | 31.9286 | 31.9157 | 37.0028 | 36.9899 | 36.977 | 36.9641 | 36.959 | 36.9435 | 36.9177 | 36.9023 | 36.8739
MELKSHAM GSP | NORRINGTON | ASHTON PARK | MINIMUM HEADROOM | ST 87141 57741 | YES | 31.3906 | 31.3906 | 31.3906 | 31.3875 | 31.3812 | 31.366 | 31.3285 | 31.2771 | 31.2477 | 31.1523 | 30.9045 | 29.3895 | 28.0267 | 25.0259 | 24.792 | 24.4122 | 24.1199 | 23.8503 | 23.5149 | 23.1734 | 22.8175 | 22.4714 | 21.4623 | 19.7657 | 17.9936 | 16.3819 | 27.1082 | 26.8846 | 26.5214 | 26.2419 | 25.9838 | 25.6627 | 25.3356 | 24.9941 | 24.663 | 23.6972 | 22.0839 | 20.4378 | 18.948
|  | ASHTON PARK | CT |  |  | 31.3906 | 31.3906 | 31.3906 | 31.3897 | 31.3879 | 31.3853 | 31.3735 | 31.3415 | 31.3154 | 31.2364 | 31.0531 | 29.7412 | 28.3644 | 25.0615 | 24.847 | 24.5084 | 24.2583 | 24.0329 | 23.8182 | 23.4867 | 23.1502 | 22.8073 | 21.8148 | 20.1214 | 18.3918 | 16.7663 | 27.1421 | 26.9371 | 26.6134 | 26.3742 | 26.1586 | 25.9533 | 25.6362 | 25.3141 | 24.9862 | 24.037 | 22.4169 | 20.8132 | 19.3096
|  | ASHTON PARK | LW |  |  | 31.3906 | 31.3906 | 31.3906 | 31.3875 | 31.3812 | 31.366 | 31.3285 | 31.2771 | 31.2477 | 31.1523 | 30.9045 | 29.3895 | 28.0267 | 25.0259 | 24.792 | 24.4122 | 24.1199 | 23.8503 | 23.5149 | 23.1734 | 22.8175 | 22.4714 | 21.4623 | 19.7657 | 17.9936 | 16.3819 | 27.1082 | 26.8846 | 26.5214 | 26.2419 | 25.9838 | 25.6627 | 25.3356 | 24.9941 | 24.663 | 23.6972 | 22.0839 | 20.4378 | 18.948
|  | ASHTON PARK | ST |  |  | 31.3906 | 31.3906 | 31.3906 | 31.3899 | 31.3887 | 31.3867 | 31.3838 | 31.3768 | 31.3569 | 31.2921 | 31.1917 | 31.0405 | 30.582 | 25.0834 | 24.9111 | 24.6662 | 24.4435 | 24.1997 | 24.0089 | 23.8161 | 23.586 | 23.3496 | 22.6655 | 21.5547 | 20.4456 | 19.3858 | 27.1631 | 26.9984 | 26.7642 | 26.5513 | 26.3182 | 26.1357 | 25.9512 | 25.7309 | 25.5048 | 24.85 | 23.7871 | 22.7233 | 21.7322
|  | ASHTON PARK | FS |  |  | 31.3906 | 31.3906 | 31.3906 | 31.3906 | 31.3905 | 31.3904 | 31.3903 | 31.39 | 31.389 | 31.383 | 31.3782 | 31.3553 | 31.3114 | 25.2584 | 25.1923 | 25.1241 | 25.0632 | 25.005 | 24.9443 | 24.8833 | 24.8072 | 24.7153 | 24.4503 | 24.0271 | 23.6243 | 23.25 | 27.3304 | 27.2673 | 27.2021 | 27.1438 | 27.0882 | 27.0301 | 26.9718 | 26.8991 | 26.8111 | 26.5575 | 26.1527 | 25.7666 | 25.4078
BRAMLEY (FLEE) | BRACKNELL RESERVE | BAGSHOT | MINIMUM HEADROOM | SU 91122 63523 | YES | 36.0366 | 36.027 | 36.0068 | 35.8907 | 35.7682 | 35.6439 | 35.5201 | 35.3348 | 35.3 | 35.1897 | 34.7781 | 34.3351 | 33.7314 | 33.728 | 33.7171 | 33.6941 | 33.5761 | 33.4512 | 33.3245 | 33.199 | 33.0121 | 32.9756 | 32.86 | 32.2914 | 30.9695 | 29.8313 | 30.9713 | 30.8452 | 30.5798 | 30.3006 | 29.9637 | 29.6268 | 29.3584 | 29.0297 | 28.8405 | 28.2678 | 27.0326 | 25.7009 | 24.6465
|  | BAGSHOT | CT |  |  | 36.0382 | 36.0295 | 36.0112 | 35.8907 | 35.7682 | 35.6439 | 35.5201 | 35.3348 | 35.3 | 35.1897 | 34.7781 | 34.3351 | 33.7314 | 33.7299 | 33.7199 | 33.6991 | 33.5761 | 33.4512 | 33.3245 | 33.199 | 33.0121 | 32.9756 | 32.86 | 32.2914 | 30.9695 | 29.8313 | 30.9924 | 30.8779 | 30.6371 | 30.3006 | 29.9637 | 29.6268 | 29.3584 | 29.0297 | 28.8405 | 28.2678 | 27.0326 | 25.7009 | 24.6465
|  | BAGSHOT | LW |  |  | 36.0366 | 36.027 | 36.0068 | 35.9732 | 35.9381 | 35.9086 | 35.8773 | 35.8336 | 35.8161 | 35.7589 | 35.6544 | 35.5123 | 34.9789 | 33.728 | 33.7171 | 33.6941 | 33.6578 | 33.62 | 33.5888 | 33.5559 | 33.5106 | 33.4914 | 33.4289 | 33.1387 | 32.1141 | 31.0736 | 30.9713 | 30.8452 | 30.5798 | 30.3081 | 30.0367 | 29.8617 | 29.6858 | 29.4986 | 29.3268 | 28.8071 | 27.8793 | 26.8484 | 25.8916
|  | BAGSHOT | ST |  |  | 36.0388 | 36.0388 | 36.0314 | 36.0213 | 36.0089 | 35.9984 | 35.9876 | 35.9772 | 35.9674 | 35.9358 | 35.8825 | 35.8078 | 35.7511 | 33.7367 | 33.7313 | 33.7222 | 33.7107 | 33.6966 | 33.6847 | 33.6725 | 33.661 | 33.6501 | 33.6149 | 33.5553 | 33.4741 | 33.1665 | 31.0718 | 31.0097 | 30.9036 | 30.7732 | 30.616 | 30.4854 | 30.3558 | 30.2474 | 30.1322 | 29.7879 | 29.1819 | 28.5313 | 27.9059
|  | BAGSHOT | FS |  |  | 36.0388 | 36.0388 | 36.0388 | 36.0388 | 36.0388 | 36.0388 | 36.0359 | 36.0314 | 36.0277 | 36.0156 | 35.9963 | 35.9698 | 35.9439 | 33.745 | 33.7441 | 33.7432 | 33.7395 | 33.735 | 33.7311 | 33.7272 | 33.7222 | 33.718 | 33.7045 | 33.6828 | 33.6538 | 33.6254 | 31.1671 | 31.1569 | 31.147 | 31.1034 | 31.0519 | 31.0072 | 30.9627 | 30.9059 | 30.8613 | 30.7281 | 30.4952 | 30.2457 | 30.0013
BRAMLEY (ANDO-THAT) | THATCHAM BSP | BALL HILL | MINIMUM HEADROOM | SU 42417 63142 | YES | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 19.1375 | 19.0527 | 18.8733 | 18.6994 | 18.5273 | 18.4365 | 18.3745 | 18.3131 | 18.2467 | 18.0508 | 17.7233 | 17.3826 | 17.0473 | 21.0191 | 21.0191 | 21.0152 | 20.9761 | 20.9033 | 20.8342 | 20.7869 | 20.7401 | 20.6896 | 20.5192 | 20.1928 | 19.8531 | 19.5188
|  | BALL HILL | CT |  |  | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 19.1505 | 19.0729 | 18.9088 | 18.7499 | 18.5924 | 18.4365 | 18.3745 | 18.3131 | 18.2467 | 18.0508 | 17.7233 | 17.3826 | 17.0473 | 21.0191 | 21.0191 | 21.0191 | 20.9875 | 20.952 | 20.8342 | 20.7869 | 20.7401 | 20.6896 | 20.5192 | 20.1928 | 19.8531 | 19.5188
|  | BALL HILL | LW |  |  | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 19.1375 | 19.0527 | 18.8733 | 18.6994 | 18.5273 | 18.4647 | 18.4028 | 18.3414 | 18.2751 | 18.079 | 17.7517 | 17.4107 | 17.075 | 21.0191 | 21.0191 | 21.0152 | 20.9761 | 20.9033 | 20.8557 | 20.8085 | 20.7617 | 20.7112 | 20.5474 | 20.221 | 19.8811 | 19.5464
|  | BALL HILL | ST |  |  | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 19.1629 | 19.1005 | 18.9938 | 18.8627 | 18.7048 | 18.6568 | 18.6093 | 18.5673 | 18.5222 | 18.39 | 18.1719 | 17.9519 | 17.7335 | 21.0191 | 21.0191 | 21.0191 | 21.0129 | 20.9773 | 20.9665 | 20.9558 | 20.9338 | 20.8994 | 20.7988 | 20.6326 | 20.4207 | 20.203
|  | BALL HILL | FS |  |  | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 20.8086 | 19.2704 | 19.2638 | 19.2577 | 19.2288 | 19.1943 | 19.1772 | 19.1602 | 19.1381 | 19.1206 | 19.0696 | 18.9869 | 18.9063 | 18.8294 | 21.0191 | 21.0191 | 21.0191 | 21.0191 | 21.0191 | 21.0191 | 21.0191 | 21.0191 | 21.0191 | 21.0191 | 21.0191 | 21.0191 | 21.0054
BRAMLEY (ANDO-THAT) | ANDOVER BSP | BARTON STACEY | MINIMUM HEADROOM | SU 42075 42720 | YES | 21.952 | 21.946 | 21.9334 | 21.8698 | 21.8049 | 21.7387 | 21.6386 | 21.5065 | 21.449 | 21.274 | 20.8507 | 20.4058 | 20.1216 | 20.1957 | 20.189 | 20.1748 | 20.1097 | 20.0433 | 19.9756 | 19.8702 | 19.7309 | 19.6656 | 19.4678 | 19.0036 | 18.5141 | 18.1861 | 20.6761 | 20.6761 | 20.6761 | 20.6248 | 20.5721 | 20.5181 | 20.461 | 20.3715 | 20.3599 | 20.3207 | 20.1221 | 19.8222 | 19.5037
|  | BARTON STACEY | CT |  |  | 21.952 | 21.946 | 21.9334 | 21.8698 | 21.8049 | 21.7387 | 21.6386 | 21.5065 | 21.449 | 21.274 | 20.8507 | 20.4058 | 20.1216 | 20.1957 | 20.189 | 20.1748 | 20.1097 | 20.0433 | 19.9756 | 19.8702 | 19.7309 | 19.6656 | 19.4678 | 19.0036 | 18.5141 | 18.1861 | 20.6761 | 20.6761 | 20.6761 | 20.6248 | 20.5721 | 20.5181 | 20.461 | 20.3715 | 20.3599 | 20.3207 | 20.1221 | 19.8222 | 19.5037
|  | BARTON STACEY | LW |  |  | 21.9523 | 21.9465 | 21.9343 | 21.9205 | 21.9048 | 21.8555 | 21.8042 | 21.7449 | 21.696 | 21.5456 | 21.285 | 20.9822 | 20.7483 | 20.1961 | 20.1896 | 20.1759 | 20.1606 | 20.1435 | 20.0888 | 20.0308 | 19.9643 | 19.9077 | 19.7343 | 19.4323 | 19.0849 | 18.8071 | 20.6761 | 20.6761 | 20.6761 | 20.6742 | 20.6704 | 20.6644 | 20.6561 | 20.6394 | 20.6365 | 20.6218 | 20.586 | 20.3951 | 20.1256
|  | BARTON STACEY | ST |  |  | 21.9558 | 21.9524 | 21.9466 | 21.939 | 21.9296 | 21.8981 | 21.8664 | 21.8334 | 21.8002 | 21.6987 | 21.5358 | 21.3396 | 21.1738 | 20.2 | 20.1962 | 20.1896 | 20.1812 | 20.1707 | 20.1356 | 20.1002 | 20.0629 | 20.0244 | 19.9075 | 19.7194 | 19.4952 | 19.3009 | 20.6761 | 20.6761 | 20.6761 | 20.6757 | 20.6749 | 20.6737 | 20.672 | 20.6681 | 20.6662 | 20.6562 | 20.643 | 20.5968 | 20.58
|  | BARTON STACEY | FS |  |  | 21.9613 | 21.9609 | 21.9605 | 21.9585 | 21.9563 | 21.9455 | 21.9347 | 21.9208 | 21.908 | 21.869 | 21.8095 | 21.7412 | 21.6758 | 20.2062 | 20.2057 | 20.2052 | 20.2031 | 20.2005 | 20.1884 | 20.1764 | 20.1607 | 20.1465 | 20.1031 | 20.0349 | 19.9574 | 19.8832 | 20.6761 | 20.6761 | 20.6761 | 20.6761 | 20.676 | 20.676 | 20.6759 | 20.6758 | 20.6751 | 20.6715 | 20.6686 | 20.6548 | 20.6414
BRAMLEY (BASI) | BASINGSTOKE T1A & T2A | BASINGSTOKE | MINIMUM HEADROOM | SU 65155 52705 | YES | 40.757 | 40.7381 | 39.9995 | 39.925 | 39.8498 | 39.7669 | 39.5825 | 39.3962 | 39.2416 | 38.7788 | 37.9691 | 37.0851 | 36.2666 | 38.7557 | 38.7439 | 37.8689 | 37.6162 | 37.3627 | 37.1511 | 36.9395 | 36.7263 | 36.5426 | 35.9936 | 34.9773 | 33.9143 | 32.9276 | 39.9504 | 39.8491 | 38.9364 | 38.6922 | 38.4472 | 38.2421 | 38.0371 | 37.8304 | 37.6537 | 37.1118 | 36.1183 | 35.0776 | 34.1131
|  | BASINGSTOKE | CT |  |  | 40.8169 | 40.8018 | 40.3507 | 40.2984 | 40.246 | 40.0484 | 39.8902 | 39.7322 | 39.5878 | 39.1574 | 37.9691 | 37.0851 | 36.2666 | 38.8174 | 38.8103 | 38.161 | 37.9061 | 37.6512 | 37.3993 | 37.2139 | 37.029 | 36.8555 | 36.3367 | 34.9773 | 33.9143 | 32.9276 | 39.9895 | 39.8806 | 39.2313 | 38.986 | 38.7408 | 38.4984 | 38.3195 | 38.141 | 37.9746 | 37.4563 | 36.1183 | 35.0776 | 34.1131
|  | BASINGSTOKE | LW |  |  | 40.757 | 40.7381 | 39.9995 | 39.925 | 39.8498 | 39.7669 | 39.5825 | 39.3962 | 39.2416 | 38.7788 | 37.9927 | 37.2105 | 36.4039 | 38.7557 | 38.7439 | 37.8689 | 37.6162 | 37.3627 | 37.1511 | 36.9395 | 36.7263 | 36.5426 | 35.9936 | 35.0398 | 34.0787 | 33.0955 | 39.9504 | 39.8491 | 38.9364 | 38.6922 | 38.4472 | 38.2421 | 38.0371 | 37.8304 | 37.6537 | 37.1118 | 36.1759 | 35.2372 | 34.276
|  | BASINGSTOKE | ST |  |  | 40.8545 | 40.8459 | 40.5498 | 40.5178 | 40.4838 | 40.4514 | 40.4188 | 40.386 | 40.3676 | 40.1281 | 39.6394 | 39.1518 | 38.6557 | 38.8483 | 38.8435 | 38.554 | 38.4881 | 38.3324 | 38.1978 | 38.0642 | 37.9385 | 37.82 | 37.4696 | 36.8834 | 36.2889 | 35.6782 | 40.1058 | 40.052 | 39.6784 | 39.5509 | 39.4009 | 39.2712 | 39.1424 | 39.021 | 38.9073 | 38.5709 | 38.0024 | 37.4138 | 36.8174
|  | BASINGSTOKE | FS |  |  | 40.8916 | 40.8887 | 40.7435 | 40.7292 | 40.7145 | 40.6998 | 40.6851 | 40.6696 | 40.6615 | 40.6367 | 40.5966 | 40.562 | 40.5162 | 38.8791 | 38.8768 | 38.732 | 38.7201 | 38.7083 | 38.6964 | 38.6845 | 38.6726 | 38.6676 | 38.5727 | 38.3452 | 38.1259 | 37.9028 | 40.2172 | 40.208 | 40.0566 | 40.0143 | 39.9659 | 39.9185 | 39.8713 | 39.8142 | 39.7694 | 39.637 | 39.4185 | 39.208 | 38.9933
NURSLING GSP | VELMORE BSP | BASSETT | MINIMUM HEADROOM | SU 42193 15958 | YES | 43.3574 | 43.3574 | 43.3574 | 43.3002 | 43.2419 | 43.1827 | 43.1209 | 43.0256 | 43.0135 | 42.9748 | 42.7879 | 42.0738 | 40.9488 | 39.9816 | 39.9781 | 39.971 | 39.9067 | 39.8414 | 39.7753 | 39.707 | 39.6053 | 39.5863 | 39.526 | 39.292 | 37.8774 | 36.5647 | 42.5895 | 42.5895 | 42.5895 | 42.5322 | 42.474 | 42.4148 | 42.353 | 42.2577 | 42.2456 | 42.2068 | 41.3085 | 39.8722 | 38.5689
|  | BASSETT | CT |  |  | 43.3574 | 43.3574 | 43.3574 | 43.3002 | 43.2419 | 43.1827 | 43.1209 | 43.0256 | 43.0135 | 42.9748 | 42.7879 | 42.0738 | 40.9488 | 39.9816 | 39.9781 | 39.971 | 39.9067 | 39.8414 | 39.7753 | 39.707 | 39.6053 | 39.5863 | 39.526 | 39.292 | 37.8774 | 36.5647 | 42.5895 | 42.5895 | 42.5895 | 42.5322 | 42.474 | 42.4148 | 42.353 | 42.2577 | 42.2456 | 42.2068 | 41.3085 | 39.8722 | 38.5689
|  | BASSETT | LW |  |  | 43.3574 | 43.3574 | 43.3574 | 43.3266 | 43.2949 | 43.2617 | 43.2272 | 43.175 | 43.1677 | 43.1429 | 43.1021 | 42.5367 | 41.4591 | 39.9817 | 39.9783 | 39.9713 | 39.9337 | 39.895 | 39.8554 | 39.8145 | 39.7558 | 39.7417 | 39.6953 | 39.6073 | 38.3443 | 37.079 | 42.5895 | 42.5895 | 42.5895 | 42.5587 | 42.5269 | 42.4937 | 42.4593 | 42.407 | 42.3998 | 42.375 | 41.6487 | 40.3383 | 39.0832
|  | BASSETT | ST |  |  | 43.3574 | 43.3574 | 43.3574 | 43.3574 | 43.3574 | 43.3574 | 43.3574 | 43.3574 | 43.3574 | 43.3574 | 43.3574 | 43.3574 | 43.3468 | 39.9835 | 39.9813 | 39.9777 | 39.9734 | 39.9681 | 39.9638 | 39.9595 | 39.9551 | 39.9504 | 39.9357 | 39.9033 | 39.8666 | 39.2351 | 42.5895 | 42.5895 | 42.5895 | 42.5895 | 42.5895 | 42.5895 | 42.5895 | 42.5895 | 42.5895 | 42.5895 | 42.5895 | 41.9907 | 41.2116
|  | BASSETT | FS |  |  | 43.3574 | 43.3574 | 43.3574 | 43.3574 | 43.3574 | 43.3574 | 43.3574 | 43.3574 | 43.3574 | 43.3574 | 43.3574 | 43.3574 | 43.3574 | 39.9869 | 39.9866 | 39.9862 | 39.9852 | 39.984 | 39.9824 | 39.9808 | 39.9788 | 39.977 | 39.9713 | 39.9583 | 39.9423 | 39.9258 | 42.5895 | 42.5895 | 42.5895 | 42.5895 | 42.5895 | 42.5895 | 42.5895 | 42.5895 | 42.5895 | 42.5895 | 42.5895 | 42.5895 | 42.5895
NORTH HYDE GSP | NORTH HYDE 22kV | BATH ROAD EAST | MINIMUM HEADROOM | TQ 09097 76885 | YES | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.3628 | 15.3666 | 14.3594 | 14.9943 | 14.993 | 14.9907 | 14.9884 | 14.9859 | 14.9807 | 14.9754 | 14.97 | 14.9644 | 14.8637 | 13.9642 | 12.8145 | 11.6519 | 15.3538 | 15.3487 | 15.3395 | 15.33 | 15.32 | 15.2991 | 15.2569 | 15.2105 | 15.1617 | 14.9303 | 14.015 | 12.8451 | 11.6622
|  | BATH ROAD EAST | CT |  |  | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.403 | 15.4068 | 14.3996 | 14.9943 | 14.993 | 14.9907 | 14.9884 | 14.9859 | 14.9833 | 14.9781 | 14.9727 | 14.9671 | 14.8892 | 14.0106 | 12.8609 | 11.6984 | 15.3538 | 15.3487 | 15.3395 | 15.33 | 15.32 | 15.3098 | 15.2799 | 15.2335 | 15.1848 | 14.9706 | 14.0622 | 12.8923 | 11.7094
|  | BATH ROAD EAST | LW |  |  | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.3628 | 15.3666 | 14.3594 | 14.9943 | 14.993 | 14.9907 | 14.9884 | 14.9859 | 14.9807 | 14.9754 | 14.97 | 14.9644 | 14.8637 | 13.9642 | 12.8145 | 11.6519 | 15.3538 | 15.3487 | 15.3395 | 15.33 | 15.32 | 15.2991 | 15.2569 | 15.2105 | 15.1617 | 14.9303 | 14.015 | 12.8451 | 11.6622
|  | BATH ROAD EAST | ST |  |  | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.2424 | 15.6044 | 15.0004 | 14.9942 | 14.993 | 14.9916 | 14.9899 | 14.988 | 14.986 | 14.9824 | 14.9786 | 14.9655 | 14.586 | 13.8254 | 13.0889 | 15.3782 | 15.3534 | 15.3488 | 15.3431 | 15.3363 | 15.3286 | 15.3206 | 15.306 | 15.2843 | 15.1714 | 14.6477 | 13.8737 | 13.1243
|  | BATH ROAD EAST | FS |  |  | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 15.0012 | 14.9955 | 14.9953 | 14.9948 | 14.9942 | 14.9935 | 14.9929 | 14.9921 | 14.9906 | 14.9855 | 14.9706 | 14.9046 | 14.5637 | 15.3815 | 15.3588 | 15.3576 | 15.3556 | 15.3533 | 15.3507 | 15.348 | 15.3449 | 15.3389 | 15.3186 | 15.2156 | 14.9973 | 14.625
IVER 132KV | LONGFORD | BATH ROAD WEST | MINIMUM HEADROOM | TQ 05814 76820 | YES | 25.2319 | 25.2283 | 25.2208 | 25.2134 | 25.2061 | 25.1933 | 25.1806 | 25.168 | 25.1544 | 25.1138 | 25.0432 | 24.968 | 24.8936 | 31.6801 | 31.6788 | 31.6762 | 31.6737 | 31.6712 | 31.6668 | 31.6624 | 31.658 | 31.6533 | 31.6393 | 31.615 | 31.5891 | 31.5634 | 31.8016 | 31.8016 | 31.8016 | 31.8016 | 31.8016 | 31.8016 | 31.8016 | 31.8016 | 31.8016 | 31.8016 | 31.8016 | 31.8016 | 31.8016
|  | BATH ROAD WEST | CT |  |  | 25.2319 | 25.2283 | 25.2208 | 25.2134 | 25.2061 | 25.1988 | 25.1861 | 25.1734 | 25.1599 | 25.1192 | 25.0486 | 24.9734 | 24.8991 | 31.6801 | 31.6788 | 31.6762 | 31.6737 | 31.6712 | 31.6687 | 31.6643 | 31.6599 | 31.6552 | 31.6412 | 31.6169 | 31.5909 | 31.5653 | 31.8016 | 31.8016 | 31.8016 | 31.8016 | 31.8016 | 31.8016 | 31.8016 | 31.8016 | 31.8016 | 31.8016 | 31.8016 | 31.8016 | 31.8016
|  | BATH ROAD WEST | LW |  |  | 25.2319 | 25.2283 | 25.2208 | 25.2134 | 25.2061 | 25.1933 | 25.1806 | 25.168 | 25.1544 | 25.1138 | 25.0432 | 24.968 | 24.8936 | 31.6801 | 31.6788 | 31.6762 | 31.6737 | 31.6712 | 31.6668 | 31.6624 | 31.658 | 31.6533 | 31.6393 | 31.615 | 31.5891 | 31.5634 | 31.8016 | 31.8016 | 31.8016 | 31.8016 | 31.8016 | 31.8016 | 31.8016 | 31.8016 | 31.8016 | 31.8016 | 31.8016 | 31.8016 | 31.8016
|  | BATH ROAD WEST | ST |  |  | 25.2342 | 25.2322 | 25.2288 | 25.2246 | 25.2196 | 25.2137 | 25.2078 | 25.1992 | 25.19 | 25.1626 | 25.1155 | 25.0669 | 25.0188 | 31.6809 | 31.6802 | 31.679 | 31.6776 | 31.6758 | 31.6738 | 31.6718 | 31.6688 | 31.6656 | 31.6562 | 31.6399 | 31.6232 | 31.6066 | 31.8016 | 31.8016 | 31.8016 | 31.8016 | 31.8016 | 31.8016 | 31.8016 | 31.8016 | 31.8016 | 31.8016 | 31.8016 | 31.8016 | 31.8016
|  | BATH ROAD WEST | FS |  |  | 25.2374 | 25.2371 | 25.2368 | 25.2357 | 25.2343 | 25.2326 | 25.2308 | 25.2286 | 25.2251 | 25.2147 | 25.1967 | 25.1784 | 25.1606 | 31.682 | 31.6819 | 31.6818 | 31.6814 | 31.6809 | 31.6803 | 31.6797 | 31.679 | 31.6777 | 31.6741 | 31.6679 | 31.6616 | 31.6555 | 31.8016 | 31.8016 | 31.8016 | 31.8016 | 31.8016 | 31.8016 | 31.8016 | 31.8016 | 31.8016 | 31.8016 | 31.8016 | 31.8016 | 31.8016
IVER 132KV | UPTON BSP | BEACONSFIELD (END B/B) | MINIMUM HEADROOM | SU 93668 91219 | YES | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | BEACONSFIELD (END B/B) | CT |  |  | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | BEACONSFIELD (END B/B) | LW |  |  | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | BEACONSFIELD (END B/B) | ST |  |  | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | BEACONSFIELD (END B/B) | FS |  |  | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IVER 132KV | DENHAM | BEACONSFIELD (MIDDLE B/B) | MINIMUM HEADROOM | SU 93668 91219 | YES | 13 | 13 | 13 | 13 | 13 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 31.65 | 31.65 | 31.65 | 31.65 | 31.65 | 31.65 | 31.65 | 31.65 | 13 | 13 | 13 | 13 | 13 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4
|  | BEACONSFIELD (MIDDLE B/B) | CT |  |  | 13 | 13 | 13 | 13 | 13 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 31.65 | 31.65 | 31.65 | 31.65 | 31.65 | 31.65 | 31.65 | 31.65 | 13 | 13 | 13 | 13 | 13 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4
|  | BEACONSFIELD (MIDDLE B/B) | LW |  |  | 13 | 13 | 13 | 13 | 13 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 31.65 | 31.65 | 31.65 | 31.65 | 31.65 | 31.65 | 31.65 | 31.65 | 13 | 13 | 13 | 13 | 13 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4
|  | BEACONSFIELD (MIDDLE B/B) | ST |  |  | 13 | 13 | 13 | 13 | 13 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 31.65 | 31.65 | 31.65 | 31.65 | 31.65 | 31.65 | 31.65 | 31.65 | 13 | 13 | 13 | 13 | 13 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4
|  | BEACONSFIELD (MIDDLE B/B) | FS |  |  | 13 | 13 | 13 | 13 | 13 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 31.65 | 31.65 | 31.65 | 31.65 | 31.65 | 31.65 | 31.65 | 31.65 | 13 | 13 | 13 | 13 | 13 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4
BRAMLEY (ANDO-THAT) | THATCHAM BSP | BEENHAM | MINIMUM HEADROOM | SU 58204 69025 | YES | 19.0948 | 19.0832 | 19.0586 | 19.0345 | 19.0096 | 18.9859 | 18.9704 | 18.9485 | 18.9316 | 18.8207 | 18.615 | 18.3908 | 18.2024 | 17.1392 | 17.0932 | 16.9961 | 16.9015 | 16.8074 | 16.7139 | 16.6565 | 16.598 | 16.5376 | 16.3577 | 16.0399 | 15.7084 | 15.4 | 18.3772 | 18.3772 | 18.3772 | 18.3761 | 18.3738 | 18.3702 | 18.3652 | 18.3552 | 18.3534 | 18.3446 | 18.3231 | 18.2811 | 18.1712
|  | BEENHAM | CT |  |  | 19.0948 | 19.0832 | 19.0586 | 19.0345 | 19.0102 | 18.9859 | 18.9704 | 18.9533 | 18.933 | 18.8207 | 18.615 | 18.4 | 18.2062 | 17.1392 | 17.0932 | 16.9961 | 16.9015 | 16.8074 | 16.7139 | 16.6565 | 16.598 | 16.5376 | 16.3577 | 16.0399 | 15.7084 | 15.4 | 18.3772 | 18.3772 | 18.3772 | 18.3769 | 18.3763 | 18.3753 | 18.374 | 18.3709 | 18.3704 | 18.3675 | 18.3435 | 18.3168 | 18.1712
|  | BEENHAM | LW |  |  | 19.0952 | 19.0838 | 19.0596 | 19.0351 | 19.0096 | 18.9917 | 18.9726 | 18.9485 | 18.9316 | 18.8244 | 18.6213 | 18.3908 | 18.2024 | 17.1407 | 17.0955 | 17 | 16.9062 | 16.8121 | 16.7521 | 16.691 | 16.6255 | 16.5639 | 16.3779 | 16.0626 | 15.7157 | 15.4127 | 18.3772 | 18.3772 | 18.3772 | 18.3761 | 18.3738 | 18.3702 | 18.3652 | 18.3552 | 18.3534 | 18.3446 | 18.3231 | 18.2811 | 18.1841
|  | BEENHAM | ST |  |  | 19.0984 | 19.09 | 19.0755 | 19.0576 | 19.0357 | 19.023 | 19.0101 | 18.9982 | 18.9868 | 18.9507 | 18.8434 | 18.6942 | 18.5634 | 17.1536 | 17.1203 | 17.063 | 16.9925 | 16.9073 | 16.8592 | 16.8115 | 16.7713 | 16.7293 | 16.6041 | 16.4008 | 16.1765 | 15.9711 | 18.3772 | 18.3772 | 18.3772 | 18.377 | 18.3765 | 18.3758 | 18.3748 | 18.3724 | 18.3713 | 18.3653 | 18.3574 | 18.3296 | 18.3195
|  | BEENHAM | FS |  |  | 19.113 | 19.1122 | 19.1113 | 19.1075 | 19.1028 | 19.0986 | 19.0944 | 19.089 | 19.0847 | 19.0709 | 19.0505 | 19.0242 | 18.9989 | 17.2113 | 17.2079 | 17.2046 | 17.1893 | 17.1711 | 17.1545 | 17.1381 | 17.117 | 17.1009 | 17.0527 | 16.9773 | 16.8976 | 16.8215 | 18.3772 | 18.3772 | 18.3772 | 18.3772 | 18.3772 | 18.3772 | 18.3771 | 18.377 | 18.3767 | 18.3745 | 18.3728 | 18.3645 | 18.3564
MANNINGTON GSP | SALISBURY | BEMERTON | MINIMUM HEADROOM | SU 11583 31233 | YES | 44.0955 | 44.0955 | 44.0955 | 44.0146 | 43.9319 | 43.847 | 43.7585 | 43.6201 | 43.5723 | 43.4144 | 43.2805 | 42.8489 | 42.7057 | 41.4349 | 41.4317 | 41.4269 | 41.3509 | 41.267 | 41.1783 | 41.0861 | 40.942 | 40.8884 | 40.6891 | 40.3995 | 39.8163 | 39.4296 | 42.6708 | 42.6708 | 42.6708 | 42.5899 | 42.5073 | 42.4223 | 42.3339 | 42.1954 | 42.1477 | 41.9897 | 41.8558 | 41.4242 | 41.1978
|  | BEMERTON | CT |  |  | 44.0955 | 44.0955 | 44.0955 | 44.0856 | 44.0749 | 44.0634 | 44.0504 | 44.0284 | 44.0252 | 44.0125 | 43.9296 | 43.7805 | 43.129 | 41.4349 | 41.4317 | 41.4269 | 41.4137 | 41.4 | 41.3854 | 41.3642 | 41.3339 | 41.2885 | 41.1352 | 40.8193 | 40.1923 | 39.4296 | 42.6708 | 42.6708 | 42.6708 | 42.6609 | 42.6502 | 42.6387 | 42.6257 | 42.6037 | 42.6005 | 42.5878 | 42.4963 | 41.9582 | 41.1978
|  | BEMERTON | LW |  |  | 44.0955 | 44.0955 | 44.0955 | 44.093 | 44.0877 | 44.0795 | 44.0682 | 44.0453 | 44.0414 | 44.0213 | 43.9723 | 43.8182 | 43.1871 | 41.4359 | 41.4333 | 41.4297 | 41.4249 | 41.4179 | 41.4015 | 41.3819 | 41.3508 | 41.3046 | 41.1439 | 40.8619 | 40.2299 | 39.4876 | 42.6708 | 42.6708 | 42.6708 | 42.6683 | 42.6631 | 42.6549 | 42.6435 | 42.6206 | 42.6167 | 42.5966 | 42.539 | 41.9958 | 41.2557
|  | BEMERTON | ST |  |  | 44.0955 | 44.0955 | 44.0955 | 44.0146 | 43.9319 | 43.847 | 43.7585 | 43.6201 | 43.5723 | 43.4144 | 43.2805 | 42.8489 | 42.7057 | 41.4369 | 41.4352 | 41.4331 | 41.3509 | 41.267 | 41.1783 | 41.0861 | 40.942 | 40.8884 | 40.6891 | 40.3995 | 39.8163 | 39.5238 | 42.6708 | 42.6708 | 42.6708 | 42.5899 | 42.5073 | 42.4223 | 42.3339 | 42.1954 | 42.1477 | 41.9897 | 41.8558 | 41.4242 | 41.2586
|  | BEMERTON | FS |  |  | 44.0955 | 44.0955 | 44.0955 | 44.0955 | 44.0955 | 44.0954 | 44.0953 | 44.0951 | 44.0942 | 44.0892 | 44.0853 | 44.0665 | 44.0481 | 41.4507 | 41.4371 | 41.4363 | 41.4358 | 41.4353 | 41.4341 | 41.4329 | 41.4312 | 41.428 | 41.4165 | 41.4018 | 41.373 | 41.3132 | 42.6708 | 42.6708 | 42.6708 | 42.6708 | 42.6708 | 42.6707 | 42.6706 | 42.6704 | 42.6695 | 42.6646 | 42.6606 | 42.6418 | 42.6234
COWLEY GSP | COWLEY LOCAL (2 X 45) | BERINSFIELD | MINIMUM HEADROOM | SU 58382 95467 | NO | 31.9868 | 31.9327 | 31.154 | 30.8924 | 30.5153 | 30.0313 | 29.4778 | 28.8522 | 28.2223 | 25.8448 | 22.4815 | 21.4618 | 20.7368 | 29.7293 | 29.6683 | 28.8705 | 28.5763 | 28.1486 | 27.5973 | 26.966 | 26.2525 | 25.5266 | 22.5412 | 18.2707 | 17.0575 | 16.2113 | 30.9206 | 30.8563 | 30.0491 | 29.7389 | 29.2865 | 28.7024 | 28.033 | 27.2767 | 26.5038 | 23.5834 | 19.4622 | 18.2902 | 17.4698
|  | BERINSFIELD | CT |  |  | 32.0229 | 31.9621 | 31.4234 | 31.1624 | 30.7876 | 30.3656 | 29.8406 | 29.2498 | 28.6307 | 26.2906 | 22.5538 | 21.4618 | 20.7368 | 29.7622 | 29.6928 | 29.1313 | 28.834 | 28.4051 | 27.9214 | 27.3186 | 26.64 | 25.9248 | 22.9689 | 18.3289 | 17.0575 | 16.2113 | 30.9519 | 30.8783 | 30.3056 | 29.9907 | 29.5353 | 29.0215 | 28.3807 | 27.6592 | 26.8971 | 24.0141 | 19.5234 | 18.2902 | 17.4698
|  | BERINSFIELD | LW |  |  | 31.9868 | 31.9327 | 31.154 | 30.8924 | 30.5153 | 30.0313 | 29.4778 | 28.8522 | 28.2223 | 25.8448 | 22.4815 | 21.4623 | 20.7473 | 29.7293 | 29.6683 | 28.8705 | 28.5763 | 28.1486 | 27.5973 | 26.966 | 26.2525 | 25.5266 | 22.5412 | 18.2707 | 17.0719 | 16.2358 | 30.9206 | 30.8563 | 30.0491 | 29.7389 | 29.2865 | 28.7024 | 28.033 | 27.2767 | 26.5038 | 23.5834 | 19.4622 | 18.3016 | 17.4913
|  | BERINSFIELD | ST |  |  | 32.1078 | 32.0803 | 31.754 | 31.6074 | 31.3803 | 31.0817 | 30.7379 | 30.3417 | 29.9156 | 28.2342 | 25.8636 | 25.2444 | 24.8171 | 29.8562 | 29.825 | 29.4886 | 29.3223 | 29.0627 | 28.7203 | 28.3257 | 27.8706 | 27.3785 | 25.3975 | 22.3728 | 21.6006 | 21.0712 | 31.0503 | 31.0173 | 30.6761 | 30.5001 | 30.2246 | 29.8608 | 29.4413 | 28.9575 | 28.4332 | 26.3631 | 23.4458 | 22.6987 | 22.1861
|  | BERINSFIELD | FS |  |  | 32.1607 | 32.1479 | 31.9868 | 31.9126 | 31.805 | 31.6786 | 31.539 | 31.3824 | 31.2121 | 30.5404 | 29.544 | 29.2956 | 29.1322 | 29.913 | 29.8985 | 29.7327 | 29.6484 | 29.5255 | 29.3807 | 29.2207 | 29.041 | 28.8444 | 28.0688 | 26.918 | 26.6347 | 26.4515 | 31.109 | 31.0937 | 30.9256 | 30.8365 | 30.706 | 30.5522 | 30.3822 | 30.1912 | 29.9818 | 29.1554 | 27.9293 | 27.6289 | 27.436
NURSLING GSP | SOUTHAMPTON (2 X 60) | BEVOIS VALLEY | MINIMUM HEADROOM | SU 42648 13187 | YES | 33.7776 | 33.7612 | 32.76 | 32.6779 | 32.5958 | 32.5137 | 32.4317 | 32.3496 | 32.3168 | 32.2183 | 31.1863 | 30.0619 | 28.8614 | 31.4637 | 31.4379 | 30.4181 | 30.2869 | 30.1596 | 30.0222 | 29.8809 | 29.7348 | 29.6357 | 29.3622 | 28.1179 | 26.8197 | 25.4463 | 32.2374 | 32.221 | 31.2197 | 31.1377 | 31.0556 | 30.9735 | 30.8915 | 30.8094 | 30.7766 | 30.6781 | 29.4432 | 28.1399 | 26.7614
|  | BEVOIS VALLEY | CT |  |  | 33.863 | 33.8531 | 33.2524 | 33.2031 | 33.1539 | 33.1046 | 33.0554 | 33.0062 | 32.9865 | 32.9274 | 31.4055 | 30.1262 | 28.9259 | 31.5506 | 31.5322 | 30.9148 | 30.8212 | 30.7293 | 30.6367 | 30.5283 | 30.415 | 30.3291 | 30.095 | 28.348 | 26.8948 | 25.5218 | 32.3228 | 32.3129 | 31.7122 | 31.6629 | 31.6137 | 31.5644 | 31.5152 | 31.466 | 31.4463 | 31.3872 | 29.6737 | 28.2154 | 26.8372
|  | BEVOIS VALLEY | LW |  |  | 33.7776 | 33.7612 | 32.76 | 32.6779 | 32.5958 | 32.5137 | 32.4317 | 32.3496 | 32.3168 | 32.2183 | 31.1863 | 30.0619 | 28.8614 | 31.4637 | 31.4379 | 30.4181 | 30.2869 | 30.1596 | 30.0222 | 29.8809 | 29.7348 | 29.6357 | 29.3622 | 28.1179 | 26.8197 | 25.4463 | 32.2374 | 32.221 | 31.2197 | 31.1377 | 31.0556 | 30.9735 | 30.8915 | 30.8094 | 30.7766 | 30.6781 | 29.4432 | 28.1399 | 26.7614
|  | BEVOIS VALLEY | ST |  |  | 33.9056 | 33.8991 | 33.4986 | 33.4658 | 33.4329 | 33.4001 | 33.3673 | 33.3344 | 33.3213 | 33.2819 | 33.1368 | 32.422 | 31.7002 | 31.5964 | 31.5837 | 31.1733 | 31.1169 | 31.0509 | 30.9801 | 30.9068 | 30.8308 | 30.7724 | 30.6117 | 30.2019 | 29.3727 | 28.5409 | 32.3654 | 32.3589 | 31.9584 | 31.9255 | 31.8927 | 31.8599 | 31.8271 | 31.7942 | 31.7811 | 31.7417 | 31.5312 | 30.6986 | 29.8635
|  | BEVOIS VALLEY | FS |  |  | 33.9483 | 33.945 | 33.7448 | 33.7284 | 33.712 | 33.6955 | 33.6791 | 33.6627 | 33.6562 | 33.6365 | 33.6036 | 33.5839 | 33.5478 | 31.6485 | 31.644 | 31.4425 | 31.4166 | 31.3925 | 31.3661 | 31.3392 | 31.3085 | 31.2842 | 31.2171 | 31.0876 | 30.9564 | 30.8045 | 32.4081 | 32.4048 | 32.2046 | 32.1882 | 32.1718 | 32.1553 | 32.1389 | 32.1225 | 32.1159 | 32.0963 | 32.0634 | 32.0437 | 32.0076
EAST CLAYDON GSP | BICESTER NORTH BSP | BICESTER | MINIMUM HEADROOM | SP 58381 21988 | NO | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 63.7704 | 63.7704 | 63.7704 | 63.7704 | 63.7704 | 63.7704 | 63.7704 | 63.7704 | 63.7704 | 63.7704 | 63.7704 | 63.7704 | 63.7704
|  | BICESTER | CT |  |  | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 63.7704 | 63.7704 | 63.7704 | 63.7704 | 63.7704 | 63.7704 | 63.7704 | 63.7704 | 63.7704 | 63.7704 | 63.7704 | 63.7704 | 63.7704
|  | BICESTER | LW |  |  | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 63.7704 | 63.7704 | 63.7704 | 63.7704 | 63.7704 | 63.7704 | 63.7704 | 63.7704 | 63.7704 | 63.7704 | 63.7704 | 63.7704 | 63.7704
|  | BICESTER | ST |  |  | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 63.7704 | 63.7704 | 63.7704 | 63.7704 | 63.7704 | 63.7704 | 63.7704 | 63.7704 | 63.7704 | 63.7704 | 63.7704 | 63.7704 | 63.7704
|  | BICESTER | FS |  |  | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 65.0844 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 60.8834 | 63.7704 | 63.7704 | 63.7704 | 63.7704 | 63.7704 | 63.7704 | 63.7704 | 63.7704 | 63.7704 | 63.7704 | 63.7704 | 63.7704 | 63.7704
EAST CLAYDON GSP | BICESTER NORTH BSP | BICESTER NORTH | MINIMUM HEADROOM |  |  | 33.8342 | 33.8342 | 33.8342 | 33.8342 | 33.8342 | 33.8342 | 33.8342 | 33.8342 | 33.8342 | 33.8342 | 33.8342 | 33.8342 | 33.8342 | 34.288 | 34.288 | 34.288 | 34.288 | 34.288 | 34.288 | 34.288 | 34.288 | 34.288 | 34.288 | 34.288 | 34.288 | 34.288 | 38.8597 | -3.1959 | -3.591 | -3.6856 | -3.7819 | -3.8799 | -3.9837 | -4.1302 | -4.1581 | -4.2491 | -4.9972 | -5.4811 | -5.687
|  | BICESTER NORTH | CT |  |  | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 38.9158 | -3.1959 | -3.591 | -3.6856 | -3.7819 | -3.8799 | -3.9837 | -4.1302 | -4.1581 | -4.2491 | -4.9972 | -5.4811 | -5.687
|  | BICESTER NORTH | LW |  |  | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 38.8597 | 38.8489 | 38.1905 | 38.1276 | 38.062 | 37.9917 | 37.9163 | 37.8218 | 37.7935 | 37.6962 | 37.5146 | 37.3048 | 37.1758
|  | BICESTER NORTH | ST |  |  | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 38.9439 | 38.9396 | 38.6762 | 38.5962 | 38.5149 | 38.4313 | 38.3446 | 38.2198 | 38.1752 | 38.0284 | 37.8783 | 37.498 | 37.3398
|  | BICESTER NORTH | FS |  |  | 33.8342 | 33.8342 | 33.8342 | 33.8342 | 33.8342 | 33.8342 | 33.8342 | 33.8342 | 33.8342 | 33.8342 | 33.8342 | 33.8342 | 33.8342 | 34.288 | 34.288 | 34.288 | 34.288 | 34.288 | 34.288 | 34.288 | 34.288 | 34.288 | 34.288 | 34.288 | 34.288 | 34.288 | 38.9719 | 38.9698 | 38.8381 | 38.8273 | 38.8165 | 38.8056 | 38.7947 | 38.7836 | 38.778 | 38.7583 | 38.7316 | 38.6958 | 38.6503
LOVEDEAN GSP | CHICHESTER & HUNSTON | BILLINGSHURST | MINIMUM HEADROOM | TQ 08305 26315 | YES | 12.5946 | 12.5946 | 12.5946 | 12.5929 | 12.5894 | 12.5839 | 12.5764 | 12.5611 | 12.5585 | 12.5451 | 12.5124 | 12.4418 | 12.2021 | 9.872 | 9.8099 | 9.6749 | 9.5393 | 9.4043 | 9.2701 | 9.1848 | 9.0975 | 9.0077 | 8.7377 | 8.2357 | 7.6974 | 7.1926 | 9.8625 | 9.7959 | 9.6509 | 9.5053 | 9.3604 | 9.2164 | 9.125 | 9.0316 | 8.9353 | 8.6457 | 8.1093 | 7.5342 | 6.9931
|  | BILLINGSHURST | CT |  |  | 12.5946 | 12.5946 | 12.5946 | 12.5941 | 12.5931 | 12.5917 | 12.5896 | 12.585 | 12.5842 | 12.5798 | 12.5435 | 12.4891 | 12.2021 | 9.88 | 9.814 | 9.6749 | 9.5393 | 9.4043 | 9.2701 | 9.1848 | 9.0975 | 9.0077 | 8.7377 | 8.2357 | 7.6974 | 7.1926 | 9.8712 | 9.8003 | 9.6509 | 9.5053 | 9.3604 | 9.2164 | 9.125 | 9.0316 | 8.9353 | 8.6457 | 8.1093 | 7.5342 | 6.9931
|  | BILLINGSHURST | LW |  |  | 12.5946 | 12.5946 | 12.5946 | 12.5929 | 12.5894 | 12.5839 | 12.5764 | 12.5611 | 12.5585 | 12.5451 | 12.5124 | 12.4418 | 12.238 | 9.8888 | 9.8276 | 9.6985 | 9.5715 | 9.4437 | 9.3543 | 9.2634 | 9.1655 | 9.0739 | 8.7948 | 8.2968 | 7.735 | 7.2386 | 9.8806 | 9.8148 | 9.6762 | 9.54 | 9.403 | 9.3074 | 9.2104 | 9.1064 | 9.0082 | 8.7095 | 8.1771 | 7.5787 | 7.0459
|  | BILLINGSHURST | ST |  |  | 12.5946 | 12.5946 | 12.5946 | 12.5942 | 12.5935 | 12.5925 | 12.5909 | 12.5873 | 12.5856 | 12.5765 | 12.5644 | 12.5223 | 12.507 | 9.872 | 9.8099 | 9.7039 | 9.5734 | 9.4158 | 9.3399 | 9.2642 | 9.2041 | 9.1418 | 8.953 | 8.6292 | 8.2649 | 7.9311 | 9.8625 | 9.7959 | 9.682 | 9.5419 | 9.3728 | 9.2913 | 9.2101 | 9.1459 | 9.0791 | 8.8771 | 8.5302 | 8.1422 | 7.7849
|  | BILLINGSHURST | FS |  |  | 12.5946 | 12.5946 | 12.5946 | 12.5946 | 12.5946 | 12.5945 | 12.5945 | 12.5943 | 12.5937 | 12.5904 | 12.5878 | 12.5752 | 12.563 | 9.9842 | 9.9793 | 9.9746 | 9.9535 | 9.9283 | 9.9037 | 9.8792 | 9.8478 | 9.8237 | 9.751 | 9.6284 | 9.4923 | 9.3603 | 9.9831 | 9.9778 | 9.9727 | 9.95 | 9.923 | 9.8966 | 9.8703 | 9.8366 | 9.8108 | 9.7329 | 9.6015 | 9.4563 | 9.3154
LOVEDEAN GSP | CHICHESTER & HUNSTON | BILSHAM | MINIMUM HEADROOM | SU 97366 01594 | YES | 33.5492 | 33.3493 | 31.9859 | 31.555 | 31.0722 | 30.5329 | 29.9612 | 29.3713 | 28.8556 | 27.188 | 25.6525 | 24.3796 | 23.2373 | 28.1 | 27.8709 | 26.4605 | 25.9748 | 25.4288 | 24.8173 | 24.1683 | 23.4982 | 22.9057 | 20.9884 | 19.2356 | 17.8174 | 16.5123 | 28.2125 | 27.9797 | 26.5633 | 26.0706 | 25.5166 | 24.8959 | 24.2371 | 23.5567 | 22.9544 | 21.0053 | 19.2249 | 17.7963 | 16.4866
|  | BILSHAM | CT |  |  | 33.6564 | 33.4723 | 32.5552 | 32.1557 | 31.7036 | 31.2444 | 30.6844 | 30.0935 | 29.5872 | 27.9471 | 25.748 | 24.3796 | 23.2373 | 28.2097 | 27.9978 | 27.0367 | 26.5852 | 26.0729 | 25.5523 | 24.9149 | 24.2438 | 23.6607 | 21.7709 | 19.3545 | 17.8174 | 16.5123 | 28.3225 | 28.1071 | 27.1404 | 26.6823 | 26.1623 | 25.6338 | 24.9866 | 24.3053 | 23.7124 | 21.7908 | 19.3468 | 17.7963 | 16.4866
|  | BILSHAM | LW |  |  | 33.5492 | 33.3493 | 31.9859 | 31.555 | 31.0722 | 30.5329 | 29.9612 | 29.3713 | 28.8556 | 27.188 | 25.6525 | 24.5367 | 23.4139 | 28.1 | 27.8709 | 26.4605 | 25.9748 | 25.4288 | 24.8173 | 24.1683 | 23.4982 | 22.9057 | 20.9884 | 19.2356 | 17.9488 | 16.6631 | 28.2125 | 27.9797 | 26.5633 | 26.0706 | 25.5166 | 24.8959 | 24.2371 | 23.5567 | 22.9544 | 21.0053 | 19.2249 | 17.927 | 16.6367
|  | BILSHAM | ST |  |  | 33.8331 | 33.6176 | 33.0077 | 32.6931 | 32.3233 | 31.9459 | 31.5455 | 31.0983 | 30.7295 | 29.5051 | 28.4332 | 27.512 | 26.7635 | 28.4074 | 28.1585 | 27.5196 | 27.1674 | 26.7515 | 26.3267 | 25.8757 | 25.3745 | 24.9531 | 23.5526 | 22.3313 | 21.3058 | 20.4608 | 28.5228 | 28.2697 | 27.6271 | 27.2702 | 26.8484 | 26.4176 | 25.9602 | 25.4521 | 25.024 | 23.6011 | 22.3607 | 21.322 | 20.4647
|  | BILSHAM | FS |  |  | 33.9883 | 33.8443 | 33.5621 | 33.4487 | 33.321 | 33.1899 | 33.0545 | 32.9089 | 32.7719 | 32.3157 | 31.9119 | 31.6484 | 31.4021 | 28.5801 | 28.4136 | 28.1205 | 27.9918 | 27.8465 | 27.6972 | 27.543 | 27.377 | 27.2192 | 26.6935 | 26.2307 | 25.9284 | 25.649 | 28.6978 | 28.5285 | 28.234 | 28.1033 | 27.9558 | 27.8042 | 27.6475 | 27.4789 | 27.3185 | 26.7839 | 26.3137 | 26.0065 | 25.7228
FAWLEY GSP | COWES & WOOTTON COMMON BSP | BINSTEAD | MINIMUM HEADROOM | SZ 56409 91399 | YES | 21.3434 | 21.3434 | 21.3434 | 21.3423 | 21.3401 | 21.3367 | 21.3319 | 21.3222 | 21.3205 | 21.312 | 21.2913 | 21.0185 | 20.5557 | 20.0391 | 20.0168 | 19.97 | 19.9233 | 19.8759 | 19.7644 | 19.6524 | 19.5367 | 19.4207 | 19.0735 | 18.4853 | 17.8498 | 17.2568 | 20.838 | 20.8368 | 20.8341 | 20.8304 | 20.8256 | 20.816 | 20.805 | 20.7893 | 20.7764 | 20.5061 | 20.0466 | 19.4847 | 18.9395
|  | BINSTEAD | CT |  |  | 21.3434 | 21.3434 | 21.3434 | 21.3431 | 21.3425 | 21.3416 | 21.3403 | 21.3373 | 21.3368 | 21.334 | 21.311 | 21.1241 | 20.6562 | 20.0434 | 20.0236 | 19.982 | 19.9413 | 19.9005 | 19.8596 | 19.7513 | 19.6422 | 19.5273 | 19.186 | 18.5951 | 17.9755 | 17.3776 | 20.8383 | 20.8371 | 20.8348 | 20.8321 | 20.8292 | 20.826 | 20.8186 | 20.8096 | 20.8026 | 20.598 | 20.136 | 19.6031 | 19.0528
|  | BINSTEAD | LW |  |  | 21.3434 | 21.3434 | 21.3434 | 21.3423 | 21.3401 | 21.3367 | 21.3319 | 21.3222 | 21.3205 | 21.312 | 21.2913 | 21.0185 | 20.5557 | 20.0391 | 20.0168 | 19.97 | 19.9233 | 19.8759 | 19.7644 | 19.6524 | 19.5367 | 19.4207 | 19.0735 | 18.4853 | 17.8498 | 17.2568 | 20.838 | 20.8368 | 20.8341 | 20.8304 | 20.8256 | 20.816 | 20.805 | 20.7893 | 20.7764 | 20.5061 | 20.0466 | 19.4847 | 18.9395
|  | BINSTEAD | ST |  |  | 21.3434 | 21.3434 | 21.3434 | 21.3432 | 21.3427 | 21.3421 | 21.341 | 21.3388 | 21.3377 | 21.3319 | 21.3243 | 21.2976 | 21.2879 | 20.0691 | 20.064 | 20.0556 | 20.0449 | 20.0319 | 19.9713 | 19.9113 | 19.8365 | 19.7573 | 19.5229 | 19.1367 | 18.7277 | 18.3389 | 20.8397 | 20.8395 | 20.839 | 20.8381 | 20.837 | 20.8329 | 20.8285 | 20.8221 | 20.8166 | 20.7977 | 20.5577 | 20.2354 | 19.9327
|  | BINSTEAD | FS |  |  | 21.3434 | 21.3434 | 21.3434 | 21.3434 | 21.3434 | 21.3434 | 21.3433 | 21.3432 | 21.3429 | 21.3408 | 21.3391 | 21.3311 | 21.3234 | 20.0735 | 20.0717 | 20.0699 | 20.0623 | 20.0533 | 20.0405 | 20.0278 | 20.0111 | 19.9804 | 19.8898 | 19.7439 | 19.5949 | 19.4529 | 20.84 | 20.8399 | 20.8398 | 20.8393 | 20.8388 | 20.8381 | 20.8373 | 20.8363 | 20.8342 | 20.827 | 20.8171 | 20.8011 | 20.7856
LOVEDEAN GSP | CHICHESTER & HUNSTON | BIRDHAM | MINIMUM HEADROOM | SZ 81965 99422 | YES | 18.3136 | 18.3136 | 18.3136 | 18.3136 | 18.3136 | 18.3136 | 44.3136 | 44.3136 | 44.3136 | 44.3136 | 43.7416 | 42.9373 | 42.1467 | 15.2996 | 15.2963 | 15.2894 | 15.2827 | 15.2761 | 15.2682 | 40.2604 | 40.2513 | 40.2413 | 40.209 | 39.2887 | 38.4228 | 37.4993 | 16.2058 | 16.2058 | 16.2058 | 16.2058 | 16.2058 | 16.2058 | 42.2058 | 42.2058 | 42.1678 | 41.4659 | 40.4214 | 39.5071 | 38.608
|  | BIRDHAM | CT |  |  | 18.3136 | 18.3136 | 18.3136 | 18.3136 | 18.3136 | 18.3136 | 44.3136 | 44.3136 | 44.3136 | 44.3136 | 43.8742 | 43.0701 | 42.2798 | 15.3005 | 15.2978 | 15.292 | 15.2863 | 15.2807 | 15.2751 | 40.2674 | 40.2583 | 40.2482 | 40.216 | 39.4252 | 38.5747 | 37.6568 | 16.2058 | 16.2058 | 16.2058 | 16.2058 | 16.2058 | 16.2058 | 42.2058 | 42.2058 | 42.2058 | 41.617 | 40.5722 | 39.658 | 38.7594
|  | BIRDHAM | LW |  |  | 18.3136 | 18.3136 | 18.3136 | 18.3136 | 18.3136 | 18.3136 | 44.3136 | 44.3136 | 44.3136 | 44.3136 | 43.7416 | 42.9373 | 42.1467 | 15.2996 | 15.2963 | 15.2894 | 15.2827 | 15.2761 | 15.2682 | 40.2604 | 40.2513 | 40.2413 | 40.209 | 39.2887 | 38.4228 | 37.4993 | 16.2058 | 16.2058 | 16.2058 | 16.2058 | 16.2058 | 16.2058 | 42.2058 | 42.2058 | 42.1678 | 41.4659 | 40.4214 | 39.5071 | 38.608
|  | BIRDHAM | ST |  |  | 18.3136 | 18.3136 | 18.3136 | 18.3136 | 18.3136 | 18.3136 | 44.3136 | 44.3136 | 44.3136 | 44.3136 | 44.3136 | 44.0533 | 43.5391 | 15.3004 | 15.2979 | 15.2937 | 15.2885 | 15.2822 | 15.2771 | 40.272 | 40.2658 | 40.259 | 40.2369 | 40.1427 | 39.6096 | 39.0803 | 16.2058 | 16.2058 | 16.2058 | 16.2058 | 16.2058 | 16.2058 | 42.2058 | 42.2058 | 42.2058 | 42.0716 | 41.3647 | 40.7759 | 40.1912
|  | BIRDHAM | FS |  |  | 18.3136 | 18.3136 | 18.3136 | 18.3136 | 18.3136 | 18.3136 | 44.3136 | 44.3136 | 44.3136 | 44.3136 | 44.3136 | 44.3136 | 44.3136 | 15.3047 | 15.3044 | 15.3042 | 15.3031 | 15.3018 | 15.3002 | 40.2987 | 40.2964 | 40.2938 | 40.2852 | 40.2727 | 40.2629 | 40.2536 | 16.2058 | 16.2058 | 16.2058 | 16.2058 | 16.2058 | 16.2058 | 42.2058 | 42.2058 | 42.2058 | 42.2058 | 42.2058 | 42.2058 | 42.2058
BOTLEY WOOD GSP | NETLEY COMMON BSP | BISHOPS WALTHAM | MINIMUM HEADROOM | SU 56691 16683 | YES | 32.0613 | 31.8518 | 30.4521 | 50.7316 | 50.0939 | 49.6099 | 49.1269 | 48.5313 | 48.2558 | 47.4166 | 46.0015 | 44.4041 | 43.2005 | 27.6498 | 27.4343 | 26.0229 | 45.4578 | 44.7228 | 44.1856 | 43.6523 | 43.0074 | 42.6794 | 41.6862 | 40.0647 | 38.2742 | 36.8816 | 27.4343 | 27.1978 | 25.7274 | 45.9377 | 45.2313 | 44.7098 | 44.1912 | 43.5608 | 43.2483 | 42.3004 | 40.7528 | 39.0371 | 37.7178
|  | BISHOPS WALTHAM | CT |  |  | 32.1156 | 31.8945 | 30.8666 | 51.213 | 50.7611 | 50.3102 | 50.0696 | 49.8283 | 49.6111 | 48.9624 | 47.1749 | 45.8464 | 44.6564 | 27.7031 | 27.4753 | 26.4346 | 45.9051 | 45.3459 | 44.7881 | 44.4974 | 44.2066 | 43.937 | 43.1424 | 41.1638 | 39.6423 | 38.2634 | 27.4853 | 27.2308 | 26.1249 | 46.3949 | 45.8673 | 45.341 | 45.065 | 44.7888 | 44.5346 | 43.7853 | 41.8807 | 40.434 | 39.1283
|  | BISHOPS WALTHAM | LW |  |  | 32.0613 | 31.8518 | 30.4521 | 50.7316 | 50.0939 | 49.6099 | 49.1269 | 48.5313 | 48.2558 | 47.4166 | 46.0015 | 44.4041 | 43.2005 | 27.6498 | 27.4343 | 26.0229 | 45.4578 | 44.7228 | 44.1856 | 43.6523 | 43.0074 | 42.6794 | 41.6862 | 40.0647 | 38.2742 | 36.8816 | 27.4343 | 27.1978 | 25.7274 | 45.9377 | 45.2313 | 44.7098 | 44.1912 | 43.5608 | 43.2483 | 42.3004 | 40.7528 | 39.0371 | 37.7178
|  | BISHOPS WALTHAM | ST |  |  | 32.3477 | 32.1911 | 31.6057 | 52.1573 | 51.8659 | 51.6761 | 51.4937 | 51.3291 | 51.1796 | 50.7387 | 50.0293 | 49.3163 | 48.5802 | 27.941 | 27.7797 | 27.1889 | 46.9338 | 46.6343 | 46.439 | 46.2173 | 46.019 | 45.8337 | 45.2889 | 44.4121 | 43.5353 | 42.6729 | 27.7361 | 27.5646 | 26.9561 | 47.4672 | 47.1271 | 46.9081 | 46.6979 | 46.5095 | 46.3348 | 45.8205 | 44.993 | 44.1643 | 43.3496
|  | BISHOPS WALTHAM | FS |  |  | 32.5567 | 32.4932 | 32.2707 | 52.9918 | 52.9025 | 52.8318 | 52.7646 | 52.6838 | 52.6246 | 52.4498 | 52.1762 | 51.9172 | 51.6559 | 28.1553 | 28.0898 | 27.8668 | 47.786 | 47.6944 | 47.622 | 47.5532 | 47.4705 | 47.4096 | 47.2302 | 46.9491 | 46.6833 | 46.3845 | 27.9615 | 27.892 | 27.6678 | 48.3828 | 48.2863 | 48.2102 | 48.138 | 48.051 | 47.9861 | 47.783 | 47.4646 | 47.164 | 46.8637
NURSLING GSP | VELMORE BSP | BISHOPSTOKE | MINIMUM HEADROOM | SU 46463 18472 | YES | 19.9462 | 19.9462 | 19.9462 | 19.9138 | 19.8804 | 19.8454 | 19.8092 | 19.7542 | 19.7465 | 19.7204 | 19.6731 | 19.535 | 19.4667 | 19.2329 | 19.2321 | 19.2305 | 19.1965 | 19.1615 | 19.1236 | 19.0845 | 19.0266 | 19.0159 | 18.9798 | 18.9166 | 18.8109 | 18.7752 | 19.3979 | 19.3979 | 19.3979 | 19.3654 | 19.332 | 19.297 | 19.2608 | 19.2058 | 19.1982 | 19.172 | 19.133 | 19.0571 | 19.0187
|  | BISHOPSTOKE | CT |  |  | 19.9462 | 19.9462 | 19.9462 | 19.9462 | 19.9462 | 19.9462 | 19.9462 | 19.9462 | 19.9462 | 19.9462 | 19.9406 | 19.8784 | 19.8157 | 19.2329 | 19.2321 | 19.2305 | 19.2289 | 19.2273 | 19.2257 | 19.2228 | 19.2199 | 19.2168 | 19.2068 | 19.1827 | 19.1529 | 19.1229 | 19.3979 | 19.3979 | 19.3979 | 19.3979 | 19.3979 | 19.3979 | 19.3979 | 19.3979 | 19.3979 | 19.3979 | 19.3979 | 19.3979 | 19.3683
|  | BISHOPSTOKE | LW |  |  | 19.9462 | 19.9462 | 19.9462 | 19.9138 | 19.8804 | 19.8454 | 19.8092 | 19.7542 | 19.7465 | 19.7204 | 19.6731 | 19.535 | 19.4667 | 19.2329 | 19.2321 | 19.2305 | 19.1965 | 19.1615 | 19.1236 | 19.0845 | 19.0266 | 19.0159 | 18.9798 | 18.9166 | 18.8109 | 18.7752 | 19.3979 | 19.3979 | 19.3979 | 19.3654 | 19.332 | 19.297 | 19.2608 | 19.2058 | 19.1982 | 19.172 | 19.133 | 19.0571 | 19.0187
|  | BISHOPSTOKE | ST |  |  | 19.9462 | 19.9462 | 19.9462 | 19.9462 | 19.9462 | 19.9462 | 19.9462 | 19.9462 | 19.9462 | 19.9462 | 19.9462 | 19.9327 | 19.8929 | 19.2333 | 19.2329 | 19.2321 | 19.2312 | 19.2301 | 19.2281 | 19.2261 | 19.2242 | 19.2221 | 19.2153 | 19.1985 | 19.1789 | 19.1599 | 19.3979 | 19.3979 | 19.3979 | 19.3979 | 19.3979 | 19.3979 | 19.3979 | 19.3979 | 19.3979 | 19.3979 | 19.3979 | 19.3979 | 19.3979
|  | BISHOPSTOKE | FS |  |  | 19.9462 | 19.9462 | 19.9462 | 19.9462 | 19.9462 | 19.9462 | 19.9462 | 19.9462 | 19.9462 | 19.9462 | 19.9462 | 19.9462 | 19.9462 | 19.2339 | 19.2338 | 19.2337 | 19.2334 | 19.2331 | 19.2324 | 19.2318 | 19.231 | 19.2302 | 19.2275 | 19.2207 | 19.2119 | 19.2026 | 19.3979 | 19.3979 | 19.3979 | 19.3979 | 19.3979 | 19.3979 | 19.3979 | 19.3979 | 19.3979 | 19.3979 | 19.3979 | 19.3979 | 19.3979
BOTLEY WOOD GSP | NETLEY COMMON BSP | BITTERNE | MINIMUM HEADROOM | SU 45116 13082 | YES | 16.6138 | 16.6138 | 16.6138 | 16.4947 | 16.3486 | 16.196 | 16.0379 | 15.7976 | 15.7644 | 15.6503 | 15.4779 | 14.0142 | 12.2966 | 14.9648 | 14.9633 | 14.9609 | 14.8419 | 14.6936 | 14.5332 | 14.367 | 14.1186 | 14.0769 | 13.9336 | 12.823 | 10.5857 | 8.5663 | 15.5047 | 15.5047 | 15.5047 | 15.3856 | 15.2395 | 15.0869 | 14.9287 | 14.6885 | 14.6551 | 14.5117 | 14.1563 | 11.8714 | 9.858
|  | BITTERNE | CT |  |  | 16.6138 | 16.6138 | 16.6138 | 16.6138 | 16.6138 | 16.6138 | 16.6138 | 16.6138 | 16.6138 | 16.6138 | 16.6138 | 15.5529 | 13.8577 | 14.966 | 14.9648 | 14.963 | 14.961 | 14.9588 | 14.9565 | 14.9485 | 14.9404 | 14.9319 | 14.9027 | 14.054 | 12.1392 | 10.1422 | 15.5047 | 15.5047 | 15.5047 | 15.5047 | 15.5047 | 15.5047 | 15.5047 | 15.5047 | 15.5047 | 15.4808 | 15.3903 | 13.4246 | 11.4337
|  | BITTERNE | LW |  |  | 16.6138 | 16.6138 | 16.6138 | 16.4947 | 16.3486 | 16.196 | 16.0379 | 15.7976 | 15.7644 | 15.6503 | 15.4779 | 14.0142 | 12.2966 | 14.966 | 14.9648 | 14.963 | 14.8419 | 14.6936 | 14.5332 | 14.367 | 14.1186 | 14.0769 | 13.9336 | 12.823 | 10.5857 | 8.5663 | 15.5047 | 15.5047 | 15.5047 | 15.3856 | 15.2395 | 15.0869 | 14.9287 | 14.6885 | 14.6551 | 14.5117 | 14.1563 | 11.8714 | 9.858
|  | BITTERNE | ST |  |  | 16.6138 | 16.6138 | 16.6138 | 16.5883 | 16.5623 | 16.5358 | 16.5085 | 16.4661 | 16.4517 | 16.4059 | 16.369 | 16.2369 | 15.173 | 14.9648 | 14.9633 | 14.9609 | 14.9325 | 14.9031 | 14.8717 | 14.8394 | 14.7915 | 14.7713 | 14.7053 | 14.4288 | 13.0329 | 11.7656 | 15.5047 | 15.5047 | 15.5047 | 15.4792 | 15.4532 | 15.4267 | 15.3993 | 15.357 | 15.3426 | 15.2834 | 15.1868 | 14.3489 | 13.0509
|  | BITTERNE | FS |  |  | 16.6138 | 16.6138 | 16.6138 | 16.6041 | 16.5946 | 16.5851 | 16.5755 | 16.5603 | 16.5183 | 16.385 | 16.3215 | 16.1216 | 15.9544 | 14.9669 | 14.9665 | 14.9661 | 14.9558 | 14.9457 | 14.9346 | 14.9233 | 14.9063 | 14.862 | 14.7207 | 14.6323 | 14.3973 | 13.9815 | 15.5047 | 15.5047 | 15.5047 | 15.495 | 15.4855 | 15.476 | 15.4663 | 15.4512 | 15.4092 | 15.2759 | 15.2105 | 14.9754 | 14.7703
MINETY GSP | STRATTON (2 X 60) | BLACK BOURTON | MINIMUM HEADROOM | SP 28349 03818 | YES | 15.0696 | 15.0696 | 15.0696 | 15.067 | 15.0615 | 15.053 | 15.0411 | 15.0173 | 15.0131 | 14.839 | 14.5269 | 14.1662 | 13.9031 | 13.6391 | 13.6391 | 13.6391 | 13.6365 | 13.6133 | 13.5331 | 13.4495 | 13.3566 | 13.2788 | 13.0404 | 12.6288 | 12.1685 | 11.8077 | 14.4439 | 14.4439 | 14.4439 | 14.4413 | 14.4358 | 14.4273 | 14.4154 | 14.3915 | 14.3874 | 14.2575 | 13.8702 | 13.4257 | 13.0804
|  | BLACK BOURTON | CT |  |  | 15.0696 | 15.0696 | 15.0696 | 15.0688 | 15.0673 | 15.0651 | 15.0618 | 15.0546 | 15.0534 | 14.93 | 14.612 | 14.2877 | 14.0118 | 13.6391 | 13.6391 | 13.6391 | 13.6383 | 13.6368 | 13.5957 | 13.5208 | 13.4446 | 13.3695 | 13.1454 | 12.7278 | 12.304 | 11.9303 | 14.4439 | 14.4439 | 14.4439 | 14.4431 | 14.4416 | 14.4394 | 14.4361 | 14.4289 | 14.4277 | 14.3517 | 13.9669 | 13.5589 | 13.2008
|  | BLACK BOURTON | LW |  |  | 15.0696 | 15.0696 | 15.0696 | 15.067 | 15.0615 | 15.053 | 15.0411 | 15.0173 | 15.0131 | 14.839 | 14.5269 | 14.1662 | 13.9031 | 13.6391 | 13.6391 | 13.6391 | 13.6365 | 13.6133 | 13.5331 | 13.4495 | 13.3566 | 13.2788 | 13.0404 | 12.6288 | 12.1685 | 11.8077 | 14.4439 | 14.4439 | 14.4439 | 14.4413 | 14.4358 | 14.4273 | 14.4154 | 14.3915 | 14.3874 | 14.2575 | 13.8702 | 13.4257 | 13.0804
|  | BLACK BOURTON | ST |  |  | 15.0696 | 15.0696 | 15.0696 | 15.0691 | 15.068 | 15.0663 | 15.0638 | 15.0583 | 15.0556 | 15.0413 | 14.8743 | 14.6402 | 14.4498 | 13.6391 | 13.6391 | 13.6391 | 13.6385 | 13.6374 | 13.6358 | 13.604 | 13.5514 | 13.4984 | 13.3373 | 13.0776 | 12.7795 | 12.5256 | 14.4439 | 14.4439 | 14.4439 | 14.4434 | 14.4423 | 14.4406 | 14.4381 | 14.4325 | 14.4299 | 14.4155 | 14.2932 | 14.0148 | 13.7711
|  | BLACK BOURTON | FS |  |  | 15.0696 | 15.0696 | 15.0696 | 15.0696 | 15.0696 | 15.0695 | 15.0694 | 15.0692 | 15.0683 | 15.0631 | 15.059 | 15.0393 | 15.0201 | 13.6391 | 13.6391 | 13.6391 | 13.6391 | 13.6391 | 13.639 | 13.6389 | 13.6386 | 13.6377 | 13.6326 | 13.626 | 13.5217 | 13.4227 | 14.4439 | 14.4439 | 14.4439 | 14.4439 | 14.4439 | 14.4438 | 14.4437 | 14.4435 | 14.4426 | 14.4374 | 14.4333 | 14.4136 | 14.3944
MANNINGTON GSP | LYTCHETT | BLANDFORD | MINIMUM HEADROOM | ST 88810 05536 | YES | 30.7215 | 30.6989 | 29.9551 | 29.8685 | 29.7799 | 29.6742 | 29.562 | 29.4274 | 29.3582 | 29.1522 | 28.7884 | 28.4046 | 28.1205 | 34.7137 | 34.6959 | 33.9621 | 33.8857 | 33.8062 | 33.7148 | 33.4967 | 33.1546 | 32.8611 | 32.0743 | 30.7788 | 29.5412 | 28.429 | 35.5269 | 35.5107 | 34.7804 | 34.7075 | 34.631 | 34.5445 | 34.4521 | 34.3387 | 34.2925 | 34.1459 | 33.8774 | 32.6882 | 31.559
|  | BLANDFORD | CT |  |  | 30.7848 | 30.768 | 30.3148 | 30.257 | 30.2008 | 30.1422 | 30.068 | 29.9848 | 29.9298 | 29.7756 | 29.0033 | 28.5681 | 28.2629 | 34.7762 | 34.7637 | 34.3196 | 34.2711 | 34.2229 | 34.1729 | 34.1135 | 33.8419 | 33.5625 | 32.8275 | 31.1235 | 29.8346 | 28.7017 | 35.5891 | 35.578 | 35.1371 | 35.0917 | 35.0463 | 34.9993 | 34.9448 | 34.8828 | 34.8507 | 34.756 | 34.0789 | 32.9842 | 31.8344
|  | BLANDFORD | LW |  |  | 30.7215 | 30.6989 | 29.9551 | 29.8685 | 29.7799 | 29.6742 | 29.562 | 29.4274 | 29.3582 | 29.1522 | 28.7884 | 28.4046 | 28.1205 | 34.7137 | 34.6959 | 33.9621 | 33.8857 | 33.8062 | 33.7148 | 33.4967 | 33.1546 | 32.8611 | 32.0743 | 30.7788 | 29.5412 | 28.429 | 35.5269 | 35.5107 | 34.7804 | 34.7075 | 34.631 | 34.5445 | 34.4521 | 34.3387 | 34.2925 | 34.1459 | 33.8774 | 32.6882 | 31.559
|  | BLANDFORD | ST |  |  | 30.8173 | 30.8049 | 30.5029 | 30.4546 | 30.4046 | 30.3498 | 30.2929 | 30.2238 | 30.1795 | 30.0463 | 29.8493 | 29.5848 | 29.3894 | 34.8079 | 34.7989 | 34.5029 | 34.462 | 34.4196 | 34.374 | 34.3266 | 34.2683 | 34.1033 | 33.5746 | 32.7508 | 31.9363 | 31.2026 | 35.6206 | 35.6127 | 35.3187 | 35.2803 | 35.2405 | 35.1982 | 35.154 | 35.0994 | 35.0707 | 34.9779 | 34.8451 | 34.6368 | 34.3634
|  | BLANDFORD | FS |  |  | 30.8587 | 30.8545 | 30.7074 | 30.6798 | 30.6528 | 30.6231 | 30.593 | 30.5543 | 30.4912 | 30.2942 | 30.1515 | 29.8484 | 29.5731 | 34.8446 | 34.8412 | 34.6954 | 34.67 | 34.6451 | 34.6185 | 34.5917 | 34.5573 | 34.4987 | 34.3134 | 34.1892 | 33.8134 | 33.3521 | 35.6556 | 35.6525 | 35.5071 | 35.4825 | 35.4582 | 35.4328 | 35.407 | 35.3741 | 35.3171 | 35.1358 | 35.0179 | 34.7354 | 34.4791
COWLEY GSP | WITNEY BSP | BLEDINGTON | MINIMUM HEADROOM | SP 25641 22580 | NO | 6.4335 | 6.3969 | 6.3195 | 6.0259 | 5.7262 | 5.442 | 5.1497 | 4.7312 | 4.6282 | 4.2997 | 3.7843 | 2.9959 | 2.7048 | 6.243 | 6.2392 | 6.231 | 6.0047 | 5.7715 | 5.5309 | 5.2818 | 4.9062 | 4.8494 | 4.6574 | 4.3421 | 3.7353 | 3.6229 | 7.884 | 7.8421 | 7.7535 | 7.4492 | 7.1388 | 6.8476 | 6.5483 | 6.123 | 6.0126 | 5.6622 | 5.1105 | 4.2846 | 3.9566
|  | BLEDINGTON | CT |  |  | 6.443 | 6.4117 | 6.3454 | 6.2625 | 6.18 | 6.0977 | 6.0294 | 5.9507 | 5.8952 | 5.7302 | 5.4189 | 5.0935 | 4.8202 | 6.244 | 6.2407 | 6.2337 | 6.2084 | 6.1829 | 6.1571 | 6.132 | 6.0961 | 6.0868 | 6.0582 | 5.9538 | 5.8099 | 5.7153 | 7.8948 | 7.859 | 7.7831 | 7.6911 | 7.5994 | 7.508 | 7.4328 | 7.3472 | 7.2843 | 7.0974 | 6.7499 | 6.3869 | 6.0767
|  | BLEDINGTON | LW |  |  | 6.4335 | 6.3969 | 6.3195 | 6.0259 | 5.7262 | 5.442 | 5.1497 | 4.7312 | 4.6282 | 4.2997 | 3.7843 | 2.9959 | 2.7048 | 6.243 | 6.2392 | 6.231 | 6.0047 | 5.7715 | 5.5309 | 5.2818 | 4.9062 | 4.8494 | 4.6574 | 4.3421 | 3.7353 | 3.6229 | 7.884 | 7.8421 | 7.7535 | 7.4492 | 7.1388 | 6.8476 | 6.5483 | 6.123 | 6.0126 | 5.6622 | 5.1105 | 4.2846 | 3.9566
|  | BLEDINGTON | ST |  |  | 6.4431 | 6.4155 | 6.3683 | 6.3104 | 6.2405 | 6.2115 | 6.1829 | 6.1502 | 6.115 | 6.0121 | 5.8444 | 5.6764 | 5.5093 | 6.244 | 6.2411 | 6.2361 | 6.23 | 6.2227 | 6.2196 | 6.2166 | 6.2132 | 6.2095 | 6.1987 | 6.181 | 6.1593 | 6.1083 | 7.8949 | 7.8634 | 7.8094 | 7.7431 | 7.6632 | 7.63 | 7.5973 | 7.5599 | 7.5197 | 7.4021 | 7.2103 | 7.0181 | 6.827
|  | BLEDINGTON | FS |  |  | 6.4908 | 6.488 | 6.4853 | 6.4675 | 6.4475 | 6.4329 | 6.4183 | 6.3982 | 6.3615 | 6.2487 | 6.15 | 5.9789 | 5.8292 | 6.249 | 6.2487 | 6.2485 | 6.2418 | 6.2351 | 6.2288 | 6.2225 | 6.213 | 6.1885 | 6.1111 | 6.0695 | 5.9533 | 5.8553 | 7.9495 | 7.9463 | 7.9432 | 7.9236 | 7.9015 | 7.8855 | 7.8696 | 7.8477 | 7.8091 | 7.6906 | 7.5828 | 7.4029 | 7.2448
BRAMLEY (FLEE) | ALTON | BORDON | MINIMUM HEADROOM | SU 82256 35269 | YES | 38.9777 | 38.9777 | 38.9777 | 38.9751 | 38.9697 | 38.9612 | 38.9494 | 38.9258 | 38.9217 | 38.3745 | 37.0794 | 35.8198 | 34.6911 | 37.5211 | 37.5118 | 37.4965 | 37.4798 | 37.4586 | 37.432 | 37.4006 | 37.2593 | 36.8085 | 35.5197 | 33.9165 | 32.3696 | 30.9631 | 38.083 | 38.0716 | 38.0531 | 38.0332 | 38.0086 | 37.9503 | 37.5264 | 37.0705 | 36.6143 | 35.3105 | 33.6889 | 32.1249 | 30.7018
|  | BORDON | CT |  |  | 38.9777 | 38.9777 | 38.9777 | 38.9769 | 38.9754 | 38.9732 | 38.97 | 38.9628 | 38.9616 | 38.4412 | 37.1401 | 35.9167 | 34.7759 | 37.5211 | 37.5118 | 37.4965 | 37.481 | 37.4636 | 37.4448 | 37.4219 | 37.3123 | 36.8641 | 35.5895 | 33.9803 | 32.4697 | 31.0513 | 38.083 | 38.0716 | 38.0531 | 38.0343 | 38.0134 | 37.9782 | 37.563 | 37.1236 | 36.6701 | 35.3805 | 33.7529 | 32.2251 | 30.7902
|  | BORDON | LW |  |  | 38.9777 | 38.9777 | 38.9777 | 38.9751 | 38.9697 | 38.9612 | 38.9494 | 38.9258 | 38.9217 | 38.3745 | 37.0794 | 35.8198 | 34.6911 | 37.5213 | 37.512 | 37.497 | 37.4798 | 37.4586 | 37.432 | 37.4006 | 37.2593 | 36.8085 | 35.5197 | 33.9165 | 32.3696 | 30.9631 | 38.0832 | 38.0719 | 38.0536 | 38.0332 | 38.0086 | 37.9503 | 37.5264 | 37.0705 | 36.6143 | 35.3105 | 33.6889 | 32.1249 | 30.7018
|  | BORDON | ST |  |  | 38.9777 | 38.9777 | 38.9777 | 38.9772 | 38.9761 | 38.9744 | 38.9719 | 38.9664 | 38.9638 | 38.9496 | 38.7298 | 37.9155 | 37.1621 | 37.5259 | 37.52 | 37.5122 | 37.5027 | 37.4905 | 37.4764 | 37.4607 | 37.4412 | 37.4238 | 37.0199 | 35.9554 | 34.9557 | 34.0218 | 38.0888 | 38.0817 | 38.0722 | 38.0607 | 38.046 | 38.0293 | 38.0106 | 37.9882 | 37.7273 | 36.828 | 35.751 | 34.7403 | 33.7956
|  | BORDON | FS |  |  | 38.9777 | 38.9777 | 38.9777 | 38.9777 | 38.9776 | 38.9776 | 38.9775 | 38.9772 | 38.9764 | 38.9712 | 38.9672 | 38.9477 | 38.9287 | 37.5321 | 37.5299 | 37.5281 | 37.5251 | 37.5213 | 37.5169 | 37.5122 | 37.5064 | 37.4997 | 37.478 | 37.4545 | 37.4184 | 37.3841 | 38.0964 | 38.0937 | 38.0915 | 38.0878 | 38.0833 | 38.0779 | 38.0722 | 38.0651 | 38.0572 | 38.0319 | 38.0042 | 37.9366 | 37.5966
MELKSHAM GSP | AMESBURY | BOSCOMBE DOWN | MINIMUM HEADROOM | SU 17186 41044 | YES | 40.6135 | 40.5898 | 40.552 | 40.524 | 40.4976 | 40.429 | 40.358 | 40.2802 | 40.2106 | 40.0017 | 39.6442 | 39.2542 | 38.9263 | 35.6908 | 35.665 | 35.6238 | 35.5935 | 35.565 | 35.4909 | 35.4142 | 35.3308 | 35.2552 | 35.0289 | 34.6424 | 34.223 | 33.8664 | 35.7695 | 35.7418 | 35.6974 | 35.6648 | 35.6343 | 35.5548 | 35.4726 | 35.3838 | 35.3024 | 35.0594 | 34.645 | 34.1974 | 33.8132
|  | BOSCOMBE DOWN | CT |  |  | 40.6158 | 40.5934 | 40.5582 | 40.5339 | 40.5124 | 40.4896 | 40.4237 | 40.3558 | 40.2879 | 40.0873 | 39.7265 | 39.3578 | 39.0227 | 35.6933 | 35.6689 | 35.6306 | 35.6042 | 35.5808 | 35.5562 | 35.4846 | 35.4111 | 35.3372 | 35.1192 | 34.7294 | 34.3313 | 33.9676 | 35.7723 | 35.746 | 35.7047 | 35.6762 | 35.6511 | 35.6247 | 35.5476 | 35.4687 | 35.389 | 35.1542 | 34.7365 | 34.3103 | 33.9189
|  | BOSCOMBE DOWN | LW |  |  | 40.6135 | 40.5898 | 40.552 | 40.524 | 40.4976 | 40.429 | 40.358 | 40.2802 | 40.2106 | 40.0017 | 39.6442 | 39.2542 | 38.9263 | 35.6908 | 35.665 | 35.6238 | 35.5935 | 35.565 | 35.4909 | 35.4142 | 35.3308 | 35.2552 | 35.0289 | 34.6424 | 34.223 | 33.8664 | 35.7695 | 35.7418 | 35.6974 | 35.6648 | 35.6343 | 35.5548 | 35.4726 | 35.3838 | 35.3024 | 35.0594 | 34.645 | 34.1974 | 33.8132
|  | BOSCOMBE DOWN | ST |  |  | 40.6206 | 40.6038 | 40.5802 | 40.5435 | 40.5051 | 40.4507 | 40.3949 | 40.32 | 40.263 | 40.0912 | 39.8359 | 39.4957 | 39.2456 | 35.6986 | 35.6802 | 35.6545 | 35.6162 | 35.5759 | 35.5183 | 35.4593 | 35.3806 | 35.3195 | 35.136 | 34.8613 | 34.5021 | 34.2334 | 35.778 | 35.7582 | 35.7305 | 35.6905 | 35.6485 | 35.5878 | 35.5257 | 35.4433 | 35.3783 | 35.1834 | 34.8901 | 34.5127 | 34.226
|  | BOSCOMBE DOWN | FS |  |  | 40.6368 | 40.6299 | 40.6227 | 40.6114 | 40.6006 | 40.5834 | 40.566 | 40.5422 | 40.4977 | 40.3606 | 40.2351 | 40.021 | 39.832 | 35.7161 | 35.7086 | 35.7008 | 35.689 | 35.6779 | 35.6596 | 35.6413 | 35.6161 | 35.5701 | 35.4284 | 35.2955 | 35.0745 | 34.8789 | 35.7969 | 35.7888 | 35.7804 | 35.7681 | 35.7566 | 35.7374 | 35.718 | 35.6917 | 35.6441 | 35.498 | 35.358 | 35.1303 | 34.9284
MANNINGTON GSP | CHRISTCHURCH BSP | BOSCOMBE EAST | MINIMUM HEADROOM | SZ 11636 92447 | YES | 31.5321 | 31.5321 | 31.5321 | 31.5321 | 31.5321 | 31.5321 | 31.5321 | 31.5321 | 31.5321 | 31.5321 | 31.5321 | 30.3302 | 29.0194 | 29.9484 | 29.9484 | 29.9484 | 29.9484 | 29.9484 | 29.9484 | 29.9484 | 29.9484 | 29.9484 | 29.9321 | 28.8334 | 27.311 | 25.7722 | 30.506 | 30.5033 | 30.4983 | 30.4932 | 30.488 | 30.4827 | 30.4745 | 30.4662 | 30.4574 | 30.4288 | 29.7433 | 28.2358 | 26.7175
|  | BOSCOMBE EAST | CT |  |  | 31.5321 | 31.5321 | 31.5321 | 31.5321 | 31.5321 | 31.5321 | 31.5321 | 31.5321 | 31.5321 | 31.5321 | 31.5321 | 30.3302 | 29.0194 | 29.9484 | 29.9484 | 29.9484 | 29.9484 | 29.9484 | 29.9484 | 29.9484 | 29.9484 | 29.9484 | 29.9321 | 28.8334 | 27.311 | 25.7722 | 30.506 | 30.5033 | 30.4983 | 30.4932 | 30.488 | 30.4827 | 30.4745 | 30.4662 | 30.4574 | 30.4288 | 29.7433 | 28.2358 | 26.7175
|  | BOSCOMBE EAST | LW |  |  | 31.5321 | 31.5321 | 31.5321 | 31.5321 | 31.5321 | 31.5321 | 31.5321 | 31.5321 | 31.5321 | 31.5321 | 31.5321 | 30.3548 | 29.0438 | 29.9484 | 29.9484 | 29.9484 | 29.9484 | 29.9484 | 29.9484 | 29.9484 | 29.9484 | 29.9484 | 29.9335 | 28.8615 | 27.3399 | 25.8008 | 30.5069 | 30.5048 | 30.5008 | 30.4967 | 30.4926 | 30.4844 | 30.4761 | 30.4678 | 30.459 | 30.4304 | 29.7719 | 28.2643 | 26.7458
|  | BOSCOMBE EAST | ST |  |  | 31.5321 | 31.5321 | 31.5321 | 31.5321 | 31.5321 | 31.5321 | 31.5321 | 31.5321 | 31.5321 | 31.5321 | 31.5321 | 31.4468 | 30.6132 | 29.9484 | 29.9484 | 29.9484 | 29.9484 | 29.9484 | 29.9484 | 29.9484 | 29.9484 | 29.9484 | 29.9484 | 29.5994 | 28.622 | 27.6434 | 30.5189 | 30.5068 | 30.5049 | 30.5025 | 30.4997 | 30.4914 | 30.4831 | 30.4775 | 30.4715 | 30.4519 | 30.4036 | 29.5292 | 28.5637
|  | BOSCOMBE EAST | FS |  |  | 31.5321 | 31.5321 | 31.5321 | 31.5321 | 31.5321 | 31.5321 | 31.5321 | 31.5321 | 31.5321 | 31.5321 | 31.5321 | 31.5321 | 31.5321 | 29.9484 | 29.9484 | 29.9484 | 29.9484 | 29.9484 | 29.9484 | 29.9484 | 29.9484 | 29.9484 | 29.9484 | 29.9484 | 29.944 | 29.8069 | 30.5205 | 30.5093 | 30.5089 | 30.5081 | 30.5072 | 30.5045 | 30.5017 | 30.4983 | 30.4959 | 30.4884 | 30.4687 | 30.4429 | 30.4156
EALING GSP | EALING 22kV | BOSTON MANOR ROAD | MINIMUM HEADROOM |  |  | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.7631 | 37.7256 | 37.6875 | 37.6477 | 37.5863 | 37.5786 | 37.5536 | 37.4383 | 37.3066 | 37.2724
|  | BOSTON MANOR ROAD | CT |  |  | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.7631 | 37.7256 | 37.6875 | 37.6477 | 37.5863 | 37.5786 | 37.5536 | 37.4383 | 37.3066 | 37.2724
|  | BOSTON MANOR ROAD | LW |  |  | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8
|  | BOSTON MANOR ROAD | ST |  |  | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8
|  | BOSTON MANOR ROAD | FS |  |  | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8
MANNINGTON GSP | BOURNEMOUTH | BOURNE VALLEY | MINIMUM HEADROOM | SZ 06207 92415 | YES | 47.0786 | 47.0786 | 47.0786 | 47.0445 | 47.0098 | 46.9745 | 46.9376 | 46.8808 | 46.8736 | 46.8505 | 46.6553 | 45.419 | 43.3904 | 43.1922 | 43.1869 | 43.1766 | 43.1322 | 43.087 | 43.0412 | 42.9924 | 42.9235 | 42.9036 | 42.8387 | 41.7731 | 39.3189 | 36.9314 | 44.9672 | 44.9672 | 44.9672 | 44.933 | 44.8983 | 44.863 | 44.8262 | 44.7693 | 44.7621 | 44.739 | 43.8375 | 41.444 | 39.1175
|  | BOURNE VALLEY | CT |  |  | 47.0786 | 47.0786 | 47.0786 | 47.0445 | 47.0098 | 46.9745 | 46.9376 | 46.8808 | 46.8736 | 46.8505 | 46.6553 | 45.419 | 43.3904 | 43.1922 | 43.1869 | 43.1766 | 43.1322 | 43.087 | 43.0412 | 42.9924 | 42.9235 | 42.9036 | 42.8387 | 41.7731 | 39.3189 | 36.9314 | 44.9672 | 44.9672 | 44.9672 | 44.933 | 44.8983 | 44.863 | 44.8262 | 44.7693 | 44.7621 | 44.739 | 43.8375 | 41.444 | 39.1175
|  | BOURNE VALLEY | LW |  |  | 47.0786 | 47.0786 | 47.0786 | 47.0786 | 47.0786 | 47.0786 | 47.0786 | 47.0786 | 47.0786 | 47.0786 | 47.0083 | 46.0901 | 44.0927 | 43.1954 | 43.1919 | 43.1853 | 43.1787 | 43.1718 | 43.1599 | 43.148 | 43.1359 | 43.1232 | 43.0814 | 42.3622 | 40.0295 | 37.6731 | 44.9672 | 44.9672 | 44.9672 | 44.9672 | 44.9672 | 44.9672 | 44.9672 | 44.9672 | 44.9672 | 44.9672 | 44.4247 | 42.1478 | 39.8525
|  | BOURNE VALLEY | ST |  |  | 47.0786 | 47.0786 | 47.0786 | 47.0786 | 47.0786 | 47.0786 | 47.0786 | 47.0786 | 47.0786 | 47.0786 | 47.0769 | 46.969 | 46.326 | 43.2031 | 43.1924 | 43.1876 | 43.1817 | 43.1745 | 43.1622 | 43.15 | 43.1418 | 43.133 | 43.1044 | 43.0312 | 41.8051 | 40.3078 | 44.9672 | 44.9672 | 44.9672 | 44.9672 | 44.9672 | 44.9672 | 44.9672 | 44.9672 | 44.9672 | 44.9672 | 44.9672 | 43.8773 | 42.4189
|  | BOURNE VALLEY | FS |  |  | 47.0786 | 47.0786 | 47.0786 | 47.0786 | 47.0786 | 47.0786 | 47.0786 | 47.0786 | 47.0786 | 47.0786 | 47.0786 | 47.0786 | 47.0786 | 43.2074 | 43.1991 | 43.1984 | 43.1968 | 43.1949 | 43.1911 | 43.1872 | 43.1823 | 43.1789 | 43.1677 | 43.1376 | 43.0977 | 43.0554 | 44.9672 | 44.9672 | 44.9672 | 44.9672 | 44.9672 | 44.9672 | 44.9672 | 44.9672 | 44.9672 | 44.9672 | 44.9672 | 44.9672 | 44.9672
MANNINGTON GSP | SHAFTESBURY BSP | BOURTON | MINIMUM HEADROOM | ST 77363 30262 | YES | 15.7601 | 15.7569 | 15.7501 | 15.66 | 15.5684 | 15.4755 | 15.3091 | 15.0677 | 14.9399 | 14.5575 | 13.7504 | 12.8993 | 12.2692 | 11.765 | 11.7555 | 11.7359 | 11.6333 | 11.5291 | 11.4236 | 11.2091 | 10.9468 | 10.7963 | 10.3471 | 9.4285 | 8.4614 | 7.7173 | 13.9195 | 13.9123 | 13.8973 | 13.7992 | 13.6995 | 13.5985 | 13.4133 | 13.18 | 13.0342 | 12.5951 | 11.6936 | 10.7442 | 10.0174
|  | BOURTON | CT |  |  | 15.7601 | 15.7569 | 15.7502 | 15.66 | 15.5684 | 15.4755 | 15.3091 | 15.0677 | 14.9399 | 14.5575 | 13.7504 | 12.8993 | 12.2692 | 11.765 | 11.7556 | 11.736 | 11.6333 | 11.5291 | 11.4236 | 11.2091 | 10.9468 | 10.7963 | 10.3471 | 9.4285 | 8.4614 | 7.7173 | 13.9195 | 13.9124 | 13.8974 | 13.7992 | 13.6995 | 13.5985 | 13.4133 | 13.18 | 13.0342 | 12.5951 | 11.6936 | 10.7442 | 10.0174
|  | BOURTON | LW |  |  | 15.7601 | 15.7569 | 15.7501 | 15.6982 | 15.6447 | 15.5278 | 15.3739 | 15.1947 | 15.0739 | 14.7114 | 14.1134 | 13.4562 | 12.8944 | 11.765 | 11.7555 | 11.7359 | 11.6713 | 11.6052 | 11.4308 | 11.2558 | 11.0556 | 10.9121 | 10.4828 | 9.7734 | 9.0002 | 8.3242 | 13.9195 | 13.9123 | 13.8973 | 13.8372 | 13.7757 | 13.6309 | 13.4851 | 13.2928 | 13.1528 | 12.7337 | 12.0412 | 11.2857 | 10.6271
|  | BOURTON | ST |  |  | 15.828 | 15.7604 | 15.7573 | 15.7535 | 15.7489 | 15.7263 | 15.6935 | 15.6236 | 15.5485 | 15.3286 | 14.9668 | 14.6023 | 14.2405 | 11.9627 | 11.7657 | 11.7567 | 11.7457 | 11.7323 | 11.6664 | 11.6015 | 11.5173 | 11.4268 | 11.1618 | 10.7258 | 10.2865 | 9.8505 | 14.0706 | 13.9201 | 13.9132 | 13.9048 | 13.8946 | 13.8442 | 13.7946 | 13.7302 | 13.661 | 13.4032 | 12.9785 | 12.5507 | 12.126
|  | BOURTON | FS |  |  | 15.8309 | 15.7648 | 15.7645 | 15.7601 | 15.7555 | 15.7457 | 15.7361 | 15.7226 | 15.6957 | 15.589 | 15.4286 | 15.2242 | 15.0379 | 11.9711 | 11.7786 | 11.7778 | 11.7713 | 11.7643 | 11.7424 | 11.7208 | 11.6916 | 11.6416 | 11.4921 | 11.3034 | 11.0716 | 10.8591 | 14.077 | 13.9299 | 13.9293 | 13.9235 | 13.9174 | 13.8999 | 13.8825 | 13.859 | 13.8173 | 13.692 | 13.5385 | 13.3108 | 13.1023
MANNINGTON GSP | WAREHAM | BOVINGTON | MINIMUM HEADROOM | SY 83933 87831 | YES | 9.0161 | 8.999 | 8.964 | 8.9048 | 8.8194 | 8.6968 | 8.5541 | 8.3949 | 8.2735 | 7.91 | 7.5595 | 7.2411 | 7.0401 | 7.4106 | 7.3906 | 7.3495 | 7.2812 | 7.1826 | 7.0409 | 6.8762 | 6.6945 | 6.5529 | 6.1301 | 5.7279 | 5.3727 | 5.1379 | 5.5537 | 5.5339 | 5.4933 | 5.4259 | 5.3285 | 5.1885 | 5.0258 | 4.8461 | 4.7063 | 4.2889 | 3.8913 | 3.5395 | 3.3077
|  | BOVINGTON | CT |  |  | 9.0161 | 8.999 | 8.964 | 8.9111 | 8.8342 | 8.751 | 8.6215 | 8.4856 | 8.3679 | 8.0213 | 7.6715 | 7.4009 | 7.1889 | 7.4106 | 7.3906 | 7.3495 | 7.2875 | 7.1974 | 7.1001 | 6.9486 | 6.7902 | 6.6523 | 6.2464 | 5.8449 | 5.5374 | 5.2917 | 5.5537 | 5.5339 | 5.4933 | 5.4322 | 5.3432 | 5.2472 | 5.0977 | 4.9413 | 4.8053 | 4.4047 | 4.0079 | 3.7037 | 3.461
|  | BOVINGTON | LW |  |  | 9.0161 | 8.999 | 8.964 | 8.9048 | 8.8194 | 8.6968 | 8.5541 | 8.3949 | 8.2735 | 7.91 | 7.5595 | 7.2411 | 7.0401 | 7.4106 | 7.3906 | 7.3495 | 7.2812 | 7.1826 | 7.0409 | 6.8762 | 6.6945 | 6.5529 | 6.1301 | 5.7279 | 5.3727 | 5.1379 | 5.5537 | 5.5339 | 5.4933 | 5.4259 | 5.3285 | 5.1885 | 5.0258 | 4.8461 | 4.7063 | 4.2889 | 3.8913 | 3.5395 | 3.3077
|  | BOVINGTON | ST |  |  | 9.0184 | 9.0069 | 8.9852 | 8.9506 | 8.899 | 8.8258 | 8.7409 | 8.649 | 8.5666 | 8.3135 | 8.0905 | 7.8922 | 7.744 | 7.4133 | 7.3999 | 7.3743 | 7.3338 | 7.2734 | 7.1878 | 7.0884 | 6.9814 | 6.8852 | 6.5904 | 6.3316 | 6.1094 | 5.9393 | 5.5563 | 5.543 | 5.5178 | 5.4778 | 5.4183 | 5.3338 | 5.2357 | 5.1301 | 5.035 | 4.744 | 4.4885 | 4.2684 | 4.1003
|  | BOVINGTON | FS |  |  | 9.0215 | 9.015 | 9.0036 | 8.9855 | 8.961 | 8.9312 | 8.8979 | 8.8625 | 8.8259 | 8.7131 | 8.6216 | 8.5316 | 8.4525 | 7.417 | 7.4093 | 7.3959 | 7.3748 | 7.3463 | 7.3114 | 7.2725 | 7.2313 | 7.1892 | 7.0599 | 6.9542 | 6.8551 | 6.7682 | 5.5599 | 5.5523 | 5.5392 | 5.5183 | 5.4901 | 5.4557 | 5.4173 | 5.3767 | 5.335 | 5.2072 | 5.1028 | 5.0045 | 4.9184
AMERSHAM | LOUDWATER BSP | BOWERDEAN | MINIMUM HEADROOM | SU 87718 93880 | YES | 32.5915 | 32.5915 | 32.5915 | 32.5915 | 32.5915 | 32.573 | 32.5491 | 32.5261 | 32.5019 | 32.4308 | 32.3089 | 31.157 | 29.7222 | 29.7256 | 29.714 | 29.695 | 29.6769 | 29.6584 | 29.6399 | 29.6254 | 29.6114 | 29.5966 | 29.5533 | 28.1097 | 26.4012 | 24.7279 | 30.977 | 30.9622 | 30.938 | 30.9149 | 30.8913 | 30.8677 | 30.8492 | 30.8313 | 30.8125 | 29.9022 | 28.2702 | 26.5716 | 24.8784
|  | BOWERDEAN | CT |  |  | 32.5915 | 32.5915 | 32.5915 | 32.5915 | 32.5915 | 32.573 | 32.5491 | 32.5261 | 32.5019 | 32.4308 | 32.3089 | 31.157 | 29.7222 | 29.7256 | 29.714 | 29.695 | 29.6769 | 29.6584 | 29.6399 | 29.6254 | 29.6114 | 29.5966 | 29.5533 | 28.1097 | 26.4012 | 24.7279 | 30.977 | 30.9622 | 30.938 | 30.9149 | 30.8913 | 30.8677 | 30.8492 | 30.8313 | 30.8125 | 29.9022 | 28.2702 | 26.5716 | 24.8784
|  | BOWERDEAN | LW |  |  | 32.5915 | 32.5915 | 32.5915 | 32.5915 | 32.5915 | 32.5913 | 32.5674 | 32.5444 | 32.5202 | 32.4491 | 32.3272 | 31.3707 | 29.9351 | 29.7272 | 29.7165 | 29.6993 | 29.683 | 29.6663 | 29.6511 | 29.6365 | 29.6225 | 29.6078 | 29.5645 | 28.3591 | 26.6504 | 24.9761 | 30.979 | 30.9654 | 30.9435 | 30.9227 | 30.9014 | 30.882 | 30.8634 | 30.8455 | 30.8268 | 30.1475 | 28.516 | 26.8238 | 25.1296
|  | BOWERDEAN | ST |  |  | 32.5915 | 32.5915 | 32.5915 | 32.5915 | 32.5915 | 32.5915 | 32.5915 | 32.5915 | 32.5842 | 32.536 | 32.4542 | 32.3729 | 32.293 | 29.7309 | 29.7235 | 29.7137 | 29.7022 | 29.6881 | 29.677 | 29.6664 | 29.6568 | 29.6467 | 29.6174 | 29.5676 | 28.9789 | 27.894 | 30.9838 | 30.9743 | 30.9618 | 30.9471 | 30.9292 | 30.915 | 30.9014 | 30.8892 | 30.8764 | 30.839 | 30.2152 | 29.1266 | 28.0577
|  | BOWERDEAN | FS |  |  | 32.5915 | 32.5915 | 32.5915 | 32.5915 | 32.5915 | 32.5915 | 32.5915 | 32.5915 | 32.5915 | 32.5915 | 32.5915 | 32.5915 | 32.5846 | 29.7403 | 29.7382 | 29.7369 | 29.7339 | 29.7303 | 29.7264 | 29.7228 | 29.7183 | 29.7144 | 29.703 | 29.6838 | 29.665 | 29.647 | 30.9957 | 30.993 | 30.9914 | 30.9876 | 30.983 | 30.978 | 30.9734 | 30.9677 | 30.9627 | 30.9482 | 30.9237 | 30.8997 | 30.8768
BRAMLEY (FLEE) | BRACKNELL MAIN | BRACKNELL | MINIMUM HEADROOM | SU 86075 69397 | YES | 91.0554 | 91.0364 | 90.997 | 90.814 | 90.6195 | 90.4276 | 90.2382 | 89.9532 | 89.8878 | 89.6755 | 88.6278 | 86.9466 | 85.7181 | 87.9361 | 87.9231 | 87.8963 | 87.7227 | 87.5405 | 87.3592 | 87.1774 | 86.9019 | 86.847 | 86.6692 | 84.7789 | 82.8227 | 81.3305 | 87.8175 | 87.7958 | 87.7508 | 87.5636 | 87.3637 | 87.1671 | 86.9744 | 86.6852 | 86.6151 | 86.3875 | 85.7467 | 84.8967 | 83.4312
|  | BRACKNELL | CT |  |  | 91.0596 | 91.0428 | 91.0083 | 90.814 | 90.6195 | 90.4276 | 90.2382 | 89.9532 | 89.8878 | 89.6755 | 88.6278 | 86.9466 | 85.7181 | 87.9389 | 87.9275 | 87.904 | 87.7227 | 87.5405 | 87.3592 | 87.1774 | 86.9019 | 86.847 | 86.6692 | 84.7789 | 82.8227 | 81.3305 | 87.8222 | 87.8031 | 87.7637 | 87.5636 | 87.3637 | 87.1671 | 86.9744 | 86.6852 | 86.6151 | 86.3875 | 85.7467 | 84.8967 | 83.4312
|  | BRACKNELL | LW |  |  | 91.0554 | 91.0364 | 90.997 | 90.9351 | 90.8752 | 90.8356 | 90.7936 | 90.7364 | 90.6994 | 90.5779 | 89.8943 | 88.7016 | 87.6021 | 87.9361 | 87.9231 | 87.8963 | 87.8489 | 87.8027 | 87.7702 | 87.7358 | 87.688 | 87.6616 | 87.5745 | 86.02 | 84.5523 | 83.189 | 87.8175 | 87.7958 | 87.7508 | 87.6825 | 87.6165 | 87.5738 | 87.5285 | 87.467 | 87.4254 | 87.2886 | 87.1079 | 86.6288 | 85.2922
|  | BRACKNELL | ST |  |  | 91.0757 | 91.0553 | 91.0354 | 90.9926 | 90.9473 | 90.917 | 90.8851 | 90.8409 | 90.8101 | 90.7077 | 90.5879 | 90.4562 | 90.3367 | 87.9499 | 87.936 | 87.9225 | 87.8887 | 87.8531 | 87.8276 | 87.8009 | 87.7631 | 87.7395 | 87.6613 | 87.5729 | 87.332 | 86.6244 | 87.8406 | 87.8174 | 87.7947 | 87.7479 | 87.6983 | 87.6659 | 87.6316 | 87.5846 | 87.5506 | 87.4374 | 87.3037 | 87.1628 | 87.0708
|  | BRACKNELL | FS |  |  | 91.0956 | 91.0805 | 91.0766 | 91.0668 | 91.0573 | 91.0515 | 91.0454 | 91.0369 | 91.0279 | 90.9979 | 90.9585 | 90.9323 | 90.9074 | 87.9635 | 87.9532 | 87.9505 | 87.9438 | 87.9374 | 87.9334 | 87.9293 | 87.9235 | 87.9174 | 87.8968 | 87.87 | 87.8521 | 87.8351 | 87.8634 | 87.8461 | 87.8417 | 87.8305 | 87.8196 | 87.8131 | 87.8061 | 87.7964 | 87.7862 | 87.7518 | 87.707 | 87.677 | 87.6486
MELKSHAM GSP | NORRINGTON | BRADFORD-ON-AVON | MINIMUM HEADROOM | ST 81260 60564 | YES | 27.7034 | 27.2776 | 27.2675 | 27.2568 | 27.2454 | 27.2275 | 27.2015 | 27.1627 | 27.1441 | 26.8231 | 25.9367 | 24.9989 | 24.1378 | 25.9903 | 25.564 | 25.5496 | 25.5313 | 25.4871 | 25.3515 | 25.1647 | 24.9752 | 24.7778 | 24.1902 | 23.1568 | 22.0737 | 21.0535 | 25.5084 | 25.0369 | 24.9306 | 24.8266 | 24.7226 | 24.6187 | 24.4756 | 24.3294 | 24.1787 | 23.7294 | 22.8158 | 21.8091 | 20.8657
|  | BRADFORD-ON-AVON | CT |  |  | 27.7034 | 27.2776 | 27.2675 | 27.2568 | 27.2454 | 27.2334 | 27.2166 | 27.1957 | 27.1801 | 26.8231 | 25.9367 | 25.007 | 24.1378 | 25.9903 | 25.564 | 25.5496 | 25.5313 | 25.4871 | 25.3515 | 25.1647 | 24.9752 | 24.7778 | 24.1902 | 23.1568 | 22.0737 | 21.0535 | 25.5084 | 25.0369 | 24.9306 | 24.8266 | 24.7226 | 24.6187 | 24.4756 | 24.3294 | 24.1787 | 23.7294 | 22.8158 | 21.8099 | 20.8657
|  | BRADFORD-ON-AVON | LW |  |  | 27.7056 | 27.281 | 27.2734 | 27.2632 | 27.2501 | 27.2275 | 27.2015 | 27.1627 | 27.1441 | 26.8478 | 25.9676 | 24.9989 | 24.1429 | 25.9927 | 25.5677 | 25.5594 | 25.5443 | 25.5254 | 25.4362 | 25.2401 | 25.0328 | 24.8324 | 24.2297 | 23.2024 | 22.0804 | 21.0732 | 25.5312 | 25.0724 | 24.9929 | 24.9128 | 24.8302 | 24.6801 | 24.5277 | 24.3637 | 24.2101 | 23.7456 | 22.854 | 21.8091 | 20.878
|  | BRADFORD-ON-AVON | ST |  |  | 27.7417 | 27.7042 | 27.6998 | 27.2728 | 27.2651 | 27.2531 | 27.2403 | 27.2254 | 27.2128 | 27.1691 | 26.762 | 26.1355 | 25.5582 | 26.0321 | 25.9912 | 25.9863 | 25.5588 | 25.5467 | 25.5268 | 25.4652 | 25.3349 | 25.1983 | 24.7916 | 24.1228 | 23.3973 | 22.7218 | 25.91 | 25.5166 | 25.4703 | 24.9919 | 24.9223 | 24.8133 | 24.7049 | 24.6043 | 24.4996 | 24.1862 | 23.6719 | 23.0353 | 22.4093
|  | BRADFORD-ON-AVON | FS |  |  | 27.7461 | 27.7109 | 27.7106 | 27.7072 | 27.7035 | 27.6978 | 27.2711 | 27.263 | 27.2485 | 27.2008 | 27.1636 | 27.0783 | 27.0019 | 26.0369 | 25.9985 | 25.9982 | 25.9946 | 25.9907 | 25.9848 | 25.5577 | 25.5493 | 25.5344 | 25.4782 | 25.3478 | 25.0389 | 24.7493 | 25.9562 | 25.5869 | 25.584 | 25.5691 | 25.5517 | 25.5143 | 25.0562 | 25.0077 | 24.9574 | 24.8055 | 24.598 | 24.3466 | 24.1118
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | BRAMLEY GREEN | MINIMUM HEADROOM | SU 67431 58511 | YES | 21.0431 | 20.9881 | 20.8719 | 20.7563 | 20.6384 | 20.533 | 20.4728 | 20.4062 | 20.3451 | 20.1594 | 19.7725 | 19.3506 | 19.0144 | 19.6712 | 19.5919 | 19.4243 | 19.2587 | 19.0914 | 19.011 | 18.971 | 18.9244 | 18.8848 | 18.7445 | 18.4841 | 18.1472 | 17.7769 | 20.6851 | 20.6734 | 20.6485 | 20.6213 | 20.5235 | 20.3704 | 20.3003 | 20.2238 | 20.1521 | 19.9348 | 19.4947 | 19.0204 | 18.6258
|  | BRAMLEY GREEN | CT |  |  | 21.0517 | 21.0014 | 20.8951 | 20.7912 | 20.6875 | 20.533 | 20.4728 | 20.4062 | 20.3451 | 20.1594 | 19.7725 | 19.354 | 19.0144 | 19.6837 | 19.6111 | 19.4578 | 19.3082 | 19.1593 | 19.011 | 18.971 | 18.9244 | 18.8848 | 18.7629 | 18.4841 | 18.1726 | 17.7769 | 20.687 | 20.6762 | 20.6535 | 20.6305 | 20.6069 | 20.3704 | 20.3003 | 20.2238 | 20.1521 | 19.9348 | 19.4947 | 19.0204 | 18.6258
|  | BRAMLEY GREEN | LW |  |  | 21.0431 | 20.9881 | 20.8719 | 20.7563 | 20.6384 | 20.5957 | 20.5249 | 20.4381 | 20.3735 | 20.1693 | 19.8024 | 19.3506 | 19.035 | 19.6712 | 19.5919 | 19.4243 | 19.2587 | 19.0914 | 19.0453 | 18.9947 | 18.9279 | 18.8848 | 18.7445 | 18.4856 | 18.1472 | 17.8117 | 20.6851 | 20.6734 | 20.6485 | 20.6213 | 20.5235 | 20.447 | 20.3664 | 20.2697 | 20.1945 | 19.9588 | 19.5386 | 19.031 | 18.6603
|  | BRAMLEY GREEN | ST |  |  | 21.0591 | 21.0185 | 20.949 | 20.8632 | 20.7591 | 20.7346 | 20.7091 | 20.6849 | 20.6636 | 20.5926 | 20.3719 | 20.0836 | 19.8534 | 19.6943 | 19.6358 | 19.5355 | 19.4119 | 19.2624 | 19.2279 | 19.1926 | 19.1611 | 19.1319 | 19.038 | 18.8877 | 18.6726 | 18.5149 | 20.6886 | 20.6799 | 20.665 | 20.6461 | 20.6228 | 20.6159 | 20.6078 | 20.5965 | 20.589 | 20.4487 | 20.1906 | 19.8662 | 19.6003
|  | BRAMLEY GREEN | FS |  |  | 21.1297 | 21.1257 | 21.1219 | 21.1038 | 21.0823 | 21.0746 | 21.0669 | 21.0568 | 21.0487 | 21.0216 | 20.9829 | 20.9246 | 20.8686 | 19.7963 | 19.7905 | 19.785 | 19.7589 | 19.728 | 19.7168 | 19.7057 | 19.6914 | 19.6802 | 19.6442 | 19.5908 | 19.518 | 19.4481 | 20.7037 | 20.7028 | 20.702 | 20.6981 | 20.6935 | 20.6918 | 20.69 | 20.6876 | 20.6849 | 20.6735 | 20.6609 | 20.6283 | 20.597
LOVEDEAN GSP | PORTSMOUTH BSP | BRANDON ROAD | MINIMUM HEADROOM | SZ 64712 98665 | YES | 45.6261 | 45.6261 | 45.6261 | 45.5972 | 45.5678 | 45.5378 | 45.5068 | 45.4589 | 45.4426 | 45.3907 | 45.349 | 44.5821 | 43.3653 | 41.8425 | 41.8318 | 41.8113 | 41.7916 | 41.7519 | 41.7027 | 41.6525 | 41.5935 | 41.5655 | 41.4785 | 40.3775 | 39.0317 | 37.6947 | 43.594 | 43.5864 | 43.5718 | 43.5515 | 43.5128 | 43.4692 | 43.4245 | 43.3687 | 43.3442 | 43.2673 | 43.1764 | 42.1653 | 40.7494
|  | BRANDON ROAD | CT |  |  | 45.6261 | 45.6261 | 45.6261 | 45.6261 | 45.6261 | 45.6261 | 45.6261 | 45.6261 | 45.6261 | 45.6261 | 45.6261 | 44.7219 | 43.5158 | 41.8453 | 41.8362 | 41.8189 | 41.8023 | 41.7855 | 41.7686 | 41.7511 | 41.7349 | 41.7178 | 41.666 | 40.5418 | 39.196 | 37.8593 | 43.596 | 43.5895 | 43.5773 | 43.5655 | 43.5536 | 43.5415 | 43.5292 | 43.5176 | 43.5055 | 43.4688 | 43.3964 | 42.3394 | 40.9237
|  | BRANDON ROAD | LW |  |  | 45.6261 | 45.6261 | 45.6261 | 45.6261 | 45.6261 | 45.6261 | 45.6261 | 45.6261 | 45.6261 | 45.6261 | 45.6261 | 44.5821 | 43.3653 | 41.8425 | 41.8318 | 41.8113 | 41.7916 | 41.7716 | 41.7545 | 41.7371 | 41.7209 | 41.7038 | 41.5705 | 40.3775 | 39.0317 | 37.6947 | 43.594 | 43.5864 | 43.5718 | 43.5579 | 43.5437 | 43.5316 | 43.5192 | 43.5077 | 43.4955 | 43.4588 | 43.3865 | 42.1653 | 40.7494
|  | BRANDON ROAD | ST |  |  | 45.6261 | 45.6261 | 45.6261 | 45.5972 | 45.5678 | 45.5378 | 45.5068 | 45.4589 | 45.4426 | 45.3907 | 45.349 | 45.2105 | 44.7315 | 41.8494 | 41.8434 | 41.8342 | 41.7944 | 41.7519 | 41.7027 | 41.6525 | 41.5935 | 41.5655 | 41.4785 | 41.2062 | 40.1895 | 39.2879 | 43.5989 | 43.5947 | 43.5881 | 43.5515 | 43.5128 | 43.4692 | 43.4245 | 43.3687 | 43.3442 | 43.2673 | 43.1764 | 42.9847 | 42.4638
|  | BRANDON ROAD | FS |  |  | 45.6261 | 45.6261 | 45.6261 | 45.6261 | 45.6261 | 45.6261 | 45.6261 | 45.6261 | 45.6261 | 45.6261 | 45.6261 | 45.6261 | 45.6261 | 41.8571 | 41.8555 | 41.8541 | 41.8505 | 41.8462 | 41.8391 | 41.832 | 41.8234 | 41.8189 | 41.8053 | 41.7779 | 41.7467 | 41.7152 | 43.6044 | 43.6033 | 43.6022 | 43.5997 | 43.5967 | 43.5916 | 43.5866 | 43.5805 | 43.5773 | 43.5676 | 43.5482 | 43.526 | 43.5037
BRAMLEY (FLEE) | MAIDENHEAD BSP | BRAYWICK ROAD | MINIMUM HEADROOM | SU 88887 80726 | YES | 31.4358 | 31.4358 | 31.4358 | 31.4091 | 31.3819 | 31.3541 | 31.3254 | 31.281 | 31.2659 | 31.2179 | 30.71 | 29.8116 | 28.9936 | 29.5208 | 29.5084 | 29.4844 | 29.4415 | 29.3975 | 29.3638 | 29.3278 | 29.2794 | 29.2554 | 28.3934 | 27.015 | 25.9616 | 25.0017 | 29.9825 | 29.9825 | 29.9825 | 29.9557 | 29.9285 | 29.9007 | 29.872 | 29.8277 | 29.8126 | 29.7434 | 28.4779 | 27.4378 | 26.4907
|  | BRAYWICK ROAD | CT |  |  | 31.4358 | 31.4358 | 31.4358 | 31.4358 | 31.4358 | 31.4358 | 31.4358 | 31.4358 | 31.4358 | 31.4358 | 30.7963 | 29.9476 | 29.133 | 29.522 | 29.5103 | 29.4877 | 29.4647 | 29.4411 | 29.4173 | 29.4019 | 29.3849 | 29.3653 | 28.4387 | 27.0871 | 26.0852 | 25.1288 | 29.9825 | 29.9825 | 29.9825 | 29.9825 | 29.9825 | 29.9825 | 29.9825 | 29.9677 | 29.9445 | 29.8674 | 28.551 | 27.5625 | 26.6189
|  | BRAYWICK ROAD | LW |  |  | 31.4358 | 31.4358 | 31.4358 | 31.4174 | 31.3983 | 31.3784 | 31.3577 | 31.3264 | 31.322 | 31.3071 | 30.71 | 29.8116 | 28.9936 | 29.5208 | 29.5084 | 29.4844 | 29.4415 | 29.3975 | 29.3638 | 29.3278 | 29.2794 | 29.2554 | 28.3934 | 27.015 | 25.9616 | 25.0017 | 29.9825 | 29.9825 | 29.9825 | 29.964 | 29.9449 | 29.925 | 29.9044 | 29.863 | 29.8354 | 29.7434 | 28.4779 | 27.4378 | 26.4907
|  | BRAYWICK ROAD | ST |  |  | 31.4358 | 31.4358 | 31.4358 | 31.4091 | 31.3819 | 31.3541 | 31.3254 | 31.281 | 31.2659 | 31.2179 | 31.1793 | 31.052 | 31.012 | 29.529 | 29.5224 | 29.5119 | 29.4723 | 29.4299 | 29.3901 | 29.3483 | 29.2925 | 29.264 | 29.17 | 29.0761 | 28.3019 | 27.6446 | 29.9825 | 29.9825 | 29.9825 | 29.9557 | 29.9285 | 29.9007 | 29.872 | 29.8277 | 29.8126 | 29.7534 | 29.6616 | 29.4976 | 29.0954
|  | BRAYWICK ROAD | FS |  |  | 31.4358 | 31.4358 | 31.4358 | 31.4358 | 31.4358 | 31.4358 | 31.4358 | 31.4358 | 31.4358 | 31.4358 | 31.4358 | 31.4358 | 31.4358 | 29.5359 | 29.5337 | 29.5312 | 29.5261 | 29.5204 | 29.5157 | 29.5106 | 29.5045 | 29.4992 | 29.4811 | 29.4632 | 29.4508 | 29.4391 | 29.9825 | 29.9825 | 29.9825 | 29.9825 | 29.9825 | 29.9825 | 29.9825 | 29.9825 | 29.9825 | 29.9825 | 29.9825 | 29.9825 | 29.9825
EALING GSP | EALING 22kV | BRENTFORD | MINIMUM HEADROOM | TQ 17659 78277 | YES | 47.808 | 47.808 | 47.808 | 47.7425 | 47.6758 | 47.6078 | 47.5305 | 47.4096 | 47.3785 | 47.27 | 47.0617 | 45.8769 | 43.7622 | 44.3409 | 44.3264 | 44.3004 | 44.2144 | 44.1255 | 44.0405 | 43.9524 | 43.8292 | 43.7958 | 43.6844 | 43.1195 | 40.5455 | 38.0338 | 46.1937 | 46.1792 | 46.1532 | 46.0671 | 45.9781 | 45.8984 | 45.8158 | 45.6981 | 45.6701 | 45.5528 | 45.3798 | 43.1847 | 40.6777
|  | BRENTFORD | CT |  |  | 47.808 | 47.808 | 47.808 | 47.7762 | 47.7438 | 47.6943 | 47.6429 | 47.5735 | 47.5501 | 47.4742 | 47.2359 | 45.8902 | 43.7622 | 44.3409 | 44.3264 | 44.3004 | 44.2435 | 44.1853 | 44.1162 | 44.0625 | 43.9908 | 43.9651 | 43.8817 | 43.1195 | 40.5455 | 38.0338 | 46.1937 | 46.1792 | 46.1532 | 46.0961 | 46.0381 | 45.9795 | 45.9314 | 45.8651 | 45.8449 | 45.7795 | 45.5677 | 43.1847 | 40.6777
|  | BRENTFORD | LW |  |  | 47.808 | 47.808 | 47.808 | 47.7464 | 47.6829 | 47.6164 | 47.5305 | 47.4096 | 47.3785 | 47.2746 | 47.0617 | 45.8769 | 43.7651 | 44.341 | 44.3267 | 44.3009 | 44.2144 | 44.1255 | 44.0405 | 43.9524 | 43.8292 | 43.7958 | 43.6844 | 43.1645 | 40.5686 | 38.073 | 46.1939 | 46.1795 | 46.1536 | 46.0671 | 45.9781 | 45.8984 | 45.8158 | 45.6981 | 45.6701 | 45.5767 | 45.3904 | 43.2035 | 40.7164
|  | BRENTFORD | ST |  |  | 47.808 | 47.808 | 47.808 | 47.7425 | 47.6758 | 47.6078 | 47.5376 | 47.4289 | 47.392 | 47.27 | 47.0784 | 46.6649 | 46.4608 | 44.3519 | 44.3447 | 44.3347 | 44.2573 | 44.1763 | 44.0953 | 44.0117 | 43.8941 | 43.848 | 43.6936 | 43.4887 | 43.0594 | 41.4738 | 46.2048 | 46.1976 | 46.1876 | 46.1102 | 46.0291 | 45.948 | 45.8644 | 45.7468 | 45.7007 | 45.5528 | 45.3798 | 44.9881 | 44.0589
|  | BRENTFORD | FS |  |  | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.7563 | 44.3601 | 44.3578 | 44.3562 | 44.3517 | 44.3465 | 44.3416 | 44.3366 | 44.3307 | 44.3271 | 44.3154 | 44.2834 | 44.237 | 44.1733 | 46.2131 | 46.2108 | 46.2091 | 46.2047 | 46.1994 | 46.1945 | 46.1895 | 46.1835 | 46.1799 | 46.1682 | 46.1361 | 46.0935 | 46.0482
EALING GSP | EALING 22kV | BRIDGE ROAD | MINIMUM HEADROOM | TQ 14778 75741 |  | 88.6005 | 88.5886 | 87.8594 | 87.7996 | 87.7398 | 87.6801 | 87.6203 | 87.5605 | 87.5366 | 87.4623 | 87.1378 | 85.095 | 82.1285 | 85.7918 | 85.7612 | 84.9966 | 84.9008 | 84.8034 | 84.7156 | 84.6254 | 84.5404 | 84.4932 | 84.0959 | 82.0556 | 78.5923 | 75.1089 | 86.4747 | 86.4628 | 85.7336 | 85.6738 | 85.614 | 85.5543 | 85.4945 | 85.4347 | 85.4108 | 85.3218 | 83.4371 | 80.0267 | 76.5954
|  | BRIDGE ROAD | CT |  |  | 88.6627 | 88.6555 | 88.218 | 88.1821 | 88.1463 | 88.1104 | 88.0746 | 88.0387 | 88.0243 | 87.9813 | 87.2598 | 85.2062 | 82.2399 | 85.8567 | 85.8324 | 85.3627 | 85.2938 | 85.2234 | 85.1522 | 85.0859 | 85.0248 | 84.9872 | 84.6682 | 82.2998 | 78.7238 | 75.2405 | 86.5369 | 86.5297 | 86.0922 | 86.0563 | 86.0205 | 85.9846 | 85.9487 | 85.9129 | 85.8985 | 85.8458 | 83.6793 | 80.1561 | 76.725
|  | BRIDGE ROAD | LW |  |  | 88.6005 | 88.5886 | 87.8594 | 87.7996 | 87.7398 | 87.6801 | 87.6203 | 87.5605 | 87.5366 | 87.4623 | 87.1378 | 85.095 | 82.1285 | 85.7918 | 85.7612 | 84.9966 | 84.9008 | 84.8034 | 84.7156 | 84.6254 | 84.5404 | 84.4932 | 84.0959 | 82.0556 | 78.5923 | 75.1089 | 86.4747 | 86.4628 | 85.7336 | 85.6738 | 85.614 | 85.5543 | 85.4945 | 85.4347 | 85.4108 | 85.3218 | 83.4371 | 80.0267 | 76.5954
|  | BRIDGE ROAD | ST |  |  | 88.6937 | 88.689 | 88.3973 | 88.3734 | 88.3495 | 88.3256 | 88.3017 | 88.2778 | 88.2682 | 88.2395 | 88.1917 | 88.0442 | 87.8423 | 85.9086 | 85.8832 | 85.5763 | 85.5338 | 85.4875 | 85.4409 | 85.3928 | 85.3518 | 85.3264 | 85.2512 | 85.0607 | 84.0863 | 81.9533 | 86.5679 | 86.5632 | 86.2715 | 86.2476 | 86.2237 | 86.1998 | 86.1759 | 86.152 | 86.1424 | 86.1137 | 86.0659 | 85.5082 | 83.3484
|  | BRIDGE ROAD | FS |  |  | 88.7248 | 88.7224 | 88.5766 | 88.5646 | 88.5527 | 88.5407 | 88.5288 | 88.5168 | 88.5121 | 88.4977 | 88.4738 | 88.4595 | 88.4332 | 85.9497 | 85.9439 | 85.7943 | 85.7748 | 85.7541 | 85.7335 | 85.7124 | 85.6913 | 85.6803 | 85.6479 | 85.5851 | 85.5244 | 85.4507 | 86.599 | 86.5966 | 86.4508 | 86.4388 | 86.4269 | 86.4149 | 86.403 | 86.391 | 86.3863 | 86.3719 | 86.348 | 86.3337 | 86.3074
LOVEDEAN GSP | HAVANT | BROCKHAMPTON | MINIMUM HEADROOM | SU 70868 05828 | YES | 44.3521 | 44.3521 | 44.3521 | 44.3489 | 44.3456 | 44.3422 | 44.3376 | 44.3288 | 44.3276 | 44.3226 | 44.2883 | 44.2354 | 44.1926 | 42.07 | 42.0528 | 42.0168 | 41.9785 | 41.9402 | 41.902 | 41.8489 | 41.7921 | 41.7391 | 41.578 | 41.2569 | 40.8969 | 40.5714 | 42.9686 | 42.9672 | 42.9643 | 42.9582 | 42.9521 | 42.9459 | 42.9373 | 42.9247 | 42.9193 | 42.9017 | 42.8443 | 42.7292 | 42.3941
|  | BROCKHAMPTON | CT |  |  | 44.3521 | 44.3521 | 44.3521 | 44.3489 | 44.3456 | 44.3422 | 44.3376 | 44.3288 | 44.3276 | 44.3226 | 44.2883 | 44.2354 | 44.1926 | 42.07 | 42.0528 | 42.0168 | 41.9785 | 41.9402 | 41.902 | 41.8489 | 41.7921 | 41.7391 | 41.578 | 41.2569 | 40.8969 | 40.5714 | 42.9686 | 42.9672 | 42.9643 | 42.9582 | 42.9521 | 42.9459 | 42.9373 | 42.9247 | 42.9193 | 42.9017 | 42.8443 | 42.7292 | 42.3941
|  | BROCKHAMPTON | LW |  |  | 44.3521 | 44.3521 | 44.3521 | 44.3521 | 44.3521 | 44.3514 | 44.3497 | 44.3456 | 44.3448 | 44.3402 | 44.3291 | 44.2978 | 44.2666 | 42.0728 | 42.0571 | 42.0244 | 41.9925 | 41.9606 | 41.9111 | 41.861 | 41.8088 | 41.7563 | 41.5955 | 41.2977 | 40.9593 | 40.6453 | 42.9688 | 42.9675 | 42.9649 | 42.9623 | 42.9597 | 42.955 | 42.9495 | 42.9415 | 42.9366 | 42.9193 | 42.8851 | 42.7915 | 42.4679
|  | BROCKHAMPTON | ST |  |  | 44.3521 | 44.3521 | 44.3521 | 44.3521 | 44.3521 | 44.3519 | 44.3515 | 44.3503 | 44.3498 | 44.3475 | 44.3447 | 44.3342 | 44.3305 | 42.2567 | 42.0895 | 42.0831 | 42.0753 | 42.0659 | 42.0345 | 42.0033 | 41.9692 | 41.9334 | 41.8256 | 41.6295 | 41.4148 | 41.2097 | 42.9836 | 42.9701 | 42.9696 | 42.969 | 42.9682 | 42.9655 | 42.9626 | 42.9587 | 42.9554 | 42.9446 | 42.9262 | 42.8993 | 42.8793
|  | BROCKHAMPTON | FS |  |  | 44.3521 | 44.3521 | 44.3521 | 44.3521 | 44.3521 | 44.3521 | 44.3521 | 44.3521 | 44.3519 | 44.3509 | 44.3502 | 44.3478 | 44.3456 | 42.2601 | 42.2587 | 42.2573 | 42.2519 | 42.2455 | 42.2352 | 42.2251 | 42.2121 | 42.1983 | 42.1565 | 42.0808 | 41.9976 | 41.9155 | 42.9839 | 42.9838 | 42.9837 | 42.9832 | 42.9827 | 42.9819 | 42.9811 | 42.98 | 42.9787 | 42.9744 | 42.9677 | 42.9587 | 42.9501
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | BROCKHURST | MINIMUM HEADROOM | SU 59381 02061 | YES | 35.3976 | 35.3976 | 35.3976 | 35.3976 | 35.3976 | 35.3976 | 35.3976 | 35.3976 | 35.3976 | 35.3976 | 35.3976 | 34.1761 | 32.7262 | 33.5803 | 33.5803 | 33.5803 | 33.5803 | 33.5744 | 33.5529 | 33.5334 | 33.5151 | 33.4945 | 32.7366 | 30.8728 | 29.1713 | 27.4885 | 34.8755 | 34.873 | 34.8687 | 34.8636 | 34.8578 | 34.8425 | 34.8287 | 34.8157 | 34.8011 | 34.7508 | 33.4607 | 31.7843 | 30.1262
|  | BROCKHURST | CT |  |  | 35.3976 | 35.3976 | 35.3976 | 35.3976 | 35.3976 | 35.3976 | 35.3976 | 35.3976 | 35.3976 | 35.3976 | 35.3976 | 34.3139 | 32.8643 | 33.5803 | 33.5803 | 33.5803 | 33.5803 | 33.5744 | 33.5658 | 33.5463 | 33.5281 | 33.5074 | 32.897 | 31.0327 | 29.3313 | 27.6488 | 34.8755 | 34.873 | 34.8687 | 34.8636 | 34.8578 | 34.8517 | 34.8379 | 34.8249 | 34.8102 | 34.76 | 33.6183 | 31.9419 | 30.2842
|  | BROCKHURST | LW |  |  | 35.3976 | 35.3976 | 35.3976 | 35.3976 | 35.3976 | 35.3976 | 35.3976 | 35.3976 | 35.3976 | 35.3976 | 35.3976 | 34.1761 | 32.7262 | 33.5803 | 33.5803 | 33.5803 | 33.5803 | 33.5744 | 33.5529 | 33.5334 | 33.5151 | 33.4945 | 32.7366 | 30.8728 | 29.1713 | 27.4885 | 34.8755 | 34.873 | 34.8687 | 34.8636 | 34.8578 | 34.8425 | 34.8287 | 34.8157 | 34.8011 | 34.7508 | 33.4607 | 31.7843 | 30.1262
|  | BROCKHURST | ST |  |  | 35.3976 | 35.3976 | 35.3976 | 35.3976 | 35.3976 | 35.3976 | 35.3976 | 35.3976 | 35.3976 | 35.3976 | 35.3976 | 35.3976 | 34.8876 | 33.5803 | 33.5803 | 33.5803 | 33.5803 | 33.5803 | 33.5714 | 33.5591 | 33.5467 | 33.5325 | 33.4817 | 32.1883 | 31.0744 | 29.9971 | 34.8847 | 34.8749 | 34.8725 | 34.8693 | 34.8653 | 34.8556 | 34.8469 | 34.8381 | 34.8281 | 34.7934 | 34.7195 | 33.6594 | 32.5979
|  | BROCKHURST | FS |  |  | 35.3976 | 35.3976 | 35.3976 | 35.3976 | 35.3976 | 35.3976 | 35.3976 | 35.3976 | 35.3976 | 35.3976 | 35.3976 | 35.3976 | 35.3976 | 33.5803 | 33.5803 | 33.5803 | 33.5803 | 33.5803 | 33.5803 | 33.5803 | 33.5803 | 33.5783 | 33.5592 | 33.5168 | 33.4153 | 32.9297 | 34.8858 | 34.8769 | 34.8759 | 34.8744 | 34.8728 | 34.8698 | 34.8673 | 34.8645 | 34.8606 | 34.847 | 34.8169 | 34.7896 | 34.7618
MELKSHAM GSP | NORRINGTON | BROMHAM | MINIMUM HEADROOM | ST 98670 65994 | YES | 5.9242 | 5.9222 | 5.918 | 5.7964 | 5.6695 | 5.5413 | 5.4085 | 5.2037 | 5.1322 | 4.901 | 4.7055 | 4.0943 | 3.8786 | 4.9567 | 4.9328 | 4.8824 | 4.7497 | 4.579 | 4.4201 | 4.2566 | 4.0263 | 3.9275 | 3.6163 | 3.2897 | 2.5471 | 2.2234 | 4.9503 | 4.923 | 4.8652 | 4.7307 | 4.553 | 4.3939 | 4.2305 | 4.0003 | 3.9016 | 3.5907 | 3.2645 | 2.5223 | 2.199
|  | BROMHAM | CT |  |  | 5.9249 | 5.9233 | 5.9199 | 5.9048 | 5.889 | 5.8726 | 5.8553 | 5.8289 | 5.8226 | 5.8013 | 5.7145 | 5.5276 | 5.3326 | 4.9651 | 4.9459 | 4.9053 | 4.854 | 4.8025 | 4.7459 | 4.6911 | 4.6275 | 4.5809 | 4.441 | 4.1575 | 3.8519 | 3.6128 | 4.96 | 4.938 | 4.8914 | 4.8344 | 4.7771 | 4.7197 | 4.665 | 4.6015 | 4.5551 | 4.4156 | 4.1327 | 3.8278 | 3.5894
|  | BROMHAM | LW |  |  | 5.9242 | 5.9222 | 5.918 | 5.9123 | 5.9048 | 5.8964 | 5.886 | 5.8681 | 5.8623 | 5.8398 | 5.7922 | 5.5968 | 5.4172 | 4.9567 | 4.9328 | 4.8824 | 4.8318 | 4.7746 | 4.7283 | 4.6802 | 4.6251 | 4.5792 | 4.438 | 4.1938 | 3.9111 | 3.6904 | 4.9503 | 4.923 | 4.8652 | 4.8074 | 4.7484 | 4.7022 | 4.6543 | 4.5992 | 4.5535 | 4.4128 | 4.1692 | 3.8871 | 3.6671
|  | BROMHAM | ST |  |  | 5.9246 | 5.923 | 5.9203 | 5.7964 | 5.6695 | 5.5413 | 5.4085 | 5.2037 | 5.1322 | 4.901 | 4.7055 | 4.0943 | 3.8786 | 4.9611 | 4.9423 | 4.91 | 4.7497 | 4.579 | 4.4201 | 4.2566 | 4.0263 | 3.9275 | 3.6163 | 3.2897 | 2.5471 | 2.2234 | 4.9554 | 4.9338 | 4.8968 | 4.7307 | 4.553 | 4.3939 | 4.2305 | 4.0003 | 3.9016 | 3.5907 | 3.2645 | 2.5223 | 2.199
|  | BROMHAM | FS |  |  | 5.9273 | 5.9272 | 5.927 | 5.9244 | 5.9216 | 5.9189 | 5.916 | 5.9118 | 5.902 | 5.8696 | 5.8504 | 5.7942 | 5.745 | 4.9939 | 4.992 | 4.9902 | 4.98 | 4.9683 | 4.9567 | 4.945 | 4.9295 | 4.9105 | 4.8514 | 4.7896 | 4.6906 | 4.5957 | 4.993 | 4.9909 | 4.9888 | 4.9773 | 4.9642 | 4.9512 | 4.9381 | 4.9207 | 4.9003 | 4.837 | 4.7684 | 4.6644 | 4.5696
BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | BROOK STREET | MINIMUM HEADROOM | SU 63480 52228 | YES | 43.6269 | 43.6269 | 43.6269 | 43.6269 | 43.6229 | 43.6156 | 43.6054 | 43.594 | 43.5812 | 43.5501 | 43.37 | 42.6239 | 41.6282 | 40.8893 | 40.8852 | 40.8771 | 40.8691 | 40.8608 | 40.8526 | 40.841 | 40.8279 | 40.8134 | 40.6491 | 40.0106 | 39.2083 | 38.1994 | 42.5436 | 42.5436 | 42.5436 | 42.5436 | 42.5436 | 42.5436 | 42.5436 | 42.5436 | 42.5436 | 42.5328 | 42.301 | 41.1498 | 39.8958
|  | BROOK STREET | CT |  |  | 43.6269 | 43.6269 | 43.6269 | 43.6269 | 43.6229 | 43.6156 | 43.6054 | 43.594 | 43.5812 | 43.5501 | 43.37 | 42.6239 | 41.6282 | 40.8893 | 40.8852 | 40.8771 | 40.8691 | 40.8608 | 40.8526 | 40.841 | 40.8279 | 40.8134 | 40.6491 | 40.0106 | 39.2083 | 38.1994 | 42.5436 | 42.5436 | 42.5436 | 42.5436 | 42.5436 | 42.5436 | 42.5436 | 42.5436 | 42.5436 | 42.5328 | 42.301 | 41.1498 | 39.8958
|  | BROOK STREET | LW |  |  | 43.6269 | 43.6269 | 43.6269 | 43.6269 | 43.6235 | 43.6173 | 43.6071 | 43.5957 | 43.5829 | 43.5518 | 43.376 | 42.643 | 41.6473 | 40.8895 | 40.8854 | 40.8775 | 40.8696 | 40.8615 | 40.8545 | 40.8429 | 40.8299 | 40.8153 | 40.6647 | 40.0261 | 39.2239 | 38.2228 | 42.5436 | 42.5436 | 42.5436 | 42.5436 | 42.5436 | 42.5436 | 42.5436 | 42.5436 | 42.5436 | 42.5341 | 42.3233 | 41.1722 | 39.9199
|  | BROOK STREET | ST |  |  | 43.6269 | 43.6269 | 43.6269 | 43.6269 | 43.6269 | 43.6269 | 43.6268 | 43.6191 | 43.6103 | 43.5887 | 43.5402 | 43.3759 | 42.9969 | 40.8925 | 40.8905 | 40.8872 | 40.8832 | 40.8784 | 40.8733 | 40.8652 | 40.8565 | 40.8465 | 40.8219 | 40.5574 | 40.0258 | 39.5125 | 42.5436 | 42.5436 | 42.5436 | 42.5436 | 42.5436 | 42.5436 | 42.5436 | 42.5436 | 42.5436 | 42.5436 | 42.5248 | 42.3229 | 41.5863
|  | BROOK STREET | FS |  |  | 43.6269 | 43.6269 | 43.6269 | 43.6269 | 43.6269 | 43.6269 | 43.6269 | 43.6269 | 43.6269 | 43.6269 | 43.609 | 43.5816 | 43.5521 | 40.8951 | 40.8945 | 40.8939 | 40.8924 | 40.8906 | 40.8887 | 40.8855 | 40.8816 | 40.8777 | 40.868 | 40.845 | 40.8138 | 40.6669 | 42.5436 | 42.5436 | 42.5436 | 42.5436 | 42.5436 | 42.5436 | 42.5436 | 42.5436 | 42.5436 | 42.5436 | 42.5436 | 42.5436 | 42.5343
MELKSHAM GSP | FROME BSP | BRUTON | MINIMUM HEADROOM | ST 69094 35148 | YES | 11.973 | 11.9542 | 11.9145 | 11.8748 | 11.834 | 11.7927 | 11.7502 | 11.7024 | 11.661 | 11.5343 | 11.316 | 11.0674 | 10.8652 | 11.0675 | 11.0457 | 10.9996 | 10.9537 | 10.9068 | 10.8595 | 10.811 | 10.7574 | 10.7096 | 10.5641 | 10.3145 | 10.0334 | 9.7993 | 11.4604 | 11.4436 | 11.4079 | 11.3721 | 11.3353 | 11.2921 | 11.2437 | 11.1901 | 11.1424 | 10.9972 | 10.7481 | 10.4675 | 10.2338
|  | BRUTON | CT |  |  | 11.9776 | 11.9614 | 11.927 | 11.8932 | 11.8595 | 11.8256 | 11.7872 | 11.7472 | 11.7071 | 11.587 | 11.3658 | 11.1342 | 10.9262 | 11.0728 | 11.054 | 11.0141 | 10.9749 | 10.9359 | 10.8968 | 10.8524 | 10.8065 | 10.7601 | 10.6212 | 10.3688 | 10.1046 | 9.8647 | 11.4645 | 11.45 | 11.4191 | 11.3888 | 11.3584 | 11.328 | 11.285 | 11.2392 | 11.1928 | 11.0542 | 10.8022 | 10.5386 | 10.2991
|  | BRUTON | LW |  |  | 11.973 | 11.9542 | 11.9145 | 11.8748 | 11.834 | 11.7927 | 11.7502 | 11.7024 | 11.661 | 11.5343 | 11.316 | 11.0674 | 10.8652 | 11.0675 | 11.0457 | 10.9996 | 10.9537 | 10.9068 | 10.8595 | 10.811 | 10.7574 | 10.7096 | 10.5641 | 10.3145 | 10.0334 | 9.7993 | 11.4604 | 11.4436 | 11.4079 | 11.3721 | 11.3353 | 11.2921 | 11.2437 | 11.1901 | 11.1424 | 10.9972 | 10.7481 | 10.4675 | 10.2338
|  | BRUTON | ST |  |  | 11.9981 | 11.9938 | 11.9864 | 11.977 | 11.9654 | 11.9415 | 11.9174 | 11.8898 | 11.8616 | 11.7761 | 11.638 | 11.477 | 11.3365 | 11.0967 | 11.0917 | 11.083 | 11.0722 | 11.0589 | 11.0312 | 11.0034 | 10.9718 | 10.9392 | 10.8411 | 10.6823 | 10.5003 | 10.3389 | 11.483 | 11.4791 | 11.4724 | 11.464 | 11.4536 | 11.432 | 11.4102 | 11.3852 | 11.3598 | 11.2737 | 11.1152 | 10.9335 | 10.7724
|  | BRUTON | FS |  |  | 12.0023 | 12.0008 | 11.9993 | 11.9928 | 11.9853 | 11.9779 | 11.9704 | 11.9609 | 11.9501 | 11.9172 | 11.8662 | 11.8093 | 11.7551 | 11.1015 | 11.0997 | 11.098 | 11.0905 | 11.0818 | 11.0731 | 11.0645 | 11.0535 | 11.041 | 11.0032 | 10.9443 | 10.8797 | 10.8183 | 11.4867 | 11.4853 | 11.484 | 11.4782 | 11.4714 | 11.4648 | 11.4581 | 11.4496 | 11.4398 | 11.4101 | 11.364 | 11.312 | 11.2509
COWLEY GSP | WITNEY BSP | BURFORD | MINIMUM HEADROOM | SP 25671 12529 | NO | 6.5556 | 6.5462 | 6.5409 | 6.5355 | 6.5292 | 6.5112 | 6.4932 | 6.476 | 6.4544 | 6.3879 | 6.2762 | 6.1649 | 6.0557 | 5.8834 | 5.8825 | 5.8821 | 5.8816 | 5.881 | 5.8794 | 5.8778 | 5.8763 | 5.8747 | 5.8699 | 5.8618 | 5.8325 | 5.655 | 6.1808 | 6.1691 | 6.1626 | 6.1559 | 6.1481 | 6.1258 | 6.1034 | 6.0821 | 6.0595 | 5.9928 | 5.8808 | 5.7693 | 5.6598
|  | BURFORD | CT |  |  | 6.5556 | 6.5462 | 6.5409 | 6.5355 | 6.5293 | 6.5225 | 6.5045 | 6.4873 | 6.4684 | 6.4019 | 6.2902 | 6.179 | 6.0698 | 5.8834 | 5.8825 | 5.8821 | 5.8816 | 5.881 | 5.8804 | 5.8788 | 5.8773 | 5.8757 | 5.8709 | 5.8628 | 5.8548 | 5.678 | 6.1808 | 6.1691 | 6.1626 | 6.1559 | 6.1482 | 6.1398 | 6.1175 | 6.0962 | 6.0735 | 6.0068 | 5.8948 | 5.7834 | 5.674
|  | BURFORD | LW |  |  | 6.5556 | 6.5462 | 6.5409 | 6.5355 | 6.5292 | 6.5112 | 6.4932 | 6.476 | 6.4544 | 6.3879 | 6.2762 | 6.1649 | 6.0557 | 5.8834 | 5.8825 | 5.8821 | 5.8816 | 5.881 | 5.8794 | 5.8778 | 5.8763 | 5.8747 | 5.8699 | 5.8618 | 5.8325 | 5.655 | 6.1808 | 6.1691 | 6.1626 | 6.1559 | 6.1481 | 6.1258 | 6.1034 | 6.0821 | 6.0595 | 5.9928 | 5.8808 | 5.7693 | 5.6598
|  | BURFORD | ST |  |  | 6.5596 | 6.5533 | 6.551 | 6.5478 | 6.5435 | 6.5367 | 6.5299 | 6.5181 | 6.5057 | 6.4688 | 6.394 | 6.3222 | 6.2512 | 5.8837 | 5.8832 | 5.883 | 5.8827 | 5.8823 | 5.8817 | 5.8811 | 5.88 | 5.8789 | 5.8757 | 5.8703 | 5.8651 | 5.86 | 6.1858 | 6.178 | 6.175 | 6.1711 | 6.1658 | 6.1574 | 6.1489 | 6.1344 | 6.1189 | 6.0739 | 5.9989 | 5.927 | 5.8558
|  | BURFORD | FS |  |  | 6.5638 | 6.5604 | 6.5602 | 6.5593 | 6.5579 | 6.5556 | 6.5532 | 6.5505 | 6.5457 | 6.5317 | 6.5086 | 6.4873 | 6.466 | 5.8841 | 5.8838 | 5.8838 | 5.8837 | 5.8836 | 5.8834 | 5.8832 | 5.8829 | 5.8825 | 5.8812 | 5.8792 | 5.8773 | 5.8755 | 6.1909 | 6.1867 | 6.1865 | 6.1853 | 6.1837 | 6.1807 | 6.1778 | 6.1745 | 6.1685 | 6.1511 | 6.1226 | 6.0961 | 6.071
MANNINGTON GSP | WAREHAM | BUSHEY | MINIMUM HEADROOM | SY 97671 83532 | YES | 3.4975 | 3.4921 | 3.4806 | 3.4694 | 3.4582 | 3.4386 | 3.4191 | 3.3998 | 3.3789 | 3.3172 | 3.2159 | 3.1114 | 3.0085 | 3.3419 | 3.3355 | 3.322 | 3.3088 | 3.2957 | 3.2727 | 3.2498 | 3.2271 | 3.2026 | 3.1302 | 3.0112 | 2.8885 | 2.7678 | 3.3418 | 3.3354 | 3.3219 | 3.3088 | 3.2957 | 3.2726 | 3.2497 | 3.227 | 3.2025 | 3.1301 | 3.0111 | 2.8883 | 2.7675
|  | BUSHEY | CT |  |  | 3.4975 | 3.4921 | 3.4806 | 3.4694 | 3.4582 | 3.4471 | 3.4277 | 3.4083 | 3.3875 | 3.3258 | 3.2244 | 3.1199 | 3.017 | 3.3419 | 3.3355 | 3.322 | 3.3088 | 3.2957 | 3.2827 | 3.2599 | 3.2372 | 3.2127 | 3.1403 | 3.0212 | 2.8985 | 2.7777 | 3.3418 | 3.3354 | 3.3219 | 3.3088 | 3.2957 | 3.2827 | 3.2598 | 3.2371 | 3.2126 | 3.1402 | 3.0211 | 2.8983 | 2.7774
|  | BUSHEY | LW |  |  | 3.4975 | 3.4921 | 3.4806 | 3.4694 | 3.4582 | 3.4386 | 3.4191 | 3.3998 | 3.3789 | 3.3172 | 3.2159 | 3.1114 | 3.0085 | 3.3419 | 3.3355 | 3.322 | 3.3088 | 3.2957 | 3.2727 | 3.2498 | 3.2271 | 3.2026 | 3.1302 | 3.0112 | 2.8885 | 2.7678 | 3.3418 | 3.3354 | 3.3219 | 3.3088 | 3.2957 | 3.2726 | 3.2497 | 3.227 | 3.2025 | 3.1301 | 3.0111 | 2.8883 | 2.7675
|  | BUSHEY | ST |  |  | 3.5011 | 3.4981 | 3.4929 | 3.4866 | 3.4789 | 3.4687 | 3.4586 | 3.4454 | 3.4312 | 3.3898 | 3.3225 | 3.2554 | 3.1885 | 3.3461 | 3.3426 | 3.3365 | 3.329 | 3.32 | 3.308 | 3.2962 | 3.2807 | 3.264 | 3.2154 | 3.1364 | 3.0576 | 2.979 | 3.3461 | 3.3425 | 3.3364 | 3.329 | 3.32 | 3.308 | 3.2961 | 3.2807 | 3.2639 | 3.2153 | 3.1363 | 3.0574 | 2.9789
|  | BUSHEY | FS |  |  | 3.506 | 3.5056 | 3.5053 | 3.5035 | 3.5015 | 3.4983 | 3.4951 | 3.4909 | 3.4855 | 3.4696 | 3.4444 | 3.4203 | 3.3978 | 3.3519 | 3.3514 | 3.351 | 3.3489 | 3.3465 | 3.3428 | 3.3391 | 3.3341 | 3.3277 | 3.3092 | 3.2795 | 3.2513 | 3.2247 | 3.3518 | 3.3514 | 3.3509 | 3.3489 | 3.3465 | 3.3427 | 3.339 | 3.3341 | 3.3277 | 3.3091 | 3.2794 | 3.2512 | 3.2247
FAWLEY GSP | LANGLEY BSP | BUTTS ASH | MINIMUM HEADROOM | SU 41923 05772 | YES | 27.0969 | 27.0969 | 27.0969 | 27.0963 | 27.0951 | 27.0932 | 27.0907 | 27.0855 | 27.0846 | 27.08 | 27.0688 | 27.0471 | 26.3319 | 25.4407 | 25.4407 | 25.4407 | 25.4402 | 25.439 | 25.4371 | 25.4345 | 25.4293 | 25.4284 | 25.4238 | 24.4156 | 23.1897 | 22.0023 | 26.5008 | 26.5008 | 26.5008 | 26.5002 | 26.499 | 26.4971 | 26.4945 | 26.4893 | 26.4884 | 26.4839 | 26.4727 | 25.4769 | 24.2688
|  | BUTTS ASH | CT |  |  | 27.0969 | 27.0969 | 27.0969 | 27.0967 | 27.0964 | 27.0959 | 27.0952 | 27.0936 | 27.0933 | 27.0918 | 27.0794 | 27.0656 | 26.6273 | 25.4407 | 25.4407 | 25.4407 | 25.4406 | 25.4402 | 25.4398 | 25.439 | 25.4375 | 25.4372 | 25.4357 | 24.7438 | 23.5261 | 22.3365 | 26.5008 | 26.5008 | 26.5008 | 26.5006 | 26.5003 | 26.4998 | 26.4991 | 26.4975 | 26.4972 | 26.4957 | 26.4833 | 25.8138 | 24.6086
|  | BUTTS ASH | LW |  |  | 27.0969 | 27.0969 | 27.0969 | 27.0963 | 27.0951 | 27.0932 | 27.0907 | 27.0855 | 27.0846 | 27.08 | 27.0688 | 27.0471 | 26.3319 | 25.4407 | 25.4407 | 25.4407 | 25.4402 | 25.439 | 25.4371 | 25.4345 | 25.4293 | 25.4284 | 25.4238 | 24.4156 | 23.1897 | 22.0023 | 26.5008 | 26.5008 | 26.5008 | 26.5002 | 26.499 | 26.4971 | 26.4945 | 26.4893 | 26.4884 | 26.4839 | 26.4727 | 25.4769 | 24.2688
|  | BUTTS ASH | ST |  |  | 27.0969 | 27.0969 | 27.0969 | 27.0968 | 27.0965 | 27.0961 | 27.0956 | 27.0944 | 27.0938 | 27.0907 | 27.0866 | 27.0722 | 27.067 | 25.4407 | 25.4407 | 25.4407 | 25.4406 | 25.4404 | 25.44 | 25.4395 | 25.4383 | 25.4377 | 25.4346 | 25.4087 | 24.6201 | 23.8445 | 26.5008 | 26.5008 | 26.5008 | 26.5006 | 26.5004 | 26.5 | 26.4995 | 26.4983 | 26.4977 | 26.4946 | 26.4905 | 26.4761 | 26.1183
|  | BUTTS ASH | FS |  |  | 27.0969 | 27.0969 | 27.0969 | 27.0969 | 27.0969 | 27.0968 | 27.0968 | 27.0968 | 27.0966 | 27.0954 | 27.0946 | 27.0903 | 27.0861 | 25.4407 | 25.4407 | 25.4407 | 25.4407 | 25.4407 | 25.4407 | 25.4407 | 25.4406 | 25.4404 | 25.4393 | 25.4384 | 25.4341 | 25.4299 | 26.5008 | 26.5008 | 26.5008 | 26.5008 | 26.5008 | 26.5007 | 26.5007 | 26.5007 | 26.5005 | 26.4993 | 26.4984 | 26.4942 | 26.49
MELKSHAM GSP | CHIPPENHAM | CALNE | MINIMUM HEADROOM | SU 00521 72497 | YES | 18.5113 | 18.4632 | 18.3653 | 18.2696 | 18.1729 | 18.0196 | 17.868 | 17.7184 | 17.5574 | 17.0822 | 16.3002 | 15.4984 | 14.7103 | 18.6839 | 18.6807 | 18.6741 | 18.6678 | 18.6613 | 18.6511 | 18.641 | 18.631 | 18.6203 | 18.3862 | 17.3119 | 16.2107 | 15.1281 | 17.5883 | 17.5845 | 17.5768 | 17.5692 | 17.5616 | 17.5495 | 17.5375 | 17.5257 | 17.513 | 17.4755 | 16.4757 | 15.446 | 14.4147
|  | CALNE | CT |  |  | 18.5244 | 18.4835 | 18.4007 | 18.3197 | 18.2376 | 18.1564 | 18.005 | 17.8554 | 17.6944 | 17.2193 | 16.437 | 15.6355 | 14.8477 | 18.6847 | 18.682 | 18.6765 | 18.6711 | 18.6656 | 18.6602 | 18.6501 | 18.6402 | 18.6294 | 18.5744 | 17.4998 | 16.399 | 15.3168 | 17.5893 | 17.5861 | 17.5796 | 17.5732 | 17.5667 | 17.5603 | 17.5483 | 17.5365 | 17.5238 | 17.4863 | 16.6514 | 15.622 | 14.6041
|  | CALNE | LW |  |  | 18.5113 | 18.4632 | 18.3653 | 18.2696 | 18.1729 | 18.0196 | 17.868 | 17.7184 | 17.5574 | 17.0822 | 16.3002 | 15.4984 | 14.7103 | 18.6839 | 18.6807 | 18.6741 | 18.6678 | 18.6613 | 18.6511 | 18.641 | 18.631 | 18.6203 | 18.3862 | 17.3119 | 16.2107 | 15.1281 | 17.5883 | 17.5845 | 17.5768 | 17.5692 | 17.5616 | 17.5495 | 17.5375 | 17.5257 | 17.513 | 17.4755 | 16.4757 | 15.446 | 14.4147
|  | CALNE | ST |  |  | 18.5281 | 18.4923 | 18.4332 | 18.3601 | 18.2711 | 18.1711 | 18.0727 | 17.9704 | 17.8605 | 17.54 | 17.0193 | 16.5029 | 15.9901 | 18.685 | 18.6826 | 18.6787 | 18.6738 | 18.6679 | 18.6612 | 18.6547 | 18.6478 | 18.6405 | 18.6192 | 18.2998 | 17.5904 | 16.8861 | 17.5896 | 17.5868 | 17.5821 | 17.5764 | 17.5693 | 17.5614 | 17.5537 | 17.5456 | 17.5369 | 17.5116 | 17.3993 | 16.7361 | 16.0775
|  | CALNE | FS |  |  | 18.5908 | 18.5863 | 18.5829 | 18.5631 | 18.5397 | 18.5046 | 18.4698 | 18.4243 | 18.3649 | 18.1875 | 17.9646 | 17.6975 | 17.4539 | 18.6892 | 18.6889 | 18.6886 | 18.6837 | 18.6786 | 18.6727 | 18.6668 | 18.6582 | 18.6385 | 18.5771 | 18.5386 | 18.4463 | 18.3678 | 17.5946 | 17.5942 | 17.5939 | 17.5888 | 17.5835 | 17.5772 | 17.5709 | 17.5618 | 17.5416 | 17.4786 | 17.4377 | 17.3431 | 17.2625
BRAMLEY (FLEE) | CAMBERLEY MAIN | CAMBERLEY | MINIMUM HEADROOM | SU 86584 59452 | YES | 115.205 | 115.1902 | 114.2869 | 114.2129 | 114.1388 | 114.0648 | 113.9907 | 113.9167 | 113.8871 | 113.7982 | 113.2334 | 112.8157 | 112.6094 | 108.4157 | 108.3867 | 107.4302 | 107.2426 | 107.0497 | 106.8866 | 106.7235 | 106.5605 | 106.4359 | 106.0411 | 104.3256 | 102.2593 | 100.4063 | 112.6508 | 112.636 | 111.7304 | 111.6353 | 111.5403 | 111.4541 | 111.3679 | 111.2817 | 111.2392 | 111.1102 | 110.4685 | 108.9613 | 107.1617
|  | CAMBERLEY | CT |  |  | 115.282 | 115.2731 | 114.7311 | 114.6305 | 114.5289 | 114.4264 | 114.3212 | 114.1833 | 114.1536 | 114.0622 | 113.2334 | 112.8157 | 112.6094 | 108.4961 | 108.4748 | 107.9071 | 107.7107 | 107.5104 | 107.2927 | 107.0986 | 106.8717 | 106.7471 | 106.3612 | 104.3256 | 102.2593 | 100.4063 | 112.7278 | 112.7189 | 112.177 | 112.0623 | 111.9424 | 111.8218 | 111.7045 | 111.5544 | 111.5118 | 111.3803 | 110.4685 | 108.9613 | 107.1617
|  | CAMBERLEY | LW |  |  | 115.205 | 115.1902 | 114.2869 | 114.2129 | 114.1388 | 114.0648 | 113.9907 | 113.9167 | 113.8871 | 113.7982 | 113.6501 | 113.5613 | 113.3984 | 108.4157 | 108.3867 | 107.4302 | 107.2426 | 107.0497 | 106.8866 | 106.7235 | 106.5605 | 106.4359 | 106.0411 | 104.6381 | 102.9006 | 101.0906 | 112.6508 | 112.636 | 111.7304 | 111.6353 | 111.5403 | 111.4541 | 111.3679 | 111.2817 | 111.2392 | 111.1102 | 110.8792 | 109.606 | 107.8494
|  | CAMBERLEY | ST |  |  | 115.3205 | 115.3146 | 114.9533 | 114.9236 | 114.894 | 114.8644 | 114.8348 | 114.8052 | 114.7933 | 114.7578 | 114.6986 | 114.663 | 114.5979 | 108.5482 | 108.5321 | 108.1604 | 108.118 | 108.073 | 107.9995 | 107.9144 | 107.8402 | 107.7806 | 107.5649 | 107.091 | 106.2999 | 105.1983 | 112.7663 | 112.7604 | 112.3991 | 112.3695 | 112.3399 | 112.3064 | 112.2665 | 112.2286 | 112.2079 | 112.1451 | 112.0293 | 111.931 | 111.8043
|  | CAMBERLEY | FS |  |  | 115.359 | 115.356 | 115.1754 | 115.157 | 115.1387 | 115.1204 | 115.102 | 115.0816 | 115.0601 | 114.9931 | 114.94 | 114.8484 | 114.754 | 108.5954 | 108.5912 | 108.4093 | 108.3859 | 108.3618 | 108.3386 | 108.3155 | 108.289 | 108.2629 | 108.1813 | 108.046 | 107.8108 | 107.5275 | 112.8048 | 112.8019 | 112.6212 | 112.6028 | 112.5845 | 112.5662 | 112.5478 | 112.5274 | 112.506 | 112.4389 | 112.3766 | 112.2584 | 112.1368
WILLESDEN GSP | CANAL BANK | CANAL BANK 11kV | MINIMUM HEADROOM | TQ 20927 83082 | YES | 51.5314 | 51.5268 | 51.5173 | 51.4955 | 51.4647 | 51.4382 | 51.4109 | 51.3709 | 51.3554 | 51.3053 | 51.2457 | 51.0976 | 50.9448 | 52.2685 | 52.2563 | 52.2314 | 52.2071 | 52.1673 | 52.1357 | 52.1031 | 52.0588 | 52.0387 | 51.973 | 51.8576 | 51.6354 | 51.4834 | 52.6747 | 52.6747 | 52.6747 | 52.6522 | 52.6293 | 52.606 | 52.5819 | 52.5446 | 52.532 | 52.4884 | 52.4367 | 52.2739 | 52.1377
|  | CANAL BANK 11kV | CT |  |  | 51.5329 | 51.529 | 51.5212 | 51.5135 | 51.5058 | 51.4981 | 51.4942 | 51.4902 | 51.486 | 51.4719 | 51.4329 | 51.3829 | 51.3323 | 52.2723 | 52.2622 | 52.2418 | 52.2217 | 52.2015 | 52.1813 | 52.1711 | 52.1607 | 52.1498 | 52.1129 | 51.9626 | 51.7675 | 51.5701 | 52.6747 | 52.6747 | 52.6747 | 52.6747 | 52.6747 | 52.6747 | 52.6747 | 52.6747 | 52.6747 | 52.6747 | 52.6747 | 52.6747 | 52.6747
|  | CANAL BANK 11kV | LW |  |  | 51.5314 | 51.5268 | 51.5173 | 51.5079 | 51.4986 | 51.4947 | 51.4908 | 51.4868 | 51.4827 | 51.4685 | 51.4296 | 51.3795 | 51.3289 | 52.2685 | 52.2563 | 52.2314 | 52.2071 | 52.1826 | 52.1725 | 52.1623 | 52.1519 | 52.141 | 52.1016 | 51.9495 | 51.7544 | 51.557 | 52.6747 | 52.6747 | 52.6747 | 52.6747 | 52.6747 | 52.6747 | 52.6747 | 52.6747 | 52.6747 | 52.6747 | 52.6747 | 52.6747 | 52.6747
|  | CANAL BANK 11kV | ST |  |  | 51.5665 | 51.53 | 51.5246 | 51.4955 | 51.4647 | 51.4382 | 51.4109 | 51.3709 | 51.3554 | 51.3053 | 51.2457 | 51.1195 | 51.0605 | 52.36 | 52.2647 | 52.2506 | 52.2109 | 52.1673 | 52.1357 | 52.1031 | 52.0588 | 52.0387 | 51.973 | 51.8576 | 51.6354 | 51.4834 | 52.6747 | 52.6747 | 52.6747 | 52.6522 | 52.6293 | 52.606 | 52.5819 | 52.5446 | 52.532 | 52.4916 | 52.4591 | 52.3661 | 52.3391
|  | CANAL BANK 11kV | FS |  |  | 51.5716 | 51.5378 | 51.5374 | 51.5278 | 51.5181 | 51.5092 | 51.5002 | 51.4865 | 51.4512 | 51.3389 | 51.2759 | 51.0976 | 50.9448 | 52.3734 | 52.2852 | 52.2839 | 52.2717 | 52.2589 | 52.2481 | 52.2372 | 52.2212 | 52.1842 | 52.0658 | 51.9847 | 51.7813 | 51.6016 | 52.6747 | 52.6747 | 52.6747 | 52.6668 | 52.6591 | 52.6513 | 52.6434 | 52.6311 | 52.5969 | 52.4884 | 52.4367 | 52.2739 | 52.1377
WILLESDEN GSP | ACTON LANE | CANAL BANK 6.6kV | MINIMUM HEADROOM | TQ 20927 83082 | YES | 4.3707 | 4.3707 | 56.3707 | 56.3682 | 56.3656 | 56.3631 | 56.3604 | 56.3562 | 56.3548 | 56.35 | 56.3442 | 56.3262 | 56.311 | 4.2591 | 4.2591 | 56.2591 | 56.2566 | 56.254 | 56.2514 | 56.2487 | 56.2446 | 56.2432 | 56.2384 | 56.2295 | 56.1996 | 56.1728 | 4.1423 | 4.1419 | 56.141 | 56.1386 | 56.1353 | 56.1325 | 56.1295 | 56.1251 | 56.1235 | 56.1181 | 56.1121 | 56.0948 | 56.0461
|  | CANAL BANK 6.6kV | CT |  |  | 4.3707 | 4.3707 | 56.3707 | 56.3707 | 56.3707 | 56.3707 | 56.3707 | 56.3707 | 56.3707 | 56.3707 | 56.3707 | 56.3707 | 56.3707 | 4.2591 | 4.2591 | 56.2591 | 56.2591 | 56.2591 | 56.2591 | 56.2591 | 56.2591 | 56.2591 | 56.2591 | 56.2367 | 56.2073 | 56.177 | 4.1424 | 4.1421 | 56.1414 | 56.1407 | 56.14 | 56.1393 | 56.139 | 56.1386 | 56.1382 | 56.137 | 56.1335 | 56.1096 | 56.0507
|  | CANAL BANK 6.6kV | LW |  |  | 4.3707 | 4.3707 | 56.3707 | 56.3707 | 56.3707 | 56.3707 | 56.3707 | 56.3707 | 56.3707 | 56.3707 | 56.3707 | 56.3707 | 56.3707 | 4.2591 | 4.2591 | 56.2591 | 56.2591 | 56.2591 | 56.2591 | 56.2591 | 56.2591 | 56.2591 | 56.2577 | 56.2348 | 56.2053 | 56.1728 | 4.1423 | 4.1419 | 56.141 | 56.1402 | 56.1394 | 56.139 | 56.1387 | 56.1383 | 56.1379 | 56.1367 | 56.1332 | 56.1062 | 56.0461
|  | CANAL BANK 6.6kV | ST |  |  | 4.3707 | 4.3707 | 56.3707 | 56.3682 | 56.3656 | 56.3631 | 56.3604 | 56.3562 | 56.3548 | 56.3503 | 56.3467 | 56.3364 | 56.3334 | 4.2591 | 4.2591 | 56.2591 | 56.2566 | 56.254 | 56.2514 | 56.2487 | 56.2446 | 56.2432 | 56.2387 | 56.2295 | 56.1996 | 56.1778 | 4.1454 | 4.1421 | 56.1417 | 56.1386 | 56.1353 | 56.1325 | 56.1295 | 56.1251 | 56.1235 | 56.1181 | 56.1121 | 56.0988 | 56.0859
|  | CANAL BANK 6.6kV | FS |  |  | 4.3707 | 4.3707 | 56.3707 | 56.3698 | 56.369 | 56.3681 | 56.3672 | 56.3658 | 56.362 | 56.35 | 56.3442 | 56.3262 | 56.311 | 4.2591 | 4.2591 | 56.2591 | 56.2582 | 56.2573 | 56.2565 | 56.2556 | 56.2542 | 56.2504 | 56.2384 | 56.2326 | 56.2145 | 56.1994 | 4.1458 | 4.1428 | 56.1428 | 56.1418 | 56.1407 | 56.1398 | 56.1388 | 56.1373 | 56.1334 | 56.121 | 56.1143 | 56.0948 | 56.0782
COWLEY GSP | WITNEY BSP | CARTERTON | MINIMUM HEADROOM | SP 28261 07823 | NO | 45.4602 | 45.4568 | 45.4523 | 45.3821 | 45.3082 | 45.2341 | 45.1578 | 45.0438 | 45.0243 | 44.9595 | 44.8539 | 44.6259 | 44.5845 | 42.7262 | 42.7236 | 42.7202 | 42.6514 | 42.5792 | 42.5062 | 42.4309 | 42.3178 | 42.2994 | 42.2377 | 42.139 | 41.9188 | 41.7005 | 44.1042 | 44.0648 | 44.0133 | 43.8881 | 43.7412 | 43.6232 | 43.5071 | 43.3513 | 43.2879 | 43.0914 | 42.7001 | 42.1485 | 41.7643
|  | CARTERTON | CT |  |  | 45.4602 | 45.4568 | 45.4523 | 45.447 | 45.44 | 45.4374 | 45.4336 | 45.4296 | 45.4254 | 45.4127 | 45.3853 | 45.3542 | 45.3243 | 42.7262 | 42.7236 | 42.7202 | 42.7163 | 42.711 | 42.7091 | 42.7062 | 42.7032 | 42.7001 | 42.6906 | 42.67 | 42.6467 | 42.4603 | 44.1043 | 44.0649 | 44.0134 | 43.953 | 43.873 | 43.844 | 43.8003 | 43.7546 | 43.7065 | 43.5622 | 43.249 | 42.8943 | 42.5242
|  | CARTERTON | LW |  |  | 45.4602 | 45.4568 | 45.4523 | 45.3821 | 45.3082 | 45.2341 | 45.1578 | 45.0438 | 45.0243 | 44.9595 | 44.8539 | 44.6259 | 44.5845 | 42.7262 | 42.7236 | 42.7202 | 42.6514 | 42.5792 | 42.5062 | 42.4309 | 42.3178 | 42.2994 | 42.2377 | 42.139 | 41.9188 | 41.7005 | 44.1042 | 44.0648 | 44.0133 | 43.8881 | 43.7412 | 43.6232 | 43.5071 | 43.3513 | 43.2879 | 43.0914 | 42.7001 | 42.1485 | 41.7643
|  | CARTERTON | ST |  |  | 45.4613 | 45.4589 | 45.4561 | 45.4527 | 45.448 | 45.4457 | 45.4437 | 45.441 | 45.4381 | 45.4293 | 45.4103 | 45.3897 | 45.3707 | 42.727 | 42.7252 | 42.7231 | 42.7205 | 42.717 | 42.7153 | 42.7138 | 42.7118 | 42.7096 | 42.703 | 42.6887 | 42.6733 | 42.659 | 44.1166 | 44.0896 | 44.0574 | 44.018 | 43.9644 | 43.9384 | 43.9152 | 43.8844 | 43.8514 | 43.7516 | 43.5338 | 43.2996 | 43.0822
|  | CARTERTON | FS |  |  | 45.4623 | 45.4609 | 45.4594 | 45.4577 | 45.4555 | 45.4548 | 45.4542 | 45.4534 | 45.4523 | 45.4489 | 45.441 | 45.4317 | 45.4223 | 42.7278 | 42.7267 | 42.7256 | 42.7243 | 42.7227 | 42.7221 | 42.7217 | 42.7211 | 42.7203 | 42.7177 | 42.7118 | 42.7048 | 42.6977 | 44.1281 | 44.1118 | 44.0947 | 44.0751 | 44.0505 | 44.042 | 44.035 | 44.0268 | 44.014 | 43.9749 | 43.8852 | 43.7784 | 43.6711
AXMINSTER | YEOVIL BSP | CASTLE CARY | MINIMUM HEADROOM | ST 64534 31039 | YES | 11.4545 | 11.4491 | 11.4409 | 11.4318 | 11.4211 | 11.3894 | 11.3592 | 11.3285 | 11.299 | 11.211 | 11.0633 | 10.9045 | 10.7666 | 10.2251 | 10.2142 | 10.1978 | 10.1795 | 10.1579 | 10.095 | 10.0355 | 9.9771 | 9.9187 | 9.7455 | 9.4577 | 9.1579 | 8.8824 | 10.3598 | 10.3481 | 10.3305 | 10.3109 | 10.2877 | 10.2201 | 10.1564 | 10.094 | 10.0312 | 9.8455 | 9.5372 | 9.2167 | 8.921
|  | CASTLE CARY | CT |  |  | 11.4545 | 11.4491 | 11.4409 | 11.4318 | 11.4211 | 11.4104 | 11.3806 | 11.3505 | 11.3212 | 11.2347 | 11.0769 | 10.9113 | 10.7666 | 10.2251 | 10.2142 | 10.1978 | 10.1795 | 10.1579 | 10.1365 | 10.0775 | 10.0197 | 9.9614 | 9.7898 | 9.4918 | 9.1854 | 8.903 | 10.3598 | 10.3481 | 10.3305 | 10.3109 | 10.2877 | 10.2646 | 10.2014 | 10.1396 | 10.077 | 9.8929 | 9.5743 | 9.2472 | 8.9446
|  | CASTLE CARY | LW |  |  | 11.4545 | 11.4491 | 11.4409 | 11.4318 | 11.4211 | 11.3894 | 11.3592 | 11.3285 | 11.299 | 11.211 | 11.0633 | 10.9045 | 10.7667 | 10.2251 | 10.2142 | 10.1978 | 10.1795 | 10.1579 | 10.095 | 10.0355 | 9.9771 | 9.9187 | 9.7455 | 9.4577 | 9.1579 | 8.8824 | 10.3598 | 10.3481 | 10.3305 | 10.3109 | 10.2877 | 10.2201 | 10.1564 | 10.094 | 10.0312 | 9.8455 | 9.5372 | 9.2167 | 8.921
|  | CASTLE CARY | ST |  |  | 11.4585 | 11.4551 | 11.4508 | 11.4428 | 11.4329 | 11.4134 | 11.3951 | 11.3712 | 11.3497 | 11.2863 | 11.1875 | 11.0759 | 10.9803 | 10.2332 | 10.2263 | 10.2177 | 10.2041 | 10.1868 | 10.1505 | 10.1168 | 10.0741 | 10.0328 | 9.9118 | 9.7194 | 9.5168 | 9.3316 | 10.3685 | 10.3611 | 10.3519 | 10.3375 | 10.3191 | 10.2804 | 10.2444 | 10.1989 | 10.1547 | 10.0252 | 9.819 | 9.6032 | 9.4048
|  | CASTLE CARY | FS |  |  | 11.526 | 11.4612 | 11.4599 | 11.4578 | 11.455 | 11.4493 | 11.4443 | 11.4384 | 11.4307 | 11.4078 | 11.3719 | 11.3369 | 11.3042 | 10.3688 | 10.2386 | 10.236 | 10.2317 | 10.2261 | 10.2147 | 10.2047 | 10.1929 | 10.1774 | 10.1322 | 10.0606 | 9.9924 | 9.9283 | 10.5142 | 10.3743 | 10.3716 | 10.3669 | 10.3609 | 10.3486 | 10.3379 | 10.3252 | 10.3086 | 10.2602 | 10.1833 | 10.1102 | 10.0416
LALEHAM | STAINES | CAUSEWAY | MINIMUM HEADROOM | TQ 02763 71680 | YES | 50.1052 | 50.1052 | 50.1052 | 50.0923 | 50.0796 | 50.0668 | 50.0539 | 50.0336 | 49.9774 | 49.7989 | 49.7139 | 49.0553 | 47.609 | 47.9789 | 47.8709 | 47.7276 | 47.5859 | 47.3861 | 47.1039 | 46.7978 | 46.5802 | 46.3647 | 45.7118 | 44.2679 | 42.5453 | 40.8222 | 48.1575 | 48.0689 | 47.9514 | 47.8195 | 47.6264 | 47.3618 | 47.0748 | 46.8707 | 46.6686 | 46.0563 | 44.6736 | 42.9408 | 41.1973
|  | CAUSEWAY | CT |  |  | 50.1052 | 50.1052 | 50.1052 | 50.1052 | 50.1052 | 50.1052 | 50.1052 | 50.1052 | 50.1052 | 50.1052 | 50.1052 | 49.1746 | 47.7286 | 47.9964 | 47.8982 | 47.7754 | 47.6537 | 47.479 | 47.2459 | 46.9398 | 46.7223 | 46.5066 | 45.8539 | 44.4098 | 42.6875 | 40.9646 | 48.1718 | 48.0913 | 47.9905 | 47.8869 | 47.7135 | 47.495 | 47.2079 | 47.004 | 46.8017 | 46.1896 | 44.8152 | 43.0847 | 41.3414
|  | CAUSEWAY | LW |  |  | 50.1052 | 50.1052 | 50.1052 | 50.1052 | 50.1052 | 50.1052 | 50.1052 | 50.1052 | 50.1052 | 50.1052 | 50.1052 | 49.0553 | 47.609 | 47.9789 | 47.8709 | 47.7276 | 47.5859 | 47.3861 | 47.1039 | 46.7978 | 46.5802 | 46.3647 | 45.7118 | 44.2679 | 42.5453 | 40.8222 | 48.1575 | 48.0689 | 47.9514 | 47.8195 | 47.6264 | 47.3618 | 47.0748 | 46.8707 | 46.6686 | 46.0563 | 44.6736 | 42.9408 | 41.1973
|  | CAUSEWAY | ST |  |  | 50.1052 | 50.1052 | 50.1052 | 50.0963 | 50.0873 | 50.078 | 50.0684 | 50.0536 | 50.0486 | 50.0326 | 50.0197 | 49.9736 | 49.485 | 48.0081 | 47.9336 | 47.8531 | 47.7453 | 47.5834 | 47.3838 | 47.1616 | 46.9991 | 46.8468 | 46.3841 | 45.3757 | 44.1967 | 43.085 | 48.1814 | 48.1203 | 48.0543 | 47.9643 | 47.8169 | 47.6226 | 47.4136 | 47.2603 | 47.1172 | 46.6823 | 45.7359 | 44.6023 | 43.4887
|  | CAUSEWAY | FS |  |  | 50.1052 | 50.1052 | 50.1052 | 50.0923 | 50.0796 | 50.0668 | 50.0539 | 50.0336 | 49.9774 | 49.7989 | 49.7139 | 49.4463 | 49.2225 | 48.0841 | 48.0585 | 48.0498 | 48.011 | 47.9517 | 47.8688 | 47.7813 | 47.7 | 47.5897 | 47.2477 | 46.7638 | 45.9929 | 45.2448 | 48.2438 | 48.2229 | 48.2156 | 48.1815 | 48.1306 | 48.0603 | 47.9862 | 47.9158 | 47.8153 | 47.4814 | 47.0185 | 46.2789 | 45.5634
BRAMLEY (FLEE) | READING TOWN BSP | CAVERSHAM | MINIMUM HEADROOM | SU 71512 75747 | YES | 43.0234 | 43.0234 | 43.0077 | 42.9669 | 42.9264 | 42.8897 | 42.8754 | 42.7876 | 42.6019 | 42.0295 | 40.8708 | 39.541 | 38.2145 | 40.361 | 40.3449 | 40.3111 | 40.2782 | 39.9239 | 39.401 | 39.1962 | 38.9921 | 38.7738 | 38.1013 | 36.7397 | 35.177 | 33.6183 | 41.9894 | 41.9732 | 41.9393 | 41.9063 | 41.3717 | 40.8843 | 40.6815 | 40.4793 | 40.2631 | 39.5969 | 38.2483 | 36.7004 | 35.1564
|  | CAVERSHAM | CT |  |  | 43.0234 | 43.0234 | 43.0092 | 42.9691 | 42.9292 | 42.8897 | 42.8754 | 42.7876 | 42.6019 | 42.0295 | 40.8708 | 39.541 | 38.2145 | 40.3615 | 40.3456 | 40.3123 | 40.28 | 39.964 | 39.401 | 39.1962 | 38.9921 | 38.7738 | 38.1013 | 36.7397 | 35.177 | 33.6183 | 41.9898 | 41.9739 | 41.9405 | 41.9081 | 41.409 | 40.8843 | 40.6815 | 40.4793 | 40.2631 | 39.5969 | 38.2483 | 36.7004 | 35.1564
|  | CAVERSHAM | LW |  |  | 43.0234 | 43.0234 | 43.0077 | 42.9669 | 42.9264 | 42.912 | 42.8977 | 42.8833 | 42.868 | 42.2998 | 41.1416 | 39.8115 | 38.4847 | 40.361 | 40.3449 | 40.3111 | 40.2782 | 39.9239 | 39.7187 | 39.5141 | 39.3099 | 39.0916 | 38.4189 | 37.0579 | 35.4949 | 33.9358 | 41.9894 | 41.9732 | 41.9393 | 41.9063 | 41.3717 | 41.1807 | 40.9903 | 40.7941 | 40.5779 | 39.9115 | 38.5634 | 37.0152 | 35.4709
|  | CAVERSHAM | ST |  |  | 43.0234 | 43.0234 | 43.0234 | 43.0234 | 43.0044 | 42.9917 | 42.9791 | 42.9693 | 42.9589 | 42.9267 | 42.796 | 41.927 | 41.0753 | 40.3722 | 40.3635 | 40.3486 | 40.3304 | 40.3085 | 40.2982 | 40.2881 | 40.2802 | 40.2717 | 39.9284 | 39.002 | 37.9808 | 36.98 | 42.0006 | 41.9919 | 41.977 | 41.9587 | 41.9367 | 41.9264 | 41.9162 | 41.9083 | 41.8017 | 41.3759 | 40.4891 | 39.4776 | 38.4862
|  | CAVERSHAM | FS |  |  | 43.0234 | 43.0234 | 43.0234 | 43.0234 | 43.0234 | 43.0234 | 43.0234 | 43.0234 | 43.0234 | 43.0234 | 43.0234 | 42.9955 | 42.9649 | 40.386 | 40.3847 | 40.3834 | 40.378 | 40.3715 | 40.3679 | 40.3643 | 40.3598 | 40.3565 | 40.3464 | 40.3256 | 40.3013 | 40.2766 | 42.0145 | 42.0132 | 42.0119 | 42.0064 | 41.9999 | 41.9963 | 41.9927 | 41.9881 | 41.9848 | 41.9747 | 41.9538 | 41.9295 | 41.8812
MANNINGTON GSP | BOURNEMOUTH | CENTRAL | MINIMUM HEADROOM | SZ 10293 91931 | YES | 48.449 | 48.449 | 48.449 | 48.449 | 48.449 | 48.449 | 48.449 | 48.449 | 48.449 | 48.449 | 48.3929 | 47.6018 | 46.341 | 43.844 | 43.8383 | 43.8265 | 43.8143 | 43.8021 | 43.7927 | 43.7827 | 43.7725 | 43.7615 | 43.7282 | 43.6559 | 42.4823 | 41.0399 | 45.8411 | 45.8411 | 45.8411 | 45.8411 | 45.8411 | 45.8411 | 45.8411 | 45.8411 | 45.8411 | 45.8411 | 45.798 | 45.0834 | 43.5954
|  | CENTRAL | CT |  |  | 48.449 | 48.449 | 48.449 | 48.449 | 48.449 | 48.449 | 48.449 | 48.449 | 48.449 | 48.449 | 48.4061 | 47.7618 | 46.501 | 43.8463 | 43.8417 | 43.8325 | 43.8229 | 43.8131 | 43.8033 | 43.7933 | 43.7831 | 43.7721 | 43.7389 | 43.6665 | 42.6653 | 41.223 | 45.8411 | 45.8411 | 45.8411 | 45.8411 | 45.8411 | 45.8411 | 45.8411 | 45.8411 | 45.8411 | 45.8411 | 45.8087 | 45.2722 | 43.7842
|  | CENTRAL | LW |  |  | 48.449 | 48.449 | 48.449 | 48.449 | 48.449 | 48.449 | 48.449 | 48.449 | 48.449 | 48.449 | 48.3929 | 47.6018 | 46.341 | 43.844 | 43.8383 | 43.8265 | 43.8143 | 43.8021 | 43.7927 | 43.7827 | 43.7725 | 43.7615 | 43.7282 | 43.6559 | 42.4823 | 41.0399 | 45.8411 | 45.8411 | 45.8411 | 45.8411 | 45.8411 | 45.8411 | 45.8411 | 45.8411 | 45.8411 | 45.8411 | 45.798 | 45.0834 | 43.5954
|  | CENTRAL | ST |  |  | 48.449 | 48.449 | 48.449 | 48.449 | 48.449 | 48.449 | 48.449 | 48.449 | 48.449 | 48.449 | 48.449 | 48.4095 | 48.2563 | 43.8508 | 43.849 | 43.8462 | 43.8423 | 43.8377 | 43.8245 | 43.8111 | 43.8042 | 43.7967 | 43.774 | 43.7241 | 43.6692 | 43.231 | 45.8411 | 45.8411 | 45.8411 | 45.8411 | 45.8411 | 45.8411 | 45.8411 | 45.8411 | 45.8411 | 45.8411 | 45.8411 | 45.8114 | 45.7579
|  | CENTRAL | FS |  |  | 48.449 | 48.449 | 48.449 | 48.449 | 48.449 | 48.449 | 48.449 | 48.449 | 48.449 | 48.449 | 48.449 | 48.449 | 48.449 | 43.8524 | 43.8517 | 43.851 | 43.8485 | 43.8456 | 43.8411 | 43.8364 | 43.8306 | 43.8277 | 43.8189 | 43.7988 | 43.7746 | 43.7493 | 45.8411 | 45.8411 | 45.8411 | 45.8411 | 45.8411 | 45.8411 | 45.8411 | 45.8411 | 45.8411 | 45.8411 | 45.8411 | 45.8411 | 45.8411
NURSLING GSP | SOUTHAMPTON (2 X 60) | CENTRAL BRIDGE | MINIMUM HEADROOM | SU 42591 11255 | YES | 58.6221 | 58.6221 | 58.6221 | 58.5773 | 58.531 | 58.4827 | 58.4327 | 58.3566 | 58.3461 | 58.31 | 57.6014 | 56.4702 | 55.44 | 54.3478 | 54.3263 | 54.2097 | 54.0162 | 53.7582 | 53.5976 | 53.4259 | 53.2328 | 53.1073 | 52.7097 | 51.7174 | 50.5241 | 49.3406 | 57.0038 | 56.8719 | 56.7356 | 56.5788 | 56.418 | 56.2984 | 56.1186 | 55.9176 | 55.7844 | 55.3627 | 54.3075 | 53.0412 | 51.8765
|  | CENTRAL BRIDGE | CT |  |  | 58.6221 | 58.6221 | 58.6221 | 58.6221 | 58.6221 | 58.6221 | 58.6221 | 58.6221 | 58.6221 | 58.6221 | 58.0533 | 57.0261 | 56.0038 | 54.3504 | 54.3303 | 54.2475 | 54.1657 | 53.9958 | 53.8281 | 53.7064 | 53.5893 | 53.4743 | 53.1129 | 52.1745 | 51.0851 | 49.9197 | 57.0198 | 56.8967 | 56.7789 | 56.6851 | 56.5883 | 56.4976 | 56.4051 | 56.2802 | 56.1575 | 55.7719 | 54.7706 | 53.6084 | 52.4516
|  | CENTRAL BRIDGE | LW |  |  | 58.6221 | 58.6221 | 58.6221 | 58.5773 | 58.531 | 58.4827 | 58.4327 | 58.3566 | 58.3461 | 58.31 | 57.6014 | 56.4702 | 55.44 | 54.3478 | 54.3263 | 54.2097 | 54.0162 | 53.7582 | 53.5976 | 53.4259 | 53.2328 | 53.1073 | 52.7097 | 51.7174 | 50.5241 | 49.3406 | 57.0038 | 56.8719 | 56.7356 | 56.5788 | 56.418 | 56.2984 | 56.1186 | 55.9176 | 55.7844 | 55.3627 | 54.3075 | 53.0412 | 51.8765
|  | CENTRAL BRIDGE | ST |  |  | 58.6221 | 58.6221 | 58.6221 | 58.6221 | 58.6221 | 58.6221 | 58.6221 | 58.6221 | 58.6221 | 58.6221 | 58.6221 | 58.2317 | 57.5847 | 54.3575 | 54.344 | 54.3333 | 54.3146 | 54.2541 | 54.2058 | 54.1515 | 54.0727 | 53.9942 | 53.7437 | 53.0853 | 52.3637 | 51.6776 | 57.0638 | 56.9809 | 56.9149 | 56.856 | 56.7865 | 56.731 | 56.6725 | 56.6299 | 56.5875 | 56.445 | 55.7425 | 54.9725 | 54.2405
|  | CENTRAL BRIDGE | FS |  |  | 58.6221 | 58.6221 | 58.6221 | 58.6221 | 58.6221 | 58.6221 | 58.6221 | 58.6221 | 58.6221 | 58.6221 | 58.6221 | 58.6221 | 58.6221 | 54.3656 | 54.3583 | 54.3546 | 54.3507 | 54.3464 | 54.3429 | 54.3393 | 54.3352 | 54.3325 | 54.3161 | 54.1869 | 53.879 | 53.5195 | 57.1133 | 57.0684 | 57.0457 | 57.0219 | 56.9954 | 56.974 | 56.9518 | 56.9266 | 56.9102 | 56.8576 | 56.7093 | 56.5251 | 56.2058
CHICKERELL GSP | CHICKERELL BSP | CERNE ABBAS | MINIMUM HEADROOM | ST 66140 01039 | YES | 2.6147 | 2.6147 | 5.2147 | 5.2147 | 5.2147 | 5.2147 | 5.2147 | 5.2147 | 5.2147 | 5.2147 | 5.2147 | 5.2147 | 5.2147 | 2.7068 | 2.7058 | 5.2037 | 5.2016 | 5.1996 | 5.1868 | 5.1742 | 5.1617 | 5.1482 | 5.1083 | 5.041 | 4.9706 | 4.9012 | 2.9098 | 2.9089 | 5.5069 | 5.505 | 5.5031 | 5.4913 | 5.4797 | 5.4681 | 5.4557 | 5.4188 | 5.3566 | 5.2916 | 5.2275
|  | CERNE ABBAS | CT |  |  | 2.6147 | 2.6147 | 5.2147 | 5.2147 | 5.2147 | 5.2147 | 5.2147 | 5.2147 | 5.2147 | 5.2147 | 5.2147 | 5.2147 | 5.2147 | 2.7068 | 2.7058 | 5.2037 | 5.2016 | 5.1996 | 5.1975 | 5.1849 | 5.1724 | 5.1589 | 5.119 | 5.0517 | 4.9813 | 4.9119 | 2.9098 | 2.9089 | 5.5069 | 5.505 | 5.5031 | 5.5012 | 5.4895 | 5.478 | 5.4655 | 5.4287 | 5.3665 | 5.3014 | 5.2373
|  | CERNE ABBAS | LW |  |  | 2.6147 | 2.6147 | 5.2147 | 5.2147 | 5.2147 | 5.2147 | 5.2147 | 5.2147 | 5.2147 | 5.2147 | 5.2147 | 5.2147 | 5.2147 | 2.7068 | 2.7058 | 5.2037 | 5.2016 | 5.1996 | 5.1868 | 5.1742 | 5.1617 | 5.1482 | 5.1083 | 5.041 | 4.9706 | 4.9012 | 2.9098 | 2.9089 | 5.5069 | 5.505 | 5.5031 | 5.4913 | 5.4797 | 5.4681 | 5.4557 | 5.4188 | 5.3566 | 5.2916 | 5.2275
|  | CERNE ABBAS | ST |  |  | 2.6147 | 2.6147 | 5.2147 | 5.2147 | 5.2147 | 5.2147 | 5.2147 | 5.2147 | 5.2147 | 5.2147 | 5.2147 | 5.2147 | 5.2147 | 2.7075 | 2.7069 | 5.2059 | 5.2048 | 5.2033 | 5.1966 | 5.19 | 5.1814 | 5.1722 | 5.1453 | 5.1004 | 5.055 | 5.01 | 2.9104 | 2.9099 | 5.509 | 5.5079 | 5.5066 | 5.5004 | 5.4942 | 5.4863 | 5.4779 | 5.4529 | 5.4115 | 5.3695 | 5.328
|  | CERNE ABBAS | FS |  |  | 2.6147 | 2.6147 | 5.2147 | 5.2147 | 5.2147 | 5.2147 | 5.2147 | 5.2147 | 5.2147 | 5.2147 | 5.2147 | 5.2147 | 5.2147 | 2.7083 | 2.7083 | 5.2082 | 5.2078 | 5.2074 | 5.2052 | 5.2031 | 5.2003 | 5.1968 | 5.1864 | 5.1692 | 5.1523 | 5.1363 | 2.9112 | 2.9111 | 5.511 | 5.5107 | 5.5104 | 5.5083 | 5.5064 | 5.5038 | 5.5005 | 5.4909 | 5.475 | 5.4595 | 5.4447
IVER 132KV | CHALVEY BSP | CHALVEY | MINIMUM HEADROOM | SU 96669 79364 | YES | 106.6353 | 106.6241 | 105.9412 | 105.8767 | 105.8121 | 105.747 | 105.6816 | 105.5801 | 105.5109 | 105.3228 | 105.0066 | 104.2641 | 101.8114 | 103.6785 | 103.6044 | 102.823 | 102.6546 | 102.4808 | 102.2961 | 102.103 | 101.8975 | 101.6227 | 100.7143 | 98.3421 | 95.5698 | 92.6897 | 104.3738 | 104.3236 | 103.5795 | 103.4505 | 103.3181 | 103.1787 | 103.0341 | 102.8048 | 102.2355 | 100.7743 | 98.1727 | 95.2619 | 92.3835
|  | CHALVEY | CT |  |  | 106.6935 | 106.6868 | 106.277 | 106.2434 | 106.2098 | 106.1763 | 106.1427 | 106.0903 | 106.032 | 105.8776 | 105.1936 | 104.4783 | 102.0519 | 103.739 | 103.6706 | 103.165 | 103.03 | 102.8899 | 102.7626 | 102.6014 | 102.4326 | 102.2072 | 101.3523 | 98.6773 | 95.8261 | 92.9573 | 104.4334 | 104.3884 | 103.9192 | 103.8226 | 103.7229 | 103.6311 | 103.5183 | 103.4008 | 102.8954 | 101.4678 | 98.5186 | 95.5203 | 92.6441
|  | CHALVEY | LW |  |  | 106.6353 | 106.6241 | 105.9412 | 105.8767 | 105.8121 | 105.747 | 105.6816 | 105.5801 | 105.5109 | 105.3228 | 105.0066 | 104.2641 | 101.8114 | 103.6785 | 103.6044 | 102.823 | 102.6546 | 102.4808 | 102.2961 | 102.103 | 101.8975 | 101.6227 | 100.7143 | 98.3421 | 95.5698 | 92.6897 | 104.3738 | 104.3236 | 103.5795 | 103.4505 | 103.3181 | 103.1787 | 103.0341 | 102.8048 | 102.2355 | 100.7743 | 98.1727 | 95.2619 | 92.3835
|  | CHALVEY | ST |  |  | 106.7226 | 106.7181 | 106.4449 | 106.3785 | 106.3113 | 106.2431 | 106.1735 | 106.078 | 106.0443 | 105.9147 | 105.6731 | 105.3222 | 105.0895 | 103.8053 | 103.7659 | 103.4487 | 103.3292 | 103.2007 | 103.0544 | 102.9014 | 102.7145 | 102.5886 | 102.2476 | 101.2941 | 99.7858 | 98.0226 | 104.4856 | 104.4595 | 104.159 | 104.0596 | 103.9543 | 103.8376 | 103.7163 | 103.564 | 103.473 | 103.2102 | 101.507 | 99.6616 | 97.8239
|  | CHALVEY | FS |  |  | 106.7517 | 106.7495 | 106.6129 | 106.6017 | 106.5905 | 106.5793 | 106.5681 | 106.5569 | 106.5524 | 106.539 | 106.5166 | 106.5032 | 106.4545 | 103.8578 | 103.8377 | 103.6838 | 103.6475 | 103.6091 | 103.5687 | 103.5269 | 103.4784 | 103.4378 | 103.3328 | 103.1527 | 102.9736 | 102.7865 | 104.5293 | 104.5159 | 104.3686 | 104.3418 | 104.3138 | 104.2844 | 104.2542 | 104.2198 | 104.193 | 104.1226 | 104.0023 | 103.8861 | 103.7482
NURSLING GSP | VELMORE BSP | CHANDLERS FORD | MINIMUM HEADROOM | SU 43494 21552 | YES | 43.2035 | 43.2035 | 43.2035 | 43.2001 | 43.1955 | 43.17 | 43.1551 | 43.1402 | 43.1246 | 43.0755 | 42.5247 | 41.0029 | 39.4836 | 40.6403 | 40.6327 | 40.6167 | 40.6008 | 40.5844 | 40.5682 | 40.5588 | 40.5494 | 40.3643 | 39.6629 | 38.1497 | 36.3629 | 34.5792 | 42.8826 | 42.8826 | 42.8826 | 42.8793 | 42.876 | 42.8727 | 42.7253 | 42.5281 | 42.3204 | 41.6702 | 40.2673 | 38.6109 | 36.9572
|  | CHANDLERS FORD | CT |  |  | 43.2035 | 43.2035 | 43.2035 | 43.2035 | 43.1955 | 43.17 | 43.1551 | 43.1402 | 43.1246 | 43.0755 | 42.5247 | 41.0029 | 39.4836 | 40.6403 | 40.6327 | 40.6167 | 40.6008 | 40.5844 | 40.5682 | 40.5588 | 40.5494 | 40.3643 | 39.6629 | 38.1497 | 36.3629 | 34.5792 | 42.8826 | 42.8826 | 42.8826 | 42.8826 | 42.8826 | 42.8826 | 42.7253 | 42.5281 | 42.3204 | 41.6702 | 40.2673 | 38.6109 | 36.9572
|  | CHANDLERS FORD | LW |  |  | 43.2035 | 43.2035 | 43.2035 | 43.2035 | 43.2035 | 43.2035 | 43.194 | 43.1791 | 43.1635 | 43.1144 | 42.9987 | 41.4768 | 39.9567 | 40.644 | 40.6386 | 40.6269 | 40.6153 | 40.6031 | 40.5929 | 40.5835 | 40.574 | 40.5641 | 40.2193 | 38.7062 | 36.9193 | 35.1347 | 42.8826 | 42.8826 | 42.8826 | 42.8826 | 42.8826 | 42.8826 | 42.8826 | 42.8826 | 42.8363 | 42.186 | 40.7832 | 39.1267 | 37.4722
|  | CHANDLERS FORD | ST |  |  | 43.2035 | 43.2035 | 43.2035 | 43.2035 | 43.2035 | 43.2035 | 43.2035 | 43.2035 | 43.2035 | 43.1729 | 43.1004 | 43.0185 | 42.147 | 40.6471 | 40.6437 | 40.6379 | 40.6306 | 40.6216 | 40.6128 | 40.6045 | 40.5981 | 40.5913 | 40.5701 | 40.0193 | 38.8475 | 37.7062 | 42.8826 | 42.8826 | 42.8826 | 42.8826 | 42.8826 | 42.8826 | 42.8826 | 42.8826 | 42.8826 | 42.8826 | 42.0006 | 40.9143 | 39.8562
|  | CHANDLERS FORD | FS |  |  | 43.2035 | 43.2035 | 43.2035 | 43.2001 | 43.1969 | 43.1936 | 43.1902 | 43.185 | 43.1705 | 43.1246 | 43.1027 | 43.0267 | 42.9323 | 40.6523 | 40.6517 | 40.6511 | 40.6456 | 40.6398 | 40.6334 | 40.6273 | 40.6185 | 40.6014 | 40.5472 | 40.5068 | 40.4153 | 40.3343 | 42.8826 | 42.8826 | 42.8826 | 42.8793 | 42.876 | 42.8727 | 42.8694 | 42.8642 | 42.8497 | 42.8037 | 42.7818 | 42.7129 | 42.5589
NURSLING GSP | SOUTHAMPTON (2 X 60) | CHAPEL | MINIMUM HEADROOM | SU 42849 11983 | YES | 23.911 | 23.911 | 23.911 | 23.8654 | 23.8191 | 23.7721 | 23.723 | 23.6472 | 23.6376 | 23.6068 | 23.4644 | 23.281 | 22.3911 | 21.5485 | 21.546 | 21.542 | 21.4937 | 21.4452 | 21.3958 | 21.3432 | 21.2638 | 21.2506 | 21.1446 | 20.3203 | 19.1527 | 18.1154 | 22.376 | 22.376 | 22.376 | 22.3305 | 22.2842 | 22.2371 | 22.188 | 22.1122 | 22.1026 | 22.0718 | 21.7154 | 20.4979 | 19.4134
|  | CHAPEL | CT |  |  | 23.911 | 23.911 | 23.911 | 23.8654 | 23.8191 | 23.7721 | 23.723 | 23.6472 | 23.6376 | 23.6068 | 23.4644 | 23.281 | 22.3911 | 21.5485 | 21.546 | 21.542 | 21.4937 | 21.4452 | 21.3958 | 21.3432 | 21.2638 | 21.2506 | 21.1446 | 20.3203 | 19.1527 | 18.1154 | 22.376 | 22.376 | 22.376 | 22.3305 | 22.2842 | 22.2371 | 22.188 | 22.1122 | 22.1026 | 22.0718 | 21.7154 | 20.4979 | 19.4134
|  | CHAPEL | LW |  |  | 23.911 | 23.911 | 23.911 | 23.911 | 23.911 | 23.911 | 23.911 | 23.911 | 23.911 | 23.911 | 23.911 | 23.911 | 23.0454 | 21.5485 | 21.546 | 21.542 | 21.5392 | 21.537 | 21.5338 | 21.5303 | 21.5266 | 21.523 | 21.4313 | 20.7467 | 19.7626 | 18.7666 | 22.376 | 22.376 | 22.376 | 22.376 | 22.376 | 22.376 | 22.376 | 22.376 | 22.376 | 22.376 | 22.1408 | 21.1069 | 20.0645
|  | CHAPEL | ST |  |  | 23.911 | 23.911 | 23.911 | 23.911 | 23.911 | 23.911 | 23.911 | 23.911 | 23.911 | 23.911 | 23.911 | 23.911 | 23.911 | 21.5494 | 21.5478 | 21.5454 | 21.5437 | 21.5422 | 21.5406 | 21.5388 | 21.5363 | 21.5339 | 21.5254 | 21.2323 | 20.6359 | 20.0093 | 22.376 | 22.376 | 22.376 | 22.376 | 22.376 | 22.376 | 22.376 | 22.376 | 22.376 | 22.376 | 22.376 | 22.0243 | 21.366
|  | CHAPEL | FS |  |  | 23.911 | 23.911 | 23.911 | 23.911 | 23.911 | 23.911 | 23.911 | 23.911 | 23.911 | 23.911 | 23.911 | 23.911 | 23.911 | 21.5505 | 21.5496 | 21.5485 | 21.5478 | 21.5473 | 21.5467 | 21.546 | 21.5452 | 21.5443 | 21.541 | 21.5304 | 21.5157 | 21.229 | 22.376 | 22.376 | 22.376 | 22.376 | 22.376 | 22.376 | 22.376 | 22.376 | 22.376 | 22.376 | 22.376 | 22.376 | 22.376
COWLEY GSP | YARNTON BSP | CHARLBURY | MINIMUM HEADROOM | SP 36034 18376 | NO | 18.9922 | 18.9556 | 18.8783 | 18.8033 | 18.7291 | 18.6555 | 18.5816 | 18.5083 | 18.4293 | 18.1962 | 17.8117 | 17.4149 | 17.0248 | 14.9676 | 14.9248 | 14.8344 | 14.7468 | 14.6599 | 14.5735 | 14.4865 | 14.4003 | 14.3073 | 14.033 | 13.5805 | 13.1137 | 12.6546 | 17.2486 | 17.2157 | 17.1437 | 17.0622 | 16.9814 | 16.9013 | 16.8208 | 16.7411 | 16.6551 | 16.4014 | 15.9802 | 15.5264 | 15.0803
|  | CHARLBURY | CT |  |  | 18.9922 | 18.9556 | 18.8783 | 18.8033 | 18.7291 | 18.6555 | 18.5816 | 18.5083 | 18.4293 | 18.1962 | 17.8117 | 17.4149 | 17.0248 | 14.9676 | 14.9248 | 14.8344 | 14.7468 | 14.6599 | 14.5735 | 14.4865 | 14.4003 | 14.3073 | 14.033 | 13.5805 | 13.1137 | 12.6546 | 17.2486 | 17.2157 | 17.1437 | 17.0622 | 16.9814 | 16.9013 | 16.8208 | 16.7411 | 16.6551 | 16.4014 | 15.9802 | 15.5264 | 15.0803
|  | CHARLBURY | LW |  |  | 19.0089 | 18.9816 | 18.9239 | 18.8679 | 18.8123 | 18.7376 | 18.6636 | 18.5903 | 18.5113 | 18.2781 | 17.8939 | 17.4969 | 17.1066 | 14.9872 | 14.9553 | 14.8877 | 14.8222 | 14.7573 | 14.67 | 14.583 | 14.4968 | 14.4038 | 14.1293 | 13.6773 | 13.2102 | 12.7509 | 17.2636 | 17.2391 | 17.1873 | 17.1324 | 17.072 | 16.9907 | 16.9101 | 16.8304 | 16.7444 | 16.4905 | 16.0723 | 15.6202 | 15.1739
|  | CHARLBURY | ST |  |  | 19.0519 | 19.0486 | 19.0431 | 19.0363 | 19.0281 | 18.9799 | 18.9321 | 18.882 | 18.8281 | 18.6708 | 18.4153 | 18.1597 | 17.9055 | 15.0374 | 15.0336 | 15.0272 | 15.0192 | 15.0096 | 14.9532 | 14.8974 | 14.8388 | 14.7758 | 14.5914 | 14.2907 | 13.99 | 13.6909 | 17.3021 | 17.2992 | 17.2943 | 17.2882 | 17.2808 | 17.2375 | 17.1947 | 17.1479 | 17.0892 | 16.9179 | 16.6398 | 16.3616 | 16.085
|  | CHARLBURY | FS |  |  | 19.0543 | 19.0531 | 19.0518 | 19.0459 | 19.0389 | 19.0219 | 19.005 | 18.9833 | 18.9609 | 18.8953 | 18.7962 | 18.6962 | 18.6027 | 15.0403 | 15.0388 | 15.0374 | 15.0305 | 15.0224 | 15.0025 | 14.9829 | 14.9575 | 14.9316 | 14.8557 | 14.7402 | 14.6244 | 14.5153 | 17.3043 | 17.3032 | 17.3021 | 17.2967 | 17.2904 | 17.2751 | 17.26 | 17.2404 | 17.2201 | 17.1609 | 17.0554 | 16.9471 | 16.8458
CHICKERELL GSP | CHICKERELL BSP | CHARMINSTER | MINIMUM HEADROOM | SY 67309 93186 | YES | 22.3398 | 22.3398 | 22.3398 | 22.3398 | 22.3398 | 22.3398 | 22.3398 | 22.3398 | 22.1244 | 20.8663 | 18.2325 | 17.7344 | 17.3125 | 19.7268 | 19.6905 | 19.6521 | 19.6243 | 19.5778 | 19.4599 | 19.3384 | 18.9988 | 18.6008 | 16.9792 | 13.8615 | 13.2719 | 12.7726 | 22.051 | 22.051 | 22.051 | 22.051 | 22.051 | 22.051 | 22.051 | 22.0436 | 21.6613 | 20.1037 | 17.1091 | 16.5427 | 16.0631
|  | CHARMINSTER | CT |  |  | 22.3398 | 22.3398 | 22.3398 | 22.3398 | 22.3398 | 22.3398 | 22.3398 | 22.3398 | 22.1766 | 20.9283 | 18.2941 | 17.7963 | 17.3745 | 19.7271 | 19.6909 | 19.6528 | 19.6254 | 19.5792 | 19.5328 | 19.4116 | 19.072 | 18.674 | 17.0526 | 13.9345 | 13.3452 | 12.8459 | 22.051 | 22.051 | 22.051 | 22.051 | 22.051 | 22.051 | 22.051 | 22.051 | 21.7316 | 20.1742 | 17.1791 | 16.6132 | 16.1336
|  | CHARMINSTER | LW |  |  | 22.3398 | 22.3398 | 22.3398 | 22.3398 | 22.3398 | 22.3398 | 22.3398 | 22.3398 | 22.1244 | 20.8663 | 18.2325 | 17.7344 | 17.3125 | 19.7268 | 19.6905 | 19.6521 | 19.6243 | 19.5778 | 19.4599 | 19.3384 | 18.9988 | 18.6008 | 16.9792 | 13.8615 | 13.2719 | 12.7726 | 22.051 | 22.051 | 22.051 | 22.051 | 22.051 | 22.051 | 22.051 | 22.0436 | 21.6613 | 20.1037 | 17.1091 | 16.5427 | 16.0631
|  | CHARMINSTER | ST |  |  | 22.3398 | 22.3398 | 22.3398 | 22.3398 | 22.3398 | 22.3398 | 22.3398 | 22.3398 | 22.3398 | 21.5969 | 19.7234 | 19.3997 | 19.125 | 19.7458 | 19.722 | 19.7017 | 19.6852 | 19.6531 | 19.5879 | 19.5205 | 19.2925 | 19.0194 | 17.8613 | 15.6263 | 15.2432 | 14.918 | 22.051 | 22.051 | 22.051 | 22.051 | 22.051 | 22.051 | 22.051 | 22.051 | 22.051 | 20.951 | 18.8042 | 18.4362 | 18.1239
|  | CHARMINSTER | FS |  |  | 22.3398 | 22.3398 | 22.3398 | 22.3398 | 22.3398 | 22.3398 | 22.3398 | 22.3398 | 22.3398 | 22.3398 | 21.7515 | 21.6473 | 21.5681 | 19.7664 | 19.7545 | 19.7487 | 19.7439 | 19.7323 | 19.709 | 19.6852 | 19.5982 | 19.4899 | 19.0296 | 18.078 | 17.932 | 17.821 | 22.051 | 22.051 | 22.051 | 22.051 | 22.051 | 22.051 | 22.051 | 22.051 | 22.051 | 22.051 | 21.1591 | 21.0189 | 20.9122
LOVEDEAN GSP | CHICHESTER & HUNSTON | CHICHESTER | MINIMUM HEADROOM | SU 92198 07420 | YES | 25.3919 | 25.2619 | 25.0466 | 24.8043 | 24.5253 | 24.1289 | 23.6839 | 23.2913 | 22.9292 | 21.9357 | 20.791 | 19.7762 | 18.8548 | 19.3114 | 19.1526 | 18.8895 | 18.6082 | 18.2818 | 17.8127 | 17.2861 | 16.8222 | 16.3935 | 15.2176 | 13.8641 | 12.6671 | 11.5759 | 21.9109 | 21.7691 | 21.5344 | 21.2832 | 20.9975 | 20.5916 | 20.077 | 19.6221 | 19.2017 | 18.0488 | 16.6971 | 15.4959 | 14.4007
|  | CHICHESTER | CT |  |  | 25.3998 | 25.2741 | 25.0679 | 24.8371 | 24.5685 | 24.2813 | 23.8388 | 23.4509 | 23.0895 | 22.1004 | 20.9537 | 19.9498 | 19.0254 | 19.3211 | 19.1675 | 18.9157 | 18.6458 | 18.3328 | 17.9926 | 17.4685 | 17.0094 | 16.5812 | 15.4098 | 14.0543 | 12.8683 | 11.7742 | 21.9195 | 21.7825 | 21.5577 | 21.3168 | 21.0418 | 20.7476 | 20.2559 | 19.8058 | 19.386 | 18.2376 | 16.8879 | 15.6977 | 14.5997
|  | CHICHESTER | LW |  |  | 25.3919 | 25.2619 | 25.0466 | 24.8043 | 24.5253 | 24.1289 | 23.6839 | 23.2913 | 22.9292 | 21.9357 | 20.791 | 19.7762 | 18.8548 | 19.3114 | 19.1526 | 18.8895 | 18.6082 | 18.2818 | 17.8127 | 17.2861 | 16.8222 | 16.3935 | 15.2176 | 13.8641 | 12.6671 | 11.5759 | 21.9109 | 21.7691 | 21.5344 | 21.2832 | 20.9975 | 20.5916 | 20.077 | 19.6221 | 19.2017 | 18.0488 | 16.6971 | 15.4959 | 14.4007
|  | CHICHESTER | ST |  |  | 25.6457 | 25.3303 | 25.1874 | 25.0221 | 24.8118 | 24.5541 | 24.2645 | 24.0028 | 23.7549 | 23.0657 | 22.2935 | 21.6371 | 21.0326 | 19.6214 | 19.2361 | 19.0616 | 18.8597 | 18.6168 | 18.3157 | 17.9728 | 17.663 | 17.3694 | 16.5537 | 15.6398 | 14.8657 | 14.1508 | 22.1875 | 21.8437 | 21.6879 | 21.5077 | 21.2909 | 21.0269 | 20.7304 | 20.4466 | 20.1588 | 19.359 | 18.4629 | 17.7023 | 16.9848
|  | CHICHESTER | FS |  |  | 25.7206 | 25.5256 | 25.4673 | 25.4007 | 25.327 | 25.2317 | 25.1276 | 25.0307 | 24.9303 | 24.6434 | 24.3352 | 24.0681 | 23.8346 | 19.7129 | 19.4746 | 19.4035 | 19.3224 | 19.2326 | 19.1165 | 18.9896 | 18.8716 | 18.7544 | 18.427 | 18.0634 | 17.7526 | 17.4808 | 22.2692 | 22.0566 | 21.9931 | 21.9206 | 21.8403 | 21.7366 | 21.6232 | 21.5177 | 21.4125 | 21.1192 | 20.8037 | 20.5309 | 20.2662
CHICKERELL GSP | CHICKERELL BSP | CHICKERELL | MINIMUM HEADROOM | SY 65479 80511 | YES | 38.489 | 27.2262 | 26.446 | 26.3351 | 26.2151 | 26.0258 | 25.8249 | 25.6283 | 25.4699 | 24.9668 | 24.0534 | 23.318 | 22.5766 | 36.8832 | 25.6098 | 24.815 | 24.6934 | 24.561 | 24.3451 | 24.1156 | 23.892 | 23.7059 | 23.1144 | 22.0394 | 21.1737 | 20.3053 | 38.3655 | 27.0972 | 26.3094 | 26.193 | 26.0666 | 25.8635 | 25.6477 | 25.4372 | 25.2643 | 24.7154 | 23.7183 | 22.9153 | 22.1081
|  | CHICKERELL | CT |  |  | 38.5495 | 27.2914 | 26.7952 | 26.7083 | 26.6131 | 26.5115 | 26.3373 | 26.1703 | 26.0222 | 25.5525 | 24.2438 | 23.4126 | 22.6665 | 36.9437 | 25.675 | 25.1642 | 25.0666 | 24.959 | 24.8437 | 24.6408 | 24.4469 | 24.271 | 23.713 | 22.2427 | 21.2812 | 20.4081 | 38.426 | 27.1624 | 26.6587 | 26.5662 | 26.4646 | 26.3559 | 26.1668 | 25.9858 | 25.8233 | 25.3078 | 23.9153 | 23.0166 | 22.2046
|  | CHICKERELL | LW |  |  | 38.489 | 27.2262 | 26.446 | 26.3351 | 26.2151 | 26.0258 | 25.8249 | 25.6283 | 25.4699 | 24.9668 | 24.0534 | 23.318 | 22.5766 | 36.8832 | 25.6098 | 24.815 | 24.6934 | 24.561 | 24.3451 | 24.1156 | 23.892 | 23.7059 | 23.1144 | 22.0394 | 21.1737 | 20.3053 | 38.3655 | 27.0972 | 26.3094 | 26.193 | 26.0666 | 25.8635 | 25.6477 | 25.4372 | 25.2643 | 24.7154 | 23.7183 | 22.9153 | 22.1081
|  | CHICKERELL | ST |  |  | 38.5956 | 38.5565 | 38.23 | 26.974 | 26.9101 | 26.8128 | 26.7083 | 26.5953 | 26.4936 | 26.1653 | 25.5718 | 25.1091 | 24.6562 | 36.9931 | 36.9468 | 36.6116 | 25.3488 | 25.2765 | 25.1639 | 25.0428 | 24.9116 | 24.7909 | 24.4013 | 23.6957 | 23.1478 | 22.6133 | 38.4738 | 38.431 | 38.1 | 26.8405 | 26.7722 | 26.667 | 26.5539 | 26.4314 | 26.3198 | 25.9598 | 25.3082 | 24.8013 | 24.306
|  | CHICKERELL | FS |  |  | 38.6419 | 38.6198 | 38.4571 | 38.4309 | 38.4026 | 38.3664 | 27.1281 | 27.0894 | 27.0485 | 26.917 | 26.6739 | 26.483 | 26.2836 | 37.0428 | 37.0165 | 36.8495 | 36.8204 | 36.7886 | 36.7473 | 25.5034 | 25.4591 | 25.4108 | 25.2553 | 24.9667 | 24.7406 | 24.5067 | 38.5219 | 38.4976 | 38.3326 | 38.305 | 38.2749 | 38.236 | 26.9948 | 26.9531 | 26.9084 | 26.7645 | 26.4978 | 26.2887 | 26.0714
AXMINSTER | YEOVIL BSP | CHILTON CANTELO | MINIMUM HEADROOM | ST 57910 21616 | YES | 10.7519 | 10.7214 | 10.6772 | 10.5915 | 10.4929 | 10.3874 | 10.2348 | 10.0568 | 9.9346 | 9.6735 | 9.2146 | 8.7674 | 8.439 | 7.4541 | 7.419 | 7.3695 | 7.2795 | 7.1775 | 7.0669 | 6.9097 | 6.7253 | 6.5972 | 6.324 | 5.8479 | 5.3848 | 5.0414 | 7.8103 | 7.7707 | 7.7148 | 7.6171 | 7.506 | 7.3793 | 7.2123 | 7.0111 | 6.8672 | 6.5615 | 6.0397 | 5.5341 | 5.151
|  | CHILTON CANTELO | CT |  |  | 10.7519 | 10.7214 | 10.6772 | 10.5915 | 10.4929 | 10.3874 | 10.2348 | 10.0568 | 9.9346 | 9.6735 | 9.2146 | 8.7674 | 8.439 | 7.4541 | 7.419 | 7.3695 | 7.2795 | 7.1775 | 7.0682 | 6.9097 | 6.7253 | 6.5972 | 6.324 | 5.8479 | 5.3848 | 5.0414 | 7.8103 | 7.7707 | 7.7148 | 7.6171 | 7.506 | 7.3869 | 7.2123 | 7.0111 | 6.8672 | 6.5615 | 6.0397 | 5.5341 | 5.151
|  | CHILTON CANTELO | LW |  |  | 10.7519 | 10.7214 | 10.6772 | 10.6081 | 10.5251 | 10.3884 | 10.25 | 10.0924 | 9.9723 | 9.7143 | 9.3398 | 8.9535 | 8.6579 | 7.4541 | 7.419 | 7.3695 | 7.2961 | 7.2097 | 7.0669 | 6.9225 | 6.7586 | 6.6325 | 6.3623 | 5.9707 | 5.5685 | 5.258 | 7.8103 | 7.7707 | 7.7148 | 7.6337 | 7.5383 | 7.3793 | 7.2188 | 7.0381 | 6.8963 | 6.5936 | 6.1563 | 5.7116 | 5.3613
|  | CHILTON CANTELO | ST |  |  | 10.8987 | 10.7418 | 10.7141 | 10.68 | 10.637 | 10.5699 | 10.5027 | 10.4176 | 10.3376 | 10.1681 | 9.9342 | 9.702 | 9.5017 | 7.633 | 7.4418 | 7.4109 | 7.3727 | 7.3257 | 7.2552 | 7.1846 | 7.0953 | 7.0112 | 6.8333 | 6.5878 | 6.3453 | 6.1353 | 8.0127 | 7.7965 | 7.7615 | 7.7184 | 7.6654 | 7.5857 | 7.5061 | 7.4054 | 7.3105 | 7.1103 | 6.8339 | 6.5639 | 6.328
|  | CHILTON CANTELO | FS |  |  | 10.9077 | 10.7586 | 10.7452 | 10.7285 | 10.7096 | 10.6845 | 10.6608 | 10.6331 | 10.6016 | 10.5355 | 10.4462 | 10.3619 | 10.2862 | 7.644 | 7.4623 | 7.4459 | 7.427 | 7.4058 | 7.3778 | 7.3512 | 7.3216 | 7.2885 | 7.2191 | 7.1253 | 7.0372 | 6.9581 | 8.0251 | 7.8196 | 7.8011 | 7.7797 | 7.7557 | 7.7241 | 7.6941 | 7.6606 | 7.6232 | 7.5451 | 7.4393 | 7.3409 | 7.2527
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | CHINEHAM | MINIMUM HEADROOM | SU 65105 55805 | YES | 43.1067 | 43.1067 | 43.1067 | 43.0229 | 42.9354 | 42.8431 | 42.7464 | 42.5974 | 42.5765 | 42.5025 | 42.3462 | 42.0863 | 42.0222 | 40.3266 | 40.2793 | 40.1858 | 40.0186 | 39.8465 | 39.7053 | 39.5608 | 39.3641 | 39.2957 | 39.0844 | 38.736 | 38.0495 | 37.3162 | 42.1336 | 42.1336 | 42.1336 | 42.0498 | 41.9623 | 41.8176 | 41.5739 | 41.278 | 41.1111 | 40.615 | 39.7876 | 38.8568 | 38.1468
|  | CHINEHAM | CT |  |  | 43.1067 | 43.1067 | 43.1067 | 43.1064 | 43.1059 | 43.1052 | 43.104 | 43.1015 | 43.1011 | 43.0987 | 43.0396 | 42.9652 | 42.908 | 40.3337 | 40.2903 | 40.2049 | 40.1293 | 40.0521 | 39.9636 | 39.9147 | 39.8645 | 39.8165 | 39.6769 | 39.4265 | 38.9174 | 38.1913 | 42.1336 | 42.1336 | 42.1336 | 42.1333 | 42.1328 | 42.0683 | 41.9202 | 41.7709 | 41.6243 | 41.1999 | 40.4704 | 39.7251 | 39.0222
|  | CHINEHAM | LW |  |  | 43.1067 | 43.1067 | 43.1067 | 43.0229 | 42.9354 | 42.8431 | 42.7464 | 42.5974 | 42.5765 | 42.5025 | 42.3462 | 42.0863 | 42.0222 | 40.3266 | 40.2793 | 40.1858 | 40.0186 | 39.8465 | 39.7053 | 39.5608 | 39.3641 | 39.2957 | 39.0844 | 38.736 | 38.0495 | 37.3162 | 42.1336 | 42.1336 | 42.1336 | 42.0498 | 41.9623 | 41.8176 | 41.5739 | 41.278 | 41.1111 | 40.615 | 39.7876 | 38.8568 | 38.1468
|  | CHINEHAM | ST |  |  | 43.1067 | 43.1067 | 43.1067 | 43.1065 | 43.1061 | 43.1056 | 43.1047 | 43.1028 | 43.1019 | 43.0969 | 43.0904 | 43.0677 | 43.0469 | 40.3533 | 40.3261 | 40.2816 | 40.2346 | 40.1779 | 40.1476 | 40.1224 | 40.0987 | 40.076 | 40.0087 | 39.858 | 39.6831 | 39.5282 | 42.1336 | 42.1336 | 42.1336 | 42.1334 | 42.133 | 42.1324 | 42.1316 | 42.1297 | 42.1287 | 42.1238 | 41.7739 | 41.2834 | 40.824
|  | CHINEHAM | FS |  |  | 43.1067 | 43.1067 | 43.1067 | 43.1067 | 43.1067 | 43.1067 | 43.1066 | 43.1066 | 43.1063 | 43.1045 | 43.103 | 43.0963 | 43.0896 | 40.4897 | 40.3766 | 40.3668 | 40.351 | 40.3325 | 40.3212 | 40.3122 | 40.3012 | 40.2925 | 40.2665 | 40.2249 | 40.1793 | 40.1366 | 42.1336 | 42.1336 | 42.1336 | 42.1336 | 42.1336 | 42.1336 | 42.1335 | 42.1334 | 42.1331 | 42.1313 | 42.1299 | 42.1231 | 42.1165
COWLEY GSP | YARNTON BSP | CHIPPING NORTON | MINIMUM HEADROOM | SP 31382 26792 | NO | 24.2361 | 24.2361 | 24.2361 | 24.1566 | 24.0746 | 23.9889 | 23.9001 | 23.7652 | 23.7465 | 23.6824 | 23.3173 | 22.6664 | 22.2326 | 22.4053 | 22.4026 | 22.3988 | 22.315 | 22.2281 | 22.1267 | 21.8599 | 21.5466 | 21.3606 | 20.9085 | 20.2413 | 19.491 | 18.9634 | 23.3727 | 23.3693 | 23.3644 | 23.2795 | 23.1913 | 23.0956 | 22.8632 | 22.5491 | 22.3624 | 21.9085 | 21.2388 | 20.4799 | 19.936
|  | CHIPPING NORTON | CT |  |  | 24.2361 | 24.2361 | 24.2361 | 24.2302 | 24.2242 | 24.2181 | 24.2117 | 24.2018 | 24.2006 | 24.1966 | 23.9745 | 23.5109 | 23.0859 | 22.4053 | 22.4026 | 22.3988 | 22.3887 | 22.3778 | 22.3672 | 22.2474 | 22.0591 | 21.8905 | 21.4985 | 20.9123 | 20.3495 | 19.8306 | 23.3727 | 23.3693 | 23.3645 | 23.3532 | 23.341 | 23.3292 | 23.2511 | 23.062 | 22.8926 | 22.4989 | 21.9101 | 21.3407 | 20.8056
|  | CHIPPING NORTON | LW |  |  | 24.2361 | 24.2361 | 24.2361 | 24.1566 | 24.0746 | 23.9889 | 23.9001 | 23.7652 | 23.7465 | 23.6824 | 23.3173 | 22.6664 | 22.2326 | 22.4053 | 22.4026 | 22.3988 | 22.315 | 22.2281 | 22.1267 | 21.8599 | 21.5466 | 21.3606 | 20.9085 | 20.2413 | 19.491 | 18.9634 | 23.3727 | 23.3693 | 23.3644 | 23.2795 | 23.1913 | 23.0956 | 22.8632 | 22.5491 | 22.3624 | 21.9085 | 21.2388 | 20.4799 | 19.936
|  | CHIPPING NORTON | ST |  |  | 24.2361 | 24.2361 | 24.2361 | 24.2361 | 24.2361 | 24.2361 | 24.2361 | 24.2361 | 24.2361 | 24.2361 | 24.2361 | 24.2361 | 23.9672 | 22.4059 | 22.4041 | 22.4018 | 22.3991 | 22.3958 | 22.3908 | 22.3856 | 22.3364 | 22.2219 | 21.9569 | 21.5753 | 21.2246 | 20.8904 | 23.3736 | 23.3712 | 23.3684 | 23.3648 | 23.3606 | 23.3542 | 23.3476 | 23.3404 | 23.2254 | 22.9591 | 22.5758 | 22.2235 | 21.8879
|  | CHIPPING NORTON | FS |  |  | 24.2361 | 24.2361 | 24.2361 | 24.2348 | 24.2334 | 24.2321 | 24.2307 | 24.2286 | 24.2227 | 24.204 | 24.1951 | 24.167 | 24.1435 | 22.4067 | 22.4057 | 22.4047 | 22.402 | 22.3993 | 22.396 | 22.3927 | 22.3884 | 22.3804 | 22.357 | 22.3414 | 22.1901 | 22.0521 | 23.3746 | 23.3733 | 23.372 | 23.369 | 23.3658 | 23.362 | 23.3582 | 23.3533 | 23.3447 | 23.32 | 23.3026 | 23.1937 | 23.0552
COWLEY GSP | HIGH WYCOMBE BSP | CHISBRIDGE | MINIMUM HEADROOM | SU 80226 89155 | YES | 11.7348 | 11.7277 | 11.7127 | 11.6408 | 11.5589 | 11.4769 | 11.3923 | 11.268 | 11.2432 | 11.1625 | 11.0338 | 10.8297 | 10.725 | 9.812 | 9.812 | 9.812 | 9.7435 | 9.6728 | 9.5989 | 9.5224 | 9.4061 | 9.39 | 9.3348 | 9.2485 | 9.0881 | 9.0774 | 10.9991 | 10.9974 | 10.9938 | 10.9245 | 10.8511 | 10.7753 | 10.6968 | 10.5787 | 10.5605 | 10.4992 | 10.4027 | 10.1177 | 9.9482
|  | CHISBRIDGE | CT |  |  | 11.7348 | 11.7277 | 11.7127 | 11.6982 | 11.6838 | 11.6695 | 11.6614 | 11.6534 | 11.6448 | 11.6192 | 11.5769 | 11.531 | 11.3955 | 9.812 | 9.812 | 9.812 | 9.812 | 9.812 | 9.812 | 9.812 | 9.812 | 9.812 | 9.812 | 9.812 | 9.812 | 9.812 | 10.9991 | 10.9974 | 10.9938 | 10.9904 | 10.9869 | 10.9835 | 10.9815 | 10.9796 | 10.9775 | 10.9714 | 10.9277 | 10.7663 | 10.6077
|  | CHISBRIDGE | LW |  |  | 11.7377 | 11.7322 | 11.7206 | 11.6408 | 11.5589 | 11.4769 | 11.3923 | 11.268 | 11.2432 | 11.1625 | 11.0338 | 10.8297 | 10.725 | 9.812 | 9.812 | 9.812 | 9.7435 | 9.6728 | 9.5989 | 9.5224 | 9.4061 | 9.39 | 9.3348 | 9.2485 | 9.0881 | 9.0774 | 10.9998 | 10.9985 | 10.9957 | 10.9245 | 10.8511 | 10.7753 | 10.6968 | 10.5787 | 10.5605 | 10.4992 | 10.4027 | 10.1177 | 9.9482
|  | CHISBRIDGE | ST |  |  | 11.7411 | 11.738 | 11.7326 | 11.7259 | 11.7179 | 11.7118 | 11.7058 | 11.7003 | 11.6944 | 11.6772 | 11.649 | 11.6209 | 11.5928 | 9.812 | 9.812 | 9.812 | 9.812 | 9.812 | 9.812 | 9.812 | 9.812 | 9.812 | 9.812 | 9.812 | 9.812 | 9.812 | 11.0006 | 10.9999 | 10.9986 | 10.997 | 10.9951 | 10.9936 | 10.9922 | 10.9908 | 10.9894 | 10.9853 | 10.9786 | 10.9718 | 10.9651
|  | CHISBRIDGE | FS |  |  | 11.7464 | 11.7461 | 11.7457 | 11.7441 | 11.7422 | 11.74 | 11.7379 | 11.7351 | 11.7328 | 11.7262 | 11.7155 | 11.7053 | 11.6956 | 9.812 | 9.812 | 9.812 | 9.812 | 9.812 | 9.812 | 9.812 | 9.812 | 9.812 | 9.812 | 9.812 | 9.812 | 9.812 | 11.0019 | 11.0018 | 11.0017 | 11.0014 | 11.0009 | 11.0004 | 10.9999 | 10.9992 | 10.9987 | 10.9971 | 10.9945 | 10.9921 | 10.9897
MINETY GSP | TOOTHILL BSP | CHISLEDON | MINIMUM HEADROOM | SU 18894 79934 | YES | 21.0643 | 21.0643 | 21.0643 | 21.0286 | 20.9923 | 20.6874 | 20.2811 | 19.8034 | 19.2825 | 17.3368 | 16.1157 | 15.7932 | 15.5414 | 19.7639 | 19.7504 | 19.7297 | 19.6943 | 19.6375 | 19.4098 | 18.9343 | 18.3696 | 17.756 | 15.4667 | 14.0298 | 13.6503 | 13.3541 | 20.7875 | 20.7875 | 20.7875 | 20.7518 | 20.4031 | 20.0104 | 19.5375 | 18.9815 | 18.3775 | 16.1238 | 14.7093 | 14.3357 | 14.0441
|  | CHISLEDON | CT |  |  | 21.0643 | 21.0643 | 21.0643 | 21.0643 | 21.0643 | 20.7165 | 20.3102 | 19.8326 | 19.3117 | 17.3662 | 16.145 | 15.8226 | 15.5708 | 19.7647 | 19.7516 | 19.7318 | 19.7083 | 19.6787 | 19.4438 | 18.9688 | 18.4041 | 17.7905 | 15.5012 | 14.0643 | 13.6849 | 13.3887 | 20.7875 | 20.7875 | 20.7875 | 20.7875 | 20.4501 | 20.0443 | 19.5714 | 19.0154 | 18.4114 | 16.1578 | 14.7432 | 14.3698 | 14.0781
|  | CHISLEDON | LW |  |  | 21.0643 | 21.0643 | 21.0643 | 21.0643 | 21.0248 | 20.6874 | 20.2811 | 19.8034 | 19.2825 | 17.3368 | 16.1157 | 15.7932 | 15.5414 | 19.7639 | 19.7504 | 19.7297 | 19.7054 | 19.6749 | 19.4098 | 18.9343 | 18.3696 | 17.756 | 15.4667 | 14.0298 | 13.6503 | 13.3541 | 20.7875 | 20.7875 | 20.7875 | 20.7804 | 20.4031 | 20.0104 | 19.5375 | 18.9815 | 18.3775 | 16.1238 | 14.7093 | 14.3357 | 14.0441
|  | CHISLEDON | ST |  |  | 21.0643 | 21.0643 | 21.0643 | 21.0286 | 20.9923 | 20.9553 | 20.7457 | 20.3673 | 19.9907 | 18.5305 | 17.5945 | 17.1994 | 16.9822 | 19.7773 | 19.758 | 19.7456 | 19.6943 | 19.6375 | 19.5791 | 19.5023 | 19.0709 | 18.6323 | 16.9226 | 15.8303 | 15.398 | 15.1519 | 20.7875 | 20.7875 | 20.7875 | 20.7518 | 20.7155 | 20.4583 | 20.1024 | 19.6716 | 19.2366 | 17.5525 | 16.4764 | 16.048 | 15.8049
|  | CHISLEDON | FS |  |  | 21.0643 | 21.0643 | 21.0643 | 21.0643 | 21.0643 | 21.0643 | 21.0643 | 21.0643 | 21.0643 | 20.7148 | 20.3548 | 20.272 | 20.2152 | 19.781 | 19.7657 | 19.7598 | 19.7524 | 19.7433 | 19.7341 | 19.7235 | 19.7113 | 19.698 | 19.4419 | 19.0215 | 18.9235 | 18.8564 | 20.7875 | 20.7875 | 20.7875 | 20.7875 | 20.7875 | 20.7875 | 20.7875 | 20.7875 | 20.6886 | 20.0423 | 19.6232 | 19.5268 | 19.4608
BRAMLEY (FLEE) | BRACKNELL RESERVE | CHOBHAM | MINIMUM HEADROOM | SU 97173 63223 | YES | 16.5084 | 16.4857 | 33.338 | 33.2895 | 33.2389 | 33.2027 | 33.1642 | 33.1167 | 33.0823 | 32.9727 | 32.7691 | 32.5165 | 32.3382 | 15.4754 | 15.4548 | 31.6301 | 31.498 | 31.3641 | 31.2588 | 31.1743 | 31.0838 | 30.9933 | 30.7158 | 30.2172 | 29.5973 | 28.9696 | 16.9253 | 16.9198 | 33.8081 | 33.7947 | 33.7791 | 33.7652 | 33.7488 | 33.7232 | 33.7123 | 33.6732 | 33.5933 | 32.9956 | 32.2676
|  | CHOBHAM | CT |  |  | 16.5095 | 16.4875 | 33.3412 | 33.2955 | 33.2493 | 33.2031 | 33.1713 | 33.1367 | 33.1045 | 33.0059 | 32.7977 | 32.5735 | 32.3852 | 15.4765 | 15.4564 | 31.6391 | 31.5123 | 31.3852 | 31.2588 | 31.1743 | 31.0875 | 30.9992 | 30.7327 | 30.2295 | 29.6307 | 28.9932 | 16.9256 | 16.9202 | 33.8089 | 33.7972 | 33.785 | 33.7724 | 33.7627 | 33.75 | 33.7414 | 33.7132 | 33.6289 | 33.0238 | 32.2859
|  | CHOBHAM | LW |  |  | 16.5084 | 16.4857 | 33.338 | 33.2895 | 33.2389 | 33.2027 | 33.1642 | 33.1167 | 33.0823 | 32.9727 | 32.7691 | 32.5165 | 32.3382 | 15.4754 | 15.4548 | 31.6301 | 31.498 | 31.3641 | 31.2748 | 31.1836 | 31.0838 | 30.9933 | 30.7158 | 30.2172 | 29.5973 | 28.9696 | 16.9253 | 16.9198 | 33.8081 | 33.7947 | 33.7791 | 33.7652 | 33.7488 | 33.7232 | 33.7123 | 33.6732 | 33.5933 | 32.9956 | 32.2676
|  | CHOBHAM | ST |  |  | 16.5335 | 16.5255 | 33.4119 | 33.3947 | 33.3736 | 33.3484 | 33.3228 | 33.2987 | 33.2754 | 33.2012 | 33.0767 | 32.9121 | 32.7814 | 15.4982 | 15.491 | 31.7286 | 31.713 | 31.6936 | 31.6639 | 31.5959 | 31.5361 | 31.4745 | 31.287 | 30.9646 | 30.596 | 30.2638 | 16.9315 | 16.9295 | 33.8262 | 33.8217 | 33.8158 | 33.8087 | 33.801 | 33.7918 | 33.7845 | 33.758 | 33.7164 | 33.6374 | 33.5914
|  | CHOBHAM | FS |  |  | 16.5779 | 16.5451 | 33.4439 | 33.4388 | 33.4325 | 33.4242 | 33.416 | 33.4053 | 33.3964 | 33.368 | 33.3226 | 33.2639 | 33.2067 | 15.5386 | 15.5088 | 31.7578 | 31.753 | 31.7474 | 31.7398 | 31.7323 | 31.7226 | 31.7144 | 31.6883 | 31.6021 | 31.4653 | 31.332 | 16.9424 | 16.9343 | 33.8341 | 33.8328 | 33.8312 | 33.8291 | 33.8271 | 33.8243 | 33.8216 | 33.8116 | 33.7981 | 33.7722 | 33.7469
COWLEY GSP | DRAYTON BSP | CHOLSEY | MINIMUM HEADROOM | SU 58223 84685 | NO | 21.8392 | 21.8359 | 21.8297 | 21.8203 | 21.7968 | 21.7699 | 21.7424 | 21.7017 | 21.6852 | 21.6335 | 21.4222 | 21.0661 | 20.7157 | 20.1799 | 20.1799 | 20.1799 | 20.1576 | 20.1349 | 20.1118 | 20.0878 | 20.0509 | 20.0383 | 19.9982 | 19.641 | 19.2516 | 18.8684 | 19.3014 | 19.2665 | 19.2009 | 19.1367 | 19.0718 | 19.0071 | 18.9486 | 18.8911 | 18.8295 | 18.6476 | 18.3442 | 18.0344 | 17.7296
|  | CHOLSEY | CT |  |  | 21.8392 | 21.8359 | 21.8297 | 21.8236 | 21.8175 | 21.8114 | 21.8059 | 21.8005 | 21.7946 | 21.7708 | 21.4222 | 21.0661 | 20.7157 | 20.1799 | 20.1799 | 20.1799 | 20.1799 | 20.1799 | 20.1799 | 20.1799 | 20.1799 | 20.1799 | 20.0224 | 19.641 | 19.2516 | 18.8684 | 19.3014 | 19.2665 | 19.2009 | 19.1367 | 19.0718 | 19.0071 | 18.9486 | 18.8911 | 18.8295 | 18.6476 | 18.3442 | 18.0344 | 17.7296
|  | CHOLSEY | LW |  |  | 21.8405 | 21.838 | 21.8333 | 21.8288 | 21.8242 | 21.8186 | 21.8131 | 21.8076 | 21.8018 | 21.7847 | 21.5098 | 21.1534 | 20.8029 | 20.1799 | 20.1799 | 20.1799 | 20.1799 | 20.1799 | 20.1799 | 20.1799 | 20.1799 | 20.1799 | 20.118 | 19.7369 | 19.3471 | 18.9638 | 19.3158 | 19.2887 | 19.2397 | 19.1916 | 19.1426 | 19.0833 | 19.0247 | 18.9673 | 18.9057 | 18.7237 | 18.4204 | 18.1104 | 17.8055
|  | CHOLSEY | ST |  |  | 21.857 | 21.8437 | 21.8432 | 21.8203 | 21.7968 | 21.7699 | 21.7424 | 21.7017 | 21.6852 | 21.6335 | 21.5822 | 21.4476 | 21.1862 | 20.1799 | 20.1799 | 20.1799 | 20.1576 | 20.1349 | 20.1118 | 20.0878 | 20.0509 | 20.0383 | 19.9982 | 19.9661 | 19.6988 | 19.4161 | 19.4903 | 19.3497 | 19.3446 | 19.3157 | 19.2843 | 19.2218 | 19.1592 | 19.0829 | 19.0283 | 18.8653 | 18.6307 | 18.3247 | 18.093
|  | CHOLSEY | FS |  |  | 21.8573 | 21.8569 | 21.8568 | 21.856 | 21.8551 | 21.8537 | 21.8523 | 21.8506 | 21.849 | 21.8446 | 21.8373 | 21.8304 | 21.8238 | 20.1799 | 20.1799 | 20.1799 | 20.1799 | 20.1799 | 20.1799 | 20.1799 | 20.1799 | 20.1799 | 20.1799 | 20.1799 | 20.1799 | 20.1799 | 19.4933 | 19.4898 | 19.488 | 19.4799 | 19.47 | 19.4552 | 19.4408 | 19.4225 | 19.4061 | 19.3585 | 19.2816 | 19.2083 | 19.1388
MANNINGTON GSP | CHRISTCHURCH BSP | CHRISTCHURCH | MINIMUM HEADROOM | SZ 15698 93141 | YES | 47.0484 | 47.0348 | 46.2077 | 46.1392 | 46.07 | 46 | 45.9291 | 45.7527 | 45.7123 | 45.5852 | 44.6201 | 44.0055 | 43.7541 | 43.3841 | 43.3677 | 42.5352 | 42.4619 | 42.3883 | 42.3066 | 42.2241 | 42.0432 | 41.9903 | 41.8259 | 40.7935 | 40.106 | 38.3606 | 45.1443 | 45.1307 | 44.3036 | 44.2351 | 44.1659 | 44.0959 | 44.025 | 43.8486 | 43.8082 | 43.6811 | 42.716 | 42.0642 | 40.7057
|  | CHRISTCHURCH | CT |  |  | 47.1189 | 47.1107 | 46.6145 | 46.4606 | 46.3047 | 46.1467 | 45.9832 | 45.7527 | 45.7123 | 45.5852 | 44.6201 | 44.0055 | 43.7541 | 43.4546 | 43.4436 | 42.9419 | 42.7833 | 42.623 | 42.4605 | 42.2853 | 42.0432 | 41.9903 | 41.8259 | 40.7935 | 40.106 | 38.3606 | 45.2148 | 45.2066 | 44.7104 | 44.5565 | 44.4006 | 44.2426 | 44.0791 | 43.8486 | 43.8082 | 43.6811 | 42.716 | 42.0642 | 40.7057
|  | CHRISTCHURCH | LW |  |  | 47.0484 | 47.0348 | 46.2077 | 46.1392 | 46.07 | 46 | 45.9291 | 45.8552 | 45.827 | 45.7402 | 45.5914 | 45.4843 | 45.3334 | 43.3841 | 43.3677 | 42.5352 | 42.4619 | 42.3883 | 42.3066 | 42.2241 | 42.1385 | 42.0979 | 41.9738 | 41.7577 | 41.4413 | 39.7899 | 45.1443 | 45.1307 | 44.3036 | 44.2351 | 44.1659 | 44.0959 | 44.025 | 43.9511 | 43.9229 | 43.8361 | 43.6873 | 43.5346 | 42.1404
|  | CHRISTCHURCH | ST |  |  | 47.1541 | 47.1487 | 46.8179 | 46.7836 | 46.7491 | 46.7143 | 46.679 | 46.6389 | 46.6234 | 46.5746 | 46.5054 | 46.4248 | 46.3484 | 43.491 | 43.4836 | 43.1498 | 43.1123 | 43.0742 | 43.0306 | 42.9865 | 42.9384 | 42.9144 | 42.8404 | 42.7259 | 42.598 | 42.4752 | 45.25 | 45.2446 | 44.9138 | 44.8795 | 44.845 | 44.8102 | 44.7749 | 44.7348 | 44.7193 | 44.6705 | 44.6013 | 44.5207 | 44.4382
|  | CHRISTCHURCH | FS |  |  | 47.1894 | 47.1867 | 47.0212 | 47.0077 | 46.9941 | 46.9805 | 46.967 | 46.9533 | 46.9477 | 46.9301 | 46.9019 | 46.8805 | 46.8457 | 43.5287 | 43.5254 | 43.3594 | 43.3449 | 43.3305 | 43.3142 | 43.2979 | 43.2808 | 43.2719 | 43.2446 | 43.1988 | 43.1589 | 43.106 | 45.2853 | 45.2826 | 45.1172 | 45.1036 | 45.09 | 45.0764 | 45.0629 | 45.0492 | 45.0436 | 45.026 | 44.9978 | 44.9764 | 44.9417
LALEHAM | EAST BEDFONT A | CHURCH ROAD | MINIMUM HEADROOM | TQ 06820 71722 | YES | 20.1444 | 20.1444 | 20.1444 | 20.1336 | 20.1225 | 20.1113 | 20.0996 | 20.0815 | 20.0792 | 20.0719 | 20.0379 | 19.4985 | 18.0924 | 18.2196 | 18.2166 | 18.2062 | 18.1838 | 18.1669 | 18.1497 | 18.1141 | 18.0715 | 18.0431 | 17.5636 | 16.1995 | 14.5681 | 12.9389 | 19.1363 | 19.1363 | 19.1363 | 19.1254 | 19.1144 | 19.1032 | 19.0915 | 19.0734 | 19.0711 | 19.0637 | 18.2608 | 16.7261 | 15.2022
|  | CHURCH ROAD | CT |  |  | 20.1444 | 20.1444 | 20.1444 | 20.1336 | 20.1225 | 20.1113 | 20.0996 | 20.0815 | 20.0792 | 20.0719 | 20.0379 | 19.4985 | 18.0924 | 18.2196 | 18.2166 | 18.2062 | 18.1838 | 18.1669 | 18.1497 | 18.1141 | 18.0715 | 18.0431 | 17.625 | 16.2265 | 14.5681 | 12.9389 | 19.1363 | 19.1363 | 19.1363 | 19.1254 | 19.1144 | 19.1032 | 19.0915 | 19.0734 | 19.0711 | 19.0637 | 18.2791 | 16.7261 | 15.2022
|  | CHURCH ROAD | LW |  |  | 20.1444 | 20.1444 | 20.1444 | 20.1444 | 20.1444 | 20.1444 | 20.1444 | 20.1444 | 20.1444 | 20.1444 | 20.1444 | 19.5268 | 18.1308 | 18.2196 | 18.2166 | 18.2062 | 18.1947 | 18.1888 | 18.1652 | 18.1414 | 18.1168 | 18.0907 | 17.5636 | 16.1995 | 14.578 | 12.959 | 19.1363 | 19.1363 | 19.1363 | 19.1363 | 19.1363 | 19.1363 | 19.1363 | 19.1363 | 19.1363 | 19.1363 | 18.2608 | 16.7447 | 15.2309
|  | CHURCH ROAD | ST |  |  | 20.1444 | 20.1444 | 20.1444 | 20.1444 | 20.1444 | 20.1444 | 20.1444 | 20.1444 | 20.1444 | 20.1444 | 20.1444 | 20.1444 | 19.9118 | 18.2212 | 18.2193 | 18.2133 | 18.2061 | 18.202 | 18.1834 | 18.1647 | 18.148 | 18.1301 | 18.0594 | 17.1224 | 16.058 | 15.0244 | 19.1363 | 19.1363 | 19.1363 | 19.1363 | 19.1363 | 19.1363 | 19.1363 | 19.1363 | 19.1363 | 19.1363 | 19.1237 | 18.1285 | 17.1621
|  | CHURCH ROAD | FS |  |  | 20.1444 | 20.1444 | 20.1444 | 20.1444 | 20.1444 | 20.1444 | 20.1444 | 20.1444 | 20.1444 | 20.1444 | 20.1444 | 20.1444 | 20.1444 | 18.2232 | 18.2225 | 18.2199 | 18.2166 | 18.2153 | 18.2094 | 18.2035 | 18.1958 | 18.1889 | 18.1674 | 18.1178 | 17.918 | 17.434 | 19.1363 | 19.1363 | 19.1363 | 19.1363 | 19.1363 | 19.1363 | 19.1363 | 19.1363 | 19.1363 | 19.1363 | 19.1363 | 19.1363 | 19.1363
MINETY GSP | CIRENCESTER BSP | CIRENCESTER TOWN | MINIMUM HEADROOM | SP 02761 00827 | YES | 26.3908 | 26.3549 | 26.3478 | 26.2952 | 26.2393 | 26.1822 | 26.1179 | 26.0228 | 26.0011 | 25.9323 | 25.6839 | 25.4162 | 25.3066 | 22.7544 | 22.7299 | 22.725 | 22.6737 | 22.6197 | 22.5644 | 22.5033 | 22.4112 | 22.3929 | 22.334 | 21.4876 | 20.5209 | 19.7233 | 23.6818 | 23.6489 | 23.6424 | 23.5901 | 23.5347 | 23.4781 | 23.4147 | 23.3203 | 23.2996 | 23.1426 | 22.2253 | 21.2631 | 20.47
|  | CIRENCESTER TOWN | CT |  |  | 26.3915 | 26.3561 | 26.3497 | 26.2952 | 26.2393 | 26.1822 | 26.1179 | 26.0228 | 26.0011 | 25.9323 | 25.6839 | 25.4162 | 25.3066 | 22.7549 | 22.7307 | 22.7264 | 22.6737 | 22.6197 | 22.5644 | 22.5033 | 22.4112 | 22.3929 | 22.334 | 21.4876 | 20.5209 | 19.7233 | 23.6824 | 23.6499 | 23.6442 | 23.5901 | 23.5347 | 23.4781 | 23.4147 | 23.3203 | 23.2996 | 23.1426 | 22.2253 | 21.2631 | 20.47
|  | CIRENCESTER TOWN | LW |  |  | 26.3908 | 26.3549 | 26.3478 | 26.3392 | 26.3285 | 26.3122 | 26.2935 | 26.2661 | 26.2525 | 26.2059 | 26.1159 | 25.988 | 25.9296 | 22.7544 | 22.7299 | 22.725 | 22.7185 | 22.71 | 22.6969 | 22.6813 | 22.657 | 22.6468 | 22.5835 | 21.8204 | 20.9932 | 20.2467 | 23.6818 | 23.6489 | 23.6424 | 23.6343 | 23.6242 | 23.6088 | 23.5909 | 23.5643 | 23.5516 | 23.3173 | 22.5587 | 21.7361 | 20.9941
|  | CIRENCESTER TOWN | ST |  |  | 26.392 | 26.3892 | 26.385 | 26.3798 | 26.3731 | 26.3663 | 26.359 | 26.3482 | 26.339 | 26.3074 | 26.2587 | 26.1749 | 26.1226 | 22.7552 | 22.7532 | 22.7504 | 22.7467 | 22.7419 | 22.7369 | 22.7313 | 22.7226 | 22.7158 | 22.6908 | 22.6532 | 22.4931 | 21.9941 | 23.6829 | 23.6803 | 23.6765 | 23.6716 | 23.6654 | 23.6591 | 23.6523 | 23.642 | 23.6335 | 23.6036 | 23.5578 | 23.2273 | 22.7313
|  | CIRENCESTER TOWN | FS |  |  | 26.396 | 26.3953 | 26.395 | 26.3938 | 26.3925 | 26.3906 | 26.3886 | 26.386 | 26.3825 | 26.3706 | 26.3543 | 26.3269 | 26.3004 | 22.7579 | 22.7575 | 22.7572 | 22.7564 | 22.7555 | 22.7542 | 22.7528 | 22.751 | 22.7484 | 22.7391 | 22.727 | 22.7037 | 22.6811 | 23.6865 | 23.6859 | 23.6856 | 23.6846 | 23.6833 | 23.6815 | 23.6797 | 23.6774 | 23.6741 | 23.6629 | 23.6477 | 23.6213 | 23.5959
IVER 132KV | CIPPENHAM | CLARENCE ROAD | MINIMUM HEADROOM | SU 95654 76652 | YES | 55.6676 | 55.6567 | 54.9928 | 54.8694 | 54.7429 | 54.6122 | 54.4778 | 54.2998 | 54.2607 | 54.1335 | 53.9255 | 53.6675 | 53.5335 | 52.7745 | 52.7288 | 51.9914 | 51.7967 | 51.5977 | 51.2103 | 50.6991 | 50.1335 | 49.6771 | 48.3777 | 46.3904 | 44.2987 | 42.3622 | 53.1782 | 53.1673 | 52.4694 | 52.2954 | 52.1174 | 51.9659 | 51.6282 | 51.0766 | 50.6353 | 49.3784 | 47.4556 | 45.4303 | 43.559
|  | CLARENCE ROAD | CT |  |  | 55.7242 | 55.7176 | 55.3193 | 55.2864 | 55.2532 | 55.2198 | 55.1861 | 55.151 | 55.1375 | 55.0961 | 54.6008 | 54.4115 | 53.9604 | 52.8322 | 52.7914 | 52.3209 | 52.2179 | 52.1134 | 51.3531 | 50.9425 | 50.5198 | 50.0889 | 48.8755 | 46.6003 | 44.5776 | 42.6495 | 53.2348 | 53.2282 | 52.798 | 52.7153 | 52.6316 | 52.2854 | 51.8884 | 51.4798 | 51.064 | 49.893 | 47.6823 | 45.726 | 43.8632
|  | CLARENCE ROAD | LW |  |  | 55.6676 | 55.6567 | 54.9928 | 54.8694 | 54.7429 | 54.6122 | 54.4778 | 54.2998 | 54.2607 | 54.1335 | 53.9255 | 53.6675 | 53.5335 | 52.7745 | 52.7288 | 51.9914 | 51.7967 | 51.5977 | 51.2103 | 50.6991 | 50.1335 | 49.6771 | 48.3777 | 46.3904 | 44.2987 | 42.3622 | 53.1782 | 53.1673 | 52.4694 | 52.2954 | 52.1174 | 51.9659 | 51.6282 | 51.0766 | 50.6353 | 49.3784 | 47.4556 | 45.4303 | 43.559
|  | CLARENCE ROAD | ST |  |  | 55.7525 | 55.7481 | 55.4826 | 55.4606 | 55.4385 | 55.4161 | 55.3935 | 55.3699 | 55.3603 | 55.3294 | 55.2796 | 55.2313 | 55.1754 | 52.8923 | 52.8732 | 52.5826 | 52.53 | 52.4697 | 52.4214 | 52.3725 | 52.3279 | 52.2956 | 52.2012 | 51.2677 | 50.0348 | 48.8109 | 53.2631 | 53.2587 | 52.9932 | 52.9712 | 52.9382 | 52.8974 | 52.8562 | 52.8176 | 52.7919 | 52.716 | 52.2052 | 51.0152 | 49.8337
|  | CLARENCE ROAD | FS |  |  | 55.7808 | 55.7786 | 55.6458 | 55.6301 | 55.6146 | 55.599 | 55.5833 | 55.5649 | 55.5395 | 55.4591 | 55.4046 | 55.2865 | 55.1738 | 52.9419 | 52.9369 | 52.8014 | 52.7741 | 52.7443 | 52.7193 | 52.694 | 52.6635 | 52.6293 | 52.5242 | 52.4333 | 52.2798 | 52.1331 | 53.2914 | 53.2892 | 53.1564 | 53.1407 | 53.1252 | 53.1096 | 53.0939 | 53.0755 | 53.0501 | 52.9697 | 52.9026 | 52.7593 | 52.6224
MELKSHAM GSP | CHIPPENHAM | COCKLEBURY | MINIMUM HEADROOM | ST 92447 73890 | YES | 41.7543 | 41.7265 | 41.0325 | 40.952 | 40.8714 | 40.7962 | 40.7184 | 40.6322 | 40.5918 | 40.4662 | 40.2459 | 39.9394 | 38.9549 | 40.1689 | 40.128 | 39.4108 | 39.3114 | 39.2135 | 39.1203 | 39.0138 | 38.7884 | 38.6009 | 38.0506 | 37.123 | 36.1514 | 35.0138 | 40.9365 | 40.8121 | 39.9461 | 39.7265 | 39.4739 | 39.217 | 38.9488 | 38.6675 | 38.425 | 37.7156 | 36.523 | 35.3492 | 34.2146
|  | COCKLEBURY | CT |  |  | 41.8118 | 41.789 | 41.3617 | 41.3053 | 41.2504 | 41.1946 | 41.1445 | 41.0915 | 41.0617 | 40.972 | 40.3804 | 39.9771 | 38.9838 | 40.2272 | 40.1917 | 39.7421 | 39.6677 | 39.5964 | 39.5153 | 39.4259 | 39.2311 | 39.0543 | 38.5399 | 37.2409 | 36.1854 | 35.039 | 40.9997 | 40.8834 | 40.2909 | 40.1019 | 39.9138 | 39.5933 | 39.352 | 39.1041 | 38.8722 | 38.1987 | 36.6347 | 35.3832 | 34.2399
|  | COCKLEBURY | LW |  |  | 41.7543 | 41.7265 | 41.0325 | 40.952 | 40.8714 | 40.7962 | 40.7184 | 40.6322 | 40.5918 | 40.4662 | 40.2459 | 39.9394 | 38.9549 | 40.1689 | 40.128 | 39.4108 | 39.3114 | 39.2135 | 39.1203 | 39.0138 | 38.7884 | 38.6009 | 38.0506 | 37.123 | 36.1514 | 35.0138 | 40.9365 | 40.8121 | 39.9461 | 39.7265 | 39.4739 | 39.217 | 38.9488 | 38.6675 | 38.425 | 37.7156 | 36.523 | 35.3492 | 34.2146
|  | COCKLEBURY | ST |  |  | 41.9573 | 41.942 | 41.6603 | 41.6228 | 41.5832 | 41.5491 | 41.5142 | 41.4782 | 41.4569 | 41.3899 | 41.2823 | 41.162 | 41.0499 | 40.3776 | 40.3539 | 40.0596 | 40.0102 | 39.9575 | 39.9147 | 39.8711 | 39.827 | 39.7972 | 39.6584 | 39.0773 | 38.5047 | 37.9501 | 41.1814 | 41.1039 | 40.7295 | 40.6042 | 40.4672 | 40.3693 | 40.2693 | 40.1737 | 40.0316 | 39.5797 | 38.8211 | 38.0791 | 37.3588
|  | COCKLEBURY | FS |  |  | 41.9978 | 41.992 | 41.8555 | 41.8403 | 41.8251 | 41.8103 | 41.7955 | 41.7795 | 41.7704 | 41.7418 | 41.6976 | 41.653 | 41.5991 | 40.4275 | 40.4189 | 40.2795 | 40.261 | 40.2425 | 40.2248 | 40.2069 | 40.1872 | 40.1747 | 40.1369 | 40.0776 | 40.0191 | 39.9522 | 41.2916 | 41.2651 | 41.1074 | 41.0677 | 41.0278 | 40.9912 | 40.9541 | 40.9101 | 40.877 | 40.78 | 40.6239 | 40.4766 | 40.327
MELKSHAM GSP | FROME BSP | CODFORD | MINIMUM HEADROOM | ST 97372 39559 | YES | 4.8835 | 4.8742 | 4.8583 | 4.679 | 4.4578 | 4.2147 | 3.9634 | 3.5902 | 3.5238 | 3.3042 | 2.9683 | 2.4077 | 2.2969 | 4.3598 | 4.3447 | 4.3188 | 4.1593 | 3.9357 | 3.6826 | 3.4214 | 3.0383 | 2.9613 | 2.7103 | 2.3228 | 1.7089 | 1.5456 | 4.3652 | 4.3559 | 4.3399 | 4.1607 | 3.9395 | 3.6963 | 3.4451 | 3.0718 | 3.0054 | 2.7857 | 2.4496 | 1.8888 | 1.7778
|  | CODFORD | CT |  |  | 4.8993 | 4.8975 | 4.8936 | 4.8898 | 4.886 | 4.8822 | 4.8665 | 4.8508 | 4.8339 | 4.7842 | 4.7022 | 4.6175 | 4.5342 | 4.3856 | 4.3826 | 4.3763 | 4.3701 | 4.3639 | 4.3578 | 4.3321 | 4.3066 | 4.2791 | 4.198 | 4.0643 | 3.9265 | 3.7907 | 4.3811 | 4.3792 | 4.3753 | 4.3715 | 4.3677 | 4.3639 | 4.3481 | 4.3325 | 4.3155 | 4.2657 | 4.1835 | 4.0987 | 4.0152
|  | CODFORD | LW |  |  | 4.8993 | 4.8975 | 4.8936 | 4.679 | 4.4578 | 4.2147 | 3.9634 | 3.5902 | 3.5238 | 3.3042 | 2.9683 | 2.4077 | 2.2969 | 4.3856 | 4.3826 | 4.3763 | 4.1593 | 3.9357 | 3.6826 | 3.4214 | 3.0383 | 2.9613 | 2.7103 | 2.3228 | 1.7089 | 1.5456 | 4.3811 | 4.3792 | 4.3753 | 4.1607 | 3.9395 | 3.6963 | 3.4451 | 3.0718 | 3.0054 | 2.7857 | 2.4496 | 1.8888 | 1.7778
|  | CODFORD | ST |  |  | 4.8835 | 4.8742 | 4.8583 | 4.8387 | 4.8152 | 4.8075 | 4.8 | 4.7893 | 4.7778 | 4.7442 | 4.6897 | 4.6352 | 4.581 | 4.3598 | 4.3447 | 4.3188 | 4.2869 | 4.2486 | 4.2361 | 4.2238 | 4.2063 | 4.1876 | 4.1329 | 4.0441 | 3.9552 | 3.8669 | 4.3652 | 4.3559 | 4.3399 | 4.3203 | 4.2968 | 4.2891 | 4.2815 | 4.2708 | 4.2593 | 4.2256 | 4.171 | 4.1163 | 4.062
|  | CODFORD | FS |  |  | 4.9022 | 4.9021 | 4.9019 | 4.9013 | 4.9006 | 4.898 | 4.8954 | 4.8921 | 4.8876 | 4.8747 | 4.854 | 4.8343 | 4.8156 | 4.3903 | 4.3901 | 4.3899 | 4.3889 | 4.3878 | 4.3835 | 4.3793 | 4.3739 | 4.3666 | 4.3455 | 4.3119 | 4.2797 | 4.2493 | 4.3839 | 4.3838 | 4.3837 | 4.3831 | 4.3824 | 4.3798 | 4.3772 | 4.3738 | 4.3694 | 4.3564 | 4.3357 | 4.3159 | 4.2972
IVER 132KV | DENHAM | COKES LANE | MINIMUM HEADROOM | SU 99240 97483 | YES | 18.0156 | 18.0156 | 18.0156 | 18.0156 | 18.0156 | 18.0156 | 18.0156 | 18.0156 | 18.0156 | 18.0156 | 18.0156 | 17.8046 | 17.4151 | 16.4152 | 16.4152 | 16.4152 | 16.4152 | 16.4152 | 16.4152 | 16.4152 | 16.4152 | 16.4152 | 16.3858 | 15.8858 | 15.4446 | 15.0012 | 17.2945 | 17.2207 | 17.0671 | 16.9174 | 16.7684 | 16.6756 | 16.6107 | 16.5418 | 16.4686 | 16.2084 | 15.6997 | 15.2508 | 14.7996
|  | COKES LANE | CT |  |  | 18.0156 | 18.0156 | 18.0156 | 18.0156 | 18.0156 | 18.0156 | 18.0156 | 18.0156 | 18.0156 | 18.0156 | 18.0156 | 17.8046 | 17.4151 | 16.4152 | 16.4152 | 16.4152 | 16.4152 | 16.4152 | 16.4152 | 16.4152 | 16.4152 | 16.4152 | 16.3858 | 15.8858 | 15.4446 | 15.0012 | 17.3064 | 17.2392 | 17.0995 | 16.9633 | 16.8276 | 16.6756 | 16.6107 | 16.5418 | 16.4686 | 16.2084 | 15.6997 | 15.2508 | 14.7996
|  | COKES LANE | LW |  |  | 18.0156 | 18.0156 | 18.0156 | 18.0156 | 18.0156 | 18.0156 | 18.0156 | 18.0156 | 18.0156 | 18.0156 | 18.0156 | 17.8321 | 17.4424 | 16.4152 | 16.4152 | 16.4152 | 16.4152 | 16.4152 | 16.4152 | 16.4152 | 16.4152 | 16.4152 | 16.4152 | 15.9172 | 15.4759 | 15.0322 | 17.2945 | 17.2207 | 17.0671 | 16.9174 | 16.7684 | 16.7074 | 16.6426 | 16.5738 | 16.5007 | 16.2404 | 15.7317 | 15.2827 | 14.8312
|  | COKES LANE | ST |  |  | 18.0156 | 18.0156 | 18.0156 | 18.0156 | 18.0156 | 18.0156 | 18.0156 | 18.0156 | 18.0156 | 18.0156 | 18.0156 | 18.0156 | 18.0156 | 16.4152 | 16.4152 | 16.4152 | 16.4152 | 16.4152 | 16.4152 | 16.4152 | 16.4152 | 16.4152 | 16.4152 | 16.4093 | 16.1184 | 15.8359 | 17.3277 | 17.2789 | 17.1965 | 17.0953 | 16.9734 | 16.9228 | 16.8698 | 16.8232 | 16.7732 | 16.5908 | 16.2323 | 15.9363 | 15.6489
|  | COKES LANE | FS |  |  | 18.0156 | 18.0156 | 18.0156 | 18.0156 | 18.0156 | 18.0156 | 18.0156 | 18.0156 | 18.0156 | 18.0156 | 18.0156 | 18.0156 | 18.0156 | 16.4152 | 16.4152 | 16.4152 | 16.4152 | 16.4152 | 16.4152 | 16.4152 | 16.4152 | 16.4152 | 16.4152 | 16.4152 | 16.4152 | 16.4152 | 17.4063 | 17.4008 | 17.3943 | 17.3687 | 17.3385 | 17.3192 | 17.2992 | 17.275 | 17.2553 | 17.1835 | 17.0359 | 16.902 | 16.7609
LOVEDEAN GSP | WYMERING BSP | COLLEGE PARK | MINIMUM HEADROOM | SU 65893 02686 | YES | 22.1689 | 22.1689 | 22.1689 | 22.1689 | 22.1689 | 22.1689 | 22.1689 | 22.1689 | 22.1689 | 22.1689 | 22.1689 | 21.5104 | 20.294 | 20.494 | 20.4931 | 20.4915 | 20.4898 | 20.4881 | 20.4801 | 20.472 | 20.4639 | 20.4553 | 20.4284 | 19.6726 | 18.2824 | 16.8782 | 20.9665 | 20.9665 | 20.9665 | 20.9665 | 20.9665 | 20.9665 | 20.9665 | 20.9665 | 20.9665 | 20.9665 | 20.6473 | 19.251 | 17.8181
|  | COLLEGE PARK | CT |  |  | 22.1689 | 22.1689 | 22.1689 | 22.1689 | 22.1689 | 22.1689 | 22.1689 | 22.1689 | 22.1689 | 22.1689 | 22.1689 | 21.6224 | 20.4062 | 20.494 | 20.4931 | 20.4915 | 20.4898 | 20.4881 | 20.4864 | 20.4783 | 20.4702 | 20.4616 | 20.4347 | 19.8007 | 18.4106 | 17.0105 | 20.9665 | 20.9665 | 20.9665 | 20.9665 | 20.9665 | 20.9665 | 20.9665 | 20.9665 | 20.9665 | 20.9665 | 20.7761 | 19.3797 | 17.9505
|  | COLLEGE PARK | LW |  |  | 22.1689 | 22.1689 | 22.1689 | 22.1689 | 22.1689 | 22.1689 | 22.1689 | 22.1689 | 22.1689 | 22.1689 | 22.1689 | 21.5104 | 20.294 | 20.494 | 20.4931 | 20.4915 | 20.4898 | 20.4881 | 20.4801 | 20.472 | 20.4639 | 20.4553 | 20.4284 | 19.6726 | 18.2824 | 16.8782 | 20.9665 | 20.9665 | 20.9665 | 20.9665 | 20.9665 | 20.9665 | 20.9665 | 20.9665 | 20.9665 | 20.9665 | 20.6473 | 19.251 | 17.8181
|  | COLLEGE PARK | ST |  |  | 22.1689 | 22.1689 | 22.1689 | 22.1689 | 22.1689 | 22.1689 | 22.1689 | 22.1689 | 22.1689 | 22.1689 | 22.1689 | 22.1689 | 21.8736 | 20.5049 | 20.4939 | 20.4931 | 20.4921 | 20.4909 | 20.4857 | 20.4805 | 20.4749 | 20.4691 | 20.4507 | 20.411 | 19.5874 | 18.698 | 20.9665 | 20.9665 | 20.9665 | 20.9665 | 20.9665 | 20.9665 | 20.9665 | 20.9665 | 20.9665 | 20.9665 | 20.9665 | 20.5618 | 19.6684
|  | COLLEGE PARK | FS |  |  | 22.1689 | 22.1689 | 22.1689 | 22.1689 | 22.1689 | 22.1689 | 22.1689 | 22.1689 | 22.1689 | 22.1689 | 22.1689 | 22.1689 | 22.1689 | 20.5055 | 20.4948 | 20.4946 | 20.4943 | 20.4939 | 20.4925 | 20.4911 | 20.4893 | 20.487 | 20.4799 | 20.464 | 20.4446 | 20.4246 | 20.9665 | 20.9665 | 20.9665 | 20.9665 | 20.9665 | 20.9665 | 20.9665 | 20.9665 | 20.9665 | 20.9665 | 20.9665 | 20.9665 | 20.9665
EALING GSP | EALING 22kV | COPLEY DENE | MINIMUM HEADROOM | TQ 17445 80798 |  | 46.9934 | 46.9545 | 46.8735 | 46.7947 | 46.716 | 46.6381 | 46.6212 | 46.6043 | 46.5865 | 46.5305 | 46.4112 | 45.2273 | 43.5415 | 44.3292 | 44.2979 | 44.2327 | 44.1692 | 44.1058 | 44.043 | 44.0294 | 43.9023 | 43.6476 | 42.8506 | 41.1502 | 39.1713 | 37.1902 | 44.8271 | 44.7828 | 44.6903 | 44.6004 | 44.0962 | 43.1287 | 42.9061 | 42.6851 | 42.4501 | 41.7146 | 40.1454 | 38.3192 | 36.491
|  | COPLEY DENE | CT |  |  | 46.9934 | 46.9545 | 46.8735 | 46.7947 | 46.716 | 46.6381 | 46.6212 | 46.6043 | 46.5865 | 46.5305 | 46.4112 | 45.2273 | 43.5415 | 44.3292 | 44.2979 | 44.2327 | 44.1692 | 44.1058 | 44.043 | 44.0294 | 43.9023 | 43.6476 | 42.8506 | 41.1502 | 39.1713 | 37.1902 | 44.8271 | 44.7828 | 44.6903 | 44.6004 | 44.0962 | 43.1287 | 42.9061 | 42.6851 | 42.4501 | 41.7146 | 40.1454 | 38.3192 | 36.491
|  | COPLEY DENE | LW |  |  | 47.0024 | 46.9685 | 46.8981 | 46.8294 | 46.7608 | 46.7438 | 46.7269 | 46.7101 | 46.6922 | 46.6363 | 46.5169 | 46.378 | 44.8235 | 44.3365 | 44.3092 | 44.2524 | 44.1971 | 44.1419 | 44.1282 | 44.1146 | 44.101 | 44.0866 | 44.0416 | 42.6568 | 40.6778 | 38.6967 | 44.8374 | 44.7988 | 44.7184 | 44.64 | 44.5617 | 44.3913 | 44.212 | 44.0339 | 43.8404 | 43.105 | 41.5357 | 39.7094 | 37.8812
|  | COPLEY DENE | ST |  |  | 47.0437 | 47.0336 | 47.0169 | 46.9962 | 46.971 | 46.9483 | 46.9258 | 46.9143 | 46.9021 | 46.8641 | 46.7823 | 46.6914 | 46.6025 | 44.3698 | 44.3616 | 44.3481 | 44.3315 | 44.3112 | 44.2929 | 44.2747 | 44.2655 | 44.2557 | 44.2251 | 44.1592 | 44.0859 | 43.8759 | 44.8846 | 44.873 | 44.8539 | 44.8303 | 44.8016 | 44.7757 | 44.75 | 44.7369 | 44.723 | 44.6796 | 44.5863 | 43.8292 | 42.6607
|  | COPLEY DENE | FS |  |  | 47.0635 | 47.0546 | 47.0523 | 47.0393 | 47.0244 | 47.0127 | 47.001 | 46.9854 | 46.9677 | 46.912 | 46.8597 | 46.759 | 46.6671 | 44.3857 | 44.3785 | 44.3767 | 44.3656 | 44.353 | 44.343 | 44.3331 | 44.3196 | 44.3028 | 44.2499 | 44.2041 | 44.111 | 44.0269 | 44.9072 | 44.897 | 44.8943 | 44.8799 | 44.8633 | 44.8504 | 44.8375 | 44.8203 | 44.802 | 44.7441 | 44.6873 | 44.5811 | 44.4835
BRAMLEY (FLEE) | MAIDENHEAD BSP | CORDWALLIS | MINIMUM HEADROOM | SU 88285 81857 | YES | 47.2465 | 47.2465 | 47.2465 | 47.0356 | 46.818 | 46.5907 | 46.355 | 45.9972 | 45.9476 | 45.7777 | 45.5211 | 44.9641 | 43.838 | 44.3753 | 44.3656 | 44.3466 | 44.1188 | 43.8833 | 43.6478 | 43.4038 | 43.037 | 42.7858 | 42.0045 | 40.6149 | 38.885 | 37.5614 | 46.0635 | 46.0635 | 46.0635 | 45.8526 | 45.616 | 45.3783 | 45.132 | 44.7628 | 44.701 | 44.1195 | 42.8265 | 41.1664 | 39.8749
|  | CORDWALLIS | CT |  |  | 47.2465 | 47.2465 | 47.2465 | 47.2465 | 47.2465 | 47.2465 | 47.2465 | 47.2465 | 47.2465 | 47.2465 | 47.2465 | 46.93 | 45.8315 | 44.3753 | 44.3656 | 44.3466 | 44.3284 | 44.3101 | 44.2926 | 44.2477 | 44.0525 | 43.8423 | 43.231 | 42.0978 | 40.8129 | 39.5168 | 46.0635 | 46.0635 | 46.0635 | 46.0635 | 46.0424 | 46.0201 | 46.0093 | 45.998 | 45.9116 | 45.376 | 44.3221 | 43.1033 | 41.8336
|  | CORDWALLIS | LW |  |  | 47.2465 | 47.2465 | 47.2465 | 47.0356 | 46.818 | 46.5907 | 46.355 | 45.9972 | 45.9476 | 45.7777 | 45.5211 | 44.9641 | 43.838 | 44.3756 | 44.3662 | 44.3476 | 44.1188 | 43.8833 | 43.6478 | 43.4038 | 43.037 | 42.7858 | 42.0045 | 40.6149 | 38.885 | 37.5614 | 46.0635 | 46.0635 | 46.0635 | 45.8526 | 45.616 | 45.3783 | 45.132 | 44.7628 | 44.701 | 44.1195 | 42.8265 | 41.1664 | 39.8749
|  | CORDWALLIS | ST |  |  | 47.2465 | 47.2465 | 47.2465 | 47.2388 | 47.231 | 47.2231 | 47.2148 | 47.2021 | 47.1978 | 47.184 | 47.1729 | 47.1412 | 47.1297 | 44.3871 | 44.378 | 44.3704 | 44.3539 | 44.3355 | 44.3208 | 44.3056 | 44.2868 | 44.276 | 44.243 | 43.8653 | 43.0027 | 42.1863 | 46.0635 | 46.0635 | 46.0635 | 46.0559 | 46.0481 | 46.0401 | 46.0319 | 46.0192 | 46.0123 | 45.9741 | 45.9178 | 45.1629 | 44.3998
|  | CORDWALLIS | FS |  |  | 47.2465 | 47.2465 | 47.2465 | 47.2462 | 47.2459 | 47.2456 | 47.2453 | 47.2448 | 47.2434 | 47.2391 | 47.237 | 47.2305 | 47.2251 | 44.3932 | 44.3876 | 44.3862 | 44.3829 | 44.379 | 44.3763 | 44.3735 | 44.3699 | 44.366 | 44.3542 | 44.3379 | 44.3152 | 44.2933 | 46.0635 | 46.0635 | 46.0635 | 46.0632 | 46.0629 | 46.0626 | 46.0623 | 46.0618 | 46.0604 | 46.0561 | 46.054 | 46.0475 | 46.0269
MANNINGTON GSP | LYTCHETT | CORFE MULLEN | MINIMUM HEADROOM | SY 98583 96071 | YES | 38.9914 | 38.9862 | 38.9792 | 38.826 | 38.6633 | 38.4774 | 38.2821 | 37.9936 | 37.9268 | 37.6953 | 37.3205 | 36.7905 | 36.6117 | 37.4394 | 37.4033 | 37.3535 | 37.1444 | 36.9108 | 36.5691 | 36.2121 | 35.7562 | 35.5089 | 34.6778 | 33.336 | 31.8544 | 30.7317 | 41.0901 | 41.088 | 41.0852 | 40.9374 | 40.7818 | 40.6112 | 40.4318 | 40.1597 | 40.1107 | 39.5416 | 38.2186 | 36.7555 | 35.6512
|  | CORFE MULLEN | CT |  |  | 38.9914 | 38.9862 | 38.9792 | 38.9691 | 38.956 | 38.9419 | 38.9123 | 38.8784 | 38.8474 | 38.7422 | 38.5332 | 38.3211 | 38.148 | 37.4394 | 37.4033 | 37.3535 | 37.2868 | 37.2025 | 37.1148 | 36.9234 | 36.7223 | 36.5107 | 35.806 | 34.6297 | 33.4663 | 32.3495 | 41.0901 | 41.088 | 41.0852 | 41.0807 | 41.0746 | 41.0677 | 41.054 | 41.0365 | 41.0233 | 40.6682 | 39.5108 | 38.3658 | 37.2674
|  | CORFE MULLEN | LW |  |  | 38.9914 | 38.9863 | 38.9793 | 38.826 | 38.6633 | 38.4774 | 38.2821 | 37.9936 | 37.9268 | 37.6953 | 37.3205 | 36.7905 | 36.6117 | 37.4396 | 37.4036 | 37.3541 | 37.1444 | 36.9108 | 36.5691 | 36.2121 | 35.7562 | 35.5089 | 34.6778 | 33.336 | 31.8544 | 30.7317 | 41.0902 | 41.0881 | 41.0852 | 40.9374 | 40.7818 | 40.6112 | 40.4318 | 40.1597 | 40.1107 | 39.5416 | 38.2186 | 36.7555 | 35.6512
|  | CORFE MULLEN | ST |  |  | 38.9932 | 38.9897 | 38.9858 | 38.8895 | 38.7887 | 38.6737 | 38.5544 | 38.3826 | 38.3095 | 38.0679 | 37.8116 | 37.2433 | 36.9979 | 37.4521 | 37.4274 | 37.3998 | 37.265 | 37.1106 | 36.87 | 36.6217 | 36.3363 | 36.1397 | 35.4825 | 34.5594 | 33.3693 | 32.518 | 41.0909 | 41.0894 | 41.0879 | 40.9953 | 40.8999 | 40.7972 | 40.6906 | 40.5299 | 40.469 | 40.2682 | 39.4277 | 38.2497 | 37.4102
|  | CORFE MULLEN | FS |  |  | 38.997 | 38.9958 | 38.9953 | 38.9925 | 38.9889 | 38.981 | 38.9729 | 38.9625 | 38.951 | 38.9111 | 38.8595 | 38.7866 | 38.7159 | 37.479 | 37.4705 | 37.4671 | 37.4514 | 37.4296 | 37.3778 | 37.3251 | 37.2596 | 37.1996 | 36.9967 | 36.6795 | 36.3462 | 36.0124 | 41.0924 | 41.0919 | 41.0917 | 41.0902 | 41.0884 | 41.0847 | 41.081 | 41.0761 | 41.0694 | 41.0454 | 41.0199 | 40.9727 | 40.8701
MELKSHAM GSP | NORRINGTON | CORSHAM | MINIMUM HEADROOM | ST 86766 69583 | YES | 17.4066 | 17.4066 | 17.4066 | 17.4052 | 17.4024 | 17.3931 | 17.3776 | 17.3559 | 17.3438 | 17.3032 | 17.2263 | 16.7287 | 16.0911 | 15.2581 | 15.2521 | 15.2397 | 15.2262 | 15.2113 | 15.1961 | 15.1793 | 15.1564 | 15.1429 | 14.7507 | 14.0519 | 13.2823 | 12.5282 | 16.1287 | 16.1287 | 16.1287 | 16.1273 | 16.1245 | 16.12 | 16.1139 | 16.1015 | 16.0969 | 15.9999 | 15.3038 | 14.5132 | 13.781
|  | CORSHAM | CT |  |  | 17.4066 | 17.4066 | 17.4066 | 17.4061 | 17.4054 | 17.4005 | 17.3894 | 17.3764 | 17.3657 | 17.3324 | 17.2525 | 16.7859 | 16.1415 | 15.2584 | 15.2527 | 15.2407 | 15.2286 | 15.2163 | 15.2036 | 15.1913 | 15.177 | 15.1649 | 14.7935 | 14.0913 | 13.3419 | 12.581 | 16.1287 | 16.1287 | 16.1287 | 16.1282 | 16.1275 | 16.1263 | 16.1246 | 16.1209 | 16.1186 | 16.0426 | 15.3437 | 14.5723 | 13.8334
|  | CORSHAM | LW |  |  | 17.4066 | 17.4066 | 17.4066 | 17.4052 | 17.4024 | 17.3931 | 17.3776 | 17.3559 | 17.3438 | 17.3032 | 17.2263 | 16.7287 | 16.0911 | 15.2581 | 15.2521 | 15.2397 | 15.2262 | 15.2113 | 15.1961 | 15.1793 | 15.1564 | 15.1429 | 14.7507 | 14.0519 | 13.2823 | 12.5282 | 16.1287 | 16.1287 | 16.1287 | 16.1273 | 16.1245 | 16.12 | 16.1139 | 16.1015 | 16.0969 | 15.9999 | 15.3038 | 14.5132 | 13.781
|  | CORSHAM | ST |  |  | 17.4066 | 17.4066 | 17.4066 | 17.4063 | 17.4057 | 17.4048 | 17.4035 | 17.3972 | 17.389 | 17.3615 | 17.3181 | 17.2498 | 17.1961 | 15.2598 | 15.2554 | 15.2479 | 15.2384 | 15.2268 | 15.2188 | 15.2106 | 15.2005 | 15.1913 | 15.161 | 14.7565 | 14.2665 | 13.8025 | 16.1287 | 16.1287 | 16.1287 | 16.1284 | 16.1278 | 16.1269 | 16.1256 | 16.1228 | 16.1214 | 16.114 | 16.0057 | 15.5179 | 15.0432
|  | CORSHAM | FS |  |  | 17.4066 | 17.4066 | 17.4066 | 17.4065 | 17.4065 | 17.4065 | 17.4064 | 17.4063 | 17.4059 | 17.4032 | 17.401 | 17.3909 | 17.3714 | 15.2673 | 15.2668 | 15.2664 | 15.2644 | 15.2619 | 15.2596 | 15.2572 | 15.2542 | 15.2507 | 15.2392 | 15.2224 | 15.1977 | 15.1738 | 16.1287 | 16.1287 | 16.1287 | 16.1286 | 16.1286 | 16.1286 | 16.1285 | 16.1284 | 16.1279 | 16.1253 | 16.1231 | 16.113 | 16.103
EAST CLAYDON GSP | BICESTER NORTH BSP | COTTISFORD | MINIMUM HEADROOM | SP 59021 31128 | NO | 2.8642 | 2.8642 | 2.8642 | 2.8156 | 2.7657 | 2.7142 | 2.6577 | 2.5664 | 2.5543 | 2.4568 | 2.1098 | 1.7298 | 1.5393 | 2.0663 | 2.0643 | 2.0599 | 2.0092 | 1.9556 | 1.9007 | 1.8418 | 1.7482 | 1.7337 | 1.6835 | 1.4387 | 1.1641 | 1.0774 | 2.0286 | 2.0058 | 1.9576 | 1.8845 | 1.7946 | 1.7035 | 1.6212 | 1.5044 | 1.4647 | 1.3404 | 0.97282 | 0.57154 | 0.36013
|  | COTTISFORD | CT |  |  | 2.8642 | 2.8642 | 2.8642 | 2.8156 | 2.7657 | 2.7142 | 2.6577 | 2.5664 | 2.5543 | 2.4568 | 2.1098 | 1.7298 | 1.5393 | 2.0668 | 2.065 | 2.0613 | 2.0092 | 1.9556 | 1.9007 | 1.8418 | 1.7482 | 1.7337 | 1.6835 | 1.4387 | 1.1641 | 1.0774 | 2.0344 | 2.0147 | 1.9733 | 1.8845 | 1.7946 | 1.7035 | 1.6212 | 1.5044 | 1.4647 | 1.3404 | 0.97282 | 0.57154 | 0.36013
|  | COTTISFORD | LW |  |  | 2.8642 | 2.8642 | 2.8642 | 2.8618 | 2.8568 | 2.8475 | 2.8333 | 2.8038 | 2.7986 | 2.7038 | 2.5239 | 2.2748 | 2.1494 | 2.0663 | 2.0643 | 2.0599 | 2.0533 | 2.0443 | 2.0326 | 2.0161 | 1.9843 | 1.9766 | 1.942 | 1.8641 | 1.7205 | 1.699 | 2.0286 | 2.0058 | 1.9576 | 1.9084 | 1.8572 | 1.8218 | 1.7818 | 1.7268 | 1.694 | 1.5851 | 1.3847 | 1.1143 | 0.96797
|  | COTTISFORD | ST |  |  | 2.8642 | 2.8642 | 2.8642 | 2.8259 | 2.7866 | 2.7455 | 2.7019 | 2.6321 | 2.6075 | 2.5227 | 2.3883 | 2.062 | 1.9057 | 2.0669 | 2.0654 | 2.0627 | 2.0213 | 1.9781 | 1.9353 | 1.8899 | 1.8185 | 1.7922 | 1.7025 | 1.6174 | 1.3591 | 1.2705 | 2.035 | 2.0181 | 1.9891 | 1.9152 | 1.8329 | 1.7718 | 1.7084 | 1.6211 | 1.5777 | 1.438 | 1.2714 | 0.93136 | 0.76153
|  | COTTISFORD | FS |  |  | 2.8642 | 2.8642 | 2.8642 | 2.8642 | 2.8641 | 2.864 | 2.8639 | 2.8636 | 2.8624 | 2.8557 | 2.8505 | 2.8277 | 2.8059 | 2.0695 | 2.0693 | 2.0692 | 2.0685 | 2.0676 | 2.0669 | 2.0662 | 2.0651 | 2.0633 | 2.0546 | 2.0465 | 2.0207 | 1.9961 | 2.0644 | 2.0626 | 2.061 | 2.0533 | 2.044 | 2.0371 | 2.0303 | 2.0213 | 2.0128 | 1.9849 | 1.946 | 1.8907 | 1.838
BRAMLEY (FLEE) | BURGHFIELD MAIN | COURAGES | MINIMUM HEADROOM | SU 70990 69570 | YES | 32.7321 | 32.7321 | 32.7321 | 32.7065 | 32.68 | 32.6524 | 32.6238 | 32.5699 | 32.5624 | 32.5368 | 32.4985 | 32.4281 | 32.4232 | 31.4365 | 31.4339 | 31.4289 | 31.3981 | 31.3663 | 31.3314 | 31.2955 | 31.2343 | 31.2191 | 31.1693 | 31.0788 | 30.9473 | 30.8813 | 31.0606 | 31.0606 | 31.0606 | 31.035 | 31.0086 | 30.981 | 30.9524 | 30.8985 | 30.891 | 30.8654 | 30.6974 | 30.4392 | 30.2463
|  | COURAGES | CT |  |  | 32.7321 | 32.7321 | 32.7321 | 32.7278 | 32.7234 | 32.7189 | 32.7142 | 32.6998 | 32.698 | 32.6921 | 32.6651 | 32.6372 | 32.6308 | 31.4367 | 31.4343 | 31.4296 | 31.4204 | 31.4109 | 31.4014 | 31.3894 | 31.3678 | 31.3583 | 31.3282 | 31.2489 | 31.16 | 31.0924 | 31.0606 | 31.0606 | 31.0606 | 31.0563 | 31.0519 | 31.0475 | 31.0428 | 31.0284 | 31.0266 | 31.0207 | 30.8749 | 30.6594 | 30.465
|  | COURAGES | LW |  |  | 32.7321 | 32.7321 | 32.7321 | 32.7065 | 32.68 | 32.6524 | 32.6238 | 32.5699 | 32.5624 | 32.5368 | 32.4985 | 32.4281 | 32.4232 | 31.4365 | 31.4339 | 31.4289 | 31.3981 | 31.3663 | 31.3314 | 31.2955 | 31.2343 | 31.2191 | 31.1693 | 31.0788 | 30.9473 | 30.8813 | 31.0606 | 31.0606 | 31.0606 | 31.035 | 31.0086 | 30.981 | 30.9524 | 30.8985 | 30.891 | 30.8654 | 30.6974 | 30.4392 | 30.2463
|  | COURAGES | ST |  |  | 32.7321 | 32.7321 | 32.7321 | 32.7287 | 32.7252 | 32.7217 | 32.7181 | 32.7097 | 32.7068 | 32.6977 | 32.6903 | 32.6693 | 32.6632 | 31.4381 | 31.4364 | 31.4338 | 31.427 | 31.4194 | 31.4107 | 31.4019 | 31.3885 | 31.3804 | 31.3548 | 31.3117 | 31.2506 | 31.2055 | 31.0606 | 31.0606 | 31.0606 | 31.0573 | 31.0538 | 31.0503 | 31.0467 | 31.0382 | 31.0354 | 31.0262 | 31.0157 | 30.8717 | 30.7453
|  | COURAGES | FS |  |  | 32.7321 | 32.7321 | 32.7321 | 32.7316 | 32.7312 | 32.7307 | 32.7303 | 32.7296 | 32.7276 | 32.7214 | 32.7184 | 32.709 | 32.7012 | 31.4979 | 31.4405 | 31.4402 | 31.4389 | 31.4373 | 31.435 | 31.4327 | 31.4297 | 31.4257 | 31.4131 | 31.3958 | 31.3692 | 31.3434 | 31.0606 | 31.0606 | 31.0606 | 31.0602 | 31.0597 | 31.0593 | 31.0588 | 31.0581 | 31.0562 | 31.0499 | 31.047 | 31.0376 | 31.0298
BRAMLEY (FLEE) | CAMBERLEY RESERVE | COVE | MINIMUM HEADROOM | SU 85415 55937 | YES | 34.8335 | 34.8292 | 34.8235 | 34.818 | 34.8123 | 34.8019 | 34.7915 | 34.7809 | 34.7696 | 34.735 | 34.6678 | 34.5695 | 33.7 | 33.1061 | 33.1012 | 33.0948 | 33.0885 | 33.0821 | 33.0702 | 33.0584 | 33.0468 | 33.0344 | 32.9966 | 32.553 | 31.5527 | 30.5581 | 33.6761 | 33.6424 | 33.5983 | 33.5548 | 33.5104 | 33.429 | 33.3475 | 33.2673 | 33.1818 | 32.9214 | 32.4152 | 31.8497 | 31.2874
|  | COVE | CT |  |  | 34.8341 | 34.8301 | 34.8252 | 34.8204 | 34.8154 | 34.8103 | 34.7999 | 34.7897 | 34.7783 | 34.7437 | 34.6766 | 34.6015 | 33.8021 | 33.1068 | 33.1023 | 33.0968 | 33.0913 | 33.0856 | 33.0798 | 33.0679 | 33.0563 | 33.0439 | 33.0061 | 32.6691 | 31.6689 | 30.6749 | 33.6811 | 33.6501 | 33.6116 | 33.5737 | 33.5347 | 33.4946 | 33.4131 | 33.3329 | 33.2474 | 32.9871 | 32.4808 | 31.9154 | 31.3535
|  | COVE | LW |  |  | 34.8335 | 34.8292 | 34.8235 | 34.818 | 34.8123 | 34.8019 | 34.7915 | 34.7809 | 34.7696 | 34.735 | 34.6678 | 34.5695 | 33.7 | 33.1061 | 33.1012 | 33.0948 | 33.0885 | 33.0821 | 33.0702 | 33.0584 | 33.0468 | 33.0344 | 32.9966 | 32.553 | 31.5527 | 30.5581 | 33.6761 | 33.6424 | 33.5983 | 33.5548 | 33.5104 | 33.429 | 33.3475 | 33.2673 | 33.1818 | 32.9214 | 32.4152 | 31.8497 | 31.2874
|  | COVE | ST |  |  | 34.8376 | 34.8359 | 34.835 | 34.8338 | 34.8324 | 34.8269 | 34.8213 | 34.8143 | 34.8069 | 34.7841 | 34.7385 | 34.6896 | 34.6416 | 33.1108 | 33.1089 | 33.1079 | 33.1066 | 33.1049 | 33.0986 | 33.0923 | 33.0843 | 33.0759 | 33.0502 | 33.0003 | 32.8423 | 32.2027 | 33.7084 | 33.6954 | 33.6881 | 33.6792 | 33.6678 | 33.6243 | 33.5808 | 33.526 | 33.4677 | 33.2909 | 32.9473 | 32.5788 | 32.2172
|  | COVE | FS |  |  | 34.8382 | 34.8372 | 34.8369 | 34.8359 | 34.8347 | 34.8328 | 34.8309 | 34.8286 | 34.8257 | 34.817 | 34.7997 | 34.78 | 34.7597 | 33.1115 | 33.1103 | 33.11 | 33.1089 | 33.1075 | 33.1054 | 33.1033 | 33.1006 | 33.0973 | 33.0874 | 33.0677 | 33.0457 | 33.0236 | 33.7131 | 33.7052 | 33.7029 | 33.6952 | 33.6859 | 33.6711 | 33.6564 | 33.6381 | 33.6154 | 33.5468 | 33.4113 | 33.2599 | 33.1074
FAWLEY GSP | COWES & WOOTTON COMMON BSP | COWES | MINIMUM HEADROOM | SP 56113 03074 | YES | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
|  | COWES | CT |  |  | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
|  | COWES | LW |  |  | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
|  | COWES | ST |  |  | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
|  | COWES | FS |  |  | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
COWLEY GSP | COWLEY LOCAL (2 X 90) | COWLEY LOCAL | MINIMUM HEADROOM | SP 56113 03074 | YES | 47.9985 | 47.981 | 46.9172 | 46.8103 | 46.6993 | 46.5834 | 46.4626 | 46.3167 | 46.2726 | 46.1274 | 45.8648 | 44.7416 | 42.7123 | 44.3757 | 44.3547 | 43.2837 | 43.1703 | 43.0516 | 42.9182 | 42.7807 | 42.6166 | 42.548 | 42.2762 | 41.1797 | 38.7689 | 36.4463 | 46.2567 | 46.2329 | 45.1561 | 45.0375 | 44.9127 | 44.7654 | 44.6163 | 44.4447 | 44.3662 | 44.0932 | 42.4725 | 40.202 | 38.016
|  | COWLEY LOCAL | CT |  |  | 48.0891 | 48.0787 | 47.4404 | 47.387 | 47.3327 | 47.2775 | 47.2209 | 47.1592 | 47.1366 | 47.0648 | 46.2274 | 44.8762 | 42.8335 | 44.4638 | 44.4483 | 43.7998 | 43.737 | 43.6722 | 43.604 | 43.5284 | 43.4485 | 43.3877 | 43.1893 | 41.366 | 38.8778 | 36.5418 | 46.3427 | 46.3233 | 45.6667 | 45.5963 | 45.5231 | 45.4445 | 45.3597 | 45.2707 | 45.2057 | 45.0061 | 42.6622 | 40.3239 | 38.1161
|  | COWLEY LOCAL | LW |  |  | 47.9985 | 47.981 | 46.9172 | 46.8103 | 46.6993 | 46.5834 | 46.4626 | 46.3167 | 46.2726 | 46.1274 | 45.8648 | 44.7416 | 42.7123 | 44.3757 | 44.3547 | 43.2837 | 43.1703 | 43.0516 | 42.9182 | 42.7807 | 42.6166 | 42.548 | 42.2762 | 41.1797 | 38.7689 | 36.4463 | 46.2567 | 46.2329 | 45.1561 | 45.0375 | 44.9127 | 44.7654 | 44.6163 | 44.4447 | 44.3662 | 44.0932 | 42.4725 | 40.202 | 38.016
|  | COWLEY LOCAL | ST |  |  | 48.1345 | 48.1275 | 47.702 | 47.6664 | 47.63 | 47.593 | 47.5548 | 47.5127 | 47.4953 | 47.4347 | 47.3403 | 47.2122 | 47.1042 | 44.5146 | 44.5061 | 44.0779 | 44.0397 | 43.9997 | 43.9533 | 43.907 | 43.8551 | 43.8278 | 43.7323 | 43.4846 | 42.8671 | 41.5301 | 46.398 | 46.3883 | 45.958 | 45.9176 | 45.8746 | 45.8208 | 45.768 | 45.7083 | 45.6731 | 45.5593 | 45.3015 | 44.2492 | 42.8763
|  | COWLEY LOCAL | FS |  |  | 48.1798 | 48.1763 | 47.9636 | 47.9461 | 47.9286 | 47.9111 | 47.8935 | 47.8758 | 47.8676 | 47.8399 | 47.7997 | 47.753 | 47.6896 | 44.5612 | 44.5571 | 44.3434 | 44.3248 | 44.3057 | 44.2845 | 44.2639 | 44.243 | 44.231 | 44.1919 | 44.1288 | 44.0509 | 43.9261 | 46.4456 | 46.4409 | 46.2265 | 46.2069 | 46.1866 | 46.1625 | 46.1395 | 46.116 | 46.1009 | 46.0527 | 45.9714 | 45.8781 | 45.7439
BRAMLEY (FLEE) | COXMOOR WOOD BSP | COXMOOR WOOD | MINIMUM HEADROOM | SU 78275 50779 | YES | 12.0659 | 12.0569 | 12.0388 | 12.0187 | 11.9978 | 11.9837 | 11.9666 | 11.9389 | 11.9283 | 11.8893 | 11.8103 | 11.6879 | 11.5842 | 10.8427 | 10.7398 | 10.5337 | 10.3283 | 10.1401 | 10.0584 | 9.9731 | 9.8769 | 9.7928 | 9.5417 | 9.1107 | 8.6314 | 8.2441 | 11.4879 | 11.4804 | 11.4655 | 11.4484 | 11.4302 | 11.4173 | 11.4013 | 11.3748 | 11.3653 | 11.3298 | 11.2566 | 10.997 | 10.5313
|  | COXMOOR WOOD | CT |  |  | 12.0682 | 12.0605 | 12.0451 | 12.0293 | 12.0145 | 11.9991 | 11.9896 | 11.9767 | 11.9685 | 11.942 | 11.858 | 11.7676 | 11.7031 | 10.8693 | 10.7811 | 10.6059 | 10.4323 | 10.2774 | 10.1225 | 10.0448 | 9.9634 | 9.8818 | 9.6432 | 9.2071 | 8.7599 | 8.3616 | 11.4898 | 11.4834 | 11.4707 | 11.4574 | 11.4449 | 11.4319 | 11.4236 | 11.4117 | 11.4047 | 11.3818 | 11.3035 | 11.1364 | 10.6599
|  | COXMOOR WOOD | LW |  |  | 12.0659 | 12.0569 | 12.0388 | 12.0187 | 11.9978 | 11.9837 | 11.9666 | 11.9389 | 11.9283 | 11.8893 | 11.8103 | 11.6879 | 11.5842 | 10.8427 | 10.7398 | 10.5337 | 10.3283 | 10.1401 | 10.0584 | 9.9731 | 9.8769 | 9.7928 | 9.5417 | 9.1107 | 8.6314 | 8.2441 | 11.4879 | 11.4804 | 11.4655 | 11.4484 | 11.4302 | 11.4173 | 11.4013 | 11.3748 | 11.3653 | 11.3298 | 11.2566 | 10.997 | 10.5313
|  | COXMOOR WOOD | ST |  |  | 12.0723 | 12.0675 | 12.0598 | 12.0498 | 12.0388 | 12.0325 | 12.0256 | 12.0162 | 12.009 | 11.9825 | 11.9433 | 11.8629 | 11.82 | 10.9159 | 10.8615 | 10.7731 | 10.6649 | 10.5488 | 10.4931 | 10.4366 | 10.3804 | 10.3231 | 10.1532 | 9.8786 | 9.5681 | 9.2992 | 11.4932 | 11.4893 | 11.4829 | 11.4745 | 11.4652 | 11.4598 | 11.4536 | 11.445 | 11.4386 | 11.4145 | 11.3792 | 11.3025 | 11.2633
|  | COXMOOR WOOD | FS |  |  | 12.0791 | 12.078 | 12.0769 | 12.0741 | 12.0714 | 12.0696 | 12.0678 | 12.0653 | 12.0627 | 12.0528 | 12.0405 | 12.015 | 11.9904 | 10.993 | 10.9812 | 10.9689 | 10.9366 | 10.9059 | 10.8862 | 10.8664 | 10.8409 | 10.8188 | 10.7534 | 10.6511 | 10.541 | 10.4369 | 11.4988 | 11.498 | 11.4971 | 11.4947 | 11.4925 | 11.491 | 11.4894 | 11.4874 | 11.4851 | 11.4761 | 11.4653 | 11.4411 | 11.4178
MANNINGTON GSP | LYTCHETT | CREEKMOOR | MINIMUM HEADROOM | SZ 00552 94121 | YES | 38.8762 | 38.8661 | 38.8486 | 38.5839 | 38.3144 | 38.0408 | 37.7517 | 37.3181 | 37.2429 | 37.0045 | 36.0849 | 35.112 | 34.7624 | 41.2042 | 41.2008 | 41.195 | 40.9417 | 40.684 | 40.4223 | 40.082 | 39.523 | 39.3142 | 38.6652 | 36.9193 | 34.9887 | 33.673 | 42.7823 | 42.7823 | 42.7823 | 42.5348 | 42.2831 | 42.0272 | 41.76 | 41.3481 | 41.2959 | 40.981 | 39.2307 | 37.318 | 36.0315
|  | CREEKMOOR | CT |  |  | 38.8762 | 38.8661 | 38.8486 | 38.5839 | 38.3144 | 38.0408 | 37.7517 | 37.3181 | 37.2429 | 37.0045 | 36.0849 | 35.112 | 34.7624 | 41.2042 | 41.2008 | 41.195 | 40.9417 | 40.684 | 40.4223 | 40.082 | 39.523 | 39.3142 | 38.6652 | 36.9193 | 34.9887 | 33.673 | 42.7823 | 42.7823 | 42.7823 | 42.5348 | 42.2831 | 42.0272 | 41.76 | 41.3481 | 41.2959 | 40.981 | 39.2307 | 37.318 | 36.0315
|  | CREEKMOOR | LW |  |  | 38.882 | 38.8749 | 38.8642 | 38.8203 | 38.7748 | 38.7171 | 38.6581 | 38.5803 | 38.5495 | 38.452 | 38.2683 | 38.022 | 37.8554 | 41.2061 | 41.2038 | 41.2002 | 41.1635 | 41.1255 | 41.0824 | 41.0381 | 40.9253 | 40.7611 | 40.2529 | 39.243 | 38.0439 | 36.9107 | 42.7823 | 42.7823 | 42.7823 | 42.7492 | 42.715 | 42.6793 | 42.6423 | 42.5861 | 42.5783 | 42.5516 | 41.5551 | 40.3688 | 39.2649
|  | CREEKMOOR | ST |  |  | 38.9895 | 38.883 | 38.8784 | 38.8727 | 38.8655 | 38.849 | 38.8328 | 38.818 | 38.8023 | 38.7542 | 38.6571 | 38.5518 | 38.4486 | 41.2421 | 41.2065 | 41.2049 | 41.203 | 41.2006 | 41.1951 | 41.1897 | 41.1847 | 41.1795 | 40.9696 | 40.3098 | 39.5936 | 38.8893 | 42.7823 | 42.7823 | 42.7823 | 42.7823 | 42.7823 | 42.7823 | 42.7823 | 42.7823 | 42.7823 | 42.7823 | 42.6255 | 41.9061 | 41.2015
|  | CREEKMOOR | FS |  |  | 38.9944 | 38.8905 | 38.8899 | 38.8808 | 38.8713 | 38.8596 | 38.8478 | 38.8309 | 38.7938 | 38.6771 | 38.5918 | 38.4006 | 38.2326 | 41.2437 | 41.209 | 41.2088 | 41.201 | 41.1932 | 41.1846 | 41.1759 | 41.1628 | 41.1299 | 41.0255 | 40.9659 | 40.6659 | 40.2376 | 42.7823 | 42.7823 | 42.7823 | 42.7752 | 42.7682 | 42.7612 | 42.7541 | 42.7429 | 42.712 | 42.6139 | 42.5672 | 42.4201 | 42.2971
MINETY GSP | CIRENCESTER BSP | CRICKLADE | MINIMUM HEADROOM | SU 09400 93270 | YES | 22.8114 | 22.8114 | 22.8114 | 22.8056 | 22.7998 | 22.794 | 22.7825 | 22.7583 | 22.7524 | 22.6666 | 22.4363 | 21.8723 | 21.4101 | 20.7277 | 20.7234 | 20.7144 | 20.7031 | 20.6889 | 20.6749 | 20.6576 | 20.6282 | 20.6184 | 20.4601 | 19.8401 | 19.1437 | 18.5514 | 21.5996 | 21.5118 | 21.3259 | 21.1431 | 20.9591 | 20.8119 | 20.6996 | 20.5843 | 20.4663 | 20.1006 | 19.4817 | 18.7946 | 18.2114
|  | CRICKLADE | CT |  |  | 22.8114 | 22.8114 | 22.8114 | 22.8106 | 22.8091 | 22.8068 | 22.8035 | 22.7962 | 22.7949 | 22.7879 | 22.4533 | 21.926 | 21.451 | 20.7279 | 20.7237 | 20.715 | 20.7057 | 20.6958 | 20.6852 | 20.6766 | 20.6641 | 20.6572 | 20.4747 | 19.8477 | 19.1882 | 18.5831 | 21.6038 | 21.5183 | 21.3374 | 21.1613 | 20.9862 | 20.8119 | 20.6996 | 20.5843 | 20.4664 | 20.115 | 19.49 | 18.8397 | 18.2437
|  | CRICKLADE | LW |  |  | 22.8114 | 22.8114 | 22.8114 | 22.8088 | 22.8032 | 22.7945 | 22.7825 | 22.7583 | 22.7541 | 22.7328 | 22.4363 | 21.8723 | 21.4101 | 20.7277 | 20.7234 | 20.7144 | 20.7031 | 20.6889 | 20.6749 | 20.6576 | 20.6282 | 20.6184 | 20.4601 | 19.8401 | 19.1437 | 18.5514 | 21.5996 | 21.5118 | 21.3259 | 21.1431 | 20.9591 | 20.8403 | 20.7193 | 20.587 | 20.4663 | 20.1006 | 19.4817 | 18.7946 | 18.2114
|  | CRICKLADE | ST |  |  | 22.8114 | 22.8114 | 22.8114 | 22.8109 | 22.8097 | 22.808 | 22.8055 | 22.7999 | 22.7972 | 22.7826 | 22.7636 | 22.5378 | 22.2263 | 20.7277 | 20.724 | 20.7176 | 20.7093 | 20.6987 | 20.693 | 20.6865 | 20.6773 | 20.6708 | 20.645 | 20.4204 | 19.9771 | 19.5724 | 21.6006 | 21.5238 | 21.3923 | 21.2301 | 21.0343 | 20.9494 | 20.8648 | 20.7854 | 20.7031 | 20.4567 | 20.0607 | 19.6168 | 19.2181
|  | CRICKLADE | FS |  |  | 22.8114 | 22.8114 | 22.8114 | 22.8056 | 22.7998 | 22.794 | 22.788 | 22.7787 | 22.7524 | 22.6666 | 22.6241 | 22.4834 | 22.363 | 20.7343 | 20.734 | 20.7337 | 20.7264 | 20.7189 | 20.7117 | 20.7044 | 20.6933 | 20.6655 | 20.5755 | 20.526 | 20.3788 | 20.2521 | 21.7371 | 21.7304 | 21.7241 | 21.6883 | 21.6471 | 21.6132 | 21.5795 | 21.5343 | 21.4773 | 21.3021 | 21.117 | 20.8396 | 20.5903
MELKSHAM GSP | FROME BSP | CROCKERTON | MINIMUM HEADROOM | ST 87736 43371 | YES | 22.8677 | 22.8677 | 22.8677 | 22.8626 | 22.8577 | 22.8527 | 22.8477 | 22.8398 | 22.818 | 22.7486 | 22.7155 | 22.6115 | 22.5245 | 20.5393 | 20.5365 | 20.5304 | 20.5245 | 20.5187 | 20.5056 | 20.4926 | 20.4797 | 20.3848 | 19.8769 | 19.0449 | 18.188 | 17.3457 | 21.6173 | 21.6173 | 21.6173 | 21.6123 | 21.6073 | 21.6024 | 21.5974 | 21.5895 | 21.5676 | 21.4982 | 21.4652 | 21.0126 | 20.2295
|  | CROCKERTON | CT |  |  | 22.8677 | 22.8677 | 22.8677 | 22.8677 | 22.8677 | 22.8677 | 22.8677 | 22.8677 | 22.8677 | 22.8677 | 22.8677 | 22.8677 | 22.6856 | 20.5397 | 20.5371 | 20.5315 | 20.5261 | 20.5207 | 20.5154 | 20.5024 | 20.4895 | 20.4757 | 19.9989 | 19.1668 | 18.3102 | 17.4685 | 21.6173 | 21.6173 | 21.6173 | 21.6173 | 21.6173 | 21.6173 | 21.6173 | 21.6173 | 21.6173 | 21.6173 | 21.6173 | 21.1262 | 20.3436
|  | CROCKERTON | LW |  |  | 22.8677 | 22.8677 | 22.8677 | 22.8677 | 22.8677 | 22.8677 | 22.8677 | 22.8677 | 22.8677 | 22.8677 | 22.8677 | 22.8677 | 22.5803 | 20.5393 | 20.5365 | 20.5304 | 20.5245 | 20.5187 | 20.5056 | 20.4926 | 20.4797 | 20.3848 | 19.8769 | 19.0449 | 18.188 | 17.3457 | 21.6173 | 21.6173 | 21.6173 | 21.6173 | 21.6173 | 21.6173 | 21.6173 | 21.6173 | 21.6173 | 21.6173 | 21.6173 | 21.0126 | 20.2295
|  | CROCKERTON | ST |  |  | 22.8677 | 22.8677 | 22.8677 | 22.8677 | 22.8677 | 22.8677 | 22.8677 | 22.8677 | 22.8677 | 22.8677 | 22.8677 | 22.8677 | 22.8677 | 20.5551 | 20.5383 | 20.5348 | 20.5306 | 20.5255 | 20.5196 | 20.5138 | 20.5051 | 20.4956 | 20.4119 | 19.8585 | 19.3068 | 18.7588 | 21.6173 | 21.6173 | 21.6173 | 21.6173 | 21.6173 | 21.6173 | 21.6173 | 21.6173 | 21.6173 | 21.6173 | 21.6173 | 21.6173 | 21.5434
|  | CROCKERTON | FS |  |  | 22.8677 | 22.8677 | 22.8677 | 22.8626 | 22.8577 | 22.8527 | 22.8477 | 22.8398 | 22.818 | 22.7486 | 22.7155 | 22.6115 | 22.5245 | 20.5586 | 20.5584 | 20.5582 | 20.5521 | 20.5461 | 20.5393 | 20.5325 | 20.5223 | 20.4967 | 20.4167 | 20.3668 | 20.2468 | 20.1447 | 21.6173 | 21.6173 | 21.6173 | 21.6123 | 21.6073 | 21.6024 | 21.5974 | 21.5895 | 21.5676 | 21.4982 | 21.4652 | 21.3611 | 21.2741
BRAMLEY (FLEE) | PYESTOCK BSP | CROOKHAM | MINIMUM HEADROOM | SU 81702 53403 | YES | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
|  | CROOKHAM | CT |  |  | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
|  | CROOKHAM | LW |  |  | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
|  | CROOKHAM | ST |  |  | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
|  | CROOKHAM | FS |  |  | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
BRAMLEY (FLEE) | CAMBERLEY MAIN | CROWTHORNE | MINIMUM HEADROOM | SU 84470 64352 | YES | 46.3039 | 46.2916 | 45.5434 | 45.4792 | 45.4119 | 45.3413 | 45.2671 | 45.1798 | 45.1508 | 44.985 | 43.3663 | 41.9147 | 40.5436 | 42.8787 | 42.8296 | 41.977 | 41.8032 | 41.4584 | 40.946 | 40.4593 | 39.9518 | 39.516 | 38.1692 | 36.2916 | 34.5954 | 33.0058 | 44.9453 | 44.933 | 44.1667 | 44.0545 | 43.9373 | 43.8398 | 43.5295 | 43.026 | 42.6007 | 41.2863 | 39.4528 | 37.7983 | 36.2459
|  | CROWTHORNE | CT |  |  | 46.3676 | 46.3603 | 45.9114 | 45.8737 | 45.8353 | 45.796 | 45.7557 | 45.7111 | 45.695 | 45.482 | 43.4426 | 41.9149 | 40.5436 | 42.9469 | 42.9052 | 42.3647 | 42.2256 | 42.0811 | 41.2993 | 40.8463 | 40.3744 | 39.9514 | 38.6497 | 36.3514 | 34.5954 | 33.0058 | 45.0091 | 45.0017 | 44.5433 | 44.4612 | 44.3763 | 44.2884 | 43.9122 | 43.4514 | 43.039 | 41.7696 | 39.5154 | 37.7983 | 36.2459
|  | CROWTHORNE | LW |  |  | 46.3039 | 46.2916 | 45.5434 | 45.4792 | 45.4119 | 45.3413 | 45.2671 | 45.1798 | 45.1508 | 44.985 | 43.3663 | 41.9147 | 40.5568 | 42.8787 | 42.8296 | 41.977 | 41.8032 | 41.4584 | 40.946 | 40.4593 | 39.9518 | 39.516 | 38.1692 | 36.2916 | 34.6117 | 33.0354 | 44.9453 | 44.933 | 44.1667 | 44.0545 | 43.9373 | 43.8398 | 43.5295 | 43.026 | 42.6007 | 41.2863 | 39.4528 | 37.8118 | 36.2726
|  | CROWTHORNE | ST |  |  | 46.3995 | 46.3946 | 46.0953 | 46.0702 | 46.0445 | 46.0181 | 45.9909 | 45.9603 | 45.9476 | 45.9026 | 45.8331 | 45.732 | 44.995 | 43.0144 | 42.9687 | 42.6355 | 42.5561 | 42.4514 | 42.3763 | 42.3032 | 42.2353 | 42.1867 | 41.3545 | 40.1537 | 39.0838 | 38.0736 | 45.041 | 45.0361 | 44.7368 | 44.7116 | 44.6561 | 44.6084 | 44.5611 | 44.5142 | 44.4857 | 44.3919 | 43.2396 | 42.1948 | 41.2087
|  | CROWTHORNE | FS |  |  | 46.4314 | 46.429 | 46.2793 | 46.267 | 46.2547 | 46.2424 | 46.23 | 46.2175 | 46.2116 | 46.1913 | 46.1623 | 46.1262 | 46.0783 | 43.0744 | 43.047 | 42.8913 | 42.8668 | 42.84 | 42.816 | 42.793 | 42.7686 | 42.754 | 42.7015 | 42.6142 | 42.5307 | 42.4392 | 45.0729 | 45.0704 | 44.9208 | 44.9085 | 44.8962 | 44.8838 | 44.8715 | 44.8589 | 44.8531 | 44.8327 | 44.7936 | 44.7368 | 44.6698
COWLEY GSP |  | CULHAM | MINIMUM HEADROOM |  |  | 3.9837 | 3.9837 | 3.9837 | 3.8117 | 3.6342 | 3.4488 | 3.2566 | 2.9648 | 2.9243 | 2.7858 | 2.5781 | 1.7646 | 1.1664 | 3.5294 | 3.527 | 3.5231 | 3.3535 | 3.1738 | 2.986 | 2.7915 | 2.4973 | 2.4545 | 2.2998 | 1.5744 | 0.51873 | -0.18195 | 3.6673 | 3.6643 | 3.6593 | 3.4904 | 3.31 | 3.1216 | 2.9265 | 2.6317 | 2.5882 | 2.4391 | 1.807 | 0.80456 | 0.10366
|  | CULHAM | CT |  |  | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
|  | CULHAM | LW |  |  | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
|  | CULHAM | ST |  |  | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
|  | CULHAM | FS |  |  | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
EALING GSP | EALING 22kV | DEAN GARDENS | MINIMUM HEADROOM | TQ 16546 80368 | YES | 3.9837 | 3.9837 | 3.9837 | 3.8117 | 3.6342 | 3.4488 | 3.2566 | 2.9648 | 2.9243 | 2.7858 | 2.5781 | 1.7646 | 1.1664 | 3.5294 | 3.527 | 3.5231 | 3.3535 | 3.1738 | 2.986 | 2.7915 | 2.4973 | 2.4545 | 2.2998 | 1.5744 | 0.51873 | -0.18195 | 3.6673 | 3.6643 | 3.6593 | 3.4904 | 3.31 | 3.1216 | 2.9265 | 2.6317 | 2.5882 | 2.4391 | 1.807 | 0.80456 | 0.10366
|  | DEAN GARDENS | CT |  |  | 3.9837 | 3.9837 | 3.9837 | 3.9837 | 3.9837 | 3.9837 | 3.9837 | 3.9837 | 3.9837 | 3.9837 | 3.9447 | 3.3823 | 2.8121 | 3.5294 | 3.527 | 3.5231 | 3.5191 | 3.515 | 3.5108 | 3.5084 | 3.5061 | 3.4595 | 3.2852 | 2.7676 | 2.1041 | 1.4314 | 3.6673 | 3.6643 | 3.6593 | 3.6543 | 3.649 | 3.6437 | 3.6407 | 3.6378 | 3.6347 | 3.4931 | 3.0172 | 2.3898 | 1.7169
|  | DEAN GARDENS | LW |  |  | 3.9837 | 3.9837 | 3.9837 | 3.8117 | 3.6342 | 3.4488 | 3.2566 | 2.9648 | 2.9243 | 2.7858 | 2.5781 | 1.7646 | 1.1664 | 3.531 | 3.5296 | 3.5276 | 3.3535 | 3.1738 | 2.986 | 2.7915 | 2.4973 | 2.4545 | 2.2998 | 1.5744 | 0.51873 | -0.18195 | 3.6694 | 3.6676 | 3.665 | 3.4904 | 3.31 | 3.1216 | 2.9265 | 2.6317 | 2.5882 | 2.4391 | 1.807 | 0.80456 | 0.10366
|  | DEAN GARDENS | ST |  |  | 3.9837 | 3.9837 | 3.9837 | 3.8676 | 3.7497 | 3.6294 | 3.505 | 3.3127 | 3.2474 | 3.0391 | 2.8718 | 2.364 | 1.9592 | 3.5327 | 3.5321 | 3.5316 | 3.415 | 3.2962 | 3.1737 | 3.0473 | 2.8534 | 2.7865 | 2.5724 | 2.2628 | 1.3146 | 0.74275 | 3.6715 | 3.6707 | 3.6701 | 3.5533 | 3.4343 | 3.3113 | 3.1843 | 2.99 | 2.9227 | 2.707 | 2.4634 | 1.5508 | 1.0133
|  | DEAN GARDENS | FS |  |  | 3.9837 | 3.9837 | 3.9837 | 3.9837 | 3.9837 | 3.9837 | 3.9837 | 3.9837 | 3.9837 | 3.9837 | 3.9837 | 3.9837 | 3.9837 | 3.5333 | 3.5329 | 3.5327 | 3.5323 | 3.5318 | 3.531 | 3.5301 | 3.5292 | 3.5285 | 3.5263 | 3.519 | 3.5089 | 3.3388 | 3.6722 | 3.6717 | 3.6715 | 3.671 | 3.6703 | 3.6692 | 3.6682 | 3.667 | 3.6662 | 3.6633 | 3.6541 | 3.6413 | 3.5423
COWLEY GSP | YARNTON BSP | DEDDINGTON | MINIMUM HEADROOM | SP 46729 30325 | NO | 6.1553 | 6.1553 | 6.1553 | 6.141 | 6.1263 | 6.0664 | 6.0074 | 5.9421 | 5.8897 | 5.7343 | 5.4521 | 5.1537 | 4.8945 | 4.1769 | 4.1531 | 4.1026 | 4.0424 | 3.9823 | 3.9225 | 3.8767 | 3.8244 | 3.7861 | 3.6711 | 3.459 | 3.2318 | 3.0427 | 5.4785 | 5.4762 | 5.4712 | 5.4527 | 5.4333 | 5.4146 | 5.3953 | 5.3678 | 5.3609 | 5.3389 | 5.0579 | 4.7218 | 4.4256
|  | DEDDINGTON | CT |  |  | 6.1553 | 6.1553 | 6.1553 | 6.1439 | 6.1323 | 6.0664 | 6.0074 | 5.9421 | 5.8897 | 5.7343 | 5.4521 | 5.1537 | 4.8945 | 4.1769 | 4.1531 | 4.1026 | 4.0424 | 3.9823 | 3.9225 | 3.8767 | 3.8244 | 3.7861 | 3.6723 | 3.459 | 3.2318 | 3.0427 | 5.4785 | 5.4762 | 5.4712 | 5.455 | 5.4386 | 5.4221 | 5.4064 | 5.3842 | 5.3783 | 5.36 | 5.0579 | 4.7218 | 4.4256
|  | DEDDINGTON | LW |  |  | 6.1553 | 6.1553 | 6.1553 | 6.141 | 6.1263 | 6.0877 | 6.0249 | 5.9544 | 5.901 | 5.7417 | 5.4804 | 5.196 | 4.9447 | 4.1786 | 4.1556 | 4.1071 | 4.0457 | 3.9843 | 3.935 | 3.8855 | 3.828 | 3.7888 | 3.6711 | 3.4786 | 3.2654 | 3.0843 | 5.4787 | 5.4764 | 5.4716 | 5.4527 | 5.4333 | 5.4146 | 5.3953 | 5.3678 | 5.3609 | 5.3389 | 5.0908 | 4.7687 | 4.4804
|  | DEDDINGTON | ST |  |  | 6.1553 | 6.1553 | 6.1553 | 6.1553 | 6.1553 | 6.1553 | 6.1553 | 6.1553 | 6.1553 | 6.1038 | 5.9414 | 5.7786 | 5.6168 | 4.3327 | 4.1897 | 4.1726 | 4.1517 | 4.1264 | 4.1019 | 4.0778 | 4.0551 | 4.0306 | 3.9592 | 3.8425 | 3.7256 | 3.6094 | 5.494 | 5.4798 | 5.4781 | 5.476 | 5.4735 | 5.4711 | 5.4687 | 5.4665 | 5.464 | 5.457 | 5.4454 | 5.4161 | 5.2302
|  | DEDDINGTON | FS |  |  | 6.1553 | 6.1553 | 6.1553 | 6.1553 | 6.1553 | 6.1553 | 6.1553 | 6.1553 | 6.1553 | 6.1553 | 6.1553 | 6.1553 | 6.1553 | 4.3475 | 4.3458 | 4.3441 | 4.3363 | 4.3271 | 4.3187 | 4.3105 | 4.2999 | 4.2905 | 4.2629 | 4.219 | 4.1766 | 4.1365 | 5.4954 | 5.4953 | 5.4951 | 5.4943 | 5.4934 | 5.4926 | 5.4918 | 5.4907 | 5.4898 | 5.4871 | 5.4827 | 5.4785 | 5.4745
IVER 132KV | DENHAM | DENHAM AVENUE | MINIMUM HEADROOM | TQ 03761 86587 | YES | 16.3788 | 16.3788 | 16.3788 | 16.3067 | 16.2332 | 16.158 | 16.0801 | 15.9591 | 15.9178 | 15.7842 | 15.6746 | 15.3565 | 15.2629 | 15.4071 | 15.4071 | 15.4071 | 15.335 | 15.2615 | 15.1863 | 15.1084 | 14.9874 | 14.9461 | 14.8125 | 14.7029 | 14.3848 | 14.2912 | 16.4077 | 16.4077 | 16.4077 | 16.3355 | 16.2621 | 16.1869 | 16.109 | 15.988 | 15.9467 | 15.8131 | 15.7034 | 15.3853 | 15.2918
|  | DENHAM AVENUE | CT |  |  | 16.3788 | 16.3788 | 16.3788 | 16.3786 | 16.3781 | 16.3774 | 16.3764 | 16.3742 | 16.3738 | 16.3717 | 16.3542 | 16.3347 | 16.3287 | 15.4071 | 15.4071 | 15.4071 | 15.4069 | 15.4064 | 15.4057 | 15.4047 | 15.4025 | 15.4021 | 15.4 | 15.3825 | 15.363 | 15.357 | 16.4077 | 16.4077 | 16.4077 | 16.4075 | 16.407 | 16.4063 | 16.4053 | 16.4031 | 16.4027 | 16.4006 | 16.3831 | 16.3636 | 16.3576
|  | DENHAM AVENUE | LW |  |  | 16.3788 | 16.3788 | 16.3788 | 16.378 | 16.3763 | 16.3737 | 16.37 | 16.3627 | 16.3614 | 16.355 | 16.3392 | 16.3086 | 16.3065 | 15.4071 | 15.4071 | 15.4071 | 15.4063 | 15.4046 | 15.402 | 15.3984 | 15.391 | 15.3897 | 15.3833 | 15.3676 | 15.3369 | 15.3348 | 16.4077 | 16.4077 | 16.4077 | 16.4069 | 16.4052 | 16.4026 | 16.3989 | 16.3916 | 16.3903 | 16.3838 | 16.3681 | 16.3374 | 16.3354
|  | DENHAM AVENUE | ST |  |  | 16.3788 | 16.3788 | 16.3788 | 16.3067 | 16.2332 | 16.158 | 16.0801 | 15.9591 | 15.9178 | 15.7842 | 15.6746 | 15.3565 | 15.2629 | 15.4071 | 15.4071 | 15.4071 | 15.335 | 15.2615 | 15.1863 | 15.1084 | 14.9874 | 14.9461 | 14.8125 | 14.7029 | 14.3848 | 14.2912 | 16.4077 | 16.4077 | 16.4077 | 16.3355 | 16.2621 | 16.1869 | 16.109 | 15.988 | 15.9467 | 15.8131 | 15.7034 | 15.3853 | 15.2918
|  | DENHAM AVENUE | FS |  |  | 16.3788 | 16.3788 | 16.3788 | 16.3788 | 16.3788 | 16.3788 | 16.3787 | 16.3787 | 16.3784 | 16.3768 | 16.3755 | 16.3695 | 16.3636 | 15.4071 | 15.4071 | 15.4071 | 15.4071 | 15.4071 | 15.4071 | 15.4071 | 15.407 | 15.4067 | 15.4051 | 15.4039 | 15.3978 | 15.3919 | 16.4077 | 16.4077 | 16.4077 | 16.4077 | 16.4077 | 16.4077 | 16.4076 | 16.4076 | 16.4073 | 16.4057 | 16.4044 | 16.3984 | 16.3925
MELKSHAM GSP | NORRINGTON | DEVIZES | MINIMUM HEADROOM | SU 00106 60986 | YES | 37.2545 | 37.2316 | 36.1773 | 36.077 | 35.9737 | 35.8568 | 35.7205 | 35.5713 | 35.3929 | 34.6197 | 33.3288 | 32.0213 | 30.7493 | 33.5129 | 33.4958 | 32.4537 | 32.3654 | 32.1205 | 31.7799 | 31.438 | 31.0854 | 30.787 | 29.8949 | 28.4085 | 26.8999 | 25.4301 | 39.5794 | 39.4852 | 38.2799 | 38.0328 | 37.7828 | 37.4429 | 37.1018 | 36.7499 | 36.4523 | 35.5625 | 34.08 | 32.5753 | 31.1094
|  | DEVIZES | CT |  |  | 37.3467 | 37.3326 | 36.6991 | 36.6156 | 36.531 | 36.4453 | 36.3472 | 36.2182 | 36.151 | 35.5723 | 33.6236 | 32.1111 | 30.8038 | 33.6017 | 33.5915 | 32.9662 | 32.8908 | 32.8143 | 32.7037 | 32.3807 | 32.0421 | 31.7556 | 30.9044 | 28.7602 | 27.0466 | 25.5415 | 39.7138 | 39.6516 | 38.9163 | 38.7337 | 38.5496 | 38.3656 | 38.0433 | 37.7054 | 37.4198 | 36.5709 | 34.4306 | 32.7209 | 31.2197
|  | DEVIZES | LW |  |  | 37.2545 | 37.2316 | 36.1773 | 36.077 | 35.9737 | 35.8568 | 35.7205 | 35.5713 | 35.3929 | 34.6197 | 33.3288 | 32.0213 | 30.7493 | 33.5129 | 33.4958 | 32.4537 | 32.3654 | 32.1205 | 31.7799 | 31.438 | 31.0854 | 30.787 | 29.8949 | 28.4085 | 26.8999 | 25.4301 | 39.5794 | 39.4852 | 38.2799 | 38.0328 | 37.7828 | 37.4429 | 37.1018 | 36.7499 | 36.4523 | 35.5625 | 34.08 | 32.5753 | 31.1094
|  | DEVIZES | ST |  |  | 37.3895 | 37.3783 | 36.9541 | 36.8661 | 36.7749 | 36.6824 | 36.5876 | 36.4546 | 36.3856 | 36.0738 | 35.2133 | 34.1954 | 33.3338 | 33.6461 | 33.6393 | 33.2225 | 33.1435 | 33.0633 | 32.8437 | 32.6179 | 32.34 | 32.1214 | 31.4687 | 30.4784 | 29.331 | 28.3408 | 39.7362 | 39.6721 | 39.157 | 38.9573 | 38.7307 | 38.5059 | 38.2806 | 38.0031 | 37.7851 | 37.134 | 36.1462 | 35.0014 | 34.0137
|  | DEVIZES | FS |  |  | 37.4414 | 37.4376 | 37.2287 | 37.2096 | 37.1901 | 37.1697 | 37.1493 | 37.1277 | 37.1148 | 37.0737 | 37.0113 | 36.9291 | 36.8261 | 33.6905 | 33.6871 | 33.4787 | 33.4616 | 33.4445 | 33.4273 | 33.4101 | 33.3928 | 33.385 | 33.3588 | 33.0527 | 32.7084 | 32.365 | 39.8811 | 39.8718 | 39.6578 | 39.6143 | 39.5656 | 39.5047 | 39.4444 | 39.3713 | 39.2951 | 39.0701 | 38.7153 | 38.372 | 38.0294
MINETY GSP | TOOTHILL BSP | DORCAN SOUTH | MINIMUM HEADROOM | SU 19288 83540 | YES | 24.4537 | 24.4533 | 24.4526 | 24.3748 | 24.295 | 24.2126 | 24.1273 | 23.9958 | 23.9495 | 23.8015 | 23.6694 | 23.3234 | 23.1091 | 25.645 | 25.6447 | 25.6443 | 25.5664 | 25.4868 | 25.4048 | 25.3201 | 25.1892 | 25.1437 | 24.9983 | 24.8723 | 24.4859 | 24.0692 | 26.106 | 26.106 | 26.106 | 26.028 | 25.9487 | 25.8678 | 25.7842 | 25.6549 | 25.611 | 25.4699 | 25.3411 | 24.9991 | 24.8869
|  | DORCAN SOUTH | CT |  |  | 24.4537 | 24.4533 | 24.4526 | 24.4519 | 24.4512 | 24.4504 | 24.447 | 24.4437 | 24.4402 | 24.4286 | 24.4003 | 24.2036 | 23.8025 | 25.645 | 25.6447 | 25.6443 | 25.6438 | 25.6432 | 25.6427 | 25.6404 | 25.6382 | 25.6357 | 25.6279 | 25.6085 | 25.1454 | 24.6374 | 26.106 | 26.106 | 26.106 | 26.106 | 26.106 | 26.106 | 26.106 | 26.106 | 26.106 | 26.0984 | 26.0748 | 26.0147 | 25.5268
|  | DORCAN SOUTH | LW |  |  | 24.4537 | 24.4533 | 24.4526 | 24.4519 | 24.4512 | 24.4479 | 24.4445 | 24.4412 | 24.4377 | 24.4262 | 24.3978 | 24.1753 | 23.774 | 25.645 | 25.6447 | 25.6443 | 25.6438 | 25.6432 | 25.641 | 25.6387 | 25.6365 | 25.634 | 25.6262 | 25.6068 | 25.1095 | 24.6014 | 26.106 | 26.106 | 26.106 | 26.106 | 26.106 | 26.106 | 26.106 | 26.106 | 26.1058 | 26.0963 | 26.0727 | 25.9803 | 25.4922
|  | DORCAN SOUTH | ST |  |  | 24.4539 | 24.4537 | 24.4533 | 24.3748 | 24.295 | 24.2126 | 24.1273 | 23.9958 | 23.9495 | 23.8015 | 23.6694 | 23.3234 | 23.1091 | 25.6451 | 25.6449 | 25.6447 | 25.5664 | 25.4868 | 25.4048 | 25.3201 | 25.1892 | 25.1437 | 24.9983 | 24.8723 | 24.4859 | 24.0692 | 26.106 | 26.106 | 26.106 | 26.028 | 25.9487 | 25.8678 | 25.7842 | 25.6549 | 25.611 | 25.4699 | 25.3411 | 24.9991 | 24.8869
|  | DORCAN SOUTH | FS |  |  | 24.4541 | 24.454 | 24.4539 | 24.4537 | 24.4535 | 24.453 | 24.4525 | 24.4519 | 24.451 | 24.4479 | 24.4398 | 24.4292 | 24.4181 | 25.6453 | 25.6452 | 25.6451 | 25.645 | 25.6449 | 25.6445 | 25.6442 | 25.6438 | 25.6431 | 25.641 | 25.6355 | 25.6283 | 25.6207 | 26.106 | 26.106 | 26.106 | 26.106 | 26.106 | 26.106 | 26.106 | 26.106 | 26.106 | 26.106 | 26.106 | 26.0989 | 26.0896
CHICKERELL GSP | CHICKERELL BSP | DORCHESTER | MINIMUM HEADROOM | SY 69113 90401 | YES | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
|  | DORCHESTER | CT |  |  | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
|  | DORCHESTER | LW |  |  | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
|  | DORCHESTER | ST |  |  | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
|  | DORCHESTER | FS |  |  | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | DOWN GRANGE | MINIMUM HEADROOM | SU 61604 50238 | YES | 39.1305 | 39.1305 | 39.1305 | 39.1305 | 39.1305 | 39.1305 | 39.1305 | 39.1305 | 39.1305 | 39.1305 | 37.5768 | 35.6704 | 33.7922 | 40.6976 | 40.6854 | 40.6622 | 40.6389 | 40.6148 | 40.5858 | 40.5528 | 40.519 | 40.4827 | 39.6557 | 37.6186 | 35.4482 | 33.31 | 38.9217 | 38.9125 | 38.8949 | 38.8772 | 38.859 | 38.837 | 38.812 | 38.7864 | 38.7589 | 38.6821 | 36.7288 | 34.5717 | 32.4465
|  | DOWN GRANGE | CT |  |  | 39.1305 | 39.1305 | 39.1305 | 39.1305 | 39.1305 | 39.1305 | 39.1305 | 39.1305 | 39.1305 | 39.1305 | 37.6266 | 35.7204 | 33.8428 | 40.6976 | 40.6854 | 40.6622 | 40.6389 | 40.6148 | 40.5905 | 40.5575 | 40.5237 | 40.4874 | 39.7133 | 37.6753 | 35.5052 | 33.3676 | 38.9217 | 38.9125 | 38.8949 | 38.8772 | 38.859 | 38.8406 | 38.8156 | 38.79 | 38.7624 | 38.6857 | 36.7852 | 34.6283 | 32.5037
|  | DOWN GRANGE | LW |  |  | 39.1305 | 39.1305 | 39.1305 | 39.1305 | 39.1305 | 39.1305 | 39.1305 | 39.1305 | 39.1305 | 39.1305 | 37.5768 | 35.6704 | 33.7922 | 40.6982 | 40.6864 | 40.6639 | 40.6413 | 40.6179 | 40.5858 | 40.5528 | 40.519 | 40.4827 | 39.6557 | 37.6186 | 35.4482 | 33.31 | 38.9222 | 38.9132 | 38.8962 | 38.879 | 38.8613 | 38.837 | 38.812 | 38.7864 | 38.7589 | 38.6821 | 36.7288 | 34.5717 | 32.4465
|  | DOWN GRANGE | ST |  |  | 39.1305 | 39.1305 | 39.1305 | 39.1305 | 39.1305 | 39.1305 | 39.1305 | 39.1305 | 39.1305 | 39.1305 | 39.1305 | 38.204 | 36.9925 | 40.7043 | 40.6971 | 40.6857 | 40.6717 | 40.6547 | 40.6369 | 40.6185 | 40.5955 | 40.5706 | 40.5014 | 39.7423 | 38.3326 | 36.9534 | 38.9268 | 38.9213 | 38.9127 | 38.9021 | 38.8893 | 38.8757 | 38.8618 | 38.8443 | 38.8255 | 38.7731 | 38.6875 | 37.4385 | 36.0677
|  | DOWN GRANGE | FS |  |  | 39.1305 | 39.1305 | 39.1305 | 39.1305 | 39.1305 | 39.1305 | 39.1305 | 39.1305 | 39.1305 | 39.1305 | 39.1305 | 39.1305 | 39.1305 | 40.714 | 40.7121 | 40.7102 | 40.706 | 40.701 | 40.6947 | 40.6882 | 40.6802 | 40.6705 | 40.6435 | 40.5993 | 40.5532 | 40.5081 | 38.9342 | 38.9327 | 38.9313 | 38.9281 | 38.9243 | 38.9195 | 38.9146 | 38.9086 | 38.9012 | 38.8808 | 38.8472 | 38.8123 | 38.7782
MINETY GSP | STRATTON (2 X 90) | DRAKES WAY | MINIMUM HEADROOM | SU 16899 85647 | YES | 21.2819 | 21.2819 | 21.2819 | 21.2819 | 21.2819 | 21.2819 | 21.2819 | 21.2819 | 21.2819 | 21.2819 | 21.2819 | 21.1875 | 20.5602 | 18.9373 | 18.9368 | 18.9358 | 18.9348 | 18.9337 | 18.9309 | 18.9281 | 18.9252 | 18.9222 | 18.912 | 18.8847 | 18.85 | 18.8149 | 20.7158 | 20.7151 | 20.7139 | 20.7126 | 20.7113 | 20.7077 | 20.7041 | 20.7005 | 20.6966 | 20.6838 | 20.3755 | 19.6564 | 18.9297
|  | DRAKES WAY | CT |  |  | 21.2819 | 21.2819 | 21.2819 | 21.2819 | 21.2819 | 21.2819 | 21.2819 | 21.2819 | 21.2819 | 21.2819 | 21.2819 | 21.2182 | 20.5909 | 18.9373 | 18.9368 | 18.9358 | 18.9348 | 18.9337 | 18.9327 | 18.9298 | 18.9269 | 18.9239 | 18.9137 | 18.8864 | 18.8517 | 18.8166 | 20.7158 | 20.7151 | 20.7139 | 20.7126 | 20.7113 | 20.7099 | 20.7063 | 20.7027 | 20.6988 | 20.686 | 20.4109 | 19.6918 | 18.9652
|  | DRAKES WAY | LW |  |  | 21.2819 | 21.2819 | 21.2819 | 21.2819 | 21.2819 | 21.2819 | 21.2819 | 21.2819 | 21.2819 | 21.2819 | 21.2819 | 21.1875 | 20.5602 | 18.9373 | 18.9368 | 18.9358 | 18.9348 | 18.9337 | 18.9309 | 18.9281 | 18.9252 | 18.9222 | 18.912 | 18.8847 | 18.85 | 18.8149 | 20.7158 | 20.7151 | 20.7139 | 20.7126 | 20.7113 | 20.7077 | 20.7041 | 20.7005 | 20.6966 | 20.6838 | 20.3755 | 19.6564 | 18.9297
|  | DRAKES WAY | ST |  |  | 21.2819 | 21.2819 | 21.2819 | 21.2819 | 21.2819 | 21.2819 | 21.2819 | 21.2819 | 21.2819 | 21.2819 | 21.2819 | 21.2819 | 21.2819 | 18.9376 | 18.9373 | 18.9368 | 18.9362 | 18.9354 | 18.934 | 18.9325 | 18.9306 | 18.9285 | 18.9215 | 18.9025 | 18.8795 | 18.8573 | 20.7162 | 20.7157 | 20.7151 | 20.7143 | 20.7134 | 20.7116 | 20.7098 | 20.7073 | 20.7047 | 20.6958 | 20.6351 | 20.268 | 19.8074
|  | DRAKES WAY | FS |  |  | 21.2819 | 21.2819 | 21.2819 | 21.2819 | 21.2819 | 21.2819 | 21.2819 | 21.2819 | 21.2819 | 21.2819 | 21.2819 | 21.2819 | 21.2819 | 18.9379 | 18.9378 | 18.9377 | 18.9374 | 18.9372 | 18.9367 | 18.9362 | 18.9357 | 18.9349 | 18.9321 | 18.9243 | 18.9135 | 18.902 | 20.7166 | 20.7164 | 20.7163 | 20.716 | 20.7156 | 20.715 | 20.7144 | 20.7137 | 20.7127 | 20.7092 | 20.6993 | 20.6857 | 20.6287
NURSLING GSP | WINCHESTER | DUNBRIDGE | MINIMUM HEADROOM | SU 31520 26244 | YES | 12.5488 | 12.5488 | 12.5488 | 12.4752 | 12.3822 | 12.267 | 12.129 | 11.8959 | 11.8603 | 11.7106 | 11.4072 | 10.5773 | 10.1305 | 11.1132 | 11.0436 | 10.8965 | 10.7182 | 10.4948 | 10.2883 | 10.0597 | 9.7368 | 9.6045 | 9.169 | 8.3941 | 7.3236 | 6.8058 | 12.0493 | 12.0493 | 12.0493 | 11.9757 | 11.8826 | 11.7675 | 11.6295 | 11.3963 | 11.3608 | 11.2111 | 10.877 | 9.8421 | 9.3356
|  | DUNBRIDGE | CT |  |  | 12.5488 | 12.5488 | 12.5488 | 12.5438 | 12.5344 | 12.5204 | 12.5 | 12.4598 | 12.4532 | 12.4209 | 12.1713 | 11.5676 | 11.0834 | 11.1132 | 11.0436 | 10.8965 | 10.7487 | 10.5978 | 10.4438 | 10.333 | 10.203 | 10.0996 | 9.7816 | 9.0604 | 8.2995 | 7.7442 | 12.0493 | 12.0493 | 12.0493 | 12.0443 | 12.0348 | 12.0208 | 12.0005 | 11.9603 | 11.9537 | 11.9214 | 11.5504 | 10.8235 | 10.2753
|  | DUNBRIDGE | LW |  |  | 12.5488 | 12.5488 | 12.5488 | 12.4752 | 12.3822 | 12.267 | 12.129 | 11.8959 | 11.8603 | 11.7106 | 11.4072 | 10.5773 | 10.1305 | 11.1231 | 11.059 | 10.9233 | 10.7182 | 10.4948 | 10.2883 | 10.0597 | 9.7368 | 9.6045 | 9.169 | 8.3941 | 7.3236 | 6.8058 | 12.0493 | 12.0493 | 12.0493 | 11.9757 | 11.8826 | 11.7675 | 11.6295 | 11.3963 | 11.3608 | 11.2111 | 10.877 | 9.8421 | 9.3356
|  | DUNBRIDGE | ST |  |  | 12.5488 | 12.5488 | 12.5488 | 12.5346 | 12.5168 | 12.4952 | 12.4681 | 12.4194 | 12.3998 | 12.3135 | 12.215 | 11.8836 | 11.7735 | 11.2037 | 11.1865 | 11.1568 | 11.1063 | 11.0446 | 10.952 | 10.855 | 10.7449 | 10.6593 | 10.3805 | 9.9684 | 9.3232 | 8.9017 | 12.0493 | 12.0493 | 12.0493 | 12.0351 | 12.0173 | 11.9956 | 11.9686 | 11.9199 | 11.9002 | 11.814 | 11.7154 | 11.3841 | 11.274
|  | DUNBRIDGE | FS |  |  | 12.5488 | 12.5488 | 12.5488 | 12.5437 | 12.5385 | 12.533 | 12.5272 | 12.5177 | 12.4892 | 12.3814 | 12.3177 | 12.0667 | 11.8363 | 11.2985 | 11.2214 | 11.2173 | 11.1935 | 11.1663 | 11.1362 | 11.106 | 11.0648 | 11.0107 | 10.8288 | 10.6466 | 10.2818 | 9.9441 | 12.0493 | 12.0493 | 12.0493 | 12.0442 | 12.039 | 12.0335 | 12.0277 | 12.0181 | 11.9897 | 11.8819 | 11.8182 | 11.5672 | 11.3368
EALING GSP | EALING 22kV | EALING 11kV | MINIMUM HEADROOM | SZ 06789 95116 | YES | 61.9515 | 61.9515 | 61.9515 | 61.9353 | 61.9186 | 61.9011 | 61.883 | 61.8555 | 61.8517 | 61.8386 | 61.8171 | 61.2287 | 59.1367 | 57.0201 | 56.8807 | 56.6019 | 56.3268 | 56.014 | 55.1698 | 54.7912 | 54.4611 | 54.1453 | 53.1998 | 51.1656 | 48.7219 | 46.2636 | 58.9076 | 58.8802 | 58.83 | 58.7804 | 58.7223 | 58.3918 | 58.0539 | 57.7593 | 57.4774 | 56.6336 | 54.6837 | 52.2852 | 49.8756
|  | EALING 11kV | CT |  |  | 61.9515 | 61.9515 | 61.9515 | 61.9515 | 61.9515 | 61.9515 | 61.9515 | 61.9515 | 61.9515 | 61.9515 | 61.9515 | 61.2287 | 59.1367 | 57.0201 | 56.8807 | 56.6019 | 56.3268 | 56.014 | 55.1698 | 54.7912 | 54.4611 | 54.1453 | 53.1998 | 51.1656 | 48.7219 | 46.2636 | 58.9076 | 58.8802 | 58.83 | 58.7804 | 58.7295 | 58.3918 | 58.0539 | 57.7593 | 57.4774 | 56.6336 | 54.6837 | 52.2852 | 49.8756
|  | EALING 11kV | LW |  |  | 61.9515 | 61.9515 | 61.9515 | 61.9353 | 61.9186 | 61.9011 | 61.883 | 61.8555 | 61.8517 | 61.8386 | 61.8171 | 61.7679 | 59.7707 | 57.0395 | 56.9254 | 56.6802 | 56.4213 | 56.1545 | 56.0195 | 55.6441 | 55.2865 | 54.9669 | 54.0084 | 51.9526 | 49.5023 | 47.0412 | 58.9128 | 58.8883 | 58.8441 | 58.7841 | 58.7223 | 58.6836 | 58.6431 | 58.4856 | 58.2 | 57.3432 | 55.4821 | 53.0344 | 50.653
|  | EALING 11kV | ST |  |  | 61.9515 | 61.9515 | 61.9515 | 61.9515 | 61.9515 | 61.9515 | 61.9515 | 61.9515 | 61.9515 | 61.9515 | 61.9515 | 61.9515 | 61.9515 | 57.1133 | 57.0711 | 57.0126 | 56.9157 | 56.7873 | 56.6809 | 56.5704 | 56.4969 | 56.4258 | 56.2127 | 55.1225 | 53.5658 | 52.0675 | 58.9326 | 58.9213 | 58.9055 | 58.8866 | 58.8634 | 58.8442 | 58.8243 | 58.811 | 58.7982 | 58.7598 | 58.3496 | 56.9603 | 55.5966
|  | EALING 11kV | FS |  |  | 61.9515 | 61.9515 | 61.9515 | 61.9515 | 61.9515 | 61.9515 | 61.9515 | 61.9515 | 61.9515 | 61.9515 | 61.9515 | 61.9515 | 61.9515 | 57.154 | 57.1383 | 57.1251 | 57.0937 | 57.0567 | 57.0285 | 56.9996 | 56.9549 | 56.9273 | 56.8446 | 56.6575 | 56.4308 | 56.1975 | 58.9436 | 58.9394 | 58.9358 | 58.9274 | 58.9174 | 58.9098 | 58.902 | 58.8936 | 58.8887 | 58.8737 | 58.84 | 58.7991 | 58.7571
MANNINGTON GSP | REDHILL BSP | EAST HOWE | MINIMUM HEADROOM | SZ 06789 95116 | YES | 37.3664 | 37.3664 | 37.3664 | 37.3664 | 37.3664 | 37.3664 | 37.3664 | 37.3664 | 37.3664 | 37.3664 | 37.3664 | 36.8043 | 35.2351 | 34.6868 | 34.6837 | 34.6789 | 34.6735 | 34.6675 | 34.6517 | 34.6353 | 34.6183 | 34.601 | 34.5547 | 33.7131 | 31.9061 | 30.0768 | 35.686 | 35.686 | 35.686 | 35.686 | 35.686 | 35.686 | 35.686 | 35.686 | 35.5714 | 34.7476 | 33.1102 | 31.2461 | 29.3943
|  | EAST HOWE | CT |  |  | 37.3664 | 37.3664 | 37.3664 | 37.3664 | 37.3664 | 37.3664 | 37.3664 | 37.3664 | 37.3664 | 37.3664 | 37.3664 | 36.961 | 35.3923 | 34.687 | 34.684 | 34.6793 | 34.6742 | 34.6683 | 34.6621 | 34.6457 | 34.6287 | 34.6115 | 34.5651 | 33.8922 | 32.0855 | 30.2623 | 35.686 | 35.686 | 35.686 | 35.686 | 35.686 | 35.686 | 35.686 | 35.686 | 35.686 | 34.9328 | 33.295 | 31.4311 | 29.5798
|  | EAST HOWE | LW |  |  | 37.3664 | 37.3664 | 37.3664 | 37.3664 | 37.3664 | 37.3664 | 37.3664 | 37.3664 | 37.3664 | 37.3664 | 37.3664 | 36.8043 | 35.2351 | 34.6868 | 34.6837 | 34.6789 | 34.6735 | 34.6675 | 34.6517 | 34.6353 | 34.6183 | 34.601 | 34.5547 | 33.7131 | 31.9061 | 30.0768 | 35.686 | 35.686 | 35.686 | 35.686 | 35.686 | 35.686 | 35.686 | 35.686 | 35.5714 | 34.7476 | 33.1102 | 31.2461 | 29.3943
|  | EAST HOWE | ST |  |  | 37.3664 | 37.3664 | 37.3664 | 37.3664 | 37.3664 | 37.3664 | 37.3664 | 37.3664 | 37.3664 | 37.3664 | 37.3664 | 37.3664 | 37.3664 | 34.6883 | 34.6862 | 34.6833 | 34.6798 | 34.6754 | 34.665 | 34.6542 | 34.6426 | 34.6309 | 34.5991 | 34.536 | 33.7964 | 32.6473 | 35.686 | 35.686 | 35.686 | 35.686 | 35.686 | 35.686 | 35.686 | 35.686 | 35.686 | 35.5377 | 34.4167 | 33.1961 | 32.0107
|  | EAST HOWE | FS |  |  | 37.3664 | 37.3664 | 37.3664 | 37.3664 | 37.3664 | 37.3664 | 37.3664 | 37.3664 | 37.3664 | 37.3664 | 37.3664 | 37.3664 | 37.3664 | 34.6903 | 34.6894 | 34.6884 | 34.687 | 34.6854 | 34.6822 | 34.6789 | 34.6749 | 34.6703 | 34.6579 | 34.6326 | 34.6031 | 34.5731 | 35.686 | 35.686 | 35.686 | 35.686 | 35.686 | 35.686 | 35.686 | 35.686 | 35.686 | 35.686 | 35.686 | 35.6087 | 35.0746
MELKSHAM GSP | NORRINGTON | EASTERTON | MINIMUM HEADROOM | SU 01568 54730 | YES | 23.0394 | 23.0167 | 22.9685 | 22.9207 | 22.8723 | 22.8163 | 22.7224 | 22.6127 | 22.5243 | 22.2515 | 21.7817 | 21.2328 | 20.8198 | 20.5251 | 20.4976 | 20.4396 | 20.3822 | 20.3243 | 20.2609 | 20.1512 | 20.0257 | 19.9204 | 19.5976 | 19.046 | 18.4128 | 17.917 | 21.6316 | 21.6062 | 21.5524 | 21.4991 | 21.4453 | 21.385 | 21.2821 | 21.1634 | 21.0654 | 20.764 | 20.2474 | 19.6503 | 19.19
|  | EASTERTON | CT |  |  | 23.0394 | 23.0167 | 22.9685 | 22.9207 | 22.8723 | 22.8234 | 22.7416 | 22.6549 | 22.5704 | 22.3173 | 21.8394 | 21.3411 | 20.9107 | 20.5251 | 20.4976 | 20.4396 | 20.3822 | 20.3243 | 20.266 | 20.1683 | 20.0659 | 19.9644 | 19.6614 | 19.1017 | 18.5191 | 18.0061 | 21.6316 | 21.6062 | 21.5524 | 21.4991 | 21.4453 | 21.391 | 21.3001 | 21.2045 | 21.1102 | 20.8286 | 20.304 | 19.7575 | 19.2799
|  | EASTERTON | LW |  |  | 23.0475 | 23.0298 | 22.9915 | 22.9507 | 22.9063 | 22.8163 | 22.7224 | 22.6127 | 22.5243 | 22.2515 | 21.7817 | 21.2328 | 20.8198 | 20.5352 | 20.5134 | 20.4673 | 20.4189 | 20.3669 | 20.2609 | 20.1512 | 20.0257 | 19.9204 | 19.5976 | 19.046 | 18.4128 | 17.917 | 21.6411 | 21.6209 | 21.5781 | 21.5329 | 21.4842 | 21.385 | 21.2821 | 21.1634 | 21.0654 | 20.764 | 20.2474 | 19.6503 | 19.19
|  | EASTERTON | ST |  |  | 23.0692 | 23.0648 | 23.0572 | 23.0471 | 23.0339 | 22.9904 | 22.9466 | 22.8864 | 22.8263 | 22.6422 | 22.3507 | 21.9946 | 21.6985 | 20.5631 | 20.5574 | 20.5476 | 20.5349 | 20.5189 | 20.467 | 20.4149 | 20.344 | 20.2723 | 20.0545 | 19.7085 | 19.2981 | 18.9481 | 21.6669 | 21.6616 | 21.6526 | 21.6407 | 21.6257 | 21.5775 | 21.5289 | 21.4626 | 21.3959 | 21.1925 | 20.8699 | 20.4827 | 20.1558
|  | EASTERTON | FS |  |  | 23.0741 | 23.0727 | 23.0715 | 23.0657 | 23.0494 | 23.0266 | 23.003 | 22.9696 | 22.9047 | 22.7014 | 22.5325 | 22.2112 | 21.9286 | 20.5693 | 20.5676 | 20.566 | 20.5586 | 20.5404 | 20.5138 | 20.4871 | 20.45 | 20.3805 | 20.1642 | 19.9747 | 19.6339 | 19.3328 | 21.6727 | 21.6711 | 21.6696 | 21.6627 | 21.6452 | 21.6198 | 21.5944 | 21.5588 | 21.4913 | 21.2806 | 21.0999 | 20.7675 | 20.4743
BRAMLEY (FLEE) | BRACKNELL RESERVE | EASTHAMPSTEAD | MINIMUM HEADROOM | SU 86148 67194 | YES | 45.4721 | 45.4721 | 45.4721 | 45.4537 | 45.4349 | 45.4155 | 45.3953 | 45.3635 | 45.3525 | 45.3158 | 45.284 | 45.164 | 43.8187 | 42.4482 | 42.4482 | 42.4482 | 42.4298 | 42.411 | 42.3916 | 42.3714 | 42.3396 | 42.3286 | 42.2919 | 42.0476 | 40.3433 | 38.6836 | 44.0216 | 44.0216 | 44.0216 | 44.0032 | 43.9844 | 43.965 | 43.9448 | 43.913 | 43.902 | 43.8653 | 43.8335 | 42.2304 | 40.5633
|  | EASTHAMPSTEAD | CT |  |  | 45.4721 | 45.4721 | 45.4721 | 45.4719 | 45.4715 | 45.4709 | 45.47 | 45.468 | 45.4676 | 45.4657 | 45.45 | 45.4324 | 44.0856 | 42.4482 | 42.4482 | 42.4482 | 42.448 | 42.4476 | 42.4469 | 42.446 | 42.444 | 42.4437 | 42.4418 | 42.3432 | 40.6492 | 38.9862 | 44.0216 | 44.0216 | 44.0216 | 44.0214 | 44.021 | 44.0204 | 44.0195 | 44.0175 | 44.0171 | 44.0152 | 43.9995 | 42.5376 | 40.8672
|  | EASTHAMPSTEAD | LW |  |  | 45.4721 | 45.4721 | 45.4721 | 45.4714 | 45.4699 | 45.4675 | 45.4642 | 45.4576 | 45.4565 | 45.4507 | 45.4365 | 45.2697 | 43.8187 | 42.4482 | 42.4482 | 42.4482 | 42.4475 | 42.446 | 42.4436 | 42.4403 | 42.4337 | 42.4326 | 42.4267 | 42.0476 | 40.3433 | 38.6836 | 44.0216 | 44.0216 | 44.0216 | 44.0209 | 44.0194 | 44.017 | 44.0137 | 44.0071 | 44.006 | 44.0002 | 43.9305 | 42.2304 | 40.5633
|  | EASTHAMPSTEAD | ST |  |  | 45.4721 | 45.4721 | 45.4721 | 45.4537 | 45.4349 | 45.4155 | 45.3953 | 45.3635 | 45.3525 | 45.3158 | 45.284 | 45.1766 | 45.1427 | 42.4482 | 42.4482 | 42.4482 | 42.4298 | 42.411 | 42.3916 | 42.3714 | 42.3396 | 42.3286 | 42.2919 | 42.2601 | 42.0736 | 40.9687 | 44.0216 | 44.0216 | 44.0216 | 44.0032 | 43.9844 | 43.965 | 43.9448 | 43.913 | 43.902 | 43.8653 | 43.8335 | 43.7261 | 42.8564
|  | EASTHAMPSTEAD | FS |  |  | 45.4721 | 45.4721 | 45.4721 | 45.4662 | 45.4604 | 45.4546 | 45.4487 | 45.4394 | 45.4136 | 45.331 | 45.2912 | 45.164 | 45.0568 | 42.4482 | 42.4482 | 42.4482 | 42.4423 | 42.4365 | 42.4307 | 42.4248 | 42.4155 | 42.3897 | 42.307 | 42.2672 | 42.14 | 42.0329 | 44.0216 | 44.0216 | 44.0216 | 44.0157 | 44.0099 | 44.0041 | 43.9982 | 43.9889 | 43.9631 | 43.8805 | 43.8407 | 43.7135 | 43.6063
NURSLING GSP | VELMORE BSP | EASTLEIGH NORTH | MINIMUM HEADROOM | SU 45426 18958 | YES | 61.5598 | 61.5598 | 61.5598 | 61.5152 | 61.4696 | 61.423 | 61.3739 | 61.2973 | 61.2874 | 61.2546 | 61.0924 | 60.9222 | 60.5257 | 57.4646 | 57.4568 | 57.4442 | 57.3898 | 57.3319 | 57.2728 | 57.2042 | 57.1086 | 57.0786 | 56.9908 | 55.2537 | 53.1328 | 51.179 | 59.7504 | 59.7504 | 59.7504 | 59.7059 | 59.6603 | 59.6137 | 59.5646 | 59.4879 | 59.4781 | 59.4452 | 59.2831 | 59.1129 | 59.0698
|  | EASTLEIGH NORTH | CT |  |  | 61.5598 | 61.5598 | 61.5598 | 61.5152 | 61.4696 | 61.423 | 61.3739 | 61.2973 | 61.2874 | 61.2546 | 61.0924 | 60.9222 | 60.5257 | 57.4653 | 57.458 | 57.4463 | 57.3898 | 57.3319 | 57.2728 | 57.2042 | 57.1086 | 57.0786 | 56.9908 | 55.2537 | 53.1328 | 51.179 | 59.7504 | 59.7504 | 59.7504 | 59.7059 | 59.6603 | 59.6137 | 59.5646 | 59.4879 | 59.4781 | 59.4452 | 59.2831 | 59.1129 | 59.0698
|  | EASTLEIGH NORTH | LW |  |  | 61.5598 | 61.5598 | 61.5598 | 61.5587 | 61.5564 | 61.5528 | 61.5478 | 61.5377 | 61.536 | 61.5272 | 61.5057 | 61.4637 | 60.8811 | 57.4646 | 57.4568 | 57.4442 | 57.4303 | 57.4149 | 57.3896 | 57.3651 | 57.3361 | 57.3142 | 57.2504 | 55.4036 | 53.4055 | 51.4911 | 59.7504 | 59.7504 | 59.7504 | 59.7493 | 59.747 | 59.7434 | 59.7384 | 59.7284 | 59.7267 | 59.7178 | 59.6963 | 59.6544 | 59.6515
|  | EASTLEIGH NORTH | ST |  |  | 61.5598 | 61.5598 | 61.5598 | 61.5595 | 61.5591 | 61.5584 | 61.5573 | 61.555 | 61.5539 | 61.5478 | 61.5399 | 61.5122 | 61.5021 | 57.471 | 57.4612 | 57.4535 | 57.4443 | 57.4335 | 57.4194 | 57.4063 | 57.3911 | 57.3762 | 57.3329 | 57.2631 | 56.0326 | 54.8075 | 59.7504 | 59.7504 | 59.7504 | 59.7502 | 59.7497 | 59.749 | 59.748 | 59.7456 | 59.7445 | 59.7385 | 59.7306 | 59.7028 | 59.6927
|  | EASTLEIGH NORTH | FS |  |  | 61.5598 | 61.5598 | 61.5598 | 61.5598 | 61.5598 | 61.5597 | 61.5597 | 61.5596 | 61.5592 | 61.557 | 61.5553 | 61.547 | 61.5389 | 57.476 | 57.4739 | 57.4717 | 57.4685 | 57.465 | 57.4603 | 57.4563 | 57.4515 | 57.4458 | 57.4291 | 57.4035 | 57.3718 | 57.3417 | 59.7504 | 59.7504 | 59.7504 | 59.7504 | 59.7504 | 59.7504 | 59.7503 | 59.7502 | 59.7499 | 59.7477 | 59.746 | 59.7377 | 59.7296
LOVEDEAN GSP | PORTSMOUTH BSP | EASTNEY | MINIMUM HEADROOM | SZ 66357 99040 | YES | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.2801 | 21.1452 | 20.0022 | 21.8338 | 21.8327 | 21.831 | 21.8289 | 21.8264 | 21.8208 | 21.8148 | 21.8088 | 21.8023 | 21.7815 | 21.0796 | 19.7697 | 18.4505 | 21.7295 | 21.7277 | 21.7248 | 21.7213 | 21.717 | 21.7078 | 21.6977 | 21.6876 | 21.6768 | 21.6419 | 21.4518 | 20.1372 | 18.8133
|  | EASTNEY | CT |  |  | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.3826 | 21.2478 | 20.1051 | 21.8344 | 21.8335 | 21.8319 | 21.8302 | 21.8284 | 21.8266 | 21.8206 | 21.8145 | 21.8081 | 21.7872 | 21.1979 | 19.8881 | 18.5692 | 21.7305 | 21.729 | 21.7263 | 21.7235 | 21.7204 | 21.7174 | 21.7073 | 21.6972 | 21.6864 | 21.6515 | 21.5657 | 20.256 | 18.9324
|  | EASTNEY | LW |  |  | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.2801 | 21.1452 | 20.0022 | 21.8341 | 21.833 | 21.831 | 21.829 | 21.8268 | 21.8208 | 21.8148 | 21.8088 | 21.8023 | 21.7815 | 21.0796 | 19.7697 | 18.4505 | 21.73 | 21.7281 | 21.7248 | 21.7214 | 21.7178 | 21.7078 | 21.6977 | 21.6876 | 21.6768 | 21.6419 | 21.4518 | 20.1372 | 18.8133
|  | EASTNEY | ST |  |  | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.0512 | 21.3245 | 21.8338 | 21.8327 | 21.831 | 21.8289 | 21.8264 | 21.822 | 21.8176 | 21.8135 | 21.8091 | 21.7948 | 21.6682 | 20.8153 | 19.9766 | 21.7295 | 21.7277 | 21.7248 | 21.7213 | 21.717 | 21.7097 | 21.7024 | 21.6955 | 21.6881 | 21.6642 | 21.6047 | 21.1866 | 20.3449
|  | EASTNEY | FS |  |  | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 21.8354 | 21.8352 | 21.835 | 21.8345 | 21.834 | 21.8325 | 21.831 | 21.8292 | 21.8275 | 21.8219 | 21.8073 | 21.7882 | 21.768 | 21.7322 | 21.7318 | 21.7314 | 21.7307 | 21.7298 | 21.7273 | 21.7248 | 21.7217 | 21.7188 | 21.7095 | 21.6851 | 21.6532 | 21.6194
LALEHAM | STAINES | EGHAM | MINIMUM HEADROOM | TQ 01030 71404 | YES | 48.9841 | 48.9841 | 48.9841 | 48.9832 | 48.9814 | 48.9785 | 48.9745 | 48.9665 | 48.9651 | 48.9581 | 48.9409 | 48.9039 | 48.1838 | 45.6282 | 45.6169 | 45.5993 | 45.5807 | 45.5607 | 45.5401 | 45.522 | 45.5002 | 45.4852 | 45.439 | 45.3234 | 44.2317 | 43.2013 | 46.9305 | 46.9305 | 46.9305 | 46.9296 | 46.9278 | 46.9249 | 46.9209 | 46.7968 | 46.563 | 45.8909 | 44.7671 | 43.6623 | 42.6193
|  | EGHAM | CT |  |  | 48.9841 | 48.9841 | 48.9841 | 48.9838 | 48.9833 | 48.9826 | 48.9815 | 48.9791 | 48.9786 | 48.9763 | 48.9573 | 48.9273 | 48.1838 | 45.6282 | 45.6169 | 45.5993 | 45.5807 | 45.5607 | 45.5401 | 45.5249 | 45.5087 | 45.4946 | 45.4532 | 45.3234 | 44.2317 | 43.2013 | 46.9305 | 46.9305 | 46.9305 | 46.9302 | 46.9297 | 46.929 | 46.9279 | 46.7968 | 46.563 | 45.8909 | 44.7671 | 43.6623 | 42.6193
|  | EGHAM | LW |  |  | 48.9841 | 48.9841 | 48.9841 | 48.9832 | 48.9814 | 48.9785 | 48.9745 | 48.9665 | 48.9651 | 48.9581 | 48.9409 | 48.9039 | 48.2211 | 45.6289 | 45.6179 | 45.6011 | 45.5826 | 45.562 | 45.5402 | 45.522 | 45.5002 | 45.4852 | 45.439 | 45.3573 | 44.2723 | 43.2458 | 46.9305 | 46.9305 | 46.9305 | 46.9296 | 46.9278 | 46.9249 | 46.9209 | 46.8542 | 46.6196 | 45.9425 | 44.8209 | 43.7037 | 42.6647
|  | EGHAM | ST |  |  | 48.9841 | 48.9841 | 48.9841 | 48.9839 | 48.9835 | 48.983 | 48.9821 | 48.9803 | 48.9794 | 48.9746 | 48.9683 | 48.9461 | 48.9381 | 45.6358 | 45.6296 | 45.6222 | 45.6127 | 45.6014 | 45.5868 | 45.5753 | 45.564 | 45.5538 | 45.5224 | 45.4726 | 45.4096 | 45.3623 | 46.9305 | 46.9305 | 46.9305 | 46.9303 | 46.9299 | 46.9294 | 46.9285 | 46.9267 | 46.9258 | 46.921 | 46.3539 | 45.6313 | 44.9512
|  | EGHAM | FS |  |  | 48.9841 | 48.9841 | 48.9841 | 48.9841 | 48.9841 | 48.9841 | 48.984 | 48.984 | 48.9836 | 48.9819 | 48.9805 | 48.9739 | 48.9675 | 45.6407 | 45.6377 | 45.6352 | 45.6311 | 45.6264 | 45.6209 | 45.617 | 45.6122 | 45.6083 | 45.5963 | 45.5781 | 45.5561 | 45.5355 | 46.9305 | 46.9305 | 46.9305 | 46.9305 | 46.9305 | 46.9305 | 46.9304 | 46.9303 | 46.93 | 46.9283 | 46.9269 | 46.9203 | 46.9139
MANNINGTON GSP | BOURNEMOUTH | ELECTRIC HOUSE | MINIMUM HEADROOM | SZ 08757 91379 | YES | 40.3248 | 40.3178 | 40.3057 | 40.2755 | 40.2474 | 40.2198 | 40.1909 | 40.1518 | 40.1378 | 40.0932 | 39.9878 | 38.9128 | 37.869 | 37.1464 | 37.1094 | 37.0451 | 36.9546 | 36.8779 | 36.8067 | 36.7313 | 36.6425 | 36.5846 | 36.399 | 35.6327 | 34.4117 | 33.2237 | 38.7601 | 38.7531 | 38.7411 | 38.676 | 38.5904 | 38.5113 | 38.4273 | 38.3295 | 38.2636 | 38.0582 | 37.5571 | 36.3917 | 35.1663
|  | ELECTRIC HOUSE | CT |  |  | 40.3252 | 40.3184 | 40.3067 | 40.2931 | 40.2822 | 40.2709 | 40.2601 | 40.2485 | 40.2383 | 40.2067 | 40.125 | 39.0899 | 38.0489 | 37.1483 | 37.1124 | 37.0504 | 36.9783 | 36.9205 | 36.8605 | 36.8032 | 36.7418 | 36.6878 | 36.517 | 35.7727 | 34.5897 | 33.4045 | 38.7604 | 38.7537 | 38.7421 | 38.7008 | 38.6344 | 38.5655 | 38.4997 | 38.4293 | 38.3673 | 38.175 | 37.6934 | 36.5699 | 35.3474
|  | ELECTRIC HOUSE | LW |  |  | 40.3248 | 40.3178 | 40.3057 | 40.2755 | 40.2474 | 40.2198 | 40.1909 | 40.1518 | 40.1378 | 40.0932 | 39.9878 | 38.9128 | 37.869 | 37.1464 | 37.1094 | 37.0451 | 36.9546 | 36.8779 | 36.8067 | 36.7313 | 36.6425 | 36.5846 | 36.399 | 35.6327 | 34.4117 | 33.2237 | 38.7601 | 38.7531 | 38.7411 | 38.676 | 38.5904 | 38.5113 | 38.4273 | 38.3295 | 38.2636 | 38.0582 | 37.5571 | 36.3917 | 35.1663
|  | ELECTRIC HOUSE | ST |  |  | 40.3382 | 40.3255 | 40.3202 | 40.3129 | 40.3065 | 40.2957 | 40.2844 | 40.2767 | 40.2697 | 40.248 | 40.1929 | 40.1281 | 39.4755 | 37.2174 | 37.1502 | 37.1222 | 37.0831 | 37.0493 | 36.9919 | 36.9324 | 36.8912 | 36.8543 | 36.7392 | 36.4058 | 35.7797 | 35.0286 | 38.7734 | 38.7608 | 38.7555 | 38.7482 | 38.7419 | 38.7164 | 38.6481 | 38.6007 | 38.5585 | 38.4263 | 38.0909 | 37.6969 | 37.0228
|  | ELECTRIC HOUSE | FS |  |  | 40.3412 | 40.3307 | 40.329 | 40.3242 | 40.3203 | 40.3149 | 40.3095 | 40.3022 | 40.2933 | 40.2653 | 40.2332 | 40.1736 | 40.1171 | 37.2335 | 37.1775 | 37.1685 | 37.1494 | 37.1345 | 37.1123 | 37.0894 | 37.0606 | 37.0403 | 36.9763 | 36.8467 | 36.6579 | 36.4646 | 38.7764 | 38.7659 | 38.7642 | 38.7595 | 38.7555 | 38.7502 | 38.7448 | 38.7376 | 38.7287 | 38.7007 | 38.5561 | 38.3438 | 38.1255
BRAMLEY (FLEE) | WOKINGHAM BSP | ELMS ROAD | MINIMUM HEADROOM | SU 81057 68532 | YES | 38.2254 | 38.2123 | 37.4124 | 37.3053 | 37.1963 | 37.0847 | 36.9707 | 36.8302 | 36.7934 | 36.0038 | 34.4143 | 32.8689 | 31.5277 | 35.224 | 35.183 | 34.3525 | 34.1242 | 33.3011 | 32.8733 | 32.4332 | 31.9449 | 31.5983 | 30.6074 | 28.8059 | 27.0668 | 25.5335 | 36.7036 | 36.6905 | 35.8906 | 35.7743 | 35.6237 | 35.4936 | 35.3606 | 35.1827 | 34.8379 | 33.8524 | 32.0611 | 30.3531 | 28.8343
|  | ELMS ROAD | CT |  |  | 38.2936 | 38.2857 | 37.8058 | 37.7262 | 37.6457 | 37.5645 | 37.4811 | 37.3734 | 37.1216 | 36.2815 | 34.4143 | 32.8689 | 31.5277 | 35.2924 | 35.2568 | 34.7463 | 34.5597 | 33.7696 | 32.9886 | 32.5792 | 32.1238 | 31.7894 | 30.8392 | 28.8059 | 27.0668 | 25.5335 | 36.7718 | 36.764 | 36.284 | 36.196 | 36.0742 | 35.9522 | 35.8171 | 35.3638 | 35.0313 | 34.0864 | 32.0611 | 30.3531 | 28.8343
|  | ELMS ROAD | LW |  |  | 38.2254 | 38.2123 | 37.4124 | 37.3053 | 37.1963 | 37.0847 | 36.9707 | 36.8302 | 36.7934 | 36.0038 | 34.6553 | 33.2581 | 31.9496 | 35.224 | 35.183 | 34.3525 | 34.1242 | 33.3011 | 32.8733 | 32.4332 | 31.9449 | 31.5983 | 30.6074 | 29.0927 | 27.509 | 26.0083 | 36.7036 | 36.6905 | 35.8906 | 35.7743 | 35.6237 | 35.4936 | 35.3606 | 35.1827 | 34.8379 | 33.8524 | 32.3458 | 30.7859 | 29.3135
|  | ELMS ROAD | ST |  |  | 38.3277 | 38.3224 | 38.0025 | 37.9761 | 37.9496 | 37.923 | 37.8962 | 37.8687 | 37.8575 | 37.8227 | 37.7658 | 37.1603 | 36.351 | 35.3338 | 35.3193 | 34.9835 | 34.9361 | 34.8846 | 34.8458 | 34.7773 | 34.5146 | 34.2915 | 33.6578 | 32.7087 | 31.7803 | 30.8636 | 36.8059 | 36.8007 | 36.4807 | 36.4544 | 36.4279 | 36.4012 | 36.3688 | 36.3275 | 36.3041 | 36.2343 | 35.9475 | 35.0245 | 34.113
|  | ELMS ROAD | FS |  |  | 38.3618 | 38.3591 | 38.1992 | 38.186 | 38.1729 | 38.1598 | 38.1467 | 38.1335 | 38.128 | 38.1111 | 38.0839 | 38.0635 | 38.0301 | 35.3824 | 35.3783 | 35.2166 | 35.1972 | 35.1769 | 35.1591 | 35.1413 | 35.1223 | 35.1131 | 35.0855 | 35.0424 | 35.0062 | 34.9577 | 36.84 | 36.8374 | 36.6774 | 36.6643 | 36.6512 | 36.638 | 36.6249 | 36.6117 | 36.6063 | 36.5893 | 36.5621 | 36.5418 | 36.5084
LOVEDEAN GSP | HAVANT | EMSWORTH | MINIMUM HEADROOM | SU 74861 05807 | YES | 16.6259 | 16.6259 | 16.6259 | 16.5312 | 16.435 | 16.3367 | 16.2352 | 16.0783 | 16.025 | 15.855 | 15.7183 | 15.2812 | 15.146 | 15.1472 | 15.1472 | 15.1472 | 15.0525 | 14.9563 | 14.8581 | 14.7566 | 14.5996 | 14.5463 | 14.3763 | 13.7824 | 12.6744 | 11.6161 | 15.8398 | 15.8398 | 15.8398 | 15.745 | 15.6488 | 15.5506 | 15.4491 | 15.2921 | 15.2389 | 15.0689 | 14.9321 | 14.4693 | 13.7138
|  | EMSWORTH | CT |  |  | 16.6259 | 16.6259 | 16.6259 | 16.6145 | 16.6029 | 16.5912 | 16.5789 | 16.56 | 16.5576 | 16.5498 | 16.512 | 16.3217 | 15.4084 | 15.1472 | 15.1472 | 15.1472 | 15.1358 | 15.1243 | 15.1125 | 15.1002 | 15.0813 | 15.0789 | 14.7903 | 13.7824 | 12.6744 | 11.6161 | 15.8398 | 15.8398 | 15.8398 | 15.8284 | 15.8168 | 15.805 | 15.7927 | 15.7738 | 15.7714 | 15.7637 | 15.6924 | 14.77 | 13.7138
|  | EMSWORTH | LW |  |  | 16.6259 | 16.6259 | 16.6259 | 16.6259 | 16.6259 | 16.6259 | 16.6259 | 16.6259 | 16.6259 | 16.6259 | 16.6259 | 16.5127 | 15.6097 | 15.1472 | 15.1472 | 15.1472 | 15.1472 | 15.1472 | 15.1472 | 15.1472 | 15.1472 | 15.1472 | 14.9027 | 13.9329 | 12.8704 | 11.8223 | 15.8398 | 15.8398 | 15.8398 | 15.8398 | 15.8398 | 15.8398 | 15.8398 | 15.8398 | 15.8398 | 15.8398 | 15.8084 | 14.9659 | 13.9199
|  | EMSWORTH | ST |  |  | 16.6259 | 16.6259 | 16.6259 | 16.5312 | 16.435 | 16.3367 | 16.2352 | 16.0783 | 16.025 | 15.855 | 15.7183 | 15.2812 | 15.146 | 15.1472 | 15.1472 | 15.1472 | 15.0525 | 14.9563 | 14.8581 | 14.7566 | 14.5996 | 14.5463 | 14.3763 | 13.8146 | 12.6859 | 11.8753 | 15.8398 | 15.8398 | 15.8398 | 15.745 | 15.6488 | 15.5506 | 15.4491 | 15.2921 | 15.2389 | 15.0689 | 14.9321 | 14.4693 | 13.9698
|  | EMSWORTH | FS |  |  | 16.6259 | 16.6259 | 16.6259 | 16.6247 | 16.6235 | 16.6224 | 16.6212 | 16.6193 | 16.6141 | 16.5977 | 16.5899 | 16.5653 | 16.5447 | 15.1472 | 15.1472 | 15.1472 | 15.146 | 15.1449 | 15.1437 | 15.1425 | 15.1406 | 15.1355 | 15.119 | 15.1112 | 15.0866 | 15.066 | 15.8398 | 15.8398 | 15.8398 | 15.8386 | 15.8374 | 15.8362 | 15.835 | 15.8332 | 15.828 | 15.8116 | 15.8038 | 15.7791 | 15.7585
MELKSHAM GSP | AMESBURY | ENFORD | MINIMUM HEADROOM | SU 13728 51712 | YES | 11.2664 | 11.2664 | 11.2664 | 11.2582 | 11.2498 | 11.2408 | 11.2313 | 11.2157 | 11.21 | 11.1892 | 11.1692 | 11.1026 | 11.0797 | 10.2086 | 10.2086 | 10.2086 | 10.2005 | 10.192 | 10.183 | 10.1735 | 10.1579 | 10.1522 | 10.1315 | 10.1114 | 10.0448 | 10.0219 | 10.9731 | 10.9706 | 10.9654 | 10.9591 | 10.948 | 10.9121 | 10.8715 | 10.8257 | 10.7864 | 10.6662 | 10.4605 | 10.2261 | 10.0379
|  | ENFORD | CT |  |  | 11.2664 | 11.2664 | 11.2664 | 11.266 | 11.2653 | 11.2643 | 11.2627 | 11.2594 | 11.2588 | 11.2556 | 11.2292 | 11.1998 | 11.1908 | 10.2086 | 10.2086 | 10.2086 | 10.2082 | 10.2075 | 10.2065 | 10.2049 | 10.2016 | 10.201 | 10.1978 | 10.1714 | 10.142 | 10.133 | 10.9731 | 10.9706 | 10.9654 | 10.9599 | 10.9542 | 10.9481 | 10.9115 | 10.8735 | 10.8355 | 10.7218 | 10.5133 | 10.2958 | 10.1017
|  | ENFORD | LW |  |  | 11.2664 | 11.2664 | 11.2664 | 11.2651 | 11.2626 | 11.2586 | 11.2531 | 11.242 | 11.2401 | 11.2304 | 11.2067 | 11.1604 | 11.1573 | 10.2086 | 10.2086 | 10.2086 | 10.2073 | 10.2048 | 10.2008 | 10.1953 | 10.1842 | 10.1823 | 10.1726 | 10.1489 | 10.1026 | 10.0995 | 10.9731 | 10.9706 | 10.9654 | 10.9591 | 10.9515 | 10.9121 | 10.8715 | 10.8257 | 10.7864 | 10.6662 | 10.4605 | 10.2261 | 10.0379
|  | ENFORD | ST |  |  | 11.2664 | 11.2664 | 11.2664 | 11.2582 | 11.2498 | 11.2408 | 11.2313 | 11.2157 | 11.21 | 11.1892 | 11.1692 | 11.1026 | 11.0797 | 10.2086 | 10.2086 | 10.2086 | 10.2005 | 10.192 | 10.183 | 10.1735 | 10.1579 | 10.1522 | 10.1315 | 10.1114 | 10.0448 | 10.0219 | 10.9747 | 10.9734 | 10.971 | 10.96 | 10.948 | 10.928 | 10.9075 | 10.8682 | 10.837 | 10.7418 | 10.6008 | 10.4131 | 10.2697
|  | ENFORD | FS |  |  | 11.2664 | 11.2664 | 11.2664 | 11.2664 | 11.2663 | 11.2663 | 11.2663 | 11.2661 | 11.2657 | 11.2633 | 11.2614 | 11.2523 | 11.2434 | 10.2086 | 10.2086 | 10.2086 | 10.2086 | 10.2085 | 10.2085 | 10.2085 | 10.2084 | 10.2079 | 10.2055 | 10.2036 | 10.1945 | 10.1856 | 10.977 | 10.9768 | 10.9766 | 10.9758 | 10.9748 | 10.971 | 10.9673 | 10.9623 | 10.952 | 10.9208 | 10.8729 | 10.8196 | 10.7692
COWLEY GSP | YARNTON BSP | EYNSHAM | MINIMUM HEADROOM | SP 42236 10266 | NO | 36.026 | 36.026 | 36.026 | 36.024 | 36.0199 | 36.0135 | 36.0047 | 35.9869 | 35.9719 | 35.1572 | 34.4694 | 33.9198 | 33.4515 | 34.1842 | 34.1842 | 34.1842 | 34.1823 | 33.8995 | 33.5596 | 33.1765 | 32.7886 | 32.3716 | 31.4021 | 30.5982 | 29.9584 | 29.4086 | 35.7308 | 35.7308 | 35.7308 | 35.7288 | 35.7247 | 35.7183 | 35.7095 | 35.6917 | 35.5058 | 34.5493 | 33.7556 | 33.1237 | 32.581
|  | EYNSHAM | CT |  |  | 36.026 | 36.026 | 36.026 | 36.0254 | 36.0242 | 36.0226 | 36.0202 | 36.0148 | 35.9719 | 35.1572 | 34.4694 | 33.9198 | 33.4515 | 34.1842 | 34.1842 | 34.1842 | 34.1836 | 33.8995 | 33.5596 | 33.1765 | 32.7886 | 32.3716 | 31.4021 | 30.5982 | 29.9584 | 29.4086 | 35.7308 | 35.7308 | 35.7308 | 35.7302 | 35.729 | 35.7274 | 35.725 | 35.7196 | 35.5058 | 34.5493 | 33.7556 | 33.1237 | 32.581
|  | EYNSHAM | LW |  |  | 36.026 | 36.026 | 36.026 | 36.024 | 36.0199 | 36.0135 | 36.0047 | 35.9869 | 35.9839 | 35.2015 | 34.5179 | 33.9414 | 33.4823 | 34.1842 | 34.1842 | 34.1842 | 34.1823 | 34.0049 | 33.6507 | 33.2611 | 32.8608 | 32.4416 | 31.4616 | 30.662 | 29.9952 | 29.4545 | 35.7308 | 35.7308 | 35.7308 | 35.7288 | 35.7247 | 35.7183 | 35.7095 | 35.6917 | 35.5746 | 34.6075 | 33.818 | 33.1591 | 32.6256
|  | EYNSHAM | ST |  |  | 36.026 | 36.026 | 36.026 | 36.0256 | 36.0247 | 36.0235 | 36.0216 | 36.0175 | 36.0155 | 36.0048 | 35.6314 | 35.258 | 34.9452 | 34.1842 | 34.1842 | 34.1842 | 34.1838 | 34.183 | 34.0022 | 33.7403 | 33.4795 | 33.1919 | 32.5034 | 31.966 | 31.533 | 31.1672 | 35.7308 | 35.7308 | 35.7308 | 35.7303 | 35.7295 | 35.7283 | 35.7264 | 35.7223 | 35.7203 | 35.6357 | 35.1054 | 34.6775 | 34.3164
|  | EYNSHAM | FS |  |  | 36.026 | 36.026 | 36.026 | 36.026 | 36.0259 | 36.0259 | 36.0258 | 36.0256 | 36.025 | 36.0211 | 36.018 | 36.0034 | 35.9891 | 34.1842 | 34.1842 | 34.1842 | 34.1842 | 34.1842 | 34.1841 | 34.184 | 34.1839 | 34.165 | 33.8929 | 33.6821 | 33.5214 | 33.3839 | 35.7308 | 35.7308 | 35.7308 | 35.7308 | 35.7307 | 35.7307 | 35.7306 | 35.7304 | 35.7297 | 35.7259 | 35.7228 | 35.7082 | 35.6939
MINETY GSP | CIRENCESTER BSP | FAIRFORD | MINIMUM HEADROOM | SP 14418 00559 | YES | 23.8318 | 23.8318 | 23.8318 | 23.8294 | 23.827 | 23.8246 | 23.8218 | 23.8134 | 23.8073 | 23.772 | 23.4842 | 22.9856 | 22.5276 | 21.0097 | 21.0083 | 21.0053 | 21.0022 | 20.9987 | 20.9911 | 20.9824 | 20.9696 | 20.9633 | 20.7011 | 20.1915 | 19.6495 | 19.1488 | 22.2435 | 22.2435 | 22.2435 | 22.241 | 22.2386 | 22.2362 | 22.2334 | 22.2251 | 22.219 | 22.1836 | 22.1445 | 21.58 | 21.0529
|  | FAIRFORD | CT |  |  | 23.8318 | 23.8318 | 23.8318 | 23.8315 | 23.831 | 23.8302 | 23.8291 | 23.8265 | 23.8261 | 23.8237 | 23.4993 | 23.0135 | 22.5513 | 21.0097 | 21.0083 | 21.0053 | 21.0022 | 20.9989 | 20.9953 | 20.9896 | 20.9826 | 20.9773 | 20.7181 | 20.2065 | 19.6772 | 19.1724 | 22.2435 | 22.2435 | 22.2435 | 22.2432 | 22.2427 | 22.2419 | 22.2407 | 22.2382 | 22.2378 | 22.2353 | 22.1594 | 21.6075 | 21.0763
|  | FAIRFORD | LW |  |  | 23.8318 | 23.8318 | 23.8318 | 23.8309 | 23.829 | 23.826 | 23.8218 | 23.8134 | 23.8119 | 23.8045 | 23.4842 | 22.9856 | 22.5276 | 21.01 | 21.0089 | 21.0064 | 21.003 | 20.9987 | 20.9911 | 20.9824 | 20.9696 | 20.9633 | 20.7011 | 20.1915 | 19.6495 | 19.1488 | 22.2435 | 22.2435 | 22.2435 | 22.2426 | 22.2406 | 22.2376 | 22.2334 | 22.2251 | 22.2236 | 22.2162 | 22.1445 | 21.58 | 21.0529
|  | FAIRFORD | ST |  |  | 23.8318 | 23.8318 | 23.8318 | 23.8316 | 23.8312 | 23.8306 | 23.8298 | 23.8278 | 23.8269 | 23.8218 | 23.8152 | 23.6231 | 23.3181 | 21.0104 | 21.0096 | 21.0081 | 21.0061 | 21.0035 | 21.0006 | 20.9975 | 20.9924 | 20.9882 | 20.9736 | 20.6925 | 20.3429 | 20.0101 | 22.2435 | 22.2435 | 22.2435 | 22.2433 | 22.2429 | 22.2423 | 22.2414 | 22.2395 | 22.2385 | 22.2335 | 22.2269 | 22.2037 | 21.9555
|  | FAIRFORD | FS |  |  | 23.8318 | 23.8318 | 23.8318 | 23.8294 | 23.827 | 23.8246 | 23.8221 | 23.8182 | 23.8073 | 23.772 | 23.7545 | 23.6973 | 23.6485 | 21.0119 | 21.0118 | 21.0117 | 21.0089 | 21.006 | 21.0028 | 20.9995 | 20.9946 | 20.9824 | 20.9433 | 20.92 | 20.8572 | 20.8031 | 22.2435 | 22.2435 | 22.2435 | 22.241 | 22.2386 | 22.2362 | 22.2337 | 22.2299 | 22.219 | 22.1836 | 22.1662 | 22.109 | 22.0602
MINETY GSP | STRATTON (2 X 60) | FARINGDON | MINIMUM HEADROOM | SU 28819 94924 | YES | 20.2337 | 20.2337 | 20.2337 | 20.1983 | 20.1617 | 20.1237 | 20.0836 | 20.0194 | 19.9966 | 19.917 | 19.8443 | 19.3459 | 18.7276 | 17.2237 | 17.216 | 17.2019 | 17.1738 | 17.1273 | 17.0828 | 17.036 | 16.9658 | 16.937 | 16.7237 | 15.9772 | 15.18 | 14.4548 | 18.2921 | 18.2841 | 18.2696 | 18.2417 | 18.1949 | 18.1502 | 18.0689 | 17.9106 | 17.7581 | 17.3158 | 16.5477 | 15.7766 | 15.0768
|  | FARINGDON | CT |  |  | 20.2337 | 20.2337 | 20.2337 | 20.2327 | 20.2309 | 20.2282 | 20.2242 | 20.2155 | 20.2139 | 20.2056 | 20.0334 | 19.3459 | 18.7276 | 17.2237 | 17.216 | 17.2019 | 17.1871 | 17.1712 | 17.1543 | 17.1407 | 17.1233 | 17.1129 | 16.7237 | 15.9772 | 15.18 | 14.4548 | 18.2921 | 18.2841 | 18.2696 | 18.2544 | 18.238 | 18.2207 | 18.0689 | 17.9106 | 17.7581 | 17.3158 | 16.5477 | 15.7766 | 15.0768
|  | FARINGDON | LW |  |  | 20.2337 | 20.2337 | 20.2337 | 20.2264 | 20.2156 | 20.2008 | 20.1818 | 20.146 | 20.1401 | 20.1113 | 20.0446 | 19.3554 | 18.7518 | 17.2248 | 17.2177 | 17.2048 | 17.185 | 17.1613 | 17.1371 | 17.1086 | 17.064 | 17.0492 | 16.7985 | 16.056 | 15.2171 | 14.5066 | 18.2932 | 18.2859 | 18.2726 | 18.2524 | 18.2283 | 18.2038 | 18.175 | 18.0161 | 17.8592 | 17.3964 | 16.6306 | 15.8072 | 15.1221
|  | FARINGDON | ST |  |  | 20.2337 | 20.2337 | 20.2337 | 20.1983 | 20.1617 | 20.1237 | 20.0836 | 20.0194 | 19.9966 | 19.917 | 19.8443 | 19.6183 | 19.545 | 17.2284 | 17.2239 | 17.2172 | 17.1738 | 17.1273 | 17.0828 | 17.036 | 16.9658 | 16.937 | 16.8403 | 16.7328 | 16.0745 | 15.576 | 18.2969 | 18.2923 | 18.2854 | 18.2417 | 18.1949 | 18.1502 | 18.1032 | 18.0328 | 18.0039 | 17.877 | 17.3377 | 16.6645 | 16.1513
|  | FARINGDON | FS |  |  | 20.2337 | 20.2337 | 20.2337 | 20.2336 | 20.2336 | 20.2335 | 20.2334 | 20.2331 | 20.232 | 20.2257 | 20.2208 | 20.1969 | 20.1737 | 17.2349 | 17.2338 | 17.233 | 17.2308 | 17.2282 | 17.2256 | 17.2229 | 17.2198 | 17.2163 | 17.2034 | 17.188 | 17.1547 | 17.1227 | 18.3036 | 18.3025 | 18.3017 | 18.2994 | 18.2967 | 18.294 | 18.2913 | 18.288 | 18.2845 | 18.2714 | 18.2557 | 18.2221 | 18.1898
LOVEDEAN GSP | WYMERING BSP | FARLINGTON | MINIMUM HEADROOM | SU 67400 04843 | YES | 28.4787 | 28.4787 | 28.4787 | 28.4787 | 28.4787 | 28.4777 | 28.4755 | 28.4705 | 28.4675 | 28.4427 | 27.9835 | 27.2733 | 26.5869 | 27.002 | 27.0014 | 27.0002 | 26.9983 | 26.9959 | 26.9792 | 26.9551 | 26.9321 | 26.9125 | 26.8491 | 26.2031 | 25.3739 | 24.5684 | 28.0722 | 28.0713 | 28.0696 | 28.0668 | 28.0635 | 28.0561 | 28.0472 | 28.0367 | 28.0271 | 27.755 | 27.11 | 26.3099 | 25.5336
|  | FARLINGTON | CT |  |  | 28.4787 | 28.4787 | 28.4787 | 28.4787 | 28.4787 | 28.4787 | 28.4773 | 28.4737 | 28.4731 | 28.4522 | 28.0204 | 27.3061 | 26.6121 | 27.002 | 27.0014 | 27.0002 | 26.9983 | 26.9959 | 26.9905 | 26.9672 | 26.9456 | 26.9264 | 26.8653 | 26.2472 | 25.414 | 24.6009 | 28.0722 | 28.0713 | 28.0696 | 28.0668 | 28.0635 | 28.0602 | 28.0522 | 28.0431 | 28.0368 | 27.8082 | 27.1524 | 26.3482 | 25.5643
|  | FARLINGTON | LW |  |  | 28.4787 | 28.4787 | 28.4787 | 28.4787 | 28.4787 | 28.4777 | 28.4755 | 28.4705 | 28.4675 | 28.4427 | 27.9835 | 27.2733 | 26.5869 | 27.002 | 27.0014 | 27.0002 | 26.9983 | 26.9959 | 26.9792 | 26.9551 | 26.9321 | 26.9125 | 26.8491 | 26.2031 | 25.3739 | 24.5684 | 28.0722 | 28.0713 | 28.0696 | 28.0668 | 28.0635 | 28.0561 | 28.0472 | 28.0367 | 28.0271 | 27.755 | 27.11 | 26.3099 | 25.5336
|  | FARLINGTON | ST |  |  | 28.4787 | 28.4787 | 28.4787 | 28.4787 | 28.4787 | 28.4784 | 28.4778 | 28.4763 | 28.4757 | 28.4694 | 28.3901 | 27.9277 | 27.4887 | 27.0024 | 27.002 | 27.0014 | 27.0002 | 26.9986 | 26.9951 | 26.981 | 26.9673 | 26.954 | 26.9114 | 26.6773 | 26.1364 | 25.6218 | 28.0727 | 28.0722 | 28.0713 | 28.0696 | 28.0673 | 28.0623 | 28.0568 | 28.0515 | 28.047 | 28.0093 | 27.5677 | 27.046 | 26.5499
|  | FARLINGTON | FS |  |  | 28.4787 | 28.4787 | 28.4787 | 28.4787 | 28.4787 | 28.4787 | 28.4787 | 28.4786 | 28.4784 | 28.4771 | 28.4762 | 28.4641 | 28.4436 | 27.0028 | 27.0027 | 27.0025 | 27.002 | 27.0013 | 27.0002 | 26.9991 | 26.9979 | 26.9967 | 26.9888 | 26.9489 | 26.8952 | 26.8027 | 28.0734 | 28.0732 | 28.0729 | 28.0722 | 28.0712 | 28.0697 | 28.068 | 28.0664 | 28.0646 | 28.0586 | 28.0458 | 27.9351 | 27.6887
BRAMLEY (FLEE) | CAMBERLEY RESERVE | FARNBOROUGH | MINIMUM HEADROOM | SU 88404 53930 | YES | 44.2511 | 44.2511 | 44.2511 | 44.1435 | 44.0323 | 43.9162 | 43.7959 | 43.6132 | 43.5879 | 43.0075 | 41.4933 | 39.9813 | 38.7766 | 41.6308 | 41.6207 | 41.6037 | 41.4798 | 41.351 | 40.9174 | 40.2805 | 39.527 | 38.8932 | 37.4144 | 35.6593 | 33.9288 | 32.517 | 43.3607 | 43.3607 | 43.3607 | 43.253 | 43.1418 | 42.8544 | 42.2402 | 41.5118 | 40.9047 | 39.4871 | 37.7741 | 36.0778 | 34.6656
|  | FARNBOROUGH | CT |  |  | 44.2511 | 44.2511 | 44.2511 | 44.2398 | 44.2282 | 44.2164 | 44.2041 | 44.1852 | 44.1828 | 43.8342 | 42.4139 | 41.1199 | 39.9201 | 41.6318 | 41.6222 | 41.6063 | 41.5798 | 41.5516 | 41.3915 | 40.8626 | 40.2729 | 39.6619 | 38.2677 | 36.6065 | 35.0939 | 33.6872 | 43.3607 | 43.3607 | 43.3607 | 43.3493 | 43.3377 | 43.3209 | 42.8147 | 42.2501 | 41.6658 | 40.3356 | 38.7166 | 37.2423 | 35.8358
|  | FARNBOROUGH | LW |  |  | 44.2511 | 44.2511 | 44.2511 | 44.1435 | 44.0323 | 43.9162 | 43.7959 | 43.6132 | 43.5879 | 43.0075 | 41.4933 | 39.9813 | 38.7766 | 41.6308 | 41.6207 | 41.6037 | 41.4798 | 41.351 | 40.9174 | 40.2805 | 39.527 | 38.8932 | 37.4144 | 35.6593 | 33.9288 | 32.517 | 43.3607 | 43.3607 | 43.3607 | 43.253 | 43.1418 | 42.8544 | 42.2402 | 41.5118 | 40.9047 | 39.4871 | 37.7741 | 36.0778 | 34.6656
|  | FARNBOROUGH | ST |  |  | 44.2511 | 44.2511 | 44.2511 | 44.2511 | 44.2511 | 44.2511 | 44.2511 | 44.2511 | 44.2511 | 44.2511 | 44.2511 | 43.4694 | 42.7017 | 41.6358 | 41.6293 | 41.6197 | 41.6097 | 41.5977 | 41.5821 | 41.5652 | 41.2381 | 40.8208 | 39.8721 | 38.7842 | 37.8262 | 36.9249 | 43.3607 | 43.3607 | 43.3607 | 43.3607 | 43.3607 | 43.3607 | 43.3607 | 43.1757 | 42.7768 | 41.8698 | 40.8377 | 39.9076 | 39.0296
|  | FARNBOROUGH | FS |  |  | 44.2511 | 44.2511 | 44.2511 | 44.2511 | 44.2511 | 44.2511 | 44.2511 | 44.2511 | 44.2511 | 44.2511 | 44.2511 | 44.2511 | 44.2511 | 41.6411 | 41.6378 | 41.6339 | 41.6296 | 41.6249 | 41.6188 | 41.6123 | 41.6046 | 41.5971 | 41.58 | 41.5188 | 41.1485 | 40.8043 | 43.3607 | 43.3607 | 43.3607 | 43.3607 | 43.3607 | 43.3607 | 43.3607 | 43.3607 | 43.3607 | 43.3607 | 43.3607 | 43.0901 | 42.761
BRAMLEY (FLEE) | ALDERSHOT BSP | FARNHAM | MINIMUM HEADROOM | SU 84517 47217 | YES | 34.4305 | 34.4305 | 34.4305 | 34.4135 | 34.3951 | 34.375 | 34.3533 | 34.3185 | 34.2949 | 34.1047 | 34.0136 | 33.7247 | 33.4823 | 32.7321 | 32.7321 | 32.7321 | 32.7064 | 32.6622 | 32.6315 | 32.5989 | 32.5545 | 32.5395 | 32.4064 | 31.9994 | 30.9958 | 30.0314 | 33.1269 | 33.1269 | 33.1269 | 33.0842 | 33.0353 | 33.0026 | 32.968 | 32.9219 | 32.9049 | 32.8011 | 32.4175 | 31.3877 | 30.3922
|  | FARNHAM | CT |  |  | 34.4305 | 34.4305 | 34.4305 | 34.4302 | 34.4298 | 34.4291 | 34.4281 | 34.4259 | 34.4255 | 34.4234 | 34.4061 | 34.3868 | 33.8621 | 32.7321 | 32.7321 | 32.7321 | 32.7261 | 32.7008 | 32.6752 | 32.6634 | 32.6516 | 32.6412 | 32.6101 | 31.9994 | 30.9982 | 30.0331 | 33.1269 | 33.1269 | 33.1269 | 33.1045 | 33.0746 | 33.0444 | 33.0306 | 33.017 | 33.0048 | 32.9683 | 32.4175 | 31.3877 | 30.3922
|  | FARNHAM | LW |  |  | 34.4305 | 34.4305 | 34.4305 | 34.4135 | 34.3951 | 34.375 | 34.3533 | 34.3185 | 34.3134 | 34.294 | 34.2535 | 34.1739 | 33.8341 | 32.7321 | 32.7321 | 32.7321 | 32.7064 | 32.6622 | 32.6315 | 32.5989 | 32.5545 | 32.5395 | 32.491 | 32.0574 | 30.9958 | 30.0314 | 33.1269 | 33.1269 | 33.1269 | 33.0842 | 33.0353 | 33.0026 | 32.968 | 32.9219 | 32.9049 | 32.8511 | 32.4765 | 31.3919 | 30.3972
|  | FARNHAM | ST |  |  | 34.4305 | 34.4305 | 34.4305 | 34.4214 | 34.412 | 34.4022 | 34.3919 | 34.3754 | 34.3696 | 34.3492 | 34.3301 | 34.2638 | 34.2432 | 32.7321 | 32.7321 | 32.7321 | 32.723 | 32.7136 | 32.7039 | 32.6922 | 32.6692 | 32.6565 | 32.6165 | 32.5652 | 32.4678 | 32.4166 | 33.1269 | 33.1269 | 33.1269 | 33.1178 | 33.1084 | 33.0925 | 33.0714 | 33.0472 | 33.0333 | 32.9896 | 32.9324 | 32.8293 | 32.7723
|  | FARNHAM | FS |  |  | 34.4305 | 34.4305 | 34.4305 | 34.4168 | 34.4033 | 34.3898 | 34.3761 | 34.3547 | 34.2949 | 34.1047 | 34.0136 | 33.7247 | 33.4823 | 32.7321 | 32.7321 | 32.7321 | 32.7184 | 32.705 | 32.6915 | 32.6778 | 32.6563 | 32.5966 | 32.4064 | 32.3152 | 32.0264 | 31.7839 | 33.1269 | 33.1269 | 33.1269 | 33.1132 | 33.0997 | 33.0862 | 33.0725 | 33.0511 | 32.9913 | 32.8011 | 32.71 | 32.4211 | 32.1735
IVER 132KV | SLOUGH | FARNHAM ROYAL | MINIMUM HEADROOM | SU 95597 82844 | YES | 52.2174 | 52.2019 | 51.2523 | 51.1734 | 51.0932 | 51.0118 | 50.929 | 50.8412 | 50.8084 | 50.7062 | 50.4123 | 48.1953 | 45.7448 | 43.647 | 43.6314 | 42.6819 | 42.6029 | 42.5228 | 42.4414 | 42.3586 | 42.2708 | 42.2379 | 42.1357 | 41.8418 | 40.3277 | 37.5186 | 48.6678 | 48.6385 | 47.659 | 47.5499 | 47.4392 | 47.3283 | 47.2165 | 47.0996 | 47.0357 | 46.8385 | 44.9905 | 41.994 | 39.1755
|  | FARNHAM ROYAL | CT |  |  | 52.2984 | 52.289 | 51.7193 | 51.6436 | 51.5671 | 51.4898 | 51.4108 | 51.3133 | 51.2881 | 51.2097 | 50.4123 | 48.1953 | 45.7448 | 43.7279 | 43.7186 | 43.1488 | 43.0731 | 42.9966 | 42.9194 | 42.8403 | 42.7429 | 42.7176 | 42.6393 | 41.8418 | 40.3277 | 37.5186 | 48.7501 | 48.7279 | 48.1299 | 48.0257 | 47.9202 | 47.8162 | 47.7082 | 47.5817 | 47.5253 | 47.352 | 44.9965 | 41.994 | 39.1755
|  | FARNHAM ROYAL | LW |  |  | 52.2174 | 52.2019 | 51.2523 | 51.1734 | 51.0932 | 51.0118 | 50.929 | 50.8412 | 50.8084 | 50.7062 | 50.5292 | 48.4439 | 46.0246 | 43.647 | 43.6314 | 42.6819 | 42.6029 | 42.5228 | 42.4414 | 42.3586 | 42.2708 | 42.2379 | 42.1357 | 41.9587 | 40.5593 | 37.7813 | 48.6678 | 48.6385 | 47.659 | 47.5499 | 47.4392 | 47.3283 | 47.2165 | 47.0996 | 47.0357 | 46.8385 | 44.9905 | 42.2252 | 39.4378
|  | FARNHAM ROYAL | ST |  |  | 52.3388 | 52.3326 | 51.9528 | 51.89 | 51.8265 | 51.7621 | 51.6962 | 51.6107 | 51.5794 | 51.4797 | 51.3641 | 51.1479 | 50.5807 | 43.7684 | 43.7622 | 43.3823 | 43.3196 | 43.256 | 43.1916 | 43.1258 | 43.0402 | 43.009 | 42.9092 | 42.7937 | 42.5775 | 42.4519 | 48.8077 | 48.7898 | 48.3992 | 48.3228 | 48.2429 | 48.1608 | 48.0778 | 47.9724 | 47.92 | 47.7557 | 47.5128 | 46.4013 | 44.6093
|  | FARNHAM ROYAL | FS |  |  | 52.3793 | 52.3762 | 52.1863 | 52.1707 | 52.1551 | 52.1395 | 52.1239 | 52.1083 | 52.1017 | 52.0808 | 52.048 | 52.021 | 51.9788 | 43.8089 | 43.8057 | 43.6158 | 43.6003 | 43.5847 | 43.5691 | 43.5535 | 43.5378 | 43.5312 | 43.5104 | 43.4775 | 43.4506 | 43.4083 | 48.8564 | 48.8521 | 48.6603 | 48.6395 | 48.6179 | 48.5964 | 48.5752 | 48.5524 | 48.5376 | 48.4917 | 48.4085 | 48.324 | 48.2236
LALEHAM | EAST BEDFONT A | FELTHAM | MINIMUM HEADROOM | TQ 10628 72811 | YES | 37.0343 | 37.0343 | 37.0343 | 37.0343 | 37.0343 | 37.0343 | 37.0343 | 37.0343 | 37.0343 | 37.0343 | 36.8565 | 35.7184 | 34.5983 | 34.7138 | 34.7033 | 34.6851 | 34.6657 | 34.6446 | 34.6243 | 34.6009 | 34.4925 | 34.3799 | 34.0648 | 33.0435 | 31.7027 | 30.3833 | 36.3509 | 36.3337 | 36.304 | 36.2722 | 36.2375 | 36.2044 | 36.0769 | 35.8587 | 35.6844 | 35.1966 | 34.0888 | 32.7521 | 31.4367
|  | FELTHAM | CT |  |  | 37.0343 | 37.0343 | 37.0343 | 37.0343 | 37.0343 | 37.0343 | 37.0343 | 37.0343 | 37.0343 | 37.0343 | 36.8905 | 35.7525 | 34.6326 | 34.7146 | 34.7046 | 34.6874 | 34.669 | 34.6487 | 34.6275 | 34.604 | 34.5183 | 34.4057 | 34.0907 | 33.0836 | 31.743 | 30.4237 | 36.3523 | 36.3358 | 36.3078 | 36.2775 | 36.2444 | 36.2096 | 36.1169 | 35.8987 | 35.7244 | 35.2367 | 34.1288 | 32.7923 | 31.477
|  | FELTHAM | LW |  |  | 37.0343 | 37.0343 | 37.0343 | 37.0343 | 37.0343 | 37.0343 | 37.0343 | 37.0343 | 37.0343 | 37.0343 | 36.8565 | 35.7184 | 34.5983 | 34.7138 | 34.7033 | 34.6851 | 34.6657 | 34.6446 | 34.6243 | 34.6009 | 34.4925 | 34.3799 | 34.0648 | 33.0435 | 31.7027 | 30.3833 | 36.3509 | 36.3337 | 36.304 | 36.2722 | 36.2375 | 36.2044 | 36.0769 | 35.8587 | 35.6844 | 35.1966 | 34.0888 | 32.7521 | 31.4367
|  | FELTHAM | ST |  |  | 37.0343 | 37.0343 | 37.0343 | 37.0343 | 37.0343 | 37.0343 | 37.0343 | 37.0343 | 37.0343 | 37.0343 | 37.0343 | 37.0343 | 36.4186 | 34.7289 | 34.7114 | 34.7018 | 34.6903 | 34.6767 | 34.6636 | 34.6483 | 34.6366 | 34.6271 | 34.6002 | 34.1274 | 33.3643 | 32.5277 | 36.3757 | 36.3469 | 36.3313 | 36.3125 | 36.2902 | 36.2687 | 36.2437 | 36.2245 | 36.209 | 36.0684 | 35.2935 | 34.4087 | 33.5746
|  | FELTHAM | FS |  |  | 37.0343 | 37.0343 | 37.0343 | 37.0343 | 37.0343 | 37.0343 | 37.0343 | 37.0343 | 37.0343 | 37.0343 | 37.0343 | 37.0343 | 37.0343 | 34.7327 | 34.7296 | 34.7258 | 34.7207 | 34.715 | 34.7096 | 34.7035 | 34.6988 | 34.6951 | 34.6845 | 34.6589 | 34.6259 | 34.5592 | 36.3819 | 36.3768 | 36.3706 | 36.3622 | 36.3528 | 36.344 | 36.334 | 36.3264 | 36.3203 | 36.303 | 36.2611 | 36.207 | 35.962
MANNINGTON GSP | MANNINGTON BSP | FERNDOWN | MINIMUM HEADROOM | SU 06593 00685 | YES | 38.003 | 37.9794 | 36.5401 | 36.4207 | 36.2996 | 36.1767 | 36.052 | 35.9205 | 35.871 | 35.7175 | 35.4525 | 34.9223 | 33.466 | 35.9025 | 35.8735 | 34.4228 | 34.2923 | 34.1601 | 33.9987 | 33.8306 | 33.6536 | 33.5545 | 33.2375 | 31.357 | 29.7198 | 28.0442 | 29.9955 | 29.9359 | 28.421 | 28.2278 | 28.0332 | 27.6545 | 27.2414 | 26.8084 | 26.4298 | 25.1907 | 23.1803 | 21.7533 | 20.2841
|  | FERNDOWN | CT |  |  | 38.1257 | 38.1116 | 37.248 | 37.1739 | 37.0993 | 37.0243 | 36.9486 | 36.8689 | 36.8393 | 36.7485 | 35.6747 | 35.1032 | 33.6379 | 36.0258 | 36.0066 | 35.1323 | 35.0477 | 34.9627 | 34.8721 | 34.753 | 34.6279 | 34.5487 | 34.2944 | 31.7801 | 29.9319 | 28.2475 | 30.1221 | 30.074 | 29.1392 | 28.9957 | 28.8519 | 28.6736 | 28.3097 | 27.9286 | 27.5698 | 26.3936 | 23.574 | 21.936 | 20.4579
|  | FERNDOWN | LW |  |  | 38.003 | 37.9794 | 36.5401 | 36.4207 | 36.2996 | 36.1767 | 36.052 | 35.9205 | 35.871 | 35.7175 | 35.4525 | 34.9223 | 33.466 | 35.9025 | 35.8735 | 34.4228 | 34.2923 | 34.1601 | 33.9987 | 33.8306 | 33.6536 | 33.5545 | 33.2375 | 31.357 | 29.7198 | 28.0442 | 29.9955 | 29.9359 | 28.421 | 28.2278 | 28.0332 | 27.6545 | 27.2414 | 26.8084 | 26.4298 | 25.1907 | 23.1803 | 21.7533 | 20.2841
|  | FERNDOWN | ST |  |  | 38.1871 | 38.1776 | 37.6019 | 37.5544 | 37.5066 | 37.4584 | 37.4098 | 37.3595 | 37.3391 | 37.2743 | 37.1693 | 37.0752 | 36.9577 | 36.0858 | 36.0712 | 35.4867 | 35.4284 | 35.3675 | 35.2908 | 35.2104 | 35.1293 | 35.075 | 34.8971 | 34.5083 | 33.4859 | 32.4514 | 30.1742 | 30.1305 | 29.4965 | 29.3773 | 29.2431 | 29.0049 | 28.7456 | 28.4906 | 28.2452 | 27.4294 | 26.1219 | 25.2352 | 24.3347
|  | FERNDOWN | FS |  |  | 38.2484 | 38.2437 | 37.9558 | 37.9322 | 37.9086 | 37.885 | 37.8613 | 37.8376 | 37.8277 | 37.7964 | 37.7469 | 37.7074 | 37.6446 | 36.1563 | 36.1511 | 35.8629 | 35.8375 | 35.8117 | 35.7792 | 35.7454 | 35.7089 | 35.6857 | 35.6102 | 35.489 | 35.4053 | 35.3006 | 30.2965 | 30.2889 | 29.9982 | 29.9626 | 29.9248 | 29.8421 | 29.7512 | 29.6425 | 29.5447 | 29.2195 | 28.6942 | 28.3617 | 28.0204
BRAMLEY (FLEE) | FERNHURST | FIVE OAKS | MINIMUM HEADROOM | TQ 10647 29057 | YES | 19.8539 | 19.7336 | 19.5164 | 19.289 | 19.0457 | 18.9408 | 18.8199 | 18.6874 | 18.5835 | 18.2762 | 17.7612 | 17.171 | 16.7729 | 17.2028 | 17.0613 | 16.8058 | 16.539 | 16.2544 | 16.1337 | 15.9953 | 15.847 | 15.726 | 15.3712 | 14.7814 | 14.1188 | 13.6525 | 18.2203 | 18.0827 | 17.8344 | 17.5749 | 17.2981 | 17.1804 | 17.0453 | 16.8999 | 16.7821 | 16.4362 | 15.8604 | 15.2113 | 14.7578
|  | FIVE OAKS | CT |  |  | 19.8773 | 19.7701 | 19.5802 | 19.3826 | 19.1727 | 19.0189 | 18.9137 | 18.8112 | 18.7123 | 18.4306 | 17.9052 | 17.3806 | 16.9597 | 17.2304 | 17.1042 | 16.8808 | 16.6485 | 16.402 | 16.2218 | 16.099 | 15.9807 | 15.8648 | 15.5355 | 14.9354 | 14.3383 | 13.8493 | 18.2471 | 18.1244 | 17.9073 | 17.6815 | 17.4418 | 17.2666 | 17.1471 | 17.0318 | 16.919 | 16.5986 | 16.0125 | 15.4289 | 14.9527
|  | FIVE OAKS | LW |  |  | 19.8539 | 19.7336 | 19.5164 | 19.289 | 19.0457 | 18.9408 | 18.8199 | 18.6874 | 18.5835 | 18.2762 | 17.7612 | 17.171 | 16.7729 | 17.2028 | 17.0613 | 16.8058 | 16.539 | 16.2544 | 16.1337 | 15.9953 | 15.847 | 15.726 | 15.3712 | 14.7814 | 14.1188 | 13.6525 | 18.2203 | 18.0827 | 17.8344 | 17.5749 | 17.2981 | 17.1804 | 17.0453 | 16.8999 | 16.7821 | 16.4362 | 15.8604 | 15.2113 | 14.7578
|  | FIVE OAKS | ST |  |  | 19.8758 | 19.7851 | 19.6459 | 19.4742 | 19.2666 | 19.1848 | 19.0956 | 19.0248 | 18.954 | 18.745 | 18.4275 | 18.0437 | 17.7494 | 17.2286 | 17.1219 | 16.9581 | 16.7563 | 16.5123 | 16.4166 | 16.3124 | 16.2309 | 16.1485 | 15.9071 | 15.5395 | 15.1089 | 14.7703 | 18.2453 | 18.1416 | 17.9824 | 17.7862 | 17.5491 | 17.456 | 17.3546 | 17.2751 | 17.1948 | 16.9595 | 16.6013 | 16.1795 | 15.8492
|  | FIVE OAKS | FS |  |  | 19.9891 | 19.9643 | 19.9389 | 19.8872 | 19.8282 | 19.7972 | 19.7637 | 19.7243 | 19.6831 | 19.5587 | 19.4214 | 19.2223 | 19.0463 | 17.362 | 17.3328 | 17.3028 | 17.2426 | 17.1738 | 17.1378 | 17.099 | 17.0536 | 17.0079 | 16.8709 | 16.7144 | 16.4981 | 16.3068 | 18.3749 | 18.3466 | 18.3175 | 18.2589 | 18.1919 | 18.1568 | 18.119 | 18.0747 | 18.0299 | 17.8952 | 17.7423 | 17.5292 | 17.3408
AMERSHAM | LOUDWATER BSP | FLACKWELL HEATH | MINIMUM HEADROOM | SU 90667 89318 | YES | 40.936 | 40.936 | 40.936 | 40.8604 | 40.7835 | 40.7053 | 40.6237 | 40.4979 | 40.4819 | 40.4307 | 40.1943 | 39.9289 | 39.8679 | 37.3542 | 37.2737 | 37.1044 | 36.8746 | 36.6374 | 36.4002 | 36.1589 | 35.8746 | 35.6881 | 35.1277 | 33.9995 | 32.7801 | 31.7766 | 40.1231 | 40.1231 | 40.1231 | 40.0475 | 39.9706 | 39.8924 | 39.8108 | 39.685 | 39.6691 | 39.6179 | 39.3636 | 38.1853 | 37.218
|  | FLACKWELL HEATH | CT |  |  | 40.936 | 40.936 | 40.936 | 40.8604 | 40.7835 | 40.7053 | 40.6237 | 40.4979 | 40.4819 | 40.4307 | 40.1943 | 39.9289 | 39.8679 | 37.3567 | 37.2776 | 37.1116 | 36.8746 | 36.6374 | 36.4002 | 36.1589 | 35.8746 | 35.6881 | 35.1277 | 33.9995 | 32.7801 | 31.7766 | 40.1231 | 40.1231 | 40.1231 | 40.0475 | 39.9706 | 39.8924 | 39.8108 | 39.685 | 39.6691 | 39.6179 | 39.3636 | 38.1853 | 37.218
|  | FLACKWELL HEATH | LW |  |  | 40.936 | 40.936 | 40.936 | 40.936 | 40.936 | 40.936 | 40.936 | 40.936 | 40.936 | 40.936 | 40.936 | 40.936 | 40.936 | 37.3542 | 37.2737 | 37.1044 | 36.94 | 36.7766 | 36.6158 | 36.4561 | 36.2977 | 36.1272 | 35.6179 | 34.7261 | 33.772 | 32.829 | 40.1231 | 40.1231 | 40.1231 | 40.1231 | 40.1231 | 40.1231 | 40.1231 | 40.1231 | 40.1231 | 40.1231 | 40.0953 | 39.1778 | 38.271
|  | FLACKWELL HEATH | ST |  |  | 40.936 | 40.936 | 40.936 | 40.936 | 40.936 | 40.936 | 40.936 | 40.936 | 40.936 | 40.936 | 40.936 | 40.936 | 40.936 | 37.3801 | 37.3218 | 37.2227 | 37.101 | 36.9543 | 36.8265 | 36.7 | 36.5916 | 36.4753 | 36.1313 | 35.5331 | 34.9155 | 34.3052 | 40.1231 | 40.1231 | 40.1231 | 40.1231 | 40.1231 | 40.1231 | 40.1231 | 40.1231 | 40.1231 | 40.1231 | 40.1231 | 40.1151 | 39.6906
|  | FLACKWELL HEATH | FS |  |  | 40.936 | 40.936 | 40.936 | 40.936 | 40.936 | 40.936 | 40.936 | 40.936 | 40.936 | 40.936 | 40.936 | 40.936 | 40.936 | 37.4788 | 37.4722 | 37.4657 | 37.4381 | 37.4052 | 37.3617 | 37.3186 | 37.2635 | 37.2184 | 37.0854 | 36.8556 | 36.6198 | 36.3903 | 40.1231 | 40.1231 | 40.1231 | 40.1231 | 40.1231 | 40.1231 | 40.1231 | 40.1231 | 40.1231 | 40.1231 | 40.1231 | 40.1231 | 40.1231
NURSLING GSP | ROWNHAMS | FLETCHWOOD | MINIMUM HEADROOM | SU 33800 12142 | YES | 45.4015 | 45.4015 | 45.4015 | 45.3925 | 45.3835 | 45.3742 | 45.3647 | 45.3499 | 45.3448 | 45.3023 | 45.2748 | 44.8849 | 43.8686 | 40.8371 | 40.8371 | 40.8371 | 40.8282 | 40.8191 | 40.8099 | 40.8003 | 40.7855 | 40.7805 | 39.6225 | 37.97 | 36.667 | 35.4523 | 44.3907 | 44.3907 | 44.3907 | 44.3818 | 44.3727 | 44.3635 | 44.3539 | 44.3391 | 44.2276 | 43.0623 | 41.4178 | 40.1211 | 38.9123
|  | FLETCHWOOD | CT |  |  | 45.4015 | 45.4015 | 45.4015 | 45.4015 | 45.4015 | 45.4015 | 45.4015 | 45.4015 | 45.4015 | 45.4015 | 45.4015 | 44.979 | 43.9631 | 40.8371 | 40.8371 | 40.8371 | 40.8371 | 40.8371 | 40.8371 | 40.8371 | 40.8371 | 40.8371 | 39.735 | 38.0821 | 36.7794 | 35.5653 | 44.3907 | 44.3907 | 44.3907 | 44.3907 | 44.3907 | 44.3907 | 44.3907 | 44.3907 | 44.3393 | 43.1743 | 41.5294 | 40.2329 | 39.0248
|  | FLETCHWOOD | LW |  |  | 45.4015 | 45.4015 | 45.4015 | 45.4015 | 45.4015 | 45.4015 | 45.4015 | 45.4015 | 45.4015 | 45.4015 | 45.4015 | 44.8849 | 43.8686 | 40.8371 | 40.8371 | 40.8371 | 40.8371 | 40.8371 | 40.8371 | 40.8371 | 40.8371 | 40.7935 | 39.6225 | 37.97 | 36.667 | 35.4523 | 44.3907 | 44.3907 | 44.3907 | 44.3907 | 44.3907 | 44.3907 | 44.3907 | 44.3907 | 44.2276 | 43.0623 | 41.4178 | 40.1211 | 38.9123
|  | FLETCHWOOD | ST |  |  | 45.4015 | 45.4015 | 45.4015 | 45.3925 | 45.3835 | 45.3742 | 45.3647 | 45.3499 | 45.3448 | 45.3288 | 45.3159 | 45.2735 | 45.2602 | 40.8371 | 40.8371 | 40.8371 | 40.8282 | 40.8191 | 40.8099 | 40.8003 | 40.7855 | 40.7805 | 40.5154 | 39.3727 | 38.4886 | 37.6851 | 44.3907 | 44.3907 | 44.3907 | 44.3818 | 44.3727 | 44.3635 | 44.3539 | 44.3391 | 44.3341 | 43.9506 | 42.8133 | 41.9333 | 41.1336
|  | FLETCHWOOD | FS |  |  | 45.4015 | 45.4015 | 45.4015 | 45.3973 | 45.3932 | 45.389 | 45.3848 | 45.3783 | 45.3601 | 45.3023 | 45.2748 | 45.1881 | 45.1156 | 40.8371 | 40.8371 | 40.8371 | 40.8329 | 40.8288 | 40.8247 | 40.8205 | 40.8139 | 40.7957 | 40.7379 | 40.7104 | 40.6237 | 40.5512 | 44.3907 | 44.3907 | 44.3907 | 44.3865 | 44.3824 | 44.3783 | 44.3741 | 44.3675 | 44.3493 | 44.2915 | 44.264 | 44.1773 | 44.043
MANNINGTON GSP | MANNINGTON BSP | FORDINGBRIDGE | MINIMUM HEADROOM | SU 14069 15523 | YES | 22.3129 | 22.3129 | 22.3129 | 22.2682 | 22.2212 | 22.1712 | 22.1184 | 22.0362 | 22.0246 | 21.9823 | 21.8457 | 21.2874 | 20.8674 | 18.7439 | 18.7267 | 18.693 | 18.6231 | 18.5335 | 18.3816 | 18.2167 | 18.0252 | 17.9041 | 17.5344 | 17.1283 | 16.6917 | 16.3889 | 21.1842 | 21.1826 | 21.1794 | 21.1323 | 21.0813 | 21.0215 | 20.958 | 20.8654 | 20.8433 | 20.7699 | 20.6314 | 19.9987 | 19.5071
|  | FORDINGBRIDGE | CT |  |  | 22.3129 | 22.3129 | 22.3129 | 22.3126 | 22.3121 | 22.3113 | 22.3103 | 22.3079 | 22.3075 | 22.3052 | 22.2742 | 21.8268 | 21.4098 | 18.7439 | 18.7267 | 18.693 | 18.6662 | 18.6227 | 18.5609 | 18.4478 | 18.336 | 18.2261 | 17.8965 | 17.5412 | 17.2155 | 16.9157 | 21.1842 | 21.1826 | 21.1794 | 21.1766 | 21.172 | 21.1654 | 21.1537 | 21.1408 | 21.13 | 21.0965 | 21.0456 | 20.5478 | 20.0591
|  | FORDINGBRIDGE | LW |  |  | 22.3129 | 22.3129 | 22.3129 | 22.2682 | 22.2212 | 22.1712 | 22.1184 | 22.0362 | 22.0246 | 21.9823 | 21.8457 | 21.2874 | 20.8674 | 18.7442 | 18.7273 | 18.6939 | 18.6231 | 18.5335 | 18.3816 | 18.2167 | 18.0252 | 17.9041 | 17.5344 | 17.1283 | 16.6917 | 16.3889 | 21.1843 | 21.1826 | 21.1795 | 21.1323 | 21.0813 | 21.0215 | 20.958 | 20.8654 | 20.8433 | 20.7699 | 20.6314 | 19.9987 | 19.5071
|  | FORDINGBRIDGE | ST |  |  | 22.3129 | 22.3129 | 22.3129 | 22.2902 | 22.2669 | 22.2431 | 22.2181 | 22.179 | 22.1655 | 22.1204 | 22.081 | 21.9495 | 21.8568 | 18.7491 | 18.7382 | 18.7193 | 18.6807 | 18.6287 | 18.5362 | 18.4359 | 18.323 | 18.2346 | 17.962 | 17.6956 | 17.3675 | 17.1349 | 21.1847 | 21.1837 | 21.1819 | 21.1577 | 21.1317 | 21.1013 | 21.0692 | 21.023 | 21.0023 | 20.9355 | 20.8746 | 20.7242 | 20.6453
|  | FORDINGBRIDGE | FS |  |  | 22.3129 | 22.3129 | 22.3129 | 22.3117 | 22.3105 | 22.3093 | 22.308 | 22.3061 | 22.3006 | 22.2825 | 22.2733 | 22.2422 | 22.2152 | 18.75 | 18.75 | 18.7429 | 18.7354 | 18.7224 | 18.696 | 18.6674 | 18.6362 | 18.6012 | 18.4937 | 18.3971 | 18.2942 | 18.2014 | 21.1853 | 21.1849 | 21.1841 | 21.1823 | 21.18 | 21.1764 | 21.1726 | 21.1679 | 21.1596 | 21.1329 | 21.1154 | 21.0774 | 21.0442
LOVEDEAN GSP | PORTSMOUTH BSP | FRATTON PARK | MINIMUM HEADROOM | SU 66139 00180 | YES | 42.5648 | 42.5529 | 41.8319 | 41.7381 | 41.6432 | 41.5467 | 41.4489 | 41.3309 | 41.2991 | 41.2003 | 41.0322 | 38.9518 | 36.4532 | 39.2393 | 39.223 | 38.4953 | 38.3945 | 38.2915 | 38.1701 | 38.0473 | 37.9039 | 37.845 | 37.6597 | 34.9438 | 31.9802 | 29.0704 | 40.9657 | 40.9491 | 40.221 | 40.1196 | 40.0161 | 39.8929 | 39.7683 | 39.6231 | 39.5623 | 39.3709 | 37.6233 | 34.6972 | 31.8244
|  | FRATTON PARK | CT |  |  | 42.6262 | 42.6191 | 42.1865 | 42.1397 | 42.0927 | 42.0454 | 41.9977 | 41.9433 | 41.9267 | 41.8764 | 41.3178 | 39.428 | 36.9254 | 39.3007 | 39.2892 | 38.8499 | 38.796 | 38.7409 | 38.6857 | 38.613 | 38.5332 | 38.4895 | 38.3528 | 35.5297 | 32.5009 | 29.5871 | 41.0271 | 41.0153 | 40.5756 | 40.5211 | 40.4655 | 40.4096 | 40.3352 | 40.2536 | 40.208 | 40.0652 | 38.2052 | 35.2139 | 32.3372
|  | FRATTON PARK | LW |  |  | 42.5648 | 42.5529 | 41.8319 | 41.7381 | 41.6432 | 41.5467 | 41.4489 | 41.3309 | 41.2991 | 41.2003 | 41.0322 | 38.9518 | 36.4532 | 39.2393 | 39.223 | 38.4953 | 38.3945 | 38.2915 | 38.1701 | 38.0473 | 37.9039 | 37.845 | 37.6597 | 34.9438 | 31.9802 | 29.0704 | 40.9657 | 40.9491 | 40.221 | 40.1196 | 40.0161 | 39.8929 | 39.7683 | 39.6231 | 39.5623 | 39.3709 | 37.6233 | 34.6972 | 31.8244
|  | FRATTON PARK | ST |  |  | 42.657 | 42.6522 | 42.3638 | 42.3402 | 42.3165 | 42.2929 | 42.2693 | 42.2456 | 42.2362 | 42.2078 | 42.1605 | 42.1322 | 41.0515 | 39.3571 | 39.3203 | 39.025 | 38.9931 | 38.9593 | 38.9209 | 38.8825 | 38.8416 | 38.8136 | 38.7258 | 37.9232 | 36.0669 | 34.2345 | 41.0853 | 41.0462 | 40.7504 | 40.7179 | 40.6835 | 40.644 | 40.6046 | 40.5624 | 40.5331 | 40.4411 | 40.2888 | 38.7461 | 36.9375
|  | FRATTON PARK | FS |  |  | 42.6877 | 42.6853 | 42.5411 | 42.5293 | 42.5175 | 42.5057 | 42.4938 | 42.482 | 42.4773 | 42.4631 | 42.4395 | 42.4253 | 42.3993 | 39.3938 | 39.3657 | 39.2201 | 39.2064 | 39.1924 | 39.1758 | 39.1594 | 39.1419 | 39.1299 | 39.0925 | 39.0299 | 38.9728 | 38.9037 | 41.1224 | 41.0925 | 40.9468 | 40.9329 | 40.9188 | 40.9019 | 40.8852 | 40.8672 | 40.8547 | 40.8157 | 40.7504 | 40.6902 | 40.618
COWLEY GSP | OXFORD BSP | FRENCHAY ROAD | MINIMUM HEADROOM | SP 50426 08256 | YES | 23.1354 | 23.1354 | 23.1354 | 22.9255 | 22.4557 | 22.0083 | 21.9186 | 21.8051 | 21.6733 | 21.3416 | 20.6458 | 19.8221 | 18.9982 | 21.1953 | 21.1712 | 21.1237 | 20.6775 | 20.1232 | 19.5954 | 19.4896 | 19.3557 | 19.2002 | 18.8089 | 17.9881 | 17.0163 | 16.0443 | 22.8503 | 22.8332 | 22.7995 | 22.7677 | 22.6784 | 22.189 | 22.0909 | 21.9668 | 21.8158 | 21.4244 | 20.6032 | 19.6311 | 18.6589
|  | FRENCHAY ROAD | CT |  |  | 23.1354 | 23.1354 | 23.1354 | 22.9378 | 22.4716 | 22.0083 | 21.9186 | 21.8051 | 21.6733 | 21.3416 | 20.6458 | 19.8221 | 18.9982 | 21.1956 | 21.1717 | 21.1245 | 20.692 | 20.142 | 19.5954 | 19.4896 | 19.3557 | 19.2002 | 18.8089 | 17.9881 | 17.0163 | 16.0443 | 22.8505 | 22.8336 | 22.8 | 22.7685 | 22.6957 | 22.189 | 22.0909 | 21.9668 | 21.8158 | 21.4244 | 20.6032 | 19.6311 | 18.6589
|  | FRENCHAY ROAD | LW |  |  | 23.1354 | 23.1354 | 23.1354 | 22.9255 | 22.4557 | 22.3696 | 22.2799 | 22.1664 | 22.0346 | 21.703 | 21.007 | 20.1833 | 19.3591 | 21.1953 | 21.1712 | 21.1237 | 20.6775 | 20.1232 | 20.0216 | 19.9158 | 19.7819 | 19.6265 | 19.2352 | 18.4142 | 17.4424 | 16.4701 | 22.8503 | 22.8332 | 22.7995 | 22.7677 | 22.6784 | 22.5842 | 22.4861 | 22.3619 | 22.2179 | 21.8508 | 21.0295 | 20.0574 | 19.0847
|  | FRENCHAY ROAD | ST |  |  | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 22.6834 | 22.1417 | 21.6164 | 21.2181 | 21.2083 | 21.1933 | 21.1762 | 21.1558 | 21.1472 | 21.1383 | 21.1311 | 21.1227 | 20.9585 | 20.3919 | 19.7528 | 19.1331 | 22.8665 | 22.8596 | 22.8489 | 22.8368 | 22.8223 | 22.8161 | 22.8099 | 22.8048 | 22.7987 | 22.7836 | 22.7516 | 22.335 | 21.7486
|  | FRENCHAY ROAD | FS |  |  | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 21.2292 | 21.2264 | 21.224 | 21.2166 | 21.208 | 21.2044 | 21.2008 | 21.1958 | 21.1924 | 21.1841 | 21.1658 | 21.1431 | 21.1195 | 22.8744 | 22.8724 | 22.8707 | 22.8654 | 22.8593 | 22.8568 | 22.8543 | 22.8506 | 22.8483 | 22.8424 | 22.8294 | 22.8133 | 22.7965
FAWLEY GSP | COWES & WOOTTON COMMON BSP | FRESHWATER | MINIMUM HEADROOM | SZ 34325 86965 | YES | 21.6178 | 21.6178 | 21.6178 | 21.6178 | 21.6178 | 21.6178 | 21.6178 | 21.6178 | 21.5763 | 21.3925 | 21.1168 | 20.839 | 20.567 | 20.2706 | 20.2677 | 20.2628 | 20.2575 | 20.2536 | 20.2387 | 20.2235 | 20.2079 | 20.171 | 19.7809 | 19.196 | 18.6065 | 18.0293 | 21.2633 | 21.262 | 21.2598 | 21.2575 | 21.2558 | 21.2493 | 21.2426 | 21.2358 | 21.2285 | 20.9574 | 20.3734 | 19.7817 | 19.2025
|  | FRESHWATER | CT |  |  | 21.6178 | 21.6178 | 21.6178 | 21.6178 | 21.6178 | 21.6178 | 21.6178 | 21.6178 | 21.615 | 21.4312 | 21.1554 | 20.8777 | 20.6058 | 20.2706 | 20.2677 | 20.2628 | 20.2575 | 20.2536 | 20.2494 | 20.2342 | 20.2187 | 20.2019 | 19.8629 | 19.2779 | 18.6886 | 18.1117 | 21.2633 | 21.262 | 21.2598 | 21.2575 | 21.2558 | 21.254 | 21.2473 | 21.2405 | 21.2332 | 21.0387 | 20.4556 | 19.8641 | 19.2852
|  | FRESHWATER | LW |  |  | 21.6178 | 21.6178 | 21.6178 | 21.6178 | 21.6178 | 21.6178 | 21.6178 | 21.6178 | 21.5763 | 21.3925 | 21.1168 | 20.839 | 20.567 | 20.2706 | 20.2677 | 20.2628 | 20.2575 | 20.2536 | 20.2387 | 20.2235 | 20.2079 | 20.171 | 19.7809 | 19.196 | 18.6065 | 18.0293 | 21.2633 | 21.262 | 21.2598 | 21.2575 | 21.2558 | 21.2493 | 21.2426 | 21.2358 | 21.2285 | 20.9574 | 20.3734 | 19.7817 | 19.2025
|  | FRESHWATER | ST |  |  | 21.6178 | 21.6178 | 21.6178 | 21.6178 | 21.6178 | 21.6178 | 21.6178 | 21.6178 | 21.6178 | 21.5657 | 21.381 | 21.2017 | 21.0253 | 20.2718 | 20.27 | 20.2674 | 20.2642 | 20.2615 | 20.2534 | 20.2451 | 20.2345 | 20.2231 | 20.1483 | 19.7564 | 19.3761 | 19.0018 | 21.2638 | 21.263 | 21.2618 | 21.2604 | 21.2593 | 21.2557 | 21.2521 | 21.2475 | 21.2424 | 21.2272 | 20.9332 | 20.5541 | 20.1785
|  | FRESHWATER | FS |  |  | 21.6178 | 21.6178 | 21.6178 | 21.6178 | 21.6178 | 21.6178 | 21.6178 | 21.6178 | 21.6178 | 21.6178 | 21.6178 | 21.6178 | 21.5652 | 20.2733 | 20.2725 | 20.2717 | 20.2704 | 20.2695 | 20.2673 | 20.265 | 20.262 | 20.2575 | 20.244 | 20.2242 | 20.2057 | 20.1474 | 21.2644 | 21.2641 | 21.2637 | 21.2632 | 21.2628 | 21.2618 | 21.2608 | 21.2595 | 21.2575 | 21.2516 | 21.243 | 21.2348 | 21.2271
BRAMLEY (FLEE) | CAMBERLEY RESERVE | FRIMLEY | MINIMUM HEADROOM | SU 87745 57942 | YES | 45.405 | 45.405 | 45.405 | 45.405 | 45.405 | 45.405 | 45.405 | 45.405 | 45.405 | 45.405 | 45.405 | 45.405 | 45.2468 | 42.4368 | 42.4294 | 42.4139 | 42.3988 | 42.3837 | 42.3707 | 42.3578 | 42.3449 | 42.3311 | 42.289 | 41.8123 | 40.2017 | 38.5783 | 44.3262 | 44.3188 | 44.3032 | 44.2881 | 44.273 | 44.2599 | 44.247 | 44.2341 | 44.2202 | 44.178 | 43.6069 | 42.088 | 40.5763
|  | FRIMLEY | CT |  |  | 45.405 | 45.405 | 45.405 | 45.405 | 45.405 | 45.405 | 45.405 | 45.405 | 45.405 | 45.405 | 45.405 | 45.405 | 45.3214 | 42.438 | 42.4311 | 42.4169 | 42.4031 | 42.3893 | 42.3756 | 42.3627 | 42.3498 | 42.336 | 42.2939 | 41.8978 | 40.2875 | 38.6659 | 44.3274 | 44.3205 | 44.3063 | 44.2924 | 44.2786 | 44.2648 | 44.2519 | 44.239 | 44.2251 | 44.1829 | 43.6875 | 42.1689 | 40.6579
|  | FRIMLEY | LW |  |  | 45.405 | 45.405 | 45.405 | 45.405 | 45.405 | 45.405 | 45.405 | 45.405 | 45.405 | 45.405 | 45.405 | 45.405 | 45.2468 | 42.4368 | 42.4294 | 42.4139 | 42.3988 | 42.3837 | 42.3707 | 42.3578 | 42.3449 | 42.3311 | 42.289 | 41.8123 | 40.2017 | 38.5783 | 44.3262 | 44.3188 | 44.3032 | 44.2881 | 44.273 | 44.2599 | 44.247 | 44.2341 | 44.2202 | 44.178 | 43.6069 | 42.088 | 40.5763
|  | FRIMLEY | ST |  |  | 45.405 | 45.405 | 45.405 | 45.405 | 45.405 | 45.405 | 45.405 | 45.405 | 45.405 | 45.405 | 45.405 | 45.405 | 45.405 | 42.4427 | 42.439 | 42.4328 | 42.4252 | 42.416 | 42.4058 | 42.3957 | 42.3869 | 42.3775 | 42.3489 | 42.2934 | 42.2333 | 41.2368 | 44.3322 | 44.3285 | 44.3222 | 44.3146 | 44.3054 | 44.2952 | 44.285 | 44.2762 | 44.2667 | 44.2381 | 44.1824 | 44.0366 | 43.0641
|  | FRIMLEY | FS |  |  | 45.405 | 45.405 | 45.405 | 45.405 | 45.405 | 45.405 | 45.405 | 45.405 | 45.405 | 45.405 | 45.405 | 45.405 | 45.405 | 42.4482 | 42.4475 | 42.4468 | 42.4442 | 42.4412 | 42.4377 | 42.4343 | 42.4299 | 42.4262 | 42.4151 | 42.3933 | 42.3686 | 42.3437 | 44.3376 | 44.337 | 44.3363 | 44.3337 | 44.3306 | 44.3271 | 44.3237 | 44.3193 | 44.3156 | 44.3045 | 44.2826 | 44.2578 | 44.2328
MELKSHAM GSP | FROME BSP | FROME | MINIMUM HEADROOM | ST 78850 48051 | YES | 89.7392 | 89.7163 | 88.3178 | 88.187 | 88.039 | 87.872 | 87.6849 | 87.4361 | 87.3684 | 87.1272 | 85.5098 | 83.3357 | 81.5354 | 82.5568 | 82.4835 | 81.0666 | 80.9177 | 80.7515 | 80.5633 | 80.3548 | 80.0349 | 79.444 | 77.5432 | 74.6986 | 72.2959 | 70.2768 | 86.8581 | 86.8352 | 85.4367 | 85.3059 | 85.1499 | 84.9491 | 84.3489 | 83.6664 | 83.1364 | 81.4289 | 78.802 | 76.4791 | 74.4719
|  | FROME | CT |  |  | 89.8584 | 89.8447 | 89.0056 | 88.9319 | 88.8539 | 88.7715 | 88.6828 | 88.5744 | 88.5403 | 88.4253 | 86.2071 | 83.988 | 82.1393 | 82.6768 | 82.6132 | 81.7567 | 81.6659 | 81.5707 | 81.4727 | 81.3627 | 81.2318 | 80.8332 | 79.059 | 75.4232 | 72.9756 | 70.9083 | 86.9773 | 86.9636 | 86.1245 | 86.0508 | 85.9704 | 85.8676 | 85.5389 | 84.9968 | 84.5004 | 82.9193 | 79.5171 | 77.1493 | 75.1043
|  | FROME | LW |  |  | 89.7392 | 89.7163 | 88.3178 | 88.187 | 88.039 | 87.872 | 87.6849 | 87.4361 | 87.3684 | 87.1272 | 85.5098 | 83.3357 | 81.5354 | 82.5568 | 82.4835 | 81.0666 | 80.9177 | 80.7515 | 80.5633 | 80.3548 | 80.0349 | 79.444 | 77.5432 | 74.6986 | 72.2959 | 70.2768 | 86.8581 | 86.8352 | 85.4367 | 85.3059 | 85.1499 | 84.9491 | 84.3489 | 83.6664 | 83.1364 | 81.4289 | 78.802 | 76.4791 | 74.4719
|  | FROME | ST |  |  | 89.918 | 89.9089 | 89.3495 | 89.2979 | 89.243 | 89.1846 | 89.1211 | 89.041 | 89.0078 | 88.8814 | 88.7024 | 88.3529 | 87.8335 | 82.7454 | 82.7215 | 82.1504 | 82.0857 | 82.0158 | 81.9442 | 81.8675 | 81.7722 | 81.7226 | 81.5437 | 79.9953 | 78.4737 | 77.1422 | 87.0369 | 87.0278 | 86.4684 | 86.4169 | 86.3619 | 86.3035 | 86.24 | 86.1599 | 86.1218 | 85.3985 | 83.7789 | 82.3938 | 81.1941
|  | FROME | FS |  |  | 89.9776 | 89.9731 | 89.6934 | 89.6703 | 89.6471 | 89.6236 | 89.6 | 89.5754 | 89.5597 | 89.4948 | 89.4193 | 89.2499 | 89.061 | 82.8129 | 82.7983 | 82.5153 | 82.4879 | 82.4601 | 82.4321 | 82.404 | 82.3738 | 82.3517 | 82.2663 | 82.1617 | 81.9726 | 81.7659 | 87.0965 | 87.092 | 86.8123 | 86.7892 | 86.766 | 86.7425 | 86.7189 | 86.6943 | 86.6786 | 86.6138 | 86.5382 | 86.3688 | 86.162
COWLEY GSP | HIGH WYCOMBE BSP | FRYERS LANE | MINIMUM HEADROOM | SU 84935 93873 | YES | 30.7443 | 30.7221 | 29.8146 | 29.7272 | 29.6405 | 29.5522 | 29.4639 | 29.3758 | 29.3304 | 29.1951 | 28.9684 | 28.7969 | 28.2328 | 27.8048 | 27.7761 | 26.856 | 26.7565 | 26.6583 | 26.5572 | 26.4562 | 26.3553 | 26.2963 | 26.0249 | 24.7255 | 23.4379 | 22.0979 | 29.2872 | 29.2665 | 28.3619 | 28.2772 | 28.1931 | 28.1077 | 28.0224 | 27.9371 | 27.8948 | 27.7687 | 27.5574 | 26.3657 | 25.028
|  | FRYERS LANE | CT |  |  | 30.8222 | 30.8069 | 30.2586 | 30.2026 | 30.1472 | 30.0921 | 30.0331 | 29.9742 | 29.9405 | 29.8404 | 29.1197 | 28.8101 | 28.3948 | 27.8843 | 27.8635 | 27.3044 | 27.238 | 27.173 | 27.1084 | 27.0366 | 26.965 | 26.9177 | 26.7773 | 25.0534 | 23.6279 | 22.2885 | 29.3648 | 29.3508 | 28.805 | 28.7512 | 28.6981 | 28.6451 | 28.589 | 28.533 | 28.5024 | 28.4114 | 27.7062 | 26.5554 | 25.2182
|  | FRYERS LANE | LW |  |  | 30.7443 | 30.7221 | 29.8146 | 29.7272 | 29.6405 | 29.5522 | 29.4639 | 29.3758 | 29.3304 | 29.1951 | 28.9684 | 28.7969 | 28.2328 | 27.8048 | 27.7761 | 26.856 | 26.7565 | 26.6583 | 26.5572 | 26.4562 | 26.3553 | 26.2963 | 26.0249 | 24.7255 | 23.4379 | 22.0979 | 29.2872 | 29.2665 | 28.3619 | 28.2772 | 28.1931 | 28.1077 | 28.0224 | 27.9371 | 27.8948 | 27.7687 | 27.5574 | 26.3657 | 25.028
|  | FRYERS LANE | ST |  |  | 30.8604 | 30.8489 | 30.4827 | 30.4425 | 30.4006 | 30.3612 | 30.3218 | 30.2823 | 30.2596 | 30.1924 | 30.0801 | 29.9909 | 29.8732 | 27.9226 | 27.9063 | 27.5323 | 27.4829 | 27.4303 | 27.3823 | 27.3344 | 27.2862 | 27.2542 | 27.1598 | 26.8501 | 26.0402 | 25.211 | 29.403 | 29.3925 | 29.0281 | 28.99 | 28.9506 | 28.9131 | 28.8757 | 28.8381 | 28.8175 | 28.7565 | 28.6545 | 28.5757 | 28.1374
|  | FRYERS LANE | FS |  |  | 30.9071 | 30.9032 | 30.7237 | 30.7064 | 30.6891 | 30.671 | 30.6529 | 30.6339 | 30.6238 | 30.5938 | 30.544 | 30.5063 | 30.4549 | 27.9767 | 27.9719 | 27.7915 | 27.7721 | 27.7524 | 27.7314 | 27.7105 | 27.6877 | 27.674 | 27.6335 | 27.5663 | 27.5115 | 27.4438 | 29.448 | 29.4443 | 29.265 | 29.2482 | 29.2314 | 29.214 | 29.1966 | 29.1784 | 29.1691 | 29.1415 | 29.0956 | 29.0618 | 29.0141
COWLEY GSP | DRAYTON BSP | FULSCOT | MINIMUM HEADROOM | SU 54413 89511 | NO | 24.5659 | 24.5659 | 24.5659 | 24.5659 | 24.5659 | 24.5659 | 24.5659 | 24.5659 | 24.5659 | 24.5659 | 24.1098 | 23.243 | 22.3963 | 22.8481 | 22.8378 | 22.8208 | 22.8039 | 22.7843 | 22.7638 | 22.7443 | 22.726 | 22.4093 | 21.5126 | 20.3668 | 19.3065 | 18.3076 | 19.3161 | 19.1008 | 18.7444 | 18.3897 | 17.9792 | 17.5477 | 17.1387 | 16.7557 | 16.3797 | 15.4828 | 14.3365 | 13.2759 | 12.2767
|  | FULSCOT | CT |  |  | 24.5659 | 24.5659 | 24.5659 | 24.5659 | 24.5659 | 24.5659 | 24.5659 | 24.5659 | 24.5659 | 24.5659 | 24.1098 | 23.243 | 22.3963 | 22.8481 | 22.8378 | 22.8208 | 22.8039 | 22.7843 | 22.7638 | 22.7443 | 22.726 | 22.4093 | 21.5126 | 20.3668 | 19.3065 | 18.3076 | 19.3161 | 19.1008 | 18.7444 | 18.3897 | 17.9792 | 17.5477 | 17.1387 | 16.7557 | 16.3797 | 15.4828 | 14.3365 | 13.2759 | 12.2767
|  | FULSCOT | LW |  |  | 24.5659 | 24.5659 | 24.5659 | 24.5659 | 24.5659 | 24.5659 | 24.5659 | 24.5659 | 24.5659 | 24.5659 | 24.1816 | 23.3297 | 22.4825 | 22.8487 | 22.8387 | 22.8224 | 22.8062 | 22.7873 | 22.7686 | 22.7491 | 22.7309 | 22.5118 | 21.6151 | 20.469 | 19.4088 | 18.4093 | 19.3288 | 19.1205 | 18.7786 | 18.438 | 18.0414 | 17.65 | 17.241 | 16.8581 | 16.4823 | 15.5853 | 14.4388 | 13.3782 | 12.3784
|  | FULSCOT | ST |  |  | 24.5659 | 24.5659 | 24.5659 | 24.5659 | 24.5659 | 24.5659 | 24.5659 | 24.5659 | 24.5659 | 24.5659 | 24.5659 | 24.5659 | 24.5348 | 22.8589 | 22.8486 | 22.8409 | 22.8322 | 22.8208 | 22.8079 | 22.7944 | 22.7821 | 22.7698 | 22.7403 | 22.3065 | 21.62 | 20.9723 | 19.5439 | 19.3284 | 19.1665 | 18.984 | 18.7439 | 18.4728 | 18.1906 | 17.9322 | 17.6747 | 17.0555 | 16.2769 | 15.5902 | 14.9422
|  | FULSCOT | FS |  |  | 24.5659 | 24.5659 | 24.5659 | 24.5659 | 24.5659 | 24.5659 | 24.5659 | 24.5659 | 24.5659 | 24.5659 | 24.5659 | 24.5659 | 24.5659 | 22.8654 | 22.856 | 22.8532 | 22.8494 | 22.8447 | 22.8396 | 22.8344 | 22.8291 | 22.8243 | 22.8127 | 22.7982 | 22.7857 | 22.7744 | 19.6804 | 19.4824 | 19.424 | 19.3451 | 19.2459 | 19.1383 | 19.0299 | 18.9188 | 18.8174 | 18.5746 | 18.2699 | 18.0077 | 17.7705
COWLEY GSP | WITNEY BSP | FYFIELD | MINIMUM HEADROOM | SU 42256 99551 | NO | 22.8852 | 22.8852 | 22.8852 | 22.8251 | 22.7631 | 22.6989 | 22.6314 | 22.5244 | 22.4868 | 22.3577 | 22.018 | 21.3821 | 20.9926 | 20.9083 | 20.9035 | 20.8932 | 20.8443 | 20.7621 | 20.5467 | 20.3959 | 20.2036 | 20.0834 | 19.7391 | 19.1621 | 18.4633 | 18.0137 | 19.5 | 19.5 | 19.5 | 19.4398 | 19.3778 | 19.3137 | 19.2462 | 19.1391 | 19.1016 | 18.9724 | 18.8572 | 18.4857 | 18.3705
|  | FYFIELD | CT |  |  | 22.8852 | 22.8852 | 22.8852 | 22.884 | 22.8816 | 22.8781 | 22.8729 | 22.8615 | 22.8595 | 22.6539 | 22.1684 | 21.6765 | 21.2719 | 20.9083 | 20.9035 | 20.8932 | 20.8815 | 20.7621 | 20.5467 | 20.3959 | 20.2535 | 20.1445 | 19.8354 | 19.2863 | 18.7316 | 18.2669 | 19.5 | 19.5 | 19.5 | 19.4987 | 19.4963 | 19.4928 | 19.4877 | 19.4763 | 19.4742 | 19.4634 | 19.3735 | 19.2733 | 19.2424
|  | FYFIELD | LW |  |  | 22.8852 | 22.8852 | 22.8852 | 22.8525 | 22.8145 | 22.7701 | 22.7195 | 22.6334 | 22.6202 | 22.5321 | 22.018 | 21.3821 | 20.9926 | 20.9093 | 20.9051 | 20.896 | 20.854 | 20.7943 | 20.6172 | 20.4208 | 20.2036 | 20.0834 | 19.7391 | 19.1621 | 18.4633 | 18.0137 | 19.5 | 19.5 | 19.5 | 19.4673 | 19.4292 | 19.3849 | 19.3343 | 19.2481 | 19.2349 | 19.1787 | 19.0601 | 18.8159 | 18.8002
|  | FYFIELD | ST |  |  | 22.8852 | 22.8852 | 22.8852 | 22.8251 | 22.7631 | 22.6989 | 22.6314 | 22.5244 | 22.4868 | 22.3577 | 22.2424 | 21.8709 | 21.5979 | 20.9132 | 20.9115 | 20.9083 | 20.8443 | 20.7776 | 20.7087 | 20.636 | 20.5244 | 20.4831 | 20.2266 | 19.8218 | 19.1743 | 18.7854 | 19.5 | 19.5 | 19.5 | 19.4398 | 19.3778 | 19.3137 | 19.2462 | 19.1391 | 19.1016 | 18.9724 | 18.8572 | 18.4857 | 18.3705
|  | FYFIELD | FS |  |  | 22.8852 | 22.8852 | 22.8852 | 22.8852 | 22.8851 | 22.885 | 22.8849 | 22.8845 | 22.8831 | 22.8749 | 22.8684 | 22.8373 | 22.8069 | 20.9149 | 20.9143 | 20.9134 | 20.9116 | 20.9095 | 20.9075 | 20.9054 | 20.903 | 20.9001 | 20.888 | 20.8758 | 20.8395 | 20.8045 | 19.5 | 19.5 | 19.5 | 19.5 | 19.4999 | 19.4998 | 19.4996 | 19.4993 | 19.4978 | 19.4897 | 19.4831 | 19.452 | 19.4217
LOVEDEAN GSP | HAVANT | GABLE HEAD | MINIMUM HEADROOM | SZ 72204 99904 | YES | 43.4892 | 43.4892 | 43.4892 | 43.488 | 43.4868 | 43.4856 | 43.4845 | 43.4826 | 43.4774 | 43.461 | 42.6773 | 41.7221 | 40.7878 | 40.1715 | 40.1715 | 40.1715 | 40.1703 | 40.1691 | 40.1679 | 40.1667 | 40.1649 | 40.1263 | 39.4495 | 38.355 | 37.2281 | 36.1258 | 41.8023 | 41.7977 | 41.7896 | 41.7839 | 41.7779 | 41.7638 | 41.7489 | 41.735 | 41.7205 | 41.1966 | 40.1017 | 38.9745 | 37.8718
|  | GABLE HEAD | CT |  |  | 43.4892 | 43.4892 | 43.4892 | 43.4892 | 43.4892 | 43.4892 | 43.4892 | 43.4892 | 43.4892 | 43.4892 | 42.9312 | 41.9759 | 41.0421 | 40.1715 | 40.1715 | 40.1715 | 40.1715 | 40.1715 | 40.1715 | 40.1715 | 40.1715 | 40.1715 | 39.7491 | 38.6545 | 37.5275 | 36.4258 | 41.8044 | 41.8004 | 41.7944 | 41.7908 | 41.7867 | 41.7807 | 41.7658 | 41.7519 | 41.7375 | 41.4964 | 40.4013 | 39.274 | 38.1719
|  | GABLE HEAD | LW |  |  | 43.4892 | 43.4892 | 43.4892 | 43.4892 | 43.4892 | 43.4892 | 43.4892 | 43.4892 | 43.4892 | 43.4892 | 42.6773 | 41.7221 | 40.7878 | 40.1715 | 40.1715 | 40.1715 | 40.1715 | 40.1715 | 40.1715 | 40.1715 | 40.1715 | 40.1263 | 39.4495 | 38.355 | 37.2281 | 36.1258 | 41.8027 | 41.7977 | 41.7896 | 41.7839 | 41.7779 | 41.7638 | 41.7489 | 41.735 | 41.7205 | 41.1966 | 40.1017 | 38.9745 | 37.8718
|  | GABLE HEAD | ST |  |  | 43.4892 | 43.4892 | 43.4892 | 43.4892 | 43.4892 | 43.4892 | 43.4892 | 43.4892 | 43.4892 | 43.4892 | 43.4375 | 42.8182 | 42.2142 | 40.1715 | 40.1715 | 40.1715 | 40.1715 | 40.1715 | 40.1715 | 40.1715 | 40.1715 | 40.1715 | 39.9898 | 39.2517 | 38.5212 | 37.8086 | 41.8023 | 41.798 | 41.7917 | 41.7861 | 41.7791 | 41.7689 | 41.7582 | 41.7488 | 41.7389 | 41.7128 | 40.9988 | 40.268 | 39.5552
|  | GABLE HEAD | FS |  |  | 43.4892 | 43.4892 | 43.4892 | 43.488 | 43.4868 | 43.4856 | 43.4845 | 43.4826 | 43.4774 | 43.461 | 43.4532 | 43.4286 | 43.408 | 40.1715 | 40.1715 | 40.1715 | 40.1703 | 40.1691 | 40.1679 | 40.1667 | 40.1649 | 40.1597 | 40.1433 | 40.1355 | 40.1109 | 40.0903 | 41.8068 | 41.8053 | 41.8036 | 41.8012 | 41.7986 | 41.794 | 41.7891 | 41.7833 | 41.7742 | 41.7477 | 41.7236 | 41.683 | 41.647
LOVEDEAN GSP | WYMERING BSP | GAMBLE ROAD | MINIMUM HEADROOM | SU 64771 01769 | YES | 45.3694 | 45.3694 | 45.3694 | 45.2344 | 45.0951 | 44.9496 | 44.7988 | 44.5697 | 44.538 | 44.4292 | 43.2629 | 41.1503 | 39.4934 | 43.1923 | 43.1736 | 43.127 | 42.9427 | 42.7241 | 42.4287 | 42.1142 | 41.7057 | 41.4827 | 40.1262 | 36.5307 | 33.9773 | 31.926 | 44.4293 | 44.4259 | 44.4172 | 44.2731 | 44.1191 | 43.9458 | 43.7647 | 43.5024 | 43.4352 | 42.5708 | 38.9629 | 36.4013 | 34.3427
|  | GAMBLE ROAD | CT |  |  | 45.3694 | 45.3694 | 45.3694 | 45.3694 | 45.3694 | 45.3694 | 45.3694 | 45.3694 | 45.3694 | 45.3694 | 44.5309 | 42.6981 | 41.059 | 43.1923 | 43.1736 | 43.127 | 43.0777 | 42.9984 | 42.9138 | 42.7503 | 42.5708 | 42.3795 | 41.2694 | 37.8385 | 35.5648 | 33.5315 | 44.4293 | 44.4259 | 44.4172 | 44.4081 | 44.3934 | 44.3777 | 44.3474 | 44.3142 | 44.2788 | 43.7169 | 40.2715 | 37.9896 | 35.949
|  | GAMBLE ROAD | LW |  |  | 45.3694 | 45.3694 | 45.3694 | 45.2344 | 45.0951 | 44.9496 | 44.7988 | 44.5697 | 44.538 | 44.4292 | 43.2629 | 41.1503 | 39.4934 | 43.1923 | 43.1736 | 43.127 | 42.9427 | 42.7241 | 42.4287 | 42.1142 | 41.7057 | 41.4827 | 40.1262 | 36.5307 | 33.9773 | 31.926 | 44.4293 | 44.4259 | 44.4172 | 44.2731 | 44.1191 | 43.9458 | 43.7647 | 43.5024 | 43.4352 | 42.5708 | 38.9629 | 36.4013 | 34.3427
|  | GAMBLE ROAD | ST |  |  | 45.3694 | 45.3694 | 45.3694 | 45.3605 | 45.3514 | 45.3421 | 45.3326 | 45.3178 | 45.3128 | 45.2967 | 45.2829 | 45.2347 | 44.1696 | 43.2203 | 43.1876 | 43.1602 | 43.12 | 43.0577 | 42.9738 | 42.8802 | 42.7444 | 42.6082 | 42.1207 | 40.2827 | 38.7435 | 37.4254 | 44.4345 | 44.4285 | 44.4234 | 44.4087 | 44.3897 | 44.3666 | 44.3415 | 44.3043 | 44.275 | 44.1716 | 42.7247 | 41.1802 | 39.8574
|  | GAMBLE ROAD | FS |  |  | 45.3694 | 45.3694 | 45.3694 | 45.3694 | 45.3694 | 45.3694 | 45.3694 | 45.3694 | 45.3694 | 45.3694 | 45.3694 | 45.3694 | 45.3694 | 43.2291 | 43.2028 | 43.1904 | 43.1761 | 43.1527 | 43.1259 | 43.0963 | 43.0616 | 43.0099 | 42.8237 | 42.5061 | 42.3031 | 42.1227 | 44.4361 | 44.4313 | 44.429 | 44.4263 | 44.422 | 44.417 | 44.4115 | 44.4051 | 44.3955 | 44.361 | 44.3022 | 44.2646 | 44.2312
IVER 132KV | DENHAM | GERRARDS CROSS | MINIMUM HEADROOM | SU 99973 87964 | YES | 21.3883 | 21.3883 | 21.3883 | 21.3636 | 21.3382 | 21.312 | 21.2843 | 21.2406 | 21.2349 | 21.0201 | 20.4115 | 19.754 | 19.1895 | 18.6586 | 18.6487 | 18.6279 | 18.4976 | 18.0572 | 17.748 | 17.6205 | 17.4777 | 17.3654 | 17.0264 | 16.3459 | 15.6108 | 14.9695 | 20.6318 | 20.6192 | 20.5927 | 20.5495 | 20.5007 | 20.4513 | 20.4178 | 20.3683 | 20.3564 | 20.3183 | 19.7384 | 19.007 | 18.3695
|  | GERRARDS CROSS | CT |  |  | 21.3883 | 21.3883 | 21.3883 | 21.3636 | 21.3382 | 21.312 | 21.2843 | 21.2406 | 21.2349 | 21.0201 | 20.4115 | 19.754 | 19.1895 | 18.6601 | 18.651 | 18.6319 | 18.5887 | 18.1718 | 17.748 | 17.6205 | 17.4777 | 17.3654 | 17.0264 | 16.3459 | 15.6108 | 14.9695 | 20.6337 | 20.6222 | 20.5978 | 20.5495 | 20.5007 | 20.4513 | 20.4178 | 20.3683 | 20.3564 | 20.3183 | 19.7384 | 19.007 | 18.3695
|  | GERRARDS CROSS | LW |  |  | 21.3883 | 21.3883 | 21.3883 | 21.3872 | 21.3848 | 21.381 | 21.3758 | 21.3653 | 21.3635 | 21.2779 | 20.7567 | 20.1736 | 19.6368 | 18.6586 | 18.6487 | 18.6279 | 18.4976 | 18.0572 | 17.953 | 17.848 | 17.7384 | 17.6301 | 17.3012 | 16.7082 | 16.0475 | 15.4339 | 20.6318 | 20.6192 | 20.5927 | 20.5658 | 20.5378 | 20.5282 | 20.5172 | 20.5009 | 20.4929 | 20.4651 | 20.0999 | 19.4429 | 18.8331
|  | GERRARDS CROSS | ST |  |  | 21.3883 | 21.3883 | 21.3883 | 21.3881 | 21.3876 | 21.3869 | 21.3858 | 21.3833 | 21.3821 | 21.3758 | 21.3676 | 21.3386 | 21.3281 | 18.6688 | 18.665 | 18.6585 | 18.6504 | 18.6404 | 18.6348 | 18.6289 | 18.6234 | 18.6189 | 18.6027 | 18.2592 | 17.8305 | 17.4254 | 20.6408 | 20.64 | 20.6317 | 20.6214 | 20.6088 | 20.6019 | 20.5947 | 20.5883 | 20.5829 | 20.564 | 20.5334 | 20.4812 | 20.4477
|  | GERRARDS CROSS | FS |  |  | 21.3883 | 21.3883 | 21.3883 | 21.3883 | 21.3883 | 21.3883 | 21.3882 | 21.3881 | 21.3877 | 21.3854 | 21.3836 | 21.375 | 21.3666 | 18.6742 | 18.6735 | 18.6728 | 18.6697 | 18.6659 | 18.6642 | 18.6624 | 18.6601 | 18.6584 | 18.6523 | 18.6438 | 18.628 | 18.6126 | 20.6408 | 20.6408 | 20.6408 | 20.6408 | 20.6408 | 20.6389 | 20.6367 | 20.6338 | 20.6317 | 20.6246 | 20.6142 | 20.5965 | 20.5792
MANNINGTON GSP | SHAFTESBURY BSP | GILLINGHAM | MINIMUM HEADROOM | ST 80185 25765 | YES | 40.9253 | 40.9253 | 40.9253 | 40.9246 | 40.9232 | 40.9211 | 40.9181 | 40.8649 | 40.6875 | 40.1112 | 39.2339 | 38.8433 | 38.5051 | 38.5991 | 38.5679 | 38.4961 | 38.4039 | 38.2841 | 38.1027 | 37.9312 | 37.7206 | 37.5095 | 36.8239 | 35.7811 | 35.3206 | 34.9179 | 39.3884 | 39.3577 | 39.2869 | 39.1961 | 39.0781 | 38.8993 | 38.7302 | 38.5227 | 38.3146 | 37.6391 | 36.6114 | 36.1573 | 35.7606
|  | GILLINGHAM | CT |  |  | 40.9253 | 40.9253 | 40.9253 | 40.9251 | 40.9247 | 40.9241 | 40.9233 | 40.9161 | 40.7394 | 40.1667 | 39.2878 | 38.9063 | 38.5649 | 38.5991 | 38.5679 | 38.4961 | 38.4043 | 38.2856 | 38.1556 | 37.9862 | 37.7798 | 37.5694 | 36.8874 | 35.843 | 35.3915 | 34.9857 | 39.3884 | 39.3577 | 39.2869 | 39.1965 | 39.0795 | 38.9514 | 38.7845 | 38.5812 | 38.3738 | 37.7018 | 36.6726 | 36.2275 | 35.8276
|  | GILLINGHAM | LW |  |  | 40.9253 | 40.9253 | 40.9253 | 40.9246 | 40.9232 | 40.9211 | 40.9181 | 40.8649 | 40.6875 | 40.1112 | 39.2339 | 38.8433 | 38.5051 | 38.5991 | 38.5679 | 38.4961 | 38.4039 | 38.2841 | 38.1027 | 37.9312 | 37.7206 | 37.5095 | 36.8239 | 35.7811 | 35.3206 | 34.9179 | 39.3884 | 39.3577 | 39.2869 | 39.1961 | 39.0781 | 38.8993 | 38.7302 | 38.5227 | 38.3146 | 37.6391 | 36.6114 | 36.1573 | 35.7606
|  | GILLINGHAM | ST |  |  | 40.9253 | 40.9253 | 40.9253 | 40.9251 | 40.9248 | 40.9244 | 40.9238 | 40.9224 | 40.9217 | 40.6234 | 40.0062 | 39.7524 | 39.5288 | 38.782 | 38.5881 | 38.5442 | 38.4848 | 38.4052 | 38.2995 | 38.2007 | 38.0618 | 37.9171 | 37.4317 | 36.6973 | 36.3981 | 36.1328 | 39.8087 | 39.3776 | 39.3343 | 39.2758 | 39.1974 | 39.0932 | 38.9958 | 38.859 | 38.7164 | 38.2381 | 37.5145 | 37.2194 | 36.958
|  | GILLINGHAM | FS |  |  | 40.9253 | 40.9253 | 40.9253 | 40.9253 | 40.9252 | 40.9252 | 40.9252 | 40.9251 | 40.9249 | 40.9236 | 40.9226 | 40.87 | 40.7834 | 38.7826 | 38.6066 | 38.5866 | 38.5575 | 38.5216 | 38.4788 | 38.441 | 38.3922 | 38.335 | 38.1432 | 37.841 | 37.7257 | 37.6234 | 39.8194 | 39.3978 | 39.3761 | 39.3475 | 39.3121 | 39.2699 | 39.2327 | 39.1846 | 39.1283 | 38.9392 | 38.6414 | 38.5277 | 38.4269
BRAMLEY (FLEE) | ALDERSHOT BSP | GODALMING | MINIMUM HEADROOM | SU 96743 44375 | YES | 45.584 | 45.584 | 45.584 | 45.584 | 45.584 | 45.584 | 45.584 | 45.584 | 45.584 | 45.584 | 45.1093 | 44.0398 | 42.9879 | 42.2882 | 42.2643 | 42.2154 | 42.169 | 42.1228 | 41.566 | 41.3434 | 41.123 | 40.8872 | 40.1893 | 39.0101 | 37.7867 | 36.5833 | 43.9495 | 43.9495 | 43.9495 | 43.9495 | 43.9427 | 43.9101 | 43.8971 | 43.8843 | 43.8615 | 43.1943 | 41.9903 | 40.7283 | 39.4869
|  | GODALMING | CT |  |  | 45.584 | 45.584 | 45.584 | 45.584 | 45.584 | 45.584 | 45.584 | 45.584 | 45.584 | 45.584 | 45.1093 | 44.0398 | 42.9879 | 42.2882 | 42.2643 | 42.2154 | 42.169 | 42.1228 | 41.566 | 41.3434 | 41.123 | 40.8872 | 40.1893 | 39.0101 | 37.7867 | 36.5833 | 43.9495 | 43.9495 | 43.9495 | 43.9495 | 43.9427 | 43.9101 | 43.8971 | 43.8843 | 43.8615 | 43.1943 | 41.9903 | 40.7283 | 39.4869
|  | GODALMING | LW |  |  | 45.584 | 45.584 | 45.584 | 45.584 | 45.584 | 45.584 | 45.584 | 45.584 | 45.584 | 45.584 | 45.584 | 44.5278 | 43.4749 | 42.2919 | 42.27 | 42.2255 | 42.1832 | 42.1411 | 42.1227 | 41.9017 | 41.6812 | 41.4455 | 40.7476 | 39.5684 | 38.3449 | 37.1404 | 43.9495 | 43.9495 | 43.9495 | 43.9495 | 43.9495 | 43.9426 | 43.9296 | 43.9168 | 43.9031 | 43.728 | 42.5663 | 41.3041 | 40.0616
|  | GODALMING | ST |  |  | 45.584 | 45.584 | 45.584 | 45.584 | 45.584 | 45.584 | 45.584 | 45.584 | 45.584 | 45.584 | 45.584 | 45.584 | 45.584 | 42.3089 | 42.2979 | 42.2798 | 42.2584 | 42.2325 | 42.2166 | 42.2009 | 42.1886 | 42.1754 | 42.1367 | 41.5079 | 40.7184 | 39.9363 | 43.9495 | 43.9495 | 43.9495 | 43.9495 | 43.9495 | 43.9495 | 43.9495 | 43.9495 | 43.9495 | 43.9495 | 43.9067 | 43.7001 | 42.9458
|  | GODALMING | FS |  |  | 45.584 | 45.584 | 45.584 | 45.584 | 45.584 | 45.584 | 45.584 | 45.584 | 45.584 | 45.584 | 45.584 | 45.584 | 45.584 | 42.3253 | 42.3231 | 42.3212 | 42.3142 | 42.3057 | 42.3 | 42.2943 | 42.2871 | 42.282 | 42.267 | 42.2423 | 42.2183 | 42.1953 | 43.9495 | 43.9495 | 43.9495 | 43.9495 | 43.9495 | 43.9495 | 43.9495 | 43.9495 | 43.9495 | 43.9495 | 43.9495 | 43.9495 | 43.9495
WILLESDEN GSP | ACTON LANE | GOLDSMITHS | MINIMUM HEADROOM | TQ 21089 80758 | YES | 14.69 | 14.6865 | 14.6799 | 14.673 | 14.6654 | 14.6548 | 14.6454 | 14.6365 | 14.6275 | 14.5998 | 14.5409 | 13.868 | 13.0712 | 13.8057 | 13.803 | 13.7979 | 13.7925 | 13.7867 | 13.7784 | 13.7711 | 13.7643 | 13.7573 | 13.7359 | 13.0813 | 12.1842 | 11.2685 | 14.002 | 13.9981 | 13.9909 | 13.9833 | 13.975 | 13.9633 | 13.953 | 13.9433 | 13.9334 | 13.8964 | 13.5027 | 12.7453 | 11.8096
|  | GOLDSMITHS | CT |  |  | 14.6901 | 14.6867 | 14.6802 | 14.6734 | 14.6659 | 14.6583 | 14.6489 | 14.6401 | 14.6311 | 14.6034 | 14.5444 | 13.9099 | 13.1131 | 13.8058 | 13.8031 | 13.7981 | 13.7928 | 13.787 | 13.7812 | 13.7739 | 13.7671 | 13.7601 | 13.7386 | 13.1282 | 12.2311 | 11.3178 | 14.0021 | 13.9983 | 13.9912 | 13.9837 | 13.9756 | 13.9673 | 13.957 | 13.9473 | 13.9374 | 13.907 | 13.5268 | 12.7945 | 11.8587
|  | GOLDSMITHS | LW |  |  | 14.69 | 14.6865 | 14.6799 | 14.673 | 14.6654 | 14.6548 | 14.6454 | 14.6365 | 14.6275 | 14.5998 | 14.5409 | 13.868 | 13.0712 | 13.8057 | 13.803 | 13.7979 | 13.7925 | 13.7867 | 13.7784 | 13.7711 | 13.7643 | 13.7573 | 13.7359 | 13.0813 | 12.1842 | 11.2685 | 14.002 | 13.9981 | 13.9909 | 13.9833 | 13.975 | 13.9633 | 13.953 | 13.9433 | 13.9334 | 13.8964 | 13.5027 | 12.7453 | 11.8096
|  | GOLDSMITHS | ST |  |  | 14.6917 | 14.6896 | 14.6861 | 14.6818 | 14.6766 | 14.6689 | 14.6621 | 14.6561 | 14.65 | 14.6311 | 14.5907 | 14.5457 | 14.2186 | 13.807 | 13.8053 | 13.8027 | 13.7994 | 13.7953 | 13.7894 | 13.7841 | 13.7795 | 13.7747 | 13.7601 | 13.7288 | 13.1447 | 12.5761 | 14.0039 | 14.0015 | 13.9977 | 13.993 | 13.9873 | 13.9789 | 13.9714 | 13.9648 | 13.9581 | 13.9374 | 13.8371 | 13.5353 | 13.157
|  | GOLDSMITHS | FS |  |  | 14.6939 | 14.6931 | 14.6921 | 14.6905 | 14.6883 | 14.685 | 14.6821 | 14.6787 | 14.675 | 14.6636 | 14.6454 | 14.6197 | 14.5945 | 13.8088 | 13.8081 | 13.8073 | 13.8061 | 13.8043 | 13.8017 | 13.7994 | 13.7966 | 13.7935 | 13.7837 | 13.7692 | 13.7479 | 13.7272 | 14.0063 | 14.0054 | 14.0043 | 14.0025 | 14.0002 | 13.9966 | 13.9934 | 13.9897 | 13.9858 | 13.9737 | 13.9539 | 13.9263 | 13.8992
NURSLING GSP | WINCHESTER | GORDON ROAD | MINIMUM HEADROOM | SU 48217 29991 | YES | 43.34 | 43.34 | 43.34 | 43.34 | 43.34 | 43.34 | 43.34 | 43.34 | 43.34 | 43.34 | 43.3389 | 43.2683 | 43.1993 | 41.9839 | 41.7872 | 41.3632 | 40.9275 | 40.474 | 40.0032 | 39.748 | 39.5202 | 39.3053 | 38.6925 | 37.7104 | 36.7006 | 35.7149 | 39.3082 | 39.3082 | 39.1477 | 38.7774 | 38.3404 | 37.8818 | 37.6333 | 37.4113 | 37.202 | 36.5992 | 35.6303 | 34.634 | 33.6614
|  | GORDON ROAD | CT |  |  | 43.34 | 43.34 | 43.34 | 43.34 | 43.34 | 43.34 | 43.34 | 43.34 | 43.34 | 43.34 | 43.3389 | 43.2683 | 43.1993 | 41.9839 | 41.7872 | 41.3632 | 40.9275 | 40.474 | 40.0032 | 39.748 | 39.5202 | 39.3053 | 38.6925 | 37.7104 | 36.7006 | 35.7149 | 39.3082 | 39.3082 | 39.1477 | 38.7774 | 38.3404 | 37.8818 | 37.6333 | 37.4113 | 37.202 | 36.5992 | 35.6303 | 34.634 | 33.6614
|  | GORDON ROAD | LW |  |  | 43.34 | 43.34 | 43.34 | 43.34 | 43.34 | 43.34 | 43.34 | 43.34 | 43.34 | 43.34 | 43.34 | 43.2966 | 43.2277 | 42.0227 | 41.8474 | 41.4689 | 41.0772 | 40.6673 | 40.4091 | 40.154 | 39.9261 | 39.7112 | 39.0983 | 38.1163 | 37.1063 | 36.1204 | 39.3082 | 39.3082 | 39.2375 | 38.9047 | 38.5287 | 38.2772 | 38.0287 | 37.8067 | 37.5974 | 36.9996 | 36.0308 | 35.0343 | 34.0616
|  | GORDON ROAD | ST |  |  | 43.34 | 43.34 | 43.34 | 43.34 | 43.34 | 43.34 | 43.34 | 43.34 | 43.34 | 43.34 | 43.34 | 43.34 | 43.34 | 42.1762 | 42.0966 | 41.9548 | 41.7655 | 41.5275 | 41.3287 | 41.1331 | 40.9783 | 40.8318 | 40.4179 | 39.7631 | 39.1121 | 38.4719 | 39.3082 | 39.3082 | 39.3082 | 39.3082 | 39.2873 | 39.1184 | 38.9521 | 38.8206 | 38.6889 | 38.2858 | 37.6479 | 37.0133 | 36.3816
|  | GORDON ROAD | FS |  |  | 43.34 | 43.34 | 43.34 | 43.34 | 43.34 | 43.34 | 43.34 | 43.34 | 43.34 | 43.34 | 43.34 | 43.34 | 43.34 | 42.297 | 42.2837 | 42.2679 | 42.1971 | 42.1094 | 42.0335 | 41.9599 | 41.8792 | 41.8227 | 41.6635 | 41.4155 | 41.1774 | 40.9537 | 39.3082 | 39.3082 | 39.3082 | 39.3082 | 39.3082 | 39.3082 | 39.3082 | 39.3082 | 39.3082 | 39.3082 | 39.1922 | 38.9898 | 38.7997
BRAMLEY (FLEE) | BURGHFIELD RESERVE | GORING | MINIMUM HEADROOM | SU 60305 82895 | YES | 20.9611 | 20.9245 | 20.8476 | 20.7729 | 20.6989 | 20.6255 | 20.5864 | 20.5475 | 20.5057 | 20.3803 | 20.1549 | 19.9103 | 19.6683 | 20.072 | 20.072 | 20.072 | 20.072 | 20.072 | 20.072 | 20.072 | 20.072 | 20.072 | 20.072 | 20.072 | 20.072 | 20.072 | 20.7963 | 20.7963 | 20.7963 | 20.7963 | 20.7963 | 20.7963 | 20.7963 | 20.7963 | 20.7963 | 20.7963 | 20.7963 | 20.7963 | 20.7963
|  | GORING | CT |  |  | 20.9611 | 20.9245 | 20.8476 | 20.7729 | 20.6989 | 20.6255 | 20.5864 | 20.5475 | 20.5057 | 20.3803 | 20.1549 | 19.9103 | 19.6683 | 20.072 | 20.072 | 20.072 | 20.072 | 20.072 | 20.072 | 20.072 | 20.072 | 20.072 | 20.072 | 20.072 | 20.072 | 20.072 | 20.7963 | 20.7963 | 20.7963 | 20.7963 | 20.7963 | 20.7963 | 20.7963 | 20.7963 | 20.7963 | 20.7963 | 20.7963 | 20.7963 | 20.7963
|  | GORING | LW |  |  | 20.9934 | 20.9746 | 20.9352 | 20.897 | 20.8589 | 20.8196 | 20.7804 | 20.7416 | 20.6998 | 20.5744 | 20.3489 | 20.1042 | 19.8619 | 20.072 | 20.072 | 20.072 | 20.072 | 20.072 | 20.072 | 20.072 | 20.072 | 20.072 | 20.072 | 20.072 | 20.072 | 20.072 | 20.7963 | 20.7963 | 20.7963 | 20.7963 | 20.7963 | 20.7963 | 20.7963 | 20.7963 | 20.7963 | 20.7963 | 20.7963 | 20.7963 | 20.7963
|  | GORING | ST |  |  | 21.0095 | 21.0008 | 20.9861 | 20.9679 | 20.9461 | 20.9155 | 20.8853 | 20.8587 | 20.8302 | 20.7455 | 20.5938 | 20.4349 | 20.2779 | 20.072 | 20.072 | 20.072 | 20.072 | 20.072 | 20.072 | 20.072 | 20.072 | 20.072 | 20.072 | 20.072 | 20.072 | 20.072 | 20.7963 | 20.7963 | 20.7963 | 20.7963 | 20.7963 | 20.7963 | 20.7963 | 20.7963 | 20.7963 | 20.7963 | 20.7963 | 20.7963 | 20.7963
|  | GORING | FS |  |  | 21.0236 | 21.0223 | 21.0211 | 21.0164 | 21.0107 | 20.9997 | 20.9886 | 20.9744 | 20.9632 | 20.9303 | 20.8718 | 20.81 | 20.7491 | 20.072 | 20.072 | 20.072 | 20.072 | 20.072 | 20.072 | 20.072 | 20.072 | 20.072 | 20.072 | 20.072 | 20.072 | 20.072 | 20.7963 | 20.7963 | 20.7963 | 20.7963 | 20.7963 | 20.7963 | 20.7963 | 20.7963 | 20.7963 | 20.7963 | 20.7963 | 20.7963 | 20.7963
IVER 132KV | DENHAM | GRASSINGHAM ROAD | MINIMUM HEADROOM | TQ 00165 90988 | YES | 43.0567 | 43.0567 | 43.0567 | 43.0362 | 43.015 | 42.9932 | 42.9698 | 42.9327 | 42.9278 | 42.866 | 42.8119 | 42.3106 | 41.6013 | 41.4214 | 41.4214 | 41.4214 | 41.401 | 41.3798 | 41.3579 | 41.3346 | 41.2974 | 41.2925 | 41.1922 | 40.3405 | 39.4356 | 38.6283 | 41.3601 | 41.3601 | 41.3601 | 41.3397 | 41.3185 | 41.2966 | 41.2733 | 41.2361 | 41.2312 | 41.1695 | 41.1154 | 40.9414 | 40.2758
|  | GRASSINGHAM ROAD | CT |  |  | 43.0567 | 43.0567 | 43.0567 | 43.0362 | 43.015 | 42.9932 | 42.9698 | 42.9327 | 42.9278 | 42.9106 | 42.8139 | 42.3106 | 41.6013 | 41.4214 | 41.4214 | 41.4214 | 41.401 | 41.3798 | 41.3579 | 41.3346 | 41.2974 | 41.2925 | 41.1922 | 40.3405 | 39.4356 | 38.6283 | 41.3601 | 41.3601 | 41.3601 | 41.3397 | 41.3185 | 41.2966 | 41.2733 | 41.2361 | 41.2312 | 41.214 | 41.1174 | 41.0031 | 40.2758
|  | GRASSINGHAM ROAD | LW |  |  | 43.0567 | 43.0567 | 43.0567 | 43.0553 | 43.0524 | 43.0478 | 43.0416 | 43.0289 | 43.0268 | 43.0157 | 42.9886 | 42.6249 | 41.9403 | 41.4214 | 41.4214 | 41.4214 | 41.42 | 41.4171 | 41.4126 | 41.4063 | 41.3937 | 41.3915 | 41.3804 | 40.6047 | 39.7612 | 38.9785 | 41.3601 | 41.3601 | 41.3601 | 41.3587 | 41.3559 | 41.3513 | 41.345 | 41.3324 | 41.3302 | 41.3191 | 41.2921 | 41.2394 | 40.6254
|  | GRASSINGHAM ROAD | ST |  |  | 43.0567 | 43.0567 | 43.0567 | 43.0564 | 43.0558 | 43.0549 | 43.0536 | 43.0506 | 43.0492 | 43.0416 | 43.0317 | 42.9968 | 42.9841 | 41.4214 | 41.4214 | 41.4214 | 41.4211 | 41.4205 | 41.4197 | 41.4183 | 41.4154 | 41.414 | 41.4064 | 41.3965 | 41.1801 | 40.6616 | 41.3601 | 41.3601 | 41.3601 | 41.3598 | 41.3593 | 41.3584 | 41.3571 | 41.3541 | 41.3527 | 41.3451 | 41.3352 | 41.3003 | 41.2876
|  | GRASSINGHAM ROAD | FS |  |  | 43.0567 | 43.0567 | 43.0567 | 43.0487 | 43.0409 | 43.0331 | 43.0251 | 43.0127 | 42.9778 | 42.866 | 42.8119 | 42.6379 | 42.491 | 41.4214 | 41.4214 | 41.4214 | 41.4135 | 41.4057 | 41.3979 | 41.3899 | 41.3774 | 41.3426 | 41.2308 | 41.1766 | 41.0027 | 40.8557 | 41.3601 | 41.3601 | 41.3601 | 41.3522 | 41.3444 | 41.3366 | 41.3286 | 41.3161 | 41.2813 | 41.1695 | 41.1154 | 40.9414 | 40.7945
BRAMLEY (FLEE) | BURGHFIELD MAIN | GREEN PARK | MINIMUM HEADROOM |  |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
|  | GREEN PARK | CT |  |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
|  | GREEN PARK | LW |  |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
|  | GREEN PARK | ST |  |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
|  | GREEN PARK | FS |  |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
WILLESDEN GSP |  | GREENFORD | MINIMUM HEADROOM | TQ 14695 83785 |  | 55.2121 | 55.2121 | 55.2121 | 55.188 | 55.1635 | 55.1385 | 55.1127 | 55.0728 | 55.0592 | 55.016 | 54.9812 | 53.2626 | 51.3576 | 54.0955 | 54.0654 | 54.0567 | 54.0473 | 54.0271 | 53.9884 | 53.947 | 53.8867 | 53.8544 | 53.7587 | 53.0761 | 50.8441 | 48.4523 | 46.7844 | 46.431 | 46.3289 | 46.2186 | 46.0935 | 45.7892 | 45.4525 | 45.1 | 44.778 | 43.883 | 42.3855 | 40.7732 | 39.1872
|  | GREENFORD | CT |  |  | 55.2121 | 55.2121 | 55.2121 | 55.2121 | 55.2121 | 55.2121 | 55.2121 | 55.2121 | 55.2121 | 55.2121 | 55.2121 | 53.4671 | 51.564 | 54.0955 | 54.0654 | 54.0567 | 54.0473 | 54.0366 | 54.0252 | 53.9965 | 53.9664 | 53.939 | 53.8627 | 53.309 | 51.1011 | 48.7091 | 46.7844 | 46.431 | 46.3289 | 46.2186 | 46.0935 | 45.9594 | 45.6227 | 45.2702 | 44.9483 | 44.0533 | 42.5557 | 40.9436 | 39.3574
|  | GREENFORD | LW |  |  | 55.2121 | 55.2121 | 55.2121 | 55.2121 | 55.2121 | 55.2121 | 55.2121 | 55.2121 | 55.2121 | 55.2121 | 55.197 | 53.2626 | 51.3576 | 54.0955 | 54.0654 | 54.0567 | 54.0473 | 54.0366 | 54.0107 | 53.982 | 53.9519 | 53.9245 | 53.8482 | 53.0761 | 50.8441 | 48.4523 | 46.7844 | 46.431 | 46.3289 | 46.2186 | 46.0935 | 45.7892 | 45.4525 | 45.1 | 44.778 | 43.883 | 42.3855 | 40.7732 | 39.1872
|  | GREENFORD | ST |  |  | 55.2121 | 55.2121 | 55.2121 | 55.188 | 55.1635 | 55.1385 | 55.1127 | 55.0728 | 55.0592 | 55.016 | 54.9812 | 54.8705 | 54.4109 | 54.103 | 54.0939 | 54.0888 | 54.0588 | 54.0271 | 53.9884 | 53.947 | 53.8867 | 53.8544 | 53.7587 | 53.6368 | 53.4365 | 52.2327 | 46.8718 | 46.7648 | 46.7054 | 46.6116 | 46.5029 | 46.3169 | 46.1086 | 45.8302 | 45.5961 | 44.9384 | 43.8819 | 42.7195 | 41.6677
|  | GREENFORD | FS |  |  | 55.2121 | 55.2121 | 55.2121 | 55.2121 | 55.2121 | 55.2121 | 55.2121 | 55.2121 | 55.2121 | 55.2121 | 55.2121 | 55.2121 | 55.2121 | 54.1054 | 54.0982 | 54.0959 | 54.0932 | 54.0902 | 54.0852 | 54.0796 | 54.0729 | 54.0655 | 54.0451 | 54.0105 | 53.9733 | 53.9363 | 46.9005 | 46.8151 | 46.789 | 46.7575 | 46.7223 | 46.6634 | 46.5971 | 46.519 | 46.4326 | 46.1928 | 45.7872 | 45.3507 | 44.9168
LOVEDEAN GSP | PORTSMOUTH BSP | GREETHAM STREET | MINIMUM HEADROOM | SU 64445 00178 | YES | 43.8013 | 43.8013 | 43.8013 | 43.7066 | 43.6102 | 43.5122 | 43.4099 | 43.2522 | 43.2322 | 43.168 | 42.8716 | 42.5632 | 42.1724 | 41.1398 | 41.1384 | 41.1354 | 41.0374 | 40.9372 | 40.8357 | 40.7287 | 40.5668 | 40.5426 | 40.4542 | 39.3774 | 38.0226 | 36.8545 | 42.9235 | 42.9219 | 42.9183 | 42.8197 | 42.7188 | 42.6167 | 42.5088 | 42.3461 | 42.3211 | 42.2401 | 41.8964 | 41.5267 | 41.3905
|  | GREETHAM STREET | CT |  |  | 43.8013 | 43.8013 | 43.8013 | 43.7066 | 43.6102 | 43.5122 | 43.4099 | 43.2522 | 43.2322 | 43.168 | 42.8716 | 42.5632 | 42.1724 | 41.1398 | 41.1384 | 41.1354 | 41.0374 | 40.9372 | 40.8357 | 40.7287 | 40.5668 | 40.5426 | 40.4542 | 39.3774 | 38.0226 | 36.8545 | 42.9235 | 42.9219 | 42.9183 | 42.8197 | 42.7188 | 42.6167 | 42.5088 | 42.3461 | 42.3211 | 42.2401 | 41.8964 | 41.5267 | 41.3905
|  | GREETHAM STREET | LW |  |  | 43.8013 | 43.8013 | 43.8013 | 43.8013 | 43.8013 | 43.8013 | 43.8013 | 43.8013 | 43.8013 | 43.8013 | 43.8013 | 43.8013 | 43.4684 | 41.1398 | 41.1384 | 41.1354 | 41.1321 | 41.1284 | 41.1239 | 41.1192 | 41.115 | 41.1108 | 41.0693 | 40.2889 | 39.2418 | 38.1474 | 42.9235 | 42.9219 | 42.9183 | 42.9144 | 42.9099 | 42.9047 | 42.8991 | 42.8941 | 42.8891 | 42.8723 | 42.825 | 42.7638 | 42.702
|  | GREETHAM STREET | ST |  |  | 43.8013 | 43.8013 | 43.8013 | 43.8013 | 43.8013 | 43.8013 | 43.8013 | 43.8013 | 43.8013 | 43.8013 | 43.8013 | 43.8013 | 43.8013 | 41.1406 | 41.1398 | 41.1381 | 41.1362 | 41.1336 | 41.1308 | 41.1278 | 41.125 | 41.1221 | 41.1124 | 40.8311 | 40.1602 | 39.49 | 42.9244 | 42.9235 | 42.9215 | 42.9192 | 42.9162 | 42.9129 | 42.9093 | 42.906 | 42.9026 | 42.891 | 42.8578 | 42.8173 | 42.7782
|  | GREETHAM STREET | FS |  |  | 43.8013 | 43.8013 | 43.8013 | 43.8001 | 43.7989 | 43.7978 | 43.7966 | 43.7947 | 43.7896 | 43.7731 | 43.7653 | 43.7407 | 43.7201 | 41.1439 | 41.1413 | 41.1408 | 41.1389 | 41.1367 | 41.1346 | 41.1323 | 41.1294 | 41.1231 | 41.1029 | 41.0834 | 41.0425 | 40.7751 | 42.9284 | 42.9253 | 42.9247 | 42.9226 | 42.9203 | 42.918 | 42.9155 | 42.9124 | 42.9059 | 42.885 | 42.8634 | 42.8195 | 42.7782
COWLEY GSP | DRAYTON BSP | GROVE | MINIMUM HEADROOM | SU 39515 89611 | NO | 22.3589 | 22.3483 | 21.7035 | 21.649 | 21.5926 | 21.5343 | 21.474 | 21.4059 | 21.3822 | 20.5964 | 19.0413 | 18.097 | 17.3543 | 15.073 | 15.0082 | 14.283 | 14.1485 | 14.0031 | 13.8047 | 13.5893 | 13.3204 | 13.1254 | 12.5491 | 11.5689 | 10.9563 | 10.466 | 21.0913 | 21.0808 | 20.4359 | 20.3814 | 20.3251 | 20.2668 | 20.2064 | 20.0953 | 19.7262 | 18.6362 | 16.7898 | 15.6775 | 14.807
|  | GROVE | CT |  |  | 22.4139 | 22.4075 | 22.0206 | 21.9884 | 21.9557 | 21.9226 | 21.8888 | 21.8525 | 21.839 | 21.0962 | 19.1805 | 18.1595 | 17.4092 | 15.1227 | 15.0591 | 14.5857 | 14.4676 | 14.3398 | 14.198 | 14.0093 | 13.7722 | 13.5874 | 13.0455 | 11.7047 | 11.0154 | 10.5173 | 21.1463 | 21.14 | 20.7531 | 20.7208 | 20.6882 | 20.655 | 20.6213 | 20.5515 | 20.1934 | 19.1378 | 16.9308 | 15.7418 | 14.8638
|  | GROVE | LW |  |  | 22.3589 | 22.3483 | 21.7035 | 21.649 | 21.5926 | 21.5343 | 21.474 | 21.4059 | 21.3822 | 20.5964 | 19.0413 | 18.097 | 17.3543 | 15.073 | 15.0082 | 14.283 | 14.1485 | 14.0031 | 13.8047 | 13.5893 | 13.3204 | 13.1254 | 12.5491 | 11.5689 | 10.9563 | 10.466 | 21.0913 | 21.0808 | 20.4359 | 20.3814 | 20.3251 | 20.2668 | 20.2064 | 20.0953 | 19.7262 | 18.6362 | 16.7898 | 15.6775 | 14.807
|  | GROVE | ST |  |  | 22.4414 | 22.4371 | 22.1792 | 22.1386 | 22.0973 | 22.0553 | 22.0121 | 21.9558 | 21.9349 | 21.8661 | 20.9503 | 20.2547 | 19.7594 | 15.1771 | 15.1379 | 14.8352 | 14.7461 | 14.6462 | 14.5159 | 14.3744 | 14.1831 | 14.0448 | 13.626 | 12.9531 | 12.4744 | 12.1434 | 21.1738 | 21.1696 | 20.9116 | 20.871 | 20.8298 | 20.7878 | 20.7446 | 20.6882 | 20.6673 | 20.2438 | 18.9648 | 18.1593 | 17.5807
|  | GROVE | FS |  |  | 22.4688 | 22.4667 | 22.3378 | 22.3272 | 22.3166 | 22.306 | 22.2953 | 22.2846 | 22.2798 | 22.2638 | 22.2401 | 22.2149 | 22.1794 | 15.2254 | 15.2047 | 15.0565 | 15.024 | 14.989 | 14.943 | 14.8941 | 14.8298 | 14.7787 | 14.6247 | 14.3584 | 14.2081 | 14.0897 | 21.2013 | 21.1992 | 21.0702 | 21.0596 | 21.049 | 21.0384 | 21.0278 | 21.017 | 21.0122 | 20.9963 | 20.9725 | 20.9473 | 20.861
MANNINGTON GSP | SHAFTESBURY BSP | GUSSAGE ST MICHAEL | MINIMUM HEADROOM | ST 98638 11417 | YES | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.1905 | 3.1895 | 3.1871 | 3.1849 | 3.1826 | 3.1765 | 3.1704 | 3.1644 | 3.1579 | 3.1386 | 3.1064 | 3.0728 | 3.0396 | 3.2156 | 3.215 | 3.2139 | 3.2127 | 3.2116 | 3.2085 | 3.2054 | 3.2024 | 3.1991 | 3.1893 | 3.173 | 3.156 | 3.1393
|  | GUSSAGE ST MICHAEL | CT |  |  | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.1905 | 3.1895 | 3.1871 | 3.1849 | 3.1826 | 3.1804 | 3.1743 | 3.1683 | 3.1618 | 3.1425 | 3.1103 | 3.0767 | 3.0435 | 3.2156 | 3.215 | 3.2139 | 3.2127 | 3.2116 | 3.2105 | 3.2074 | 3.2043 | 3.201 | 3.1913 | 3.175 | 3.158 | 3.1412
|  | GUSSAGE ST MICHAEL | LW |  |  | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.1905 | 3.1895 | 3.1871 | 3.1849 | 3.1826 | 3.1765 | 3.1704 | 3.1644 | 3.1579 | 3.1386 | 3.1064 | 3.0728 | 3.0396 | 3.2156 | 3.215 | 3.2139 | 3.2127 | 3.2116 | 3.2085 | 3.2054 | 3.2024 | 3.1991 | 3.1893 | 3.173 | 3.156 | 3.1393
|  | GUSSAGE ST MICHAEL | ST |  |  | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.1913 | 3.1907 | 3.1896 | 3.1883 | 3.1868 | 3.1846 | 3.1824 | 3.1783 | 3.1739 | 3.1609 | 3.1394 | 3.1178 | 3.0964 | 3.216 | 3.2156 | 3.2151 | 3.2145 | 3.2137 | 3.2126 | 3.2115 | 3.2094 | 3.2071 | 3.2006 | 3.1897 | 3.1788 | 3.168
|  | GUSSAGE ST MICHAEL | FS |  |  | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.1923 | 3.1922 | 3.1921 | 3.1917 | 3.1913 | 3.1906 | 3.1899 | 3.189 | 3.1873 | 3.1823 | 3.1741 | 3.1662 | 3.1586 | 3.2165 | 3.2164 | 3.2164 | 3.2162 | 3.216 | 3.2156 | 3.2153 | 3.2148 | 3.2139 | 3.2114 | 3.2073 | 3.2033 | 3.1994
BOTLEY WOOD GSP | NETLEY COMMON BSP | HAMBLE | MINIMUM HEADROOM | SU 47370 08794 | YES | 45.7835 | 45.7835 | 45.7835 | 45.7835 | 45.7835 | 45.7835 | 45.7835 | 45.7835 | 45.7835 | 45.7835 | 45.7835 | 45.3379 | 44.6502 | 43.5317 | 43.5294 | 43.5246 | 43.5199 | 43.5152 | 43.5104 | 43.5049 | 43.4994 | 43.396 | 43.0079 | 42.2855 | 41.4876 | 40.6954 | 45.242 | 45.242 | 45.242 | 45.242 | 45.242 | 45.242 | 45.242 | 45.242 | 45.242 | 45.242 | 45.242 | 44.556 | 43.7388
|  | HAMBLE | CT |  |  | 45.7835 | 45.7835 | 45.7835 | 45.7835 | 45.7835 | 45.7835 | 45.7835 | 45.7835 | 45.7835 | 45.7835 | 45.7835 | 45.3408 | 44.6534 | 43.5317 | 43.5294 | 43.5246 | 43.5199 | 43.5152 | 43.5106 | 43.5051 | 43.4996 | 43.3996 | 43.0116 | 42.2889 | 41.4912 | 40.6991 | 45.242 | 45.242 | 45.242 | 45.242 | 45.242 | 45.242 | 45.242 | 45.242 | 45.242 | 45.242 | 45.242 | 44.5597 | 43.7426
|  | HAMBLE | LW |  |  | 45.7835 | 45.7835 | 45.7835 | 45.7835 | 45.7835 | 45.7835 | 45.7835 | 45.7835 | 45.7835 | 45.7835 | 45.7835 | 45.3379 | 44.6502 | 43.5318 | 43.5296 | 43.525 | 43.5204 | 43.5159 | 43.5104 | 43.5049 | 43.4994 | 43.396 | 43.0079 | 42.2855 | 41.4876 | 40.6954 | 45.242 | 45.242 | 45.242 | 45.242 | 45.242 | 45.242 | 45.242 | 45.242 | 45.242 | 45.242 | 45.242 | 44.556 | 43.7388
|  | HAMBLE | ST |  |  | 45.7835 | 45.7835 | 45.7835 | 45.7835 | 45.7835 | 45.7835 | 45.7835 | 45.7835 | 45.7835 | 45.7835 | 45.7835 | 45.7835 | 45.647 | 43.5431 | 43.5308 | 43.528 | 43.5246 | 43.5205 | 43.5166 | 43.5127 | 43.509 | 43.505 | 43.3828 | 42.8952 | 42.3766 | 41.8658 | 45.242 | 45.242 | 45.242 | 45.242 | 45.242 | 45.242 | 45.242 | 45.242 | 45.242 | 45.242 | 45.242 | 45.242 | 44.9462
|  | HAMBLE | FS |  |  | 45.7835 | 45.7835 | 45.7835 | 45.7835 | 45.7835 | 45.7835 | 45.7835 | 45.7835 | 45.7835 | 45.7835 | 45.7835 | 45.7835 | 45.7835 | 43.5459 | 43.535 | 43.5348 | 43.5341 | 43.5331 | 43.5319 | 43.5306 | 43.529 | 43.5274 | 43.5228 | 43.5141 | 43.5046 | 43.4314 | 45.242 | 45.242 | 45.242 | 45.242 | 45.242 | 45.242 | 45.242 | 45.242 | 45.242 | 45.242 | 45.242 | 45.242 | 45.242
MANNINGTON GSP | POOLE PS (HAMWORTHY) | HAMWORTHY | MINIMUM HEADROOM | SZ 00104 90800 | YES | 20.0494 | 20.0383 | 19.3608 | 19.3033 | 19.2435 | 19.1814 | 19.1167 | 19.0427 | 19.0173 | 18.9344 | 18.6272 | 17.2393 | 15.9104 | 18.5804 | 18.5692 | 17.8918 | 17.8342 | 17.7744 | 17.6921 | 17.595 | 17.486 | 17.0484 | 15.7987 | 14.1538 | 12.5423 | 10.9974 | 18.8843 | 18.865 | 18.1807 | 18.1105 | 18.0359 | 17.9515 | 17.8637 | 17.408 | 16.9322 | 15.7248 | 14.1339 | 12.5449 | 11.0189
|  | HAMWORTHY | CT |  |  | 28.5282 | 28.5216 | 28.1151 | 28.0811 | 28.0467 | 28.0116 | 27.9758 | 27.9369 | 27.9226 | 27.8773 | 27.2961 | 25.8315 | 24.4926 | 27.0592 | 27.0525 | 26.646 | 26.6121 | 26.5776 | 26.5322 | 26.464 | 26.3901 | 26.0781 | 24.8661 | 22.8416 | 21.1534 | 19.5986 | 27.3631 | 27.3482 | 26.9349 | 26.8884 | 26.839 | 26.7887 | 26.7299 | 26.4222 | 25.9573 | 24.7876 | 22.8173 | 21.1544 | 19.6185
|  | HAMWORTHY | LW |  |  | 20.0494 | 20.0383 | 19.3608 | 19.3033 | 19.2435 | 19.1814 | 19.1167 | 19.0427 | 19.0173 | 18.9344 | 18.6272 | 17.2393 | 15.9104 | 18.5804 | 18.5692 | 17.8918 | 17.8342 | 17.7744 | 17.6921 | 17.595 | 17.486 | 17.0484 | 15.7987 | 14.1538 | 12.5423 | 10.9974 | 18.8843 | 18.865 | 18.1807 | 18.1105 | 18.0359 | 17.9515 | 17.8637 | 17.408 | 16.9322 | 15.7248 | 14.1339 | 12.5449 | 11.0189
|  | HAMWORTHY | ST |  |  | 28.5571 | 28.5527 | 28.2817 | 28.259 | 28.236 | 28.2125 | 28.1883 | 28.1618 | 28.1509 | 28.1131 | 28.0542 | 27.9766 | 27.5415 | 27.088 | 27.0836 | 26.8126 | 26.79 | 26.7669 | 26.7434 | 26.7071 | 26.657 | 26.6206 | 26.1325 | 25.0447 | 24.0075 | 23.0301 | 27.394 | 27.3836 | 27.108 | 27.0763 | 27.0422 | 27.0037 | 26.9641 | 26.9209 | 26.8364 | 26.0167 | 24.9662 | 23.9637 | 23.0164
|  | HAMWORTHY | FS |  |  | 28.586 | 28.5838 | 28.4483 | 28.4371 | 28.426 | 28.4148 | 28.4037 | 28.3924 | 28.3872 | 28.3699 | 28.3445 | 28.316 | 28.2767 | 27.1169 | 27.1147 | 26.9792 | 26.9681 | 26.9569 | 26.9458 | 26.9346 | 26.9233 | 26.9182 | 26.9008 | 26.843 | 26.7824 | 26.6728 | 27.4264 | 27.421 | 27.2839 | 27.2687 | 27.253 | 27.2364 | 27.2198 | 27.2022 | 27.1899 | 27.1546 | 27.1059 | 26.9615 | 26.5434
IVER 132KV | DENHAM | HAREFIELD | MINIMUM HEADROOM | TQ 04001 91227 | YES | 16.013 | 16.013 | 16.013 | 16.0124 | 16.0112 | 16.0093 | 16.0067 | 16.0014 | 16.0005 | 15.9959 | 15.9846 | 15.9443 | 15.9187 | 15.6296 | 15.6296 | 15.6296 | 15.629 | 15.6278 | 15.6259 | 15.6233 | 15.618 | 15.6171 | 15.6125 | 15.6012 | 15.506 | 15.1645 | 15.7794 | 15.7794 | 15.7794 | 15.7788 | 15.7776 | 15.7757 | 15.7731 | 15.7679 | 15.7669 | 15.7623 | 15.751 | 15.6561 | 15.3094
|  | HAREFIELD | CT |  |  | 16.013 | 16.013 | 16.013 | 16.0128 | 16.0125 | 16.012 | 16.0112 | 16.0097 | 16.0094 | 16.0078 | 15.9953 | 15.9657 | 15.9373 | 15.6296 | 15.6296 | 15.6296 | 15.6294 | 15.6291 | 15.6286 | 15.6279 | 15.6263 | 15.626 | 15.6245 | 15.6119 | 15.5615 | 15.2184 | 15.7794 | 15.7794 | 15.7794 | 15.7792 | 15.7789 | 15.7784 | 15.7777 | 15.7761 | 15.7758 | 15.7743 | 15.7618 | 15.7127 | 15.3633
|  | HAREFIELD | LW |  |  | 16.013 | 16.013 | 16.013 | 16.0124 | 16.0112 | 16.0093 | 16.0067 | 16.0014 | 16.0005 | 15.9959 | 15.9846 | 15.9443 | 15.9187 | 15.6296 | 15.6296 | 15.6296 | 15.629 | 15.6278 | 15.6259 | 15.6233 | 15.618 | 15.6171 | 15.6125 | 15.6012 | 15.506 | 15.1645 | 15.7794 | 15.7794 | 15.7794 | 15.7788 | 15.7776 | 15.7757 | 15.7731 | 15.7679 | 15.7669 | 15.7623 | 15.751 | 15.6561 | 15.3094
|  | HAREFIELD | ST |  |  | 16.013 | 16.013 | 16.013 | 16.0128 | 16.0126 | 16.0122 | 16.0117 | 16.0104 | 16.0099 | 16.0067 | 16.0026 | 15.988 | 15.9772 | 15.6296 | 15.6296 | 15.6296 | 15.6295 | 15.6292 | 15.6289 | 15.6283 | 15.6271 | 15.6265 | 15.6233 | 15.6192 | 15.6046 | 15.5993 | 15.7794 | 15.7794 | 15.7794 | 15.7793 | 15.779 | 15.7787 | 15.7781 | 15.7769 | 15.7763 | 15.7731 | 15.769 | 15.7544 | 15.7492
|  | HAREFIELD | FS |  |  | 16.013 | 16.013 | 16.013 | 16.013 | 16.013 | 16.0129 | 16.0129 | 16.0129 | 16.0127 | 16.0115 | 16.0106 | 16.0063 | 16.002 | 15.6296 | 15.6296 | 15.6296 | 15.6296 | 15.6296 | 15.6296 | 15.6295 | 15.6295 | 15.6293 | 15.6281 | 15.6272 | 15.6229 | 15.6187 | 15.7794 | 15.7794 | 15.7794 | 15.7794 | 15.7794 | 15.7794 | 15.7794 | 15.7793 | 15.7791 | 15.778 | 15.7771 | 15.7727 | 15.7685
NURSLING GSP | WINCHESTER | HARESTOCK | MINIMUM HEADROOM | SU 45908 31300 | YES | 30.6946 | 25.4315 | 25.4315 | 25.4303 | 25.4279 | 25.4232 | 25.416 | 25.4005 | 25.3978 | 24.8578 | 23.4861 | 22.5163 | 21.6292 | 28.9458 | 23.4188 | 22.8898 | 22.3571 | 21.8112 | 21.2598 | 20.9453 | 20.6004 | 20.2284 | 19.0085 | 17.4074 | 16.2805 | 15.2428 | 29.6009 | 24.3377 | 24.3377 | 24.0584 | 23.5365 | 23.0093 | 22.7085 | 22.3829 | 22.0379 | 20.9065 | 19.4182 | 18.3585 | 17.3471
|  | HARESTOCK | CT |  |  | 30.6946 | 25.4315 | 25.4315 | 25.4311 | 25.4305 | 25.4295 | 25.4266 | 25.4194 | 25.4181 | 24.8578 | 23.4861 | 22.5163 | 21.6292 | 28.9458 | 23.4188 | 22.8898 | 22.3571 | 21.8112 | 21.2598 | 20.9453 | 20.6004 | 20.2284 | 19.0085 | 17.4074 | 16.2805 | 15.2428 | 29.6009 | 24.3377 | 24.3377 | 24.0584 | 23.5365 | 23.0093 | 22.7085 | 22.3829 | 22.0379 | 20.9065 | 19.4182 | 18.3585 | 17.3471
|  | HARESTOCK | LW |  |  | 30.6946 | 25.4315 | 25.4315 | 25.4303 | 25.4279 | 25.4232 | 25.416 | 25.4005 | 25.3978 | 25.0978 | 23.744 | 22.7685 | 21.897 | 28.9546 | 23.4328 | 22.9151 | 22.3921 | 21.8551 | 21.5597 | 21.2408 | 20.8922 | 20.5237 | 19.2953 | 17.7121 | 16.5795 | 15.5572 | 29.6009 | 24.3377 | 24.3377 | 24.0919 | 23.5783 | 23.2958 | 22.9906 | 22.6566 | 22.3102 | 21.1703 | 19.6999 | 18.6445 | 17.6534
|  | HARESTOCK | ST |  |  | 30.6946 | 30.6946 | 30.6946 | 25.4312 | 25.4307 | 25.4297 | 25.4281 | 25.4242 | 25.4224 | 25.4134 | 25.4017 | 24.9078 | 24.3295 | 29.0105 | 28.9019 | 28.6324 | 23.0279 | 22.6119 | 22.4055 | 22.1852 | 21.9559 | 21.708 | 20.877 | 19.801 | 19.0762 | 18.3999 | 29.6009 | 29.6009 | 29.6009 | 24.3375 | 24.3021 | 24.1047 | 23.894 | 23.6746 | 23.4375 | 22.6426 | 21.6405 | 20.9655 | 20.3374
|  | HARESTOCK | FS |  |  | 30.6946 | 30.6946 | 30.6946 | 30.6946 | 30.6946 | 30.6946 | 25.4313 | 25.4312 | 25.4306 | 25.4271 | 25.4245 | 25.4129 | 25.4018 | 29.0105 | 29.0105 | 29.0105 | 29.0104 | 29.0104 | 28.941 | 23.5974 | 23.4992 | 23.4055 | 23.0826 | 22.6715 | 22.4169 | 22.1847 | 29.6009 | 29.6009 | 29.6009 | 29.6009 | 29.6008 | 29.6008 | 24.3376 | 24.3374 | 24.3368 | 24.3333 | 24.3307 | 24.1149 | 23.8923
EALING GSP | EALING 22kV | HARVARD LANE | MINIMUM HEADROOM | TQ 20021 78030 | YES | 35.1736 | 35.1736 | 35.1736 | 34.982 | 34.7842 | 85.5827 | 85.3686 | 85.0435 | 84.9984 | 84.8441 | 84.6132 | 83.8724 | 81.9921 | 32.1763 | 32.1763 | 32.1763 | 31.718 | 30.6825 | 80.897 | 80.6521 | 80.2383 | 79.9685 | 79.1046 | 77.1649 | 74.4876 | 72.3516 | 30.6577 | 30.6304 | 30.5748 | 30.2599 | 29.1793 | 79.3731 | 79.1239 | 78.7228 | 78.4491 | 77.5728 | 75.6032 | 72.8893 | 70.7166
|  | HARVARD LANE | CT |  |  | 35.1736 | 35.1736 | 35.1736 | 35.1736 | 35.1736 | 86.1786 | 86.1786 | 86.1786 | 86.1786 | 86.1786 | 86.1786 | 85.1877 | 83.3413 | 32.1763 | 32.1763 | 32.1763 | 31.7425 | 30.82 | 80.897 | 80.6521 | 80.4262 | 80.2014 | 79.4919 | 77.783 | 75.6878 | 73.5857 | 30.6577 | 30.6304 | 30.5748 | 30.2599 | 29.3124 | 79.3731 | 79.1239 | 78.8942 | 78.6654 | 77.9435 | 76.2048 | 74.0729 | 71.9342
|  | HARVARD LANE | LW |  |  | 35.1736 | 35.1736 | 35.1736 | 34.982 | 34.7842 | 85.5827 | 85.3686 | 85.0435 | 84.9984 | 84.8441 | 84.6132 | 83.8724 | 81.9921 | 32.1763 | 32.1763 | 32.1763 | 31.718 | 30.6825 | 81.2482 | 80.7893 | 80.2383 | 79.9685 | 79.1046 | 77.1649 | 74.4876 | 72.3516 | 30.6607 | 30.635 | 30.5829 | 30.2669 | 29.1793 | 79.7409 | 79.2777 | 78.7228 | 78.4491 | 77.5728 | 75.6032 | 72.8893 | 70.7166
|  | HARVARD LANE | ST |  |  | 35.1736 | 35.1736 | 35.1736 | 35.1579 | 35.1419 | 86.1306 | 86.1138 | 86.0877 | 86.0789 | 86.0507 | 86.0272 | 85.9459 | 85.9224 | 32.1763 | 32.1763 | 32.1763 | 32.1606 | 32.1447 | 83.1334 | 83.1165 | 83.0905 | 83.0817 | 82.8547 | 81.6956 | 80.2328 | 78.873 | 30.7126 | 30.6757 | 30.6593 | 30.6237 | 30.5836 | 81.5563 | 81.523 | 81.4881 | 81.4703 | 81.4138 | 80.1883 | 78.7014 | 77.3182
|  | HARVARD LANE | FS |  |  | 35.1736 | 35.1736 | 35.1736 | 35.1736 | 35.1736 | 86.1786 | 86.1786 | 86.1786 | 86.1786 | 86.1786 | 86.1786 | 86.1786 | 86.1786 | 32.1763 | 32.1763 | 32.1763 | 32.1763 | 32.1763 | 83.1813 | 83.1813 | 83.1813 | 83.1813 | 83.1813 | 83.1813 | 83.1813 | 82.9998 | 30.7164 | 30.696 | 30.6934 | 30.6851 | 30.6753 | 81.6742 | 81.668 | 81.6607 | 81.6572 | 81.6462 | 81.6181 | 81.5814 | 81.5429
BRAMLEY (FLEE) | FERNHURST | HASLEMERE | MINIMUM HEADROOM | SU 89300 31710 | YES | 40.0526 | 40.0526 | 40.0526 | 39.9783 | 39.9027 | 39.8254 | 39.7453 | 39.6208 | 39.5785 | 39.4427 | 39.3325 | 39.0059 | 38.9076 | 32.2264 | 32.0734 | 31.7547 | 31.4607 | 31.1681 | 30.8778 | 30.6911 | 30.5033 | 30.3054 | 29.7186 | 28.699 | 27.6249 | 26.5897 | 33.5273 | 33.3747 | 33.057 | 32.7639 | 32.4722 | 32.1827 | 31.9966 | 31.8093 | 31.6121 | 31.027 | 30.0104 | 28.9395 | 27.9075
|  | HASLEMERE | CT |  |  | 40.0526 | 40.0526 | 40.0526 | 40.0526 | 40.0526 | 40.0526 | 40.0513 | 40.0478 | 40.0472 | 40.0442 | 40.0194 | 39.9853 | 39.3581 | 32.2264 | 32.0734 | 31.7547 | 31.4607 | 31.1681 | 30.8778 | 30.6911 | 30.5033 | 30.3054 | 29.7186 | 28.699 | 27.6249 | 26.5897 | 33.5273 | 33.3747 | 33.057 | 32.7639 | 32.4722 | 32.1827 | 31.9966 | 31.8093 | 31.6121 | 31.027 | 30.0104 | 28.9395 | 27.9075
|  | HASLEMERE | LW |  |  | 40.0526 | 40.0526 | 40.0526 | 40.0526 | 40.0526 | 40.0518 | 40.05 | 40.0457 | 40.0449 | 40.04 | 40.0282 | 40.0031 | 39.5157 | 32.2367 | 32.0894 | 31.7825 | 31.5001 | 31.219 | 31.0323 | 30.8451 | 30.6564 | 30.4585 | 29.8695 | 28.8634 | 27.7978 | 26.7713 | 33.5375 | 33.3906 | 33.0847 | 32.8032 | 32.5229 | 32.3367 | 32.1501 | 31.962 | 31.7647 | 31.1775 | 30.1744 | 29.112 | 28.0886
|  | HASLEMERE | ST |  |  | 40.0526 | 40.0526 | 40.0526 | 39.9783 | 39.9027 | 39.8254 | 39.7453 | 39.6208 | 39.5785 | 39.4427 | 39.3325 | 39.0059 | 38.9076 | 32.3813 | 32.3221 | 32.2216 | 32.037 | 31.8278 | 31.5979 | 31.3661 | 31.1157 | 30.939 | 30.409 | 29.634 | 28.6357 | 27.8729 | 33.6817 | 33.6227 | 33.5225 | 33.3382 | 33.1294 | 32.8999 | 32.6686 | 32.4186 | 32.2423 | 31.7135 | 30.9405 | 29.9443 | 29.1835
|  | HASLEMERE | FS |  |  | 40.0526 | 40.0526 | 40.0526 | 40.0494 | 40.0462 | 40.043 | 40.0398 | 40.0347 | 40.0206 | 39.9752 | 39.9533 | 39.8843 | 39.8264 | 32.459 | 32.4443 | 32.428 | 32.3806 | 32.3248 | 32.269 | 32.2135 | 32.1416 | 32.0753 | 31.8778 | 31.6023 | 31.2821 | 30.9835 | 33.7591 | 33.7445 | 33.7283 | 33.6809 | 33.6253 | 33.5697 | 33.5143 | 33.4426 | 33.3765 | 33.1794 | 32.9047 | 32.5853 | 32.2874
BRAMLEY (FLEE) | FERNHURST | HASLINGBOURNE | MINIMUM HEADROOM | SU 98188 20276 | YES | 19.3713 | 19.3713 | 33.6713 | 33.5903 | 33.5066 | 33.4193 | 33.3287 | 33.1912 | 33.1721 | 33.1068 | 33.0092 | 32.4714 | 32.098 | 17.0463 | 17.0407 | 30.7788 | 30.6862 | 30.5911 | 30.4666 | 30.3392 | 30.1652 | 30.1068 | 29.9254 | 29.6374 | 29.195 | 28.9878 | 17.6977 | 17.6846 | 31.9567 | 31.8485 | 31.7378 | 31.5632 | 31.3862 | 31.1629 | 31.0514 | 30.7133 | 30.1682 | 29.4611 | 28.9934
|  | HASLINGBOURNE | CT |  |  | 19.3713 | 19.3713 | 33.6713 | 33.6713 | 33.6713 | 33.6713 | 33.6713 | 33.6713 | 33.6713 | 33.6713 | 33.6713 | 33.4277 | 33.0689 | 17.0463 | 17.0407 | 30.7788 | 30.7673 | 30.7558 | 30.7444 | 30.7076 | 30.6711 | 30.6317 | 30.5156 | 30.3253 | 30.1291 | 29.9364 | 17.6977 | 17.6846 | 31.9567 | 31.9295 | 31.9025 | 31.8757 | 31.7893 | 31.7035 | 31.611 | 31.3381 | 30.8908 | 30.43 | 29.977
|  | HASLINGBOURNE | LW |  |  | 19.3713 | 19.3713 | 33.6713 | 33.5903 | 33.5066 | 33.4193 | 33.3287 | 33.1912 | 33.1721 | 33.1068 | 33.0092 | 32.4714 | 32.098 | 17.0463 | 17.0407 | 30.7788 | 30.6862 | 30.5911 | 30.4666 | 30.3392 | 30.1652 | 30.1068 | 29.9254 | 29.6374 | 29.195 | 28.9878 | 17.6977 | 17.6846 | 31.9567 | 31.8485 | 31.7378 | 31.5632 | 31.3862 | 31.1629 | 31.0514 | 30.7133 | 30.1682 | 29.4611 | 28.9934
|  | HASLINGBOURNE | ST |  |  | 19.3713 | 19.3713 | 33.6713 | 33.6713 | 33.6713 | 33.6713 | 33.6713 | 33.6713 | 33.6713 | 33.6713 | 33.6713 | 33.6713 | 33.6211 | 17.05 | 17.0469 | 30.7916 | 30.785 | 30.7771 | 30.759 | 30.7411 | 30.7163 | 30.6894 | 30.6112 | 30.4848 | 30.3586 | 30.233 | 17.7065 | 17.6992 | 31.9866 | 31.9712 | 31.9526 | 31.9101 | 31.8681 | 31.8096 | 31.7466 | 31.5628 | 31.2657 | 30.9692 | 30.674
|  | HASLINGBOURNE | FS |  |  | 19.3713 | 19.3713 | 33.6713 | 33.6688 | 33.6663 | 33.6638 | 33.6612 | 33.6572 | 33.6462 | 33.611 | 33.5943 | 33.5416 | 33.4976 | 17.0551 | 17.0547 | 30.8043 | 30.7999 | 30.7953 | 30.7864 | 30.7775 | 30.7652 | 30.7438 | 30.6785 | 30.6141 | 30.516 | 30.429 | 17.7184 | 17.7174 | 32.0165 | 32.0097 | 32.0022 | 31.9847 | 31.9671 | 31.9437 | 31.9083 | 31.8023 | 31.6735 | 31.5141 | 31.3692
MELKSHAM GSP | FROME BSP | HAWKERIDGE | MINIMUM HEADROOM | ST 86422 53026 | YES | 22.2295 | 22.2178 | 21.4995 | 21.3175 | 21.1315 | 20.9399 | 20.7435 | 20.4757 | 20.4232 | 20.2534 | 19.9873 | 19.6673 | 19.5233 | 20.8074 | 20.7956 | 20.0773 | 19.8953 | 19.7094 | 19.5178 | 19.3213 | 19.0536 | 19.0011 | 18.8312 | 18.5651 | 18.2452 | 18.1012 | 22.4258 | 22.4067 | 21.6696 | 21.4693 | 21.2653 | 21.0643 | 20.8587 | 20.5817 | 20.5192 | 20.2959 | 19.8921 | 19.4275 | 19.1407
|  | HAWKERIDGE | CT |  |  | 22.2908 | 22.2837 | 21.8527 | 21.8174 | 21.7821 | 21.7468 | 21.7114 | 21.6761 | 21.662 | 21.6196 | 21.1043 | 20.9225 | 20.793 | 20.8686 | 20.8616 | 20.4306 | 20.3953 | 20.3599 | 20.3246 | 20.2893 | 20.254 | 20.2398 | 20.1974 | 19.6822 | 19.5003 | 19.3708 | 22.4889 | 22.4772 | 22.031 | 21.9808 | 21.9307 | 21.8808 | 21.8362 | 21.7917 | 21.7676 | 21.6886 | 21.0356 | 20.7091 | 20.4368
|  | HAWKERIDGE | LW |  |  | 22.2295 | 22.2178 | 21.4995 | 21.3175 | 21.1315 | 20.9399 | 20.7435 | 20.4757 | 20.4232 | 20.2534 | 19.9873 | 19.6673 | 19.5233 | 20.8074 | 20.7956 | 20.0773 | 19.8953 | 19.7094 | 19.5178 | 19.3213 | 19.0536 | 19.0011 | 18.8312 | 18.5651 | 18.2452 | 18.1012 | 22.4258 | 22.4067 | 21.6696 | 21.4693 | 21.2653 | 21.0643 | 20.8587 | 20.5817 | 20.5192 | 20.2959 | 19.8921 | 19.4275 | 19.1407
|  | HAWKERIDGE | ST |  |  | 22.3214 | 22.3167 | 22.0294 | 22.0058 | 21.9823 | 21.9587 | 21.9352 | 21.9116 | 21.9022 | 21.8739 | 21.8268 | 21.7986 | 21.7468 | 20.8992 | 20.8945 | 20.6072 | 20.5837 | 20.5601 | 20.5366 | 20.513 | 20.4895 | 20.48 | 20.4518 | 20.4047 | 20.3764 | 20.3246 | 22.5407 | 22.5099 | 22.2109 | 22.173 | 22.1323 | 22.1015 | 22.0708 | 22.041 | 22.0248 | 21.9768 | 21.8776 | 21.7561 | 21.6117
|  | HAWKERIDGE | FS |  |  | 22.352 | 22.3497 | 22.206 | 22.1942 | 22.1824 | 22.1707 | 22.1589 | 22.1471 | 22.1424 | 22.1283 | 22.1047 | 22.0906 | 22.0647 | 20.9299 | 20.9275 | 20.7838 | 20.7721 | 20.7603 | 20.7485 | 20.7367 | 20.725 | 20.7203 | 20.7061 | 20.6826 | 20.6684 | 20.6425 | 22.5788 | 22.5543 | 22.4102 | 22.3965 | 22.3824 | 22.3692 | 22.3559 | 22.3423 | 22.3359 | 22.3142 | 22.2781 | 22.2515 | 22.2136
BRAMLEY (FLEE) | COXMOOR WOOD BSP | HAWLEY | MINIMUM HEADROOM | SU 85973 57691 | YES | 26.3 | 26.2981 | 26.2951 | 26.2921 | 26.2887 | 26.2808 | 26.2683 | 26.2558 | 26.2426 | 26.201 | 26.1104 | 25.77 | 24.5558 | 25.5946 | 25.5934 | 25.5914 | 25.5893 | 25.587 | 25.5816 | 25.573 | 25.5645 | 25.5555 | 25.5272 | 25.2958 | 23.8123 | 22.3266 | 25.6675 | 25.666 | 25.6636 | 25.6611 | 25.6584 | 25.6519 | 25.6419 | 25.6318 | 25.6211 | 25.5875 | 25.5143 | 24.3702 | 22.8936
|  | HAWLEY | CT |  |  | 26.3 | 26.2981 | 26.2951 | 26.2921 | 26.2887 | 26.2853 | 26.2729 | 26.2604 | 26.2472 | 26.2056 | 26.115 | 25.822 | 24.6082 | 25.5946 | 25.5934 | 25.5914 | 25.5893 | 25.587 | 25.5847 | 25.5762 | 25.5677 | 25.5586 | 25.5303 | 25.3595 | 23.876 | 22.3907 | 25.6675 | 25.666 | 25.6636 | 25.6611 | 25.6584 | 25.6556 | 25.6456 | 25.6355 | 25.6248 | 25.5912 | 25.518 | 24.4335 | 22.9573
|  | HAWLEY | LW |  |  | 26.3009 | 26.2995 | 26.2976 | 26.2956 | 26.2932 | 26.2808 | 26.2683 | 26.2558 | 26.2426 | 26.201 | 26.1104 | 25.77 | 24.5558 | 25.5953 | 25.5944 | 25.5931 | 25.5917 | 25.5901 | 25.5816 | 25.573 | 25.5645 | 25.5555 | 25.5272 | 25.2958 | 23.8123 | 22.3266 | 25.6682 | 25.6671 | 25.6656 | 25.6639 | 25.662 | 25.6519 | 25.6419 | 25.6318 | 25.6211 | 25.5875 | 25.5143 | 24.3702 | 22.8936
|  | HAWLEY | ST |  |  | 26.3002 | 26.2987 | 26.2965 | 26.2937 | 26.2904 | 26.285 | 26.2796 | 26.2711 | 26.262 | 26.2337 | 26.1715 | 26.1013 | 26.0328 | 25.5948 | 25.5938 | 25.5923 | 25.5904 | 25.5881 | 25.5844 | 25.5808 | 25.575 | 25.5688 | 25.5494 | 25.507 | 25.1702 | 24.2201 | 25.6677 | 25.6664 | 25.6647 | 25.6624 | 25.6597 | 25.6554 | 25.651 | 25.6441 | 25.6368 | 25.6139 | 25.5637 | 25.5069 | 24.7755
|  | HAWLEY | FS |  |  | 26.3026 | 26.3022 | 26.3019 | 26.3014 | 26.3008 | 26.2991 | 26.2974 | 26.2952 | 26.2917 | 26.2806 | 26.2556 | 26.225 | 26.1934 | 25.5964 | 25.5962 | 25.596 | 25.5956 | 25.5952 | 25.5941 | 25.5929 | 25.5914 | 25.589 | 25.5815 | 25.5644 | 25.5435 | 25.522 | 25.6696 | 25.6693 | 25.669 | 25.6686 | 25.6682 | 25.6668 | 25.6654 | 25.6636 | 25.6608 | 25.6518 | 25.6316 | 25.6069 | 25.5813
NORTH HYDE GSP |  | HAYES | MINIMUM HEADROOM | TQ 09519 79541 |  | 54.4927 | 54.4665 | 52.8667 | 52.7225 | 52.5693 | 52.3815 | 52.1943 | 52.0083 | 51.8977 | 51.5633 | 50.931 | 48.8273 | 46.5291 | 51.9693 | 51.9386 | 50.3329 | 50.1957 | 50.0578 | 49.9094 | 49.7611 | 49.6132 | 49.5429 | 49.2081 | 47.8013 | 45.4628 | 42.8273 | 51.9625 | 51.9309 | 50.3242 | 50.1859 | 50.0468 | 49.8951 | 49.7437 | 49.5926 | 49.5191 | 49.2976 | 48.0825 | 45.6408 | 43.0732
|  | HAYES | CT |  |  | 54.6291 | 54.6134 | 53.6535 | 53.5618 | 53.461 | 53.3607 | 53.226 | 53.0924 | 53.0028 | 52.7314 | 51.2433 | 49.0187 | 46.7211 | 52.1057 | 52.0854 | 51.1197 | 51.035 | 50.9495 | 50.8642 | 50.7684 | 50.673 | 50.6237 | 50.4116 | 48.1941 | 45.6808 | 43.0519 | 52.0989 | 52.0778 | 51.111 | 51.0252 | 50.9385 | 50.852 | 50.753 | 50.6544 | 50.6019 | 50.4433 | 48.5367 | 45.8574 | 43.2956
|  | HAYES | LW |  |  | 54.4927 | 54.4665 | 52.8667 | 52.7225 | 52.5693 | 52.3815 | 52.1943 | 52.0083 | 51.8977 | 51.5633 | 50.931 | 48.8273 | 46.5291 | 51.9693 | 51.9386 | 50.3329 | 50.1957 | 50.0578 | 49.9094 | 49.7611 | 49.6132 | 49.5429 | 49.2081 | 47.8013 | 45.4628 | 42.8273 | 51.9625 | 51.9309 | 50.3242 | 50.1859 | 50.0468 | 49.8951 | 49.7437 | 49.5926 | 49.5191 | 49.2976 | 48.0825 | 45.6408 | 43.0732
|  | HAYES | ST |  |  | 54.6973 | 54.6868 | 54.0469 | 53.9944 | 53.942 | 53.8757 | 53.8017 | 53.7118 | 53.6512 | 53.468 | 53.132 | 52.8279 | 51.7804 | 52.1842 | 52.1645 | 51.5217 | 51.4657 | 51.4086 | 51.3494 | 51.2904 | 51.2265 | 51.1934 | 51.0937 | 50.7507 | 49.8991 | 48.5868 | 52.1793 | 52.1579 | 51.5146 | 51.4579 | 51.4 | 51.3396 | 51.2793 | 51.2133 | 51.178 | 51.0715 | 50.8828 | 50.3087 | 48.7569
|  | HAYES | FS |  |  | 54.7655 | 54.7602 | 54.4403 | 54.414 | 54.3878 | 54.3616 | 54.3354 | 54.3091 | 54.2987 | 54.2361 | 54.0926 | 53.9627 | 53.8059 | 52.2563 | 52.2435 | 51.923 | 51.8955 | 51.8677 | 51.8395 | 51.8112 | 51.7827 | 51.7675 | 51.7218 | 51.6415 | 51.58 | 51.492 | 52.2522 | 52.238 | 51.9173 | 51.8896 | 51.8616 | 51.8329 | 51.8043 | 51.7754 | 51.7593 | 51.711 | 51.6256 | 51.5584 | 51.4648
COWLEY GSP | HEADINGTON BSP | HEADINGTON | MINIMUM HEADROOM | SP 54440 08085 | NO | 57.9683 | 57.9683 | 57.9683 | 57.9683 | 57.9683 | 57.9683 | 57.9683 | 57.9683 | 57.9683 | 57.9683 | 57.1951 | 55.9474 | 54.7319 | 54.585 | 54.5755 | 54.5539 | 54.5285 | 54.5024 | 54.4779 | 54.4597 | 54.4396 | 54.4174 | 54.1595 | 52.8254 | 51.405 | 50.0212 | 56.1072 | 56.1072 | 56.1072 | 56.1072 | 56.1072 | 56.1072 | 56.1072 | 56.1045 | 55.7694 | 54.9422 | 53.7161 | 52.3696 | 51.0579
|  | HEADINGTON | CT |  |  | 57.9683 | 57.9683 | 57.9683 | 57.9683 | 57.9683 | 57.9683 | 57.9683 | 57.9683 | 57.9683 | 57.9683 | 57.1951 | 55.9474 | 54.7319 | 54.585 | 54.5755 | 54.5539 | 54.5285 | 54.5024 | 54.4779 | 54.4597 | 54.4396 | 54.4174 | 54.1595 | 52.8254 | 51.405 | 50.0212 | 56.1072 | 56.1072 | 56.1072 | 56.1072 | 56.1072 | 56.1072 | 56.1072 | 56.1045 | 55.7694 | 54.9422 | 53.7161 | 52.3696 | 51.0579
|  | HEADINGTON | LW |  |  | 57.9683 | 57.9683 | 57.9683 | 57.9683 | 57.9683 | 57.9683 | 57.9683 | 57.9683 | 57.9683 | 57.9683 | 57.4264 | 56.1784 | 54.9629 | 54.5866 | 54.578 | 54.5583 | 54.5347 | 54.5104 | 54.4932 | 54.475 | 54.4549 | 54.4327 | 54.3778 | 53.0887 | 51.668 | 50.2841 | 56.1072 | 56.1072 | 56.1072 | 56.1072 | 56.1072 | 56.1072 | 56.1072 | 56.1072 | 56.0001 | 55.1727 | 53.9657 | 52.6189 | 51.3071
|  | HEADINGTON | ST |  |  | 57.9683 | 57.9683 | 57.9683 | 57.9683 | 57.9683 | 57.9683 | 57.9683 | 57.9683 | 57.9683 | 57.9683 | 57.9683 | 57.9683 | 57.6689 | 54.5961 | 54.5932 | 54.5869 | 54.5768 | 54.5654 | 54.5541 | 54.5421 | 54.5285 | 54.5133 | 54.4752 | 54.4219 | 54.2506 | 53.3648 | 56.1072 | 56.1072 | 56.1072 | 56.1072 | 56.1072 | 56.1072 | 56.1072 | 56.1072 | 56.1072 | 56.1072 | 55.8379 | 55.0223 | 54.2274
|  | HEADINGTON | FS |  |  | 57.9683 | 57.9683 | 57.9683 | 57.9683 | 57.9683 | 57.9683 | 57.9683 | 57.9683 | 57.9683 | 57.9683 | 57.9683 | 57.9683 | 57.9683 | 54.5991 | 54.5981 | 54.596 | 54.5908 | 54.5852 | 54.5806 | 54.5759 | 54.5702 | 54.5642 | 54.5492 | 54.5278 | 54.5046 | 54.4815 | 56.1072 | 56.1072 | 56.1072 | 56.1072 | 56.1072 | 56.1072 | 56.1072 | 56.1072 | 56.1072 | 56.1072 | 56.1072 | 56.1072 | 56.1072
NURSLING GSP | VELMORE BSP | HEDGE END | MINIMUM HEADROOM | SU 49035 15685 | YES | 14.2419 | 14.2419 | 14.2419 | 14.1074 | 13.9706 | 13.8316 | 13.6864 | 13.4625 | 13.4341 | 13.343 | 12.9223 | 12.3803 | 12.2557 | 16.2294 | 16.2121 | 16.1834 | 16.0267 | 15.828 | 15.3733 | 14.9893 | 14.589 | 14.4027 | 13.9102 | 12.8196 | 11.6133 | 10.8724 | 16.3776 | 16.3653 | 16.345 | 16.1947 | 15.7704 | 15.3174 | 14.9397 | 14.5441 | 14.3614 | 13.8596 | 12.7535 | 11.5319 | 10.7755
|  | HEDGE END | CT |  |  | 14.2419 | 14.2419 | 14.2419 | 14.1074 | 13.9706 | 13.8316 | 13.6864 | 13.4625 | 13.4341 | 13.343 | 12.9223 | 12.3803 | 12.2557 | 16.2315 | 16.2154 | 16.1892 | 16.0267 | 15.828 | 15.3733 | 14.9893 | 14.589 | 14.4027 | 13.9102 | 12.8196 | 11.6133 | 10.8724 | 16.3791 | 16.3676 | 16.349 | 16.1947 | 15.7704 | 15.3174 | 14.9397 | 14.5441 | 14.3614 | 13.8596 | 12.7535 | 11.5319 | 10.7755
|  | HEDGE END | LW |  |  | 14.2419 | 14.2419 | 14.2419 | 14.2419 | 14.2419 | 14.2419 | 14.2419 | 14.2419 | 14.2419 | 14.2419 | 14.2419 | 14.2419 | 14.2419 | 16.2294 | 16.2121 | 16.1834 | 16.1531 | 15.9801 | 15.7488 | 15.5099 | 15.3335 | 15.1755 | 14.7741 | 14.1043 | 13.4399 | 12.8236 | 16.3776 | 16.3653 | 16.345 | 16.2888 | 15.9191 | 15.6939 | 15.4613 | 15.2894 | 15.1334 | 14.7226 | 14.0375 | 13.3578 | 12.7248
|  | HEDGE END | ST |  |  | 14.2419 | 14.2419 | 14.2419 | 14.2419 | 14.2419 | 14.2419 | 14.2419 | 14.2419 | 14.2419 | 14.2419 | 14.2419 | 14.2419 | 14.2419 | 16.2348 | 16.223 | 16.2061 | 16.1856 | 16.1616 | 16.141 | 16.1032 | 16.0047 | 15.8964 | 15.6193 | 15.1593 | 14.725 | 14.3289 | 16.3815 | 16.373 | 16.3611 | 16.3465 | 16.3294 | 16.2256 | 16.0589 | 15.943 | 15.8376 | 15.5677 | 15.1168 | 14.6725 | 14.2673
|  | HEDGE END | FS |  |  | 14.2419 | 14.2419 | 14.2419 | 14.2398 | 14.2378 | 14.2357 | 14.2336 | 14.2303 | 14.2212 | 14.1923 | 14.1786 | 14.1352 | 14.099 | 16.2458 | 16.2412 | 16.2362 | 16.2268 | 16.2168 | 16.2091 | 16.2014 | 16.1935 | 16.1808 | 16.1428 | 16.1136 | 16.0551 | 15.9985 | 16.3893 | 16.386 | 16.3825 | 16.3752 | 16.3675 | 16.3614 | 16.3553 | 16.3488 | 16.3371 | 16.3018 | 16.277 | 16.2229 | 16.0849
BRAMLEY (FLEE) | READING BSP | HENLEY | MINIMUM HEADROOM | SU 76070 82422 | YES | 45.1728 | 45.1728 | 45.1728 | 45.1334 | 45.0927 | 45.0502 | 45.0062 | 44.9393 | 44.93 | 44.6915 | 43.7601 | 42.8601 | 42.0615 | 41.9686 | 41.9609 | 41.9438 | 41.8928 | 41.8339 | 41.7787 | 41.721 | 41.6392 | 41.6137 | 40.5109 | 39.4653 | 38.4973 | 37.5891 | 43.6206 | 43.6206 | 43.6206 | 43.5812 | 43.5405 | 43.498 | 43.454 | 43.3871 | 43.3778 | 43.0183 | 42.0133 | 41.0744 | 40.2126
|  | HENLEY | CT |  |  | 45.1728 | 45.1728 | 45.1728 | 45.1728 | 45.1728 | 45.1728 | 45.1728 | 45.1728 | 45.1728 | 44.6915 | 43.7601 | 42.9384 | 42.1468 | 41.9686 | 41.9609 | 41.9438 | 41.925 | 41.9046 | 41.8841 | 41.8704 | 41.8555 | 41.7343 | 40.5109 | 39.4653 | 38.5298 | 37.6257 | 43.6206 | 43.6206 | 43.6206 | 43.6206 | 43.6206 | 43.6206 | 43.6206 | 43.6206 | 43.6206 | 43.0183 | 42.0133 | 41.1265 | 40.2503
|  | HENLEY | LW |  |  | 45.1728 | 45.1728 | 45.1728 | 45.1334 | 45.0927 | 45.0502 | 45.0062 | 44.9393 | 44.93 | 44.7483 | 43.7698 | 42.8601 | 42.0615 | 41.9705 | 41.9638 | 41.9489 | 41.8928 | 41.8339 | 41.7787 | 41.721 | 41.6392 | 41.6137 | 40.6068 | 39.5186 | 38.4973 | 37.5891 | 43.6206 | 43.6206 | 43.6206 | 43.5812 | 43.5405 | 43.498 | 43.454 | 43.3871 | 43.3778 | 43.1014 | 42.0492 | 41.0744 | 40.2126
|  | HENLEY | ST |  |  | 45.1728 | 45.1728 | 45.1728 | 45.1728 | 45.1728 | 45.1728 | 45.1728 | 45.1728 | 45.1728 | 45.1728 | 45.1728 | 45.1728 | 44.7161 | 41.9828 | 41.9745 | 41.9694 | 41.9619 | 41.9521 | 41.9424 | 41.932 | 41.922 | 41.9108 | 41.8708 | 41.707 | 41.1133 | 40.5384 | 43.6206 | 43.6206 | 43.6206 | 43.6206 | 43.6206 | 43.6206 | 43.6206 | 43.6206 | 43.6206 | 43.6206 | 43.6206 | 43.5863 | 43.0449
|  | HENLEY | FS |  |  | 45.1728 | 45.1728 | 45.1728 | 45.1728 | 45.1728 | 45.1728 | 45.1728 | 45.1728 | 45.1728 | 45.1728 | 45.1728 | 45.1728 | 45.1728 | 41.9868 | 41.9807 | 41.9799 | 41.9769 | 41.9731 | 41.9693 | 41.9654 | 41.9606 | 41.9562 | 41.9404 | 41.9277 | 41.9174 | 41.9079 | 43.6206 | 43.6206 | 43.6206 | 43.6206 | 43.6206 | 43.6206 | 43.6206 | 43.6206 | 43.6206 | 43.6206 | 43.6206 | 43.6206 | 43.6206
AXMINSTER | YEOVIL BSP | HENSTRIDGE | MINIMUM HEADROOM | ST 72676 19263 | YES | 31.3131 | 31.2823 | 31.2488 | 31.1542 | 31.0527 | 30.9469 | 30.771 | 30.5577 | 30.4198 | 30.0699 | 29.444 | 28.7807 | 28.3107 | 30.1046 | 30.0609 | 30.0134 | 29.9029 | 29.7832 | 29.6577 | 29.4565 | 29.2194 | 29.0562 | 28.6459 | 27.9394 | 27.1981 | 26.6531 | 31.0967 | 31.0539 | 31.0075 | 30.8982 | 30.7798 | 30.6558 | 30.4576 | 30.2237 | 30.0639 | 29.6633 | 28.9705 | 28.2425 | 27.7103
|  | HENSTRIDGE | CT |  |  | 31.3131 | 31.2823 | 31.2488 | 31.1542 | 31.0527 | 30.9469 | 30.771 | 30.5577 | 30.4198 | 30.0699 | 29.444 | 28.7807 | 28.3107 | 30.1046 | 30.0609 | 30.0134 | 29.9029 | 29.7832 | 29.6577 | 29.4565 | 29.2194 | 29.0562 | 28.6459 | 27.9394 | 27.1981 | 26.6531 | 31.0967 | 31.0539 | 31.0075 | 30.8982 | 30.7798 | 30.6558 | 30.4576 | 30.2237 | 30.0639 | 29.6633 | 28.9705 | 28.2425 | 27.7103
|  | HENSTRIDGE | LW |  |  | 31.3132 | 31.2824 | 31.249 | 31.2113 | 31.1678 | 31.0617 | 30.9452 | 30.8266 | 30.7007 | 30.388 | 29.94 | 29.5058 | 29.0883 | 30.1047 | 30.061 | 30.0137 | 29.9601 | 29.8984 | 29.7583 | 29.6184 | 29.4761 | 29.3246 | 28.9528 | 28.4243 | 27.9121 | 27.4195 | 31.0968 | 31.054 | 31.0078 | 30.9554 | 30.895 | 30.758 | 30.6212 | 30.482 | 30.3343 | 29.972 | 29.4573 | 28.9584 | 28.4785
|  | HENSTRIDGE | ST |  |  | 31.3217 | 31.301 | 31.2814 | 31.2574 | 31.228 | 31.1704 | 31.1128 | 31.0332 | 30.9471 | 30.7361 | 30.4385 | 30.1583 | 29.8872 | 30.1168 | 30.0874 | 30.0597 | 30.0256 | 29.9839 | 29.9022 | 29.8204 | 29.7241 | 29.6208 | 29.3673 | 29.0123 | 28.6819 | 28.362 | 31.1086 | 31.0798 | 31.0527 | 31.0194 | 30.9786 | 30.8987 | 30.8188 | 30.7246 | 30.6235 | 30.3758 | 30.0301 | 29.7082 | 29.3966
|  | HENSTRIDGE | FS |  |  | 31.3309 | 31.319 | 31.3104 | 31.2895 | 31.2674 | 31.2382 | 31.2094 | 31.1725 | 31.1008 | 30.8946 | 30.7193 | 30.4125 | 30.1474 | 30.1298 | 30.113 | 30.1007 | 30.0753 | 30.048 | 30.0106 | 29.974 | 29.928 | 29.8444 | 29.609 | 29.4073 | 29.0802 | 28.7962 | 31.1213 | 31.1049 | 31.0929 | 31.0678 | 31.0408 | 31.0041 | 30.9681 | 30.9228 | 30.84 | 30.6069 | 30.4082 | 30.0837 | 29.8023
BRAMLEY (FLEE) | ALTON | HERRIARD | MINIMUM HEADROOM | SU 66770 44972 | YES | 3.1063 | 3.0921 | 3.062 | 3.0329 | 3.004 | 2.9913 | 2.9788 | 2.9663 | 2.9528 | 2.913 | 2.8471 | 2.7789 | 2.7118 | 1.4314 | 1.4115 | 1.3695 | 1.3287 | 1.2882 | 1.2704 | 1.2528 | 1.2353 | 1.2164 | 1.1606 | 1.0684 | 0.97288 | 0.87886 | 1.9562 | 1.936 | 1.8932 | 1.8517 | 1.8105 | 1.7924 | 1.7745 | 1.7567 | 1.7375 | 1.6807 | 1.5868 | 1.4896 | 1.394
|  | HERRIARD | CT |  |  | 3.1104 | 3.0984 | 3.0732 | 3.0487 | 3.0244 | 3.0004 | 2.9878 | 2.9753 | 2.9618 | 2.922 | 2.8561 | 2.7879 | 2.7209 | 1.4371 | 1.4204 | 1.385 | 1.3507 | 1.3168 | 1.2831 | 1.2655 | 1.248 | 1.2291 | 1.1733 | 1.081 | 0.98556 | 0.89162 | 1.962 | 1.945 | 1.909 | 1.8741 | 1.8395 | 1.8053 | 1.7874 | 1.7696 | 1.7503 | 1.6936 | 1.5997 | 1.5025 | 1.407
|  | HERRIARD | LW |  |  | 3.1063 | 3.0921 | 3.062 | 3.0329 | 3.004 | 2.9913 | 2.9788 | 2.9663 | 2.9528 | 2.913 | 2.8471 | 2.7789 | 2.7118 | 1.4314 | 1.4115 | 1.3695 | 1.3287 | 1.2882 | 1.2704 | 1.2528 | 1.2353 | 1.2164 | 1.1606 | 1.0684 | 0.97288 | 0.87886 | 1.9562 | 1.936 | 1.8932 | 1.8517 | 1.8105 | 1.7924 | 1.7745 | 1.7567 | 1.7375 | 1.6807 | 1.5868 | 1.4896 | 1.394
|  | HERRIARD | ST |  |  | 3.1167 | 3.1093 | 3.0965 | 3.0809 | 3.062 | 3.0542 | 3.0466 | 3.0381 | 3.0289 | 3.002 | 2.9582 | 2.9143 | 2.8705 | 1.4461 | 1.4356 | 1.4178 | 1.3959 | 1.3694 | 1.3585 | 1.3478 | 1.3359 | 1.323 | 1.2854 | 1.2241 | 1.1625 | 1.1012 | 1.9711 | 1.9605 | 1.9423 | 1.92 | 1.8931 | 1.8821 | 1.8711 | 1.859 | 1.8459 | 1.8076 | 1.7452 | 1.6826 | 1.6203
|  | HERRIARD | FS |  |  | 3.1285 | 3.1274 | 3.1264 | 3.1215 | 3.1157 | 3.113 | 3.1103 | 3.107 | 3.1034 | 3.0931 | 3.0766 | 3.0606 | 3.0455 | 1.4625 | 1.461 | 1.4595 | 1.4527 | 1.4446 | 1.4408 | 1.4371 | 1.4324 | 1.4274 | 1.4129 | 1.3898 | 1.3675 | 1.3463 | 1.9879 | 1.9863 | 1.9848 | 1.9779 | 1.9696 | 1.9658 | 1.962 | 1.9572 | 1.9522 | 1.9374 | 1.9139 | 1.8912 | 1.8696
COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE | MINIMUM HEADROOM | SU 84733 92200 | YES | 46.461 | 46.4444 | 45.4323 | 45.3493 | 45.2664 | 45.1834 | 45.1004 | 45.0175 | 44.9843 | 44.8847 | 44.7188 | 44.1734 | 43.2875 | 43.6029 | 43.5766 | 42.5442 | 42.4415 | 42.339 | 42.2376 | 42.1363 | 42.0351 | 41.9823 | 41.8238 | 41.4511 | 40.7704 | 39.8659 | 45.277 | 45.2556 | 44.2334 | 44.1406 | 44.0479 | 43.9558 | 43.8638 | 43.7718 | 43.7288 | 43.2854 | 42.3231 | 41.3567 | 40.3152
|  | HIGH WYCOMBE | CT |  |  | 46.5473 | 46.5373 | 45.9301 | 45.8803 | 45.8305 | 45.7807 | 45.7309 | 45.6812 | 45.6613 | 45.6015 | 44.8754 | 44.1821 | 43.298 | 43.6896 | 43.6702 | 43.0431 | 42.9741 | 42.9052 | 42.8364 | 42.7683 | 42.7003 | 42.6608 | 42.5421 | 41.6153 | 40.7782 | 39.8783 | 45.3635 | 45.3488 | 44.7317 | 44.6724 | 44.6131 | 44.5539 | 44.495 | 44.4362 | 44.4066 | 44.0139 | 42.4912 | 41.3684 | 40.3271
|  | HIGH WYCOMBE | LW |  |  | 46.461 | 46.4444 | 45.4323 | 45.3493 | 45.2664 | 45.1834 | 45.1004 | 45.0175 | 44.9843 | 44.8847 | 44.7188 | 44.1734 | 43.2875 | 43.6029 | 43.5766 | 42.5442 | 42.4415 | 42.339 | 42.2376 | 42.1363 | 42.0351 | 41.9823 | 41.8238 | 41.4511 | 40.7704 | 39.8659 | 45.277 | 45.2556 | 44.2334 | 44.1406 | 44.0479 | 43.9558 | 43.8638 | 43.7718 | 43.7288 | 43.2854 | 42.3231 | 41.3567 | 40.3152
|  | HIGH WYCOMBE | ST |  |  | 46.5904 | 46.5838 | 46.1789 | 46.1458 | 46.1126 | 46.0794 | 46.0462 | 46.013 | 45.9997 | 45.9599 | 45.8935 | 45.8537 | 45.712 | 43.7362 | 43.723 | 43.307 | 43.2601 | 43.2103 | 43.1638 | 43.1174 | 43.0718 | 43.0451 | 42.9655 | 42.8274 | 42.7123 | 42.2723 | 45.4083 | 45.3984 | 44.988 | 44.948 | 44.9066 | 44.8668 | 44.8271 | 44.7877 | 44.7678 | 44.7082 | 44.2555 | 43.6536 | 43.026
|  | HIGH WYCOMBE | FS |  |  | 46.6336 | 46.6302 | 46.4278 | 46.4112 | 46.3946 | 46.378 | 46.3615 | 46.3449 | 46.3382 | 46.3183 | 46.2851 | 46.2652 | 46.2287 | 43.7903 | 43.7861 | 43.5829 | 43.5629 | 43.5424 | 43.5214 | 43.5004 | 43.4783 | 43.4665 | 43.4312 | 43.3703 | 43.321 | 43.2555 | 45.4569 | 45.4531 | 45.2503 | 45.2321 | 45.2135 | 45.1947 | 45.176 | 45.1566 | 45.1474 | 45.1199 | 45.0729 | 45.0384 | 44.9875
COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE TOWN | MINIMUM HEADROOM | SU 86304 92972 | YES | 85.8116 | 85.7981 | 84.9737 | 84.9061 | 84.8385 | 84.771 | 84.7034 | 84.6358 | 84.6088 | 84.5277 | 83.6722 | 83.1849 | 82.9722 | 80.7988 | 80.7811 | 79.9481 | 79.872 | 79.7958 | 79.7164 | 79.6369 | 79.5574 | 79.5176 | 79.3965 | 78.1976 | 76.8704 | 75.5928 | 84.5928 | 84.5793 | 83.7549 | 83.6873 | 83.6197 | 83.5521 | 83.4846 | 83.417 | 83.39 | 83.3089 | 82.4533 | 81.9048 | 81.5787
|  | HIGH WYCOMBE TOWN | CT |  |  | 85.8819 | 85.8738 | 85.3791 | 85.2522 | 85.1237 | 84.9938 | 84.86 | 84.6756 | 84.6411 | 84.5339 | 83.6722 | 83.1849 | 82.9722 | 80.8688 | 80.8563 | 80.3528 | 80.217 | 80.0797 | 79.9409 | 79.7952 | 79.5988 | 79.5517 | 79.4045 | 78.1976 | 76.8704 | 75.5928 | 84.6631 | 84.6549 | 84.1603 | 84.0333 | 83.9049 | 83.775 | 83.6411 | 83.4567 | 83.4223 | 83.3151 | 82.4533 | 81.9048 | 81.5787
|  | HIGH WYCOMBE TOWN | LW |  |  | 85.8116 | 85.7981 | 84.9737 | 84.9061 | 84.8385 | 84.771 | 84.7034 | 84.6358 | 84.6088 | 84.5277 | 84.3926 | 84.3115 | 84.1628 | 80.7988 | 80.7811 | 79.9481 | 79.872 | 79.7958 | 79.7164 | 79.6369 | 79.5574 | 79.5176 | 79.3965 | 78.9039 | 77.9829 | 76.7613 | 84.5928 | 84.5793 | 83.7549 | 83.6873 | 83.6197 | 83.5521 | 83.4846 | 83.417 | 83.39 | 83.3089 | 83.1737 | 83.0302 | 82.7475
|  | HIGH WYCOMBE TOWN | ST |  |  | 85.917 | 85.9116 | 85.5819 | 85.5548 | 85.5278 | 85.5008 | 85.4737 | 85.4467 | 85.4359 | 85.4035 | 85.3494 | 85.317 | 85.2575 | 80.9064 | 80.8983 | 80.564 | 80.5316 | 80.4979 | 80.4612 | 80.4246 | 80.3894 | 80.3699 | 80.3103 | 80.1965 | 79.8099 | 79.2124 | 84.6982 | 84.6928 | 84.363 | 84.336 | 84.309 | 84.2819 | 84.2549 | 84.2279 | 84.2171 | 84.1846 | 84.1306 | 84.0981 | 84.001
|  | HIGH WYCOMBE TOWN | FS |  |  | 85.9522 | 85.9495 | 85.7846 | 85.7711 | 85.7576 | 85.744 | 85.7305 | 85.717 | 85.7116 | 85.6954 | 85.6684 | 85.6521 | 85.6224 | 80.9456 | 80.9424 | 80.777 | 80.762 | 80.7467 | 80.7298 | 80.713 | 80.6953 | 80.6865 | 80.6598 | 80.6089 | 80.5633 | 80.503 | 84.7333 | 84.7306 | 84.5658 | 84.5522 | 84.5387 | 84.5252 | 84.5117 | 84.4982 | 84.4928 | 84.4766 | 84.4495 | 84.4333 | 84.4036
LOVEDEAN GSP | WYMERING BSP | HILSEA | MINIMUM HEADROOM | SU 66394 03806 | YES | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 40.9554 | 40.9548 | 40.9537 | 40.9526 | 40.9515 | 40.9496 | 40.9477 | 40.9458 | 40.9438 | 40.9375 | 40.9249 | 40.9103 | 40.8958
|  | HILSEA | CT |  |  | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 40.9554 | 40.9548 | 40.9537 | 40.9526 | 40.9515 | 40.9503 | 40.9485 | 40.9466 | 40.9445 | 40.9383 | 40.9256 | 40.9111 | 40.8965
|  | HILSEA | LW |  |  | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 40.9554 | 40.9548 | 40.9537 | 40.9526 | 40.9515 | 40.9496 | 40.9477 | 40.9458 | 40.9438 | 40.9375 | 40.9249 | 40.9103 | 40.8958
|  | HILSEA | ST |  |  | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 40.9557 | 40.9554 | 40.9549 | 40.9542 | 40.9535 | 40.9521 | 40.9507 | 40.9495 | 40.9481 | 40.9439 | 40.9352 | 40.9257 | 40.9164
|  | HILSEA | FS |  |  | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 41.3915 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 39.3922 | 40.9562 | 40.9561 | 40.956 | 40.9559 | 40.9556 | 40.9552 | 40.9548 | 40.9542 | 40.9536 | 40.952 | 40.9486 | 40.9447 | 40.9406
MANNINGTON GSP | ARNEWOOD | HINCHESLEA | MINIMUM HEADROOM | SU 27805 00447 | YES | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 21.6154 | 20.6414 | 20.6404 | 20.6383 | 20.6363 | 20.6343 | 20.6314 | 20.628 | 20.6246 | 20.621 | 20.6102 | 20.5925 | 20.5251 | 20.1265 | 21.4413 | 21.4413 | 21.4413 | 21.4413 | 21.4413 | 21.4413 | 21.4413 | 21.4413 | 21.4413 | 21.4413 | 21.1153 | 20.7028 | 20.2972
|  | HINCHESLEA | CT |  |  | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 21.6322 | 20.6414 | 20.6404 | 20.6383 | 20.6363 | 20.6343 | 20.6323 | 20.6289 | 20.6255 | 20.6218 | 20.611 | 20.5933 | 20.5443 | 20.1459 | 21.4413 | 21.4413 | 21.4413 | 21.4413 | 21.4413 | 21.4413 | 21.4413 | 21.4413 | 21.4413 | 21.4413 | 21.1347 | 20.7223 | 20.3169
|  | HINCHESLEA | LW |  |  | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 21.6154 | 20.6415 | 20.6406 | 20.6386 | 20.6367 | 20.6349 | 20.6314 | 20.628 | 20.6246 | 20.621 | 20.6102 | 20.5925 | 20.5251 | 20.1265 | 21.4413 | 21.4413 | 21.4413 | 21.4413 | 21.4413 | 21.4413 | 21.4413 | 21.4413 | 21.4413 | 21.4413 | 21.1153 | 20.7028 | 20.2972
|  | HINCHESLEA | ST |  |  | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 20.6419 | 20.6412 | 20.6401 | 20.6388 | 20.6372 | 20.6345 | 20.6319 | 20.6296 | 20.6271 | 20.6198 | 20.6081 | 20.5963 | 20.5846 | 21.4413 | 21.4413 | 21.4413 | 21.4413 | 21.4413 | 21.4413 | 21.4413 | 21.4413 | 21.4413 | 21.4413 | 21.4413 | 21.2014 | 20.9373
|  | HINCHESLEA | FS |  |  | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 21.8905 | 20.6429 | 20.6429 | 20.6428 | 20.6425 | 20.6421 | 20.6413 | 20.6404 | 20.6394 | 20.6384 | 20.6356 | 20.6311 | 20.6269 | 20.6229 | 21.4413 | 21.4413 | 21.4413 | 21.4413 | 21.4413 | 21.4413 | 21.4413 | 21.4413 | 21.4413 | 21.4413 | 21.4413 | 21.4413 | 21.4413
BRAMLEY (FLEE) | ALDERSHOT BSP | HINDHEAD | MINIMUM HEADROOM | SU 88631 36479 | YES | 25.5051 | 25.5051 | 25.5051 | 25.5051 | 25.5007 | 25.4882 | 25.4776 | 25.4644 | 25.4541 | 25.4222 | 25.3459 | 25.258 | 25.197 | 24.1122 | 24.0944 | 24.0566 | 24.0201 | 23.9838 | 23.9478 | 23.9205 | 23.8905 | 23.8623 | 23.7773 | 23.4687 | 22.812 | 22.1644 | 24.1959 | 24.1959 | 24.1959 | 24.1959 | 24.1959 | 24.1947 | 24.192 | 24.1857 | 24.1846 | 24.1778 | 24.1566 | 23.9574 | 23.3257
|  | HINDHEAD | CT |  |  | 25.5051 | 25.5051 | 25.5051 | 25.5051 | 25.5007 | 25.4882 | 25.4776 | 25.4644 | 25.4541 | 25.4222 | 25.3459 | 25.258 | 25.197 | 24.1122 | 24.0944 | 24.0566 | 24.0201 | 23.9838 | 23.9478 | 23.9205 | 23.8905 | 23.8623 | 23.7773 | 23.4687 | 22.812 | 22.1644 | 24.1959 | 24.1959 | 24.1959 | 24.1959 | 24.1959 | 24.1959 | 24.1942 | 24.1898 | 24.189 | 24.1854 | 24.1566 | 23.9574 | 23.3257
|  | HINDHEAD | LW |  |  | 25.5051 | 25.5051 | 25.5051 | 25.5051 | 25.5051 | 25.4972 | 25.4856 | 25.4705 | 25.4598 | 25.4249 | 25.3615 | 25.2783 | 25.2266 | 24.1161 | 24.1004 | 24.0673 | 24.0351 | 24.0032 | 23.976 | 23.9477 | 23.916 | 23.8874 | 23.7993 | 23.601 | 22.9489 | 22.321 | 24.1959 | 24.1959 | 24.1959 | 24.1959 | 24.1959 | 24.1947 | 24.192 | 24.1857 | 24.1846 | 24.1778 | 24.1619 | 24.0965 | 23.4734
|  | HINDHEAD | ST |  |  | 25.5051 | 25.5051 | 25.5051 | 25.5051 | 25.5051 | 25.5048 | 25.504 | 25.4989 | 25.4917 | 25.4693 | 25.4334 | 25.3863 | 25.3494 | 24.1238 | 24.1138 | 24.0966 | 24.0755 | 24.05 | 24.0268 | 24.0034 | 23.9841 | 23.9647 | 23.9065 | 23.8108 | 23.703 | 23.4185 | 24.1959 | 24.1959 | 24.1959 | 24.1959 | 24.1959 | 24.1956 | 24.1949 | 24.193 | 24.1923 | 24.1889 | 24.1848 | 24.1698 | 24.1648
|  | HINDHEAD | FS |  |  | 25.5051 | 25.5051 | 25.5051 | 25.5051 | 25.5051 | 25.5051 | 25.5051 | 25.505 | 25.5047 | 25.5031 | 25.502 | 25.4981 | 25.4851 | 24.1406 | 24.1394 | 24.1382 | 24.1328 | 24.1265 | 24.1182 | 24.1099 | 24.0993 | 24.0917 | 24.069 | 24.033 | 23.9948 | 23.9585 | 24.1959 | 24.1959 | 24.1959 | 24.1959 | 24.1959 | 24.1959 | 24.1959 | 24.1958 | 24.1955 | 24.1939 | 24.1928 | 24.1889 | 24.1854
MANNINGTON GSP | MANNINGTON BSP | HINTON MARTELL | MINIMUM HEADROOM | SU 00702 06030 | YES | 4.0401 | 4.029 | 4.0056 | 3.8953 | 3.7658 | 3.6418 | 3.5139 | 3.3263 | 3.2547 | 3.0267 | 2.8125 | 2.183 | 1.9609 | 4.0651 | 4.0596 | 4.0478 | 3.9398 | 3.8211 | 3.704 | 3.5829 | 3.4004 | 3.3343 | 3.112 | 2.8913 | 2.2552 | 2.0265 | 4.3557 | 4.3445 | 4.3209 | 4.2105 | 4.0808 | 3.9566 | 3.8286 | 3.6409 | 3.5692 | 3.3408 | 3.1261 | 2.496 | 2.2733
|  | HINTON MARTELL | CT |  |  | 4.0432 | 4.0338 | 4.0141 | 3.9947 | 3.9751 | 3.9553 | 3.9388 | 3.9206 | 3.9039 | 3.8531 | 3.7472 | 3.6348 | 3.5437 | 4.0667 | 4.062 | 4.0521 | 4.0421 | 4.032 | 4.0215 | 4.0125 | 4.0017 | 3.9909 | 3.9342 | 3.8185 | 3.6957 | 3.5945 | 4.3589 | 4.3494 | 4.3295 | 4.3099 | 4.2901 | 4.2701 | 4.2534 | 4.235 | 4.2182 | 4.1669 | 4.0601 | 3.9468 | 3.8548
|  | HINTON MARTELL | LW |  |  | 4.0401 | 4.029 | 4.0056 | 3.9817 | 3.9567 | 3.9376 | 3.9172 | 3.8913 | 3.8734 | 3.8161 | 3.7129 | 3.5839 | 3.4986 | 4.0651 | 4.0596 | 4.0478 | 4.0352 | 4.0214 | 4.0099 | 3.9969 | 3.9785 | 3.9588 | 3.8957 | 3.7826 | 3.6433 | 3.5478 | 4.3557 | 4.3445 | 4.3209 | 4.2967 | 4.2715 | 4.2522 | 4.2316 | 4.2056 | 4.1875 | 4.1298 | 4.0257 | 3.8958 | 3.8095
|  | HINTON MARTELL | ST |  |  | 4.0425 | 4.0339 | 4.0192 | 3.8953 | 3.7658 | 3.6418 | 3.5139 | 3.3263 | 3.2547 | 3.0267 | 2.8125 | 2.183 | 1.9609 | 4.0663 | 4.062 | 4.0546 | 3.9398 | 3.8211 | 3.704 | 3.5829 | 3.4004 | 3.3343 | 3.112 | 2.8913 | 2.2552 | 2.0265 | 4.3582 | 4.3494 | 4.3346 | 4.2105 | 4.0808 | 3.9566 | 3.8286 | 3.6409 | 3.5692 | 3.3408 | 3.1261 | 2.496 | 2.2733
|  | HINTON MARTELL | FS |  |  | 4.0573 | 4.0564 | 4.0556 | 4.0517 | 4.0472 | 4.0424 | 4.0376 | 4.0314 | 4.0268 | 4.012 | 3.9899 | 3.961 | 3.9333 | 4.0738 | 4.0733 | 4.0729 | 4.0709 | 4.0687 | 4.0662 | 4.0638 | 4.0607 | 4.0581 | 4.0495 | 4.0375 | 4.0185 | 4.0003 | 4.3732 | 4.3723 | 4.3714 | 4.3675 | 4.3629 | 4.3581 | 4.3532 | 4.347 | 4.3423 | 4.3274 | 4.305 | 4.276 | 4.2481
BRAMLEY (FLEE) | COXMOOR WOOD BSP | HITCHES LANE | MINIMUM HEADROOM | SU 79461 54769 | YES | 34.3328 | 34.3328 | 34.3328 | 34.2817 | 34.2075 | 34.1077 | 33.9809 | 33.7747 | 33.7443 | 33.1121 | 31.8033 | 30.3653 | 29.3479 | 29.4581 | 29.1251 | 28.4513 | 27.7324 | 26.9797 | 26.6075 | 26.188 | 25.6706 | 25.2883 | 24.1502 | 22.6612 | 21.0535 | 19.8714 | 31.2174 | 30.886 | 30.2154 | 29.4998 | 28.7503 | 28.3795 | 27.9614 | 27.4491 | 27.0887 | 26.0138 | 24.5592 | 22.9373 | 21.7416
|  | HITCHES LANE | CT |  |  | 34.3328 | 34.3328 | 34.3328 | 34.3265 | 34.3147 | 34.2972 | 34.2718 | 34.2275 | 34.221 | 33.6253 | 32.3583 | 31.1375 | 30.0931 | 29.5139 | 29.2112 | 28.6021 | 27.9908 | 27.3625 | 26.7345 | 26.4165 | 26.0571 | 25.6987 | 24.6539 | 23.2068 | 21.8161 | 20.6072 | 31.2729 | 30.9717 | 30.3655 | 29.7571 | 29.1318 | 28.5068 | 28.1902 | 27.8397 | 27.5031 | 26.5217 | 25.1039 | 23.6992 | 22.4766
|  | HITCHES LANE | LW |  |  | 34.3328 | 34.3328 | 34.3328 | 34.2817 | 34.2075 | 34.1077 | 33.9809 | 33.7747 | 33.7443 | 33.1121 | 31.8033 | 30.3653 | 29.3479 | 29.4581 | 29.1251 | 28.4513 | 27.7324 | 26.9797 | 26.6075 | 26.188 | 25.6706 | 25.2883 | 24.1502 | 22.6612 | 21.0535 | 19.8714 | 31.2174 | 30.886 | 30.2154 | 29.4998 | 28.7503 | 28.3795 | 27.9614 | 27.4491 | 27.0887 | 26.0138 | 24.5592 | 22.9373 | 21.7416
|  | HITCHES LANE | ST |  |  | 34.3328 | 34.3328 | 34.3328 | 34.3284 | 34.3198 | 34.3066 | 34.2872 | 34.2531 | 34.2398 | 34.1835 | 34.1214 | 33.5493 | 32.8378 | 29.7962 | 29.4457 | 29.1125 | 28.6959 | 28.1858 | 27.9386 | 27.6726 | 27.4301 | 27.1899 | 26.4737 | 25.5829 | 24.6111 | 23.7926 | 31.5539 | 31.205 | 30.8735 | 30.4588 | 29.9511 | 29.7051 | 29.4403 | 29.1988 | 28.9597 | 28.2467 | 27.3883 | 26.4644 | 25.6926
|  | HITCHES LANE | FS |  |  | 34.3328 | 34.3328 | 34.3328 | 34.3326 | 34.3323 | 34.3317 | 34.3308 | 34.3288 | 34.321 | 34.2762 | 34.2406 | 34.0705 | 33.9046 | 30.1072 | 29.9222 | 29.8864 | 29.7688 | 29.6286 | 29.5412 | 29.449 | 29.3338 | 29.2372 | 28.9347 | 28.5913 | 28.1566 | 27.7455 | 31.8633 | 31.6792 | 31.6436 | 31.5266 | 31.3871 | 31.3 | 31.2083 | 31.0937 | 30.9975 | 30.6962 | 30.3543 | 29.9209 | 29.511
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | HOEFORD | MINIMUM HEADROOM | SU 57855 04433 | YES | 30.9635 | 30.9014 | 30.164 | 30.0499 | 29.934 | 29.6995 | 29.463 | 29.218 | 29.0214 | 28.403 | 27.0409 | 25.3942 | 23.7846 | 29.7473 | 29.6762 | 28.929 | 28.8074 | 28.6835 | 28.4202 | 28.1546 | 27.8807 | 27.6537 | 26.9394 | 25.3588 | 23.4727 | 21.603 | 30.9538 | 30.8828 | 30.1358 | 30.0144 | 29.8907 | 29.6279 | 29.3629 | 29.0895 | 28.8632 | 28.1508 | 26.5746 | 24.6933 | 22.8289
|  | HOEFORD | CT |  |  | 31.0217 | 30.9641 | 30.4998 | 30.3959 | 30.2901 | 30.1796 | 29.9527 | 29.7103 | 29.5204 | 28.9225 | 27.1183 | 25.3942 | 23.7846 | 29.8055 | 29.7389 | 29.2649 | 29.1534 | 29.0397 | 28.9206 | 28.6647 | 28.3932 | 28.173 | 27.4792 | 25.4564 | 23.4727 | 21.603 | 31.012 | 30.9455 | 30.4717 | 30.3603 | 30.2468 | 30.1279 | 29.8725 | 29.6017 | 29.382 | 28.6902 | 26.6718 | 24.6933 | 22.8289
|  | HOEFORD | LW |  |  | 30.9635 | 30.9014 | 30.164 | 30.0499 | 29.934 | 29.6995 | 29.463 | 29.218 | 29.0214 | 28.403 | 27.0409 | 25.4686 | 23.8815 | 29.7473 | 29.6762 | 28.929 | 28.8074 | 28.6835 | 28.4202 | 28.1546 | 27.8807 | 27.6537 | 26.9394 | 25.3588 | 23.5269 | 21.6796 | 30.9538 | 30.8828 | 30.1358 | 30.0144 | 29.8907 | 29.6279 | 29.3629 | 29.0895 | 28.8632 | 28.1508 | 26.5746 | 24.7479 | 22.9059
|  | HOEFORD | ST |  |  | 31.0723 | 31.034 | 30.7303 | 30.6821 | 30.6297 | 30.5387 | 30.4466 | 30.3133 | 30.1878 | 29.7925 | 28.9016 | 27.9161 | 26.9348 | 29.86 | 29.8157 | 29.5065 | 29.4536 | 29.3959 | 29.2928 | 29.1882 | 29.0352 | 28.8889 | 28.428 | 27.3865 | 26.2303 | 25.0832 | 31.0663 | 31.0221 | 30.7131 | 30.6603 | 30.6027 | 30.4998 | 30.3955 | 30.2429 | 30.097 | 29.6375 | 28.599 | 27.4463 | 26.3025
|  | HOEFORD | FS |  |  | 31.1233 | 31.1025 | 30.954 | 30.9328 | 30.9109 | 30.8799 | 30.8486 | 30.8135 | 30.7637 | 30.607 | 30.2412 | 29.802 | 29.3333 | 29.9148 | 29.8908 | 29.74 | 29.7171 | 29.6933 | 29.6587 | 29.6239 | 29.5846 | 29.5267 | 29.3444 | 28.9175 | 28.4026 | 27.8548 | 31.1211 | 31.0971 | 30.9464 | 30.9236 | 30.8998 | 30.8653 | 30.8305 | 30.7913 | 30.7335 | 30.5518 | 30.1261 | 29.6127 | 29.0665
MANNINGTON GSP | LYTCHETT | HOLES BAY | MINIMUM HEADROOM | SZ 00725 91955 | YES | 30.9611 | 30.9426 | 29.9073 | 29.8173 | 29.7273 | 29.6321 | 29.5368 | 29.4416 | 29.3963 | 29.2594 | 29.018 | 28.8331 | 28.5639 | 30.3924 | 30.3755 | 29.3443 | 29.2598 | 29.1753 | 29.0908 | 29.0062 | 28.9217 | 28.8879 | 28.7865 | 28.6174 | 28.516 | 28.3301 | 31.68 | 31.6601 | 30.623 | 30.5326 | 30.4421 | 30.3459 | 30.2496 | 30.1534 | 30.1071 | 29.967 | 29.7191 | 29.5268 | 28.9636
|  | HOLES BAY | CT |  |  | 31.049 | 31.0373 | 30.4144 | 30.3583 | 30.3021 | 30.2459 | 30.1845 | 30.123 | 30.0913 | 29.9949 | 29.1828 | 28.8384 | 28.5692 | 30.4803 | 30.4702 | 29.8515 | 29.8008 | 29.75 | 29.6993 | 29.6486 | 29.5979 | 29.5776 | 29.5168 | 28.777 | 28.516 | 28.3301 | 31.7679 | 31.7548 | 31.1301 | 31.0735 | 31.0168 | 30.9602 | 30.8977 | 30.8353 | 30.8026 | 30.703 | 29.8844 | 29.5325 | 28.9992
|  | HOLES BAY | LW |  |  | 30.9611 | 30.9426 | 29.9073 | 29.8173 | 29.7273 | 29.6321 | 29.5368 | 29.4416 | 29.3963 | 29.2594 | 29.018 | 28.8331 | 28.5639 | 30.3924 | 30.3755 | 29.3443 | 29.2598 | 29.1753 | 29.0908 | 29.0062 | 28.9217 | 28.8879 | 28.7865 | 28.6174 | 28.516 | 28.3301 | 31.68 | 31.6601 | 30.623 | 30.5326 | 30.4421 | 30.3459 | 30.2496 | 30.1534 | 30.1071 | 29.967 | 29.7191 | 29.5268 | 28.9636
|  | HOLES BAY | ST |  |  | 31.1212 | 31.0863 | 30.6723 | 30.5921 | 30.5093 | 30.4212 | 30.3317 | 30.2167 | 30.1702 | 30.0255 | 29.8442 | 29.5184 | 29.3238 | 30.5243 | 30.5175 | 30.105 | 30.0266 | 29.9474 | 29.8673 | 29.7857 | 29.6779 | 29.6393 | 29.5186 | 29.3866 | 29.1152 | 28.974 | 31.8658 | 31.8052 | 31.39 | 31.3082 | 31.2249 | 31.1362 | 31.046 | 30.9302 | 30.8831 | 30.7362 | 30.5505 | 30.2198 | 30.0204
|  | HOLES BAY | FS |  |  | 31.1739 | 31.1356 | 30.9292 | 30.9117 | 30.8942 | 30.8759 | 30.8576 | 30.8385 | 30.8288 | 30.7992 | 30.746 | 30.7028 | 30.6423 | 30.5682 | 30.5648 | 30.3586 | 30.3417 | 30.3248 | 30.3079 | 30.291 | 30.2741 | 30.2673 | 30.247 | 30.2132 | 30.1929 | 30.1557 | 31.9264 | 31.8563 | 31.6498 | 31.6318 | 31.6137 | 31.5942 | 31.5747 | 31.5544 | 31.5444 | 31.514 | 31.459 | 31.4138 | 31.3512
MELKSHAM GSP | FROME BSP | HOLWELL | MINIMUM HEADROOM | ST 72191 44633 | YES | 21.1846 | 21.1846 | 21.1846 | 21.1716 | 21.1447 | 21.1024 | 21.044 | 20.9377 | 20.9206 | 20.8412 | 20.6639 | 20.3294 | 20.3083 | 19.484 | 19.484 | 19.484 | 19.471 | 19.4441 | 19.4018 | 19.3434 | 19.2371 | 19.22 | 19.1406 | 18.9633 | 18.6288 | 18.6077 | 20.2581 | 20.2581 | 20.2581 | 20.2451 | 20.2181 | 20.1759 | 20.1174 | 20.0112 | 19.9941 | 19.9147 | 19.7346 | 19.2923 | 19.1649
|  | HOLWELL | CT |  |  | 21.1846 | 21.1846 | 21.1846 | 21.1806 | 21.1732 | 21.1622 | 21.1462 | 21.1149 | 21.1098 | 21.0853 | 20.8974 | 20.6921 | 20.6362 | 19.484 | 19.484 | 19.484 | 19.48 | 19.4726 | 19.4616 | 19.4456 | 19.4143 | 19.4092 | 19.3847 | 19.1968 | 18.9915 | 18.9357 | 20.2581 | 20.2581 | 20.2581 | 20.2541 | 20.2467 | 20.2357 | 20.2196 | 20.1884 | 20.1833 | 20.1588 | 19.9693 | 19.6697 | 19.5077
|  | HOLWELL | LW |  |  | 21.1846 | 21.1846 | 21.1846 | 21.1716 | 21.1447 | 21.1024 | 21.044 | 20.9377 | 20.9206 | 20.8412 | 20.6639 | 20.3294 | 20.3083 | 19.484 | 19.484 | 19.484 | 19.471 | 19.4441 | 19.4018 | 19.3434 | 19.2371 | 19.22 | 19.1406 | 18.9633 | 18.6288 | 18.6077 | 20.2581 | 20.2581 | 20.2581 | 20.2451 | 20.2181 | 20.1759 | 20.1174 | 20.0112 | 19.9941 | 19.9147 | 19.7346 | 19.2923 | 19.1649
|  | HOLWELL | ST |  |  | 21.1846 | 21.1846 | 21.1846 | 21.1818 | 21.1764 | 21.1681 | 21.1558 | 21.1318 | 21.1213 | 21.0704 | 21.0078 | 20.7979 | 20.7287 | 19.484 | 19.484 | 19.484 | 19.4812 | 19.4758 | 19.4675 | 19.4552 | 19.4312 | 19.4207 | 19.3698 | 19.3072 | 19.0973 | 19.0281 | 20.2581 | 20.2581 | 20.2581 | 20.2553 | 20.2499 | 20.2416 | 20.2293 | 20.2053 | 20.1948 | 20.1439 | 20.0797 | 19.8149 | 19.6763
|  | HOLWELL | FS |  |  | 21.1846 | 21.1846 | 21.1846 | 21.1845 | 21.1842 | 21.1838 | 21.1832 | 21.1818 | 21.1764 | 21.1452 | 21.1204 | 21.0018 | 20.8861 | 19.484 | 19.484 | 19.484 | 19.4839 | 19.4837 | 19.4832 | 19.4826 | 19.4812 | 19.4758 | 19.4446 | 19.4198 | 19.3012 | 19.1855 | 20.2581 | 20.2581 | 20.2581 | 20.258 | 20.2577 | 20.2573 | 20.2567 | 20.2553 | 20.2498 | 20.2186 | 20.1938 | 20.0752 | 19.9596
MANNINGTON GSP | SALISBURY | HOMINGTON | MINIMUM HEADROOM | SU 11742 26037 | YES | 20.8862 | 20.8862 | 20.8862 | 20.8182 | 20.7489 | 20.6781 | 20.6046 | 20.4903 | 20.4513 | 20.3248 | 20.2206 | 19.9179 | 19.8286 | 20.3921 | 20.3917 | 20.3909 | 20.3233 | 20.2535 | 20.1807 | 20.1053 | 19.9886 | 19.9469 | 19.8125 | 19.6958 | 19.3804 | 19.2786 | 21.1937 | 21.1933 | 21.1927 | 21.125 | 21.0553 | 20.983 | 20.9081 | 20.792 | 20.7509 | 20.6185 | 20.5048 | 20.1925 | 20.0524
|  | HOMINGTON | CT |  |  | 20.8862 | 20.8862 | 20.8862 | 20.8859 | 20.8854 | 20.8847 | 20.8836 | 20.8811 | 20.8807 | 20.8784 | 20.8592 | 20.8379 | 20.8313 | 20.3921 | 20.3917 | 20.3909 | 20.3897 | 20.3884 | 20.3868 | 20.382 | 20.376 | 20.3716 | 20.3577 | 20.3196 | 20.2786 | 20.2527 | 21.1937 | 21.1933 | 21.1927 | 21.1918 | 21.1906 | 21.1892 | 21.1854 | 21.1802 | 21.1768 | 21.1657 | 21.1321 | 20.9456 | 20.6969
|  | HOMINGTON | LW |  |  | 20.8862 | 20.8862 | 20.8862 | 20.8853 | 20.8835 | 20.8806 | 20.8766 | 20.8685 | 20.8671 | 20.8601 | 20.8428 | 20.8092 | 20.807 | 20.3921 | 20.3917 | 20.3909 | 20.3891 | 20.3864 | 20.3798 | 20.3722 | 20.3605 | 20.3552 | 20.3365 | 20.3003 | 20.2471 | 20.2256 | 21.1937 | 21.1933 | 21.1927 | 21.1912 | 21.1887 | 21.183 | 21.1762 | 21.1654 | 21.161 | 21.1452 | 21.1136 | 20.881 | 20.6364
|  | HOMINGTON | ST |  |  | 20.8862 | 20.8862 | 20.8862 | 20.8182 | 20.7489 | 20.6781 | 20.6046 | 20.4903 | 20.4513 | 20.3248 | 20.2206 | 19.9179 | 19.8286 | 20.3924 | 20.3922 | 20.3918 | 20.3233 | 20.2535 | 20.1807 | 20.1053 | 19.9886 | 19.9469 | 19.8125 | 19.6958 | 19.3804 | 19.2786 | 21.1939 | 21.1937 | 21.1934 | 21.125 | 21.0553 | 20.983 | 20.9081 | 20.792 | 20.7509 | 20.6185 | 20.5048 | 20.1925 | 20.0524
|  | HOMINGTON | FS |  |  | 20.8862 | 20.8862 | 20.8862 | 20.8862 | 20.8862 | 20.8861 | 20.8861 | 20.886 | 20.8857 | 20.884 | 20.8826 | 20.876 | 20.8695 | 20.3928 | 20.3928 | 20.3927 | 20.3926 | 20.3924 | 20.3917 | 20.3911 | 20.3901 | 20.3888 | 20.3841 | 20.3779 | 20.3667 | 20.3559 | 21.1941 | 21.1941 | 21.1941 | 21.194 | 21.1939 | 21.1933 | 21.1928 | 21.1921 | 21.191 | 21.187 | 21.182 | 21.1719 | 21.1622
BRAMLEY (FLEE) | COXMOOR WOOD BSP | HOOK | MINIMUM HEADROOM | SU 72602 53780 | YES | 44.0186 | 44.0186 | 44.0186 | 43.9832 | 43.941 | 43.8911 | 43.8334 | 43.7337 | 43.7182 | 43.6511 | 43.5105 | 43.0862 | 42.3756 | 41.0864 | 41.0864 | 41.0864 | 41.051 | 41.0089 | 40.959 | 40.9012 | 40.8015 | 40.7861 | 40.4882 | 39.5466 | 38.4467 | 37.613 | 42.8938 | 42.8825 | 42.8584 | 42.8021 | 42.7375 | 42.6777 | 42.6101 | 42.5008 | 42.4749 | 42.3769 | 41.7171 | 40.631 | 39.811
|  | HOOK | CT |  |  | 44.0186 | 44.0186 | 44.0186 | 44.0169 | 44.0139 | 44.0093 | 44.0026 | 43.9879 | 43.9853 | 43.9712 | 43.8552 | 43.3554 | 42.6244 | 41.0864 | 41.0864 | 41.0864 | 41.0848 | 41.0817 | 41.0772 | 41.0705 | 41.0558 | 41.0184 | 40.5518 | 39.6344 | 38.6771 | 37.8231 | 42.8938 | 42.8825 | 42.8584 | 42.8333 | 42.807 | 42.7795 | 42.763 | 42.7386 | 42.7256 | 42.6807 | 41.8092 | 40.8658 | 40.0254
|  | HOOK | LW |  |  | 44.0186 | 44.0186 | 44.0186 | 43.9832 | 43.941 | 43.8911 | 43.8334 | 43.7337 | 43.7182 | 43.6511 | 43.5105 | 43.0862 | 42.3756 | 41.0864 | 41.0864 | 41.0864 | 41.051 | 41.0089 | 40.959 | 40.9012 | 40.8015 | 40.7861 | 40.4882 | 39.5466 | 38.4467 | 37.613 | 42.8945 | 42.8835 | 42.8602 | 42.8021 | 42.7375 | 42.6777 | 42.6101 | 42.5008 | 42.4749 | 42.3769 | 41.7171 | 40.631 | 39.811
|  | HOOK | ST |  |  | 44.0186 | 44.0186 | 44.0186 | 44.0174 | 44.0152 | 44.0117 | 44.0067 | 43.9953 | 43.9899 | 43.9606 | 43.9222 | 43.7874 | 43.7384 | 41.0864 | 41.0864 | 41.0864 | 41.0853 | 41.083 | 41.0796 | 41.0745 | 41.0632 | 41.0577 | 41.0284 | 40.99 | 40.4098 | 39.8315 | 42.9 | 42.8929 | 42.8807 | 42.8646 | 42.8443 | 42.8336 | 42.8214 | 42.8034 | 42.7909 | 42.7408 | 42.6683 | 42.4995 | 42.0011
|  | HOOK | FS |  |  | 44.0186 | 44.0186 | 44.0186 | 44.0185 | 44.0185 | 44.0183 | 44.0181 | 44.0176 | 44.0158 | 44.0052 | 43.9968 | 43.9566 | 43.9174 | 41.0864 | 41.0864 | 41.0864 | 41.0864 | 41.0863 | 41.0862 | 41.086 | 41.0855 | 41.0837 | 41.0731 | 41.0647 | 41.0245 | 40.9853 | 42.912 | 42.9111 | 42.9103 | 42.9065 | 42.9019 | 42.8992 | 42.8964 | 42.8926 | 42.888 | 42.8694 | 42.8481 | 42.7954 | 42.7445
LALEHAM | EAST BEDFONT A | HOPE AND ANCHOR | MINIMUM HEADROOM | TQ 12710 72057 | YES | 2.1744 | 2.1744 | 2.1744 | 2.0576 | 1.9372 | 1.8114 | 1.681 | 1.4829 | 1.4555 | 1.3615 | 0.9359 | -0.66187 | -1.9527 | 1.39 | 1.39 | 1.39 | 1.2733 | 1.1528 | 1.027 | 0.89661 | 0.69856 | 0.67113 | 0.57709 | -0.023648 | -1.8499 | -3.3741 | 1.3625 | 1.3461 | 1.3244 | 1.1825 | 1.0322 | 0.85314 | 0.66587 | 0.40811 | 0.32088 | -0.021499 | -1.2172 | -3.0389 | -4.5586
|  | HOPE AND ANCHOR | CT |  |  | 2.1744 | 2.1744 | 2.1744 | 2.1744 | 2.1744 | 2.1744 | 2.1744 | 2.1744 | 2.1744 | 2.1744 | 1.9222 | 0.67891 | -0.59131 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 0.9661 | -0.50564 | -2.0092 | 1.3625 | 1.3461 | 1.3244 | 1.2992 | 1.2694 | 1.2382 | 1.1813 | 1.1216 | 1.0618 | 0.81341 | -0.22754 | -1.6948 | -3.1938
|  | HOPE AND ANCHOR | LW |  |  | 2.1744 | 2.1744 | 2.1744 | 2.0576 | 1.9372 | 1.8114 | 1.681 | 1.4829 | 1.4555 | 1.3615 | 0.9359 | -0.66187 | -1.9527 | 1.39 | 1.39 | 1.39 | 1.2733 | 1.1528 | 1.027 | 0.89661 | 0.69856 | 0.67113 | 0.57709 | -0.023648 | -1.8499 | -3.3741 | 1.3625 | 1.3461 | 1.3244 | 1.1825 | 1.0322 | 0.85314 | 0.66587 | 0.40811 | 0.32088 | -0.021499 | -1.2172 | -3.0389 | -4.5586
|  | HOPE AND ANCHOR | ST |  |  | 2.1744 | 2.1744 | 2.1744 | 2.1744 | 2.1744 | 2.1744 | 2.1744 | 2.1744 | 2.1744 | 2.1744 | 2.1744 | 1.4996 | 0.70254 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 0.46587 | -0.47767 | 1.3679 | 1.3567 | 1.3431 | 1.3267 | 1.3068 | 1.2832 | 1.257 | 1.2168 | 1.1758 | 0.99982 | 0.25507 | -0.72625 | -1.6669
|  | HOPE AND ANCHOR | FS |  |  | 2.1744 | 2.1744 | 2.1744 | 2.1744 | 2.1744 | 2.1744 | 2.1744 | 2.1744 | 2.1744 | 2.1744 | 2.1744 | 2.1744 | 1.9869 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.0417 | 1.373 | 1.3662 | 1.359 | 1.3509 | 1.3418 | 1.332 | 1.3216 | 1.3104 | 1.2942 | 1.2246 | 0.90218 | 0.40153 | -0.15117
LOVEDEAN GSP | HAVANT | HORNDEAN | MINIMUM HEADROOM | SU 70271 12802 | YES | 44.6393 | 44.6393 | 44.6393 | 44.5966 | 44.5518 | 44.5043 | 44.4545 | 44.3773 | 44.3665 | 44.3047 | 43.665 | 41.429 | 39.2824 | 36.4988 | 36.4325 | 36.3233 | 36.1739 | 36.019 | 35.8248 | 35.6235 | 35.3915 | 35.2152 | 34.6445 | 33.6948 | 31.7463 | 29.2582 | 40.8493 | 40.6971 | 40.4462 | 40.1586 | 39.8607 | 39.4762 | 39.0786 | 38.6458 | 38.2549 | 36.8593 | 34.4178 | 31.7329 | 29.2013
|  | HORNDEAN | CT |  |  | 44.6393 | 44.6393 | 44.6393 | 44.6178 | 44.5956 | 44.573 | 44.5491 | 44.5118 | 44.507 | 44.4909 | 44.0132 | 41.8672 | 39.7064 | 36.5106 | 36.4508 | 36.3553 | 36.2403 | 36.1211 | 35.9988 | 35.8236 | 35.6316 | 35.4613 | 34.9135 | 33.9461 | 32.2228 | 29.7206 | 40.8764 | 40.739 | 40.5196 | 40.2835 | 40.0384 | 39.787 | 39.4155 | 39.0227 | 38.6378 | 37.3058 | 34.8465 | 32.2143 | 29.6686
|  | HORNDEAN | LW |  |  | 44.6393 | 44.6393 | 44.6393 | 44.5966 | 44.5518 | 44.5043 | 44.4545 | 44.3773 | 44.3665 | 44.3276 | 43.665 | 41.429 | 39.2824 | 36.4988 | 36.4325 | 36.3233 | 36.1739 | 36.019 | 35.8248 | 35.6235 | 35.3915 | 35.2152 | 34.6445 | 33.6948 | 31.7463 | 29.2582 | 40.8493 | 40.6971 | 40.4462 | 40.1586 | 39.8607 | 39.4762 | 39.0786 | 38.6458 | 38.2549 | 36.8593 | 34.4178 | 31.7329 | 29.2013
|  | HORNDEAN | ST |  |  | 44.6393 | 44.6393 | 44.6393 | 44.6392 | 44.639 | 44.6386 | 44.638 | 44.6367 | 44.636 | 44.6327 | 44.6283 | 44.4856 | 43.2541 | 36.5371 | 36.4995 | 36.4508 | 36.3936 | 36.3241 | 36.2262 | 36.1252 | 36.0186 | 35.9048 | 35.5351 | 34.9243 | 34.289 | 33.679 | 40.9374 | 40.851 | 40.7391 | 40.6078 | 40.4486 | 40.2242 | 39.993 | 39.7499 | 39.4893 | 38.6446 | 37.1037 | 35.4263 | 33.7999
|  | HORNDEAN | FS |  |  | 44.6393 | 44.6393 | 44.6393 | 44.6252 | 44.6114 | 44.5975 | 44.5834 | 44.5614 | 44.5 | 44.3047 | 44.2113 | 43.9157 | 43.6678 | 36.5737 | 36.5597 | 36.5491 | 36.5137 | 36.475 | 36.428 | 36.3799 | 36.3158 | 36.2101 | 35.8714 | 35.5368 | 34.9825 | 34.4737 | 41.0214 | 40.9891 | 40.9649 | 40.9018 | 40.8309 | 40.7409 | 40.6487 | 40.53 | 40.3669 | 39.8422 | 39.1949 | 38.3051 | 37.4579
NURSLING GSP | WINCHESTER | HOUGHTON | MINIMUM HEADROOM | SU 33784 31741 | YES | 22.0698 | 22.0633 | 22.0494 | 21.9915 | 21.9202 | 21.8433 | 21.7268 | 21.5292 | 21.4755 | 21.2703 | 20.8274 | 20.0377 | 19.7145 | 19.5973 | 19.5938 | 19.5862 | 19.5615 | 19.513 | 19.4401 | 19.3406 | 19.1635 | 19.1316 | 18.9911 | 18.6849 | 17.974 | 17.6001 | 20.2309 | 20.1719 | 20.0471 | 19.9089 | 19.766 | 19.6182 | 19.5202 | 19.3342 | 19.242 | 18.9234 | 18.3256 | 17.462 | 17.1127
|  | HOUGHTON | CT |  |  | 22.0698 | 22.0633 | 22.0494 | 21.9915 | 21.9202 | 21.8433 | 21.7812 | 21.6883 | 21.6519 | 21.5169 | 20.9821 | 20.3217 | 19.9296 | 19.5973 | 19.5938 | 19.5862 | 19.5615 | 19.5311 | 19.4947 | 19.4531 | 19.3804 | 19.366 | 19.3074 | 18.9471 | 18.2304 | 17.788 | 20.2309 | 20.1719 | 20.0471 | 19.9089 | 19.766 | 19.6182 | 19.5202 | 19.3916 | 19.3168 | 19.0802 | 18.4282 | 17.7317 | 17.314
|  | HOUGHTON | LW |  |  | 22.0723 | 22.0671 | 22.0562 | 22.0223 | 21.9403 | 21.8467 | 21.7268 | 21.5292 | 21.4755 | 21.2703 | 20.8274 | 20.0377 | 19.7145 | 19.5987 | 19.5959 | 19.5899 | 19.5628 | 19.513 | 19.4401 | 19.3406 | 19.1635 | 19.1316 | 18.9911 | 18.6849 | 17.974 | 17.6001 | 20.2533 | 20.2068 | 20.1084 | 19.9916 | 19.853 | 19.7231 | 19.5673 | 19.3342 | 19.242 | 18.9234 | 18.3256 | 17.462 | 17.1127
|  | HOUGHTON | ST |  |  | 22.0738 | 22.07 | 22.0635 | 22.0292 | 21.987 | 21.9346 | 21.8753 | 21.7837 | 21.7368 | 21.564 | 21.3484 | 20.8117 | 20.5536 | 19.5995 | 19.5974 | 19.5939 | 19.5632 | 19.527 | 19.4884 | 19.4426 | 19.3649 | 19.333 | 19.2037 | 19.0586 | 18.6045 | 18.4439 | 20.2667 | 20.2324 | 20.1736 | 20.0752 | 19.9571 | 19.8805 | 19.7973 | 19.6814 | 19.6083 | 19.3592 | 19.0202 | 18.3728 | 18.02
|  | HOUGHTON | FS |  |  | 22.0804 | 22.08 | 22.0796 | 22.0777 | 22.0752 | 22.073 | 22.0704 | 22.0663 | 22.0559 | 22.0018 | 21.9546 | 21.7615 | 21.5533 | 19.6031 | 19.6029 | 19.6027 | 19.6016 | 19.6001 | 19.5985 | 19.5967 | 19.5934 | 19.5839 | 19.5323 | 19.4889 | 19.2996 | 19.1151 | 20.3261 | 20.3226 | 20.3192 | 20.3033 | 20.2841 | 20.2693 | 20.2542 | 20.2341 | 20.2086 | 20.1107 | 19.9941 | 19.7353 | 19.4851
BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | HOUNDMILLS | MINIMUM HEADROOM | SU 62187 52886 | YES | 59.8133 | 59.8133 | 59.8133 | 59.8133 | 59.8133 | 59.8133 | 59.8133 | 59.8133 | 59.8133 | 59.0096 | 58.2062 | 57.6175 | 57.0845 | 56.5994 | 56.5932 | 56.5812 | 56.5656 | 56.5524 | 56.5353 | 56.5155 | 56.4926 | 56.1263 | 54.702 | 53.7511 | 53.0542 | 52.4233 | 58.6957 | 58.6894 | 58.6774 | 58.6617 | 58.6485 | 58.6313 | 58.6114 | 58.5885 | 58.3227 | 56.9547 | 56.0413 | 55.3719 | 54.7659
|  | HOUNDMILLS | CT |  |  | 59.8133 | 59.8133 | 59.8133 | 59.8133 | 59.8133 | 59.8133 | 59.8133 | 59.8133 | 59.8133 | 59.0721 | 58.2685 | 57.6798 | 57.147 | 56.5996 | 56.5935 | 56.5817 | 56.5663 | 56.5534 | 56.5394 | 56.5196 | 56.4967 | 56.2003 | 54.7761 | 53.8249 | 53.128 | 52.4973 | 58.6958 | 58.6897 | 58.6779 | 58.6624 | 58.6494 | 58.6355 | 58.6156 | 58.5926 | 58.3938 | 57.0258 | 56.1121 | 55.4427 | 54.837
|  | HOUNDMILLS | LW |  |  | 59.8133 | 59.8133 | 59.8133 | 59.8133 | 59.8133 | 59.8133 | 59.8133 | 59.8133 | 59.8133 | 59.0096 | 58.2062 | 57.6175 | 57.0845 | 56.5994 | 56.5932 | 56.5812 | 56.5656 | 56.5524 | 56.5353 | 56.5155 | 56.4926 | 56.1263 | 54.702 | 53.7511 | 53.0542 | 52.4233 | 58.6957 | 58.6894 | 58.6774 | 58.6617 | 58.6485 | 58.6313 | 58.6114 | 58.5885 | 58.3227 | 56.9547 | 56.0413 | 55.3719 | 54.7659
|  | HOUNDMILLS | ST |  |  | 59.8133 | 59.8133 | 59.8133 | 59.8133 | 59.8133 | 59.8133 | 59.8133 | 59.8133 | 59.8133 | 59.8133 | 59.4897 | 59.1085 | 58.7629 | 56.6068 | 56.596 | 56.5884 | 56.5778 | 56.5684 | 56.5579 | 56.5456 | 56.5302 | 56.5131 | 55.9267 | 55.2704 | 54.8192 | 54.41 | 58.703 | 58.6922 | 58.6846 | 58.674 | 58.6645 | 58.654 | 58.6416 | 58.6262 | 58.609 | 58.131 | 57.5006 | 57.0672 | 56.6742
|  | HOUNDMILLS | FS |  |  | 59.8133 | 59.8133 | 59.8133 | 59.8133 | 59.8133 | 59.8133 | 59.8133 | 59.8133 | 59.8133 | 59.8133 | 59.8133 | 59.8133 | 59.8133 | 56.6089 | 56.6002 | 56.5967 | 56.5918 | 56.588 | 56.5837 | 56.5788 | 56.573 | 56.5663 | 56.5438 | 56.5291 | 56.5194 | 56.5112 | 58.7051 | 58.6964 | 58.6929 | 58.688 | 58.6842 | 58.6799 | 58.675 | 58.6692 | 58.6624 | 58.6398 | 58.6251 | 58.6154 | 58.6072
BRAMLEY (ANDO-THAT) | THATCHAM BSP | HUNGERFORD | MINIMUM HEADROOM | SU 34066 68957 | YES | 20.0292 | 20.0292 | 22.6292 | 22.6232 | 22.6174 | 22.6115 | 22.6056 | 22.5963 | 22.5704 | 22.4883 | 22.4492 | 22.3261 | 22.2231 | 18.0268 | 18.0251 | 20.5214 | 20.5178 | 20.5141 | 20.5101 | 20.5033 | 20.4928 | 20.4658 | 20.3805 | 20.1476 | 19.6685 | 19.1967 | 18.9965 | 18.9942 | 21.5893 | 21.5846 | 21.5798 | 21.5751 | 21.5438 | 21.4755 | 21.4019 | 21.1843 | 20.8238 | 20.4534 | 20.0887
|  | HUNGERFORD | CT |  |  | 20.0292 | 20.0292 | 22.6292 | 22.6292 | 22.6292 | 22.6292 | 22.6292 | 22.6292 | 22.6292 | 22.6292 | 22.6292 | 22.6292 | 22.6292 | 18.0268 | 18.0251 | 20.5214 | 20.5178 | 20.5141 | 20.5105 | 20.5065 | 20.5026 | 20.4983 | 20.4857 | 20.1476 | 19.6685 | 19.1967 | 18.9965 | 18.9942 | 21.5893 | 21.5846 | 21.5798 | 21.5751 | 21.5438 | 21.4755 | 21.4019 | 21.1843 | 20.8238 | 20.4534 | 20.0887
|  | HUNGERFORD | LW |  |  | 20.0292 | 20.0292 | 22.6292 | 22.6292 | 22.6292 | 22.6292 | 22.6292 | 22.6292 | 22.6292 | 22.6292 | 22.6292 | 22.6292 | 22.6292 | 18.0272 | 18.0256 | 20.5223 | 20.5191 | 20.5159 | 20.5118 | 20.5078 | 20.5039 | 20.4996 | 20.487 | 20.1765 | 19.6973 | 19.2256 | 18.9969 | 18.9949 | 21.5906 | 21.5864 | 21.5821 | 21.5768 | 21.566 | 21.4977 | 21.4241 | 21.2064 | 20.8461 | 20.4756 | 20.111
|  | HUNGERFORD | ST |  |  | 20.0292 | 20.0292 | 22.6292 | 22.6292 | 22.6292 | 22.6292 | 22.6292 | 22.6292 | 22.6292 | 22.6292 | 22.6292 | 22.6292 | 22.6292 | 18.0294 | 18.029 | 20.5284 | 20.5277 | 20.5267 | 20.5241 | 20.5215 | 20.5188 | 20.5159 | 20.5074 | 20.4935 | 20.4797 | 20.1736 | 18.9998 | 18.9993 | 21.5985 | 21.5975 | 21.5963 | 21.5929 | 21.5895 | 21.586 | 21.5822 | 21.5593 | 21.3193 | 21.0808 | 20.8439
|  | HUNGERFORD | FS |  |  | 20.0292 | 20.0292 | 22.6292 | 22.6232 | 22.6174 | 22.6115 | 22.6056 | 22.5963 | 22.5704 | 22.4883 | 22.4492 | 22.3261 | 22.2231 | 18.0299 | 18.0298 | 20.5297 | 20.5233 | 20.5169 | 20.5101 | 20.5033 | 20.4928 | 20.4658 | 20.3805 | 20.3361 | 20.208 | 20.1003 | 19.0005 | 19.0003 | 21.6002 | 21.5937 | 21.5871 | 21.5801 | 21.5729 | 21.5621 | 21.5348 | 21.4484 | 21.4024 | 21.2727 | 21.1343
LOVEDEAN GSP | CHICHESTER & HUNSTON | HUNSTON | MINIMUM HEADROOM | SU 86949 02632 | YES | 44.9037 | 44.8667 | 44.8071 | 44.7446 | 44.6765 | 44.5713 | 44.461 | 44.3281 | 44.1825 | 43.678 | 43.1195 | 42.6807 | 42.2547 | 41.9268 | 41.8776 | 41.7985 | 41.7155 | 41.6253 | 41.4855 | 41.3392 | 41.1628 | 40.9696 | 40.3 | 39.5589 | 38.9765 | 38.4112 | 41.3698 | 41.3295 | 41.2646 | 41.1965 | 41.1225 | 41.0078 | 40.8877 | 40.743 | 40.5845 | 40.0352 | 39.4271 | 38.9493 | 38.4856
|  | HUNSTON | CT |  |  | 44.9062 | 44.8706 | 44.8139 | 44.7543 | 44.6891 | 44.6213 | 44.511 | 44.3781 | 44.2325 | 43.728 | 43.1696 | 42.7308 | 42.3052 | 41.9301 | 41.8828 | 41.8076 | 41.7284 | 41.6419 | 41.5519 | 41.4055 | 41.2292 | 41.036 | 40.3664 | 39.6253 | 39.0429 | 38.4781 | 41.3725 | 41.3338 | 41.272 | 41.2071 | 41.1361 | 41.0622 | 40.9422 | 40.7975 | 40.639 | 40.0897 | 39.4816 | 39.0038 | 38.5405
|  | HUNSTON | LW |  |  | 44.9037 | 44.8667 | 44.8071 | 44.7446 | 44.6765 | 44.5713 | 44.461 | 44.3281 | 44.1825 | 43.678 | 43.1195 | 42.6807 | 42.2547 | 41.9268 | 41.8776 | 41.7985 | 41.7155 | 41.6253 | 41.4855 | 41.3392 | 41.1628 | 40.9696 | 40.3 | 39.5589 | 38.9765 | 38.4112 | 41.3698 | 41.3295 | 41.2646 | 41.1965 | 41.1225 | 41.0078 | 40.8877 | 40.743 | 40.5845 | 40.0352 | 39.4271 | 38.9493 | 38.4856
|  | HUNSTON | ST |  |  | 44.92 | 44.8951 | 44.8614 | 44.8197 | 44.7684 | 44.7041 | 44.6366 | 44.5468 | 44.4472 | 44.0942 | 43.7112 | 43.4277 | 43.1514 | 41.9484 | 41.9154 | 41.8706 | 41.8153 | 41.7472 | 41.6618 | 41.5722 | 41.4531 | 41.3209 | 40.8525 | 40.3441 | 39.9679 | 39.6012 | 41.3876 | 41.3605 | 41.3237 | 41.2784 | 41.2225 | 41.1525 | 41.0789 | 40.9812 | 40.8727 | 40.4884 | 40.0713 | 39.7627 | 39.4619
|  | HUNSTON | FS |  |  | 44.9479 | 44.9387 | 44.9306 | 44.9166 | 44.9001 | 44.8765 | 44.8519 | 44.8175 | 44.7785 | 44.6397 | 44.4899 | 44.384 | 44.2844 | 41.9853 | 41.9732 | 41.9625 | 41.9439 | 41.9219 | 41.8906 | 41.8579 | 41.8124 | 41.7606 | 41.5764 | 41.3775 | 41.237 | 41.1049 | 41.4179 | 41.4079 | 41.3991 | 41.3838 | 41.3658 | 41.3401 | 41.3133 | 41.276 | 41.2335 | 41.0823 | 40.9192 | 40.8039 | 40.6955
BRAMLEY (ANDO-THAT) | ANDOVER BSP | HURSTBOURNE TARRANT | MINIMUM HEADROOM | SU 39384 52476 | YES | 10.0062 | 10.0062 | 10.0062 | 9.8153 | 9.6182 | 9.4124 | 9.199 | 8.875 | 8.8301 | 8.6762 | 8.4461 | 8.0595 | 7.9524 | 9.232 | 9.232 | 9.232 | 9.041 | 8.844 | 8.6381 | 8.4248 | 8.1007 | 8.0559 | 7.902 | 7.5619 | 6.9732 | 6.752 | 9.7495 | 9.7495 | 9.7495 | 9.5586 | 9.3615 | 9.1557 | 8.9423 | 8.6183 | 8.5734 | 8.4195 | 8.1894 | 7.8028 | 7.7804
|  | HURSTBOURNE TARRANT | CT |  |  | 10.0062 | 10.0062 | 10.0062 | 10.0062 | 10.0062 | 10.0062 | 10.0062 | 10.0062 | 10.0062 | 10.0062 | 10.0062 | 10.0062 | 9.9348 | 9.232 | 9.232 | 9.232 | 9.232 | 9.232 | 9.232 | 9.232 | 9.232 | 9.232 | 9.232 | 9.1395 | 8.9376 | 8.7391 | 9.7495 | 9.7495 | 9.7495 | 9.7495 | 9.7495 | 9.7495 | 9.7495 | 9.7495 | 9.7495 | 9.7495 | 9.7495 | 9.7495 | 9.7495
|  | HURSTBOURNE TARRANT | LW |  |  | 10.0062 | 10.0062 | 10.0062 | 9.8153 | 9.6182 | 9.4124 | 9.199 | 8.875 | 8.8301 | 8.6762 | 8.4461 | 8.0595 | 7.9524 | 9.232 | 9.232 | 9.232 | 9.041 | 8.844 | 8.6381 | 8.4248 | 8.1007 | 8.0559 | 7.902 | 7.5619 | 6.9732 | 6.752 | 9.7495 | 9.7495 | 9.7495 | 9.5586 | 9.3615 | 9.1557 | 8.9423 | 8.6183 | 8.5734 | 8.4195 | 8.1894 | 7.8028 | 7.7804
|  | HURSTBOURNE TARRANT | ST |  |  | 10.0062 | 10.0062 | 10.0062 | 10.0062 | 10.0062 | 10.0062 | 10.0062 | 10.0062 | 10.0062 | 10.0062 | 10.0062 | 10.0062 | 10.0062 | 9.232 | 9.232 | 9.232 | 9.232 | 9.232 | 9.232 | 9.232 | 9.232 | 9.232 | 9.232 | 9.232 | 9.156 | 9.0264 | 9.7495 | 9.7495 | 9.7495 | 9.7495 | 9.7495 | 9.7495 | 9.7495 | 9.7495 | 9.7495 | 9.7495 | 9.7495 | 9.7495 | 9.7495
|  | HURSTBOURNE TARRANT | FS |  |  | 10.0062 | 10.0062 | 10.0062 | 9.9972 | 9.9883 | 9.9794 | 9.9703 | 9.9562 | 9.9169 | 9.7922 | 9.7328 | 9.5458 | 9.3894 | 9.232 | 9.232 | 9.232 | 9.223 | 9.2141 | 9.2052 | 9.1961 | 9.182 | 9.1427 | 9.018 | 8.9586 | 8.7716 | 8.6152 | 9.7495 | 9.7495 | 9.7495 | 9.7405 | 9.7316 | 9.7227 | 9.7136 | 9.6995 | 9.6602 | 9.5355 | 9.4761 | 9.2891 | 9.1327
EALING GSP |  | IRONBRIDGE | MINIMUM HEADROOM | TQ 14226 80171 |  | 36.9542 | 36.9436 | 36.9226 | 36.8831 | 36.8406 | 36.7974 | 36.7516 | 36.696 | 36.6715 | 36.5972 | 36.4097 | 36.1985 | 35.9465 | 34.3878 | 34.3757 | 34.3517 | 34.3097 | 34.2643 | 34.2182 | 34.1692 | 34.1108 | 34.0834 | 34.0008 | 33.7965 | 32.4214 | 30.4097 | 35.4057 | 35.4057 | 35.4057 | 35.3846 | 35.3632 | 35.3414 | 35.3186 | 35.2835 | 35.2791 | 35.2648 | 34.6378 | 32.638 | 30.705
|  | IRONBRIDGE | CT |  |  | 36.955 | 36.9447 | 36.9246 | 36.8831 | 36.8406 | 36.7974 | 36.7516 | 36.696 | 36.6715 | 36.5972 | 36.4097 | 36.1985 | 35.9465 | 34.3886 | 34.377 | 34.354 | 34.3097 | 34.2643 | 34.2182 | 34.1692 | 34.1108 | 34.0834 | 34.0008 | 33.7965 | 32.4214 | 30.4097 | 35.4057 | 35.4057 | 35.4057 | 35.3846 | 35.3632 | 35.3414 | 35.3186 | 35.2835 | 35.2791 | 35.2648 | 34.6378 | 32.638 | 30.705
|  | IRONBRIDGE | LW |  |  | 36.9542 | 36.9436 | 36.9226 | 36.8883 | 36.853 | 36.8173 | 36.7798 | 36.7372 | 36.7141 | 36.6436 | 36.5048 | 36.3255 | 36.0455 | 34.3878 | 34.3757 | 34.3517 | 34.3146 | 34.2762 | 34.2375 | 34.1968 | 34.1514 | 34.1255 | 34.0467 | 33.8911 | 32.4938 | 30.4997 | 35.4057 | 35.4057 | 35.4057 | 35.3927 | 35.3793 | 35.3653 | 35.3508 | 35.3288 | 35.3258 | 35.3153 | 34.6806 | 32.7127 | 30.7972
|  | IRONBRIDGE | ST |  |  | 36.9623 | 36.9572 | 36.9489 | 36.9388 | 36.9268 | 36.9124 | 36.8972 | 36.8832 | 36.8695 | 36.8286 | 36.7454 | 36.6538 | 36.565 | 34.3969 | 34.3911 | 34.3817 | 34.3703 | 34.3565 | 34.3401 | 34.3229 | 34.307 | 34.2913 | 34.2448 | 34.1501 | 34.0459 | 33.9447 | 35.4057 | 35.4057 | 35.4057 | 35.4057 | 35.4057 | 35.4057 | 35.4057 | 35.4057 | 35.4057 | 35.4057 | 35.4057 | 35.3601 | 34.1355
|  | IRONBRIDGE | FS |  |  | 36.9674 | 36.9657 | 36.9636 | 36.9595 | 36.9547 | 36.9493 | 36.9436 | 36.9377 | 36.9323 | 36.9165 | 36.8833 | 36.8441 | 36.8043 | 34.4028 | 34.4008 | 34.3985 | 34.3937 | 34.3883 | 34.3821 | 34.3757 | 34.3689 | 34.3628 | 34.3448 | 34.307 | 34.2625 | 34.2171 | 35.4057 | 35.4057 | 35.4057 | 35.4057 | 35.4057 | 35.4057 | 35.4057 | 35.4057 | 35.4057 | 35.4057 | 35.4057 | 35.4057 | 35.4057
BRAMLEY (BASI) | BASINGSTOKE T1A & T2A | JAYS CLOSE | MINIMUM HEADROOM | SU 63055 50105 | YES | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 56.5628 | 56.5607 | 56.5561 | 56.5517 | 56.5474 | 56.5394 | 56.5316 | 56.5238 | 56.5154 | 56.4857 | 56.3698 | 56.2291 | 56.0905 | 57.49 | 57.4536 | 57.3771 | 57.3027 | 57.2286 | 57.0949 | 56.9624 | 56.8309 | 56.6893 | 56.2687 | 55.5548 | 54.804 | 54.0638
|  | JAYS CLOSE | CT |  |  | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 56.5636 | 56.5619 | 56.5583 | 56.5548 | 56.5513 | 56.5478 | 56.54 | 56.5322 | 56.5238 | 56.4989 | 56.3963 | 56.2557 | 56.1171 | 57.5035 | 57.4745 | 57.4135 | 57.3543 | 57.2952 | 57.2366 | 57.104 | 56.9725 | 56.8308 | 56.4102 | 55.6965 | 54.9457 | 54.2061
|  | JAYS CLOSE | LW |  |  | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 56.5628 | 56.5607 | 56.5561 | 56.5517 | 56.5474 | 56.5394 | 56.5316 | 56.5238 | 56.5154 | 56.4857 | 56.3698 | 56.2291 | 56.0905 | 57.49 | 57.4536 | 57.3771 | 57.3027 | 57.2286 | 57.0949 | 56.9624 | 56.8309 | 56.6893 | 56.2687 | 55.5548 | 54.804 | 54.0638
|  | JAYS CLOSE | ST |  |  | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 56.571 | 56.5617 | 56.559 | 56.5556 | 56.5514 | 56.5459 | 56.5403 | 56.535 | 56.5293 | 56.5125 | 56.4747 | 56.3929 | 56.3029 | 57.6281 | 57.4716 | 57.4247 | 57.3672 | 57.2977 | 57.2033 | 57.11 | 57.0202 | 56.9235 | 56.6398 | 56.163 | 55.6784 | 55.1977
|  | JAYS CLOSE | FS |  |  | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 60.6251 | 56.5738 | 56.566 | 56.5658 | 56.5651 | 56.5642 | 56.5623 | 56.5605 | 56.5581 | 56.5559 | 56.5494 | 56.5386 | 56.5279 | 56.5177 | 57.6753 | 57.5434 | 57.5405 | 57.528 | 57.5133 | 57.4818 | 57.4505 | 57.4103 | 57.3728 | 57.2631 | 57.081 | 56.9007 | 56.7272
MINETY GSP | CIRENCESTER BSP | KEMBLE RAF | MINIMUM HEADROOM |  |  | 2.3782 | 2.3782 | 2.3782 | 2.1083 | 1.8298 | 1.5388 | 1.2373 | 0.77927 | 0.71584 | 0.49837 | 0.17317 | -0.40522 | -0.44644 | 1.9879 | 1.9812 | 1.9671 | 1.6834 | 1.3913 | 1.0959 | 0.78988 | 0.32751 | 0.25935 | 0.027884 | -0.32021 | -0.92214 | -0.98655 | 2.3441 | 2.3375 | 2.3234 | 2.0398 | 1.7477 | 1.4523 | 1.1463 | 0.68394 | 0.61578 | 0.38436 | 0.03634 | -0.56552 | -0.62986
|  | KEMBLE RAF | CT |  |  | 2.3782 | 2.3782 | 2.3782 | 2.2963 | 2.213 | 2.1283 | 2.0398 | 1.9034 | 1.8862 | 1.8307 | 1.5582 | 1.2281 | 1.1522 | 1.9897 | 1.984 | 1.9719 | 1.8783 | 1.7833 | 1.6871 | 1.5942 | 1.4535 | 1.4314 | 1.362 | 1.0666 | 0.71293 | 0.61388 | 2.346 | 2.3403 | 2.3282 | 2.2346 | 2.1397 | 2.0435 | 1.9506 | 1.8099 | 1.7879 | 1.7184 | 1.4232 | 1.0695 | 0.97056
|  | KEMBLE RAF | LW |  |  | 2.3782 | 2.3782 | 2.3782 | 2.1083 | 1.8298 | 1.5388 | 1.2373 | 0.77927 | 0.71584 | 0.49837 | 0.17317 | -0.40522 | -0.44644 | 1.9879 | 1.9812 | 1.9671 | 1.6834 | 1.3913 | 1.0959 | 0.78988 | 0.32751 | 0.25935 | 0.027884 | -0.32021 | -0.92214 | -0.98655 | 2.3441 | 2.3375 | 2.3234 | 2.0398 | 1.7477 | 1.4523 | 1.1463 | 0.68394 | 0.61578 | 0.38436 | 0.03634 | -0.56552 | -0.62986
|  | KEMBLE RAF | ST |  |  | 2.3782 | 2.3782 | 2.3782 | 2.3782 | 2.3782 | 2.3782 | 2.3782 | 2.3782 | 2.3782 | 2.3782 | 2.3782 | 2.3782 | 2.3782 | 1.9898 | 1.9849 | 1.9765 | 1.9662 | 1.9538 | 1.9502 | 1.9465 | 1.9435 | 1.9403 | 1.9309 | 1.9157 | 1.9006 | 1.8855 | 2.346 | 2.3412 | 2.3328 | 2.3225 | 2.3102 | 2.3065 | 2.3029 | 2.2999 | 2.2967 | 2.2874 | 2.2722 | 2.2571 | 2.2421
|  | KEMBLE RAF | FS |  |  | 2.3782 | 2.3782 | 2.3782 | 2.3782 | 2.3782 | 2.3782 | 2.3782 | 2.3782 | 2.3782 | 2.3782 | 2.3782 | 2.3782 | 2.3782 | 1.9983 | 1.9978 | 1.9973 | 1.995 | 1.9924 | 1.9911 | 1.9899 | 1.9884 | 1.9871 | 1.9836 | 1.9779 | 1.9726 | 1.9675 | 2.3545 | 2.354 | 2.3535 | 2.3512 | 2.3486 | 2.3474 | 2.3461 | 2.3446 | 2.3434 | 2.3398 | 2.3342 | 2.3289 | 2.3238
COWLEY GSP | COWLEY LOCAL (2 X 45) | KENNINGTON | MINIMUM HEADROOM | SP 52881 01094 | NO | 4.3927 | 4.3927 | 4.3927 | 4.3758 | 4.3585 | 4.3406 | 4.3219 | 4.2926 | 4.2824 | 4.2484 | 4.219 | 4.0603 | 3.7381 | 4.0399 | 4.0379 | 4.0352 | 4.022 | 4.0043 | 3.9843 | 3.9634 | 3.9318 | 3.9194 | 3.8787 | 3.7993 | 3.4829 | 3.1173 | 3.1552 | 3.1098 | 3.0475 | 3.0074 | 2.9708 | 2.9197 | 2.843 | 2.7637 | 2.6871 | 2.4609 | 2.0645 | 1.6503 | 1.2704
|  | KENNINGTON | CT |  |  | 4.3927 | 4.3927 | 4.3927 | 4.3925 | 4.3921 | 4.3915 | 4.3906 | 4.3886 | 4.3883 | 4.3864 | 4.3708 | 4.0912 | 3.7655 | 4.0399 | 4.0379 | 4.0352 | 4.0332 | 4.0312 | 4.0289 | 4.0247 | 4.0195 | 4.0158 | 4.0042 | 3.8193 | 3.5129 | 3.146 | 3.1552 | 3.1098 | 3.0475 | 3.0074 | 2.9708 | 2.9321 | 2.8578 | 2.783 | 2.7073 | 2.485 | 2.0867 | 1.6826 | 1.2992
|  | KENNINGTON | LW |  |  | 4.3927 | 4.3927 | 4.3927 | 4.392 | 4.3905 | 4.3882 | 4.3849 | 4.3784 | 4.3773 | 4.3715 | 4.3575 | 4.0603 | 3.7381 | 4.0402 | 4.0383 | 4.0358 | 4.0335 | 4.0307 | 4.0252 | 4.0187 | 4.0089 | 4.0044 | 3.9889 | 3.7993 | 3.4829 | 3.1173 | 3.1602 | 3.1176 | 3.0611 | 3.0261 | 2.9939 | 2.9197 | 2.843 | 2.7637 | 2.6871 | 2.4609 | 2.0645 | 1.6503 | 1.2704
|  | KENNINGTON | ST |  |  | 4.3927 | 4.3927 | 4.3927 | 4.3758 | 4.3585 | 4.3406 | 4.3219 | 4.2926 | 4.2824 | 4.2484 | 4.219 | 4.125 | 4.0852 | 4.0414 | 4.0404 | 4.0394 | 4.022 | 4.0043 | 3.9843 | 3.9634 | 3.9318 | 3.9194 | 3.8787 | 3.8379 | 3.6915 | 3.4769 | 3.1883 | 3.1655 | 3.1424 | 3.116 | 3.0907 | 3.0233 | 2.9541 | 2.8752 | 2.8135 | 2.6297 | 2.3431 | 1.9988 | 1.7223
|  | KENNINGTON | FS |  |  | 4.3927 | 4.3927 | 4.3927 | 4.3927 | 4.3927 | 4.3927 | 4.3927 | 4.3926 | 4.3924 | 4.391 | 4.3898 | 4.3844 | 4.3792 | 4.0419 | 4.0412 | 4.0407 | 4.0405 | 4.0404 | 4.0396 | 4.0388 | 4.0377 | 4.0366 | 4.0326 | 4.027 | 4.0174 | 4.0081 | 3.1984 | 3.1843 | 3.172 | 3.1679 | 3.165 | 3.1475 | 3.1295 | 3.1073 | 3.087 | 3.0274 | 2.9261 | 2.8249 | 2.7281
BRAMLEY (FLEE) | BURGHFIELD MAIN | KENTWOOD HILL | MINIMUM HEADROOM | SU 67102 74048 | YES | 27.511 | 27.511 | 27.511 | 27.4814 | 27.4513 | 27.4208 | 27.3888 | 27.3396 | 27.3333 | 27.3133 | 27.2207 | 25.8426 | 23.5477 | 26.3388 | 26.335 | 26.3289 | 26.2933 | 26.257 | 26.2201 | 26.1687 | 26.1002 | 26.0733 | 25.9897 | 24.9064 | 22.3747 | 19.8827 | 26.5244 | 26.5203 | 26.5137 | 26.4777 | 26.441 | 26.4037 | 26.3509 | 26.281 | 26.2527 | 26.1645 | 25.5026 | 22.8575 | 20.2444
|  | KENTWOOD HILL | CT |  |  | 27.511 | 27.511 | 27.511 | 27.4814 | 27.4513 | 27.4208 | 27.3888 | 27.3396 | 27.3333 | 27.3133 | 27.2207 | 25.8426 | 23.5477 | 26.3388 | 26.335 | 26.3289 | 26.2933 | 26.257 | 26.2201 | 26.1687 | 26.1002 | 26.0733 | 25.9897 | 24.9879 | 22.3902 | 19.8827 | 26.5244 | 26.5203 | 26.5137 | 26.4777 | 26.441 | 26.4037 | 26.3509 | 26.281 | 26.2527 | 26.1645 | 25.5926 | 22.8815 | 20.247
|  | KENTWOOD HILL | LW |  |  | 27.511 | 27.511 | 27.511 | 27.4883 | 27.4649 | 27.4404 | 27.4151 | 27.3766 | 27.3712 | 27.353 | 27.3256 | 25.8431 | 23.5722 | 26.3392 | 26.3356 | 26.3299 | 26.3016 | 26.2724 | 26.2285 | 26.1837 | 26.1259 | 26.1 | 26.018 | 24.9064 | 22.3747 | 19.8912 | 26.5248 | 26.5209 | 26.5148 | 26.4862 | 26.4565 | 26.4113 | 26.3651 | 26.3059 | 26.2785 | 26.1921 | 25.5026 | 22.8575 | 20.2444
|  | KENTWOOD HILL | ST |  |  | 27.511 | 27.511 | 27.511 | 27.5025 | 27.4939 | 27.4851 | 27.476 | 27.462 | 27.4572 | 27.442 | 27.4291 | 27.3853 | 26.7923 | 26.3414 | 26.3393 | 26.3367 | 26.3252 | 26.3128 | 26.2921 | 26.271 | 26.2438 | 26.2249 | 26.1664 | 26.0645 | 25.0082 | 23.4041 | 26.5271 | 26.5249 | 26.5221 | 26.5104 | 26.4977 | 26.4761 | 26.4543 | 26.4261 | 26.4062 | 26.3447 | 26.2365 | 25.6063 | 23.9296
|  | KENTWOOD HILL | FS |  |  | 27.511 | 27.511 | 27.511 | 27.5081 | 27.5053 | 27.5024 | 27.4995 | 27.495 | 27.4824 | 27.4425 | 27.4235 | 27.3636 | 27.3135 | 26.3436 | 26.3428 | 26.3422 | 26.3382 | 26.3341 | 26.3274 | 26.3206 | 26.3113 | 26.2932 | 26.2364 | 26.1819 | 26.0804 | 25.9878 | 26.5295 | 26.5286 | 26.528 | 26.524 | 26.5197 | 26.5127 | 26.5057 | 26.496 | 26.4776 | 26.4196 | 26.3626 | 26.2582 | 26.1626
COWLEY GSP | YARNTON BSP | KIDDINGTON | MINIMUM HEADROOM | SP 43362 24301 | NO | 33.5843 | 33.5843 | 33.5843 | 33.4611 | 33.334 | 33.2012 | 33.0635 | 32.8545 | 32.8255 | 32.7262 | 32.5778 | 32.3284 | 32.3139 | 32.4032 | 32.4032 | 32.4032 | 32.2799 | 32.1528 | 32.0199 | 31.8748 | 31.6584 | 31.6215 | 31.4987 | 31.3114 | 30.8585 | 30.5682 | 33.5204 | 33.5087 | 33.4838 | 33.3907 | 33.2553 | 33.0781 | 32.8964 | 32.6437 | 32.5677 | 32.3031 | 31.8607 | 31.3064 | 30.992
|  | KIDDINGTON | CT |  |  | 33.5843 | 33.5843 | 33.5843 | 33.5843 | 33.5843 | 33.5843 | 33.5843 | 33.5843 | 33.5843 | 33.5843 | 33.5843 | 33.5843 | 33.5843 | 32.4032 | 32.4032 | 32.4032 | 32.4028 | 32.3987 | 32.3947 | 32.3873 | 32.3799 | 32.372 | 32.3485 | 32.3004 | 32.0665 | 31.7778 | 33.5204 | 33.5087 | 33.4838 | 33.4597 | 33.4358 | 33.4121 | 33.3681 | 33.3244 | 33.2757 | 33.0986 | 32.8047 | 32.4999 | 32.2002
|  | KIDDINGTON | LW |  |  | 33.5843 | 33.5843 | 33.5843 | 33.4611 | 33.334 | 33.2012 | 33.0635 | 32.8545 | 32.8255 | 32.7262 | 32.5778 | 32.3284 | 32.3139 | 32.4032 | 32.4032 | 32.4032 | 32.2799 | 32.1528 | 32.0199 | 31.8748 | 31.6584 | 31.6215 | 31.4987 | 31.3114 | 30.8585 | 30.5682 | 33.5346 | 33.5306 | 33.5221 | 33.3907 | 33.2553 | 33.0781 | 32.8964 | 32.6437 | 32.5677 | 32.3031 | 31.8607 | 31.3064 | 30.992
|  | KIDDINGTON | ST |  |  | 33.5843 | 33.5843 | 33.5843 | 33.5843 | 33.5843 | 33.5843 | 33.5843 | 33.5843 | 33.5843 | 33.5843 | 33.5843 | 33.5843 | 33.5843 | 32.4032 | 32.4032 | 32.4032 | 32.4032 | 32.4032 | 32.4032 | 32.4032 | 32.3988 | 32.3934 | 32.3776 | 32.3516 | 32.3256 | 32.2434 | 33.6619 | 33.5352 | 33.5316 | 33.5271 | 33.5216 | 33.4936 | 33.4661 | 33.4363 | 33.4042 | 33.3104 | 33.1222 | 32.9256 | 32.7304
|  | KIDDINGTON | FS |  |  | 33.5843 | 33.5843 | 33.5843 | 33.5843 | 33.5843 | 33.5843 | 33.5843 | 33.5843 | 33.5843 | 33.5843 | 33.5843 | 33.5843 | 33.5843 | 32.4032 | 32.4032 | 32.4032 | 32.4032 | 32.4032 | 32.4032 | 32.4032 | 32.4032 | 32.4032 | 32.4021 | 32.3922 | 32.3827 | 32.3737 | 33.6653 | 33.5404 | 33.5401 | 33.5388 | 33.5373 | 33.5271 | 33.5172 | 33.5043 | 33.4919 | 33.4555 | 33.3971 | 33.3409 | 33.2876
BRAMLEY (FLEE) | READING BSP | KIDMORE END | MINIMUM HEADROOM | SU 69953 78205 | YES | 16.9435 | 16.9435 | 16.9435 | 16.9435 | 16.9435 | 16.9435 | 16.9435 | 16.9435 | 16.9435 | 16.9419 | 16.2471 | 15.4119 | 14.5738 | 15.3089 | 15.2834 | 15.2304 | 15.1787 | 15.0352 | 14.794 | 14.6812 | 14.568 | 14.4476 | 14.0657 | 13.199 | 12.1571 | 11.1116 | 15.904 | 15.8882 | 15.8553 | 15.6984 | 15.5361 | 15.3749 | 15.2995 | 15.2239 | 15.1434 | 14.8883 | 14.3092 | 13.5381 | 12.4802
|  | KIDMORE END | CT |  |  | 16.9435 | 16.9435 | 16.9435 | 16.9435 | 16.9435 | 16.9435 | 16.9435 | 16.9435 | 16.9435 | 16.9419 | 16.2471 | 15.4119 | 14.5738 | 15.3089 | 15.2834 | 15.2304 | 15.1787 | 15.0352 | 14.794 | 14.6812 | 14.568 | 14.4476 | 14.0657 | 13.199 | 12.1571 | 11.1116 | 15.904 | 15.8882 | 15.8553 | 15.6984 | 15.5361 | 15.3749 | 15.2995 | 15.2239 | 15.1434 | 14.8883 | 14.3092 | 13.5381 | 12.4802
|  | KIDMORE END | LW |  |  | 16.9435 | 16.9435 | 16.9435 | 16.9435 | 16.9435 | 16.9435 | 16.9435 | 16.9435 | 16.9435 | 16.9435 | 16.5985 | 15.7631 | 14.9247 | 15.3222 | 15.3039 | 15.2664 | 15.2296 | 15.1929 | 15.169 | 15.1194 | 15.0062 | 14.8859 | 14.5038 | 13.6373 | 12.5951 | 11.5493 | 15.9123 | 15.9009 | 15.8776 | 15.8548 | 15.7429 | 15.6677 | 15.5923 | 15.5167 | 15.4363 | 15.181 | 14.6021 | 13.9058 | 12.9232
|  | KIDMORE END | ST |  |  | 16.9435 | 16.9435 | 16.9435 | 16.9435 | 16.9435 | 16.9435 | 16.9435 | 16.9435 | 16.9435 | 16.9435 | 16.9435 | 16.7998 | 16.2648 | 15.339 | 15.3312 | 15.3181 | 15.3022 | 15.2829 | 15.2638 | 15.2448 | 15.2284 | 15.211 | 15.1556 | 14.5734 | 13.8885 | 13.221 | 15.9227 | 15.9178 | 15.9097 | 15.8998 | 15.8879 | 15.876 | 15.8642 | 15.854 | 15.7999 | 15.6256 | 15.2275 | 14.7699 | 14.3239
|  | KIDMORE END | FS |  |  | 16.9435 | 16.9435 | 16.9435 | 16.9435 | 16.9435 | 16.9435 | 16.9435 | 16.9435 | 16.9435 | 16.9435 | 16.9435 | 16.9435 | 16.9435 | 15.3498 | 15.348 | 15.3462 | 15.3401 | 15.3329 | 15.326 | 15.3191 | 15.3104 | 15.3036 | 15.2821 | 15.2309 | 15.1665 | 14.9048 | 15.9294 | 15.9283 | 15.9272 | 15.9234 | 15.9189 | 15.9146 | 15.9104 | 15.905 | 15.9007 | 15.8873 | 15.8556 | 15.6601 | 15.4489
BRAMLEY (FLEE) | CAMBERLEY MAIN | KINGS RIDE | MINIMUM HEADROOM | SU 87551 61530 | YES | 28.3928 | 28.3928 | 28.3928 | 28.2585 | 28.1218 | 27.9827 | 27.8372 | 27.6124 | 27.5838 | 27.4914 | 27.0158 | 26.5121 | 25.8578 | 27.3554 | 27.3554 | 27.3554 | 27.2212 | 27.0845 | 26.9454 | 26.7999 | 26.3837 | 26.1728 | 25.5075 | 24.2494 | 23.0034 | 22.117 | 27.5757 | 27.5757 | 27.5757 | 27.4415 | 27.3048 | 27.1657 | 27.0202 | 26.7954 | 26.7668 | 26.6744 | 26.2416 | 25.6279 | 24.7902
|  | KINGS RIDE | CT |  |  | 28.3928 | 28.3928 | 28.3928 | 28.2585 | 28.1218 | 27.9827 | 27.8372 | 27.6124 | 27.5838 | 27.4914 | 27.0158 | 26.5121 | 25.8578 | 27.3554 | 27.3554 | 27.3554 | 27.2212 | 27.0845 | 26.9454 | 26.7999 | 26.3837 | 26.1728 | 25.5075 | 24.2494 | 23.0034 | 22.117 | 27.5757 | 27.5757 | 27.5757 | 27.4415 | 27.3048 | 27.1657 | 27.0202 | 26.7954 | 26.7668 | 26.6744 | 26.2416 | 25.6279 | 24.7902
|  | KINGS RIDE | LW |  |  | 28.3928 | 28.3928 | 28.3928 | 28.3922 | 28.3909 | 28.3888 | 28.386 | 28.3803 | 28.3794 | 28.3744 | 28.3272 | 28.247 | 27.7808 | 27.3554 | 27.3554 | 27.3554 | 27.3548 | 27.3535 | 27.3515 | 27.3486 | 27.2611 | 27.0777 | 26.4998 | 25.6625 | 24.84 | 24.0556 | 27.5757 | 27.5757 | 27.5757 | 27.5751 | 27.5738 | 27.5718 | 27.569 | 27.5633 | 27.5623 | 27.5573 | 27.5452 | 27.4577 | 26.722
|  | KINGS RIDE | ST |  |  | 28.3928 | 28.3928 | 28.3928 | 28.3927 | 28.3924 | 28.392 | 28.3914 | 28.3901 | 28.3895 | 28.386 | 28.3816 | 28.3659 | 28.3441 | 27.3554 | 27.3554 | 27.3554 | 27.3553 | 27.355 | 27.3546 | 27.354 | 27.3527 | 27.3521 | 27.3487 | 26.9733 | 26.4387 | 25.928 | 27.5757 | 27.5757 | 27.5757 | 27.5756 | 27.5753 | 27.5749 | 27.5744 | 27.573 | 27.5724 | 27.569 | 27.5645 | 27.5489 | 27.5432
|  | KINGS RIDE | FS |  |  | 28.3928 | 28.3928 | 28.3928 | 28.3928 | 28.3928 | 28.3928 | 28.3927 | 28.3927 | 28.3925 | 28.3912 | 28.3903 | 28.3856 | 28.381 | 27.3554 | 27.3554 | 27.3554 | 27.3554 | 27.3554 | 27.3554 | 27.3554 | 27.3553 | 27.3551 | 27.3539 | 27.3529 | 27.3482 | 27.3437 | 27.5757 | 27.5757 | 27.5757 | 27.5757 | 27.5757 | 27.5757 | 27.5757 | 27.5756 | 27.5754 | 27.5742 | 27.5732 | 27.5685 | 27.564
BRAMLEY (ANDO-THAT) | THATCHAM BSP | KINGSCLERE | MINIMUM HEADROOM | SU 51982 59358 | YES | 15.3353 | 15.2785 | 15.158 | 15.0408 | 14.9242 | 14.808 | 14.7463 | 14.6821 | 14.6178 | 14.4257 | 14.075 | 13.7067 | 13.3842 | 14.0723 | 14.0723 | 14.0723 | 14.0703 | 13.9407 | 13.8062 | 13.735 | 13.6613 | 13.5868 | 13.3647 | 12.9647 | 12.549 | 12.1732 | 14.6525 | 14.6525 | 14.6525 | 14.6505 | 14.6463 | 14.6397 | 14.5818 | 14.513 | 14.4436 | 14.2306 | 13.8396 | 13.433 | 13.0664
|  | KINGSCLERE | CT |  |  | 15.3353 | 15.2785 | 15.158 | 15.0408 | 14.9242 | 14.808 | 14.7463 | 14.6821 | 14.6178 | 14.4257 | 14.075 | 13.71 | 13.3842 | 14.0723 | 14.0723 | 14.0723 | 14.0717 | 13.9407 | 13.8062 | 13.735 | 13.6613 | 13.5868 | 13.3647 | 12.9647 | 12.549 | 12.1732 | 14.6525 | 14.6525 | 14.6525 | 14.6519 | 14.6507 | 14.6482 | 14.5818 | 14.513 | 14.4436 | 14.2306 | 13.8396 | 13.433 | 13.0664
|  | KINGSCLERE | LW |  |  | 15.3369 | 15.2809 | 15.1623 | 15.0453 | 14.9272 | 14.8608 | 14.7926 | 14.7154 | 14.6489 | 14.4458 | 14.0998 | 13.7067 | 13.3905 | 14.0723 | 14.0723 | 14.0723 | 14.0703 | 13.945 | 13.869 | 13.7912 | 13.7046 | 13.628 | 13.3948 | 12.9995 | 12.5556 | 12.1895 | 14.6525 | 14.6525 | 14.6525 | 14.6505 | 14.6463 | 14.6397 | 14.6305 | 14.5512 | 14.4797 | 14.259 | 13.8725 | 13.4379 | 13.0808
|  | KINGSCLERE | ST |  |  | 15.3587 | 15.32 | 15.2535 | 15.1716 | 15.0725 | 15.024 | 14.9753 | 14.931 | 14.8857 | 14.7488 | 14.5305 | 14.2761 | 14.0553 | 14.0723 | 14.0723 | 14.0723 | 14.0719 | 14.071 | 14.0566 | 14.0005 | 13.9497 | 13.8975 | 13.7404 | 13.4894 | 13.2022 | 12.9489 | 14.6525 | 14.6525 | 14.6525 | 14.6521 | 14.6512 | 14.6499 | 14.648 | 14.6437 | 14.6417 | 14.5857 | 14.3513 | 14.0705 | 13.8231
|  | KINGSCLERE | FS |  |  | 15.4246 | 15.4204 | 15.4163 | 15.3972 | 15.3742 | 15.358 | 15.3418 | 15.3208 | 15.3035 | 15.2509 | 15.1708 | 15.0822 | 14.9981 | 14.0723 | 14.0723 | 14.0723 | 14.0723 | 14.0722 | 14.0722 | 14.0721 | 14.0719 | 14.0712 | 14.0672 | 14.0641 | 14.0489 | 14.0324 | 14.6525 | 14.6525 | 14.6525 | 14.6525 | 14.6525 | 14.6524 | 14.6523 | 14.6522 | 14.6515 | 14.6475 | 14.6443 | 14.6291 | 14.6143
BRAMLEY (ANDO-THAT) | THATCHAM BSP | KINTBURY | MINIMUM HEADROOM | SU 37657 67143 | YES | 15.2461 | 15.2461 | 15.2461 | 15.2296 | 15.2128 | 15.1956 | 15.1779 | 15.1505 | 15.1412 | 15.008 | 14.7637 | 14.5053 | 14.2786 | 13.4994 | 13.4983 | 13.4959 | 13.4838 | 13.4667 | 13.4481 | 13.429 | 13.4001 | 13.3893 | 13.355 | 13.2823 | 13.0135 | 12.7468 | 14.1675 | 14.166 | 14.163 | 14.1509 | 14.135 | 14.116 | 14.0964 | 14.0671 | 14.0558 | 13.9565 | 13.6803 | 13.3888 | 13.1287
|  | KINTBURY | CT |  |  | 15.2461 | 15.2461 | 15.2461 | 15.237 | 15.2278 | 15.2183 | 15.2085 | 15.1889 | 15.1432 | 15.008 | 14.7637 | 14.5053 | 14.2786 | 13.4994 | 13.4983 | 13.4959 | 13.4846 | 13.4731 | 13.4614 | 13.4495 | 13.4322 | 13.428 | 13.4151 | 13.2823 | 13.0135 | 12.7468 | 14.1675 | 14.166 | 14.163 | 14.1509 | 14.1387 | 14.1264 | 14.1138 | 14.0959 | 14.091 | 13.9565 | 13.6803 | 13.3888 | 13.1287
|  | KINTBURY | LW |  |  | 15.2461 | 15.2461 | 15.2461 | 15.2461 | 15.2461 | 15.2461 | 15.2461 | 15.2461 | 15.2461 | 15.1196 | 14.9057 | 14.6838 | 14.4654 | 13.4999 | 13.4991 | 13.4973 | 13.4957 | 13.494 | 13.4919 | 13.4897 | 13.4876 | 13.4853 | 13.4786 | 13.4183 | 13.2013 | 12.9428 | 14.1681 | 14.1671 | 14.1648 | 14.1627 | 14.1605 | 14.1577 | 14.1549 | 14.1521 | 14.1491 | 14.0757 | 13.8298 | 13.5749 | 13.3238
|  | KINTBURY | ST |  |  | 15.2461 | 15.2461 | 15.2461 | 15.2296 | 15.2128 | 15.1956 | 15.1779 | 15.1505 | 15.1412 | 15.1116 | 15.0292 | 14.8091 | 14.6422 | 13.5095 | 13.5009 | 13.5007 | 13.4838 | 13.4667 | 13.4481 | 13.429 | 13.4001 | 13.3893 | 13.355 | 13.3237 | 13.2392 | 13.1552 | 14.1808 | 14.1695 | 14.1692 | 14.1523 | 14.135 | 14.116 | 14.0964 | 14.0671 | 14.0558 | 14.0201 | 13.9865 | 13.754 | 13.5659
|  | KINTBURY | FS |  |  | 15.2461 | 15.2461 | 15.2461 | 15.2461 | 15.2461 | 15.2461 | 15.2461 | 15.2461 | 15.2461 | 15.2461 | 15.2461 | 15.2461 | 15.2461 | 13.5096 | 13.5011 | 13.501 | 13.5008 | 13.5004 | 13.4999 | 13.4994 | 13.4988 | 13.4982 | 13.4965 | 13.4936 | 13.4909 | 13.4883 | 14.1809 | 14.1697 | 14.1696 | 14.1693 | 14.1689 | 14.1682 | 14.1676 | 14.1668 | 14.166 | 14.1637 | 14.16 | 14.1564 | 14.153
BRAMLEY (FLEE) | MAIDENHEAD BSP | KNOWL HILL | MINIMUM HEADROOM | SU 82849 79105 | YES | 9.0486 | 9.0354 | 9.0076 | 8.7908 | 8.5707 | 8.3474 | 8.1146 | 7.7695 | 7.7 | 7.4833 | 6.725 | 5.9251 | 5.6089 | 8.5475 | 8.5467 | 8.5451 | 8.3538 | 8.1589 | 7.9607 | 7.7533 | 7.4335 | 7.3914 | 7.2554 | 6.6322 | 5.8226 | 5.4763 | 8.1802 | 8.1747 | 8.1633 | 7.9624 | 7.758 | 7.5504 | 7.3334 | 7.0041 | 6.9517 | 6.7854 | 6.1113 | 5.3991 | 5.1694
|  | KNOWL HILL | CT |  |  | 9.0486 | 9.0354 | 9.0076 | 8.7908 | 8.5707 | 8.3474 | 8.1146 | 7.7695 | 7.7 | 7.4833 | 6.725 | 5.9251 | 5.6089 | 8.5475 | 8.5467 | 8.5451 | 8.3538 | 8.1589 | 7.9607 | 7.7533 | 7.4335 | 7.3914 | 7.2554 | 6.6322 | 5.8226 | 5.4763 | 8.1802 | 8.1747 | 8.1633 | 7.9624 | 7.758 | 7.5504 | 7.3334 | 7.0041 | 6.9517 | 6.7854 | 6.1113 | 5.3991 | 5.1694
|  | KNOWL HILL | LW |  |  | 9.0627 | 9.0574 | 9.046 | 9.0339 | 9.0208 | 8.9901 | 8.9584 | 8.9222 | 8.8916 | 8.7976 | 8.6342 | 8.4457 | 8.2959 | 8.5483 | 8.548 | 8.5473 | 8.5456 | 8.5429 | 8.5379 | 8.5317 | 8.5208 | 8.5175 | 8.5043 | 8.476 | 8.3574 | 8.1775 | 8.186 | 8.1838 | 8.1791 | 8.1735 | 8.1669 | 8.1522 | 8.1364 | 8.116 | 8.1024 | 8.0588 | 7.9797 | 7.879 | 7.8157
|  | KNOWL HILL | ST |  |  | 9.0669 | 9.0642 | 9.0596 | 8.9895 | 8.917 | 8.8306 | 8.7418 | 8.6148 | 8.5579 | 8.3791 | 8.1799 | 7.7252 | 7.524 | 8.5485 | 8.5484 | 8.5481 | 8.4833 | 8.4172 | 8.3487 | 8.2778 | 8.1681 | 8.1297 | 8.0054 | 7.8962 | 7.5323 | 7.4212 | 8.1877 | 8.1866 | 8.1847 | 8.1179 | 8.0494 | 7.9742 | 7.8966 | 7.7803 | 7.735 | 7.5902 | 7.4471 | 7.0491 | 6.904
|  | KNOWL HILL | FS |  |  | 9.0712 | 9.0708 | 9.0705 | 9.0689 | 9.067 | 9.0603 | 9.0535 | 9.0445 | 9.0365 | 9.0123 | 8.9745 | 8.9316 | 8.8905 | 8.5488 | 8.5487 | 8.5487 | 8.5486 | 8.5485 | 8.5481 | 8.5477 | 8.5471 | 8.5463 | 8.543 | 8.5393 | 8.5295 | 8.52 | 8.1895 | 8.1894 | 8.1892 | 8.1886 | 8.1878 | 8.185 | 8.1822 | 8.1784 | 8.1749 | 8.1637 | 8.1472 | 8.125 | 8.1036
BRAMLEY (FLEE) | ALDERSHOT BSP | LABURNUM ROAD | MINIMUM HEADROOM | SU 86017 50475 | YES | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3
|  | LABURNUM ROAD | CT |  |  | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3
|  | LABURNUM ROAD | LW |  |  | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3
|  | LABURNUM ROAD | ST |  |  | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3
|  | LABURNUM ROAD | FS |  |  | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3
BRAMLEY (ANDO-THAT) | THATCHAM BSP | LAMBOURN | MINIMUM HEADROOM | SU 33280 78217 | YES | 15.0556 | 15.0556 | 15.0556 | 15.0324 | 15.0088 | 14.9848 | 14.9599 | 14.9214 | 14.9084 | 14.8667 | 14.8333 | 14.717 | 14.5171 | 13.6326 | 13.6318 | 13.6299 | 13.6088 | 13.5844 | 13.5578 | 13.5305 | 13.4894 | 13.4736 | 13.4239 | 13.079 | 12.5971 | 12.162 | 14.2275 | 14.2265 | 14.2242 | 14.2036 | 14.1791 | 14.152 | 14.1241 | 14.0826 | 14.0663 | 14.0151 | 13.9661 | 13.8342 | 13.5128
|  | LAMBOURN | CT |  |  | 15.0556 | 15.0556 | 15.0556 | 15.0397 | 15.0235 | 15.007 | 14.9898 | 14.9633 | 14.96 | 14.9492 | 14.8993 | 14.848 | 14.5171 | 13.6327 | 13.6319 | 13.6301 | 13.6124 | 13.5945 | 13.5763 | 13.5553 | 13.5251 | 13.5177 | 13.4949 | 13.079 | 12.5971 | 12.162 | 14.2276 | 14.2266 | 14.2245 | 14.2065 | 14.1883 | 14.1698 | 14.1481 | 14.1171 | 14.109 | 14.084 | 14.0107 | 13.8831 | 13.5128
|  | LAMBOURN | LW |  |  | 15.0556 | 15.0556 | 15.0556 | 15.0556 | 15.0556 | 15.0556 | 15.0556 | 15.0556 | 15.0556 | 15.0556 | 15.0556 | 15.0291 | 14.6944 | 13.6326 | 13.6318 | 13.6299 | 13.628 | 13.6262 | 13.6224 | 13.6186 | 13.6149 | 13.6108 | 13.5984 | 13.1824 | 12.7518 | 12.3281 | 14.2275 | 14.2265 | 14.2242 | 14.2221 | 14.2199 | 14.2154 | 14.2109 | 14.2065 | 14.2017 | 14.1875 | 14.1641 | 14.046 | 13.6871
|  | LAMBOURN | ST |  |  | 15.0556 | 15.0556 | 15.0556 | 15.0324 | 15.0088 | 14.9848 | 14.9599 | 14.9214 | 14.9084 | 14.8667 | 14.8333 | 14.717 | 14.6822 | 13.6336 | 13.6333 | 13.6327 | 13.6088 | 13.5844 | 13.5578 | 13.5305 | 13.4894 | 13.4736 | 13.4239 | 13.3773 | 12.9995 | 12.6891 | 14.2286 | 14.2283 | 14.2276 | 14.2036 | 14.1791 | 14.152 | 14.1241 | 14.0826 | 14.0663 | 14.0151 | 13.9661 | 13.8342 | 13.7839
|  | LAMBOURN | FS |  |  | 15.0556 | 15.0556 | 15.0556 | 15.0545 | 15.0534 | 15.0523 | 15.0511 | 15.0494 | 15.0445 | 15.0289 | 15.0214 | 14.9981 | 14.9785 | 13.6341 | 13.6341 | 13.634 | 13.6327 | 13.6314 | 13.6294 | 13.6275 | 13.6246 | 13.6186 | 13.5999 | 13.5875 | 13.5594 | 13.5353 | 14.2292 | 14.2292 | 14.2291 | 14.2278 | 14.2264 | 14.2243 | 14.2222 | 14.2192 | 14.213 | 14.1937 | 14.1804 | 14.1513 | 14.1264
FAWLEY GSP | LANGLEY BSP | LANGLEY | MINIMUM HEADROOM | SU 45158 01418 | YES | 16.5297 | 16.5149 | 16.4837 | 16.4337 | 16.3579 | 16.1892 | 16.0117 | 15.8082 | 15.5727 | 14.7385 | 13.6833 | 13.039 | 12.4135 | 14.6729 | 14.6556 | 14.6191 | 14.5607 | 14.472 | 14.2747 | 14.0672 | 13.8291 | 13.5537 | 12.5782 | 11.3443 | 10.5908 | 9.8593 | 17.0089 | 16.993 | 16.9593 | 16.9054 | 16.8235 | 16.6414 | 16.4499 | 16.2302 | 15.9761 | 15.0759 | 13.8619 | 13.1155 | 12.391
|  | LANGLEY | CT |  |  | 16.5297 | 16.5149 | 16.4837 | 16.4337 | 16.3579 | 16.2789 | 16.1015 | 15.898 | 15.6624 | 14.8283 | 13.773 | 13.1288 | 12.5036 | 14.6729 | 14.6556 | 14.6191 | 14.5607 | 14.472 | 14.3796 | 14.1722 | 13.9342 | 13.6586 | 12.6833 | 11.4492 | 10.6958 | 9.9648 | 17.0089 | 16.993 | 16.9593 | 16.9054 | 16.8235 | 16.7383 | 16.5468 | 16.3272 | 16.0729 | 15.1728 | 13.9658 | 13.2195 | 12.4954
|  | LANGLEY | LW |  |  | 16.5297 | 16.5149 | 16.4837 | 16.4337 | 16.3579 | 16.1892 | 16.0117 | 15.8082 | 15.5727 | 14.7385 | 13.6833 | 13.039 | 12.4135 | 14.6729 | 14.6556 | 14.6191 | 14.5607 | 14.472 | 14.2747 | 14.0672 | 13.8291 | 13.5537 | 12.5782 | 11.3443 | 10.5908 | 9.8593 | 17.0089 | 16.993 | 16.9593 | 16.9054 | 16.8235 | 16.6414 | 16.4499 | 16.2302 | 15.9761 | 15.0759 | 13.8619 | 13.1155 | 12.391
|  | LANGLEY | ST |  |  | 16.5393 | 16.5311 | 16.517 | 16.4866 | 16.4352 | 16.3436 | 16.2462 | 16.1084 | 15.9472 | 15.3624 | 14.6276 | 14.2123 | 13.8055 | 14.6842 | 14.6746 | 14.658 | 14.6225 | 14.5624 | 14.4553 | 14.3414 | 14.1803 | 13.9917 | 13.3079 | 12.4486 | 11.963 | 11.4871 | 17.0193 | 17.0104 | 16.9952 | 16.9624 | 16.9069 | 16.808 | 16.7029 | 16.5543 | 16.3802 | 15.7492 | 14.9557 | 14.4747 | 14.0034
|  | LANGLEY | FS |  |  | 16.5527 | 16.5516 | 16.5506 | 16.5389 | 16.5185 | 16.4881 | 16.4561 | 16.4129 | 16.3496 | 16.1192 | 15.8298 | 15.6788 | 15.539 | 14.6998 | 14.6986 | 14.6973 | 14.6837 | 14.6598 | 14.6243 | 14.5868 | 14.5364 | 14.4623 | 14.1929 | 13.8544 | 13.6779 | 13.5144 | 17.0337 | 17.0326 | 17.0314 | 17.0188 | 16.9968 | 16.964 | 16.9295 | 16.8829 | 16.8145 | 16.5659 | 16.2536 | 16.0906 | 15.9398
BRAMLEY (FLEE) | FERNHURST | LANGLEY COURT | MINIMUM HEADROOM | SU 80847 29056 | YES | 34.3586 | 34.3586 | 34.3586 | 34.2721 | 34.1842 | 34.0948 | 34.0014 | 33.8574 | 33.8392 | 33.7806 | 33.5101 | 33.2313 | 32.9628 | 32.4712 | 32.4653 | 32.4545 | 32.3584 | 32.2608 | 32.1617 | 32.0601 | 31.9079 | 31.8809 | 31.7966 | 31.1166 | 30.2885 | 29.6853 | 33.7946 | 33.7904 | 33.7827 | 33.6894 | 33.5946 | 33.4984 | 33.3991 | 33.2493 | 33.2249 | 33.148 | 32.4541 | 31.6661 | 31.1022
|  | LANGLEY COURT | CT |  |  | 34.3586 | 34.3586 | 34.3586 | 34.2721 | 34.1842 | 34.0948 | 34.0014 | 33.8574 | 33.8392 | 33.7806 | 33.5101 | 33.2313 | 32.9628 | 32.4712 | 32.4653 | 32.4545 | 32.3584 | 32.2608 | 32.1617 | 32.0601 | 31.9079 | 31.8809 | 31.7966 | 31.1166 | 30.2885 | 29.6853 | 33.7946 | 33.7904 | 33.7827 | 33.6894 | 33.5946 | 33.4984 | 33.3991 | 33.2493 | 33.2249 | 33.148 | 32.4541 | 31.6661 | 31.1022
|  | LANGLEY COURT | LW |  |  | 34.3586 | 34.3586 | 34.3586 | 34.3586 | 34.3586 | 34.3586 | 34.3586 | 34.3586 | 34.3586 | 34.3586 | 34.3586 | 34.3586 | 34.1706 | 32.4713 | 32.4654 | 32.4546 | 32.4451 | 32.4355 | 32.4272 | 32.4188 | 32.4106 | 32.4019 | 32.3761 | 31.985 | 31.4354 | 30.896 | 33.7947 | 33.7905 | 33.7828 | 33.776 | 33.7692 | 33.7633 | 33.7574 | 33.7516 | 33.7454 | 33.7271 | 33.321 | 32.8115 | 32.3115
|  | LANGLEY COURT | ST |  |  | 34.3586 | 34.3586 | 34.3586 | 34.3586 | 34.3586 | 34.3586 | 34.3586 | 34.3586 | 34.3586 | 34.3586 | 34.3586 | 34.3586 | 34.3586 | 32.477 | 32.4747 | 32.4715 | 32.4684 | 32.4646 | 32.4586 | 32.4525 | 32.4469 | 32.4409 | 32.4236 | 32.395 | 32.3669 | 32.0561 | 33.7987 | 33.7971 | 33.7948 | 33.7926 | 33.7899 | 33.7856 | 33.7813 | 33.7773 | 33.7731 | 33.7608 | 33.7405 | 33.7119 | 33.387
|  | LANGLEY COURT | FS |  |  | 34.3586 | 34.3586 | 34.3586 | 34.3586 | 34.3586 | 34.3586 | 34.3586 | 34.3586 | 34.3586 | 34.3586 | 34.3586 | 34.3586 | 34.3586 | 32.4793 | 32.4784 | 32.4777 | 32.4763 | 32.4746 | 32.4725 | 32.4704 | 32.4678 | 32.4654 | 32.4587 | 32.4479 | 32.4376 | 32.4278 | 33.8003 | 33.7997 | 33.7992 | 33.7982 | 33.797 | 33.7955 | 33.794 | 33.7921 | 33.7905 | 33.7857 | 33.778 | 33.7707 | 33.7638
AXMINSTER | YEOVIL BSP | LARKHILL | MINIMUM HEADROOM | ST 53677 16914 | YES | 26.5184 | 26.5169 | 26.514 | 26.5111 | 26.508 | 26.4973 | 26.4865 | 26.4757 | 26.4643 | 26.4283 | 26.3508 | 26.2594 | 25.521 | 22.609 | 22.5869 | 22.5454 | 22.5035 | 22.4598 | 22.3054 | 22.1508 | 21.9962 | 21.8314 | 21.3155 | 20.2032 | 18.8914 | 17.5782 | 25.6733 | 25.6721 | 25.6698 | 25.6674 | 25.6649 | 25.6562 | 25.6475 | 25.6388 | 25.6296 | 25.3319 | 24.3822 | 23.1876 | 21.8784
|  | LARKHILL | CT |  |  | 26.5187 | 26.5173 | 26.5147 | 26.5121 | 26.5093 | 26.5065 | 26.4958 | 26.485 | 26.4735 | 26.4376 | 26.36 | 26.2687 | 25.634 | 22.6128 | 22.5926 | 22.5556 | 22.5178 | 22.4783 | 22.4384 | 22.2837 | 22.1291 | 21.9642 | 21.4484 | 20.3359 | 19.0244 | 17.7114 | 25.6736 | 25.6724 | 25.6703 | 25.6682 | 25.666 | 25.6637 | 25.655 | 25.6463 | 25.637 | 25.4454 | 24.4955 | 23.3202 | 22.0112
|  | LARKHILL | LW |  |  | 26.5184 | 26.5169 | 26.514 | 26.5111 | 26.508 | 26.4973 | 26.4865 | 26.4757 | 26.4643 | 26.4283 | 26.3508 | 26.2594 | 25.521 | 22.609 | 22.5869 | 22.5454 | 22.5035 | 22.4598 | 22.3054 | 22.1508 | 21.9962 | 21.8314 | 21.3155 | 20.2032 | 18.8914 | 17.5782 | 25.6733 | 25.6721 | 25.6698 | 25.6674 | 25.6649 | 25.6562 | 25.6475 | 25.6388 | 25.6296 | 25.3319 | 24.3822 | 23.1876 | 21.8784
|  | LARKHILL | ST |  |  | 26.5329 | 26.5178 | 26.5161 | 26.514 | 26.5115 | 26.5064 | 26.5013 | 26.494 | 26.4861 | 26.4616 | 26.4085 | 26.3486 | 26.2901 | 22.8172 | 22.6004 | 22.5758 | 22.5457 | 22.5093 | 22.4365 | 22.3634 | 22.2579 | 22.1453 | 21.7937 | 21.0317 | 20.172 | 19.3322 | 25.6851 | 25.6729 | 25.6715 | 25.6698 | 25.6677 | 25.6636 | 25.6595 | 25.6536 | 25.6472 | 25.6274 | 25.0896 | 24.3555 | 23.627
|  | LARKHILL | FS |  |  | 26.5449 | 26.5341 | 26.5338 | 26.5332 | 26.5325 | 26.5311 | 26.5297 | 26.528 | 26.5249 | 26.5154 | 26.494 | 26.4681 | 26.4413 | 22.989 | 22.8342 | 22.8301 | 22.8215 | 22.8116 | 22.7913 | 22.771 | 22.7456 | 22.7017 | 22.5651 | 22.2589 | 21.8863 | 21.5015 | 25.6947 | 25.686 | 25.6858 | 25.6853 | 25.6847 | 25.6836 | 25.6825 | 25.681 | 25.6786 | 25.6709 | 25.6536 | 25.6326 | 25.4908
COWLEY GSP | WITNEY BSP | LEAFIELD | MINIMUM HEADROOM | SP 30282 15270 | NO | 8.0072 | 8.0046 | 7.9991 | 7.9055 | 7.7981 | 7.6864 | 7.571 | 7.3941 | 7.332 | 7.1303 | 6.833 | 6.2538 | 5.9848 | 6.2693 | 6.2347 | 6.1613 | 6.0898 | 6.0179 | 5.9472 | 5.8034 | 5.593 | 5.4949 | 5.1927 | 4.8567 | 4.2391 | 3.932 | 6.6353 | 6.6008 | 6.5277 | 6.4563 | 6.3846 | 6.3142 | 6.1695 | 5.9592 | 5.8613 | 5.5594 | 5.2239 | 4.6069 | 4.3003
|  | LEAFIELD | CT |  |  | 8.0072 | 8.0046 | 7.9991 | 7.9937 | 7.9619 | 7.9061 | 7.8637 | 7.822 | 7.777 | 7.6442 | 7.4253 | 7.2017 | 6.9816 | 6.2693 | 6.2347 | 6.1613 | 6.0898 | 6.0179 | 5.9472 | 5.8935 | 5.8407 | 5.7837 | 5.6156 | 5.3385 | 5.0553 | 4.7767 | 6.6353 | 6.6008 | 6.5277 | 6.4563 | 6.3846 | 6.3142 | 6.2607 | 6.208 | 6.1512 | 5.9836 | 5.7073 | 5.425 | 5.1472
|  | LEAFIELD | LW |  |  | 8.0079 | 8.0057 | 8.001 | 7.9965 | 7.9919 | 7.9561 | 7.9136 | 7.8719 | 7.8269 | 7.694 | 7.4752 | 7.2515 | 7.0315 | 6.2789 | 6.2494 | 6.1871 | 6.1262 | 6.0648 | 6.0105 | 5.9567 | 5.9038 | 5.8469 | 5.6786 | 5.4016 | 5.1183 | 4.8398 | 6.6449 | 6.6155 | 6.5533 | 6.4926 | 6.4314 | 6.3773 | 6.3237 | 6.271 | 6.2142 | 6.0465 | 5.7703 | 5.4879 | 5.2101
|  | LEAFIELD | ST |  |  | 8.059 | 8.0114 | 8.0111 | 7.9055 | 7.7981 | 7.6864 | 7.571 | 7.3941 | 7.332 | 7.1303 | 6.833 | 6.2538 | 5.9848 | 6.7523 | 6.3266 | 6.3222 | 6.2114 | 6.0971 | 5.9518 | 5.8034 | 5.593 | 5.4949 | 5.1927 | 4.8567 | 4.2391 | 3.932 | 6.9977 | 6.6924 | 6.688 | 6.5772 | 6.463 | 6.3178 | 6.1695 | 5.9592 | 5.8613 | 5.5594 | 5.2239 | 4.6069 | 4.3003
|  | LEAFIELD | FS |  |  | 8.0593 | 8.0118 | 8.0117 | 8.0113 | 8.0108 | 8.0099 | 8.009 | 8.0078 | 8.0067 | 8.0034 | 7.9982 | 7.9932 | 7.964 | 6.7529 | 6.3308 | 6.3297 | 6.3243 | 6.3176 | 6.3055 | 6.2936 | 6.2784 | 6.2633 | 6.2194 | 6.1493 | 6.083 | 6.0205 | 6.9979 | 6.6966 | 6.6955 | 6.6901 | 6.6835 | 6.6714 | 6.6596 | 6.6444 | 6.6293 | 6.5856 | 6.5156 | 6.4496 | 6.3873
WILLESDEN GSP | ACTON LANE | LEAMINGTON PARK | MINIMUM HEADROOM | TQ 20539 81536 | YES | 42.1456 | 42.1409 | 97.632 | 97.6229 | 97.6136 | 97.6024 | 97.5709 | 97.5337 | 97.4948 | 97.36 | 96.9311 | 96.1053 | 95.2682 | 40.737 | 40.7206 | 92.5898 | 92.5587 | 92.5265 | 92.4878 | 92.4483 | 92.4011 | 92.3363 | 92.1117 | 91.4104 | 90.469 | 89.5149 | 41.334 | 41.3271 | 96.8142 | 96.8011 | 96.7876 | 96.7713 | 96.7547 | 96.7339 | 96.6857 | 96.5187 | 95.7929 | 94.7648 | 93.7226
|  | LEAMINGTON PARK | CT |  |  | 42.1465 | 42.1422 | 97.6343 | 97.6262 | 97.6178 | 97.6093 | 97.5929 | 97.5557 | 97.5168 | 97.382 | 96.9662 | 96.1402 | 95.3032 | 40.7399 | 40.7251 | 92.5977 | 92.5699 | 92.5409 | 92.5116 | 92.472 | 92.4318 | 92.3729 | 92.1483 | 91.4503 | 90.5089 | 89.5548 | 41.3352 | 41.329 | 96.8175 | 96.8058 | 96.7936 | 96.7813 | 96.7647 | 96.7478 | 96.7129 | 96.5459 | 95.8365 | 94.8083 | 93.7662
|  | LEAMINGTON PARK | LW |  |  | 42.1456 | 42.1409 | 97.632 | 97.6229 | 97.6136 | 97.6024 | 97.5709 | 97.5337 | 97.4948 | 97.36 | 96.9311 | 96.1053 | 95.2682 | 40.737 | 40.7206 | 92.5898 | 92.5587 | 92.5265 | 92.4878 | 92.4483 | 92.4011 | 92.3363 | 92.1117 | 91.4104 | 90.469 | 89.5149 | 41.334 | 41.3271 | 96.8142 | 96.8011 | 96.7876 | 96.7713 | 96.7547 | 96.7339 | 96.6857 | 96.5187 | 95.7929 | 94.7648 | 93.7226
|  | LEAMINGTON PARK | ST |  |  | 42.1476 | 42.1445 | 97.6395 | 97.6335 | 97.6263 | 97.6176 | 97.6088 | 97.6009 | 97.5762 | 97.4831 | 97.2044 | 96.768 | 96.2388 | 40.7439 | 40.733 | 92.616 | 92.5953 | 92.5702 | 92.5403 | 92.5099 | 92.4827 | 92.4539 | 92.3168 | 91.8487 | 91.2244 | 90.6213 | 41.3369 | 41.3323 | 96.8252 | 96.8165 | 96.8059 | 96.7934 | 96.7806 | 96.7692 | 96.7571 | 96.6712 | 96.2717 | 95.5898 | 94.931
|  | LEAMINGTON PARK | FS |  |  | 42.1517 | 42.1509 | 97.65 | 97.6482 | 97.6461 | 97.6429 | 97.6396 | 97.6356 | 97.6324 | 97.621 | 97.5505 | 97.3857 | 97.2078 | 40.758 | 40.7551 | 92.6522 | 92.6459 | 92.6386 | 92.6275 | 92.6163 | 92.6025 | 92.5914 | 92.5522 | 92.4262 | 92.1545 | 91.8549 | 41.3428 | 41.3416 | 96.8404 | 96.8377 | 96.8347 | 96.83 | 96.8253 | 96.8195 | 96.8148 | 96.7984 | 96.7455 | 96.5506 | 96.2784
MINETY GSP | STRATTON (2 X 60) | LECHLADE | MINIMUM HEADROOM | SP 22074 00496 | YES | 11.9696 | 11.9402 | 12.528 | 12.4614 | 12.3888 | 12.3257 | 12.2552 | 12.1567 | 12.1017 | 11.918 | 11.5742 | 11.1066 | 10.8625 | 10.2814 | 10.279 | 10.87 | 10.7837 | 10.6914 | 10.6144 | 10.53 | 10.4178 | 10.3445 | 10.1039 | 9.6655 | 9.0995 | 8.7585 | 11.2929 | 11.2608 | 11.8431 | 11.7652 | 11.6733 | 11.5966 | 11.5125 | 11.4005 | 11.331 | 11.1043 | 10.6891 | 10.1471 | 9.8299
|  | LECHLADE | CT |  |  | 11.9781 | 11.9533 | 12.5508 | 12.498 | 12.444 | 12.3888 | 12.3388 | 12.2797 | 12.2315 | 12.0812 | 11.7238 | 11.3419 | 11.0678 | 10.2821 | 10.2801 | 10.9002 | 10.8308 | 10.7603 | 10.6888 | 10.6249 | 10.5521 | 10.4889 | 10.2818 | 9.8297 | 9.3494 | 8.9785 | 11.3021 | 11.2751 | 11.8679 | 11.8106 | 11.7419 | 11.6707 | 11.6071 | 11.5346 | 11.4718 | 11.2787 | 10.8496 | 10.3934 | 10.0462
|  | LECHLADE | LW |  |  | 11.9696 | 11.9402 | 12.528 | 12.4614 | 12.3888 | 12.3257 | 12.2552 | 12.1567 | 12.1017 | 11.918 | 11.5742 | 11.1066 | 10.8625 | 10.2814 | 10.279 | 10.87 | 10.7837 | 10.6914 | 10.6144 | 10.53 | 10.4178 | 10.3445 | 10.1039 | 9.6655 | 9.0995 | 8.7585 | 11.2929 | 11.2608 | 11.8431 | 11.7652 | 11.6733 | 11.5966 | 11.5125 | 11.4005 | 11.331 | 11.1043 | 10.6891 | 10.1471 | 9.8299
|  | LECHLADE | ST |  |  | 11.9766 | 11.9541 | 12.5657 | 12.51 | 12.4433 | 12.406 | 12.367 | 12.3133 | 12.2721 | 12.135 | 11.9314 | 11.5891 | 11.3736 | 10.282 | 10.2802 | 10.9021 | 10.8489 | 10.7636 | 10.7178 | 10.6704 | 10.6074 | 10.5561 | 10.3883 | 10.1217 | 9.7161 | 9.4377 | 11.3005 | 11.276 | 11.8842 | 11.8243 | 11.7451 | 11.6995 | 11.6523 | 11.5894 | 11.5384 | 11.3722 | 11.121 | 10.7309 | 10.4679
|  | LECHLADE | FS |  |  | 12.0156 | 12.0133 | 12.6612 | 12.6488 | 12.6347 | 12.6233 | 12.6119 | 12.5965 | 12.5729 | 12.4954 | 12.4146 | 12.2676 | 12.1321 | 10.2851 | 10.2849 | 10.9097 | 10.9067 | 10.9035 | 10.9004 | 10.8972 | 10.8923 | 10.8796 | 10.8342 | 10.7495 | 10.5846 | 10.4321 | 11.343 | 11.3405 | 11.9881 | 11.9749 | 11.9596 | 11.9475 | 11.9353 | 11.9189 | 11.8942 | 11.8136 | 11.7278 | 11.5663 | 11.4141
BRAMLEY (ANDO-THAT) | THATCHAM BSP | LECKHAMPSTEAD | MINIMUM HEADROOM | SU 43962 77635 | YES | 10.9582 | 10.9453 | 10.9181 | 10.8052 | 10.6439 | 10.481 | 10.313 | 10.0589 | 9.967 | 9.662 | 9.3237 | 8.5451 | 8.2172 | 10.1337 | 10.1229 | 10.1002 | 9.9814 | 9.8218 | 9.6603 | 9.4938 | 9.241 | 9.1505 | 8.8634 | 8.5744 | 7.7628 | 7.4022 | 10.5104 | 10.4629 | 10.3625 | 10.2652 | 10.1568 | 9.9701 | 9.7787 | 9.5038 | 9.3895 | 9.033 | 8.6737 | 7.8741 | 7.5253
|  | LECKHAMPSTEAD | CT |  |  | 10.9582 | 10.9453 | 10.9181 | 10.8909 | 10.8085 | 10.7269 | 10.691 | 10.6552 | 10.6167 | 10.503 | 10.3164 | 10.1165 | 9.9145 | 10.1337 | 10.1229 | 10.1002 | 10.0782 | 10.0564 | 9.9721 | 9.9265 | 9.8812 | 9.8324 | 9.6886 | 9.4523 | 9.2087 | 8.9696 | 10.5104 | 10.4629 | 10.3625 | 10.2652 | 10.1688 | 10.0734 | 10.0313 | 9.9895 | 9.9444 | 9.8115 | 9.5931 | 9.3682 | 9.1472
|  | LECKHAMPSTEAD | LW |  |  | 10.9707 | 10.9646 | 10.9519 | 10.9395 | 10.9273 | 10.9157 | 10.9042 | 10.8929 | 10.8562 | 10.7426 | 10.556 | 10.3637 | 10.1705 | 10.1441 | 10.1391 | 10.1284 | 10.1181 | 10.1079 | 10.0982 | 10.0887 | 10.0792 | 10.069 | 9.9919 | 9.7557 | 9.5121 | 9.2727 | 10.5563 | 10.5341 | 10.487 | 10.4415 | 10.3963 | 10.3537 | 10.3115 | 10.2697 | 10.2247 | 10.0917 | 9.8735 | 9.6484 | 9.4272
|  | LECKHAMPSTEAD | ST |  |  | 10.9733 | 10.9692 | 10.9623 | 10.8052 | 10.6439 | 10.481 | 10.313 | 10.0589 | 9.967 | 9.662 | 9.3237 | 8.5451 | 8.2172 | 10.1463 | 10.1429 | 10.1371 | 9.9814 | 9.8218 | 9.6603 | 9.4938 | 9.241 | 9.1505 | 8.8634 | 8.5744 | 7.7628 | 7.4022 | 10.5659 | 10.551 | 10.5255 | 10.3456 | 10.1568 | 9.9701 | 9.7787 | 9.5038 | 9.3895 | 9.033 | 8.6737 | 7.8741 | 7.5253
|  | LECKHAMPSTEAD | FS |  |  | 10.9802 | 10.9798 | 10.9794 | 10.9689 | 10.9583 | 10.9467 | 10.9351 | 10.9177 | 10.8772 | 10.7496 | 10.6784 | 10.4869 | 10.3253 | 10.1521 | 10.1517 | 10.1514 | 10.1412 | 10.1309 | 10.1199 | 10.1088 | 10.092 | 10.0521 | 9.926 | 9.8573 | 9.6682 | 9.5087 | 10.5915 | 10.5899 | 10.5885 | 10.5729 | 10.5563 | 10.5363 | 10.5164 | 10.4883 | 10.4392 | 10.2864 | 10.1751 | 9.9456 | 9.7479
LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | LEE-ON-SOLENT | MINIMUM HEADROOM | SU 56858 00293 | YES | 35.1147 | 35.1147 | 35.1147 | 35.1147 | 35.1147 | 35.1147 | 35.1147 | 35.1147 | 35.1147 | 35.1147 | 34.5921 | 33.1789 | 31.7652 | 31.2835 | 31.2835 | 31.2835 | 31.2835 | 31.2835 | 31.2835 | 31.2835 | 31.2835 | 31.2835 | 31.2835 | 31.2835 | 29.8215 | 28.1537 | 34.1777 | 34.1777 | 34.1777 | 34.1777 | 34.1777 | 34.1777 | 34.1777 | 34.1777 | 34.1777 | 34.1777 | 32.9678 | 31.3427 | 29.7181
|  | LEE-ON-SOLENT | CT |  |  | 35.1147 | 35.1147 | 35.1147 | 35.1147 | 35.1147 | 35.1147 | 35.1147 | 35.1147 | 35.1147 | 35.1147 | 34.7157 | 33.3052 | 31.8921 | 31.2835 | 31.2835 | 31.2835 | 31.2835 | 31.2835 | 31.2835 | 31.2835 | 31.2835 | 31.2835 | 31.2835 | 31.2835 | 29.9705 | 28.3034 | 34.1777 | 34.1777 | 34.1777 | 34.1777 | 34.1777 | 34.1777 | 34.1777 | 34.1777 | 34.1777 | 34.1777 | 33.1129 | 31.4878 | 29.8639
|  | LEE-ON-SOLENT | LW |  |  | 35.1147 | 35.1147 | 35.1147 | 35.1147 | 35.1147 | 35.1147 | 35.1147 | 35.1147 | 35.1147 | 35.1147 | 34.5921 | 33.1789 | 31.7652 | 31.2835 | 31.2835 | 31.2835 | 31.2835 | 31.2835 | 31.2835 | 31.2835 | 31.2835 | 31.2835 | 31.2835 | 31.2835 | 29.8215 | 28.1537 | 34.1777 | 34.1777 | 34.1777 | 34.1777 | 34.1777 | 34.1777 | 34.1777 | 34.1777 | 34.1777 | 34.1777 | 32.9678 | 31.3427 | 29.7181
|  | LEE-ON-SOLENT | ST |  |  | 35.1147 | 35.1147 | 35.1147 | 35.1147 | 35.1147 | 35.1147 | 35.1147 | 35.1147 | 35.1147 | 35.1147 | 35.1147 | 34.8199 | 33.9224 | 31.2835 | 31.2835 | 31.2835 | 31.2835 | 31.2835 | 31.2835 | 31.2835 | 31.2835 | 31.2835 | 31.2835 | 31.2835 | 31.2835 | 30.6986 | 34.1777 | 34.1777 | 34.1777 | 34.1777 | 34.1777 | 34.1777 | 34.1777 | 34.1777 | 34.1777 | 34.1777 | 34.1777 | 33.2352 | 32.197
|  | LEE-ON-SOLENT | FS |  |  | 35.1147 | 35.1147 | 35.1147 | 35.1147 | 35.1147 | 35.1147 | 35.1147 | 35.1147 | 35.1147 | 35.1147 | 35.1147 | 35.1147 | 35.1147 | 31.2835 | 31.2835 | 31.2835 | 31.2835 | 31.2835 | 31.2835 | 31.2835 | 31.2835 | 31.2835 | 31.2835 | 31.2835 | 31.2835 | 31.2835 | 34.1777 | 34.1777 | 34.1777 | 34.1777 | 34.1777 | 34.1777 | 34.1777 | 34.1777 | 34.1777 | 34.1777 | 34.1777 | 34.1777 | 34.1777
LOVEDEAN GSP | HAVANT | LEIGH PARK | MINIMUM HEADROOM | SU 72144 07875 | YES | 35.5385 | 35.5348 | 35.5293 | 35.5014 | 35.4727 | 35.4367 | 35.3995 | 35.3482 | 35.3319 | 35.2791 | 35.1716 | 35.0093 | 34.4562 | 34.864 | 34.864 | 34.864 | 34.8397 | 34.8146 | 34.7839 | 34.7278 | 34.6574 | 34.6212 | 34.5059 | 34.2373 | 33.0683 | 31.844 | 34.8309 | 34.8309 | 34.8309 | 34.8066 | 34.7815 | 34.7553 | 34.7282 | 34.6869 | 34.6812 | 34.6616 | 34.5753 | 34.2401 | 33.0514
|  | LEIGH PARK | CT |  |  | 35.5387 | 35.5351 | 35.5298 | 35.5265 | 35.523 | 35.5195 | 35.5094 | 35.4993 | 35.4888 | 35.4556 | 35.3813 | 35.2929 | 34.8196 | 34.864 | 34.864 | 34.864 | 34.864 | 34.864 | 34.864 | 34.8511 | 34.822 | 34.7915 | 34.6958 | 34.4814 | 33.4426 | 32.2226 | 34.8309 | 34.8309 | 34.8309 | 34.8309 | 34.8309 | 34.8309 | 34.8309 | 34.8309 | 34.8309 | 34.8309 | 34.7838 | 34.6114 | 33.4271
|  | LEIGH PARK | LW |  |  | 35.5385 | 35.5348 | 35.5293 | 35.5014 | 35.4727 | 35.4367 | 35.3995 | 35.3482 | 35.3319 | 35.2791 | 35.1716 | 35.0093 | 34.4562 | 34.864 | 34.864 | 34.864 | 34.8397 | 34.8146 | 34.7839 | 34.7278 | 34.6574 | 34.6212 | 34.5059 | 34.2373 | 33.0683 | 31.844 | 34.8309 | 34.8309 | 34.8309 | 34.8066 | 34.7815 | 34.7553 | 34.7282 | 34.6869 | 34.6812 | 34.6616 | 34.5753 | 34.2401 | 33.0514
|  | LEIGH PARK | ST |  |  | 35.5403 | 35.5382 | 35.5357 | 35.5218 | 35.5074 | 35.4911 | 35.474 | 35.4464 | 35.4322 | 35.3871 | 35.318 | 35.2082 | 35.1368 | 34.864 | 34.864 | 34.864 | 34.8515 | 34.8388 | 34.8258 | 34.8124 | 34.7917 | 34.7777 | 34.6899 | 34.5245 | 34.3054 | 33.6753 | 34.8309 | 34.8309 | 34.8309 | 34.8184 | 34.8058 | 34.7928 | 34.7794 | 34.7587 | 34.7517 | 34.7292 | 34.7109 | 34.6111 | 34.5493
|  | LEIGH PARK | FS |  |  | 35.5409 | 35.5398 | 35.5386 | 35.5348 | 35.531 | 35.5267 | 35.5224 | 35.516 | 35.4997 | 35.4482 | 35.4072 | 35.3176 | 35.2375 | 34.864 | 34.864 | 34.864 | 34.8609 | 34.8579 | 34.8548 | 34.8517 | 34.8469 | 34.8334 | 34.7907 | 34.7326 | 34.5947 | 34.4645 | 34.8309 | 34.8309 | 34.8309 | 34.8278 | 34.8248 | 34.8218 | 34.8187 | 34.8138 | 34.8004 | 34.7577 | 34.7373 | 34.6733 | 34.6198
BRAMLEY (FLEE) | READING BSP | LITTLE HUNGERFORD | MINIMUM HEADROOM | SU 75372 72019 | YES | 52.114 | 52.1069 | 52.0495 | 51.9934 | 51.9055 | 51.815 | 51.7221 | 51.5916 | 51.5354 | 51.3579 | 50.8264 | 49.1486 | 47.5095 | 50.8855 | 50.8683 | 50.8319 | 50.7837 | 50.6903 | 50.3673 | 50.0327 | 49.6975 | 49.3392 | 48.271 | 46.4028 | 44.4213 | 42.4824 | 50.8562 | 50.8562 | 50.8562 | 50.7881 | 50.7188 | 50.6477 | 50.5717 | 50.2841 | 49.9399 | 48.9138 | 47.1185 | 45.2142 | 43.3516
|  | LITTLE HUNGERFORD | CT |  |  | 52.114 | 52.1069 | 52.0495 | 51.9934 | 51.9375 | 51.8819 | 51.8572 | 51.8313 | 51.8058 | 51.7289 | 50.8264 | 49.1486 | 47.5095 | 50.8855 | 50.8683 | 50.8319 | 50.7963 | 50.7606 | 50.3673 | 50.0327 | 49.6975 | 49.3392 | 48.271 | 46.4028 | 44.4213 | 42.4824 | 50.8562 | 50.8562 | 50.8562 | 50.845 | 50.7997 | 50.7546 | 50.6061 | 50.2841 | 49.9399 | 48.9138 | 47.1185 | 45.2142 | 43.3516
|  | LITTLE HUNGERFORD | LW |  |  | 52.114 | 52.1092 | 52.0535 | 51.9985 | 51.9427 | 51.9158 | 51.8878 | 51.8554 | 51.8289 | 51.7465 | 51.2752 | 49.5831 | 47.9481 | 50.8865 | 50.8698 | 50.8345 | 50.7992 | 50.7631 | 50.7448 | 50.5714 | 50.2363 | 49.8771 | 48.8031 | 46.9375 | 44.9416 | 43.0067 | 50.8562 | 50.8562 | 50.8562 | 50.849 | 50.8035 | 50.7811 | 50.7576 | 50.7296 | 50.456 | 49.4241 | 47.6313 | 45.7127 | 43.854
|  | LITTLE HUNGERFORD | ST |  |  | 52.114 | 52.114 | 52.1123 | 52.0128 | 51.9055 | 51.815 | 51.7221 | 51.5916 | 51.5354 | 51.3579 | 51.1666 | 50.7722 | 50.4017 | 50.8974 | 50.8879 | 50.8717 | 50.7837 | 50.6903 | 50.607 | 50.5211 | 50.3965 | 50.3465 | 50.1874 | 49.0036 | 47.432 | 46.0901 | 50.8562 | 50.8562 | 50.8562 | 50.7881 | 50.7188 | 50.6477 | 50.5717 | 50.4443 | 50.3913 | 50.2234 | 49.5915 | 48.0698 | 46.7773
|  | LITTLE HUNGERFORD | FS |  |  | 52.114 | 52.114 | 52.114 | 52.114 | 52.114 | 52.114 | 52.1139 | 52.1138 | 52.1135 | 52.1023 | 52.0675 | 52.0264 | 51.9865 | 50.9177 | 50.9116 | 50.9103 | 50.9045 | 50.8976 | 50.8933 | 50.8889 | 50.8833 | 50.8788 | 50.8645 | 50.8418 | 50.813 | 50.785 | 50.8562 | 50.8562 | 50.8562 | 50.8562 | 50.8561 | 50.8561 | 50.8561 | 50.856 | 50.8556 | 50.8536 | 50.8521 | 50.8445 | 50.8358
COWLEY GSP | HIGH WYCOMBE BSP | LITTLE MARLOW | MINIMUM HEADROOM | SU 86037 87794 | YES | 45.4997 | 45.4997 | 45.4997 | 45.4997 | 45.4997 | 45.4997 | 45.4997 | 45.4997 | 45.4997 | 45.4997 | 45.4997 | 45.2784 | 44.2632 | 42.7891 | 42.7746 | 42.744 | 42.7143 | 42.6849 | 42.6557 | 42.6399 | 42.6242 | 42.6072 | 42.3883 | 41.2963 | 40.1218 | 38.9604 | 44.5538 | 44.5435 | 44.5218 | 44.5007 | 44.4798 | 44.4591 | 44.4479 | 44.4367 | 44.4247 | 44.3887 | 43.9786 | 42.7849 | 41.6032
|  | LITTLE MARLOW | CT |  |  | 45.4997 | 45.4997 | 45.4997 | 45.4997 | 45.4997 | 45.4997 | 45.4997 | 45.4997 | 45.4997 | 45.4997 | 45.4997 | 45.2784 | 44.2632 | 42.7891 | 42.7746 | 42.744 | 42.7143 | 42.6849 | 42.6557 | 42.6399 | 42.6242 | 42.6072 | 42.3883 | 41.2963 | 40.1218 | 38.9604 | 44.5538 | 44.5435 | 44.5218 | 44.5007 | 44.4798 | 44.4591 | 44.4479 | 44.4367 | 44.4247 | 44.3887 | 43.9786 | 42.7849 | 41.6032
|  | LITTLE MARLOW | LW |  |  | 45.4997 | 45.4997 | 45.4997 | 45.4997 | 45.4997 | 45.4997 | 45.4997 | 45.4997 | 45.4997 | 45.4997 | 45.4997 | 45.4997 | 44.6579 | 42.7939 | 42.7821 | 42.7571 | 42.7328 | 42.7088 | 42.6928 | 42.677 | 42.6613 | 42.6443 | 42.5937 | 41.7485 | 40.5738 | 39.412 | 44.5572 | 44.5488 | 44.5311 | 44.5138 | 44.4968 | 44.4854 | 44.4742 | 44.463 | 44.451 | 44.4151 | 44.3514 | 43.2448 | 42.0626
|  | LITTLE MARLOW | ST |  |  | 45.4997 | 45.4997 | 45.4997 | 45.4997 | 45.4997 | 45.4997 | 45.4997 | 45.4997 | 45.4997 | 45.4997 | 45.4997 | 45.4997 | 45.4997 | 42.8073 | 42.8033 | 42.7966 | 42.7884 | 42.7784 | 42.7661 | 42.7539 | 42.7431 | 42.7316 | 42.6974 | 42.6373 | 42.5749 | 41.859 | 44.5667 | 44.5639 | 44.5591 | 44.5533 | 44.5462 | 44.5374 | 44.5288 | 44.5211 | 44.5129 | 44.4887 | 44.446 | 44.4017 | 44.3579
|  | LITTLE MARLOW | FS |  |  | 45.4997 | 45.4997 | 45.4997 | 45.4997 | 45.4997 | 45.4997 | 45.4997 | 45.4997 | 45.4997 | 45.4997 | 45.4997 | 45.4997 | 45.4997 | 42.8129 | 42.8121 | 42.8113 | 42.8079 | 42.804 | 42.7996 | 42.7953 | 42.7897 | 42.7853 | 42.7721 | 42.7489 | 42.7248 | 42.7014 | 44.5707 | 44.5701 | 44.5695 | 44.5672 | 44.5643 | 44.5612 | 44.5582 | 44.5542 | 44.5511 | 44.5417 | 44.5252 | 44.5082 | 44.4915
NURSLING GSP | ROWNHAMS | LORDSHILL | MINIMUM HEADROOM | SU 38746 16055 | YES | 43.3441 | 43.3441 | 43.3441 | 43.2363 | 43.1251 | 43.0088 | 42.8884 | 42.7055 | 42.6802 | 42.5933 | 41.79 | 40.2447 | 38.9995 | 40.4139 | 40.412 | 40.4083 | 40.2974 | 40.1824 | 40.0597 | 39.9327 | 39.7432 | 39.7109 | 39.6015 | 38.5584 | 36.9332 | 35.4741 | 41.9126 | 41.9126 | 41.9126 | 41.8048 | 41.6935 | 41.5773 | 41.4569 | 41.274 | 41.2486 | 41.1618 | 40.0442 | 38.3748 | 36.9087
|  | LORDSHILL | CT |  |  | 43.3441 | 43.3441 | 43.3441 | 43.3441 | 43.3441 | 43.3441 | 43.3441 | 43.3441 | 43.3441 | 43.3441 | 42.7058 | 41.4879 | 40.2621 | 40.4139 | 40.412 | 40.4083 | 40.4046 | 40.4008 | 40.397 | 40.3904 | 40.3838 | 40.3769 | 40.3543 | 39.4766 | 38.1787 | 36.743 | 41.9126 | 41.9126 | 41.9126 | 41.9126 | 41.9126 | 41.9126 | 41.9126 | 41.9126 | 41.9126 | 41.9126 | 40.963 | 39.6244 | 38.1777
|  | LORDSHILL | LW |  |  | 43.3441 | 43.3441 | 43.3441 | 43.2363 | 43.1251 | 43.0088 | 42.8884 | 42.7055 | 42.6802 | 42.5933 | 41.79 | 40.2447 | 38.9995 | 40.4141 | 40.4122 | 40.4087 | 40.2974 | 40.1824 | 40.0597 | 39.9327 | 39.7432 | 39.7109 | 39.6015 | 38.5584 | 36.9332 | 35.4741 | 41.9126 | 41.9126 | 41.9126 | 41.8048 | 41.6935 | 41.5773 | 41.4569 | 41.274 | 41.2486 | 41.1618 | 40.0442 | 38.3748 | 36.9087
|  | LORDSHILL | ST |  |  | 43.3441 | 43.3441 | 43.3441 | 43.3441 | 43.3441 | 43.3441 | 43.3441 | 43.3441 | 43.3441 | 43.3441 | 43.3155 | 42.5124 | 41.7321 | 40.414 | 40.4124 | 40.4098 | 40.4066 | 40.4026 | 40.3995 | 40.3963 | 40.3918 | 40.387 | 40.3715 | 40.1263 | 39.2705 | 38.439 | 41.9126 | 41.9126 | 41.9126 | 41.9126 | 41.9126 | 41.9126 | 41.9126 | 41.9126 | 41.9126 | 41.9126 | 41.6242 | 40.7533 | 39.9072
|  | LORDSHILL | FS |  |  | 43.3441 | 43.3441 | 43.3441 | 43.3441 | 43.3441 | 43.3441 | 43.3441 | 43.3441 | 43.3441 | 43.3441 | 43.3441 | 43.3441 | 43.3441 | 40.4165 | 40.4161 | 40.4158 | 40.4149 | 40.4138 | 40.4128 | 40.4117 | 40.4104 | 40.4086 | 40.4025 | 40.3868 | 40.3662 | 40.341 | 41.9126 | 41.9126 | 41.9126 | 41.9126 | 41.9126 | 41.9126 | 41.9126 | 41.9126 | 41.9126 | 41.9126 | 41.9126 | 41.9126 | 41.8427
BRAMLEY (ANDO-THAT) | THATCHAM BSP | LOVE LANE | MINIMUM HEADROOM | SU 47334 68495 | YES | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 56.8347 | 56.8347 | 56.8347 | 56.8347 | 56.8221 | 56.8094 | 56.7974 | 56.7871 | 56.7765 | 56.7452 | 56.3037 | 55.3052 | 54.3357 | 59.2197 | 59.2197 | 59.2197 | 59.2197 | 59.2197 | 59.2197 | 59.2197 | 59.21 | 59.1609 | 58.5071 | 57.4486 | 56.4753 | 55.5312
|  | LOVE LANE | CT |  |  | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 56.8347 | 56.8347 | 56.8347 | 56.8347 | 56.8234 | 56.8094 | 56.7974 | 56.7871 | 56.7765 | 56.7452 | 56.3037 | 55.3052 | 54.3357 | 59.2197 | 59.2197 | 59.2197 | 59.2197 | 59.2197 | 59.2197 | 59.2197 | 59.21 | 59.1609 | 58.5071 | 57.4486 | 56.4753 | 55.5312
|  | LOVE LANE | LW |  |  | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 56.8347 | 56.8347 | 56.8347 | 56.8347 | 56.8221 | 56.8111 | 56.799 | 56.7887 | 56.7781 | 56.7468 | 56.337 | 55.3402 | 54.3701 | 59.2197 | 59.2197 | 59.2197 | 59.2197 | 59.2197 | 59.2197 | 59.2197 | 59.2121 | 59.1951 | 58.5412 | 57.4828 | 56.5093 | 55.5647
|  | LOVE LANE | ST |  |  | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 56.8347 | 56.8347 | 56.8347 | 56.8347 | 56.8347 | 56.8347 | 56.8295 | 56.8225 | 56.8153 | 56.794 | 56.7599 | 56.7299 | 56.4251 | 59.2197 | 59.2197 | 59.2197 | 59.2197 | 59.2197 | 59.2197 | 59.2197 | 59.2197 | 59.2197 | 59.2188 | 58.8144 | 58.1866 | 57.5732
|  | LOVE LANE | FS |  |  | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 60.8439 | 56.8347 | 56.8347 | 56.8347 | 56.8347 | 56.8347 | 56.8347 | 56.8347 | 56.8347 | 56.8347 | 56.8347 | 56.8347 | 56.8281 | 56.8178 | 59.2197 | 59.2197 | 59.2197 | 59.2197 | 59.2197 | 59.2197 | 59.2197 | 59.2197 | 59.2197 | 59.2197 | 59.2197 | 59.2197 | 59.2197
COWLEY GSP | YARNTON BSP | LOVELACE ROAD | MINIMUM HEADROOM | SP 50395 10376 | NO | 21.2528 | 21.2445 | 21.2275 | 21.2088 | 21.1914 | 21.0986 | 21.0359 | 20.9664 | 20.88 | 20.5626 | 20.0475 | 19.4692 | 18.8978 | 19.9134 | 19.9066 | 19.893 | 19.7471 | 19.5012 | 19.281 | 19.202 | 19.121 | 19.0202 | 18.65 | 18.0493 | 17.3748 | 16.7084 | 20.7498 | 20.7425 | 20.7279 | 20.7117 | 20.5668 | 20.3603 | 20.2862 | 20.2103 | 20.1158 | 19.7686 | 19.2053 | 18.5276 | 17.8533
|  | LOVELACE ROAD | CT |  |  | 21.2528 | 21.2445 | 21.2275 | 21.2088 | 21.1914 | 21.0986 | 21.0359 | 20.9664 | 20.88 | 20.5626 | 20.0475 | 19.4692 | 18.8978 | 19.9134 | 19.9066 | 19.893 | 19.7471 | 19.5012 | 19.281 | 19.202 | 19.121 | 19.0202 | 18.65 | 18.0493 | 17.3748 | 16.7084 | 20.7498 | 20.7425 | 20.7279 | 20.7117 | 20.5668 | 20.3603 | 20.2862 | 20.2103 | 20.1158 | 19.7686 | 19.2053 | 18.5276 | 17.8533
|  | LOVELACE ROAD | LW |  |  | 21.258 | 21.2525 | 21.2415 | 21.2286 | 21.217 | 21.2112 | 21.2057 | 21.1999 | 21.1928 | 20.9925 | 20.4774 | 19.8991 | 19.3273 | 19.9175 | 19.9131 | 19.9042 | 19.8938 | 19.863 | 19.7824 | 19.7035 | 19.6224 | 19.5218 | 19.1514 | 18.5507 | 17.8761 | 17.2094 | 20.7542 | 20.7495 | 20.74 | 20.7288 | 20.7188 | 20.7139 | 20.7091 | 20.6805 | 20.5861 | 20.2388 | 19.6755 | 19.0349 | 18.3602
|  | LOVELACE ROAD | ST |  |  | 21.2628 | 21.2603 | 21.2563 | 21.2502 | 21.2441 | 21.2393 | 21.2346 | 21.2307 | 21.2259 | 21.2077 | 21.1243 | 20.7546 | 20.3894 | 19.9214 | 19.9194 | 19.9162 | 19.9112 | 19.9063 | 19.9025 | 19.8987 | 19.8956 | 19.8916 | 19.7317 | 19.3172 | 18.8739 | 18.448 | 20.7583 | 20.7562 | 20.7528 | 20.7475 | 20.7422 | 20.7381 | 20.7341 | 20.7307 | 20.7265 | 20.7108 | 20.3942 | 19.9786 | 19.5792
|  | LOVELACE ROAD | FS |  |  | 21.2657 | 21.265 | 21.2642 | 21.2608 | 21.2578 | 21.255 | 21.2521 | 21.2483 | 21.2422 | 21.2219 | 21.2038 | 21.1703 | 21.1398 | 19.9237 | 19.9232 | 19.9225 | 19.9196 | 19.917 | 19.9145 | 19.9121 | 19.9087 | 19.903 | 19.8841 | 19.8683 | 19.8375 | 19.626 | 20.7609 | 20.7603 | 20.7595 | 20.7565 | 20.7538 | 20.7512 | 20.7486 | 20.7451 | 20.7393 | 20.72 | 20.7035 | 20.6719 | 20.6433
MANNINGTON GSP | ARNEWOOD | LYMINGTON | MINIMUM HEADROOM | SZ 31720 96856 | YES | 46.4146 | 46.3659 | 45.3752 | 45.2149 | 45.0495 | 44.7721 | 44.468 | 44.1943 | 43.9541 | 43.2053 | 41.9875 | 40.8008 | 39.5622 | 37.2525 | 37.2033 | 36.2112 | 36.0494 | 35.8823 | 35.6014 | 35.3164 | 35.0593 | 34.8373 | 34.1921 | 33.1423 | 32.128 | 31.0583 | 43.7091 | 43.6575 | 42.6599 | 42.481 | 42.2865 | 41.9442 | 41.5966 | 41.2853 | 41.0061 | 40.1955 | 38.8777 | 37.5881 | 36.249
|  | LYMINGTON | CT |  |  | 46.482 | 46.4336 | 45.7963 | 45.6541 | 45.5068 | 45.3497 | 45.08 | 44.8362 | 44.6085 | 43.899 | 42.175 | 40.847 | 39.6089 | 37.3198 | 37.2707 | 36.6318 | 36.4879 | 36.3388 | 36.1797 | 35.9248 | 35.6977 | 35.4875 | 34.8785 | 33.3225 | 32.167 | 31.0977 | 43.7756 | 43.7237 | 43.0785 | 42.9072 | 42.7271 | 42.5341 | 42.2166 | 41.9352 | 41.6679 | 40.8936 | 39.0695 | 37.6387 | 36.3
|  | LYMINGTON | LW |  |  | 46.4146 | 46.3659 | 45.3752 | 45.2149 | 45.0495 | 44.7721 | 44.468 | 44.1943 | 43.9541 | 43.2053 | 41.9875 | 40.8008 | 39.5622 | 37.2525 | 37.2033 | 36.2112 | 36.0494 | 35.8823 | 35.6014 | 35.3164 | 35.0593 | 34.8373 | 34.1921 | 33.1423 | 32.128 | 31.0583 | 43.7091 | 43.6575 | 42.6599 | 42.481 | 42.2865 | 41.9442 | 41.5966 | 41.2853 | 41.0061 | 40.1955 | 38.8777 | 37.5881 | 36.249
|  | LYMINGTON | ST |  |  | 46.5477 | 46.52 | 46.1136 | 46.0272 | 45.9276 | 45.7689 | 45.6079 | 45.4485 | 45.2935 | 44.8488 | 44.0782 | 43.3361 | 42.572 | 37.3859 | 37.3578 | 36.9507 | 36.8633 | 36.7625 | 36.6015 | 36.4382 | 36.2838 | 36.1408 | 35.7302 | 35.071 | 34.44 | 33.7857 | 43.8437 | 43.814 | 43.404 | 43.3126 | 43.2011 | 43.0011 | 42.7981 | 42.6067 | 42.4247 | 41.9025 | 41.0649 | 40.2566 | 39.427
|  | LYMINGTON | FS |  |  | 46.623 | 46.6175 | 46.4301 | 46.3982 | 46.363 | 46.3025 | 46.2417 | 46.1773 | 46.1214 | 45.9614 | 45.7019 | 45.4485 | 45.1949 | 37.4618 | 37.4563 | 37.2688 | 37.2367 | 37.2011 | 37.1398 | 37.0781 | 37.0129 | 36.9561 | 36.7936 | 36.5366 | 36.3029 | 36.0678 | 43.9222 | 43.9164 | 43.7286 | 43.6953 | 43.6583 | 43.5937 | 43.5288 | 43.4601 | 43.3917 | 43.1862 | 42.8616 | 42.5636 | 42.2683
MELKSHAM GSP | CHIPPENHAM | LYNEHAM | MINIMUM HEADROOM | ST 99348 80481 | YES | 15.6897 | 15.6566 | 15.5864 | 15.5128 | 15.4349 | 15.3526 | 15.2207 | 14.9929 | 14.8854 | 14.5271 | 13.8727 | 12.9817 | 12.543 | 14.8885 | 14.8498 | 14.7671 | 14.6812 | 14.5912 | 14.4969 | 14.3714 | 14.1298 | 14.0072 | 13.6048 | 12.878 | 11.9123 | 11.4002 | 13.8909 | 13.8668 | 13.8157 | 13.7606 | 13.701 | 13.6348 | 13.4952 | 13.2885 | 13.2036 | 12.9122 | 12.3674 | 11.5894 | 11.2618
|  | LYNEHAM | CT |  |  | 15.6897 | 15.6566 | 15.5864 | 15.5128 | 15.4349 | 15.3526 | 15.252 | 15.1305 | 15.04 | 14.7596 | 14.0901 | 13.3829 | 12.8935 | 14.8885 | 14.8498 | 14.7671 | 14.6812 | 14.5912 | 14.4969 | 14.3823 | 14.2469 | 14.1415 | 13.8168 | 13.0749 | 12.2931 | 11.7304 | 13.8909 | 13.8668 | 13.8157 | 13.7606 | 13.701 | 13.6368 | 13.5574 | 13.4569 | 13.3891 | 13.1755 | 12.6157 | 12.0215 | 11.6431
|  | LYNEHAM | LW |  |  | 15.7151 | 15.6959 | 15.6552 | 15.5973 | 15.52 | 15.3815 | 15.2207 | 14.9929 | 14.8854 | 14.5271 | 13.8727 | 12.9817 | 12.543 | 14.9159 | 14.8957 | 14.8482 | 14.7832 | 14.6989 | 14.5462 | 14.3714 | 14.1298 | 14.0072 | 13.6048 | 12.878 | 11.9123 | 11.4002 | 13.9093 | 13.8954 | 13.8658 | 13.8186 | 13.7519 | 13.6348 | 13.4952 | 13.2885 | 13.2036 | 12.9122 | 12.3674 | 11.5894 | 11.2618
|  | LYNEHAM | ST |  |  | 15.7394 | 15.7343 | 15.7256 | 15.7109 | 15.6902 | 15.6368 | 15.5783 | 15.4915 | 15.4199 | 15.1822 | 14.8256 | 14.259 | 13.8925 | 14.9175 | 14.9172 | 14.9166 | 14.912 | 14.8909 | 14.8307 | 14.7648 | 14.6685 | 14.5867 | 14.3192 | 13.9146 | 13.2999 | 12.8856 | 13.927 | 13.9233 | 13.917 | 13.9052 | 13.888 | 13.846 | 13.7987 | 13.7262 | 13.67 | 13.4774 | 13.1937 | 12.6998 | 12.4057
|  | LYNEHAM | FS |  |  | 15.7473 | 15.7465 | 15.7457 | 15.729 | 15.7117 | 15.6841 | 15.656 | 15.6155 | 15.5295 | 15.2431 | 15.0222 | 14.4938 | 14.0191 | 14.9181 | 14.918 | 14.9179 | 14.9045 | 14.8911 | 14.8767 | 14.8581 | 14.8146 | 14.7249 | 14.4272 | 14.188 | 13.6423 | 13.1513 | 13.9328 | 13.9322 | 13.9316 | 13.9158 | 13.8997 | 13.8759 | 13.8517 | 13.8162 | 13.7361 | 13.4671 | 13.2738 | 12.7717 | 12.3217
BRAMLEY (FLEE) | BRACKNELL RESERVE | M V E E | MINIMUM HEADROOM | SU 98120 65945 | YES | 28.3638 | 28.3638 | 39.0138 | 38.8904 | 38.7649 | 38.6374 | 38.5043 | 38.2989 | 38.2729 | 38.1894 | 37.8013 | 37.3777 | 37.2682 | 28.2442 | 28.2059 | 37.2955 | 37.1041 | 36.904 | 36.6994 | 36.4888 | 36.2112 | 36.1405 | 35.9465 | 35.3998 | 34.8415 | 34.6091 | 28.2364 | 28.1952 | 38.7804 | 38.584 | 38.3784 | 38.1681 | 37.9517 | 37.6688 | 37.5949 | 37.3927 | 36.8343 | 36.266 | 36.0246
|  | M V E E | CT |  |  | 28.3638 | 28.3638 | 39.0138 | 38.8904 | 38.7649 | 38.6374 | 38.5043 | 38.2989 | 38.2729 | 38.1894 | 37.8013 | 37.3777 | 37.2682 | 28.2442 | 28.2059 | 37.2955 | 37.1041 | 36.904 | 36.6994 | 36.4888 | 36.2112 | 36.1405 | 35.9465 | 35.3998 | 34.8415 | 34.6091 | 28.2364 | 28.1952 | 38.7804 | 38.584 | 38.3784 | 38.1681 | 37.9517 | 37.6688 | 37.5949 | 37.3927 | 36.8343 | 36.266 | 36.0246
|  | M V E E | LW |  |  | 28.3638 | 28.3638 | 39.0138 | 38.9429 | 38.8698 | 38.7934 | 38.7143 | 38.5941 | 38.5774 | 38.5204 | 38.435 | 38.2916 | 38.2833 | 28.2604 | 28.2309 | 37.3393 | 37.2186 | 37.0889 | 36.9439 | 36.7872 | 36.5948 | 36.5335 | 36.3659 | 36.122 | 35.8437 | 35.7126 | 28.2538 | 28.2222 | 38.8275 | 38.703 | 38.5692 | 38.4191 | 38.2567 | 38.0589 | 37.9944 | 37.8186 | 37.563 | 37.2748 | 37.1346
|  | M V E E | ST |  |  | 28.3638 | 28.3638 | 39.0138 | 39.0138 | 39.0138 | 39.0138 | 39.0138 | 39.0138 | 39.0138 | 39.0138 | 39.0138 | 39.0138 | 39.0138 | 28.2806 | 28.2622 | 37.3892 | 37.36 | 37.3257 | 37.2785 | 37.2255 | 37.177 | 37.1465 | 37.0697 | 36.9606 | 36.8728 | 36.7934 | 28.2755 | 28.2557 | 38.881 | 38.8496 | 38.8128 | 38.7622 | 38.7052 | 38.6532 | 38.6204 | 38.5379 | 38.4208 | 38.3265 | 38.2412
|  | M V E E | FS |  |  | 28.3638 | 28.3638 | 39.0138 | 39.0138 | 39.0138 | 39.0138 | 39.0138 | 39.0138 | 39.0138 | 39.0138 | 39.0138 | 39.0138 | 39.0138 | 28.2931 | 28.2814 | 37.4185 | 37.4027 | 37.3857 | 37.3659 | 37.3446 | 37.3241 | 37.3121 | 37.282 | 37.2382 | 37.203 | 37.172 | 28.2889 | 28.2763 | 38.9125 | 38.8955 | 38.8772 | 38.856 | 38.8332 | 38.8111 | 38.7982 | 38.7659 | 38.7189 | 38.6811 | 38.6478
CHICKERELL GSP | CHICKERELL BSP | MAIDEN NEWTON | MINIMUM HEADROOM | SY 59138 97747 | YES | 11.0561 | 11.0362 | 10.994 | 10.9531 | 10.9126 | 10.8602 | 10.8084 | 10.757 | 10.7016 | 10.5383 | 10.2711 | 9.9961 | 9.7259 | 9.7646 | 9.7394 | 9.6862 | 9.6346 | 9.5835 | 9.5175 | 9.4521 | 9.3873 | 9.3174 | 9.1114 | 8.7744 | 8.4277 | 8.0869 | 10.5303 | 10.5191 | 10.4952 | 10.472 | 10.4491 | 10.4195 | 10.3901 | 10.3611 | 10.3297 | 10.2373 | 10.086 | 9.9304 | 9.7775
|  | MAIDEN NEWTON | CT |  |  | 11.0607 | 11.0432 | 11.0064 | 10.9707 | 10.9354 | 10.9003 | 10.8485 | 10.7971 | 10.7417 | 10.5784 | 10.3112 | 10.0363 | 9.7663 | 9.7703 | 9.7483 | 9.7018 | 9.6568 | 9.6122 | 9.568 | 9.5026 | 9.4379 | 9.3681 | 9.162 | 8.825 | 8.4784 | 8.1379 | 10.5329 | 10.523 | 10.5022 | 10.482 | 10.462 | 10.4421 | 10.4128 | 10.3838 | 10.3524 | 10.26 | 10.1088 | 9.9532 | 9.8004
|  | MAIDEN NEWTON | LW |  |  | 11.0561 | 11.0362 | 10.994 | 10.9531 | 10.9126 | 10.8602 | 10.8084 | 10.757 | 10.7016 | 10.5383 | 10.2711 | 9.9961 | 9.7259 | 9.7646 | 9.7394 | 9.6862 | 9.6346 | 9.5835 | 9.5175 | 9.4521 | 9.3873 | 9.3174 | 9.1114 | 8.7744 | 8.4277 | 8.0869 | 10.5303 | 10.5191 | 10.4952 | 10.472 | 10.4491 | 10.4195 | 10.3901 | 10.3611 | 10.3297 | 10.2373 | 10.086 | 9.9304 | 9.7775
|  | MAIDEN NEWTON | ST |  |  | 11.0621 | 11.0475 | 11.0224 | 10.9916 | 10.9544 | 10.9253 | 10.8965 | 10.8614 | 10.8237 | 10.7136 | 10.5363 | 10.3594 | 10.1834 | 9.7721 | 9.7537 | 9.722 | 9.6831 | 9.6363 | 9.5996 | 9.5632 | 9.519 | 9.4714 | 9.3325 | 9.1089 | 8.8858 | 8.6638 | 10.5337 | 10.5254 | 10.5112 | 10.4938 | 10.4728 | 10.4563 | 10.44 | 10.4201 | 10.3988 | 10.3365 | 10.2361 | 10.136 | 10.0364
|  | MAIDEN NEWTON | FS |  |  | 11.0873 | 11.0858 | 11.0844 | 11.0777 | 11.0697 | 11.0606 | 11.0516 | 11.0401 | 11.0254 | 10.9829 | 10.9157 | 10.8521 | 10.7922 | 9.8039 | 9.802 | 9.8002 | 9.7917 | 9.7817 | 9.7702 | 9.7589 | 9.7443 | 9.7259 | 9.6723 | 9.5875 | 9.5072 | 9.4317 | 10.548 | 10.5472 | 10.5463 | 10.5425 | 10.538 | 10.5329 | 10.5278 | 10.5213 | 10.513 | 10.4889 | 10.4509 | 10.4148 | 10.381
BRAMLEY (FLEE) | MAIDENHEAD BSP | MAIDENHEAD | MINIMUM HEADROOM | SU 86485 79800 | YES | 57.5433 | 57.5433 | 57.5433 | 57.5413 | 57.5373 | 57.531 | 57.5222 | 57.5045 | 57.5015 | 57.486 | 57.4482 | 57.3745 | 56.8973 | 52.946 | 52.9323 | 52.904 | 52.8743 | 52.8405 | 52.8173 | 52.7813 | 52.6463 | 52.4666 | 52.0095 | 50.6613 | 49.3113 | 48.0607 | 54.6203 | 54.6203 | 54.6203 | 54.6183 | 54.6143 | 54.6079 | 54.5992 | 54.5815 | 54.5785 | 54.563 | 53.7294 | 52.4341 | 51.2285
|  | MAIDENHEAD | CT |  |  | 57.5433 | 57.5433 | 57.5433 | 57.5427 | 57.5416 | 57.5399 | 57.5375 | 57.5322 | 57.5312 | 57.5261 | 57.4842 | 57.4373 | 56.959 | 52.9483 | 52.9359 | 52.9102 | 52.8845 | 52.8561 | 52.8268 | 52.7973 | 52.6779 | 52.5004 | 52.0538 | 50.7065 | 49.3835 | 48.1239 | 54.6203 | 54.6203 | 54.6203 | 54.6197 | 54.6186 | 54.6169 | 54.6145 | 54.6092 | 54.6082 | 54.6031 | 53.7739 | 52.5059 | 51.2914
|  | MAIDENHEAD | LW |  |  | 57.5433 | 57.5433 | 57.5433 | 57.5413 | 57.5373 | 57.531 | 57.5222 | 57.5045 | 57.5015 | 57.486 | 57.4482 | 57.3745 | 56.8973 | 52.946 | 52.9323 | 52.904 | 52.8743 | 52.8405 | 52.8173 | 52.7813 | 52.6463 | 52.4666 | 52.0095 | 50.6613 | 49.3113 | 48.0607 | 54.6203 | 54.6203 | 54.6203 | 54.6183 | 54.6143 | 54.6079 | 54.5992 | 54.5815 | 54.5785 | 54.563 | 53.7294 | 52.4341 | 51.2285
|  | MAIDENHEAD | ST |  |  | 57.5433 | 57.5433 | 57.5433 | 57.5429 | 57.542 | 57.5408 | 57.539 | 57.5349 | 57.5329 | 57.5223 | 57.5084 | 57.4596 | 57.4419 | 52.9579 | 52.9517 | 52.9412 | 52.928 | 52.9102 | 52.8958 | 52.8789 | 52.8599 | 52.842 | 52.7845 | 52.4573 | 52.058 | 51.3347 | 54.6203 | 54.6203 | 54.6203 | 54.6199 | 54.619 | 54.6178 | 54.6159 | 54.6118 | 54.6099 | 54.5993 | 54.5854 | 54.5366 | 54.3479
|  | MAIDENHEAD | FS |  |  | 57.5433 | 57.5433 | 57.5433 | 57.5433 | 57.5432 | 57.5432 | 57.5431 | 57.5429 | 57.5423 | 57.5384 | 57.5354 | 57.5209 | 57.5067 | 52.9671 | 52.9659 | 52.9648 | 52.9604 | 52.9545 | 52.9496 | 52.9439 | 52.9366 | 52.9296 | 52.9101 | 52.888 | 52.8562 | 52.8259 | 54.6203 | 54.6203 | 54.6203 | 54.6202 | 54.6202 | 54.6202 | 54.6201 | 54.6199 | 54.6193 | 54.6154 | 54.6124 | 54.5978 | 54.5837
MELKSHAM GSP | CHIPPENHAM | MALMESBURY | MINIMUM HEADROOM | ST 92288 87493 | YES | 18.3265 | 18.3156 | 18.2949 | 18.2571 | 18.2181 | 18.1781 | 18.1469 | 18.1008 | 18.0866 | 17.8473 | 17.1884 | 16.5009 | 15.9328 | 16.5155 | 16.5086 | 16.4955 | 16.4649 | 16.3978 | 16.1006 | 15.9572 | 15.8009 | 15.6688 | 15.2753 | 14.5286 | 13.7518 | 13.0961 | 17.2849 | 17.2849 | 17.2849 | 17.2215 | 16.9419 | 16.662 | 16.5261 | 16.3772 | 16.253 | 15.8827 | 15.1743 | 14.4185 | 13.7719
|  | MALMESBURY | CT |  |  | 18.3265 | 18.3156 | 18.2949 | 18.2571 | 18.2181 | 18.1781 | 18.1469 | 18.1008 | 18.0866 | 17.8473 | 17.1884 | 16.5009 | 15.9328 | 16.5155 | 16.5086 | 16.4955 | 16.4649 | 16.3978 | 16.1006 | 15.9572 | 15.8009 | 15.6688 | 15.2753 | 14.5286 | 13.7518 | 13.0961 | 17.2849 | 17.2849 | 17.2849 | 17.2215 | 16.9419 | 16.662 | 16.5261 | 16.3772 | 16.253 | 15.8827 | 15.1743 | 14.4185 | 13.7719
|  | MALMESBURY | LW |  |  | 18.3272 | 18.3166 | 18.2967 | 18.2744 | 18.2485 | 18.2289 | 18.205 | 18.1658 | 18.1515 | 18.0654 | 17.4713 | 16.8056 | 16.2697 | 16.5159 | 16.5092 | 16.4966 | 16.4812 | 16.4622 | 16.3402 | 16.2041 | 16.0547 | 15.9226 | 15.5224 | 14.8405 | 14.0854 | 13.4618 | 17.2849 | 17.2849 | 17.2849 | 17.271 | 17.0136 | 16.8889 | 16.7603 | 16.6183 | 16.4941 | 16.1171 | 15.4735 | 14.7492 | 14.1346
|  | MALMESBURY | ST |  |  | 18.3313 | 18.324 | 18.313 | 18.299 | 18.2815 | 18.2726 | 18.2627 | 18.2498 | 18.2403 | 18.204 | 18.1507 | 17.837 | 17.4631 | 16.5185 | 16.5139 | 16.5069 | 16.4978 | 16.4862 | 16.4797 | 16.4723 | 16.4615 | 16.4542 | 16.1871 | 15.7523 | 15.2636 | 14.8327 | 17.2849 | 17.2849 | 17.2849 | 17.2842 | 17.2828 | 17.2579 | 17.1666 | 17.0835 | 16.999 | 16.7443 | 16.3352 | 15.8716 | 15.4655
|  | MALMESBURY | FS |  |  | 18.3423 | 18.341 | 18.3401 | 18.337 | 18.3331 | 18.3306 | 18.328 | 18.3247 | 18.3211 | 18.3076 | 18.2912 | 18.2555 | 18.221 | 16.5231 | 16.5231 | 16.5231 | 16.5221 | 16.5196 | 16.518 | 16.5163 | 16.5141 | 16.5114 | 16.5004 | 16.4881 | 16.4562 | 16.4252 | 17.2849 | 17.2849 | 17.2849 | 17.2849 | 17.2848 | 17.2847 | 17.2846 | 17.2843 | 17.2831 | 17.2765 | 17.2712 | 17.2458 | 17.221
MINETY GSP | SWINDON BSP | MANCHESTER ROAD | MINIMUM HEADROOM | SU 15254 85130 | YES | 44.9291 | 44.8915 | 43.3183 | 43.1737 | 43.0287 | 42.8768 | 42.7243 | 42.5722 | 42.4921 | 42.2534 | 41.8519 | 41.5389 | 39.9313 | 44.0962 | 44.0492 | 42.4609 | 42.3028 | 42.1442 | 41.9733 | 41.8013 | 41.6302 | 41.5274 | 40.8837 | 39.7702 | 38.5605 | 36.2858 | 44.6211 | 44.5859 | 43.0168 | 42.8756 | 42.7342 | 42.5873 | 42.4398 | 42.2928 | 42.2185 | 41.9972 | 41.2545 | 38.899 | 36.4363
|  | MANCHESTER ROAD | CT |  |  | 45.0624 | 45.0355 | 44.0847 | 43.992 | 43.8989 | 43.8053 | 43.7037 | 43.6026 | 43.5428 | 43.3653 | 42.104 | 41.5505 | 40.0667 | 44.2302 | 44.1942 | 43.2291 | 43.1237 | 43.0177 | 42.9108 | 42.7897 | 42.6695 | 42.5872 | 42.052 | 40.0786 | 38.6463 | 36.446 | 44.7542 | 44.7296 | 43.7827 | 43.6932 | 43.6035 | 43.5134 | 43.4169 | 43.3208 | 43.2669 | 43.1067 | 41.6546 | 39.0586 | 36.596
|  | MANCHESTER ROAD | LW |  |  | 44.9291 | 44.8915 | 43.3183 | 43.1737 | 43.0287 | 42.8768 | 42.7243 | 42.5722 | 42.4921 | 42.2534 | 41.8519 | 41.5389 | 39.9313 | 44.0962 | 44.0492 | 42.4609 | 42.3028 | 42.1442 | 41.9733 | 41.8013 | 41.6302 | 41.5274 | 40.8837 | 39.7702 | 38.5605 | 36.2858 | 44.6211 | 44.5859 | 43.0168 | 42.8756 | 42.7342 | 42.5873 | 42.4398 | 42.2928 | 42.2185 | 41.9972 | 41.2545 | 38.899 | 36.4363
|  | MANCHESTER ROAD | ST |  |  | 45.133 | 45.1149 | 44.483 | 44.4211 | 44.3571 | 44.2931 | 44.2287 | 44.161 | 44.1207 | 44.0008 | 43.7989 | 43.6332 | 43.4193 | 44.3041 | 44.28 | 43.6399 | 43.5696 | 43.4955 | 43.4214 | 43.3465 | 43.2658 | 43.2101 | 43.0447 | 42.4146 | 41.742 | 41.0339 | 44.8239 | 44.8075 | 44.1777 | 44.118 | 44.0566 | 43.9953 | 43.9336 | 43.8693 | 43.833 | 43.725 | 43.5433 | 43.3988 | 42.0238
|  | MANCHESTER ROAD | FS |  |  | 45.2073 | 45.1993 | 44.8862 | 44.8557 | 44.8247 | 44.7931 | 44.7614 | 44.7279 | 44.7027 | 44.6263 | 44.5248 | 44.4164 | 44.2879 | 44.3847 | 44.3745 | 44.0595 | 44.0264 | 43.9925 | 43.9574 | 43.922 | 43.8843 | 43.8531 | 43.7591 | 43.627 | 43.4851 | 43.3228 | 44.8966 | 44.8892 | 44.5766 | 44.5467 | 44.5166 | 44.4859 | 44.455 | 44.4226 | 44.399 | 44.3273 | 44.2338 | 44.1342 | 44.0145
MANNINGTON GSP | MANNINGTON BSP | MANNINGTON | MINIMUM HEADROOM | SU 07592 05256 | YES | 21.1015 | 21.1015 | 21.1015 | 21.0924 | 21.0835 | 21.0746 | 21.0654 | 21.0511 | 21.0112 | 20.8829 | 20.8207 | 20.6202 | 20.4507 | 19.9384 | 19.9384 | 19.9384 | 19.9293 | 19.9204 | 19.9115 | 19.9023 | 19.888 | 19.8481 | 19.7198 | 19.6576 | 19.4571 | 19.2876 | 21.0041 | 21.0041 | 21.0041 | 20.995 | 20.9861 | 20.9772 | 20.968 | 20.9537 | 20.9138 | 20.7855 | 20.7233 | 20.5228 | 20.3533
|  | MANNINGTON | CT |  |  | 21.1015 | 21.1015 | 21.1015 | 21.101 | 21.0999 | 21.0984 | 21.0962 | 21.0913 | 21.0905 | 21.0858 | 21.0472 | 21.0042 | 20.991 | 19.9384 | 19.9384 | 19.9384 | 19.9379 | 19.9369 | 19.9353 | 19.9331 | 19.9282 | 19.9274 | 19.9227 | 19.8841 | 19.8234 | 19.6975 | 21.0041 | 21.0041 | 21.0041 | 21.0036 | 21.0026 | 21.001 | 20.9988 | 20.9939 | 20.9931 | 20.9884 | 20.9498 | 20.9068 | 20.8936
|  | MANNINGTON | LW |  |  | 21.1015 | 21.1015 | 21.1015 | 21.0997 | 21.096 | 21.0902 | 21.0821 | 21.066 | 21.0632 | 21.0489 | 21.0142 | 20.9466 | 20.942 | 19.9384 | 19.9384 | 19.9384 | 19.9366 | 19.9329 | 19.9271 | 19.9191 | 19.9029 | 19.9001 | 19.8858 | 19.8511 | 19.7542 | 19.6369 | 21.0041 | 21.0041 | 21.0041 | 21.0023 | 20.9986 | 20.9928 | 20.9848 | 20.9686 | 20.9658 | 20.9515 | 20.9168 | 20.8492 | 20.8446
|  | MANNINGTON | ST |  |  | 21.1015 | 21.1015 | 21.1015 | 21.1011 | 21.1004 | 21.0992 | 21.0976 | 21.0938 | 21.092 | 21.0822 | 21.0695 | 21.0247 | 21.0084 | 19.9384 | 19.9384 | 19.9384 | 19.938 | 19.9373 | 19.9362 | 19.9345 | 19.9307 | 19.9289 | 19.9192 | 19.9064 | 19.8616 | 19.8454 | 21.0041 | 21.0041 | 21.0041 | 21.0037 | 21.003 | 21.0019 | 21.0002 | 20.9964 | 20.9946 | 20.9849 | 20.9721 | 20.9273 | 20.9111
|  | MANNINGTON | FS |  |  | 21.1015 | 21.1015 | 21.1015 | 21.0924 | 21.0835 | 21.0746 | 21.0654 | 21.0511 | 21.0112 | 20.8829 | 20.8207 | 20.6202 | 20.4507 | 19.9384 | 19.9384 | 19.9384 | 19.9293 | 19.9204 | 19.9115 | 19.9023 | 19.888 | 19.8481 | 19.7198 | 19.6576 | 19.4571 | 19.2876 | 21.0041 | 21.0041 | 21.0041 | 20.995 | 20.9861 | 20.9772 | 20.968 | 20.9537 | 20.9138 | 20.7855 | 20.7233 | 20.5228 | 20.3533
LOVEDEAN GSP | CHICHESTER & HUNSTON | MARKET | MINIMUM HEADROOM | SU 86479 04732 | YES | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 38.0734 | 38.047 | 37.9929 | 37.9409 | 37.8899 | 37.8524 | 37.8137 | 37.7725 | 37.6918 | 37.3763 | 36.1346 | 34.7077 | 33.2837 | 38.7869 | 38.7869 | 38.7869 | 38.7869 | 38.7869 | 38.7869 | 38.7869 | 38.7274 | 38.5253 | 37.8588 | 36.6661 | 35.2955 | 33.9277
|  | MARKET | CT |  |  | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 38.0808 | 38.0584 | 38.0127 | 37.969 | 37.9261 | 37.8829 | 37.8442 | 37.803 | 37.7536 | 37.4592 | 36.2804 | 34.8536 | 33.4299 | 38.7869 | 38.7869 | 38.7869 | 38.7869 | 38.7869 | 38.7869 | 38.7869 | 38.7869 | 38.6653 | 37.9988 | 36.8061 | 35.4357 | 34.0681
|  | MARKET | LW |  |  | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 38.0734 | 38.047 | 37.9929 | 37.9409 | 37.8899 | 37.8524 | 37.8137 | 37.7725 | 37.6918 | 37.3763 | 36.1346 | 34.7077 | 33.2837 | 38.7869 | 38.7869 | 38.7869 | 38.7869 | 38.7869 | 38.7869 | 38.7869 | 38.7274 | 38.5253 | 37.8588 | 36.6661 | 35.2955 | 33.9277
|  | MARKET | ST |  |  | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 38.0857 | 38.0687 | 38.0396 | 38.0057 | 37.9661 | 37.9321 | 37.8974 | 37.8695 | 37.8394 | 37.7136 | 37.2677 | 36.3315 | 35.4224 | 38.7869 | 38.7869 | 38.7869 | 38.7869 | 38.7869 | 38.7869 | 38.7869 | 38.7869 | 38.7869 | 38.5748 | 37.7545 | 36.8552 | 35.982
|  | MARKET | FS |  |  | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 41.0728 | 38.1101 | 38.1064 | 38.1016 | 38.0917 | 38.0807 | 38.0686 | 38.0564 | 38.0407 | 38.0291 | 37.99 | 37.9181 | 37.8325 | 37.7232 | 38.7869 | 38.7869 | 38.7869 | 38.7869 | 38.7869 | 38.7869 | 38.7869 | 38.7869 | 38.7869 | 38.7869 | 38.7869 | 38.7869 | 38.5965
MELKSHAM GSP | WEST GRAFTON | MARLBOROUGH SOUTH | MINIMUM HEADROOM | SU 19293 68264 | YES | 25.6127 | 25.6127 | 25.6127 | 25.6127 | 25.6127 | 25.6127 | 25.6127 | 25.6127 | 25.6127 | 25.6127 | 25.6127 | 25.4525 | 24.9056 | 18.6135 | 18.5443 | 18.3978 | 18.2553 | 18.1136 | 17.9735 | 17.8661 | 17.7595 | 17.6446 | 17.3058 | 16.7504 | 16.1803 | 15.62 | 24.1914 | 24.1866 | 24.1765 | 24.1666 | 24.0862 | 23.9374 | 23.8232 | 23.71 | 23.5879 | 23.2279 | 22.6378 | 22.0321 | 21.4368
|  | MARLBOROUGH SOUTH | CT |  |  | 25.6127 | 25.6127 | 25.6127 | 25.6127 | 25.6127 | 25.6127 | 25.6127 | 25.6127 | 25.6127 | 25.6127 | 25.6127 | 25.4525 | 24.9056 | 18.6135 | 18.5443 | 18.3978 | 18.2553 | 18.1136 | 17.9735 | 17.8661 | 17.7595 | 17.6446 | 17.3058 | 16.7504 | 16.1803 | 15.62 | 24.1914 | 24.1866 | 24.1765 | 24.1666 | 24.0862 | 23.9374 | 23.8232 | 23.71 | 23.5879 | 23.2279 | 22.6378 | 22.0321 | 21.4368
|  | MARLBOROUGH SOUTH | LW |  |  | 25.6127 | 25.6127 | 25.6127 | 25.6127 | 25.6127 | 25.6127 | 25.6127 | 25.6127 | 25.6127 | 25.6127 | 25.6127 | 25.496 | 24.9487 | 18.6163 | 18.5485 | 18.405 | 18.2656 | 18.1268 | 18.0182 | 17.9106 | 17.8041 | 17.6893 | 17.3503 | 16.7951 | 16.2249 | 15.6642 | 24.1916 | 24.1869 | 24.177 | 24.1674 | 24.1003 | 23.9848 | 23.8705 | 23.7574 | 23.6354 | 23.2752 | 22.6853 | 22.0794 | 21.4837
|  | MARLBOROUGH SOUTH | ST |  |  | 25.6127 | 25.6127 | 25.6127 | 25.6127 | 25.6127 | 25.6127 | 25.6127 | 25.6127 | 25.6127 | 25.6127 | 25.6127 | 25.6127 | 25.6127 | 18.6528 | 18.6104 | 18.5377 | 18.4482 | 18.34 | 18.265 | 18.1911 | 18.1184 | 18.0402 | 17.8121 | 17.4431 | 17.0762 | 16.7115 | 24.1941 | 24.1912 | 24.1862 | 24.18 | 24.1725 | 24.1673 | 24.1622 | 24.0913 | 24.0082 | 23.7658 | 23.3738 | 22.984 | 22.5965
|  | MARLBOROUGH SOUTH | FS |  |  | 25.6127 | 25.6127 | 25.6127 | 25.6127 | 25.6127 | 25.6127 | 25.6127 | 25.6127 | 25.6127 | 25.6127 | 25.6127 | 25.6127 | 25.6127 | 18.7246 | 18.7196 | 18.7148 | 18.6919 | 18.6646 | 18.6383 | 18.6123 | 18.579 | 18.5487 | 18.4611 | 18.3218 | 18.1898 | 18.0657 | 24.1991 | 24.1987 | 24.1984 | 24.1968 | 24.1949 | 24.1931 | 24.1913 | 24.189 | 24.1869 | 24.1809 | 24.1712 | 24.1621 | 24.0353
NURSLING GSP | ROWNHAMS | MAYBUSH | MINIMUM HEADROOM | SU 38426 14930 | YES | 33.9442 | 33.9442 | 33.9442 | 33.8685 | 33.7915 | 33.7133 | 33.6316 | 33.5057 | 33.4897 | 33.4384 | 33.2017 | 32.8968 | 31.676 | 31.92 | 31.9188 | 31.9167 | 31.8388 | 31.759 | 31.6776 | 31.5878 | 31.4537 | 31.4292 | 31.351 | 30.4936 | 28.5788 | 26.8972 | 33.4844 | 33.4844 | 33.4844 | 33.4087 | 33.3317 | 33.2535 | 33.1718 | 33.0459 | 33.0299 | 32.9787 | 32.7392 | 30.9595 | 29.4131
|  | MAYBUSH | CT |  |  | 33.9442 | 33.9442 | 33.9442 | 33.8685 | 33.7915 | 33.7133 | 33.6316 | 33.5057 | 33.4897 | 33.4384 | 33.2017 | 32.8968 | 31.676 | 31.9201 | 31.919 | 31.9171 | 31.8388 | 31.759 | 31.6776 | 31.5878 | 31.4537 | 31.4292 | 31.351 | 30.4936 | 28.5788 | 26.8972 | 33.4844 | 33.4844 | 33.4844 | 33.4087 | 33.3317 | 33.2535 | 33.1718 | 33.0459 | 33.0299 | 32.9787 | 32.7392 | 30.9595 | 29.4131
|  | MAYBUSH | LW |  |  | 33.9442 | 33.9442 | 33.9442 | 33.9442 | 33.9442 | 33.9442 | 33.9442 | 33.9442 | 33.9442 | 33.9442 | 33.9442 | 33.9442 | 32.671 | 31.92 | 31.9188 | 31.9167 | 31.914 | 31.9111 | 31.9022 | 31.894 | 31.8859 | 31.8773 | 31.8504 | 31.0922 | 29.4819 | 27.8704 | 33.4844 | 33.4844 | 33.4844 | 33.4844 | 33.4844 | 33.4844 | 33.4844 | 33.4844 | 33.4844 | 33.4844 | 33.3499 | 31.8747 | 30.3984
|  | MAYBUSH | ST |  |  | 33.9442 | 33.9442 | 33.9442 | 33.9442 | 33.9442 | 33.9442 | 33.9442 | 33.9442 | 33.9442 | 33.9442 | 33.9442 | 33.9442 | 33.9442 | 31.9204 | 31.9197 | 31.9185 | 31.9167 | 31.9146 | 31.9119 | 31.9097 | 31.9042 | 31.8984 | 31.88 | 31.8391 | 31.1277 | 30.0984 | 33.4844 | 33.4844 | 33.4844 | 33.4844 | 33.4844 | 33.4844 | 33.4844 | 33.4844 | 33.4844 | 33.4844 | 33.4844 | 33.3824 | 32.4394
|  | MAYBUSH | FS |  |  | 33.9442 | 33.9442 | 33.9442 | 33.9442 | 33.9442 | 33.9442 | 33.9442 | 33.9442 | 33.9442 | 33.9442 | 33.9442 | 33.9442 | 33.9442 | 31.9213 | 31.9211 | 31.9209 | 31.9202 | 31.9195 | 31.9185 | 31.9178 | 31.917 | 31.9147 | 31.9075 | 31.891 | 31.8705 | 31.8492 | 33.4844 | 33.4844 | 33.4844 | 33.4844 | 33.4844 | 33.4844 | 33.4844 | 33.4844 | 33.4844 | 33.4844 | 33.4844 | 33.4844 | 33.4844
MELKSHAM GSP | NORRINGTON | MELKSHAM TOWN | MINIMUM HEADROOM | ST 90170 64096 | YES | 27.8772 | 27.8557 | 26.547 | 26.4242 | 26.2849 | 26.1274 | 25.9505 | 25.7163 | 25.6528 | 25.4287 | 25.0002 | 24.4671 | 24.2055 | 29.212 | 29.0416 | 27.4752 | 27.1132 | 26.7335 | 26.281 | 25.8105 | 25.2874 | 24.9148 | 23.7804 | 21.8525 | 19.7945 | 18.0359 | 31.6175 | 31.596 | 30.2873 | 30.1576 | 30.0037 | 29.8282 | 29.6319 | 29.1607 | 28.7988 | 27.6688 | 25.7279 | 23.6004 | 21.7735
|  | MELKSHAM TOWN | CT |  |  | 27.9887 | 27.9759 | 27.1906 | 27.1215 | 27.0483 | 26.9709 | 26.8874 | 26.7857 | 26.7538 | 26.6471 | 25.481 | 24.9012 | 24.5968 | 29.353 | 29.2073 | 28.1985 | 27.9232 | 27.6424 | 27.3571 | 26.9801 | 26.5894 | 26.2483 | 25.2314 | 22.566 | 20.4616 | 18.6612 | 31.7291 | 31.7162 | 30.931 | 30.8617 | 30.7759 | 30.6858 | 30.5846 | 30.4209 | 30.1311 | 29.1186 | 26.452 | 24.2781 | 22.4095
|  | MELKSHAM TOWN | LW |  |  | 27.8772 | 27.8557 | 26.547 | 26.4242 | 26.2849 | 26.1274 | 25.9505 | 25.7163 | 25.6528 | 25.4287 | 25.0002 | 24.4671 | 24.2055 | 29.212 | 29.0416 | 27.4752 | 27.1132 | 26.7335 | 26.281 | 25.8105 | 25.2874 | 24.9148 | 23.7804 | 21.8525 | 19.7945 | 18.0359 | 31.6175 | 31.596 | 30.2873 | 30.1576 | 30.0037 | 29.8282 | 29.6319 | 29.1607 | 28.7988 | 27.6688 | 25.7279 | 23.6004 | 21.7735
|  | MELKSHAM TOWN | ST |  |  | 28.0445 | 28.0359 | 27.5124 | 27.4663 | 27.4168 | 27.3641 | 27.3066 | 27.2349 | 27.2051 | 27.0923 | 26.9308 | 26.6248 | 26.4458 | 29.4772 | 29.3222 | 28.6518 | 28.4349 | 28.178 | 27.9527 | 27.7239 | 27.4549 | 27.2142 | 26.4873 | 25.3267 | 24.0388 | 22.886 | 31.7848 | 31.7763 | 31.2528 | 31.2066 | 31.1546 | 31.0913 | 31.0234 | 30.9398 | 30.8972 | 30.3707 | 29.2149 | 27.9317 | 26.7426
|  | MELKSHAM TOWN | FS |  |  | 28.1003 | 28.096 | 27.8343 | 27.8127 | 27.7909 | 27.769 | 27.7468 | 27.7237 | 27.7087 | 27.6462 | 27.5742 | 27.4089 | 27.2256 | 29.7862 | 29.657 | 29.3824 | 29.3268 | 29.2641 | 29.1884 | 29.1129 | 29.022 | 28.9252 | 28.6257 | 28.1743 | 27.6533 | 27.135 | 31.8406 | 31.8363 | 31.5746 | 31.553 | 31.5313 | 31.5093 | 31.4871 | 31.464 | 31.449 | 31.3866 | 31.3021 | 31.1153 | 30.9117
LOVEDEAN GSP | HAVANT | MEYRICK ROAD | MINIMUM HEADROOM | SU 70849 06469 | YES | 28.564 | 28.5589 | 28.5499 | 28.4072 | 28.2533 | 28.0794 | 27.9007 | 27.6422 | 27.5789 | 27.373 | 26.6102 | 24.2924 | 22.2603 | 27.0549 | 27.0456 | 27.0289 | 26.8796 | 26.7133 | 26.5152 | 26.3127 | 26.0292 | 25.9391 | 25.3716 | 23.009 | 20.3374 | 17.9551 | 27.1228 | 27.1185 | 27.1107 | 26.9691 | 26.8172 | 26.6472 | 26.4724 | 26.218 | 26.159 | 25.4544 | 23.0712 | 20.3988 | 18.0158
|  | MEYRICK ROAD | CT |  |  | 28.564 | 28.5589 | 28.5499 | 28.5373 | 28.5211 | 28.5052 | 28.4771 | 28.4474 | 28.4158 | 28.3185 | 27.7897 | 25.7564 | 23.7453 | 27.0549 | 27.0456 | 27.0289 | 27.0055 | 26.9757 | 26.9464 | 26.8945 | 26.8398 | 26.7814 | 26.4013 | 24.2022 | 21.8149 | 19.4538 | 27.1228 | 27.1185 | 27.1107 | 27.0998 | 27.0858 | 27.0721 | 27.0479 | 27.0223 | 26.995 | 26.4851 | 24.2644 | 21.8763 | 19.5145
|  | MEYRICK ROAD | LW |  |  | 28.5653 | 28.5609 | 28.5533 | 28.4072 | 28.2533 | 28.0794 | 27.9007 | 27.6422 | 27.5789 | 27.373 | 26.6102 | 24.2924 | 22.2603 | 27.0573 | 27.0492 | 27.0352 | 26.8796 | 26.7133 | 26.5152 | 26.3127 | 26.0292 | 25.9391 | 25.3716 | 23.009 | 20.3374 | 17.9551 | 27.1239 | 27.1202 | 27.1136 | 26.9691 | 26.8172 | 26.6472 | 26.4724 | 26.218 | 26.159 | 25.4544 | 23.0712 | 20.3988 | 18.0158
|  | MEYRICK ROAD | ST |  |  | 28.5781 | 28.5656 | 28.562 | 28.5557 | 28.5466 | 28.5292 | 28.5121 | 28.4921 | 28.4704 | 28.4029 | 28.2958 | 28.0703 | 26.7838 | 27.0809 | 27.0579 | 27.0513 | 27.0396 | 27.0229 | 26.9908 | 26.9592 | 26.9221 | 26.8821 | 26.7576 | 26.0803 | 24.5316 | 23.0212 | 27.135 | 27.1242 | 27.1211 | 27.1157 | 27.1079 | 27.0928 | 27.0781 | 27.0608 | 27.0421 | 26.9839 | 26.1603 | 24.5939 | 23.083
|  | MEYRICK ROAD | FS |  |  | 28.5797 | 28.5684 | 28.5668 | 28.5636 | 28.5594 | 28.553 | 28.547 | 28.5397 | 28.5312 | 28.5047 | 28.4614 | 28.4139 | 28.3655 | 27.0839 | 27.063 | 27.0601 | 27.0542 | 27.0464 | 27.0346 | 27.0235 | 27.01 | 26.9943 | 26.9454 | 26.8656 | 26.7779 | 26.6885 | 27.1364 | 27.1266 | 27.1253 | 27.1225 | 27.1188 | 27.1133 | 27.1081 | 27.1018 | 27.0945 | 27.0717 | 27.0344 | 26.9934 | 26.9516
BRAMLEY (ANDO-THAT) | ANDOVER BSP | MIDDLE WALLOP | MINIMUM HEADROOM | SU 30984 40155 | YES | 5.6703 | 5.65 | 5.6068 | 5.5108 | 5.3949 | 5.2756 | 5.1499 | 4.9685 | 4.9124 | 4.7283 | 4.4082 | 3.9019 | 3.7117 | 2.5372 | 2.515 | 2.468 | 2.3701 | 2.2511 | 2.1289 | 2.0005 | 1.8168 | 1.7584 | 1.5677 | 1.2278 | 0.69402 | 0.47665 | 2.8335 | 2.8108 | 2.7626 | 2.6641 | 2.544 | 2.421 | 2.2916 | 2.1071 | 2.0477 | 1.8541 | 1.5183 | 0.99587 | 0.78971
|  | MIDDLE WALLOP | CT |  |  | 5.6703 | 5.65 | 5.6068 | 5.5641 | 5.5208 | 5.4772 | 5.4412 | 5.4009 | 5.3649 | 5.2551 | 5.0221 | 4.7762 | 4.584 | 2.5372 | 2.515 | 2.468 | 2.4216 | 2.3747 | 2.3274 | 2.2892 | 2.2468 | 2.2085 | 2.0921 | 1.8359 | 1.5624 | 1.3432 | 2.8335 | 2.8108 | 2.7626 | 2.7149 | 2.6668 | 2.6184 | 2.5793 | 2.536 | 2.4967 | 2.3774 | 2.1288 | 1.8667 | 1.6586
|  | MIDDLE WALLOP | LW |  |  | 5.6758 | 5.6584 | 5.6215 | 5.5108 | 5.3949 | 5.2756 | 5.1499 | 4.9685 | 4.9124 | 4.7283 | 4.4082 | 3.9019 | 3.7117 | 2.5431 | 2.5242 | 2.484 | 2.3701 | 2.2511 | 2.1289 | 2.0005 | 1.8168 | 1.7584 | 1.5677 | 1.2278 | 0.69402 | 0.47665 | 2.8397 | 2.8202 | 2.779 | 2.6641 | 2.544 | 2.421 | 2.2916 | 2.1071 | 2.0477 | 1.8541 | 1.5183 | 0.99587 | 0.78971
|  | MIDDLE WALLOP | ST |  |  | 5.6812 | 5.6685 | 5.6467 | 5.6194 | 5.5859 | 5.565 | 5.5434 | 5.5156 | 5.4895 | 5.4049 | 5.272 | 5.0844 | 4.9462 | 2.549 | 2.5352 | 2.5115 | 2.4818 | 2.4455 | 2.4229 | 2.3996 | 2.3699 | 2.3418 | 2.2521 | 2.1119 | 1.9143 | 1.7585 | 2.8457 | 2.8315 | 2.8072 | 2.7767 | 2.7395 | 2.7164 | 2.6925 | 2.6622 | 2.6334 | 2.5419 | 2.3985 | 2.2005 | 2.052
|  | MIDDLE WALLOP | FS |  |  | 5.7031 | 5.7018 | 5.7005 | 5.6946 | 5.6875 | 5.6806 | 5.6736 | 5.6646 | 5.6546 | 5.6227 | 5.5767 | 5.5147 | 5.4554 | 2.5729 | 2.5714 | 2.57 | 2.5636 | 2.5559 | 2.5483 | 2.5408 | 2.531 | 2.5202 | 2.486 | 2.4363 | 2.3709 | 2.3082 | 2.8702 | 2.8687 | 2.8673 | 2.8607 | 2.8528 | 2.845 | 2.8373 | 2.8272 | 2.8162 | 2.7812 | 2.7304 | 2.6638 | 2.6001
BRAMLEY (FLEE) | FERNHURST | MIDHURST | MINIMUM HEADROOM | SU 88127 19555 | YES | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 41.0682 | 41.066 | 41.0614 | 41.057 | 41.0526 | 41.0404 | 41.0284 | 41.0164 | 41.0036 | 40.9656 | 40.9034 | 40.2821 | 39.4887 | 42.6084 | 42.6069 | 42.6035 | 42.6003 | 42.597 | 42.5882 | 42.5794 | 42.5707 | 42.5613 | 42.5336 | 42.4883 | 41.7087 | 40.9178
|  | MIDHURST | CT |  |  | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 41.0683 | 41.0663 | 41.0619 | 41.0576 | 41.0534 | 41.0492 | 41.0371 | 41.0252 | 41.0123 | 40.9744 | 40.9122 | 40.3931 | 39.6002 | 42.6086 | 42.6071 | 42.6039 | 42.6007 | 42.5977 | 42.5946 | 42.5858 | 42.5771 | 42.5677 | 42.54 | 42.4947 | 41.8194 | 41.0289
|  | MIDHURST | LW |  |  | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 41.0682 | 41.066 | 41.0614 | 41.057 | 41.0526 | 41.0404 | 41.0284 | 41.0164 | 41.0036 | 40.9656 | 40.9034 | 40.2821 | 39.4887 | 42.6084 | 42.6069 | 42.6035 | 42.6003 | 42.597 | 42.5882 | 42.5794 | 42.5707 | 42.5613 | 42.5336 | 42.4883 | 41.7087 | 40.9178
|  | MIDHURST | ST |  |  | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 41.0794 | 41.0693 | 41.0678 | 41.0659 | 41.0636 | 41.0569 | 41.0504 | 41.0422 | 41.0335 | 41.0079 | 40.9666 | 40.9254 | 40.8495 | 42.6166 | 42.6093 | 42.6082 | 42.6068 | 42.6051 | 42.6003 | 42.5955 | 42.5895 | 42.5831 | 42.5645 | 42.5343 | 42.5043 | 42.2744
|  | MIDHURST | FS |  |  | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 39.0918 | 41.0808 | 41.0715 | 41.0714 | 41.0708 | 41.0701 | 41.068 | 41.0658 | 41.063 | 41.0596 | 41.0498 | 41.0342 | 41.0194 | 41.0054 | 42.6177 | 42.6109 | 42.6108 | 42.6104 | 42.6099 | 42.6083 | 42.6067 | 42.6047 | 42.6022 | 42.595 | 42.5836 | 42.5728 | 42.5627
AXMINSTER | YEOVIL BSP | MILBORNE PORT | MINIMUM HEADROOM | ST 67929 19741 | YES | 1.6061 | 1.604 | 1.5997 | 1.4359 | 1.267 | 1.059 | 0.84503 | 0.53893 | 0.46328 | 0.22166 | -0.16109 | -0.72249 | -0.94499 | 1.7009 | 1.6985 | 1.6935 | 1.529 | 1.3595 | 1.1457 | 0.92603 | 0.61427 | 0.53252 | 0.27283 | -0.14248 | -0.74054 | -0.99915 | 1.837 | 1.8346 | 1.8294 | 1.6649 | 1.4953 | 1.2807 | 1.0604 | 0.74788 | 0.66535 | 0.40336 | -0.013711 | -0.61105 | -0.86896
|  | MILBORNE PORT | CT |  |  | 1.6061 | 1.604 | 1.5997 | 1.5954 | 1.5911 | 1.5869 | 1.5512 | 1.5157 | 1.4775 | 1.3644 | 1.1739 | 0.97438 | 0.77798 | 1.7009 | 1.6985 | 1.6935 | 1.6886 | 1.6836 | 1.6787 | 1.6372 | 1.5961 | 1.5518 | 1.4207 | 1.1983 | 0.96218 | 0.7297 | 1.837 | 1.8346 | 1.8294 | 1.8244 | 1.8194 | 1.8144 | 1.7722 | 1.7304 | 1.6853 | 1.5519 | 1.327 | 1.0915 | 0.85978
|  | MILBORNE PORT | LW |  |  | 1.6061 | 1.604 | 1.5997 | 1.4359 | 1.267 | 1.059 | 0.84503 | 0.53893 | 0.46328 | 0.22166 | -0.16109 | -0.72249 | -0.94499 | 1.7009 | 1.6985 | 1.6935 | 1.529 | 1.3595 | 1.1457 | 0.92603 | 0.61427 | 0.53252 | 0.27283 | -0.14248 | -0.74054 | -0.99915 | 1.837 | 1.8346 | 1.8294 | 1.6649 | 1.4953 | 1.2807 | 1.0604 | 0.74788 | 0.66535 | 0.40336 | -0.013711 | -0.61105 | -0.86896
|  | MILBORNE PORT | ST |  |  | 1.6074 | 1.6062 | 1.6043 | 1.6018 | 1.5989 | 1.5783 | 1.5579 | 1.5336 | 1.5076 | 1.4312 | 1.304 | 1.1753 | 1.0476 | 1.7025 | 1.7011 | 1.6988 | 1.696 | 1.6926 | 1.6687 | 1.645 | 1.6169 | 1.5867 | 1.4981 | 1.3506 | 1.2 | 1.0489 | 1.8386 | 1.8372 | 1.8349 | 1.832 | 1.8285 | 1.8042 | 1.7801 | 1.7515 | 1.7208 | 1.6307 | 1.4806 | 1.3286 | 1.178
|  | MILBORNE PORT | FS |  |  | 1.6092 | 1.609 | 1.6088 | 1.6081 | 1.6073 | 1.6009 | 1.5946 | 1.5865 | 1.5764 | 1.5467 | 1.4981 | 1.4504 | 1.4047 | 1.7046 | 1.7043 | 1.7041 | 1.7033 | 1.7023 | 1.695 | 1.6876 | 1.6783 | 1.6665 | 1.6321 | 1.5757 | 1.5204 | 1.4674 | 1.8407 | 1.8405 | 1.8403 | 1.8394 | 1.8385 | 1.8309 | 1.8235 | 1.814 | 1.802 | 1.767 | 1.7096 | 1.6533 | 1.5994
BRAMLEY (FLEE) | ALDERSHOT BSP | MILFORD | MINIMUM HEADROOM | SU 94719 43018 | YES | 36.3957 | 36.3861 | 36.3683 | 36.3528 | 36.3382 | 36.3236 | 36.312 | 36.2823 | 36.2669 | 36.2201 | 36.0879 | 35.3931 | 34.7144 | 33.7708 | 33.7532 | 33.7203 | 33.6917 | 33.6648 | 33.6377 | 33.6175 | 33.5973 | 33.5759 | 33.2863 | 32.4796 | 31.6611 | 30.8616 | 35.5892 | 35.5809 | 35.5656 | 35.5522 | 35.5396 | 35.527 | 35.4909 | 35.3456 | 35.1922 | 34.745 | 33.9996 | 33.2434 | 32.5047
|  | MILFORD | CT |  |  | 36.3957 | 36.3861 | 36.3683 | 36.3528 | 36.3382 | 36.3236 | 36.3126 | 36.3016 | 36.2901 | 36.2563 | 36.0879 | 35.3931 | 34.7144 | 33.7708 | 33.7532 | 33.7203 | 33.6917 | 33.6648 | 33.6377 | 33.6175 | 33.5973 | 33.5759 | 33.2863 | 32.4796 | 31.6611 | 30.8616 | 35.5892 | 35.5809 | 35.5656 | 35.5522 | 35.5396 | 35.527 | 35.4909 | 35.3456 | 35.1922 | 34.745 | 33.9996 | 33.2434 | 32.5047
|  | MILFORD | LW |  |  | 36.4005 | 36.3937 | 36.3816 | 36.3716 | 36.3625 | 36.3516 | 36.3406 | 36.3297 | 36.3181 | 36.2844 | 36.2282 | 35.7349 | 35.0558 | 33.7798 | 33.7672 | 33.7448 | 33.7264 | 33.7096 | 33.6895 | 33.6693 | 33.6491 | 33.6277 | 33.5654 | 32.8824 | 32.0638 | 31.2637 | 35.5934 | 35.5875 | 35.577 | 35.5684 | 35.5605 | 35.5512 | 35.5417 | 35.5323 | 35.5223 | 35.117 | 34.3718 | 33.6154 | 32.8762
|  | MILFORD | ST |  |  | 36.404 | 36.3998 | 36.3938 | 36.3746 | 36.3547 | 36.3336 | 36.312 | 36.2823 | 36.2669 | 36.2201 | 36.1625 | 36.0565 | 36.0003 | 33.7862 | 33.7785 | 33.7674 | 33.7433 | 33.718 | 33.6908 | 33.6631 | 33.6271 | 33.605 | 33.5389 | 33.4496 | 33.0648 | 32.5253 | 35.5964 | 35.5928 | 35.5875 | 35.5692 | 35.5501 | 35.53 | 35.5094 | 35.4808 | 35.4664 | 35.4227 | 35.0821 | 34.5252 | 34.0252
|  | MILFORD | FS |  |  | 36.4084 | 36.4069 | 36.4054 | 36.4036 | 36.4017 | 36.3991 | 36.3965 | 36.3932 | 36.3902 | 36.3813 | 36.367 | 36.3535 | 36.3407 | 33.7943 | 33.7915 | 33.7888 | 33.7854 | 33.782 | 33.7773 | 33.7724 | 33.7663 | 33.7606 | 33.7444 | 33.7179 | 33.6929 | 33.6694 | 35.6001 | 35.5988 | 35.5976 | 35.596 | 35.5944 | 35.5922 | 35.5899 | 35.5871 | 35.5844 | 35.5768 | 35.5644 | 35.5528 | 35.5418
MANNINGTON GSP | ARNEWOOD | MILFORD-ON-SEA | MINIMUM HEADROOM | SZ 28252 93347 | YES | 20.0767 | 20.0767 | 20.0767 | 20.0605 | 20.0437 | 20.0263 | 20.0081 | 19.9806 | 19.9768 | 19.9638 | 19.9423 | 19.4758 | 18.6821 | 18.2394 | 18.2394 | 18.2394 | 18.2232 | 18.2065 | 18.189 | 18.1663 | 18.1293 | 18.1163 | 17.6462 | 16.7003 | 15.7011 | 14.7759 | 19.0338 | 19.0338 | 19.0338 | 19.0176 | 19.0009 | 18.9834 | 18.9653 | 18.9378 | 18.934 | 18.9209 | 18.7356 | 17.7353 | 16.7992
|  | MILFORD-ON-SEA | CT |  |  | 20.0767 | 20.0767 | 20.0767 | 20.0767 | 20.0767 | 20.0767 | 20.0767 | 20.0767 | 20.0767 | 20.0767 | 20.0767 | 19.7597 | 18.9692 | 18.2394 | 18.2394 | 18.2394 | 18.2394 | 18.2394 | 18.2394 | 18.2394 | 18.2306 | 18.2213 | 17.8759 | 16.9515 | 16.0016 | 15.0797 | 19.0338 | 19.0338 | 19.0338 | 19.0338 | 19.0338 | 19.0338 | 19.0338 | 19.0338 | 19.0338 | 19.0338 | 18.9865 | 18.0372 | 17.1043
|  | MILFORD-ON-SEA | LW |  |  | 20.0767 | 20.0767 | 20.0767 | 20.0605 | 20.0437 | 20.0263 | 20.0081 | 19.9806 | 19.9768 | 19.9638 | 19.9423 | 19.4758 | 18.6821 | 18.2394 | 18.2394 | 18.2394 | 18.2232 | 18.2065 | 18.189 | 18.1663 | 18.1293 | 18.1163 | 17.6462 | 16.7003 | 15.7011 | 14.7759 | 19.0338 | 19.0338 | 19.0338 | 19.0176 | 19.0009 | 18.9834 | 18.9653 | 18.9378 | 18.934 | 18.9209 | 18.7356 | 17.7353 | 16.7992
|  | MILFORD-ON-SEA | ST |  |  | 20.0767 | 20.0767 | 20.0767 | 20.0767 | 20.0767 | 20.0767 | 20.0767 | 20.0767 | 20.0767 | 20.0767 | 20.0767 | 20.0767 | 20.0767 | 18.2394 | 18.2394 | 18.2394 | 18.2394 | 18.2394 | 18.2394 | 18.2394 | 18.2394 | 18.2333 | 18.2159 | 17.7121 | 17.0993 | 16.5003 | 19.0338 | 19.0338 | 19.0338 | 19.0338 | 19.0338 | 19.0338 | 19.0338 | 19.0338 | 19.0338 | 19.0338 | 19.0338 | 19.0338 | 18.5362
|  | MILFORD-ON-SEA | FS |  |  | 20.0767 | 20.0767 | 20.0767 | 20.0767 | 20.0767 | 20.0767 | 20.0767 | 20.0767 | 20.0767 | 20.0767 | 20.0767 | 20.0767 | 20.0767 | 18.2394 | 18.2394 | 18.2394 | 18.2394 | 18.2394 | 18.2394 | 18.2394 | 18.2394 | 18.2394 | 18.2394 | 18.2394 | 18.2315 | 18.2221 | 19.0338 | 19.0338 | 19.0338 | 19.0338 | 19.0338 | 19.0338 | 19.0338 | 19.0338 | 19.0338 | 19.0338 | 19.0338 | 19.0338 | 19.0338
MANNINGTON GSP | MANNINGTON BSP | MILL LANE | MINIMUM HEADROOM | SU 14691 05633 | YES | 45.6533 | 45.6397 | 44.8099 | 44.4835 | 44.1466 | 43.7953 | 43.431 | 42.9081 | 42.8172 | 42.5113 | 42.023 | 41.2422 | 41.0416 | 42.2171 | 42.2008 | 41.3653 | 41.0334 | 40.6889 | 40.3228 | 39.9431 | 39.4053 | 39.2972 | 38.9388 | 37.612 | 35.798 | 34.5854 | 43.9733 | 43.9597 | 43.1299 | 42.8035 | 42.4666 | 42.1153 | 41.751 | 41.2281 | 41.1372 | 40.8313 | 40.343 | 38.9006 | 37.6911
|  | MILL LANE | CT |  |  | 45.7241 | 45.7159 | 45.218 | 45.1765 | 45.1344 | 45.0917 | 45.0481 | 45.0011 | 44.9836 | 44.9288 | 44.2848 | 44.0204 | 43.8541 | 42.2852 | 42.273 | 41.7664 | 41.7164 | 41.6638 | 41.6086 | 41.5495 | 41.4876 | 41.4529 | 41.3457 | 39.6839 | 38.3868 | 37.2086 | 44.0441 | 44.0359 | 43.538 | 43.4965 | 43.4544 | 43.4117 | 43.3681 | 43.3211 | 43.3036 | 43.2488 | 42.6048 | 41.49 | 40.3149
|  | MILL LANE | LW |  |  | 45.6533 | 45.6397 | 44.8099 | 44.4835 | 44.1466 | 43.7953 | 43.431 | 42.9081 | 42.8172 | 42.5113 | 42.023 | 41.2422 | 41.0416 | 42.2171 | 42.2008 | 41.3653 | 41.0334 | 40.6889 | 40.3228 | 39.9431 | 39.4053 | 39.2972 | 38.9388 | 37.612 | 35.798 | 34.5854 | 43.9733 | 43.9597 | 43.1299 | 42.8035 | 42.4666 | 42.1153 | 41.751 | 41.2281 | 41.1372 | 40.8313 | 40.343 | 38.9006 | 37.6911
|  | MILL LANE | ST |  |  | 45.7594 | 45.754 | 45.422 | 45.3944 | 45.3662 | 45.3376 | 45.3082 | 45.2762 | 45.2631 | 45.2182 | 45.1476 | 45.0585 | 44.9781 | 42.3243 | 42.317 | 41.9819 | 41.9503 | 41.9161 | 41.8763 | 41.8354 | 41.7933 | 41.7684 | 41.6872 | 41.5745 | 41.0845 | 40.3471 | 44.0794 | 44.074 | 43.742 | 43.7144 | 43.6862 | 43.6576 | 43.6282 | 43.5962 | 43.5831 | 43.5382 | 43.4676 | 43.3785 | 43.2981
|  | MILL LANE | FS |  |  | 45.7948 | 45.7921 | 45.6261 | 45.6125 | 45.5988 | 45.5852 | 45.5715 | 45.5577 | 45.5515 | 45.5307 | 45.5 | 45.4668 | 45.4204 | 42.3627 | 42.3598 | 42.1937 | 42.1791 | 42.1638 | 42.1461 | 42.1283 | 42.1098 | 42.099 | 42.0641 | 42.0172 | 41.9703 | 41.911 | 44.1148 | 44.1121 | 43.9461 | 43.9325 | 43.9188 | 43.9052 | 43.8915 | 43.8777 | 43.8715 | 43.8507 | 43.82 | 43.7868 | 43.7404
COWLEY GSP | DRAYTON BSP | MILTON | MINIMUM HEADROOM | SU 49992 92060 | NO | 58.5253 | 58.5253 | 58.5253 | 58.5244 | 58.5225 | 58.5045 | 58.4482 | 58.0786 | 57.3744 | 56.0259 | 54.6411 | 53.4547 | 52.377 | 56.6331 | 56.6183 | 56.5883 | 56.4798 | 56.3418 | 56.1886 | 55.4738 | 54.6811 | 53.9306 | 52.4938 | 51.0202 | 49.6532 | 48.4035 | 50.9564 | 50.9564 | 50.9564 | 50.9555 | 50.9536 | 50.9507 | 50.9466 | 50.9384 | 50.937 | 50.9297 | 50.9121 | 50.8778 | 50.8755
|  | MILTON | CT |  |  | 58.5253 | 58.5253 | 58.5253 | 58.525 | 58.5245 | 58.5045 | 58.4482 | 58.0786 | 57.3744 | 56.0259 | 54.6411 | 53.4547 | 52.377 | 56.6331 | 56.6183 | 56.5883 | 56.4798 | 56.3418 | 56.1886 | 55.4738 | 54.6811 | 53.9306 | 52.4938 | 51.0202 | 49.6532 | 48.4035 | 50.9564 | 50.9564 | 50.9564 | 50.9562 | 50.9556 | 50.9549 | 50.9537 | 50.9513 | 50.9508 | 50.9485 | 50.9289 | 50.9071 | 50.9003
|  | MILTON | LW |  |  | 58.5253 | 58.5253 | 58.5253 | 58.5244 | 58.5225 | 58.5182 | 58.4589 | 58.2819 | 57.5767 | 56.2233 | 54.8417 | 53.6428 | 52.5695 | 56.6356 | 56.6222 | 56.5982 | 56.5154 | 56.3866 | 56.2391 | 55.6972 | 54.8986 | 54.1472 | 52.7054 | 51.2342 | 49.8763 | 48.6309 | 50.9564 | 50.9564 | 50.9564 | 50.9555 | 50.9536 | 50.9507 | 50.9466 | 50.9384 | 50.937 | 50.9297 | 50.9121 | 50.8778 | 50.8755
|  | MILTON | ST |  |  | 58.5253 | 58.5253 | 58.5253 | 58.5251 | 58.5247 | 58.5241 | 58.5233 | 58.5077 | 58.467 | 58.1295 | 57.1897 | 56.4151 | 55.7162 | 56.6623 | 56.632 | 56.6183 | 56.6014 | 56.5391 | 56.4412 | 56.3291 | 56.204 | 55.7425 | 54.7356 | 53.7345 | 52.9105 | 52.1664 | 50.9564 | 50.9564 | 50.9564 | 50.9562 | 50.9559 | 50.9553 | 50.9544 | 50.9525 | 50.9516 | 50.9467 | 50.9402 | 50.9175 | 50.9092
|  | MILTON | FS |  |  | 58.5253 | 58.5253 | 58.5253 | 58.5253 | 58.5253 | 58.5252 | 58.5252 | 58.5251 | 58.5248 | 58.523 | 58.5216 | 58.5148 | 58.4922 | 56.669 | 56.6434 | 56.6381 | 56.631 | 56.6214 | 56.6106 | 56.5987 | 56.5659 | 56.5182 | 56.4246 | 56.3318 | 56.2531 | 56.1836 | 50.9564 | 50.9564 | 50.9564 | 50.9564 | 50.9564 | 50.9564 | 50.9564 | 50.9563 | 50.956 | 50.9542 | 50.9528 | 50.946 | 50.9394
MANNINGTON GSP | SHAFTESBURY BSP | MINCHINGTON | MINIMUM HEADROOM | ST 96164 14520 | YES | 6.114 | 6.114 | 6.114 | 6.0194 | 5.9231 | 5.8253 | 5.7231 | 5.5655 | 5.5456 | 5.4359 | 5.0162 | 4.5775 | 4.3721 | 5 | 5 | 5 | 4.9053 | 4.8091 | 4.7112 | 4.609 | 4.4515 | 4.4315 | 4.3674 | 4.0713 | 3.7607 | 3.681 | 5.5289 | 5.5262 | 5.5205 | 5.4204 | 5.3186 | 5.2153 | 5.0902 | 4.91 | 4.8657 | 4.7166 | 4.2685 | 3.8005 | 3.5663
|  | MINCHINGTON | CT |  |  | 6.114 | 6.114 | 6.114 | 6.0194 | 5.9231 | 5.8253 | 5.7231 | 5.5655 | 5.5456 | 5.4359 | 5.0162 | 4.5775 | 4.3721 | 5 | 5 | 5 | 4.9053 | 4.8091 | 4.7112 | 4.609 | 4.4515 | 4.4315 | 4.3674 | 4.0713 | 3.7607 | 3.681 | 5.5289 | 5.5262 | 5.5205 | 5.4204 | 5.3186 | 5.2153 | 5.0902 | 4.91 | 4.8657 | 4.7166 | 4.2685 | 3.8005 | 3.5663
|  | MINCHINGTON | LW |  |  | 6.114 | 6.114 | 6.114 | 6.0534 | 5.9908 | 5.9255 | 5.8578 | 5.7549 | 5.7406 | 5.628 | 5.4313 | 5.1192 | 4.9825 | 5 | 5 | 5 | 4.9394 | 4.8768 | 4.8114 | 4.7437 | 4.6408 | 4.6266 | 4.5777 | 4.5047 | 4.3206 | 4.3099 | 5.5289 | 5.5262 | 5.5205 | 5.4544 | 5.3863 | 5.2979 | 5.2073 | 5.0818 | 5.0432 | 4.9045 | 4.6795 | 4.338 | 4.1725
|  | MINCHINGTON | ST |  |  | 6.114 | 6.114 | 6.114 | 6.0547 | 5.9944 | 5.9328 | 5.8692 | 5.7708 | 5.7374 | 5.6309 | 5.4761 | 5.0867 | 4.9159 | 5 | 5 | 5 | 4.9406 | 4.8803 | 4.8188 | 4.7552 | 4.6568 | 4.6234 | 4.5168 | 4.4312 | 4.1242 | 4.0354 | 5.5306 | 5.5291 | 5.5266 | 5.4641 | 5.4 | 5.3282 | 5.2545 | 5.1406 | 5.0906 | 4.9354 | 4.7514 | 4.3431 | 4.1535
|  | MINCHINGTON | FS |  |  | 6.114 | 6.114 | 6.114 | 6.114 | 6.114 | 6.114 | 6.114 | 6.114 | 6.114 | 6.114 | 6.114 | 6.114 | 6.114 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5.533 | 5.5328 | 5.5326 | 5.5318 | 5.5307 | 5.5267 | 5.5229 | 5.5178 | 5.5113 | 5.4926 | 5.4624 | 5.4336 | 5.4054
MINETY GSP | CIRENCESTER BSP | MINETY VILLAGE | MINIMUM HEADROOM | SU 01647 91932 | YES | 21.4736 | -33.8304 | -33.8506 | -34.0633 | -34.3922 | -34.6233 | -34.9083 | -35.3023 | -35.5689 | -36.4769 | -37.3705 | -38.1638 | -38.4586 | 19.8584 | -35.4465 | -35.4685 | -35.6256 | -36.0036 | -36.2623 | -36.5799 | -37.0124 | -37.3215 | -38.3688 | -39.3737 | -40.2184 | -40.5597 | 20.6715 | -34.7507 | -35.0274 | -35.3561 | -35.7331 | -35.9913 | -36.3082 | -36.74 | -37.0482 | -38.0927 | -39.0953 | -39.939 | -40.2794
|  | MINETY VILLAGE | CT |  |  | 21.4761 | 21.4682 | 21.4511 | 21.372 | 21.1185 | 20.848 | 20.6406 | 20.3788 | 20.1329 | 19.3149 | 18.4232 | 17.8429 | 17.4999 | 19.8612 | 19.8526 | 19.8338 | 19.8075 | 19.5333 | 19.2175 | 18.9774 | 18.6772 | 18.3888 | 17.4314 | 16.4285 | 15.7969 | 15.4073 | 20.7063 | 20.598 | 20.362 | 20.099 | 19.8033 | 19.4884 | 19.249 | 18.9495 | 18.662 | 17.7074 | 16.7067 | 16.0761 | 15.6874
|  | MINETY VILLAGE | LW |  |  | 21.4736 | -33.8304 | -33.8506 | -34.0633 | -34.3922 | -34.6233 | -34.9083 | -35.3023 | -35.5689 | -36.4769 | -37.3705 | -38.1638 | -38.4586 | 19.8584 | -35.4465 | -35.4685 | -35.6256 | -36.0036 | -36.2623 | -36.5799 | -37.0124 | -37.3215 | -38.3688 | -39.3737 | -40.2184 | -40.5597 | 20.6715 | -34.7507 | -35.0274 | -35.3561 | -35.7331 | -35.9913 | -36.3082 | -36.74 | -37.0482 | -38.0927 | -39.0953 | -39.939 | -40.2794
|  | MINETY VILLAGE | ST |  |  | 21.4769 | 21.4705 | 21.459 | 21.4399 | 21.2831 | 21.1575 | 21.0067 | 20.8267 | 20.6478 | 20.017 | 19.4861 | 19.0004 | 18.7297 | 19.8621 | 19.8551 | 19.8424 | 19.822 | 19.7263 | 19.5806 | 19.4062 | 19.2004 | 18.9924 | 18.2622 | 17.6527 | 17.1337 | 16.8327 | 20.7176 | 20.6298 | 20.4704 | 20.2607 | 19.9957 | 19.8503 | 19.6764 | 19.4712 | 19.2637 | 18.5356 | 17.9276 | 17.4093 | 17.1089
|  | MINETY VILLAGE | FS |  |  | 21.4862 | 21.4849 | 21.4828 | 21.478 | 21.472 | 21.4674 | 21.462 | 21.4546 | 21.4413 | 21.3425 | 21.1295 | 20.8905 | 20.6669 | 19.8722 | 19.8708 | 19.8686 | 19.8633 | 19.8567 | 19.8518 | 19.846 | 19.8381 | 19.8242 | 19.759 | 19.5596 | 19.3081 | 19.074 | 20.7328 | 20.7313 | 20.7291 | 20.7238 | 20.6558 | 20.6009 | 20.5384 | 20.462 | 20.3779 | 20.0732 | 19.8292 | 19.578 | 19.3441
BRAMLEY (FLEE) | BURGHFIELD RESERVE | MORTIMER | MINIMUM HEADROOM | SU 62236 64103 | YES | 22.436 | 22.436 | 22.436 | 22.3843 | 22.3307 | 22.2751 | 22.2157 | 22.1206 | 22.108 | 22.0633 | 21.8109 | 21.5107 | 21.3836 | 20.5309 | 20.5309 | 20.5309 | 20.4792 | 20.4255 | 20.3593 | 20.1897 | 19.9864 | 19.8576 | 19.4686 | 18.6323 | 17.7259 | 17.0526 | 21.478 | 21.478 | 21.478 | 21.4263 | 21.3727 | 21.3171 | 21.2577 | 21.1626 | 21.1501 | 20.941 | 20.1133 | 19.2157 | 18.5513
|  | MORTIMER | CT |  |  | 22.436 | 22.436 | 22.436 | 22.3843 | 22.3307 | 22.2751 | 22.2157 | 22.1206 | 22.108 | 22.0633 | 21.8109 | 21.5107 | 21.3836 | 20.5309 | 20.5309 | 20.5309 | 20.4792 | 20.4255 | 20.3593 | 20.1897 | 19.9864 | 19.8576 | 19.4686 | 18.6323 | 17.7259 | 17.0526 | 21.478 | 21.478 | 21.478 | 21.4263 | 21.3727 | 21.3171 | 21.2577 | 21.1626 | 21.1501 | 20.941 | 20.1133 | 19.2157 | 18.5513
|  | MORTIMER | LW |  |  | 22.436 | 22.436 | 22.436 | 22.432 | 22.4236 | 22.4106 | 22.3924 | 22.356 | 22.3497 | 22.3177 | 22.2397 | 22.0875 | 22.0772 | 20.5309 | 20.5309 | 20.5309 | 20.5268 | 20.5185 | 20.5054 | 20.4873 | 20.4164 | 20.2939 | 19.9174 | 19.2558 | 18.4973 | 17.8897 | 21.478 | 21.478 | 21.478 | 21.474 | 21.4657 | 21.4526 | 21.4345 | 21.398 | 21.3917 | 21.3597 | 20.7339 | 19.9843 | 19.3856
|  | MORTIMER | ST |  |  | 22.436 | 22.436 | 22.436 | 22.4352 | 22.4335 | 22.4309 | 22.4271 | 22.4186 | 22.4146 | 22.3927 | 22.364 | 22.2633 | 22.2267 | 20.5309 | 20.5309 | 20.5309 | 20.53 | 20.5283 | 20.5257 | 20.522 | 20.5135 | 20.5094 | 20.4669 | 20.0484 | 19.5563 | 19.1319 | 21.478 | 21.478 | 21.478 | 21.4772 | 21.4755 | 21.4729 | 21.4691 | 21.4606 | 21.4566 | 21.4347 | 21.406 | 21.0303 | 20.6117
|  | MORTIMER | FS |  |  | 22.436 | 22.436 | 22.436 | 22.436 | 22.4359 | 22.4358 | 22.4357 | 22.4353 | 22.4339 | 22.426 | 22.4197 | 22.3897 | 22.3604 | 20.5309 | 20.5309 | 20.5309 | 20.5308 | 20.5308 | 20.5307 | 20.5305 | 20.5301 | 20.5288 | 20.5209 | 20.5146 | 20.4846 | 20.4553 | 21.478 | 21.478 | 21.478 | 21.478 | 21.4779 | 21.4778 | 21.4777 | 21.4773 | 21.4759 | 21.468 | 21.4618 | 21.4317 | 21.4024
MANNINGTON GSP | SALISBURY | NETHERHAMPTON | MINIMUM HEADROOM | SU 12478 29102 | YES | 14.2514 | 14.2514 | 14.2514 | 14.2496 | 14.2478 | 14.2451 | 14.2406 | 14.2316 | 14.2301 | 14.2067 | 14.1934 | 13.9215 | 13.6147 | 12.7365 | 12.7338 | 12.7281 | 12.7211 | 12.7122 | 12.7036 | 12.6923 | 12.6752 | 12.6662 | 12.6233 | 12.3 | 11.8941 | 11.5387 | 13.2727 | 13.2727 | 13.2727 | 13.2709 | 13.2692 | 13.2664 | 13.262 | 13.2529 | 13.2514 | 13.1611 | 12.7512 | 12.3388 | 11.9773
|  | NETHERHAMPTON | CT |  |  | 14.2514 | 14.2514 | 14.2514 | 14.2511 | 14.2505 | 14.2497 | 14.2485 | 14.2457 | 14.2453 | 14.2427 | 14.2212 | 13.9882 | 13.6766 | 12.7371 | 12.7347 | 12.7297 | 12.7241 | 12.7174 | 12.71 | 12.7019 | 12.6911 | 12.6832 | 12.6566 | 12.3585 | 11.9662 | 11.6061 | 13.2727 | 13.2727 | 13.2727 | 13.2724 | 13.2719 | 13.271 | 13.2698 | 13.2671 | 13.2666 | 13.2224 | 12.8104 | 12.4117 | 12.0453
|  | NETHERHAMPTON | LW |  |  | 14.2514 | 14.2514 | 14.2514 | 14.2504 | 14.2484 | 14.2451 | 14.2406 | 14.2316 | 14.2301 | 14.2221 | 14.2028 | 13.9215 | 13.6147 | 12.7365 | 12.7338 | 12.7281 | 12.7211 | 12.7122 | 12.7036 | 12.6923 | 12.6752 | 12.6662 | 12.6233 | 12.3 | 11.8941 | 11.5387 | 13.2727 | 13.2727 | 13.2727 | 13.2717 | 13.2697 | 13.2664 | 13.262 | 13.2529 | 13.2514 | 13.1611 | 12.7512 | 12.3388 | 11.9773
|  | NETHERHAMPTON | ST |  |  | 14.2514 | 14.2514 | 14.2514 | 14.2512 | 14.2508 | 14.2501 | 14.2492 | 14.2471 | 14.2461 | 14.2407 | 14.2336 | 14.2087 | 14.1996 | 12.7383 | 12.7368 | 12.7343 | 12.7308 | 12.7259 | 12.7217 | 12.7161 | 12.7085 | 12.7025 | 12.6875 | 12.6687 | 12.6241 | 12.4966 | 13.2727 | 13.2727 | 13.2727 | 13.2725 | 13.2721 | 13.2715 | 13.2705 | 13.2684 | 13.2674 | 13.262 | 13.2549 | 13.193 | 12.9513
|  | NETHERHAMPTON | FS |  |  | 14.2514 | 14.2514 | 14.2514 | 14.2496 | 14.2478 | 14.2461 | 14.2442 | 14.2414 | 14.2333 | 14.2067 | 14.1934 | 14.149 | 14.1109 | 12.7402 | 12.7398 | 12.7394 | 12.7364 | 12.7332 | 12.73 | 12.7264 | 12.7213 | 12.7112 | 12.6808 | 12.663 | 12.6145 | 12.5726 | 13.2727 | 13.2727 | 13.2727 | 13.2709 | 13.2692 | 13.2674 | 13.2656 | 13.2627 | 13.2546 | 13.228 | 13.2147 | 13.1704 | 13.1322
BOTLEY WOOD GSP | NETLEY COMMON BSP | NETLEY COMMON | MINIMUM HEADROOM | SU 47615 12025 | YES | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
|  | NETLEY COMMON | CT |  |  | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
|  | NETLEY COMMON | LW |  |  | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
|  | NETLEY COMMON | ST |  |  | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
|  | NETLEY COMMON | FS |  |  | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
MANNINGTON GSP | ARNEWOOD | NEW MILTON | MINIMUM HEADROOM | SZ 23049 94942 | YES | 48.7653 | 48.7545 | 48.096 | 48.0039 | 47.8954 | 47.6598 | 47.421 | 47.177 | 46.9471 | 46.2369 | 44.9467 | 43.5808 | 42.1937 | 42.4608 | 42.4483 | 41.7863 | 41.7283 | 41.6688 | 41.5985 | 41.5273 | 41.4531 | 41.4156 | 40.7967 | 39.3906 | 37.8982 | 36.3856 | 44.7351 | 44.7243 | 44.0659 | 44.0113 | 43.9561 | 43.9002 | 43.8436 | 43.7843 | 43.7618 | 43.6923 | 43.5729 | 42.2591 | 40.6438
|  | NEW MILTON | CT |  |  | 48.8214 | 48.8149 | 48.4198 | 48.3545 | 48.2699 | 48.1784 | 47.9632 | 47.7445 | 47.5378 | 46.8691 | 45.2133 | 43.7538 | 42.3645 | 42.5171 | 42.5089 | 42.1104 | 42.0745 | 42.0376 | 42 | 41.9523 | 41.9035 | 41.8753 | 41.4442 | 39.6724 | 38.0863 | 36.5717 | 44.7912 | 44.7847 | 44.3897 | 44.3571 | 44.3244 | 44.2915 | 44.2584 | 44.2244 | 44.2112 | 44.1708 | 43.6857 | 42.4598 | 40.8425
|  | NEW MILTON | LW |  |  | 48.7653 | 48.7545 | 48.096 | 48.0039 | 47.8954 | 47.6598 | 47.421 | 47.177 | 46.9471 | 46.2369 | 44.9467 | 43.5808 | 42.1937 | 42.4608 | 42.4483 | 41.7863 | 41.7283 | 41.6688 | 41.5985 | 41.5273 | 41.4531 | 41.4156 | 40.7967 | 39.3906 | 37.8982 | 36.3856 | 44.7351 | 44.7243 | 44.0659 | 44.0113 | 43.9561 | 43.9002 | 43.8436 | 43.7843 | 43.7618 | 43.6923 | 43.5729 | 42.2591 | 40.6438
|  | NEW MILTON | ST |  |  | 48.8494 | 48.8451 | 48.5818 | 48.5427 | 48.4681 | 48.3246 | 48.1801 | 48.0314 | 47.8945 | 47.4673 | 46.6304 | 45.7591 | 44.8887 | 42.545 | 42.5392 | 42.2733 | 42.2485 | 42.2224 | 42.1907 | 42.1588 | 42.1258 | 42.1063 | 42.0479 | 41.1636 | 40.21 | 39.2587 | 44.8193 | 44.815 | 44.5516 | 44.5299 | 44.508 | 44.4861 | 44.4639 | 44.4411 | 44.4319 | 44.4027 | 44.3554 | 44.3147 | 43.6451
|  | NEW MILTON | FS |  |  | 48.8775 | 48.8754 | 48.7437 | 48.7329 | 48.7221 | 48.7113 | 48.7004 | 48.6681 | 48.6139 | 48.4581 | 48.1812 | 47.8803 | 47.5451 | 42.5756 | 42.5732 | 42.4414 | 42.43 | 42.4182 | 42.405 | 42.3917 | 42.3777 | 42.3692 | 42.3437 | 42.3008 | 42.2616 | 42.1473 | 44.8473 | 44.8452 | 44.7135 | 44.7027 | 44.6919 | 44.6811 | 44.6703 | 44.6594 | 44.6549 | 44.6408 | 44.6183 | 44.6009 | 44.5729
FAWLEY GSP | COWES & WOOTTON COMMON BSP | NEWPORT | MINIMUM HEADROOM | SZ 50076 89544 | YES | 47.5077 | 47.4905 | 46.4375 | 46.0729 | 45.6979 | 45.3084 | 44.9063 | 44.3372 | 44.2354 | 43.8973 | 43.3633 | 42.083 | 40.6378 | 43.9382 | 43.9174 | 42.8579 | 42.4862 | 42.1039 | 41.6977 | 41.2799 | 40.6952 | 40.5769 | 40.1893 | 38.8703 | 36.5326 | 34.7517 | 45.5975 | 45.5802 | 44.5273 | 44.1626 | 43.7876 | 43.3982 | 42.9961 | 42.427 | 42.3252 | 41.9871 | 41.4531 | 39.3078 | 37.6012
|  | NEWPORT | CT |  |  | 47.5975 | 47.5871 | 46.9553 | 46.9031 | 46.8505 | 46.7975 | 46.744 | 46.6883 | 46.6669 | 46.601 | 45.8147 | 45.1433 | 43.7361 | 44.028 | 44.0141 | 43.3757 | 43.3164 | 43.2566 | 43.1965 | 43.1273 | 43.056 | 43.0181 | 42.9027 | 41.5261 | 39.638 | 37.8926 | 45.6872 | 45.6769 | 45.0451 | 44.9929 | 44.9403 | 44.8873 | 44.8337 | 44.778 | 44.7566 | 44.6907 | 43.9045 | 42.3983 | 40.7346
|  | NEWPORT | LW |  |  | 47.5077 | 47.4905 | 46.4375 | 46.0729 | 45.6979 | 45.3084 | 44.9063 | 44.3372 | 44.2354 | 43.8973 | 43.3633 | 42.083 | 40.6378 | 43.9382 | 43.9174 | 42.8579 | 42.4862 | 42.1039 | 41.6977 | 41.2799 | 40.6952 | 40.5769 | 40.1893 | 38.8703 | 36.5326 | 34.7517 | 45.5975 | 45.5802 | 44.5273 | 44.1626 | 43.7876 | 43.3982 | 42.9961 | 42.427 | 42.3252 | 41.9871 | 41.4531 | 39.3078 | 37.6012
|  | NEWPORT | ST |  |  | 47.6424 | 47.6354 | 47.2143 | 47.1794 | 47.1443 | 47.1089 | 47.073 | 47.0355 | 47.0202 | 46.971 | 46.8917 | 46.8144 | 46.7255 | 44.0716 | 44.0612 | 43.6344 | 43.5926 | 43.5493 | 43.5046 | 43.4604 | 43.4122 | 43.3856 | 43.3028 | 43.1733 | 42.6572 | 41.5642 | 45.7321 | 45.7252 | 45.304 | 45.2692 | 45.2341 | 45.1986 | 45.1628 | 45.1252 | 45.11 | 45.0607 | 44.9815 | 44.9042 | 44.2724
|  | NEWPORT | FS |  |  | 47.6872 | 47.6838 | 47.4732 | 47.4559 | 47.4386 | 47.4213 | 47.404 | 47.3866 | 47.3792 | 47.3557 | 47.3189 | 47.2875 | 47.2391 | 44.1207 | 44.1163 | 43.9046 | 43.8852 | 43.8656 | 43.8454 | 43.8256 | 43.8051 | 43.7933 | 43.7568 | 43.7009 | 43.6518 | 43.5868 | 45.777 | 45.7735 | 45.5629 | 45.5457 | 45.5284 | 45.5111 | 45.4938 | 45.4764 | 45.469 | 45.4455 | 45.4087 | 45.3773 | 45.3289
BRAMLEY (FLEE) | ALDERSHOT BSP | NORMANDY | MINIMUM HEADROOM | SU 93221 52894 | YES | 1.6116 | 1.6116 | 1.6116 | 1.5687 | 1.5249 | 1.4801 | 1.4329 | 1.3594 | 1.3071 | 1.0181 | 0.67412 | 0.33116 | 0.14731 | 0.99481 | 0.96279 | 0.9015 | 0.79749 | 0.6867 | 0.57221 | 0.46466 | 0.32265 | 0.23887 | -0.019645 | -0.34119 | -0.66665 | -0.83429 | 1.3348 | 1.3348 | 1.3348 | 1.2823 | 1.1501 | 1.0133 | 0.88646 | 0.72253 | 0.61498 | 0.28381 | -0.091339 | -0.4586 | -0.66495
|  | NORMANDY | CT |  |  | 1.6116 | 1.6116 | 1.6116 | 1.5687 | 1.5249 | 1.4801 | 1.4329 | 1.3594 | 1.3071 | 1.0181 | 0.67412 | 0.33116 | 0.14731 | 0.99551 | 0.96392 | 0.90358 | 0.79749 | 0.6867 | 0.57221 | 0.46466 | 0.32265 | 0.23887 | -0.019645 | -0.34119 | -0.66665 | -0.83429 | 1.3348 | 1.3348 | 1.3348 | 1.2823 | 1.1501 | 1.0133 | 0.88646 | 0.72253 | 0.61498 | 0.28381 | -0.091339 | -0.4586 | -0.66495
|  | NORMANDY | LW |  |  | 1.6116 | 1.6116 | 1.6116 | 1.6106 | 1.6086 | 1.6055 | 1.6011 | 1.5923 | 1.5627 | 1.2973 | 1.0886 | 0.90378 | 0.76391 | 0.99481 | 0.96279 | 0.9015 | 0.83643 | 0.76658 | 0.71063 | 0.64586 | 0.56857 | 0.49273 | 0.25783 | 0.071519 | -0.095771 | -0.21941 | 1.3348 | 1.3348 | 1.3348 | 1.3203 | 1.2288 | 1.1559 | 1.0718 | 0.97262 | 0.87301 | 0.56544 | 0.32554 | 0.11644 | -0.045951
|  | NORMANDY | ST |  |  | 1.6116 | 1.6116 | 1.6116 | 1.6114 | 1.611 | 1.6104 | 1.6094 | 1.6074 | 1.6064 | 1.552 | 1.4143 | 1.294 | 1.1962 | 0.99907 | 0.97523 | 0.936 | 0.88808 | 0.83076 | 0.79309 | 0.75017 | 0.70211 | 0.65015 | 0.48454 | 0.36234 | 0.25339 | 0.16605 | 1.3348 | 1.3348 | 1.3348 | 1.3346 | 1.3127 | 1.2632 | 1.2068 | 1.1441 | 1.0758 | 0.85889 | 0.69981 | 0.56376 | 0.4513
|  | NORMANDY | FS |  |  | 1.6116 | 1.6116 | 1.6116 | 1.6036 | 1.5959 | 1.588 | 1.5801 | 1.5676 | 1.5329 | 1.4218 | 1.3683 | 1.1973 | 1.0533 | 1.0251 | 1.0178 | 1.0082 | 0.98487 | 0.95999 | 0.93733 | 0.913 | 0.88107 | 0.82615 | 0.65156 | 0.55248 | 0.34911 | 0.17633 | 1.3348 | 1.3348 | 1.3348 | 1.3269 | 1.3191 | 1.3113 | 1.3033 | 1.2909 | 1.2561 | 1.1367 | 1.0231 | 0.80932 | 0.62733
NURSLING GSP | ROWNHAMS | NORTH BADDESLEY | MINIMUM HEADROOM | SU 38080 20568 | YES | 25.1698 | 25.1698 | 44.6698 | 44.5951 | 44.5187 | 44.4403 | 44.3586 | 44.2309 | 44.1869 | 44.0416 | 43.9188 | 43.5415 | 43.4204 | 23.1593 | 23.1537 | 41.8949 | 41.8309 | 41.7504 | 41.667 | 41.5805 | 41.4481 | 41.3992 | 41.2394 | 40.5031 | 39.5865 | 38.7819 | 24.0681 | 24.0681 | 43.5681 | 43.4934 | 43.417 | 43.3386 | 43.257 | 43.1293 | 43.0739 | 42.5786 | 41.7407 | 40.842 | 40.0582
|  | NORTH BADDESLEY | CT |  |  | 25.1698 | 25.1698 | 44.6698 | 44.66 | 44.6495 | 44.6382 | 44.6256 | 44.6044 | 44.6015 | 44.5895 | 44.5135 | 44.4307 | 44.4059 | 23.161 | 23.1564 | 41.8997 | 41.8834 | 41.8661 | 41.848 | 41.8284 | 41.8004 | 41.7902 | 41.5778 | 40.7195 | 39.8347 | 39.0128 | 24.0681 | 24.0681 | 43.5681 | 43.5584 | 43.5478 | 43.5366 | 43.524 | 43.4654 | 43.3026 | 42.8198 | 41.958 | 41.085 | 40.2838
|  | NORTH BADDESLEY | LW |  |  | 25.1698 | 25.1698 | 44.6698 | 44.6595 | 44.6465 | 44.6306 | 44.6116 | 44.5779 | 44.5725 | 44.5484 | 44.4958 | 44.3878 | 44.3791 | 23.1593 | 23.1537 | 41.8949 | 41.876 | 41.8544 | 41.8313 | 41.8053 | 41.7648 | 41.7522 | 41.3376 | 40.5031 | 39.5865 | 38.7819 | 24.0681 | 24.0681 | 43.5681 | 43.5578 | 43.5449 | 43.529 | 43.4225 | 43.2389 | 43.0739 | 42.5786 | 41.7407 | 40.842 | 40.0582
|  | NORTH BADDESLEY | ST |  |  | 25.1698 | 25.1698 | 44.6698 | 44.5951 | 44.5187 | 44.4403 | 44.3586 | 44.2309 | 44.1869 | 44.0416 | 43.9188 | 43.5415 | 43.4204 | 23.1643 | 23.1617 | 41.909 | 41.8309 | 41.7504 | 41.667 | 41.5805 | 41.4481 | 41.3992 | 41.2394 | 41.0513 | 40.1664 | 39.5427 | 24.0681 | 24.0681 | 43.5681 | 43.4934 | 43.417 | 43.3386 | 43.257 | 43.1293 | 43.0853 | 42.94 | 42.2939 | 41.4068 | 40.7808
|  | NORTH BADDESLEY | FS |  |  | 25.1698 | 25.1698 | 44.6698 | 44.6698 | 44.6697 | 44.6697 | 44.6696 | 44.6694 | 44.6686 | 44.6643 | 44.6608 | 44.6444 | 44.6283 | 23.1672 | 23.1663 | 41.916 | 41.9148 | 41.9132 | 41.9115 | 41.9097 | 41.9075 | 41.9048 | 41.8948 | 41.8823 | 41.8573 | 41.8332 | 24.0681 | 24.0681 | 43.5681 | 43.5681 | 43.5681 | 43.568 | 43.5679 | 43.5677 | 43.567 | 43.5627 | 43.5592 | 43.5427 | 43.5267
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | NORTH FAREHAM | MINIMUM HEADROOM | SU 56427 07430 | YES | 16.6451 | 16.6451 | 16.6451 | 16.6055 | 16.5653 | 16.5242 | 16.4818 | 16.4162 | 16.3939 | 16.3228 | 16.2643 | 16.0072 | 15.0688 | 14.7341 | 14.7323 | 14.7287 | 14.689 | 14.6456 | 14.5975 | 14.5482 | 14.4758 | 14.4462 | 14.3379 | 13.2948 | 12.1318 | 11.0443 | 15.8467 | 15.8449 | 15.8413 | 15.8016 | 15.7582 | 15.7101 | 15.6607 | 15.5883 | 15.5587 | 15.4659 | 14.6478 | 13.4809 | 12.3896
|  | NORTH FAREHAM | CT |  |  | 16.6451 | 16.6451 | 16.6451 | 16.6451 | 16.6451 | 16.6451 | 16.6451 | 16.6451 | 16.6451 | 16.6451 | 16.6451 | 16.3617 | 15.4288 | 14.7341 | 14.7323 | 14.7287 | 14.7251 | 14.7215 | 14.7179 | 14.7079 | 14.698 | 14.6873 | 14.5928 | 13.5851 | 12.4926 | 11.4106 | 15.8467 | 15.8449 | 15.8413 | 15.8377 | 15.8341 | 15.8305 | 15.8205 | 15.8105 | 15.7998 | 15.7676 | 14.9378 | 13.8419 | 12.756
|  | NORTH FAREHAM | LW |  |  | 16.6451 | 16.6451 | 16.6451 | 16.6151 | 16.5841 | 16.5518 | 16.5183 | 16.4674 | 16.4604 | 16.4362 | 16.4001 | 16.0072 | 15.0688 | 14.7349 | 14.7335 | 14.7308 | 14.6981 | 14.6644 | 14.622 | 14.5785 | 14.5177 | 14.5 | 14.3379 | 13.2948 | 12.1318 | 11.0443 | 15.8475 | 15.8461 | 15.8434 | 15.8107 | 15.777 | 15.7346 | 15.691 | 15.6302 | 15.6124 | 15.5561 | 14.6478 | 13.4809 | 12.3896
|  | NORTH FAREHAM | ST |  |  | 16.6451 | 16.6451 | 16.6451 | 16.6055 | 16.5653 | 16.5242 | 16.4818 | 16.4162 | 16.3939 | 16.3228 | 16.2643 | 16.0596 | 16.0003 | 14.7403 | 14.7334 | 14.7312 | 14.689 | 14.6456 | 14.5975 | 14.5482 | 14.4758 | 14.4462 | 14.3474 | 13.8925 | 12.9795 | 12.2209 | 15.8529 | 15.846 | 15.8439 | 15.8016 | 15.7582 | 15.7101 | 15.6607 | 15.5883 | 15.5587 | 15.4659 | 15.2388 | 14.3323 | 13.5715
|  | NORTH FAREHAM | FS |  |  | 16.6451 | 16.6451 | 16.6451 | 16.6451 | 16.6451 | 16.6451 | 16.6451 | 16.6451 | 16.6451 | 16.6451 | 16.6451 | 16.6451 | 16.6451 | 14.7425 | 14.7423 | 14.7422 | 14.7417 | 14.7412 | 14.739 | 14.7367 | 14.7339 | 14.7311 | 14.7227 | 14.7077 | 14.6918 | 14.671 | 15.8551 | 15.855 | 15.8549 | 15.8544 | 15.8538 | 15.8516 | 15.8494 | 15.8465 | 15.8437 | 15.8353 | 15.8202 | 15.8043 | 15.7887
LALEHAM | EAST BEDFONT A | NORTH FELTHAM | MINIMUM HEADROOM | TQ 10987 74875 | YES | 31.3616 | 31.3616 | 31.3616 | 31.2738 | 31.1845 | 31.0934 | 30.9993 | 30.8538 | 30.8044 | 30.6467 | 30.52 | 30.115 | 29.9895 | 28.5913 | 28.5869 | 28.5799 | 28.4945 | 28.4001 | 28.3016 | 28.1981 | 28.0391 | 27.9756 | 27.7715 | 27.5725 | 27.0928 | 26.8947 | 26.0222 | 25.9896 | 25.9375 | 25.8679 | 25.7401 | 25.5932 | 25.4298 | 25.1839 | 25.0287 | 24.5244 | 23.8471 | 22.8635 | 22.1542
|  | NORTH FELTHAM | CT |  |  | 31.3616 | 31.3616 | 31.3616 | 31.3616 | 31.3616 | 31.3616 | 31.3616 | 31.3616 | 31.3616 | 31.3616 | 31.3616 | 31.3616 | 30.9819 | 28.5913 | 28.5869 | 28.5799 | 28.5728 | 28.5653 | 28.5574 | 28.5374 | 28.5176 | 28.4969 | 28.4297 | 28.3241 | 28.0037 | 27.2421 | 26.0222 | 25.9896 | 25.9375 | 25.8847 | 25.828 | 25.7691 | 25.62 | 25.4719 | 25.3171 | 24.8096 | 23.991 | 23.1056 | 22.227
|  | NORTH FELTHAM | LW |  |  | 31.3616 | 31.3616 | 31.3616 | 31.3616 | 31.3616 | 31.3616 | 31.3616 | 31.3616 | 31.3616 | 31.3616 | 31.3616 | 31.3616 | 30.9242 | 28.5913 | 28.5869 | 28.5799 | 28.5728 | 28.5653 | 28.548 | 28.528 | 28.5082 | 28.4875 | 28.4203 | 28.3147 | 27.9434 | 27.1705 | 26.0222 | 25.9896 | 25.9375 | 25.8847 | 25.828 | 25.6991 | 25.55 | 25.4019 | 25.2472 | 24.7369 | 23.9184 | 23.0329 | 22.1542
|  | NORTH FELTHAM | ST |  |  | 31.3616 | 31.3616 | 31.3616 | 31.2738 | 31.1845 | 31.0934 | 30.9993 | 30.8538 | 30.8044 | 30.6467 | 30.52 | 30.115 | 29.9895 | 28.593 | 28.5903 | 28.5866 | 28.4945 | 28.4001 | 28.3016 | 28.1981 | 28.0391 | 27.9756 | 27.7715 | 27.5725 | 27.0928 | 26.8947 | 26.0355 | 26.015 | 25.9877 | 25.8679 | 25.7401 | 25.5932 | 25.4298 | 25.1839 | 25.0287 | 24.5244 | 23.8471 | 22.8635 | 22.1749
|  | NORTH FELTHAM | FS |  |  | 31.3616 | 31.3616 | 31.3616 | 31.3616 | 31.3616 | 31.3616 | 31.3616 | 31.3616 | 31.3616 | 31.3616 | 31.3616 | 31.3616 | 31.3616 | 28.5953 | 28.5941 | 28.593 | 28.5913 | 28.5895 | 28.587 | 28.5837 | 28.5802 | 28.5747 | 28.5565 | 28.5277 | 28.4963 | 28.4644 | 26.0521 | 26.0433 | 26.035 | 26.0229 | 26.0091 | 25.9902 | 25.9661 | 25.9395 | 25.8982 | 25.7628 | 25.5478 | 25.3129 | 25.0747
COWLEY GSP | OXFORD BSP | NORTH HINKSEY | MINIMUM HEADROOM | SP 48645 04403 | YES | 11.932 | 11.932 | 1.4056 | 1.3554 | 1.3038 | 1.2509 | 1.1951 | 1.1076 | 1.0963 | 1.0581 | 0.80426 | 0.18926 | -0.26719 | 10.8708 | 10.864 | 0.32329 | 0.2591 | -0.027881 | -0.31918 | -0.4602 | -0.6321 | -0.73446 | -1.0422 | -1.69 | -2.3687 | -2.8878 | 11.3383 | 11.3383 | 0.81202 | 0.76176 | 0.53694 | 0.24146 | 0.098945 | -0.07444 | -0.17839 | -0.49084 | -1.1466 | -1.8337 | -2.3611
|  | NORTH HINKSEY | CT |  |  | 11.932 | 11.932 | 1.4056 | 1.3554 | 1.3038 | 1.2509 | 1.1951 | 1.1076 | 1.0963 | 1.0581 | 0.80426 | 0.18926 | -0.26719 | 10.8708 | 10.864 | 0.32329 | 0.2591 | -0.027881 | -0.31918 | -0.4602 | -0.6321 | -0.73446 | -1.0422 | -1.69 | -2.3687 | -2.8878 | 11.3383 | 11.3383 | 0.81202 | 0.76176 | 0.53694 | 0.24146 | 0.098945 | -0.07444 | -0.17839 | -0.49084 | -1.1466 | -1.8337 | -2.3611
|  | NORTH HINKSEY | LW |  |  | 11.932 | 11.932 | 1.4056 | 1.4039 | 1.4003 | 1.3947 | 1.3869 | 1.3713 | 1.3686 | 1.3548 | 1.3214 | 1.0856 | 0.6741 | 10.8731 | 10.8675 | 0.32949 | 0.31642 | 0.26676 | 0.1752 | 0.082319 | -0.01775 | -0.11139 | -0.39475 | -0.88324 | -1.4255 | -1.8997 | 11.3383 | 11.3383 | 0.81202 | 0.81029 | 0.80671 | 0.74199 | 0.64761 | 0.54607 | 0.45083 | 0.16274 | -0.33373 | -0.88435 | -1.3668
|  | NORTH HINKSEY | ST |  |  | 11.932 | 11.932 | 11.932 | 11.9227 | 1.3865 | 1.3762 | 1.365 | 1.3466 | 1.3398 | 1.3144 | 1.2887 | 1.1993 | 1.1702 | 10.8769 | 10.8738 | 10.8687 | 10.853 | 0.30923 | 0.29497 | 0.27993 | 0.25818 | 0.24786 | 0.11726 | -0.21251 | -0.60952 | -0.94317 | 11.3383 | 11.3383 | 11.3383 | 11.329 | 0.79293 | 0.78257 | 0.77137 | 0.75294 | 0.74617 | 0.68444 | 0.34934 | -0.053064 | -0.39206
|  | NORTH HINKSEY | FS |  |  | 11.932 | 11.932 | 11.932 | 11.9319 | 11.9319 | 11.9319 | 11.9318 | 1.4053 | 1.4047 | 1.4014 | 1.3987 | 1.3858 | 1.3732 | 10.8818 | 10.8814 | 10.881 | 10.8792 | 10.877 | 10.8756 | 10.8741 | 0.34582 | 0.34385 | 0.33643 | 0.32706 | 0.3076 | 0.28876 | 11.3383 | 11.3383 | 11.3383 | 11.3383 | 11.3383 | 11.3382 | 11.3382 | 0.81171 | 0.81112 | 0.80773 | 0.80503 | 0.79214 | 0.77956
NORTH HYDE GSP |  | NORTH HYDE 11kV | MINIMUM HEADROOM | TQ 10367 79001 |  | 88.9083 | 88.9083 | 88.9083 | 88.7061 | 88.4975 | 88.2796 | 88.0537 | 87.7107 | 87.6632 | 87.5003 | 85.2471 | 81.8229 | 78.8197 | 97.937 | 97.9275 | 97.919 | 97.7079 | 97.4908 | 97.2517 | 97.0047 | 96.6407 | 96.5714 | 96.0746 | 93.1615 | 89.263 | 85.7841 | 97.9296 | 97.9198 | 97.9109 | 97.6996 | 97.4822 | 97.2425 | 96.9949 | 96.6302 | 96.5602 | 96.0843 | 93.7431 | 90.1176 | 86.5903
|  | NORTH HYDE 11kV | CT |  |  | 88.9083 | 88.9083 | 88.9083 | 88.8806 | 88.8523 | 88.8236 | 88.7936 | 88.7474 | 88.7416 | 88.7228 | 86.8225 | 83.7418 | 80.7396 | 97.937 | 97.9275 | 97.919 | 97.8823 | 97.8456 | 97.8081 | 97.757 | 97.6898 | 97.6622 | 97.3909 | 94.7667 | 91.2117 | 87.7339 | 97.9296 | 97.9198 | 97.9109 | 97.874 | 97.837 | 97.7993 | 97.7476 | 97.6797 | 97.6514 | 97.4145 | 95.295 | 92.0671 | 88.5439
|  | NORTH HYDE 11kV | LW |  |  | 88.9083 | 88.9083 | 88.9083 | 88.7061 | 88.4975 | 88.2796 | 88.0537 | 87.7107 | 87.6632 | 87.5003 | 85.2471 | 81.8229 | 78.8197 | 97.937 | 97.9275 | 97.919 | 97.7079 | 97.4908 | 97.2517 | 97.0047 | 96.6407 | 96.5714 | 96.0746 | 93.1615 | 89.263 | 85.7841 | 97.9296 | 97.9198 | 97.9109 | 97.6996 | 97.4822 | 97.2425 | 96.9949 | 96.6302 | 96.5602 | 96.0843 | 93.7431 | 90.1176 | 86.5903
|  | NORTH HYDE 11kV | ST |  |  | 88.9083 | 88.9083 | 88.9083 | 88.9083 | 88.9083 | 88.9083 | 88.9083 | 88.9083 | 88.9083 | 88.9083 | 88.7834 | 86.9042 | 85.0106 | 97.9752 | 97.9357 | 97.931 | 97.9255 | 97.9197 | 97.9113 | 97.9028 | 97.8885 | 97.8736 | 97.826 | 97.0583 | 94.8179 | 92.6218 | 97.9689 | 97.9282 | 97.9234 | 97.9177 | 97.9117 | 97.903 | 97.8943 | 97.8796 | 97.8642 | 97.8151 | 97.111 | 95.4007 | 93.4809
|  | NORTH HYDE 11kV | FS |  |  | 88.9083 | 88.9083 | 88.9083 | 88.9083 | 88.9083 | 88.9083 | 88.9083 | 88.9083 | 88.9083 | 88.9083 | 88.9083 | 88.9083 | 88.9083 | 97.9801 | 97.9434 | 97.9416 | 97.9393 | 97.9371 | 97.9343 | 97.9315 | 97.9283 | 97.9225 | 97.904 | 97.857 | 97.7981 | 97.4004 | 97.9739 | 97.9361 | 97.9343 | 97.9319 | 97.9297 | 97.9267 | 97.9238 | 97.9206 | 97.9146 | 97.8955 | 97.8471 | 97.7864 | 97.398
MINETY GSP | CIRENCESTER BSP | NORTHLEACH | MINIMUM HEADROOM | SP 10557 14251 | YES | 15.4617 | 15.4568 | 15.4462 | 15.3111 | 15.1609 | 14.9892 | 14.8129 | 14.5442 | 14.4253 | 14.0571 | 13.6681 | 12.817 | 12.4224 | 14.1575 | 14.1514 | 14.1385 | 14.0047 | 13.853 | 13.6756 | 13.4936 | 13.218 | 13.0934 | 12.7086 | 12.2929 | 11.4152 | 10.9942 | 14.8983 | 14.8922 | 14.8793 | 14.7455 | 14.5939 | 14.4166 | 14.2349 | 13.9595 | 13.8352 | 13.4512 | 13.0367 | 12.1604 | 11.7406
|  | NORTHLEACH | CT |  |  | 15.4618 | 15.4568 | 15.4463 | 15.436 | 15.4258 | 15.4156 | 15.3646 | 15.3109 | 15.2528 | 15.082 | 14.8026 | 14.5154 | 14.2332 | 14.1576 | 14.1515 | 14.1386 | 14.126 | 14.1135 | 14.1011 | 14.0392 | 13.9777 | 13.9113 | 13.7159 | 13.3962 | 13.0678 | 12.7449 | 14.8983 | 14.8923 | 14.8794 | 14.867 | 14.8545 | 14.8422 | 14.7806 | 14.7195 | 14.6536 | 14.4594 | 14.1416 | 13.8151 | 13.4942
|  | NORTHLEACH | LW |  |  | 15.4617 | 15.4568 | 15.4462 | 15.4197 | 15.3927 | 15.324 | 15.2519 | 15.1707 | 15.1089 | 14.925 | 14.6262 | 14.303 | 14.0179 | 14.1575 | 14.1514 | 14.1385 | 14.1097 | 14.0804 | 14.0003 | 13.9201 | 13.8312 | 13.7611 | 13.5525 | 13.2135 | 12.849 | 12.5232 | 14.8983 | 14.8922 | 14.8793 | 14.8506 | 14.8214 | 14.7417 | 14.6619 | 14.5733 | 14.5036 | 14.2963 | 13.9592 | 13.5966 | 13.2729
|  | NORTHLEACH | ST |  |  | 15.4652 | 15.4625 | 15.4578 | 15.3111 | 15.1609 | 14.9892 | 14.8129 | 14.5442 | 14.4253 | 14.0571 | 13.6681 | 12.817 | 12.4224 | 14.1618 | 14.1584 | 14.1527 | 14.0047 | 13.853 | 13.6756 | 13.4936 | 13.218 | 13.0934 | 12.7086 | 12.2929 | 11.4152 | 10.9942 | 14.9024 | 14.8991 | 14.8935 | 14.7455 | 14.5939 | 14.4166 | 14.2349 | 13.9595 | 13.8352 | 13.4512 | 13.0367 | 12.1604 | 11.7406
|  | NORTHLEACH | FS |  |  | 15.4696 | 15.4692 | 15.4689 | 15.4673 | 15.4655 | 15.4567 | 15.4481 | 15.4369 | 15.4225 | 15.3811 | 15.3116 | 15.2448 | 15.1823 | 14.1671 | 14.1667 | 14.1663 | 14.1644 | 14.1621 | 14.1514 | 14.1409 | 14.1272 | 14.1096 | 14.0588 | 13.9785 | 13.9021 | 13.8306 | 14.9078 | 14.9074 | 14.907 | 14.9051 | 14.9028 | 14.8922 | 14.8817 | 14.8681 | 14.8506 | 14.8002 | 14.7203 | 14.6444 | 14.5733
IVER 66KV |  | NORTHOLT | MINIMUM HEADROOM | TQ 11550 83230 | YES | 48.457 | 48.457 | 48.457 | 48.2627 | 48.065 | 47.8641 | 47.6542 | 47.3307 | 47.2897 | 47.1581 | 46.5501 | 45.9086 | 44.0852 | 45.7684 | 45.7649 | 45.7582 | 45.5589 | 45.3546 | 45.1471 | 44.9176 | 44.5744 | 44.5125 | 44.314 | 42.8508 | 39.2948 | 35.7911 | 46.2521 | 46.2521 | 46.2521 | 46.0578 | 45.8601 | 45.6592 | 45.4493 | 45.1258 | 45.0848 | 44.9532 | 44.3452 | 41.5733 | 38.1563
|  | NORTHOLT | CT |  |  | 48.457 | 48.457 | 48.457 | 48.2627 | 48.065 | 47.8641 | 47.6542 | 47.3307 | 47.2897 | 47.1581 | 46.5501 | 45.9086 | 44.0852 | 45.7689 | 45.7656 | 45.7595 | 45.5589 | 45.3546 | 45.1471 | 44.9176 | 44.5744 | 44.5125 | 44.314 | 42.8508 | 39.2948 | 35.7911 | 46.2521 | 46.2521 | 46.2521 | 46.0578 | 45.8601 | 45.6592 | 45.4493 | 45.1258 | 45.0848 | 44.9532 | 44.3452 | 41.5733 | 38.1563
|  | NORTHOLT | LW |  |  | 48.457 | 48.457 | 48.457 | 48.457 | 48.457 | 48.457 | 48.457 | 48.457 | 48.457 | 48.457 | 48.457 | 48.457 | 46.5693 | 45.7684 | 45.7649 | 45.7582 | 45.7515 | 45.7445 | 45.7249 | 45.7052 | 45.6855 | 45.6646 | 45.5978 | 44.6125 | 41.5731 | 38.2341 | 46.2521 | 46.2521 | 46.2521 | 46.2521 | 46.2521 | 46.2521 | 46.2521 | 46.2521 | 46.2521 | 46.2521 | 46.2521 | 43.8586 | 40.6062
|  | NORTHOLT | ST |  |  | 48.457 | 48.457 | 48.457 | 48.4237 | 48.3897 | 48.3551 | 48.3193 | 48.264 | 48.2452 | 48.1853 | 48.1372 | 47.9645 | 47.9145 | 45.77 | 45.7676 | 45.764 | 45.7261 | 45.6868 | 45.6429 | 45.5977 | 45.5289 | 45.4958 | 45.3902 | 45.1957 | 44.0158 | 42.0332 | 46.2521 | 46.2521 | 46.2521 | 46.2187 | 46.1848 | 46.1502 | 46.1144 | 46.0591 | 46.0403 | 45.9804 | 45.9322 | 45.7596 | 44.2928
|  | NORTHOLT | FS |  |  | 48.457 | 48.457 | 48.457 | 48.457 | 48.457 | 48.457 | 48.457 | 48.457 | 48.457 | 48.457 | 48.457 | 48.457 | 48.457 | 45.773 | 45.7723 | 45.7716 | 45.7702 | 45.7686 | 45.766 | 45.7633 | 45.7601 | 45.7545 | 45.7367 | 45.6935 | 45.6386 | 45.5812 | 46.2521 | 46.2521 | 46.2521 | 46.2521 | 46.2521 | 46.2521 | 46.2521 | 46.2521 | 46.2521 | 46.2521 | 46.2521 | 46.2521 | 46.2521
BRAMLEY (FLEE) | READING BSP | NORTHUMBERLAND AVENUE | MINIMUM HEADROOM | SU 72207 71092 | YES | 25.2511 | 25.2436 | 25.2317 | 25.2061 | 25.1751 | 25.134 | 25.0778 | 25.0104 | 24.9443 | 24.5276 | 23.3554 | 22.179 | 21.008 | 23.5484 | 23.539 | 23.5243 | 23.4938 | 23.4566 | 23.4026 | 23.3327 | 23.2568 | 23.1748 | 22.8656 | 21.718 | 20.5661 | 19.4196 | 24.7916 | 24.7696 | 24.7347 | 24.6704 | 24.5901 | 24.4469 | 24.2815 | 24.1041 | 23.9131 | 23.2411 | 22.1536 | 20.8779 | 19.6081
|  | NORTHUMBERLAND AVENUE | CT |  |  | 25.2511 | 25.2436 | 25.2317 | 25.2061 | 25.1751 | 25.1425 | 25.0801 | 25.0104 | 24.9443 | 24.5765 | 23.3866 | 22.1873 | 21.0114 | 23.5484 | 23.539 | 23.5243 | 23.4938 | 23.4566 | 23.4174 | 23.3413 | 23.2568 | 23.1748 | 22.8868 | 21.7473 | 20.5726 | 19.4211 | 24.7916 | 24.7696 | 24.7347 | 24.6704 | 24.5901 | 24.5056 | 24.334 | 24.1472 | 23.9548 | 23.2791 | 22.1921 | 20.8936 | 19.6188
|  | NORTHUMBERLAND AVENUE | LW |  |  | 25.2511 | 25.2436 | 25.2317 | 25.2118 | 25.1865 | 25.134 | 25.0778 | 25.0176 | 24.9527 | 24.5276 | 23.3554 | 22.179 | 21.008 | 23.5484 | 23.539 | 23.5243 | 23.4995 | 23.468 | 23.4026 | 23.3327 | 23.2577 | 23.1769 | 22.8656 | 21.718 | 20.5661 | 19.4196 | 24.7916 | 24.7696 | 24.7347 | 24.6761 | 24.6016 | 24.4469 | 24.2815 | 24.1041 | 23.9131 | 23.2411 | 22.1536 | 20.8779 | 19.6081
|  | NORTHUMBERLAND AVENUE | ST |  |  | 25.2544 | 25.2496 | 25.2432 | 25.2234 | 25.1991 | 25.1687 | 25.1356 | 25.0831 | 25.0346 | 24.8617 | 24.2981 | 23.4932 | 22.7359 | 23.5525 | 23.5465 | 23.5385 | 23.5157 | 23.4872 | 23.4512 | 23.4118 | 23.3493 | 23.29 | 23.0778 | 22.6395 | 21.8508 | 21.1091 | 24.8013 | 24.7872 | 24.7683 | 24.724 | 24.6666 | 24.5916 | 24.5089 | 24.3772 | 24.2423 | 23.7581 | 23.0319 | 22.3114 | 21.491
|  | NORTHUMBERLAND AVENUE | FS |  |  | 25.2582 | 25.256 | 25.2537 | 25.2425 | 25.23 | 25.2153 | 25.1999 | 25.1797 | 25.1389 | 25.0016 | 24.8672 | 24.6534 | 24.454 | 23.5572 | 23.5545 | 23.5516 | 23.5391 | 23.5247 | 23.5078 | 23.4899 | 23.4669 | 23.4217 | 23.2689 | 23.1103 | 22.8714 | 22.6459 | 24.8126 | 24.806 | 24.7994 | 24.777 | 24.7502 | 24.7174 | 24.6825 | 24.6395 | 24.5646 | 24.3045 | 23.9777 | 23.5644 | 23.1582
COWLEY GSP | HIGH WYCOMBE BSP | NUFFIELD | MINIMUM HEADROOM | SU 68329 86784 | YES | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 6.9553 | 6.9306 | 6.8784 | 6.8278 | 6.7776 | 6.728 | 6.692 | 6.6563 | 6.6177 | 6.5038 | 6.3155 | 6.1206 | 5.9292 | 7.8799 | 7.8785 | 7.8756 | 7.8727 | 7.8699 | 7.8671 | 7.865 | 7.863 | 7.8609 | 7.8544 | 7.8438 | 7.7267 | 7.5356
|  | NUFFIELD | CT |  |  | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 6.9553 | 6.9306 | 6.8784 | 6.8278 | 6.7776 | 6.728 | 6.692 | 6.6563 | 6.6177 | 6.5038 | 6.3155 | 6.1206 | 5.9292 | 7.8799 | 7.8785 | 7.8756 | 7.8727 | 7.8699 | 7.8671 | 7.865 | 7.863 | 7.8609 | 7.8544 | 7.8438 | 7.7267 | 7.5356
|  | NUFFIELD | LW |  |  | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 6.9904 | 6.9851 | 6.9739 | 6.963 | 6.9521 | 6.9157 | 6.8796 | 6.8439 | 6.8053 | 6.6914 | 6.5031 | 6.3082 | 6.1165 | 7.8819 | 7.8816 | 7.8809 | 7.8803 | 7.8797 | 7.8777 | 7.8756 | 7.8736 | 7.8714 | 7.865 | 7.8544 | 7.8434 | 7.7225
|  | NUFFIELD | ST |  |  | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 6.9944 | 6.9917 | 6.9871 | 6.9813 | 6.9744 | 6.9477 | 6.9213 | 6.8969 | 6.8707 | 6.7939 | 6.6688 | 6.5432 | 6.4183 | 7.8821 | 7.8819 | 7.8817 | 7.8814 | 7.881 | 7.8795 | 7.878 | 7.8766 | 7.8751 | 7.8708 | 7.8637 | 7.8567 | 7.8496
|  | NUFFIELD | FS |  |  | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 8.9092 | 6.9987 | 6.9983 | 6.9979 | 6.9962 | 6.9941 | 6.9847 | 6.9753 | 6.9632 | 6.953 | 6.9233 | 6.8761 | 6.8306 | 6.7874 | 7.8823 | 7.8823 | 7.8823 | 7.8822 | 7.8821 | 7.8815 | 7.881 | 7.8803 | 7.8798 | 7.8781 | 7.8754 | 7.8729 | 7.8704
BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | OAKRIDGE | MINIMUM HEADROOM | SU 63496 53664 | YES | 42.3692 | 42.3692 | 42.3692 | 42.3476 | 42.3253 | 42.3022 | 42.2774 | 42.2379 | 42.2327 | 42.2142 | 42.1132 | 41.9691 | 41.2091 | 40.2594 | 40.2561 | 40.2501 | 40.2224 | 40.1943 | 40.1653 | 40.1308 | 40.0816 | 40.0661 | 40.0177 | 39.7972 | 38.9763 | 38.0983 | 41.8277 | 41.8277 | 41.8277 | 41.8062 | 41.7838 | 41.7607 | 41.7359 | 41.6964 | 41.6912 | 41.6727 | 40.9984 | 39.9762 | 39.0554
|  | OAKRIDGE | CT |  |  | 42.3692 | 42.3692 | 42.3692 | 42.3476 | 42.3253 | 42.3022 | 42.2774 | 42.2379 | 42.2327 | 42.2142 | 42.1132 | 41.9691 | 41.2091 | 40.2594 | 40.2561 | 40.2501 | 40.2224 | 40.1943 | 40.1653 | 40.1308 | 40.0816 | 40.0661 | 40.0177 | 39.7972 | 38.9763 | 38.0983 | 41.8277 | 41.8277 | 41.8277 | 41.8062 | 41.7838 | 41.7607 | 41.7359 | 41.6964 | 41.6912 | 41.6727 | 40.9984 | 39.9762 | 39.0554
|  | OAKRIDGE | LW |  |  | 42.3692 | 42.3692 | 42.3692 | 42.3676 | 42.3642 | 42.3589 | 42.3516 | 42.3368 | 42.3343 | 42.3213 | 42.2897 | 42.1976 | 41.4923 | 40.2608 | 40.2582 | 40.2539 | 40.2477 | 40.2401 | 40.2241 | 40.2069 | 40.1825 | 40.1697 | 40.1268 | 39.9811 | 39.2358 | 38.3849 | 41.8277 | 41.8277 | 41.8277 | 41.8261 | 41.8227 | 41.8174 | 41.8101 | 41.7953 | 41.7928 | 41.7798 | 41.2102 | 40.2374 | 39.3437
|  | OAKRIDGE | ST |  |  | 42.3692 | 42.3692 | 42.3692 | 42.3688 | 42.3682 | 42.3671 | 42.3656 | 42.3622 | 42.3605 | 42.3516 | 42.34 | 42.2993 | 42.2844 | 40.2627 | 40.2614 | 40.2596 | 40.2571 | 40.2543 | 40.2483 | 40.2424 | 40.2324 | 40.2237 | 40.1946 | 40.1495 | 40.0688 | 39.892 | 41.8277 | 41.8277 | 41.8277 | 41.8274 | 41.8267 | 41.8256 | 41.8241 | 41.8207 | 41.819 | 41.8102 | 41.7986 | 41.589 | 40.9999
|  | OAKRIDGE | FS |  |  | 42.3692 | 42.3692 | 42.3692 | 42.3639 | 42.3587 | 42.3534 | 42.3481 | 42.3397 | 42.3162 | 42.2402 | 42.2029 | 42.0816 | 41.9784 | 40.2638 | 40.2632 | 40.2625 | 40.2563 | 40.2503 | 40.2434 | 40.2368 | 40.2267 | 40.2005 | 40.1166 | 40.0666 | 39.9328 | 39.818 | 41.8277 | 41.8277 | 41.8277 | 41.8224 | 41.8172 | 41.812 | 41.8066 | 41.7982 | 41.7747 | 41.6987 | 41.6615 | 41.5401 | 41.4369
COWLEY GSP | HEADINGTON BSP | OLD ROAD | MINIMUM HEADROOM | SP 55274 06426 | NO | 45.9624 | 45.9624 | 45.9624 | 45.9507 | 45.9392 | 45.9276 | 45.9159 | 45.8976 | 45.8467 | 45.6851 | 45.6082 | 45.3659 | 45.1633 | 43.328 | 43.328 | 43.328 | 43.3163 | 43.3048 | 43.2932 | 43.2815 | 43.2632 | 43.2123 | 43.0507 | 42.4593 | 41.0984 | 39.7362 | 45.6393 | 45.6321 | 45.6193 | 45.6062 | 45.5949 | 45.5869 | 45.5792 | 45.5675 | 45.5143 | 45.3303 | 44.2247 | 42.8633 | 41.5007
|  | OLD ROAD | CT |  |  | 45.9624 | 45.9624 | 45.9624 | 45.9624 | 45.9624 | 45.9624 | 45.9624 | 45.9624 | 45.9624 | 45.9624 | 45.9624 | 45.9624 | 45.9624 | 43.328 | 43.328 | 43.328 | 43.328 | 43.328 | 43.328 | 43.328 | 43.328 | 43.328 | 43.328 | 42.4593 | 41.0984 | 39.7362 | 45.6397 | 45.6328 | 45.6205 | 45.6079 | 45.5971 | 45.5869 | 45.5792 | 45.5712 | 45.5628 | 45.3303 | 44.2247 | 42.8633 | 41.5007
|  | OLD ROAD | LW |  |  | 45.9624 | 45.9624 | 45.9624 | 45.9624 | 45.9624 | 45.9624 | 45.9624 | 45.9624 | 45.9624 | 45.9624 | 45.9624 | 45.9624 | 45.9624 | 43.328 | 43.328 | 43.328 | 43.328 | 43.328 | 43.328 | 43.328 | 43.328 | 43.328 | 43.328 | 42.4675 | 41.1066 | 39.7442 | 45.6393 | 45.6321 | 45.6193 | 45.6062 | 45.5949 | 45.5874 | 45.5797 | 45.5717 | 45.5633 | 45.3385 | 44.2329 | 42.8716 | 41.5087
|  | OLD ROAD | ST |  |  | 45.9624 | 45.9624 | 45.9624 | 45.9624 | 45.9624 | 45.9624 | 45.9624 | 45.9624 | 45.9624 | 45.9624 | 45.9624 | 45.9624 | 45.9624 | 43.328 | 43.328 | 43.328 | 43.328 | 43.328 | 43.328 | 43.328 | 43.328 | 43.328 | 43.328 | 43.328 | 42.5582 | 41.6932 | 45.6428 | 45.6385 | 45.6321 | 45.6242 | 45.6164 | 45.611 | 45.6055 | 45.6001 | 45.5943 | 45.576 | 45.2223 | 44.3236 | 43.4583
|  | OLD ROAD | FS |  |  | 45.9624 | 45.9624 | 45.9624 | 45.9507 | 45.9392 | 45.9276 | 45.9159 | 45.8976 | 45.8467 | 45.6851 | 45.6082 | 45.3659 | 45.1633 | 43.328 | 43.328 | 43.328 | 43.3163 | 43.3048 | 43.2932 | 43.2815 | 43.2632 | 43.2123 | 43.0507 | 42.9738 | 42.7315 | 42.5289 | 45.6474 | 45.6459 | 45.6444 | 45.6297 | 45.6158 | 45.6022 | 45.5884 | 45.5675 | 45.5143 | 45.3456 | 45.2495 | 44.9822 | 44.7533
COWLEY GSP | OXFORD BSP | OXFORD | MINIMUM HEADROOM | SP 50148 05901 | YES | 35.5942 | 35.4688 | 34.3085 | 33.9721 | 33.6012 | 33.3376 | 33.0537 | 32.7599 | 32.5625 | 32.0413 | 31.1113 | 30.1059 | 29.0841 | 40.6292 | 40.614 | 39.6835 | 39.6017 | 39.5198 | 39.4377 | 39.3553 | 39.2698 | 39.238 | 39.1421 | 38.983 | 38.8788 | 38.71 | 41.6573 | 41.642 | 40.7115 | 40.6298 | 40.5479 | 40.2808 | 39.9641 | 39.6339 | 39.4077 | 38.8123 | 37.7478 | 36.5752 | 35.4044
|  | OXFORD | CT |  |  | 35.677 | 35.5595 | 34.7752 | 34.4786 | 34.1476 | 33.8095 | 33.5622 | 33.3081 | 33.1242 | 32.6441 | 31.2055 | 30.1059 | 29.0841 | 40.7085 | 40.6994 | 40.1411 | 40.0953 | 40.0496 | 40.0038 | 39.958 | 39.9123 | 39.894 | 39.8391 | 39.1715 | 38.936 | 38.7682 | 41.7366 | 41.7274 | 41.1691 | 41.1234 | 41.0776 | 40.7378 | 40.4561 | 40.1657 | 39.9529 | 39.3986 | 37.8255 | 36.5752 | 35.4044
|  | OXFORD | LW |  |  | 35.5942 | 35.4688 | 34.3085 | 33.9721 | 33.6012 | 33.3376 | 33.0537 | 32.7599 | 32.5625 | 32.0413 | 31.1113 | 30.1429 | 29.12 | 40.6292 | 40.614 | 39.6835 | 39.6017 | 39.5198 | 39.4377 | 39.3553 | 39.2698 | 39.238 | 39.1421 | 38.983 | 38.8788 | 38.71 | 41.6573 | 41.642 | 40.7115 | 40.6298 | 40.5479 | 40.2808 | 39.9641 | 39.6339 | 39.4077 | 38.8123 | 37.7478 | 36.6287 | 35.4568
|  | OXFORD | ST |  |  | 35.8123 | 35.756 | 35.2993 | 35.1053 | 34.8659 | 34.6636 | 34.447 | 34.2115 | 34.0642 | 33.6664 | 33.0218 | 32.2586 | 31.5976 | 40.7482 | 40.7421 | 40.3699 | 40.3004 | 40.2302 | 40.1593 | 40.087 | 39.9918 | 39.9577 | 39.851 | 39.7337 | 39.5358 | 39.4219 | 41.7763 | 41.7702 | 41.398 | 41.3284 | 41.2583 | 41.1873 | 41.115 | 41.0199 | 40.9857 | 40.5962 | 39.8606 | 38.9988 | 38.2424
|  | OXFORD | FS |  |  | 35.9298 | 35.9179 | 35.7233 | 35.662 | 35.5843 | 35.514 | 35.4396 | 35.3558 | 35.3004 | 35.1529 | 34.9048 | 34.6222 | 34.3252 | 40.7879 | 40.7848 | 40.5987 | 40.5823 | 40.5658 | 40.5494 | 40.533 | 40.5159 | 40.5046 | 40.4699 | 40.4315 | 40.3886 | 40.3344 | 41.8159 | 41.8129 | 41.6268 | 41.6103 | 41.5939 | 41.5775 | 41.561 | 41.5439 | 41.5326 | 41.4979 | 41.4596 | 41.4167 | 41.2828
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | OVERTON | MINIMUM HEADROOM | SU 52061 50913 | YES | 34.0074 | 34.0074 | 34.0074 | 33.9832 | 33.9586 | 33.9337 | 33.9076 | 33.8674 | 33.8623 | 33.8301 | 33.7658 | 33.6714 | 33.6497 | 33.9981 | 33.9956 | 33.9902 | 33.9608 | 33.931 | 33.9009 | 33.8717 | 33.8284 | 33.82 | 33.6672 | 33.2402 | 32.7878 | 32.4139 | 34.0378 | 34.0343 | 34.0269 | 33.9956 | 33.964 | 33.932 | 33.9017 | 33.8573 | 33.8477 | 33.7179 | 33.2866 | 32.8299 | 32.4517
|  | OVERTON | CT |  |  | 34.0074 | 34.0074 | 34.0074 | 33.9832 | 33.9586 | 33.9337 | 33.9076 | 33.8674 | 33.8623 | 33.8459 | 33.7658 | 33.6714 | 33.6497 | 33.9981 | 33.9956 | 33.9902 | 33.9608 | 33.931 | 33.9009 | 33.8717 | 33.8284 | 33.82 | 33.6672 | 33.2402 | 32.7878 | 32.4139 | 34.0378 | 34.0343 | 34.0269 | 33.9956 | 33.964 | 33.932 | 33.9017 | 33.8573 | 33.8477 | 33.7179 | 33.2866 | 32.8299 | 32.4517
|  | OVERTON | LW |  |  | 34.0074 | 34.0074 | 34.0074 | 34.0074 | 34.0074 | 34.0074 | 34.0074 | 34.0074 | 34.0074 | 34.0074 | 34.0074 | 34.0074 | 34.0074 | 33.9988 | 33.9967 | 33.9921 | 33.9876 | 33.9832 | 33.9801 | 33.977 | 33.9739 | 33.9706 | 33.9457 | 33.5992 | 33.2411 | 32.889 | 34.0387 | 34.0358 | 34.0295 | 34.0234 | 34.0174 | 34.0132 | 34.0089 | 34.0047 | 34.0002 | 33.9869 | 33.647 | 33.2846 | 32.9282
|  | OVERTON | ST |  |  | 34.0074 | 34.0074 | 34.0074 | 33.9856 | 33.9635 | 33.9409 | 33.9175 | 33.8814 | 33.8692 | 33.8301 | 33.7987 | 33.686 | 33.6534 | 34.0001 | 33.9988 | 33.9966 | 33.9721 | 33.9467 | 33.9217 | 33.896 | 33.8578 | 33.8433 | 33.7976 | 33.7555 | 33.4673 | 33.2057 | 34.0404 | 34.0387 | 34.0357 | 34.0102 | 33.9836 | 33.9577 | 33.9312 | 33.8923 | 33.8769 | 33.8288 | 33.7828 | 33.5175 | 33.2531
|  | OVERTON | FS |  |  | 34.0074 | 34.0074 | 34.0074 | 34.0074 | 34.0074 | 34.0074 | 34.0074 | 34.0074 | 34.0074 | 34.0074 | 34.0074 | 34.0074 | 34.0074 | 34.0023 | 34.0021 | 34.0019 | 34.0012 | 34.0003 | 33.9995 | 33.9987 | 33.9976 | 33.9968 | 33.9942 | 33.9902 | 33.9863 | 33.9826 | 34.0433 | 34.0431 | 34.0429 | 34.0419 | 34.0407 | 34.0396 | 34.0385 | 34.0371 | 34.0359 | 34.0324 | 34.0269 | 34.0216 | 34.0166
BRAMLEY (FLEE) | BURGHFIELD RESERVE | PADWORTH | MINIMUM HEADROOM | SU 62243 66052 | YES | 5.9584 | 5.9584 | 5.9584 | 5.9466 | 5.9342 | 5.9212 | 5.9071 | 5.8842 | 5.8811 | 5.8696 | 5.7384 | 5.55 | 5.4225 | 5.5037 | 5.5019 | 5.4983 | 5.4847 | 5.4693 | 5.4533 | 5.4375 | 5.4128 | 5.4077 | 5.3905 | 5.3081 | 5.2172 | 5.1658 | 5.4935 | 5.4923 | 5.4898 | 5.4767 | 5.4621 | 5.447 | 5.4317 | 5.4075 | 5.403 | 5.3874 | 5.2273 | 5.0247 | 4.8833
|  | PADWORTH | CT |  |  | 5.9584 | 5.9584 | 5.9584 | 5.9466 | 5.9342 | 5.9212 | 5.9071 | 5.8842 | 5.8811 | 5.8696 | 5.7384 | 5.55 | 5.4225 | 5.5041 | 5.5026 | 5.4995 | 5.4847 | 5.4693 | 5.4533 | 5.4375 | 5.4128 | 5.4077 | 5.3905 | 5.3081 | 5.2172 | 5.1658 | 5.4939 | 5.4928 | 5.4906 | 5.4767 | 5.4621 | 5.447 | 5.4317 | 5.4075 | 5.403 | 5.3874 | 5.2273 | 5.0247 | 4.8833
|  | PADWORTH | LW |  |  | 5.9584 | 5.9584 | 5.9584 | 5.957 | 5.954 | 5.9492 | 5.9427 | 5.9295 | 5.9272 | 5.9156 | 5.8181 | 5.6554 | 5.5455 | 5.5037 | 5.5019 | 5.4983 | 5.4934 | 5.4869 | 5.4803 | 5.472 | 5.457 | 5.4528 | 5.4355 | 5.3977 | 5.3326 | 5.2881 | 5.4935 | 5.4923 | 5.4898 | 5.4858 | 5.4803 | 5.4743 | 5.4665 | 5.452 | 5.4484 | 5.4328 | 5.3055 | 5.1287 | 5.0048
|  | PADWORTH | ST |  |  | 5.9584 | 5.9584 | 5.9584 | 5.9581 | 5.9575 | 5.9566 | 5.9552 | 5.9521 | 5.9507 | 5.9428 | 5.9324 | 5.8843 | 5.8022 | 5.5045 | 5.5034 | 5.5015 | 5.4989 | 5.4955 | 5.4931 | 5.4901 | 5.4859 | 5.4831 | 5.4713 | 5.4545 | 5.4116 | 5.392 | 5.4941 | 5.4934 | 5.492 | 5.4901 | 5.4875 | 5.4855 | 5.483 | 5.4791 | 5.4767 | 5.466 | 5.4511 | 5.3793 | 5.2881
|  | PADWORTH | FS |  |  | 5.9584 | 5.9584 | 5.9584 | 5.9584 | 5.9584 | 5.9584 | 5.9583 | 5.9582 | 5.9577 | 5.9548 | 5.9525 | 5.9417 | 5.9311 | 5.5063 | 5.5062 | 5.5061 | 5.5055 | 5.5048 | 5.5042 | 5.5036 | 5.5028 | 5.5018 | 5.4975 | 5.4928 | 5.4795 | 5.4666 | 5.4954 | 5.4953 | 5.4952 | 5.4948 | 5.4943 | 5.4939 | 5.4935 | 5.4929 | 5.492 | 5.4881 | 5.4841 | 5.4715 | 5.4593
BRAMLEY (FLEE) | BURGHFIELD RESERVE | PANGBOURNE | MINIMUM HEADROOM | SU 62960 76144 | YES | 42.2248 | 42.2248 | 42.2248 | 42.2059 | 42.1875 | 42.169 | 42.1501 | 42.1208 | 42.039 | 41.7797 | 41.6562 | 41.2674 | 40.9421 | 39.4493 | 39.4493 | 39.4493 | 39.4305 | 39.412 | 39.3411 | 39.2544 | 39.1683 | 39.0756 | 38.8006 | 38.337 | 37.8522 | 37.3745 | 41.1199 | 41.1144 | 41.1028 | 41.0916 | 41.0805 | 41.0674 | 41.047 | 41.0157 | 40.9325 | 40.6692 | 40.5391 | 40.1437 | 39.6954
|  | PANGBOURNE | CT |  |  | 42.2248 | 42.2248 | 42.2248 | 42.2248 | 42.2248 | 42.2248 | 42.2248 | 42.2248 | 42.2248 | 42.2248 | 42.2248 | 42.1697 | 41.7642 | 39.4493 | 39.4493 | 39.4493 | 39.4493 | 39.4493 | 39.3411 | 39.2544 | 39.1683 | 39.0756 | 38.8006 | 38.337 | 37.8522 | 37.3745 | 41.1199 | 41.1144 | 41.1028 | 41.0916 | 41.0805 | 41.0695 | 41.0646 | 41.0598 | 41.0546 | 41.0391 | 40.6418 | 40.1651 | 39.6954
|  | PANGBOURNE | LW |  |  | 42.2248 | 42.2248 | 42.2248 | 42.2248 | 42.2248 | 42.2248 | 42.2248 | 42.2248 | 42.2248 | 42.2248 | 42.2248 | 42.2248 | 41.993 | 39.4493 | 39.4493 | 39.4493 | 39.4493 | 39.4493 | 39.4493 | 39.4493 | 39.4382 | 39.3454 | 39.0703 | 38.607 | 38.122 | 37.644 | 41.1217 | 41.1173 | 41.1078 | 41.0987 | 41.0896 | 41.0847 | 41.0798 | 41.075 | 41.0698 | 41.0543 | 40.9072 | 40.4304 | 39.9604
|  | PANGBOURNE | ST |  |  | 42.2248 | 42.2248 | 42.2248 | 42.2248 | 42.2248 | 42.2248 | 42.2248 | 42.2248 | 42.2248 | 42.2248 | 42.2248 | 42.2248 | 42.2248 | 39.4493 | 39.4493 | 39.4493 | 39.4493 | 39.4493 | 39.4493 | 39.4493 | 39.4493 | 39.4493 | 39.4493 | 39.2593 | 38.9467 | 38.6365 | 41.125 | 41.1227 | 41.1187 | 41.1138 | 41.1078 | 41.1037 | 41.0996 | 41.0963 | 41.0927 | 41.0823 | 41.0649 | 41.0473 | 40.9362
|  | PANGBOURNE | FS |  |  | 42.2248 | 42.2248 | 42.2248 | 42.2059 | 42.1875 | 42.169 | 42.1501 | 42.1208 | 42.039 | 41.7797 | 41.6562 | 41.2674 | 40.9421 | 39.4493 | 39.4493 | 39.4493 | 39.4305 | 39.412 | 39.3935 | 39.3747 | 39.3453 | 39.2635 | 39.0042 | 38.8807 | 38.4919 | 38.1666 | 41.1287 | 41.1284 | 41.128 | 41.1077 | 41.0874 | 41.0674 | 41.047 | 41.0157 | 40.9325 | 40.6692 | 40.5391 | 40.1437 | 39.8123
BOTLEY WOOD GSP | BOTLEY WOOD BSP | PARK GATE | MINIMUM HEADROOM | SU 51369 08259 | NO | 44.3812 | 44.3719 | 44.3526 | 44.2022 | 44.0313 | 43.8612 | 43.6855 | 43.4221 | 43.3248 | 43.0134 | 42.7359 | 42.0101 | 41.6546 | 41.3149 | 41.3048 | 41.278 | 41.1315 | 40.9304 | 40.7378 | 40.5334 | 40.2347 | 40.0991 | 39.6629 | 39.0167 | 37.9392 | 37.3292 | 42.7353 | 42.7271 | 42.7101 | 42.5595 | 42.3904 | 42.2218 | 42.0475 | 41.7855 | 41.6895 | 41.3827 | 41.112 | 40.3929 | 39.8967
|  | PARK GATE | CT |  |  | 44.3843 | 44.3768 | 44.3611 | 44.3344 | 44.3075 | 44.279 | 44.2514 | 44.2167 | 44.1974 | 44.135 | 44.0147 | 43.6867 | 43.3857 | 41.3183 | 41.3101 | 41.2929 | 41.247 | 41.1912 | 41.1248 | 41.0465 | 40.9598 | 40.8845 | 40.507 | 39.845 | 39.1805 | 38.5493 | 42.738 | 42.7314 | 42.7176 | 42.6927 | 42.6677 | 42.6411 | 42.6154 | 42.5826 | 42.5653 | 42.5095 | 42.3863 | 41.7791 | 40.902
|  | PARK GATE | LW |  |  | 44.3812 | 44.3719 | 44.3526 | 44.3337 | 44.3149 | 44.3003 | 44.2849 | 44.2692 | 44.2523 | 44.1976 | 44.0832 | 43.7901 | 43.4995 | 41.3149 | 41.3048 | 41.278 | 41.2236 | 41.1646 | 41.1017 | 41.0357 | 40.968 | 40.8881 | 40.4838 | 39.8575 | 39.2312 | 38.6101 | 42.7353 | 42.7271 | 42.7101 | 42.6935 | 42.6769 | 42.664 | 42.6506 | 42.6367 | 42.6218 | 42.5737 | 42.4079 | 41.8389 | 40.8773
|  | PARK GATE | ST |  |  | 44.3885 | 44.3787 | 44.3679 | 44.2022 | 44.0313 | 43.8612 | 43.6855 | 43.4221 | 43.3248 | 43.0134 | 42.7359 | 42.0101 | 41.6546 | 41.3229 | 41.3122 | 41.3004 | 41.1315 | 40.9304 | 40.7378 | 40.5334 | 40.2347 | 40.0991 | 39.6629 | 39.0167 | 37.9392 | 37.3292 | 42.7417 | 42.7331 | 42.7236 | 42.5595 | 42.3904 | 42.2218 | 42.0475 | 41.7855 | 41.6895 | 41.3827 | 41.112 | 40.3929 | 39.8967
|  | PARK GATE | FS |  |  | 44.3994 | 44.3952 | 44.3945 | 44.3916 | 44.3881 | 44.384 | 44.3797 | 44.3744 | 44.3699 | 44.3552 | 44.3326 | 44.3107 | 44.2889 | 41.3348 | 41.3302 | 41.3295 | 41.3263 | 41.3224 | 41.3179 | 41.3133 | 41.3075 | 41.3026 | 41.2856 | 41.2203 | 41.1465 | 41.0527 | 42.7513 | 42.7476 | 42.747 | 42.7444 | 42.7413 | 42.7377 | 42.734 | 42.7293 | 42.7253 | 42.7124 | 42.6925 | 42.6732 | 42.654
MELKSHAM GSP | AMESBURY | PARK HOUSE | MINIMUM HEADROOM | SU 23138 43780 | YES | 5.938 | 5.938 | 5.938 | 5.9176 | 5.8816 | 5.8496 | 5.813 | 5.7595 | 5.7326 | 5.6404 | 5.4622 | 5.2095 | 5.0908 | 4.9987 | 4.998 | 4.9964 | 4.9912 | 4.9819 | 4.9687 | 4.9508 | 4.9157 | 4.9088 | 4.8756 | 4.7973 | 4.6495 | 4.619 | 5.4229 | 5.422 | 5.4201 | 5.4144 | 5.4048 | 5.3912 | 5.373 | 5.3377 | 5.3305 | 5.2964 | 5.2166 | 4.9647 | 4.827
|  | PARK HOUSE | CT |  |  | 5.938 | 5.938 | 5.938 | 5.9362 | 5.9106 | 5.8841 | 5.8599 | 5.8301 | 5.8073 | 5.7352 | 5.5488 | 5.3478 | 5.211 | 4.9989 | 4.9983 | 4.997 | 4.9946 | 4.9913 | 4.9869 | 4.9812 | 4.9699 | 4.967 | 4.954 | 4.8675 | 4.7714 | 4.7379 | 5.4232 | 5.4224 | 5.4208 | 5.4181 | 5.4144 | 5.4097 | 5.4037 | 5.3922 | 5.3889 | 5.375 | 5.2871 | 5.1061 | 4.9502
|  | PARK HOUSE | LW |  |  | 5.938 | 5.938 | 5.938 | 5.9176 | 5.8816 | 5.8496 | 5.813 | 5.7595 | 5.7326 | 5.6404 | 5.4622 | 5.2095 | 5.0908 | 4.9987 | 4.998 | 4.9964 | 4.9912 | 4.9819 | 4.9687 | 4.9508 | 4.9157 | 4.9088 | 4.8756 | 4.7973 | 4.6495 | 4.6342 | 5.4229 | 5.422 | 5.4201 | 5.4144 | 5.4048 | 5.3912 | 5.373 | 5.3377 | 5.3305 | 5.2964 | 5.2166 | 4.9647 | 4.827
|  | PARK HOUSE | ST |  |  | 5.938 | 5.938 | 5.938 | 5.9372 | 5.9356 | 5.9332 | 5.9297 | 5.9218 | 5.918 | 5.8766 | 5.7793 | 5.6138 | 5.5088 | 4.9999 | 4.9999 | 4.9998 | 4.9989 | 4.9972 | 4.9942 | 4.99 | 4.9814 | 4.9769 | 4.9543 | 4.9238 | 4.8261 | 4.7882 | 5.4245 | 5.4244 | 5.4243 | 5.4234 | 5.4217 | 5.4185 | 5.4142 | 5.4054 | 5.4007 | 5.3774 | 5.346 | 5.2472 | 5.2083
|  | PARK HOUSE | FS |  |  | 5.938 | 5.938 | 5.938 | 5.9335 | 5.9291 | 5.9246 | 5.92 | 5.9127 | 5.8921 | 5.8233 | 5.7882 | 5.6455 | 5.5156 | 4.9998 | 4.9998 | 4.9997 | 4.995 | 4.9902 | 4.9856 | 4.9808 | 4.9733 | 4.9523 | 4.8827 | 4.8462 | 4.7247 | 4.619 | 5.4244 | 5.4243 | 5.4242 | 5.4194 | 5.4146 | 5.4099 | 5.4051 | 5.3975 | 5.3765 | 5.3066 | 5.2697 | 5.1478 | 5.0418
MINETY GSP | STRATTON (2 X 90) | PARK NORTH | MINIMUM HEADROOM | SU 18052 84542 | YES | 46.2609 | 46.2609 | 46.2609 | 46.2609 | 46.2609 | 46.2609 | 46.2609 | 46.2609 | 46.2609 | 46.2609 | 46.249 | 44.7417 | 43.2395 | 37.4915 | 37.4893 | 37.4851 | 37.4808 | 37.476 | 37.4643 | 37.4526 | 37.4411 | 37.4288 | 37.3909 | 37.3157 | 37.2309 | 37.1464 | 45.6365 | 45.6338 | 45.6284 | 45.6229 | 45.617 | 45.6021 | 45.5874 | 45.5728 | 45.5572 | 45.5093 | 44.8884 | 43.1563 | 41.4302
|  | PARK NORTH | CT |  |  | 46.2609 | 46.2609 | 46.2609 | 46.2609 | 46.2609 | 46.2609 | 46.2609 | 46.2609 | 46.2609 | 46.2609 | 46.2609 | 44.9183 | 43.4169 | 37.4919 | 37.49 | 37.4863 | 37.4825 | 37.4783 | 37.4742 | 37.4626 | 37.451 | 37.4387 | 37.4008 | 37.3256 | 37.2408 | 37.1564 | 45.637 | 45.6347 | 45.63 | 45.6251 | 45.6198 | 45.6147 | 45.5999 | 45.5853 | 45.5697 | 45.5219 | 45.0911 | 43.3592 | 41.634
|  | PARK NORTH | LW |  |  | 46.2609 | 46.2609 | 46.2609 | 46.2609 | 46.2609 | 46.2609 | 46.2609 | 46.2609 | 46.2609 | 46.2609 | 46.249 | 44.7417 | 43.2395 | 37.4915 | 37.4893 | 37.4851 | 37.4808 | 37.476 | 37.4643 | 37.4526 | 37.4411 | 37.4288 | 37.3909 | 37.3157 | 37.2309 | 37.1464 | 45.6365 | 45.6338 | 45.6284 | 45.6229 | 45.617 | 45.6021 | 45.5874 | 45.5728 | 45.5572 | 45.5093 | 44.8884 | 43.1563 | 41.4302
|  | PARK NORTH | ST |  |  | 46.2609 | 46.2609 | 46.2609 | 46.2609 | 46.2609 | 46.2609 | 46.2609 | 46.2609 | 46.2609 | 46.2609 | 46.2609 | 46.2609 | 45.4948 | 37.4934 | 37.4922 | 37.4903 | 37.4878 | 37.4846 | 37.4804 | 37.4761 | 37.4683 | 37.4598 | 37.4341 | 37.3829 | 37.3275 | 37.2733 | 45.6389 | 45.6374 | 45.635 | 45.6318 | 45.6278 | 45.6225 | 45.6171 | 45.6071 | 45.5965 | 45.5639 | 45.4992 | 45.1273 | 44.0218
|  | PARK NORTH | FS |  |  | 46.2609 | 46.2609 | 46.2609 | 46.2609 | 46.2609 | 46.2609 | 46.2609 | 46.2609 | 46.2609 | 46.2609 | 46.2609 | 46.2609 | 46.2609 | 37.4955 | 37.4952 | 37.4949 | 37.4941 | 37.493 | 37.4919 | 37.4907 | 37.4893 | 37.486 | 37.476 | 37.4557 | 37.4326 | 37.4092 | 45.6416 | 45.6412 | 45.6409 | 45.6398 | 45.6385 | 45.637 | 45.6355 | 45.6337 | 45.6296 | 45.6169 | 45.5912 | 45.5621 | 45.5325
WILLESDEN GSP | ACTON LANE | PARK ROYAL | MINIMUM HEADROOM | TQ 20137 82215 | YES | 17.497 | 17.497 | 17.497 | 17.4925 | 17.488 | 17.4834 | 17.4786 | 17.4712 | 17.4687 | 17.4607 | 17.4542 | 17.4311 | 17.4245 | 16.6869 | 16.6857 | 16.6834 | 16.68 | 16.6739 | 16.6673 | 16.6606 | 16.6511 | 16.6464 | 16.6313 | 16.425 | 16.0956 | 15.7212 | 17.1884 | 17.1875 | 17.1858 | 17.1822 | 17.1764 | 17.1703 | 17.1641 | 17.1551 | 17.1509 | 17.1375 | 17.1184 | 16.8636 | 16.4903
|  | PARK ROYAL | CT |  |  | 17.497 | 17.497 | 17.497 | 17.497 | 17.497 | 17.497 | 17.497 | 17.497 | 17.497 | 17.497 | 17.497 | 17.497 | 17.497 | 16.6869 | 16.6857 | 16.6834 | 16.6811 | 16.6787 | 16.6764 | 16.6734 | 16.6703 | 16.667 | 16.6566 | 16.4319 | 16.104 | 15.7295 | 17.1884 | 17.1875 | 17.1858 | 17.184 | 17.1822 | 17.1805 | 17.1782 | 17.1759 | 17.1734 | 17.1655 | 17.1471 | 16.8719 | 16.4986
|  | PARK ROYAL | LW |  |  | 17.497 | 17.497 | 17.497 | 17.497 | 17.497 | 17.497 | 17.497 | 17.497 | 17.497 | 17.497 | 17.497 | 17.497 | 17.497 | 16.6869 | 16.6857 | 16.6834 | 16.6811 | 16.6787 | 16.6757 | 16.6727 | 16.6696 | 16.6664 | 16.656 | 16.425 | 16.0956 | 15.7212 | 17.1884 | 17.1875 | 17.1858 | 17.184 | 17.1822 | 17.18 | 17.1777 | 17.1753 | 17.1729 | 17.165 | 17.1466 | 16.8636 | 16.4903
|  | PARK ROYAL | ST |  |  | 17.497 | 17.497 | 17.497 | 17.4925 | 17.488 | 17.4834 | 17.4786 | 17.4712 | 17.4687 | 17.4607 | 17.4542 | 17.4311 | 17.4245 | 16.6915 | 16.6869 | 16.6858 | 16.68 | 16.6739 | 16.6673 | 16.6606 | 16.6511 | 16.6464 | 16.6313 | 16.5831 | 16.3576 | 16.1537 | 17.1919 | 17.1885 | 17.1876 | 17.1822 | 17.1764 | 17.1703 | 17.1641 | 17.1551 | 17.1509 | 17.1375 | 17.1184 | 17.0806 | 16.9226
|  | PARK ROYAL | FS |  |  | 17.497 | 17.497 | 17.497 | 17.496 | 17.4951 | 17.4942 | 17.4932 | 17.4917 | 17.4876 | 17.4744 | 17.4682 | 17.4485 | 17.432 | 16.6924 | 16.6884 | 16.6882 | 16.6869 | 16.6855 | 16.6839 | 16.6822 | 16.6799 | 16.6749 | 16.6591 | 16.6461 | 16.6178 | 16.5922 | 17.1926 | 17.1896 | 17.1895 | 17.1882 | 17.1869 | 17.1854 | 17.184 | 17.1818 | 17.1771 | 17.1619 | 17.1505 | 17.1243 | 17.101
MANNINGTON GSP | BOURNEMOUTH | PARKSTONE NORTH | MINIMUM HEADROOM | SZ 03222 92233 | YES | 23.5337 | 23.4215 | 22.217 | 21.9465 | 21.6604 | 21.2581 | 20.8378 | 20.3993 | 19.9844 | 18.8774 | 17.0957 | 15.2338 | 13.3026 | 29.4824 | 29.4592 | 28.3618 | 28.2622 | 28.1618 | 28.0549 | 27.9469 | 27.8379 | 27.781 | 27.2431 | 25.2395 | 23.1126 | 20.9027 | 29.5878 | 29.5699 | 28.4788 | 28.3894 | 28.3 | 28.2106 | 28.1211 | 28.0317 | 27.9959 | 27.8886 | 26.0746 | 23.9608 | 21.7805
|  | PARKSTONE NORTH | CT |  |  | 23.6313 | 23.5289 | 22.7663 | 22.5368 | 22.2917 | 22.037 | 21.6524 | 21.2497 | 20.849 | 19.7849 | 17.3995 | 15.3689 | 13.4379 | 29.5756 | 29.5598 | 28.8991 | 28.8356 | 28.7712 | 28.7063 | 28.6341 | 28.5609 | 28.5182 | 28.1693 | 25.562 | 23.2694 | 21.0597 | 29.6808 | 29.67 | 29.0154 | 28.9618 | 28.9081 | 28.8544 | 28.8008 | 28.7471 | 28.7257 | 28.6613 | 26.3978 | 24.1152 | 21.9352
|  | PARKSTONE NORTH | LW |  |  | 23.5337 | 23.4215 | 22.217 | 21.9465 | 21.6604 | 21.2581 | 20.8378 | 20.3993 | 19.9844 | 18.8774 | 17.0957 | 15.2338 | 13.3026 | 29.4824 | 29.4592 | 28.3618 | 28.2622 | 28.1618 | 28.0549 | 27.9469 | 27.8379 | 27.781 | 27.2431 | 25.2395 | 23.1126 | 20.9027 | 29.5878 | 29.5699 | 28.4788 | 28.3894 | 28.3 | 28.2106 | 28.1211 | 28.0317 | 27.9959 | 27.8886 | 26.0746 | 23.9608 | 21.7805
|  | PARKSTONE NORTH | ST |  |  | 23.7159 | 23.6494 | 23.1591 | 23.0114 | 22.8406 | 22.5399 | 22.2288 | 21.9572 | 21.6833 | 20.9523 | 19.7835 | 18.5933 | 17.4035 | 29.6243 | 29.6138 | 29.1744 | 29.1323 | 29.089 | 29.0384 | 28.9872 | 28.9382 | 28.9094 | 28.8279 | 28.124 | 26.775 | 25.4297 | 29.7273 | 29.7201 | 29.2837 | 29.2479 | 29.2122 | 29.1764 | 29.1406 | 29.1049 | 29.0905 | 29.0476 | 28.9217 | 27.6115 | 26.2621
|  | PARKSTONE NORTH | FS |  |  | 23.9202 | 23.7893 | 23.5642 | 23.502 | 23.4339 | 23.3298 | 23.2227 | 23.0964 | 22.9877 | 22.6978 | 22.2243 | 21.7171 | 21.187 | 29.6796 | 29.6689 | 29.4503 | 29.4299 | 29.4092 | 29.3865 | 29.3636 | 29.3397 | 29.3269 | 29.2904 | 29.2301 | 29.1814 | 29.1146 | 29.7738 | 29.7702 | 29.552 | 29.5341 | 29.5162 | 29.4983 | 29.4805 | 29.4626 | 29.4554 | 29.4339 | 29.3982 | 29.3767 | 29.3374
MANNINGTON GSP | BOURNEMOUTH | PARKSTONE SOUTH | MINIMUM HEADROOM | SZ 04762 89848 | YES | 42.9545 | 42.941 | 42.9127 | 42.8839 | 42.8551 | 42.8268 | 42.6851 | 42.5158 | 42.3452 | 41.857 | 40.954 | 39.9516 | 39.0276 | 40.0634 | 40.0525 | 40.0297 | 40.0065 | 39.9793 | 39.954 | 39.8327 | 39.6418 | 39.4479 | 38.8935 | 37.8656 | 36.703 | 35.6205 | 41.7385 | 41.7269 | 41.7024 | 41.6776 | 41.6499 | 41.5569 | 41.3729 | 41.1764 | 40.9765 | 40.4049 | 39.3577 | 38.1971 | 37.1166
|  | PARKSTONE SOUTH | CT |  |  | 42.9545 | 42.941 | 42.9127 | 42.8839 | 42.8552 | 42.8268 | 42.6851 | 42.5158 | 42.3452 | 41.857 | 40.954 | 39.9516 | 39.0276 | 40.0634 | 40.0525 | 40.0297 | 40.0065 | 39.9835 | 39.9605 | 39.8327 | 39.6418 | 39.4479 | 38.8935 | 37.8656 | 36.703 | 35.6205 | 41.7385 | 41.7269 | 41.7024 | 41.6776 | 41.6529 | 41.5569 | 41.3729 | 41.1764 | 40.9765 | 40.4049 | 39.3577 | 38.1971 | 37.1166
|  | PARKSTONE SOUTH | LW |  |  | 42.9587 | 42.9475 | 42.9241 | 42.8897 | 42.8551 | 42.8275 | 42.7942 | 42.7449 | 42.7212 | 42.2171 | 41.3379 | 40.3279 | 39.4224 | 40.0668 | 40.0578 | 40.039 | 40.0093 | 39.9793 | 39.954 | 39.9232 | 39.8764 | 39.8594 | 39.3164 | 38.3228 | 37.1594 | 36.0953 | 41.7421 | 41.7325 | 41.7123 | 41.6813 | 41.6499 | 41.624 | 41.5924 | 41.5449 | 41.4316 | 40.8441 | 39.8207 | 38.6525 | 37.5904
|  | PARKSTONE SOUTH | ST |  |  | 42.9696 | 42.9651 | 42.9574 | 42.9307 | 42.9017 | 42.8697 | 42.8358 | 42.7933 | 42.7719 | 42.7038 | 42.5249 | 41.8113 | 41.1939 | 40.0756 | 40.0719 | 40.0658 | 40.041 | 40.0144 | 39.9851 | 39.9539 | 39.9131 | 39.8935 | 39.8306 | 39.6766 | 38.8813 | 38.1838 | 41.7515 | 41.7476 | 41.741 | 41.7157 | 41.6884 | 41.6583 | 41.6263 | 41.585 | 41.5649 | 41.5005 | 41.2179 | 40.4013 | 39.6831
|  | PARKSTONE SOUTH | FS |  |  | 42.9759 | 42.975 | 42.9741 | 42.9698 | 42.9648 | 42.96 | 42.9552 | 42.9488 | 42.9441 | 42.9283 | 42.9067 | 42.874 | 42.8431 | 40.0807 | 40.0799 | 40.0792 | 40.0757 | 40.0717 | 40.0679 | 40.0639 | 40.0587 | 40.0547 | 40.041 | 40.0228 | 39.9939 | 39.9668 | 41.757 | 41.7562 | 41.7554 | 41.7517 | 41.7474 | 41.7433 | 41.7391 | 41.7335 | 41.7293 | 41.715 | 41.6958 | 41.6658 | 41.6376
BRAMLEY (FLEE) | WOKINGHAM BSP | PEACOCK FARM | MINIMUM HEADROOM | SU 84770 68709 | YES | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.0517 | 20.051 | 20.0497 | 20.0483 | 20.0467 | 20.0453 | 20.0441 | 20.0429 | 20.0417 | 20.0378 | 20.0293 | 19.873 | 19.659 | 20.8124 | 20.8116 | 20.81 | 20.8081 | 20.8062 | 20.8043 | 20.8028 | 20.8013 | 20.7997 | 20.7948 | 20.7745 | 20.5612 | 20.3482
|  | PEACOCK FARM | CT |  |  | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.0518 | 20.0513 | 20.0501 | 20.0488 | 20.0475 | 20.0461 | 20.0449 | 20.0437 | 20.0425 | 20.0386 | 20.0301 | 19.8894 | 19.6753 | 20.8126 | 20.8119 | 20.8105 | 20.8088 | 20.8071 | 20.8053 | 20.8038 | 20.8023 | 20.8007 | 20.7958 | 20.7849 | 20.5775 | 20.3645
|  | PEACOCK FARM | LW |  |  | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.0517 | 20.051 | 20.0497 | 20.0483 | 20.0467 | 20.0453 | 20.0441 | 20.0429 | 20.0417 | 20.0378 | 20.0293 | 19.873 | 19.659 | 20.8124 | 20.8116 | 20.81 | 20.8081 | 20.8062 | 20.8043 | 20.8028 | 20.8013 | 20.7997 | 20.7948 | 20.7745 | 20.5612 | 20.3482
|  | PEACOCK FARM | ST |  |  | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.059 | 20.0526 | 20.0525 | 20.0522 | 20.0519 | 20.0509 | 20.0501 | 20.0493 | 20.0484 | 20.0458 | 20.0399 | 20.0333 | 20.0268 | 20.8218 | 20.8136 | 20.8135 | 20.8132 | 20.8128 | 20.8115 | 20.8104 | 20.8094 | 20.8083 | 20.805 | 20.7975 | 20.789 | 20.7216
|  | PEACOCK FARM | FS |  |  | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.9504 | 20.059 | 20.0525 | 20.0525 | 20.0522 | 20.0518 | 20.0514 | 20.0512 | 20.0508 | 20.0505 | 20.0495 | 20.0471 | 20.0441 | 20.0411 | 20.8217 | 20.8135 | 20.8135 | 20.8131 | 20.8126 | 20.8122 | 20.8118 | 20.8113 | 20.8109 | 20.8096 | 20.8066 | 20.8028 | 20.7989
WILLESDEN GSP |  | PERIVALE | MINIMUM HEADROOM | TQ 17544 82947 |  | 88.2647 | 88.2647 | 88.2647 | 88.2129 | 88.1593 | 88.1034 | 88.0455 | 87.9574 | 87.9452 | 87.9034 | 87.8409 | 87.7298 | 86.8007 | 87.1314 | 87.1258 | 87.1141 | 87.0508 | 86.9859 | 86.9202 | 86.8525 | 86.7547 | 86.7184 | 86.4145 | 85.0943 | 83.4892 | 81.9828 | 87.6551 | 87.6551 | 87.6551 | 87.5959 | 87.5309 | 87.4652 | 87.3975 | 87.2996 | 87.277 | 87.2022 | 85.9848 | 84.3743 | 82.8625
|  | PERIVALE | CT |  |  | 88.2647 | 88.2647 | 88.2647 | 88.2609 | 88.257 | 88.2531 | 88.2489 | 88.2426 | 88.2418 | 88.2392 | 88.2272 | 88.2142 | 87.3175 | 87.132 | 87.1267 | 87.1157 | 87.1011 | 87.0865 | 87.0718 | 87.0579 | 87.0417 | 87.0294 | 86.7786 | 85.5141 | 84.0071 | 82.5062 | 87.6551 | 87.6551 | 87.6551 | 87.6462 | 87.6315 | 87.6168 | 87.6029 | 87.5867 | 87.5754 | 87.5399 | 86.4047 | 84.8923 | 83.386
|  | PERIVALE | LW |  |  | 88.2647 | 88.2647 | 88.2647 | 88.2129 | 88.1593 | 88.1034 | 88.0455 | 87.9574 | 87.9452 | 87.9034 | 87.8409 | 87.7298 | 86.8007 | 87.1314 | 87.1258 | 87.1141 | 87.0508 | 86.9859 | 86.9202 | 86.8525 | 86.7547 | 86.7184 | 86.4145 | 85.0943 | 83.4892 | 81.9828 | 87.6551 | 87.6551 | 87.6551 | 87.5959 | 87.5309 | 87.4652 | 87.3975 | 87.2996 | 87.277 | 87.2022 | 85.9848 | 84.3743 | 82.8625
|  | PERIVALE | ST |  |  | 88.2647 | 88.2647 | 88.2647 | 88.2647 | 88.2647 | 88.2647 | 88.2647 | 88.2647 | 88.2647 | 88.2647 | 88.2647 | 88.2647 | 88.2647 | 87.1367 | 87.1343 | 87.1303 | 87.1254 | 87.1195 | 87.1137 | 87.1079 | 87.1013 | 87.0942 | 87.0718 | 86.8175 | 85.8605 | 84.9044 | 87.6551 | 87.6551 | 87.6551 | 87.6551 | 87.6551 | 87.6551 | 87.6531 | 87.6464 | 87.6392 | 87.6168 | 87.5672 | 86.7522 | 85.7927
|  | PERIVALE | FS |  |  | 88.2647 | 88.2647 | 88.2647 | 88.2595 | 88.2544 | 88.2493 | 88.2441 | 88.236 | 88.2133 | 88.1416 | 88.1074 | 87.9998 | 87.9098 | 87.1399 | 87.1393 | 87.1387 | 87.1315 | 87.1241 | 87.117 | 87.1099 | 87.0993 | 87.0739 | 86.9935 | 86.9394 | 86.8074 | 86.648 | 87.6551 | 87.6551 | 87.6551 | 87.6499 | 87.6448 | 87.6396 | 87.6344 | 87.6263 | 87.6037 | 87.5319 | 87.4845 | 87.3524 | 87.2369
BRAMLEY (FLEE) | FERNHURST | PETERSFIELD | MINIMUM HEADROOM | SU 74173 23420 | YES | 46.7066 | 46.7066 | 46.7066 | 46.6977 | 46.6886 | 46.6793 | 46.6698 | 46.655 | 46.6499 | 46.6339 | 46.6201 | 46.1693 | 45.108 | 43.1005 | 43.0856 | 43.0541 | 43.0236 | 42.9933 | 42.9633 | 42.9444 | 42.9256 | 42.9053 | 42.4696 | 41.255 | 40.0026 | 38.7718 | 45.1141 | 45.1141 | 45.1141 | 45.1052 | 45.0961 | 45.0868 | 45.0773 | 45.0625 | 45.0575 | 45.0414 | 44.3225 | 43.0817 | 41.8621
|  | PETERSFIELD | CT |  |  | 46.7066 | 46.7066 | 46.7066 | 46.7066 | 46.7066 | 46.7066 | 46.7066 | 46.7066 | 46.7066 | 46.7066 | 46.7066 | 46.1693 | 45.108 | 43.1005 | 43.0856 | 43.0541 | 43.0236 | 42.9933 | 42.9633 | 42.9444 | 42.9256 | 42.9053 | 42.4696 | 41.255 | 40.0026 | 38.7718 | 45.1141 | 45.1141 | 45.1141 | 45.1141 | 45.1141 | 45.1141 | 45.1141 | 45.1141 | 45.1141 | 45.1141 | 44.3225 | 43.0817 | 41.8621
|  | PETERSFIELD | LW |  |  | 46.7066 | 46.7066 | 46.7066 | 46.7066 | 46.7066 | 46.7066 | 46.7066 | 46.7066 | 46.7066 | 46.7066 | 46.7066 | 46.4815 | 45.4195 | 43.1043 | 43.0914 | 43.0643 | 43.0379 | 43.0118 | 42.9927 | 42.9737 | 42.9549 | 42.9346 | 42.8319 | 41.6173 | 40.3648 | 39.1331 | 45.1141 | 45.1141 | 45.1141 | 45.1141 | 45.1141 | 45.1141 | 45.1141 | 45.1141 | 45.1141 | 45.1141 | 44.6815 | 43.4405 | 42.2202
|  | PETERSFIELD | ST |  |  | 46.7066 | 46.7066 | 46.7066 | 46.6977 | 46.6886 | 46.6793 | 46.6698 | 46.655 | 46.6499 | 46.6339 | 46.6201 | 46.574 | 46.5606 | 43.1136 | 43.1068 | 43.0952 | 43.072 | 43.0458 | 43.0212 | 42.9966 | 42.9689 | 42.9501 | 42.8937 | 42.8145 | 42.218 | 41.4034 | 45.1141 | 45.1141 | 45.1141 | 45.1052 | 45.0961 | 45.0868 | 45.0773 | 45.0625 | 45.0575 | 45.0414 | 45.0276 | 44.9815 | 44.4683
|  | PETERSFIELD | FS |  |  | 46.7066 | 46.7066 | 46.7066 | 46.7066 | 46.7066 | 46.7066 | 46.7066 | 46.7066 | 46.7066 | 46.7066 | 46.7066 | 46.7066 | 46.7066 | 43.1246 | 43.1237 | 43.1229 | 43.1189 | 43.1142 | 43.109 | 43.1038 | 43.0972 | 43.0918 | 43.0763 | 43.0516 | 43.028 | 43.0058 | 45.1141 | 45.1141 | 45.1141 | 45.1141 | 45.1141 | 45.1141 | 45.1141 | 45.1141 | 45.1141 | 45.1141 | 45.1141 | 45.1141 | 45.1141
IVER 132KV | CHALVEY BSP | PETERSFIELD AVENUE | MINIMUM HEADROOM | SU 98108 80286 | YES | 50.5834 | 50.5834 | 50.5834 | 50.5644 | 50.5449 | 50.5249 | 50.504 | 50.4715 | 50.4603 | 50.4233 | 49.915 | 48.3426 | 46.8425 | 49.1595 | 49.1511 | 49.1392 | 49.1199 | 49.0896 | 49.0566 | 49.0217 | 48.8527 | 48.7106 | 48.4051 | 46.9552 | 45.2889 | 43.5299 | 49.4087 | 49.3841 | 49.349 | 49.3061 | 49.2588 | 49.193 | 49.0684 | 48.734 | 48.3404 | 47.4099 | 45.7599 | 43.9418 | 42.2043
|  | PETERSFIELD AVENUE | CT |  |  | 50.5834 | 50.5834 | 50.5834 | 50.5833 | 50.5829 | 50.5825 | 50.5818 | 50.5803 | 50.58 | 50.5786 | 50.0422 | 48.4776 | 46.9751 | 49.1598 | 49.1516 | 49.1401 | 49.1258 | 49.1102 | 49.0925 | 49.0683 | 48.9036 | 48.7621 | 48.4596 | 47.0895 | 45.431 | 43.6832 | 49.4096 | 49.3856 | 49.3516 | 49.3101 | 49.2647 | 49.2135 | 49.14 | 48.8267 | 48.4813 | 47.554 | 45.9057 | 44.0954 | 42.3555
|  | PETERSFIELD AVENUE | LW |  |  | 50.5834 | 50.5834 | 50.5834 | 50.5829 | 50.5817 | 50.58 | 50.5775 | 50.5725 | 50.5717 | 50.5673 | 49.915 | 48.3426 | 46.8425 | 49.1595 | 49.1511 | 49.1392 | 49.1242 | 49.1074 | 49.0838 | 49.0294 | 48.8527 | 48.7106 | 48.4051 | 46.9552 | 45.2889 | 43.5299 | 49.4087 | 49.3841 | 49.349 | 49.3061 | 49.2588 | 49.193 | 49.0684 | 48.734 | 48.3404 | 47.4099 | 45.7599 | 43.9418 | 42.2043
|  | PETERSFIELD AVENUE | ST |  |  | 50.5834 | 50.5834 | 50.5834 | 50.5644 | 50.5449 | 50.5249 | 50.504 | 50.4715 | 50.4603 | 50.4233 | 50.3911 | 50.2824 | 49.312 | 49.1662 | 49.1557 | 49.1484 | 49.1199 | 49.0896 | 49.0566 | 49.0217 | 48.9728 | 48.9479 | 48.7177 | 48.3227 | 47.3815 | 46.3343 | 49.4284 | 49.3976 | 49.3763 | 49.3294 | 49.2782 | 49.22 | 49.1576 | 49.077 | 49.0255 | 48.6127 | 47.5222 | 46.2508 | 45.11
|  | PETERSFIELD AVENUE | FS |  |  | 50.5834 | 50.5834 | 50.5834 | 50.5805 | 50.5777 | 50.5748 | 50.5718 | 50.5673 | 50.5544 | 50.5133 | 50.4934 | 50.4292 | 50.375 | 49.1687 | 49.1632 | 49.16 | 49.1527 | 49.1452 | 49.137 | 49.1285 | 49.118 | 49.0998 | 49.0471 | 49.0063 | 48.9188 | 48.7274 | 49.436 | 49.4198 | 49.4102 | 49.3944 | 49.3781 | 49.3595 | 49.3401 | 49.3181 | 49.2894 | 49.2143 | 49.133 | 49.0002 | 48.6787
MANNINGTON GSP | SALISBURY | PETERSFINGER | MINIMUM HEADROOM | SU 15608 29334 | YES | 27.1317 | 27.1317 | 27.1317 | 27.1221 | 27.1118 | 27.1007 | 27.0884 | 27.0674 | 27.0595 | 27.0275 | 26.989 | 26.8785 | 26.5945 | 25.3669 | 25.364 | 25.3579 | 25.3483 | 25.3328 | 25.3174 | 25.3003 | 25.2668 | 25.2542 | 25.2086 | 25.0596 | 24.1985 | 23.4532 | 25.3869 | 25.3869 | 25.3869 | 25.3774 | 25.3671 | 25.3559 | 25.3436 | 25.3227 | 25.3147 | 25.2828 | 25.2443 | 25.0958 | 24.3691
|  | PETERSFINGER | CT |  |  | 27.1317 | 27.1317 | 27.1317 | 27.1308 | 27.1291 | 27.1266 | 27.123 | 27.115 | 27.1136 | 27.106 | 27.043 | 26.9726 | 26.6642 | 25.3669 | 25.364 | 25.3579 | 25.3511 | 25.3436 | 25.3353 | 25.324 | 25.3076 | 25.2981 | 25.2683 | 25.1007 | 24.28 | 23.5212 | 25.3869 | 25.3869 | 25.3869 | 25.386 | 25.3843 | 25.3819 | 25.3782 | 25.3703 | 25.3688 | 25.3612 | 25.2982 | 25.1776 | 24.4373
|  | PETERSFINGER | LW |  |  | 27.1317 | 27.1317 | 27.1317 | 27.1287 | 27.1227 | 27.1132 | 27.1 | 27.0735 | 27.069 | 27.0457 | 26.989 | 26.8785 | 26.5945 | 25.3672 | 25.3645 | 25.3588 | 25.3504 | 25.3389 | 25.3225 | 25.3016 | 25.2668 | 25.2542 | 25.2086 | 25.0596 | 24.1985 | 23.4532 | 25.3869 | 25.3869 | 25.3869 | 25.384 | 25.3779 | 25.3684 | 25.3552 | 25.3288 | 25.3242 | 25.3009 | 25.2443 | 25.0958 | 24.3691
|  | PETERSFINGER | ST |  |  | 27.1317 | 27.1317 | 27.1317 | 27.1221 | 27.1118 | 27.1007 | 27.0884 | 27.0674 | 27.0595 | 27.0275 | 26.9938 | 26.8797 | 26.8398 | 25.3706 | 25.3658 | 25.3622 | 25.3483 | 25.3328 | 25.3174 | 25.3003 | 25.2736 | 25.2602 | 25.2132 | 25.1559 | 25.0185 | 24.6639 | 25.3869 | 25.3869 | 25.3869 | 25.3774 | 25.3671 | 25.3559 | 25.3436 | 25.3227 | 25.3147 | 25.2828 | 25.2491 | 25.135 | 25.095
|  | PETERSFINGER | FS |  |  | 27.1317 | 27.1317 | 27.1317 | 27.1316 | 27.1316 | 27.1315 | 27.1314 | 27.1311 | 27.1301 | 27.1244 | 27.1198 | 27.098 | 27.0767 | 25.3742 | 25.3712 | 25.371 | 25.3701 | 25.369 | 25.3675 | 25.3657 | 25.3632 | 25.3601 | 25.3485 | 25.335 | 25.3047 | 25.2755 | 25.3869 | 25.3869 | 25.3869 | 25.3869 | 25.3868 | 25.3868 | 25.3866 | 25.3864 | 25.3854 | 25.3796 | 25.3751 | 25.3533 | 25.332
MELKSHAM GSP | AMESBURY | PEWSEY | MINIMUM HEADROOM | SU 14710 59252 | YES | 21.009 | 20.9587 | 20.8523 | 20.748 | 20.6418 | 20.5542 | 20.4666 | 20.3772 | 20.2856 | 20.0134 | 19.5634 | 19.0892 | 18.6435 | 18.2671 | 18.2065 | 18.0782 | 17.9533 | 17.8288 | 17.7263 | 17.6239 | 17.5199 | 17.4125 | 17.0938 | 16.5674 | 16.0145 | 15.4915 | 19.4548 | 19.4548 | 19.4548 | 19.4412 | 19.4279 | 19.4145 | 19.4009 | 19.3797 | 19.3206 | 19.1326 | 18.8899 | 18.3369 | 17.8136
|  | PEWSEY | CT |  |  | 21.023 | 20.9805 | 20.8905 | 20.8031 | 20.7149 | 20.6265 | 20.5409 | 20.4553 | 20.3643 | 20.0954 | 19.644 | 19.178 | 18.7297 | 18.284 | 18.2327 | 18.1243 | 18.019 | 17.9144 | 17.8107 | 17.7104 | 17.6101 | 17.5033 | 17.1879 | 16.6602 | 16.1156 | 15.59 | 19.4548 | 19.4548 | 19.4548 | 19.4546 | 19.4542 | 19.4537 | 19.453 | 19.4514 | 19.4511 | 19.4496 | 18.9827 | 18.4379 | 17.9121
|  | PEWSEY | LW |  |  | 21.009 | 20.9587 | 20.8523 | 20.748 | 20.6418 | 20.5542 | 20.4666 | 20.3772 | 20.2856 | 20.0134 | 19.5634 | 19.0892 | 18.6435 | 18.2671 | 18.2065 | 18.0782 | 17.9533 | 17.8288 | 17.7263 | 17.6239 | 17.5199 | 17.4125 | 17.0938 | 16.5674 | 16.0145 | 15.4915 | 19.4548 | 19.4548 | 19.4548 | 19.4542 | 19.4529 | 19.451 | 19.4484 | 19.443 | 19.4421 | 19.4164 | 18.8899 | 18.3369 | 17.8136
|  | PEWSEY | ST |  |  | 21.0219 | 20.9839 | 20.9185 | 20.8383 | 20.7409 | 20.6906 | 20.6407 | 20.5819 | 20.5195 | 20.336 | 20.0402 | 19.7345 | 19.4401 | 18.2826 | 18.2368 | 18.1581 | 18.0614 | 17.9448 | 17.8859 | 17.8274 | 17.7586 | 17.6854 | 17.4705 | 17.124 | 16.7677 | 16.4229 | 19.4548 | 19.4548 | 19.4548 | 19.4546 | 19.4544 | 19.454 | 19.4535 | 19.4522 | 19.4516 | 19.4484 | 19.4442 | 19.0902 | 18.7454
|  | PEWSEY | FS |  |  | 21.0877 | 21.0839 | 21.0802 | 21.0494 | 21.0158 | 20.9863 | 20.9567 | 20.9148 | 20.8324 | 20.5766 | 20.3791 | 19.9901 | 19.6524 | 18.362 | 18.3574 | 18.3529 | 18.3186 | 18.2808 | 18.248 | 18.2151 | 18.169 | 18.0818 | 17.8121 | 17.5925 | 17.1846 | 16.8297 | 19.4548 | 19.4548 | 19.4548 | 19.4412 | 19.4279 | 19.4145 | 19.4009 | 19.3797 | 19.3206 | 19.1326 | 19.0427 | 18.7581 | 18.5195
CHICKERELL GSP | CHICKERELL BSP | PIDDLETRENTHIDE | MINIMUM HEADROOM | SY 70169 99809 | YES | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.1291 | 8.1253 | 8.1173 | 8.1095 | 8.1016 | 8.0702 | 8.0391 | 8.0082 | 7.9749 | 7.8764 | 7.7122 | 7.5412 | 7.3728 | 8.4656 | 8.462 | 8.4544 | 8.447 | 8.4396 | 8.41 | 8.3806 | 8.3515 | 8.3201 | 8.2272 | 8.0723 | 7.9111 | 7.7523
|  | PIDDLETRENTHIDE | CT |  |  | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.1291 | 8.1253 | 8.1173 | 8.1095 | 8.1016 | 8.0939 | 8.0627 | 8.0319 | 7.9985 | 7.9 | 7.7358 | 7.5648 | 7.3967 | 8.4656 | 8.462 | 8.4544 | 8.447 | 8.4396 | 8.4323 | 8.4029 | 8.3738 | 8.3424 | 8.2495 | 8.0946 | 7.9334 | 7.7748
|  | PIDDLETRENTHIDE | LW |  |  | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.1291 | 8.1253 | 8.1173 | 8.1095 | 8.1016 | 8.0702 | 8.0391 | 8.0082 | 7.9749 | 7.8764 | 7.7122 | 7.5412 | 7.3728 | 8.4656 | 8.462 | 8.4544 | 8.447 | 8.4396 | 8.41 | 8.3806 | 8.3515 | 8.3201 | 8.2272 | 8.0723 | 7.9111 | 7.7523
|  | PIDDLETRENTHIDE | ST |  |  | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.1317 | 8.1295 | 8.1259 | 8.1214 | 8.1161 | 8.0971 | 8.0785 | 8.0574 | 8.0347 | 7.9683 | 7.8588 | 7.7486 | 7.6391 | 8.4679 | 8.4659 | 8.4625 | 8.4583 | 8.4532 | 8.4354 | 8.4178 | 8.3979 | 8.3765 | 8.3139 | 8.2106 | 8.1067 | 8.0035
|  | PIDDLETRENTHIDE | FS |  |  | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.45 | 8.1351 | 8.1348 | 8.1345 | 8.1332 | 8.1318 | 8.1254 | 8.1192 | 8.1112 | 8.1024 | 8.0767 | 8.0352 | 7.9949 | 7.9565 | 8.4711 | 8.4708 | 8.4706 | 8.4694 | 8.468 | 8.462 | 8.4562 | 8.4486 | 8.4403 | 8.4161 | 8.377 | 8.339 | 8.3027
BRAMLEY (FLEE) | FERNHURST | PLAISTOW | MINIMUM HEADROOM | TQ 02071 29626 | YES | 19.3688 | 19.3235 | 19.2278 | 19.1327 | 19.036 | 18.9543 | 18.9076 | 18.8578 | 18.8097 | 18.6576 | 18.3787 | 18.0464 | 17.7986 | 19.5514 | 19.5514 | 19.5514 | 19.5491 | 19.5444 | 19.5369 | 19.5159 | 19.4583 | 19.4019 | 19.232 | 18.9061 | 18.5356 | 18.2447 | 19.3459 | 19.2927 | 19.1803 | 19.0691 | 18.9563 | 18.8598 | 18.8054 | 18.748 | 18.6918 | 18.5223 | 18.1973 | 17.8275 | 17.5375
|  | PLAISTOW | CT |  |  | 19.3699 | 19.3252 | 19.2307 | 19.1383 | 19.0462 | 18.9543 | 18.9076 | 18.8578 | 18.8097 | 18.6645 | 18.3804 | 18.08 | 17.8212 | 19.5514 | 19.5514 | 19.5514 | 19.5507 | 19.5494 | 19.5474 | 19.5159 | 19.4583 | 19.4019 | 19.232 | 18.9061 | 18.5619 | 18.2601 | 19.3473 | 19.2947 | 19.1837 | 19.0753 | 18.9674 | 18.8598 | 18.8054 | 18.748 | 18.6918 | 18.5223 | 18.1973 | 17.854 | 17.553
|  | PLAISTOW | LW |  |  | 19.3688 | 19.3235 | 19.2278 | 19.1327 | 19.036 | 18.9843 | 18.9299 | 18.8656 | 18.8151 | 18.6576 | 18.3787 | 18.0464 | 17.7986 | 19.5514 | 19.5514 | 19.5514 | 19.5491 | 19.5444 | 19.5369 | 19.5266 | 19.4734 | 19.4145 | 19.2322 | 18.9115 | 18.5356 | 18.2447 | 19.3459 | 19.2927 | 19.1803 | 19.0691 | 18.9563 | 18.8969 | 18.8348 | 18.7629 | 18.7042 | 18.5224 | 18.2026 | 17.8275 | 17.5375
|  | PLAISTOW | ST |  |  | 19.4272 | 19.3429 | 19.2826 | 19.208 | 19.1176 | 19.0754 | 19.0332 | 18.9986 | 18.9643 | 18.8579 | 18.6853 | 18.4696 | 18.2915 | 19.5514 | 19.5514 | 19.5514 | 19.5509 | 19.55 | 19.5485 | 19.5463 | 19.5415 | 19.5392 | 19.4606 | 19.2602 | 19.0163 | 18.8102 | 19.4145 | 19.3155 | 19.2446 | 19.1571 | 19.0512 | 19.0019 | 18.9526 | 18.9129 | 18.873 | 18.7503 | 18.5504 | 18.307 | 18.1015
|  | PLAISTOW | FS |  |  | 19.4886 | 19.4361 | 19.4328 | 19.4167 | 19.3977 | 19.3833 | 19.3689 | 19.3502 | 19.3344 | 19.2855 | 19.2187 | 19.1307 | 19.0477 | 19.5514 | 19.5514 | 19.5514 | 19.5508 | 19.5502 | 19.5495 | 19.5488 | 19.5477 | 19.5443 | 19.5316 | 19.5241 | 19.4947 | 19.4677 | 19.4866 | 19.425 | 19.4211 | 19.4023 | 19.3801 | 19.3633 | 19.3465 | 19.3247 | 19.3068 | 19.2515 | 19.1744 | 19.0762 | 18.9834
MINETY GSP | STRATTON (2 X 90) | PLESSEY | MINIMUM HEADROOM | SU 16381 86720 | YES | 22.8966 | 22.8766 | 21.7842 | 21.6909 | 21.5974 | 21.4981 | 21.3987 | 21.2994 | 21.2528 | 21.1117 | 20.8589 | 20.0293 | 18.7555 | 18.5155 | 18.4962 | 17.4051 | 17.3131 | 17.221 | 17.1248 | 17.0287 | 16.9326 | 16.8895 | 16.7592 | 16.5301 | 16.3628 | 16.0183 | 22.6531 | 22.6333 | 21.5412 | 21.4482 | 21.3551 | 21.2566 | 21.1581 | 21.0596 | 21.014 | 20.8757 | 20.6292 | 20.3186 | 18.8569
|  | PLESSEY | CT |  |  | 22.9896 | 22.9769 | 22.3201 | 22.2628 | 22.2053 | 22.1478 | 22.0841 | 22.0204 | 21.9882 | 21.8899 | 21.0347 | 20.1196 | 18.846 | 18.6084 | 18.5964 | 17.9408 | 17.8846 | 17.8284 | 17.7722 | 17.7117 | 17.6513 | 17.6225 | 17.535 | 16.7035 | 16.3679 | 16.1113 | 22.7461 | 22.7335 | 22.077 | 22.02 | 21.9629 | 21.9057 | 21.8429 | 21.78 | 21.7487 | 21.6533 | 20.8044 | 20.4248 | 18.9631
|  | PLESSEY | LW |  |  | 22.8966 | 22.8766 | 21.7842 | 21.6909 | 21.5974 | 21.4981 | 21.3987 | 21.2994 | 21.2528 | 21.1117 | 20.8589 | 20.0293 | 18.7555 | 18.5155 | 18.4962 | 17.4051 | 17.3131 | 17.221 | 17.1248 | 17.0287 | 16.9326 | 16.8895 | 16.7592 | 16.5301 | 16.3628 | 16.0183 | 22.6531 | 22.6333 | 21.5412 | 21.4482 | 21.3551 | 21.2566 | 21.1581 | 21.0596 | 21.014 | 20.8757 | 20.6292 | 20.3186 | 18.8569
|  | PLESSEY | ST |  |  | 23.0367 | 23.0281 | 22.5906 | 22.5521 | 22.5131 | 22.4733 | 22.4334 | 22.3908 | 22.3691 | 22.3031 | 22.1807 | 22.08 | 21.674 | 18.6553 | 18.6472 | 18.2103 | 18.1728 | 18.1348 | 18.0963 | 18.0578 | 18.0173 | 17.998 | 17.9394 | 17.8332 | 17.7509 | 17.6339 | 22.7931 | 22.7846 | 22.3472 | 22.309 | 22.2703 | 22.2308 | 22.1913 | 22.1493 | 22.1282 | 22.0642 | 21.946 | 21.8502 | 21.7199
|  | PLESSEY | FS |  |  | 23.085 | 23.0811 | 22.8632 | 22.8445 | 22.8258 | 22.8066 | 22.7874 | 22.7679 | 22.7579 | 22.7275 | 22.6713 | 22.6247 | 22.5594 | 18.703 | 18.6992 | 18.4813 | 18.463 | 18.4445 | 18.4257 | 18.407 | 18.388 | 18.3789 | 18.3514 | 18.3017 | 18.2631 | 18.2061 | 22.8412 | 22.8374 | 22.6194 | 22.6009 | 22.5822 | 22.5631 | 22.5441 | 22.5247 | 22.5149 | 22.4853 | 22.4308 | 22.3863 | 22.3232
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | PLESSEY TITCHFIELD | MINIMUM HEADROOM | SU 53390 06922 | YES | 44.4439 | 44.4439 | 44.4439 | 44.4367 | 44.4292 | 44.4217 | 44.4139 | 44.4017 | 44.4002 | 44.0257 | 43.156 | 42.1319 | 41.1264 | 41.62 | 41.6108 | 41.5928 | 41.5738 | 41.2803 | 41.1436 | 41.0058 | 40.8682 | 40.7237 | 40.2715 | 39.2736 | 38.0889 | 36.9229 | 43.2932 | 43.2838 | 43.157 | 42.9003 | 42.6459 | 42.5275 | 42.4081 | 42.2888 | 42.1636 | 41.7389 | 40.7299 | 39.5315 | 38.3518
|  | PLESSEY TITCHFIELD | CT |  |  | 44.4439 | 44.4439 | 44.4439 | 44.4367 | 44.4292 | 44.4217 | 44.4139 | 44.4017 | 44.4002 | 44.0328 | 43.156 | 42.1319 | 41.1264 | 41.622 | 41.614 | 41.5984 | 41.5766 | 41.4457 | 41.1861 | 41.0404 | 40.8907 | 40.7447 | 40.2876 | 39.2736 | 38.0889 | 36.9229 | 43.2953 | 43.2871 | 43.2426 | 43.0141 | 42.7874 | 42.5614 | 42.4341 | 42.3027 | 42.1759 | 41.7557 | 40.7299 | 39.5315 | 38.3518
|  | PLESSEY TITCHFIELD | LW |  |  | 44.4439 | 44.4439 | 44.4439 | 44.4439 | 44.4439 | 44.4439 | 44.4439 | 44.4439 | 44.4152 | 44.0257 | 43.1717 | 42.1725 | 41.1734 | 41.62 | 41.6108 | 41.5928 | 41.5738 | 41.2803 | 41.1436 | 41.0058 | 40.8682 | 40.7237 | 40.2715 | 39.2803 | 38.1206 | 36.961 | 43.2932 | 43.2838 | 43.157 | 42.9003 | 42.6459 | 42.5275 | 42.4081 | 42.2888 | 42.1636 | 41.7389 | 40.7359 | 39.5624 | 38.389
|  | PLESSEY TITCHFIELD | ST |  |  | 44.4439 | 44.4439 | 44.4439 | 44.4439 | 44.4439 | 44.4439 | 44.4439 | 44.4439 | 44.4439 | 44.4439 | 43.9068 | 43.2509 | 42.6125 | 41.6303 | 41.6152 | 41.6039 | 41.5905 | 41.5498 | 41.433 | 41.3159 | 41.2221 | 41.1233 | 40.8146 | 40.1335 | 39.3723 | 38.6313 | 43.3039 | 43.2883 | 43.2766 | 43.1222 | 42.8795 | 42.7783 | 42.6768 | 42.5955 | 42.5099 | 42.2424 | 41.5992 | 40.8289 | 40.0792
|  | PLESSEY TITCHFIELD | FS |  |  | 44.4439 | 44.4439 | 44.4439 | 44.4417 | 44.4396 | 44.4374 | 44.4352 | 44.4317 | 44.4222 | 44.3918 | 44.3773 | 44.3318 | 44.2937 | 41.6541 | 41.632 | 41.6309 | 41.6256 | 41.62 | 41.6155 | 41.6109 | 41.6046 | 41.5928 | 41.5556 | 41.5255 | 41.4119 | 41.0291 | 43.3284 | 43.3057 | 43.3045 | 43.2991 | 43.2934 | 43.2888 | 43.2842 | 43.2777 | 43.2659 | 43.2285 | 43.0792 | 42.7451 | 42.4082
MANNINGTON GSP | POOLE PS (HAMWORTHY) | POOLE | MINIMUM HEADROOM | SZ 01091 90595 |  | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48
|  | POOLE | CT |  |  | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48
|  | POOLE | LW |  |  | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48
|  | POOLE | ST |  |  | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48
|  | POOLE | FS |  |  | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48 | 30.48
LOVEDEAN GSP | WYMERING BSP | PORTCHESTER | MINIMUM HEADROOM | SU 62043 05575 | YES | 35.6577 | 35.6577 | 35.6577 | 35.6209 | 35.583 | 35.5442 | 35.5032 | 35.4388 | 35.4305 | 35.4022 | 35.2379 | 33.3428 | 31.5557 | 35.0188 | 35.0188 | 35.0188 | 34.9819 | 34.9435 | 34.8949 | 34.8344 | 34.7506 | 34.7218 | 34.591 | 32.8792 | 30.6857 | 28.5853 | 34.7544 | 34.7544 | 34.7544 | 34.7175 | 34.6797 | 34.6409 | 34.5999 | 34.5355 | 34.5271 | 34.4988 | 34.3551 | 32.4154 | 30.465
|  | PORTCHESTER | CT |  |  | 35.6577 | 35.6577 | 35.6577 | 35.6209 | 35.583 | 35.5442 | 35.5032 | 35.4388 | 35.4305 | 35.4022 | 35.2379 | 33.3428 | 31.5557 | 35.0188 | 35.0188 | 35.0188 | 34.9819 | 34.9435 | 34.8949 | 34.8344 | 34.7506 | 34.7218 | 34.591 | 32.8938 | 30.6857 | 28.5853 | 34.7544 | 34.7544 | 34.7544 | 34.7175 | 34.6797 | 34.6409 | 34.5999 | 34.5355 | 34.5271 | 34.4988 | 34.3551 | 32.4154 | 30.465
|  | PORTCHESTER | LW |  |  | 35.6577 | 35.6577 | 35.6577 | 35.6531 | 35.6469 | 35.6389 | 35.6291 | 35.6111 | 35.6082 | 35.5946 | 35.2721 | 33.4714 | 31.7235 | 35.0188 | 35.0188 | 35.0188 | 35.0112 | 34.9918 | 34.9642 | 34.9348 | 34.8975 | 34.8741 | 34.6673 | 32.8792 | 30.7655 | 28.7042 | 34.7544 | 34.7544 | 34.7544 | 34.7498 | 34.7436 | 34.7356 | 34.7258 | 34.7078 | 34.7048 | 34.6912 | 34.4825 | 32.5187 | 30.6073
|  | PORTCHESTER | ST |  |  | 35.6577 | 35.6577 | 35.6577 | 35.6544 | 35.6508 | 35.6468 | 35.6423 | 35.6344 | 35.6313 | 35.6184 | 35.6042 | 35.3962 | 34.2642 | 35.0188 | 35.0188 | 35.0188 | 35.0155 | 35.0118 | 35.0076 | 34.9907 | 34.9696 | 34.9525 | 34.8957 | 34.4236 | 33.0272 | 31.6948 | 34.7544 | 34.7544 | 34.7544 | 34.7511 | 34.7474 | 34.7434 | 34.7389 | 34.731 | 34.7279 | 34.715 | 34.7008 | 34.6191 | 33.3826
|  | PORTCHESTER | FS |  |  | 35.6577 | 35.6577 | 35.6577 | 35.6577 | 35.6577 | 35.6576 | 35.6576 | 35.6575 | 35.657 | 35.6543 | 35.6521 | 35.6418 | 35.6317 | 35.0188 | 35.0188 | 35.0188 | 35.0187 | 35.0187 | 35.0187 | 35.0186 | 35.0185 | 35.018 | 35.0139 | 34.9731 | 34.9161 | 34.8165 | 34.7544 | 34.7544 | 34.7544 | 34.7544 | 34.7543 | 34.7543 | 34.7542 | 34.7541 | 34.7536 | 34.7509 | 34.7488 | 34.7384 | 34.7283
CHICKERELL GSP | CHICKERELL BSP | PORTLAND | MINIMUM HEADROOM | SY 68307 73941 | YES | 21.8806 | 21.8648 | 20.9044 | 20.8257 | 20.747 | 20.6682 | 20.5895 | 20.5108 | 20.4793 | 20.3848 | 20.2274 | 19.9944 | 18.8445 | 17.7006 | 17.6287 | 16.5984 | 16.4557 | 16.3084 | 16.0297 | 15.7524 | 15.4784 | 15.2387 | 14.5219 | 13.2629 | 12.0041 | 10.6804 | 21.0988 | 21.0797 | 20.115 | 20.0325 | 19.9496 | 19.8589 | 19.7682 | 19.6778 | 19.6338 | 19.5019 | 18.7984 | 17.5737 | 16.2836
|  | PORTLAND | CT |  |  | 21.9625 | 21.953 | 21.3768 | 21.3295 | 21.2823 | 21.2351 | 21.1878 | 21.1406 | 21.1217 | 21.065 | 20.376 | 20.104 | 18.9544 | 17.7825 | 17.7169 | 17.0707 | 16.9595 | 16.8437 | 16.7256 | 16.4797 | 16.2372 | 16.01 | 15.3311 | 13.5405 | 12.1332 | 10.8099 | 21.1807 | 21.1678 | 20.5874 | 20.5363 | 20.4849 | 20.4334 | 20.3743 | 20.3153 | 20.2839 | 20.1898 | 19.0723 | 17.699 | 16.4093
|  | PORTLAND | LW |  |  | 21.8806 | 21.8648 | 20.9044 | 20.8257 | 20.747 | 20.6682 | 20.5895 | 20.5108 | 20.4793 | 20.3848 | 20.2274 | 19.9944 | 18.8445 | 17.7006 | 17.6287 | 16.5984 | 16.4557 | 16.3084 | 16.0297 | 15.7524 | 15.4784 | 15.2387 | 14.5219 | 13.2629 | 12.0041 | 10.6804 | 21.0988 | 21.0797 | 20.115 | 20.0325 | 19.9496 | 19.8589 | 19.7682 | 19.6778 | 19.6338 | 19.5019 | 18.7984 | 17.5737 | 16.2836
|  | PORTLAND | ST |  |  | 22.0034 | 21.9971 | 21.6129 | 21.5814 | 21.55 | 21.5185 | 21.487 | 21.4555 | 21.4429 | 21.4051 | 21.3421 | 21.3043 | 21.2351 | 17.9378 | 17.8142 | 17.3968 | 17.3286 | 17.25 | 17.1246 | 17 | 16.8354 | 16.6807 | 16.2224 | 15.419 | 14.6276 | 13.815 | 21.2285 | 21.2151 | 20.829 | 20.7953 | 20.7609 | 20.7238 | 20.6867 | 20.6472 | 20.6261 | 20.563 | 20.4556 | 20.1548 | 19.3638
|  | PORTLAND | FS |  |  | 22.0443 | 22.0412 | 21.8491 | 21.8334 | 21.8176 | 21.8019 | 21.7861 | 21.7704 | 21.7641 | 21.7452 | 21.7137 | 21.6948 | 21.6602 | 18.0153 | 17.9976 | 17.8002 | 17.7737 | 17.7439 | 17.7028 | 17.6621 | 17.6156 | 17.5544 | 17.3733 | 17.0565 | 16.7476 | 16.4299 | 21.2716 | 21.2676 | 21.0752 | 21.0588 | 21.0422 | 21.0249 | 21.0077 | 20.9901 | 20.9805 | 20.9519 | 20.9032 | 20.8669 | 20.8152
LOVEDEAN GSP | PORTSMOUTH BSP | PORTSMOUTH | MINIMUM HEADROOM | SZ 63405 99685 | YES | 56.8619 | 56.8557 | 56.8452 | 56.8285 | 56.8086 | 56.7933 | 56.775 | 56.7467 | 56.5084 | 55.0568 | 52.5557 | 51.597 | 50.8035 | 53.2389 | 53.2202 | 53.1887 | 53.1384 | 53.0789 | 52.8734 | 52.6252 | 52.2393 | 51.8112 | 50.1768 | 47.2606 | 46.1313 | 45.1964 | 55.7861 | 55.7807 | 55.7717 | 55.7572 | 55.7331 | 55.5213 | 55.27 | 54.8794 | 54.4462 | 52.8037 | 49.9737 | 48.8889 | 47.9909
|  | PORTSMOUTH | CT |  |  | 56.8619 | 56.8557 | 56.8452 | 56.8285 | 56.8086 | 56.7933 | 56.775 | 56.7467 | 56.5084 | 55.0568 | 52.5557 | 51.597 | 50.8035 | 53.2389 | 53.2202 | 53.1887 | 53.1384 | 53.0789 | 52.8734 | 52.6252 | 52.2393 | 51.8112 | 50.1768 | 47.2606 | 46.1313 | 45.1964 | 55.7861 | 55.7807 | 55.7717 | 55.7572 | 55.7331 | 55.5213 | 55.27 | 54.8794 | 54.4462 | 52.8037 | 49.9737 | 48.8889 | 47.9909
|  | PORTSMOUTH | LW |  |  | 56.8626 | 56.8568 | 56.8472 | 56.8312 | 56.8122 | 56.796 | 56.7778 | 56.7494 | 56.5416 | 55.09 | 52.5888 | 51.6301 | 50.8363 | 53.241 | 53.2235 | 53.1946 | 53.1467 | 53.0896 | 52.9104 | 52.6621 | 52.2763 | 51.8484 | 50.2151 | 47.2996 | 46.1702 | 45.2351 | 55.7867 | 55.7817 | 55.7734 | 55.7596 | 55.7432 | 55.5587 | 55.3075 | 54.9169 | 54.4837 | 52.8413 | 50.0111 | 48.9263 | 48.0281
|  | PORTSMOUTH | ST |  |  | 56.865 | 56.8611 | 56.8551 | 56.8446 | 56.8319 | 56.8201 | 56.807 | 56.7881 | 56.7665 | 56.0906 | 54.2828 | 53.6425 | 53.1405 | 53.2481 | 53.2363 | 53.2183 | 53.1869 | 53.1487 | 53.1134 | 53.061 | 52.803 | 52.5092 | 51.3442 | 49.2834 | 48.5409 | 47.9494 | 55.7888 | 55.7854 | 55.7802 | 55.7712 | 55.7602 | 55.7501 | 55.7112 | 55.4501 | 55.1526 | 53.9734 | 51.9279 | 51.2034 | 50.6353
|  | PORTSMOUTH | FS |  |  | 56.8671 | 56.8648 | 56.8616 | 56.8536 | 56.845 | 56.8375 | 56.8297 | 56.8176 | 56.798 | 56.7291 | 56.5576 | 56.1978 | 55.8869 | 53.2545 | 53.2474 | 53.2379 | 53.2189 | 53.1981 | 53.1807 | 53.1622 | 53.1338 | 53.097 | 52.7543 | 51.8753 | 51.4793 | 51.1368 | 55.7906 | 55.7886 | 55.7858 | 55.7786 | 55.7708 | 55.764 | 55.7569 | 55.746 | 55.7276 | 55.4015 | 54.5119 | 54.1117 | 53.7656
BRAMLEY (ANDO-THAT) | ANDOVER BSP | PORTWAY | MINIMUM HEADROOM | SU 34402 46001 | YES | 26.1373 | 26.0792 | 24.961 | 24.7914 | 24.6215 | 24.4486 | 24.2756 | 24.0998 | 23.9737 | 23.5956 | 22.9513 | 22.3366 | 21.6698 | 26.1125 | 26.0585 | 24.949 | 24.7877 | 24.6125 | 24.4217 | 24.2308 | 24.0374 | 23.8922 | 23.4574 | 22.7166 | 22.0003 | 21.2333 | 26.1906 | 26.1315 | 25.0113 | 24.8396 | 24.6677 | 24.4928 | 24.3177 | 24.1399 | 24.0116 | 23.6269 | 22.9715 | 22.3452 | 21.6622
|  | PORTWAY | CT |  |  | 26.2444 | 26.2036 | 25.5204 | 25.4068 | 25.2933 | 25.1802 | 25.0432 | 24.9059 | 24.7941 | 24.4605 | 23.2439 | 22.4798 | 21.8096 | 26.2177 | 26.18 | 25.5032 | 25.3958 | 25.2885 | 25.1782 | 25.0234 | 24.8684 | 24.7375 | 24.3473 | 23.0342 | 22.1685 | 21.3982 | 26.2981 | 26.2566 | 25.5719 | 25.4568 | 25.3418 | 25.2271 | 25.0882 | 24.9488 | 24.8348 | 24.4947 | 23.267 | 22.4912 | 21.8095
|  | PORTWAY | LW |  |  | 26.1373 | 26.0792 | 24.961 | 24.7914 | 24.6215 | 24.4486 | 24.2756 | 24.0998 | 23.9737 | 23.5956 | 22.9513 | 22.3366 | 21.6698 | 26.1125 | 26.0585 | 24.949 | 24.7877 | 24.6125 | 24.4217 | 24.2308 | 24.0374 | 23.8922 | 23.4574 | 22.7166 | 22.0003 | 21.2333 | 26.1906 | 26.1315 | 25.0113 | 24.8396 | 24.6677 | 24.4928 | 24.3177 | 24.1399 | 24.0116 | 23.6269 | 22.9715 | 22.3452 | 21.6622
|  | PORTWAY | ST |  |  | 26.2839 | 26.2481 | 25.7859 | 25.6909 | 25.5832 | 25.4801 | 25.3776 | 25.2845 | 25.2081 | 24.981 | 24.6003 | 24.2279 | 23.8364 | 26.2577 | 26.2247 | 25.7675 | 25.6785 | 25.5781 | 25.4772 | 25.3604 | 25.2552 | 25.1659 | 24.9006 | 24.4555 | 24.0175 | 23.561 | 26.3376 | 26.301 | 25.8376 | 25.7412 | 25.6317 | 25.527 | 25.4228 | 25.3283 | 25.2504 | 25.019 | 24.6309 | 24.2509 | 23.8519
|  | PORTWAY | FS |  |  | 26.3772 | 26.3705 | 26.1611 | 26.1287 | 26.0938 | 26.0539 | 26.0141 | 25.9671 | 25.9309 | 25.8223 | 25.6621 | 25.4949 | 25.3194 | 26.3461 | 26.3397 | 26.1306 | 26.0997 | 26.0664 | 26.0287 | 25.991 | 25.9469 | 25.913 | 25.8114 | 25.6614 | 25.4697 | 25.2707 | 26.432 | 26.4253 | 26.2158 | 26.1831 | 26.1477 | 26.1073 | 26.067 | 26.0194 | 25.9826 | 25.8723 | 25.7093 | 25.5392 | 25.361
IVER 132KV | LONGFORD | POYLE | MINIMUM HEADROOM | TQ 03425 75555 | YES | 32.9357 | 32.9357 | 32.9357 | 32.904 | 32.8713 | 32.8371 | 32.8017 | 32.7479 | 32.7405 | 32.7149 | 32.6749 | 32.5955 | 32.0912 | 31.3269 | 31.3224 | 31.313 | 31.2721 | 31.2302 | 31.181 | 31.1307 | 31.062 | 31.0386 | 30.9505 | 30.3855 | 29.5262 | 28.7456 | 30.8462 | 30.8383 | 30.7856 | 30.6854 | 30.584 | 30.4378 | 30.2908 | 30.1259 | 29.9991 | 29.5067 | 28.7762 | 27.928 | 27.1578
|  | POYLE | CT |  |  | 32.9357 | 32.9357 | 32.9357 | 32.9357 | 32.9357 | 32.9357 | 32.9357 | 32.9357 | 32.9357 | 32.9357 | 32.9357 | 32.9357 | 32.4941 | 31.3274 | 31.3231 | 31.3143 | 31.3056 | 31.297 | 31.2883 | 31.2734 | 31.2585 | 31.2425 | 31.18 | 30.7135 | 29.9336 | 29.1589 | 30.8471 | 30.8396 | 30.7951 | 30.7305 | 30.6658 | 30.6012 | 30.4897 | 30.3786 | 30.2593 | 29.7925 | 29.1018 | 28.3345 | 27.5701
|  | POYLE | LW |  |  | 32.9357 | 32.9357 | 32.9357 | 32.904 | 32.8713 | 32.8371 | 32.8017 | 32.7479 | 32.7405 | 32.7149 | 32.6749 | 32.5955 | 32.0912 | 31.3269 | 31.3224 | 31.313 | 31.2721 | 31.2302 | 31.181 | 31.1307 | 31.062 | 31.0386 | 30.9505 | 30.3855 | 29.5262 | 28.7456 | 30.8462 | 30.8383 | 30.7856 | 30.6854 | 30.584 | 30.4378 | 30.2908 | 30.1259 | 29.9991 | 29.5067 | 28.7762 | 27.928 | 27.1578
|  | POYLE | ST |  |  | 32.9357 | 32.9357 | 32.9357 | 32.9357 | 32.9357 | 32.9357 | 32.9357 | 32.9357 | 32.9357 | 32.9357 | 32.9357 | 32.9357 | 32.9357 | 31.3434 | 31.329 | 31.3257 | 31.3217 | 31.3168 | 31.3055 | 31.2943 | 31.2842 | 31.2733 | 31.2302 | 31.1678 | 30.8281 | 30.3287 | 30.8751 | 30.8499 | 30.8442 | 30.8371 | 30.8138 | 30.7297 | 30.6462 | 30.5706 | 30.4892 | 30.1672 | 29.7008 | 29.2123 | 28.7243
|  | POYLE | FS |  |  | 32.9357 | 32.9357 | 32.9357 | 32.9346 | 32.9334 | 32.9322 | 32.931 | 32.9292 | 32.924 | 32.9076 | 32.8998 | 32.8751 | 32.8546 | 31.3461 | 31.3333 | 31.3329 | 31.3301 | 31.3272 | 31.3227 | 31.3183 | 31.3122 | 31.3028 | 31.2697 | 31.2375 | 31.1867 | 31.1401 | 30.8798 | 30.8574 | 30.8567 | 30.8528 | 30.8485 | 30.8416 | 30.8347 | 30.8221 | 30.7856 | 30.6441 | 30.4546 | 30.2347 | 30.0192
MINETY GSP | STRATTON (2 X 90) | PRESSED STEEL SWINDON | MINIMUM HEADROOM | SU 16963 86368 | YES | 26.5405 | 26.5405 | 26.5405 | 26.5405 | 26.5405 | 26.5405 | 26.5405 | 26.5405 | 26.5405 | 26.5405 | 26.5158 | 26.2309 | 25.3235 | 23.8367 | 23.8358 | 23.8341 | 23.8323 | 23.8305 | 23.8248 | 23.8191 | 23.8133 | 23.8072 | 23.788 | 23.7453 | 23.6944 | 23.3413 | 25.9985 | 25.9969 | 25.994 | 25.9911 | 25.988 | 25.9785 | 25.9689 | 25.9594 | 25.9492 | 25.917 | 25.6282 | 24.6383 | 23.6153
|  | PRESSED STEEL SWINDON | CT |  |  | 26.5405 | 26.5405 | 26.5405 | 26.5405 | 26.5405 | 26.5405 | 26.5405 | 26.5405 | 26.5405 | 26.5405 | 26.5233 | 26.3119 | 25.4082 | 23.8369 | 23.836 | 23.8345 | 23.8329 | 23.8312 | 23.8295 | 23.8238 | 23.8181 | 23.812 | 23.7928 | 23.7501 | 23.6992 | 23.4396 | 25.9988 | 25.9973 | 25.9947 | 25.9921 | 25.9893 | 25.9865 | 25.9769 | 25.9673 | 25.9571 | 25.925 | 25.7205 | 24.7307 | 23.7126
|  | PRESSED STEEL SWINDON | LW |  |  | 26.5405 | 26.5405 | 26.5405 | 26.5405 | 26.5405 | 26.5405 | 26.5405 | 26.5405 | 26.5405 | 26.5405 | 26.5158 | 26.2309 | 25.3235 | 23.8367 | 23.8358 | 23.8341 | 23.8323 | 23.8305 | 23.8248 | 23.8191 | 23.8133 | 23.8072 | 23.788 | 23.7453 | 23.6944 | 23.3413 | 25.9985 | 25.9969 | 25.994 | 25.9911 | 25.988 | 25.9785 | 25.9689 | 25.9594 | 25.9492 | 25.917 | 25.6282 | 24.6383 | 23.6153
|  | PRESSED STEEL SWINDON | ST |  |  | 26.5405 | 26.5405 | 26.5405 | 26.5405 | 26.5405 | 26.5405 | 26.5405 | 26.5405 | 26.5405 | 26.5405 | 26.5405 | 26.5096 | 26.4583 | 23.837 | 23.8364 | 23.8354 | 23.8342 | 23.8327 | 23.829 | 23.8253 | 23.8214 | 23.8172 | 23.8041 | 23.7748 | 23.7414 | 23.7088 | 25.9991 | 25.998 | 25.9963 | 25.9942 | 25.9917 | 25.9856 | 25.9794 | 25.9729 | 25.9659 | 25.9439 | 25.8949 | 25.5514 | 24.9175
|  | PRESSED STEEL SWINDON | FS |  |  | 26.5405 | 26.5405 | 26.5405 | 26.5405 | 26.5405 | 26.5405 | 26.5405 | 26.5405 | 26.5405 | 26.5405 | 26.5405 | 26.5405 | 26.5405 | 23.8379 | 23.8377 | 23.8376 | 23.8372 | 23.8368 | 23.8358 | 23.8348 | 23.8336 | 23.8319 | 23.8268 | 23.815 | 23.8004 | 23.7851 | 26.0005 | 26.0002 | 25.9999 | 25.9993 | 25.9986 | 25.9969 | 25.9953 | 25.9932 | 25.9905 | 25.982 | 25.9622 | 25.9377 | 25.9122
BRAMLEY (FLEE) | FERNHURST | PRESTON CANDOVER | MINIMUM HEADROOM | SU 60879 41131 | YES | 21.3616 | 21.2823 | 21.137 | 20.9599 | 20.7893 | 20.7326 | 20.6738 | 20.6101 | 20.5442 | 20.3597 | 20.0651 | 19.7856 | 19.5228 | 19.6662 | 19.5532 | 19.3492 | 19.1394 | 18.9391 | 18.8726 | 18.8036 | 18.7288 | 18.6514 | 18.4348 | 18.0889 | 17.7608 | 17.4522 | 20.616 | 20.5071 | 20.3104 | 20.1083 | 19.9153 | 19.8512 | 19.7846 | 19.7126 | 19.6379 | 19.4292 | 19.0958 | 18.7796 | 18.471
|  | PRESTON CANDOVER | CT |  |  | 21.3769 | 21.306 | 21.1805 | 21.031 | 20.881 | 20.7663 | 20.7076 | 20.644 | 20.578 | 20.3936 | 20.0988 | 19.8195 | 19.5568 | 19.6881 | 19.587 | 19.4082 | 19.223 | 19.0468 | 18.9122 | 18.8433 | 18.7685 | 18.6911 | 18.4746 | 18.1285 | 17.8006 | 17.4922 | 20.6371 | 20.5397 | 20.3674 | 20.1888 | 20.0191 | 19.8893 | 19.8229 | 19.7508 | 19.6762 | 19.4676 | 19.134 | 18.8179 | 18.511
|  | PRESTON CANDOVER | LW |  |  | 21.3616 | 21.2823 | 21.137 | 20.9599 | 20.7893 | 20.7326 | 20.6738 | 20.6101 | 20.5442 | 20.3597 | 20.0651 | 19.7856 | 19.5228 | 19.6662 | 19.5532 | 19.3492 | 19.1394 | 18.9391 | 18.8726 | 18.8036 | 18.7288 | 18.6514 | 18.4348 | 18.0889 | 17.7608 | 17.4522 | 20.616 | 20.5071 | 20.3104 | 20.1083 | 19.9153 | 19.8512 | 19.7846 | 19.7126 | 19.6379 | 19.4292 | 19.0958 | 18.7796 | 18.471
|  | PRESTON CANDOVER | ST |  |  | 21.3832 | 21.3248 | 21.2357 | 21.1217 | 20.9736 | 20.9317 | 20.8885 | 20.8453 | 20.8002 | 20.6747 | 20.4763 | 20.2957 | 20.1248 | 19.6971 | 19.6139 | 19.4868 | 19.3307 | 19.1556 | 19.1064 | 19.0556 | 19.0049 | 18.952 | 18.8046 | 18.5717 | 18.3597 | 18.159 | 20.6457 | 20.5656 | 20.4431 | 20.2927 | 20.1238 | 20.0765 | 20.0275 | 19.9786 | 19.9277 | 19.7856 | 19.5611 | 19.3568 | 19.1634
|  | PRESTON CANDOVER | FS |  |  | 21.4583 | 21.4419 | 21.4252 | 21.3932 | 21.3609 | 21.3477 | 21.3341 | 21.3163 | 21.3018 | 21.2616 | 21.1985 | 21.1424 | 21.0844 | 19.8039 | 19.7806 | 19.7569 | 19.7113 | 19.6653 | 19.6464 | 19.627 | 19.6017 | 19.5811 | 19.5238 | 19.434 | 19.3556 | 19.2858 | 20.7487 | 20.7263 | 20.7034 | 20.6595 | 20.6151 | 20.5969 | 20.5782 | 20.5538 | 20.5339 | 20.4787 | 20.3922 | 20.3166 | 20.2493
CHICKERELL GSP | CHICKERELL BSP | PUDDLETOWN | MINIMUM HEADROOM | SY 74226 95039 | YES | 8.19 | 8.19 | 8.19 | 8.1838 | 8.1769 | 8.1691 | 8.159 | 8.1301 | 8.125 | 8.0983 | 8.0337 | 7.9053 | 7.8962 | 8.3101 | 8.2718 | 8.1907 | 8.1096 | 8.0266 | 7.9842 | 7.9376 | 7.8762 | 7.8362 | 7.7063 | 7.4718 | 7.1678 | 6.986 | 8.6426 | 8.6037 | 8.5211 | 8.4386 | 8.3543 | 8.3113 | 8.2641 | 8.2022 | 8.1615 | 8.0298 | 7.7923 | 7.4852 | 7.3004
|  | PUDDLETOWN | CT |  |  | 8.19 | 8.19 | 8.19 | 8.1892 | 8.1878 | 8.1857 | 8.1809 | 8.1695 | 8.1675 | 8.1573 | 8.074 | 7.9748 | 7.9441 | 8.3228 | 8.2915 | 8.2252 | 8.1601 | 8.095 | 8.0298 | 7.9923 | 7.9486 | 7.9117 | 7.7983 | 7.5448 | 7.27 | 7.0666 | 8.6555 | 8.6236 | 8.5562 | 8.49 | 8.4238 | 8.3575 | 8.3194 | 8.2751 | 8.2376 | 8.1224 | 7.8659 | 7.5881 | 7.3816
|  | PUDDLETOWN | LW |  |  | 8.19 | 8.19 | 8.19 | 8.1875 | 8.1823 | 8.173 | 8.159 | 8.1301 | 8.125 | 8.0983 | 8.0337 | 7.9053 | 7.8962 | 8.3101 | 8.2718 | 8.1907 | 8.1096 | 8.0266 | 7.9842 | 7.9376 | 7.8762 | 7.8362 | 7.7063 | 7.4718 | 7.1678 | 6.986 | 8.6426 | 8.6037 | 8.5211 | 8.4386 | 8.3543 | 8.3113 | 8.2641 | 8.2022 | 8.1615 | 8.0298 | 7.7923 | 7.4852 | 7.3004
|  | PUDDLETOWN | ST |  |  | 8.19 | 8.19 | 8.19 | 8.1838 | 8.1769 | 8.1691 | 8.1598 | 8.1432 | 8.1367 | 8.1095 | 8.0793 | 7.9745 | 7.9381 | 8.3156 | 8.2845 | 8.2313 | 8.1599 | 8.0744 | 8.0451 | 8.0147 | 7.976 | 7.9456 | 7.8489 | 7.7059 | 7.4882 | 7.3393 | 8.6481 | 8.6165 | 8.5624 | 8.4898 | 8.403 | 8.3733 | 8.3425 | 8.3034 | 8.2727 | 8.1747 | 8.0297 | 7.81 | 7.6592
|  | PUDDLETOWN | FS |  |  | 8.19 | 8.19 | 8.19 | 8.19 | 8.1899 | 8.1899 | 8.1898 | 8.1894 | 8.1883 | 8.1818 | 8.1768 | 8.1542 | 8.1325 | 8.37 | 8.3671 | 8.3642 | 8.3509 | 8.3353 | 8.3275 | 8.3197 | 8.3095 | 8.2991 | 8.2657 | 8.2181 | 8.1545 | 8.0941 | 8.7036 | 8.7006 | 8.6976 | 8.6841 | 8.6682 | 8.6603 | 8.6523 | 8.642 | 8.6315 | 8.5976 | 8.5492 | 8.4849 | 8.4239
AXMINSTER | YEOVIL BSP | PULHAM | MINIMUM HEADROOM | ST 71579 09451 | YES | 10.4 | 10.4 | 10.4 | 10.3691 | 10.3054 | 10.2053 | 10.0667 | 9.8308 | 9.7946 | 9.6405 | 9.3246 | 8.7379 | 8.7008 | 9.9614 | 9.9401 | 9.895 | 9.8204 | 9.7133 | 9.5597 | 9.3682 | 9.0798 | 8.987 | 8.6657 | 8.0741 | 7.2024 | 6.8849 | 10.3615 | 10.3403 | 10.2953 | 10.2209 | 10.1139 | 9.9605 | 9.7691 | 9.4809 | 9.3883 | 9.0674 | 8.4767 | 7.6059 | 7.2892
|  | PULHAM | CT |  |  | 10.4 | 10.4 | 10.4 | 10.3906 | 10.373 | 10.3469 | 10.3089 | 10.2408 | 10.2306 | 10.1857 | 9.8696 | 9.5252 | 9.4301 | 9.968 | 9.9503 | 9.9129 | 9.8671 | 9.8135 | 9.7517 | 9.6608 | 9.5402 | 9.4733 | 9.2614 | 8.6694 | 8.0402 | 7.6647 | 10.3681 | 10.3504 | 10.3131 | 10.2675 | 10.214 | 10.1523 | 10.0616 | 9.9411 | 9.8744 | 9.663 | 9.0718 | 8.4435 | 8.0689
|  | PULHAM | LW |  |  | 10.4 | 10.4 | 10.4 | 10.3691 | 10.3054 | 10.2053 | 10.0667 | 9.8308 | 9.7946 | 9.6405 | 9.3246 | 8.7379 | 8.7008 | 9.9614 | 9.9401 | 9.895 | 9.8204 | 9.7133 | 9.5597 | 9.3682 | 9.0798 | 8.987 | 8.6657 | 8.0741 | 7.2024 | 6.8849 | 10.3615 | 10.3403 | 10.2953 | 10.2209 | 10.1139 | 9.9605 | 9.7691 | 9.4809 | 9.3883 | 9.0674 | 8.4767 | 7.6059 | 7.2892
|  | PULHAM | ST |  |  | 10.4 | 10.4 | 10.4 | 10.3935 | 10.3805 | 10.3609 | 10.3318 | 10.2795 | 10.2583 | 10.1655 | 10.0592 | 9.7072 | 9.5895 | 9.9656 | 9.9489 | 9.9203 | 9.8787 | 9.8235 | 9.7735 | 9.7146 | 9.6264 | 9.5667 | 9.3611 | 9.0716 | 8.536 | 8.2359 | 10.3657 | 10.3491 | 10.3206 | 10.279 | 10.2239 | 10.1741 | 10.1153 | 10.0272 | 9.9676 | 9.7623 | 9.4734 | 8.9384 | 8.6388
|  | PULHAM | FS |  |  | 10.4 | 10.4 | 10.4 | 10.3998 | 10.3992 | 10.3983 | 10.3969 | 10.3939 | 10.3821 | 10.3143 | 10.2604 | 10.0026 | 9.7513 | 9.9947 | 9.9931 | 9.9916 | 9.984 | 9.9749 | 9.9651 | 9.955 | 9.9404 | 9.9137 | 9.8024 | 9.6791 | 9.3548 | 9.0406 | 10.3947 | 10.3931 | 10.3916 | 10.3841 | 10.375 | 10.3652 | 10.3551 | 10.3406 | 10.3139 | 10.2027 | 10.0797 | 9.7556 | 9.4416
LOVEDEAN GSP | FORT WIDLEY | PURBROOK | MINIMUM HEADROOM | SU 67047 07819 | YES | 17.9766 | 17.9471 | 17.9022 | 17.8508 | 17.774 | 17.5988 | 17.4095 | 17.2074 | 17.0501 | 16.5143 | 15.528 | 14.4098 | 13.4213 | 19.2134 | 19.2114 | 19.2085 | 19.1787 | 19.1435 | 19.0998 | 19.0523 | 18.8977 | 18.7146 | 18.0915 | 16.9449 | 15.6558 | 14.4968 | 19.1602 | 19.1373 | 19.1025 | 19.0621 | 18.9895 | 18.846 | 18.6907 | 18.5204 | 18.3964 | 17.9731 | 16.9707 | 15.7114 | 14.5823
|  | PURBROOK | CT |  |  | 17.9766 | 17.9471 | 17.9022 | 17.8508 | 17.7757 | 17.6958 | 17.5393 | 17.3883 | 17.2384 | 16.7309 | 15.7613 | 14.7209 | 13.7229 | 19.2134 | 19.2114 | 19.2085 | 19.2027 | 19.195 | 19.1867 | 19.172 | 19.0805 | 18.9047 | 18.31 | 17.1801 | 15.9688 | 14.8002 | 19.1602 | 19.1373 | 19.1025 | 19.0621 | 19.0031 | 18.9405 | 18.818 | 18.6989 | 18.5823 | 18.1873 | 17.2056 | 16.0241 | 14.8854
|  | PURBROOK | LW |  |  | 17.9873 | 17.9637 | 17.9314 | 17.8655 | 17.774 | 17.5988 | 17.4095 | 17.2074 | 17.0501 | 16.5143 | 15.528 | 14.4098 | 13.4213 | 19.2141 | 19.2125 | 19.2104 | 19.1787 | 19.1435 | 19.0998 | 19.0523 | 18.8977 | 18.7146 | 18.0915 | 16.9449 | 15.6558 | 14.4968 | 19.1685 | 19.1502 | 19.1252 | 19.0675 | 18.9895 | 18.846 | 18.6907 | 18.5204 | 18.3964 | 17.9731 | 16.9707 | 15.7114 | 14.5823
|  | PURBROOK | ST |  |  | 17.9929 | 17.977 | 17.9574 | 17.905 | 17.8351 | 17.7124 | 17.581 | 17.4345 | 17.3153 | 16.9069 | 16.213 | 15.4047 | 14.7259 | 19.2144 | 19.2134 | 19.2121 | 19.1818 | 19.1496 | 19.1131 | 19.0746 | 19.0177 | 18.9935 | 18.5544 | 17.7486 | 16.8276 | 16.0403 | 19.1728 | 19.1605 | 19.1453 | 19.0982 | 19.0374 | 18.9354 | 18.8263 | 18.7014 | 18.605 | 18.2751 | 17.7256 | 16.8523 | 16.084
|  | PURBROOK | FS |  |  | 17.9989 | 17.9896 | 17.98 | 17.9683 | 17.9496 | 17.9161 | 17.8805 | 17.8434 | 17.8011 | 17.6551 | 17.3873 | 17.0763 | 16.7549 | 19.2148 | 19.2142 | 19.2136 | 19.2124 | 19.2108 | 19.2082 | 19.2054 | 19.2023 | 19.1974 | 19.1799 | 19.0785 | 18.7165 | 18.3419 | 19.1775 | 19.1703 | 19.1628 | 19.1537 | 19.1391 | 19.113 | 19.0853 | 19.0563 | 19.023 | 18.9079 | 18.6992 | 18.454 | 18.2011
BRAMLEY (FLEE) | PYESTOCK BSP | PYESTOCK | MINIMUM HEADROOM | SU 82940 54553 |  | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2
|  | PYESTOCK | CT |  |  | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2
|  | PYESTOCK | LW |  |  | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2
|  | PYESTOCK | ST |  |  | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2
|  | PYESTOCK | FS |  |  | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2 | 31.2
MINETY GSP | TOOTHILL BSP | QUARRY ROAD | MINIMUM HEADROOM | SU 15334 83380 | YES | 31.1537 | 31.1417 | 30.4125 | 30.3528 | 30.293 | 30.2332 | 30.1735 | 30.1137 | 30.0898 | 30.0181 | 29.8985 | 28.8367 | 27.3179 | 28.6241 | 28.6019 | 27.853 | 27.7735 | 27.6933 | 27.6158 | 27.5069 | 27.2082 | 26.9601 | 26.234 | 24.7292 | 23.0347 | 21.2851 | 29.9502 | 29.9279 | 29.179 | 29.0994 | 29.0192 | 28.9417 | 28.8634 | 28.7843 | 28.7423 | 28.3199 | 27.2401 | 25.6424 | 23.9334
|  | QUARRY ROAD | CT |  |  | 31.2158 | 31.2087 | 30.7711 | 30.7353 | 30.6994 | 30.6636 | 30.6277 | 30.5918 | 30.5775 | 30.5345 | 30.0114 | 28.8565 | 27.338 | 28.6871 | 28.67 | 28.2138 | 28.159 | 28.1036 | 28.048 | 27.984 | 27.7093 | 27.4707 | 26.7735 | 24.8649 | 23.0577 | 21.3087 | 30.0131 | 29.9961 | 29.5397 | 29.4849 | 29.4295 | 29.3738 | 29.3194 | 29.2643 | 29.2319 | 28.8507 | 27.3743 | 25.6648 | 23.9563
|  | QUARRY ROAD | LW |  |  | 31.1537 | 31.1417 | 30.4125 | 30.3528 | 30.293 | 30.2332 | 30.1735 | 30.1137 | 30.0898 | 30.0181 | 29.8985 | 28.8367 | 27.3179 | 28.6241 | 28.6019 | 27.853 | 27.7735 | 27.6933 | 27.6158 | 27.5069 | 27.2082 | 26.9601 | 26.234 | 24.7292 | 23.0347 | 21.2851 | 29.9502 | 29.9279 | 29.179 | 29.0994 | 29.0192 | 28.9417 | 28.8634 | 28.7843 | 28.7423 | 28.3199 | 27.2401 | 25.6424 | 23.9334
|  | QUARRY ROAD | ST |  |  | 31.2469 | 31.2421 | 30.9505 | 30.9265 | 30.9026 | 30.8787 | 30.8548 | 30.8309 | 30.8214 | 30.7927 | 30.7449 | 30.7162 | 30.4555 | 28.7247 | 28.7146 | 28.4146 | 28.3805 | 28.3442 | 28.3059 | 28.2672 | 28.2303 | 28.2084 | 27.963 | 26.963 | 25.8692 | 24.7835 | 30.0508 | 30.0406 | 29.7406 | 29.7064 | 29.6701 | 29.6318 | 29.5931 | 29.5562 | 29.5342 | 29.4694 | 29.0481 | 28.3546 | 27.3443
|  | QUARRY ROAD | FS |  |  | 31.278 | 31.2756 | 31.1298 | 31.1178 | 31.1058 | 31.0939 | 31.0819 | 31.07 | 31.0652 | 31.0509 | 31.027 | 31.0126 | 30.9863 | 28.7622 | 28.7582 | 28.6107 | 28.5948 | 28.5782 | 28.5609 | 28.5435 | 28.5247 | 28.5152 | 28.4868 | 28.4319 | 28.38 | 27.8777 | 30.0883 | 30.0842 | 29.9367 | 29.9208 | 29.9043 | 29.887 | 29.8695 | 29.8507 | 29.8411 | 29.8127 | 29.7578 | 29.7058 | 29.6405
BRAMLEY (FLEE) | CAMBERLEY RESERVE | QUEENSMEAD | MINIMUM HEADROOM | SU 87062 55683 | YES | 19.6614 | 19.6614 | 19.6614 | 19.6614 | 19.6614 | 19.6614 | 19.6614 | 19.6614 | 19.6614 | 19.6614 | 19.4791 | 18.6333 | 17.7965 | 18.1779 | 18.1779 | 18.1779 | 18.1779 | 18.1779 | 18.1779 | 18.1779 | 18.1779 | 18.1779 | 18.0704 | 17.2204 | 16.2394 | 15.2689 | 18.5811 | 18.481 | 18.3839 | 18.288 | 18.0749 | 17.8351 | 17.5997 | 17.3624 | 17.1476 | 16.6903 | 15.8254 | 14.8272 | 13.8396
|  | QUEENSMEAD | CT |  |  | 19.6614 | 19.6614 | 19.6614 | 19.6614 | 19.6614 | 19.6614 | 19.6614 | 19.6614 | 19.6614 | 19.6614 | 19.5288 | 18.683 | 17.8464 | 18.1779 | 18.1779 | 18.1779 | 18.1779 | 18.1779 | 18.1779 | 18.1779 | 18.1779 | 18.1779 | 18.1282 | 17.2781 | 16.2971 | 15.3268 | 18.5873 | 18.495 | 18.4085 | 18.3229 | 18.1198 | 17.8938 | 17.6585 | 17.4212 | 17.2063 | 16.7491 | 15.884 | 14.8858 | 13.8986
|  | QUEENSMEAD | LW |  |  | 19.6614 | 19.6614 | 19.6614 | 19.6614 | 19.6614 | 19.6614 | 19.6614 | 19.6614 | 19.6614 | 19.6614 | 19.4791 | 18.6333 | 17.7965 | 18.1779 | 18.1779 | 18.1779 | 18.1779 | 18.1779 | 18.1779 | 18.1779 | 18.1779 | 18.1779 | 18.0704 | 17.2204 | 16.2394 | 15.2689 | 18.5811 | 18.481 | 18.3839 | 18.288 | 18.0749 | 17.8351 | 17.5997 | 17.3624 | 17.1476 | 16.6903 | 15.8254 | 14.8272 | 13.8396
|  | QUEENSMEAD | ST |  |  | 19.6614 | 19.6614 | 19.6614 | 19.6614 | 19.6614 | 19.6614 | 19.6614 | 19.6614 | 19.6614 | 19.6614 | 19.6614 | 19.6435 | 19.1104 | 18.1779 | 18.1779 | 18.1779 | 18.1779 | 18.1779 | 18.1779 | 18.1779 | 18.1779 | 18.1779 | 18.1779 | 18.0565 | 17.411 | 16.7928 | 18.5882 | 18.5325 | 18.4782 | 18.4115 | 18.2535 | 18.0736 | 17.8971 | 17.7375 | 17.5904 | 17.2743 | 16.6761 | 16.0193 | 15.3903
|  | QUEENSMEAD | FS |  |  | 19.6614 | 19.6614 | 19.6614 | 19.6614 | 19.6614 | 19.6614 | 19.6614 | 19.6614 | 19.6614 | 19.6614 | 19.6614 | 19.6614 | 19.6614 | 18.1779 | 18.1779 | 18.1779 | 18.1779 | 18.1779 | 18.1779 | 18.1779 | 18.1779 | 18.1779 | 18.1779 | 18.1779 | 18.1779 | 18.1779 | 18.5924 | 18.59 | 18.5896 | 18.5882 | 18.5436 | 18.4728 | 18.4059 | 18.3332 | 18.2754 | 18.152 | 17.9082 | 17.6143 | 17.3115
MELKSHAM GSP | WEST GRAFTON | RAMSBURY | MINIMUM HEADROOM | SU 27380 72108 | YES | 11.9092 | 11.9092 | 11.9092 | 11.887 | 11.8643 | 11.8413 | 11.8173 | 11.7803 | 11.7756 | 11.7605 | 11.689 | 11.6098 | 11.5702 | 10.4313 | 10.4055 | 10.3508 | 10.2877 | 10.2248 | 10.1647 | 10.0958 | 10.0142 | 9.9615 | 9.8048 | 9.5007 | 9.1817 | 8.9254 | 11.2291 | 11.2072 | 11.1607 | 11.1056 | 11.0506 | 10.9924 | 10.9302 | 10.8554 | 10.8099 | 10.6746 | 10.4055 | 10.1226 | 9.9018
|  | RAMSBURY | CT |  |  | 11.9092 | 11.9092 | 11.9092 | 11.887 | 11.8643 | 11.8413 | 11.8173 | 11.7803 | 11.7756 | 11.7605 | 11.689 | 11.6098 | 11.5702 | 10.4377 | 10.4155 | 10.3683 | 10.3004 | 10.2326 | 10.1647 | 10.0958 | 10.0142 | 9.9615 | 9.8048 | 9.5007 | 9.1817 | 8.9254 | 11.2345 | 11.2156 | 11.1756 | 11.1146 | 11.0535 | 10.9924 | 10.9302 | 10.8554 | 10.8099 | 10.6746 | 10.4055 | 10.1226 | 9.9018
|  | RAMSBURY | LW |  |  | 11.9092 | 11.9092 | 11.9092 | 11.8991 | 11.8887 | 11.8778 | 11.8665 | 11.8493 | 11.8469 | 11.8387 | 11.8266 | 11.7958 | 11.7434 | 10.4313 | 10.4055 | 10.3508 | 10.2877 | 10.2248 | 10.1685 | 10.1123 | 10.0506 | 10.0002 | 9.8504 | 9.6057 | 9.3351 | 9.0975 | 11.2291 | 11.2072 | 11.1607 | 11.1056 | 11.0506 | 11.0011 | 10.9517 | 10.8967 | 10.8536 | 10.7251 | 10.5154 | 10.281 | 10.079
|  | RAMSBURY | ST |  |  | 11.9092 | 11.9092 | 11.9092 | 11.9092 | 11.9092 | 11.9092 | 11.9092 | 11.9092 | 11.9092 | 11.9092 | 11.9092 | 11.9092 | 11.9092 | 10.4537 | 10.4419 | 10.4215 | 10.3966 | 10.3665 | 10.3367 | 10.3073 | 10.2769 | 10.2441 | 10.1486 | 9.994 | 9.8397 | 9.6862 | 11.2481 | 11.238 | 11.2207 | 11.1996 | 11.174 | 11.1488 | 11.1238 | 11.0979 | 11.0701 | 10.989 | 10.8577 | 10.7266 | 10.5962
|  | RAMSBURY | FS |  |  | 11.9092 | 11.9092 | 11.9092 | 11.9092 | 11.9092 | 11.9092 | 11.9092 | 11.9092 | 11.9092 | 11.9092 | 11.9092 | 11.9092 | 11.9092 | 10.5513 | 10.4698 | 10.468 | 10.4592 | 10.4488 | 10.4384 | 10.4281 | 10.4149 | 10.4021 | 10.3653 | 10.3068 | 10.251 | 10.1984 | 11.3309 | 11.2618 | 11.2602 | 11.2527 | 11.2439 | 11.2351 | 11.2263 | 11.2151 | 11.2043 | 11.173 | 11.1233 | 11.0759 | 11.0312
MELKSHAM GSP | AMESBURY | RATFYN | MINIMUM HEADROOM |  |  | 35.3714 | 35.3714 | 35.3714 | 35.3683 | 35.362 | 35.352 | 35.3383 | 35.3106 | 35.3058 | 35.2814 | 34.7881 | 33.9763 | 33.2867 | 32.5898 | 32.5881 | 32.5847 | 32.5778 | 32.567 | 32.5484 | 32.5257 | 32.49 | 32.477 | 32.0843 | 31.264 | 30.3663 | 29.5927 | 34.2034 | 34.2034 | 34.2034 | 34.2003 | 34.194 | 34.184 | 34.1703 | 34.1426 | 33.9957 | 33.5471 | 32.7922 | 31.9151 | 31.1617
|  | RATFYN | CT |  |  | 35.3714 | 35.3714 | 35.3714 | 35.3705 | 35.3687 | 35.3661 | 35.3623 | 35.354 | 35.3525 | 35.3445 | 34.9568 | 34.1872 | 33.4833 | 32.5901 | 32.5887 | 32.5857 | 32.5814 | 32.5756 | 32.5687 | 32.5561 | 32.5397 | 32.53 | 32.2735 | 31.4464 | 30.5911 | 29.8031 | 34.2034 | 34.2034 | 34.2034 | 34.2025 | 34.2007 | 34.1981 | 34.1943 | 34.186 | 34.1559 | 33.7237 | 32.9714 | 32.1366 | 31.3688
|  | RATFYN | LW |  |  | 35.3714 | 35.3714 | 35.3714 | 35.3683 | 35.362 | 35.352 | 35.3383 | 35.3106 | 35.3058 | 35.2814 | 34.7881 | 33.9763 | 33.2867 | 32.5898 | 32.5881 | 32.5847 | 32.5778 | 32.567 | 32.5484 | 32.5257 | 32.49 | 32.477 | 32.0843 | 31.264 | 30.3663 | 29.5927 | 34.2034 | 34.2034 | 34.2034 | 34.2003 | 34.194 | 34.184 | 34.1703 | 34.1426 | 33.9957 | 33.5471 | 32.7922 | 31.9151 | 31.1617
|  | RATFYN | ST |  |  | 35.3714 | 35.3714 | 35.3714 | 35.3707 | 35.3694 | 35.3675 | 35.3646 | 35.3582 | 35.3551 | 35.3384 | 35.3166 | 35.062 | 34.5908 | 32.5904 | 32.5892 | 32.5873 | 32.5839 | 32.579 | 32.5731 | 32.5661 | 32.5542 | 32.5455 | 32.5129 | 32.1496 | 31.5693 | 31.0435 | 34.2034 | 34.2034 | 34.2034 | 34.2027 | 34.2015 | 34.1995 | 34.1966 | 34.1902 | 34.1871 | 34.087 | 33.6094 | 33.0796 | 32.5773
|  | RATFYN | FS |  |  | 35.3714 | 35.3714 | 35.3714 | 35.3714 | 35.3713 | 35.3712 | 35.3711 | 35.3708 | 35.3698 | 35.3638 | 35.359 | 35.3362 | 35.3139 | 32.5923 | 32.5921 | 32.592 | 32.5913 | 32.5902 | 32.5888 | 32.5873 | 32.5857 | 32.5825 | 32.5703 | 32.5559 | 32.5239 | 32.493 | 34.2034 | 34.2034 | 34.2034 | 34.2034 | 34.2033 | 34.2032 | 34.2031 | 34.2029 | 34.2018 | 34.1958 | 34.191 | 34.1682 | 34.1454
BRAMLEY (FLEE) | READING BSP | READING | MINIMUM HEADROOM | SU 74591 73788 | YES | 67.0844 | 67.0693 | 66.147 | 66.0714 | 65.9958 | 65.9202 | 65.8446 | 65.769 | 65.7387 | 65.648 | 64.3973 | 62.0092 | 59.6523 | 62.3022 | 62.2573 | 61.2731 | 61.1372 | 61.0014 | 60.8808 | 60.7271 | 60.5427 | 60.396 | 59.9475 | 57.453 | 54.6183 | 51.859 | 64.8093 | 64.7803 | 63.829 | 63.7252 | 63.6215 | 63.5249 | 63.4283 | 63.3317 | 63.1847 | 62.0976 | 59.5188 | 56.7868 | 54.1298
|  | READING | CT |  |  | 67.1631 | 67.154 | 66.6006 | 66.5552 | 66.5099 | 66.4645 | 66.4191 | 66.3738 | 66.3556 | 66.3012 | 64.3973 | 62.0092 | 59.6523 | 62.3748 | 62.3327 | 61.7105 | 61.5982 | 61.4861 | 61.3332 | 61.1787 | 61.0245 | 60.8898 | 60.3967 | 57.453 | 54.6183 | 51.859 | 64.8851 | 64.8606 | 64.2751 | 64.1984 | 64.1218 | 64.0455 | 63.9792 | 63.8042 | 63.4735 | 62.3724 | 59.5188 | 56.7868 | 54.1298
|  | READING | LW |  |  | 67.0844 | 67.0693 | 66.147 | 66.0714 | 65.9958 | 65.9202 | 65.8446 | 65.769 | 65.7387 | 65.648 | 64.4965 | 62.3419 | 59.9846 | 62.3022 | 62.2573 | 61.2731 | 61.1372 | 61.0014 | 60.8808 | 60.7271 | 60.5427 | 60.396 | 59.9475 | 57.7047 | 55.0122 | 52.2523 | 64.8093 | 64.7803 | 63.829 | 63.7252 | 63.6215 | 63.5249 | 63.4283 | 63.3317 | 63.1847 | 62.0976 | 59.7549 | 57.1651 | 54.5076
|  | READING | ST |  |  | 67.2024 | 67.1963 | 66.8274 | 66.7972 | 66.7669 | 66.7367 | 66.7064 | 66.6762 | 66.6641 | 66.6278 | 66.5673 | 66.0252 | 64.8724 | 62.4794 | 62.4236 | 62.0303 | 61.9703 | 61.904 | 61.8387 | 61.7735 | 61.7127 | 61.6678 | 61.4814 | 60.9364 | 59.5446 | 57.8132 | 64.9549 | 64.9256 | 64.5453 | 64.5011 | 64.4541 | 64.4074 | 64.3609 | 64.3163 | 64.2889 | 64.2059 | 63.2308 | 61.563 | 59.8973
|  | READING | FS |  |  | 67.2417 | 67.2387 | 67.0542 | 67.0391 | 67.024 | 67.0088 | 66.9937 | 66.9786 | 66.9726 | 66.9544 | 66.9242 | 66.906 | 66.8728 | 62.5407 | 62.4999 | 62.313 | 62.2885 | 62.2622 | 62.235 | 62.2079 | 62.1774 | 62.1586 | 62.1017 | 61.9927 | 61.8837 | 61.6818 | 65.0045 | 64.9839 | 64.7982 | 64.7787 | 64.7584 | 64.7376 | 64.7169 | 64.6946 | 64.6826 | 64.6463 | 64.5793 | 64.5187 | 64.4423
BRAMLEY (FLEE) | READING TOWN BSP | READING TOWN | MINIMUM HEADROOM | SU 71540 74122 | YES | 103.7652 | 103.7533 | 103.0296 | 102.9702 | 102.9109 | 102.8516 | 102.7923 | 102.733 | 102.7092 | 102.638 | 102.5194 | 101.3374 | 99.9535 | 101.0578 | 101.0459 | 100.3222 | 100.2629 | 100.2035 | 100.1442 | 100.0849 | 100.0256 | 99.8679 | 98.4047 | 96.2343 | 94.5307 | 92.9383 | 101.2784 | 101.2665 | 100.5428 | 100.4835 | 100.4241 | 100.3648 | 100.3055 | 100.2462 | 100.2224 | 98.9787 | 96.8126 | 95.112 | 93.5226
|  | READING TOWN | CT |  |  | 103.8269 | 103.8197 | 103.3855 | 103.3499 | 103.3143 | 103.2787 | 103.2431 | 103.2075 | 103.1933 | 103.1506 | 102.6314 | 101.3374 | 99.9535 | 101.1195 | 101.1123 | 100.6781 | 100.6425 | 100.6069 | 100.5713 | 100.5357 | 100.3299 | 99.8952 | 98.4607 | 96.2343 | 94.5307 | 92.9383 | 101.3401 | 101.3329 | 100.8987 | 100.8631 | 100.8275 | 100.7919 | 100.7563 | 100.7207 | 100.4674 | 99.0356 | 96.8126 | 95.112 | 93.5226
|  | READING TOWN | LW |  |  | 103.7652 | 103.7533 | 103.0296 | 102.9702 | 102.9109 | 102.8516 | 102.7923 | 102.733 | 102.7092 | 102.638 | 102.5194 | 101.7288 | 100.3448 | 101.0578 | 101.0459 | 100.3222 | 100.2629 | 100.2035 | 100.1442 | 100.0849 | 100.0256 | 99.8679 | 98.4047 | 96.579 | 94.9871 | 93.3946 | 101.2784 | 101.2665 | 100.5428 | 100.4835 | 100.4241 | 100.3648 | 100.3055 | 100.2462 | 100.2224 | 98.9787 | 97.1564 | 95.5676 | 93.978
|  | READING TOWN | ST |  |  | 103.8577 | 103.853 | 103.5635 | 103.5397 | 103.516 | 103.4923 | 103.4685 | 103.4448 | 103.4353 | 103.4069 | 103.3594 | 103.3309 | 103.2787 | 101.1503 | 101.1456 | 100.8561 | 100.8323 | 100.8086 | 100.7849 | 100.7612 | 100.7374 | 100.7279 | 100.6995 | 100.6428 | 99.6355 | 98.6503 | 101.3709 | 101.3662 | 101.0767 | 101.0529 | 101.0292 | 101.0055 | 100.9818 | 100.958 | 100.9485 | 100.9201 | 100.8726 | 100.2084 | 99.2251
|  | READING TOWN | FS |  |  | 103.8885 | 103.8862 | 103.7414 | 103.7296 | 103.7177 | 103.7058 | 103.694 | 103.6821 | 103.6774 | 103.6631 | 103.6394 | 103.6252 | 103.5991 | 101.1812 | 101.1788 | 101.034 | 101.0222 | 101.0103 | 100.9984 | 100.9866 | 100.9747 | 100.97 | 100.9557 | 100.932 | 100.9178 | 100.8917 | 101.4018 | 101.3994 | 101.2546 | 101.2428 | 101.2309 | 101.219 | 101.2072 | 101.1953 | 101.1906 | 101.1763 | 101.1526 | 101.1384 | 101.1123
MANNINGTON GSP | REDHILL BSP | REDHILL | MINIMUM HEADROOM | SZ 08512 96149 | YES | 55.7184 | 55.6744 | 55.5931 | 55.5039 | 55.4042 | 55.2012 | 54.9959 | 54.7882 | 54.5651 | 53.8813 | 52.4816 | 50.8749 | 49.2815 | 50.3115 | 50.2613 | 50.1687 | 50.0672 | 49.9538 | 49.7226 | 49.4889 | 49.2525 | 48.9984 | 48.1999 | 46.5566 | 44.6703 | 42.7996 | 52.6904 | 52.6405 | 52.5485 | 52.4476 | 52.3349 | 52.1051 | 51.8729 | 51.6378 | 51.3854 | 50.6116 | 49.0279 | 47.2099 | 45.4069
|  | REDHILL | CT |  |  | 55.7184 | 55.6744 | 55.5931 | 55.5039 | 55.4042 | 55.3506 | 55.1455 | 54.9378 | 54.7145 | 54.0308 | 52.6311 | 51.0245 | 49.4317 | 50.3115 | 50.2613 | 50.1687 | 50.0672 | 49.9538 | 49.8927 | 49.6592 | 49.4227 | 49.1686 | 48.3755 | 46.7321 | 44.8459 | 42.9758 | 52.6904 | 52.6405 | 52.5485 | 52.4476 | 52.3349 | 52.2742 | 52.0421 | 51.8071 | 51.5545 | 50.7808 | 49.197 | 47.3792 | 45.5768
|  | REDHILL | LW |  |  | 55.7184 | 55.6744 | 55.5931 | 55.5039 | 55.4042 | 55.2012 | 54.9959 | 54.7882 | 54.5651 | 53.8813 | 52.4816 | 50.8749 | 49.2815 | 50.3115 | 50.2613 | 50.1687 | 50.0672 | 49.9538 | 49.7226 | 49.4889 | 49.2525 | 48.9984 | 48.1999 | 46.5566 | 44.6703 | 42.7996 | 52.6904 | 52.6405 | 52.5485 | 52.4476 | 52.3349 | 52.1051 | 51.8729 | 51.6378 | 51.3854 | 50.6116 | 49.0279 | 47.2099 | 45.4069
|  | REDHILL | ST |  |  | 56.276 | 55.709 | 55.6632 | 55.6075 | 55.5402 | 55.3878 | 55.2347 | 55.0932 | 54.9408 | 54.475 | 53.5185 | 52.4672 | 51.4464 | 50.9462 | 50.3007 | 50.2486 | 50.1852 | 50.1086 | 49.9351 | 49.7608 | 49.5996 | 49.4261 | 48.8958 | 47.7739 | 46.5396 | 45.3412 | 53.3213 | 52.6797 | 52.6279 | 52.5649 | 52.4888 | 52.3163 | 52.1431 | 51.9829 | 51.8105 | 51.2834 | 50.2011 | 49.0115 | 47.8565
|  | REDHILL | FS |  |  | 56.9183 | 55.7458 | 55.7276 | 55.7027 | 55.6749 | 55.6279 | 55.5809 | 55.5202 | 55.4576 | 55.2662 | 54.8793 | 54.416 | 53.948 | 51.6774 | 50.3426 | 50.3219 | 50.2937 | 50.2621 | 50.2088 | 50.1553 | 50.0864 | 50.0156 | 49.7992 | 49.3594 | 48.8341 | 48.2872 | 54.048 | 52.7214 | 52.7008 | 52.6727 | 52.6414 | 52.5883 | 52.5351 | 52.4666 | 52.3963 | 52.1811 | 51.744 | 51.2218 | 50.6939
CHICKERELL GSP | CHICKERELL BSP | REDLANDS | MINIMUM HEADROOM | SY 67131 82321 | YES | 18.2248 | 18.2248 | 18.2248 | 18.0945 | 17.9595 | 17.8177 | 17.6701 | 17.4447 | 17.4133 | 17.3041 | 17.1363 | 16.2595 | 15.3757 | 17.4964 | 17.4942 | 17.4905 | 17.356 | 17.2162 | 17.0612 | 16.8756 | 16.5077 | 16.3248 | 15.6171 | 14.4613 | 13.0997 | 12.0662 | 17.6245 | 17.6223 | 17.6185 | 17.4839 | 17.3439 | 17.1885 | 17.0254 | 16.7846 | 16.7397 | 16.3946 | 15.2746 | 13.9504 | 12.9535
|  | REDLANDS | CT |  |  | 18.2248 | 18.2248 | 18.2248 | 18.2048 | 18.1843 | 18.1634 | 18.1413 | 18.1067 | 18.1022 | 18.0872 | 18.0096 | 17.4905 | 16.6093 | 17.4964 | 17.4942 | 17.4905 | 17.4664 | 17.441 | 17.4149 | 17.3777 | 17.2462 | 17.1171 | 16.5428 | 15.4768 | 14.3517 | 13.3209 | 17.6245 | 17.6223 | 17.6185 | 17.5942 | 17.5687 | 17.5424 | 17.5048 | 17.4548 | 17.4369 | 17.3152 | 16.2849 | 15.1973 | 14.2031
|  | REDLANDS | LW |  |  | 18.2248 | 18.2248 | 18.2248 | 18.0945 | 17.9595 | 17.8177 | 17.6701 | 17.4447 | 17.4133 | 17.3041 | 17.1363 | 16.2595 | 15.3757 | 17.4964 | 17.4942 | 17.4905 | 17.356 | 17.2162 | 17.0612 | 16.8756 | 16.5077 | 16.3248 | 15.6171 | 14.4613 | 13.0997 | 12.0662 | 17.6245 | 17.6223 | 17.6185 | 17.4839 | 17.3439 | 17.1885 | 17.0254 | 16.7846 | 16.7397 | 16.3946 | 15.2746 | 13.9504 | 12.9535
|  | REDLANDS | ST |  |  | 18.2248 | 18.2248 | 18.2248 | 18.2229 | 18.2209 | 18.2186 | 18.2162 | 18.212 | 18.2104 | 18.204 | 18.1972 | 18.1744 | 18.1663 | 17.5014 | 17.4954 | 17.4932 | 17.4886 | 17.4833 | 17.4731 | 17.4614 | 17.4471 | 17.3949 | 17.1647 | 16.49 | 15.7947 | 15.1351 | 17.6297 | 17.6236 | 17.6213 | 17.6166 | 17.6112 | 17.6007 | 17.5888 | 17.5742 | 17.5634 | 17.5332 | 17.2682 | 16.5973 | 15.9613
|  | REDLANDS | FS |  |  | 18.2248 | 18.2248 | 18.2248 | 18.221 | 18.2172 | 18.2135 | 18.2096 | 18.2036 | 18.1869 | 18.1331 | 18.1072 | 18.024 | 17.9537 | 17.502 | 17.4967 | 17.4955 | 17.4904 | 17.4852 | 17.4787 | 17.4717 | 17.4623 | 17.442 | 17.3793 | 17.3387 | 17.1152 | 16.8938 | 17.6303 | 17.6248 | 17.6237 | 17.6185 | 17.6133 | 17.6067 | 17.5996 | 17.59 | 17.5696 | 17.5067 | 17.4656 | 17.3669 | 17.2818
MANNINGTON GSP | SALISBURY | REDLYNCH | MINIMUM HEADROOM | SU 19073 20576 | YES | 9.9335 | 9.9059 | 9.8477 | 9.7904 | 9.7329 | 9.6384 | 9.5399 | 9.4306 | 9.3335 | 9.0382 | 8.5347 | 7.9685 | 7.4995 | 6.7315 | 6.7014 | 6.6377 | 6.5751 | 6.5124 | 6.4103 | 6.3036 | 6.1862 | 6.0804 | 5.7594 | 5.2133 | 4.5886 | 4.0406 | 7.1192 | 7.0945 | 7.0423 | 6.9908 | 6.939 | 6.8528 | 6.7633 | 6.6628 | 6.5753 | 6.3065 | 5.7311 | 5.0904 | 4.5481
|  | REDLYNCH | CT |  |  | 9.9335 | 9.9059 | 9.8477 | 9.7904 | 9.7329 | 9.6752 | 9.5849 | 9.4916 | 9.3973 | 9.1156 | 8.6065 | 8.0752 | 7.5944 | 6.7315 | 6.7014 | 6.6377 | 6.5751 | 6.5124 | 6.4495 | 6.351 | 6.2496 | 6.1465 | 5.8391 | 5.2874 | 4.6993 | 4.1399 | 7.1192 | 7.0945 | 7.0423 | 6.9908 | 6.939 | 6.8871 | 6.8057 | 6.7213 | 6.6365 | 6.3831 | 5.8068 | 5.201 | 4.647
|  | REDLYNCH | LW |  |  | 9.9349 | 9.9082 | 9.8516 | 9.7943 | 9.7346 | 9.6384 | 9.5399 | 9.4306 | 9.3335 | 9.0382 | 8.5347 | 7.9685 | 7.4995 | 6.7331 | 6.7038 | 6.642 | 6.5795 | 6.5148 | 6.4103 | 6.3036 | 6.1862 | 6.0804 | 5.7594 | 5.2133 | 4.5886 | 4.0406 | 7.1205 | 7.0965 | 7.0458 | 6.9941 | 6.94 | 6.8528 | 6.7633 | 6.6628 | 6.5753 | 6.3065 | 5.7311 | 5.0904 | 4.5481
|  | REDLYNCH | ST |  |  | 9.9617 | 9.9512 | 9.9332 | 9.9105 | 9.8828 | 9.8196 | 9.7566 | 9.6922 | 9.6261 | 9.4268 | 9.1064 | 8.7401 | 8.4164 | 6.7624 | 6.7509 | 6.7312 | 6.7065 | 6.6762 | 6.6073 | 6.5386 | 6.4687 | 6.3966 | 6.1799 | 5.8312 | 5.4365 | 5.0847 | 7.1446 | 7.1351 | 7.119 | 7.0986 | 7.0736 | 7.0168 | 6.96 | 6.9016 | 6.842 | 6.6618 | 6.3725 | 5.9666 | 5.5953
|  | REDLYNCH | FS |  |  | 9.9766 | 9.9745 | 9.9725 | 9.9635 | 9.9527 | 9.9318 | 9.9112 | 9.8843 | 9.8588 | 9.7822 | 9.6633 | 9.5344 | 9.4115 | 6.7787 | 6.7764 | 6.7742 | 6.7643 | 6.7525 | 6.7297 | 6.7072 | 6.6778 | 6.65 | 6.5667 | 6.437 | 6.2977 | 6.1651 | 7.1579 | 7.1561 | 7.1543 | 7.1462 | 7.1365 | 7.1177 | 7.0992 | 7.0751 | 7.0521 | 6.9828 | 6.8758 | 6.7581 | 6.646
NURSLING GSP | SOUTHAMPTON (2 X 90) | REGENTS PARK | MINIMUM HEADROOM | SU 39267 13050 | YES | 43.1659 | 43.15 | 42.1814 | 42.102 | 42.0226 | 41.9432 | 41.8638 | 41.7844 | 41.7527 | 41.6574 | 41.4986 | 41.4033 | 40.986 | 40.6995 | 40.6822 | 39.7107 | 39.6285 | 39.5462 | 39.4612 | 39.3762 | 39.2912 | 39.2534 | 39.1395 | 38.9417 | 38.8011 | 37.9411 | 42.8522 | 42.8348 | 41.8632 | 41.7809 | 41.6986 | 41.6134 | 41.5282 | 41.443 | 41.405 | 41.2905 | 40.7768 | 39.925 | 38.9745
|  | REGENTS PARK | CT |  |  | 43.2484 | 43.2389 | 42.6577 | 42.6101 | 42.5625 | 42.5148 | 42.4672 | 42.4196 | 42.4005 | 42.3433 | 41.6485 | 41.4033 | 41.044 | 40.7823 | 40.7714 | 40.1876 | 40.1373 | 40.087 | 40.0367 | 39.9834 | 39.9302 | 39.9051 | 39.8293 | 39.0954 | 38.8049 | 38.0091 | 42.9349 | 42.924 | 42.3401 | 42.2898 | 42.2394 | 42.189 | 42.1355 | 42.0821 | 42.0568 | 41.9804 | 40.9892 | 39.9907 | 39.0404
|  | REGENTS PARK | LW |  |  | 43.1659 | 43.15 | 42.1814 | 42.102 | 42.0226 | 41.9432 | 41.8638 | 41.7844 | 41.7527 | 41.6574 | 41.4986 | 41.4033 | 40.986 | 40.6995 | 40.6822 | 39.7107 | 39.6285 | 39.5462 | 39.4612 | 39.3762 | 39.2912 | 39.2534 | 39.1395 | 38.9417 | 38.8011 | 37.9411 | 42.8522 | 42.8348 | 41.8632 | 41.7809 | 41.6986 | 41.6134 | 41.5282 | 41.443 | 41.405 | 41.2905 | 40.7768 | 39.925 | 38.9745
|  | REGENTS PARK | ST |  |  | 43.2897 | 43.2834 | 42.8959 | 42.8642 | 42.8324 | 42.8007 | 42.7689 | 42.7371 | 42.7244 | 42.6863 | 42.6228 | 42.5847 | 42.5148 | 40.824 | 40.8167 | 40.4278 | 40.3941 | 40.3601 | 40.3253 | 40.2906 | 40.255 | 40.2382 | 40.1874 | 40.0973 | 40.0295 | 39.9306 | 42.9767 | 42.9694 | 42.5803 | 42.5466 | 42.5125 | 42.4777 | 42.4429 | 42.4071 | 42.3902 | 42.339 | 42.2481 | 41.8908 | 41.345
|  | REGENTS PARK | FS |  |  | 43.331 | 43.3278 | 43.1341 | 43.1182 | 43.1023 | 43.0865 | 43.0706 | 43.0547 | 43.0484 | 43.0293 | 42.9975 | 42.9785 | 42.9436 | 40.8667 | 40.8633 | 40.6694 | 40.6531 | 40.6366 | 40.6198 | 40.603 | 40.586 | 40.578 | 40.5541 | 40.5118 | 40.4801 | 40.4322 | 43.0194 | 43.016 | 42.8221 | 42.8057 | 42.7892 | 42.7724 | 42.7556 | 42.7385 | 42.7306 | 42.7065 | 42.6638 | 42.6317 | 42.5834
COWLEY GSP | WITNEY BSP | RISSINGTON | MINIMUM HEADROOM | SP 19225 19563 | NO | 12.7266 | 12.7266 | 12.7266 | 12.6935 | 12.6585 | 12.6213 | 12.5818 | 12.5203 | 12.5116 | 12.4798 | 12.4229 | 12.1345 | 11.7562 | 10.1163 | 10.0931 | 10.044 | 9.9631 | 9.8808 | 9.7596 | 9.6369 | 9.4929 | 9.3952 | 9.1008 | 8.6118 | 8.04 | 7.5935 | 11.7841 | 11.7841 | 11.7841 | 11.7509 | 11.716 | 11.6787 | 11.6393 | 11.5778 | 11.569 | 11.5372 | 11.4804 | 11.0938 | 10.6487
|  | RISSINGTON | CT |  |  | 12.7266 | 12.7266 | 12.7266 | 12.7193 | 12.7117 | 12.7037 | 12.6952 | 12.6814 | 12.6795 | 12.6728 | 12.6352 | 12.4816 | 12.0991 | 10.1209 | 10.1002 | 10.0565 | 10.0067 | 9.9568 | 9.907 | 9.8153 | 9.7191 | 9.6282 | 9.3591 | 8.8891 | 8.3971 | 7.9465 | 11.7841 | 11.7841 | 11.7841 | 11.7767 | 11.7691 | 11.7611 | 11.7526 | 11.7388 | 11.737 | 11.7303 | 11.6926 | 11.4508 | 11.0015
|  | RISSINGTON | LW |  |  | 12.7266 | 12.7266 | 12.7266 | 12.6935 | 12.6585 | 12.6213 | 12.5818 | 12.5203 | 12.5116 | 12.4798 | 12.4229 | 12.1345 | 11.7562 | 10.1163 | 10.0931 | 10.044 | 9.9631 | 9.8808 | 9.7596 | 9.6369 | 9.4929 | 9.3952 | 9.1008 | 8.6118 | 8.04 | 7.5935 | 11.7841 | 11.7841 | 11.7841 | 11.7509 | 11.716 | 11.6787 | 11.6393 | 11.5778 | 11.569 | 11.5372 | 11.4804 | 11.0938 | 10.6487
|  | RISSINGTON | ST |  |  | 12.7266 | 12.7266 | 12.7266 | 12.709 | 12.691 | 12.6724 | 12.653 | 12.6226 | 12.612 | 12.5768 | 12.5462 | 12.4437 | 12.411 | 10.1471 | 10.1416 | 10.1322 | 10.1031 | 10.0711 | 10.0141 | 9.9567 | 9.87 | 9.7987 | 9.5866 | 9.2685 | 8.8784 | 8.5602 | 11.7841 | 11.7841 | 11.7841 | 11.7664 | 11.7484 | 11.7298 | 11.7104 | 11.68 | 11.6695 | 11.6342 | 11.6036 | 11.5011 | 11.4684
|  | RISSINGTON | FS |  |  | 12.7266 | 12.7266 | 12.7266 | 12.7266 | 12.7266 | 12.7266 | 12.7266 | 12.7265 | 12.7263 | 12.7248 | 12.7237 | 12.7184 | 12.7132 | 10.2976 | 10.1553 | 10.1546 | 10.1514 | 10.1476 | 10.1349 | 10.1225 | 10.1063 | 10.0825 | 10.0128 | 9.9029 | 9.7935 | 9.6901 | 11.7841 | 11.7841 | 11.7841 | 11.784 | 11.784 | 11.784 | 11.784 | 11.7839 | 11.7837 | 11.7823 | 11.7812 | 11.7758 | 11.7706
BRAMLEY (ANDO-THAT) | THATCHAM BSP | RIVERSIDE | MINIMUM HEADROOM | SU 47846 67187 | YES | 24.1873 | 24.1598 | 23.3356 | 23.2476 | 23.1565 | 23.0811 | 23.0052 | 22.9291 | 22.892 | 22.768 | 22.5581 | 22.2263 | 21.526 | 22.4813 | 22.4064 | 21.5018 | 21.3395 | 21.1639 | 21.056 | 20.8619 | 20.6522 | 20.4753 | 19.7719 | 18.474 | 17.6083 | 16.809 | 22.8985 | 22.789 | 21.824 | 21.4496 | 21.0326 | 20.8319 | 20.624 | 20.4147 | 20.2383 | 19.5368 | 18.2428 | 17.3791 | 16.5818
|  | RIVERSIDE | CT |  |  | 24.2556 | 24.2335 | 23.7294 | 23.6677 | 23.603 | 23.5383 | 23.4886 | 23.4388 | 23.4122 | 23.3197 | 22.6671 | 22.2263 | 21.526 | 22.55 | 22.4807 | 21.8967 | 21.7613 | 21.6125 | 21.3378 | 21.1556 | 20.9722 | 20.8057 | 20.1338 | 18.474 | 17.6083 | 16.809 | 22.9675 | 22.8637 | 22.2216 | 21.876 | 21.4874 | 21.1001 | 20.9183 | 20.7353 | 20.5693 | 19.8993 | 18.2428 | 17.3791 | 16.5818
|  | RIVERSIDE | LW |  |  | 24.1873 | 24.1598 | 23.3356 | 23.2476 | 23.1565 | 23.0811 | 23.0052 | 22.9291 | 22.892 | 22.768 | 22.5581 | 22.3999 | 21.6995 | 22.4813 | 22.4064 | 21.5018 | 21.3395 | 21.1639 | 21.056 | 20.8619 | 20.6522 | 20.4753 | 19.7719 | 18.5547 | 17.8128 | 17.0134 | 22.8985 | 22.789 | 21.824 | 21.4496 | 21.0326 | 20.8319 | 20.624 | 20.4147 | 20.2383 | 19.5368 | 18.3229 | 17.583 | 16.7856
|  | RIVERSIDE | ST |  |  | 24.295 | 24.2792 | 23.9443 | 23.901 | 23.852 | 23.8165 | 23.7807 | 23.7474 | 23.7295 | 23.6661 | 23.5579 | 23.495 | 23.4068 | 22.6067 | 22.556 | 22.1721 | 22.072 | 21.9477 | 21.8816 | 21.8143 | 21.7577 | 21.7151 | 21.2888 | 20.4667 | 20.0017 | 19.5242 | 23.0368 | 22.9606 | 22.541 | 22.3996 | 22.0687 | 21.9153 | 21.7579 | 21.6348 | 21.5215 | 21.0516 | 20.2319 | 19.7682 | 19.2919
|  | RIVERSIDE | FS |  |  | 24.3448 | 24.3396 | 24.1781 | 24.1611 | 24.1424 | 24.1258 | 24.1091 | 24.0918 | 24.0837 | 24.0554 | 24.0066 | 23.9776 | 23.9354 | 22.7085 | 22.6949 | 22.5285 | 22.4987 | 22.4614 | 22.4332 | 22.4048 | 22.3737 | 22.3559 | 22.2862 | 22.1626 | 22.0899 | 22.0035 | 23.1764 | 23.1568 | 22.9867 | 22.9475 | 22.8967 | 22.8602 | 22.8232 | 22.7821 | 22.7572 | 22.6573 | 22.4559 | 22.2582 | 22.0456
MANNINGTON GSP | MANNINGTON BSP | ROCKBOURNE | MINIMUM HEADROOM | SU 11617 17810 | YES | 2.7287 | 2.7267 | 2.7225 | 2.7184 | 2.7143 | 2.7011 | 2.6878 | 2.6746 | 2.6604 | 2.6183 | 2.5488 | 2.4769 | 2.4062 | 1.9949 | 1.992 | 1.986 | 1.9801 | 1.9742 | 1.9555 | 1.9365 | 1.9176 | 1.8973 | 1.8372 | 1.738 | 1.6354 | 1.5343 | 1.9982 | 1.9972 | 1.995 | 1.993 | 1.9909 | 1.9843 | 1.9776 | 1.9709 | 1.9637 | 1.9425 | 1.9075 | 1.8712 | 1.8355
|  | ROCKBOURNE | CT |  |  | 2.7287 | 2.7267 | 2.7225 | 2.7184 | 2.7143 | 2.7102 | 2.6969 | 2.6837 | 2.6694 | 2.6274 | 2.5578 | 2.486 | 2.4153 | 1.9949 | 1.992 | 1.986 | 1.9801 | 1.9742 | 1.9684 | 1.9494 | 1.9305 | 1.9102 | 1.8501 | 1.7509 | 1.6483 | 1.5473 | 1.9982 | 1.9972 | 1.995 | 1.993 | 1.9909 | 1.9888 | 1.9821 | 1.9755 | 1.9683 | 1.9471 | 1.912 | 1.8758 | 1.8401
|  | ROCKBOURNE | LW |  |  | 2.7288 | 2.7268 | 2.7227 | 2.7186 | 2.7146 | 2.7011 | 2.6878 | 2.6746 | 2.6604 | 2.6183 | 2.5488 | 2.4769 | 2.4062 | 1.9949 | 1.9921 | 1.9862 | 1.9804 | 1.9747 | 1.9555 | 1.9365 | 1.9176 | 1.8973 | 1.8372 | 1.738 | 1.6354 | 1.5343 | 1.9982 | 1.9972 | 1.9951 | 1.9931 | 1.991 | 1.9843 | 1.9776 | 1.9709 | 1.9637 | 1.9425 | 1.9075 | 1.8712 | 1.8355
|  | ROCKBOURNE | ST |  |  | 2.7301 | 2.729 | 2.7271 | 2.7248 | 2.722 | 2.715 | 2.708 | 2.699 | 2.6893 | 2.6609 | 2.6147 | 2.5684 | 2.5225 | 1.9968 | 1.9952 | 1.9926 | 1.9893 | 1.9853 | 1.9752 | 1.9652 | 1.9524 | 1.9385 | 1.898 | 1.832 | 1.7659 | 1.7004 | 1.9989 | 1.9983 | 1.9974 | 1.9962 | 1.9948 | 1.9912 | 1.9877 | 1.9832 | 1.9783 | 1.964 | 1.9407 | 1.9173 | 1.8942
|  | ROCKBOURNE | FS |  |  | 2.7319 | 2.7317 | 2.7316 | 2.7309 | 2.7302 | 2.7278 | 2.7255 | 2.7224 | 2.7186 | 2.7077 | 2.6903 | 2.6735 | 2.6576 | 1.9993 | 1.9991 | 1.9989 | 1.998 | 1.9969 | 1.9935 | 1.9902 | 1.9858 | 1.9804 | 1.9649 | 1.9399 | 1.916 | 1.8933 | 1.9998 | 1.9997 | 1.9996 | 1.9993 | 1.9989 | 1.9977 | 1.9965 | 1.995 | 1.9931 | 1.9876 | 1.9788 | 1.9703 | 1.9623
NURSLING GSP | ROWNHAMS | ROMSEY | MINIMUM HEADROOM | SU 36092 21110 | YES | 18.4355 | 18.4209 | 17.5285 | 17.453 | 17.375 | 17.2944 | 17.2108 | 17.1166 | 17.0837 | 16.9775 | 16.7862 | 16.6107 | 15.497 | 15.7726 | 15.758 | 14.8656 | 14.7901 | 14.7122 | 14.6315 | 14.5479 | 14.4537 | 14.4208 | 14.1437 | 12.7528 | 11.4059 | 10.1045 | 16.515 | 16.5004 | 15.6079 | 15.5325 | 15.4545 | 15.3738 | 15.2902 | 15.1961 | 15.0784 | 13.9279 | 12.5817 | 11.3203 | 10.1015
|  | ROMSEY | CT |  |  | 18.5116 | 18.5028 | 17.9674 | 17.9228 | 17.8776 | 17.8317 | 17.7849 | 17.7347 | 17.716 | 17.6573 | 16.9671 | 16.6854 | 15.5903 | 15.8487 | 15.8399 | 15.3045 | 15.2599 | 15.2147 | 15.1688 | 15.1221 | 15.0718 | 15.0531 | 14.8558 | 12.968 | 11.5152 | 10.2031 | 16.5911 | 16.5823 | 16.0468 | 16.0022 | 15.957 | 15.9112 | 15.8644 | 15.8142 | 15.7426 | 14.6398 | 12.7944 | 11.427 | 10.1976
|  | ROMSEY | LW |  |  | 18.4355 | 18.4209 | 17.5285 | 17.453 | 17.375 | 17.2944 | 17.2108 | 17.1166 | 17.0837 | 16.9775 | 16.7862 | 16.6107 | 15.497 | 15.7726 | 15.758 | 14.8656 | 14.7901 | 14.7122 | 14.6315 | 14.5479 | 14.4537 | 14.4208 | 14.1437 | 12.7528 | 11.4059 | 10.1045 | 16.515 | 16.5004 | 15.6079 | 15.5325 | 15.4545 | 15.3738 | 15.2902 | 15.1961 | 15.0784 | 13.9279 | 12.5817 | 11.3203 | 10.1015
|  | ROMSEY | ST |  |  | 18.5496 | 18.5438 | 18.1868 | 18.1571 | 18.1268 | 18.0961 | 18.0646 | 18.0305 | 18.0164 | 17.9687 | 17.8937 | 17.8005 | 17.715 | 15.8867 | 15.8809 | 15.5239 | 15.4942 | 15.4639 | 15.4332 | 15.4018 | 15.3676 | 15.3536 | 15.3058 | 15.2308 | 14.54 | 13.7318 | 16.6291 | 16.6233 | 16.2663 | 16.2365 | 16.2063 | 16.1756 | 16.1441 | 16.11 | 16.0959 | 15.9707 | 15.1191 | 14.3262 | 13.5571
|  | ROMSEY | FS |  |  | 18.5877 | 18.5847 | 18.4063 | 18.3916 | 18.3769 | 18.3623 | 18.3475 | 18.3327 | 18.3261 | 18.3039 | 18.2711 | 18.2362 | 18.1871 | 15.9248 | 15.9219 | 15.7434 | 15.7287 | 15.7141 | 15.6994 | 15.6846 | 15.6698 | 15.6632 | 15.6411 | 15.6082 | 15.5733 | 15.5242 | 16.6671 | 16.6642 | 16.4857 | 16.4711 | 16.4564 | 16.4417 | 16.427 | 16.4122 | 16.4055 | 16.3834 | 16.3505 | 16.3157 | 16.2666
LOVEDEAN GSP | CHICHESTER & HUNSTON | ROSE GREEN | MINIMUM HEADROOM | SZ 89974 99335 | YES | 26.5435 | 26.5435 | 26.5435 | 26.2857 | 26.0198 | 25.742 | 25.454 | 25.0167 | 24.9562 | 24.7485 | 24.438 | 23.6791 | 23.6344 | 25.5043 | 25.5043 | 25.5043 | 25.2466 | 24.9806 | 24.7028 | 24.4149 | 23.9776 | 23.917 | 23.7094 | 23.0881 | 21.3464 | 20.3454 | 25.2411 | 25.2411 | 25.2411 | 24.9834 | 24.7174 | 24.4396 | 24.1343 | 23.5381 | 23.3161 | 22.6413 | 21.454 | 19.7735 | 18.832
|  | ROSE GREEN | CT |  |  | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 25.5043 | 25.5043 | 25.5043 | 25.5043 | 25.5043 | 25.5043 | 25.5043 | 25.5043 | 25.5043 | 25.5043 | 25.3307 | 24.3482 | 23.3926 | 25.2411 | 25.2411 | 25.2411 | 25.2411 | 25.2411 | 25.2411 | 25.2411 | 25.1839 | 25.0224 | 24.5554 | 23.6881 | 22.7668 | 21.8706
|  | ROSE GREEN | LW |  |  | 26.5435 | 26.5435 | 26.5435 | 26.2857 | 26.0198 | 25.742 | 25.454 | 25.0167 | 24.9562 | 24.7485 | 24.438 | 23.6791 | 23.6344 | 25.5043 | 25.5043 | 25.5043 | 25.2466 | 24.9806 | 24.7028 | 24.4149 | 23.9776 | 23.917 | 23.7094 | 23.0881 | 21.3464 | 20.3454 | 25.2411 | 25.2411 | 25.2411 | 24.9834 | 24.7174 | 24.4396 | 24.1343 | 23.5381 | 23.3161 | 22.6413 | 21.454 | 19.7735 | 18.832
|  | ROSE GREEN | ST |  |  | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 25.5043 | 25.5043 | 25.5043 | 25.5043 | 25.5043 | 25.5043 | 25.5043 | 25.5043 | 25.5043 | 25.5043 | 25.5043 | 25.4499 | 24.8312 | 25.2411 | 25.2411 | 25.2411 | 25.2411 | 25.2411 | 25.2411 | 25.2411 | 25.2411 | 25.2411 | 24.9459 | 24.3925 | 23.7999 | 23.2197
|  | ROSE GREEN | FS |  |  | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 25.5043 | 25.5043 | 25.5043 | 25.5043 | 25.5043 | 25.5043 | 25.5043 | 25.5043 | 25.5043 | 25.5043 | 25.5043 | 25.5043 | 25.5043 | 25.2411 | 25.2411 | 25.2411 | 25.2411 | 25.2411 | 25.2411 | 25.2411 | 25.2411 | 25.2411 | 25.2411 | 25.2411 | 25.0976 | 24.8892
COWLEY GSP | COWLEY LOCAL (2 X 90) | ROSE HILL | MINIMUM HEADROOM | SP 53637 03027 | YES | 30.9613 | 30.9613 | 30.9613 | 30.8703 | 30.7777 | 30.6836 | 30.5853 | 30.4338 | 30.4146 | 30.246 | 28.0155 | 26.3634 | 24.9524 | 28.6289 | 28.6289 | 28.6289 | 28.5378 | 28.4453 | 28.3511 | 28.2529 | 28.1013 | 28.0821 | 26.98 | 24.4199 | 22.5406 | 20.9048 | 29.5513 | 29.5439 | 29.5303 | 29.4232 | 29.3105 | 29.1926 | 29.075 | 28.898 | 28.7811 | 27.0462 | 24.5598 | 22.7313 | 21.1458
|  | ROSE HILL | CT |  |  | 30.9613 | 30.9613 | 30.9613 | 30.8703 | 30.7777 | 30.6836 | 30.5853 | 30.4338 | 30.4146 | 30.246 | 28.0155 | 26.3634 | 24.9524 | 28.6289 | 28.6289 | 28.6289 | 28.5378 | 28.4453 | 28.3511 | 28.2529 | 28.1013 | 28.0821 | 26.98 | 24.4199 | 22.5406 | 20.9048 | 29.5513 | 29.5439 | 29.5303 | 29.4232 | 29.3105 | 29.1926 | 29.075 | 28.898 | 28.7811 | 27.0462 | 24.5598 | 22.7313 | 21.1458
|  | ROSE HILL | LW |  |  | 30.9613 | 30.9613 | 30.9613 | 30.9613 | 30.9613 | 30.9613 | 30.9613 | 30.9613 | 30.9613 | 30.9183 | 28.9727 | 27.6315 | 26.3044 | 28.6289 | 28.6289 | 28.6289 | 28.6289 | 28.6289 | 28.6289 | 28.6289 | 28.6289 | 28.6289 | 27.6632 | 25.3879 | 23.8195 | 22.2676 | 29.5516 | 29.5443 | 29.531 | 29.5152 | 29.4954 | 29.4747 | 29.4554 | 29.4299 | 29.3969 | 27.7269 | 25.5253 | 24.0078 | 22.5062
|  | ROSE HILL | ST |  |  | 30.9613 | 30.9613 | 30.9613 | 30.9458 | 30.93 | 30.9139 | 30.8972 | 30.8715 | 30.8628 | 30.8349 | 30.8118 | 29.8713 | 29.0014 | 28.6289 | 28.6289 | 28.6289 | 28.6134 | 28.5976 | 28.5815 | 28.5648 | 28.5391 | 28.5303 | 28.5025 | 27.5831 | 26.4769 | 25.4634 | 29.5586 | 29.5553 | 29.5508 | 29.5278 | 29.5008 | 29.4712 | 29.4419 | 29.399 | 29.3713 | 29.1582 | 27.6446 | 26.5718 | 25.5904
|  | ROSE HILL | FS |  |  | 30.9613 | 30.9613 | 30.9613 | 30.9611 | 30.9608 | 30.9606 | 30.9604 | 30.96 | 30.959 | 30.9557 | 30.9542 | 30.9493 | 30.9452 | 28.6289 | 28.6289 | 28.6289 | 28.6286 | 28.6284 | 28.6282 | 28.6279 | 28.6276 | 28.6265 | 28.6233 | 28.6217 | 28.6168 | 28.6128 | 29.5631 | 29.5621 | 29.5614 | 29.5579 | 29.5528 | 29.5471 | 29.542 | 29.5346 | 29.5261 | 29.4932 | 29.4533 | 29.4221 | 29.391
MELKSHAM GSP | CHIPPENHAM | ROWDEN | MINIMUM HEADROOM | ST 90805 72608 | YES | 28.0156 | 28.0156 | 28.0156 | 27.9922 | 27.9659 | 27.9363 | 27.9034 | 27.8489 | 27.8408 | 27.8076 | 27.7403 | 27.3675 | 26.4095 | 25.5566 | 25.5566 | 25.5566 | 25.5332 | 25.5069 | 25.3886 | 25.1401 | 24.8714 | 24.6309 | 23.9141 | 22.7009 | 21.4009 | 20.2482 | 26.4886 | 26.4372 | 26.4208 | 26.3838 | 26.3448 | 26.3021 | 26.2561 | 26.1885 | 26.1667 | 25.5902 | 24.4483 | 23.2228 | 22.1535
|  | ROWDEN | CT |  |  | 28.0156 | 28.0156 | 28.0156 | 28.015 | 28.0138 | 28.0121 | 28.0096 | 28.0042 | 28.0032 | 27.9979 | 27.9547 | 27.8 | 26.8362 | 25.5566 | 25.5566 | 25.5566 | 25.556 | 25.5548 | 25.5531 | 25.3904 | 25.1709 | 24.943 | 24.2544 | 23.0647 | 21.8591 | 20.7006 | 26.4901 | 26.4394 | 26.4247 | 26.4121 | 26.3997 | 26.3867 | 26.3711 | 26.3526 | 26.3378 | 25.9212 | 24.8028 | 23.67 | 22.5949
|  | ROWDEN | LW |  |  | 28.0156 | 28.0156 | 28.0156 | 27.9922 | 27.9659 | 27.9363 | 27.9034 | 27.8489 | 27.8408 | 27.8076 | 27.7403 | 27.3675 | 26.4095 | 25.5566 | 25.5566 | 25.5566 | 25.5332 | 25.5069 | 25.3886 | 25.1401 | 24.8714 | 24.6309 | 23.9141 | 22.7009 | 21.4009 | 20.2482 | 26.4886 | 26.4372 | 26.4208 | 26.3838 | 26.3448 | 26.3021 | 26.2561 | 26.1885 | 26.1667 | 25.5902 | 24.4483 | 23.2228 | 22.1535
|  | ROWDEN | ST |  |  | 28.0156 | 28.0156 | 28.0156 | 28.0152 | 28.0143 | 28.013 | 28.0111 | 28.0069 | 28.0049 | 27.994 | 27.9797 | 27.9295 | 27.9112 | 25.5566 | 25.5566 | 25.5566 | 25.5561 | 25.5553 | 25.554 | 25.5521 | 25.5479 | 25.5459 | 25.535 | 24.916 | 24.1196 | 23.367 | 26.4923 | 26.486 | 26.4767 | 26.4669 | 26.4555 | 26.4461 | 26.4361 | 26.423 | 26.4116 | 26.3735 | 26.3141 | 25.7905 | 25.0836
|  | ROWDEN | FS |  |  | 28.0156 | 28.0156 | 28.0156 | 28.0156 | 28.0155 | 28.0155 | 28.0154 | 28.0152 | 28.0145 | 28.0106 | 28.0075 | 27.9925 | 27.9779 | 25.5566 | 25.5566 | 25.5566 | 25.5566 | 25.5565 | 25.5565 | 25.5564 | 25.5562 | 25.5555 | 25.5516 | 25.5485 | 25.5335 | 25.5189 | 26.5 | 26.4981 | 26.4962 | 26.4937 | 26.491 | 26.4883 | 26.4855 | 26.4818 | 26.4775 | 26.463 | 26.4426 | 26.4114 | 26.3815
LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | ROWNER PARK | MINIMUM HEADROOM | SU 58018 00782 | YES | 30.9032 | 30.9006 | 30.8957 | 30.8907 | 30.8855 | 30.8797 | 30.8634 | 30.8471 | 30.8298 | 30.7748 | 30.536 | 29.9488 | 29.3528 | 28.7732 | 28.7724 | 28.7709 | 28.7693 | 28.7677 | 28.766 | 28.761 | 28.756 | 28.7507 | 28.7339 | 28.696 | 27.8903 | 26.9304 | 29.9072 | 29.9072 | 29.9072 | 29.9072 | 29.9072 | 29.9072 | 29.9072 | 29.9072 | 29.9072 | 29.9072 | 29.9072 | 29.3154 | 28.3584
|  | ROWNER PARK | CT |  |  | 30.9032 | 30.9006 | 30.8957 | 30.8907 | 30.8855 | 30.8803 | 30.864 | 30.8477 | 30.8303 | 30.7754 | 30.5379 | 29.9508 | 29.3554 | 28.7732 | 28.7724 | 28.7709 | 28.7693 | 28.7677 | 28.7661 | 28.7612 | 28.7562 | 28.7509 | 28.7341 | 28.6962 | 27.8936 | 26.934 | 29.9072 | 29.9072 | 29.9072 | 29.9072 | 29.9072 | 29.9072 | 29.9072 | 29.9072 | 29.9072 | 29.9072 | 29.9072 | 29.3187 | 28.3621
|  | ROWNER PARK | LW |  |  | 30.9053 | 30.9038 | 30.9014 | 30.8988 | 30.896 | 30.8797 | 30.8634 | 30.8471 | 30.8298 | 30.7748 | 30.536 | 29.9488 | 29.3528 | 28.7738 | 28.7734 | 28.7726 | 28.7718 | 28.7709 | 28.766 | 28.761 | 28.756 | 28.7507 | 28.7339 | 28.696 | 27.8903 | 26.9304 | 29.9072 | 29.9072 | 29.9072 | 29.9072 | 29.9072 | 29.9072 | 29.9072 | 29.9072 | 29.9072 | 29.9072 | 29.9072 | 29.3154 | 28.3584
|  | ROWNER PARK | ST |  |  | 30.906 | 30.9051 | 30.9038 | 30.9022 | 30.9002 | 30.8933 | 30.8864 | 30.8752 | 30.8634 | 30.8259 | 30.7407 | 30.5044 | 30.1285 | 28.774 | 28.7737 | 28.7733 | 28.7728 | 28.7723 | 28.7701 | 28.768 | 28.7646 | 28.761 | 28.7495 | 28.7235 | 28.6936 | 28.1832 | 29.9072 | 29.9072 | 29.9072 | 29.9072 | 29.9072 | 29.9072 | 29.9072 | 29.9072 | 29.9072 | 29.9072 | 29.9072 | 29.9072 | 29.6075
|  | ROWNER PARK | FS |  |  | 30.9068 | 30.9064 | 30.906 | 30.9053 | 30.9046 | 30.9024 | 30.9001 | 30.8973 | 30.8926 | 30.878 | 30.8436 | 30.8004 | 30.7555 | 28.7743 | 28.7741 | 28.774 | 28.7738 | 28.7736 | 28.7729 | 28.7722 | 28.7713 | 28.7699 | 28.7655 | 28.7549 | 28.7417 | 28.728 | 29.9072 | 29.9072 | 29.9072 | 29.9072 | 29.9072 | 29.9072 | 29.9072 | 29.9072 | 29.9072 | 29.9072 | 29.9072 | 29.9072 | 29.9072
FAWLEY GSP | COWES & WOOTTON COMMON BSP | RYDE | MINIMUM HEADROOM | SZ 59554 91973 | YES | 45.9036 | 45.9036 | 45.9036 | 45.9036 | 45.9036 | 45.9036 | 45.9036 | 45.9036 | 45.9036 | 45.9036 | 45.8268 | 44.6108 | 43.4272 | 42.1216 | 42.1044 | 42.0986 | 42.0933 | 42.0875 | 42.0731 | 42.0601 | 42.0477 | 42.0348 | 41.9973 | 41.3535 | 39.9315 | 38.5473 | 43.9222 | 43.8973 | 43.889 | 43.8814 | 43.873 | 43.8521 | 43.8333 | 43.8154 | 43.7967 | 43.7425 | 42.6 | 41.2765 | 39.9881
|  | RYDE | CT |  |  | 45.9036 | 45.9036 | 45.9036 | 45.9036 | 45.9036 | 45.9036 | 45.9036 | 45.9036 | 45.9036 | 45.9036 | 45.9036 | 44.7719 | 43.5885 | 42.1216 | 42.1044 | 42.0987 | 42.0934 | 42.0876 | 42.0815 | 42.0685 | 42.0561 | 42.0432 | 42.0057 | 41.5417 | 40.1199 | 38.736 | 43.9222 | 43.8973 | 43.8891 | 43.8814 | 43.8731 | 43.8642 | 43.8454 | 43.8275 | 43.8088 | 43.7546 | 42.7752 | 41.4518 | 40.1638
|  | RYDE | LW |  |  | 45.9036 | 45.9036 | 45.9036 | 45.9036 | 45.9036 | 45.9036 | 45.9036 | 45.9036 | 45.9036 | 45.9036 | 45.8268 | 44.6108 | 43.4272 | 42.1216 | 42.1044 | 42.0986 | 42.0933 | 42.0875 | 42.0731 | 42.0601 | 42.0477 | 42.0348 | 41.9973 | 41.3535 | 39.9315 | 38.5473 | 43.9222 | 43.8973 | 43.889 | 43.8814 | 43.873 | 43.8521 | 43.8333 | 43.8154 | 43.7967 | 43.7425 | 42.6 | 41.2765 | 39.9881
|  | RYDE | ST |  |  | 45.9036 | 45.9036 | 45.9036 | 45.9036 | 45.9036 | 45.9036 | 45.9036 | 45.9036 | 45.9036 | 45.9036 | 45.9036 | 45.9036 | 45.4903 | 42.1231 | 42.1073 | 42.1042 | 42.101 | 42.0971 | 42.0894 | 42.0826 | 42.0741 | 42.0653 | 42.04 | 41.9985 | 41.8587 | 40.9599 | 43.9244 | 43.9015 | 43.897 | 43.8924 | 43.8868 | 43.8756 | 43.8658 | 43.8536 | 43.8409 | 43.8042 | 43.7442 | 43.0702 | 42.2337
|  | RYDE | FS |  |  | 45.9036 | 45.9036 | 45.9036 | 45.9036 | 45.9036 | 45.9036 | 45.9036 | 45.9036 | 45.9036 | 45.9036 | 45.9036 | 45.9036 | 45.9036 | 42.1248 | 42.1102 | 42.1091 | 42.1078 | 42.1064 | 42.1041 | 42.1022 | 42.1001 | 42.0967 | 42.0869 | 42.0711 | 42.056 | 42.0419 | 43.9268 | 43.9057 | 43.9041 | 43.9023 | 43.9002 | 43.8969 | 43.8942 | 43.8911 | 43.8862 | 43.872 | 43.8491 | 43.8274 | 43.8069
MANNINGTON GSP | SALISBURY | SALISBURY CENTRAL | MINIMUM HEADROOM | SU 14215 30481 | YES | 50.6558 | 50.6363 | 49.4446 | 49.346 | 49.2466 | 49.1462 | 49.0446 | 48.9393 | 48.8989 | 48.7749 | 48.5631 | 48.4137 | 48.1966 | 47.756 | 47.7307 | 46.5267 | 46.4162 | 46.3048 | 46.1897 | 46.0737 | 45.9539 | 45.8979 | 45.7278 | 44.7773 | 42.9824 | 41.1437 | 48.4899 | 48.4704 | 47.2787 | 47.1801 | 47.0807 | 46.9802 | 46.8787 | 46.7734 | 46.733 | 46.5808 | 45.6078 | 43.7841 | 41.9171
|  | SALISBURY CENTRAL | CT |  |  | 50.7574 | 50.7457 | 50.0307 | 49.9718 | 49.9127 | 49.8534 | 49.7937 | 49.7328 | 49.7089 | 49.6364 | 48.7632 | 48.4411 | 48.2199 | 47.8581 | 47.8408 | 47.114 | 47.0437 | 46.9732 | 46.9026 | 46.8284 | 46.7531 | 46.7137 | 46.595 | 45.0931 | 43.1258 | 41.2832 | 48.5915 | 48.5798 | 47.8647 | 47.8059 | 47.7468 | 47.6874 | 47.6278 | 47.5669 | 47.543 | 47.4491 | 45.9256 | 43.9295 | 42.0586
|  | SALISBURY CENTRAL | LW |  |  | 50.6558 | 50.6363 | 49.4446 | 49.346 | 49.2466 | 49.1462 | 49.0446 | 48.9393 | 48.8989 | 48.7749 | 48.5631 | 48.4137 | 48.1966 | 47.756 | 47.7307 | 46.5267 | 46.4162 | 46.3048 | 46.1897 | 46.0737 | 45.9539 | 45.8979 | 45.7278 | 44.7773 | 42.9824 | 41.1437 | 48.4899 | 48.4704 | 47.2787 | 47.1801 | 47.0807 | 46.9802 | 46.8787 | 46.7734 | 46.733 | 46.5808 | 45.6078 | 43.7841 | 41.9171
|  | SALISBURY CENTRAL | ST |  |  | 50.8082 | 50.8004 | 50.3237 | 50.2844 | 50.245 | 50.2054 | 50.1655 | 50.1247 | 50.1082 | 50.0567 | 49.9725 | 49.9043 | 49.8106 | 47.9141 | 47.9039 | 47.4231 | 47.3789 | 47.3334 | 47.2846 | 47.2358 | 47.185 | 47.1579 | 47.0754 | 46.9395 | 46.8192 | 45.7742 | 48.6423 | 48.6345 | 48.1578 | 48.1185 | 48.0791 | 48.0395 | 47.9996 | 47.9587 | 47.9423 | 47.8908 | 47.7951 | 47.6652 | 46.6003
|  | SALISBURY CENTRAL | FS |  |  | 50.859 | 50.8551 | 50.6167 | 50.5972 | 50.5776 | 50.5581 | 50.5385 | 50.5189 | 50.5108 | 50.4857 | 50.4453 | 50.4155 | 50.3663 | 47.9684 | 47.964 | 47.7252 | 47.7037 | 47.6818 | 47.6592 | 47.6367 | 47.6132 | 47.601 | 47.5639 | 47.5039 | 47.4549 | 47.3874 | 48.6931 | 48.6892 | 48.4508 | 48.4313 | 48.4117 | 48.3922 | 48.3726 | 48.353 | 48.3449 | 48.3198 | 48.2794 | 48.2496 | 48.2004
BRAMLEY (FLEE) | CAMBERLEY MAIN | SANDHURST | MINIMUM HEADROOM | SU 83597 60930 | YES | 45.7567 | 45.7567 | 45.7567 | 45.7337 | 45.7101 | 45.6858 | 45.6601 | 45.6199 | 45.6147 | 45.597 | 45.5026 | 44.6946 | 43.0844 | 42.7624 | 42.7532 | 42.7341 | 42.708 | 42.6703 | 42.632 | 42.5828 | 42.5191 | 42.4887 | 42.2482 | 40.5048 | 38.5801 | 36.7025 | 44.3778 | 44.371 | 44.3571 | 44.3318 | 44.2979 | 44.2634 | 44.2206 | 44.1632 | 44.1397 | 44.0666 | 42.3888 | 40.4417 | 38.5418
|  | SANDHURST | CT |  |  | 45.7567 | 45.7567 | 45.7567 | 45.7337 | 45.7101 | 45.6858 | 45.6601 | 45.6199 | 45.6147 | 45.597 | 45.5026 | 44.7216 | 43.0872 | 42.7665 | 42.7595 | 42.7451 | 42.708 | 42.6703 | 42.632 | 42.5828 | 42.5191 | 42.4887 | 42.3952 | 40.6646 | 38.6601 | 36.7584 | 44.3807 | 44.3756 | 44.3651 | 44.3318 | 44.2979 | 44.2634 | 44.2206 | 44.1632 | 44.1397 | 44.0666 | 42.553 | 40.526 | 38.6021
|  | SANDHURST | LW |  |  | 45.7567 | 45.7567 | 45.7567 | 45.7559 | 45.7541 | 45.7512 | 45.7473 | 45.7395 | 45.7381 | 45.7312 | 45.7144 | 44.6946 | 43.0844 | 42.7624 | 42.7532 | 42.7341 | 42.7145 | 42.6941 | 42.6675 | 42.6401 | 42.6087 | 42.5822 | 42.2482 | 40.5048 | 38.5801 | 36.7025 | 44.3778 | 44.371 | 44.3571 | 44.3426 | 44.3272 | 44.3071 | 44.2859 | 44.261 | 44.2413 | 44.1008 | 42.3888 | 40.4417 | 38.5418
|  | SANDHURST | ST |  |  | 45.7567 | 45.7567 | 45.7567 | 45.751 | 45.7449 | 45.7386 | 45.7318 | 45.7207 | 45.7167 | 45.702 | 45.6878 | 45.6372 | 45.5538 | 42.7903 | 42.7633 | 42.7545 | 42.7381 | 42.7191 | 42.6945 | 42.6697 | 42.6426 | 42.6214 | 42.5553 | 42.0978 | 40.8191 | 39.5922 | 44.3981 | 44.3784 | 44.372 | 44.3584 | 44.343 | 44.3233 | 44.3034 | 44.2806 | 44.2641 | 44.2119 | 43.9647 | 42.7077 | 41.4665
|  | SANDHURST | FS |  |  | 45.7567 | 45.7567 | 45.7567 | 45.7544 | 45.7521 | 45.7498 | 45.7474 | 45.7437 | 45.7333 | 45.6994 | 45.6828 | 45.6282 | 45.5816 | 42.7985 | 42.7759 | 42.7752 | 42.7699 | 42.7642 | 42.756 | 42.7477 | 42.7364 | 42.7193 | 42.6655 | 42.6124 | 42.5186 | 42.4333 | 44.4041 | 44.3876 | 44.3871 | 44.3826 | 44.3778 | 44.3711 | 44.3645 | 44.3552 | 44.3399 | 44.2916 | 44.2483 | 44.1651 | 44.0903
FAWLEY GSP | COWES & WOOTTON COMMON BSP | SANDOWN | MINIMUM HEADROOM | SZ 59877 85052 | YES | 23.7597 | 23.7597 | 23.7597 | 23.7597 | 23.7597 | 23.7597 | 23.7597 | 23.7597 | 23.7597 | 23.7597 | 23.7597 | 23.7547 | 22.9291 | 21.9098 | 21.9087 | 21.906 | 21.9034 | 21.9006 | 21.892 | 21.8834 | 21.8747 | 21.866 | 21.722 | 20.784 | 19.8083 | 18.8501 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.2728 | 21.3774 | 20.4211
|  | SANDOWN | CT |  |  | 23.7597 | 23.7597 | 23.7597 | 23.7597 | 23.7597 | 23.7597 | 23.7597 | 23.7597 | 23.7597 | 23.7597 | 23.7597 | 23.7597 | 23.0393 | 21.9098 | 21.9087 | 21.906 | 21.9034 | 21.9006 | 21.8978 | 21.8892 | 21.8804 | 21.8717 | 21.8463 | 20.9115 | 19.9359 | 18.978 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.3833 | 21.5048 | 20.5488
|  | SANDOWN | LW |  |  | 23.7597 | 23.7597 | 23.7597 | 23.7597 | 23.7597 | 23.7597 | 23.7597 | 23.7597 | 23.7597 | 23.7597 | 23.7597 | 23.7547 | 22.9291 | 21.9098 | 21.9087 | 21.906 | 21.9034 | 21.9006 | 21.892 | 21.8834 | 21.8747 | 21.866 | 21.722 | 20.784 | 19.8083 | 18.8501 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.2728 | 21.3774 | 20.4211
|  | SANDOWN | ST |  |  | 23.7597 | 23.7597 | 23.7597 | 23.7597 | 23.7597 | 23.7597 | 23.7597 | 23.7597 | 23.7597 | 23.7597 | 23.7597 | 23.7597 | 23.7597 | 21.9105 | 21.9099 | 21.9086 | 21.907 | 21.9051 | 21.901 | 21.8969 | 21.891 | 21.885 | 21.8679 | 21.7049 | 21.0757 | 20.454 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.5256 | 21.9868
|  | SANDOWN | FS |  |  | 23.7597 | 23.7597 | 23.7597 | 23.7597 | 23.7597 | 23.7597 | 23.7597 | 23.7597 | 23.7597 | 23.7597 | 23.7597 | 23.7597 | 23.7597 | 21.9114 | 21.9113 | 21.9111 | 21.9106 | 21.91 | 21.9089 | 21.9078 | 21.9065 | 21.9042 | 21.8975 | 21.8869 | 21.8764 | 21.8665 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871
LOVEDEAN GSP | CHICHESTER & HUNSTON | SELSEY | MINIMUM HEADROOM | SZ 85667 94289 | YES | 23.2222 | 23.2222 | 23.2222 | 23.2222 | 23.2222 | 23.2222 | 23.2222 | 23.2222 | 23.2222 | 22.7554 | 21.7031 | 20.6206 | 19.5563 | 21.6636 | 21.6636 | 21.6636 | 21.6617 | 21.6493 | 21.5984 | 21.5433 | 21.4876 | 21.4275 | 20.9022 | 19.6313 | 18.3237 | 17.0383 | 22.4264 | 22.4264 | 22.4264 | 22.4264 | 22.4264 | 22.4264 | 22.4264 | 22.2743 | 21.998 | 21.2078 | 19.9393 | 18.6342 | 17.3512
|  | SELSEY | CT |  |  | 23.2222 | 23.2222 | 23.2222 | 23.2222 | 23.2222 | 23.2222 | 23.2222 | 23.2222 | 23.2222 | 22.8402 | 21.7877 | 20.7053 | 19.6411 | 21.6636 | 21.6636 | 21.6636 | 21.6618 | 21.6493 | 21.6198 | 21.5647 | 21.5091 | 21.4489 | 21.0046 | 19.7334 | 18.4261 | 17.1407 | 22.4264 | 22.4264 | 22.4264 | 22.4264 | 22.4264 | 22.4264 | 22.4264 | 22.3727 | 22.0964 | 21.31 | 20.0412 | 18.7363 | 17.4534
|  | SELSEY | LW |  |  | 23.2222 | 23.2222 | 23.2222 | 23.2222 | 23.2222 | 23.2222 | 23.2222 | 23.2222 | 23.2222 | 22.7554 | 21.7031 | 20.6206 | 19.5563 | 21.6636 | 21.6636 | 21.6636 | 21.6617 | 21.6493 | 21.5984 | 21.5433 | 21.4876 | 21.4275 | 20.9022 | 19.6313 | 18.3237 | 17.0383 | 22.4264 | 22.4264 | 22.4264 | 22.4264 | 22.4264 | 22.4264 | 22.4264 | 22.2743 | 21.998 | 21.2078 | 19.9393 | 18.6342 | 17.3512
|  | SELSEY | ST |  |  | 23.2222 | 23.2222 | 23.2222 | 23.2222 | 23.2222 | 23.2222 | 23.2222 | 23.2222 | 23.2222 | 23.2222 | 22.8178 | 22.1201 | 21.4298 | 21.6636 | 21.6636 | 21.6636 | 21.6636 | 21.6636 | 21.6586 | 21.6459 | 21.6081 | 21.5671 | 21.455 | 20.9776 | 20.1349 | 19.3011 | 22.4264 | 22.4264 | 22.4264 | 22.4264 | 22.4264 | 22.4264 | 22.4264 | 22.4264 | 22.4264 | 22.1244 | 21.283 | 20.4419 | 19.6097
|  | SELSEY | FS |  |  | 23.2222 | 23.2222 | 23.2222 | 23.2222 | 23.2222 | 23.2222 | 23.2222 | 23.2222 | 23.2222 | 23.2222 | 23.2222 | 23.2222 | 23.2222 | 21.6636 | 21.6636 | 21.6636 | 21.6636 | 21.6636 | 21.6636 | 21.6636 | 21.6636 | 21.6636 | 21.6597 | 21.6129 | 21.548 | 21.4862 | 22.4264 | 22.4264 | 22.4264 | 22.4264 | 22.4264 | 22.4264 | 22.4264 | 22.4264 | 22.4264 | 22.4264 | 22.4264 | 22.4264 | 22.2675
MANNINGTON GSP | SHAFTESBURY BSP | SHAFTESBURY | MINIMUM HEADROOM | ST 85605 23325 | YES | 20.3297 | 20.3297 | 20.3297 | 20.1647 | 19.993 | 19.8121 | 19.6231 | 19.3331 | 19.2925 | 19.1497 | 18.9261 | 18.5403 | 18.0867 | 17.5631 | 17.5351 | 17.4877 | 17.2893 | 17.0815 | 16.7573 | 16.426 | 15.995 | 15.8045 | 15.2183 | 14.2401 | 13.0571 | 12.2489 | 18.7008 | 18.6991 | 18.6962 | 18.5292 | 18.3553 | 18.1658 | 17.9681 | 17.6695 | 17.6198 | 17.2554 | 16.2383 | 15.0301 | 14.198
|  | SHAFTESBURY | CT |  |  | 20.3297 | 20.3297 | 20.3297 | 20.3293 | 20.3285 | 20.3273 | 20.3257 | 20.3219 | 20.3213 | 20.3177 | 20.2883 | 20.2554 | 19.9123 | 17.5631 | 17.5351 | 17.4877 | 17.4539 | 17.4171 | 17.3788 | 17.2348 | 17.0902 | 16.9396 | 16.4927 | 15.7128 | 14.8827 | 14.0894 | 18.7008 | 18.6991 | 18.6962 | 18.6938 | 18.6908 | 18.6874 | 18.6771 | 18.6648 | 18.6551 | 18.5346 | 17.7145 | 16.8592 | 16.0412
|  | SHAFTESBURY | LW |  |  | 20.3297 | 20.3297 | 20.3297 | 20.1647 | 19.993 | 19.8121 | 19.6231 | 19.3331 | 19.2925 | 19.1497 | 18.9261 | 18.5403 | 18.0867 | 17.5631 | 17.5351 | 17.4877 | 17.2893 | 17.0815 | 16.7573 | 16.426 | 15.995 | 15.8045 | 15.2183 | 14.2401 | 13.0571 | 12.2489 | 18.7008 | 18.6991 | 18.6962 | 18.5292 | 18.3553 | 18.1658 | 17.9681 | 17.6695 | 17.6198 | 17.2554 | 16.2383 | 15.0301 | 14.198
|  | SHAFTESBURY | ST |  |  | 20.3297 | 20.3297 | 20.3297 | 20.3294 | 20.3288 | 20.328 | 20.3267 | 20.3238 | 20.3224 | 20.315 | 20.3053 | 20.2711 | 20.2586 | 17.7337 | 17.5637 | 17.5392 | 17.5198 | 17.4944 | 17.4102 | 17.3263 | 17.2272 | 17.1235 | 16.8167 | 16.3094 | 15.7798 | 15.2588 | 18.7112 | 18.7009 | 18.6994 | 18.6979 | 18.6958 | 18.6899 | 18.6836 | 18.6749 | 18.6673 | 18.6417 | 18.3435 | 17.7842 | 17.2471
|  | SHAFTESBURY | FS |  |  | 20.3297 | 20.3297 | 20.3297 | 20.3297 | 20.3297 | 20.3296 | 20.3296 | 20.3295 | 20.329 | 20.3263 | 20.3242 | 20.314 | 20.304 | 17.7538 | 17.7469 | 17.7399 | 17.7344 | 17.7271 | 17.7027 | 17.6786 | 17.6478 | 17.6077 | 17.4894 | 17.297 | 17.1041 | 16.9205 | 18.7124 | 18.712 | 18.7115 | 18.7112 | 18.7107 | 18.7092 | 18.7077 | 18.7057 | 18.7029 | 18.6932 | 18.6795 | 18.6582 | 18.6377
FAWLEY GSP | COWES & WOOTTON COMMON BSP | SHALFLEET | MINIMUM HEADROOM | SZ 40828 88643 | YES | 21.7702 | 21.7539 | 21.7184 | 21.6671 | 21.6121 | 21.5114 | 21.4146 | 21.3056 | 21.2236 | 20.9772 | 20.5681 | 20.1059 | 19.7374 | 19.409 | 19.3881 | 19.3426 | 19.2808 | 19.2151 | 19.0913 | 18.9732 | 18.8438 | 18.7402 | 18.4306 | 17.9191 | 17.352 | 16.881 | 19.4849 | 19.4747 | 19.4525 | 19.4148 | 19.3741 | 19.3038 | 19.235 | 19.153 | 19.0995 | 18.9364 | 18.6624 | 18.3386 | 18.1052
|  | SHALFLEET | CT |  |  | 21.7708 | 21.7548 | 21.7201 | 21.6835 | 21.6451 | 21.6054 | 21.5284 | 21.4517 | 21.3745 | 21.1472 | 20.7503 | 20.3407 | 19.9669 | 19.4098 | 19.3893 | 19.3448 | 19.2979 | 19.2489 | 19.1984 | 19.1002 | 19.003 | 18.9042 | 18.6138 | 18.1144 | 17.6 | 17.1238 | 19.4853 | 19.4753 | 19.4535 | 19.4304 | 19.4059 | 19.3806 | 19.3316 | 19.2818 | 19.2331 | 19.0891 | 18.8272 | 18.556 | 18.3172
|  | SHALFLEET | LW |  |  | 21.7702 | 21.7539 | 21.7184 | 21.6671 | 21.6121 | 21.5114 | 21.4146 | 21.3056 | 21.2236 | 20.9772 | 20.5681 | 20.1059 | 19.7374 | 19.409 | 19.3881 | 19.3426 | 19.2808 | 19.2151 | 19.0913 | 18.9732 | 18.8438 | 18.7402 | 18.4306 | 17.9191 | 17.352 | 16.881 | 19.4849 | 19.4747 | 19.4525 | 19.4148 | 19.3741 | 19.3038 | 19.235 | 19.153 | 19.0995 | 18.9364 | 18.6624 | 18.3386 | 18.1052
|  | SHALFLEET | ST |  |  | 21.7781 | 21.7681 | 21.7498 | 21.7266 | 21.6985 | 21.645 | 21.5954 | 21.5427 | 21.4889 | 21.3297 | 21.0773 | 20.798 | 20.5473 | 19.4191 | 19.4063 | 19.3828 | 19.3531 | 19.3174 | 19.249 | 19.1858 | 19.1191 | 19.0506 | 18.8488 | 18.5282 | 18.1814 | 17.864 | 19.4898 | 19.4836 | 19.4721 | 19.4574 | 19.4396 | 19.4057 | 19.374 | 19.3397 | 19.3054 | 19.2023 | 19.0397 | 18.8496 | 18.687
|  | SHALFLEET | FS |  |  | 21.7911 | 21.7888 | 21.785 | 21.7774 | 21.7687 | 21.7515 | 21.7363 | 21.7176 | 21.6968 | 21.6357 | 21.5422 | 21.4442 | 21.3521 | 19.4358 | 19.4328 | 19.428 | 19.4182 | 19.4071 | 19.385 | 19.3655 | 19.3416 | 19.3151 | 19.2375 | 19.1183 | 18.9961 | 18.8812 | 19.498 | 19.4966 | 19.4942 | 19.4894 | 19.484 | 19.4732 | 19.4636 | 19.4518 | 19.4386 | 19.3991 | 19.3395 | 19.2736 | 19.2115
FAWLEY GSP | COWES & WOOTTON COMMON BSP | SHANKLIN | MINIMUM HEADROOM | SZ 57809 81912 | YES | 42.5849 | 42.553 | 42.4961 | 42.4501 | 42.4039 | 42.2527 | 42.1021 | 41.9526 | 41.7926 | 41.3201 | 40.5335 | 39.7204 | 38.9209 | 39.3139 | 39.2764 | 39.2096 | 39.1556 | 39.1013 | 38.9238 | 38.747 | 38.5716 | 38.3837 | 37.8289 | 36.9054 | 35.9508 | 35.0122 | 41.2809 | 41.2523 | 41.2012 | 41.16 | 41.1185 | 40.9828 | 40.8477 | 40.7068 | 40.5238 | 39.9835 | 39.0839 | 38.154 | 37.2398
|  | SHANKLIN | CT |  |  | 42.5849 | 42.553 | 42.4961 | 42.4501 | 42.4039 | 42.3567 | 42.2062 | 42.0567 | 41.8967 | 41.4243 | 40.6376 | 39.8247 | 39.0254 | 39.3139 | 39.2764 | 39.2096 | 39.1556 | 39.1013 | 39.0459 | 38.8692 | 38.6938 | 38.5058 | 37.9513 | 37.0276 | 36.0733 | 35.1348 | 41.2809 | 41.2523 | 41.2012 | 41.16 | 41.1185 | 41.0761 | 40.9411 | 40.807 | 40.6428 | 40.1027 | 39.203 | 38.2734 | 37.3592
|  | SHANKLIN | LW |  |  | 42.5849 | 42.553 | 42.4961 | 42.4501 | 42.4039 | 42.2527 | 42.1021 | 41.9526 | 41.7926 | 41.3201 | 40.5335 | 39.7204 | 38.9209 | 39.3139 | 39.2764 | 39.2096 | 39.1556 | 39.1013 | 38.9238 | 38.747 | 38.5716 | 38.3837 | 37.8289 | 36.9054 | 35.9508 | 35.0122 | 41.2809 | 41.2523 | 41.2012 | 41.16 | 41.1185 | 40.9828 | 40.8477 | 40.7068 | 40.5238 | 39.9835 | 39.0839 | 38.154 | 37.2398
|  | SHANKLIN | ST |  |  | 42.5896 | 42.5646 | 42.5268 | 42.4883 | 42.4416 | 42.355 | 42.2692 | 42.1672 | 42.058 | 41.7397 | 41.2152 | 40.6911 | 40.1716 | 39.3193 | 39.29 | 39.2456 | 39.2004 | 39.1456 | 39.0439 | 38.9433 | 38.8234 | 38.6953 | 38.3216 | 37.7058 | 37.0904 | 36.4805 | 41.2851 | 41.2627 | 41.2287 | 41.1942 | 41.1523 | 41.0746 | 40.9977 | 40.9061 | 40.8081 | 40.4634 | 39.8635 | 39.2641 | 38.67
|  | SHANKLIN | FS |  |  | 42.6231 | 42.617 | 42.6114 | 42.6042 | 42.5955 | 42.5744 | 42.5534 | 42.5263 | 42.484 | 42.3614 | 42.1627 | 41.9711 | 41.7896 | 39.3587 | 39.3515 | 39.345 | 39.3365 | 39.3263 | 39.3016 | 39.2769 | 39.245 | 39.1954 | 39.0515 | 38.8182 | 38.5932 | 38.3801 | 41.3152 | 41.3097 | 41.3047 | 41.2982 | 41.2904 | 41.2715 | 41.2527 | 41.2283 | 41.1904 | 41.0804 | 40.9021 | 40.7279 | 40.5204
AXMINSTER | YEOVIL BSP | SHERBORNE | MINIMUM HEADROOM | ST 63978 18163 | YES | 13.0592 | 22.7824 | 22.7802 | 22.5972 | 22.4103 | 22.2204 | 22.0161 | 21.7039 | 21.6534 | 21.4888 | 20.5547 | 19.287 | 18.5864 | 11.9258 | 21.3008 | 21.3008 | 21.1199 | 20.9358 | 20.7488 | 20.5535 | 20.2524 | 20.2143 | 19.7068 | 18.1217 | 16.7579 | 15.9642 | 11.7548 | 21.5048 | 21.5048 | 21.3239 | 21.1399 | 20.9529 | 20.7576 | 20.4565 | 20.4183 | 20.2958 | 19.4682 | 18.1212 | 17.3438
|  | SHERBORNE | CT |  |  | 13.0605 | 22.7824 | 22.7802 | 22.5972 | 22.4103 | 22.2204 | 22.0161 | 21.7039 | 21.6534 | 21.4888 | 20.5547 | 19.287 | 18.5864 | 11.9258 | 21.3008 | 21.3008 | 21.1199 | 20.9358 | 20.7488 | 20.5535 | 20.2524 | 20.2143 | 19.7068 | 18.1217 | 16.7579 | 15.9642 | 11.7548 | 21.5048 | 21.5048 | 21.3239 | 21.1399 | 20.9529 | 20.7576 | 20.4565 | 20.4183 | 20.2958 | 19.4682 | 18.1212 | 17.3438
|  | SHERBORNE | LW |  |  | 13.0605 | 22.7824 | 22.7802 | 22.7782 | 22.7752 | 22.7664 | 22.7575 | 22.7463 | 22.734 | 22.692 | 22.2579 | 21.7052 | 21.1704 | 11.9258 | 21.3008 | 21.3008 | 21.3008 | 21.3008 | 21.3008 | 21.3008 | 21.3008 | 21.3008 | 20.8316 | 19.8125 | 19.1636 | 18.5357 | 11.7548 | 21.5048 | 21.5048 | 21.5048 | 21.5048 | 21.5048 | 21.5048 | 21.5048 | 21.5048 | 21.5048 | 21.1612 | 20.5291 | 19.9175
|  | SHERBORNE | ST |  |  | 13.0592 | 22.8076 | 22.805 | 22.8018 | 22.7973 | 22.793 | 22.7887 | 22.7811 | 22.7727 | 22.7435 | 22.6942 | 22.6649 | 22.4488 | 11.9258 | 21.3008 | 21.3008 | 21.3008 | 21.3008 | 21.3008 | 21.3008 | 21.3008 | 21.3008 | 21.3008 | 20.8632 | 20.444 | 20.0366 | 11.7548 | 21.5048 | 21.5048 | 21.5048 | 21.5048 | 21.5048 | 21.5048 | 21.5048 | 21.5048 | 21.5048 | 21.5048 | 21.5048 | 21.3794
|  | SHERBORNE | FS |  |  | 13.0621 | 22.812 | 22.8119 | 22.8116 | 22.8109 | 22.8094 | 22.8078 | 22.8053 | 22.802 | 22.7906 | 22.7707 | 22.7598 | 22.7495 | 11.9258 | 21.3008 | 21.3008 | 21.3008 | 21.3008 | 21.3008 | 21.3008 | 21.3008 | 21.3008 | 21.3008 | 21.3008 | 21.3008 | 21.3008 | 11.7548 | 21.5048 | 21.5048 | 21.5048 | 21.5048 | 21.5048 | 21.5048 | 21.5048 | 21.5048 | 21.5048 | 21.5048 | 21.5048 | 21.5048
MINETY GSP | CIRENCESTER BSP | SHIPTON OLIFFE | MINIMUM HEADROOM | SP 03884 19102 | YES | 6.2091 | 6.1851 | 6.1343 | 6.07 | 5.9929 | 5.9029 | 5.8106 | 5.6754 | 5.6171 | 5.4361 | 5.2476 | 4.8231 | 4.6314 | 4.9487 | 4.9204 | 4.8606 | 4.7875 | 4.7147 | 4.6268 | 4.5317 | 4.3935 | 4.332 | 4.1416 | 3.9378 | 3.4982 | 3.2914 | 6.1144 | 6.1144 | 6.1144 | 6.0429 | 5.9704 | 5.8963 | 5.8198 | 5.7015 | 5.6613 | 5.5331 | 5.3655 | 4.9261 | 4.7196
|  | SHIPTON OLIFFE | CT |  |  | 6.2091 | 6.1851 | 6.1343 | 6.07 | 6.0059 | 5.942 | 5.901 | 5.8513 | 5.8216 | 5.7331 | 5.5546 | 5.3616 | 5.2176 | 4.9487 | 4.9204 | 4.8606 | 4.7875 | 4.7147 | 4.6422 | 4.5968 | 4.5428 | 4.5083 | 4.4058 | 4.2045 | 3.9879 | 3.8207 | 6.1144 | 6.1144 | 6.1144 | 6.0993 | 6.0841 | 6.0685 | 6.0243 | 5.9704 | 5.936 | 5.8338 | 5.6329 | 5.4169 | 5.2501
|  | SHIPTON OLIFFE | LW |  |  | 6.2226 | 6.206 | 6.171 | 6.1371 | 6.1034 | 6.0783 | 6.0535 | 6.0289 | 6.0023 | 5.9239 | 5.7954 | 5.663 | 5.5328 | 4.9646 | 4.9451 | 4.9039 | 4.8639 | 4.8242 | 4.7947 | 4.7654 | 4.7364 | 4.7051 | 4.6128 | 4.4614 | 4.3054 | 4.152 | 6.1144 | 6.1144 | 6.1144 | 6.1144 | 6.1144 | 6.1144 | 6.1144 | 6.1144 | 6.1144 | 6.0405 | 5.8895 | 5.734 | 5.5811
|  | SHIPTON OLIFFE | ST |  |  | 6.2272 | 6.2149 | 6.1938 | 6.0966 | 5.9929 | 5.9029 | 5.8106 | 5.6754 | 5.6171 | 5.4361 | 5.2476 | 4.8231 | 4.6314 | 4.97 | 4.9555 | 4.9307 | 4.8289 | 4.7196 | 4.6268 | 4.5317 | 4.3935 | 4.332 | 4.1416 | 3.9378 | 3.4982 | 3.2914 | 6.1144 | 6.1144 | 6.1144 | 6.0429 | 5.9704 | 5.8963 | 5.8198 | 5.7015 | 5.6613 | 5.5331 | 5.3655 | 4.9261 | 4.7196
|  | SHIPTON OLIFFE | FS |  |  | 6.2485 | 6.2472 | 6.246 | 6.2384 | 6.2296 | 6.222 | 6.2144 | 6.2041 | 6.188 | 6.139 | 6.0931 | 6.0195 | 5.9546 | 4.9951 | 4.9936 | 4.9922 | 4.9836 | 4.9736 | 4.965 | 4.9565 | 4.9449 | 4.9276 | 4.8749 | 4.8232 | 4.7442 | 4.6741 | 6.1144 | 6.1144 | 6.1144 | 6.1123 | 6.1102 | 6.1082 | 6.1061 | 6.1029 | 6.0939 | 6.0653 | 6.0517 | 6.0089 | 5.9731
NURSLING GSP | SOUTHAMPTON (2 X 90) | SHIRLEY | MINIMUM HEADROOM | SU 39988 13808 | YES | 45.5247 | 45.4986 | 45.4456 | 45.3656 | 45.2841 | 45.2025 | 45.1196 | 45.0203 | 44.959 | 44.7636 | 44.2428 | 42.8498 | 41.4862 | 41.5154 | 41.5071 | 41.4904 | 41.4457 | 41.3999 | 41.3533 | 41.3054 | 41.2411 | 41.2172 | 41.1398 | 40.0683 | 38.1634 | 36.3345 | 43.8994 | 43.876 | 43.8285 | 43.7538 | 43.6776 | 43.6012 | 43.5236 | 43.4295 | 43.3738 | 43.1961 | 41.7473 | 39.9013 | 38.1315
|  | SHIRLEY | CT |  |  | 45.5247 | 45.4986 | 45.4456 | 45.3936 | 45.3413 | 45.2892 | 45.238 | 45.1867 | 45.1321 | 44.9595 | 44.4701 | 43.1632 | 41.8044 | 41.5154 | 41.5071 | 41.4904 | 41.4739 | 41.4574 | 41.4409 | 41.4247 | 41.4085 | 41.3912 | 41.3367 | 40.294 | 38.4752 | 36.6516 | 43.8994 | 43.876 | 43.8285 | 43.7818 | 43.7348 | 43.6881 | 43.6421 | 43.5961 | 43.547 | 43.3922 | 41.9731 | 40.2133 | 38.4488
|  | SHIRLEY | LW |  |  | 45.5248 | 45.4988 | 45.4459 | 45.3656 | 45.2841 | 45.2025 | 45.1196 | 45.0203 | 44.959 | 44.7636 | 44.2428 | 42.8498 | 41.4862 | 41.5154 | 41.5072 | 41.4905 | 41.4457 | 41.3999 | 41.3533 | 41.3054 | 41.2411 | 41.2172 | 41.1398 | 40.0683 | 38.1634 | 36.3345 | 43.8995 | 43.8762 | 43.8287 | 43.7538 | 43.6776 | 43.6012 | 43.5236 | 43.4295 | 43.3738 | 43.1961 | 41.7473 | 39.9013 | 38.1315
|  | SHIRLEY | ST |  |  | 45.5438 | 45.5303 | 45.5081 | 45.4808 | 45.4478 | 45.4109 | 45.374 | 45.339 | 45.3017 | 45.1841 | 44.9199 | 44.5934 | 43.7567 | 41.5214 | 41.5172 | 41.5101 | 41.5015 | 41.4911 | 41.4794 | 41.4677 | 41.4567 | 41.4449 | 41.4077 | 41.3241 | 40.4656 | 39.3012 | 43.9166 | 43.9045 | 43.8845 | 43.86 | 43.8305 | 43.7973 | 43.7642 | 43.7328 | 43.6993 | 43.5937 | 43.2944 | 42.1392 | 41.0125
|  | SHIRLEY | FS |  |  | 45.5635 | 45.5608 | 45.5581 | 45.5495 | 45.5394 | 45.5264 | 45.5135 | 45.4971 | 45.4826 | 45.4369 | 45.3304 | 45.1979 | 45.0601 | 41.5277 | 41.5268 | 41.5259 | 41.5232 | 41.52 | 41.5159 | 41.5118 | 41.5067 | 41.5021 | 41.4876 | 41.4539 | 41.4121 | 41.3685 | 43.9343 | 43.9319 | 43.9294 | 43.9217 | 43.9127 | 43.901 | 43.8894 | 43.8747 | 43.8617 | 43.8206 | 43.725 | 43.6062 | 43.4824
MINETY GSP | STRATTON (2 X 60) | SHRIVENHAM | MINIMUM HEADROOM | SU 23782 87902 | YES | 21.9306 | 21.9306 | 21.9306 | 21.9106 | 21.89 | 21.8684 | 21.846 | 21.812 | 21.8073 | 21.7869 | 21.7531 | 21.6964 | 21.396 | 20.5946 | 20.5906 | 20.5833 | 20.5605 | 20.5347 | 20.5092 | 20.4829 | 20.445 | 20.4362 | 20.4037 | 20.0235 | 19.6085 | 19.2542 | 21.6328 | 21.6285 | 21.6206 | 21.5977 | 21.5716 | 21.5458 | 21.5191 | 21.4809 | 21.4719 | 21.4386 | 21.2936 | 20.8794 | 20.5256
|  | SHRIVENHAM | CT |  |  | 21.9306 | 21.9306 | 21.9306 | 21.9166 | 21.9023 | 21.8878 | 21.8726 | 21.8492 | 21.8462 | 21.8336 | 21.7676 | 21.6995 | 21.396 | 20.5946 | 20.5906 | 20.5833 | 20.5633 | 20.543 | 20.5225 | 20.5033 | 20.476 | 20.4689 | 20.4424 | 20.0235 | 19.6085 | 19.2542 | 21.6328 | 21.6285 | 21.6206 | 21.6003 | 21.5795 | 21.5586 | 21.5391 | 21.5115 | 21.5042 | 21.4787 | 21.2936 | 20.8794 | 20.5256
|  | SHRIVENHAM | LW |  |  | 21.9306 | 21.9306 | 21.9306 | 21.9106 | 21.89 | 21.8684 | 21.846 | 21.812 | 21.8073 | 21.7869 | 21.7531 | 21.6964 | 21.4977 | 20.5954 | 20.5919 | 20.5855 | 20.5605 | 20.5347 | 20.5092 | 20.4829 | 20.445 | 20.4362 | 20.4037 | 20.1185 | 19.7146 | 19.3723 | 21.6337 | 21.6299 | 21.623 | 21.5977 | 21.5716 | 21.5458 | 21.5191 | 21.4809 | 21.4719 | 21.4386 | 21.3836 | 20.9852 | 20.6436
|  | SHRIVENHAM | ST |  |  | 21.9306 | 21.9306 | 21.9306 | 21.9196 | 21.9084 | 21.897 | 21.8852 | 21.8669 | 21.8607 | 21.8376 | 21.8177 | 21.7607 | 21.7442 | 20.5983 | 20.5966 | 20.5941 | 20.581 | 20.5673 | 20.5532 | 20.5387 | 20.5177 | 20.5088 | 20.4776 | 20.4444 | 20.3748 | 20.1932 | 21.6368 | 21.6349 | 21.6322 | 21.619 | 21.6051 | 21.5908 | 21.5762 | 21.555 | 21.5458 | 21.5141 | 21.48 | 21.4095 | 21.3797
|  | SHRIVENHAM | FS |  |  | 21.9306 | 21.9306 | 21.9306 | 21.9292 | 21.9277 | 21.9263 | 21.9248 | 21.9225 | 21.9161 | 21.8958 | 21.886 | 21.848 | 21.8162 | 20.6002 | 20.5995 | 20.5988 | 20.5967 | 20.5944 | 20.592 | 20.5895 | 20.586 | 20.5786 | 20.5552 | 20.5403 | 20.4977 | 20.4616 | 21.6388 | 21.6381 | 21.6373 | 21.6351 | 21.6328 | 21.6303 | 21.6278 | 21.6242 | 21.6166 | 21.593 | 21.5778 | 21.5349 | 21.4985
MANNINGTON GSP | SHAFTESBURY BSP | SHROTON | MINIMUM HEADROOM | ST 85356 13659 | YES | 32.4586 | 32.4333 | 32.3732 | 32.3095 | 32.2408 | 32.1035 | 31.9602 | 31.8009 | 31.6686 | 31.2705 | 30.6027 | 29.8496 | 29.2436 | 29.1895 | 29.1603 | 29.0909 | 29.0179 | 28.9399 | 28.7833 | 28.6206 | 28.442 | 28.2903 | 27.8355 | 27.0761 | 26.2292 | 25.5313 | 30.7119 | 30.6898 | 30.6375 | 30.5816 | 30.5208 | 30.3998 | 30.2729 | 30.1297 | 30.0139 | 29.6636 | 29.0729 | 28.3989 | 27.8705
|  | SHROTON | CT |  |  | 32.4626 | 32.4396 | 32.3842 | 32.3277 | 32.2693 | 32.2095 | 32.0789 | 31.9436 | 31.8153 | 31.4379 | 30.7615 | 30.0611 | 29.437 | 29.1941 | 29.1675 | 29.1036 | 29.0386 | 28.9714 | 28.903 | 28.7529 | 28.5984 | 28.4506 | 28.0165 | 27.2486 | 26.4544 | 25.7383 | 30.7154 | 30.6953 | 30.6471 | 30.5978 | 30.5467 | 30.4943 | 30.38 | 30.261 | 30.1491 | 29.8194 | 29.2203 | 28.599 | 28.0523
|  | SHROTON | LW |  |  | 32.4586 | 32.4333 | 32.3732 | 32.3095 | 32.2408 | 32.1035 | 31.9602 | 31.8009 | 31.6686 | 31.2705 | 30.6027 | 29.8496 | 29.2436 | 29.1895 | 29.1603 | 29.0909 | 29.0179 | 28.9399 | 28.7833 | 28.6206 | 28.442 | 28.2903 | 27.8355 | 27.0761 | 26.2292 | 25.5313 | 30.7119 | 30.6898 | 30.6375 | 30.5816 | 30.5208 | 30.3998 | 30.2729 | 30.1297 | 30.0139 | 29.6636 | 29.0729 | 28.3989 | 27.8705
|  | SHROTON | ST |  |  | 32.5538 | 32.4509 | 32.4165 | 32.3557 | 32.2853 | 32.2033 | 32.1186 | 31.9959 | 31.8957 | 31.5948 | 31.1457 | 30.5659 | 30.1168 | 29.2993 | 29.1805 | 29.1408 | 29.0735 | 28.9954 | 28.9039 | 28.8097 | 28.6738 | 28.5604 | 28.2212 | 27.7112 | 27.071 | 26.5621 | 30.7946 | 30.7051 | 30.6752 | 30.6199 | 30.5561 | 30.482 | 30.4054 | 30.2937 | 30.2047 | 29.9361 | 29.5383 | 29.0095 | 28.6107
|  | SHROTON | FS |  |  | 32.5836 | 32.5817 | 32.5772 | 32.5653 | 32.5515 | 32.5314 | 32.5111 | 32.4855 | 32.4475 | 32.3338 | 32.1734 | 31.9878 | 31.8146 | 29.3337 | 29.3315 | 29.3264 | 29.3128 | 29.297 | 29.2739 | 29.2506 | 29.2212 | 29.178 | 29.0496 | 28.8661 | 28.6587 | 28.465 | 30.8206 | 30.8189 | 30.8151 | 30.8046 | 30.7925 | 30.7749 | 30.7571 | 30.7346 | 30.7009 | 30.5998 | 30.4588 | 30.2916 | 30.1356
LALEHAM | STAINES | SIDNEY ROAD | MINIMUM HEADROOM | TQ 04100 71760 | YES | 40.4061 | 40.4061 | 40.4061 | 40.3526 | 40.2974 | 40.2397 | 40.1362 | 39.8606 | 39.6454 | 38.6227 | 37.6375 | 36.6387 | 35.7692 | 40.4372 | 40.433 | 40.4247 | 40.3631 | 40.2983 | 40.231 | 40.1624 | 40.0594 | 40.0333 | 39.1773 | 38.1084 | 36.975 | 35.9729 | 41.6693 | 41.6693 | 41.6693 | 41.6158 | 41.5606 | 41.5029 | 41.4432 | 41.3524 | 41.3398 | 41.2967 | 40.6529 | 39.5392 | 38.5566
|  | SIDNEY ROAD | CT |  |  | 40.4061 | 40.4061 | 40.4061 | 40.4061 | 40.4061 | 40.4061 | 40.3723 | 40.1874 | 39.9848 | 39.0052 | 38.0846 | 37.2111 | 36.3515 | 40.4372 | 40.433 | 40.4247 | 40.416 | 40.4063 | 40.398 | 40.3892 | 40.3769 | 40.3635 | 39.5604 | 38.5571 | 37.549 | 36.5568 | 41.6693 | 41.6693 | 41.6693 | 41.6693 | 41.6693 | 41.6693 | 41.6693 | 41.6693 | 41.6693 | 41.6693 | 41.1013 | 40.113 | 39.1403
|  | SIDNEY ROAD | LW |  |  | 40.4061 | 40.4061 | 40.4061 | 40.3526 | 40.2974 | 40.2397 | 40.1362 | 39.8606 | 39.6454 | 38.6227 | 37.6375 | 36.6387 | 35.7692 | 40.4373 | 40.4332 | 40.4251 | 40.3631 | 40.2983 | 40.231 | 40.1624 | 40.0594 | 40.0333 | 39.1773 | 38.1084 | 36.975 | 35.9729 | 41.6693 | 41.6693 | 41.6693 | 41.6158 | 41.5606 | 41.5029 | 41.4432 | 41.3524 | 41.3398 | 41.2967 | 40.6529 | 39.5392 | 38.5566
|  | SIDNEY ROAD | ST |  |  | 40.4061 | 40.4061 | 40.4061 | 40.4061 | 40.4061 | 40.4061 | 40.4061 | 40.4061 | 40.3278 | 39.6357 | 39.0026 | 38.4347 | 37.8821 | 40.4538 | 40.4374 | 40.4326 | 40.4266 | 40.4191 | 40.4111 | 40.4038 | 40.3955 | 40.3862 | 40.2323 | 39.5577 | 38.9528 | 38.3233 | 41.6693 | 41.6693 | 41.6693 | 41.6693 | 41.6693 | 41.6693 | 41.6693 | 41.6693 | 41.6693 | 41.6693 | 41.6693 | 41.4975 | 40.8721
|  | SIDNEY ROAD | FS |  |  | 40.4061 | 40.4061 | 40.4061 | 40.4061 | 40.4061 | 40.4061 | 40.4061 | 40.4061 | 40.4061 | 40.4061 | 40.3995 | 40.1639 | 39.9288 | 40.4587 | 40.4445 | 40.4435 | 40.4416 | 40.4392 | 40.4363 | 40.4337 | 40.4296 | 40.426 | 40.4078 | 40.391 | 40.3754 | 40.3597 | 41.6693 | 41.6693 | 41.6693 | 41.6693 | 41.6693 | 41.6693 | 41.6693 | 41.6693 | 41.6693 | 41.6693 | 41.6693 | 41.6693 | 41.6693
NURSLING GSP | ROWNHAMS | SILKSTEAD | MINIMUM HEADROOM | SU 44578 24565 | YES | 15.6109 | 15.6109 | 15.6109 | 15.2972 | 14.9703 | 14.6255 | 14.2646 | 13.7099 | 13.6321 | 13.2878 | 12.485 | 11.3115 | 10.897 | 13.7917 | 13.6631 | 13.391 | 12.8106 | 12.2135 | 11.7857 | 11.3426 | 10.7065 | 10.541 | 10.007 | 9.1307 | 7.8812 | 7.3918 | 14.5301 | 14.4071 | 14.147 | 13.5809 | 13.0036 | 12.5818 | 12.1447 | 11.5145 | 11.3555 | 10.8403 | 9.9955 | 8.7786 | 8.3213
|  | SILKSTEAD | CT |  |  | 15.6109 | 15.6109 | 15.6109 | 15.4951 | 15.3765 | 15.2551 | 15.1273 | 14.9278 | 14.9021 | 14.728 | 13.9448 | 13.129 | 12.6549 | 13.8174 | 13.703 | 13.4611 | 13.1105 | 12.7518 | 12.3928 | 12.1828 | 11.9018 | 11.7884 | 11.4433 | 10.5866 | 9.6949 | 9.1459 | 14.5546 | 14.4452 | 14.2139 | 13.8736 | 13.5322 | 13.1905 | 12.9865 | 12.7115 | 12.6045 | 12.2783 | 11.4531 | 10.5939 | 10.077
|  | SILKSTEAD | LW |  |  | 15.6109 | 15.6109 | 15.6109 | 15.2972 | 14.9703 | 14.6255 | 14.2646 | 13.7099 | 13.6321 | 13.2878 | 12.485 | 11.3115 | 10.897 | 13.7917 | 13.6631 | 13.391 | 12.8106 | 12.2135 | 11.7857 | 11.3426 | 10.7065 | 10.541 | 10.007 | 9.1307 | 7.8812 | 7.3918 | 14.5301 | 14.4071 | 14.147 | 13.5809 | 13.0036 | 12.5818 | 12.1447 | 11.5145 | 11.3555 | 10.8403 | 9.9955 | 8.7786 | 8.3213
|  | SILKSTEAD | ST |  |  | 15.6109 | 15.6109 | 15.6109 | 15.6102 | 15.609 | 15.607 | 15.6041 | 15.5977 | 15.5946 | 15.578 | 15.5562 | 15.3619 | 15.0972 | 13.8477 | 13.7612 | 13.6129 | 13.4303 | 13.209 | 13.1351 | 13.0612 | 12.9992 | 12.9363 | 12.7445 | 12.4354 | 12.0712 | 11.7579 | 14.5836 | 14.5009 | 14.3591 | 14.1845 | 13.9731 | 13.9043 | 13.8357 | 13.7777 | 13.7191 | 13.5402 | 13.252 | 12.9087 | 12.6163
|  | SILKSTEAD | FS |  |  | 15.6109 | 15.6109 | 15.6109 | 15.6109 | 15.6108 | 15.6107 | 15.6106 | 15.6103 | 15.6093 | 15.6033 | 15.5985 | 15.5757 | 15.5535 | 13.9946 | 13.9847 | 13.9752 | 13.9312 | 13.8784 | 13.8538 | 13.8293 | 13.7979 | 13.7744 | 13.7029 | 13.5918 | 13.4668 | 13.3476 | 14.724 | 14.7145 | 14.7055 | 14.6634 | 14.6129 | 14.5894 | 14.566 | 14.536 | 14.5135 | 14.4448 | 14.3384 | 14.2179 | 14.1029
BRAMLEY (FLEE) | READING BSP | SILVER STREET | MINIMUM HEADROOM | SU 71957 72821 | YES | 33.3705 | 33.3705 | 33.3705 | 33.3614 | 33.3521 | 33.3427 | 33.3329 | 33.3177 | 33.3158 | 33.3096 | 33.2812 | 32.541 | 31.2476 | 30.5691 | 30.5114 | 30.3919 | 30.2661 | 30.1403 | 30.0152 | 29.9608 | 29.9009 | 29.8515 | 29.6911 | 29.2833 | 28.6624 | 27.1538 | 30.9318 | 30.9318 | 30.9318 | 30.9227 | 30.9135 | 30.8144 | 30.7168 | 30.591 | 30.4604 | 30.036 | 28.9682 | 27.5602 | 26.165
|  | SILVER STREET | CT |  |  | 33.3705 | 33.3705 | 33.3705 | 33.3614 | 33.3521 | 33.3427 | 33.3329 | 33.3177 | 33.3158 | 33.3096 | 33.2812 | 32.541 | 31.2476 | 30.5691 | 30.5114 | 30.3919 | 30.2661 | 30.1403 | 30.0152 | 29.9608 | 29.9009 | 29.8515 | 29.6911 | 29.2833 | 28.6624 | 27.1538 | 30.9318 | 30.9318 | 30.9318 | 30.9227 | 30.9135 | 30.8144 | 30.7168 | 30.591 | 30.4604 | 30.036 | 28.9682 | 27.5602 | 26.165
|  | SILVER STREET | LW |  |  | 33.3705 | 33.3705 | 33.3705 | 33.3705 | 33.3705 | 33.3705 | 33.3705 | 33.3705 | 33.3705 | 33.3705 | 33.3705 | 33.0145 | 31.7294 | 30.5809 | 30.5296 | 30.4238 | 30.3204 | 30.2169 | 30.1728 | 30.1283 | 30.0835 | 30.0361 | 29.8819 | 29.5026 | 29.0332 | 27.6985 | 30.9318 | 30.9318 | 30.9318 | 30.9318 | 30.9318 | 30.9318 | 30.9318 | 30.9212 | 30.8286 | 30.4492 | 29.4207 | 28.0617 | 26.6748
|  | SILVER STREET | ST |  |  | 33.3705 | 33.3705 | 33.3705 | 33.3705 | 33.3705 | 33.3705 | 33.3705 | 33.3705 | 33.3705 | 33.3705 | 33.3705 | 33.3705 | 33.3705 | 30.6243 | 30.6004 | 30.5606 | 30.5117 | 30.4527 | 30.4076 | 30.3625 | 30.332 | 30.2996 | 30.1941 | 29.9313 | 29.6218 | 29.3211 | 30.9318 | 30.9318 | 30.9318 | 30.9318 | 30.9318 | 30.9318 | 30.9318 | 30.9318 | 30.9318 | 30.9318 | 30.5832 | 29.7439 | 28.9064
|  | SILVER STREET | FS |  |  | 33.3705 | 33.3705 | 33.3705 | 33.3705 | 33.3705 | 33.3705 | 33.3705 | 33.3705 | 33.3705 | 33.3705 | 33.3705 | 33.3705 | 33.3705 | 30.6591 | 30.6543 | 30.6497 | 30.6327 | 30.6127 | 30.5942 | 30.5759 | 30.5525 | 30.5399 | 30.4989 | 30.3914 | 30.2505 | 30.1016 | 30.9318 | 30.9318 | 30.9318 | 30.9318 | 30.9318 | 30.9318 | 30.9318 | 30.9318 | 30.9318 | 30.9318 | 30.9318 | 30.9318 | 30.9318
MANNINGTON GSP | CHRISTCHURCH BSP | SOMERFORD | MINIMUM HEADROOM | SZ 18262 93590 | YES | 27.6298 | 27.6156 | 26.7476 | 26.6765 | 26.6053 | 26.5342 | 26.4631 | 26.3919 | 26.3339 | 26.045 | 25.7834 | 25.0261 | 24.7531 | 25.7662 | 25.752 | 24.884 | 24.8129 | 24.7417 | 24.6706 | 24.5995 | 24.5283 | 24.4703 | 23.7016 | 22.0395 | 20.2547 | 18.434 | 25.8396 | 25.8254 | 24.9575 | 24.8863 | 24.8152 | 24.744 | 24.6729 | 24.6018 | 24.5437 | 24.2548 | 22.7984 | 21.0563 | 19.2774
|  | SOMERFORD | CT |  |  | 27.7038 | 27.6952 | 27.1745 | 27.1318 | 27.0891 | 27.0464 | 27.0037 | 26.9611 | 26.944 | 26.8928 | 26.2701 | 26.0504 | 25.4145 | 25.8402 | 25.8316 | 25.3109 | 25.2682 | 25.2255 | 25.1828 | 25.1401 | 25.0974 | 25.0804 | 24.5884 | 22.4586 | 20.5436 | 18.7234 | 25.9136 | 25.9051 | 25.3843 | 25.3416 | 25.2989 | 25.2563 | 25.2136 | 25.1709 | 25.1538 | 25.1026 | 23.214 | 21.3379 | 19.5594
|  | SOMERFORD | LW |  |  | 27.6298 | 27.6156 | 26.7476 | 26.6765 | 26.6053 | 26.5342 | 26.4631 | 26.3919 | 26.3635 | 26.2781 | 26.1358 | 26.0504 | 25.1664 | 25.7662 | 25.752 | 24.884 | 24.8129 | 24.7417 | 24.6706 | 24.5995 | 24.5283 | 24.4999 | 23.7016 | 22.0395 | 20.2547 | 18.434 | 25.8396 | 25.8254 | 24.9575 | 24.8863 | 24.8152 | 24.744 | 24.6729 | 24.6018 | 24.5733 | 24.4837 | 22.7984 | 21.0563 | 19.2774
|  | SOMERFORD | ST |  |  | 27.7408 | 27.7351 | 27.3879 | 27.2175 | 27.0449 | 26.8692 | 26.6887 | 26.4251 | 26.3339 | 26.045 | 25.7834 | 25.0261 | 24.7531 | 25.8772 | 25.8715 | 25.5243 | 25.3539 | 25.1813 | 25.0056 | 24.8251 | 24.5615 | 24.4703 | 24.1814 | 23.0663 | 21.2545 | 19.9123 | 25.9506 | 25.9449 | 25.5977 | 25.4274 | 25.2547 | 25.0791 | 24.8986 | 24.6349 | 24.5437 | 24.2548 | 23.8436 | 22.0096 | 20.6899
|  | SOMERFORD | FS |  |  | 27.7778 | 27.7749 | 27.6013 | 27.5871 | 27.5729 | 27.5586 | 27.5444 | 27.5302 | 27.5245 | 27.5074 | 27.479 | 27.4619 | 27.4306 | 25.9142 | 25.9113 | 25.7377 | 25.7235 | 25.7093 | 25.695 | 25.6808 | 25.6666 | 25.6609 | 25.6438 | 25.6154 | 25.5983 | 25.567 | 25.9876 | 25.9848 | 25.8112 | 25.7969 | 25.7827 | 25.7685 | 25.7543 | 25.74 | 25.7343 | 25.7173 | 25.6888 | 25.6717 | 25.6404
LOVEDEAN GSP | CHICHESTER & HUNSTON | SOUTH BERSTED | MINIMUM HEADROOM | SU 94025 00705 | YES | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.1503 | 28.5485 | 28.5473 | 28.5448 | 28.5424 | 28.5399 | 28.5287 | 28.5176 | 28.5065 | 28.4946 | 28.4588 | 27.6737 | 26.264 | 24.8659 | 30.103 | 30.103 | 30.103 | 30.103 | 30.103 | 30.103 | 30.103 | 30.103 | 30.103 | 30.103 | 30.103 | 29.2826 | 27.7813
|  | SOUTH BERSTED | CT |  |  | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.3061 | 28.5485 | 28.5473 | 28.5448 | 28.5424 | 28.5399 | 28.5374 | 28.5263 | 28.5152 | 28.5033 | 28.4675 | 27.8438 | 26.4342 | 25.0371 | 30.103 | 30.103 | 30.103 | 30.103 | 30.103 | 30.103 | 30.103 | 30.103 | 30.103 | 30.103 | 30.103 | 29.4654 | 27.9652
|  | SOUTH BERSTED | LW |  |  | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.1503 | 28.5485 | 28.5473 | 28.5448 | 28.5424 | 28.5399 | 28.5287 | 28.5176 | 28.5065 | 28.4946 | 28.4588 | 27.6737 | 26.264 | 24.8659 | 30.103 | 30.103 | 30.103 | 30.103 | 30.103 | 30.103 | 30.103 | 30.103 | 30.103 | 30.103 | 30.103 | 29.2826 | 27.7813
|  | SOUTH BERSTED | ST |  |  | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 28.563 | 28.5486 | 28.5474 | 28.546 | 28.5443 | 28.5385 | 28.5328 | 28.5252 | 28.5171 | 28.4929 | 28.4485 | 27.8426 | 26.9403 | 30.103 | 30.103 | 30.103 | 30.103 | 30.103 | 30.103 | 30.103 | 30.103 | 30.103 | 30.103 | 30.103 | 30.103 | 30.0088
|  | SOUTH BERSTED | FS |  |  | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 28.564 | 28.5501 | 28.55 | 28.5495 | 28.549 | 28.5475 | 28.546 | 28.544 | 28.5409 | 28.5315 | 28.5143 | 28.4957 | 28.4774 | 30.103 | 30.103 | 30.103 | 30.103 | 30.103 | 30.103 | 30.103 | 30.103 | 30.103 | 30.103 | 30.103 | 30.103 | 30.103
MANNINGTON GSP | CHRISTCHURCH BSP | SOUTHBOURNE | MINIMUM HEADROOM | SZ 13563 92074 | YES | 29.5896 | 29.5828 | 29.5695 | 29.5238 | 29.4769 | 29.4297 | 29.381 | 29.3134 | 29.2926 | 29.2224 | 28.9121 | 27.1209 | 25.3829 | 27.0931 | 27.0879 | 27.0776 | 27.0349 | 26.9911 | 26.9466 | 26.9007 | 26.836 | 26.8181 | 26.7579 | 25.6315 | 23.5372 | 21.4932 | 28.26 | 28.2544 | 28.2434 | 28.2 | 28.1554 | 28.1102 | 28.0637 | 27.9983 | 27.9797 | 27.917 | 27.0627 | 24.9723 | 22.9322
|  | SOUTHBOURNE | CT |  |  | 29.5903 | 29.584 | 29.5715 | 29.559 | 29.5464 | 29.5338 | 29.5213 | 29.5087 | 29.4955 | 29.4514 | 29.2146 | 27.4995 | 25.7672 | 27.0937 | 27.0888 | 27.0791 | 27.0695 | 27.0597 | 27.0499 | 27.0403 | 27.0306 | 27.0203 | 26.9862 | 25.9407 | 23.9226 | 21.8842 | 28.2606 | 28.2553 | 28.245 | 28.2347 | 28.2242 | 28.2137 | 28.2034 | 28.193 | 28.182 | 28.1455 | 27.3718 | 25.3576 | 23.323
|  | SOUTHBOURNE | LW |  |  | 29.5896 | 29.5828 | 29.5695 | 29.5238 | 29.4769 | 29.4297 | 29.381 | 29.3134 | 29.2926 | 29.2224 | 28.9121 | 27.1209 | 25.3829 | 27.0931 | 27.0879 | 27.0776 | 27.0349 | 26.9911 | 26.9466 | 26.9007 | 26.836 | 26.8181 | 26.7579 | 25.6315 | 23.5372 | 21.4932 | 28.26 | 28.2544 | 28.2434 | 28.2 | 28.1554 | 28.1102 | 28.0637 | 27.9983 | 27.9797 | 27.917 | 27.0627 | 24.9723 | 22.9322
|  | SOUTHBOURNE | ST |  |  | 29.5933 | 29.5893 | 29.5827 | 29.5629 | 29.5412 | 29.5147 | 29.4878 | 29.4597 | 29.4441 | 29.3927 | 29.2944 | 28.7538 | 27.6374 | 27.096 | 27.0929 | 27.0878 | 27.0698 | 27.0504 | 27.0271 | 27.0034 | 26.9772 | 26.9636 | 26.9191 | 26.8242 | 25.4293 | 24.1187 | 28.2631 | 28.2597 | 28.2543 | 28.2359 | 28.2159 | 28.1918 | 28.1673 | 28.1407 | 28.1266 | 28.0804 | 27.9959 | 26.8611 | 25.553
|  | SOUTHBOURNE | FS |  |  | 29.599 | 29.5982 | 29.5973 | 29.5852 | 29.573 | 29.5589 | 29.5446 | 29.5237 | 29.4788 | 29.3357 | 29.2399 | 28.998 | 28.7853 | 27.1005 | 27.0998 | 27.0991 | 27.0876 | 27.076 | 27.063 | 27.0498 | 27.0302 | 26.9861 | 26.8457 | 26.7574 | 26.5256 | 26.3238 | 28.2678 | 28.2671 | 28.2664 | 28.2548 | 28.243 | 28.2297 | 28.2162 | 28.1964 | 28.1521 | 28.011 | 27.9209 | 27.6867 | 27.4822
BRAMLEY (FLEE) | BURGHFIELD RESERVE | SOUTHCOTE | MINIMUM HEADROOM | SU 68199 71325 | YES | 28.9475 | 28.9475 | 28.9475 | 28.9261 | 28.904 | 28.8809 | 28.857 | 28.8207 | 28.8157 | 28.7985 | 28.141 | 26.3153 | 24.5278 | 27.0684 | 27.0665 | 27.0633 | 27.0385 | 27.0128 | 26.9816 | 26.9493 | 26.9045 | 26.8906 | 26.4851 | 24.882 | 22.7635 | 20.6793 | 28.1445 | 28.1445 | 28.1445 | 28.1231 | 28.101 | 28.078 | 28.0541 | 28.0178 | 28.0127 | 27.9955 | 26.6782 | 24.5353 | 22.4265
|  | SOUTHCOTE | CT |  |  | 28.9475 | 28.9475 | 28.9475 | 28.9276 | 28.9074 | 28.8868 | 28.8653 | 28.8322 | 28.828 | 28.8146 | 28.2214 | 26.3804 | 24.5786 | 27.0687 | 27.067 | 27.0642 | 27.0413 | 27.0178 | 26.9939 | 26.9641 | 26.9225 | 26.9094 | 26.6156 | 24.9787 | 22.8449 | 20.7465 | 28.1445 | 28.1445 | 28.1445 | 28.1246 | 28.1044 | 28.0838 | 28.0624 | 28.0293 | 28.0251 | 28.0116 | 26.7762 | 24.618 | 22.495
|  | SOUTHCOTE | LW |  |  | 28.9475 | 28.9475 | 28.9475 | 28.9261 | 28.904 | 28.8809 | 28.857 | 28.8207 | 28.8157 | 28.7985 | 28.141 | 26.3153 | 24.5278 | 27.0684 | 27.0665 | 27.0633 | 27.0385 | 27.0128 | 26.9816 | 26.9493 | 26.9045 | 26.8906 | 26.4851 | 24.882 | 22.7635 | 20.6793 | 28.1445 | 28.1445 | 28.1445 | 28.1231 | 28.101 | 28.078 | 28.0541 | 28.0178 | 28.0127 | 27.9955 | 26.6782 | 24.5353 | 22.4265
|  | SOUTHCOTE | ST |  |  | 28.9475 | 28.9475 | 28.9475 | 28.9475 | 28.9475 | 28.9475 | 28.9475 | 28.9475 | 28.9475 | 28.9475 | 28.9475 | 27.9265 | 26.7986 | 27.0732 | 27.0674 | 27.0654 | 27.0629 | 27.0599 | 27.0548 | 27.0495 | 27.0438 | 27.0377 | 27.0165 | 25.9643 | 24.6023 | 23.2868 | 28.1445 | 28.1445 | 28.1445 | 28.1445 | 28.1445 | 28.1445 | 28.1445 | 28.1445 | 28.1445 | 28.1445 | 27.7598 | 26.393 | 25.0619
|  | SOUTHCOTE | FS |  |  | 28.9475 | 28.9475 | 28.9475 | 28.9475 | 28.9475 | 28.9475 | 28.9475 | 28.9475 | 28.9475 | 28.9475 | 28.9475 | 28.9475 | 28.9475 | 27.0747 | 27.0699 | 27.0694 | 27.0686 | 27.0676 | 27.0659 | 27.0641 | 27.0619 | 27.0595 | 27.0512 | 27.0248 | 26.5643 | 25.8617 | 28.1445 | 28.1445 | 28.1445 | 28.1445 | 28.1445 | 28.1445 | 28.1445 | 28.1445 | 28.1445 | 28.1445 | 28.1445 | 28.1445 | 27.6587
NURSLING GSP |  | SOUTHFIELD ROAD | MINIMUM HEADROOM | TQ 20533 79746 |  | 46.5941 | 46.5941 | 65.4941 | 65.4917 | 65.4894 | 65.4871 | 65.4847 | 65.481 | 65.4706 | 65.4378 | 65.4221 | 65.3729 | 65.3317 | 45.6883 | 45.6858 | 64.5809 | 64.576 | 64.5711 | 64.5664 | 64.565 | 64.5636 | 64.5621 | 64.5293 | 64.5074 | 64.4488 | 64.3973 | 46.0091 | 46.0067 | 64.9017 | 64.8969 | 64.8919 | 64.8872 | 64.8858 | 64.8843 | 64.8828 | 64.8501 | 64.8282 | 64.7696 | 64.7181
|  | SOUTHFIELD ROAD | CT |  |  | 46.5941 | 46.5941 | 65.4941 | 65.4941 | 65.4941 | 65.4941 | 65.4941 | 65.4941 | 65.4941 | 65.4941 | 65.4941 | 65.4941 | 65.4941 | 45.6883 | 45.6859 | 64.581 | 64.5762 | 64.5713 | 64.5664 | 64.565 | 64.5636 | 64.5621 | 64.5564 | 64.5357 | 64.5075 | 64.4788 | 46.0091 | 46.0067 | 64.9018 | 64.897 | 64.8921 | 64.8872 | 64.8858 | 64.8843 | 64.8828 | 64.8771 | 64.8564 | 64.8281 | 64.7993
|  | SOUTHFIELD ROAD | LW |  |  | 46.5941 | 46.5941 | 65.4941 | 65.4941 | 65.4941 | 65.4941 | 65.4941 | 65.4941 | 65.4941 | 65.4941 | 65.4941 | 65.4941 | 65.4941 | 45.6883 | 45.6858 | 64.5809 | 64.576 | 64.5711 | 64.5698 | 64.5683 | 64.5669 | 64.5654 | 64.5597 | 64.539 | 64.5109 | 64.4821 | 46.0091 | 46.0067 | 64.9017 | 64.8969 | 64.8919 | 64.8906 | 64.8891 | 64.8877 | 64.8862 | 64.8804 | 64.8597 | 64.8315 | 64.8026
|  | SOUTHFIELD ROAD | ST |  |  | 46.5941 | 46.5941 | 65.4941 | 65.4941 | 65.4941 | 65.4941 | 65.4941 | 65.4941 | 65.4941 | 65.4941 | 65.4941 | 65.4941 | 65.4941 | 45.6893 | 45.6877 | 64.585 | 64.5818 | 64.5778 | 64.5763 | 64.5748 | 64.5738 | 64.5727 | 64.5688 | 64.5541 | 64.5353 | 64.5173 | 46.0102 | 46.0086 | 64.9059 | 64.9026 | 64.8986 | 64.8971 | 64.8956 | 64.8946 | 64.8936 | 64.8895 | 64.8749 | 64.856 | 64.8379
|  | SOUTHFIELD ROAD | FS |  |  | 46.5941 | 46.5941 | 65.4941 | 65.4917 | 65.4894 | 65.4871 | 65.4847 | 65.481 | 65.4706 | 65.4378 | 65.4221 | 65.3729 | 65.3317 | 45.6919 | 45.6916 | 64.5913 | 64.5881 | 64.5847 | 64.5818 | 64.5789 | 64.5744 | 64.5637 | 64.5293 | 64.5074 | 64.4488 | 64.3973 | 46.0127 | 46.0125 | 64.9122 | 64.909 | 64.9056 | 64.9027 | 64.8997 | 64.8953 | 64.8845 | 64.8501 | 64.8282 | 64.7696 | 64.7181
AXMINSTER | YEOVIL BSP | SPARKFORD | MINIMUM HEADROOM | ST 60767 25496 | YES | 7.6607 | 7.6318 | 7.6128 | 7.5895 | 7.5614 | 7.5498 | 7.5152 | 7.4522 | 7.4202 | 7.3247 | 7.1214 | 6.9054 | 6.7224 | 6.6293 | 6.5894 | 6.5632 | 6.531 | 6.4921 | 6.4761 | 6.4602 | 6.3915 | 6.3492 | 6.2232 | 5.9694 | 5.7032 | 5.4968 | 6.7466 | 6.7054 | 6.6783 | 6.6451 | 6.6051 | 6.5885 | 6.5721 | 6.5055 | 6.4619 | 6.3324 | 6.0729 | 5.8007 | 5.5885
|  | SPARKFORD | CT |  |  | 7.6607 | 7.6579 | 7.6519 | 7.6234 | 7.5944 | 7.5651 | 7.5152 | 7.4522 | 7.4202 | 7.3247 | 7.1214 | 6.9054 | 6.7224 | 6.6293 | 6.6254 | 6.6172 | 6.5864 | 6.5553 | 6.5238 | 6.4642 | 6.3915 | 6.3492 | 6.2232 | 5.9694 | 5.7032 | 5.4968 | 6.7466 | 6.7426 | 6.7341 | 6.703 | 6.6716 | 6.6399 | 6.5792 | 6.5055 | 6.4619 | 6.3324 | 6.0729 | 5.8007 | 5.5885
|  | SPARKFORD | LW |  |  | 7.6607 | 7.6579 | 7.6519 | 7.6461 | 7.6403 | 7.6147 | 7.5893 | 7.5641 | 7.537 | 7.4569 | 7.3248 | 7.1824 | 7.0202 | 6.6293 | 6.6254 | 6.6172 | 6.6092 | 6.6012 | 6.5658 | 6.5307 | 6.4959 | 6.4584 | 6.3477 | 6.1653 | 5.9767 | 5.7912 | 6.7466 | 6.7426 | 6.7341 | 6.7258 | 6.7176 | 6.681 | 6.6448 | 6.609 | 6.5703 | 6.4561 | 6.2679 | 6.0733 | 5.8819
|  | SPARKFORD | ST |  |  | 7.6844 | 7.6318 | 7.6128 | 7.5895 | 7.5614 | 7.5498 | 7.5382 | 7.521 | 7.5025 | 7.4485 | 7.3607 | 7.2727 | 7.179 | 6.6621 | 6.5894 | 6.5632 | 6.531 | 6.4921 | 6.4761 | 6.4602 | 6.4364 | 6.4108 | 6.3362 | 6.2149 | 6.0934 | 5.9727 | 6.7804 | 6.7054 | 6.6783 | 6.6451 | 6.6051 | 6.5885 | 6.5721 | 6.5476 | 6.5212 | 6.4442 | 6.3191 | 6.1937 | 6.0692
|  | SPARKFORD | FS |  |  | 7.7066 | 7.7064 | 7.7062 | 7.7053 | 7.7042 | 7.7 | 7.6959 | 7.6904 | 7.6832 | 7.6624 | 7.6291 | 7.5972 | 7.5671 | 6.6928 | 6.6925 | 6.6922 | 6.691 | 6.6895 | 6.6837 | 6.678 | 6.6704 | 6.6605 | 6.6317 | 6.5857 | 6.5416 | 6.5 | 6.812 | 6.8117 | 6.8115 | 6.8102 | 6.8086 | 6.8026 | 6.7967 | 6.7889 | 6.7787 | 6.749 | 6.7016 | 6.6561 | 6.6132
MELKSHAM GSP | NORRINGTON | SPRING QUARRY WEST | MINIMUM HEADROOM | ST 84368 68717 | YES | 41.7363 | 41.7135 | 41.6653 | 41.5452 | 41.4238 | 41.3012 | 41.1645 | 40.9834 | 40.9069 | 40.6176 | 40.0426 | 39.3841 | 38.9511 | 37.819 | 37.7897 | 37.7277 | 37.5941 | 37.4594 | 37.3237 | 37.1708 | 36.9737 | 36.8802 | 36.5881 | 35.912 | 35.1926 | 34.6998 | 39.9423 | 39.9122 | 39.8486 | 39.7134 | 39.5772 | 39.4399 | 39.285 | 39.0861 | 38.9905 | 38.7027 | 38.0444 | 37.3436 | 36.869
|  | SPRING QUARRY WEST | CT |  |  | 41.7363 | 41.7135 | 41.6653 | 41.5452 | 41.4238 | 41.3012 | 41.1645 | 40.9834 | 40.9072 | 40.66 | 40.0426 | 39.3841 | 38.9511 | 37.819 | 37.7897 | 37.7277 | 37.5941 | 37.4594 | 37.3237 | 37.1708 | 36.9737 | 36.8802 | 36.5881 | 35.912 | 35.1926 | 34.6998 | 39.9423 | 39.9122 | 39.8486 | 39.7134 | 39.5772 | 39.4399 | 39.285 | 39.0861 | 38.9905 | 38.7027 | 38.0444 | 37.3436 | 36.869
|  | SPRING QUARRY WEST | LW |  |  | 41.7414 | 41.7215 | 41.6794 | 41.6209 | 41.5607 | 41.4819 | 41.4012 | 41.3052 | 41.2391 | 41.0235 | 40.6288 | 40.1771 | 39.8156 | 37.8256 | 37.8 | 37.7458 | 37.6755 | 37.6037 | 37.5086 | 37.4118 | 37.2998 | 37.2164 | 36.9545 | 36.5011 | 35.9886 | 35.5672 | 39.9491 | 39.9227 | 39.8671 | 39.7955 | 39.7223 | 39.6253 | 39.5265 | 39.4127 | 39.3272 | 39.0682 | 38.6326 | 38.1387 | 37.7355
|  | SPRING QUARRY WEST | ST |  |  | 41.7483 | 41.7341 | 41.7099 | 41.5897 | 41.4618 | 41.3276 | 41.1905 | 41.0001 | 40.9069 | 40.6176 | 40.2643 | 39.6207 | 39.2672 | 37.8345 | 37.8162 | 37.785 | 37.6563 | 37.5181 | 37.3726 | 37.2241 | 37.0228 | 36.9178 | 36.5941 | 36.1911 | 35.5084 | 35.116 | 39.9582 | 39.9394 | 39.9074 | 39.7777 | 39.6382 | 39.4914 | 39.3416 | 39.139 | 39.0326 | 38.7049 | 38.3061 | 37.6353 | 37.2547
|  | SPRING QUARRY WEST | FS |  |  | 41.7725 | 41.771 | 41.7695 | 41.7628 | 41.7548 | 41.7413 | 41.728 | 41.7109 | 41.6945 | 41.6456 | 41.5691 | 41.4869 | 41.4088 | 37.8656 | 37.8637 | 37.8618 | 37.8532 | 37.8428 | 37.8255 | 37.8084 | 37.7864 | 37.7655 | 37.7033 | 37.6054 | 37.5026 | 37.4052 | 39.9902 | 39.9881 | 39.9862 | 39.9773 | 39.9668 | 39.9489 | 39.9314 | 39.9088 | 39.8874 | 39.8236 | 39.7232 | 39.618 | 39.5182
NORTH HYDE GSP | NORTH HYDE 22kV | SPRINGFIELD ROAD | MINIMUM HEADROOM | TQ 11409 80620 | YES | 35.4126 | 35.4126 | 35.4126 | 35.4054 | 35.3982 | 35.3908 | 35.3831 | 35.3713 | 35.3673 | 35.3254 | 35.1776 | 33.5841 | 31.7709 | 33.2625 | 33.26 | 33.2535 | 33.24 | 33.2259 | 33.2114 | 33.1784 | 33.1413 | 33.1121 | 33.0161 | 31.9596 | 29.6997 | 27.4207 | 34.7801 | 34.7781 | 34.7748 | 34.7649 | 34.7546 | 34.7441 | 34.7243 | 34.7005 | 34.6854 | 34.6356 | 33.2823 | 31.0439 | 28.7864
|  | SPRINGFIELD ROAD | CT |  |  | 35.4126 | 35.4126 | 35.4126 | 35.4062 | 35.3997 | 35.3931 | 35.3863 | 35.3757 | 35.3743 | 35.3254 | 35.1776 | 33.6055 | 31.7865 | 33.2625 | 33.26 | 33.2535 | 33.24 | 33.2259 | 33.2114 | 33.1784 | 33.1413 | 33.1121 | 33.0161 | 32.0351 | 29.7496 | 27.4649 | 34.7801 | 34.7781 | 34.7748 | 34.7649 | 34.7546 | 34.7441 | 34.7243 | 34.7005 | 34.6854 | 34.6356 | 33.3565 | 31.0924 | 28.8293
|  | SPRINGFIELD ROAD | LW |  |  | 35.4126 | 35.4126 | 35.4126 | 35.4126 | 35.4126 | 35.4126 | 35.4126 | 35.4126 | 35.4079 | 35.3582 | 35.2316 | 33.5841 | 31.7709 | 33.2625 | 33.26 | 33.2535 | 33.2464 | 33.2387 | 33.2128 | 33.1866 | 33.1602 | 33.1323 | 33.0406 | 31.9596 | 29.6997 | 27.4207 | 34.7801 | 34.7781 | 34.7748 | 34.7713 | 34.7675 | 34.7546 | 34.7416 | 34.7285 | 34.7147 | 34.6692 | 33.2823 | 31.0439 | 28.7864
|  | SPRINGFIELD ROAD | ST |  |  | 35.4126 | 35.4126 | 35.4126 | 35.4054 | 35.3982 | 35.3908 | 35.3831 | 35.3713 | 35.3673 | 35.3522 | 35.2539 | 35.1153 | 33.9596 | 33.2636 | 33.2621 | 33.2599 | 33.2487 | 33.2362 | 33.222 | 33.2073 | 33.1775 | 33.1544 | 33.0787 | 32.906 | 31.6584 | 30.2007 | 34.7811 | 34.7798 | 34.7781 | 34.7688 | 34.759 | 34.7482 | 34.737 | 34.7163 | 34.7028 | 34.6588 | 34.4947 | 32.9831 | 31.5391
|  | SPRINGFIELD ROAD | FS |  |  | 35.4126 | 35.4126 | 35.4126 | 35.4126 | 35.4126 | 35.4126 | 35.4126 | 35.4126 | 35.4126 | 35.4126 | 35.4126 | 35.3729 | 35.3216 | 33.2651 | 33.2644 | 33.2638 | 33.2627 | 33.2616 | 33.2602 | 33.2582 | 33.2555 | 33.2481 | 33.2235 | 33.1567 | 33.0676 | 32.9731 | 34.7822 | 34.7817 | 34.7812 | 34.7804 | 34.7794 | 34.7783 | 34.7771 | 34.7758 | 34.7721 | 34.7599 | 34.7268 | 34.6826 | 34.5528
NURSLING GSP | WINCHESTER | ST CROSS | MINIMUM HEADROOM | SU 47287 28156 | YES | 25.6192 | 25.6192 | 25.6192 | 25.6181 | 25.6158 | 25.6121 | 25.6071 | 25.5969 | 25.5952 | 25.5863 | 25.5645 | 25.5221 | 24.8427 | 23.2837 | 23.2733 | 23.2512 | 23.2287 | 23.205 | 23.1876 | 23.1778 | 23.1608 | 23.15 | 22.8106 | 21.7937 | 20.717 | 19.6753 | 24.3158 | 24.3025 | 24.2744 | 24.2459 | 24.2164 | 24.093 | 23.9071 | 23.722 | 23.5251 | 22.9406 | 21.944 | 20.9088 | 19.9078
|  | ST CROSS | CT |  |  | 25.6192 | 25.6192 | 25.6192 | 25.6189 | 25.6183 | 25.6173 | 25.6159 | 25.6129 | 25.6123 | 25.6094 | 25.5852 | 25.5582 | 24.8427 | 23.284 | 23.2738 | 23.2522 | 23.2308 | 23.2092 | 23.1876 | 23.1778 | 23.1663 | 23.1568 | 22.8106 | 21.7937 | 20.717 | 19.6753 | 24.3162 | 24.3032 | 24.2756 | 24.2484 | 24.2211 | 24.093 | 23.9071 | 23.722 | 23.5251 | 22.9406 | 21.944 | 20.9088 | 19.9078
|  | ST CROSS | LW |  |  | 25.6192 | 25.6192 | 25.6192 | 25.6181 | 25.6158 | 25.6121 | 25.6071 | 25.5969 | 25.5952 | 25.5863 | 25.5645 | 25.5221 | 25.0094 | 23.2837 | 23.2733 | 23.2512 | 23.2287 | 23.205 | 23.1928 | 23.1793 | 23.1608 | 23.15 | 23.0045 | 22.007 | 20.9148 | 19.8783 | 24.3158 | 24.3025 | 24.2744 | 24.2459 | 24.2164 | 24.2019 | 24.123 | 23.9306 | 23.7326 | 23.142 | 22.1481 | 21.0973 | 20.1015
|  | ST CROSS | ST |  |  | 25.6192 | 25.6192 | 25.6192 | 25.619 | 25.6185 | 25.6178 | 25.6168 | 25.6144 | 25.6133 | 25.6072 | 25.5992 | 25.5711 | 25.5609 | 23.2988 | 23.2909 | 23.2842 | 23.2758 | 23.2654 | 23.2584 | 23.2511 | 23.243 | 23.2357 | 23.2116 | 23.1738 | 23.1158 | 22.7064 | 24.335 | 24.3249 | 24.3165 | 24.3058 | 24.2926 | 24.2839 | 24.2749 | 24.2652 | 24.2562 | 24.2271 | 24.1675 | 23.4893 | 22.8344
|  | ST CROSS | FS |  |  | 25.6192 | 25.6192 | 25.6192 | 25.6192 | 25.6192 | 25.6192 | 25.6191 | 25.619 | 25.6187 | 25.6165 | 25.6147 | 25.6063 | 25.5982 | 23.3046 | 23.3039 | 23.3032 | 23.3 | 23.2962 | 23.2939 | 23.2915 | 23.2885 | 23.2857 | 23.2766 | 23.2635 | 23.2441 | 23.2254 | 24.3424 | 24.3415 | 24.3407 | 24.3366 | 24.3318 | 24.3288 | 24.3258 | 24.322 | 24.3185 | 24.3075 | 24.2912 | 24.2688 | 24.2473
COWLEY GSP | OXFORD BSP | ST EBBES | MINIMUM HEADROOM | SP 51259 05741 | YES | 45.7168 | 45.6917 | 44.1599 | 44.0343 | 43.9087 | 43.7832 | 43.6576 | 43.5321 | 43.4818 | 43.3312 | 43.0801 | 42.2173 | 40.941 | 41.9874 | 41.9534 | 40.4038 | 40.2618 | 40.1201 | 39.9877 | 39.8552 | 39.7226 | 39.6649 | 39.4908 | 39.185 | 37.8501 | 36.3998 | 44.0803 | 44.0469 | 42.4973 | 42.3552 | 42.2135 | 42.0811 | 41.9485 | 41.8159 | 41.7582 | 41.584 | 41.278 | 41.0478 | 40.7053
|  | ST EBBES | CT |  |  | 45.8474 | 45.8323 | 44.9132 | 44.8379 | 44.7625 | 44.6872 | 44.6119 | 44.5365 | 44.5064 | 44.416 | 43.3171 | 42.2173 | 40.941 | 42.1173 | 42.093 | 41.1553 | 41.0627 | 40.9705 | 40.8784 | 40.7961 | 40.7137 | 40.6761 | 40.5622 | 39.4083 | 37.8501 | 36.3998 | 44.2108 | 44.1865 | 43.2488 | 43.1562 | 43.0639 | 42.9717 | 42.8894 | 42.807 | 42.7694 | 42.6554 | 41.5017 | 41.0478 | 40.7053
|  | ST EBBES | LW |  |  | 45.7168 | 45.6917 | 44.1599 | 44.0343 | 43.9087 | 43.7832 | 43.6576 | 43.5321 | 43.4818 | 43.3312 | 43.0801 | 42.4193 | 41.1431 | 41.9874 | 41.9534 | 40.4038 | 40.2618 | 40.1201 | 39.9877 | 39.8552 | 39.7226 | 39.6649 | 39.4908 | 39.185 | 38.0873 | 36.637 | 44.0803 | 44.0469 | 42.4973 | 42.3552 | 42.2135 | 42.0811 | 41.9485 | 41.8159 | 41.7582 | 41.584 | 41.278 | 41.0612 | 40.7187
|  | ST EBBES | ST |  |  | 45.9126 | 45.9026 | 45.2899 | 45.2397 | 45.1894 | 45.1392 | 45.089 | 45.0388 | 45.0187 | 44.9584 | 44.858 | 44.7977 | 44.6872 | 42.1904 | 42.1761 | 41.5566 | 41.4987 | 41.4396 | 41.3829 | 41.3262 | 41.2712 | 41.2461 | 41.1698 | 41.0317 | 40.9281 | 40.7196 | 44.2762 | 44.2661 | 43.6501 | 43.5923 | 43.5331 | 43.4764 | 43.4197 | 43.3646 | 43.3395 | 43.2632 | 43.1249 | 43.0212 | 42.8685
|  | ST EBBES | FS |  |  | 45.9779 | 45.9729 | 45.6666 | 45.6225 | 45.5788 | 45.535 | 45.491 | 45.4363 | 45.3439 | 45.0528 | 44.8783 | 44.4567 | 44.0741 | 42.2608 | 42.2547 | 41.9471 | 41.9001 | 41.8532 | 41.8069 | 41.7603 | 41.7024 | 41.6081 | 41.3108 | 41.1211 | 40.6802 | 40.2774 | 44.3415 | 44.3364 | 44.0301 | 43.986 | 43.9423 | 43.8986 | 43.8539 | 43.7959 | 43.7017 | 43.4044 | 43.2145 | 42.7736 | 42.3708
BRAMLEY (ANDO-THAT) | THATCHAM BSP | ST JOHNS | MINIMUM HEADROOM | SU 47113 66363 | YES | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 34.9988 | 34.9981 | 34.9968 | 34.9955 | 34.9894 | 34.9819 | 34.9731 | 34.9629 | 34.952 | 34.9071 | 34.8652 | 34.8391 | 34.8133 | 36.3868 | 36.3793 | 36.3656 | 36.3515 | 36.2847 | 36.2031 | 36.1076 | 35.997 | 35.8777 | 35.3899 | 34.9346 | 34.6514 | 34.3703
|  | ST JOHNS | CT |  |  | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 34.9988 | 34.9981 | 34.9969 | 34.9957 | 34.9896 | 34.9821 | 34.9733 | 34.9631 | 34.9521 | 34.9072 | 34.8654 | 34.8393 | 34.8134 | 36.3872 | 36.3798 | 36.3665 | 36.3529 | 36.2865 | 36.205 | 36.1094 | 35.9989 | 35.8796 | 35.3917 | 34.9365 | 34.6532 | 34.3721
|  | ST JOHNS | LW |  |  | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 34.9988 | 34.9981 | 34.9968 | 34.9955 | 34.9894 | 34.9819 | 34.9731 | 34.9629 | 34.952 | 34.9071 | 34.8652 | 34.8391 | 34.8133 | 36.3868 | 36.3793 | 36.3656 | 36.3515 | 36.2847 | 36.2031 | 36.1076 | 35.997 | 35.8777 | 35.3899 | 34.9346 | 34.6514 | 34.3703
|  | ST JOHNS | ST |  |  | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 34.9991 | 34.9987 | 34.998 | 34.9972 | 34.993 | 34.9879 | 34.9819 | 34.9751 | 34.9676 | 34.9353 | 34.9048 | 34.8875 | 34.8712 | 36.3903 | 36.3854 | 36.3781 | 36.3691 | 36.3235 | 36.2681 | 36.2034 | 36.1296 | 36.0476 | 35.6964 | 35.3655 | 35.1768 | 34.9998
|  | ST JOHNS | FS |  |  | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 43.5555 | 34.9996 | 34.9995 | 34.9994 | 34.9991 | 34.9972 | 34.995 | 34.9926 | 34.9898 | 34.9868 | 34.9739 | 34.9612 | 34.9527 | 34.9435 | 36.396 | 36.3945 | 36.393 | 36.3901 | 36.3699 | 36.3459 | 36.3192 | 36.2891 | 36.2565 | 36.1165 | 35.9786 | 35.8854 | 35.7862
COWLEY GSP | WITNEY BSP | STANDLAKE | MINIMUM HEADROOM | SP 38923 02349 | NO | 8.7877 | 8.7877 | 8.7877 | 8.7646 | 8.7408 | 8.7163 | 8.6903 | 8.6493 | 8.6439 | 8.5662 | 8.262 | 7.9408 | 7.6992 | 7.8474 | 7.8474 | 7.8474 | 7.8243 | 7.8005 | 7.7759 | 7.7499 | 7.6974 | 7.6418 | 7.4746 | 7.1322 | 6.7714 | 6.4909 | 7.6722 | 7.6316 | 7.5457 | 7.4612 | 7.3763 | 7.3029 | 7.2335 | 7.1493 | 7.0974 | 6.9353 | 6.6001 | 6.2468 | 5.9736
|  | STANDLAKE | CT |  |  | 8.7877 | 8.7877 | 8.7877 | 8.7646 | 8.7408 | 8.7163 | 8.6903 | 8.6493 | 8.6439 | 8.5662 | 8.262 | 7.9408 | 7.6992 | 7.8474 | 7.8474 | 7.8474 | 7.8243 | 7.8005 | 7.7759 | 7.7499 | 7.6974 | 7.6418 | 7.4746 | 7.1322 | 6.7714 | 6.4909 | 7.6847 | 7.6511 | 7.5798 | 7.4875 | 7.3952 | 7.3029 | 7.2335 | 7.1493 | 7.0974 | 6.9353 | 6.6001 | 6.2468 | 5.9736
|  | STANDLAKE | LW |  |  | 8.7877 | 8.7877 | 8.7877 | 8.7866 | 8.7842 | 8.7804 | 8.7752 | 8.7647 | 8.7629 | 8.6593 | 8.4289 | 8.1695 | 7.9545 | 7.8474 | 7.8474 | 7.8474 | 7.8462 | 7.8438 | 7.8401 | 7.8285 | 7.7713 | 7.7192 | 7.5613 | 7.2926 | 6.9937 | 6.7397 | 7.6722 | 7.6316 | 7.5457 | 7.4612 | 7.3763 | 7.3286 | 7.2799 | 7.2263 | 7.1768 | 7.0232 | 6.7617 | 6.4703 | 6.2236
|  | STANDLAKE | ST |  |  | 8.7877 | 8.7877 | 8.7877 | 8.7875 | 8.787 | 8.7863 | 8.7852 | 8.7827 | 8.7816 | 8.7753 | 8.6775 | 8.5098 | 8.3615 | 7.8474 | 7.8474 | 7.8474 | 7.8471 | 7.8466 | 7.8459 | 7.8448 | 7.8424 | 7.8412 | 7.7522 | 7.5803 | 7.3872 | 7.2136 | 7.7417 | 7.6487 | 7.5943 | 7.5274 | 7.4465 | 7.4098 | 7.3731 | 7.3412 | 7.3084 | 7.2092 | 7.0421 | 6.8537 | 6.6849
|  | STANDLAKE | FS |  |  | 8.7877 | 8.7877 | 8.7877 | 8.7862 | 8.7846 | 8.783 | 8.7814 | 8.7788 | 8.7716 | 8.7477 | 8.7355 | 8.6944 | 8.6588 | 7.8474 | 7.8474 | 7.8474 | 7.8458 | 7.8442 | 7.8427 | 7.841 | 7.8385 | 7.8313 | 7.8073 | 7.7952 | 7.754 | 7.7184 | 7.7971 | 7.7327 | 7.7297 | 7.7142 | 7.6961 | 7.6829 | 7.6698 | 7.6524 | 7.633 | 7.5733 | 7.5038 | 7.4072 | 7.3193
MINETY GSP | STRATTON (2 X 60) | STANTON FITZWARREN | MINIMUM HEADROOM | SU 17585 90987 | YES | 30.3271 | 30.1881 | 29.3665 | 29.0956 | 28.8445 | 28.5331 | 28.207 | 27.8422 | 27.511 | 26.5466 | 25.5533 | 24.6224 | 23.8632 | 26.8092 | 26.644 | 25.7877 | 25.4728 | 25.1823 | 24.82 | 24.4404 | 24.0168 | 23.623 | 22.4785 | 21.3142 | 20.252 | 19.3682 | 29.1727 | 29.02 | 28.1801 | 27.8862 | 27.6144 | 27.2762 | 26.922 | 26.5263 | 26.1622 | 25.1032 | 24.0201 | 23.0202 | 22.1956
|  | STANTON FITZWARREN | CT |  |  | 30.3744 | 30.2352 | 29.665 | 29.393 | 29.1428 | 28.9083 | 28.5964 | 28.2453 | 27.9224 | 26.9885 | 25.5777 | 24.6224 | 23.8632 | 26.8548 | 26.6884 | 26.0816 | 25.7637 | 25.4722 | 25.1998 | 24.8346 | 24.4247 | 24.0391 | 22.9251 | 21.3434 | 20.252 | 19.3682 | 29.2192 | 29.0656 | 28.4762 | 28.1801 | 27.9082 | 27.6539 | 27.3139 | 26.9319 | 26.5761 | 25.5476 | 24.047 | 23.0202 | 22.1956
|  | STANTON FITZWARREN | LW |  |  | 30.3271 | 30.1881 | 29.3665 | 29.0956 | 28.8445 | 28.5331 | 28.207 | 27.8422 | 27.511 | 26.5466 | 25.5533 | 24.7215 | 23.9894 | 26.8092 | 26.644 | 25.7877 | 25.4728 | 25.1823 | 24.82 | 24.4404 | 24.0168 | 23.623 | 22.4785 | 21.3142 | 20.3463 | 19.4896 | 29.1727 | 29.02 | 28.1801 | 27.8862 | 27.6144 | 27.2762 | 26.922 | 26.5263 | 26.1622 | 25.1032 | 24.0201 | 23.1169 | 22.3193
|  | STANTON FITZWARREN | ST |  |  | 31.1279 | 30.3656 | 30.0071 | 29.838 | 29.6798 | 29.4837 | 29.2787 | 29.0327 | 28.8032 | 28.119 | 27.4631 | 26.8583 | 26.3686 | 27.7914 | 26.8394 | 26.461 | 26.2649 | 26.0821 | 25.8539 | 25.6152 | 25.3296 | 25.0571 | 24.2467 | 23.4736 | 22.7807 | 22.21 | 30.0823 | 29.2069 | 28.8379 | 28.6546 | 28.4835 | 28.2706 | 28.0478 | 27.7811 | 27.529 | 26.7785 | 26.061 | 25.4099 | 24.8777
|  | STANTON FITZWARREN | FS |  |  | 31.2112 | 30.4553 | 30.2725 | 30.1933 | 30.1257 | 30.0525 | 29.9784 | 29.8927 | 29.8048 | 29.5438 | 29.2931 | 29.0977 | 28.9159 | 27.8984 | 26.9414 | 26.7478 | 26.6547 | 26.5754 | 26.4893 | 26.4022 | 26.3013 | 26.1963 | 25.8856 | 25.5887 | 25.3601 | 25.1499 | 30.1829 | 29.303 | 29.1146 | 29.028 | 28.9543 | 28.8743 | 28.7934 | 28.6997 | 28.6028 | 28.3157 | 28.0407 | 27.828 | 27.6312
LALEHAM | STAINES | STANWELL | MINIMUM HEADROOM | TQ 06003 72766 | YES | 23.5843 | 23.5843 | 23.5843 | 23.5663 | 23.5477 | 23.5283 | 23.5082 | 23.4777 | 23.4734 | 23.3246 | 22.3771 | 21.3824 | 20.4262 | 22.5061 | 22.4999 | 22.4913 | 22.4631 | 22.4326 | 22.3966 | 22.3457 | 22.2488 | 22.0752 | 21.0249 | 19.8482 | 18.6622 | 17.5528 | 22.2987 | 22.2844 | 22.2645 | 22.2229 | 22.1768 | 22.119 | 22.0547 | 21.983 | 21.9392 | 21.7882 | 21.0016 | 19.8021 | 18.6796
|  | STANWELL | CT |  |  | 23.5843 | 23.5843 | 23.5843 | 23.5843 | 23.5843 | 23.5843 | 23.5843 | 23.5843 | 23.5843 | 23.4989 | 22.573 | 21.6242 | 20.6712 | 22.5061 | 22.4999 | 22.4913 | 22.4811 | 22.4692 | 22.4561 | 22.4348 | 22.3684 | 22.2471 | 21.2113 | 20.0562 | 18.9124 | 17.8063 | 22.2987 | 22.2844 | 22.2645 | 22.2409 | 22.2134 | 22.183 | 22.1388 | 22.0976 | 22.0581 | 21.9216 | 21.2104 | 20.053 | 18.9338
|  | STANWELL | LW |  |  | 23.5843 | 23.5843 | 23.5843 | 23.5663 | 23.5477 | 23.5283 | 23.5082 | 23.4777 | 23.4734 | 23.3246 | 22.3771 | 21.3824 | 20.4262 | 22.5061 | 22.4999 | 22.4913 | 22.4631 | 22.4326 | 22.3966 | 22.3457 | 22.2488 | 22.0752 | 21.0249 | 19.8482 | 18.6622 | 17.5528 | 22.2987 | 22.2844 | 22.2645 | 22.2229 | 22.1768 | 22.119 | 22.0547 | 21.983 | 21.9392 | 21.7882 | 21.0016 | 19.8021 | 18.6796
|  | STANWELL | ST |  |  | 23.5843 | 23.5843 | 23.5843 | 23.5843 | 23.5843 | 23.5843 | 23.5843 | 23.5843 | 23.5843 | 23.5843 | 23.569 | 22.9613 | 22.3993 | 22.5069 | 22.5026 | 22.497 | 22.4903 | 22.4823 | 22.4721 | 22.4603 | 22.4483 | 22.4335 | 22.1157 | 21.2988 | 20.5407 | 19.8395 | 22.3005 | 22.2907 | 22.2777 | 22.2622 | 22.2438 | 22.2202 | 22.1928 | 22.1651 | 22.138 | 22.0408 | 21.9331 | 21.7006 | 20.9911
|  | STANWELL | FS |  |  | 23.5843 | 23.5843 | 23.5843 | 23.5843 | 23.5843 | 23.5843 | 23.5843 | 23.5843 | 23.5843 | 23.5843 | 23.5843 | 23.5843 | 23.5843 | 22.5076 | 22.5049 | 22.5017 | 22.4982 | 22.4944 | 22.4903 | 22.4857 | 22.4815 | 22.4769 | 22.4602 | 22.4408 | 22.3731 | 22.2051 | 22.3023 | 22.296 | 22.2886 | 22.2805 | 22.2718 | 22.2622 | 22.2516 | 22.2419 | 22.2312 | 22.1925 | 22.1476 | 22.1006 | 22.0526
MANNINGTON GSP | SALISBURY | STAPLEFORD | MINIMUM HEADROOM | SU 06871 37078 | YES | 22.4094 | 22.4094 | 22.4094 | 22.391 | 22.3718 | 22.3516 | 22.3301 | 22.2952 | 22.2826 | 22.142 | 21.8452 | 21.4945 | 21.2375 | 20.9555 | 20.9437 | 20.9188 | 20.8921 | 20.8581 | 20.8159 | 20.7707 | 20.712 | 20.6694 | 20.4683 | 20.0723 | 19.6196 | 19.2622 | 21.6013 | 21.5827 | 21.5434 | 21.5027 | 21.4596 | 21.3938 | 21.3252 | 21.2458 | 21.1808 | 20.9808 | 20.6376 | 20.2392 | 19.9352
|  | STAPLEFORD | CT |  |  | 22.4094 | 22.4094 | 22.4094 | 22.4086 | 22.4071 | 22.405 | 22.4019 | 22.395 | 22.3932 | 22.2353 | 21.9329 | 21.6172 | 21.3481 | 20.9584 | 20.9483 | 20.9269 | 20.9053 | 20.8833 | 20.8607 | 20.8214 | 20.7787 | 20.7388 | 20.578 | 20.1764 | 19.7587 | 19.3894 | 21.606 | 21.59 | 21.5561 | 21.5225 | 21.4885 | 21.4541 | 21.3939 | 21.3304 | 21.2681 | 21.0818 | 20.733 | 20.3696 | 20.0536
|  | STAPLEFORD | LW |  |  | 22.4094 | 22.4094 | 22.4094 | 22.4068 | 22.4016 | 22.3934 | 22.382 | 22.359 | 22.3136 | 22.142 | 21.8452 | 21.4945 | 21.2375 | 20.9555 | 20.9437 | 20.9188 | 20.8921 | 20.863 | 20.8183 | 20.7707 | 20.712 | 20.6694 | 20.4683 | 20.0723 | 19.6196 | 19.2622 | 21.6013 | 21.5827 | 21.5434 | 21.5027 | 21.4596 | 21.3938 | 21.3252 | 21.2458 | 21.1808 | 20.9808 | 20.6376 | 20.2392 | 19.9352
|  | STAPLEFORD | ST |  |  | 22.4094 | 22.4094 | 22.4094 | 22.391 | 22.3718 | 22.3516 | 22.3301 | 22.2952 | 22.2826 | 22.1964 | 21.9878 | 21.6754 | 21.4625 | 20.959 | 20.9504 | 20.9356 | 20.8991 | 20.8581 | 20.8159 | 20.7728 | 20.7134 | 20.6744 | 20.5519 | 20.3091 | 19.931 | 19.6529 | 21.6069 | 21.5933 | 21.5699 | 21.5229 | 21.4692 | 21.4143 | 21.3586 | 21.285 | 21.2308 | 21.0638 | 20.8243 | 20.4812 | 20.2378
|  | STAPLEFORD | FS |  |  | 22.4094 | 22.4094 | 22.4094 | 22.4094 | 22.4093 | 22.4092 | 22.4091 | 22.4089 | 22.4081 | 22.4031 | 22.3991 | 22.3802 | 22.3618 | 21.0165 | 20.973 | 20.9722 | 20.9682 | 20.9634 | 20.9562 | 20.949 | 20.9396 | 20.9285 | 20.8939 | 20.8432 | 20.7799 | 20.7196 | 21.6977 | 21.629 | 21.6276 | 21.6214 | 21.6139 | 21.6025 | 21.5912 | 21.5765 | 21.5595 | 21.5077 | 21.4299 | 21.3408 | 21.2563
COWLEY GSP | HIGH WYCOMBE BSP | STOKENCHURCH | MINIMUM HEADROOM | SU 77124 94355 | YES | 13.0229 | 13.0229 | 13.0229 | 13.0002 | 12.9768 | 12.9524 | 12.927 | 12.8885 | 12.8826 | 12.8429 | 12.811 | 12.7076 | 12.3223 | 11.4891 | 11.4875 | 11.4842 | 11.4605 | 11.4345 | 11.4042 | 11.3731 | 11.3289 | 11.3175 | 11.2808 | 11.1856 | 10.603 | 10.0782 | 12.0085 | 12.0069 | 12.0035 | 11.9799 | 11.9538 | 11.9235 | 11.8924 | 11.8482 | 11.8367 | 11.8001 | 11.3831 | 10.8238 | 10.3218
|  | STOKENCHURCH | CT |  |  | 13.0229 | 13.0229 | 13.0229 | 13.0116 | 13 | 12.9882 | 12.9759 | 12.957 | 12.9546 | 12.9469 | 12.9113 | 12.8339 | 12.3982 | 11.4891 | 11.4875 | 11.4842 | 11.4695 | 11.4546 | 11.4396 | 11.4216 | 11.397 | 11.3885 | 11.3627 | 11.2521 | 10.6836 | 10.1528 | 12.0085 | 12.0069 | 12.0035 | 11.9889 | 11.974 | 11.959 | 11.9409 | 11.9163 | 11.9077 | 11.8819 | 11.45 | 10.9047 | 10.3968
|  | STOKENCHURCH | LW |  |  | 13.0229 | 13.0229 | 13.0229 | 13.0002 | 12.9768 | 12.9524 | 12.927 | 12.8885 | 12.8832 | 12.8649 | 12.8375 | 12.752 | 12.3223 | 11.4897 | 11.4885 | 11.4858 | 11.4605 | 11.4345 | 11.4042 | 11.3731 | 11.3289 | 11.3175 | 11.2811 | 11.1856 | 10.603 | 10.0782 | 12.0091 | 12.0078 | 12.0052 | 11.9799 | 11.9538 | 11.9235 | 11.8924 | 11.8482 | 11.8367 | 11.8003 | 11.3831 | 10.8238 | 10.3218
|  | STOKENCHURCH | ST |  |  | 13.0229 | 13.0229 | 13.0229 | 13.0008 | 12.9783 | 12.9554 | 12.9317 | 12.895 | 12.8826 | 12.8429 | 12.811 | 12.7076 | 12.6745 | 11.4913 | 11.491 | 11.4904 | 11.4675 | 11.444 | 11.4173 | 11.3899 | 11.3494 | 11.3327 | 11.2808 | 11.2291 | 11.1059 | 10.8888 | 12.0107 | 12.0104 | 12.0097 | 11.9869 | 11.9634 | 11.9367 | 11.9093 | 11.8687 | 11.8521 | 11.8001 | 11.7483 | 11.4493 | 11.0922
|  | STOKENCHURCH | FS |  |  | 13.0229 | 13.0229 | 13.0229 | 13.0229 | 13.0229 | 13.0229 | 13.0229 | 13.0229 | 13.0229 | 13.0229 | 13.0229 | 13.0229 | 13.0229 | 11.492 | 11.4919 | 11.4919 | 11.4917 | 11.4914 | 11.4901 | 11.4889 | 11.4873 | 11.4857 | 11.4809 | 11.4734 | 11.4662 | 11.4594 | 12.0114 | 12.0113 | 12.0113 | 12.0111 | 12.0108 | 12.0095 | 12.0083 | 12.0066 | 12.005 | 12.0003 | 11.9927 | 11.9855 | 11.9787
MINETY GSP | STRATTON (2 X 60) | STRATTON | MINIMUM HEADROOM | SU 16998 88837 | YES | 44.3992 | 44.3914 | 44.3788 | 44.3491 | 44.3038 | 44.2547 | 44.202 | 44.1258 | 44.0893 | 43.9782 | 43.0445 | 42.1668 | 41.3187 | 40.8424 | 40.7386 | 40.5699 | 40.3893 | 40.1911 | 39.9371 | 39.6343 | 39.2785 | 38.9526 | 38.0356 | 36.9832 | 35.9695 | 34.944 | 43.1688 | 43.1599 | 43.097 | 42.9774 | 42.8461 | 42.6779 | 42.4773 | 42.1582 | 41.8176 | 40.8587 | 39.7583 | 38.728 | 37.7324
|  | STRATTON | CT |  |  | 44.3996 | 44.392 | 44.3797 | 44.3665 | 44.352 | 44.3368 | 44.314 | 44.2873 | 44.2629 | 44.0471 | 43.1097 | 42.2319 | 41.3843 | 40.8471 | 40.7457 | 40.5822 | 40.4068 | 40.2136 | 40.0104 | 39.7075 | 39.3517 | 39.0258 | 38.1088 | 37.0564 | 36.0483 | 35.0233 | 43.1692 | 43.1605 | 43.1051 | 42.989 | 42.861 | 42.7264 | 42.5258 | 42.2348 | 41.8941 | 40.9353 | 39.8348 | 38.8045 | 37.8094
|  | STRATTON | LW |  |  | 44.3992 | 44.3914 | 44.3788 | 44.3652 | 44.3503 | 44.3313 | 44.3086 | 44.2818 | 44.2574 | 43.9819 | 43.0445 | 42.1668 | 41.3187 | 40.8424 | 40.7386 | 40.5699 | 40.3893 | 40.1911 | 39.9371 | 39.6343 | 39.2785 | 38.9526 | 38.0356 | 36.9832 | 35.9695 | 34.944 | 43.1688 | 43.1599 | 43.097 | 42.9774 | 42.8461 | 42.6779 | 42.4773 | 42.1582 | 41.8176 | 40.8587 | 39.7583 | 38.728 | 37.7324
|  | STRATTON | ST |  |  | 44.4032 | 44.3985 | 44.3921 | 44.3491 | 44.3038 | 44.2547 | 44.202 | 44.1258 | 44.0893 | 43.9782 | 43.8717 | 43.1521 | 42.5529 | 40.8955 | 40.8326 | 40.747 | 40.6071 | 40.4438 | 40.2389 | 40.0005 | 39.7027 | 39.4595 | 38.7557 | 37.9829 | 37.167 | 36.5007 | 43.1733 | 43.168 | 43.1606 | 43.1098 | 42.9896 | 42.8416 | 42.6709 | 42.454 | 42.2863 | 41.6247 | 40.8191 | 39.9739 | 39.2797
|  | STRATTON | FS |  |  | 44.4069 | 44.4047 | 44.4024 | 44.3884 | 44.3742 | 44.359 | 44.3428 | 44.319 | 44.2666 | 44.1021 | 44.0113 | 43.7738 | 43.5728 | 40.9449 | 40.9156 | 40.8853 | 40.8292 | 40.7668 | 40.6926 | 40.6065 | 40.4937 | 40.3597 | 39.9618 | 39.6069 | 39.1315 | 38.7025 | 43.1776 | 43.1751 | 43.1725 | 43.158 | 43.1432 | 43.1273 | 43.1071 | 43.0268 | 42.9225 | 42.6098 | 42.3514 | 41.9628 | 41.5889
LALEHAM | STAINES | SUNBURY CROSS | MINIMUM HEADROOM | TQ 10053 69996 | YES | 52.389 | 52.2492 | 51.3378 | 51.0447 | 50.7326 | 50.2625 | 49.7631 | 49.3265 | 48.9407 | 47.8211 | 45.7348 | 43.4821 | 41.2089 | 53.4956 | 53.4526 | 52.7114 | 52.5968 | 52.4775 | 52.2212 | 51.6428 | 51.1385 | 50.688 | 49.3811 | 46.9435 | 44.3018 | 41.6459 | 52.3603 | 52.198 | 51.2473 | 50.9128 | 50.5561 | 50.0138 | 49.4371 | 48.9341 | 48.485 | 47.1818 | 44.7513 | 42.1174 | 39.4692
|  | SUNBURY CROSS | CT |  |  | 52.4743 | 52.3537 | 51.748 | 51.5077 | 51.2481 | 50.9798 | 50.5027 | 50.0887 | 49.7119 | 48.6192 | 46.153 | 43.7944 | 41.5216 | 53.5606 | 53.5258 | 53.0666 | 52.9819 | 52.8925 | 52.801 | 52.438 | 51.9563 | 51.5148 | 50.2349 | 47.4173 | 44.6696 | 42.0143 | 52.4502 | 52.3098 | 51.6702 | 51.3939 | 51.0948 | 50.7856 | 50.2312 | 49.7508 | 49.3106 | 48.0344 | 45.2239 | 42.4841 | 39.8365
|  | SUNBURY CROSS | LW |  |  | 52.389 | 52.2492 | 51.3378 | 51.0447 | 50.7326 | 50.2625 | 49.7631 | 49.3265 | 48.9407 | 47.8211 | 45.7348 | 43.4821 | 41.2089 | 53.4956 | 53.4526 | 52.7114 | 52.5968 | 52.4775 | 52.2212 | 51.6428 | 51.1385 | 50.688 | 49.3811 | 46.9435 | 44.3018 | 41.6459 | 52.3603 | 52.198 | 51.2473 | 50.9128 | 50.5561 | 50.0138 | 49.4371 | 48.9341 | 48.485 | 47.1818 | 44.7513 | 42.1174 | 39.4692
|  | SUNBURY CROSS | ST |  |  | 52.5264 | 52.4406 | 52.0448 | 51.871 | 51.6675 | 51.3501 | 51.014 | 50.7249 | 50.4647 | 49.7114 | 48.3158 | 46.8371 | 45.3993 | 53.5955 | 53.5709 | 53.2667 | 53.2032 | 53.1323 | 53.0332 | 52.9294 | 52.671 | 52.3665 | 51.4855 | 49.8508 | 48.1183 | 46.4347 | 52.5063 | 52.4063 | 51.9893 | 51.79 | 51.5559 | 51.1879 | 50.798 | 50.4639 | 50.1603 | 49.2819 | 47.652 | 45.9246 | 44.246
|  | SUNBURY CROSS | FS |  |  | 52.6225 | 52.5864 | 52.41 | 52.3393 | 52.2612 | 52.1459 | 52.0244 | 51.9024 | 51.7969 | 51.4914 | 50.9301 | 50.3053 | 49.6755 | 53.6412 | 53.6306 | 53.4838 | 53.4572 | 53.4288 | 53.3911 | 53.352 | 53.3124 | 53.2799 | 53.1845 | 52.8798 | 52.1497 | 51.4151 | 52.614 | 52.572 | 52.3888 | 52.3079 | 52.2184 | 52.085 | 51.9445 | 51.8033 | 51.681 | 51.3269 | 50.6726 | 49.9447 | 49.2122
BRAMLEY (FLEE) | BRACKNELL RESERVE | SUNNINGHILL | MINIMUM HEADROOM | SU 93757 67606 | YES | 34.0922 | 33.9967 | 33.8027 | 33.6141 | 33.4256 | 33.2554 | 33.1903 | 33.1261 | 33.0574 | 32.8518 | 32.462 | 32.0483 | 31.6393 | 33.0483 | 33.0483 | 33.0483 | 33.0483 | 33.0483 | 33.0483 | 33.0483 | 33.0443 | 33.0374 | 33.0167 | 32.6684 | 32.1883 | 31.7136 | 34.5371 | 34.5371 | 34.5371 | 34.5371 | 34.5371 | 34.5371 | 34.5371 | 34.5371 | 34.5371 | 34.5371 | 34.5371 | 34.3725 | 33.8987
|  | SUNNINGHILL | CT |  |  | 34.0952 | 34.0012 | 33.8105 | 33.6249 | 33.4395 | 33.2554 | 33.1903 | 33.1261 | 33.0574 | 32.8518 | 32.462 | 32.0483 | 31.6393 | 33.0483 | 33.0483 | 33.0483 | 33.0483 | 33.0483 | 33.0483 | 33.0483 | 33.0443 | 33.0374 | 33.0167 | 32.6684 | 32.1883 | 31.7136 | 34.5371 | 34.5371 | 34.5371 | 34.5371 | 34.5371 | 34.5371 | 34.5371 | 34.5371 | 34.5371 | 34.5371 | 34.5371 | 34.3725 | 33.8987
|  | SUNNINGHILL | LW |  |  | 34.0922 | 33.9967 | 33.8027 | 33.6141 | 33.4256 | 33.3595 | 33.2944 | 33.2301 | 33.1615 | 32.9559 | 32.5739 | 32.1602 | 31.7511 | 33.0483 | 33.0483 | 33.0483 | 33.0483 | 33.0483 | 33.0483 | 33.0483 | 33.0483 | 33.0478 | 33.0272 | 32.7984 | 32.3182 | 31.8433 | 34.5371 | 34.5371 | 34.5371 | 34.5371 | 34.5371 | 34.5371 | 34.5371 | 34.5371 | 34.5371 | 34.5371 | 34.5371 | 34.502 | 34.0281
|  | SUNNINGHILL | ST |  |  | 34.1784 | 34.1349 | 34.0646 | 33.9781 | 33.8728 | 33.8023 | 33.7329 | 33.6891 | 33.6423 | 33.5033 | 33.2592 | 33.01 | 32.7581 | 33.0483 | 33.0483 | 33.0483 | 33.0483 | 33.0483 | 33.0483 | 33.0483 | 33.0483 | 33.0483 | 33.0483 | 33.0483 | 33.0326 | 33.0079 | 34.5371 | 34.5371 | 34.5371 | 34.5371 | 34.5371 | 34.5371 | 34.5371 | 34.5371 | 34.5371 | 34.5371 | 34.5371 | 34.5371 | 34.5371
|  | SUNNINGHILL | FS |  |  | 34.2467 | 34.2399 | 34.2343 | 34.2089 | 34.1782 | 34.1529 | 34.128 | 34.0967 | 34.0786 | 34.025 | 33.9307 | 33.8349 | 33.7413 | 33.0483 | 33.0483 | 33.0483 | 33.0483 | 33.0483 | 33.0483 | 33.0483 | 33.0483 | 33.0483 | 33.0483 | 33.0483 | 33.0483 | 33.0483 | 34.5371 | 34.5371 | 34.5371 | 34.5371 | 34.5371 | 34.5371 | 34.5371 | 34.5371 | 34.5371 | 34.5371 | 34.5371 | 34.5371 | 34.5371
MELKSHAM GSP | CHIPPENHAM | SUTTON BENGER | MINIMUM HEADROOM | ST 93394 80051 | YES | 9.4952 | 9.4952 | 8.5335 | 8.5317 | 8.528 | 8.5222 | 8.5142 | 8.4982 | 8.4954 | 8.4813 | 8.4469 | 8.3754 | 8.2114 | 8.5718 | 8.5462 | 7.5219 | 7.457 | 7.3903 | 7.3616 | 7.3309 | 7.2924 | 7.2655 | 7.1799 | 7.0171 | 6.7728 | 6.5938 | 7.5678 | 7.5325 | 6.4962 | 6.422 | 6.346 | 6.3139 | 6.2799 | 6.2381 | 6.2077 | 6.1116 | 5.9405 | 5.7325 | 5.5892
|  | SUTTON BENGER | CT |  |  | 9.4952 | 9.4952 | 8.5335 | 8.5329 | 8.5319 | 8.5304 | 8.5282 | 8.5234 | 8.5225 | 8.5179 | 8.4796 | 8.4369 | 8.2807 | 8.5792 | 8.5578 | 7.5464 | 7.4928 | 7.439 | 7.3854 | 7.3605 | 7.3332 | 7.3081 | 7.2321 | 7.0723 | 6.8526 | 6.6651 | 7.5781 | 7.5485 | 6.5242 | 6.4629 | 6.4014 | 6.34 | 6.3118 | 6.2812 | 6.2526 | 6.1661 | 5.9912 | 5.8077 | 5.6558
|  | SUTTON BENGER | LW |  |  | 9.4952 | 9.4952 | 8.5335 | 8.5317 | 8.528 | 8.5222 | 8.5142 | 8.4982 | 8.4954 | 8.4813 | 8.4469 | 8.3754 | 8.2114 | 8.5718 | 8.5462 | 7.5219 | 7.457 | 7.3903 | 7.3616 | 7.3309 | 7.2924 | 7.2655 | 7.1799 | 7.0171 | 6.7728 | 6.5938 | 7.5678 | 7.5325 | 6.4962 | 6.422 | 6.346 | 6.3139 | 6.2799 | 6.2381 | 6.2077 | 6.1116 | 5.9405 | 5.7325 | 5.5892
|  | SUTTON BENGER | ST |  |  | 9.4952 | 9.4952 | 9.4952 | 9.4949 | 9.4941 | 9.493 | 9.4913 | 9.4876 | 9.4858 | 9.4761 | 9.4635 | 9.419 | 9.4029 | 8.7006 | 8.6094 | 8.6041 | 8.5971 | 8.5881 | 8.573 | 8.5574 | 8.5409 | 8.5254 | 8.4678 | 8.3755 | 8.2517 | 8.1568 | 7.7453 | 7.6196 | 7.6123 | 7.6028 | 7.5908 | 7.5703 | 7.5495 | 7.5282 | 7.5075 | 7.4425 | 7.3386 | 7.2031 | 7.0966
|  | SUTTON BENGER | FS |  |  | 9.4952 | 9.4952 | 9.4952 | 9.4952 | 9.4952 | 9.4951 | 9.4951 | 9.4949 | 9.4943 | 9.4908 | 9.4881 | 9.4748 | 9.4619 | 8.7036 | 8.7024 | 8.7012 | 8.6959 | 8.6895 | 8.6844 | 8.6792 | 8.6725 | 8.6666 | 8.6476 | 8.6198 | 8.5824 | 8.5464 | 7.7494 | 7.7477 | 7.7461 | 7.7388 | 7.73 | 7.7229 | 7.7158 | 7.7068 | 7.6988 | 7.6739 | 7.6367 | 7.5901 | 7.5454
IVER 132KV | UPTON BSP | SUTTON LANE | MINIMUM HEADROOM | TQ 02185 78595 | YES | 24.0851 | 24.0813 | 24.075 | 23.8262 | 23.5684 | 23.2952 | 23.0123 | 22.5881 | 22.5199 | 22.2882 | 21.9032 | 21.1453 | 20.9966 | 25.1459 | 25.1439 | 25.1404 | 24.8938 | 24.6387 | 24.3701 | 24.0919 | 23.6723 | 23.609 | 23.3932 | 23.0472 | 22.3051 | 21.2882 | 25.5813 | 25.5783 | 25.5735 | 25.3257 | 25.0692 | 24.7983 | 24.5178 | 24.0958 | 24.0301 | 23.8062 | 23.4406 | 22.7063 | 22.5815
|  | SUTTON LANE | CT |  |  | 24.0851 | 24.0813 | 24.075 | 24.0689 | 24.0625 | 24.056 | 24.0458 | 24.0355 | 24.0247 | 23.9895 | 23.9034 | 23.7974 | 23.6908 | 25.1459 | 25.1439 | 25.1404 | 25.1371 | 25.1336 | 25.13 | 25.1244 | 25.1188 | 25.1128 | 25.0936 | 25.0464 | 24.9594 | 24.0006 | 25.5813 | 25.5783 | 25.5735 | 25.5687 | 25.5637 | 25.5587 | 25.5508 | 25.5428 | 25.5344 | 25.5071 | 25.4402 | 25.358 | 25.2752
|  | SUTTON LANE | LW |  |  | 24.0854 | 24.0818 | 24.0759 | 23.8262 | 23.5684 | 23.2952 | 23.0123 | 22.5881 | 22.5199 | 22.2882 | 21.9032 | 21.1453 | 20.9966 | 25.1461 | 25.1441 | 25.1409 | 24.8938 | 24.6387 | 24.3701 | 24.0919 | 23.6723 | 23.609 | 23.3932 | 23.0472 | 22.3051 | 21.2882 | 25.5815 | 25.5787 | 25.5741 | 25.3257 | 25.0692 | 24.7983 | 24.5178 | 24.0958 | 24.0301 | 23.8062 | 23.4406 | 22.7063 | 22.5815
|  | SUTTON LANE | ST |  |  | 24.0866 | 24.0841 | 24.0806 | 24.0585 | 24.0353 | 24.0108 | 23.9856 | 23.949 | 23.9316 | 23.8754 | 23.79 | 23.6354 | 23.5408 | 25.1468 | 25.1454 | 25.1435 | 25.1233 | 25.1024 | 25.0806 | 25.0581 | 25.0247 | 25.0106 | 24.9654 | 24.9069 | 24.7838 | 24.7199 | 25.5825 | 25.5805 | 25.5777 | 25.5566 | 25.5345 | 25.5114 | 25.4876 | 25.4525 | 25.4367 | 25.386 | 25.3139 | 25.1749 | 25.0955
|  | SUTTON LANE | FS |  |  | 24.0899 | 24.0892 | 24.0886 | 24.0854 | 24.082 | 24.0779 | 24.0738 | 24.0681 | 24.0561 | 24.0181 | 23.9799 | 23.9051 | 23.8355 | 25.1486 | 25.1482 | 25.1479 | 25.1452 | 25.1424 | 25.1392 | 25.136 | 25.1314 | 25.1208 | 25.0869 | 25.0599 | 24.9994 | 24.945 | 25.585 | 25.5844 | 25.584 | 25.581 | 25.5779 | 25.5743 | 25.5707 | 25.5655 | 25.5542 | 25.5182 | 25.4856 | 25.4178 | 25.3558
MANNINGTON GSP | WAREHAM | SWANAGE | MINIMUM HEADROOM | SZ 02010 79296 | YES | 21.2484 | 21.2349 | 20.5262 | 55.5645 | 55.5028 | 55.4345 | 55.3661 | 55.2977 | 55.2631 | 55.1588 | 54.9622 | 54.235 | 53.4602 | 18.8002 | 18.7873 | 18.0799 | 51.7694 | 51.709 | 51.644 | 51.579 | 51.514 | 51.4829 | 51.013 | 50.1078 | 49.2694 | 48.3819 | 19.6508 | 19.6393 | 18.9346 | 53.9768 | 53.919 | 53.8613 | 53.8035 | 53.7458 | 53.7227 | 53.6494 | 53.0087 | 52.187 | 51.3192
|  | SWANAGE | CT |  |  | 21.3085 | 21.2996 | 20.8728 | 55.9342 | 55.8956 | 55.8565 | 55.8112 | 55.7659 | 55.7406 | 55.6639 | 55.1014 | 54.3088 | 53.5343 | 18.8602 | 18.852 | 18.4264 | 52.1391 | 52.1018 | 52.064 | 52.0221 | 51.9802 | 51.9585 | 51.5963 | 50.3009 | 49.3562 | 48.4689 | 19.7109 | 19.7039 | 19.2811 | 54.3465 | 54.3118 | 54.2772 | 54.2425 | 54.2079 | 54.194 | 54.1524 | 53.2022 | 52.2715 | 51.4039
|  | SWANAGE | LW |  |  | 21.2484 | 21.2349 | 20.5262 | 55.5645 | 55.5028 | 55.4345 | 55.3661 | 55.2977 | 55.2631 | 55.1588 | 54.9622 | 54.235 | 53.4602 | 18.8002 | 18.7873 | 18.0799 | 51.7694 | 51.709 | 51.644 | 51.579 | 51.514 | 51.4829 | 51.013 | 50.1078 | 49.2694 | 48.3819 | 19.6508 | 19.6393 | 18.9346 | 53.9768 | 53.919 | 53.8613 | 53.8035 | 53.7458 | 53.7227 | 53.6494 | 53.0087 | 52.187 | 51.3192
|  | SWANAGE | ST |  |  | 21.3398 | 21.3341 | 21.0504 | 56.1133 | 56.0755 | 56.0345 | 55.993 | 55.9431 | 55.9194 | 55.8468 | 55.7447 | 55.6213 | 55.3238 | 18.8911 | 18.8858 | 18.6027 | 52.3163 | 52.2793 | 52.2401 | 52.2005 | 52.1529 | 52.1317 | 52.0665 | 51.5618 | 50.9909 | 50.4405 | 19.7409 | 19.7363 | 19.4544 | 54.5195 | 54.4845 | 54.4491 | 54.4134 | 54.3708 | 54.3549 | 54.306 | 54.2358 | 53.893 | 53.3437
|  | SWANAGE | FS |  |  | 21.3715 | 21.3691 | 21.228 | 56.3158 | 56.3036 | 56.2905 | 56.2774 | 56.2638 | 56.2562 | 56.2332 | 56.1955 | 56.1689 | 56.1315 | 18.9223 | 18.9199 | 18.7789 | 52.5169 | 52.5049 | 52.4923 | 52.4797 | 52.4668 | 52.4601 | 52.44 | 52.4069 | 52.3844 | 52.3508 | 19.7709 | 19.7686 | 19.6277 | 54.7161 | 54.7046 | 54.693 | 54.6815 | 54.6699 | 54.6653 | 54.6515 | 54.6284 | 54.6145 | 54.5891
MINETY GSP | SWINDON BSP | SWINDON | MINIMUM HEADROOM | SU 12449 86967 | YES | 88.9657 | 88.9657 | 88.9657 | 88.9651 | 88.9636 | 88.9614 | 88.9583 | 88.952 | 88.951 | 88.9455 | 88.9321 | 88.9061 | 87.0605 | 83.4625 | 83.4568 | 83.4453 | 83.4332 | 83.4204 | 83.3946 | 83.368 | 83.3384 | 83.3122 | 83.231 | 81.4529 | 78.7762 | 76.1323 | 87.1186 | 87.1126 | 87.1002 | 87.0873 | 87.0737 | 87.0462 | 87.0179 | 86.9867 | 86.9588 | 86.8722 | 85.4019 | 82.8296 | 80.3018
|  | SWINDON | CT |  |  | 88.9657 | 88.9657 | 88.9657 | 88.9655 | 88.9651 | 88.9646 | 88.9637 | 88.9618 | 88.9615 | 88.9597 | 88.9448 | 88.9283 | 87.3127 | 83.463 | 83.4576 | 83.4466 | 83.4357 | 83.4245 | 83.4132 | 83.3888 | 83.3636 | 83.3382 | 83.2607 | 81.7209 | 79.0643 | 76.4181 | 87.1192 | 87.1134 | 87.1017 | 87.0899 | 87.078 | 87.0659 | 87.0399 | 87.013 | 86.9859 | 86.903 | 85.6686 | 83.106 | 80.5759
|  | SWINDON | LW |  |  | 88.9657 | 88.9657 | 88.9657 | 88.9651 | 88.9636 | 88.9614 | 88.9583 | 88.952 | 88.951 | 88.9455 | 88.9321 | 88.9061 | 87.0605 | 83.4625 | 83.4568 | 83.4453 | 83.4332 | 83.4204 | 83.3946 | 83.368 | 83.3384 | 83.3122 | 83.231 | 81.4529 | 78.7762 | 76.1323 | 87.1186 | 87.1126 | 87.1002 | 87.0873 | 87.0737 | 87.0462 | 87.0179 | 86.9867 | 86.9588 | 86.8722 | 85.4019 | 82.8296 | 80.3018
|  | SWINDON | ST |  |  | 88.9657 | 88.9657 | 88.9657 | 88.9656 | 88.9653 | 88.9649 | 88.9642 | 88.9628 | 88.9621 | 88.9583 | 88.9534 | 88.9362 | 88.9299 | 83.4696 | 83.4621 | 83.4563 | 83.4491 | 83.4402 | 83.4261 | 83.4119 | 83.3945 | 83.3766 | 83.3216 | 83.2219 | 81.8353 | 80.1537 | 87.1263 | 87.1182 | 87.112 | 87.1043 | 87.0949 | 87.0797 | 87.0646 | 87.046 | 87.027 | 86.9683 | 86.862 | 85.7824 | 84.1476
|  | SWINDON | FS |  |  | 88.9657 | 88.9657 | 88.9657 | 88.9657 | 88.9657 | 88.9657 | 88.9657 | 88.9656 | 88.9654 | 88.964 | 88.963 | 88.9578 | 88.9528 | 83.4751 | 83.4705 | 83.4699 | 83.468 | 83.4658 | 83.4615 | 83.4571 | 83.4515 | 83.4446 | 83.4234 | 83.3853 | 83.34 | 83.2951 | 87.1321 | 87.1272 | 87.1266 | 87.1246 | 87.1222 | 87.1175 | 87.1129 | 87.1069 | 87.0995 | 87.0769 | 87.0362 | 86.9881 | 86.9404
BRAMLEY (ANDO-THAT) | THATCHAM BSP | TADLEY | MINIMUM HEADROOM | SU 57753 62717 | YES | 25.3112 | 25.3112 | 25.3112 | 25.298 | 25.2842 | 25.2698 | 25.2541 | 25.2285 | 25.225 | 25.2121 | 25.1365 | 25.0532 | 24.844 | 24.6213 | 24.6213 | 24.6213 | 24.6082 | 24.5944 | 24.5799 | 24.5642 | 24.5386 | 24.5351 | 24.5222 | 23.8342 | 23.0063 | 22.2319 | 24.5528 | 24.5504 | 24.5454 | 24.5298 | 24.5119 | 24.4933 | 24.4698 | 24.4364 | 24.4246 | 24.3868 | 24.2387 | 23.43 | 22.6717
|  | TADLEY | CT |  |  | 25.3112 | 25.3112 | 25.3112 | 25.298 | 25.2842 | 25.2698 | 25.2541 | 25.2285 | 25.225 | 25.2121 | 25.1365 | 25.0532 | 24.844 | 24.6213 | 24.6213 | 24.6213 | 24.6082 | 24.5944 | 24.5799 | 24.5642 | 24.5386 | 24.5351 | 24.5222 | 23.8581 | 23.0102 | 22.2319 | 24.5534 | 24.5514 | 24.5471 | 24.5298 | 24.5119 | 24.4933 | 24.4698 | 24.4364 | 24.4246 | 24.3868 | 24.2597 | 23.431 | 22.6717
|  | TADLEY | LW |  |  | 25.3112 | 25.3112 | 25.3112 | 25.3095 | 25.306 | 25.3006 | 25.2931 | 25.278 | 25.2754 | 25.262 | 25.2296 | 25.1664 | 24.8759 | 24.6213 | 24.6213 | 24.6213 | 24.6196 | 24.6162 | 24.6107 | 24.6032 | 24.5881 | 24.5855 | 24.5721 | 23.8342 | 23.0063 | 22.2476 | 24.5528 | 24.5504 | 24.5454 | 24.5389 | 24.5306 | 24.5173 | 24.502 | 24.4791 | 24.4681 | 24.4299 | 24.2387 | 23.43 | 22.6903
|  | TADLEY | ST |  |  | 25.3112 | 25.3112 | 25.3112 | 25.3108 | 25.3101 | 25.3091 | 25.3075 | 25.304 | 25.3023 | 25.2932 | 25.2813 | 25.2394 | 25.2242 | 24.6213 | 24.6213 | 24.6213 | 24.6209 | 24.6202 | 24.6192 | 24.6176 | 24.6141 | 24.6124 | 24.6033 | 24.5057 | 23.9701 | 23.4659 | 24.5535 | 24.5517 | 24.5487 | 24.5447 | 24.5395 | 24.5327 | 24.5255 | 24.5167 | 24.5093 | 24.4834 | 24.443 | 24.3714 | 23.8796
|  | TADLEY | FS |  |  | 25.3112 | 25.3112 | 25.3112 | 25.3088 | 25.3064 | 25.304 | 25.3016 | 25.2977 | 25.2868 | 25.2507 | 25.2324 | 25.1707 | 25.1174 | 24.6213 | 24.6213 | 24.6213 | 24.6189 | 24.6165 | 24.6141 | 24.6117 | 24.6078 | 24.5969 | 24.5608 | 24.5425 | 24.4808 | 24.4275 | 24.5565 | 24.5563 | 24.5561 | 24.5529 | 24.5496 | 24.5453 | 24.541 | 24.5348 | 24.5216 | 24.479 | 24.4499 | 24.3773 | 24.3135
IVER 132KV | SLOUGH | TAPLOW | MINIMUM HEADROOM | SU 91721 81234 | YES | 43.7314 | 43.7314 | 43.7314 | 43.7152 | 43.6986 | 43.6816 | 43.6636 | 43.6352 | 43.6315 | 43.5332 | 43.4221 | 42.076 | 40.7639 | 41.6393 | 41.6393 | 41.6393 | 41.6232 | 41.6066 | 41.5895 | 41.5715 | 41.5431 | 41.5394 | 41.4411 | 41.1998 | 39.6908 | 38.1997 | 41.7901 | 41.7901 | 41.7901 | 41.7739 | 41.7573 | 41.7403 | 41.7223 | 41.6939 | 41.6902 | 41.5919 | 41.098 | 39.5972 | 38.1151
|  | TAPLOW | CT |  |  | 43.7314 | 43.7314 | 43.7314 | 43.7152 | 43.6986 | 43.6816 | 43.6636 | 43.6352 | 43.6315 | 43.619 | 43.4366 | 42.076 | 40.7639 | 41.6393 | 41.6393 | 41.6393 | 41.6232 | 41.6066 | 41.5895 | 41.5715 | 41.5431 | 41.5394 | 41.5269 | 41.23 | 39.6908 | 38.1997 | 41.7901 | 41.7901 | 41.7901 | 41.7739 | 41.7573 | 41.7403 | 41.7223 | 41.6939 | 41.6902 | 41.6777 | 41.1274 | 39.5972 | 38.1151
|  | TAPLOW | LW |  |  | 43.7314 | 43.7314 | 43.7314 | 43.7251 | 43.718 | 43.7099 | 43.7006 | 43.6851 | 43.6827 | 43.6729 | 43.4221 | 42.0952 | 40.8 | 41.6393 | 41.6393 | 41.6393 | 41.6331 | 41.626 | 41.6178 | 41.6085 | 41.593 | 41.5907 | 41.5808 | 41.1998 | 39.6943 | 38.2201 | 41.7901 | 41.7901 | 41.7901 | 41.7839 | 41.7767 | 41.7686 | 41.7593 | 41.7438 | 41.7414 | 41.7316 | 41.098 | 39.6015 | 38.1362
|  | TAPLOW | ST |  |  | 43.7314 | 43.7314 | 43.7314 | 43.7223 | 43.7129 | 43.7033 | 43.6931 | 43.6768 | 43.6711 | 43.6514 | 43.6337 | 43.5744 | 42.7698 | 41.6393 | 41.6393 | 41.6393 | 41.6302 | 41.6209 | 41.6112 | 41.601 | 41.5848 | 41.5791 | 41.5594 | 41.5417 | 41.4285 | 40.4708 | 41.7901 | 41.7901 | 41.7901 | 41.781 | 41.7716 | 41.762 | 41.7518 | 41.7355 | 41.7298 | 41.7101 | 41.6924 | 41.3249 | 40.3728
|  | TAPLOW | FS |  |  | 43.7314 | 43.7314 | 43.7314 | 43.723 | 43.7149 | 43.7067 | 43.6984 | 43.6853 | 43.649 | 43.5332 | 43.4776 | 43.3009 | 43.1524 | 41.6393 | 41.6393 | 41.6393 | 41.631 | 41.6228 | 41.6146 | 41.6063 | 41.5932 | 41.5569 | 41.4411 | 41.3855 | 41.2088 | 41.0603 | 41.7901 | 41.7901 | 41.7901 | 41.7817 | 41.7736 | 41.7654 | 41.7571 | 41.744 | 41.7077 | 41.5919 | 41.5363 | 41.3596 | 41.2111
MANNINGTON GSP | SHAFTESBURY BSP | TARRANT RUSHTON | MINIMUM HEADROOM | ST 94510 07307 | YES | 8.3252 | 8.3225 | 8.3168 | 8.3113 | 8.3057 | 8.2626 | 8.2151 | 8.163 | 8.1072 | 7.8637 | 7.4082 | 7.2843 | 7.1668 | 7.8265 | 7.823 | 7.8157 | 7.8085 | 7.8014 | 7.7458 | 7.6848 | 7.6177 | 7.5458 | 7.2324 | 6.6792 | 6.5293 | 6.3873 | 8.6349 | 8.6349 | 8.6349 | 8.6349 | 8.6349 | 8.6349 | 8.6349 | 8.6349 | 8.6349 | 8.6349 | 8.6046 | 8.4586 | 8.317
|  | TARRANT RUSHTON | CT |  |  | 8.3252 | 8.3225 | 8.3168 | 8.3113 | 8.3057 | 8.2779 | 8.2304 | 8.1783 | 8.1225 | 7.879 | 7.4245 | 7.3006 | 7.1832 | 7.8265 | 7.823 | 7.8157 | 7.8085 | 7.8014 | 7.7655 | 7.7045 | 7.6374 | 7.5655 | 7.2521 | 6.6989 | 6.549 | 6.4071 | 8.6349 | 8.6349 | 8.6349 | 8.6349 | 8.6349 | 8.6349 | 8.6349 | 8.6349 | 8.6349 | 8.6349 | 8.6213 | 8.4782 | 8.3367
|  | TARRANT RUSHTON | LW |  |  | 8.3252 | 8.3225 | 8.3168 | 8.3113 | 8.3057 | 8.2626 | 8.2151 | 8.163 | 8.1072 | 7.8637 | 7.4082 | 7.2843 | 7.1668 | 7.8265 | 7.823 | 7.8157 | 7.8085 | 7.8014 | 7.7458 | 7.6848 | 7.6177 | 7.5458 | 7.2324 | 6.6792 | 6.5293 | 6.3873 | 8.6349 | 8.6349 | 8.6349 | 8.6349 | 8.6349 | 8.6349 | 8.6349 | 8.6349 | 8.6349 | 8.6349 | 8.6046 | 8.4586 | 8.317
|  | TARRANT RUSHTON | ST |  |  | 8.327 | 8.3255 | 8.3229 | 8.3198 | 8.316 | 8.294 | 8.2691 | 8.234 | 8.1958 | 8.0227 | 7.708 | 7.628 | 7.5517 | 7.8288 | 7.8268 | 7.8235 | 7.8195 | 7.8146 | 7.7863 | 7.7542 | 7.7091 | 7.6598 | 7.437 | 7.0417 | 6.9449 | 6.8528 | 8.6349 | 8.6349 | 8.6349 | 8.6349 | 8.6349 | 8.6349 | 8.6349 | 8.6349 | 8.6349 | 8.6349 | 8.6349 | 8.6349 | 8.6349
|  | TARRANT RUSHTON | FS |  |  | 8.3294 | 8.3292 | 8.329 | 8.3282 | 8.3271 | 8.3176 | 8.3072 | 8.2952 | 8.2801 | 8.2115 | 8.0836 | 8.0559 | 8.0309 | 7.8319 | 7.8316 | 7.8314 | 7.8302 | 7.8289 | 7.8166 | 7.8033 | 7.7878 | 7.7683 | 7.6801 | 7.5154 | 7.4797 | 7.4476 | 8.6349 | 8.6349 | 8.6349 | 8.6349 | 8.6349 | 8.6349 | 8.6349 | 8.6349 | 8.6349 | 8.6349 | 8.6349 | 8.6349 | 8.6349
MANNINGTON GSP | SALISBURY | TEFFONT | MINIMUM HEADROOM | ST 99837 30994 | YES | 8.3369 | 8.3323 | 8.3227 | 8.3134 | 8.3041 | 8.2728 | 8.2407 | 8.209 | 8.1748 | 8.0739 | 7.9082 | 7.7374 | 7.5695 | 7.0266 | 7.0213 | 7.0101 | 6.9992 | 6.9884 | 6.9518 | 6.9145 | 6.8775 | 6.8376 | 6.7199 | 6.5267 | 6.3275 | 6.1317 | 6.5344 | 6.5291 | 6.5177 | 6.5067 | 6.4958 | 6.4588 | 6.421 | 6.3836 | 6.3432 | 6.224 | 6.0286 | 5.827 | 5.6289
|  | TEFFONT | CT |  |  | 8.3369 | 8.3323 | 8.3227 | 8.3134 | 8.3041 | 8.2949 | 8.2629 | 8.2312 | 8.197 | 8.0961 | 7.9303 | 7.7596 | 7.5918 | 7.0266 | 7.0213 | 7.0101 | 6.9992 | 6.9884 | 6.9776 | 6.9404 | 6.9034 | 6.8635 | 6.7458 | 6.5524 | 6.3533 | 6.1576 | 6.5344 | 6.5291 | 6.5177 | 6.5067 | 6.4958 | 6.4849 | 6.4472 | 6.4097 | 6.3694 | 6.2503 | 6.0546 | 5.8532 | 5.6551
|  | TEFFONT | LW |  |  | 8.3371 | 8.3326 | 8.3233 | 8.3141 | 8.305 | 8.2728 | 8.2407 | 8.209 | 8.1748 | 8.0739 | 7.9082 | 7.7374 | 7.5695 | 7.0268 | 7.0217 | 7.0107 | 7.0001 | 6.9895 | 6.9518 | 6.9145 | 6.8775 | 6.8376 | 6.7199 | 6.5267 | 6.3275 | 6.1317 | 6.5347 | 6.5294 | 6.5184 | 6.5076 | 6.4969 | 6.4588 | 6.421 | 6.3836 | 6.3432 | 6.224 | 6.0286 | 5.827 | 5.6289
|  | TEFFONT | ST |  |  | 8.3399 | 8.3375 | 8.3332 | 8.328 | 8.3216 | 8.3062 | 8.2909 | 8.2693 | 8.2459 | 8.1779 | 8.0679 | 7.958 | 7.8486 | 7.0302 | 7.0273 | 7.0223 | 7.0162 | 7.0088 | 6.9908 | 6.973 | 6.9478 | 6.9206 | 6.8413 | 6.7129 | 6.5847 | 6.4572 | 6.5381 | 6.5351 | 6.5301 | 6.5239 | 6.5164 | 6.4982 | 6.4802 | 6.4546 | 6.4271 | 6.3469 | 6.217 | 6.0873 | 5.9583
|  | TEFFONT | FS |  |  | 8.344 | 8.3436 | 8.3433 | 8.3419 | 8.3402 | 8.3356 | 8.331 | 8.3251 | 8.3161 | 8.2898 | 8.2483 | 8.2086 | 8.1712 | 7.0349 | 7.0345 | 7.0342 | 7.0325 | 7.0305 | 7.0251 | 7.0197 | 7.0129 | 7.0023 | 6.9718 | 6.9233 | 6.877 | 6.8335 | 6.5428 | 6.5424 | 6.542 | 6.5404 | 6.5384 | 6.5329 | 6.5274 | 6.5205 | 6.5099 | 6.4789 | 6.4299 | 6.3831 | 6.339
BRAMLEY (FLEE) | MAIDENHEAD BSP | TEMPLE FARM | MINIMUM HEADROOM | SU 84178 83872 | YES | 6.092 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 5.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6936 | 4.6429 | 4.5561 | 4.4643 | 4.3738 | 5.1795 | 3.9682 | 3.9443 | 3.9211 | 3.8981 | 3.8753 | 3.8591 | 3.843 | 3.8256 | 3.774 | 3.6856 | 3.5923 | 3.5002
|  | TEMPLE FARM | CT |  |  | 6.092 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 5.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6936 | 4.6429 | 4.5561 | 4.4643 | 4.3738 | 5.1795 | 3.9682 | 3.9443 | 3.9211 | 3.8981 | 3.8753 | 3.8591 | 3.843 | 3.8256 | 3.774 | 3.6856 | 3.5923 | 3.5002
|  | TEMPLE FARM | LW |  |  | 6.092 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 5.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6217 | 4.5299 | 4.4394 | 5.1917 | 3.987 | 3.9773 | 3.9679 | 3.9584 | 3.9421 | 3.9259 | 3.9098 | 3.8924 | 3.8408 | 3.7524 | 3.6591 | 3.5669
|  | TEMPLE FARM | ST |  |  | 6.092 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 5.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.649 | 4.5902 | 5.1966 | 3.9949 | 3.9921 | 3.9886 | 3.9843 | 3.9708 | 3.9574 | 3.9464 | 3.9346 | 3.8998 | 3.8407 | 3.7803 | 3.7204
|  | TEMPLE FARM | FS |  |  | 6.092 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 5.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 5.1992 | 3.999 | 3.9987 | 3.9978 | 3.9966 | 3.9919 | 3.9872 | 3.9812 | 3.9766 | 3.9632 | 3.9408 | 3.9183 | 3.8965
MELKSHAM GSP | CHIPPENHAM | TETBURY | MINIMUM HEADROOM | ST 89708 93444 | YES | 12.3646 | 12.3646 | 12.3646 | 12.3274 | 12.2884 | 12.247 | 12.2034 | 12.1359 | 12.1263 | 12.092 | 11.8983 | 11.3957 | 11.025 | 10.936 | 10.9321 | 10.924 | 10.884 | 10.8387 | 10.7905 | 10.7401 | 10.6659 | 10.5783 | 10.2869 | 9.7929 | 9.2079 | 8.7561 | 11.4453 | 11.3981 | 11.2982 | 11.2013 | 11.1049 | 10.9856 | 10.8593 | 10.7098 | 10.6119 | 10.3161 | 9.8202 | 9.2332 | 8.7794
|  | TETBURY | CT |  |  | 12.3646 | 12.3646 | 12.3646 | 12.3644 | 12.364 | 12.3635 | 12.3628 | 12.3611 | 12.3608 | 12.3592 | 12.1372 | 11.7541 | 11.3869 | 10.936 | 10.9321 | 10.924 | 10.9159 | 10.9077 | 10.8994 | 10.8889 | 10.8089 | 10.7236 | 10.4618 | 10.0149 | 9.5494 | 9.1011 | 11.4453 | 11.3981 | 11.2982 | 11.2013 | 11.1049 | 11.0093 | 10.9259 | 10.8423 | 10.7536 | 10.4906 | 10.0418 | 9.5742 | 9.124
|  | TETBURY | LW |  |  | 12.3646 | 12.3646 | 12.3646 | 12.3274 | 12.2884 | 12.247 | 12.2034 | 12.1359 | 12.1263 | 12.092 | 11.8983 | 11.3957 | 11.025 | 10.9373 | 10.9342 | 10.9276 | 10.884 | 10.8387 | 10.7905 | 10.7401 | 10.6659 | 10.5783 | 10.2869 | 9.7929 | 9.2079 | 8.7561 | 11.4617 | 11.4234 | 11.3426 | 11.2271 | 11.1104 | 10.9856 | 10.8593 | 10.7098 | 10.6119 | 10.3161 | 9.8202 | 9.2332 | 8.7794
|  | TETBURY | ST |  |  | 12.3646 | 12.3646 | 12.3646 | 12.3644 | 12.3642 | 12.3638 | 12.3632 | 12.3619 | 12.3613 | 12.358 | 12.3536 | 12.3383 | 12.1453 | 10.9398 | 10.9383 | 10.9356 | 10.9323 | 10.9281 | 10.9235 | 10.9187 | 10.9129 | 10.9073 | 10.8896 | 10.6277 | 10.3218 | 10.0277 | 11.4921 | 11.4732 | 11.441 | 11.4012 | 11.3531 | 11.3009 | 11.2493 | 11.1921 | 11.1311 | 10.9516 | 10.6574 | 10.3501 | 10.0547
|  | TETBURY | FS |  |  | 12.3646 | 12.3646 | 12.3646 | 12.3622 | 12.3598 | 12.3575 | 12.355 | 12.3513 | 12.3407 | 12.3067 | 12.2901 | 12.2363 | 12.1907 | 10.9422 | 10.942 | 10.9417 | 10.9383 | 10.9347 | 10.931 | 10.9273 | 10.9219 | 10.9095 | 10.8699 | 10.8443 | 10.7817 | 10.7278 | 11.5213 | 11.5184 | 11.5155 | 11.5001 | 11.4824 | 11.4642 | 11.4462 | 11.4223 | 11.3883 | 11.2863 | 11.1597 | 10.9989 | 10.8518
BRAMLEY (ANDO-THAT) | THATCHAM BSP | THATCHAM | MINIMUM HEADROOM | SU 52758 66466 | YES | 47.6728 | 47.6594 | 46.8404 | 46.7703 | 46.6971 | 46.5948 | 46.366 | 46.0327 | 45.979 | 45.5495 | 43.0766 | 40.8284 | 39.1895 | 43.5996 | 43.5662 | 42.7052 | 42.0772 | 41.1851 | 40.8195 | 40.4444 | 39.8272 | 39.4674 | 38.3902 | 35.687 | 33.199 | 31.3242 | 40.3825 | 40.185 | 38.9769 | 38.5297 | 38.0829 | 37.8788 | 37.5711 | 37.1125 | 36.9238 | 36.3525 | 34.4941 | 32.8856 | 31.8763
|  | THATCHAM | CT |  |  | 47.7426 | 47.7345 | 47.2432 | 47.0307 | 46.8146 | 46.5948 | 46.366 | 46.0327 | 45.979 | 45.5495 | 43.0766 | 40.8284 | 39.1895 | 43.675 | 43.6501 | 43.1232 | 42.7596 | 41.8772 | 40.9595 | 40.4444 | 39.8272 | 39.4674 | 38.3902 | 35.687 | 33.199 | 31.3242 | 40.5042 | 40.3407 | 39.5207 | 38.9899 | 38.4582 | 37.9262 | 37.5711 | 37.1125 | 36.9238 | 36.3525 | 34.4941 | 32.8856 | 31.8763
|  | THATCHAM | LW |  |  | 47.6728 | 47.6594 | 46.8404 | 46.7703 | 46.6971 | 46.6205 | 46.5402 | 46.4465 | 46.4151 | 45.913 | 44.4409 | 42.9153 | 41.4465 | 43.5996 | 43.5662 | 42.7052 | 42.0772 | 41.1851 | 40.8195 | 40.4528 | 40.0753 | 39.7379 | 38.7285 | 37.026 | 35.2606 | 33.5558 | 40.3825 | 40.185 | 38.9769 | 38.5297 | 38.0829 | 37.8788 | 37.6721 | 37.4532 | 37.2868 | 36.7835 | 35.9257 | 35.04 | 34.2012
|  | THATCHAM | ST |  |  | 47.7775 | 47.7721 | 47.4446 | 47.4171 | 47.389 | 47.3603 | 47.3307 | 47.2976 | 47.2839 | 47.2358 | 47.0868 | 46.1211 | 45.182 | 43.716 | 43.6902 | 43.3375 | 43.2792 | 42.716 | 42.436 | 42.1513 | 41.9242 | 41.7016 | 41.0428 | 39.9604 | 38.8401 | 37.7476 | 40.5953 | 40.4008 | 39.8412 | 39.529 | 39.1578 | 39.0101 | 38.8632 | 38.7445 | 38.6387 | 38.3211 | 37.802 | 37.2488 | 36.7189
|  | THATCHAM | FS |  |  | 47.8124 | 47.8097 | 47.6459 | 47.6325 | 47.619 | 47.6055 | 47.592 | 47.5783 | 47.5719 | 47.5501 | 47.5186 | 47.4806 | 47.4298 | 43.7762 | 43.7663 | 43.6011 | 43.5809 | 43.5595 | 43.5417 | 43.5239 | 43.5048 | 43.4945 | 43.4614 | 43.4117 | 43.356 | 43.2882 | 40.865 | 40.7949 | 40.6181 | 40.5428 | 40.4559 | 40.4026 | 40.3497 | 40.2852 | 40.2431 | 40.1172 | 39.9168 | 39.7144 | 39.5072
NORTH HYDE GSP | NORTH HYDE 22kV | THE GREEN | MINIMUM HEADROOM | TQ 12414 79503 | YES | 14.43 | 14.43 | 14.43 | 14.4219 | 14.4135 | 14.4048 | 14.3957 | 14.3801 | 14.369 | 14.3342 | 13.9014 | 12.9633 | 12.0464 | 13.9783 | 13.9755 | 13.9708 | 13.9547 | 13.9371 | 13.9148 | 13.8647 | 13.7563 | 13.6446 | 13.3022 | 12.5284 | 11.5278 | 10.4646 | 14.0289 | 14.0252 | 14.0194 | 14.0048 | 13.989 | 13.9675 | 13.9459 | 13.9211 | 13.8695 | 13.5191 | 12.6061 | 11.5168 | 10.4498
|  | THE GREEN | CT |  |  | 14.43 | 14.43 | 14.43 | 14.43 | 14.43 | 14.43 | 14.43 | 14.43 | 14.4223 | 14.394 | 14.003 | 13.0874 | 12.1717 | 13.9783 | 13.9755 | 13.9708 | 13.9628 | 13.9535 | 13.9439 | 13.9198 | 13.845 | 13.7352 | 13.3992 | 12.6353 | 11.6572 | 10.5965 | 14.0289 | 14.0252 | 14.0194 | 14.0129 | 14.0055 | 13.9966 | 13.9841 | 13.973 | 13.961 | 13.6171 | 12.7206 | 11.6478 | 10.5819
|  | THE GREEN | LW |  |  | 14.43 | 14.43 | 14.43 | 14.4219 | 14.4135 | 14.4048 | 14.3957 | 14.3801 | 14.369 | 14.3342 | 13.9014 | 12.9633 | 12.0464 | 13.9783 | 13.9755 | 13.9708 | 13.9547 | 13.9371 | 13.9148 | 13.8647 | 13.7563 | 13.6446 | 13.3022 | 12.5284 | 11.5278 | 10.4646 | 14.0289 | 14.0252 | 14.0194 | 14.0048 | 13.989 | 13.9675 | 13.9459 | 13.9211 | 13.8695 | 13.5191 | 12.6061 | 11.5168 | 10.4498
|  | THE GREEN | ST |  |  | 14.43 | 14.43 | 14.43 | 14.43 | 14.43 | 14.43 | 14.43 | 14.43 | 14.43 | 14.4283 | 14.3837 | 14.0428 | 13.474 | 13.9798 | 13.9779 | 13.9755 | 13.9725 | 13.9668 | 13.9597 | 13.9533 | 13.9459 | 13.9387 | 13.8058 | 13.2762 | 12.6815 | 12.0914 | 14.0309 | 14.0284 | 14.0252 | 14.0211 | 14.0161 | 14.0104 | 14.0053 | 13.9986 | 13.9914 | 13.9693 | 13.4826 | 12.7756 | 12.0977
|  | THE GREEN | FS |  |  | 14.43 | 14.43 | 14.43 | 14.4284 | 14.4269 | 14.4253 | 14.4237 | 14.4213 | 14.4145 | 14.3928 | 14.3825 | 14.3466 | 14.2959 | 13.9813 | 13.9804 | 13.9794 | 13.9765 | 13.9735 | 13.9703 | 13.9673 | 13.9635 | 13.9543 | 13.924 | 13.893 | 13.7064 | 13.4001 | 14.0329 | 14.0317 | 14.0304 | 14.0271 | 14.0235 | 14.0197 | 14.0163 | 14.0121 | 14.003 | 13.9744 | 13.9457 | 13.8874 | 13.6205
BRAMLEY (FLEE) | READING TOWN BSP | THE MALL | MINIMUM HEADROOM | SU 71319 73293 | YES | 30.8568 | 30.7979 | 30.683 | 30.5674 | 30.3525 | 30.1429 | 30.0257 | 29.8993 | 29.765 | 29.2776 | 28.4191 | 27.4249 | 26.4277 | 30.332 | 30.325 | 30.3114 | 30.2976 | 30.2835 | 30.2709 | 30.2646 | 30.2579 | 30.2507 | 30.2248 | 29.9522 | 28.8204 | 27.6824 | 30.5876 | 30.5787 | 30.5613 | 30.5438 | 30.4141 | 30.2746 | 30.2056 | 30.1183 | 29.9733 | 29.3975 | 28.403 | 27.2515 | 26.0963
|  | THE MALL | CT |  |  | 30.8591 | 30.8014 | 30.689 | 30.5758 | 30.3726 | 30.1429 | 30.0257 | 29.8993 | 29.765 | 29.2776 | 28.4191 | 27.4249 | 26.4277 | 30.3323 | 30.3254 | 30.3121 | 30.2986 | 30.2848 | 30.2709 | 30.2646 | 30.2579 | 30.2507 | 30.2248 | 29.9522 | 28.8204 | 27.6824 | 30.588 | 30.5792 | 30.5622 | 30.5451 | 30.4281 | 30.2746 | 30.2056 | 30.1183 | 29.9733 | 29.3975 | 28.403 | 27.2515 | 26.0963
|  | THE MALL | LW |  |  | 30.8568 | 30.7979 | 30.683 | 30.5674 | 30.3525 | 30.2608 | 30.1542 | 30.0279 | 29.8937 | 29.4094 | 28.551 | 27.5568 | 26.5595 | 30.332 | 30.325 | 30.3114 | 30.2976 | 30.2835 | 30.2778 | 30.2715 | 30.2647 | 30.2576 | 30.2317 | 30.1024 | 28.9706 | 27.8346 | 30.5876 | 30.5787 | 30.5613 | 30.5438 | 30.4141 | 30.3503 | 30.2813 | 30.2068 | 30.1125 | 29.5504 | 28.5559 | 27.4043 | 26.249
|  | THE MALL | ST |  |  | 30.958 | 30.9071 | 30.8801 | 30.8465 | 30.8056 | 30.7591 | 30.7103 | 30.672 | 30.6307 | 30.4062 | 29.8552 | 29.2087 | 28.5773 | 30.3465 | 30.338 | 30.3348 | 30.3308 | 30.3259 | 30.3204 | 30.3146 | 30.3101 | 30.3051 | 30.2869 | 30.2555 | 30.2213 | 30.1324 | 30.6061 | 30.5953 | 30.5912 | 30.5861 | 30.5799 | 30.5728 | 30.5654 | 30.5596 | 30.5534 | 30.4515 | 30.0731 | 29.3176 | 28.5863
|  | THE MALL | FS |  |  | 30.9636 | 30.9303 | 30.922 | 30.9008 | 30.8762 | 30.8574 | 30.838 | 30.8143 | 30.7981 | 30.7378 | 30.6279 | 30.4327 | 30.1522 | 30.3481 | 30.3408 | 30.3398 | 30.3373 | 30.3343 | 30.3321 | 30.3298 | 30.327 | 30.325 | 30.3179 | 30.3048 | 30.2886 | 30.2714 | 30.6081 | 30.5988 | 30.5975 | 30.5943 | 30.5906 | 30.5877 | 30.5848 | 30.5812 | 30.5788 | 30.5696 | 30.5529 | 30.47 | 30.28
BRAMLEY (FLEE) | BURGHFIELD RESERVE | THEALE | MINIMUM HEADROOM | SU 64755 71015 | YES | 34.2676 | 34.2676 | 34.2676 | 34.2577 | 34.2476 | 34.2373 | 34.2267 | 34.2103 | 34.2047 | 34.1869 | 34.1726 | 34.1256 | 34.1107 | 32.1651 | 32.1625 | 32.1576 | 32.1493 | 32.1366 | 32.1236 | 32.1102 | 32.0909 | 32.0823 | 32.0559 | 32.0272 | 31.9664 | 31.8608 | 33.5832 | 33.5805 | 33.5754 | 33.5671 | 33.5544 | 33.5414 | 33.5278 | 33.5085 | 33.4998 | 33.3169 | 32.9939 | 32.6718 | 32.3628
|  | THEALE | CT |  |  | 34.2676 | 34.2676 | 34.2676 | 34.2676 | 34.2676 | 34.2676 | 34.2676 | 34.2676 | 34.2676 | 34.2676 | 34.2676 | 34.2676 | 34.2676 | 32.1651 | 32.1625 | 32.1576 | 32.1536 | 32.1498 | 32.1475 | 32.1434 | 32.1393 | 32.1348 | 32.1222 | 32.1008 | 32.0794 | 31.8887 | 33.5832 | 33.5805 | 33.5754 | 33.5713 | 33.5674 | 33.565 | 33.5609 | 33.5565 | 33.5322 | 33.3409 | 33.0178 | 32.6958 | 32.387
|  | THEALE | LW |  |  | 34.2676 | 34.2676 | 34.2676 | 34.2676 | 34.2676 | 34.2676 | 34.2676 | 34.2676 | 34.2676 | 34.2676 | 34.2676 | 34.2676 | 34.2676 | 32.1651 | 32.1625 | 32.1576 | 32.1536 | 32.1498 | 32.1459 | 32.1419 | 32.1377 | 32.1333 | 32.1206 | 32.0992 | 32.0778 | 31.8608 | 33.5832 | 33.5805 | 33.5754 | 33.5713 | 33.5674 | 33.5634 | 33.5592 | 33.5549 | 33.5083 | 33.3169 | 32.9939 | 32.6718 | 32.3628
|  | THEALE | ST |  |  | 34.2676 | 34.2676 | 34.2676 | 34.2577 | 34.2476 | 34.2373 | 34.2267 | 34.2103 | 34.2047 | 34.1869 | 34.1726 | 34.1256 | 34.1107 | 32.1662 | 32.1645 | 32.1616 | 32.1493 | 32.1366 | 32.1236 | 32.1102 | 32.0909 | 32.0823 | 32.0559 | 32.0272 | 31.9664 | 31.9383 | 33.5843 | 33.5826 | 33.5796 | 33.5671 | 33.5544 | 33.5414 | 33.5278 | 33.5085 | 33.4998 | 33.4731 | 33.2462 | 32.9908 | 32.776
|  | THEALE | FS |  |  | 34.2676 | 34.2676 | 34.2676 | 34.2676 | 34.2676 | 34.2676 | 34.2676 | 34.2676 | 34.2676 | 34.2676 | 34.2676 | 34.2676 | 34.2676 | 32.1674 | 32.1666 | 32.1653 | 32.1643 | 32.1633 | 32.1624 | 32.1615 | 32.1602 | 32.1591 | 32.1558 | 32.1502 | 32.145 | 32.1401 | 33.5856 | 33.5847 | 33.5834 | 33.5823 | 33.5814 | 33.5804 | 33.5794 | 33.5781 | 33.577 | 33.5735 | 33.5678 | 33.5624 | 33.5574
BRAMLEY (ANDO-THAT) | ANDOVER BSP | THRUXTON | MINIMUM HEADROOM | SU 29134 45674 | YES | 10.4414 | 10.1225 | 10.1159 | 10.1057 | 10.0914 | 10.0743 | 10.0524 | 10.0133 | 10.0022 | 9.9568 | 9.8581 | 9.6887 | 9.6531 | 8.7979 | 8.4821 | 8.4821 | 8.4783 | 8.4467 | 8.3868 | 8.3225 | 8.2414 | 8.1851 | 8.0057 | 7.685 | 7.2852 | 7.023 | 9.6873 | 9.3697 | 9.3658 | 9.3583 | 9.3467 | 9.3315 | 9.3116 | 9.2744 | 9.2353 | 9.0766 | 8.7567 | 8.3577 | 8.0962
|  | THRUXTON | CT |  |  | 10.4424 | 10.124 | 10.1185 | 10.1121 | 10.1046 | 10.0962 | 10.0867 | 10.0715 | 10.0645 | 10.0394 | 9.9324 | 9.8151 | 9.7612 | 8.7979 | 8.4821 | 8.4821 | 8.481 | 8.4788 | 8.448 | 8.3961 | 8.339 | 8.2867 | 8.1278 | 7.7986 | 7.4511 | 7.1706 | 9.6879 | 9.3706 | 9.3674 | 9.3631 | 9.3578 | 9.3515 | 9.344 | 9.3309 | 9.322 | 9.1985 | 8.8701 | 8.5234 | 8.2437
|  | THRUXTON | LW |  |  | 10.4414 | 10.1225 | 10.1159 | 10.1057 | 10.0914 | 10.0743 | 10.0524 | 10.0133 | 10.0022 | 9.9568 | 9.8581 | 9.6887 | 9.6531 | 8.7979 | 8.4821 | 8.4821 | 8.4783 | 8.4467 | 8.3868 | 8.3225 | 8.2414 | 8.1851 | 8.0057 | 7.685 | 7.2852 | 7.023 | 9.6873 | 9.3697 | 9.3658 | 9.3583 | 9.3467 | 9.3315 | 9.3116 | 9.2744 | 9.2353 | 9.0766 | 8.7567 | 8.3577 | 8.0962
|  | THRUXTON | ST |  |  | 10.444 | 10.4425 | 10.4398 | 10.12 | 10.1146 | 10.1089 | 10.1021 | 10.0909 | 10.0835 | 10.0526 | 10.0088 | 9.8971 | 9.8459 | 8.7979 | 8.7979 | 8.7979 | 8.4813 | 8.4797 | 8.4773 | 8.4738 | 8.4658 | 8.4443 | 8.3232 | 8.1317 | 7.8716 | 7.673 | 9.6888 | 9.6879 | 9.6864 | 9.3679 | 9.3641 | 9.3597 | 9.3543 | 9.3444 | 9.3385 | 9.3119 | 9.2023 | 8.9428 | 8.7447
|  | THRUXTON | FS |  |  | 10.4463 | 10.4461 | 10.4458 | 10.4447 | 10.4434 | 10.4422 | 10.1252 | 10.1234 | 10.1208 | 10.1094 | 10.0971 | 10.0626 | 10.0292 | 8.7979 | 8.7979 | 8.7979 | 8.7979 | 8.7978 | 8.7977 | 8.4818 | 8.4815 | 8.4802 | 8.4727 | 8.4668 | 8.4386 | 8.3604 | 9.6902 | 9.6901 | 9.6899 | 9.6893 | 9.6885 | 9.6877 | 9.3711 | 9.37 | 9.3679 | 9.3581 | 9.3485 | 9.3166 | 9.2856
MELKSHAM GSP | WEST GRAFTON | TIDWORTH | MINIMUM HEADROOM | SU 24088 49593 | YES | 23.026 | 23.026 | 23.026 | 23.0131 | 22.9996 | 22.9854 | 22.9702 | 22.8856 | 22.7897 | 22.503 | 22.0165 | 21.4942 | 20.9884 | 20.4016 | 20.3957 | 20.3872 | 20.3778 | 20.3628 | 20.3397 | 20.3155 | 20.2781 | 20.2559 | 20.1845 | 19.5172 | 18.7493 | 18.0655 | 21.3122 | 21.2897 | 21.2577 | 21.2347 | 21.2138 | 21.14 | 21.0608 | 20.9733 | 20.8965 | 20.6658 | 20.272 | 19.7142 | 18.996
|  | TIDWORTH | CT |  |  | 23.026 | 23.026 | 23.026 | 23.0215 | 23.0164 | 23.0108 | 23.0042 | 22.9589 | 22.8642 | 22.5853 | 22.0822 | 21.574 | 21.0756 | 20.4017 | 20.3958 | 20.3874 | 20.3778 | 20.3686 | 20.3585 | 20.3333 | 20.3031 | 20.2818 | 20.2173 | 19.6202 | 18.8665 | 18.1705 | 21.3124 | 21.29 | 21.2583 | 21.2347 | 21.2138 | 21.1914 | 21.1142 | 21.0324 | 20.9569 | 20.734 | 20.3236 | 19.8368 | 19.1063
|  | TIDWORTH | LW |  |  | 23.026 | 23.026 | 23.026 | 23.024 | 23.0201 | 23.0138 | 22.9914 | 22.8856 | 22.7897 | 22.503 | 22.0165 | 21.4942 | 20.9884 | 20.4016 | 20.3957 | 20.3872 | 20.3802 | 20.372 | 20.3472 | 20.3199 | 20.284 | 20.2615 | 20.1893 | 19.5172 | 18.7493 | 18.0655 | 21.3122 | 21.2897 | 21.2577 | 21.2364 | 21.2164 | 21.14 | 21.0608 | 20.9733 | 20.8965 | 20.6658 | 20.272 | 19.7142 | 18.996
|  | TIDWORTH | ST |  |  | 23.026 | 23.026 | 23.026 | 23.0131 | 22.9996 | 22.9854 | 22.9702 | 22.9454 | 22.9364 | 22.7286 | 22.3968 | 21.9996 | 21.6781 | 20.4042 | 20.4003 | 20.3953 | 20.3793 | 20.3628 | 20.3397 | 20.3155 | 20.2781 | 20.2559 | 20.1845 | 20.0899 | 19.5828 | 19.1055 | 21.3222 | 21.3071 | 21.2884 | 21.2635 | 21.2387 | 21.1909 | 21.1418 | 21.0692 | 21.0098 | 20.8313 | 20.5614 | 20.224 | 19.9614
|  | TIDWORTH | FS |  |  | 23.026 | 23.026 | 23.026 | 23.0248 | 23.0236 | 23.0223 | 23.0211 | 23.019 | 23.0132 | 22.993 | 22.9822 | 22.8563 | 22.7225 | 20.4071 | 20.405 | 20.4029 | 20.4005 | 20.3984 | 20.3944 | 20.3904 | 20.3848 | 20.3738 | 20.3388 | 20.3039 | 20.2426 | 20.1872 | 21.3329 | 21.325 | 21.317 | 21.3115 | 21.3068 | 21.2951 | 21.2833 | 21.268 | 21.2426 | 21.1661 | 21.0641 | 20.9409 | 20.8275
MANNINGTON GSP | SHAFTESBURY BSP | TISBURY | MINIMUM HEADROOM | ST 93438 29127 | YES | 12.3956 | 12.3902 | 12.3786 | 12.3674 | 12.3562 | 12.3077 | 12.2597 | 12.2121 | 12.1608 | 12.0094 | 11.761 | 11.5048 | 11.2529 | 11.0481 | 11.0422 | 11.0295 | 11.0172 | 11.005 | 10.952 | 10.8994 | 10.8474 | 10.7877 | 10.61 | 10.3182 | 10.0174 | 9.7217 | 11.7068 | 11.7019 | 11.6915 | 11.6814 | 11.6714 | 11.6279 | 11.5848 | 11.5371 | 11.4855 | 11.3333 | 11.0833 | 10.8256 | 10.5545
|  | TISBURY | CT |  |  | 12.3956 | 12.3902 | 12.3786 | 12.3674 | 12.3562 | 12.3451 | 12.2972 | 12.2496 | 12.1982 | 12.0469 | 11.7982 | 11.5422 | 11.2904 | 11.0481 | 11.0422 | 11.0295 | 11.0172 | 11.005 | 10.9928 | 10.9404 | 10.8884 | 10.8316 | 10.6539 | 10.362 | 10.0614 | 9.7658 | 11.7068 | 11.7019 | 11.6915 | 11.6814 | 11.6714 | 11.6614 | 11.6184 | 11.5748 | 11.5231 | 11.3709 | 11.1208 | 10.8632 | 10.5985
|  | TISBURY | LW |  |  | 12.3956 | 12.3902 | 12.3786 | 12.3674 | 12.3562 | 12.3077 | 12.2597 | 12.2121 | 12.1608 | 12.0094 | 11.761 | 11.5048 | 11.2529 | 11.0481 | 11.0422 | 11.0295 | 11.0172 | 11.005 | 10.952 | 10.8994 | 10.8474 | 10.7877 | 10.61 | 10.3182 | 10.0174 | 9.7217 | 11.7068 | 11.7019 | 11.6915 | 11.6814 | 11.6714 | 11.6279 | 11.5848 | 11.5371 | 11.4855 | 11.3333 | 11.0833 | 10.8256 | 10.5545
|  | TISBURY | ST |  |  | 12.3993 | 12.3962 | 12.391 | 12.3846 | 12.3769 | 12.3465 | 12.3163 | 12.2838 | 12.2488 | 12.1468 | 11.9815 | 11.8166 | 11.6526 | 11.0521 | 11.0488 | 11.0431 | 11.0361 | 11.0277 | 10.9943 | 10.9614 | 10.9258 | 10.8875 | 10.7712 | 10.5772 | 10.3835 | 10.191 | 11.71 | 11.7073 | 11.7026 | 11.6969 | 11.69 | 11.6626 | 11.6356 | 11.6064 | 11.5741 | 11.4714 | 11.3052 | 11.1393 | 10.9743
|  | TISBURY | FS |  |  | 12.4042 | 12.4038 | 12.4034 | 12.4016 | 12.3996 | 12.3896 | 12.3798 | 12.3667 | 12.3532 | 12.3138 | 12.2513 | 12.1917 | 12.1356 | 11.0575 | 11.057 | 11.0566 | 11.0547 | 11.0524 | 11.0415 | 11.0308 | 11.0165 | 11.0017 | 10.9586 | 10.8902 | 10.8239 | 10.758 | 11.7144 | 11.7141 | 11.7137 | 11.7121 | 11.7103 | 11.7013 | 11.6926 | 11.6808 | 11.6686 | 11.6333 | 11.5765 | 11.5166 | 11.4601
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | TITCHFIELD | MINIMUM HEADROOM | SU 54104 05695 | YES | 22.4224 | 22.4224 | 22.4224 | 22.4212 | 22.4189 | 22.4152 | 22.4101 | 22.3998 | 22.398 | 21.8677 | 20.6869 | 19.9486 | 19.2937 | 20.797 | 20.6605 | 20.4527 | 20.234 | 19.9918 | 19.6967 | 19.3666 | 18.9968 | 18.6066 | 17.2029 | 15.8285 | 14.9651 | 14.1931 | 21.7984 | 21.7984 | 21.7984 | 21.7973 | 21.795 | 21.73 | 21.3941 | 21.018 | 20.6233 | 19.2223 | 17.8516 | 16.9992 | 16.2375
|  | TITCHFIELD | CT |  |  | 22.4224 | 22.4224 | 22.4224 | 22.422 | 22.4214 | 22.4204 | 22.419 | 22.4159 | 22.4153 | 21.971 | 20.7878 | 20.0651 | 19.4054 | 20.8061 | 20.6745 | 20.4774 | 20.2698 | 20.0394 | 19.7934 | 19.4669 | 19.1043 | 18.7171 | 17.3195 | 15.9435 | 15.096 | 14.3193 | 21.7984 | 21.7984 | 21.7984 | 21.7981 | 21.7974 | 21.7965 | 21.496 | 21.1271 | 20.7335 | 19.3387 | 17.9655 | 17.1288 | 16.3623
|  | TITCHFIELD | LW |  |  | 22.4224 | 22.4224 | 22.4224 | 22.4212 | 22.4189 | 22.4152 | 22.4101 | 22.3998 | 22.398 | 21.8677 | 20.6869 | 19.9486 | 19.2937 | 20.797 | 20.6605 | 20.4527 | 20.234 | 19.9918 | 19.6967 | 19.3666 | 18.9968 | 18.6066 | 17.2029 | 15.8285 | 14.9651 | 14.1931 | 21.7984 | 21.7984 | 21.7984 | 21.7973 | 21.795 | 21.73 | 21.3941 | 21.018 | 20.6233 | 19.2223 | 17.8516 | 16.9992 | 16.2375
|  | TITCHFIELD | ST |  |  | 22.4224 | 22.4224 | 22.4224 | 22.4221 | 22.4217 | 22.4209 | 22.4199 | 22.4175 | 22.4163 | 22.4101 | 22.1446 | 21.6658 | 21.2326 | 20.9309 | 20.7881 | 20.6842 | 20.5639 | 20.4196 | 20.2057 | 19.9696 | 19.7253 | 19.4593 | 18.4796 | 17.5237 | 16.97 | 16.4664 | 21.7984 | 21.7984 | 21.7984 | 21.7982 | 21.7977 | 21.797 | 21.7959 | 21.7589 | 21.4883 | 20.4965 | 19.5425 | 18.9899 | 18.4873
|  | TITCHFIELD | FS |  |  | 22.4224 | 22.4224 | 22.4224 | 22.4224 | 22.4224 | 22.4223 | 22.4223 | 22.4222 | 22.4218 | 22.4196 | 22.4178 | 22.4093 | 22.401 | 20.9797 | 20.8742 | 20.8285 | 20.771 | 20.7071 | 20.6226 | 20.5314 | 20.4231 | 20.318 | 19.9321 | 19.5605 | 19.3562 | 19.1725 | 21.7984 | 21.7984 | 21.7984 | 21.7984 | 21.7984 | 21.7984 | 21.7983 | 21.7982 | 21.7979 | 21.7956 | 21.5913 | 21.3835 | 21.1968
BRAMLEY (FLEE) | ALDERSHOT BSP | TONGHAM | MINIMUM HEADROOM | SU 88310 49487 | YES | 42.9047 | 42.9047 | 42.9047 | 42.9041 | 42.9029 | 42.9009 | 42.8983 | 42.8929 | 42.8919 | 42.8872 | 42.8756 | 42.8531 | 41.7334 | 40.5545 | 40.5515 | 40.547 | 40.5415 | 40.5354 | 40.5217 | 40.508 | 40.4918 | 40.4796 | 40.4402 | 40.3567 | 38.8639 | 37.1632 | 42.2003 | 42.1968 | 42.1915 | 42.1851 | 42.1781 | 42.1622 | 42.1464 | 42.1282 | 42.1139 | 42.0682 | 40.9428 | 39.1815 | 37.4509
|  | TONGHAM | CT |  |  | 42.9047 | 42.9047 | 42.9047 | 42.9045 | 42.9042 | 42.9037 | 42.9029 | 42.9013 | 42.901 | 42.8995 | 42.8866 | 42.8723 | 41.8789 | 40.5546 | 40.5517 | 40.5472 | 40.5422 | 40.5371 | 40.5317 | 40.5199 | 40.5075 | 40.4959 | 40.4597 | 40.3749 | 39.0323 | 37.3293 | 42.2004 | 42.197 | 42.1917 | 42.1858 | 42.1798 | 42.1735 | 42.1596 | 42.1452 | 42.1316 | 42.089 | 41.1053 | 39.3525 | 37.6197
|  | TONGHAM | LW |  |  | 42.9047 | 42.9047 | 42.9047 | 42.9041 | 42.9029 | 42.9009 | 42.8983 | 42.8929 | 42.8919 | 42.8872 | 42.8756 | 42.8531 | 41.7334 | 40.5545 | 40.5515 | 40.547 | 40.5415 | 40.5354 | 40.5217 | 40.508 | 40.4918 | 40.4796 | 40.4402 | 40.3567 | 38.8639 | 37.1632 | 42.2003 | 42.1968 | 42.1915 | 42.1851 | 42.1781 | 42.1622 | 42.1464 | 42.1282 | 42.1139 | 42.0682 | 40.9428 | 39.1815 | 37.4509
|  | TONGHAM | ST |  |  | 42.9047 | 42.9047 | 42.9047 | 42.9046 | 42.9043 | 42.9039 | 42.9034 | 42.9021 | 42.9015 | 42.8983 | 42.894 | 42.8791 | 42.8737 | 40.5557 | 40.5537 | 40.551 | 40.5477 | 40.5439 | 40.5367 | 40.5299 | 40.5213 | 40.513 | 40.4861 | 40.4326 | 40.3634 | 39.5733 | 42.2017 | 42.1994 | 42.1963 | 42.1923 | 42.1878 | 42.1794 | 42.1714 | 42.1615 | 42.1517 | 42.1205 | 42.0579 | 41.015 | 39.903
|  | TONGHAM | FS |  |  | 42.9047 | 42.9047 | 42.9047 | 42.9047 | 42.9047 | 42.9047 | 42.9046 | 42.9046 | 42.9044 | 42.9032 | 42.9023 | 42.8978 | 42.8935 | 40.5575 | 40.5566 | 40.5558 | 40.5546 | 40.5533 | 40.551 | 40.5489 | 40.5463 | 40.5431 | 40.5328 | 40.5121 | 40.4844 | 40.4563 | 42.2039 | 42.2028 | 42.2019 | 42.2004 | 42.1989 | 42.1962 | 42.1937 | 42.1907 | 42.1869 | 42.1749 | 42.1506 | 42.1186 | 42.086
MINETY GSP | TOOTHILL BSP | TOOTHILL | MINIMUM HEADROOM | SU 13215 83986 | YES | 44.4273 | 44.4238 | 44.4187 | 44.3875 | 44.3548 | 44.3213 | 44.2781 | 44.2188 | 44.1992 | 44.143 | 43.9813 | 42.8887 | 41.8172 | 41.8285 | 41.822 | 41.8126 | 41.7768 | 41.7385 | 41.699 | 41.6427 | 41.5695 | 41.5378 | 41.3599 | 40.3902 | 39.0435 | 37.7897 | 43.6896 | 43.6521 | 43.5981 | 43.5139 | 43.4181 | 43.3127 | 43.125 | 42.9072 | 42.7508 | 42.3225 | 41.4269 | 40.4022 | 39.3903
|  | TOOTHILL | CT |  |  | 44.4274 | 44.4239 | 44.4188 | 44.3875 | 44.3548 | 44.3213 | 44.2781 | 44.2188 | 44.1992 | 44.143 | 43.9813 | 42.8887 | 41.8172 | 41.8287 | 41.8222 | 41.8129 | 41.7768 | 41.7385 | 41.699 | 41.6427 | 41.5695 | 41.5378 | 41.3599 | 40.3902 | 39.0435 | 37.7897 | 43.6902 | 43.6531 | 43.5998 | 43.5139 | 43.4181 | 43.3171 | 43.125 | 42.9072 | 42.7508 | 42.3225 | 41.4269 | 40.4022 | 39.3903
|  | TOOTHILL | LW |  |  | 44.4273 | 44.4238 | 44.4187 | 44.4129 | 44.4063 | 44.3918 | 44.3762 | 44.3597 | 44.3455 | 44.3067 | 44.2127 | 43.1538 | 42.1059 | 41.8285 | 41.822 | 41.8126 | 41.802 | 41.7897 | 41.7629 | 41.7343 | 41.7038 | 41.6702 | 41.4965 | 40.5353 | 39.2922 | 38.0618 | 43.6896 | 43.6521 | 43.5981 | 43.5371 | 43.4667 | 43.3127 | 43.1483 | 42.9732 | 42.8222 | 42.4114 | 41.601 | 40.6797 | 39.6624
|  | TOOTHILL | ST |  |  | 44.4708 | 44.4267 | 44.4239 | 44.4204 | 44.4162 | 44.4076 | 44.3984 | 44.3872 | 44.3775 | 44.3509 | 44.2983 | 44.2413 | 43.678 | 41.9088 | 41.8273 | 41.8222 | 41.8158 | 41.808 | 41.7922 | 41.7752 | 41.7546 | 41.7365 | 41.6875 | 41.4589 | 40.6938 | 39.9076 | 43.9022 | 43.6827 | 43.6529 | 43.6164 | 43.5716 | 43.4808 | 43.3831 | 43.2647 | 43.1613 | 42.8794 | 42.3225 | 41.7184 | 41.1357
|  | TOOTHILL | FS |  |  | 44.4768 | 44.4289 | 44.4276 | 44.4259 | 44.424 | 44.4209 | 44.4176 | 44.4137 | 44.4099 | 44.3995 | 44.3783 | 44.3536 | 44.3284 | 41.9199 | 41.8315 | 41.829 | 41.8259 | 41.8224 | 41.8167 | 41.8107 | 41.8035 | 41.7964 | 41.7773 | 41.7382 | 41.6925 | 41.5936 | 43.9134 | 43.7063 | 43.6923 | 43.6747 | 43.6546 | 43.6218 | 43.5871 | 43.5455 | 43.505 | 43.3951 | 43.1705 | 42.9084 | 42.6411
NURSLING GSP | ROWNHAMS | TOTTON | MINIMUM HEADROOM | SU 35835 13428 | YES | 25.8574 | 25.8464 | 25.1771 | 25.1027 | 25.0276 | 24.9517 | 24.875 | 24.7843 | 24.7 | 24.4325 | 24.194 | 23.5069 | 23.2602 | 28.8489 | 28.8222 | 28.1204 | 28.0141 | 27.9027 | 27.7231 | 27.5313 | 27.3029 | 27.0184 | 25.7887 | 24.0284 | 22.7456 | 21.4773 | 30.7507 | 30.7397 | 30.0704 | 29.996 | 29.921 | 29.8451 | 29.7684 | 29.6777 | 29.5934 | 29.3259 | 28.1394 | 26.9287 | 25.7164
|  | TOTTON | CT |  |  | 25.9144 | 25.9078 | 25.5062 | 25.4733 | 25.4404 | 25.4075 | 25.3746 | 25.3417 | 25.3285 | 25.289 | 24.8088 | 24.6394 | 24.5187 | 28.9089 | 28.8882 | 28.4576 | 28.3962 | 28.3301 | 28.259 | 28.1144 | 27.9643 | 27.7399 | 26.5523 | 24.4451 | 23.1182 | 21.8538 | 30.8078 | 30.8012 | 30.3996 | 30.3667 | 30.3338 | 30.3008 | 30.2679 | 30.235 | 30.2218 | 30.1823 | 28.5466 | 27.2917 | 26.0906
|  | TOTTON | LW |  |  | 25.8574 | 25.8464 | 25.1771 | 25.1027 | 25.0276 | 24.9517 | 24.875 | 24.787 | 24.7604 | 24.6789 | 24.5456 | 24.4204 | 24.2963 | 28.8489 | 28.8222 | 28.1204 | 28.0141 | 27.9027 | 27.7231 | 27.5313 | 27.3029 | 27.0184 | 25.7887 | 24.0284 | 22.7456 | 21.4773 | 30.7507 | 30.7397 | 30.0704 | 29.996 | 29.921 | 29.8451 | 29.7684 | 29.6803 | 29.6538 | 29.5722 | 28.1394 | 26.9287 | 25.7164
|  | TOTTON | ST |  |  | 25.9429 | 25.9386 | 25.6708 | 25.5145 | 25.3561 | 25.1948 | 25.0289 | 24.7843 | 24.7 | 24.4325 | 24.194 | 23.5069 | 23.2602 | 29.1124 | 28.9079 | 28.6123 | 28.4217 | 28.2188 | 28.0035 | 27.7757 | 27.4513 | 27.271 | 26.2033 | 24.8315 | 23.3935 | 22.4079 | 30.8363 | 30.8319 | 30.5642 | 30.4079 | 30.2494 | 30.0882 | 29.9223 | 29.6777 | 29.5934 | 29.3259 | 28.8541 | 27.4794 | 26.5397
|  | TOTTON | FS |  |  | 25.9715 | 25.9693 | 25.8354 | 25.8244 | 25.8135 | 25.8025 | 25.7915 | 25.7806 | 25.7762 | 25.763 | 25.7411 | 25.7279 | 25.7037 | 29.1575 | 28.9829 | 28.8475 | 28.8311 | 28.8123 | 28.7865 | 28.7604 | 28.7307 | 28.6966 | 28.533 | 28.2324 | 27.9261 | 27.6145 | 30.8648 | 30.8626 | 30.7288 | 30.7178 | 30.7068 | 30.6959 | 30.6849 | 30.6739 | 30.6695 | 30.6564 | 30.6344 | 30.6212 | 30.5971
BOTLEY WOOD GSP | NETLEY COMMON BSP | TOWNHILL PARK | MINIMUM HEADROOM | SU 45156 14783 | YES | 45.8547 | 45.8547 | 45.8547 | 45.8547 | 45.8547 | 45.8541 | 45.8527 | 45.8495 | 45.8489 | 45.8453 | 45.8301 | 43.8505 | 41.8535 | 42.0324 | 42.0324 | 42.0324 | 42.0324 | 42.0324 | 42.0317 | 42.0304 | 42.0272 | 42.0265 | 42.0229 | 40.1243 | 37.7892 | 35.4733 | 43.7369 | 43.7369 | 43.7369 | 43.7369 | 43.7369 | 43.7363 | 43.735 | 43.7317 | 43.7311 | 43.4558 | 41.4935 | 39.15 | 36.8258
|  | TOWNHILL PARK | CT |  |  | 45.8547 | 45.8547 | 45.8547 | 45.8547 | 45.8547 | 45.8547 | 45.8538 | 45.8511 | 45.8507 | 45.8485 | 45.8301 | 44.1538 | 42.1508 | 42.0324 | 42.0324 | 42.0324 | 42.0324 | 42.0324 | 42.0324 | 42.0314 | 42.0288 | 42.0284 | 42.0261 | 40.4846 | 38.1431 | 35.8213 | 43.7369 | 43.7369 | 43.7369 | 43.7369 | 43.7369 | 43.7369 | 43.736 | 43.7334 | 43.7329 | 43.7307 | 41.8551 | 39.5052 | 37.1751
|  | TOWNHILL PARK | LW |  |  | 45.8547 | 45.8547 | 45.8547 | 45.8547 | 45.8547 | 45.8541 | 45.8527 | 45.8495 | 45.8489 | 45.8453 | 45.8365 | 43.8505 | 41.8535 | 42.0324 | 42.0324 | 42.0324 | 42.0324 | 42.0324 | 42.0317 | 42.0304 | 42.0272 | 42.0265 | 42.0229 | 40.1243 | 37.7892 | 35.4733 | 43.7369 | 43.7369 | 43.7369 | 43.7369 | 43.7369 | 43.7363 | 43.735 | 43.7317 | 43.7311 | 43.4558 | 41.4935 | 39.15 | 36.8258
|  | TOWNHILL PARK | ST |  |  | 45.8547 | 45.8547 | 45.8547 | 45.8547 | 45.8547 | 45.8545 | 45.8542 | 45.8532 | 45.8528 | 45.851 | 45.8488 | 45.8405 | 45.0314 | 42.0324 | 42.0324 | 42.0324 | 42.0324 | 42.0324 | 42.0322 | 42.0318 | 42.0309 | 42.0305 | 42.0287 | 42.0264 | 40.6388 | 39.1556 | 43.7369 | 43.7369 | 43.7369 | 43.7369 | 43.7369 | 43.7368 | 43.7364 | 43.7354 | 43.735 | 43.7332 | 43.5028 | 42.0098 | 40.5213
|  | TOWNHILL PARK | FS |  |  | 45.8547 | 45.8547 | 45.8547 | 45.8547 | 45.8547 | 45.8547 | 45.8547 | 45.8547 | 45.8545 | 45.8537 | 45.8532 | 45.8512 | 45.8495 | 42.0324 | 42.0324 | 42.0324 | 42.0324 | 42.0324 | 42.0324 | 42.0324 | 42.0323 | 42.0322 | 42.0314 | 42.0308 | 42.0289 | 42.0272 | 43.7369 | 43.7369 | 43.7369 | 43.7369 | 43.7369 | 43.7369 | 43.7369 | 43.7369 | 43.7367 | 43.7359 | 43.7354 | 43.7334 | 43.7317
MINETY GSP | SWINDON BSP | TRADING ESTATE | MINIMUM HEADROOM | SU 13490 85868 | YES | 23.6552 | 11.0023 | 9.7992 | 9.6976 | 9.5959 | 9.4904 | 9.3849 | 9.2794 | 9.2324 | 9.0906 | 8.8437 | 8.5965 | 8.052 | 23.113 | 10.46 | 9.2567 | 9.1549 | 9.0531 | 8.9471 | 8.8412 | 8.7353 | 8.6879 | 8.5446 | 8.2946 | 8.0441 | 7.2885 | 22.6951 | 10.0332 | 8.8121 | 8.6926 | 8.5727 | 8.4279 | 8.283 | 8.1381 | 8.0491 | 7.7761 | 7.2521 | 6.3678 | 5.3633
|  | TRADING ESTATE | CT |  |  | 23.7575 | 11.1124 | 10.3892 | 10.3213 | 10.2532 | 10.185 | 10.1127 | 10.0371 | 10.0046 | 9.9061 | 8.9773 | 8.5965 | 8.052 | 23.2153 | 10.5702 | 9.8468 | 9.7787 | 9.7104 | 9.642 | 9.5692 | 9.4932 | 9.4603 | 9.3603 | 8.4285 | 8.0441 | 7.2885 | 22.7974 | 10.1433 | 9.4022 | 9.3164 | 9.23 | 9.1435 | 9.0318 | 8.9168 | 8.8422 | 8.6126 | 7.4067 | 6.3678 | 5.3633
|  | TRADING ESTATE | LW |  |  | 23.6552 | 11.0023 | 9.7992 | 9.6976 | 9.5959 | 9.4904 | 9.3849 | 9.2794 | 9.2324 | 9.0906 | 8.8437 | 8.6669 | 8.094 | 23.113 | 10.46 | 9.2567 | 9.1549 | 9.0531 | 8.9471 | 8.8412 | 8.7353 | 8.6879 | 8.5446 | 8.2946 | 8.112 | 7.3169 | 22.6951 | 10.0332 | 8.8121 | 8.6926 | 8.5727 | 8.4279 | 8.283 | 8.1381 | 8.0491 | 7.7761 | 7.2521 | 6.3911 | 5.3908
|  | TRADING ESTATE | ST |  |  | 23.8096 | 23.8008 | 23.3193 | 10.6465 | 10.6049 | 10.5619 | 10.5189 | 10.4747 | 10.4538 | 10.3904 | 10.2774 | 10.1917 | 10.0675 | 23.2675 | 23.2586 | 22.7771 | 10.1042 | 10.0624 | 10.0192 | 9.976 | 9.9315 | 9.9102 | 9.8459 | 9.7308 | 9.6428 | 9.5164 | 22.8551 | 22.841 | 22.3511 | 9.6679 | 9.6138 | 9.5508 | 9.4877 | 9.4167 | 9.367 | 9.2146 | 8.9123 | 8.6146 | 8.0853
|  | TRADING ESTATE | FS |  |  | 23.862 | 23.8579 | 23.6177 | 23.5975 | 23.5771 | 23.5564 | 10.9042 | 10.8832 | 10.8733 | 10.8435 | 10.7905 | 10.7505 | 10.6903 | 23.32 | 23.3159 | 23.0757 | 23.0554 | 23.035 | 23.0143 | 10.3619 | 10.3409 | 10.3309 | 10.3007 | 10.2469 | 10.2059 | 10.1446 | 22.9147 | 22.9094 | 22.668 | 22.6446 | 22.6205 | 22.5942 | 9.9363 | 9.9084 | 9.8874 | 9.8233 | 9.6951 | 9.5644 | 9.4109
BRAMLEY (FLEE) | BURGHFIELD RESERVE | TRASH GREEN | MINIMUM HEADROOM | SU 66254 68745 | YES | 22.21 | 22.21 | 22.21 | 22.1395 | 22.0629 | 21.9789 | 21.8875 | 21.7406 | 21.7191 | 21.6357 | 21.4834 | 21.2043 | 20.7802 | 20.3178 | 20.1702 | 19.8871 | 19.5333 | 19.1681 | 18.9811 | 18.7894 | 18.5404 | 18.4073 | 18.007 | 17.343 | 16.561 | 16.0628 | 21.7156 | 21.6183 | 21.4317 | 21.1745 | 20.9077 | 20.7558 | 20.5983 | 20.3841 | 20.2891 | 19.9969 | 19.3509 | 18.5698 | 18.0725
|  | TRASH GREEN | CT |  |  | 22.21 | 22.21 | 22.21 | 22.2089 | 22.2068 | 22.2036 | 22.1991 | 22.1889 | 22.1871 | 22.1774 | 22.0975 | 21.8604 | 21.4265 | 20.3178 | 20.1702 | 19.8871 | 19.5785 | 19.281 | 19.0323 | 18.9276 | 18.8153 | 18.7018 | 18.3754 | 17.7836 | 17.1904 | 16.6828 | 21.7156 | 21.6183 | 21.4317 | 21.228 | 21.0311 | 20.8662 | 20.7956 | 20.7181 | 20.6427 | 20.3826 | 19.7917 | 19.1995 | 18.6929
|  | TRASH GREEN | LW |  |  | 22.21 | 22.21 | 22.21 | 22.1395 | 22.0629 | 21.9789 | 21.8875 | 21.7406 | 21.7191 | 21.6357 | 21.4834 | 21.2043 | 20.7802 | 20.3243 | 20.1801 | 19.9042 | 19.5333 | 19.1681 | 18.9811 | 18.7894 | 18.5404 | 18.4073 | 18.007 | 17.343 | 16.561 | 16.0628 | 21.7199 | 21.6248 | 21.443 | 21.1745 | 20.9077 | 20.7558 | 20.5983 | 20.3841 | 20.2891 | 19.9969 | 19.3509 | 18.5698 | 18.0725
|  | TRASH GREEN | ST |  |  | 22.21 | 22.21 | 22.21 | 22.2092 | 22.2077 | 22.2053 | 22.2018 | 22.194 | 22.1902 | 22.1701 | 22.1436 | 22.0507 | 22.017 | 20.4242 | 20.3467 | 20.2267 | 20.0633 | 19.8818 | 19.796 | 19.7115 | 19.6341 | 19.5542 | 19.3189 | 18.9491 | 18.5307 | 18.1847 | 21.7857 | 21.7346 | 21.6555 | 21.5476 | 21.4274 | 21.3701 | 21.3132 | 21.2595 | 21.2056 | 21.0436 | 20.7909 | 20.4835 | 20.192
|  | TRASH GREEN | FS |  |  | 22.21 | 22.21 | 22.21 | 22.207 | 22.204 | 22.201 | 22.1978 | 22.1928 | 22.1786 | 22.1301 | 22.1047 | 22.0152 | 21.9365 | 20.5172 | 20.4938 | 20.4702 | 20.4035 | 20.3354 | 20.302 | 20.2695 | 20.2271 | 20.1832 | 20.0514 | 19.8945 | 19.6845 | 19.4968 | 21.847 | 21.8316 | 21.816 | 21.771 | 21.7251 | 21.7021 | 21.6796 | 21.65 | 21.6162 | 21.5127 | 21.4007 | 21.2318 | 21.0812
MELKSHAM GSP | NORRINGTON | TROWBRIDGE TOWN | MINIMUM HEADROOM | ST 84668 58036 | YES | 37.3337 | 37.3205 | 36.6544 | 36.5936 | 36.5311 | 36.4572 | 36.3812 | 36.2975 | 36.2582 | 36.135 | 35.9181 | 35.7092 | 34.8357 | 34.9166 | 34.9038 | 34.2387 | 34.1789 | 34.1173 | 34.0461 | 33.9729 | 33.8919 | 33.8554 | 33.7409 | 33.5386 | 32.4142 | 31.1993 | 35.5168 | 35.506 | 34.8448 | 34.7889 | 34.7311 | 34.6713 | 34.6094 | 34.5396 | 34.5152 | 34.4365 | 33.5523 | 32.378 | 31.2252
|  | TROWBRIDGE TOWN | CT |  |  | 37.3902 | 37.3815 | 36.9801 | 36.9425 | 36.9045 | 36.8659 | 36.8173 | 36.7662 | 36.7373 | 36.6494 | 36.0629 | 35.7754 | 35.0041 | 34.9731 | 34.9648 | 34.5643 | 34.5276 | 34.4904 | 34.4528 | 34.4069 | 34.3585 | 34.3325 | 34.2532 | 33.6813 | 32.6198 | 31.3969 | 35.5732 | 35.5667 | 35.17 | 35.1369 | 35.1034 | 35.0695 | 35.0348 | 34.9976 | 34.9837 | 34.9402 | 33.8279 | 32.575 | 31.4143
|  | TROWBRIDGE TOWN | LW |  |  | 37.3337 | 37.3205 | 36.6544 | 36.5936 | 36.5311 | 36.4572 | 36.3812 | 36.2975 | 36.2582 | 36.135 | 35.9181 | 35.7092 | 34.8357 | 34.9166 | 34.9038 | 34.2387 | 34.1789 | 34.1173 | 34.0461 | 33.9729 | 33.8919 | 33.8554 | 33.7409 | 33.5386 | 32.4142 | 31.1993 | 35.5168 | 35.506 | 34.8448 | 34.7889 | 34.7311 | 34.6713 | 34.6094 | 34.5396 | 34.5152 | 34.4365 | 33.5523 | 32.378 | 31.2252
|  | TROWBRIDGE TOWN | ST |  |  | 37.4424 | 37.4136 | 37.1467 | 37.1185 | 37.0893 | 37.0557 | 37.0216 | 36.9817 | 36.9594 | 36.8885 | 36.7784 | 36.6459 | 36.5286 | 35.0206 | 34.9966 | 34.7301 | 34.7026 | 34.6741 | 34.642 | 34.6093 | 34.5713 | 34.5509 | 34.4859 | 34.3855 | 34.2629 | 33.8428 | 35.6013 | 35.597 | 35.3326 | 35.3075 | 35.282 | 35.256 | 35.2294 | 35.1991 | 35.1869 | 35.1461 | 35.086 | 34.5035 | 33.7692
|  | TROWBRIDGE TOWN | FS |  |  | 37.4729 | 37.4477 | 37.3152 | 37.3036 | 37.2918 | 37.2787 | 37.2655 | 37.2517 | 37.2428 | 37.2148 | 37.1714 | 37.1267 | 37.0723 | 35.0507 | 35.0299 | 34.8975 | 34.886 | 34.8744 | 34.8617 | 34.849 | 34.8357 | 34.8276 | 34.8019 | 34.7622 | 34.7211 | 34.6702 | 35.6295 | 35.6274 | 35.4951 | 35.4843 | 35.4734 | 35.4625 | 35.4516 | 35.4406 | 35.4357 | 35.4193 | 35.395 | 35.3691 | 35.3327
BRAMLEY (FLEE) | READING BSP | TWYFORD | MINIMUM HEADROOM | SU 78430 76339 | YES | 23.9411 | 23.9411 | 23.9411 | 23.94 | 23.9378 | 23.9344 | 23.9297 | 23.9203 | 23.9187 | 23.9103 | 23.8901 | 23.2511 | 22.5314 | 21.5423 | 21.5423 | 21.5423 | 21.5413 | 21.5391 | 21.321 | 21.1691 | 21.0168 | 20.8552 | 20.3755 | 19.5503 | 18.686 | 17.8518 | 22.0303 | 22.0175 | 21.9905 | 21.964 | 21.9375 | 21.911 | 21.7837 | 21.6407 | 21.4891 | 21.0391 | 20.2489 | 19.3863 | 18.5538
|  | TWYFORD | CT |  |  | 23.9411 | 23.9411 | 23.9411 | 23.9407 | 23.9401 | 23.9393 | 23.938 | 23.9351 | 23.9346 | 23.9319 | 23.9094 | 23.2511 | 22.5314 | 21.5423 | 21.5423 | 21.5423 | 21.542 | 21.5414 | 21.321 | 21.1691 | 21.0168 | 20.8552 | 20.3755 | 19.5503 | 18.686 | 17.8518 | 22.0303 | 22.0175 | 21.9905 | 21.964 | 21.9375 | 21.911 | 21.7837 | 21.6407 | 21.4891 | 21.0391 | 20.2489 | 19.3863 | 18.5538
|  | TWYFORD | LW |  |  | 23.9411 | 23.9411 | 23.9411 | 23.94 | 23.9378 | 23.9344 | 23.9297 | 23.9203 | 23.9187 | 23.9103 | 23.8901 | 23.8506 | 23.1629 | 21.5423 | 21.5423 | 21.5423 | 21.5413 | 21.5391 | 21.5357 | 21.531 | 21.5215 | 21.5199 | 21.1207 | 20.298 | 19.419 | 18.5895 | 22.036 | 22.0264 | 22.006 | 21.9852 | 21.9635 | 21.9512 | 21.9376 | 21.9194 | 21.9083 | 21.7366 | 20.9638 | 20.1178 | 19.2898
|  | TWYFORD | ST |  |  | 23.9411 | 23.9411 | 23.9411 | 23.9408 | 23.9404 | 23.9397 | 23.9387 | 23.9365 | 23.9355 | 23.9298 | 23.9224 | 23.8962 | 23.8867 | 21.5423 | 21.5423 | 21.5423 | 21.5421 | 21.5416 | 21.541 | 21.54 | 21.5378 | 21.5367 | 21.5311 | 21.4386 | 20.8707 | 20.3238 | 22.0414 | 22.0355 | 22.0254 | 22.0129 | 21.9975 | 21.9895 | 21.9812 | 21.973 | 21.9654 | 21.9409 | 21.902 | 21.5013 | 20.9879
|  | TWYFORD | FS |  |  | 23.9411 | 23.9411 | 23.9411 | 23.941 | 23.941 | 23.941 | 23.941 | 23.9409 | 23.9405 | 23.9385 | 23.9368 | 23.929 | 23.9214 | 21.5423 | 21.5423 | 21.5423 | 21.5423 | 21.5423 | 21.5423 | 21.5422 | 21.5421 | 21.5418 | 21.5397 | 21.5381 | 21.5303 | 21.5227 | 22.0512 | 22.0505 | 22.0498 | 22.0467 | 22.043 | 22.0403 | 22.0376 | 22.0342 | 22.0313 | 22.0219 | 22.0083 | 21.9888 | 21.9699
COWLEY GSP | COWLEY LOCAL (2 X 90) | UNION STREET | MINIMUM HEADROOM | SP 52865 05849 | NO | 31.9184 | 31.9035 | 30.992 | 30.9173 | 30.8426 | 30.7679 | 30.6932 | 30.6069 | 30.4446 | 29.855 | 28.5709 | 27.1567 | 25.6733 | 29.1856 | 29.1631 | 28.2326 | 28.1061 | 27.9311 | 27.7987 | 27.6651 | 27.4154 | 27.1895 | 26.4728 | 24.9912 | 23.3465 | 21.6335 | 30.5066 | 30.4916 | 29.5802 | 29.5055 | 29.4308 | 29.356 | 29.2813 | 29.2066 | 29.139 | 28.4306 | 26.9668 | 25.343 | 23.6506
|  | UNION STREET | CT |  |  | 31.9961 | 31.9872 | 31.4403 | 31.3955 | 31.3506 | 31.3058 | 31.261 | 31.2162 | 31.1635 | 30.6351 | 28.8534 | 27.2982 | 25.8152 | 29.2657 | 29.2505 | 28.6873 | 28.6285 | 28.5159 | 28.3886 | 28.285 | 28.1678 | 27.9601 | 27.2843 | 25.2983 | 23.5126 | 21.8001 | 30.5843 | 30.5753 | 30.0284 | 29.9836 | 29.9388 | 29.894 | 29.8491 | 29.8043 | 29.7864 | 29.2399 | 27.2717 | 25.5068 | 23.815
|  | UNION STREET | LW |  |  | 31.9184 | 31.9035 | 30.992 | 30.9173 | 30.8426 | 30.7679 | 30.6932 | 30.6069 | 30.4446 | 29.855 | 28.5709 | 27.1567 | 25.6733 | 29.1856 | 29.1631 | 28.2326 | 28.1061 | 27.9311 | 27.7987 | 27.6651 | 27.4154 | 27.1895 | 26.4728 | 24.9912 | 23.3465 | 21.6335 | 30.5066 | 30.4916 | 29.5802 | 29.5055 | 29.4308 | 29.356 | 29.2813 | 29.2066 | 29.139 | 28.4306 | 26.9668 | 25.343 | 23.6506
|  | UNION STREET | ST |  |  | 32.035 | 32.029 | 31.6644 | 31.6345 | 31.6047 | 31.5748 | 31.5449 | 31.515 | 31.503 | 31.4672 | 31.3728 | 30.5354 | 29.6259 | 29.3327 | 29.3074 | 28.9393 | 28.9069 | 28.8751 | 28.8384 | 28.8016 | 28.7654 | 28.7468 | 28.6524 | 28.1695 | 27.1197 | 26.0634 | 30.6231 | 30.6172 | 30.2526 | 30.2227 | 30.1928 | 30.1629 | 30.133 | 30.1031 | 30.0912 | 30.0553 | 29.9956 | 29.0806 | 28.0375
|  | UNION STREET | FS |  |  | 32.0738 | 32.0708 | 31.8886 | 31.8736 | 31.8587 | 31.8437 | 31.8288 | 31.8138 | 31.8079 | 31.7899 | 31.7601 | 31.7421 | 31.7092 | 29.3711 | 29.349 | 29.1647 | 29.1467 | 29.1288 | 29.1113 | 29.0936 | 29.0752 | 29.0667 | 29.0409 | 28.9936 | 28.8562 | 28.6821 | 30.662 | 30.659 | 30.4767 | 30.4618 | 30.4468 | 30.4319 | 30.4169 | 30.402 | 30.396 | 30.3781 | 30.3482 | 30.3303 | 30.2974
COWLEY GSP | OXFORD BSP | UNIVERSITY PARKS | MINIMUM HEADROOM |  |  | 48.2767 | 48.2646 | 47.5273 | 47.4669 | 47.4064 | 47.346 | 47.2856 | 47.2251 | 47.2009 | 47.1284 | 47.0075 | 46.935 | 46.8021 | 46.0146 | 46.0025 | 45.2651 | 45.2047 | 45.1443 | 45.0838 | 45.0234 | 44.9629 | 44.9388 | 44.8662 | 44.7454 | 44.6729 | 44.5399 | 47.0306 | 47.0164 | 46.2748 | 46.2101 | 46.1455 | 46.0817 | 46.0178 | 45.954 | 45.9262 | 45.8426 | 45.6996 | 45.5968 | 45.4387
|  | UNIVERSITY PARKS | CT |  |  | 48.3396 | 48.3323 | 47.8899 | 47.8537 | 47.8174 | 47.7811 | 47.7449 | 47.7086 | 47.6941 | 47.6506 | 47.1217 | 46.935 | 46.8021 | 46.0774 | 46.0702 | 45.6278 | 45.5915 | 45.5552 | 45.519 | 45.4827 | 45.4464 | 45.4319 | 45.3884 | 44.8595 | 44.6729 | 44.5399 | 47.0928 | 47.0831 | 46.6355 | 46.5943 | 46.553 | 46.5118 | 46.4722 | 46.4325 | 46.4144 | 46.3598 | 45.8087 | 45.5968 | 45.4387
|  | UNIVERSITY PARKS | LW |  |  | 48.2767 | 48.2646 | 47.5273 | 47.4669 | 47.4064 | 47.346 | 47.2856 | 47.2251 | 47.2009 | 47.1284 | 47.0075 | 46.935 | 46.8021 | 46.0146 | 46.0025 | 45.2651 | 45.2047 | 45.1443 | 45.0838 | 45.0234 | 44.9629 | 44.9388 | 44.8662 | 44.7454 | 44.6729 | 44.5399 | 47.0306 | 47.0164 | 46.2748 | 46.2101 | 46.1455 | 46.0817 | 46.0178 | 45.954 | 45.9262 | 45.8426 | 45.6996 | 45.6018 | 45.4437
|  | UNIVERSITY PARKS | ST |  |  | 48.371 | 48.3662 | 48.0712 | 48.0471 | 48.0229 | 47.9987 | 47.9745 | 47.9504 | 47.9407 | 47.9117 | 47.8633 | 47.8343 | 47.7811 | 46.1088 | 46.104 | 45.8091 | 45.7849 | 45.7607 | 45.7365 | 45.7124 | 45.6882 | 45.6785 | 45.6495 | 45.6012 | 45.5722 | 45.519 | 47.1582 | 47.1211 | 46.8247 | 46.7988 | 46.7724 | 46.7458 | 46.7192 | 46.6928 | 46.6806 | 46.6441 | 46.5807 | 46.5353 | 46.466
|  | UNIVERSITY PARKS | FS |  |  | 48.4024 | 48.4 | 48.2526 | 48.2405 | 48.2284 | 48.2163 | 48.2042 | 48.1921 | 48.1873 | 48.1728 | 48.1486 | 48.1341 | 48.1075 | 46.1403 | 46.1378 | 45.9904 | 45.9783 | 45.9662 | 45.9541 | 45.942 | 45.9299 | 45.9251 | 45.9106 | 45.8864 | 45.8719 | 45.8453 | 47.1908 | 47.1569 | 47.0092 | 46.9964 | 46.9835 | 46.9704 | 46.9573 | 46.9439 | 46.9381 | 46.9208 | 46.8907 | 46.8694 | 46.8359
EAST CLAYDON GSP | BICESTER NORTH BSP | UPPER HEYFORD | MINIMUM HEADROOM | SP 51750 25667 | NO | 16.5218 | 16.5132 | 16.4982 | 16.4742 | 16.445 | 16.4149 | 16.3871 | 16.3119 | 16.1317 | 15.8544 | 15.4874 | 15.1582 | 14.8949 | 15.2555 | 15.2555 | 15.2555 | 15.2354 | 15.2149 | 15.1941 | 15.1725 | 14.9905 | 14.7777 | 14.4512 | 14.0246 | 13.6451 | 13.3357 | 14.53 | 14.5209 | 14.3377 | 14.1286 | 13.9042 | 13.749 | 13.5734 | 13.3629 | 13.1563 | 12.839 | 12.4237 | 12.0536 | 11.7529
|  | UPPER HEYFORD | CT |  |  | 16.5232 | 16.5153 | 16.5019 | 16.4742 | 16.445 | 16.4149 | 16.3871 | 16.3119 | 16.1317 | 15.8544 | 15.4874 | 15.1582 | 14.8949 | 15.2555 | 15.2555 | 15.2555 | 15.2418 | 15.2279 | 15.2137 | 15.1989 | 14.9905 | 14.7777 | 14.4512 | 14.0246 | 13.6451 | 13.3357 | 14.5315 | 14.5231 | 14.3859 | 14.1896 | 13.9777 | 13.7578 | 13.5747 | 13.3629 | 13.1563 | 12.839 | 12.4237 | 12.0536 | 11.7529
|  | UPPER HEYFORD | LW |  |  | 16.5218 | 16.5132 | 16.4982 | 16.4761 | 16.4527 | 16.4343 | 16.414 | 16.3264 | 16.1476 | 15.8744 | 15.5425 | 15.2546 | 15.0029 | 15.2555 | 15.2555 | 15.2555 | 15.249 | 15.2424 | 15.2354 | 15.2058 | 15.0001 | 14.7888 | 14.4663 | 14.0749 | 13.7366 | 13.4389 | 14.53 | 14.5209 | 14.3377 | 14.1286 | 13.9042 | 13.749 | 13.5734 | 13.3735 | 13.1683 | 12.8551 | 12.4749 | 12.1461 | 11.857
|  | UPPER HEYFORD | ST |  |  | 16.5291 | 16.5201 | 16.512 | 16.4819 | 16.4493 | 16.4203 | 16.3895 | 16.3463 | 16.3243 | 16.2717 | 16.0482 | 15.767 | 15.574 | 15.2555 | 15.2555 | 15.2555 | 15.2354 | 15.2149 | 15.1941 | 15.1725 | 15.1391 | 15.1278 | 14.9901 | 14.6994 | 14.3856 | 14.1627 | 14.5378 | 14.5282 | 14.5164 | 14.367 | 14.1891 | 14.0619 | 13.9207 | 13.7606 | 13.6096 | 13.36 | 13.077 | 12.7693 | 12.552
|  | UPPER HEYFORD | FS |  |  | 16.5353 | 16.5333 | 16.5313 | 16.528 | 16.5242 | 16.5209 | 16.5173 | 16.5131 | 16.5088 | 16.5024 | 16.4948 | 16.4889 | 16.484 | 15.2555 | 15.2555 | 15.2555 | 15.2555 | 15.2555 | 15.2555 | 15.2555 | 15.2555 | 15.2555 | 15.2555 | 15.2555 | 15.2555 | 15.2555 | 14.5443 | 14.5423 | 14.5401 | 14.5366 | 14.5326 | 14.5291 | 14.5252 | 14.5208 | 14.4752 | 14.3918 | 14.293 | 14.2172 | 14.1527
IVER 132KV | UPTON BSP | UPTON | MINIMUM HEADROOM | TQ 00800 79434 | YES | 41.4637 | 41.4637 | 41.4637 | 41.4457 | 41.4282 | 41.4105 | 41.3926 | 41.3646 | 41.2867 | 41.0396 | 40.9219 | 40.5514 | 40.0859 | 37.6122 | 37.6069 | 37.5954 | 37.5839 | 37.5722 | 37.5578 | 37.5366 | 37.4979 | 37.4217 | 37.0998 | 36.158 | 34.5164 | 32.8417 | 39.7696 | 39.7696 | 39.7696 | 39.7517 | 39.7341 | 39.7164 | 39.6985 | 39.6705 | 39.5926 | 39.3455 | 39.2278 | 38.7942 | 37.0666
|  | UPTON | CT |  |  | 41.4637 | 41.4637 | 41.4637 | 41.4637 | 41.4637 | 41.4637 | 41.4637 | 41.4637 | 41.4637 | 41.4637 | 41.4637 | 41.4637 | 40.3207 | 37.6145 | 37.6106 | 37.6019 | 37.5931 | 37.584 | 37.5749 | 37.5618 | 37.5467 | 37.4949 | 37.2175 | 36.4079 | 34.7848 | 33.1103 | 39.7696 | 39.7696 | 39.7696 | 39.7696 | 39.7696 | 39.7696 | 39.7696 | 39.7696 | 39.7696 | 39.7696 | 39.7696 | 39.0711 | 37.3437
|  | UPTON | LW |  |  | 41.4637 | 41.4637 | 41.4637 | 41.4637 | 41.4637 | 41.4637 | 41.4637 | 41.4637 | 41.4637 | 41.4637 | 41.4637 | 41.4637 | 40.0859 | 37.6122 | 37.6069 | 37.5954 | 37.5839 | 37.5722 | 37.5593 | 37.5462 | 37.4979 | 37.4368 | 37.0998 | 36.158 | 34.5164 | 32.8417 | 39.7696 | 39.7696 | 39.7696 | 39.7696 | 39.7696 | 39.7696 | 39.7696 | 39.7696 | 39.7696 | 39.7696 | 39.7696 | 38.7942 | 37.0666
|  | UPTON | ST |  |  | 41.4637 | 41.4637 | 41.4637 | 41.4592 | 41.4547 | 41.4501 | 41.4453 | 41.4379 | 41.4354 | 41.4274 | 41.4209 | 41.4025 | 41.3971 | 37.6232 | 37.6097 | 37.6026 | 37.5894 | 37.5742 | 37.5602 | 37.5459 | 37.5282 | 37.5133 | 37.3851 | 36.9369 | 36.1901 | 35.1573 | 39.7696 | 39.7696 | 39.7696 | 39.7652 | 39.7606 | 39.756 | 39.7512 | 39.7438 | 39.7413 | 39.7333 | 39.7269 | 39.7084 | 39.4575
|  | UPTON | FS |  |  | 41.4637 | 41.4637 | 41.4637 | 41.4457 | 41.4282 | 41.4105 | 41.3926 | 41.3646 | 41.2867 | 41.0396 | 40.9219 | 40.5514 | 40.2415 | 37.6299 | 37.6199 | 37.6191 | 37.5989 | 37.5788 | 37.5578 | 37.5366 | 37.5039 | 37.4217 | 37.162 | 37.0208 | 36.6006 | 36.1738 | 39.7696 | 39.7696 | 39.7696 | 39.7517 | 39.7341 | 39.7164 | 39.6985 | 39.6705 | 39.5926 | 39.3455 | 39.2278 | 38.8573 | 38.5474
IVER 132kV |  | UXBRIDGE | MINIMUM HEADROOM | TQ 04984 83484 |  | 87.3255 | 87.3074 | 86.2055 | 86.1144 | 86.0226 | 85.93 | 85.8365 | 85.7397 | 85.7024 | 85.5884 | 85.3939 | 85.2585 | 85.058 | 81.9054 | 81.8796 | 80.7634 | 80.6576 | 80.5532 | 80.4441 | 80.3341 | 80.2196 | 80.1574 | 79.8653 | 78.929 | 77.1158 | 75.2298 | 85.4162 | 85.3982 | 84.2963 | 84.2052 | 84.1134 | 84.0208 | 83.9272 | 83.8305 | 83.7932 | 83.6792 | 83.4847 | 83.3493 | 81.4951
|  | UXBRIDGE | CT |  |  | 87.4194 | 87.4085 | 86.7474 | 86.693 | 86.6384 | 86.5836 | 86.5285 | 86.4724 | 86.4503 | 86.3835 | 85.5776 | 85.2815 | 85.0775 | 81.9979 | 81.9785 | 81.3013 | 81.2306 | 81.1617 | 81.0935 | 81.022 | 80.9463 | 80.8994 | 80.6285 | 79.0723 | 77.1158 | 75.2298 | 85.5102 | 85.4993 | 84.8382 | 84.7838 | 84.7292 | 84.6744 | 84.6193 | 84.5632 | 84.5411 | 84.4742 | 83.6684 | 83.3651 | 81.4951
|  | UXBRIDGE | LW |  |  | 87.3255 | 87.3074 | 86.2055 | 86.1144 | 86.0226 | 85.93 | 85.8365 | 85.7397 | 85.7024 | 85.5884 | 85.3939 | 85.2585 | 85.058 | 81.9054 | 81.8796 | 80.7634 | 80.6576 | 80.5532 | 80.4441 | 80.3341 | 80.2196 | 80.1574 | 79.8653 | 78.929 | 77.1675 | 75.2842 | 85.4162 | 85.3982 | 84.2963 | 84.2052 | 84.1134 | 84.0208 | 83.9272 | 83.8305 | 83.7932 | 83.6792 | 83.4847 | 83.3493 | 81.5488
|  | UXBRIDGE | ST |  |  | 87.4664 | 87.4591 | 87.0184 | 86.9821 | 86.9457 | 86.9091 | 86.8723 | 86.8346 | 86.8195 | 86.7722 | 86.6949 | 86.6337 | 86.5477 | 82.0552 | 82.0389 | 81.591 | 81.5459 | 81.5006 | 81.4509 | 81.401 | 81.3522 | 81.325 | 81.2367 | 80.948 | 80.4126 | 79.5423 | 85.5571 | 85.5499 | 85.1091 | 85.0729 | 85.0364 | 84.9999 | 84.9631 | 84.9254 | 84.9103 | 84.863 | 84.7857 | 84.7245 | 84.6385
|  | UXBRIDGE | FS |  |  | 87.5133 | 87.5097 | 87.2893 | 87.2713 | 87.2532 | 87.2351 | 87.217 | 87.1989 | 87.1914 | 87.1683 | 87.1311 | 87.1041 | 87.0591 | 82.1079 | 82.0985 | 81.8765 | 81.8553 | 81.8346 | 81.812 | 81.7894 | 81.7655 | 81.7534 | 81.7168 | 81.6557 | 81.6044 | 81.5328 | 85.6041 | 85.6005 | 85.3801 | 85.362 | 85.344 | 85.3259 | 85.3078 | 85.2897 | 85.2822 | 85.2591 | 85.2219 | 85.1949 | 85.1499
NURSLING GSP | VELMORE BSP | VELMORE | MINIMUM HEADROOM | SU 42935 19205 | YES | 46.0438 | 45.8098 | 45.4028 | 44.9488 | 44.4903 | 44.1687 | 43.9387 | 43.6853 | 43.4893 | 42.8836 | 41.5499 | 40.0451 | 38.6596 | 41.7708 | 41.508 | 41.0508 | 40.5481 | 40.0406 | 39.6822 | 39.4302 | 39.1551 | 38.9362 | 38.2597 | 36.7798 | 35.0563 | 33.4282 | 42.4346 | 42.1981 | 41.7867 | 41.3284 | 40.8657 | 40.5408 | 40.309 | 40.0536 | 39.8557 | 39.2438 | 37.8974 | 36.378 | 34.9779
|  | VELMORE | CT |  |  | 46.0598 | 45.8347 | 45.4464 | 45.0229 | 44.5957 | 44.1687 | 43.9387 | 43.6853 | 43.4893 | 42.8836 | 41.5499 | 40.0451 | 38.6596 | 41.7888 | 41.5359 | 41.0998 | 40.6299 | 40.1559 | 39.6822 | 39.4302 | 39.1551 | 38.9362 | 38.2597 | 36.7798 | 35.0563 | 33.4282 | 42.4508 | 42.2233 | 41.8308 | 41.4032 | 40.972 | 40.5408 | 40.309 | 40.0536 | 39.8557 | 39.2438 | 37.8974 | 36.378 | 34.9779
|  | VELMORE | LW |  |  | 46.0438 | 45.8098 | 45.4028 | 44.9488 | 44.4903 | 44.2489 | 44.0036 | 43.7281 | 43.5282 | 42.9066 | 41.6487 | 40.1557 | 38.7959 | 41.7708 | 41.508 | 41.0508 | 40.5481 | 40.0406 | 39.7774 | 39.5099 | 39.2128 | 38.9899 | 38.2976 | 36.8934 | 35.1886 | 33.5862 | 42.4346 | 42.1981 | 41.7867 | 41.3284 | 40.8657 | 40.6224 | 40.3752 | 40.0978 | 39.8958 | 39.2681 | 37.9974 | 36.4899 | 35.1156
|  | VELMORE | ST |  |  | 46.1358 | 45.9767 | 45.753 | 45.4799 | 45.1477 | 45.0086 | 44.8689 | 44.7493 | 44.6222 | 44.2313 | 43.4204 | 42.5354 | 41.6706 | 41.8741 | 41.6955 | 41.4442 | 41.1375 | 40.7643 | 40.608 | 40.4511 | 40.3167 | 40.174 | 39.7349 | 38.8241 | 37.83 | 36.8545 | 42.5276 | 42.3668 | 42.1407 | 41.8647 | 41.5289 | 41.3882 | 41.247 | 41.1262 | 40.9977 | 40.6026 | 39.7831 | 38.8885 | 38.0143
|  | VELMORE | FS |  |  | 46.3613 | 46.3259 | 46.3086 | 46.2407 | 46.1591 | 46.1099 | 46.0606 | 46 | 45.9505 | 45.7987 | 45.4751 | 45.0988 | 44.7138 | 42.1275 | 42.0877 | 42.0683 | 41.992 | 41.9003 | 41.8451 | 41.7897 | 41.7216 | 41.666 | 41.4955 | 41.1321 | 40.7094 | 40.2769 | 42.7556 | 42.7198 | 42.7023 | 42.6336 | 42.5511 | 42.5014 | 42.4516 | 42.3903 | 42.3403 | 42.1869 | 41.8598 | 41.4795 | 41.0903
FAWLEY GSP | COWES & WOOTTON COMMON BSP | VENTNOR | MINIMUM HEADROOM | SZ 56148 77857 | YES | 42.8053 | 42.7914 | 42.7664 | 42.7382 | 42.7033 | 42.6061 | 42.503 | 42.4008 | 42.2906 | 41.9528 | 41.3791 | 40.7846 | 40.1996 | 39.4683 | 39.4683 | 39.4683 | 39.4679 | 39.4675 | 39.4671 | 39.4666 | 39.466 | 39.4642 | 39.4586 | 39.456 | 39.4475 | 39.4405 | 41.1959 | 41.1959 | 41.1959 | 41.1955 | 41.1951 | 41.1947 | 41.1943 | 41.1937 | 41.1919 | 41.1863 | 41.1836 | 40.9199 | 40.2146
|  | VENTNOR | CT |  |  | 42.809 | 42.7953 | 42.7664 | 42.7382 | 42.7101 | 42.6822 | 42.5791 | 42.4769 | 42.3667 | 42.0339 | 41.4599 | 40.8656 | 40.2809 | 39.4683 | 39.4683 | 39.4683 | 39.4683 | 39.4683 | 39.4683 | 39.4683 | 39.4683 | 39.4683 | 39.4683 | 39.4683 | 39.4683 | 39.4683 | 41.1959 | 41.1959 | 41.1959 | 41.1959 | 41.1959 | 41.1959 | 41.1959 | 41.1959 | 41.1959 | 41.1959 | 41.1959 | 41.0175 | 40.3127
|  | VENTNOR | LW |  |  | 42.809 | 42.7953 | 42.7664 | 42.7382 | 42.7101 | 42.6061 | 42.503 | 42.4008 | 42.2906 | 41.9528 | 41.3791 | 40.7846 | 40.1996 | 39.4683 | 39.4683 | 39.4683 | 39.4683 | 39.4683 | 39.4683 | 39.4683 | 39.4683 | 39.4683 | 39.4683 | 39.4683 | 39.4683 | 39.4683 | 41.1959 | 41.1959 | 41.1959 | 41.1959 | 41.1959 | 41.1959 | 41.1959 | 41.1959 | 41.1959 | 41.1959 | 41.1959 | 40.9199 | 40.2146
|  | VENTNOR | ST |  |  | 42.8053 | 42.7914 | 42.7677 | 42.7385 | 42.7033 | 42.6558 | 42.609 | 42.5392 | 42.464 | 42.2445 | 41.8686 | 41.4855 | 41.1052 | 39.4683 | 39.4683 | 39.4683 | 39.4683 | 39.4683 | 39.4683 | 39.4683 | 39.4683 | 39.4683 | 39.4683 | 39.4683 | 39.4683 | 39.4683 | 41.1959 | 41.1959 | 41.1959 | 41.1959 | 41.1959 | 41.1959 | 41.1959 | 41.1959 | 41.1959 | 41.1959 | 41.1959 | 41.1959 | 41.1959
|  | VENTNOR | FS |  |  | 42.8304 | 42.8293 | 42.8283 | 42.8235 | 42.8179 | 42.8068 | 42.7959 | 42.7817 | 42.7508 | 42.6604 | 42.5221 | 42.383 | 42.2519 | 39.4683 | 39.4683 | 39.4683 | 39.4679 | 39.4675 | 39.4671 | 39.4666 | 39.466 | 39.4642 | 39.4586 | 39.456 | 39.4475 | 39.4405 | 41.1959 | 41.1959 | 41.1959 | 41.1955 | 41.1951 | 41.1947 | 41.1943 | 41.1937 | 41.1919 | 41.1863 | 41.1836 | 41.1752 | 41.1682
MANNINGTON GSP | MANNINGTON BSP | VERWOOD | MINIMUM HEADROOM | SU 07716 10226 | YES | 15.3355 | 15.3355 | 15.3355 | 15.1703 | 14.9967 | 14.812 | 14.6171 | 14.3144 | 14.2715 | 14.1165 | 13.4329 | 12.2669 | 11.5638 | 14.679 | 14.6739 | 14.6639 | 14.4898 | 14.3069 | 14.1073 | 13.7677 | 13.3148 | 13.1104 | 12.466 | 11.3963 | 10.1281 | 9.309 | 15.2279 | 15.2228 | 15.2128 | 15.0386 | 14.8557 | 14.6626 | 14.4593 | 14.1478 | 14.0955 | 13.5603 | 12.4648 | 11.1802 | 10.3608
|  | VERWOOD | CT |  |  | 15.3355 | 15.3355 | 15.3355 | 15.3345 | 15.3328 | 15.3302 | 15.3264 | 15.3181 | 15.3166 | 15.3086 | 14.9416 | 14.1881 | 13.4989 | 14.6804 | 14.6762 | 14.6679 | 14.6597 | 14.6504 | 14.6405 | 14.6229 | 14.4644 | 14.3014 | 13.8041 | 12.9227 | 12.0716 | 11.2665 | 15.2293 | 15.2251 | 15.2168 | 15.2085 | 15.1992 | 15.1893 | 15.1771 | 15.16 | 15.1491 | 14.903 | 13.9959 | 13.1237 | 12.3183
|  | VERWOOD | LW |  |  | 15.3355 | 15.3355 | 15.3355 | 15.1703 | 14.9967 | 14.812 | 14.6171 | 14.3144 | 14.2715 | 14.1165 | 13.4329 | 12.2669 | 11.5638 | 14.679 | 14.6739 | 14.6639 | 14.4898 | 14.3069 | 14.1073 | 13.7677 | 13.3148 | 13.1104 | 12.466 | 11.3963 | 10.1281 | 9.309 | 15.2279 | 15.2228 | 15.2128 | 15.0386 | 14.8557 | 14.6626 | 14.4593 | 14.1478 | 14.0955 | 13.5603 | 12.4648 | 11.1802 | 10.3608
|  | VERWOOD | ST |  |  | 15.3355 | 15.3355 | 15.3355 | 15.3348 | 15.3335 | 15.3316 | 15.3287 | 15.3223 | 15.3192 | 15.3026 | 15.2808 | 15.0157 | 14.5547 | 14.6807 | 14.6772 | 14.6714 | 14.6643 | 14.655 | 14.6462 | 14.6366 | 14.62 | 14.5066 | 14.1576 | 13.5878 | 13.0124 | 12.4914 | 15.2297 | 15.2261 | 15.2203 | 15.2132 | 15.2038 | 15.1951 | 15.1854 | 15.173 | 15.1635 | 15.1275 | 14.6808 | 14.0896 | 13.553
|  | VERWOOD | FS |  |  | 15.3355 | 15.3355 | 15.3355 | 15.3355 | 15.3354 | 15.3353 | 15.3352 | 15.3349 | 15.3339 | 15.3279 | 15.3231 | 15.3003 | 15.2781 | 14.694 | 14.6857 | 14.6851 | 14.6837 | 14.682 | 14.6798 | 14.6775 | 14.6745 | 14.6709 | 14.6574 | 14.6404 | 14.6069 | 14.4831 | 15.2429 | 15.2346 | 15.234 | 15.2326 | 15.2309 | 15.2287 | 15.2264 | 15.2234 | 15.2198 | 15.2063 | 15.1892 | 15.1557 | 15.1234
NURSLING GSP |  | VICARAGE FARM ROAD | MINIMUM HEADROOM | TQ 12358 76435 |  | 46.9191 | 46.9191 | 46.9191 | 46.9191 | 46.9191 | 46.9191 | 46.9191 | 46.9191 | 46.9191 | 46.9191 | 46.8603 | 44.7914 | 42.7365 | 44.7551 | 44.7502 | 44.7429 | 44.7355 | 44.7274 | 44.711 | 44.694 | 44.6784 | 44.6626 | 44.6153 | 43.4174 | 41.018 | 38.6347 | 45.0344 | 45.0281 | 45.0185 | 45.0087 | 44.9981 | 44.9767 | 44.9544 | 44.9339 | 44.9133 | 44.8506 | 43.7912 | 41.5396 | 39.1145
|  | VICARAGE FARM ROAD | CT |  |  | 46.9191 | 46.9191 | 46.9191 | 46.9191 | 46.9191 | 46.9191 | 46.9191 | 46.9191 | 46.9191 | 46.9191 | 46.9191 | 44.972 | 42.9171 | 44.7553 | 44.7506 | 44.7435 | 44.7364 | 44.7285 | 44.7204 | 44.7034 | 44.6878 | 44.6721 | 44.6247 | 43.6264 | 41.2273 | 38.8441 | 45.0347 | 45.0286 | 45.0193 | 45.0099 | 44.9997 | 44.989 | 44.9667 | 44.9463 | 44.9257 | 44.8637 | 43.9865 | 41.7435 | 39.3276
|  | VICARAGE FARM ROAD | LW |  |  | 46.9191 | 46.9191 | 46.9191 | 46.9191 | 46.9191 | 46.9191 | 46.9191 | 46.9191 | 46.9191 | 46.9191 | 46.8603 | 44.7914 | 42.7365 | 44.7551 | 44.7502 | 44.7429 | 44.7355 | 44.7274 | 44.711 | 44.694 | 44.6784 | 44.6626 | 44.6153 | 43.4174 | 41.018 | 38.6347 | 45.0344 | 45.0281 | 45.0185 | 45.0087 | 44.9981 | 44.9767 | 44.9544 | 44.9339 | 44.9133 | 44.8506 | 43.7912 | 41.5396 | 39.1145
|  | VICARAGE FARM ROAD | ST |  |  | 46.9191 | 46.9191 | 46.9191 | 46.9191 | 46.9191 | 46.9191 | 46.9191 | 46.9191 | 46.9191 | 46.9191 | 46.9191 | 46.9191 | 45.8239 | 44.7715 | 44.7554 | 44.7522 | 44.7485 | 44.7438 | 44.7342 | 44.7241 | 44.7135 | 44.7027 | 44.6705 | 44.6055 | 43.7426 | 42.2154 | 45.056 | 45.0349 | 45.0307 | 45.0258 | 45.0197 | 45.007 | 44.9939 | 44.98 | 44.9659 | 44.9237 | 44.8364 | 44.0953 | 42.6673
|  | VICARAGE FARM ROAD | FS |  |  | 46.9191 | 46.9191 | 46.9191 | 46.9191 | 46.9191 | 46.9191 | 46.9191 | 46.9191 | 46.9191 | 46.9191 | 46.9191 | 46.9191 | 46.9191 | 44.7946 | 44.759 | 44.7579 | 44.7565 | 44.7547 | 44.7513 | 44.7477 | 44.7438 | 44.7397 | 44.7272 | 44.7013 | 44.6714 | 44.6409 | 45.0863 | 45.0396 | 45.0382 | 45.0363 | 45.034 | 45.0295 | 45.0248 | 45.0197 | 45.0143 | 44.9979 | 44.964 | 44.9248 | 44.8849
COWLEY GSP | COWLEY LOCAL (2 X 90) | WALLINGFORD | MINIMUM HEADROOM | SU 59847 89486 | NO | 15.1994 | 14.7857 | 13.9447 | 13.7224 | 13.4927 | 13.2726 | 13.0475 | 12.8161 | 12.6046 | 12.0452 | 11.1038 | 10.2172 | 9.4074 | 16.9634 | 16.9522 | 16.2693 | 16.2133 | 16.1573 | 16.1013 | 16.0454 | 15.94 | 15.7062 | 15.0887 | 14.0371 | 13.0664 | 12.1757 | 15.1663 | 14.6793 | 13.8138 | 13.5624 | 13.3025 | 13.0538 | 12.7992 | 12.5372 | 12.2927 | 11.6474 | 10.5429 | 9.5318 | 8.6022
|  | WALLINGFORD | CT |  |  | 15.2215 | 14.7924 | 14.1823 | 13.9415 | 13.6939 | 13.4766 | 13.274 | 13.065 | 12.8623 | 12.3299 | 11.1038 | 10.2172 | 9.4074 | 17.0216 | 17.0149 | 16.6051 | 16.5715 | 16.5379 | 16.5044 | 16.395 | 16.1654 | 15.9404 | 15.35 | 14.0371 | 13.0664 | 12.1757 | 15.1821 | 14.6793 | 14.0342 | 13.7573 | 13.4723 | 13.2231 | 12.9909 | 12.7513 | 12.5157 | 11.8974 | 10.5429 | 9.5318 | 8.6022
|  | WALLINGFORD | LW |  |  | 15.1994 | 14.7857 | 13.9447 | 13.7224 | 13.4927 | 13.2726 | 13.0475 | 12.8161 | 12.6046 | 12.0452 | 11.1973 | 10.4162 | 9.6059 | 16.9634 | 16.9522 | 16.2693 | 16.2133 | 16.1573 | 16.1013 | 16.0454 | 15.94 | 15.7062 | 15.0887 | 14.1541 | 13.2888 | 12.3977 | 15.1663 | 14.6824 | 13.8138 | 13.5624 | 13.3025 | 13.0538 | 12.7992 | 12.5372 | 12.2927 | 11.6474 | 10.6711 | 9.7655 | 8.8354
|  | WALLINGFORD | ST |  |  | 15.3829 | 15.3486 | 15.0317 | 14.9544 | 14.8676 | 14.7288 | 14.5872 | 14.4457 | 14.3075 | 13.9453 | 13.4072 | 12.9198 | 12.4233 | 17.0507 | 17.0462 | 16.7731 | 16.7507 | 16.7283 | 16.7059 | 16.6835 | 16.6611 | 16.6521 | 16.6253 | 16.531 | 15.9894 | 15.4402 | 15.3666 | 15.3271 | 15.0026 | 14.9156 | 14.8176 | 14.6585 | 14.4961 | 14.3339 | 14.1731 | 13.7524 | 13.1283 | 12.5605 | 11.9861
|  | WALLINGFORD | FS |  |  | 15.4315 | 15.412 | 15.255 | 15.2093 | 15.1596 | 15.1047 | 15.0492 | 14.9827 | 14.9277 | 14.7839 | 14.5725 | 14.3903 | 14.2108 | 17.0798 | 17.0776 | 16.941 | 16.9298 | 16.9186 | 16.9074 | 16.8962 | 16.885 | 16.8805 | 16.8671 | 16.8447 | 16.8313 | 16.8066 | 15.4185 | 15.3961 | 15.2355 | 15.1838 | 15.1274 | 15.0649 | 15.0016 | 14.9255 | 14.8617 | 14.6951 | 14.4507 | 14.2391 | 14.0325
COWLEY GSP | DRAYTON BSP | WANTAGE | MINIMUM HEADROOM | SU 41290 88304 | NO | 17.5626 | 17.5626 | 17.5626 | 17.5586 | 17.5539 | 17.5481 | 17.5414 | 17.5048 | 17.3626 | 16.9527 | 16.2923 | 15.634 | 15.0367 | 15.2084 | 15.0797 | 14.859 | 14.6253 | 14.3702 | 14.1415 | 13.9682 | 13.7915 | 13.6235 | 13.1397 | 12.3611 | 11.5878 | 10.8812 | 15.2093 | 15.081 | 14.861 | 14.6281 | 14.3737 | 14.1457 | 13.9729 | 13.7966 | 13.6291 | 13.1468 | 12.3706 | 11.5995 | 10.8951
|  | WANTAGE | CT |  |  | 17.5626 | 17.5626 | 17.5626 | 17.5624 | 17.562 | 17.5614 | 17.5605 | 17.5219 | 17.3812 | 16.9777 | 16.3195 | 15.6774 | 15.0776 | 15.2084 | 15.0797 | 14.859 | 14.6269 | 14.3756 | 14.1415 | 13.9734 | 13.8064 | 13.6399 | 13.1626 | 12.3861 | 11.6291 | 10.92 | 15.2093 | 15.081 | 14.861 | 14.6296 | 14.3791 | 14.1457 | 13.9781 | 13.8116 | 13.6456 | 13.1697 | 12.3956 | 11.6408 | 10.9339
|  | WANTAGE | LW |  |  | 17.5626 | 17.5626 | 17.5626 | 17.5586 | 17.5539 | 17.5481 | 17.5414 | 17.5048 | 17.3626 | 16.9527 | 16.2923 | 15.634 | 15.0367 | 15.209 | 15.0806 | 14.8606 | 14.6253 | 14.3702 | 14.1423 | 13.9682 | 13.7915 | 13.6235 | 13.1397 | 12.3611 | 11.5878 | 10.8812 | 15.21 | 15.082 | 14.8626 | 14.6281 | 14.3737 | 14.1465 | 13.9729 | 13.7966 | 13.6291 | 13.1468 | 12.3706 | 11.5995 | 10.8951
|  | WANTAGE | ST |  |  | 17.5626 | 17.5626 | 17.5626 | 17.5624 | 17.5621 | 17.5617 | 17.561 | 17.5596 | 17.5589 | 17.5552 | 17.1854 | 16.7647 | 16.3715 | 15.2714 | 15.1904 | 15.0741 | 14.9309 | 14.756 | 14.5994 | 14.4797 | 14.366 | 14.2518 | 13.9252 | 13.4096 | 12.9146 | 12.4504 | 15.2722 | 15.1914 | 15.0755 | 14.9327 | 14.7583 | 14.6022 | 14.4829 | 14.3695 | 14.2557 | 13.93 | 13.416 | 12.9225 | 12.4597
|  | WANTAGE | FS |  |  | 17.5626 | 17.5626 | 17.5626 | 17.5599 | 17.5572 | 17.5546 | 17.5518 | 17.5476 | 17.5357 | 17.4973 | 17.4786 | 17.418 | 17.3666 | 15.3527 | 15.3213 | 15.289 | 15.2322 | 15.167 | 15.1056 | 15.0613 | 15.007 | 14.951 | 14.7876 | 14.5729 | 14.3368 | 14.1278 | 15.3532 | 15.322 | 15.2898 | 15.2331 | 15.1681 | 15.1068 | 15.0627 | 15.0085 | 14.9527 | 14.7896 | 14.5756 | 14.34 | 14.1314
MANNINGTON GSP | WAREHAM | WAREHAM TOWN | MINIMUM HEADROOM | SY 92036 87463 | YES | 17.6682 | 17.647 | 16.3519 | 16.2142 | 16.0722 | 15.925 | 15.7728 | 15.5896 | 15.5354 | 15.3597 | 14.7999 | 14.0051 | 13.279 | 16.3636 | 16.3411 | 15.0433 | 14.903 | 14.7584 | 14.6047 | 14.446 | 14.2563 | 14.1077 | 13.567 | 12.6586 | 11.7336 | 10.8795 | 16.0966 | 16.0753 | 14.7802 | 14.6425 | 14.5005 | 14.3534 | 14.2011 | 14.0179 | 13.9638 | 13.788 | 13.4794 | 13.1735 | 12.9284
|  | WAREHAM TOWN | CT |  |  | 17.7786 | 17.7659 | 16.9888 | 16.8997 | 16.8093 | 16.7177 | 16.6236 | 16.5105 | 16.4783 | 16.3769 | 15.1069 | 14.134 | 13.3769 | 16.474 | 16.46 | 15.6802 | 15.5885 | 15.4955 | 15.4013 | 15.3007 | 15.1812 | 15.121 | 14.6548 | 12.9805 | 11.8775 | 10.9923 | 16.207 | 16.1942 | 15.4172 | 15.3281 | 15.2377 | 15.146 | 15.052 | 14.9388 | 14.9066 | 14.8053 | 13.7307 | 13.2466 | 12.9703
|  | WAREHAM TOWN | LW |  |  | 17.6682 | 17.647 | 16.3519 | 16.2142 | 16.0722 | 15.925 | 15.7728 | 15.5896 | 15.5354 | 15.3597 | 14.7999 | 14.0051 | 13.279 | 16.3636 | 16.3411 | 15.0433 | 14.903 | 14.7584 | 14.6047 | 14.446 | 14.2563 | 14.1077 | 13.567 | 12.6586 | 11.7336 | 10.8795 | 16.0966 | 16.0753 | 14.7802 | 14.6425 | 14.5005 | 14.3534 | 14.2011 | 14.0179 | 13.9638 | 13.788 | 13.4794 | 13.1735 | 12.9284
|  | WAREHAM TOWN | ST |  |  | 17.8338 | 17.8253 | 17.3073 | 17.2378 | 17.1672 | 17.0954 | 17.0216 | 16.9287 | 16.8937 | 16.7779 | 16.6321 | 16.27 | 15.7999 | 16.53 | 16.5208 | 16.0016 | 15.9306 | 15.8582 | 15.7824 | 15.7049 | 15.6076 | 15.5678 | 15.3603 | 14.8159 | 14.1661 | 13.6127 | 16.2622 | 16.2537 | 15.7356 | 15.6661 | 15.5955 | 15.5237 | 15.4499 | 15.357 | 15.322 | 15.2063 | 15.0605 | 14.8091 | 14.6517
|  | WAREHAM TOWN | FS |  |  | 17.889 | 17.8848 | 17.6258 | 17.6024 | 17.5791 | 17.5557 | 17.5323 | 17.5075 | 17.4889 | 17.4284 | 17.3673 | 17.2749 | 17.1688 | 16.5864 | 16.582 | 16.3229 | 16.2992 | 16.2754 | 16.2509 | 16.2263 | 16.2 | 16.1796 | 16.1138 | 16.0443 | 15.9438 | 15.768 | 16.3174 | 16.3131 | 16.0541 | 16.0308 | 16.0074 | 15.9841 | 15.9606 | 15.9359 | 15.9172 | 15.8568 | 15.7956 | 15.7032 | 15.5972
BRAMLEY (FLEE) | BRACKNELL MAIN | WARFIELD | MINIMUM HEADROOM | SU 86960 71382 | YES | 29.5269 | 29.5269 | 29.5269 | 29.5247 | 29.5201 | 29.5128 | 29.5028 | 29.4827 | 29.4793 | 29.376 | 27.5951 | 26.6131 | 25.7518 | 27.8377 | 27.8377 | 27.8377 | 27.8355 | 27.8309 | 27.8237 | 27.4062 | 26.8324 | 26.2189 | 24.3452 | 22.2731 | 21.1485 | 20.1449 | 28.26 | 28.26 | 28.26 | 28.2578 | 28.2532 | 28.246 | 28.236 | 28.2158 | 27.8348 | 25.9649 | 23.8968 | 22.7742 | 21.7726
|  | WARFIELD | CT |  |  | 29.5269 | 29.5269 | 29.5269 | 29.5262 | 29.5249 | 29.5231 | 29.5203 | 29.5142 | 29.5132 | 29.3786 | 27.5951 | 26.6414 | 25.7701 | 27.8377 | 27.8377 | 27.8377 | 27.837 | 27.8358 | 27.8339 | 27.4062 | 26.8324 | 26.2189 | 24.3452 | 22.2731 | 21.1697 | 20.1562 | 28.26 | 28.26 | 28.26 | 28.2593 | 28.2581 | 28.2562 | 28.2534 | 28.2474 | 27.8348 | 25.9649 | 23.8968 | 22.7955 | 21.784
|  | WARFIELD | LW |  |  | 29.5269 | 29.5269 | 29.5269 | 29.5247 | 29.5201 | 29.5128 | 29.5028 | 29.4827 | 29.4793 | 29.376 | 27.5976 | 26.6131 | 25.7518 | 27.8377 | 27.8377 | 27.8377 | 27.8355 | 27.8309 | 27.8237 | 27.439 | 26.8513 | 26.2355 | 24.3499 | 22.2828 | 21.1485 | 20.1449 | 28.26 | 28.26 | 28.26 | 28.2578 | 28.2532 | 28.246 | 28.236 | 28.2158 | 27.8513 | 25.9694 | 23.9064 | 22.7742 | 21.7726
|  | WARFIELD | ST |  |  | 29.5269 | 29.5269 | 29.5269 | 29.5264 | 29.5255 | 29.5241 | 29.522 | 29.5173 | 29.515 | 29.503 | 29.4871 | 29.4315 | 28.8627 | 27.8377 | 27.8377 | 27.8377 | 27.8372 | 27.8363 | 27.8349 | 27.8328 | 27.8281 | 27.8259 | 26.6018 | 25.1626 | 24.4281 | 23.7595 | 28.26 | 28.26 | 28.26 | 28.2595 | 28.2586 | 28.2572 | 28.2551 | 28.2504 | 28.2482 | 28.2169 | 26.7805 | 26.0474 | 25.3801
|  | WARFIELD | FS |  |  | 29.5269 | 29.5269 | 29.5269 | 29.5269 | 29.5268 | 29.5268 | 29.5267 | 29.5265 | 29.5257 | 29.5214 | 29.5179 | 29.5013 | 29.4852 | 27.8377 | 27.8377 | 27.8377 | 27.8377 | 27.8377 | 27.8376 | 27.8375 | 27.8373 | 27.8366 | 27.8322 | 27.8287 | 27.8121 | 27.796 | 28.26 | 28.26 | 28.26 | 28.26 | 28.26 | 28.2599 | 28.2598 | 28.2596 | 28.2588 | 28.2545 | 28.251 | 28.2344 | 28.2183
MELKSHAM GSP | FROME BSP | WARMINSTER | MINIMUM HEADROOM | ST 84936 44551 | YES | 22.4597 | 22.4597 | 22.4597 | 22.4597 | 22.4597 | 22.4597 | 22.4597 | 22.4597 | 22.4597 | 22.4597 | 22.3522 | 21.9439 | 21.5425 | 20.3371 | 20.3156 | 20.3093 | 20.2397 | 20.1681 | 20.079 | 19.9902 | 19.9025 | 19.8086 | 19.5314 | 19.0665 | 18.586 | 18.1138 | 21.093 | 21.093 | 21.093 | 21.093 | 21.093 | 21.093 | 21.093 | 21.093 | 21.093 | 21.093 | 21.093 | 21.093 | 21.093
|  | WARMINSTER | CT |  |  | 22.4597 | 22.4597 | 22.4597 | 22.4597 | 22.4597 | 22.4597 | 22.4597 | 22.4597 | 22.4597 | 22.4597 | 22.4291 | 22.0211 | 21.6196 | 20.338 | 20.317 | 20.3119 | 20.286 | 20.2278 | 20.1696 | 20.0809 | 19.9932 | 19.8992 | 19.6222 | 19.157 | 18.6768 | 18.2045 | 21.093 | 21.093 | 21.093 | 21.093 | 21.093 | 21.093 | 21.093 | 21.093 | 21.093 | 21.093 | 21.093 | 21.093 | 21.093
|  | WARMINSTER | LW |  |  | 22.4597 | 22.4597 | 22.4597 | 22.4597 | 22.4597 | 22.4597 | 22.4597 | 22.4597 | 22.4597 | 22.4597 | 22.3522 | 21.9439 | 21.5425 | 20.3371 | 20.3156 | 20.3093 | 20.2397 | 20.1681 | 20.079 | 19.9902 | 19.9025 | 19.8086 | 19.5314 | 19.0665 | 18.586 | 18.1138 | 21.093 | 21.093 | 21.093 | 21.093 | 21.093 | 21.093 | 21.093 | 21.093 | 21.093 | 21.093 | 21.093 | 21.093 | 21.093
|  | WARMINSTER | ST |  |  | 22.4597 | 22.4597 | 22.4597 | 22.4597 | 22.4597 | 22.4597 | 22.4597 | 22.4597 | 22.4597 | 22.4597 | 22.4597 | 22.4597 | 22.4099 | 20.3376 | 20.3349 | 20.3308 | 20.326 | 20.3203 | 20.3172 | 20.3141 | 20.3093 | 20.2481 | 20.0609 | 19.7506 | 19.4409 | 19.1344 | 21.093 | 21.093 | 21.093 | 21.093 | 21.093 | 21.093 | 21.093 | 21.093 | 21.093 | 21.093 | 21.093 | 21.093 | 21.093
|  | WARMINSTER | FS |  |  | 22.4597 | 22.4597 | 22.4597 | 22.4597 | 22.4597 | 22.4597 | 22.4597 | 22.4597 | 22.4597 | 22.4597 | 22.4597 | 22.4597 | 22.4597 | 20.3417 | 20.3412 | 20.3408 | 20.3398 | 20.3386 | 20.3377 | 20.3368 | 20.3357 | 20.3337 | 20.3279 | 20.3185 | 20.3094 | 20.205 | 21.093 | 21.093 | 21.093 | 21.093 | 21.093 | 21.093 | 21.093 | 21.093 | 21.093 | 21.093 | 21.093 | 21.093 | 21.093
LOVEDEAN GSP | FORT WIDLEY | WATERLOOVILLE | MINIMUM HEADROOM | SU 67988 09282 | YES | 52.2687 | 52.2563 | 51.4999 | 51.4367 | 51.3722 | 51.3063 | 51.2169 | 51.1072 | 51.0418 | 50.8513 | 49.369 | 47.4478 | 45.5455 | 50.7858 | 50.7639 | 49.9888 | 49.9047 | 49.8173 | 49.7258 | 49.6295 | 49.527 | 49.4691 | 49.1915 | 47.2196 | 44.9989 | 42.8034 | 50.7487 | 50.7363 | 49.9799 | 49.9167 | 49.8522 | 49.7862 | 49.7188 | 49.6458 | 49.6174 | 49.4474 | 47.3361 | 45.0905 | 42.8707
|  | WATERLOOVILLE | CT |  |  | 52.3332 | 52.3258 | 51.8719 | 51.8344 | 51.7965 | 51.7582 | 51.7151 | 51.6378 | 51.5836 | 51.4293 | 49.7199 | 47.6986 | 45.7912 | 50.8522 | 50.8363 | 50.3661 | 50.3099 | 50.2513 | 50.1918 | 50.1243 | 50.0542 | 50.0075 | 49.8045 | 47.6056 | 45.2848 | 43.0844 | 50.8131 | 50.8057 | 50.3519 | 50.3143 | 50.2764 | 50.2382 | 50.1995 | 50.159 | 50.1435 | 50.0221 | 47.7251 | 45.3794 | 43.1547
|  | WATERLOOVILLE | LW |  |  | 52.2687 | 52.2563 | 51.4999 | 51.4367 | 51.3722 | 51.3063 | 51.2169 | 51.1072 | 51.0418 | 50.8513 | 49.369 | 47.4478 | 45.5455 | 50.7858 | 50.7639 | 49.9888 | 49.9047 | 49.8173 | 49.7258 | 49.6295 | 49.527 | 49.4691 | 49.1915 | 47.2196 | 44.9989 | 42.8034 | 50.7487 | 50.7363 | 49.9799 | 49.9167 | 49.8522 | 49.7862 | 49.7188 | 49.6458 | 49.6174 | 49.4474 | 47.3361 | 45.0905 | 42.8707
|  | WATERLOOVILLE | ST |  |  | 52.3654 | 52.3605 | 52.0579 | 52.0329 | 52.0076 | 51.982 | 51.956 | 51.9287 | 51.9079 | 51.7978 | 51.6381 | 51.0784 | 49.8779 | 50.8876 | 50.8768 | 50.5647 | 50.5267 | 50.4853 | 50.4429 | 50.398 | 50.3507 | 50.3181 | 50.2223 | 50.0163 | 49.071 | 47.6817 | 50.8454 | 50.8404 | 50.5379 | 50.5128 | 50.4875 | 50.4619 | 50.436 | 50.4086 | 50.3975 | 50.3612 | 50.2305 | 49.1994 | 47.7944
|  | WATERLOOVILLE | FS |  |  | 52.3977 | 52.3952 | 52.2439 | 52.2309 | 52.2179 | 52.2049 | 52.1918 | 52.1784 | 52.1704 | 52.145 | 52.1144 | 52.0677 | 51.9824 | 50.9274 | 50.9233 | 50.7701 | 50.7527 | 50.7345 | 50.7154 | 50.6955 | 50.6742 | 50.6578 | 50.609 | 50.5461 | 50.4781 | 50.4004 | 50.8776 | 50.8751 | 50.7239 | 50.7109 | 50.6979 | 50.6848 | 50.6718 | 50.6584 | 50.6504 | 50.6249 | 50.5943 | 50.5581 | 50.5117
COWLEY GSP | HIGH WYCOMBE BSP | WATLINGTON | MINIMUM HEADROOM | SU 69106 94287 | YES | 12.0684 | 12.0116 | 11.9057 | 11.7604 | 11.6129 | 11.4643 | 11.3541 | 11.2165 | 11.1414 | 10.9143 | 10.4079 | 9.8779 | 9.5071 | 10.8019 | 10.7965 | 10.7866 | 10.7347 | 10.6454 | 10.4803 | 10.36 | 10.2127 | 10.1272 | 9.8693 | 9.3123 | 8.7313 | 8.3103 | 11.3054 | 11.3054 | 11.3003 | 11.2511 | 11.2005 | 11.1484 | 11.096 | 11.0152 | 11.0007 | 10.9397 | 10.3784 | 9.7929 | 9.3677
|  | WATLINGTON | CT |  |  | 12.0684 | 12.0116 | 11.9057 | 11.7604 | 11.6129 | 11.4643 | 11.3541 | 11.2165 | 11.1414 | 10.9143 | 10.4079 | 9.8779 | 9.5071 | 10.8019 | 10.7965 | 10.7866 | 10.7347 | 10.6454 | 10.4803 | 10.36 | 10.2127 | 10.1272 | 9.8693 | 9.3123 | 8.7313 | 8.3103 | 11.3054 | 11.3054 | 11.3003 | 11.2511 | 11.2005 | 11.1484 | 11.096 | 11.0152 | 11.0007 | 10.9397 | 10.3784 | 9.7929 | 9.3677
|  | WATLINGTON | LW |  |  | 12.0816 | 12.0326 | 11.9425 | 11.8518 | 11.7572 | 11.6851 | 11.6101 | 11.5234 | 11.4539 | 11.2395 | 10.8691 | 10.4426 | 10.123 | 10.8031 | 10.7985 | 10.79 | 10.779 | 10.7647 | 10.7183 | 10.6334 | 10.5369 | 10.457 | 10.2118 | 9.7908 | 9.3132 | 8.9435 | 11.3054 | 11.3054 | 11.3027 | 11.294 | 11.2822 | 11.2687 | 11.2516 | 11.2216 | 11.2128 | 11.1772 | 10.8583 | 10.3764 | 10.0023
|  | WATLINGTON | ST |  |  | 12.2009 | 12.1717 | 12.1302 | 12.0402 | 11.9373 | 11.8499 | 11.7611 | 11.6526 | 11.5847 | 11.3738 | 11.0905 | 10.659 | 10.3841 | 10.8957 | 10.8929 | 10.8889 | 10.8466 | 10.8021 | 10.7577 | 10.7112 | 10.6403 | 10.6126 | 10.3927 | 10.0757 | 9.6114 | 9.3038 | 11.3951 | 11.3951 | 11.3951 | 11.3577 | 11.3152 | 11.2721 | 11.2269 | 11.1571 | 11.1306 | 11.0404 | 10.953 | 10.6815 | 10.3712
|  | WATLINGTON | FS |  |  | 12.2437 | 12.2373 | 12.2342 | 12.2199 | 12.2023 | 12.1861 | 12.1699 | 12.1497 | 12.132 | 12.0763 | 11.9922 | 11.8967 | 11.8061 | 10.8998 | 10.8992 | 10.8989 | 10.8975 | 10.8958 | 10.8942 | 10.8925 | 10.8903 | 10.8878 | 10.8775 | 10.8655 | 10.8372 | 10.8098 | 11.3951 | 11.3951 | 11.3951 | 11.3951 | 11.3951 | 11.395 | 11.3949 | 11.3946 | 11.3936 | 11.388 | 11.379 | 11.3526 | 11.3271
AMERSHAM | LOUDWATER BSP | WELL END | MINIMUM HEADROOM | SU 88511 87957 | YES | 29.4514 | 29.4514 | 29.4514 | 29.3376 | 29.2218 | 29.1042 | 28.9767 | 28.7742 | 28.7378 | 28.6258 | 28.15 | 27.0305 | 26.2092 | 27.5405 | 27.5283 | 27.504 | 27.3668 | 27.2277 | 27.0867 | 26.9527 | 26.7528 | 26.7188 | 26.6136 | 25.9852 | 24.7337 | 23.7838 | 28.585 | 28.585 | 28.585 | 28.4593 | 28.3195 | 28.1777 | 28.0434 | 27.8432 | 27.8089 | 27.4074 | 26.2124 | 24.9607 | 24.0105
|  | WELL END | CT |  |  | 29.4514 | 29.4514 | 29.4514 | 29.3376 | 29.2218 | 29.1042 | 28.9767 | 28.7742 | 28.7378 | 28.6258 | 28.15 | 27.0305 | 26.2092 | 27.5405 | 27.5283 | 27.504 | 27.3668 | 27.2277 | 27.0867 | 26.9527 | 26.7528 | 26.7188 | 26.6136 | 25.9852 | 24.7337 | 23.7838 | 28.585 | 28.585 | 28.585 | 28.4593 | 28.3195 | 28.1777 | 28.0434 | 27.8432 | 27.8089 | 27.4074 | 26.2124 | 24.9607 | 24.0105
|  | WELL END | LW |  |  | 29.4514 | 29.4514 | 29.4514 | 29.4352 | 29.4184 | 29.401 | 29.3828 | 29.3553 | 29.3514 | 29.3035 | 29.2253 | 28.7261 | 28.0069 | 27.5428 | 27.5318 | 27.5102 | 27.4732 | 27.4357 | 27.4076 | 27.3784 | 27.3404 | 27.3266 | 27.2854 | 27.2187 | 26.4948 | 25.6468 | 28.585 | 28.585 | 28.585 | 28.566 | 28.5278 | 28.4994 | 28.4699 | 28.4316 | 28.4174 | 28.3754 | 27.6265 | 26.7219 | 25.8737
|  | WELL END | ST |  |  | 29.4514 | 29.4514 | 29.4514 | 29.4514 | 29.4514 | 29.4514 | 29.4514 | 29.4514 | 29.4514 | 29.4514 | 29.4425 | 29.4032 | 29.365 | 27.5485 | 27.5417 | 27.5307 | 27.5177 | 27.5023 | 27.4934 | 27.4842 | 27.4771 | 27.4702 | 27.4511 | 27.4194 | 27.3878 | 27.3569 | 28.585 | 28.585 | 28.585 | 28.585 | 28.585 | 28.585 | 28.5768 | 28.5695 | 28.5624 | 28.5427 | 28.51 | 28.4102 | 27.8627
|  | WELL END | FS |  |  | 29.4514 | 29.4514 | 29.4514 | 29.4514 | 29.4514 | 29.4514 | 29.4514 | 29.4514 | 29.4514 | 29.4514 | 29.4514 | 29.4514 | 29.4514 | 27.5579 | 27.5564 | 27.5547 | 27.5509 | 27.5465 | 27.5432 | 27.5399 | 27.536 | 27.5334 | 27.526 | 27.5137 | 27.5016 | 27.49 | 28.585 | 28.585 | 28.585 | 28.585 | 28.585 | 28.585 | 28.585 | 28.585 | 28.585 | 28.585 | 28.585 | 28.585 | 28.5828
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | WEST END | MINIMUM HEADROOM | SU 57216 06147 | YES | 43.7212 | 43.7212 | 43.7212 | 43.7212 | 43.7212 | 43.7212 | 43.7212 | 43.7212 | 43.7212 | 43.7212 | 42.9093 | 41.58 | 40.256 | 41.112 | 41.1097 | 41.1053 | 41.1016 | 41.0971 | 41.0869 | 41.0773 | 41.065 | 41.0455 | 40.9724 | 40.5435 | 39.876 | 38.5432 | 42.5133 | 42.5133 | 42.5133 | 42.5133 | 42.5133 | 42.5116 | 42.4985 | 42.4848 | 42.4701 | 42.4275 | 42.2455 | 40.7927 | 39.2303
|  | WEST END | CT |  |  | 43.7212 | 43.7212 | 43.7212 | 43.7212 | 43.7212 | 43.7212 | 43.7212 | 43.7212 | 43.7212 | 43.7212 | 43.0295 | 41.7004 | 40.3767 | 41.1122 | 41.11 | 41.1059 | 41.1024 | 41.0981 | 41.0932 | 41.0836 | 41.0735 | 41.0568 | 41.0006 | 40.6039 | 39.9364 | 38.6719 | 42.5133 | 42.5133 | 42.5133 | 42.5133 | 42.5133 | 42.5133 | 42.507 | 42.4934 | 42.4786 | 42.4361 | 42.3392 | 40.9348 | 39.3727
|  | WEST END | LW |  |  | 43.7212 | 43.7212 | 43.7212 | 43.7212 | 43.7212 | 43.7212 | 43.7212 | 43.7212 | 43.7212 | 43.7212 | 42.9093 | 41.58 | 40.256 | 41.112 | 41.1097 | 41.1053 | 41.1016 | 41.0971 | 41.0869 | 41.0773 | 41.065 | 41.0455 | 40.9724 | 40.5435 | 39.876 | 38.5432 | 42.5133 | 42.5133 | 42.5133 | 42.5133 | 42.5133 | 42.5116 | 42.4985 | 42.4848 | 42.4701 | 42.4275 | 42.2455 | 40.7927 | 39.2303
|  | WEST END | ST |  |  | 43.7212 | 43.7212 | 43.7212 | 43.7212 | 43.7212 | 43.7212 | 43.7212 | 43.7212 | 43.7212 | 43.7212 | 43.7212 | 42.919 | 42.0708 | 41.1129 | 41.1113 | 41.1089 | 41.1065 | 41.1031 | 41.0951 | 41.0874 | 41.0806 | 41.0732 | 41.0373 | 40.9028 | 40.5484 | 40.1224 | 42.5133 | 42.5133 | 42.5133 | 42.5133 | 42.5133 | 42.5133 | 42.5123 | 42.503 | 42.4929 | 42.4639 | 42.4075 | 42.2531 | 41.3671
|  | WEST END | FS |  |  | 43.7212 | 43.7212 | 43.7212 | 43.7212 | 43.7212 | 43.7212 | 43.7212 | 43.7212 | 43.7212 | 43.7212 | 43.7212 | 43.7212 | 43.7212 | 41.1146 | 41.1141 | 41.1135 | 41.1128 | 41.1118 | 41.1092 | 41.1067 | 41.1036 | 41.1007 | 41.0924 | 41.0759 | 41.0458 | 41.0104 | 42.5133 | 42.5133 | 42.5133 | 42.5133 | 42.5133 | 42.5133 | 42.5133 | 42.5133 | 42.5133 | 42.5133 | 42.4966 | 42.4703 | 42.4434
MELKSHAM GSP | WEST GRAFTON | WEST GRAFTON VILLAGE | MINIMUM HEADROOM | SU 24639 60279 | YES | 13.614 | 13.614 | 13.614 | 13.6086 | 13.602 | 13.5941 | 13.5849 | 13.5687 | 13.5661 | 13.5549 | 13.5308 | 13.484 | 13.4808 | 13.235 | 13.1941 | 13.1076 | 13.0234 | 12.9397 | 12.8566 | 12.7965 | 12.7355 | 12.672 | 12.4793 | 12.1514 | 11.7917 | 11.481 | 13.8949 | 13.8949 | 13.8949 | 13.8895 | 13.8142 | 13.7359 | 13.6774 | 13.6179 | 13.556 | 13.3669 | 13.0469 | 12.6953 | 12.3926
|  | WEST GRAFTON VILLAGE | CT |  |  | 13.614 | 13.614 | 13.614 | 13.6137 | 13.6131 | 13.6123 | 13.6111 | 13.6085 | 13.608 | 13.6055 | 13.5847 | 13.5614 | 13.5543 | 13.235 | 13.1941 | 13.1076 | 13.0234 | 12.9397 | 12.8566 | 12.7965 | 12.7355 | 12.672 | 12.4839 | 12.1593 | 11.8232 | 11.5093 | 13.8949 | 13.8949 | 13.8949 | 13.8918 | 13.8142 | 13.7359 | 13.6774 | 13.6179 | 13.556 | 13.3727 | 13.056 | 12.728 | 12.422
|  | WEST GRAFTON VILLAGE | LW |  |  | 13.614 | 13.614 | 13.614 | 13.6086 | 13.602 | 13.5941 | 13.5849 | 13.5687 | 13.5661 | 13.5549 | 13.5308 | 13.484 | 13.4808 | 13.2398 | 13.2015 | 13.1204 | 13.0364 | 12.952 | 12.8846 | 12.8163 | 12.7417 | 12.6762 | 12.4793 | 12.1514 | 11.7917 | 11.481 | 13.8949 | 13.8949 | 13.8949 | 13.8895 | 13.8248 | 13.7617 | 13.6959 | 13.6228 | 13.559 | 13.3669 | 13.0469 | 12.6953 | 12.3926
|  | WEST GRAFTON VILLAGE | ST |  |  | 13.614 | 13.614 | 13.614 | 13.6138 | 13.6134 | 13.6127 | 13.6118 | 13.6098 | 13.6088 | 13.6036 | 13.5967 | 13.5725 | 13.5637 | 13.2574 | 13.2323 | 13.1891 | 13.136 | 13.0717 | 13.0363 | 13.0009 | 12.9589 | 12.9149 | 12.7845 | 12.5755 | 12.3499 | 12.1407 | 13.8949 | 13.8949 | 13.8949 | 13.8947 | 13.8943 | 13.8937 | 13.8708 | 13.8317 | 13.7909 | 13.6655 | 13.4617 | 13.2414 | 13.0374
|  | WEST GRAFTON VILLAGE | FS |  |  | 13.614 | 13.614 | 13.614 | 13.614 | 13.6139 | 13.6139 | 13.6139 | 13.6138 | 13.6135 | 13.6116 | 13.6101 | 13.6029 | 13.5958 | 13.2998 | 13.2969 | 13.2941 | 13.2809 | 13.2652 | 13.2532 | 13.2412 | 13.2258 | 13.2087 | 13.1583 | 13.0801 | 13.0003 | 12.9246 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8948 | 13.8948 | 13.8947 | 13.8944 | 13.8925 | 13.891 | 13.8696 | 13.7989
AXMINSTER | YEOVIL BSP | WEST HENDFORD | MINIMUM HEADROOM | ST 55000 15442 | YES | 52.5309 | 52.5269 | 52.5195 | 52.4427 | 52.3631 | 52.2777 | 52.1883 | 52.0579 | 52.0271 | 51.9207 | 51.7856 | 51.3421 | 50.7726 | 50.1648 | 50.1648 | 50.1648 | 50.0959 | 50.0248 | 49.9505 | 49.8736 | 49.7567 | 49.7405 | 49.6849 | 49.6019 | 49.4407 | 49.3028 | 51.1382 | 51.1382 | 51.1382 | 51.0693 | 50.9982 | 50.9239 | 50.8469 | 50.73 | 50.7138 | 50.6583 | 50.5753 | 50.2809 | 49.6592
|  | WEST HENDFORD | CT |  |  | 52.5313 | 52.5275 | 52.5205 | 52.513 | 52.505 | 52.4966 | 52.4842 | 52.4707 | 52.4561 | 52.4052 | 52.3532 | 52.123 | 51.5658 | 50.1648 | 50.1648 | 50.1648 | 50.1648 | 50.1648 | 50.1648 | 50.1648 | 50.1648 | 50.1648 | 50.1648 | 50.1648 | 50.1648 | 50.1055 | 51.1382 | 51.1382 | 51.1382 | 51.1382 | 51.1382 | 51.1382 | 51.1382 | 51.1382 | 51.1382 | 51.1382 | 51.1382 | 51.0671 | 50.4577
|  | WEST HENDFORD | LW |  |  | 52.5309 | 52.5269 | 52.5195 | 52.4427 | 52.3631 | 52.2777 | 52.1883 | 52.0579 | 52.0271 | 51.9207 | 51.7856 | 51.3421 | 50.7726 | 50.1648 | 50.1648 | 50.1648 | 50.0959 | 50.0248 | 49.9505 | 49.8736 | 49.7567 | 49.7405 | 49.6849 | 49.6019 | 49.4407 | 49.3028 | 51.1382 | 51.1382 | 51.1382 | 51.0693 | 50.9982 | 50.9239 | 50.8469 | 50.73 | 50.7138 | 50.6583 | 50.5753 | 50.2809 | 49.6592
|  | WEST HENDFORD | ST |  |  | 52.5317 | 52.5289 | 52.5243 | 52.5188 | 52.5123 | 52.5047 | 52.4964 | 52.4873 | 52.4773 | 52.4415 | 52.4057 | 52.3749 | 52.3453 | 50.1648 | 50.1648 | 50.1648 | 50.1648 | 50.1648 | 50.1648 | 50.1648 | 50.1648 | 50.1648 | 50.1648 | 50.1648 | 50.1648 | 50.1648 | 51.1382 | 51.1382 | 51.1382 | 51.1382 | 51.1382 | 51.1382 | 51.1382 | 51.1382 | 51.1382 | 51.1382 | 51.1382 | 51.1382 | 51.1382
|  | WEST HENDFORD | FS |  |  | 52.5342 | 52.5332 | 52.5318 | 52.5298 | 52.5276 | 52.5248 | 52.5217 | 52.518 | 52.5141 | 52.5 | 52.4858 | 52.4733 | 52.4613 | 50.1648 | 50.1648 | 50.1648 | 50.1648 | 50.1648 | 50.1648 | 50.1648 | 50.1648 | 50.1648 | 50.1648 | 50.1648 | 50.1648 | 50.1648 | 51.1382 | 51.1382 | 51.1382 | 51.1382 | 51.1382 | 51.1382 | 51.1382 | 51.1382 | 51.1382 | 51.1382 | 51.1382 | 51.1382 | 51.1382
MANNINGTON GSP | SHAFTESBURY BSP | WEST STOUR | MINIMUM HEADROOM | ST 77699 22040 | YES | 11.4932 | 11.4884 | 11.4783 | 11.3923 | 11.3012 | 11.164 | 11.0198 | 10.8184 | 10.7449 | 10.5081 | 10.1063 | 9.5312 | 9.2582 | 10.1617 | 10.1559 | 10.1437 | 10.0557 | 9.9625 | 9.8155 | 9.6615 | 9.4504 | 9.3664 | 9.0986 | 8.6459 | 8.0181 | 7.6934 | 10.7623 | 10.7574 | 10.7469 | 10.6606 | 10.5691 | 10.4304 | 10.2847 | 10.0817 | 10.0066 | 9.7648 | 9.355 | 8.7715 | 8.4893
|  | WEST STOUR | CT |  |  | 11.4932 | 11.4884 | 11.4783 | 11.4653 | 11.4516 | 11.4372 | 11.3823 | 11.3201 | 11.2666 | 11.1043 | 10.7678 | 10.4091 | 10.1255 | 10.1617 | 10.1559 | 10.1437 | 10.1287 | 10.113 | 10.0966 | 10.0318 | 9.9599 | 9.8959 | 9.7027 | 9.3153 | 8.9039 | 8.5685 | 10.7623 | 10.7574 | 10.7469 | 10.7336 | 10.7196 | 10.7049 | 10.6484 | 10.5847 | 10.5295 | 10.3623 | 10.0178 | 9.6507 | 9.3588
|  | WEST STOUR | LW |  |  | 11.4932 | 11.4884 | 11.4783 | 11.3923 | 11.3012 | 11.164 | 11.0198 | 10.8184 | 10.7449 | 10.5081 | 10.1063 | 9.5312 | 9.2582 | 10.1617 | 10.1559 | 10.1437 | 10.0557 | 9.9625 | 9.8155 | 9.6615 | 9.4504 | 9.3664 | 9.0986 | 8.6459 | 8.0181 | 7.6934 | 10.7623 | 10.7574 | 10.7469 | 10.6606 | 10.5691 | 10.4304 | 10.2847 | 10.0817 | 10.0066 | 9.7648 | 9.355 | 8.7715 | 8.4893
|  | WEST STOUR | ST |  |  | 11.5529 | 11.4937 | 11.4892 | 11.4794 | 11.4679 | 11.4361 | 11.4034 | 11.3579 | 11.3177 | 11.1922 | 10.9993 | 10.739 | 10.5409 | 10.2336 | 10.1623 | 10.1568 | 10.1459 | 10.133 | 10.0959 | 10.0579 | 10.0057 | 9.9584 | 9.812 | 9.5852 | 9.2909 | 9.0592 | 10.8239 | 10.7628 | 10.7581 | 10.7482 | 10.7364 | 10.7038 | 10.6703 | 10.6237 | 10.5824 | 10.4536 | 10.2553 | 9.9896 | 9.7862
|  | WEST STOUR | FS |  |  | 11.5572 | 11.5004 | 11.5 | 11.497 | 11.4937 | 11.484 | 11.4744 | 11.4613 | 11.4403 | 11.3747 | 11.2976 | 11.1847 | 11.081 | 10.2388 | 10.1703 | 10.1699 | 10.1665 | 10.1629 | 10.1515 | 10.1402 | 10.125 | 10.1012 | 10.0275 | 9.9376 | 9.8124 | 9.6971 | 10.8284 | 10.7697 | 10.7693 | 10.7663 | 10.7629 | 10.7529 | 10.7431 | 10.7296 | 10.7082 | 10.6413 | 10.5621 | 10.4473 | 10.3418
MANNINGTON GSP | BOURNEMOUTH | WESTBOURNE | MINIMUM HEADROOM | SZ 07642 91485 | YES | 45.6281 | 45.6281 | 45.6281 | 45.6281 | 45.6281 | 45.6281 | 45.6281 | 45.6281 | 45.6281 | 45.6281 | 44.925 | 43.2174 | 41.4815 | 41.5563 | 41.5505 | 41.5387 | 41.526 | 41.5129 | 41.505 | 41.4969 | 41.4884 | 41.4793 | 41.4513 | 39.99 | 38.0283 | 36.0425 | 43.2413 | 43.2413 | 43.2413 | 43.2413 | 43.2413 | 43.2413 | 43.2413 | 43.2413 | 43.2413 | 43.2413 | 42.4089 | 40.4384 | 38.4249
|  | WESTBOURNE | CT |  |  | 45.6281 | 45.6281 | 45.6281 | 45.6281 | 45.6281 | 45.6281 | 45.6281 | 45.6281 | 45.6281 | 45.6281 | 44.925 | 43.2174 | 41.4815 | 41.5572 | 41.5518 | 41.541 | 41.5293 | 41.5172 | 41.505 | 41.4969 | 41.4884 | 41.4793 | 41.4513 | 39.99 | 38.0283 | 36.0425 | 43.2413 | 43.2413 | 43.2413 | 43.2413 | 43.2413 | 43.2413 | 43.2413 | 43.2413 | 43.2413 | 43.2413 | 42.4089 | 40.4384 | 38.4249
|  | WESTBOURNE | LW |  |  | 45.6281 | 45.6281 | 45.6281 | 45.6281 | 45.6281 | 45.6281 | 45.6281 | 45.6281 | 45.6281 | 45.6281 | 44.9309 | 43.2235 | 41.4877 | 41.5563 | 41.5505 | 41.5387 | 41.526 | 41.5129 | 41.5053 | 41.4973 | 41.4888 | 41.4797 | 41.4516 | 39.9972 | 38.0353 | 36.0496 | 43.2413 | 43.2413 | 43.2413 | 43.2413 | 43.2413 | 43.2413 | 43.2413 | 43.2413 | 43.2413 | 43.2413 | 42.4162 | 40.4454 | 38.4322
|  | WESTBOURNE | ST |  |  | 45.6281 | 45.6281 | 45.6281 | 45.6281 | 45.6281 | 45.6281 | 45.6281 | 45.6281 | 45.6281 | 45.6281 | 45.6079 | 44.5874 | 43.4913 | 41.5578 | 41.5533 | 41.546 | 41.5363 | 41.5246 | 41.515 | 41.5052 | 41.4995 | 41.4933 | 41.4738 | 40.8977 | 39.5956 | 38.3417 | 43.2413 | 43.2413 | 43.2413 | 43.2413 | 43.2413 | 43.2413 | 43.2413 | 43.2413 | 43.2413 | 43.2413 | 43.2413 | 42.0128 | 40.7532
|  | WESTBOURNE | FS |  |  | 45.6281 | 45.6281 | 45.6281 | 45.6281 | 45.6281 | 45.6281 | 45.6281 | 45.6281 | 45.6281 | 45.6281 | 45.6281 | 45.6281 | 45.6281 | 41.5647 | 41.564 | 41.5633 | 41.5608 | 41.5579 | 41.5545 | 41.551 | 41.5467 | 41.5443 | 41.5367 | 41.5149 | 41.484 | 41.4508 | 43.2413 | 43.2413 | 43.2413 | 43.2413 | 43.2413 | 43.2413 | 43.2413 | 43.2413 | 43.2413 | 43.2413 | 43.2413 | 43.2413 | 43.2413
MELKSHAM GSP | FROME BSP | WESTBURY | MINIMUM HEADROOM | ST 87654 51530 | YES | 29.883 | 29.8106 | 29.669 | 29.535 | 29.3995 | 29.2033 | 29.0044 | 28.7926 | 28.5921 | 27.9911 | 26.9828 | 25.8958 | 24.9411 | 28.2841 | 28.2013 | 28.0393 | 27.8864 | 27.7325 | 27.5095 | 27.284 | 27.046 | 26.8173 | 26.1336 | 24.9892 | 23.7464 | 22.6343 | 28.3657 | 28.2865 | 28.1316 | 27.9853 | 27.8378 | 27.6243 | 27.408 | 27.1791 | 26.9603 | 26.3054 | 25.2086 | 24.0312 | 22.9589
|  | WESTBURY | CT |  |  | 29.9179 | 29.8646 | 29.7637 | 29.6712 | 29.5796 | 29.4874 | 29.2991 | 29.1078 | 28.9109 | 28.3273 | 27.3118 | 26.2696 | 25.2995 | 28.324 | 28.2631 | 28.1476 | 28.042 | 27.9374 | 27.8324 | 27.6175 | 27.4 | 27.1749 | 26.5085 | 25.3569 | 24.165 | 23.0376 | 28.4038 | 28.3456 | 28.2352 | 28.1342 | 28.0341 | 27.9335 | 27.7279 | 27.5196 | 27.3043 | 26.6669 | 25.5628 | 24.4303 | 23.3575
|  | WESTBURY | LW |  |  | 29.883 | 29.8106 | 29.669 | 29.535 | 29.3995 | 29.2033 | 29.0044 | 28.7926 | 28.5921 | 27.9911 | 26.9828 | 25.8958 | 24.9411 | 28.2841 | 28.2013 | 28.0393 | 27.8864 | 27.7325 | 27.5095 | 27.284 | 27.046 | 26.8173 | 26.1336 | 24.9892 | 23.7464 | 22.6343 | 28.3657 | 28.2865 | 28.1316 | 27.9853 | 27.8378 | 27.6243 | 27.408 | 27.1791 | 26.9603 | 26.3054 | 25.2086 | 24.0312 | 22.9589
|  | WESTBURY | ST |  |  | 29.9154 | 29.8665 | 29.7879 | 29.6973 | 29.5887 | 29.4813 | 29.374 | 29.2425 | 29.1057 | 28.7 | 28.0472 | 27.3452 | 26.7001 | 28.3212 | 28.2652 | 28.1753 | 28.0717 | 27.9477 | 27.8252 | 27.7029 | 27.5534 | 27.3974 | 26.9358 | 26.1923 | 25.4009 | 24.6658 | 28.4012 | 28.3476 | 28.2617 | 28.1626 | 28.044 | 27.9267 | 27.8097 | 27.6665 | 27.5172 | 27.0751 | 26.3633 | 25.6031 | 24.9003
|  | WESTBURY | FS |  |  | 30.1823 | 29.9833 | 29.9749 | 29.9552 | 29.9327 | 29.9012 | 29.87 | 29.83 | 29.7772 | 29.6205 | 29.3763 | 29.1265 | 28.8912 | 28.6265 | 28.3989 | 28.3892 | 28.3667 | 28.341 | 28.3049 | 28.2693 | 28.2236 | 28.1633 | 27.985 | 27.7063 | 27.4241 | 27.1583 | 28.693 | 28.4754 | 28.4662 | 28.4447 | 28.4201 | 28.3856 | 28.3515 | 28.3078 | 28.2501 | 28.0794 | 27.8127 | 27.5418 | 27.2867
NURSLING GSP | SOUTHAMPTON (2 X 90) | WESTERN ESPLANADE | MINIMUM HEADROOM | SU 41618 12009 | YES | 87.994 | 87.98 | 87.1312 | 87.0616 | 86.992 | 86.9224 | 86.8528 | 86.7833 | 86.7554 | 86.6719 | 86.5328 | 85.7911 | 84.4553 | 82.0692 | 82.0446 | 81.1755 | 81.0904 | 81.0014 | 80.919 | 80.8363 | 80.7525 | 80.71 | 79.7453 | 78.1682 | 76.5561 | 74.9105 | 85.1052 | 85.0913 | 84.2424 | 84.1728 | 84.1032 | 84.0337 | 83.9641 | 83.7001 | 83.3679 | 82.3431 | 80.8181 | 79.2614 | 77.6698
|  | WESTERN ESPLANADE | CT |  |  | 88.0663 | 88.058 | 87.5486 | 87.5069 | 87.4651 | 87.4234 | 87.3816 | 87.3399 | 87.3232 | 87.2731 | 86.6641 | 85.9364 | 84.6005 | 82.1437 | 82.1259 | 81.5989 | 81.5441 | 81.4854 | 81.4281 | 81.3733 | 81.3172 | 81.2859 | 80.5298 | 78.4828 | 76.7394 | 75.0938 | 85.1776 | 85.1692 | 84.6599 | 84.6181 | 84.5764 | 84.5347 | 84.4929 | 84.4252 | 84.1041 | 83.1209 | 81.126 | 79.438 | 77.8465
|  | WESTERN ESPLANADE | LW |  |  | 87.994 | 87.98 | 87.1312 | 87.0616 | 86.992 | 86.9224 | 86.8528 | 86.7833 | 86.7554 | 86.6719 | 86.5328 | 85.7911 | 84.4553 | 82.0692 | 82.0446 | 81.1755 | 81.0904 | 81.0014 | 80.919 | 80.8363 | 80.7525 | 80.71 | 79.7453 | 78.1682 | 76.5561 | 74.9105 | 85.1052 | 85.0913 | 84.2424 | 84.1728 | 84.1032 | 84.0337 | 83.9641 | 83.7001 | 83.3679 | 82.3431 | 80.8181 | 79.2614 | 77.6698
|  | WESTERN ESPLANADE | ST |  |  | 88.1025 | 88.0969 | 87.7574 | 87.7295 | 87.7017 | 87.6739 | 87.6461 | 87.6182 | 87.6071 | 87.5737 | 87.518 | 87.4846 | 87.4234 | 82.1866 | 82.1695 | 81.8185 | 81.7809 | 81.7391 | 81.7005 | 81.6619 | 81.6245 | 81.6033 | 81.5393 | 80.8332 | 79.7941 | 78.7818 | 85.2138 | 85.2082 | 84.8686 | 84.8408 | 84.813 | 84.7851 | 84.7573 | 84.7295 | 84.7183 | 84.4153 | 83.4222 | 82.4196 | 81.4417
|  | WESTERN ESPLANADE | FS |  |  | 88.1387 | 88.1359 | 87.9661 | 87.9522 | 87.9383 | 87.9244 | 87.9105 | 87.8965 | 87.891 | 87.8743 | 87.8464 | 87.8297 | 87.7991 | 82.2291 | 82.2189 | 82.0453 | 82.0278 | 82.0087 | 81.9906 | 81.9725 | 81.9535 | 81.944 | 81.9153 | 81.8695 | 81.833 | 81.7823 | 85.2499 | 85.2472 | 85.0774 | 85.0635 | 85.0495 | 85.0356 | 85.0217 | 85.0078 | 85.0022 | 84.9855 | 84.9577 | 84.941 | 84.9104
BOTLEY WOOD GSP | NETLEY COMMON BSP | WESTON | MINIMUM HEADROOM | SU 45207 09912 | YES | 29.2843 | 29.2843 | 29.2843 | 29.0658 | 28.8403 | 28.6047 | 28.3605 | 27.9897 | 27.9383 | 27.7623 | 27.4989 | 26.6064 | 25.1196 | 26.2537 | 26.2346 | 26.2039 | 25.962 | 25.703 | 25.3229 | 24.9325 | 24.4144 | 24.2076 | 23.5192 | 21.9396 | 19.8239 | 18.1273 | 27.9032 | 27.9032 | 27.9032 | 27.6847 | 27.4592 | 27.2236 | 26.9794 | 26.6086 | 26.5572 | 26.3811 | 25.4475 | 23.3243 | 21.6202
|  | WESTON | CT |  |  | 29.2843 | 29.2843 | 29.2843 | 29.2843 | 29.2843 | 29.2843 | 29.2843 | 29.2843 | 29.2843 | 29.2843 | 29.2843 | 28.9379 | 27.4807 | 26.2537 | 26.2346 | 26.2039 | 26.1711 | 26.1348 | 26.0976 | 25.9514 | 25.804 | 25.6485 | 25.1363 | 23.82 | 22.1674 | 20.5004 | 27.9032 | 27.9032 | 27.9032 | 27.9032 | 27.9032 | 27.9032 | 27.9032 | 27.9032 | 27.9032 | 27.9032 | 27.3283 | 25.6682 | 23.9937
|  | WESTON | LW |  |  | 29.2843 | 29.2843 | 29.2843 | 29.0658 | 28.8403 | 28.6047 | 28.3605 | 27.9897 | 27.9383 | 27.7623 | 27.4989 | 26.6064 | 25.1196 | 26.2562 | 26.2384 | 26.2106 | 25.962 | 25.703 | 25.3229 | 24.9325 | 24.4144 | 24.2076 | 23.5192 | 21.9396 | 19.8239 | 18.1273 | 27.9032 | 27.9032 | 27.9032 | 27.6847 | 27.4592 | 27.2236 | 26.9794 | 26.6086 | 26.5572 | 26.3811 | 25.4475 | 23.3243 | 21.6202
|  | WESTON | ST |  |  | 29.2843 | 29.2843 | 29.2843 | 29.2843 | 29.2843 | 29.2843 | 29.2843 | 29.2843 | 29.2843 | 29.2843 | 29.2843 | 29.2843 | 29.1687 | 26.2638 | 26.2524 | 26.237 | 26.2183 | 26.1957 | 26.1262 | 26.0554 | 25.955 | 25.8488 | 25.4969 | 24.5818 | 23.4901 | 22.4314 | 27.9032 | 27.9032 | 27.9032 | 27.9032 | 27.9032 | 27.9032 | 27.9032 | 27.9032 | 27.9032 | 27.9032 | 27.9032 | 26.9969 | 25.9334
|  | WESTON | FS |  |  | 29.2843 | 29.2843 | 29.2843 | 29.2835 | 29.2787 | 29.2738 | 29.2689 | 29.2613 | 29.2399 | 29.1723 | 29.1401 | 29.0386 | 28.9538 | 26.2724 | 26.2669 | 26.2611 | 26.2524 | 26.2387 | 26.2136 | 26.1883 | 26.1558 | 26.0929 | 25.8878 | 25.4784 | 24.8725 | 24.2515 | 27.9032 | 27.9032 | 27.9032 | 27.9024 | 27.8976 | 27.8927 | 27.8878 | 27.8802 | 27.8588 | 27.7912 | 27.759 | 27.6575 | 27.5727
CHICKERELL GSP | CHICKERELL BSP | WEYMOUTH | MINIMUM HEADROOM | SY 67443 79096 | YES | 37.6625 | 37.6625 | 37.6625 | 37.63 | 37.597 | 37.5633 | 37.5285 | 37.4747 | 37.4564 | 37.3981 | 37.3512 | 37.1974 | 36.2565 | 35.1886 | 35.1852 | 35.1794 | 35.145 | 35.1051 | 35.0601 | 35.0149 | 34.9482 | 34.9162 | 34.8189 | 33.6834 | 31.5271 | 29.4191 | 34.4487 | 34.4487 | 34.4487 | 34.4162 | 34.3832 | 34.3495 | 34.3147 | 34.2608 | 34.2425 | 34.1842 | 34.084 | 31.9409 | 29.8335
|  | WEYMOUTH | CT |  |  | 37.6625 | 37.6625 | 37.6625 | 37.6625 | 37.6625 | 37.6625 | 37.6625 | 37.6625 | 37.6625 | 37.6625 | 37.6625 | 37.6625 | 36.4589 | 35.1886 | 35.1852 | 35.1794 | 35.1675 | 35.1574 | 35.148 | 35.1287 | 35.1099 | 35.0898 | 35.0327 | 33.9141 | 31.758 | 29.6506 | 34.4487 | 34.4487 | 34.4487 | 34.4487 | 34.4487 | 34.4487 | 34.4487 | 34.4487 | 34.4487 | 34.4487 | 34.3107 | 32.1704 | 30.069
|  | WEYMOUTH | LW |  |  | 37.6625 | 37.6625 | 37.6625 | 37.6625 | 37.6625 | 37.6625 | 37.6625 | 37.6625 | 37.6625 | 37.6625 | 37.6625 | 37.6625 | 36.2565 | 35.1886 | 35.1852 | 35.1794 | 35.1675 | 35.1574 | 35.1367 | 35.1174 | 35.0986 | 35.0785 | 35.0214 | 33.6834 | 31.5271 | 29.4191 | 34.4487 | 34.4487 | 34.4487 | 34.4487 | 34.4487 | 34.4487 | 34.4487 | 34.4487 | 34.4487 | 34.4487 | 34.084 | 31.9409 | 29.8335
|  | WEYMOUTH | ST |  |  | 37.6625 | 37.6625 | 37.6625 | 37.63 | 37.597 | 37.5633 | 37.5285 | 37.4747 | 37.4564 | 37.3981 | 37.3512 | 37.1974 | 37.1496 | 35.1902 | 35.1881 | 35.1851 | 35.145 | 35.1051 | 35.0601 | 35.0149 | 34.9482 | 34.9162 | 34.8189 | 34.7024 | 33.7462 | 32.3407 | 34.4487 | 34.4487 | 34.4487 | 34.4162 | 34.3832 | 34.3495 | 34.3147 | 34.2608 | 34.2425 | 34.1842 | 34.1373 | 33.9083 | 32.7464
|  | WEYMOUTH | FS |  |  | 37.6625 | 37.6625 | 37.6625 | 37.6625 | 37.6625 | 37.6625 | 37.6625 | 37.6625 | 37.6625 | 37.6625 | 37.6625 | 37.6625 | 37.6625 | 35.2051 | 35.1913 | 35.1904 | 35.1869 | 35.1842 | 35.1803 | 35.1769 | 35.173 | 35.1677 | 35.1526 | 35.1251 | 35.0974 | 35.0702 | 34.4487 | 34.4487 | 34.4487 | 34.4487 | 34.4487 | 34.4487 | 34.4487 | 34.4487 | 34.4487 | 34.4487 | 34.4487 | 34.4487 | 34.4487
COWLEY GSP | HEADINGTON BSP | WHEATLEY | MINIMUM HEADROOM | SP 60777 05379 | NO | 18.7624 | 18.6783 | 51.6196 | 51.4469 | 51.2574 | 51.1398 | 51.0045 | 50.8187 | 50.7086 | 50.3312 | 49.8131 | 48.9865 | 48.5359 | 20.4629 | 20.4383 | 52.0917 | 52.0169 | 51.8868 | 51.7695 | 51.6449 | 51.4567 | 51.3788 | 51.1173 | 50.5284 | 49.6262 | 49.0807 | 21.1369 | 21.1298 | 54.5164 | 54.4294 | 54.3235 | 54.2179 | 54.1052 | 53.9279 | 53.862 | 53.6348 | 53.4167 | 52.5559 | 52.05
|  | WHEATLEY | CT |  |  | 18.7802 | 18.7059 | 51.6677 | 51.5125 | 51.3503 | 51.2164 | 51.1109 | 50.9808 | 50.8887 | 50.612 | 49.9761 | 49.3142 | 48.865 | 20.4681 | 20.4463 | 52.1058 | 52.0495 | 51.9886 | 51.9334 | 51.882 | 51.8066 | 51.774 | 51.5052 | 50.7123 | 49.8945 | 49.2956 | 21.1384 | 21.1321 | 54.5205 | 54.4934 | 54.4625 | 54.4305 | 54.3951 | 54.3359 | 54.3209 | 54.2658 | 53.5951 | 52.8186 | 52.2594
|  | WHEATLEY | LW |  |  | 18.7624 | 18.6783 | 51.6196 | 51.4469 | 51.2574 | 51.1398 | 51.0045 | 50.8187 | 50.717 | 50.3916 | 49.8131 | 49.0669 | 48.6711 | 20.4629 | 20.4383 | 52.0917 | 52.032 | 51.9578 | 51.8936 | 51.8124 | 51.6814 | 51.6391 | 51.2638 | 50.5284 | 49.6262 | 49.0807 | 21.1369 | 21.1298 | 54.5164 | 54.4902 | 54.4501 | 54.4016 | 54.3365 | 54.2216 | 54.1969 | 54.0932 | 53.4167 | 52.5559 | 52.05
|  | WHEATLEY | ST |  |  | 18.8065 | 18.7552 | 51.7756 | 51.5862 | 51.3741 | 51.2171 | 51.0526 | 50.827 | 50.7086 | 50.3312 | 49.8754 | 48.9865 | 48.5359 | 20.4759 | 20.4608 | 52.1375 | 52.0169 | 51.8868 | 51.7695 | 51.6449 | 51.4567 | 51.3788 | 51.1173 | 50.8173 | 49.8279 | 49.2797 | 21.1406 | 21.1363 | 54.5296 | 54.4294 | 54.3235 | 54.2179 | 54.1052 | 53.9279 | 53.862 | 53.6348 | 53.4183 | 52.6827 | 52.1604
|  | WHEATLEY | FS |  |  | 18.8743 | 18.861 | 51.9474 | 51.9199 | 51.8887 | 51.8694 | 51.8496 | 51.8234 | 51.7957 | 51.7012 | 51.5769 | 51.369 | 51.1721 | 20.4958 | 20.4918 | 52.1879 | 52.1797 | 52.1704 | 52.1644 | 52.1582 | 52.1495 | 52.1376 | 52.088 | 52.0342 | 51.8908 | 51.7528 | 21.1463 | 21.1452 | 54.544 | 54.5416 | 54.5388 | 54.5368 | 54.5345 | 54.531 | 54.5238 | 54.4874 | 54.4545 | 54.3302 | 54.2097
BRAMLEY (ANDO-THAT) | ANDOVER BSP | WHITCHURCH | MINIMUM HEADROOM | SU 45924 48466 | YES | 8.3898 | 8.3406 | 8.2364 | 8.1322 | 8.0286 | 7.9258 | 7.8755 | 7.8228 | 7.7723 | 7.6223 | 7.3558 | 7.0768 | 6.8199 | 8.0196 | 7.9616 | 7.8391 | 7.717 | 7.5958 | 7.4755 | 7.417 | 7.3562 | 7.297 | 7.1211 | 6.8115 | 6.4877 | 6.1866 | 9.3002 | 9.2506 | 9.1458 | 9.041 | 8.9369 | 8.8335 | 8.7829 | 8.7299 | 8.6792 | 8.5283 | 8.2603 | 7.9799 | 7.7215
|  | WHITCHURCH | CT |  |  | 8.3898 | 8.3406 | 8.2364 | 8.1322 | 8.0286 | 7.9258 | 7.8755 | 7.8228 | 7.7723 | 7.6223 | 7.3558 | 7.0768 | 6.8199 | 8.0196 | 7.9616 | 7.8391 | 7.717 | 7.5958 | 7.4755 | 7.417 | 7.3562 | 7.297 | 7.1211 | 6.8115 | 6.4877 | 6.1866 | 9.3002 | 9.2506 | 9.1458 | 9.041 | 8.9369 | 8.8335 | 8.7829 | 8.7299 | 8.6792 | 8.5283 | 8.2603 | 7.9799 | 7.7215
|  | WHITCHURCH | LW |  |  | 8.3903 | 8.3412 | 8.2374 | 8.1362 | 8.0353 | 7.9867 | 7.9376 | 7.8863 | 7.8358 | 7.6847 | 7.4291 | 7.1525 | 6.9011 | 8.0201 | 7.9624 | 7.8403 | 7.7213 | 7.6028 | 7.5459 | 7.4887 | 7.4292 | 7.3701 | 7.193 | 6.8943 | 6.5729 | 6.2773 | 9.3006 | 9.2512 | 9.1469 | 9.0451 | 8.9436 | 8.8946 | 8.8453 | 8.7937 | 8.743 | 8.591 | 8.3339 | 8.0558 | 7.803
|  | WHITCHURCH | ST |  |  | 8.4236 | 8.3965 | 8.3502 | 8.2933 | 8.2245 | 8.1896 | 8.1549 | 8.1223 | 8.0879 | 7.9859 | 7.8192 | 7.6405 | 7.4726 | 8.0593 | 8.0275 | 7.973 | 7.9061 | 7.8252 | 7.7842 | 7.7434 | 7.7053 | 7.665 | 7.5455 | 7.3501 | 7.1425 | 6.9459 | 9.3341 | 9.3069 | 9.2603 | 9.2031 | 9.1339 | 9.0988 | 9.0639 | 9.0311 | 8.9965 | 8.8939 | 8.7262 | 8.5466 | 8.3778
|  | WHITCHURCH | FS |  |  | 8.4671 | 8.4633 | 8.4597 | 8.4429 | 8.4229 | 8.411 | 8.3991 | 8.3838 | 8.3705 | 8.3312 | 8.2685 | 8.2041 | 8.1426 | 8.1105 | 8.1061 | 8.1018 | 8.0821 | 8.0586 | 8.0445 | 8.0306 | 8.0125 | 7.997 | 7.9509 | 7.8773 | 7.8023 | 7.7307 | 9.3779 | 9.3741 | 9.3705 | 9.3536 | 9.3335 | 9.3214 | 9.3095 | 9.2941 | 9.2807 | 9.2412 | 9.1781 | 9.1133 | 9.0516
BOTLEY WOOD GSP | BOTLEY WOOD BSP | WHITELEY | MINIMUM HEADROOM | SU 52936 08794 | NO | 47.9694 | 47.9694 | 47.9694 | 47.8364 | 47.6993 | 47.556 | 47.2953 | 46.8416 | 46.5974 | 45.9241 | 44.9514 | 43.9503 | 43.2619 | 43.8654 | 43.8654 | 43.8654 | 43.7324 | 43.5953 | 43.452 | 43.1381 | 42.5992 | 42.2754 | 41.3905 | 40.1872 | 39.0723 | 38.2766 | 45.2 | 45.2 | 45.1988 | 45.0396 | 44.8751 | 44.715 | 44.2918 | 43.7474 | 43.4185 | 42.5199 | 41.2983 | 40.169 | 39.3596
|  | WHITELEY | CT |  |  | 47.9694 | 47.9694 | 47.9694 | 47.8695 | 47.7678 | 47.6646 | 47.5184 | 47.1239 | 46.8899 | 46.256 | 45.1444 | 44.0785 | 43.3172 | 43.8654 | 43.8654 | 43.8654 | 43.7655 | 43.6638 | 43.5605 | 43.3887 | 42.9091 | 42.5954 | 41.7501 | 40.3942 | 39.2145 | 38.3459 | 45.2 | 45.2 | 45.2 | 45.0834 | 44.9576 | 44.8294 | 44.5442 | 44.0591 | 43.7403 | 42.8813 | 41.5071 | 40.3129 | 39.4307
|  | WHITELEY | LW |  |  | 47.9694 | 47.9694 | 47.9694 | 47.8364 | 47.6993 | 47.556 | 47.2953 | 46.8416 | 46.5974 | 45.9241 | 44.9514 | 43.9503 | 43.2619 | 43.8654 | 43.8654 | 43.8654 | 43.7324 | 43.5953 | 43.452 | 43.1381 | 42.5992 | 42.2754 | 41.3905 | 40.1872 | 39.0723 | 38.2766 | 45.2 | 45.2 | 45.1988 | 45.0396 | 44.8751 | 44.715 | 44.2918 | 43.7474 | 43.4185 | 42.5199 | 41.2983 | 40.169 | 39.3596
|  | WHITELEY | ST |  |  | 47.9694 | 47.9694 | 47.9694 | 47.9676 | 47.9658 | 47.9639 | 47.962 | 47.9591 | 47.958 | 47.8304 | 47.3033 | 46.9052 | 46.5363 | 43.8654 | 43.8654 | 43.8654 | 43.8636 | 43.8618 | 43.8599 | 43.858 | 43.855 | 43.854 | 43.6686 | 42.9455 | 42.4014 | 41.8957 | 45.2 | 45.2 | 45.2 | 45.1982 | 45.1873 | 45.1725 | 45.1568 | 45.1417 | 45.1292 | 44.822 | 44.0863 | 43.5328 | 43.0182
|  | WHITELEY | FS |  |  | 47.9694 | 47.9694 | 47.9694 | 47.9689 | 47.9684 | 47.968 | 47.9675 | 47.9667 | 47.9647 | 47.9581 | 47.955 | 47.9451 | 47.9369 | 43.8654 | 43.8654 | 43.8654 | 43.8649 | 43.8644 | 43.8639 | 43.8635 | 43.8627 | 43.8607 | 43.8541 | 43.851 | 43.8411 | 43.8329 | 45.2 | 45.2 | 45.2 | 45.1995 | 45.1991 | 45.1986 | 45.1981 | 45.1974 | 45.1953 | 45.1888 | 45.1752 | 45.1532 | 45.1339
BRAMLEY (FLEE) | BURGHFIELD MAIN | WHITLEY WOOD | MINIMUM HEADROOM | SU 72812 69667 | YES | 38.0366 | 37.9991 | 37.9063 | 37.8078 | 37.7251 | 37.625 | 37.5111 | 37.3961 | 37.2715 | 36.908 | 36.3102 | 35.6941 | 35.0916 | 45.2945 | 45.2676 | 45.2014 | 45.1309 | 45.0718 | 45.0003 | 44.9189 | 44.8367 | 44.7477 | 44.4879 | 44.0606 | 43.6204 | 43.1898 | 41.907 | 41.9042 | 41.8972 | 41.8898 | 41.8836 | 41.876 | 41.8675 | 41.8588 | 41.8495 | 41.8221 | 41.7772 | 41.7309 | 41.6856
|  | WHITLEY WOOD | CT |  |  | 38.0366 | 37.9991 | 37.9063 | 37.8078 | 37.7251 | 37.6494 | 37.5355 | 37.4205 | 37.2959 | 36.9323 | 36.3345 | 35.7184 | 35.1164 | 45.2945 | 45.2676 | 45.2014 | 45.1309 | 45.0718 | 45.0177 | 44.9363 | 44.8541 | 44.7651 | 44.5053 | 44.078 | 43.6377 | 43.2075 | 41.907 | 41.9042 | 41.8972 | 41.8898 | 41.8836 | 41.8779 | 41.8693 | 41.8607 | 41.8513 | 41.824 | 41.779 | 41.7327 | 41.6874
|  | WHITLEY WOOD | LW |  |  | 38.0395 | 38.0036 | 37.9143 | 37.819 | 37.7395 | 37.625 | 37.5111 | 37.3961 | 37.2715 | 36.908 | 36.3102 | 35.6941 | 35.0916 | 45.2965 | 45.2708 | 45.207 | 45.139 | 45.0821 | 45.0003 | 44.9189 | 44.8367 | 44.7477 | 44.4879 | 44.0606 | 43.6204 | 43.1898 | 41.9072 | 41.9045 | 41.8978 | 41.8906 | 41.8846 | 41.876 | 41.8675 | 41.8588 | 41.8495 | 41.8221 | 41.7772 | 41.7309 | 41.6856
|  | WHITLEY WOOD | ST |  |  | 38.0509 | 38.0248 | 37.9713 | 37.9022 | 37.8319 | 37.7611 | 37.691 | 37.6124 | 37.5274 | 37.2822 | 36.8841 | 36.4874 | 36.0958 | 45.3047 | 45.286 | 45.2478 | 45.1984 | 45.1482 | 45.0976 | 45.0474 | 44.9913 | 44.9306 | 44.7553 | 44.4708 | 44.1873 | 43.9074 | 41.9081 | 41.9061 | 41.9021 | 41.8969 | 41.8916 | 41.8863 | 41.881 | 41.8751 | 41.8687 | 41.8503 | 41.8203 | 41.7905 | 41.7611
|  | WHITLEY WOOD | FS |  |  | 38.0956 | 38.0929 | 38.0849 | 38.0651 | 38.0486 | 38.0251 | 38.0016 | 37.9708 | 37.9379 | 37.8432 | 37.6917 | 37.5471 | 37.4114 | 45.3366 | 45.3347 | 45.329 | 45.3148 | 45.303 | 45.2862 | 45.2695 | 45.2474 | 45.2239 | 45.1562 | 45.048 | 44.9446 | 44.8477 | 41.9114 | 41.9112 | 41.9106 | 41.9091 | 41.9079 | 41.9061 | 41.9044 | 41.902 | 41.8996 | 41.8924 | 41.8811 | 41.8702 | 41.86
MINETY GSP | CIRENCESTER BSP | WHITEWAY | MINIMUM HEADROOM | SP 02076 03059 | YES | 41.0523 | 40.8846 | 40.5417 | 40.1214 | 39.6696 | 39.3567 | 39.0502 | 38.684 | 38.4755 | 37.8154 | 36.4369 | 34.6944 | 33.2333 | 39.5162 | 39.4907 | 39.4385 | 39.2828 | 39.1185 | 38.9702 | 38.8183 | 38.5076 | 38.2729 | 37.5314 | 35.9757 | 34.0251 | 32.3425 | 41.5866 | 41.5752 | 41.5517 | 41.4221 | 41.2863 | 41.1193 | 40.7957 | 40.4132 | 40.1876 | 39.4745 | 37.8988 | 35.9194 | 34.2219
|  | WHITEWAY | CT |  |  | 41.0523 | 40.8846 | 40.5417 | 40.1997 | 39.8513 | 39.503 | 39.3196 | 39.1416 | 38.9592 | 38.391 | 37.1394 | 35.6713 | 34.2224 | 39.5162 | 39.4907 | 39.4385 | 39.3862 | 39.3327 | 39.2789 | 39.1408 | 38.9376 | 38.7291 | 38.0794 | 36.6506 | 34.9745 | 33.2999 | 41.5866 | 41.5752 | 41.5517 | 41.528 | 41.5036 | 41.2477 | 41.0472 | 40.8528 | 40.6534 | 40.0233 | 38.5699 | 36.865 | 35.1798
|  | WHITEWAY | LW |  |  | 41.0599 | 40.8965 | 40.5626 | 40.1214 | 39.6696 | 39.3567 | 39.0502 | 38.684 | 38.4755 | 37.8154 | 36.4369 | 34.6944 | 33.2333 | 39.5174 | 39.4925 | 39.4417 | 39.2828 | 39.1185 | 38.9702 | 38.8183 | 38.5076 | 38.2729 | 37.5314 | 35.9757 | 34.0251 | 32.3425 | 41.5872 | 41.576 | 41.5531 | 41.4221 | 41.2863 | 41.1193 | 40.7957 | 40.4132 | 40.1876 | 39.4745 | 37.8988 | 35.9194 | 34.2219
|  | WHITEWAY | ST |  |  | 41.147 | 41.0438 | 40.8713 | 40.6572 | 40.3975 | 40.2621 | 40.1349 | 40.0134 | 39.8881 | 39.4961 | 38.6433 | 37.6704 | 36.74 | 39.5306 | 39.5149 | 39.4887 | 39.4559 | 39.416 | 39.3949 | 39.3747 | 39.3545 | 39.3345 | 39.2703 | 38.3693 | 37.2598 | 36.1968 | 41.5931 | 41.5861 | 41.5742 | 41.5594 | 41.5412 | 41.5314 | 41.5218 | 41.5115 | 41.502 | 41.241 | 40.3089 | 39.19 | 38.1085
|  | WHITEWAY | FS |  |  | 41.3088 | 41.2903 | 41.2705 | 41.2107 | 41.14 | 41.0906 | 41.045 | 40.9913 | 40.9424 | 40.79 | 40.4473 | 40.0247 | 39.5888 | 39.5553 | 39.5525 | 39.5494 | 39.5403 | 39.5296 | 39.522 | 39.515 | 39.5068 | 39.4991 | 39.4742 | 39.4208 | 39.3502 | 39.2778 | 41.6042 | 41.6029 | 41.6016 | 41.5975 | 41.5926 | 41.5892 | 41.5861 | 41.5823 | 41.5786 | 41.5664 | 41.5415 | 41.5057 | 41.3431
BRAMLEY (FLEE) | BURGHFIELD MAIN | WILSON ROAD | MINIMUM HEADROOM | SU 69235 73304 | YES | 33.8119 | 33.8119 | 33.8119 | 33.7795 | 33.7461 | 33.7111 | 33.6749 | 33.6199 | 33.6123 | 33.5861 | 33.5471 | 33.4776 | 32.6984 | 31.8032 | 31.7994 | 31.7925 | 31.7564 | 31.7175 | 31.6726 | 31.6264 | 31.5614 | 31.5432 | 31.4838 | 31.2272 | 29.8645 | 28.3475 | 32.2007 | 32.2007 | 32.2007 | 32.1683 | 32.1348 | 32.0999 | 32.0637 | 32.0086 | 32.001 | 31.9749 | 31.9358 | 30.9648 | 29.4423
|  | WILSON ROAD | CT |  |  | 33.8119 | 33.8119 | 33.8119 | 33.8119 | 33.8119 | 33.8119 | 33.8119 | 33.8119 | 33.8119 | 33.8119 | 33.8119 | 33.8119 | 33.0484 | 31.8032 | 31.7994 | 31.7925 | 31.7864 | 31.7803 | 31.7741 | 31.7641 | 31.7541 | 31.7435 | 31.7103 | 31.4956 | 30.2099 | 28.6989 | 32.2007 | 32.2007 | 32.2007 | 32.2007 | 32.2007 | 32.2007 | 32.2007 | 32.2007 | 32.2007 | 32.2007 | 32.2007 | 31.3102 | 29.7938
|  | WILSON ROAD | LW |  |  | 33.8119 | 33.8119 | 33.8119 | 33.7795 | 33.7461 | 33.7111 | 33.6749 | 33.6199 | 33.6123 | 33.5861 | 33.5471 | 33.4776 | 32.6984 | 31.8038 | 31.8004 | 31.7943 | 31.7564 | 31.7175 | 31.6726 | 31.6264 | 31.5614 | 31.5432 | 31.4838 | 31.2272 | 29.8645 | 28.3475 | 32.2007 | 32.2007 | 32.2007 | 32.1683 | 32.1348 | 32.0999 | 32.0637 | 32.0086 | 32.001 | 31.9749 | 31.9358 | 30.9648 | 29.4423
|  | WILSON ROAD | ST |  |  | 33.8119 | 33.8119 | 33.8119 | 33.8119 | 33.8119 | 33.8119 | 33.8119 | 33.8119 | 33.8119 | 33.8119 | 33.8119 | 33.8119 | 33.8119 | 31.805 | 31.8026 | 31.799 | 31.7951 | 31.7905 | 31.7835 | 31.7764 | 31.7696 | 31.7624 | 31.7397 | 31.6895 | 31.4713 | 30.6787 | 32.2007 | 32.2007 | 32.2007 | 32.2007 | 32.2007 | 32.2007 | 32.2007 | 32.2007 | 32.2007 | 32.2007 | 32.2007 | 32.2007 | 31.7808
|  | WILSON ROAD | FS |  |  | 33.8119 | 33.8119 | 33.8119 | 33.8119 | 33.8119 | 33.8119 | 33.8119 | 33.8119 | 33.8119 | 33.8119 | 33.8119 | 33.8119 | 33.8119 | 31.8079 | 31.8072 | 31.8065 | 31.8054 | 31.8042 | 31.8017 | 31.7992 | 31.7959 | 31.7931 | 31.7843 | 31.764 | 31.7392 | 31.7134 | 32.2007 | 32.2007 | 32.2007 | 32.2007 | 32.2007 | 32.2007 | 32.2007 | 32.2007 | 32.2007 | 32.2007 | 32.2007 | 32.2007 | 32.2007
MANNINGTON GSP | MANNINGTON BSP | WIMBORNE | MINIMUM HEADROOM | SZ 02014 99989 | YES | 31.1226 | 31.1226 | 31.1226 | 31.1106 | 31.0989 | 31.0871 | 31.0751 | 31.0563 | 31.0039 | 30.8356 | 30.7541 | 30.4923 | 30.2711 | 28.0421 | 27.8743 | 27.6501 | 27.4647 | 27.2782 | 27.0758 | 26.7607 | 26.4198 | 26.122 | 25.2237 | 23.8357 | 22.5858 | 21.4541 | 29.4775 | 29.4775 | 29.4775 | 29.4655 | 29.4538 | 29.442 | 29.43 | 29.4112 | 29.3588 | 29.1905 | 28.7414 | 27.5098 | 26.3956
|  | WIMBORNE | CT |  |  | 31.1226 | 31.1226 | 31.1226 | 31.122 | 31.1208 | 31.119 | 31.1164 | 31.1107 | 31.1096 | 31.1042 | 31.059 | 31.0085 | 30.3694 | 28.0421 | 27.8743 | 27.6501 | 27.4647 | 27.2782 | 27.0788 | 26.7706 | 26.4429 | 26.1473 | 25.2604 | 23.8676 | 22.6469 | 21.5056 | 29.4775 | 29.4775 | 29.4775 | 29.4768 | 29.4756 | 29.4739 | 29.4713 | 29.4655 | 29.4624 | 29.4073 | 28.7734 | 27.5709 | 26.4471
|  | WIMBORNE | LW |  |  | 31.1226 | 31.1226 | 31.1226 | 31.1205 | 31.1161 | 31.1093 | 31.0999 | 31.0809 | 31.0776 | 31.0609 | 31.0203 | 30.941 | 30.317 | 28.0614 | 27.9043 | 27.7024 | 27.5372 | 27.369 | 27.0758 | 26.7607 | 26.4198 | 26.122 | 25.2237 | 23.8357 | 22.5858 | 21.4541 | 29.4775 | 29.4775 | 29.4775 | 29.4754 | 29.471 | 29.4642 | 29.4548 | 29.4358 | 29.4308 | 29.3644 | 28.7414 | 27.5098 | 26.3956
|  | WIMBORNE | ST |  |  | 31.1226 | 31.1226 | 31.1226 | 31.1132 | 31.1033 | 31.0927 | 31.0811 | 31.0619 | 31.0548 | 31.0273 | 30.9995 | 30.9047 | 30.8722 | 28.1219 | 28.0199 | 27.9083 | 27.8022 | 27.6845 | 27.4592 | 27.2211 | 26.984 | 26.7755 | 26.1418 | 25.1975 | 24.3455 | 23.5822 | 29.4775 | 29.4775 | 29.4775 | 29.4681 | 29.4582 | 29.4476 | 29.436 | 29.4168 | 29.4097 | 29.3822 | 29.305 | 29.1674 | 28.4896
|  | WIMBORNE | FS |  |  | 31.1226 | 31.1226 | 31.1226 | 31.1106 | 31.0989 | 31.0871 | 31.0751 | 31.0563 | 31.0039 | 30.8356 | 30.7541 | 30.4923 | 30.2711 | 28.1832 | 28.1288 | 28.0833 | 28.0344 | 27.9852 | 27.8967 | 27.8046 | 27.6875 | 27.5562 | 27.1513 | 26.7108 | 26.1638 | 25.6781 | 29.4775 | 29.4775 | 29.4775 | 29.4655 | 29.4538 | 29.442 | 29.43 | 29.4112 | 29.3588 | 29.1905 | 29.109 | 28.8472 | 28.626
MANNINGTON GSP | MANNINGTON BSP | WIMBORNE ST GILES | MINIMUM HEADROOM | SU 03028 12678 | YES | 1.5 | 1.5 | 1.5 | 1.3466 | 1.1906 | 1.032 | 0.86636 | 0.61101 | 0.57867 | 0.47476 | -0.0050967 | -0.50844 | -0.63057 | 1.7008 | 1.6991 | 1.6955 | 1.5387 | 1.3792 | 1.2172 | 1.0436 | 0.78036 | 0.73949 | 0.61025 | 0.087065 | -0.46187 | -0.62907 | 1.498 | 1.4969 | 1.4945 | 1.3389 | 1.1805 | 1.0197 | 0.84883 | 0.58826 | 0.55028 | 0.42964 | -0.078837 | -0.6212 | -0.78723
|  | WIMBORNE ST GILES | CT |  |  | 1.5 | 1.5 | 1.5 | 1.3466 | 1.1906 | 1.032 | 0.86636 | 0.61101 | 0.57867 | 0.47476 | -0.0050967 | -0.50844 | -0.63057 | 1.7008 | 1.6991 | 1.6955 | 1.5387 | 1.3792 | 1.2172 | 1.0436 | 0.78036 | 0.73949 | 0.61025 | 0.087065 | -0.46187 | -0.62907 | 1.498 | 1.4969 | 1.4945 | 1.3389 | 1.1805 | 1.0197 | 0.84883 | 0.58826 | 0.55028 | 0.42964 | -0.078837 | -0.6212 | -0.78723
|  | WIMBORNE ST GILES | LW |  |  | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.7008 | 1.6991 | 1.6955 | 1.6921 | 1.6886 | 1.6806 | 1.6727 | 1.6648 | 1.6562 | 1.6309 | 1.5876 | 1.542 | 1.4969 | 1.498 | 1.4969 | 1.4945 | 1.4923 | 1.49 | 1.4847 | 1.4794 | 1.4742 | 1.4686 | 1.4518 | 1.4233 | 1.3828 | 1.3389
|  | WIMBORNE ST GILES | ST |  |  | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.7019 | 1.7009 | 1.6993 | 1.6974 | 1.695 | 1.6906 | 1.6863 | 1.6809 | 1.6751 | 1.658 | 1.6291 | 1.5996 | 1.5703 | 1.4987 | 1.4981 | 1.497 | 1.4957 | 1.4942 | 1.4913 | 1.4884 | 1.4849 | 1.481 | 1.4698 | 1.4506 | 1.4311 | 1.4104
|  | WIMBORNE ST GILES | FS |  |  | 1.5 | 1.5 | 1.5 | 1.4957 | 1.4914 | 1.4871 | 1.4828 | 1.476 | 1.4572 | 1.3974 | 1.369 | 1.2793 | 1.2044 | 1.7034 | 1.7032 | 1.7031 | 1.6982 | 1.6933 | 1.6871 | 1.6807 | 1.6713 | 1.6502 | 1.5839 | 1.5444 | 1.4439 | 1.3584 | 1.4997 | 1.4996 | 1.4995 | 1.4948 | 1.4901 | 1.4846 | 1.4789 | 1.4704 | 1.45 | 1.3859 | 1.3503 | 1.2534 | 1.1715
MANNINGTON GSP | SHAFTESBURY BSP | WINCANTON | MINIMUM HEADROOM | ST 71286 27802 | YES | 18.3855 | 18.3686 | 18.3374 | 18.3038 | 18.2673 | 18.1721 | 18.0875 | 18.0081 | 17.9255 | 17.6866 | 17.2994 | 16.9042 | 16.5205 | 15.544 | 15.5242 | 15.4877 | 15.4484 | 15.4058 | 15.2944 | 15.1955 | 15.1026 | 15.006 | 14.7267 | 14.2739 | 13.8117 | 13.363 | 16.3424 | 16.3241 | 16.2904 | 16.2541 | 16.2148 | 16.1121 | 16.0208 | 15.935 | 15.8459 | 15.5881 | 15.1703 | 14.7437 | 14.3297
|  | WINCANTON | CT |  |  | 18.3855 | 18.3686 | 18.3374 | 18.3038 | 18.2673 | 18.2291 | 18.1446 | 18.0651 | 17.9825 | 17.7437 | 17.3565 | 16.9614 | 16.5781 | 15.544 | 15.5242 | 15.4877 | 15.4484 | 15.4058 | 15.3611 | 15.2622 | 15.1693 | 15.0727 | 14.7934 | 14.3406 | 13.8786 | 13.4304 | 16.3424 | 16.3241 | 16.2904 | 16.2541 | 16.2148 | 16.1736 | 16.0824 | 15.9966 | 15.9075 | 15.6497 | 15.2319 | 14.8055 | 14.3919
|  | WINCANTON | LW |  |  | 18.3855 | 18.3686 | 18.3374 | 18.3038 | 18.2673 | 18.1721 | 18.0875 | 18.0081 | 17.9255 | 17.6866 | 17.2994 | 16.9042 | 16.5205 | 15.544 | 15.5242 | 15.4877 | 15.4484 | 15.4058 | 15.2944 | 15.1955 | 15.1026 | 15.006 | 14.7267 | 14.2739 | 13.8117 | 13.363 | 16.3424 | 16.3241 | 16.2904 | 16.2541 | 16.2148 | 16.1121 | 16.0208 | 15.935 | 15.8459 | 15.5881 | 15.1703 | 14.7437 | 14.3297
|  | WINCANTON | ST |  |  | 18.3908 | 18.3801 | 18.3629 | 18.3421 | 18.3175 | 18.2563 | 18.2022 | 18.1481 | 18.0917 | 17.9303 | 17.6721 | 17.4172 | 17.1675 | 15.5502 | 15.5377 | 15.5176 | 15.4933 | 15.4644 | 15.3929 | 15.3297 | 15.2663 | 15.2004 | 15.0116 | 14.7097 | 14.4117 | 14.1196 | 16.3481 | 16.3365 | 16.318 | 16.2956 | 16.2689 | 16.2029 | 16.1446 | 16.0861 | 16.0253 | 15.8511 | 15.5725 | 15.2974 | 15.0279
|  | WINCANTON | FS |  |  | 18.398 | 18.3932 | 18.3869 | 18.3782 | 18.3687 | 18.3486 | 18.3322 | 18.3127 | 18.2907 | 18.2283 | 18.1301 | 18.0373 | 17.9513 | 15.5586 | 15.553 | 15.5457 | 15.5355 | 15.5243 | 15.5009 | 15.4816 | 15.4588 | 15.4332 | 15.3601 | 15.2453 | 15.1368 | 15.0362 | 16.3558 | 16.3507 | 16.3439 | 16.3345 | 16.3242 | 16.3026 | 16.2848 | 16.2637 | 16.2401 | 16.1727 | 16.0667 | 15.9666 | 15.8737
COWLEY GSP | WITNEY BSP | WINDRUSH PARK | MINIMUM HEADROOM | SP 33366 09758 | NO | 43.0141 | 43.0116 | 43.0066 | 43.0008 | 42.9937 | 42.9843 | 42.9742 | 42.9611 | 42.9528 | 42.9256 | 42.874 | 42.4527 | 41.9985 | 40.92 | 40.9181 | 40.9142 | 40.9095 | 40.9037 | 40.896 | 40.8874 | 40.8758 | 40.8692 | 40.7324 | 40.1984 | 39.6343 | 39.1008 | 42.6477 | 42.6477 | 42.6477 | 42.6469 | 42.6455 | 42.6432 | 42.64 | 42.6337 | 42.6326 | 42.627 | 42.4573 | 41.9474 | 41.4126
|  | WINDRUSH PARK | CT |  |  | 43.0147 | 43.0127 | 43.0084 | 43.0038 | 42.9985 | 42.9932 | 42.9854 | 42.9767 | 42.9692 | 42.9458 | 42.8926 | 42.5408 | 42.0834 | 40.9205 | 40.9189 | 40.9156 | 40.912 | 40.9078 | 40.9036 | 40.8973 | 40.8902 | 40.8843 | 40.8239 | 40.2883 | 39.7338 | 39.1973 | 42.6477 | 42.6477 | 42.6477 | 42.6474 | 42.647 | 42.6464 | 42.6456 | 42.6436 | 42.6433 | 42.6415 | 42.5359 | 42.0411 | 41.5093
|  | WINDRUSH PARK | LW |  |  | 43.0141 | 43.0116 | 43.0066 | 43.0008 | 42.9937 | 42.9843 | 42.9742 | 42.9611 | 42.9528 | 42.9256 | 42.874 | 42.4527 | 41.9985 | 40.92 | 40.9181 | 40.9142 | 40.9095 | 40.9037 | 40.896 | 40.8874 | 40.8758 | 40.8692 | 40.7324 | 40.1984 | 39.6343 | 39.1008 | 42.6477 | 42.6477 | 42.6477 | 42.6469 | 42.6455 | 42.6432 | 42.64 | 42.6337 | 42.6326 | 42.627 | 42.4573 | 41.9474 | 41.4126
|  | WINDRUSH PARK | ST |  |  | 43.0149 | 43.0145 | 43.0117 | 43.008 | 43.0031 | 42.998 | 42.9929 | 42.9868 | 42.9812 | 42.9628 | 42.9322 | 42.8891 | 42.7705 | 40.9216 | 40.9203 | 40.9182 | 40.9153 | 40.9114 | 40.9074 | 40.9033 | 40.8982 | 40.8937 | 40.8786 | 40.7192 | 40.3534 | 40.0034 | 42.6477 | 42.6477 | 42.6477 | 42.6475 | 42.6472 | 42.6468 | 42.6461 | 42.6446 | 42.6439 | 42.6401 | 42.6351 | 42.5901 | 42.29
|  | WINDRUSH PARK | FS |  |  | 43.0149 | 43.0149 | 43.0149 | 43.0149 | 43.0148 | 43.0148 | 43.014 | 43.0121 | 43.0099 | 43.0029 | 42.9919 | 42.9768 | 42.9621 | 40.9244 | 40.9242 | 40.924 | 40.9233 | 40.9224 | 40.9211 | 40.9199 | 40.9184 | 40.9167 | 40.9109 | 40.9022 | 40.8893 | 40.8768 | 42.6477 | 42.6477 | 42.6477 | 42.6476 | 42.6476 | 42.6476 | 42.6476 | 42.6475 | 42.6473 | 42.6459 | 42.6448 | 42.6396 | 42.6344
COWLEY GSP | DRAYTON BSP | WINSMORE LANE | MINIMUM HEADROOM | SU 49513 96982 | NO | 32.967 | 32.967 | 32.967 | 32.8733 | 32.7778 | 32.6804 | 32.5782 | 32.4198 | 32.3996 | 32.3335 | 32.0173 | 30.8878 | 29.9666 | 29.5196 | 29.509 | 29.4868 | 29.3736 | 29.2573 | 29.1393 | 29.0289 | 28.8623 | 28.8332 | 28.3189 | 27.0524 | 25.7088 | 24.6378 | 31.3734 | 31.3734 | 31.3734 | 31.2797 | 31.1841 | 30.914 | 30.6425 | 30.3162 | 30.1149 | 29.5104 | 28.2717 | 26.9575 | 25.9155
|  | WINSMORE LANE | CT |  |  | 32.967 | 32.967 | 32.967 | 32.8733 | 32.7778 | 32.6804 | 32.5782 | 32.4198 | 32.3996 | 32.3335 | 32.0173 | 30.8878 | 29.9666 | 29.5201 | 29.5098 | 29.4882 | 29.3736 | 29.2573 | 29.1393 | 29.0289 | 28.8623 | 28.8332 | 28.3189 | 27.0524 | 25.7088 | 24.6378 | 31.3734 | 31.3734 | 31.3734 | 31.2797 | 31.1841 | 30.914 | 30.6425 | 30.3162 | 30.1149 | 29.5104 | 28.2717 | 26.9575 | 25.9155
|  | WINSMORE LANE | LW |  |  | 32.967 | 32.967 | 32.967 | 32.9659 | 32.9635 | 32.9599 | 32.9548 | 32.9446 | 32.9428 | 32.9339 | 32.912 | 32.2501 | 31.4057 | 29.5196 | 29.509 | 29.4868 | 29.4641 | 29.4404 | 29.4284 | 29.415 | 29.3966 | 29.386 | 29.1209 | 28.1488 | 27.1016 | 26.1074 | 31.3734 | 31.3734 | 31.3734 | 31.3722 | 31.3699 | 31.3662 | 31.215 | 31.0367 | 30.854 | 30.3066 | 29.3623 | 28.3444 | 27.3791
|  | WINSMORE LANE | ST |  |  | 32.967 | 32.967 | 32.967 | 32.9288 | 32.8898 | 32.8497 | 32.808 | 32.7428 | 32.7203 | 32.6461 | 32.5833 | 32.3749 | 32.3079 | 29.5357 | 29.5156 | 29.5027 | 29.4487 | 29.3906 | 29.3429 | 29.2937 | 29.2229 | 29.1943 | 29.1023 | 28.9658 | 28.1085 | 27.399 | 31.3734 | 31.3734 | 31.3734 | 31.3352 | 31.2962 | 31.2561 | 31.2144 | 31.1491 | 31.1267 | 30.8253 | 30.1458 | 29.3075 | 28.6168
|  | WINSMORE LANE | FS |  |  | 32.967 | 32.967 | 32.967 | 32.9667 | 32.9665 | 32.9662 | 32.9659 | 32.9655 | 32.9641 | 32.9586 | 32.9552 | 32.9419 | 32.9296 | 29.5486 | 29.5352 | 29.5345 | 29.5307 | 29.5262 | 29.5233 | 29.5204 | 29.5165 | 29.5128 | 29.5004 | 29.4855 | 29.4606 | 29.4371 | 31.3734 | 31.3734 | 31.3734 | 31.3731 | 31.3729 | 31.3726 | 31.3723 | 31.3718 | 31.3704 | 31.3649 | 31.3616 | 31.3483 | 31.336
MANNINGTON GSP | LYTCHETT | WINTERBORNE KINGSTON | MINIMUM HEADROOM | SY 84631 98138 | YES | 12.6529 | 12.6513 | 12.6478 | 31.9931 | 31.9386 | 31.8499 | 31.712 | 31.4735 | 31.4242 | 31.2191 | 30.7913 | 30.0306 | 29.9212 | 13.5371 | 13.5362 | 13.5342 | 31.364 | 31.3106 | 31.2298 | 31.0972 | 30.864 | 30.8204 | 30.5813 | 29.8508 | 28.7773 | 28.3601 | 14.5366 | 14.5359 | 14.5344 | 33.079 | 33.0259 | 32.9475 | 32.8166 | 32.5419 | 32.415 | 31.9806 | 31.1751 | 30.024 | 29.5305
|  | WINTERBORNE KINGSTON | CT |  |  | 12.653 | 12.6514 | 12.6481 | 32.0008 | 31.9563 | 31.9041 | 31.8265 | 31.697 | 31.6668 | 31.5555 | 30.9942 | 30.3684 | 30.1496 | 13.5372 | 13.5363 | 13.5344 | 31.3736 | 31.3305 | 31.2798 | 31.2075 | 31.0833 | 31.0588 | 30.9632 | 30.0991 | 29.1605 | 28.6343 | 14.5367 | 14.536 | 14.5346 | 33.0892 | 33.0466 | 32.9962 | 32.9257 | 32.803 | 32.7142 | 32.3737 | 31.4346 | 30.4184 | 29.816
|  | WINTERBORNE KINGSTON | LW |  |  | 12.6529 | 12.6513 | 12.6478 | 32.0083 | 31.9508 | 31.8499 | 31.712 | 31.4735 | 31.4242 | 31.2191 | 30.7913 | 30.0306 | 29.9212 | 13.5371 | 13.5362 | 13.5342 | 31.3812 | 31.3253 | 31.2298 | 31.0972 | 30.864 | 30.8204 | 30.5813 | 29.8508 | 28.7773 | 28.3601 | 14.5366 | 14.5359 | 14.5344 | 33.0969 | 33.0414 | 32.9475 | 32.8166 | 32.5419 | 32.415 | 31.9806 | 31.1751 | 30.024 | 29.5305
|  | WINTERBORNE KINGSTON | ST |  |  | 12.6539 | 12.6529 | 12.6512 | 31.9931 | 31.9386 | 31.872 | 31.7949 | 31.6674 | 31.6139 | 31.4139 | 31.1917 | 30.5454 | 30.3096 | 13.5376 | 13.5371 | 13.5361 | 31.364 | 31.3106 | 31.247 | 31.173 | 31.0492 | 30.9995 | 30.8109 | 30.5277 | 29.6802 | 29.2443 | 14.537 | 14.5366 | 14.5359 | 33.079 | 33.0259 | 32.9633 | 32.8902 | 32.7675 | 32.7191 | 32.3936 | 31.9205 | 31.0231 | 30.5377
|  | WINTERBORNE KINGSTON | FS |  |  | 12.6555 | 12.6554 | 12.6553 | 32.0445 | 32.0434 | 32.0403 | 32.0367 | 32.0308 | 32.016 | 31.9412 | 31.8743 | 31.6192 | 31.372 | 13.5385 | 13.5385 | 13.5384 | 31.4129 | 31.4121 | 31.41 | 31.4074 | 31.4028 | 31.3895 | 31.3191 | 31.2592 | 31.0108 | 30.7699 | 14.5377 | 14.5376 | 14.5376 | 33.1271 | 33.1264 | 33.1246 | 33.1224 | 33.1182 | 33.1053 | 33.0363 | 32.9785 | 32.6722 | 32.3387
MANNINGTON GSP | REDHILL BSP | WINTON | MINIMUM HEADROOM | SZ 09349 93822 | YES | 42.6241 | 42.6241 | 42.6241 | 42.552 | 42.4787 | 42.4043 | 42.3265 | 42.2065 | 42.1913 | 42.1425 | 41.9171 | 41.6601 | 41.1715 | 39.3166 | 39.3144 | 39.3103 | 39.2341 | 39.1565 | 39.0777 | 38.9902 | 38.8605 | 38.8349 | 38.7532 | 38.3817 | 36.203 | 34.1937 | 41.0197 | 41.0197 | 41.0197 | 40.9477 | 40.8744 | 40.7999 | 40.7221 | 40.6021 | 40.587 | 40.5382 | 40.3128 | 39.1939 | 37.1917
|  | WINTON | CT |  |  | 42.6241 | 42.6241 | 42.6241 | 42.552 | 42.4787 | 42.4043 | 42.3265 | 42.2065 | 42.1913 | 42.1425 | 41.9171 | 41.6601 | 41.1715 | 39.3166 | 39.3144 | 39.3103 | 39.2341 | 39.1565 | 39.0777 | 38.9902 | 38.8605 | 38.8349 | 38.7532 | 38.3817 | 36.203 | 34.1937 | 41.0197 | 41.0197 | 41.0197 | 40.9477 | 40.8744 | 40.7999 | 40.7221 | 40.6021 | 40.587 | 40.5382 | 40.3128 | 39.1939 | 37.1917
|  | WINTON | LW |  |  | 42.6241 | 42.6241 | 42.6241 | 42.6241 | 42.6241 | 42.6241 | 42.6241 | 42.6241 | 42.6241 | 42.6241 | 42.6241 | 42.6241 | 42.1561 | 39.3172 | 39.3154 | 39.3119 | 39.3085 | 39.3048 | 39.2951 | 39.2854 | 39.2756 | 39.2653 | 39.2324 | 39.0366 | 37.115 | 35.1701 | 41.0197 | 41.0197 | 41.0197 | 41.0197 | 41.0197 | 41.0197 | 41.0197 | 41.0197 | 41.0197 | 41.0197 | 41.0197 | 40.1057 | 38.1696
|  | WINTON | ST |  |  | 42.6241 | 42.6241 | 42.6241 | 42.6241 | 42.6241 | 42.6241 | 42.6241 | 42.6241 | 42.6241 | 42.6241 | 42.6241 | 42.6241 | 42.6241 | 39.3328 | 39.3176 | 39.3162 | 39.3144 | 39.3123 | 39.3046 | 39.297 | 39.2903 | 39.2832 | 39.2609 | 39.2104 | 38.9003 | 37.6697 | 41.0197 | 41.0197 | 41.0197 | 41.0197 | 41.0197 | 41.0197 | 41.0197 | 41.0197 | 41.0197 | 41.0197 | 41.0197 | 41.0197 | 40.6629
|  | WINTON | FS |  |  | 42.6241 | 42.6241 | 42.6241 | 42.6241 | 42.6241 | 42.6241 | 42.6241 | 42.6241 | 42.6241 | 42.6241 | 42.6241 | 42.6241 | 42.6241 | 39.3337 | 39.3191 | 39.3187 | 39.3178 | 39.3168 | 39.3144 | 39.312 | 39.309 | 39.3063 | 39.2976 | 39.2772 | 39.2519 | 39.2255 | 41.0197 | 41.0197 | 41.0197 | 41.0197 | 41.0197 | 41.0197 | 41.0197 | 41.0197 | 41.0197 | 41.0197 | 41.0197 | 41.0197 | 41.0197
COWLEY GSP | WITNEY BSP | WITNEY TOWN | MINIMUM HEADROOM | SP 35844 09625 | NO | 29.1198 | 29.1035 | 28.1077 | 58.7607 | 58.6732 | 58.5824 | 58.488 | 58.3807 | 58.3436 | 58.2231 | 58.0049 | 57.4544 | 56.1546 | 25.9086 | 25.8852 | 24.8768 | 53.5169 | 53.4156 | 53.3035 | 53.1863 | 53.0546 | 52.9919 | 52.3375 | 50.6728 | 49.0696 | 47.5416 | 26.2004 | 26.1841 | 25.1883 | 55.8413 | 55.7416 | 55.6295 | 55.5122 | 55.3804 | 55.3177 | 54.8648 | 53.2376 | 51.6707 | 50.1774
|  | WITNEY TOWN | CT |  |  | 29.2047 | 29.1949 | 28.5974 | 59.2851 | 59.2345 | 59.1831 | 59.1306 | 59.0739 | 59.0529 | 58.9868 | 58.2113 | 57.5349 | 56.2215 | 25.9921 | 25.9745 | 25.3628 | 54.0361 | 53.9701 | 53.9035 | 53.8282 | 53.747 | 53.7005 | 53.0884 | 50.8658 | 49.1479 | 47.6062 | 26.2853 | 26.2755 | 25.6781 | 56.3621 | 56.2962 | 56.2295 | 56.1541 | 56.0728 | 56.0262 | 55.616 | 53.4309 | 51.7493 | 50.2424
|  | WITNEY TOWN | LW |  |  | 29.1198 | 29.1035 | 28.1077 | 58.7607 | 58.6732 | 58.5824 | 58.488 | 58.3807 | 58.3436 | 58.2231 | 58.0049 | 57.4544 | 56.1546 | 25.9086 | 25.8852 | 24.8768 | 53.5169 | 53.4156 | 53.3035 | 53.1863 | 53.0546 | 52.9919 | 52.3375 | 50.6728 | 49.0696 | 47.5416 | 26.2004 | 26.1841 | 25.1883 | 55.8413 | 55.7416 | 55.6295 | 55.5122 | 55.3804 | 55.3177 | 54.8648 | 53.2376 | 51.6707 | 50.1774
|  | WITNEY TOWN | ST |  |  | 29.2471 | 29.2406 | 28.8423 | 59.4262 | 59.2701 | 59.1108 | 58.9465 | 58.7085 | 58.6249 | 58.3543 | 58.0952 | 57.4653 | 57.2129 | 26.0388 | 26.028 | 25.6231 | 54.1994 | 54.0343 | 53.861 | 53.6816 | 53.4269 | 53.3258 | 53.014 | 52.5057 | 50.9797 | 49.856 | 26.3278 | 26.3212 | 25.9229 | 56.5068 | 56.3507 | 56.187 | 56.0076 | 55.7529 | 55.6517 | 55.3398 | 55.0259 | 53.5225 | 52.4215
|  | WITNEY TOWN | FS |  |  | 29.2896 | 29.2863 | 29.0871 | 59.8083 | 59.7919 | 59.7755 | 59.7591 | 59.7425 | 59.735 | 59.7099 | 59.6728 | 59.632 | 59.5755 | 26.0843 | 26.0792 | 25.8776 | 54.5957 | 54.576 | 54.5545 | 54.5326 | 54.5093 | 54.4949 | 54.4537 | 54.3957 | 54.3363 | 54.2628 | 26.3702 | 26.367 | 26.1678 | 56.8889 | 56.8726 | 56.8562 | 56.8397 | 56.8232 | 56.8157 | 56.7798 | 56.7216 | 56.6622 | 56.5886
BRAMLEY (FLEE) | WOKINGHAM BSP | WOKINGHAM | MINIMUM HEADROOM | SU 79589 67665 | YES | 42.0323 | 42.0323 | 42.0323 | 42.0323 | 42.0323 | 42.0323 | 42.0323 | 42.0323 | 41.9426 | 41.0625 | 40.0421 | 39.2332 | 38.4483 | 39.8501 | 39.8349 | 39.8038 | 39.773 | 39.1634 | 38.5167 | 38.2638 | 37.9886 | 37.6909 | 36.6644 | 35.4743 | 34.5308 | 33.6182 | 41.4868 | 41.4868 | 41.4868 | 41.4868 | 41.3207 | 40.6664 | 40.4105 | 40.132 | 39.8307 | 38.7921 | 37.5879 | 36.6332 | 35.7098
|  | WOKINGHAM | CT |  |  | 42.0323 | 42.0323 | 42.0323 | 42.0323 | 42.0323 | 42.0323 | 42.0323 | 42.0323 | 41.9426 | 41.0625 | 40.0421 | 39.2332 | 38.4483 | 39.8501 | 39.8349 | 39.8038 | 39.773 | 39.1634 | 38.5167 | 38.2638 | 37.9886 | 37.6909 | 36.6644 | 35.4743 | 34.5308 | 33.6182 | 41.4868 | 41.4868 | 41.4868 | 41.4868 | 41.3207 | 40.6664 | 40.4105 | 40.132 | 39.8307 | 38.7921 | 37.5879 | 36.6332 | 35.7098
|  | WOKINGHAM | LW |  |  | 42.0323 | 42.0323 | 42.0323 | 42.0323 | 42.0323 | 42.0323 | 42.0323 | 42.0323 | 42.0323 | 41.4471 | 40.4268 | 39.6178 | 38.8344 | 39.8504 | 39.8354 | 39.8047 | 39.7743 | 39.1965 | 38.9654 | 38.7124 | 38.4372 | 38.1395 | 37.113 | 35.923 | 34.9794 | 34.0663 | 41.4868 | 41.4868 | 41.4868 | 41.4868 | 41.3542 | 41.1203 | 40.8643 | 40.5858 | 40.2847 | 39.2459 | 38.0419 | 37.0871 | 36.1632
|  | WOKINGHAM | ST |  |  | 42.0323 | 42.0323 | 42.0323 | 42.0323 | 42.0323 | 42.0323 | 42.0323 | 42.0323 | 42.0323 | 42.0323 | 42.0323 | 41.8285 | 41.3234 | 39.8612 | 39.8536 | 39.8409 | 39.8252 | 39.8065 | 39.7973 | 39.7874 | 39.7785 | 39.7172 | 38.9963 | 38.1712 | 37.5578 | 36.9687 | 41.4868 | 41.4868 | 41.4868 | 41.4868 | 41.4868 | 41.4868 | 41.4868 | 41.4868 | 41.4868 | 41.1516 | 40.3167 | 39.6961 | 39.1
|  | WOKINGHAM | FS |  |  | 42.0323 | 42.0323 | 42.0323 | 42.0323 | 42.0323 | 42.0323 | 42.0323 | 42.0323 | 42.0323 | 42.0323 | 42.0323 | 42.0323 | 42.0323 | 39.8712 | 39.8694 | 39.8673 | 39.8617 | 39.8552 | 39.8517 | 39.848 | 39.8434 | 39.8395 | 39.8258 | 39.81 | 39.7983 | 39.787 | 41.4868 | 41.4868 | 41.4868 | 41.4868 | 41.4868 | 41.4868 | 41.4868 | 41.4868 | 41.4868 | 41.4868 | 41.4868 | 41.4868 | 41.4868
BRAMLEY (FLEE) | BURGHFIELD RESERVE | WOODCOTE | MINIMUM HEADROOM | SU 64425 81624 | YES | 6.4342 | 6.4332 | 6.4311 | 6.4292 | 6.4272 | 6.4252 | 6.4229 | 6.4206 | 6.4181 | 6.4108 | 6.3985 | 6.3855 | 6.3291 | 5.6084 | 5.5945 | 5.5652 | 5.5368 | 5.5086 | 5.4806 | 5.4474 | 5.4145 | 5.379 | 5.2738 | 5.0967 | 4.9116 | 4.7291 | 4.9748 | 4.9609 | 4.9316 | 4.9032 | 4.8751 | 4.8471 | 4.814 | 4.7811 | 4.7457 | 4.6408 | 4.464 | 4.2792 | 4.0971
|  | WOODCOTE | CT |  |  | 6.4342 | 6.4332 | 6.4311 | 6.4292 | 6.4272 | 6.4252 | 6.4229 | 6.4206 | 6.4181 | 6.4108 | 6.3985 | 6.3855 | 6.3291 | 5.6084 | 5.5945 | 5.5652 | 5.5368 | 5.5086 | 5.4806 | 5.4474 | 5.4145 | 5.379 | 5.2738 | 5.0967 | 4.9116 | 4.7291 | 4.9748 | 4.9609 | 4.9316 | 4.9032 | 4.8751 | 4.8471 | 4.814 | 4.7811 | 4.7457 | 4.6408 | 4.464 | 4.2792 | 4.0971
|  | WOODCOTE | LW |  |  | 6.4355 | 6.4352 | 6.4347 | 6.4343 | 6.4338 | 6.4314 | 6.4291 | 6.4268 | 6.4243 | 6.417 | 6.4047 | 6.3917 | 6.379 | 5.6275 | 5.6241 | 5.6169 | 5.6099 | 5.6028 | 5.5693 | 5.5361 | 5.5032 | 5.4677 | 5.3625 | 5.1855 | 5.0003 | 4.8179 | 4.9938 | 4.9904 | 4.9832 | 4.9762 | 4.9692 | 4.9357 | 4.9026 | 4.8697 | 4.8343 | 4.7293 | 4.5526 | 4.3678 | 4.1857
|  | WOODCOTE | ST |  |  | 6.4356 | 6.4355 | 6.4353 | 6.435 | 6.4347 | 6.433 | 6.4313 | 6.4297 | 6.428 | 6.4231 | 6.4148 | 6.4065 | 6.3983 | 5.6298 | 5.6279 | 5.6246 | 5.6206 | 5.6157 | 5.5914 | 5.5674 | 5.5449 | 5.5207 | 5.4497 | 5.3317 | 5.2122 | 5.0939 | 4.9961 | 4.9941 | 4.9909 | 4.9869 | 4.982 | 4.9578 | 4.9338 | 4.9113 | 4.8872 | 4.8163 | 4.6985 | 4.5793 | 4.4612
|  | WOODCOTE | FS |  |  | 6.4359 | 6.4358 | 6.4358 | 6.4357 | 6.4356 | 6.4351 | 6.4345 | 6.4338 | 6.4331 | 6.4312 | 6.428 | 6.425 | 6.422 | 5.6328 | 5.6325 | 5.6322 | 5.6311 | 5.6298 | 5.6215 | 5.6133 | 5.6027 | 5.5933 | 5.566 | 5.5209 | 5.4766 | 5.4345 | 4.9991 | 4.9988 | 4.9985 | 4.9974 | 4.9961 | 4.9878 | 4.9796 | 4.969 | 4.9596 | 4.9324 | 4.8874 | 4.8432 | 4.8012
NURSLING GSP | SOUTHAMPTON (2 X 90) | WOODMILL LANE | MINIMUM HEADROOM | SU 43733 15470 | YES | 26.3756 | 26.3756 | 26.3756 | 26.3744 | 26.3733 | 26.3721 | 26.3709 | 26.369 | 26.3639 | 26.3474 | 26.22 | 24.9674 | 23.7031 | 25.1343 | 25.1326 | 25.1296 | 25.1265 | 25.1232 | 25.1132 | 25.103 | 25.0927 | 25.0819 | 25.0461 | 24.2317 | 22.7539 | 21.2624 | 25.4157 | 25.4144 | 25.4123 | 25.41 | 25.4076 | 25.4002 | 25.3928 | 25.3853 | 25.3775 | 25.3513 | 24.603 | 23.2076 | 21.7155
|  | WOODMILL LANE | CT |  |  | 26.3756 | 26.3756 | 26.3756 | 26.3756 | 26.3756 | 26.3756 | 26.3756 | 26.3756 | 26.3756 | 26.3756 | 26.2905 | 25.0379 | 23.7739 | 25.1343 | 25.1326 | 25.1296 | 25.1265 | 25.1232 | 25.1198 | 25.1096 | 25.0994 | 25.0886 | 25.0527 | 24.3149 | 22.8372 | 21.346 | 25.4157 | 25.4144 | 25.4123 | 25.41 | 25.4076 | 25.4051 | 25.3977 | 25.3902 | 25.3823 | 25.3562 | 24.6795 | 23.2908 | 21.7991
|  | WOODMILL LANE | LW |  |  | 26.3756 | 26.3756 | 26.3756 | 26.3756 | 26.3756 | 26.3756 | 26.3756 | 26.3756 | 26.3756 | 26.3756 | 26.22 | 24.9674 | 23.7031 | 25.1343 | 25.1326 | 25.1296 | 25.1265 | 25.1232 | 25.1132 | 25.103 | 25.0927 | 25.0819 | 25.0461 | 24.2317 | 22.7539 | 21.2624 | 25.4157 | 25.4144 | 25.4123 | 25.41 | 25.4076 | 25.4002 | 25.3928 | 25.3853 | 25.3775 | 25.3513 | 24.603 | 23.2076 | 21.7155
|  | WOODMILL LANE | ST |  |  | 26.3756 | 26.3756 | 26.3756 | 26.3756 | 26.3756 | 26.3756 | 26.3756 | 26.3756 | 26.3756 | 26.3756 | 26.3756 | 26.0523 | 25.2501 | 25.1351 | 25.1341 | 25.1325 | 25.1307 | 25.1284 | 25.1235 | 25.1186 | 25.1116 | 25.1042 | 25.0796 | 24.9767 | 24.0339 | 23.0875 | 25.4163 | 25.4155 | 25.4144 | 25.413 | 25.4114 | 25.4078 | 25.4042 | 25.3991 | 25.3937 | 25.3758 | 25.2515 | 24.4211 | 23.5413
|  | WOODMILL LANE | FS |  |  | 26.3756 | 26.3756 | 26.3756 | 26.3744 | 26.3733 | 26.3721 | 26.3709 | 26.369 | 26.3639 | 26.3474 | 26.3396 | 26.315 | 26.2944 | 25.1362 | 25.1357 | 25.1353 | 25.1334 | 25.1314 | 25.1285 | 25.1255 | 25.1214 | 25.1134 | 25.0874 | 25.0528 | 24.9921 | 24.8931 | 25.417 | 25.4167 | 25.4164 | 25.4147 | 25.4129 | 25.4105 | 25.408 | 25.4045 | 25.3972 | 25.3738 | 25.3465 | 25.2956 | 25.1675
COWLEY GSP | YARNTON BSP | WOODSTOCK | MINIMUM HEADROOM | SP 44795 17462 | NO | 22.5391 | 22.5391 | 22.5391 | 22.4386 | 22.3348 | 22.2265 | 22.1142 | 21.9437 | 21.92 | 21.8391 | 21.716 | 21.4488 | 21.4311 | 20.7858 | 20.7858 | 20.7858 | 20.6853 | 20.5816 | 20.4733 | 20.361 | 20.1904 | 20.1668 | 20.0858 | 19.9242 | 19.2006 | 18.7421 | 21.429 | 21.4252 | 21.4189 | 21.3157 | 21.2071 | 21.0926 | 20.9745 | 20.7982 | 20.7685 | 20.6547 | 20.0857 | 19.3754 | 18.9298
|  | WOODSTOCK | CT |  |  | 22.5391 | 22.5391 | 22.5391 | 22.5391 | 22.5391 | 22.5391 | 22.5391 | 22.5391 | 22.5391 | 22.5391 | 22.5391 | 22.5391 | 22.5391 | 20.7858 | 20.7858 | 20.7858 | 20.7858 | 20.7858 | 20.7858 | 20.7858 | 20.7858 | 20.7858 | 20.7858 | 20.7182 | 20.262 | 19.8215 | 21.429 | 21.4252 | 21.4189 | 21.4137 | 21.408 | 21.4034 | 21.3976 | 21.3917 | 21.3857 | 21.3267 | 20.8805 | 20.4377 | 20.01
|  | WOODSTOCK | LW |  |  | 22.5391 | 22.5391 | 22.5391 | 22.4386 | 22.3348 | 22.2265 | 22.1142 | 21.9437 | 21.92 | 21.8391 | 21.716 | 21.4488 | 21.4311 | 20.7858 | 20.7858 | 20.7858 | 20.6853 | 20.5816 | 20.4733 | 20.361 | 20.1904 | 20.1668 | 20.0858 | 19.9242 | 19.2006 | 18.7421 | 21.4297 | 21.4262 | 21.4207 | 21.3157 | 21.2071 | 21.0926 | 20.9745 | 20.7982 | 20.7685 | 20.6547 | 20.0857 | 19.3754 | 18.9298
|  | WOODSTOCK | ST |  |  | 22.5391 | 22.5391 | 22.5391 | 22.5391 | 22.5391 | 22.5391 | 22.5391 | 22.5391 | 22.5391 | 22.5391 | 22.5391 | 22.5391 | 22.5391 | 20.7858 | 20.7858 | 20.7858 | 20.7858 | 20.7858 | 20.7858 | 20.7858 | 20.7858 | 20.7858 | 20.7858 | 20.7858 | 20.7858 | 20.639 | 21.4313 | 21.429 | 21.4259 | 21.4231 | 21.4196 | 21.4149 | 21.4105 | 21.4065 | 21.4024 | 21.3905 | 21.3675 | 21.0812 | 20.8036
|  | WOODSTOCK | FS |  |  | 22.5391 | 22.5391 | 22.5391 | 22.5391 | 22.5391 | 22.5391 | 22.5391 | 22.5391 | 22.5391 | 22.5391 | 22.5391 | 22.5391 | 22.5391 | 20.7858 | 20.7858 | 20.7858 | 20.7858 | 20.7858 | 20.7858 | 20.7858 | 20.7858 | 20.7858 | 20.7858 | 20.7858 | 20.7858 | 20.7858 | 21.4332 | 21.4322 | 21.4311 | 21.4301 | 21.4288 | 21.4271 | 21.4255 | 21.4235 | 21.4219 | 21.4173 | 21.4097 | 21.4026 | 21.3961
BOTLEY WOOD GSP | NETLEY COMMON BSP | WOOLSTON | MINIMUM HEADROOM | SU 44145 11242 | YES | 19.7592 | 19.7235 | 19.7013 | 19.6773 | 19.6484 | 19.5337 | 19.4189 | 19.3061 | 19.1874 | 18.8123 | 17.9678 | 16.972 | 15.6342 | 21.1333 | 21.1152 | 21.1039 | 21.0917 | 21.0769 | 21.0186 | 20.9602 | 20.9027 | 20.8423 | 20.6515 | 19.318 | 17.6952 | 16.0684 | 21.5169 | 21.5038 | 21.4957 | 21.4869 | 21.4763 | 21.4342 | 21.3921 | 21.3507 | 21.3071 | 21.0587 | 19.6867 | 18.0688 | 16.447
|  | WOOLSTON | CT |  |  | 19.7592 | 19.7235 | 19.7013 | 19.6773 | 19.6484 | 19.6163 | 19.5016 | 19.3888 | 19.2701 | 18.8951 | 18.0504 | 17.0546 | 15.7484 | 21.1333 | 21.1152 | 21.1039 | 21.0917 | 21.0769 | 21.0606 | 21.0022 | 20.9448 | 20.8844 | 20.6936 | 19.4525 | 17.8299 | 16.203 | 21.5169 | 21.5038 | 21.4957 | 21.4869 | 21.4763 | 21.4645 | 21.4224 | 21.381 | 21.3375 | 21.1933 | 19.8208 | 18.2031 | 16.5811
|  | WOOLSTON | LW |  |  | 19.7592 | 19.7235 | 19.7013 | 19.6773 | 19.6484 | 19.5337 | 19.4189 | 19.3061 | 19.1874 | 18.8123 | 17.9678 | 16.972 | 15.6342 | 21.1333 | 21.1152 | 21.1039 | 21.0917 | 21.0769 | 21.0186 | 20.9602 | 20.9027 | 20.8423 | 20.6515 | 19.318 | 17.6952 | 16.0684 | 21.5169 | 21.5038 | 21.4957 | 21.4869 | 21.4763 | 21.4342 | 21.3921 | 21.3507 | 21.3071 | 21.0587 | 19.6867 | 18.0688 | 16.447
|  | WOOLSTON | ST |  |  | 19.7759 | 19.752 | 19.7407 | 19.7262 | 19.7066 | 19.642 | 19.5774 | 19.5006 | 19.4194 | 19.163 | 18.5816 | 17.9274 | 17.2907 | 21.1419 | 21.1297 | 21.1239 | 21.1166 | 21.1066 | 21.0737 | 21.0408 | 21.0017 | 20.9604 | 20.8299 | 20.3182 | 19.2521 | 18.2145 | 21.5231 | 21.5143 | 21.5101 | 21.5048 | 21.4976 | 21.4739 | 21.4502 | 21.422 | 21.3922 | 21.2982 | 20.6838 | 19.621 | 18.5866
|  | WOOLSTON | FS |  |  | 19.7921 | 19.7786 | 19.7755 | 19.7701 | 19.7628 | 19.7436 | 19.7246 | 19.7019 | 19.6703 | 19.5705 | 19.3349 | 19.0455 | 18.7444 | 21.1501 | 21.1432 | 21.1417 | 21.1389 | 21.1352 | 21.1254 | 21.1158 | 21.1042 | 21.0881 | 21.0373 | 20.9174 | 20.7701 | 20.5835 | 21.529 | 21.524 | 21.5229 | 21.5209 | 21.5183 | 21.5112 | 21.5042 | 21.4959 | 21.4843 | 21.4477 | 21.3612 | 21.2551 | 20.9484
MINETY GSP | SWINDON BSP | WOOTTON BASSETT | MINIMUM HEADROOM | SU 07587 81123 | YES | 34.2938 | 34.2371 | 34.1174 | 33.9186 | 33.6836 | 33.4046 | 33.1188 | 32.7513 | 32.5722 | 32.0212 | 31.1139 | 30.0318 | 29.2889 | 31.1673 | 31.0955 | 30.9436 | 30.7252 | 30.4627 | 30.1466 | 29.824 | 29.4202 | 29.2019 | 28.5351 | 27.4374 | 26.1589 | 25.2229 | 32.7518 | 32.6875 | 32.5451 | 32.3324 | 32.078 | 31.7729 | 31.4611 | 31.068 | 30.8612 | 30.2284 | 29.1868 | 27.9661 | 27.0869
|  | WOOTTON BASSETT | CT |  |  | 34.2938 | 34.2371 | 34.1174 | 34.0004 | 33.8838 | 33.7674 | 33.6275 | 33.4849 | 33.3374 | 32.8994 | 32.1345 | 31.3408 | 30.602 | 31.1673 | 31.0955 | 30.9436 | 30.7955 | 30.648 | 30.501 | 30.3243 | 30.1454 | 29.9587 | 29.4049 | 28.4496 | 27.4596 | 26.5277 | 32.7518 | 32.6875 | 32.5451 | 32.4062 | 32.2677 | 32.1297 | 31.9639 | 31.7957 | 31.6204 | 31.1008 | 30.2015 | 29.2692 | 28.3941
|  | WOOTTON BASSETT | LW |  |  | 34.3049 | 34.2545 | 34.1477 | 33.9186 | 33.6836 | 33.4046 | 33.1188 | 32.7513 | 32.5722 | 32.0212 | 31.1139 | 30.0318 | 29.2889 | 31.1815 | 31.1175 | 30.9821 | 30.7252 | 30.4627 | 30.1466 | 29.824 | 29.4202 | 29.2019 | 28.5351 | 27.4374 | 26.1589 | 25.2229 | 32.7627 | 32.7082 | 32.5812 | 32.3324 | 32.078 | 31.7729 | 31.4611 | 31.068 | 30.8612 | 30.2284 | 29.1868 | 27.9661 | 27.0869
|  | WOOTTON BASSETT | ST |  |  | 34.3187 | 34.281 | 34.2165 | 34.1367 | 34.0402 | 33.9448 | 33.8498 | 33.7517 | 33.6493 | 33.3447 | 32.8542 | 32.3186 | 31.8269 | 31.199 | 31.1512 | 31.0693 | 30.9683 | 30.8461 | 30.7256 | 30.6058 | 30.4828 | 30.3537 | 29.971 | 29.3539 | 28.6918 | 28.0744 | 32.7744 | 32.7394 | 32.663 | 32.5682 | 32.4536 | 32.3405 | 32.2279 | 32.1122 | 31.991 | 31.6313 | 31.0515 | 30.4265 | 29.8462
|  | WOOTTON BASSETT | FS |  |  | 34.3839 | 34.38 | 34.3764 | 34.3589 | 34.3381 | 34.3086 | 34.2793 | 34.2414 | 34.2004 | 34.0788 | 33.8942 | 33.6977 | 33.5123 | 31.2816 | 31.2767 | 31.2721 | 31.25 | 31.2238 | 31.1865 | 31.1493 | 31.1015 | 31.0502 | 30.8984 | 30.666 | 30.4237 | 30.1951 | 32.8296 | 32.8263 | 32.8233 | 32.8084 | 32.7908 | 32.7657 | 32.7376 | 32.693 | 32.6447 | 32.5018 | 32.2835 | 32.0546 | 31.8388
COWLEY GSP | OXFORD BSP | WOOTTON ROAD | MINIMUM HEADROOM | SU 49244 98269 | YES | 22.4195 | 22.4195 | 22.4195 | 22.3568 | 22.2929 | 22.2275 | 22.1596 | 22.054 | 22.0179 | 21.9004 | 21.8033 | 21.2496 | 20.2632 | 20.484 | 20.4758 | 20.4612 | 20.4153 | 20.3436 | 20.2654 | 19.8675 | 19.4542 | 19.1625 | 18.3847 | 17.1682 | 15.8988 | 14.7496 | 21.5692 | 21.5692 | 21.5692 | 21.5065 | 21.4426 | 21.3772 | 21.1949 | 20.8071 | 20.5335 | 19.804 | 18.6619 | 17.4505 | 16.3723
|  | WOOTTON ROAD | CT |  |  | 22.4195 | 22.4195 | 22.4195 | 22.4192 | 22.4187 | 22.4178 | 22.4166 | 22.414 | 22.4135 | 22.4109 | 22.3862 | 21.3393 | 20.353 | 20.484 | 20.4758 | 20.4612 | 20.4439 | 20.4251 | 20.2833 | 19.8675 | 19.4542 | 19.1625 | 18.3847 | 17.1682 | 15.9511 | 14.802 | 21.5692 | 21.5692 | 21.5692 | 21.5689 | 21.5683 | 21.5675 | 21.1949 | 20.8071 | 20.5335 | 19.804 | 18.6619 | 17.5191 | 16.4411
|  | WOOTTON ROAD | LW |  |  | 22.4195 | 22.4195 | 22.4195 | 22.3928 | 22.3641 | 22.3332 | 22.3 | 22.2474 | 22.2399 | 22.2113 | 22.1576 | 21.2496 | 20.2632 | 20.4864 | 20.4795 | 20.4677 | 20.4267 | 20.3825 | 20.3333 | 20.0132 | 19.5499 | 19.2512 | 18.4473 | 17.1984 | 15.8988 | 14.7496 | 21.5692 | 21.5692 | 21.5692 | 21.5424 | 21.5138 | 21.4829 | 21.3242 | 20.8865 | 20.6059 | 19.8503 | 18.6758 | 17.4505 | 16.3723
|  | WOOTTON ROAD | ST |  |  | 22.4195 | 22.4195 | 22.4195 | 22.3568 | 22.2929 | 22.2275 | 22.1596 | 22.054 | 22.0179 | 21.9004 | 21.8033 | 21.5204 | 21.4367 | 20.4943 | 20.4888 | 20.4845 | 20.4153 | 20.3436 | 20.2654 | 20.1836 | 20.0646 | 20.0188 | 19.5139 | 18.6085 | 17.5514 | 16.7281 | 21.5692 | 21.5692 | 21.5692 | 21.5065 | 21.4426 | 21.3772 | 21.3093 | 21.2037 | 21.1676 | 20.8311 | 19.9761 | 18.9672 | 18.1899
|  | WOOTTON ROAD | FS |  |  | 22.4195 | 22.4195 | 22.4195 | 22.4144 | 22.4095 | 22.4044 | 22.3993 | 22.3913 | 22.369 | 22.2973 | 22.2626 | 22.1507 | 22.056 | 20.4963 | 20.4946 | 20.4928 | 20.4844 | 20.4757 | 20.4657 | 20.4553 | 20.4415 | 20.4154 | 20.3337 | 20.2837 | 20.1573 | 20.0382 | 21.5692 | 21.5692 | 21.5692 | 21.5641 | 21.5591 | 21.5541 | 21.549 | 21.541 | 21.5187 | 21.447 | 21.4123 | 21.3003 | 21.2057
BRAMLEY (FLEE) | COXMOOR WOOD BSP | WRECCLESHAM | MINIMUM HEADROOM | SU 82093 44312 | YES | 44.1725 | 44.1725 | 44.1725 | 44.1614 | 44.1497 | 44.1373 | 44.1239 | 44.102 | 44.0939 | 44.0399 | 44.0014 | 43.875 | 43.3279 | 40.3968 | 40.3805 | 40.3461 | 40.3121 | 40.2779 | 40.1061 | 39.9674 | 39.827 | 39.6805 | 39.2439 | 38.4714 | 37.6586 | 36.8903 | 43.1219 | 43.1088 | 43.0811 | 43.0536 | 43.0259 | 42.6373 | 42.4939 | 42.3488 | 42.1973 | 41.7458 | 40.948 | 40.1088 | 39.3145
|  | WRECCLESHAM | CT |  |  | 44.1725 | 44.1725 | 44.1725 | 44.1719 | 44.1708 | 44.1691 | 44.1666 | 44.1612 | 44.1602 | 44.155 | 44.0798 | 43.9745 | 43.3279 | 40.3968 | 40.3805 | 40.3461 | 40.3121 | 40.2779 | 40.1061 | 39.9674 | 39.827 | 39.6805 | 39.2439 | 38.4714 | 37.6586 | 36.8903 | 43.1219 | 43.1088 | 43.0811 | 43.0536 | 43.0259 | 42.6373 | 42.4939 | 42.3488 | 42.1973 | 41.7458 | 40.948 | 40.1088 | 39.3145
|  | WRECCLESHAM | LW |  |  | 44.1725 | 44.1725 | 44.1725 | 44.1705 | 44.1664 | 44.1599 | 44.1509 | 44.1329 | 44.1298 | 44.1139 | 44.0753 | 43.9463 | 43.7106 | 40.4008 | 40.3867 | 40.357 | 40.3261 | 40.2934 | 40.2752 | 40.2546 | 40.2251 | 40.1292 | 39.6817 | 38.9137 | 38.0732 | 37.314 | 43.1251 | 43.1138 | 43.0899 | 43.0647 | 43.0375 | 43.0216 | 42.974 | 42.8162 | 42.6626 | 42.2002 | 41.4069 | 40.5399 | 39.7547
|  | WRECCLESHAM | ST |  |  | 44.1725 | 44.1725 | 44.1725 | 44.1614 | 44.1497 | 44.1373 | 44.1239 | 44.102 | 44.0939 | 44.0639 | 44.0342 | 43.9289 | 43.8948 | 40.4071 | 40.3978 | 40.3817 | 40.351 | 40.3156 | 40.2929 | 40.2694 | 40.2395 | 40.223 | 40.1681 | 39.8336 | 39.2342 | 38.7102 | 43.1302 | 43.1227 | 43.1098 | 43.0828 | 43.0521 | 43.0314 | 43.0099 | 42.9816 | 42.9667 | 42.8933 | 42.36 | 41.7436 | 41.2027
|  | WRECCLESHAM | FS |  |  | 44.1725 | 44.1725 | 44.1725 | 44.1671 | 44.1618 | 44.1564 | 44.1509 | 44.1423 | 44.1182 | 44.0399 | 44.0014 | 43.875 | 43.7672 | 40.4229 | 40.4219 | 40.4209 | 40.4108 | 40.3999 | 40.3909 | 40.3819 | 40.3686 | 40.3412 | 40.2533 | 40.1989 | 40.0568 | 39.9341 | 43.1429 | 43.1421 | 43.1413 | 43.1321 | 43.1223 | 43.114 | 43.1057 | 43.0933 | 43.0666 | 42.9805 | 42.9292 | 42.7902 | 42.6704
MINETY GSP | TOOTHILL BSP | WROUGHTON | MINIMUM HEADROOM | SU 14446 81504 | YES | 25.2096 | 25.2021 | 25.1886 | 25.0491 | 24.9028 | 24.7514 | 24.5925 | 24.3545 | 24.313 | 24.1733 | 23.72 | 22.9528 | 22.5092 | 24.3946 | 24.3886 | 24.3782 | 24.2419 | 23.9623 | 23.6586 | 23.344 | 22.9629 | 22.8043 | 22.3537 | 21.6524 | 20.8235 | 20.3211 | 24.9159 | 24.9099 | 24.8994 | 24.7631 | 24.4709 | 24.1682 | 23.8546 | 23.4745 | 23.3167 | 22.8681 | 22.1699 | 21.3441 | 20.8447
|  | WROUGHTON | CT |  |  | 25.2111 | 25.2045 | 25.1928 | 25.1795 | 25.1649 | 25.1493 | 25.1344 | 25.1175 | 25.1071 | 25.0769 | 24.8316 | 24.3404 | 23.9019 | 24.3957 | 24.3905 | 24.3814 | 24.371 | 24.3178 | 24.1304 | 23.9598 | 23.7998 | 23.6721 | 23.3312 | 22.7737 | 22.2208 | 21.7236 | 24.9171 | 24.9118 | 24.9026 | 24.8922 | 24.8258 | 24.6395 | 24.4699 | 24.3109 | 24.184 | 23.8451 | 23.2908 | 22.741 | 22.2467
|  | WROUGHTON | LW |  |  | 25.2096 | 25.2021 | 25.1886 | 25.0491 | 24.9028 | 24.7514 | 24.5925 | 24.3545 | 24.313 | 24.1733 | 23.72 | 22.9528 | 22.5092 | 24.3946 | 24.3886 | 24.3782 | 24.2419 | 23.9623 | 23.6586 | 23.344 | 22.9629 | 22.8043 | 22.3537 | 21.6524 | 20.8235 | 20.3211 | 24.9159 | 24.9099 | 24.8994 | 24.7631 | 24.4709 | 24.1682 | 23.8546 | 23.4745 | 23.3167 | 22.8681 | 22.1699 | 21.3441 | 20.8447
|  | WROUGHTON | ST |  |  | 25.2141 | 25.2101 | 25.2043 | 25.1758 | 25.1451 | 25.1147 | 25.083 | 25.0374 | 25.0175 | 24.9533 | 24.8843 | 24.7275 | 24.6071 | 24.3982 | 24.3949 | 24.3903 | 24.3636 | 24.3349 | 24.3064 | 24.2765 | 24.15 | 24.0501 | 23.7738 | 23.3837 | 22.9239 | 22.5688 | 24.9195 | 24.9162 | 24.9116 | 24.8849 | 24.8562 | 24.8276 | 24.7977 | 24.6583 | 24.5589 | 24.284 | 23.896 | 23.4382 | 23.0851
|  | WROUGHTON | FS |  |  | 25.2178 | 25.2162 | 25.2147 | 25.2116 | 25.208 | 25.2049 | 25.2018 | 25.1985 | 25.1953 | 25.1849 | 25.1718 | 25.1482 | 25.1259 | 24.4012 | 24.3999 | 24.3986 | 24.3961 | 24.3932 | 24.3908 | 24.3883 | 24.3857 | 24.3831 | 24.3742 | 24.3634 | 24.3419 | 24.2208 | 24.9225 | 24.9212 | 24.92 | 24.9174 | 24.9146 | 24.9121 | 24.9096 | 24.907 | 24.9044 | 24.8955 | 24.8847 | 24.8545 | 24.7292
AMERSHAM | LOUDWATER BSP | WYCOMBE MARSH | MINIMUM HEADROOM | SU 88582 91845 | YES | 20.9223 | 20.9223 | 20.9223 | 20.8836 | 20.8443 | 20.8042 | 20.7628 | 20.6987 | 20.677 | 20.6075 | 20.5518 | 20.3609 | 20.303 | 19.5959 | 19.5913 | 19.5829 | 19.5437 | 19.4976 | 19.4526 | 19.4064 | 19.3383 | 19.3124 | 19.2308 | 19.1539 | 18.8397 | 18.1793 | 19.9007 | 19.9007 | 19.9007 | 19.862 | 19.8227 | 19.7826 | 19.7412 | 19.6771 | 19.6554 | 19.5859 | 19.348 | 18.6796 | 18.0187
|  | WYCOMBE MARSH | CT |  |  | 20.9223 | 20.9223 | 20.9223 | 20.9223 | 20.9223 | 20.9223 | 20.9223 | 20.9223 | 20.9223 | 20.9223 | 20.9223 | 20.9223 | 20.5613 | 19.5977 | 19.594 | 19.5876 | 19.5818 | 19.5766 | 19.5714 | 19.5656 | 19.5598 | 19.5537 | 19.5358 | 19.5044 | 19.0297 | 18.3715 | 19.9007 | 19.9007 | 19.9007 | 19.9007 | 19.9007 | 19.9007 | 19.9007 | 19.9007 | 19.9007 | 19.9007 | 19.527 | 18.8702 | 18.2096
|  | WYCOMBE MARSH | LW |  |  | 20.9223 | 20.9223 | 20.9223 | 20.9223 | 20.9223 | 20.9223 | 20.9223 | 20.9223 | 20.9223 | 20.9223 | 20.9223 | 20.9223 | 20.3972 | 19.5959 | 19.5913 | 19.5829 | 19.5752 | 19.5679 | 19.5622 | 19.5564 | 19.5506 | 19.5445 | 19.5266 | 19.4499 | 18.8397 | 18.1793 | 19.9007 | 19.9007 | 19.9007 | 19.9007 | 19.9007 | 19.9007 | 19.9007 | 19.9007 | 19.9007 | 19.9007 | 19.348 | 18.6796 | 18.0187
|  | WYCOMBE MARSH | ST |  |  | 20.9223 | 20.9223 | 20.9223 | 20.8836 | 20.8443 | 20.8042 | 20.7628 | 20.6987 | 20.677 | 20.6075 | 20.5518 | 20.3609 | 20.303 | 19.5972 | 19.5937 | 19.5884 | 19.5437 | 19.4976 | 19.4526 | 19.4064 | 19.3383 | 19.3124 | 19.2308 | 19.1539 | 18.942 | 18.6347 | 19.9007 | 19.9007 | 19.9007 | 19.862 | 19.8227 | 19.7826 | 19.7412 | 19.6771 | 19.6554 | 19.5859 | 19.5302 | 18.9462 | 18.476
|  | WYCOMBE MARSH | FS |  |  | 20.9223 | 20.9223 | 20.9223 | 20.9223 | 20.9223 | 20.9223 | 20.9223 | 20.9223 | 20.9223 | 20.9223 | 20.9223 | 20.9223 | 20.9223 | 19.6018 | 19.6009 | 19.6001 | 19.5983 | 19.5965 | 19.5948 | 19.5932 | 19.5912 | 19.5896 | 19.5848 | 19.5767 | 19.5685 | 19.5607 | 19.9007 | 19.9007 | 19.9007 | 19.9007 | 19.9007 | 19.9007 | 19.9007 | 19.9007 | 19.9007 | 19.9007 | 19.9007 | 19.9007 | 19.9007
LOVEDEAN GSP | WYMERING BSP | WYMERING | MINIMUM HEADROOM | SU 64974 05375 | YES | 89.6261 | 89.6035 | 88.6946 | 88.36 | 88.0171 | 87.6573 | 87.288 | 86.779 | 86.6668 | 86.3052 | 85.7341 | 83.9424 | 82.1563 | 87.44 | 87.4164 | 86.5052 | 86.168 | 85.8153 | 85.3672 | 84.9095 | 84.3148 | 84.1119 | 83.477 | 81.6965 | 79.2696 | 77.2602 | 88.5191 | 88.5045 | 87.6121 | 87.2966 | 86.9733 | 86.6389 | 86.295 | 85.8107 | 85.7245 | 85.4414 | 85.0032 | 84.4247 | 84.2354
|  | WYMERING | CT |  |  | 89.7037 | 89.6879 | 89.1378 | 89.0766 | 89.0147 | 88.9537 | 88.8844 | 88.816 | 88.7724 | 88.6412 | 87.8681 | 86.5957 | 84.8381 | 87.5179 | 87.5011 | 86.949 | 86.8854 | 86.821 | 86.7198 | 86.562 | 86.4079 | 86.2736 | 85.8692 | 84.0224 | 81.9485 | 79.9676 | 88.5952 | 88.5864 | 88.051 | 88.0071 | 87.9632 | 87.9193 | 87.8754 | 87.8315 | 87.8139 | 87.7613 | 87.1211 | 86.8952 | 86.7343
|  | WYMERING | LW |  |  | 89.6261 | 89.6035 | 88.6946 | 88.36 | 88.0171 | 87.6573 | 87.288 | 86.779 | 86.6668 | 86.3052 | 85.7341 | 83.9424 | 82.1563 | 87.44 | 87.4164 | 86.5052 | 86.168 | 85.8153 | 85.3672 | 84.9095 | 84.3148 | 84.1119 | 83.477 | 81.6965 | 79.2696 | 77.2602 | 88.5191 | 88.5045 | 87.6121 | 87.2966 | 86.9733 | 86.6389 | 86.295 | 85.8107 | 85.7245 | 85.4414 | 85.0032 | 84.4247 | 84.2354
|  | WYMERING | ST |  |  | 89.7651 | 89.7346 | 89.3696 | 89.3114 | 89.2511 | 89.1897 | 89.1276 | 89.0521 | 89.0125 | 88.8914 | 88.7163 | 88.5085 | 88.2575 | 87.5825 | 87.5486 | 87.1825 | 87.1228 | 87.0607 | 86.9974 | 86.9334 | 86.8067 | 86.7051 | 86.3962 | 85.9048 | 84.9973 | 83.7382 | 88.6332 | 88.6274 | 88.2704 | 88.2233 | 88.1759 | 88.1281 | 88.0797 | 88.0209 | 87.9991 | 87.932 | 87.8477 | 87.7334 | 87.6423
|  | WYMERING | FS |  |  | 89.8113 | 89.7836 | 89.6029 | 89.5675 | 89.5322 | 89.497 | 89.4615 | 89.4166 | 89.334 | 89.0741 | 88.9034 | 88.5148 | 88.1659 | 87.6298 | 87.5987 | 87.4177 | 87.3817 | 87.3457 | 87.3098 | 87.2737 | 87.2281 | 87.1445 | 86.8817 | 86.6352 | 86.1104 | 85.6253 | 88.6713 | 88.6683 | 88.4898 | 88.4591 | 88.4287 | 88.3983 | 88.3676 | 88.3279 | 88.2523 | 88.0134 | 87.8787 | 87.5293 | 87.2195
COWLEY GSP | YARNTON BSP | YARNTON | MINIMUM HEADROOM | SP 48277 12108 | NO | 59.3047 | 59.2929 | 58.5774 | 58.5169 | 58.4544 | 58.3898 | 58.3229 | 58.2477 | 58.2214 | 58.1364 | 57.4337 | 55.8005 | 54.4822 | 55.0262 | 55.0024 | 54.2682 | 54.1849 | 54.0967 | 53.4669 | 52.7519 | 51.9944 | 51.2977 | 49.9443 | 47.7443 | 45.8454 | 44.3424 | 57.5976 | 57.5859 | 56.8703 | 56.8098 | 56.7474 | 56.41 | 55.7353 | 55.0203 | 54.3653 | 53.0909 | 50.9841 | 49.1396 | 47.6213
|  | YARNTON | CT |  |  | 59.3657 | 59.3586 | 58.9293 | 58.823 | 58.715 | 58.6053 | 58.4917 | 58.334 | 58.3042 | 58.2094 | 57.4337 | 55.8005 | 54.4822 | 55.0873 | 55.0682 | 54.6202 | 54.4911 | 54.3575 | 53.7734 | 53.0116 | 52.1718 | 51.4715 | 50.1084 | 47.7443 | 45.8454 | 44.3424 | 57.6586 | 57.6516 | 57.2222 | 57.1159 | 57.0079 | 56.7108 | 55.9894 | 55.192 | 54.5335 | 53.2493 | 50.9841 | 49.1396 | 47.6213
|  | YARNTON | LW |  |  | 59.3047 | 59.2929 | 58.5774 | 58.5169 | 58.4544 | 58.3898 | 58.3229 | 58.2477 | 58.2214 | 58.1364 | 57.9702 | 56.6205 | 55.3757 | 55.0262 | 55.0024 | 54.2682 | 54.1849 | 54.0967 | 53.4669 | 52.7519 | 51.9944 | 51.2977 | 49.9443 | 48.2034 | 46.6524 | 45.2228 | 57.5976 | 57.5859 | 56.8703 | 56.8098 | 56.7474 | 56.41 | 55.7353 | 55.0203 | 54.3653 | 53.0909 | 51.4488 | 49.9454 | 48.5006
|  | YARNTON | ST |  |  | 59.3962 | 59.3915 | 59.1052 | 59.0814 | 59.0572 | 59.0325 | 59.0073 | 58.98 | 58.9688 | 58.9307 | 58.8707 | 58.7967 | 58.7285 | 55.1273 | 55.1117 | 54.8161 | 54.7793 | 54.7396 | 54.6948 | 54.6485 | 54.1939 | 53.7231 | 52.8079 | 51.6711 | 50.6851 | 49.7751 | 57.6891 | 57.6844 | 57.3982 | 57.3743 | 57.3501 | 57.3255 | 57.3003 | 57.1285 | 56.6863 | 55.8257 | 54.7559 | 53.8267 | 52.969
|  | YARNTON | FS |  |  | 59.4267 | 59.4243 | 59.2812 | 59.2695 | 59.2577 | 59.2459 | 59.2341 | 59.2222 | 59.2169 | 59.1992 | 59.1729 | 59.1452 | 59.106 | 55.1611 | 55.151 | 55.0034 | 54.985 | 54.966 | 54.9461 | 54.9263 | 54.9054 | 54.8913 | 54.8571 | 54.7701 | 54.4012 | 54.0701 | 57.7196 | 57.7172 | 57.5741 | 57.5624 | 57.5506 | 57.5389 | 57.527 | 57.5152 | 57.5098 | 57.4922 | 57.4659 | 57.3332 | 57.0203
BRAMLEY (ANDO-THAT) | THATCHAM BSP | YATTENDON | MINIMUM HEADROOM | SU 53699 74307 | YES | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 17.3581 | 17.0166 | 16.5645 | 16.1245 | 15.6245 | 15.6208 | 15.613 | 15.6044 | 15.5958 | 15.5873 | 15.5827 | 15.5782 | 15.5458 | 15.2268 | 14.7098 | 14.179 | 13.6625 | 15.8718 | 15.8718 | 15.8718 | 15.8718 | 15.8718 | 15.8718 | 15.8718 | 15.8718 | 15.8718 | 15.8718 | 15.8718 | 15.4181 | 14.9084
|  | YATTENDON | CT |  |  | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 17.3581 | 17.0166 | 16.5645 | 16.1245 | 15.6245 | 15.6208 | 15.613 | 15.6044 | 15.5958 | 15.5873 | 15.5827 | 15.5782 | 15.5458 | 15.2268 | 14.7098 | 14.179 | 13.6625 | 15.8718 | 15.8718 | 15.8718 | 15.8718 | 15.8718 | 15.8718 | 15.8718 | 15.8718 | 15.8718 | 15.8718 | 15.8718 | 15.4181 | 14.9084
|  | YATTENDON | LW |  |  | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 17.3631 | 17.0758 | 16.6237 | 16.1833 | 15.6245 | 15.6208 | 15.6131 | 15.6045 | 15.5958 | 15.5904 | 15.5858 | 15.5813 | 15.5764 | 15.2962 | 14.7793 | 14.2485 | 13.7314 | 15.8718 | 15.8718 | 15.8718 | 15.8718 | 15.8718 | 15.8718 | 15.8718 | 15.8718 | 15.8718 | 15.8718 | 15.8718 | 15.4866 | 14.9764
|  | YATTENDON | ST |  |  | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 17.3786 | 17.3538 | 17.1201 | 15.627 | 15.625 | 15.6215 | 15.6165 | 15.6106 | 15.6065 | 15.6029 | 15.5998 | 15.5965 | 15.587 | 15.5094 | 15.1676 | 14.8314 | 15.8718 | 15.8718 | 15.8718 | 15.8718 | 15.8718 | 15.8718 | 15.8718 | 15.8718 | 15.8718 | 15.8718 | 15.8718 | 15.8718 | 15.8718
|  | YATTENDON | FS |  |  | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 17.38 | 15.6303 | 15.63 | 15.6297 | 15.6281 | 15.6262 | 15.6247 | 15.6234 | 15.6217 | 15.6205 | 15.6168 | 15.611 | 15.6055 | 15.6004 | 15.8718 | 15.8718 | 15.8718 | 15.8718 | 15.8718 | 15.8718 | 15.8718 | 15.8718 | 15.8718 | 15.8718 | 15.8718 | 15.8718 | 15.8718
MELKSHAM GSP | CHIPPENHAM | YATTON KEYNELL | MINIMUM HEADROOM | ST 87300 75782 | YES | 6.5302 | 6.5302 | 6.5302 | 6.3694 | 6.1998 | 6.0188 | 5.8193 | 5.4769 | 5.3875 | 5.094 | 4.6079 | 3.8891 | 3.6204 | 5.7259 | 5.6443 | 5.4716 | 5.1435 | 4.8082 | 4.5748 | 4.3311 | 3.9808 | 3.8828 | 3.5641 | 3.0363 | 2.2745 | 1.9635 | 6.0738 | 6.02 | 5.9063 | 5.6146 | 5.2797 | 5.0464 | 4.8027 | 4.4525 | 4.3546 | 4.0362 | 3.5089 | 2.7477 | 2.4372
|  | YATTON KEYNELL | CT |  |  | 6.5302 | 6.5302 | 6.5302 | 6.4428 | 6.353 | 6.2608 | 6.1267 | 5.9299 | 5.863 | 5.6568 | 5.0823 | 4.4814 | 4.1553 | 5.7384 | 5.6639 | 5.5063 | 5.266 | 5.0248 | 4.7827 | 4.6332 | 4.4285 | 4.3531 | 4.1216 | 3.5055 | 2.8616 | 2.4932 | 6.0821 | 6.033 | 5.9291 | 5.737 | 5.4961 | 5.2543 | 5.1049 | 4.9003 | 4.8249 | 4.5938 | 3.9782 | 3.3348 | 2.967
|  | YATTON KEYNELL | LW |  |  | 6.5302 | 6.5302 | 6.5302 | 6.3694 | 6.1998 | 6.0188 | 5.8193 | 5.4769 | 5.3875 | 5.094 | 4.6079 | 3.8891 | 3.6204 | 5.7259 | 5.6443 | 5.4716 | 5.1435 | 4.8082 | 4.5748 | 4.3311 | 3.9808 | 3.8828 | 3.5641 | 3.0363 | 2.2745 | 1.9635 | 6.0738 | 6.02 | 5.9063 | 5.6146 | 5.2797 | 5.0464 | 4.8027 | 4.4525 | 4.3546 | 4.0362 | 3.5089 | 2.7477 | 2.4372
|  | YATTON KEYNELL | ST |  |  | 6.5302 | 6.5302 | 6.5302 | 6.5295 | 6.528 | 6.5257 | 6.5224 | 6.515 | 6.5114 | 6.4922 | 6.3669 | 6.1267 | 5.9436 | 5.7643 | 5.7112 | 5.62 | 5.5075 | 5.3712 | 5.3258 | 5.2799 | 5.2374 | 5.196 | 5.0664 | 4.8619 | 4.5939 | 4.3833 | 6.0991 | 6.0642 | 6.004 | 5.9296 | 5.8393 | 5.7968 | 5.7511 | 5.7086 | 5.6673 | 5.5379 | 5.3337 | 5.0661 | 4.8558
|  | YATTON KEYNELL | FS |  |  | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5301 | 6.5299 | 6.5296 | 6.5284 | 6.5215 | 6.516 | 6.4896 | 6.4639 | 5.8536 | 5.8473 | 5.8413 | 5.8135 | 5.7805 | 5.765 | 5.7495 | 5.7296 | 5.7138 | 5.6643 | 5.591 | 5.4996 | 5.4125 | 6.158 | 6.1538 | 6.1499 | 6.1315 | 6.1098 | 6.0995 | 6.0893 | 6.0761 | 6.0652 | 6.0302 | 5.98 | 5.9109 | 5.8446
AXMINSTER | YEOVIL BSP | YEOVIL | MINIMUM HEADROOM | ST 57690 16833 | YES | 43.6372 | 43.6348 | 43.6306 | 43.6079 | 43.5845 | 43.5535 | 43.5163 | 43.468 | 43.4416 | 43.3521 | 43.1853 | 42.5117 | 41.1517 | 40.051 | 40.051 | 40.051 | 40.0329 | 40.0145 | 39.9958 | 39.9762 | 39.9461 | 39.9423 | 39.8199 | 39.5406 | 37.9125 | 36.3268 | 41.4006 | 41.3987 | 41.3953 | 41.3736 | 41.3512 | 41.3237 | 41.2903 | 41.2462 | 41.2244 | 41.1406 | 40.6634 | 39.0385 | 37.456
|  | YEOVIL | CT |  |  | 43.6372 | 43.6348 | 43.6306 | 43.6079 | 43.5845 | 43.5606 | 43.5219 | 43.4711 | 43.4447 | 43.356 | 43.1853 | 42.5683 | 41.1948 | 40.051 | 40.051 | 40.051 | 40.0329 | 40.0145 | 39.9958 | 39.9762 | 39.9461 | 39.9423 | 39.93 | 39.5969 | 37.9921 | 36.3929 | 41.4006 | 41.3987 | 41.3953 | 41.3736 | 41.3512 | 41.3284 | 41.2935 | 41.2469 | 41.225 | 41.1518 | 40.7755 | 39.1178 | 37.5218
|  | YEOVIL | LW |  |  | 43.6372 | 43.6348 | 43.6306 | 43.6098 | 43.5881 | 43.5535 | 43.5163 | 43.468 | 43.4416 | 43.3521 | 43.2223 | 42.5117 | 41.1517 | 40.051 | 40.051 | 40.051 | 40.0348 | 40.018 | 40.0005 | 39.9824 | 39.9549 | 39.9511 | 39.9381 | 39.5406 | 37.9125 | 36.3268 | 41.4006 | 41.3987 | 41.3953 | 41.3754 | 41.3547 | 41.3237 | 41.2903 | 41.2462 | 41.2244 | 41.1503 | 40.6634 | 39.0385 | 37.456
|  | YEOVIL | ST |  |  | 43.638 | 43.6365 | 43.6342 | 43.6313 | 43.6279 | 43.6219 | 43.6145 | 43.6004 | 43.5849 | 43.5318 | 43.4561 | 43.3794 | 43.3047 | 40.051 | 40.051 | 40.051 | 40.051 | 40.051 | 40.051 | 40.051 | 40.051 | 40.051 | 40.051 | 40.0363 | 39.815 | 38.9931 | 41.4013 | 41.4 | 41.3982 | 41.3959 | 41.3932 | 41.3884 | 41.3825 | 41.3712 | 41.3589 | 41.3165 | 41.2561 | 41.0686 | 40.1173
|  | YEOVIL | FS |  |  | 43.6391 | 43.6384 | 43.6376 | 43.6266 | 43.6157 | 43.6043 | 43.5922 | 43.5739 | 43.5254 | 43.3699 | 43.2755 | 43.0411 | 42.8393 | 40.051 | 40.051 | 40.051 | 40.0412 | 40.0316 | 40.022 | 40.0122 | 39.9969 | 39.9545 | 39.8199 | 39.7558 | 39.5539 | 39.385 | 41.4021 | 41.4016 | 41.4009 | 41.3902 | 41.3795 | 41.3685 | 41.3568 | 41.3392 | 41.2919 | 41.1406 | 41.0523 | 40.8245 | 40.6294
AXMINSTER | YEOVIL BSP | YETMINSTER | MINIMUM HEADROOM | ST 60294 10206 | YES | 19.1938 | 19.1938 | 19.1938 | 19.1028 | 19.0064 | 18.9045 | 18.7907 | 18.6044 | 18.5791 | 18.4858 | 17.5947 | 16.5815 | 16.0143 | 15.9288 | 15.91 | 15.8702 | 15.7182 | 15.5572 | 15.3891 | 15.1486 | 14.8293 | 14.6586 | 14.0887 | 12.9556 | 11.8665 | 11.2254 | 16.8759 | 16.8574 | 16.8183 | 16.6673 | 16.5074 | 16.3404 | 16.102 | 15.7849 | 15.6167 | 15.0547 | 13.9315 | 12.8508 | 12.2178
|  | YETMINSTER | CT |  |  | 19.1938 | 19.1938 | 19.1938 | 19.1028 | 19.0064 | 18.9045 | 18.7907 | 18.6044 | 18.5791 | 18.4858 | 17.5947 | 16.5815 | 16.0143 | 15.9288 | 15.91 | 15.8702 | 15.7182 | 15.5572 | 15.3891 | 15.1486 | 14.8293 | 14.6586 | 14.0887 | 12.9556 | 11.8665 | 11.2254 | 16.8759 | 16.8574 | 16.8183 | 16.6673 | 16.5074 | 16.3404 | 16.102 | 15.7849 | 15.6167 | 15.0547 | 13.9315 | 12.8508 | 12.2178
|  | YETMINSTER | LW |  |  | 19.1938 | 19.1938 | 19.1938 | 19.1651 | 19.1201 | 19.0554 | 18.9699 | 18.8152 | 18.7903 | 18.6754 | 18.1066 | 17.1922 | 16.7446 | 15.9481 | 15.94 | 15.923 | 15.8551 | 15.7672 | 15.5806 | 15.3683 | 15.0807 | 14.9104 | 14.3187 | 13.4736 | 12.4832 | 11.9618 | 16.8949 | 16.8869 | 16.8702 | 16.8029 | 16.7158 | 16.5312 | 16.321 | 16.0356 | 15.8678 | 15.2841 | 14.4488 | 13.4668 | 12.9535
|  | YETMINSTER | ST |  |  | 19.1938 | 19.1938 | 19.1938 | 19.1907 | 19.1845 | 19.1746 | 19.1598 | 19.1294 | 19.116 | 19.05 | 18.9678 | 18.5975 | 18.2323 | 15.9534 | 15.9489 | 15.9413 | 15.9136 | 15.8785 | 15.8048 | 15.7231 | 15.6025 | 15.4898 | 15.0933 | 14.609 | 14.0047 | 13.5912 | 16.9001 | 16.8957 | 16.8882 | 16.8609 | 16.8263 | 16.7537 | 16.6731 | 16.554 | 16.4429 | 16.0519 | 15.5744 | 14.9755 | 14.5674
|  | YETMINSTER | FS |  |  | 19.1938 | 19.1938 | 19.1938 | 19.1937 | 19.1934 | 19.1929 | 19.1922 | 19.1906 | 19.1842 | 19.1478 | 19.1191 | 18.9835 | 18.8518 | 15.9607 | 15.96 | 15.9595 | 15.9487 | 15.9368 | 15.9149 | 15.8918 | 15.8623 | 15.8169 | 15.651 | 15.4673 | 15.2138 | 14.9724 | 16.9072 | 16.9066 | 16.9061 | 16.8955 | 16.8838 | 16.8622 | 16.8395 | 16.8104 | 16.7657 | 16.602 | 16.4209 | 16.1693 | 15.9298
AXMINSTER |  | YIEWSLEY | MINIMUM HEADROOM | TQ 05643 80961 |  | 50.1361 | 50.122 | 49.2623 | 49.0948 | 48.9242 | 48.7492 | 48.5703 | 48.3352 | 48.2842 | 48.1215 | 47.7317 | 47.2563 | 46.1825 | 45.6277 | 45.6068 | 44.7338 | 44.5527 | 44.3693 | 44.1709 | 43.9687 | 43.7104 | 43.6346 | 43.3958 | 42.7361 | 40.3296 | 38.0295 | 47.7922 | 47.773 | 46.9032 | 46.7253 | 46.545 | 46.3523 | 46.1558 | 45.9031 | 45.8333 | 45.613 | 45.2143 | 42.8044 | 40.5578
|  | YIEWSLEY | CT |  |  | 50.2094 | 50.201 | 49.6851 | 49.6428 | 49.6005 | 49.5582 | 49.516 | 49.4737 | 49.4568 | 49.406 | 48.6749 | 48.306 | 47.4454 | 45.7025 | 45.688 | 45.1607 | 45.1064 | 45.0529 | 45.0002 | 44.9346 | 44.869 | 44.8273 | 44.7005 | 43.741 | 41.6119 | 39.3281 | 47.8666 | 47.8536 | 47.3291 | 47.2777 | 47.2269 | 47.1767 | 47.1167 | 47.0568 | 47.0211 | 46.9128 | 46.1806 | 44.0805 | 41.8501
|  | YIEWSLEY | LW |  |  | 50.1361 | 50.122 | 49.2623 | 49.0948 | 48.9242 | 48.7492 | 48.5703 | 48.3352 | 48.2842 | 48.1215 | 47.7317 | 47.2563 | 46.1825 | 45.6277 | 45.6068 | 44.7338 | 44.5527 | 44.3693 | 44.1709 | 43.9687 | 43.7104 | 43.6346 | 43.3958 | 42.7361 | 40.3296 | 38.0295 | 47.7922 | 47.773 | 46.9032 | 46.7253 | 46.545 | 46.3523 | 46.1558 | 45.9031 | 45.8333 | 45.613 | 45.2143 | 42.8044 | 40.5578
|  | YIEWSLEY | ST |  |  | 50.2461 | 50.2404 | 49.8965 | 49.8683 | 49.8401 | 49.8119 | 49.7838 | 49.7556 | 49.7443 | 49.7105 | 49.6332 | 49.5005 | 49.3419 | 45.7559 | 45.7307 | 45.3793 | 45.3417 | 45.3031 | 45.2617 | 45.2204 | 45.1763 | 45.1481 | 45.0626 | 44.9025 | 44.5477 | 43.2957 | 47.9219 | 47.8955 | 47.5459 | 47.5106 | 47.4745 | 47.4364 | 47.3982 | 47.358 | 47.3339 | 47.2609 | 47.1259 | 47.0069 | 45.7467
|  | YIEWSLEY | FS |  |  | 50.2827 | 50.2799 | 50.1079 | 50.0859 | 50.0641 | 50.0423 | 50.0203 | 49.9939 | 49.954 | 49.8286 | 49.7487 | 49.569 | 49.4018 | 45.7967 | 45.7795 | 45.6067 | 45.5824 | 45.5577 | 45.5314 | 45.5051 | 45.4732 | 45.4267 | 45.2813 | 45.1602 | 44.9334 | 44.7185 | 47.9637 | 47.9428 | 47.7698 | 47.7457 | 47.7217 | 47.6965 | 47.6712 | 47.6407 | 47.5958 | 47.4552 | 47.3441 | 47.1287 | 46.9254
LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | ZETLAND ROAD | MINIMUM HEADROOM | SU 60592 00043 | YES | 32.6236 | 32.6088 | 31.7082 | 31.6344 | 31.5606 | 31.4868 | 31.4129 | 31.3391 | 31.3096 | 31.221 | 30.9675 | 28.9927 | 26.9667 | 29.2881 | 29.2733 | 28.3727 | 28.2989 | 28.2251 | 28.1513 | 28.0775 | 28.0036 | 27.9741 | 27.8855 | 26.3793 | 24.1328 | 21.8385 | 30.6215 | 30.6041 | 29.696 | 29.6123 | 29.5269 | 29.4304 | 29.3338 | 29.2345 | 29.1784 | 29.0198 | 28.0147 | 25.7 | 23.3384
|  | ZETLAND ROAD | CT |  |  | 32.7003 | 32.6915 | 32.1511 | 32.1068 | 32.0625 | 32.0182 | 31.974 | 31.9297 | 31.9119 | 31.8588 | 31.137 | 29.0231 | 26.9973 | 29.3648 | 29.356 | 28.8156 | 28.7713 | 28.7271 | 28.6828 | 28.6385 | 28.5942 | 28.5765 | 28.5233 | 26.5531 | 24.1676 | 21.8735 | 30.6965 | 30.684 | 30.1341 | 30.0779 | 30.02 | 29.9641 | 29.8971 | 29.8273 | 29.7831 | 29.6599 | 28.1896 | 25.7359 | 23.3744
|  | ZETLAND ROAD | LW |  |  | 32.6236 | 32.6088 | 31.7082 | 31.6344 | 31.5606 | 31.4868 | 31.4129 | 31.3391 | 31.3096 | 31.221 | 30.9675 | 28.9927 | 26.9667 | 29.2881 | 29.2733 | 28.3727 | 28.2989 | 28.2251 | 28.1513 | 28.0775 | 28.0036 | 27.9741 | 27.8855 | 26.3793 | 24.1328 | 21.8385 | 30.6215 | 30.6041 | 29.696 | 29.6123 | 29.5269 | 29.4304 | 29.3338 | 29.2345 | 29.1784 | 29.0198 | 28.0147 | 25.7 | 23.3384
|  | ZETLAND ROAD | ST |  |  | 32.7387 | 32.7328 | 32.3726 | 32.343 | 32.3135 | 32.284 | 32.2545 | 32.2249 | 32.2131 | 32.1777 | 32.1186 | 32.0832 | 30.9386 | 29.4032 | 29.3973 | 29.0371 | 29.0076 | 28.978 | 28.9485 | 28.919 | 28.8895 | 28.8776 | 28.8422 | 28.7832 | 27.6402 | 26.2101 | 30.738 | 30.7305 | 30.3661 | 30.3302 | 30.2929 | 30.2498 | 30.2068 | 30.16 | 30.13 | 30.0465 | 29.901 | 29.2836 | 27.8103
|  | ZETLAND ROAD | FS |  |  | 32.7771 | 32.7741 | 32.594 | 32.5769 | 32.5598 | 32.5427 | 32.5255 | 32.507 | 32.4908 | 32.4402 | 32.3951 | 32.3281 | 32.2544 | 29.4416 | 29.4387 | 29.2585 | 29.2414 | 29.2243 | 29.2072 | 29.19 | 29.1716 | 29.1553 | 29.1047 | 29.0596 | 28.9926 | 28.919 | 30.7781 | 30.7746 | 30.5928 | 30.5728 | 30.5524 | 30.5307 | 30.509 | 30.4845 | 30.4611 | 30.3918 | 30.312 | 30.2052 | 30.0912

## BSP Headroom Dem
Grid Supply Point | Bulk Supply Point |  | Scenario | Grid Reference | Upstream Constraint (YES / NO) | Demand Headroom Winter (MVA) | [12 empty] | Demand Headroom Summer (MVA) | [12 empty] | Demand Headroom Spring/Autumn (MVA)
[6 empty] | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2035 | 2040 | 2045 | 2050 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2035 | 2040 | 2045 | 2050 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2035 | 2040 | 2045 | 2050
BRAMLEY (FLEE) | ALDERSHOT BSP | ALDERSHOT BSP | MINIMUM HEADROOM | SU 85922 48779 | YES | 54.753 | 49.988 | 44.4849 | 36.8819 | 29.3728 | 21.1815 | 12.3083 | 1.489 | -9.286 | -35.7642 | -68.7488 | -88.0178 | -102.8673 | 101.105 | 98.2275 | 94.9069 | 90.7813 | 86.565 | 81.7739 | 76.462 | 69.5256 | 62.6904 | 46.8065 | 25.1933 | 5.4875 | -13.4545 | 68.7723 | 64.3878 | 59.368 | 52.4493 | 45.5203 | 37.9108 | 29.614 | 19.3878 | 9.2221 | -15.4227 | -45.6363 | -61.925 | -74.1883
|  | ALDERSHOT BSP | CT |  |  | 57.2219 | 53.5362 | 48.8497 | 43.3273 | 37.9897 | 32.3529 | 26.1867 | 18.9956 | 8.353 | -17.9694 | -59.6534 | -88.0178 | -102.8673 | 101.4023 | 98.7381 | 95.3857 | 91.8484 | 88.2683 | 84.3594 | 80.0057 | 74.7777 | 67.6969 | 51.0096 | 25.1933 | 5.4875 | -12.9362 | 70.8962 | 67.4727 | 63.1505 | 58.0888 | 53.1063 | 47.8154 | 41.9866 | 35.1517 | 25.1172 | 0.61799 | -37.1224 | -61.925 | -74.1883
|  | ALDERSHOT BSP | LW |  |  | 54.753 | 49.988 | 44.4849 | 36.8819 | 29.3728 | 21.1815 | 12.3083 | 1.489 | -9.286 | -35.7642 | -68.7488 | -82.1896 | -90.2519 | 101.105 | 98.2275 | 94.9069 | 90.7813 | 86.565 | 81.7739 | 76.462 | 69.5256 | 62.6904 | 46.8065 | 28.0383 | 21.2647 | 17.1936 | 68.7723 | 64.3878 | 59.368 | 52.4493 | 45.5203 | 37.9108 | 29.614 | 19.3878 | 9.2221 | -15.4227 | -45.6363 | -57.442 | -64.3951
|  | ALDERSHOT BSP | ST |  |  | 61.3213 | 59.4525 | 57.1732 | 54.4094 | 51.8101 | 48.968 | 45.7957 | 42.1204 | 37.8427 | 19.6514 | -14.7711 | -33.4446 | -44.6327 | 104.2247 | 102.7746 | 101.0411 | 98.9794 | 96.9302 | 94.6484 | 92.0567 | 89.0293 | 85.6305 | 70.8234 | 43.2331 | 25.6194 | 8.2847 | 74.839 | 73.1541 | 71.1382 | 68.6295 | 66.1969 | 63.5238 | 60.504 | 56.999 | 52.9362 | 35.4191 | 2.7949 | -14.0917 | -23.8069
|  | ALDERSHOT BSP | FS |  |  | 61.7196 | 60.0987 | 58.1722 | 55.7675 | 52.5337 | 49.196 | 45.5307 | 40.5265 | 36.9216 | 23.8936 | -9.9045 | -30.5905 | -39.9206 | 104.3089 | 102.9374 | 101.3502 | 99.6169 | 96.8776 | 94.0059 | 90.797 | 86.2424 | 83.2782 | 72.0592 | 41.7598 | 15.6144 | -13.4545 | 104.3089 | 102.9374 | 101.3502 | 99.6169 | 96.8776 | 94.0059 | 90.797 | 86.2424 | 83.2782 | 72.0592 | 41.7598 | 15.6144 | -13.4545
BRAMLEY (FLEE) | ALTON | ALTON | MINIMUM HEADROOM | SU 72730 39772 | YES | 23.7776 | 20.1196 | 16.41 | 11.6159 | 6.6216 | 1.2259 | -4.8124 | -11.8816 | -18.3254 | -33.1746 | -50.8201 | -57.0067 | -63.4507 | 57.9229 | 55.7269 | 53.4894 | 50.8226 | 47.9867 | 44.8189 | 41.1862 | 36.7251 | 32.778 | 24.5006 | 14.7623 | 7.4502 | -1.404 | 59.486 | 56.3739 | 53.223 | 49.2949 | 45.1741 | 40.6477 | 35.5101 | 29.1871 | 23.5041 | 11.0542 | -4.7312 | -10.2906 | -15.151
|  | ALTON | CT |  |  | 26.0897 | 23.3104 | 20.3406 | 17.0145 | 13.5158 | 9.7939 | 5.5589 | 0.83117 | -5.6325 | -19.8527 | -42.1095 | -57.0067 | -63.4507 | 58.4632 | 56.5055 | 54.3979 | 52.3235 | 50.0891 | 47.6484 | 44.8089 | 41.56 | 37.3896 | 28.8969 | 16.3288 | 7.4502 | 0.71782 | 61.0474 | 58.5674 | 55.9034 | 53.0662 | 50.0605 | 46.8242 | 43.1068 | 38.8891 | 33.0978 | 21.1862 | 3.2109 | -9.7557 | -15.151
|  | ALTON | LW |  |  | 23.7776 | 20.1196 | 16.41 | 11.6159 | 6.6216 | 1.2259 | -4.8124 | -11.8816 | -18.3254 | -33.1746 | -50.8201 | -56.9895 | -60.2321 | 57.9229 | 55.7269 | 53.4894 | 50.8226 | 47.9867 | 44.8189 | 41.1862 | 36.7251 | 32.778 | 24.5006 | 14.7623 | 11.4601 | 9.817 | 59.486 | 56.3739 | 53.223 | 49.2949 | 45.1741 | 40.6477 | 35.5101 | 29.1871 | 23.5041 | 11.0542 | -4.7312 | -10.2906 | -13.0764
|  | ALTON | ST |  |  | 28.4458 | 26.7697 | 25.1019 | 23.2825 | 21.3623 | 19.294 | 17.0104 | 14.4292 | 11.4275 | -0.52284 | -17.9963 | -27.1411 | -32.6526 | 60.0949 | 58.8643 | 57.6345 | 56.3735 | 55.0107 | 53.5159 | 51.858 | 49.9516 | 47.7334 | 38.5183 | 25.1817 | 17.6557 | 11.1153 | 63.2146 | 61.7259 | 60.2446 | 58.649 | 56.9562 | 55.1187 | 53.0857 | 50.7718 | 48.1081 | 36.9887 | 21.0776 | 13.4799 | 9.1484
|  | ALTON | FS |  |  | 28.7925 | 27.332 | 25.9507 | 24.1529 | 21.1333 | 18.0433 | 14.7151 | 9.97 | 7.1927 | -2.1768 | -23.1482 | -34.1713 | -39.3868 | 60.1961 | 59.0608 | 57.9783 | 56.8457 | 54.4667 | 52.018 | 49.3659 | 45.2987 | 43.3476 | 36.4654 | 20.0498 | 9.0665 | -1.404 | 60.1961 | 59.0608 | 57.9783 | 56.8457 | 54.4667 | 52.018 | 49.3659 | 45.2987 | 43.3476 | 36.4654 | 20.0498 | 9.0665 | -1.404
MELKSHAM GSP | AMESBURY | AMESBURY | MINIMUM HEADROOM | SU 15842 42724 | YES | 58.6508 | 57.1018 | 55.4821 | 53.265 | 50.9152 | 48.4466 | 45.8242 | 42.6445 | 39.5065 | 32.4815 | 26.5477 | 24.9962 | 24.4023 | 69.4789 | 68.9875 | 68.1767 | 67.1003 | 65.9462 | 64.7129 | 63.391 | 61.7424 | 60.048 | 56.3882 | 53.3881 | 52.6817 | 50.287 | 67.2807 | 65.888 | 64.4133 | 62.3695 | 60.2091 | 57.9449 | 55.5437 | 52.6478 | 49.7816 | 43.237 | 37.6684 | 36.22 | 35.6705
|  | AMESBURY | CT |  |  | 60.4447 | 59.6292 | 58.5473 | 57.1266 | 55.5965 | 53.9773 | 52.2191 | 50.2483 | 47.365 | 40.7773 | 33.7479 | 29.7407 | 27.9854 | 69.4789 | 69.2988 | 69.059 | 68.5822 | 67.7538 | 66.8688 | 65.9002 | 64.7833 | 62.967 | 59.1349 | 55.2482 | 52.7698 | 50.6979 | 69.0095 | 68.2776 | 67.3142 | 66.0211 | 64.6326 | 63.1649 | 61.5741 | 59.7862 | 57.0715 | 50.9767 | 44.4997 | 40.7248 | 39.0743
|  | AMESBURY | LW |  |  | 58.6508 | 57.1018 | 55.4821 | 53.265 | 50.9152 | 48.4466 | 45.8242 | 42.6445 | 39.5065 | 32.4815 | 26.5477 | 24.9962 | 24.4023 | 69.5053 | 68.9875 | 68.1767 | 67.1003 | 65.9462 | 64.7129 | 63.391 | 61.7424 | 60.048 | 56.3882 | 53.3881 | 52.6817 | 52.4015 | 67.2807 | 65.888 | 64.4133 | 62.3695 | 60.2091 | 57.9449 | 55.5437 | 52.6478 | 49.7816 | 43.237 | 37.6684 | 36.22 | 35.6705
|  | AMESBURY | ST |  |  | 61.2652 | 60.8112 | 60.3129 | 59.5371 | 58.6904 | 57.8035 | 56.8465 | 55.8116 | 54.7343 | 50.2461 | 42.5594 | 38.8928 | 36.4552 | 69.6745 | 69.5823 | 69.4762 | 69.341 | 69.1819 | 68.9151 | 68.3579 | 67.7453 | 67.1238 | 64.4071 | 59.0979 | 56.5794 | 54.2505 | 69.753 | 69.3496 | 68.9074 | 68.2072 | 67.4467 | 66.6513 | 65.7941 | 64.8615 | 63.8754 | 59.7559 | 52.5151 | 49.225 | 46.9951
|  | AMESBURY | FS |  |  | 61.4617 | 61.0869 | 60.6884 | 59.8407 | 58.9422 | 58.0286 | 57.0248 | 56.0126 | 54.7563 | 50.3718 | 39.8974 | 34.2479 | 31.149 | 69.6691 | 69.5783 | 69.4764 | 69.3729 | 69.254 | 69.0609 | 68.5134 | 67.9505 | 67.2673 | 64.7985 | 58.1555 | 53.9612 | 50.287 | 69.6691 | 69.5783 | 69.4764 | 69.3729 | 69.254 | 69.0609 | 68.5134 | 67.9505 | 67.2673 | 64.7985 | 58.1555 | 53.9612 | 50.287
BRAMLEY (ANDO-THAT) | ANDOVER BSP | ANDOVER BSP | MINIMUM HEADROOM | SU 35334 46598 | YES | 36.7713 | 33.8995 | 30.9033 | 26.5431 | 21.6271 | 16.4099 | 10.8372 | 4.2079 | -2.386 | -18.8456 | -38.2677 | -46.1825 | -50.5578 | 56.116 | 54.4081 | 52.6062 | 50.1889 | 47.2859 | 44.1439 | 40.7529 | 33.6105 | 31.0556 | 22.1705 | 4.0683 | -9.333 | -21.0572 | 41.6551 | 39.0005 | 36.2174 | 32.2182 | 27.6739 | 22.8261 | 17.6285 | 11.3782 | 5.169 | -10.114 | -28.0678 | -35.3758 | -38.8147
|  | ANDOVER BSP | CT |  |  | 39.2868 | 37.4191 | 35.2176 | 32.2607 | 28.843 | 25.2764 | 21.3475 | 16.9787 | 10.7152 | -4.8582 | -28.3987 | -43.7319 | -50.5578 | 56.9443 | 55.5941 | 53.9965 | 52.0919 | 49.7752 | 47.3181 | 44.5356 | 41.3378 | 37.075 | 26.8667 | 12.6272 | 2.2489 | -5.6903 | 43.846 | 42.0868 | 39.99 | 37.2367 | 34.0329 | 30.6772 | 26.9634 | 22.8101 | 16.8965 | 2.3883 | -19.0872 | -32.8736 | -38.7196
|  | ANDOVER BSP | LW |  |  | 36.7713 | 33.8995 | 30.9033 | 26.5431 | 21.6271 | 16.4099 | 10.8372 | 4.2079 | -2.386 | -18.8456 | -38.2677 | -46.1825 | -49.9184 | 56.116 | 54.4081 | 52.6062 | 50.1889 | 47.2859 | 44.1439 | 40.7529 | 36.5533 | 32.2619 | 22.1705 | 10.571 | 5.4541 | 2.8919 | 41.6551 | 39.0005 | 36.2174 | 32.2182 | 27.6739 | 22.8261 | 17.6285 | 11.3782 | 5.169 | -10.114 | -28.0678 | -35.3758 | -38.8147
|  | ANDOVER BSP | ST |  |  | 41.2542 | 40.1491 | 38.9558 | 37.3213 | 35.2707 | 33.0922 | 30.7637 | 28.1633 | 24.2353 | 9.782 | -12.0343 | -23.3494 | -29.8029 | 58.1773 | 57.3099 | 56.3699 | 55.1907 | 53.6236 | 51.9387 | 50.1275 | 48.0929 | 44.8325 | 33.0041 | 15.4254 | 5.7195 | -1.9155 | 45.7335 | 44.7066 | 43.5873 | 42.0643 | 40.1332 | 38.074 | 35.8663 | 33.388 | 29.6116 | 15.6377 | -5.2575 | -15.7595 | -21.5638
|  | ANDOVER BSP | FS |  |  | 41.6143 | 40.6456 | 39.6611 | 38.0019 | 32.7755 | 28.5063 | 23.0568 | 13.9723 | 10.6889 | -0.3294 | -23.375 | -36.8904 | -43.0629 | 58.2954 | 57.4684 | 56.6164 | 55.4824 | 50.7909 | 47.0453 | 42.138 | 33.6105 | 31.0556 | 22.4024 | 4.0683 | -9.333 | -21.0572 | 58.2954 | 57.4684 | 56.6164 | 55.4824 | 50.7909 | 47.0453 | 42.138 | 33.6105 | 31.0556 | 22.4024 | 4.0683 | -9.333 | -21.0572
MANNINGTON GSP | ARNEWOOD | ARNEWOOD | MINIMUM HEADROOM | SZ 26094 97294 | YES | 22.5257 | 20.5361 | 18.3105 | 14.6916 | 10.6448 | 6.2699 | 1.6474 | -3.7266 | -9.1655 | -21.8823 | -36.9725 | -47.9596 | -55.1173 | 40.5128 | 39.2268 | 37.7918 | 35.7532 | 33.3466 | 30.6777 | 27.8097 | 23.9722 | 20.7991 | 13.1123 | 1.2915 | -9.6337 | -19.7493 | 30.302 | 28.4911 | 26.489 | 23.2125 | 19.5309 | 15.5202 | 11.2121 | 6.1439 | 0.99746 | -10.8728 | -24.7469 | -34.538 | -40.8989
|  | ARNEWOOD | CT |  |  | 23.8415 | 22.6222 | 20.7648 | 18.2191 | 15.3335 | 12.1972 | 8.861 | 5.2613 | -0.19599 | -13.6403 | -33.4166 | -47.9596 | -55.1173 | 40.8566 | 39.924 | 38.5118 | 36.8536 | 34.8966 | 32.7586 | 30.447 | 27.8835 | 24.2627 | 15.6764 | 4.267 | -4.7353 | -11.6772 | 31.5544 | 30.4481 | 28.7715 | 26.4186 | 23.7331 | 20.8069 | 17.6722 | 14.2571 | 9.0993 | -3.4782 | -21.4106 | -34.538 | -40.8989
|  | ARNEWOOD | LW |  |  | 22.5257 | 20.5361 | 18.3105 | 14.6916 | 10.6448 | 6.2699 | 1.6474 | -3.7266 | -9.1655 | -21.8823 | -36.9725 | -44.1781 | -47.6701 | 40.5128 | 39.2268 | 37.7918 | 35.7532 | 33.3466 | 30.6777 | 27.8097 | 24.3298 | 20.7991 | 13.1123 | 4.4792 | 0.22919 | -1.9261 | 30.302 | 28.4911 | 26.489 | 23.2125 | 19.5309 | 15.5202 | 11.2121 | 6.1439 | 0.99746 | -10.8728 | -24.7469 | -31.3066 | -34.4683
|  | ARNEWOOD | ST |  |  | 25.1914 | 24.5481 | 23.8048 | 22.5251 | 20.9412 | 19.2333 | 17.4603 | 15.5526 | 12.8409 | 2.4379 | -15.7866 | -24.9309 | -30.6231 | 41.4951 | 41.1749 | 40.6853 | 39.7575 | 38.5472 | 37.2317 | 35.8472 | 34.3215 | 32.0477 | 23.2968 | 8.6581 | 0.9374 | -5.5867 | 32.7701 | 32.1827 | 31.5266 | 30.4189 | 29.0208 | 27.4784 | 25.8089 | 23.9893 | 21.3709 | 11.2308 | -6.2693 | -14.6783 | -19.7551
|  | ARNEWOOD | FS |  |  | 25.3057 | 24.6795 | 24.0134 | 22.9448 | 19.3278 | 15.6639 | 11.8903 | 5.6257 | 3.6018 | -3.4728 | -20.7411 | -30.2633 | -33.9905 | 41.4938 | 41.1716 | 40.6574 | 39.9171 | 36.6551 | 33.3381 | 29.9105 | 23.9722 | 22.3021 | 16.3077 | 1.2915 | -9.6337 | -19.7493 | 41.4938 | 41.1716 | 40.6574 | 39.9171 | 36.6551 | 33.3381 | 29.9105 | 23.9722 | 22.3021 | 16.3077 | 1.2915 | -9.6337 | -19.7493
BRAMLEY (BASI) | BASINGSTOKE T1A & T2A | BASINGSTOKE T1A & T2A | MINIMUM HEADROOM | SU 65132 52710 | YES | 39.7556 | 39.2663 | 38.7037 | 37.9904 | 36.4098 | 34.7689 | 33.0338 | 29.6978 | 28.8802 | 23.2532 | 15.1822 | 11.6371 | 8.7562 | 69.3841 | 68.8712 | 68.3016 | 67.5769 | 66.4585 | 64.5205 | 62.5811 | 58.9966 | 58.3057 | 56.0828 | 50.1251 | 44.7667 | 39.7364 | 37.225 | 36.4017 | 35.5025 | 34.1804 | 32.6929 | 31.1436 | 29.5048 | 27.5671 | 25.5467 | 20.2305 | 13.4559 | 9.5894 | 6.9817
|  | BASINGSTOKE T1A & T2A | CT |  |  | 39.7556 | 39.2725 | 38.72 | 38.1464 | 37.4724 | 36.8117 | 35.6359 | 34.2941 | 32.2465 | 26.6782 | 17.7463 | 11.6371 | 8.7562 | 69.3883 | 68.8845 | 68.316 | 67.7183 | 67.0366 | 66.3794 | 65.6607 | 64.8961 | 63.916 | 60.6863 | 54.1608 | 51.1045 | 47.8228 | 37.5836 | 36.9399 | 36.1534 | 35.1854 | 34.0894 | 32.9937 | 31.8341 | 30.5422 | 28.598 | 23.316 | 15.1313 | 9.5894 | 6.9817
|  | BASINGSTOKE T1A & T2A | LW |  |  | 39.7647 | 39.2663 | 38.7037 | 37.9904 | 36.4098 | 34.7689 | 33.0338 | 30.9999 | 28.8802 | 23.2532 | 15.1822 | 12.3177 | 10.9424 | 69.3841 | 68.8712 | 68.3016 | 67.5769 | 66.6993 | 65.829 | 64.888 | 63.8143 | 62.6946 | 57.646 | 51.3747 | 49.2365 | 48.1262 | 37.225 | 36.4017 | 35.5025 | 34.1804 | 32.6929 | 31.1436 | 29.5048 | 27.5671 | 25.5467 | 20.2305 | 13.4559 | 10.2135 | 8.7631
|  | BASINGSTOKE T1A & T2A | ST |  |  | 40.0801 | 39.7441 | 39.376 | 38.9649 | 38.4569 | 37.9707 | 37.4682 | 36.8994 | 35.7414 | 31.7984 | 20.3821 | 14.8033 | 12.8069 | 69.6512 | 69.2678 | 68.8495 | 68.4011 | 67.8702 | 67.3785 | 66.8807 | 66.3356 | 65.222 | 61.3284 | 52.3116 | 48.3116 | 46.9878 | 37.9541 | 37.6111 | 37.236 | 36.8186 | 36.2446 | 35.6192 | 34.9608 | 34.2214 | 32.9041 | 28.1441 | 19.6711 | 15.4967 | 13.2068
|  | BASINGSTOKE T1A & T2A | FS |  |  | 40.0939 | 39.7664 | 39.4158 | 39.0433 | 37.0924 | 35.183 | 33.2657 | 29.6978 | 29.0194 | 26.8355 | 19.7888 | 12.8466 | 10.8953 | 69.6567 | 69.2758 | 68.8663 | 68.4493 | 66.4585 | 64.5205 | 62.5811 | 58.9966 | 58.3057 | 56.0828 | 50.1251 | 44.7667 | 39.7364 | 69.6567 | 69.2758 | 68.8663 | 68.4493 | 66.4585 | 64.5205 | 62.5811 | 58.9966 | 58.3057 | 56.0828 | 50.1251 | 44.7667 | 39.7364
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | BASINGSTOKE T1B & T2B | MINIMUM HEADROOM | SU 65132 52711 | YES | 38.3338 | 36.0049 | 33.426 | 29.8653 | 25.9643 | 21.7577 | 17.2608 | 11.729 | 6.3676 | -5.6867 | -21.2582 | -30.5835 | -36.72 | 61.2994 | 59.9728 | 58.5446 | 56.7069 | 54.6194 | 52.3449 | 49.893 | 46.8048 | 43.831 | 37.2623 | 27.9252 | 18.7913 | 10.329 | 49.6744 | 47.5785 | 45.275 | 42.2327 | 38.8631 | 35.1711 | 31.1586 | 26.0357 | 21.1238 | 10.6883 | -3.2267 | -11.2594 | -16.6555
|  | BASINGSTOKE T1B & T2B | CT |  |  | 39.4392 | 37.521 | 35.3009 | 32.7722 | 29.9648 | 27.0583 | 23.8945 | 20.2425 | 14.7982 | 2.4928 | -17.1833 | -30.5835 | -36.72 | 61.5788 | 60.33 | 58.9414 | 57.4712 | 55.7874 | 54.0195 | 52.0791 | 49.8309 | 46.7085 | 39.6037 | 27.9252 | 18.7913 | 11.4232 | 50.3944 | 48.5836 | 46.5078 | 44.2556 | 41.7368 | 39.0918 | 36.1555 | 32.7136 | 27.7295 | 17.0612 | 0.63846 | -11.2594 | -16.6555
|  | BASINGSTOKE T1B & T2B | LW |  |  | 38.3338 | 36.0049 | 33.426 | 29.8653 | 25.9643 | 21.7577 | 17.2608 | 11.729 | 6.3676 | -5.6867 | -21.2582 | -27.8955 | -31.0031 | 61.2994 | 59.9728 | 58.5446 | 56.7069 | 54.6194 | 52.3449 | 49.893 | 46.8048 | 43.831 | 37.2623 | 28.7282 | 24.9778 | 23.1308 | 49.6744 | 47.5785 | 45.275 | 42.2327 | 38.8631 | 35.1711 | 31.1586 | 26.0357 | 21.1238 | 10.6883 | -3.2267 | -9.1744 | -11.9198
|  | BASINGSTOKE T1B & T2B | ST |  |  | 41.3634 | 40.3593 | 39.2122 | 37.9916 | 36.5564 | 35.0217 | 33.4165 | 31.5864 | 29.203 | 19.4897 | 3.3514 | -5.1929 | -10.5379 | 62.6773 | 61.9414 | 61.1502 | 60.3418 | 59.3526 | 58.291 | 57.1684 | 55.8884 | 54.1128 | 47.1461 | 35.3944 | 27.8731 | 20.8491 | 52.2739 | 51.3347 | 50.2752 | 49.1357 | 47.7868 | 46.3347 | 44.7934 | 43.0244 | 40.7508 | 31.1908 | 15.9457 | 8.6326 | 4.3399
|  | BASINGSTOKE T1B & T2B | FS |  |  | 41.5257 | 40.6533 | 39.7211 | 38.5982 | 35.9566 | 33.2732 | 30.47 | 26.0601 | 24.1137 | 17.3319 | 0.42063 | -8.4758 | -12.3105 | 62.7222 | 62.0307 | 61.3292 | 60.6048 | 58.3668 | 56.0899 | 53.7245 | 49.7764 | 48.344 | 43.3139 | 30.5386 | 20.6309 | 10.329 | 62.7222 | 62.0307 | 61.3292 | 60.6048 | 58.3668 | 56.0899 | 53.7245 | 49.7764 | 48.344 | 43.3139 | 30.5386 | 20.6309 | 10.329
BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | BASINGSTOKE T3 & T4 | MINIMUM HEADROOM | SU 65132 52712 | YES | 75.7105 | 47.2765 | 45.4032 | 42.8024 | 40.3945 | 37.8621 | 34.9934 | 31.5856 | 27.9839 | 17.8768 | 8.0317 | 1.9992 | -2.2891 | 82.0658 | 54.2462 | 53.1685 | 51.761 | 50.4388 | 49.0259 | 47.4277 | 45.4771 | 43.392 | 37.5394 | 30.0045 | 23.5452 | 16.5734 | 79.6508 | 51.4015 | 49.7791 | 47.5216 | 45.3971 | 43.1457 | 40.5973 | 37.5399 | 34.2966 | 25.1964 | 16.2808 | 11.4045 | 7.7483
|  | BASINGSTOKE T3 & T4 | CT |  |  | 76.2072 | 48.0525 | 46.3169 | 44.145 | 42.1884 | 40.1964 | 37.9039 | 35.2343 | 31.758 | 21.8301 | 9.8177 | 1.9992 | -2.2891 | 82.1354 | 54.3876 | 53.2765 | 51.9707 | 50.7575 | 49.4981 | 48.0638 | 46.3784 | 44.2638 | 38.0927 | 30.0045 | 23.5452 | 16.5734 | 80.0821 | 52.0895 | 50.5825 | 48.7069 | 46.986 | 45.2236 | 43.199 | 40.8252 | 37.7122 | 28.8088 | 18.0177 | 11.4045 | 7.7483
|  | BASINGSTOKE T3 & T4 | LW |  |  | 75.7105 | 47.2765 | 45.4032 | 42.8024 | 40.3945 | 37.8621 | 34.9934 | 31.5856 | 27.9839 | 17.8768 | 8.0317 | 3.8855 | 1.4771 | 82.0658 | 54.2462 | 53.1685 | 51.761 | 50.4388 | 49.0259 | 47.4277 | 45.4771 | 43.392 | 37.5394 | 31.9523 | 29.9031 | 28.6664 | 79.6508 | 51.4015 | 49.7791 | 47.5216 | 45.3971 | 43.1457 | 40.5973 | 37.5399 | 34.2966 | 25.1964 | 16.2808 | 12.7334 | 10.7304
|  | BASINGSTOKE T3 & T4 | ST |  |  | 77.1041 | 76.4049 | 75.5073 | 47.3504 | 46.3 | 45.216 | 43.9484 | 42.4518 | 40.8408 | 35.3316 | 25.7682 | 20.47 | 17.2158 | 82.6903 | 82.1803 | 81.556 | 53.7892 | 53.0436 | 52.2603 | 51.3554 | 50.2849 | 49.1448 | 45.0922 | 37.1588 | 31.1849 | 24.5654 | 80.9053 | 80.3138 | 79.5622 | 51.5781 | 50.6655 | 49.7195 | 48.6138 | 47.3058 | 45.9173 | 41.0345 | 32.321 | 27.6193 | 24.8643
|  | BASINGSTOKE T3 & T4 | FS |  |  | 77.1695 | 76.5103 | 75.6863 | 74.7137 | 73.8812 | 72.9973 | 71.9631 | 70.7995 | 69.4969 | 65.3992 | 57.8648 | 52.2606 | 49.7184 | 82.6962 | 82.1875 | 81.5809 | 80.8874 | 80.2497 | 79.5552 | 78.7477 | 77.8289 | 76.7654 | 73.1833 | 65.3275 | 55.9615 | 43.6169 | 82.6962 | 82.1875 | 81.5809 | 80.8874 | 80.2497 | 79.5552 | 78.7477 | 77.8289 | 76.7654 | 73.1833 | 65.3275 | 55.9615 | 43.6169
EAST CLAYDON GSP | BICESTER NORTH BSP | BICESTER NORTH BSP | MINIMUM HEADROOM | SP5972023735 | YES | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5
|  | BICESTER NORTH BSP | CT |  |  | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31
|  | BICESTER NORTH BSP | LW |  |  | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31
|  | BICESTER NORTH BSP | ST |  |  | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31
|  | BICESTER NORTH BSP | FS |  |  | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5
BOTLEY WOOD GSP | BOTLEY WOOD BSP | BOTLEY WOOD BSP | MINIMUM HEADROOM | SU 54073 09759 | YES | 60.1031 | 58.6736 | 57.2066 | 55.2828 | 53.2562 | 51.0269 | 48.5718 | 45.7049 | 43.0356 | 37.2419 | 30.5236 | 27.1734 | 24.6274 | 87.6843 | 86.8957 | 86.0531 | 84.9989 | 83.8459 | 82.5527 | 81.1053 | 79.277 | 77.5823 | 74.2158 | 70.2991 | 67.172 | 64.4637 | 74.0247 | 72.7664 | 71.4637 | 69.7513 | 67.9409 | 65.9405 | 63.7257 | 61.0825 | 58.6174 | 53.3788 | 47.321 | 44.5208 | 42.4085
|  | BOTLEY WOOD BSP | CT |  |  | 60.4912 | 59.19 | 57.8572 | 56.3648 | 54.788 | 53.118 | 51.2524 | 49.1926 | 46.442 | 40.4606 | 32.1658 | 27.1734 | 24.6274 | 87.7362 | 87.0021 | 86.1425 | 85.2119 | 84.224 | 83.1565 | 81.9501 | 80.5778 | 78.7857 | 75.14 | 70.2991 | 67.172 | 64.4637 | 74.3577 | 73.2086 | 72.021 | 70.6955 | 69.2901 | 67.7972 | 66.1192 | 64.2418 | 61.7006 | 56.2914 | 48.8823 | 44.5208 | 42.4085
|  | BOTLEY WOOD BSP | LW |  |  | 60.1031 | 58.6736 | 57.2066 | 55.2828 | 53.2562 | 51.0269 | 48.5718 | 45.7049 | 43.0356 | 37.2419 | 30.5236 | 28.1045 | 26.8833 | 87.6843 | 86.8957 | 86.0531 | 84.9989 | 83.8459 | 82.5527 | 81.1053 | 79.277 | 77.5823 | 74.2158 | 70.4705 | 69.3596 | 68.7761 | 74.0247 | 72.7664 | 71.4637 | 69.7513 | 67.9409 | 65.9405 | 63.7257 | 61.0825 | 58.6174 | 53.3788 | 47.321 | 45.2341 | 44.2078
|  | BOTLEY WOOD BSP | ST |  |  | 61.7157 | 60.9541 | 60.1916 | 59.3928 | 58.5407 | 57.6017 | 56.57 | 55.4678 | 54.4 | 50.123 | 43.5123 | 40.2985 | 38.3211 | 88.0888 | 87.6921 | 87.3376 | 86.9618 | 86.4164 | 85.817 | 85.1183 | 84.3121 | 83.5465 | 80.3118 | 75.2299 | 72.4896 | 69.9657 | 75.5355 | 74.8992 | 74.2506 | 73.5629 | 72.8241 | 72.0071 | 71.1038 | 70.1234 | 69.1677 | 65.1908 | 59.0299 | 56.1624 | 54.4724
|  | BOTLEY WOOD BSP | FS |  |  | 61.8167 | 61.1442 | 60.51 | 59.8541 | 59.1815 | 58.4265 | 57.5671 | 56.6727 | 55.767 | 52.7507 | 45.8148 | 42.4815 | 41.0662 | 88.1095 | 87.7299 | 87.401 | 87.1238 | 86.7394 | 86.2438 | 85.6793 | 85.0833 | 84.3975 | 81.9825 | 76.0038 | 71.9879 | 67.8945 | 88.1095 | 87.7299 | 87.401 | 87.1238 | 86.7394 | 86.2438 | 85.6793 | 85.0833 | 84.3975 | 81.9825 | 76.0038 | 71.9879 | 67.8945
MANNINGTON GSP | BOURNEMOUTH | BOURNEMOUTH | MINIMUM HEADROOM | SZ 06265 92437 | YES | 11.0141 | 6.7652 | 2.31 | -5.3903 | -13.5134 | -22.2719 | -31.694 | -42.6701 | -54.5369 | -88.2016 | -132.8894 | -161.2093 | -184.1459 | 57.9853 | 56.0045 | 53.37 | 49.3539 | 44.8932 | 39.7225 | 34.101 | 27.1939 | 19.6192 | -1.5667 | -37.9262 | -72.9925 | -140.6938 | 23.1491 | 19.227 | 15.0673 | 8.0493 | 0.59697 | -7.7416 | -16.8324 | -27.4305 | -38.8893 | -71.4922 | -114.1663 | -138.6437 | -157.9985
|  | BOURNEMOUTH | CT |  |  | 13.4914 | 10.482 | 6.7347 | 1.0853 | -4.8868 | -11.0163 | -17.6912 | -25.3799 | -36.5422 | -69.06 | -122.0933 | -161.2093 | -184.1459 | 57.9853 | 56.6876 | 53.9213 | 50.1226 | 45.8671 | 41.3199 | 36.327 | 30.4715 | 22.744 | -0.26843 | -37.9262 | -72.9925 | -113.4381 | 25.3028 | 22.5079 | 18.9445 | 13.7448 | 8.2098 | 2.4911 | -3.7443 | -10.9682 | -21.3909 | -52.7389 | -103.8545 | -138.6437 | -157.9985
|  | BOURNEMOUTH | LW |  |  | 11.0141 | 6.7652 | 2.31 | -5.3903 | -13.5134 | -22.2719 | -31.694 | -42.6701 | -54.5369 | -88.2016 | -132.8894 | -154.0855 | -169.0853 | 58.2186 | 56.0045 | 53.37 | 49.3539 | 44.8932 | 39.7225 | 34.101 | 27.1939 | 19.6192 | -1.5667 | -28.0263 | -38.6038 | -45.8332 | 23.1491 | 19.227 | 15.0673 | 8.0493 | 0.59697 | -7.7416 | -16.8324 | -27.4305 | -38.8893 | -71.4922 | -114.1663 | -133.1947 | -145.7432
|  | BOURNEMOUTH | ST |  |  | 16.8183 | 15.35 | 13.8122 | 11.2228 | 8.4376 | 5.419 | 2.0672 | -1.8785 | -6.5486 | -24.2064 | -66.122 | -91.6525 | -107.7409 | 58.9563 | 58.2688 | 57.5171 | 56.3333 | 54.11 | 51.3801 | 48.3312 | 44.7365 | 40.601 | 24.6425 | -13.3828 | -44.3079 | -80.666 | 28.4749 | 27.1475 | 25.7189 | 23.3523 | 20.7758 | 17.9636 | 14.8341 | 11.1286 | 6.741 | -10.0757 | -49.566 | -72.4155 | -86.227
|  | BOURNEMOUTH | FS |  |  | 17.2136 | 15.8069 | 14.3892 | 12.1597 | 8.7664 | 5.2229 | 1.3772 | -3.9074 | -7.6658 | -20.5397 | -55.4097 | -83.1712 | -96.7959 | 59.0002 | 58.3092 | 57.5722 | 56.4424 | 53.2623 | 49.6556 | 45.7176 | 40.2455 | 36.2389 | 21.6359 | -18.7961 | -69.0585 | -140.6938 | 59.0002 | 58.3092 | 57.5722 | 56.4424 | 53.2623 | 49.6556 | 45.7176 | 40.2455 | 36.2389 | 21.6359 | -18.7961 | -69.0585 | -140.6938
BRAMLEY (FLEE) | BRACKNELL MAIN | BRACKNELL MAIN | MINIMUM HEADROOM | SU 86026 69422 | YES | 30.2929 | 27.7538 | 24.8969 | 20.4053 | 15.6703 | 10.6801 | 5.0357 | -1.6905 | -8.3624 | -25.5277 | -43.9019 | -50.2034 | -55.282 | 43.7423 | 42.3828 | 41.0037 | 38.7542 | 36.2382 | 33.5385 | 30.3427 | 26.4889 | 22.6087 | 12.4375 | 1.0674 | -6.9118 | -14.6731 | 34.031 | 31.7495 | 29.1946 | 25.1785 | 20.966 | 16.4904 | 11.4302 | 5.3106 | -0.78927 | -16.2745 | -32.8526 | -38.3298 | -42.9909
|  | BRACKNELL MAIN | CT |  |  | 31.2958 | 29.0741 | 26.5513 | 22.9662 | 19.176 | 15.3677 | 10.973 | 5.9496 | -0.64654 | -17.5027 | -39.2924 | -50.2034 | -55.282 | 43.9591 | 42.6492 | 41.3272 | 39.3783 | 37.1786 | 34.8868 | 32.1564 | 29.0584 | 25.0468 | 14.5791 | 1.0674 | -6.9118 | -14.6731 | 34.9912 | 33.0163 | 30.7841 | 27.604 | 24.2242 | 20.7755 | 16.7784 | 12.2055 | 6.1823 | -8.9875 | -28.4955 | -38.3298 | -42.9909
|  | BRACKNELL MAIN | LW |  |  | 30.2929 | 27.7538 | 24.8969 | 20.4053 | 15.6703 | 10.6801 | 5.0357 | -1.6905 | -8.3624 | -25.5277 | -43.9019 | -48.943 | -51.2541 | 43.7423 | 42.3828 | 41.0037 | 38.7542 | 36.2382 | 33.5385 | 30.3427 | 26.4889 | 22.6087 | 12.4375 | 1.8519 | -0.54877 | -1.6906 | 34.031 | 31.7495 | 29.1946 | 25.1785 | 20.966 | 16.4904 | 11.4302 | 5.3106 | -0.78927 | -16.2745 | -32.8526 | -37.2627 | -39.2395
|  | BRACKNELL MAIN | ST |  |  | 33.5702 | 32.2998 | 30.8753 | 28.8559 | 26.7368 | 24.5558 | 22.0487 | 19.1811 | 16.1735 | 4.6759 | -13.287 | -21.3457 | -25.6214 | 44.8014 | 43.8569 | 42.9601 | 41.8533 | 40.7564 | 39.54 | 37.8748 | 35.9989 | 34.0745 | 26.3484 | 12.3011 | 4.4578 | -2.8053 | 37.0472 | 35.9369 | 34.7077 | 32.9985 | 31.2258 | 29.3621 | 27.1435 | 24.5764 | 21.9056 | 11.413 | -5.2494 | -12.5866 | -16.3016
|  | BRACKNELL MAIN | FS |  |  | 33.7832 | 32.658 | 31.4645 | 29.7823 | 28.0454 | 26.2247 | 24.0953 | 21.7723 | 19.2313 | 10.7397 | -6.2357 | -15.5209 | -19.1882 | 44.8702 | 43.9651 | 43.1285 | 42.1292 | 41.1549 | 40.1312 | 38.7877 | 37.1826 | 35.4625 | 29.3247 | 14.8759 | 2.7913 | -10.1288 | 44.8702 | 43.9651 | 43.1285 | 42.1292 | 41.1549 | 40.1312 | 38.7877 | 37.1826 | 35.4625 | 29.3247 | 14.8759 | 2.7913 | -10.1288
BRAMLEY (FLEE) | BRACKNELL RESERVE | BRACKNELL RESERVE | MINIMUM HEADROOM | SU 86026 69422 | YES | 52.5766 | 50.4997 | 48.156 | 44.4591 | 40.6914 | 36.4451 | 31.7929 | 26.2612 | 21.0869 | 9.1196 | -6.2043 | -15.4719 | -21.5265 | 70.3867 | 69.0441 | 67.4765 | 65.2749 | 63.0643 | 60.4914 | 57.6176 | 53.9974 | 50.6522 | 43.5179 | 34.4056 | 26.3885 | 19.5757 | 59.0615 | 57.2958 | 55.2946 | 51.999 | 48.6943 | 45.0283 | 41.0505 | 36.2693 | 31.3664 | 20.206 | 6.1362 | -1.746 | -7.3112
|  | BRACKNELL RESERVE | CT |  |  | 53.631 | 52.0064 | 50.0044 | 47.331 | 44.6159 | 41.6371 | 38.3181 | 34.6496 | 29.3528 | 17.1339 | -2.4027 | -15.4719 | -21.5265 | 70.5683 | 69.313 | 67.7363 | 65.8863 | 64.0398 | 61.9715 | 59.6352 | 56.9908 | 53.4496 | 45.7194 | 34.4056 | 26.3885 | 19.5757 | 60.1714 | 58.8345 | 57.1841 | 54.8695 | 52.5706 | 50.0842 | 47.3279 | 43.8454 | 38.8308 | 27.45 | 9.782 | -1.746 | -7.3112
|  | BRACKNELL RESERVE | LW |  |  | 52.5766 | 50.4997 | 48.156 | 44.4591 | 40.6914 | 36.4451 | 31.7929 | 26.2612 | 21.0869 | 9.1196 | -6.2043 | -11.912 | -14.7803 | 70.3867 | 69.0441 | 67.4765 | 65.2749 | 63.0643 | 60.4914 | 57.6176 | 53.9974 | 50.6522 | 43.5179 | 34.9967 | 32.4431 | 31.1492 | 59.0615 | 57.2958 | 55.2946 | 51.999 | 48.6943 | 45.0283 | 41.0505 | 36.2693 | 31.3664 | 20.206 | 6.1362 | 1.1604 | -1.2791
|  | BRACKNELL RESERVE | ST |  |  | 55.5805 | 54.7549 | 53.7525 | 52.3897 | 51.0828 | 49.5794 | 47.9382 | 46.1188 | 44.378 | 36.3388 | 22.0978 | 14.5604 | 9.6812 | 71.9686 | 71.283 | 70.429 | 69.3312 | 68.3059 | 67.1238 | 65.8232 | 64.356 | 62.9988 | 56.5618 | 45.4115 | 38.9163 | 32.5517 | 61.7402 | 61.0541 | 60.2043 | 59.0422 | 57.9809 | 56.7757 | 55.4681 | 54.0263 | 52.585 | 45.3012 | 31.7947 | 25.0357 | 20.8313
|  | BRACKNELL RESERVE | FS |  |  | 55.7272 | 54.994 | 54.1205 | 52.7927 | 51.5438 | 50.1918 | 48.6469 | 47.0718 | 45.3854 | 39.3592 | 23.8153 | 15.598 | 12.0095 | 72.0097 | 71.3604 | 70.5666 | 69.5659 | 68.6601 | 67.6638 | 66.5127 | 65.2942 | 63.9719 | 58.9747 | 45.5469 | 35.6981 | 25.4274 | 72.0097 | 71.3604 | 70.5666 | 69.5659 | 68.6601 | 67.6638 | 66.5127 | 65.2942 | 63.9719 | 58.9747 | 45.5469 | 35.6981 | 25.4274
BRAMLEY (FLEE) | BURGHFIELD MAIN | BURGHFIELD MAIN | MINIMUM HEADROOM | SU 69442 70509 | YES | 54.8218 | 52.3888 | 49.6772 | 45.8324 | 41.9852 | 37.841 | 33.4857 | 28.1373 | 22.6064 | 7.6242 | -10.8531 | -22.8827 | -31.1398 | 54.2544 | 52.7306 | 50.9902 | 48.7971 | 46.6024 | 44.142 | 41.544 | 38.1594 | 34.6874 | 25.6717 | 14.3931 | 3.6779 | -6.2663 | 41.951 | 39.8143 | 37.4012 | 33.8682 | 30.334 | 26.5281 | 22.5418 | 17.6718 | 12.55 | -1.3454 | -18.0645 | -28.4264 | -35.444
|  | BURGHFIELD MAIN | CT |  |  | 56.4353 | 54.7872 | 52.5589 | 49.8279 | 47.1375 | 44.2765 | 41.2569 | 37.682 | 32.3234 | 17.5392 | -5.8891 | -22.8827 | -31.1398 | 54.6529 | 53.4201 | 51.7172 | 49.8728 | 48.0485 | 46.0441 | 43.9222 | 41.3316 | 37.795 | 28.1833 | 14.3931 | 3.6779 | -6.2663 | 43.5772 | 42.1284 | 40.129 | 37.6447 | 35.1983 | 32.522 | 29.6837 | 26.3007 | 21.2733 | 7.5604 | -13.4575 | -28.4264 | -35.444
|  | BURGHFIELD MAIN | LW |  |  | 54.8218 | 52.3888 | 49.6772 | 45.8324 | 41.9852 | 37.841 | 33.4857 | 28.1373 | 22.6064 | 7.6242 | -10.8531 | -18.9015 | -24.1384 | 54.2544 | 52.7306 | 50.9902 | 48.7971 | 46.6024 | 44.142 | 41.544 | 38.1594 | 34.6874 | 25.6717 | 15.6629 | 11.9844 | 9.5582 | 41.951 | 39.8143 | 37.4012 | 33.8682 | 30.334 | 26.5281 | 22.5418 | 17.6718 | 12.55 | -1.3454 | -18.0645 | -25.1531 | -29.5215
|  | BURGHFIELD MAIN | ST |  |  | 57.9318 | 56.928 | 55.7502 | 54.2873 | 52.9005 | 51.3597 | 49.7724 | 47.8744 | 45.9317 | 37.4855 | 20.1439 | 9.9949 | 3.2538 | 55.6368 | 54.8643 | 53.917 | 52.8048 | 51.7274 | 50.4947 | 49.2203 | 47.6736 | 46.1548 | 39.3729 | 25.7385 | 16.5625 | 7.0821 | 44.8227 | 43.9535 | 42.9312 | 41.668 | 40.426 | 39.028 | 37.5966 | 35.8787 | 34.1017 | 26.0771 | 9.8695 | 0.92593 | -4.7679
|  | BURGHFIELD MAIN | FS |  |  | 58.0831 | 57.1455 | 56.0537 | 54.5347 | 53.1186 | 51.6143 | 50.0556 | 48.3061 | 46.3506 | 39.0499 | 21.9571 | 10.9235 | 5.1919 | 55.6672 | 54.8822 | 53.942 | 52.8618 | 51.8527 | 50.7298 | 49.558 | 48.1918 | 46.6377 | 40.5337 | 25.5331 | 11.2687 | -5.8889 | 55.6672 | 54.8822 | 53.942 | 52.8618 | 51.8527 | 50.7298 | 49.558 | 48.1918 | 46.6377 | 40.5337 | 25.5331 | 11.2687 | -5.8889
BRAMLEY (FLEE) | BURGHFIELD RESERVE | BURGHFIELD RESERVE | MINIMUM HEADROOM | SU 69442 70509 | YES | 55.5281 | 52.9353 | 50.2298 | 46.4535 | 42.6246 | 38.8556 | 34.7099 | 29.7685 | 24.9262 | 13.4913 | -2.0273 | -10.0941 | -17.2553 | 74.8721 | 73.3852 | 71.8381 | 69.8381 | 67.7858 | 65.6857 | 63.3058 | 60.2837 | 57.3995 | 51.3491 | 43.6914 | 36.2423 | 29.8366 | 61.7247 | 59.4735 | 57.1364 | 53.7668 | 50.3461 | 46.9771 | 43.3103 | 39.0366 | 34.6238 | 24.0264 | 9.972 | 3.1171 | -3.039
|  | BURGHFIELD RESERVE | CT |  |  | 57.5437 | 55.6911 | 53.6384 | 51.0338 | 48.4101 | 45.9544 | 43.2046 | 40.1046 | 35.3823 | 24.3965 | 4.886 | -10.0941 | -17.2553 | 75.1979 | 74.1472 | 72.7337 | 71.148 | 69.5263 | 67.9299 | 66.1027 | 63.9831 | 60.9863 | 54.583 | 44.2981 | 36.2423 | 29.8366 | 63.7683 | 62.2455 | 60.5758 | 58.3385 | 56.0807 | 53.9611 | 51.5219 | 48.7382 | 44.464 | 34.3675 | 16.3059 | 3.1171 | -3.039
|  | BURGHFIELD RESERVE | LW |  |  | 55.5281 | 52.9353 | 50.2298 | 46.4535 | 42.6246 | 38.8556 | 34.7099 | 29.7685 | 24.9262 | 13.4913 | -2.0273 | -9.2295 | -13.9354 | 74.8721 | 73.3852 | 71.8381 | 69.8381 | 67.7858 | 65.6857 | 63.3058 | 60.2837 | 57.3995 | 51.3491 | 43.6914 | 40.4415 | 38.2162 | 61.7247 | 59.4735 | 57.1364 | 53.7668 | 50.3461 | 46.9771 | 43.3103 | 39.0366 | 34.6238 | 24.0264 | 9.972 | 3.8458 | -0.077781
|  | BURGHFIELD RESERVE | ST |  |  | 59.1784 | 58.0871 | 56.9431 | 55.4738 | 54.0218 | 52.7023 | 51.2482 | 49.6082 | 47.8943 | 40.375 | 26.7245 | 18.3097 | 12.2299 | 75.6391 | 75.2555 | 74.9089 | 74.0645 | 73.0904 | 72.1602 | 71.1156 | 69.9088 | 68.729 | 63.2392 | 53.5121 | 47.269 | 41.1779 | 65.0949 | 64.2062 | 63.293 | 62.0894 | 60.8894 | 59.7735 | 58.5506 | 57.1806 | 55.6987 | 49.0976 | 36.5656 | 29.2445 | 23.9339
|  | BURGHFIELD RESERVE | FS |  |  | 59.2011 | 58.5115 | 57.5825 | 55.9486 | 54.3645 | 52.9095 | 51.2939 | 49.6122 | 47.6484 | 40.7064 | 23.6751 | 13.7124 | 7.6964 | 75.6476 | 75.284 | 74.9629 | 74.3375 | 73.4078 | 72.5287 | 71.5088 | 70.418 | 69.1753 | 64.5037 | 52.1369 | 43.3933 | 34.6213 | 75.6476 | 75.284 | 74.9629 | 74.3375 | 73.4078 | 72.5287 | 71.5088 | 70.418 | 69.1753 | 64.5037 | 52.1369 | 43.3933 | 34.6213
BRAMLEY (FLEE) | CAMBERLEY MAIN | CAMBERLEY MAIN | MINIMUM HEADROOM | SU 86530 59483 | YES | 24.2347 | 20.9191 | 17.4123 | 12.2215 | 6.3777 | -0.046784 | -7.093 | -15.4895 | -22.9237 | -40.0404 | -63.2788 | -77.4078 | -87.6265 | 55.5371 | 53.3426 | 51.0702 | 48.0546 | 44.5134 | 40.5318 | 36.0414 | 30.3884 | 25.5037 | 15.1367 | -2.5845 | -19.3401 | -35.909 | 34.0187 | 30.9107 | 27.6561 | 22.8981 | 17.5168 | 11.5757 | 4.9956 | -2.9551 | -9.9713 | -25.7986 | -47.1883 | -59.3626 | -68.1767
|  | CAMBERLEY MAIN | CT |  |  | 25.4867 | 22.6059 | 19.5262 | 15.7191 | 11.3439 | 6.6626 | 1.5506 | -4.1586 | -12.0062 | -29.2151 | -57.6112 | -77.4078 | -87.6265 | 55.6655 | 53.4657 | 51.167 | 48.6273 | 45.6215 | 42.3417 | 38.6769 | 34.4981 | 29.1367 | 18.1163 | 0.34906 | -13.3408 | -24.9321 | 35.0855 | 32.349 | 29.4577 | 25.942 | 21.8869 | 17.5355 | 12.7334 | 7.328 | -0.086596 | -15.9656 | -41.7427 | -59.3626 | -68.1767
|  | CAMBERLEY MAIN | LW |  |  | 24.2347 | 20.9191 | 17.4123 | 12.2215 | 6.3777 | -0.046784 | -7.093 | -15.4895 | -22.9237 | -40.0404 | -63.2788 | -74.1496 | -80.2174 | 55.5371 | 53.3426 | 51.0702 | 48.0546 | 44.5134 | 40.5318 | 36.0414 | 30.3884 | 25.5037 | 15.1367 | 1.1209 | -5.3113 | -8.9231 | 34.0187 | 30.9107 | 27.6561 | 22.8981 | 17.5168 | 11.5757 | 4.9956 | -2.9551 | -9.9713 | -25.7986 | -47.1883 | -56.9557 | -62.3114
|  | CAMBERLEY MAIN | ST |  |  | 28.4967 | 26.9913 | 25.4058 | 23.5136 | 21.1765 | 18.6265 | 15.9579 | 12.9527 | 8.9817 | -7.6082 | -32.3168 | -45.8772 | -53.9387 | 57.8064 | 56.5598 | 55.2855 | 53.8291 | 51.978 | 49.9542 | 47.7968 | 45.3332 | 41.9703 | 28.0118 | 7.5171 | -4.9426 | -15.7689 | 38.0013 | 36.5902 | 35.1356 | 33.3991 | 31.2385 | 28.8816 | 26.3853 | 23.5447 | 19.7359 | 3.6869 | -19.8286 | -32.235 | -39.3214
|  | CAMBERLEY MAIN | FS |  |  | 28.7467 | 27.457 | 26.2055 | 24.6101 | 19.7729 | 14.7877 | 9.6267 | 1.1442 | -1.8362 | -12.6012 | -38.3324 | -52.1182 | -58.1952 | 57.8858 | 56.7451 | 55.6638 | 54.4594 | 50.0235 | 45.455 | 40.7022 | 32.6192 | 30.0551 | 20.638 | -2.5845 | -19.3401 | -35.909 | 57.8858 | 56.7451 | 55.6638 | 54.4594 | 50.0235 | 45.455 | 40.7022 | 32.6192 | 30.0551 | 20.638 | -2.5845 | -19.3401 | -35.909
BRAMLEY (FLEE) | CAMBERLEY RESERVE | CAMBERLEY RESERVE | MINIMUM HEADROOM | SU 86530 59483 | YES | 14.4654 | 11.738 | 8.9433 | 5.1814 | 0.77617 | -3.9871 | -9.0406 | -14.9937 | -21.3953 | -36.2538 | -54.0757 | -66.2959 | -74.2931 | -12.3968 | -14.342 | -16.4035 | -18.695 | -21.4213 | -24.485 | -27.8526 | -32.2887 | -36.709 | -46.0015 | -58.341 | -68.3684 | -77.9937 | -29.7982 | -32.5395 | -35.3618 | -38.9076 | -43.0554 | -47.6456 | -52.5918 | -58.8453 | -65.0716 | -78.3681 | -93.857 | -102.3674 | -108.4491
|  | CAMBERLEY RESERVE | CT |  |  | 15.3202 | 12.9776 | 10.4602 | 7.6591 | 4.2559 | 0.69047 | -3.1152 | -7.4901 | -13.8744 | -29.0217 | -51.4237 | -66.2959 | -74.2931 | -12.3968 | -14.2763 | -16.4035 | -18.4698 | -20.9161 | -23.5556 | -26.4318 | -29.8975 | -34.3994 | -44.4418 | -58.341 | -68.3684 | -77.9937 | -29.2827 | -31.7017 | -34.3969 | -37.2032 | -40.5664 | -44.1522 | -48.0413 | -52.6613 | -58.876 | -72.4596 | -90.9645 | -102.3674 | -108.4491
|  | CAMBERLEY RESERVE | LW |  |  | 14.4654 | 11.738 | 8.9433 | 5.1814 | 0.77617 | -3.9871 | -9.0406 | -14.9937 | -21.3953 | -36.2538 | -54.0757 | -61.8081 | -66.4689 | -12.3905 | -14.342 | -16.3723 | -18.695 | -21.4213 | -24.485 | -27.8526 | -32.2887 | -36.709 | -46.0015 | -56.4275 | -60.0644 | -62.3296 | -29.7982 | -32.5395 | -35.3618 | -38.9076 | -43.0554 | -47.6456 | -52.5918 | -58.8453 | -65.0716 | -78.3681 | -93.857 | -99.9564 | -103.6206
|  | CAMBERLEY RESERVE | ST |  |  | 17.2975 | 16.0057 | 14.7147 | 13.4047 | 11.7294 | 9.9031 | 7.9562 | 5.6973 | 3.2711 | -6.0369 | -24.5975 | -34.2138 | -39.9058 | -10.7859 | -11.9 | -13.0659 | -14.2885 | -15.7836 | -17.428 | -19.2059 | -21.282 | -23.3548 | -31.4739 | -46.7201 | -56.2111 | -65.1741 | -27.0414 | -28.3479 | -29.6802 | -31.1203 | -32.9197 | -34.896 | -37.0287 | -39.5129 | -42.0435 | -51.7005 | -69.3018 | -77.9923 | -82.8413
|  | CAMBERLEY RESERVE | FS |  |  | 17.4753 | 16.3184 | 15.1848 | 14.1636 | 12.8659 | 11.4642 | 9.9609 | 8.284 | 6.4551 | 0.87517 | -16.4641 | -26.9073 | -31.3063 | -10.7538 | -11.8048 | -12.8865 | -13.8535 | -15.0349 | -16.3586 | -17.8327 | -19.4967 | -21.3162 | -27.405 | -43.7162 | -57.959 | -73.5819 | -10.7538 | -11.8048 | -12.8865 | -13.8535 | -15.0349 | -16.3586 | -17.8327 | -19.4967 | -21.3162 | -27.405 | -43.7162 | -57.959 | -73.5819
IVER 132KV | CHALVEY BSP | CHALVEY BSP | MINIMUM HEADROOM | SU 96669 79364 | YES | 56.8859 | 53.7561 | 50.4132 | 46.0061 | 41.0949 | 36.1321 | 30.7103 | 24.5534 | 18.6158 | 3.4741 | -15.1767 | -26.6679 | -34.9115 | 67.5805 | 65.8499 | 63.9171 | 61.6638 | 59.1975 | 56.6416 | 53.5956 | 49.858 | 46.1447 | 35.2771 | 17.3093 | -6.141 | -48.5627 | 60.328 | 57.5212 | 54.497 | 50.4389 | 46.1034 | 41.6758 | 36.8196 | 31.2438 | 25.7924 | 11.7398 | -5.3383 | -14.8725 | -48.5627
|  | CHALVEY BSP | CT |  |  | 57.6887 | 55.0306 | 51.8777 | 48.1853 | 44.2754 | 40.4267 | 36.0923 | 31.3392 | 25.6145 | 10.7159 | -11.672 | -26.6679 | -34.9115 | 67.5991 | 65.8825 | 63.9171 | 61.6638 | 59.2333 | 56.7839 | 53.7379 | 50.3308 | 46.3433 | 35.2771 | 17.3093 | 0.02365 | -21.9788 | 61.1186 | 58.7716 | 55.9362 | 52.5771 | 48.9923 | 45.4903 | 41.6241 | 37.3504 | 32.1234 | 18.3473 | -1.9236 | -14.8725 | -21.7087
|  | CHALVEY BSP | LW |  |  | 56.8859 | 53.7561 | 50.4132 | 46.0061 | 41.0949 | 36.1321 | 30.7103 | 24.5534 | 18.6158 | 3.4741 | -15.1767 | -23.7816 | -28.5469 | 67.5805 | 65.8499 | 64.0236 | 61.7045 | 59.1975 | 56.6416 | 53.5956 | 49.858 | 46.1447 | 36.585 | 25.2987 | 20.5935 | 17.8991 | 60.328 | 57.5212 | 54.497 | 50.4389 | 46.1034 | 41.6758 | 36.8196 | 31.2438 | 25.7924 | 11.7398 | -5.3383 | -12.8632 | -16.9307
|  | CHALVEY BSP | ST |  |  | 59.668 | 58.13 | 56.5181 | 54.4647 | 52.2864 | 50.1516 | 47.7949 | 45.1632 | 42.3282 | 33.3355 | 14.744 | 4.1988 | -2.1977 | 68.6591 | 67.5287 | 66.3557 | 64.9348 | 63.3819 | 61.801 | 60.028 | 58.0266 | 55.6627 | 46.9405 | 27.8708 | 11.2902 | -9.7622 | 63.0563 | 61.7463 | 60.3569 | 58.5445 | 56.6054 | 54.6833 | 52.555 | 50.1618 | 47.5475 | 39.0017 | 21.581 | 12.1059 | 6.6082
|  | CHALVEY BSP | FS |  |  | 59.8274 | 58.3822 | 56.9013 | 55.2964 | 52.5171 | 49.7244 | 46.7436 | 42.4754 | 40.3347 | 34.205 | 19.1931 | 8.0429 | 3.0537 | 68.6826 | 67.5506 | 66.3885 | 65.0896 | 62.5751 | 59.9907 | 57.2121 | 53.0938 | 50.8576 | 43.0432 | 21.8404 | -6.141 | -48.5627 | 68.6826 | 67.5506 | 66.3885 | 65.0896 | 62.5751 | 59.9907 | 57.2121 | 53.0938 | 50.8576 | 43.0432 | 21.8404 | -6.141 | -48.5627
LOVEDEAN GSP | CHICHESTER & HUNSTON | CHICHESTER & HUNSTON | MINIMUM HEADROOM | SU 92282 07416 | YES | 36.6154 | 28.8325 | 20.2746 | 8.2627 | -4.4818 | -17.6675 | -31.8745 | -48.3364 | -65.0049 | -108.1261 | -152.9793 | -180.2902 | -199.7034 | 88.3091 | 83.5794 | 78.3917 | 71.8623 | 64.7669 | 57.1967 | 48.9703 | 38.9831 | 28.7549 | 3.8723 | -23.7253 | -49.1777 | -74.3657 | 53.3482 | 46.3247 | 38.5792 | 27.9347 | 16.5525 | 4.6256 | -8.235 | -23.3482 | -38.7187 | -77.8573 | -118.3393 | -140.1997 | -156.2131
|  | CHICHESTER & HUNSTON | CT |  |  | 40.84 | 35.0672 | 27.5241 | 18.4524 | 8.7677 | -1.1524 | -11.8988 | -23.7189 | -40.1072 | -84.0679 | -141.134 | -180.2902 | -199.7034 | 89.3078 | 85.4581 | 80.3388 | 74.7432 | 68.6744 | 62.3367 | 55.416 | 47.5864 | 37.1498 | 9.9857 | -23.7253 | -49.1777 | -72.6907 | 56.7925 | 51.7247 | 44.9622 | 36.9031 | 28.2504 | 19.3098 | 9.5908 | -1.2211 | -16.3132 | -56.2876 | -107.3616 | -140.1997 | -156.2131
|  | CHICHESTER & HUNSTON | LW |  |  | 36.6154 | 28.8325 | 20.2746 | 8.2627 | -4.4818 | -17.6675 | -31.8745 | -48.3364 | -65.0049 | -108.1261 | -152.9793 | -171.4207 | -181.8448 | 88.3091 | 83.5794 | 78.3917 | 71.8623 | 64.7669 | 57.1967 | 48.9703 | 38.9831 | 28.7549 | 3.8723 | -20.6262 | -29.6509 | -34.8009 | 53.3482 | 46.3247 | 38.5792 | 27.9347 | 16.5525 | 4.6256 | -8.235 | -23.3482 | -38.7187 | -77.8573 | -118.3393 | -134.007 | -142.7205
|  | CHICHESTER & HUNSTON | ST |  |  | 45.8644 | 42.6298 | 39.0312 | 34.0839 | 28.7197 | 23.2692 | 17.3926 | 10.9574 | 3.7838 | -23.8702 | -71.4019 | -94.9967 | -109.6412 | 92.6918 | 90.3536 | 87.7763 | 84.3619 | 80.588 | 76.6612 | 72.3957 | 67.6131 | 62.2481 | 41.0376 | 3.2894 | -18.8977 | -40.9858 | 61.7132 | 58.9608 | 55.9049 | 51.6371 | 46.959 | 42.1405 | 36.9207 | 31.1156 | 24.5939 | -0.99596 | -45.6436 | -66.9015 | -79.6446
|  | CHICHESTER & HUNSTON | FS |  |  | 46.4501 | 43.4584 | 40.1789 | 36.1736 | 29.8499 | 23.3553 | 16.4607 | 7.0985 | 1.2056 | -19.3407 | -63.3962 | -89.3839 | -100.7417 | 92.7845 | 90.4841 | 88.0213 | 85.2611 | 80.155 | 74.8149 | 69.1052 | 60.8621 | 56.2186 | 39.3672 | -0.26991 | -34.8781 | -74.3657 | 92.7845 | 90.4841 | 88.0213 | 85.2611 | 80.155 | 74.8149 | 69.1052 | 60.8621 | 56.2186 | 39.3672 | -0.26991 | -34.8781 | -74.3657
CHICKERELL GSP | CHICKERELL BSP | CHICKERELL BSP | MINIMUM HEADROOM | SY 65479 80511 | YES | 20.0683 | 15.4324 | 10.491 | 3.3985 | -4.2974 | -12.3343 | -20.7482 | -31.2683 | -42.23 | -71.9362 | -108.1825 | -121.7379 | -132.7168 | 46.0264 | 43.492 | 40.6293 | 36.908 | 32.638 | 28.0852 | 23.3067 | 17.0142 | 10.2988 | -7.081 | -28.275 | -51.1331 | -80.5813 | 27.3395 | 23.5832 | 19.4582 | 13.3389 | 6.6491 | -0.27233 | -7.4649 | -16.2345 | -25.5394 | -52.6924 | -85.2202 | -97.7024 | -107.8689
|  | CHICKERELL BSP | CT |  |  | 23.4895 | 20.5272 | 16.5884 | 11.5798 | 6.0564 | 0.31603 | -5.7552 | -13.1689 | -23.5195 | -52.6989 | -97.126 | -121.7379 | -132.7168 | 47.0931 | 45.2176 | 42.5294 | 39.4966 | 35.9707 | 32.2598 | 28.2026 | 23.1628 | 16.5428 | -1.8311 | -28.275 | -46.3522 | -63.3094 | 30.7751 | 28.4923 | 25.4427 | 21.3557 | 16.7794 | 12.0267 | 7.0427 | 0.79765 | -8.7563 | -35.4609 | -75.0567 | -97.7024 | -107.8689
|  | CHICKERELL BSP | LW |  |  | 20.0683 | 15.4324 | 10.491 | 3.3985 | -4.2974 | -12.3343 | -20.7482 | -31.2683 | -42.23 | -71.9362 | -108.1825 | -120.5253 | -127.4361 | 46.0264 | 43.492 | 40.6293 | 36.908 | 32.638 | 28.0852 | 23.3067 | 17.0142 | 10.2988 | -7.081 | -27.2472 | -34.1423 | -38.0004 | 27.3395 | 23.5832 | 19.4582 | 13.3389 | 6.6491 | -0.27233 | -7.4649 | -16.2345 | -25.5394 | -52.6924 | -85.2202 | -96.54 | -102.8592
|  | CHICKERELL BSP | ST |  |  | 26.0484 | 24.381 | 22.5233 | 19.8383 | 16.7286 | 13.5173 | 10.1195 | 5.924 | 0.50178 | -19.3106 | -56.5331 | -74.1709 | -84.5292 | 48.6712 | 47.5668 | 46.1946 | 44.3934 | 42.1559 | 39.8006 | 37.3044 | 34.2277 | 30.0451 | 14.5154 | -14.7075 | -31.5423 | -47.6212 | 32.816 | 31.5952 | 30.105 | 28.0445 | 25.5583 | 22.9837 | 20.2881 | 16.9846 | 12.3258 | -4.916 | -39.5252 | -55.5843 | -64.6943
|  | CHICKERELL BSP | FS |  |  | 26.4757 | 24.9481 | 23.2763 | 20.7023 | 14.8595 | 8.9808 | 2.9093 | -6.8445 | -11.5701 | -27.4476 | -62.6667 | -83.1266 | -92.2661 | 48.7778 | 47.6742 | 46.3287 | 44.6581 | 39.6886 | 34.6405 | 29.4278 | 20.6539 | 17.0444 | 4.5596 | -25.2122 | -51.1331 | -80.5813 | 48.7778 | 47.6742 | 46.3287 | 44.6581 | 39.6886 | 34.6405 | 29.4278 | 20.6539 | 17.0444 | 4.5596 | -25.2122 | -51.1331 | -80.5813
MELKSHAM GSP | CHIPPENHAM | CHIPPENHAM | MINIMUM HEADROOM | ST 92629 74275 | YES | 22.8715 | 18.5099 | 13.9082 | 8.0917 | 2.289 | -3.8872 | -10.5812 | -18.5843 | -26.5195 | -45.4266 | -67.1748 | -73.9519 | -81.6758 | 42.3886 | 40.0386 | 37.4938 | 34.3976 | 31.336 | 27.9583 | 24.0836 | 19.1315 | 14.2614 | 3.6806 | -7.3234 | -17.053 | -26.3512 | 25.7975 | 22.0051 | 18.0015 | 12.7304 | 7.4936 | 1.9377 | -4.1004 | -11.3956 | -18.6385 | -36.196 | -56.0989 | -62.0863 | -68.6448
|  | CHIPPENHAM | CT |  |  | 26.2424 | 23.1473 | 19.621 | 15.7939 | 12.0322 | 8.0379 | 3.5725 | -1.4441 | -9.0586 | -27.227 | -54.7926 | -73.657 | -81.6758 | 43.5574 | 41.6066 | 39.2535 | 36.8744 | 34.4616 | 31.8117 | 28.7974 | 25.3159 | 20.3608 | 9.1765 | -6.1711 | -17.053 | -26.3512 | 29.1828 | 26.6375 | 23.7346 | 20.3357 | 16.9019 | 13.269 | 9.2234 | 4.606 | -2.5748 | -19.4487 | -44.8335 | -61.6036 | -68.6448
|  | CHIPPENHAM | LW |  |  | 22.8715 | 18.5099 | 13.9082 | 8.0917 | 2.289 | -3.8872 | -10.5812 | -18.5843 | -26.5195 | -45.4266 | -67.1748 | -73.9519 | -77.023 | 42.3886 | 40.0386 | 37.4938 | 34.3976 | 31.336 | 27.9583 | 24.0836 | 19.1315 | 14.2614 | 3.6806 | -7.3234 | -10.0842 | -11.3171 | 25.7975 | 22.0051 | 18.0015 | 12.7304 | 7.4936 | 1.9377 | -4.1004 | -11.3956 | -18.6385 | -36.196 | -56.0989 | -62.0863 | -64.7774
|  | CHIPPENHAM | ST |  |  | 29.182 | 27.4187 | 25.5098 | 23.449 | 21.4855 | 19.3639 | 17.035 | 14.4177 | 11.6697 | -0.32799 | -22.017 | -32.7261 | -39.2164 | 45.2208 | 44.0494 | 42.7506 | 41.3853 | 40.1169 | 38.665 | 37.0308 | 35.1605 | 33.2491 | 24.2254 | 7.8313 | -1.294 | -10.1422 | 31.6256 | 30.2095 | 28.6597 | 26.8678 | 25.1661 | 23.3474 | 21.3696 | 19.112 | 16.601 | 5.506 | -15.0487 | -24.7585 | -30.4666
|  | CHIPPENHAM | FS |  |  | 29.6737 | 28.1818 | 26.6154 | 24.5223 | 22.5536 | 20.5516 | 18.311 | 15.9346 | 13.0296 | 2.7507 | -22.5032 | -36.4897 | -43.0413 | 45.3951 | 44.3272 | 43.1675 | 41.8381 | 40.6171 | 39.3523 | 37.9114 | 36.2892 | 34.3488 | 27.1104 | 7.3679 | -7.2255 | -22.268 | 45.3951 | 44.3272 | 43.1675 | 41.8381 | 40.6171 | 39.3523 | 37.9114 | 36.2892 | 34.3488 | 27.1104 | 7.3679 | -7.2255 | -22.268
MANNINGTON GSP | CHRISTCHURCH BSP | CHRISTCHURCH BSP | MINIMUM HEADROOM | SZ 15716 93165 | YES | 46.617 | 44.0989 | 41.3057 | 36.7881 | 32.0177 | 26.9072 | 21.4504 | 15.3015 | 8.6967 | -9.5322 | -33.4801 | -54.1848 | -67.4165 | 68.3873 | 66.857 | 65.1385 | 62.7118 | 60.0508 | 57.1021 | 53.7577 | 49.712 | 45.2866 | 33.9827 | 15.0262 | -2.8768 | -33.9733 | 54.7954 | 52.39 | 49.7072 | 45.5683 | 41.1412 | 36.3235 | 31.1562 | 25.149 | 18.6417 | 1.4725 | -20.2934 | -36.859 | -47.6867
|  | CHRISTCHURCH BSP | CT |  |  | 48.0556 | 46.3628 | 43.9829 | 40.8693 | 37.5694 | 34.0725 | 30.2887 | 26.1811 | 19.422 | 0.25177 | -30.2959 | -54.1848 | -67.4165 | 68.585 | 67.3131 | 65.5012 | 63.413 | 61.1216 | 58.5778 | 55.7157 | 52.5047 | 47.9107 | 34.8618 | 15.0262 | -2.8768 | -21.9429 | 55.9352 | 54.2998 | 51.9099 | 48.9436 | 45.7592 | 42.353 | 38.6599 | 34.6186 | 28.2594 | 10.3387 | -17.048 | -36.859 | -47.6867
|  | CHRISTCHURCH BSP | LW |  |  | 46.617 | 44.0989 | 41.3057 | 36.7881 | 32.0177 | 26.9072 | 21.4504 | 15.3015 | 8.6967 | -9.5322 | -33.4801 | -46.2048 | -54.3233 | 68.3873 | 66.857 | 65.1385 | 62.7118 | 60.0508 | 57.1021 | 53.7577 | 49.712 | 45.2866 | 33.9827 | 20.453 | 14.0638 | 9.9567 | 54.7954 | 52.39 | 49.7072 | 45.5683 | 41.1412 | 36.3235 | 31.1562 | 25.149 | 18.6417 | 1.4725 | -20.2934 | -31.145 | -37.8433
|  | CHRISTCHURCH BSP | ST |  |  | 49.8266 | 49.0148 | 48.0753 | 46.7468 | 45.2772 | 43.6678 | 41.9123 | 40.0347 | 37.5794 | 27.4446 | 3.3615 | -10.5736 | -20.1044 | 69.7322 | 69.0177 | 68.1895 | 67.0591 | 65.7639 | 64.3213 | 62.7421 | 60.9906 | 58.7673 | 49.4878 | 28.4269 | 12.9516 | -4.7217 | 57.7198 | 56.9629 | 56.0737 | 54.7703 | 53.3022 | 51.677 | 49.9047 | 47.9539 | 45.4905 | 35.5051 | 12.8063 | 0.50058 | -7.5767
|  | CHRISTCHURCH BSP | FS |  |  | 49.9917 | 49.2096 | 48.3391 | 47.279 | 44.9657 | 42.5799 | 40.0088 | 36.1793 | 34.3506 | 27.6492 | 7.5016 | -6.6794 | -13.3984 | 69.7237 | 68.9532 | 68.0921 | 67.103 | 64.7965 | 62.3784 | 59.7808 | 55.8187 | 53.8046 | 46.1565 | 23.8947 | -1.0513 | -33.9733 | 69.7237 | 68.9532 | 68.0921 | 67.103 | 64.7965 | 62.3784 | 59.7808 | 55.8187 | 53.8046 | 46.1565 | 23.8947 | -1.0513 | -33.9733
IVER 132KV | CIPPENHAM | CIPPENHAM | MINIMUM HEADROOM | SU 96266 79634 | YES | 26.6903 | 25.7865 | 24.7828 | 23.1018 | 21.2416 | 19.2029 | 16.9816 | 14.4239 | 11.6535 | 4.2481 | -4.3407 | -8.575 | -11.5224 | 38.2727 | 37.8104 | 37.2869 | 36.4805 | 35.5776 | 34.5651 | 33.4521 | 31.8282 | 29.9818 | 25.2598 | 18.4577 | 12.7624 | 3.9455 | 31.5236 | 30.6524 | 29.6763 | 28.1261 | 26.4084 | 24.4994 | 22.4008 | 19.914 | 17.2043 | 10.094 | 2.0539 | -1.1199 | -3.5327
|  | CIPPENHAM | CT |  |  | 27.357 | 26.7023 | 25.9124 | 24.7804 | 23.4983 | 22.1616 | 20.6888 | 19.0015 | 16.327 | 9.0672 | -1.8481 | -8.575 | -11.5224 | 38.3863 | 37.943 | 37.4116 | 36.7376 | 35.975 | 35.1533 | 34.1979 | 32.8708 | 30.9762 | 25.8577 | 18.4577 | 12.7624 | 6.5311 | 32.0443 | 31.3765 | 30.5621 | 29.4733 | 28.2482 | 26.9502 | 25.5127 | 23.8448 | 21.2473 | 14.3019 | 4.5031 | -1.1199 | -3.5327
|  | CIPPENHAM | LW |  |  | 26.6903 | 25.7865 | 24.7828 | 23.1018 | 21.2416 | 19.2029 | 16.9816 | 14.4239 | 11.6535 | 4.2481 | -4.3407 | -7.1327 | -8.1927 | 38.2727 | 37.8104 | 37.2869 | 36.4805 | 35.5776 | 34.5651 | 33.4521 | 31.8282 | 29.9818 | 25.2598 | 20.1792 | 18.9659 | 18.5034 | 31.5236 | 30.6524 | 29.6763 | 28.1261 | 26.4084 | 24.4994 | 22.4008 | 19.914 | 17.2043 | 10.094 | 2.0539 | -0.30734 | -1.1816
|  | CIPPENHAM | ST |  |  | 28.2156 | 27.9404 | 27.6057 | 27.163 | 26.6255 | 26.009 | 25.3109 | 24.4699 | 23.5271 | 19.7865 | 11.5285 | 7.2417 | 4.7454 | 38.8544 | 38.6201 | 38.3413 | 37.9994 | 37.5947 | 37.1273 | 36.5965 | 35.9595 | 35.2701 | 32.0253 | 24.1966 | 18.837 | 12.7699 | 32.9151 | 32.6342 | 32.2898 | 31.8421 | 31.3085 | 30.6936 | 29.9935 | 29.1423 | 28.2148 | 24.3685 | 16.0202 | 12.1448 | 10.1012
|  | CIPPENHAM | FS |  |  | 28.31 | 28.0683 | 27.7869 | 27.4074 | 26.9482 | 26.4425 | 25.8638 | 25.1927 | 24.3878 | 21.6486 | 14.4556 | 9.3155 | 7.4645 | 38.8724 | 38.6334 | 38.3589 | 38.0353 | 37.6503 | 37.2154 | 36.7188 | 36.1364 | 35.4442 | 32.8203 | 24.389 | 15.3175 | 3.9455 | 38.8724 | 38.6334 | 38.3589 | 38.0353 | 37.6503 | 37.2154 | 36.7188 | 36.1364 | 35.4442 | 32.8203 | 24.389 | 15.3175 | 3.9455
MINETY GSP | CIRENCESTER BSP | CIRENCESTER BSP | MINIMUM HEADROOM | SP 02701 00368 | NO | -171.4565 | -174.63 | -177.9936 | -182.8288 | -187.8765 | -193.1167 | -198.7297 | -205.1265 | -211.4671 | -227.8706 | -246.0222 | -251.9392 | -255.9069 | -142.5911 | -144.2254 | -145.9667 | -148.3346 | -150.8704 | -153.602 | -156.6244 | -160.3503 | -164.0392 | -172.1982 | -180.7823 | -186.0401 | -192.1052 | -163.7875 | -166.6332 | -169.6444 | -173.9538 | -178.4534 | -183.2211 | -188.3895 | -194.4454 | -200.3751 | -214.9971 | -230.9853 | -236.0181 | -239.3465
|  | CIRENCESTER BSP | CT |  |  | -167.6132 | -169.4623 | -171.5733 | -174.625 | -177.8603 | -181.215 | -184.8971 | -189.0816 | -195.0975 | -209.9926 | -232.5368 | -246.7022 | -251.9576 | -141.4473 | -142.5759 | -144.0643 | -145.8573 | -147.7707 | -149.8177 | -152.1469 | -154.9088 | -158.6548 | -166.9385 | -178.2722 | -186.0401 | -192.1052 | -160.4395 | -162.2111 | -164.2528 | -167.0628 | -170.0466 | -173.1732 | -176.6412 | -180.5842 | -186.2605 | -199.5874 | -219.3861 | -231.3677 | -235.7857
|  | CIRENCESTER BSP | LW |  |  | -171.4565 | -174.63 | -177.9936 | -182.8288 | -187.8765 | -193.1167 | -198.7297 | -205.1265 | -211.4671 | -227.8706 | -246.0222 | -251.9392 | -255.9069 | -142.5911 | -144.2254 | -145.9667 | -148.3346 | -150.8704 | -153.602 | -156.6244 | -160.3503 | -164.0392 | -172.1982 | -180.7823 | -183.3835 | -185.1557 | -163.7875 | -166.6332 | -169.6444 | -173.9538 | -178.4534 | -183.2211 | -188.3895 | -194.4454 | -200.3751 | -214.9971 | -230.9853 | -236.0181 | -239.3465
|  | CIRENCESTER BSP | ST |  |  | 0.48225 | -113.6846 | -168.5336 | -170.2843 | -172.141 | -174.0639 | -176.1183 | -178.3618 | -180.8012 | -190.5063 | -206.6157 | -216.0329 | -222.5028 | 25.5838 | -87.79 | -141.9297 | -142.9855 | -144.1122 | -145.3569 | -146.7339 | -148.2885 | -149.8482 | -156.6727 | -167.9022 | -174.4848 | -180.7872 | 7.602 | -106.4281 | -161.1266 | -162.6824 | -164.3858 | -166.1673 | -168.0871 | -170.2107 | -172.4692 | -181.8143 | -196.8991 | -204.9054 | -210.3115
|  | CIRENCESTER BSP | FS |  |  | 0.98136 | 0.042152 | -0.93444 | -3.2115 | -5.5522 | -7.9136 | -10.4259 | -13.0176 | -16.1683 | -26.2972 | -47.7558 | -60.5437 | -68.2675 | 25.587 | 25.2195 | 24.8656 | 23.8418 | 22.6146 | 21.3448 | 19.9484 | 18.4319 | 16.6629 | 10.4769 | -4.1588 | -14.0783 | -23.8069 | 25.587 | 25.2195 | 24.8656 | 23.8418 | 22.6146 | 21.3448 | 19.9484 | 18.4319 | 16.6629 | 10.4769 | -4.1588 | -14.0783 | -23.8069
FAWLEY GSP | COWES & WOOTTON COMMON BSP | COWES & WOOTTON COMMON BSP | MINIMUM HEADROOM | SZ 50519 94250 | YES | -17.9598 | -23.7259 | -50.3382 | -59.2472 | -68.7274 | -78.6958 | -89.1413 | -101.17 | -113.8828 | -149.9525 | -189.0971 | -203.5473 | -211.4708 | 28.8136 | 25.6031 | 1.7022 | -2.853 | -7.8891 | -13.3505 | -19.1407 | -26.0634 | -33.6757 | -54.5314 | -74.8758 | -81.9714 | -106.8614 | -2.1806 | -7.3754 | -33.3885 | -41.4025 | -49.9836 | -59.0633 | -68.6088 | -79.6894 | -91.6005 | -124.8531 | -160.1188 | -173.1043 | -180.1885
|  | COWES & WOOTTON COMMON BSP | CT |  |  | -12.8675 | -16.2415 | -21.1101 | -27.1074 | -33.5806 | -40.5126 | -47.8556 | -56.0346 | -68.0668 | -103.4094 | -154.3572 | -189.7281 | -204.7174 | 30.08 | 28.2018 | 25.0201 | 21.4412 | 17.4546 | 13.1511 | 8.552 | 3.1664 | -4.3395 | -26.2888 | -54.7996 | -76.6199 | -95.4426 | 2.2729 | -0.70693 | -5.2038 | -10.68 | -16.6307 | -23.027 | -29.8268 | -37.4569 | -48.6319 | -81.3121 | -126.6899 | -158.0609 | -171.3333
|  | COWES & WOOTTON COMMON BSP | LW |  |  | -17.9598 | -23.7259 | -50.3382 | -59.2472 | -68.7274 | -78.6958 | -89.1413 | -101.17 | -113.8828 | -149.9525 | -189.0971 | -203.5473 | -211.4708 | 28.8136 | 25.6031 | 1.7022 | -2.853 | -7.8891 | -13.3505 | -19.1407 | -26.0634 | -33.6757 | -54.5314 | -74.8758 | -81.9714 | -85.8067 | -2.1806 | -7.3754 | -33.3885 | -41.4025 | -49.9836 | -59.0633 | -68.6088 | -79.6894 | -91.6005 | -124.8531 | -160.1188 | -173.1043 | -180.1885
|  | COWES & WOOTTON COMMON BSP | ST |  |  | -10.3325 | -12.276 | -14.374 | -17.4745 | -21.0423 | -24.8175 | -28.8311 | -33.2809 | -38.8701 | -60.0307 | -102.0894 | -123.3027 | -135.6517 | 30.9455 | 30.2209 | 29.2871 | 27.2259 | 24.8044 | 22.1964 | 19.3904 | 16.2131 | 12.0369 | -4.0231 | -36.9096 | -55.7872 | -73.1993 | 4.6824 | 3.0126 | 1.1995 | -1.5698 | -4.7962 | -8.2672 | -11.9783 | -16.1268 | -21.3751 | -41.4246 | -81.4494 | -100.8888 | -111.8511
|  | COWES & WOOTTON COMMON BSP | FS |  |  | -9.8039 | -11.5962 | -13.5469 | -16.7136 | -22.8568 | -29.1112 | -35.6157 | -45.2397 | -50.3219 | -67.7963 | -107.0066 | -132.0697 | -142.6041 | 30.9486 | 30.206 | 29.3462 | 27.4123 | 22.4848 | 17.4264 | 12.1478 | 3.7303 | 0.053208 | -13.0787 | -45.2359 | -74.8248 | -106.8614 | 30.9486 | 30.206 | 29.3462 | 27.4123 | 22.4848 | 17.4264 | 12.1478 | 3.7303 | 0.053208 | -13.0787 | -45.2359 | -74.8248 | -106.8614
COWLEY GSP | COWLEY LOCAL (2 X 45) | COWLEY LOCAL (2 X 45) | MINIMUM HEADROOM | SP 56113 03074 | NO | 87.2649 | 86.3041 | 85.0394 | 83.1857 | 80.8553 | 78.3455 | 75.5727 | 72.3634 | 69.1085 | 59.8066 | 49.1835 | 45.8751 | 44.1339 | 93.4721 | 92.9129 | 92.2016 | 91.2568 | 90.0814 | 88.7952 | 87.3679 | 85.644 | 83.9017 | 79.423 | 74.4006 | 72.4297 | 71.0895 | 90.1805 | 89.3657 | 88.3191 | 86.7701 | 84.8455 | 82.7729 | 80.4822 | 77.843 | 75.1617 | 67.4163 | 58.5297 | 55.5115 | 53.9222
|  | COWLEY LOCAL (2 X 45) | CT |  |  | 87.7254 | 86.9841 | 85.8702 | 84.3484 | 82.3577 | 80.2097 | 77.8151 | 75.1658 | 71.9116 | 62.3375 | 50.198 | 45.8751 | 44.1339 | 93.5515 | 93.0658 | 92.366 | 91.526 | 90.4589 | 89.3066 | 88.0236 | 86.5849 | 84.8071 | 80.0091 | 74.4006 | 72.4297 | 71.0895 | 90.65 | 90.041 | 89.1507 | 87.921 | 86.3226 | 84.5894 | 82.6507 | 80.5041 | 77.8351 | 69.908 | 59.4818 | 55.5115 | 53.9222
|  | COWLEY LOCAL (2 X 45) | LW |  |  | 87.2649 | 86.3041 | 85.0394 | 83.1857 | 80.8553 | 78.3455 | 75.5727 | 72.3634 | 69.1085 | 59.8066 | 49.1835 | 47.2048 | 46.3911 | 93.4721 | 92.9129 | 92.2016 | 91.2568 | 90.0814 | 88.7952 | 87.3679 | 85.644 | 83.9017 | 79.423 | 74.4919 | 73.6781 | 73.3935 | 90.1805 | 89.3657 | 88.3191 | 86.7701 | 84.8455 | 82.7729 | 80.4822 | 77.843 | 75.1617 | 67.4163 | 58.5297 | 56.7473 | 56.0055
|  | COWLEY LOCAL (2 X 45) | ST |  |  | 88.3982 | 87.9361 | 87.2944 | 86.3482 | 85.093 | 83.7541 | 82.2743 | 80.6621 | 79.0178 | 72.7194 | 64.0246 | 61.7733 | 60.4706 | 94.0141 | 93.707 | 93.295 | 92.7119 | 91.9548 | 91.1446 | 90.2509 | 89.2722 | 88.3106 | 84.471 | 79.0989 | 77.6118 | 76.3418 | 91.2035 | 90.8308 | 90.345 | 89.651 | 88.745 | 87.7725 | 86.6924 | 85.5085 | 84.2854 | 79.324 | 71.944 | 69.9818 | 68.8359
|  | COWLEY LOCAL (2 X 45) | FS |  |  | 88.4618 | 88.0405 | 87.4774 | 86.6535 | 85.5934 | 84.3879 | 83.0705 | 81.6794 | 80.1806 | 74.8777 | 66.1266 | 63.5716 | 62.5166 | 94.0223 | 93.7283 | 93.3555 | 92.886 | 92.2832 | 91.5641 | 90.7654 | 89.9132 | 89.0093 | 85.7244 | 79.8489 | 77.6979 | 75.8962 | 94.0223 | 93.7283 | 93.3555 | 92.886 | 92.2832 | 91.5641 | 90.7654 | 89.9132 | 89.0093 | 85.7244 | 79.8489 | 77.6979 | 75.8962
COWLEY GSP | COWLEY LOCAL (2 X 90) | COWLEY LOCAL (2 X 90) | MINIMUM HEADROOM | SP 56113 03074 | NO | 47.0274 | 44.7419 | 41.7833 | 37.5618 | 33.0011 | 28.0027 | 22.9583 | 16.8264 | 10.5998 | -7.6548 | -28.7637 | -43.8531 | -54.1707 | 59.7483 | 58.3 | 56.5113 | 54.1447 | 51.5971 | 48.7728 | 45.8754 | 42.2508 | 38.572 | 27.5574 | 9.0397 | -7.7661 | -37.578 | 50.3328 | 48.2707 | 45.7477 | 41.9799 | 37.884 | 33.4054 | 28.8532 | 23.3357 | 17.7162 | 1.2577 | -17.7952 | -30.6776 | -39.2734
|  | COWLEY LOCAL (2 X 90) | CT |  |  | 48.2503 | 46.4808 | 43.9003 | 40.6912 | 37.1859 | 33.3962 | 29.5914 | 25.1401 | 18.9986 | 0.95138 | -25.4897 | -43.8531 | -54.1707 | 59.8095 | 58.4398 | 56.5463 | 54.3401 | 51.9549 | 49.3546 | 46.6558 | 43.4746 | 39.4575 | 27.5574 | 9.0397 | -7.7661 | -27.6188 | 51.478 | 49.981 | 47.8105 | 44.9499 | 41.8403 | 38.495 | 35.106 | 31.1458 | 25.6138 | 9.3845 | -14.766 | -30.6776 | -39.2734
|  | COWLEY LOCAL (2 X 90) | LW |  |  | 47.0274 | 44.7419 | 41.7833 | 37.5618 | 33.0011 | 28.0027 | 22.9583 | 16.8264 | 10.5998 | -7.6548 | -28.7637 | -37.8421 | -43.9128 | 59.7483 | 58.3 | 56.5113 | 54.1447 | 51.5971 | 48.7728 | 45.8754 | 42.2508 | 38.572 | 28.0307 | 16.6026 | 12.3455 | 9.4565 | 50.3328 | 48.2707 | 45.7477 | 41.9799 | 37.884 | 33.4054 | 28.8532 | 23.3357 | 17.7162 | 1.2577 | -17.7952 | -25.6828 | -30.7505
|  | COWLEY LOCAL (2 X 90) | ST |  |  | 49.9835 | 49.0671 | 47.7987 | 46.0818 | 44.1987 | 42.0982 | 39.9961 | 37.4577 | 34.8393 | 25.248 | 6.0747 | -4.9575 | -12.1052 | 60.9528 | 60.0481 | 58.9015 | 57.4587 | 55.9025 | 54.1689 | 52.3567 | 50.1862 | 48.0045 | 40.0576 | 22.8982 | 7.8613 | -10.9531 | 53.1084 | 52.2789 | 51.2055 | 49.8037 | 48.277 | 46.4986 | 44.6851 | 42.4855 | 40.19 | 31.8425 | 14.1953 | 4.4586 | -1.5648
|  | COWLEY LOCAL (2 X 90) | FS |  |  | 50.3613 | 49.4997 | 48.2554 | 46.7194 | 45.0726 | 43.214 | 41.3867 | 39.2351 | 36.8939 | 29.1744 | 13.0804 | 1.8937 | -3.6891 | 61.0077 | 60.0585 | 58.8957 | 57.515 | 56.0236 | 54.3348 | 52.569 | 50.474 | 48.163 | 40.1819 | 21.3462 | -2.4709 | -37.578 | 61.0077 | 60.0585 | 58.8957 | 57.515 | 56.0236 | 54.3348 | 52.569 | 50.474 | 48.163 | 40.1819 | 21.3462 | -2.4709 | -37.578
BRAMLEY (FLEE) | COXMOOR WOOD BSP | COXMOOR WOOD BSP | MINIMUM HEADROOM | SU 78324 50817 | YES | -59.1877 | -84.4147 | -87.3792 | -91.8562 | -96.4453 | -101.4074 | -106.9752 | -113.8009 | -120.2716 | -135.0693 | -153.3676 | -163.0861 | -171.0204 | -38.4496 | -62.6382 | -64.5189 | -67.0669 | -69.6913 | -72.6368 | -76.0244 | -80.465 | -84.5713 | -93.1239 | -103.4678 | -113.0412 | -121.1699 | -55.2717 | -80.2978 | -83.0617 | -87.1771 | -91.4069 | -96.0175 | -101.2137 | -107.6689 | -113.7588 | -127.4161 | -144.1488 | -152.2282 | -158.7235
|  | COXMOOR WOOD BSP | CT |  |  | -57.5995 | -82.2862 | -84.7068 | -87.8457 | -91.0447 | -94.3557 | -98.1947 | -102.6189 | -109.2169 | -123.9313 | -147.2638 | -163.0861 | -171.0204 | -38.1636 | -62.2989 | -64.1354 | -66.2192 | -68.3519 | -70.6458 | -73.3451 | -76.5217 | -80.8938 | -89.9916 | -103.4678 | -113.0412 | -121.1699 | -53.9097 | -78.4713 | -80.7676 | -83.6855 | -86.6668 | -89.7785 | -93.4002 | -97.5968 | -103.8162 | -117.4011 | -138.4688 | -152.2282 | -158.7235
|  | COXMOOR WOOD BSP | LW |  |  | -59.1877 | -84.4147 | -87.3792 | -91.8562 | -96.4453 | -101.4074 | -106.9752 | -113.8009 | -120.2716 | -135.0693 | -153.3676 | -160.134 | -163.8831 | -38.4496 | -62.6382 | -64.5189 | -67.0669 | -69.6913 | -72.6368 | -76.0244 | -80.465 | -84.5713 | -93.1239 | -103.1701 | -106.2685 | -107.9943 | -55.2717 | -80.2978 | -83.0617 | -87.1771 | -91.4069 | -96.0175 | -101.2137 | -107.6689 | -113.7588 | -127.4161 | -144.1488 | -150.0602 | -153.2714
|  | COXMOOR WOOD BSP | ST |  |  | 47.084 | 23.482 | 22.2189 | 20.6487 | 19.066 | 17.3659 | 15.4478 | 13.2242 | 10.9071 | 0.35694 | -17.3244 | -26.8109 | -32.7479 | 65.7578 | 42.3838 | 41.3588 | 40.1637 | 38.9558 | 37.6266 | 36.118 | 34.345 | 32.6127 | 24.4139 | 10.7257 | 2.6797 | -4.8772 | 50.6916 | 27.1777 | 25.9992 | 24.539 | 23.0624 | 21.462 | 19.654 | 17.5469 | 15.3692 | 5.2556 | -11.4655 | -20.0038 | -25.1467
|  | COXMOOR WOOD BSP | FS |  |  | 47.3295 | 23.9233 | 22.9331 | 21.4799 | 20.0582 | 18.5998 | 16.8841 | 14.9953 | 12.8037 | 4.8456 | -15.1224 | -25.792 | -30.7565 | 65.8229 | 42.5396 | 41.6629 | 40.62 | 39.5947 | 38.5126 | 37.2062 | 35.7414 | 34.1016 | 27.8694 | 11.3046 | -0.148 | -11.3438 | 65.8229 | 42.5396 | 41.6629 | 40.62 | 39.5947 | 38.5126 | 37.2062 | 35.7414 | 34.1016 | 27.8694 | 11.3046 | -0.148 | -11.3438
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IVER 132KV | DENHAM | DENHAM | MINIMUM HEADROOM | TQ 01785 87618 | YES | 1.0932 | -0.6057 | -2.4845 | -5.4698 | -8.7041 | -12.4019 | -16.6263 | -21.7148 | -26.217 | -36.3775 | -49.1221 | -53.8478 | -56.3337 | 23.0288 | 21.9989 | 20.7987 | 19.1588 | 17.2735 | 15.0442 | 12.4098 | 9.0055 | 6.12 | 0.26546 | -6.5026 | -8.5804 | -9.7068 | 9.0854 | 7.5259 | 5.7848 | 3.1404 | 0.23809 | -3.1409 | -7.1237 | -12.0011 | -16.2724 | -25.6926 | -37.2454 | -41.3436 | -43.4515
|  | DENHAM | CT |  |  | 23.5856 | 22.1012 | 20.6337 | 18.6896 | 16.5232 | 14.0208 | 11.2311 | 8.0342 | 3.1653 | -7.2325 | -23.6769 | -34.4171 | -39.5518 | 44.5531 | 43.3609 | 42.1749 | 40.8767 | 39.3954 | 37.6225 | 35.6115 | 33.2308 | 29.9631 | 23.5128 | 13.974 | 7.0163 | 0.63276 | 31.3032 | 29.8595 | 28.4335 | 26.6453 | 24.632 | 22.2884 | 19.659 | 16.5961 | 12.0525 | 2.6705 | -12.0759 | -21.4768 | -25.9088
|  | DENHAM | LW |  |  | 1.0932 | -0.6057 | -2.4845 | -5.4698 | -8.7041 | -12.4019 | -16.6263 | -21.7148 | -26.217 | -36.3775 | -49.1221 | -53.8478 | -56.3337 | 23.0288 | 21.9989 | 20.7987 | 19.1588 | 17.2735 | 15.0442 | 12.4098 | 9.0055 | 6.12 | 0.26546 | -6.5026 | -8.5804 | -9.7068 | 9.0854 | 7.5259 | 5.7848 | 3.1404 | 0.23809 | -3.1409 | -7.1237 | -12.0011 | -16.2724 | -25.6926 | -37.2454 | -41.3436 | -43.4515
|  | DENHAM | ST |  |  | 25.5882 | 24.9471 | 24.1982 | 23.3225 | 22.2991 | 21.0691 | 19.6708 | 17.9958 | 16.2974 | 8.0424 | -4.2296 | -10.6093 | -14.8415 | 45.9897 | 45.476 | 44.8444 | 44.134 | 43.2913 | 42.2852 | 41.1277 | 39.7075 | 38.3883 | 31.713 | 22.1722 | 16.3792 | 10.345 | 33.2599 | 32.6404 | 31.914 | 31.0774 | 30.0845 | 28.9021 | 27.5496 | 25.8966 | 24.2679 | 16.1959 | 4.8272 | -0.60805 | -4.0742
|  | DENHAM | FS |  |  | 25.7305 | 25.2788 | 24.7578 | 23.9665 | 23.0681 | 22.0521 | 20.8226 | 19.4129 | 17.8 | 11.6328 | -2.959 | -9.698 | -12.8394 | 46.0256 | 45.6038 | 45.1172 | 44.5241 | 43.8301 | 43.0425 | 42.0522 | 40.8732 | 39.5715 | 34.452 | 21.8794 | 13.6745 | 4.7283 | 46.0256 | 45.6038 | 45.1172 | 44.5241 | 43.8301 | 43.0425 | 42.0522 | 40.8732 | 39.5715 | 34.452 | 21.8794 | 13.6745 | 4.7283
COWLEY GSP | DRAYTON BSP | DRAYTON BSP | MINIMUM HEADROOM | SU 46684 92706 | YES | 66.497 | 56.8835 | 46.7549 | 38.7058 | 29.6712 | 20.2747 | 10.5991 | -0.36372 | -10.7755 | -33.9667 | -58.646 | -70.5229 | -79.2043 | 88.1573 | 79.5713 | 70.7311 | 66.1136 | 60.9265 | 55.448 | 49.842 | 43.2479 | 36.9313 | 23.4364 | 9.3633 | -3.2033 | -13.7032 | 70.3165 | 60.3417 | 49.9144 | 42.951 | 34.9943 | 26.6678 | 18.0423 | 7.9722 | -1.6706 | -22.6803 | -44.6617 | -54.6839 | -62.341
|  | DRAYTON BSP | CT |  |  | 68.9978 | 60.3864 | 50.9141 | 44.4593 | 37.1535 | 29.7428 | 22.0882 | 13.7271 | 3.5181 | -19.6214 | -50.8492 | -70.5229 | -79.2043 | 88.8104 | 80.5205 | 71.8132 | 67.6706 | 63.0351 | 58.2926 | 53.421 | 48.0672 | 41.6851 | 27.3961 | 9.3633 | -3.2033 | -13.7032 | 71.9357 | 62.7281 | 52.8059 | 47.2527 | 40.9806 | 34.5539 | 27.6716 | 20.0622 | 10.5971 | -10.5388 | -37.6318 | -54.6839 | -62.341
|  | DRAYTON BSP | LW |  |  | 66.497 | 56.8835 | 46.7549 | 38.7058 | 29.6712 | 20.2747 | 10.5991 | -0.36372 | -10.7755 | -33.9667 | -58.646 | -67.2866 | -71.6257 | 88.1573 | 79.5713 | 70.7311 | 66.1136 | 60.9265 | 55.448 | 49.842 | 43.2479 | 36.9313 | 23.4364 | 9.9475 | 5.6004 | 3.4535 | 70.3165 | 60.3417 | 49.9144 | 42.951 | 34.9943 | 26.6678 | 18.0423 | 7.9722 | -1.6706 | -22.6803 | -44.6617 | -52.127 | -55.972
|  | DRAYTON BSP | ST |  |  | 71.798 | 64.7278 | 57.4673 | 53.5719 | 49.0627 | 44.4049 | 39.7326 | 34.7199 | 29.5878 | 14.0495 | -10.5099 | -22.6788 | -29.7007 | 90.3441 | 83.1669 | 75.6405 | 72.7426 | 69.4853 | 66.1749 | 62.9002 | 59.3754 | 55.6298 | 43.6639 | 24.6094 | 13.8398 | 3.9564 | 74.8988 | 67.1996 | 59.2934 | 55.7705 | 51.7776 | 47.6693 | 43.5101 | 39.003 | 34.3876 | 19.4493 | -4.0088 | -14.6152 | -20.458
|  | DRAYTON BSP | FS |  |  | 72.1923 | 65.3546 | 58.4145 | 54.7986 | 49.7271 | 44.4354 | 39.1399 | 32.5711 | 28.0331 | 15.6197 | -8.6848 | -22.4399 | -28.2222 | 90.3675 | 83.3539 | 75.9799 | 73.3323 | 69.3186 | 65.2014 | 61.1217 | 55.7959 | 52.5144 | 42.9258 | 22.608 | 6.8111 | -9.2555 | 90.3675 | 83.3539 | 75.9799 | 73.3323 | 69.3186 | 65.2014 | 61.1217 | 55.7959 | 52.5144 | 42.9258 | 22.608 | 6.8111 | -9.2555
EALING GSP | EALING 22kV | EALING 22kV | MINIMUM HEADROOM | TQ 18371 79475 | YES | 57.471 | 55.7831 | 54.1608 | 51.6158 | 48.8819 | 45.9999 | 42.9359 | 39.7485 | 36.4464 | 25.4607 | 8.5446 | -2.9977 | -12.737 | 70.2787 | 69.0814 | 67.8177 | 66.2553 | 64.5509 | 62.7538 | 60.778 | 58.5802 | 55.9149 | 46.756 | 26.3182 | -12.7795 | -80.3561 | 60.1863 | 58.7726 | 57.4011 | 55.3608 | 53.1611 | 50.6028 | 47.8338 | 44.8523 | 41.7472 | 31.5339 | 16.2942 | -12.7795 | -80.3561
|  | EALING 22kV | CT |  |  | 58.3618 | 57.0242 | 55.6881 | 53.8695 | 51.8996 | 49.9929 | 47.9358 | 45.7462 | 42.5754 | 32.2363 | 12.2869 | -2.9977 | -12.737 | 70.2787 | 69.0814 | 67.8177 | 66.2553 | 64.5509 | 62.7538 | 60.778 | 58.5802 | 55.9149 | 46.756 | 26.3182 | 1.3105 | -34.2441 | 60.7805 | 59.6287 | 58.4435 | 56.9205 | 55.2625 | 53.6186 | 51.8387 | 49.9012 | 47.1832 | 37.7031 | 19.9099 | 7.2116 | -0.66256
|  | EALING 22kV | LW |  |  | 57.471 | 55.7831 | 54.1608 | 51.6158 | 48.8819 | 45.9999 | 42.9359 | 39.7485 | 36.4464 | 25.4607 | 8.5446 | -0.80218 | -7.4225 | 70.4469 | 69.7229 | 68.8165 | 67.5239 | 66.1312 | 64.6089 | 62.9786 | 61.1483 | 59.2301 | 52.8614 | 43.1825 | 38.6313 | 35.2752 | 60.1863 | 58.7726 | 57.4011 | 55.3608 | 53.1611 | 50.6028 | 47.8338 | 44.8523 | 41.7472 | 31.5339 | 16.2942 | 8.4729 | 3.0592
|  | EALING 22kV | ST |  |  | 59.8389 | 59.182 | 58.6023 | 57.8638 | 57.0352 | 56.1517 | 55.1754 | 54.1006 | 52.9331 | 48.3171 | 34.4653 | 24.1511 | 17.271 | 70.9553 | 70.3209 | 69.4989 | 68.475 | 67.3417 | 66.0794 | 64.6673 | 63.0649 | 61.4205 | 55.0661 | 36.3155 | 12.5091 | -21.905 | 62.0936 | 61.5343 | 61.025 | 60.3687 | 59.6292 | 58.8339 | 57.9508 | 56.9566 | 55.8927 | 51.6188 | 39.0026 | 30.2596 | 24.7621
|  | EALING 22kV | FS |  |  | 59.9939 | 59.3857 | 58.8586 | 58.2678 | 57.6192 | 56.9168 | 56.143 | 55.3466 | 54.423 | 51.0892 | 40.5873 | 30.2794 | 24.2883 | 70.9482 | 70.1826 | 69.2607 | 68.1107 | 66.8074 | 65.3263 | 63.6616 | 61.773 | 59.6064 | 51.3344 | 27.3835 | -12.7795 | -80.3561 | 70.9482 | 70.1826 | 69.2607 | 68.1107 | 66.8074 | 65.3263 | 63.6616 | 61.773 | 59.6064 | 51.3344 | 27.3835 | -12.7795 | -80.3561
LALEHAM | EAST BEDFONT B | EAST BEDFONT B | MINIMUM HEADROOM | TQ 08394 73826 | YES | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
|  | EAST BEDFONT B | CT |  |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
|  | EAST BEDFONT B | LW |  |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
|  | EAST BEDFONT B | ST |  |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
|  | EAST BEDFONT B | FS |  |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
LALEHAM | EAST BEDFONT A | EAST BEDFONT A | MINIMUM HEADROOM | TQ 08394 73826 | YES | 3.4478 | 1.6105 | -0.69148 | -3.7917 | -6.891 | -10.1619 | -13.7541 | -17.4799 | -21.0608 | -31.4192 | -46.1401 | -58.7776 | -68.1307 | 13.1396 | 12.0974 | 10.7984 | 9.1604 | 7.4869 | 5.6874 | 3.6273 | 1.2917 | -0.95599 | -7.7657 | -20.2425 | -32.7586 | -56.8148 | 5.1649 | 3.4795 | 1.3762 | -1.424 | -4.2578 | -7.2833 | -10.6064 | -14.1439 | -17.5999 | -27.3944 | -40.4642 | -50.8495 | -58.6022
|  | EAST BEDFONT A | CT |  |  | 4.1733 | 2.7077 | 0.61236 | -1.8991 | -4.3891 | -6.9692 | -9.8317 | -12.6319 | -16.1319 | -26.5669 | -44.4905 | -58.7776 | -68.1307 | 13.2355 | 12.2513 | 10.9141 | 9.3709 | 7.7917 | 6.1158 | 4.0582 | 1.9468 | -0.48136 | -7.7657 | -20.2425 | -32.7586 | -47.4384 | 5.7707 | 4.4381 | 2.4906 | 0.19491 | -2.1138 | -4.5271 | -7.1974 | -9.8727 | -13.2202 | -22.9804 | -38.8202 | -50.8495 | -58.6022
|  | EAST BEDFONT A | LW |  |  | 3.4478 | 1.6105 | -0.69148 | -3.7917 | -6.891 | -10.1619 | -13.7541 | -17.4799 | -21.0608 | -31.4192 | -46.1401 | -55.3475 | -62.0384 | 13.1396 | 12.0974 | 10.7984 | 9.1604 | 7.4869 | 5.6874 | 3.6273 | 1.2917 | -0.95599 | -7.3001 | -15.3018 | -19.8276 | -23.2366 | 5.1649 | 3.4795 | 1.3762 | -1.424 | -4.2578 | -7.2833 | -10.6064 | -14.1439 | -17.5999 | -27.3944 | -40.4642 | -48.136 | -53.5976
|  | EAST BEDFONT A | ST |  |  | 5.081 | 4.1588 | 2.9784 | 1.5505 | 0.1386 | -1.3521 | -3.0152 | -4.6193 | -6.0584 | -11.394 | -24.1517 | -33.3413 | -40.0186 | 13.7081 | 12.9911 | 12.0985 | 11.0338 | 9.9358 | 8.7511 | 7.4519 | 6.1564 | 4.9347 | -0.02146 | -11.4064 | -22.4391 | -36.0525 | 6.6662 | 5.8558 | 4.8158 | 3.5131 | 2.2015 | 0.80184 | -0.75417 | -2.2878 | -3.6631 | -8.8987 | -20.6199 | -28.4264 | -33.8672
|  | EAST BEDFONT A | FS |  |  | 5.1864 | 4.3021 | 3.1971 | 1.9787 | 0.78713 | -0.48871 | -1.9001 | -3.2057 | -4.3757 | -8.3418 | -18.337 | -27.2375 | -32.7625 | 13.7276 | 13.0008 | 12.1127 | 11.1013 | 10.0485 | 8.8945 | 7.6338 | 6.3897 | 5.1045 | 0.16574 | -12.3689 | -29.9622 | -56.8148 | 13.7276 | 13.0008 | 12.1127 | 11.1013 | 10.0485 | 8.8945 | 7.6338 | 6.3897 | 5.1045 | 0.16574 | -12.3689 | -29.9622 | -56.8148
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | FAREHAM T1A T2A (90MVAS) | MINIMUM HEADROOM | SU 56534 04031 | YES | 18.5389 | 15.0283 | -4.109 | -9.2979 | -15.0945 | -21.3892 | -28.0587 | -35.9459 | -44.245 | -66.4819 | -94.2248 | -114.1192 | -127.9369 | 24.7855 | 23.6249 | 7.013 | 5.4563 | 3.5085 | 1.3333 | -0.98939 | -3.9703 | -9.3986 | -23.4046 | -41.639 | -58.2681 | -73.9329 | -5.8552 | -9.0264 | -27.8133 | -32.7392 | -38.2419 | -44.19 | -50.4871 | -57.8268 | -65.549 | -86.0035 | -110.9702 | -128.015 | -139.9144
|  | FAREHAM T1A T2A (90MVAS) | CT |  |  | 19.8514 | 17.1422 | -1.649 | -5.5868 | -10.0428 | -14.768 | -19.8132 | -25.4974 | -33.631 | -55.8412 | -89.6323 | -114.1192 | -127.9369 | 24.8232 | 23.7276 | 7.0992 | 5.6748 | 3.9215 | 2.0174 | -0.012918 | -2.2608 | -5.483 | -20.7708 | -41.639 | -58.2681 | -73.9329 | -4.4361 | -6.8258 | -25.2076 | -28.8409 | -32.9649 | -37.3288 | -41.9896 | -47.3302 | -54.9731 | -75.8142 | -106.5745 | -128.015 | -139.9144
|  | FAREHAM T1A T2A (90MVAS) | LW |  |  | 18.5389 | 15.0283 | -4.109 | -9.2979 | -15.0945 | -21.3892 | -28.0587 | -35.9459 | -44.245 | -66.4819 | -94.2248 | -108.4754 | -117.562 | 24.7855 | 23.6249 | 7.013 | 5.4563 | 3.5085 | 1.3333 | -0.98939 | -3.9703 | -9.3986 | -23.4046 | -39.4875 | -47.2415 | -52.2268 | -5.8552 | -9.0264 | -27.8133 | -32.7392 | -38.2419 | -44.19 | -50.4871 | -57.8268 | -65.549 | -86.0035 | -110.9702 | -123.4111 | -131.1718
|  | FAREHAM T1A T2A (90MVAS) | ST |  |  | 73.3334 | 71.812 | 19.2147 | 17.1469 | 14.6616 | 11.9489 | 9.083 | 5.8882 | 1.6553 | -14.6695 | -43.5561 | -58.6966 | -68.5031 | 76.4882 | 75.7328 | 23.9696 | 22.9907 | 21.6989 | 20.2682 | 18.7462 | 17.0509 | 14.3091 | 4.8086 | -15.6504 | -30.2538 | -44.239 | 48.8547 | 47.5847 | -4.7526 | -6.5579 | -8.7941 | -11.3259 | -14.0168 | -17.0353 | -21.0411 | -36.6611 | -63.8537 | -77.4462 | -85.9805
|  | FAREHAM T1A T2A (90MVAS) | FS |  |  | 73.5249 | 72.1031 | 70.6003 | 68.9408 | 64.5299 | 59.9439 | 55.1845 | 47.6294 | 44.4445 | 33.1074 | 7.5322 | -8.2888 | -15.7253 | 76.5202 | 75.7805 | 74.9677 | 74.0936 | 70.5113 | 66.8174 | 63.0355 | 56.5331 | 54.529 | 47.8298 | 28.643 | 7.0129 | -17.3679 | 76.5202 | 75.7805 | 74.9677 | 74.0936 | 70.5113 | 66.8174 | 63.0355 | 56.5331 | 54.529 | 47.8298 | 28.643 | 7.0129 | -17.3679
LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | FAREHAM T1B T2B (1X90, 1X60MVA) | MINIMUM HEADROOM | SU 56534 04031 | YES | 36.0314 | 34.6781 | 32.9796 | 30.1039 | 27.0561 | 23.9783 | 20.6913 | 16.7272 | 12.5652 | 1.4222 | -12.8666 | -24.5261 | -32.6129 | 47.3133 | 46.4533 | 45.38 | 43.8111 | 42.1286 | 40.3873 | 38.533 | 36.1872 | 33.6376 | 26.8062 | 16.7008 | 7.0505 | -3.2762 | 40.5602 | 39.2151 | 37.5524 | 34.9258 | 32.1207 | 29.2406 | 26.1865 | 22.4252 | 18.4415 | 7.9531 | -4.8491 | -13.9634 | -20.5267
|  | FAREHAM T1B T2B (1X90, 1X60MVA) | CT |  |  | 37.01 | 36.1447 | 34.7375 | 32.6968 | 30.4278 | 28.2361 | 25.919 | 23.1372 | 19.0474 | 7.7074 | -10.6719 | -24.5261 | -32.6129 | 47.4998 | 46.8127 | 45.7135 | 44.3626 | 42.9057 | 41.4497 | 39.892 | 37.9907 | 35.3684 | 27.8459 | 16.7008 | 7.0505 | -3.2762 | 41.3032 | 40.4187 | 38.9447 | 36.9919 | 34.8863 | 32.8125 | 30.606 | 27.9268 | 24.0543 | 13.4165 | -2.5821 | -13.9634 | -20.5267
|  | FAREHAM T1B T2B (1X90, 1X60MVA) | LW |  |  | 36.0314 | 34.6781 | 32.9796 | 30.1039 | 27.0561 | 23.9783 | 20.6913 | 16.7272 | 12.5652 | 1.4222 | -12.8666 | -20.5133 | -25.6643 | 47.3133 | 46.4533 | 45.38 | 43.8111 | 42.1286 | 40.3873 | 38.533 | 36.1872 | 33.6376 | 26.8062 | 18.9679 | 15.4489 | 12.9654 | 40.5602 | 39.2151 | 37.5524 | 34.9258 | 32.1207 | 29.2406 | 26.1865 | 22.4252 | 18.4415 | 7.9531 | -4.8491 | -11.1299 | -15.3145
|  | FAREHAM T1B T2B (1X90, 1X60MVA) | ST |  |  | 38.0666 | 37.6687 | 37.0819 | 36.1716 | 35.1833 | 34.2411 | 33.1824 | 31.8597 | 30.4323 | 25.0778 | 11.7265 | 3.3047 | -2.4341 | 48.1784 | 47.8187 | 47.305 | 46.5491 | 45.7298 | 44.9092 | 44.0213 | 42.9418 | 41.8186 | 37.3985 | 26.3649 | 17.9884 | 8.7743 | 42.4019 | 42.0022 | 41.4327 | 40.5286 | 39.5435 | 38.5682 | 37.5176 | 36.23 | 34.8783 | 29.5508 | 17.0335 | 9.6988 | 4.9184
|  | FAREHAM T1B T2B (1X90, 1X60MVA) | FS |  |  | 38.1816 | 37.8139 | 37.2919 | 36.608 | 35.8849 | 35.2113 | 34.4812 | 33.5391 | 32.422 | 28.6403 | 17.9237 | 9.5968 | 5.2204 | 48.1901 | 47.8015 | 47.2894 | 46.6681 | 45.9994 | 45.325 | 44.5782 | 43.6904 | 42.6055 | 38.6609 | 27.4753 | 14.4956 | -2.5747 | 48.1901 | 47.8015 | 47.2894 | 46.6681 | 45.9994 | 45.325 | 44.5782 | 43.6904 | 42.6055 | 38.6609 | 27.4753 | 14.4956 | -2.5747
BRAMLEY (FLEE) | FERNHURST | FERNHURST | MINIMUM HEADROOM | SU 72730 39772 | YES | 29.9176 | 25.1208 | 20.0556 | 13.1932 | 6.1421 | -0.75459 | -8.2944 | -17.025 | -24.9547 | -43.3002 | -63.2176 | -69.0149 | -72.456 | 63.7901 | 61.2511 | 58.5255 | 54.9958 | 51.3224 | 47.589 | 43.3952 | 38.1818 | 33.4089 | 23.3375 | 13.1241 | 7.4685 | -1.0028 | 63.611 | 59.6635 | 55.4732 | 49.8831 | 44.1175 | 38.373 | 32.0031 | 24.4722 | 17.385 | 1.6292 | -16.4098 | -21.2654 | -24.0933
|  | FERNHURST | CT |  |  | 34.7341 | 31.6455 | 28.1536 | 23.6735 | 19.0071 | 14.52 | 9.4636 | 4.0177 | -3.6607 | -20.5467 | -45.063 | -60.7213 | -67.8811 | 65.4255 | 63.4542 | 61.1904 | 58.5539 | 55.7694 | 52.9412 | 49.5629 | 45.8176 | 40.8255 | 30.5261 | 16.8945 | 7.4685 | -0.76498 | 67.1699 | 64.5161 | 61.4279 | 57.6301 | 53.649 | 49.7219 | 45.2074 | 40.2695 | 33.412 | 19.3212 | -0.47882 | -14.0582 | -19.9223
|  | FERNHURST | LW |  |  | 29.9176 | 25.1208 | 20.0556 | 13.1932 | 6.1421 | -0.75459 | -8.2944 | -17.025 | -24.9547 | -43.3002 | -63.2176 | -69.0149 | -72.456 | 63.7901 | 61.2511 | 58.5255 | 54.9958 | 51.3224 | 47.589 | 43.3952 | 38.1818 | 33.4089 | 23.3375 | 13.1241 | 10.733 | 9.3949 | 63.611 | 59.6635 | 55.4732 | 49.8831 | 44.1175 | 38.373 | 32.0031 | 24.4722 | 17.385 | 1.6292 | -16.4098 | -21.2654 | -24.0933
|  | FERNHURST | ST |  |  | 37.6248 | 35.8336 | 33.8395 | 31.2085 | 28.4688 | 25.8613 | 22.975 | 19.7661 | 16.3504 | 1.9025 | -18.6497 | -28.7277 | -34.7052 | 67.2491 | 66.0744 | 64.7367 | 63.0814 | 61.331 | 59.6014 | 57.661 | 55.4522 | 53.2049 | 43.0104 | 28.3796 | 20.3782 | 12.7393 | 69.7963 | 68.2999 | 66.6096 | 64.4028 | 62.0967 | 59.8703 | 57.3891 | 54.5245 | 51.5615 | 38.303 | 20.2541 | 12.3148 | 7.6501
|  | FERNHURST | FS |  |  | 38.2753 | 36.831 | 35.3027 | 32.3515 | 29.3867 | 26.5685 | 23.4677 | 20.2311 | 16.1493 | 2.0871 | -27.9275 | -44.0936 | -52.4892 | 67.4716 | 66.4355 | 65.313 | 63.6111 | 61.8612 | 60.1636 | 58.2338 | 56.1622 | 53.6687 | 44.6784 | 24.3583 | 11.3535 | -1.0028 | 67.4716 | 66.4355 | 65.313 | 63.6111 | 61.8612 | 60.1636 | 58.2338 | 56.1622 | 53.6687 | 44.6784 | 24.3583 | 11.3535 | -1.0028
LOVEDEAN GSP | FORT WIDLEY | FORT WIDLEY | MINIMUM HEADROOM | SU 64948 05441 | YES | 51.669 | 50.1217 | 48.4642 | 45.9751 | 43.1322 | 40.0632 | 36.6659 | 32.724 | 28.8641 | 20.0999 | 9.9071 | 2.3076 | -3.2864 | 52.096 | 51.1194 | 50.0922 | 48.717 | 47.0995 | 45.283 | 43.2801 | 40.7992 | 38.3982 | 33.4196 | 27.7446 | 22.3198 | 16.2945 | 51.2628 | 49.9419 | 48.4868 | 46.2609 | 43.7203 | 40.9645 | 37.9366 | 34.4212 | 30.9873 | 23.0859 | 13.831 | 6.9195 | 2.1177
|  | FORT WIDLEY | CT |  |  | 52.3622 | 51.1846 | 49.7161 | 47.8172 | 45.6055 | 43.2358 | 40.5826 | 37.6107 | 33.7487 | 24.496 | 11.8003 | 2.3076 | -3.2864 | 52.2424 | 51.4118 | 50.3762 | 49.1935 | 47.8011 | 46.2581 | 44.5572 | 42.5711 | 40.13 | 34.5882 | 27.7446 | 22.3198 | 17.7654 | 51.9623 | 50.9422 | 49.6719 | 48.0005 | 46.0524 | 43.9499 | 41.6149 | 38.9881 | 35.5569 | 27.1687 | 15.6084 | 6.9195 | 2.1177
|  | FORT WIDLEY | LW |  |  | 51.669 | 50.1217 | 48.4642 | 45.9751 | 43.1322 | 40.0632 | 36.6659 | 32.724 | 28.8641 | 20.0999 | 9.9071 | 4.4178 | 0.81565 | 52.096 | 51.1194 | 50.0922 | 48.717 | 47.0995 | 45.283 | 43.2801 | 40.7992 | 38.3982 | 33.4196 | 27.9458 | 25.076 | 23.1867 | 51.2628 | 49.9419 | 48.4868 | 46.2609 | 43.7203 | 40.9645 | 37.9366 | 34.4212 | 30.9873 | 23.0859 | 13.831 | 8.9267 | 5.7962
|  | FORT WIDLEY | ST |  |  | 53.3488 | 52.6364 | 51.8818 | 50.8357 | 49.549 | 48.1437 | 46.5641 | 44.8398 | 42.9221 | 36.0661 | 25.5323 | 19.6788 | 15.6373 | 52.9175 | 52.3869 | 51.8344 | 51.0952 | 50.1724 | 49.1382 | 47.9955 | 46.7133 | 45.2583 | 39.8685 | 31.7742 | 27.2015 | 23.0833 | 52.7789 | 52.1977 | 51.6061 | 50.7321 | 49.6372 | 48.4209 | 47.0731 | 45.5828 | 43.8835 | 37.7145 | 27.8983 | 22.7334 | 19.2934
|  | FORT WIDLEY | FS |  |  | 53.4336 | 52.7726 | 52.1113 | 51.2138 | 49.2366 | 47.0998 | 44.8006 | 41.4159 | 39.8581 | 34.838 | 24.4654 | 18.6505 | 15.6071 | 52.9277 | 52.4104 | 51.9012 | 51.291 | 49.6243 | 47.8122 | 45.8888 | 42.8752 | 41.6865 | 37.6829 | 28.9064 | 22.6227 | 16.2945 | 52.9277 | 52.4104 | 51.9012 | 51.291 | 49.6243 | 47.8122 | 45.8888 | 42.8752 | 41.6865 | 37.6829 | 28.9064 | 22.6227 | 16.2945
MELKSHAM GSP | FROME BSP | FROME BSP | MINIMUM HEADROOM | ST 78803 48019 | YES | 20.2432 | 15.9087 | 11.4371 | 5.5099 | -0.85637 | -7.2904 | -14.1208 | -21.9632 | -30.0961 | -51.1983 | -76.4577 | -86.5526 | -95.4516 | 43.3764 | 42.3058 | 41.1243 | 38.148 | 34.5508 | 30.7896 | 26.7167 | 16.8638 | 13.7611 | 3.3307 | -19.8168 | -36.1839 | -50.7397 | 25.7278 | 21.8896 | 17.8905 | 12.553 | 6.7653 | 0.86704 | -5.4178 | -12.7126 | -20.2923 | -39.6781 | -62.7331 | -72.0606 | -79.7657
|  | FROME BSP | CT |  |  | 24.4624 | 21.7802 | 18.4499 | 14.4214 | 10.0429 | 5.6669 | 0.95114 | -4.2262 | -11.7625 | -31.8065 | -63.558 | -85.7363 | -95.4516 | 43.3764 | 42.3058 | 41.1243 | 39.983 | 38.0189 | 35.0597 | 31.8174 | 28.1431 | 23.1807 | 10.715 | -6.76 | -19.8461 | -29.3691 | 29.5086 | 27.0834 | 24.046 | 20.388 | 16.3694 | 12.3189 | 7.9367 | 3.0811 | -3.9293 | -22.3951 | -51.1072 | -71.0215 | -79.7657
|  | FROME BSP | LW |  |  | 20.2432 | 15.9087 | 11.4371 | 5.5099 | -0.85637 | -7.2904 | -14.1208 | -21.9632 | -30.0961 | -51.1983 | -76.4577 | -86.5526 | -92.4592 | 43.457 | 42.3527 | 41.215 | 38.148 | 34.5508 | 30.7896 | 26.7167 | 21.7768 | 16.6461 | 4.5465 | -9.4015 | -15.5441 | -18.9613 | 25.7278 | 21.8896 | 17.8905 | 12.553 | 6.7653 | 0.86704 | -5.4178 | -12.7126 | -20.2923 | -39.6781 | -62.7331 | -72.0606 | -77.4807
|  | FROME BSP | ST |  |  | 26.2391 | 24.4597 | 22.5173 | 20.0427 | 17.2439 | 14.4604 | 11.515 | 8.4006 | 3.8074 | -12.5451 | -39.7032 | -53.313 | -61.7191 | 43.9155 | 43.0876 | 42.2619 | 41.3982 | 40.2462 | 39.0947 | 37.8643 | 36.2697 | 32.552 | 19.0342 | -2.2276 | -13.544 | -22.5996 | 31.1847 | 29.6432 | 27.9394 | 25.7183 | 23.1634 | 20.5919 | 17.8597 | 14.9361 | 10.5497 | -5.1242 | -30.4746 | -43.4773 | -51.0743
|  | FROME BSP | FS |  |  | 26.7422 | 25.1249 | 23.4079 | 20.2667 | 12.9784 | 5.7737 | -1.614 | -13.2571 | -17.8773 | -32.5256 | -62.8967 | -79.9672 | -88.1576 | 43.9256 | 43.1073 | 42.3022 | 41.5235 | 36.6482 | 31.8035 | 26.8792 | 16.8638 | 13.7611 | 3.3307 | -19.8168 | -36.1839 | -50.7397 | 43.9256 | 43.1073 | 42.3022 | 41.5235 | 36.6482 | 31.8035 | 26.8792 | 16.8638 | 13.7611 | 3.3307 | -19.8168 | -36.1839 | -50.7397
MINETY GSP | GALILEO | GALILEO | MINIMUM HEADROOM | SU 10596 83733 | NO | 43.5796 | 43.3791 | 43.1587 | 42.813 | 42.447 | 42.0567 | 41.6412 | 41.122 | 40.5804 | 39.3196 | 37.4149 | 35.6342 | 34.282 | 41.5774 | 41.473 | 41.3567 | 41.1842 | 41.0004 | 40.8013 | 40.5877 | 40.3202 | 40.0339 | 39.3472 | 38.0976 | 36.7338 | 35.2457 | 41.7093 | 41.6641 | 41.6162 | 41.557 | 41.4956 | 41.4286 | 41.3517 | 41.2669 | 41.1468 | 40.3507 | 38.6659 | 37.2161 | 35.2457
|  | GALILEO | CT |  |  | 43.682 | 43.5363 | 43.3446 | 43.0967 | 42.8372 | 42.5694 | 42.278 | 41.9283 | 41.3908 | 40.0495 | 37.6661 | 35.6342 | 34.282 | 41.608 | 41.5204 | 41.4085 | 41.2704 | 41.1254 | 40.9732 | 40.8068 | 40.6102 | 40.3151 | 39.543 | 38.0976 | 36.7338 | 35.3595 | 44.3954 | 44.2731 | 44.0912 | 43.8603 | 43.6184 | 43.367 | 43.0925 | 42.76 | 42.2525 | 41.0116 | 38.9109 | 37.2161 | 36.0858
|  | GALILEO | LW |  |  | 43.5796 | 43.3791 | 43.1587 | 42.813 | 42.447 | 42.0567 | 41.6412 | 41.122 | 40.5804 | 39.3196 | 37.4149 | 36.1362 | 35.2014 | 41.5774 | 41.473 | 41.3567 | 41.1842 | 41.0004 | 40.8013 | 40.5877 | 40.3202 | 40.0339 | 39.3472 | 38.3508 | 37.7382 | 37.2826 | 44.3201 | 44.1333 | 43.9271 | 43.6089 | 43.2712 | 42.9085 | 42.521 | 42.0296 | 41.5165 | 40.3507 | 38.6659 | 37.596 | 36.8291
|  | GALILEO | ST |  |  | 43.8524 | 43.7814 | 43.7015 | 43.5935 | 43.4742 | 43.3466 | 43.2034 | 43.0395 | 42.8694 | 42.067 | 40.245 | 39.0048 | 38.0411 | 41.7003 | 41.6534 | 41.6005 | 41.5322 | 41.457 | 41.3752 | 41.283 | 41.1773 | 41.0581 | 40.5283 | 39.2459 | 38.1391 | 36.9028 | 44.5448 | 44.4941 | 44.4331 | 44.3319 | 44.2194 | 44.0981 | 43.9611 | 43.803 | 43.6444 | 42.8725 | 41.2043 | 40.1572 | 39.3791
|  | GALILEO | FS |  |  | 43.8708 | 43.8077 | 43.7425 | 43.6517 | 43.5597 | 43.461 | 43.3475 | 43.2235 | 43.0794 | 42.503 | 40.7496 | 39.5577 | 38.8079 | 41.7093 | 41.6641 | 41.6162 | 41.557 | 41.4956 | 41.4286 | 41.3517 | 41.2669 | 41.1468 | 40.6755 | 39.2608 | 37.5743 | 35.2457 | 41.7093 | 41.6641 | 41.6162 | 41.557 | 41.4956 | 41.4286 | 41.3517 | 41.2669 | 41.1468 | 40.6755 | 39.2608 | 37.5743 | 35.2457
COWLEY GSP | HARWELL | HARWELL | MINIMUM HEADROOM |  |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
|  | HARWELL | CT |  |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
|  | HARWELL | LW |  |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
|  | HARWELL | ST |  |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
|  | HARWELL | FS |  |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
LOVEDEAN GSP | HAVANT | HAVANT | MINIMUM HEADROOM | SU 70625 05720 | YES | -13.8391 | -17.4672 | -21.3665 | -26.9582 | -33.1765 | -39.8672 | -47.0271 | -55.7878 | -64.8145 | -86.9849 | -113.0922 | -133.9027 | -147.5799 | 20.7804 | 18.5037 | 16.0342 | 12.8047 | 9.1343 | 5.09 | 0.68258 | -5.0115 | -10.9058 | -24.5755 | -42.3305 | -57.6855 | -72.2781 | 5.1773 | 2.2282 | -0.9589 | -5.9135 | -11.5019 | -17.5092 | -23.9544 | -31.8322 | -39.9786 | -60.2544 | -84.0663 | -102.7544 | -114.4034
|  | HAVANT | CT |  |  | -12.5325 | -15.2948 | -18.8537 | -23.0014 | -27.6909 | -32.661 | -38.0317 | -44.2464 | -53.4538 | -76.7935 | -110.1989 | -133.9027 | -147.5799 | 20.9822 | 19.0568 | 16.5014 | 13.7402 | 10.5881 | 7.211 | 3.4957 | -0.93041 | -7.1078 | -22.3066 | -42.3305 | -57.6855 | -72.2781 | 6.511 | 4.3271 | 1.4843 | -2.1812 | -6.3365 | -10.7421 | -15.5223 | -21.0691 | -29.3657 | -50.6203 | -81.4008 | -102.7544 | -114.4034
|  | HAVANT | LW |  |  | -13.8391 | -17.4672 | -21.3665 | -26.9582 | -33.1765 | -39.8672 | -47.0271 | -55.7878 | -64.8145 | -86.9849 | -113.0922 | -125.7232 | -133.4759 | 20.7804 | 18.5037 | 16.0342 | 12.8047 | 9.1343 | 5.09 | 0.68258 | -5.0115 | -10.9058 | -24.5755 | -39.1571 | -45.1556 | -49.0343 | 5.1773 | 2.2282 | -0.9589 | -5.9135 | -11.5019 | -17.5092 | -23.9544 | -31.8322 | -39.9786 | -60.2544 | -84.0663 | -95.2057 | -101.7969
|  | HAVANT | ST |  |  | -9.8792 | -11.3133 | -12.8674 | -14.9123 | -17.3499 | -19.9489 | -22.7448 | -25.9953 | -29.3936 | -43.3827 | -70.2496 | -84.9622 | -95.0317 | 22.8116 | 21.7522 | 20.5769 | 19.008 | 17.1284 | 15.104 | 12.8886 | 10.2636 | 7.591 | -3.6596 | -24.9858 | -38.1144 | -51.5432 | 8.7254 | 7.6766 | 6.5279 | 4.935 | 3.0064 | 0.83228 | -1.5928 | -4.448 | -7.4838 | -19.948 | -44.7287 | -57.6375 | -66.131
|  | HAVANT | FS |  |  | -9.7347 | -11.0729 | -12.4503 | -14.0191 | -15.878 | -17.8652 | -20.0543 | -22.5166 | -25.3164 | -35.3625 | -59.5847 | -73.9274 | -80.8976 | 22.8 | 21.7475 | 20.6346 | 19.4014 | 17.9143 | 16.3062 | 14.4862 | 12.3834 | 9.9212 | 0.79867 | -21.9444 | -41.8102 | -65.3456 | 22.8 | 21.7475 | 20.6346 | 19.4014 | 17.9143 | 16.3062 | 14.4862 | 12.3834 | 9.9212 | 0.79867 | -21.9444 | -41.8102 | -65.3456
COWLEY GSP | HEADINGTON BSP | HEADINGTON BSP | MINIMUM HEADROOM | SP 54454 08145 | NO | 34.4959 | 32.1552 | 29.1447 | 24.9892 | 20.7647 | 17.1102 | 13.1886 | 8.8609 | 4.4157 | -6.9584 | -20.1467 | -27.2494 | -33.6697 | 64.6797 | 63.2511 | 61.4295 | 59.1725 | 56.8204 | 54.7383 | 52.4257 | 49.7226 | 46.9597 | 40.1953 | 31.9833 | 24.001 | 15.5927 | 49.5388 | 47.4351 | 44.7608 | 41.1165 | 37.3793 | 34.0741 | 30.4902 | 26.459 | 22.3322 | 11.8463 | 0.06461 | -5.5888 | -10.9228
|  | HEADINGTON BSP | CT |  |  | 36.0489 | 34.2907 | 31.7921 | 28.5659 | 25.282 | 22.6817 | 19.8496 | 16.7927 | 12.4753 | 1.4715 | -15.2456 | -27.2494 | -33.6697 | 64.987 | 63.6898 | 61.9095 | 59.9044 | 57.8018 | 56.0414 | 54.0644 | 51.8883 | 49.0648 | 41.9612 | 31.9833 | 24.001 | 15.833 | 50.8155 | 49.2119 | 46.9524 | 44.1081 | 41.1816 | 38.8022 | 36.1818 | 33.3287 | 29.3685 | 19.3605 | 4.4913 | -5.5888 | -10.9228
|  | HEADINGTON BSP | LW |  |  | 34.4959 | 32.1552 | 29.1447 | 24.9892 | 20.7647 | 17.1102 | 13.1886 | 8.8609 | 4.4157 | -6.9584 | -20.1467 | -25.9902 | -30.0464 | 64.6797 | 63.2511 | 61.4295 | 59.1725 | 56.8204 | 54.7383 | 52.4257 | 49.7226 | 46.9597 | 40.1953 | 33.213 | 30.6234 | 28.767 | 49.5388 | 47.4351 | 44.7608 | 41.1165 | 37.3793 | 34.0741 | 30.4902 | 26.459 | 22.3322 | 11.8463 | 0.06461 | -4.8263 | -8.1888
|  | HEADINGTON BSP | ST |  |  | 37.2339 | 36.1135 | 34.5916 | 32.6895 | 30.7336 | 29.2125 | 27.5559 | 25.7706 | 23.803 | 17.4333 | 4.4736 | -2.9723 | -7.4864 | 65.8811 | 65.0213 | 63.8775 | 62.4923 | 61.0359 | 59.8398 | 58.5088 | 57.0549 | 55.5502 | 50.3613 | 39.9522 | 32.651 | 25.0679 | 52.0167 | 51.0412 | 49.7311 | 48.0696 | 46.3398 | 44.9489 | 43.4196 | 41.758 | 39.9594 | 34.0155 | 22.3633 | 15.7176 | 11.7801
|  | HEADINGTON BSP | FS |  |  | 37.4495 | 36.4358 | 35.0856 | 33.234 | 31.3131 | 29.8025 | 28.1411 | 26.4566 | 24.4763 | 18.8646 | 6.5485 | -2.2345 | -6.7007 | 65.921 | 65.0866 | 64.0153 | 62.7711 | 61.4292 | 60.3177 | 59.0448 | 57.7191 | 56.1938 | 51.4536 | 40.2407 | 29.0073 | 15.5927 | 65.921 | 65.0866 | 64.0153 | 62.7711 | 61.4292 | 60.3177 | 59.0448 | 57.7191 | 56.1938 | 51.4536 | 40.2407 | 29.0073 | 15.5927
COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE BSP | MINIMUM HEADROOM | SU 84773 92191 | YES | 14.6385 | 11.5976 | 8.3825 | 3.5627 | -1.6727 | -7.2483 | -13.3884 | -20.6914 | -27.7048 | -44.7863 | -66.5821 | -76.2669 | -86.0588 | 46.429 | 45.7415 | 44.5269 | 42.4904 | 40.1199 | 37.5845 | 34.8324 | 31.5218 | 27.1394 | 17.0661 | -1.4666 | -23.8634 | -51.3814 | 25.1439 | 22.3032 | 19.3022 | 14.8736 | 10.0375 | 4.8328 | -0.91858 | -7.8308 | -14.4563 | -30.348 | -50.3888 | -58.8591 | -66.3592
|  | HIGH WYCOMBE BSP | CT |  |  | 17.2299 | 15.1405 | 12.7404 | 9.559 | 6.0453 | 2.3065 | -1.816 | -6.4395 | -13.3526 | -29.8076 | -56.7728 | -76.2669 | -86.0588 | 46.429 | 45.7415 | 44.9588 | 44.1516 | 42.5356 | 40.6121 | 38.513 | 35.7862 | 30.9986 | 19.8942 | 1.7818 | -14.0908 | -30.3872 | 27.3512 | 25.3811 | 23.0931 | 20.1246 | 16.8204 | 13.2851 | 9.3733 | 4.9594 | -1.5871 | -16.925 | -41.3998 | -58.1779 | -66.3592
|  | HIGH WYCOMBE BSP | LW |  |  | 14.6385 | 11.5976 | 8.3825 | 3.5627 | -1.6727 | -7.2483 | -13.3884 | -20.6914 | -27.7048 | -44.7863 | -66.5821 | -76.2569 | -81.9264 | 46.5988 | 45.8354 | 44.5269 | 42.4904 | 40.1199 | 37.5845 | 34.8324 | 31.5218 | 27.1394 | 17.0661 | 4.4965 | -0.87756 | -3.9763 | 25.1439 | 22.3032 | 19.3022 | 14.8736 | 10.0375 | 4.8328 | -0.91858 | -7.8308 | -14.4563 | -30.348 | -50.3888 | -58.8591 | -63.6993
|  | HIGH WYCOMBE BSP | ST |  |  | 19.7515 | 18.7264 | 17.6084 | 16.0828 | 14.2809 | 12.346 | 10.2034 | 7.7372 | 4.3328 | -9.5206 | -33.2776 | -46.0204 | -53.6777 | 47.1311 | 46.7508 | 46.3431 | 45.8588 | 45.138 | 44.3371 | 43.4421 | 42.1354 | 39.7577 | 29.9407 | 9.1722 | -5.3498 | -20.9986 | 29.7773 | 28.831 | 27.7831 | 26.3536 | 24.6443 | 22.7997 | 20.7512 | 18.3842 | 15.1099 | 1.6894 | -20.9089 | -32.5241 | -39.26
|  | HIGH WYCOMBE BSP | FS |  |  | 20.1034 | 19.261 | 18.3886 | 16.8918 | 13.0786 | 9.1899 | 5.1 | -1.4681 | -4.4009 | -14.7416 | -40.4382 | -55.7972 | -63.1029 | 47.136 | 46.7653 | 46.3822 | 45.9569 | 43.1895 | 40.3748 | 37.4341 | 31.5875 | 29.595 | 21.9837 | -1.4666 | -23.8634 | -51.3814 | 47.136 | 46.7653 | 46.3822 | 45.9569 | 43.1895 | 40.3748 | 37.4341 | 31.5875 | 29.595 | 21.9837 | -1.4666 | -23.8634 | -51.3814
FAWLEY GSP | LANGLEY BSP | LANGLEY BSP | MINIMUM HEADROOM | SU 45185 01376 | YES | 29.9189 | 29.1392 | 28.2848 | 26.6882 | 24.8839 | 22.9999 | 20.9228 | 18.3272 | 15.5055 | 8.1944 | 0.39622 | -4.6858 | -7.2907 | 31.8634 | 31.6616 | 31.3619 | 30.4631 | 29.3005 | 28.0501 | 26.6397 | 24.7667 | 22.7232 | 18.1407 | 13.7469 | 10.7734 | 8.5555 | 29.6176 | 28.8297 | 27.9614 | 26.4333 | 24.7078 | 22.8929 | 20.8849 | 18.3275 | 15.5533 | 8.7598 | 1.7383 | -2.4007 | -4.5823
|  | LANGLEY BSP | CT |  |  | 30.4681 | 30.0084 | 29.2949 | 28.1862 | 26.8907 | 25.5414 | 24.0219 | 22.1759 | 19.3555 | 11.6435 | 1.3217 | -4.6858 | -7.2907 | 31.8634 | 31.6632 | 31.3619 | 30.9242 | 29.9443 | 28.9226 | 27.755 | 26.2928 | 24.2466 | 19.1837 | 13.7469 | 10.7734 | 8.5555 | 30.0739 | 29.5975 | 28.8291 | 27.7222 | 26.4403 | 25.1079 | 23.6053 | 21.761 | 19.0002 | 11.7682 | 2.6892 | -2.4007 | -4.5823
|  | LANGLEY BSP | LW |  |  | 29.9189 | 29.1392 | 28.2848 | 26.6882 | 24.8839 | 22.9999 | 20.9228 | 18.3272 | 15.5055 | 8.1944 | 0.39622 | -2.0002 | -2.8067 | 31.8876 | 31.6616 | 31.3817 | 30.4631 | 29.3005 | 28.0501 | 26.6397 | 24.7667 | 22.7232 | 18.1407 | 13.8868 | 12.95 | 12.6262 | 29.6176 | 28.8297 | 27.9614 | 26.4333 | 24.7078 | 22.8929 | 20.8849 | 18.3275 | 15.5533 | 8.7598 | 1.7383 | -0.30334 | -0.98194
|  | LANGLEY BSP | ST |  |  | 31.0289 | 30.8131 | 30.5486 | 30.011 | 29.3484 | 28.6831 | 27.8998 | 26.956 | 25.8704 | 21.3946 | 13.72 | 10.5087 | 8.3284 | 32.0519 | 31.9382 | 31.7863 | 31.4764 | 31.0942 | 30.7449 | 30.3057 | 29.6289 | 28.745 | 24.8893 | 18.777 | 16.3446 | 14.2532 | 30.651 | 30.4274 | 30.1516 | 29.5954 | 28.9212 | 28.2477 | 27.4583 | 26.5111 | 25.4609 | 20.9948 | 13.4884 | 10.5819 | 8.7532
|  | LANGLEY BSP | FS |  |  | 31.0833 | 30.8763 | 30.6327 | 30.1837 | 29.6361 | 29.14 | 28.4843 | 27.7338 | 26.8133 | 23.3962 | 16.3031 | 12.945 | 11.8249 | 32.0506 | 31.9327 | 31.7803 | 31.5058 | 31.1661 | 30.8677 | 30.4819 | 30.0413 | 29.4843 | 26.4362 | 19.7922 | 15.8491 | 12.0949 | 32.0506 | 31.9327 | 31.7803 | 31.5058 | 31.1661 | 30.8677 | 30.4819 | 30.0413 | 29.4843 | 26.4362 | 19.7922 | 15.8491 | 12.0949
IVER 132KV | LONGFORD | LONGFORD | MINIMUM HEADROOM | TQ 03910 76751 | YES | 77.827 | 77.2413 | 76.5405 | 75.7036 | 74.7347 | 73.5763 | 72.2635 | 70.6079 | 68.609 | 61.6387 | 53.0728 | 51.5089 | 50.654 | 80.6767 | 80.4054 | 80.104 | 79.7109 | 79.275 | 78.7729 | 78.067 | 77.1417 | 76.0192 | 70.7661 | 64.6787 | 63.6413 | 63.0148 | 81.0459 | 80.9409 | 80.8356 | 80.7151 | 80.5843 | 80.4411 | 80.2775 | 78.7209 | 76.6202 | 69.5307 | 61.3737 | 59.9193 | 59.1228
|  | LONGFORD | CT |  |  | 77.8319 | 77.3284 | 76.6935 | 75.9725 | 75.1673 | 74.2732 | 73.2831 | 72.1274 | 70.6457 | 65.6177 | 56.9313 | 53.7546 | 52.1997 | 80.7328 | 80.4983 | 80.2268 | 79.9073 | 79.5595 | 79.0836 | 78.5244 | 77.8577 | 77.0273 | 73.6996 | 67.2711 | 65.448 | 64.4772 | 85.4564 | 85.1438 | 84.7269 | 84.2264 | 83.6865 | 83.0157 | 81.9911 | 80.8315 | 79.2608 | 73.9939 | 65.0686 | 62.1266 | 60.6898
|  | LONGFORD | LW |  |  | 77.827 | 77.2413 | 76.5405 | 75.7036 | 74.7347 | 73.5763 | 72.2635 | 70.6079 | 68.609 | 61.6387 | 53.0728 | 51.5089 | 50.654 | 80.6767 | 80.4054 | 80.104 | 79.7109 | 79.275 | 78.7729 | 78.067 | 77.1417 | 76.0192 | 70.7661 | 64.6787 | 63.6413 | 63.0148 | 85.2992 | 84.8746 | 84.4048 | 83.75 | 83.0396 | 81.8889 | 80.4657 | 78.7209 | 76.6202 | 69.5307 | 61.3737 | 59.9193 | 59.1228
|  | LONGFORD | ST |  |  | 78.2984 | 78.1203 | 77.926 | 77.6647 | 77.2942 | 76.8032 | 76.2229 | 75.443 | 74.4209 | 70.3393 | 59.3214 | 53.9361 | 52.5512 | 80.9959 | 80.8799 | 80.7601 | 80.6035 | 80.4293 | 80.2258 | 79.9898 | 79.6753 | 79.0979 | 76.767 | 68.7053 | 64.5365 | 63.47 | 85.8432 | 85.6952 | 85.5353 | 85.3065 | 85.0557 | 84.7665 | 84.438 | 84.0142 | 83.2028 | 79.2785 | 68.6118 | 63.2798 | 61.8963
|  | LONGFORD | FS |  |  | 78.3374 | 78.1807 | 78.0152 | 77.8189 | 77.5998 | 77.2722 | 76.8808 | 76.3959 | 75.7824 | 73.663 | 66.0772 | 58.5609 | 56.4468 | 81.0459 | 80.9409 | 80.8356 | 80.7151 | 80.5843 | 80.4411 | 80.2775 | 80.0762 | 79.8239 | 78.6846 | 73.9403 | 68.085 | 66.4163 | 81.0459 | 80.9409 | 80.8356 | 80.7151 | 80.5843 | 80.4411 | 80.2775 | 80.0762 | 79.8239 | 78.6846 | 73.9403 | 68.085 | 66.4163
AMERSHAM | LOUDWATER BSP | LOUDWATER BSP | MINIMUM HEADROOM | SU 90644 91247 | YES | 10.8567 | -34.9479 | -37.7851 | -41.7203 | -45.8066 | -50.2438 | -55.0938 | -60.9744 | -66.5761 | -78.9965 | -94.3245 | -103.1867 | -109.7773 | 33.6071 | -10.5161 | -11.6712 | -13.2899 | -14.969 | -16.7878 | -18.8891 | -22.7249 | -26.328 | -33.5769 | -42.7905 | -51.4252 | -59.1244 | 19.2056 | -26.3229 | -28.9265 | -32.5295 | -36.2902 | -40.4049 | -44.9309 | -50.508 | -55.8139 | -67.3622 | -81.3824 | -88.9314 | -94.429
|  | LOUDWATER BSP | CT |  |  | 12.3147 | -32.9172 | -35.2828 | -38.0266 | -40.8864 | -43.9011 | -47.2266 | -51.0195 | -56.7779 | -69.6685 | -89.6523 | -103.1867 | -109.7773 | 34.107 | -9.8497 | -10.8746 | -12.0695 | -13.3142 | -14.6283 | -16.4222 | -19.1667 | -23.0307 | -31.1829 | -42.7905 | -51.4252 | -59.1244 | 20.4631 | -24.5612 | -26.7604 | -29.2987 | -31.958 | -34.7819 | -37.917 | -41.5316 | -46.9876 | -58.9882 | -77.0224 | -88.9314 | -94.429
|  | LOUDWATER BSP | LW |  |  | 10.8567 | -34.9479 | -37.7851 | -41.7203 | -45.8066 | -50.2438 | -55.0938 | -60.9744 | -66.5761 | -78.9965 | -94.3245 | -100.0174 | -102.9481 | 33.6071 | -10.5161 | -11.6712 | -13.2899 | -14.969 | -16.7878 | -18.8891 | -22.7249 | -26.328 | -33.5769 | -41.8744 | -44.4075 | -45.7115 | 19.2056 | -26.3229 | -28.9265 | -32.5295 | -36.2902 | -40.4049 | -44.9309 | -50.508 | -55.8139 | -67.3622 | -81.3824 | -86.3702 | -88.8925
|  | LOUDWATER BSP | ST |  |  | 14.6824 | 13.4889 | 12.3132 | -31.9851 | -33.398 | -34.9365 | -36.604 | -38.4733 | -40.3847 | -49.1331 | -64.5687 | -72.4056 | -77.4338 | 35.0308 | 34.4649 | 33.9093 | -9.669 | -10.321 | -11.0347 | -11.8148 | -12.6976 | -13.6452 | -19.6728 | -31.876 | -38.9751 | -46.1939 | 22.7489 | 21.7175 | 20.6635 | -23.5281 | -24.8378 | -26.2757 | -27.8459 | -29.6294 | -31.445 | -39.918 | -54.5852 | -61.6433 | -66.0137
|  | LOUDWATER BSP | FS |  |  | 14.8951 | 13.8759 | 12.927 | 11.7305 | 10.4792 | 9.1799 | 7.714 | 6.1576 | 4.3477 | -2.3414 | -19.9432 | -28.6837 | -32.4041 | 35.1075 | 34.5928 | 34.1056 | 33.5352 | 32.9357 | 32.3023 | 31.5969 | 30.8329 | 29.9048 | 26.2002 | 11.1045 | 0.27171 | -11.4594 | 35.1075 | 34.5928 | 34.1056 | 33.5352 | 32.9357 | 32.3023 | 31.5969 | 30.8329 | 29.9048 | 26.2002 | 11.1045 | 0.27171 | -11.4594
MANNINGTON GSP | LYTCHETT | LYTCHETT | MINIMUM HEADROOM | SY 97796 94214 | YES | 25.1253 | 16.2636 | 15.4466 | 14.4899 | 11.5898 | 7.518 | 3.0451 | -2.5047 | -8.1621 | -21.0709 | -39.9208 | -51.9041 | -60.8281 | 45.7485 | 36.7751 | 35.2764 | 33.1766 | 30.6025 | 27.8301 | 24.7461 | 20.8444 | 17.0188 | 8.6492 | -2.1327 | -13.1523 | -24.7617 | 28.7285 | 18.5262 | 16.3517 | 12.9505 | 9.1137 | 5.1013 | 0.74785 | -4.4317 | -9.6181 | -22.4666 | -39.5693 | -49.9701 | -57.7888
|  | LYTCHETT | CT |  |  | 25.1253 | 16.2772 | 15.4466 | 14.5588 | 13.3488 | 12.1157 | 9.813 | 5.8465 | 0.27284 | -12.5257 | -34.1125 | -51.9041 | -60.8281 | 45.7485 | 36.9881 | 36.1304 | 34.3875 | 32.2746 | 30.0486 | 27.5388 | 24.6084 | 20.7282 | 11.9477 | -1.4352 | -11.7407 | -19.7343 | 30.3752 | 20.895 | 19.2235 | 16.9235 | 14.2532 | 11.4728 | 8.3972 | 4.9157 | -0.13182 | -12.6722 | -34.2102 | -49.9701 | -57.7888
|  | LYTCHETT | LW |  |  | 25.1582 | 16.2636 | 15.4477 | 14.4899 | 11.5898 | 7.518 | 3.0451 | -2.5047 | -8.1621 | -21.0709 | -39.9208 | -48.9678 | -54.5393 | 45.8206 | 36.7751 | 35.2764 | 33.1766 | 30.6025 | 27.8301 | 24.7461 | 20.8444 | 17.0188 | 8.6492 | -2.1327 | -7.2976 | -10.3953 | 28.7285 | 18.5262 | 16.3517 | 12.9505 | 9.1137 | 5.1013 | 0.74785 | -4.4317 | -9.6181 | -22.4666 | -39.5693 | -47.6624 | -52.5564
|  | LYTCHETT | ST |  |  | 25.6834 | 17.0903 | 16.6109 | 16.0099 | 15.1 | 14.1839 | 13.1855 | 12.0403 | 9.9603 | 0.91125 | -18.1674 | -28.0191 | -33.962 | 46.1921 | 37.6338 | 37.2009 | 36.6639 | 35.8036 | 34.6616 | 33.1499 | 31.405 | 28.7622 | 18.7751 | 3.1303 | -5.7885 | -13.1198 | 31.688 | 22.8017 | 21.9742 | 20.7855 | 19.2574 | 17.6868 | 15.9819 | 14.0933 | 11.1811 | 0.57742 | -16.9277 | -26.9278 | -33.0699
|  | LYTCHETT | FS |  |  | 25.7072 | 17.1239 | 16.6764 | 16.1588 | 12.7968 | 15.5823 | 12.168 | 5.9016 | 4.6326 | -0.8596 | -20.9665 | -31.9671 | -36.997 | 46.2004 | 37.6423 | 37.2262 | 36.7544 | 33.4172 | 36.0722 | 32.1281 | 25.3158 | 23.3355 | 16.2695 | -0.75718 | -13.1523 | -24.7617 | 46.2004 | 37.6423 | 37.2262 | 36.7544 | 33.4172 | 36.0722 | 32.1281 | 25.3158 | 23.3355 | 16.2695 | -0.75718 | -13.1523 | -24.7617
BRAMLEY (FLEE) | MAIDENHEAD BSP | MAIDENHEAD BSP | MINIMUM HEADROOM | SU 86592 79883 | YES | 45.0905 | 42.7756 | 40.1661 | 36.4949 | 32.5082 | 28.2934 | 23.4299 | 17.6087 | 11.718 | -2.2151 | -17.1158 | -24.7975 | -30.8638 | 63.3747 | 62.2111 | 60.9045 | 59.1361 | 57.2114 | 55.1554 | 52.5471 | 49.1613 | 45.7454 | 37.7988 | 27.4197 | 18.0502 | 8.3317 | 51.9573 | 50.0218 | 47.8524 | 44.653 | 41.1994 | 37.5663 | 33.4193 | 28.3269 | 22.9155 | 10.3156 | -3.1841 | -9.9293 | -15.1711
|  | MAIDENHEAD BSP | CT |  |  | 46.226 | 44.3417 | 42.1202 | 39.4287 | 36.4529 | 33.4446 | 29.8969 | 25.7934 | 19.8694 | 5.7552 | -12.8912 | -24.7975 | -30.8638 | 63.644 | 62.5481 | 61.2786 | 59.8104 | 58.1916 | 56.5233 | 54.2543 | 51.6114 | 47.9797 | 39.148 | 27.4197 | 18.0502 | 8.3317 | 53.1314 | 51.6276 | 49.8607 | 47.6026 | 45.1177 | 42.6196 | 39.4521 | 35.6996 | 30.2581 | 17.4897 | 0.77054 | -9.9293 | -15.1711
|  | MAIDENHEAD BSP | LW |  |  | 45.0905 | 42.7756 | 40.1661 | 36.4949 | 32.5082 | 28.2934 | 23.4299 | 17.6087 | 11.718 | -2.2151 | -17.1158 | -22.6472 | -25.361 | 63.3747 | 62.2111 | 60.9045 | 59.1361 | 57.2114 | 55.1554 | 52.5471 | 49.1613 | 45.7454 | 37.7988 | 29.6207 | 27.0497 | 25.7384 | 51.9573 | 50.0218 | 47.8524 | 44.653 | 41.1994 | 37.5663 | 33.4193 | 28.3269 | 22.9155 | 10.3156 | -3.1841 | -7.9915 | -10.2914
|  | MAIDENHEAD BSP | ST |  |  | 48.1713 | 47.2292 | 46.0935 | 44.7329 | 43.2083 | 41.63 | 39.761 | 37.5556 | 35.2036 | 26.0418 | 11.7439 | 4.5567 | -0.14821 | 64.6267 | 64.0005 | 63.2702 | 62.4278 | 61.491 | 60.5015 | 59.3391 | 57.9674 | 56.5152 | 49.9165 | 38.063 | 30.1861 | 21.1212 | 54.7346 | 54.0223 | 53.1759 | 52.1289 | 50.9621 | 49.7438 | 48.3079 | 46.6102 | 44.6407 | 36.187 | 22.7875 | 16.366 | 12.3115
|  | MAIDENHEAD BSP | FS |  |  | 48.3491 | 47.5261 | 46.5988 | 45.4668 | 44.1771 | 42.8827 | 41.2891 | 39.5128 | 37.439 | 30.506 | 15.6597 | 7.5984 | 3.9489 | 64.6727 | 64.0745 | 63.4119 | 62.6723 | 61.8347 | 60.9645 | 59.9138 | 58.7236 | 57.3149 | 51.9566 | 38.1572 | 25.7238 | 10.1355 | 64.6727 | 64.0745 | 63.4119 | 62.6723 | 61.8347 | 60.9645 | 59.9138 | 58.7236 | 57.3149 | 51.9566 | 38.1572 | 25.7238 | 10.1355
MANNINGTON GSP | MANNINGTON BSP | MANNINGTON BSP | MINIMUM HEADROOM | SU 07523 05221 | YES | -18.0984 | -22.5335 | -27.1291 | -33.5135 | -40.8153 | -49.0673 | -58.2966 | -69.177 | -79.5708 | -105.3465 | -136.2007 | -151.264 | -163.0962 | 2.3956 | 0.53686 | -1.3155 | -3.9811 | -7.2155 | -13.4903 | -21.1344 | -34.8039 | -37.9217 | -47.9815 | -75.3312 | -94.3809 | -109.3294 | -9.1601 | -13.1616 | -17.2869 | -23.1809 | -29.9264 | -37.4923 | -45.9254 | -55.8334 | -65.3017 | -89.1129 | -117.8936 | -131.254 | -141.9181
|  | MANNINGTON BSP | CT |  |  | -15.3101 | -18.4788 | -22.2537 | -26.7694 | -32.0403 | -38.1192 | -45.0377 | -52.8156 | -63.0274 | -88.241 | -125.6957 | -151.264 | -163.0962 | 3.1514 | 1.6146 | -0.024438 | -2.1442 | -4.7206 | -7.6633 | -10.986 | -14.9448 | -21.7018 | -37.6002 | -59.8953 | -75.3955 | -86.3231 | -6.5328 | -9.3364 | -12.6686 | -16.8049 | -21.6388 | -27.1694 | -33.4441 | -40.4926 | -49.7481 | -72.8852 | -108.0202 | -131.254 | -141.9181
|  | MANNINGTON BSP | LW |  |  | -18.0984 | -22.5335 | -27.1291 | -33.5135 | -40.8153 | -49.0673 | -58.2966 | -69.177 | -79.5708 | -105.3465 | -136.2007 | -149.0467 | -155.9745 | 2.3956 | 0.53686 | -1.3155 | -3.9811 | -7.2155 | -10.8799 | -14.9698 | -21.4037 | -28.0945 | -43.6905 | -62.2562 | -70.3892 | -74.7268 | -9.1601 | -13.1616 | -17.2869 | -23.1809 | -29.9264 | -37.4923 | -45.9254 | -55.8334 | -65.3017 | -89.1129 | -117.8936 | -129.7965 | -136.186
|  | MANNINGTON BSP | ST |  |  | -12.6534 | -14.5159 | -16.4231 | -18.9657 | -22.1369 | -25.7988 | -29.9571 | -34.5852 | -41.0676 | -65.001 | -100.2609 | -117.563 | -127.0047 | 4.1537 | 3.1098 | 2.1189 | 0.70809 | -1.1266 | -3.2388 | -5.6408 | -8.3357 | -12.8402 | -28.4238 | -56.4082 | -70.7917 | -81.0397 | -4.1691 | -5.7543 | -7.4115 | -9.7359 | -12.642 | -15.9578 | -19.7111 | -23.9002 | -29.9626 | -52.1009 | -85.2413 | -101.5518 | -110.5587
|  | MANNINGTON BSP | FS |  |  | -12.2489 | -13.9368 | -15.572 | -18.0766 | -26.4437 | -35.2117 | -44.4728 | -59.8203 | -64.9177 | -82.1167 | -117.8045 | -137.2752 | -145.4036 | 4.3005 | 3.3145 | 2.4068 | 1.0172 | -6.1164 | -13.4903 | -21.1344 | -34.8039 | -37.9217 | -47.9815 | -75.3312 | -94.3809 | -109.3294 | 4.3005 | 3.3145 | 2.4068 | 1.0172 | -6.1164 | -13.4903 | -21.1344 | -34.8039 | -37.9217 | -47.9815 | -75.3312 | -94.3809 | -109.3294
BOTLEY WOOD GSP | NETLEY COMMON BSP | NETLEY COMMON BSP | MINIMUM HEADROOM | SU 47559 12003 | YES | 0.46435 | -4.0632 | -8.4995 | -15.2311 | -22.3203 | -30.0323 | -38.2444 | -48.2103 | -58.465 | -85.0869 | -119.8813 | -147.5805 | -167.8874 | 35.6146 | 33.0939 | 30.4549 | 26.7876 | 22.9033 | 18.4836 | 13.5067 | 7.171 | 0.63459 | -15.3393 | -37.6968 | -59.4624 | -80.6041 | 0.28408 | -3.5025 | -7.2257 | -13.1736 | -19.3986 | -26.1082 | -33.2183 | -42.1434 | -51.4085 | -75.676 | -107.094 | -131.6018 | -148.7161
|  | NETLEY COMMON BSP | CT |  |  | 2.8177 | -0.38499 | -4.1803 | -8.9437 | -13.9766 | -19.4298 | -25.2519 | -31.9051 | -42.0367 | -69.5939 | -113.8238 | -147.5805 | -167.8874 | 36.2919 | 34.21 | 31.572 | 28.5595 | 25.371 | 21.6617 | 17.5961 | 12.8203 | 6.1009 | -11.7344 | -37.6968 | -59.4624 | -80.6041 | 2.6585 | 0.063402 | -2.9637 | -7.0058 | -11.2515 | -15.8406 | -20.9558 | -26.9094 | -36.0525 | -61.1329 | -101.4915 | -131.6018 | -148.7161
|  | NETLEY COMMON BSP | LW |  |  | 0.46435 | -4.0632 | -8.4995 | -15.2311 | -22.3203 | -30.0323 | -38.2444 | -48.2103 | -58.465 | -85.0869 | -119.8813 | -138.658 | -150.9663 | 35.6146 | 33.0939 | 30.4549 | 26.7876 | 22.9033 | 18.4836 | 13.5067 | 7.171 | 0.63459 | -15.3393 | -34.0363 | -42.9086 | -49.0458 | 0.28408 | -3.5025 | -7.2257 | -13.1736 | -19.3986 | -26.1082 | -33.2183 | -42.1434 | -51.4085 | -75.676 | -107.094 | -123.3927 | -133.6661
|  | NETLEY COMMON BSP | ST |  |  | 6.2847 | 4.5861 | 3.0241 | 0.80613 | -1.565 | -4.1795 | -6.9855 | -10.2334 | -13.5513 | -28.3582 | -62.6191 | -83.1397 | -97.9196 | 38.2401 | 37.0312 | 35.91 | 34.4059 | 32.734 | 30.7868 | 28.6662 | 26.1743 | 23.6799 | 11.7412 | -15.1548 | -33.2818 | -52.5575 | 5.5533 | 4.2329 | 3.0072 | 1.2269 | -0.6597 | -2.7494 | -4.9982 | -7.618 | -10.3914 | -23.3361 | -54.6108 | -72.3357 | -84.6168
|  | NETLEY COMMON BSP | FS |  |  | 6.5967 | 5.0078 | 3.6183 | 1.742 | -0.13968 | -2.1805 | -4.4378 | -6.9411 | -9.811 | -20.8135 | -52.099 | -73.4835 | -85.0039 | 38.3187 | 37.1132 | 36.0279 | 34.7243 | 33.3915 | 31.8165 | 30.0456 | 28.0276 | 25.5879 | 15.8734 | -12.9913 | -41.3333 | -75.5691 | 38.3187 | 37.1132 | 36.0279 | 34.7243 | 33.3915 | 31.8165 | 30.0456 | 28.0276 | 25.5879 | 15.8734 | -12.9913 | -41.3333 | -75.5691
MELKSHAM GSP | NORRINGTON | NORRINGTON | MINIMUM HEADROOM | ST 88273 64983 | YES | -89.5647 | -251.7089 | -260.9815 | -275.9483 | -283.322 | -291.2017 | -299.6489 | -310.1487 | -320.9782 | -344.9094 | -371.6149 | -381.3978 | -386.0231 | -20.9496 | -182.2765 | -190.731 | -205.1645 | -209.9258 | -215.1168 | -220.719 | -227.9307 | -235.3938 | -251.1492 | -268.0654 | -274.1339 | -277.0683 | -80.475 | -242.9089 | -252.3916 | -268.998 | -275.8869 | -283.0223 | -290.496 | -299.138 | -308.0715 | -331.2139 | -359.6498 | -370.8097 | -376.1153
|  | NORRINGTON | CT |  |  | -86.3698 | -93.8468 | -102.2052 | -115.0518 | -120.179 | -125.5948 | -131.4859 | -138.3557 | -148.8367 | -173.4039 | -206.7258 | -228.5847 | -238.3216 | -19.6734 | -27.2564 | -35.6191 | -49.1658 | -52.9497 | -56.9891 | -61.3975 | -66.6222 | -74.1186 | -91.4755 | -114.4227 | -131.6427 | -146.1159 | -76.3944 | -84.1404 | -92.3097 | -106.4604 | -110.7893 | -115.2761 | -120.0259 | -125.3048 | -133.688 | -155.8818 | -193.1113 | -219.065 | -230.7217
|  | NORRINGTON | LW |  |  | -89.5647 | -251.7089 | -260.9815 | -275.9483 | -283.322 | -291.2017 | -299.6489 | -310.1487 | -320.9782 | -344.9094 | -371.6149 | -381.3978 | -386.0231 | -20.9496 | -182.2765 | -190.731 | -205.1645 | -209.9258 | -215.1168 | -220.719 | -227.9307 | -235.3938 | -251.1492 | -268.0654 | -274.1339 | -277.0683 | -80.475 | -242.9089 | -252.3916 | -268.998 | -275.8869 | -283.0223 | -290.496 | -299.138 | -308.0715 | -331.2139 | -359.6498 | -370.8097 | -376.1153
|  | NORRINGTON | ST |  |  | -82.9526 | -88.896 | -94.9014 | -105.4484 | -108.1937 | -111.1065 | -114.2366 | -117.789 | -122.2037 | -140.617 | -172.7883 | -187.5674 | -196.3921 | -17.41 | -23.9496 | -30.5355 | -42.5111 | -44.6596 | -47.0652 | -49.6557 | -52.6335 | -56.3635 | -71.8785 | -99.2658 | -114.2744 | -128.2012 | -73.841 | -80.3974 | -86.9528 | -99.0394 | -101.2725 | -103.5862 | -106.0008 | -108.7024 | -112.5794 | -127.0711 | -155.1193 | -172.178 | -183.114
|  | NORRINGTON | FS |  |  | -82.5586 | -88.3268 | -94.0826 | -104.3787 | -105.9495 | -110.6482 | -115.6045 | -123.2111 | -127.0025 | -140.7117 | -175.2867 | -193.2235 | -200.6352 | -17.2719 | -23.7595 | -30.2508 | -42.0255 | -43.0888 | -47.2855 | -51.7236 | -58.8513 | -62.0171 | -73.7638 | -104.4267 | -127.297 | -150.6181 | -17.2719 | -23.7595 | -30.2508 | -42.0255 | -43.0888 | -47.2855 | -51.7236 | -58.8513 | -62.0171 | -73.7638 | -104.4267 | -127.297 | -150.6181
NORTH HYDE GSP | NORTH HYDE 22kV | NORTH HYDE 22kV | MINIMUM HEADROOM | TQ 10367 79001 | YES | 25.0859 | 16.1979 | 7.2403 | -2.1821 | -3.5278 | -4.9396 | -6.4098 | -8.1999 | -10.072 | -15.9808 | -25.9758 | -36.5522 | -43.8558 | 30.0864 | 19.555 | 8.9389 | -1.7925 | -2.4476 | -3.2624 | -4.1128 | -5.0236 | -6.212 | -10.3173 | -19.1555 | -29.1691 | -51.1566 | 25.3443 | 14.4084 | 3.3985 | -7.9786 | -9.2705 | -10.6614 | -12.0963 | -13.7785 | -15.5525 | -21.0938 | -29.7057 | -38.2461 | -51.1566
|  | NORTH HYDE 22kV | CT |  |  | 25.3935 | 16.698 | 7.8226 | -1.284 | -2.306 | -3.4184 | -4.5922 | -5.8654 | -7.7489 | -13.7773 | -25.9758 | -36.5522 | -43.8558 | 30.0864 | 19.555 | 8.9389 | -1.7925 | -2.4476 | -3.2624 | -4.1128 | -5.0236 | -6.212 | -10.3173 | -19.1555 | -29.1691 | -41.7224 | 25.5565 | 14.8384 | 3.8565 | -7.2765 | -8.2851 | -9.3835 | -10.5387 | -11.7502 | -13.5077 | -19.0995 | -29.5459 | -38.2461 | -44.3021
|  | NORTH HYDE 22kV | LW |  |  | 25.0859 | 16.1979 | 7.2403 | -2.1821 | -3.5278 | -4.9396 | -6.4098 | -8.1999 | -10.072 | -15.9808 | -25.8146 | -32.9971 | -38.4115 | 30.0948 | 19.5574 | 8.9884 | -1.7656 | -2.3555 | -3.0142 | -3.8042 | -4.7296 | -5.7049 | -8.8917 | -14.2022 | -17.6795 | -20.4426 | 25.3443 | 14.4084 | 3.3985 | -7.9786 | -9.2705 | -10.6614 | -12.0963 | -13.7785 | -15.5525 | -21.0938 | -29.7057 | -35.5581 | -39.946
|  | NORTH HYDE 22kV | ST |  |  | 25.9367 | 17.4979 | 9.0399 | 0.45836 | -0.0025185 | -0.48437 | -0.96509 | -1.4781 | -2.0315 | -4.4076 | -12.4183 | -18.9162 | -23.9809 | 30.2895 | 19.9134 | 9.5117 | -0.99791 | -1.3337 | -1.6987 | -2.2177 | -2.8067 | -3.412 | -5.7958 | -13.3347 | -21.9867 | -33.7043 | 26.1379 | 15.6727 | 5.18 | -5.4735 | -5.9669 | -6.4917 | -7.0255 | -7.5988 | -8.1679 | -10.5428 | -17.8763 | -23.2778 | -27.3443
|  | NORTH HYDE 22kV | FS |  |  | 25.9765 | 17.5465 | 9.106 | 0.61066 | 0.25164 | -0.13252 | -0.50558 | -0.87488 | -1.2926 | -2.8913 | -8.8229 | -14.7009 | -18.7026 | 30.284 | 19.8985 | 9.4864 | -1.029 | -1.3745 | -1.82 | -2.3937 | -3.0238 | -3.744 | -6.499 | -15.1268 | -28.9747 | -51.1566 | 30.284 | 19.8985 | 9.4864 | -1.029 | -1.3745 | -1.82 | -2.3937 | -3.0238 | -3.744 | -6.499 | -15.1268 | -28.9747 | -51.1566
COWLEY GSP | OXFORD BSP | OXFORD BSP | MINIMUM HEADROOM | SP 50054 05983 | NO | -17.5427 | -19.8641 | -22.4304 | -26.2653 | -30.4677 | -34.8598 | -39.6856 | -45.1454 | -50.1716 | -63.4317 | -80.0912 | -91.2127 | -99.6576 | 20.6421 | 19.2672 | 17.6233 | 15.6306 | 13.3464 | 10.8927 | 8.155 | 4.854 | 1.7946 | -6.2468 | -21.0047 | -34.6736 | -58.7117 | -5.5411 | -7.6182 | -9.9807 | -13.4019 | -17.1352 | -21.0831 | -25.4342 | -30.4833 | -35.1409 | -47.4137 | -62.4281 | -71.4677 | -78.659
|  | OXFORD BSP | CT |  |  | -16.3468 | -18.1932 | -20.3435 | -23.2052 | -26.3711 | -29.5408 | -33.1121 | -37.0171 | -41.921 | -54.8575 | -75.7671 | -91.2127 | -99.6576 | 20.6703 | 19.2866 | 17.6233 | 15.7121 | 13.5839 | 11.3753 | 8.8723 | 6.0787 | 2.7503 | -6.2468 | -21.0047 | -34.6736 | -51.2651 | -4.8512 | -6.1688 | -8.1723 | -10.7406 | -13.5804 | -16.4377 | -19.6545 | -23.2011 | -27.736 | -39.6869 | -58.3691 | -71.4677 | -78.659
|  | OXFORD BSP | LW |  |  | -17.5427 | -19.8641 | -22.4304 | -26.2653 | -30.4677 | -34.8598 | -39.6856 | -45.1454 | -50.1716 | -63.4317 | -80.0912 | -87.861 | -93.0447 | 20.6421 | 19.2672 | 17.6923 | 15.6306 | 13.3464 | 10.8927 | 8.155 | 4.854 | 1.7946 | -6.0784 | -15.2058 | -18.7241 | -21.147 | -5.5411 | -7.6182 | -9.9807 | -13.4019 | -17.1352 | -21.0831 | -25.4342 | -30.4833 | -35.1409 | -47.4137 | -62.4281 | -68.8288 | -73.058
|  | OXFORD BSP | ST |  |  | -14.47 | -15.4121 | -16.4836 | -17.9095 | -19.5437 | -21.2408 | -23.1792 | -25.3309 | -27.2477 | -34.3979 | -50.2919 | -59.8837 | -65.9132 | 21.8957 | 21.0815 | 20.103 | 18.9162 | 17.56 | 16.121 | 14.4783 | 12.6435 | 10.999 | 4.5786 | -10.2676 | -22.8834 | -38.1399 | -4.1139 | -4.6448 | -5.294 | -6.0092 | -7.2773 | -8.7961 | -10.5239 | -12.4541 | -14.1708 | -20.8786 | -35.7181 | -44.193 | -49.2732
|  | OXFORD BSP | FS |  |  | -14.3231 | -15.1714 | -16.1102 | -17.3358 | -18.734 | -20.2052 | -21.8973 | -23.6452 | -25.3178 | -30.7681 | -44.9656 | -55.3419 | -60.528 | 21.8883 | 21.0676 | 20.1041 | 19.0184 | 17.7674 | 16.4011 | 14.8193 | 13.1104 | 11.4183 | 5.3705 | -11.1373 | -30.8451 | -58.7117 | 21.8883 | 21.0676 | 20.1041 | 19.0184 | 17.7674 | 16.4011 | 14.8193 | 13.1104 | 11.4183 | 5.3705 | -11.1373 | -30.8451 | -58.7117
MANNINGTON GSP | POOLE PS (HAMWORTHY) | POOLE PS (HAMWORTHY) | MINIMUM HEADROOM | SZ 00203 90789 | YES | 42.0675 | 41.0564 | 40.2626 | 38.7042 | 36.8852 | 35.0319 | 33.1135 | 30.9474 | 28.6723 | 22.6468 | 15.6277 | 10.3335 | 7.0969 | 37.6265 | 37.3072 | 37.0019 | 36.5871 | 35.5344 | 33.8827 | 32.2239 | 29.2035 | 28.5662 | 26.6445 | 22.546 | 15.7912 | 7.8831 | 37.8395 | 37.4419 | 36.7381 | 35.3912 | 33.7988 | 32.1608 | 30.4571 | 28.5201 | 26.3904 | 20.9327 | 14.5929 | 9.8744 | 7.0424
|  | POOLE PS (HAMWORTHY) | CT |  |  | 42.3838 | 41.5487 | 40.8503 | 39.6012 | 38.1197 | 36.6274 | 35.0843 | 33.3923 | 31.1705 | 25.0696 | 16.4716 | 10.3335 | 7.0969 | 37.6265 | 37.3072 | 37.0019 | 36.5871 | 36.0219 | 35.44 | 34.8405 | 34.1696 | 33.4448 | 30.7713 | 25.0102 | 20.1042 | 15.4106 | 38.5706 | 37.8796 | 37.2571 | 36.184 | 34.8931 | 33.5815 | 32.2178 | 30.7164 | 28.6819 | 23.1802 | 15.3854 | 9.8744 | 7.0424
|  | POOLE PS (HAMWORTHY) | LW |  |  | 42.0675 | 41.0564 | 40.2626 | 38.7042 | 36.8852 | 35.0319 | 33.1135 | 30.9474 | 28.6723 | 22.6468 | 15.6277 | 12.0173 | 9.9191 | 37.645 | 37.3154 | 37.0159 | 36.5903 | 35.9873 | 35.3426 | 34.6695 | 33.8718 | 32.9748 | 29.7132 | 25.7114 | 23.8524 | 22.5511 | 38.2946 | 37.4419 | 36.7381 | 35.3912 | 33.7988 | 32.1608 | 30.4571 | 28.5201 | 26.3904 | 20.9327 | 14.5929 | 11.3345 | 9.4832
|  | POOLE PS (HAMWORTHY) | ST |  |  | 42.939 | 42.457 | 42.1282 | 41.4668 | 40.6216 | 39.7692 | 38.8988 | 37.9437 | 36.4858 | 32.0516 | 24.285 | 20.0496 | 17.5844 | 37.8254 | 37.6019 | 37.4229 | 37.1142 | 36.6576 | 36.1875 | 35.7043 | 35.1642 | 34.1534 | 30.9132 | 25.1614 | 22.1023 | 17.6868 | 39.0908 | 38.7251 | 38.4523 | 37.9111 | 37.1958 | 36.4635 | 35.7102 | 34.8793 | 33.5529 | 29.4102 | 22.3083 | 18.4026 | 16.2108
|  | POOLE PS (HAMWORTHY) | FS |  |  | 43.0065 | 42.5574 | 42.256 | 41.6818 | 39.7129 | 37.7356 | 35.7531 | 32.3893 | 31.379 | 28.4778 | 22.4856 | 18.0762 | 16.3439 | 37.8395 | 37.62 | 37.4479 | 37.1756 | 35.5344 | 33.8827 | 32.2239 | 29.2035 | 28.5662 | 26.6445 | 22.546 | 15.7912 | 7.8831 | 37.8395 | 37.62 | 37.4479 | 37.1756 | 35.5344 | 33.8827 | 32.2239 | 29.2035 | 28.5662 | 26.6445 | 22.546 | 15.7912 | 7.8831
LOVEDEAN GSP | PORTSMOUTH BSP | PORTSMOUTH BSP | MINIMUM HEADROOM | SZ 63405 99685 | YES | -18.4598 | -21.0761 | -24.0768 | -28.9935 | -34.286 | -39.4769 | -45.0395 | -51.6246 | -58.5591 | -81.2927 | -112.296 | -131.8351 | -145.8209 | -12.5655 | -14.3962 | -16.7103 | -19.7822 | -23.127 | -26.5103 | -30.2471 | -34.5899 | -39.841 | -58.3925 | -97.2707 | -174.8385 | -310.168 | -14.5645 | -16.8183 | -19.4046 | -23.5382 | -28.0098 | -32.4656 | -37.2658 | -43.0149 | -49.1175 | -69.5667 | -97.268 | -174.8385 | -310.168
|  | PORTSMOUTH BSP | CT |  |  | -17.1751 | -19.0441 | -21.6717 | -25.4344 | -29.5142 | -33.2866 | -37.3666 | -42.1575 | -48.8846 | -70.8304 | -107.8263 | -131.8351 | -145.8209 | -12.5655 | -14.3962 | -16.7103 | -19.7822 | -23.127 | -26.5103 | -30.2471 | -34.5899 | -39.841 | -58.3925 | -97.2707 | -143.7467 | -211.48 | -13.5219 | -15.1935 | -17.5207 | -20.7331 | -24.2253 | -27.5145 | -31.0859 | -35.3015 | -41.1329 | -60.1955 | -92.8001 | -113.0039 | -124.3524
|  | PORTSMOUTH BSP | LW |  |  | -18.4598 | -21.0761 | -24.0768 | -28.9935 | -34.286 | -39.4769 | -45.0395 | -51.6246 | -58.5591 | -81.2927 | -112.296 | -125.6395 | -134.3101 | -11.8436 | -13.2368 | -14.8523 | -17.3429 | -20.029 | -22.7128 | -25.6058 | -29.1079 | -32.8327 | -45.1617 | -62.1234 | -68.6156 | -72.9467 | -14.5645 | -16.8183 | -19.4046 | -23.5382 | -28.0098 | -32.4656 | -37.2658 | -43.0149 | -49.1175 | -69.5667 | -97.268 | -108.5698 | -115.7541
|  | PORTSMOUTH BSP | ST |  |  | -15.1489 | -16.0613 | -17.1736 | -18.8419 | -20.6809 | -22.3669 | -24.2492 | -26.6304 | -29.2982 | -39.3268 | -63.7415 | -79.0102 | -88.8911 | -11.428 | -12.7253 | -14.2304 | -16.3023 | -18.5763 | -20.9405 | -23.6048 | -26.7553 | -30.0544 | -42.4017 | -77.3242 | -121.4302 | -187.5515 | -11.6121 | -12.3848 | -13.3347 | -14.7926 | -16.4175 | -17.9481 | -19.6612 | -21.7973 | -24.1495 | -33.142 | -55.1954 | -68.1671 | -76.1898
|  | PORTSMOUTH BSP | FS |  |  | -14.9531 | -15.8437 | -16.8919 | -18.1754 | -19.586 | -20.9113 | -22.3584 | -24.1161 | -26.1858 | -33.651 | -51.8145 | -66.567 | -74.2937 | -11.557 | -13.0396 | -14.7365 | -17.1146 | -19.8109 | -22.7426 | -26.0409 | -29.9319 | -34.2734 | -50.8349 | -96.9328 | -174.8385 | -310.168 | -11.557 | -13.0396 | -14.7365 | -17.1146 | -19.8109 | -22.7426 | -26.0409 | -29.9319 | -34.2734 | -50.8349 | -96.9328 | -174.8385 | -310.168
BRAMLEY (FLEE) | PYESTOCK BSP | PYESTOCK BSP | MINIMUM HEADROOM | SU 82940 54553 | YES | -20.1347 | -31.9923 | -43.8539 | -56.0494 | -56.8493 | -57.6942 | -58.6031 | -59.781 | -60.9946 | -63.291 | -66.3325 | -68.9572 | -70.5865 | -21.7002 | -36.3492 | -50.998 | -65.7123 | -66.2262 | -66.7905 | -67.4134 | -68.3664 | -69.2337 | -70.5744 | -73.1282 | -75.4248 | -78.1703 | -23.2334 | -38.0012 | -52.7631 | -67.8143 | -68.6161 | -69.4778 | -70.417 | -71.7446 | -72.9731 | -75.1152 | -77.8779 | -79.9201 | -81.2022
|  | PYESTOCK BSP | CT |  |  | -19.9136 | -31.6873 | -43.4671 | -55.3877 | -55.9032 | -56.4146 | -56.984 | -57.7593 | -59.0853 | -61.7153 | -65.7813 | -68.9572 | -70.5865 | -21.7002 | -36.3492 | -50.998 | -65.6929 | -66.1238 | -66.5738 | -67.0864 | -67.7916 | -68.7528 | -70.5264 | -73.1282 | -75.4248 | -77.8692 | -23.0891 | -37.7976 | -52.5041 | -67.3214 | -67.8781 | -68.4415 | -69.0777 | -69.9438 | -71.2353 | -73.7017 | -77.3489 | -79.9201 | -81.2022
|  | PYESTOCK BSP | LW |  |  | -20.1347 | -31.9923 | -43.8539 | -56.0494 | -56.8493 | -57.6942 | -58.6031 | -59.781 | -60.9946 | -63.291 | -66.3325 | -67.6991 | -68.4931 | -21.6777 | -36.312 | -50.9389 | -65.7123 | -66.2262 | -66.7905 | -67.4134 | -68.3664 | -69.2337 | -70.5744 | -72.1942 | -72.7973 | -73.1473 | -23.2334 | -38.0012 | -52.7631 | -67.8143 | -68.6161 | -69.4778 | -70.417 | -71.7446 | -72.9731 | -75.1152 | -77.8779 | -79.0562 | -79.7009
|  | PYESTOCK BSP | ST |  |  | -19.4841 | -31.0733 | -42.6668 | -54.3067 | -54.522 | -54.7584 | -55.0188 | -55.3239 | -55.6612 | -57.566 | -60.8478 | -62.4794 | -63.6114 | -21.3253 | -35.811 | -50.2969 | -64.8244 | -65.069 | -65.3413 | -65.6434 | -66.0023 | -66.3541 | -68.1277 | -71.034 | -72.9928 | -75.301 | -22.5842 | -37.0743 | -51.5621 | -66.1076 | -66.3678 | -66.6549 | -66.9715 | -67.3474 | -67.737 | -69.7453 | -72.8843 | -74.3963 | -75.3727
|  | PYESTOCK BSP | FS |  |  | -19.4523 | -31.0179 | -42.5665 | -54.147 | -54.3125 | -54.467 | -54.6544 | -54.8784 | -55.1464 | -56.2153 | -60.0817 | -61.5975 | -62.2815 | -21.3268 | -35.8047 | -50.2603 | -64.7374 | -64.9452 | -65.1499 | -65.4009 | -65.6948 | -66.0245 | -67.374 | -71.2695 | -74.2011 | -78.1703 | -21.3268 | -35.8047 | -50.2603 | -64.7374 | -64.9452 | -65.1499 | -65.4009 | -65.6948 | -66.0245 | -67.374 | -71.2695 | -74.2011 | -78.1703
BRAMLEY (FLEE) | READING BSP | READING BSP | MINIMUM HEADROOM | SU 74642 73856 | YES | 32.8694 | 29.1556 | 25.0104 | 18.1438 | 10.6228 | 2.5193 | -6.3804 | -17.2791 | -28.1215 | -55.243 | -88.8728 | -111.8475 | -128.6605 | 69.6217 | 67.6707 | 64.8949 | 61.194 | 56.9004 | 52.1117 | 46.7525 | 39.7625 | 32.8942 | 17.0167 | -11.071 | -37.0822 | -84.3471 | 33.0743 | 29.5939 | 25.7068 | 19.4247 | 12.5322 | 5.0484 | -3.2029 | -13.4376 | -23.5978 | -48.4982 | -78.9773 | -98.1068 | -111.8681
|  | READING BSP | CT |  |  | 35.0348 | 32.1602 | 28.7455 | 23.9436 | 18.5877 | 13.0292 | 6.8601 | -0.33163 | -11.3419 | -39.0275 | -81.389 | -111.8475 | -128.6605 | 69.9426 | 67.7004 | 64.8949 | 61.5473 | 57.7715 | 53.696 | 49.1197 | 43.6832 | 36.1051 | 17.5916 | -11.071 | -37.0822 | -65.9387 | 34.9279 | 32.1815 | 28.9197 | 24.4846 | 19.5377 | 14.3633 | 8.6034 | 1.8469 | -8.4629 | -33.8703 | -71.8541 | -98.1068 | -111.8681
|  | READING BSP | LW |  |  | 32.8694 | 29.1556 | 25.0104 | 18.1438 | 10.6228 | 2.5193 | -6.3804 | -17.2791 | -28.1215 | -55.243 | -88.8728 | -104.6359 | -113.7709 | 69.6217 | 67.6707 | 65.0233 | 61.194 | 56.9004 | 52.1117 | 46.7525 | 39.7625 | 32.8942 | 17.0167 | -1.6402 | -9.4676 | -14.1954 | 33.0743 | 29.5939 | 25.7068 | 19.4247 | 12.5322 | 5.0484 | -3.2029 | -13.4376 | -23.5978 | -48.4982 | -78.9773 | -92.604 | -100.3046
|  | READING BSP | ST |  |  | 38.7769 | 37.5005 | 35.9389 | 33.7209 | 31.1265 | 28.3267 | 25.1958 | 21.5306 | 17.2998 | -1.2306 | -34.4839 | -53.595 | -66.1944 | 71.8567 | 70.8443 | 69.6436 | 68.0531 | 65.8069 | 63.3225 | 60.5261 | 57.2447 | 53.5889 | 37.6285 | 7.5486 | -15.8054 | -43.2876 | 38.5465 | 37.3454 | 35.877 | 33.8336 | 31.4441 | 28.842 | 25.9228 | 22.4765 | 18.5292 | 0.91184 | -30.258 | -47.236 | -57.9608
|  | READING BSP | FS |  |  | 39.0432 | 37.9526 | 36.7085 | 34.7875 | 31.5118 | 28.1455 | 24.3808 | 19.1994 | 15.6057 | 2.1913 | -30.697 | -50.2805 | -59.9143 | 71.8793 | 70.8729 | 69.7317 | 68.2518 | 65.2843 | 62.0287 | 58.3878 | 53.2478 | 49.7324 | 36.2248 | 0.75106 | -35.3096 | -84.3471 | 71.8793 | 70.8729 | 69.7317 | 68.2518 | 65.2843 | 62.0287 | 58.3878 | 53.2478 | 49.7324 | 36.2248 | 0.75106 | -35.3096 | -84.3471
BRAMLEY (FLEE) | READING TOWN BSP | READING TOWN BSP | MINIMUM HEADROOM | SU 71580 74111 | YES | 52.968 | 50.2818 | 47.4889 | 43.7218 | 39.8179 | 35.8497 | 31.7103 | 27.1426 | 22.4513 | 8.6634 | -6.8691 | -16.1459 | -23.5 | 66.6976 | 65.1164 | 63.4404 | 61.4069 | 59.2859 | 57.0379 | 54.6876 | 52.1584 | 49.5169 | 41.3587 | 27.9605 | 15.3776 | -8.8725 | 59.1942 | 56.8051 | 54.3021 | 50.9986 | 47.5507 | 43.9513 | 40.1586 | 35.9077 | 31.5082 | 18.8711 | 4.9912 | -2.4029 | -8.8725
|  | READING TOWN BSP | CT |  |  | 53.9269 | 51.6091 | 49.1492 | 46.1671 | 43.0822 | 40.1193 | 37.0267 | 33.7049 | 29.175 | 15.6512 | -3.3297 | -16.1459 | -23.5 | 66.8731 | 65.2743 | 63.4404 | 61.4925 | 59.4812 | 57.4061 | 55.2187 | 52.9578 | 50.1224 | 41.3587 | 27.9605 | 15.3776 | 0.042798 | 59.9333 | 57.8447 | 55.5995 | 52.9561 | 50.2037 | 47.4723 | 44.5882 | 41.4944 | 37.2733 | 24.9147 | 8.4043 | -2.4029 | -8.5894
|  | READING TOWN BSP | LW |  |  | 52.968 | 50.2818 | 47.4889 | 43.7218 | 39.8179 | 35.8497 | 31.7103 | 27.1426 | 22.4513 | 8.6634 | -6.8691 | -14.0572 | -18.6199 | 66.6976 | 65.1164 | 63.465 | 61.4069 | 59.2859 | 57.0379 | 54.6876 | 52.1584 | 49.5169 | 41.677 | 33.5259 | 30.1362 | 27.8749 | 59.1942 | 56.8051 | 54.3021 | 50.9986 | 47.5507 | 43.9513 | 40.1586 | 35.9077 | 31.5082 | 18.8711 | 4.9912 | -0.90434 | -4.6024
|  | READING TOWN BSP | ST |  |  | 55.6189 | 54.1936 | 52.7459 | 51.1091 | 49.4361 | 47.751 | 45.9912 | 44.1152 | 42.1212 | 34.5019 | 20.6075 | 12.0163 | 6.5155 | 67.577 | 66.3914 | 65.1841 | 63.9621 | 62.5939 | 61.1146 | 59.5467 | 57.9637 | 56.3106 | 50.0493 | 38.0056 | 26.3622 | 11.622 | 61.6062 | 60.372 | 59.0957 | 57.6378 | 56.1337 | 54.5512 | 52.8676 | 51.0996 | 49.245 | 41.9984 | 28.7375 | 21.2817 | 16.8619
|  | READING TOWN BSP | FS |  |  | 55.7537 | 54.4341 | 53.115 | 51.7286 | 50.3267 | 48.8856 | 47.3862 | 45.8862 | 44.2146 | 38.345 | 26.8791 | 17.996 | 13.4123 | 67.6043 | 66.4324 | 65.2438 | 64.0618 | 62.7522 | 61.3035 | 59.7598 | 58.2396 | 56.5437 | 50.3787 | 37.1701 | 18.5185 | -8.8725 | 67.6043 | 66.4324 | 65.2438 | 64.0618 | 62.7522 | 61.3035 | 59.7598 | 58.2396 | 56.5437 | 50.3787 | 37.1701 | 18.5185 | -8.8725
MANNINGTON GSP | REDHILL BSP | REDHILL BSP | MINIMUM HEADROOM | SZ 08581 96162 | YES | 48.9498 | 46.7158 | 44.2496 | 40.3953 | 36.3147 | 32.1442 | 27.7388 | 22.4951 | 16.7631 | 1.9994 | -16.8608 | -36.3692 | -47.4618 | 69.7908 | 68.2976 | 66.6614 | 64.4544 | 62.0948 | 59.5937 | 56.9426 | 53.4658 | 49.5747 | 40.2871 | 27.2061 | 15.2989 | 4.0818 | 55.7464 | 53.6802 | 51.4001 | 47.891 | 44.1673 | 40.311 | 36.2292 | 31.3329 | 25.9508 | 12.0538 | -4.8705 | -21.3578 | -30.8031
|  | REDHILL BSP | CT |  |  | 49.8912 | 48.3243 | 46.0722 | 43.2577 | 40.2706 | 37.2575 | 34.0592 | 30.4493 | 24.7247 | 8.4006 | -16.66 | -36.3692 | -47.4618 | 69.9889 | 68.8013 | 67.0957 | 65.2108 | 63.2046 | 61.1217 | 58.9046 | 56.1744 | 52.2656 | 41.5567 | 27.2061 | 15.2989 | 4.0818 | 56.5701 | 55.1284 | 53.0208 | 50.4344 | 47.6862 | 44.8766 | 41.89 | 38.4997 | 33.1603 | 17.862 | -4.2911 | -21.3578 | -30.8031
|  | REDHILL BSP | LW |  |  | 48.9498 | 46.7158 | 44.2496 | 40.3953 | 36.3147 | 32.1442 | 27.7388 | 22.4951 | 16.7631 | 1.9994 | -16.8608 | -27.2698 | -33.8826 | 69.7908 | 68.2976 | 66.6614 | 64.4544 | 62.0948 | 59.5937 | 56.9426 | 53.4658 | 49.5747 | 40.2871 | 30.0887 | 25.3451 | 22.1859 | 55.7464 | 53.6802 | 51.4001 | 47.891 | 44.1673 | 40.311 | 36.2292 | 31.3329 | 25.9508 | 12.0538 | -4.8705 | -13.5603 | -19.0706
|  | REDHILL BSP | ST |  |  | 51.3444 | 50.4256 | 49.4341 | 48.1001 | 46.6623 | 45.2382 | 43.7342 | 42.0354 | 40.2905 | 33.1384 | 14.1906 | 3.3994 | -4.5052 | 70.9432 | 70.1699 | 69.3474 | 68.2758 | 67.123 | 65.9342 | 64.6799 | 63.2575 | 61.8486 | 55.7124 | 40.7015 | 31.1923 | 21.0315 | 57.9557 | 57.1287 | 56.2393 | 55.0224 | 53.708 | 52.3742 | 50.9625 | 49.3612 | 47.7274 | 40.9103 | 23.1296 | 13.7204 | 7.0603
|  | REDHILL BSP | FS |  |  | 51.4432 | 50.5322 | 49.5812 | 48.4615 | 47.2963 | 46.1757 | 44.9738 | 43.6649 | 42.241 | 37.0917 | 21.5924 | 10.9006 | 5.7115 | 70.9378 | 70.1275 | 69.2884 | 68.3845 | 67.4291 | 66.4644 | 65.4231 | 64.2702 | 62.9336 | 57.9016 | 42.779 | 27.7607 | 9.8843 | 70.9378 | 70.1275 | 69.2884 | 68.3845 | 67.4291 | 66.4644 | 65.4231 | 64.2702 | 62.9336 | 57.9016 | 42.779 | 27.7607 | 9.8843
NURSLING GSP | ROWNHAMS | ROWNHAMS | MINIMUM HEADROOM | SU 37168 16854 | YES | -45.0354 | -99.5924 | -103.2482 | -108.7172 | -115.0263 | -121.964 | -129.4148 | -138.6511 | -147.9155 | -171.5496 | -199.8697 | -212.3559 | -219.1266 | -12.4217 | -65.7387 | -68.0805 | -71.3341 | -75.2523 | -79.5726 | -84.1584 | -89.8012 | -95.4138 | -110.5114 | -128.5598 | -139.1678 | -156.468 | -22.3318 | -76.6733 | -80.0664 | -85.4375 | -91.5839 | -98.4151 | -105.6931 | -114.5162 | -123.4001 | -146.9832 | -175.8156 | -188.6189 | -195.2816
|  | ROWNHAMS | CT |  |  | -32.599 | -86.1964 | -89.3807 | -93.4043 | -98.1509 | -103.3288 | -108.9443 | -115.3278 | -124.5814 | -148.4031 | -182.0697 | -204.8576 | -218.4927 | -1.0578 | -54.0115 | -56.2687 | -58.9356 | -62.1906 | -65.7445 | -69.5421 | -73.8383 | -80.1559 | -95.9417 | -119.9956 | -139.1678 | -156.468 | -9.3972 | -62.7331 | -65.4458 | -69.2349 | -73.7939 | -78.7492 | -84.0691 | -90.0575 | -98.8867 | -122.4596 | -158.1994 | -182.3214 | -194.2356
|  | ROWNHAMS | LW |  |  | -45.0354 | -99.5924 | -103.2482 | -108.7172 | -115.0263 | -121.964 | -129.4148 | -138.6511 | -147.9155 | -171.5496 | -199.8697 | -212.3559 | -219.1266 | -12.4217 | -65.7387 | -68.0805 | -71.3341 | -75.2523 | -79.5726 | -84.1584 | -89.8012 | -95.4138 | -110.5114 | -128.5598 | -136.6777 | -141.1392 | -22.3318 | -76.6733 | -80.0664 | -85.4375 | -91.5839 | -98.4151 | -105.6931 | -114.5162 | -123.4001 | -146.9832 | -175.8156 | -188.6189 | -195.2816
|  | ROWNHAMS | ST |  |  | -29.9502 | -31.4051 | -32.8937 | -34.991 | -37.6928 | -40.6407 | -43.7619 | -47.3357 | -52.186 | -71.8879 | -103.6002 | -119.5654 | -129.2105 | 0.51443 | -0.74685 | -2.0077 | -3.5733 | -5.6646 | -7.9528 | -10.3414 | -13.0614 | -17.0192 | -32.1339 | -58.427 | -74.9509 | -91.2526 | -7.1592 | -8.5063 | -9.858 | -11.6799 | -14.0546 | -16.6331 | -19.3886 | -22.6619 | -27.2757 | -45.4252 | -76.0228 | -91.7244 | -101.0989
|  | ROWNHAMS | FS |  |  | -29.759 | -31.1211 | -32.4481 | -34.3258 | -40.1197 | -46.1266 | -52.2862 | -62.4156 | -66.1716 | -80.0712 | -110.8878 | -127.864 | -135.139 | 0.57262 | -0.67496 | -1.8877 | -3.3483 | -8.7041 | -14.242 | -19.8728 | -29.4428 | -32.6178 | -44.1045 | -71.0625 | -95.5662 | -123.824 | 0.57262 | -0.67496 | -1.8877 | -3.3483 | -8.7041 | -14.242 | -19.8728 | -29.4428 | -32.6178 | -44.1045 | -71.0625 | -95.5662 | -123.824
MANNINGTON GSP | SALISBURY | SALISBURY | MINIMUM HEADROOM | SU 11049 31395 | YES | 58.0873 | 54.8826 | 51.5926 | 46.8257 | 41.7738 | 36.5015 | 30.6665 | 23.612 | 16.7164 | 0.87028 | -15.3489 | -20.759 | -24.6472 | 79.8622 | 78.0829 | 76.3115 | 73.9103 | 71.2286 | 68.3546 | 65.0968 | 60.7642 | 56.5213 | 47.6789 | 39.2407 | 29.7396 | 18.1258 | 67.5708 | 64.6495 | 61.708 | 57.3844 | 52.7664 | 48.0129 | 42.7359 | 36.1896 | 29.7819 | 15.194 | 0.42799 | -4.3501 | -7.6028
|  | SALISBURY | CT |  |  | 61.302 | 59.3568 | 56.9594 | 53.8914 | 50.5758 | 47.0567 | 43.009 | 38.2778 | 31.5979 | 16.2228 | -4.4153 | -18.4946 | -24.6472 | 80.8829 | 79.545 | 77.9975 | 76.0769 | 73.927 | 71.6198 | 68.8944 | 65.6281 | 61.3278 | 51.6362 | 39.2407 | 29.7396 | 20.1835 | 70.5866 | 68.8531 | 66.8491 | 64.0727 | 60.9702 | 57.7481 | 54.0622 | 49.7873 | 43.7193 | 29.5486 | 10.2194 | -2.2002 | -7.6028
|  | SALISBURY | LW |  |  | 58.0873 | 54.8826 | 51.5926 | 46.8257 | 41.7738 | 36.5015 | 30.6665 | 23.612 | 16.7164 | 0.87028 | -15.3489 | -20.759 | -22.8759 | 79.8622 | 78.0829 | 76.3115 | 73.9103 | 71.2286 | 68.3546 | 65.0968 | 60.7642 | 56.5213 | 47.6789 | 39.3463 | 37.1054 | 36.2011 | 67.5708 | 64.6495 | 61.708 | 57.3844 | 52.7664 | 48.0129 | 42.7359 | 36.1896 | 29.7819 | 15.194 | 0.42799 | -4.3501 | -6.2028
|  | SALISBURY | ST |  |  | 63.2129 | 62.1313 | 61.0211 | 59.4282 | 57.6359 | 55.7714 | 53.584 | 51.0966 | 48.5996 | 38.6904 | 20.6199 | 11.3871 | 6.0991 | 82.0099 | 81.1628 | 80.3499 | 79.2667 | 77.9979 | 76.7312 | 75.2108 | 73.3944 | 71.6546 | 64.1828 | 50.0944 | 41.3866 | 32.2394 | 72.23 | 71.2213 | 70.2451 | 68.8076 | 67.1767 | 65.5563 | 63.6776 | 61.4538 | 59.1776 | 50.1809 | 33.4318 | 24.883 | 19.9077
|  | SALISBURY | FS |  |  | 63.6287 | 62.6964 | 61.7669 | 60.0699 | 58.218 | 56.3829 | 54.2397 | 51.9545 | 49.2826 | 40.3802 | 19.2803 | 7.5862 | 1.9094 | 82.1238 | 81.3061 | 80.5571 | 79.463 | 78.1999 | 76.9779 | 75.5095 | 73.9045 | 72.1068 | 65.5868 | 48.5343 | 34.5942 | 18.1258 | 82.1238 | 81.3061 | 80.5571 | 79.463 | 78.1999 | 76.9779 | 75.5095 | 73.9045 | 72.1068 | 65.5868 | 48.5343 | 34.5942 | 18.1258
MANNINGTON GSP | SHAFTESBURY BSP | SHAFTESBURY BSP | MINIMUM HEADROOM | ST 85442 23791 | YES | 47.2041 | 43.3655 | 39.2472 | 33.8551 | 28.2439 | 21.6557 | 15.3563 | 7.8887 | 0.4421 | -17.6968 | -37.6159 | -42.87 | -45.9234 | 71.4881 | 69.364 | 67.0863 | 64.3594 | 61.4993 | 57.6068 | 54.1247 | 49.6706 | 45.2449 | 35.687 | 25.6329 | 22.4244 | 17.4812 | 55.0548 | 51.5973 | 47.9014 | 43.0495 | 37.9957 | 31.7865 | 25.9961 | 19.0846 | 12.1857 | -4.3502 | -22.4558 | -27.2371 | -30.0037
|  | SHAFTESBURY BSP | CT |  |  | 51.1334 | 48.9834 | 46.0813 | 42.5897 | 38.887 | 34.1837 | 29.7848 | 24.7774 | 17.8969 | 1.3899 | -22.8668 | -37.7973 | -43.8826 | 72.9386 | 71.5186 | 69.5795 | 67.5052 | 65.2963 | 62.1336 | 59.3678 | 56.1256 | 51.8507 | 42.2112 | 29.7051 | 22.4244 | 17.4812 | 58.8438 | 56.8876 | 54.2954 | 51.1343 | 47.7936 | 43.2844 | 39.2485 | 34.6805 | 28.3924 | 13.1206 | -9.3716 | -22.673 | -28.1056
|  | SHAFTESBURY BSP | LW |  |  | 47.2041 | 43.3655 | 39.2472 | 33.8551 | 28.2439 | 21.6557 | 15.3563 | 7.8887 | 0.4421 | -17.6968 | -37.6159 | -42.87 | -45.9234 | 71.4881 | 69.364 | 67.0863 | 64.3594 | 61.4993 | 57.6068 | 54.1247 | 49.6706 | 45.2449 | 35.687 | 25.6329 | 23.2046 | 21.763 | 55.0548 | 51.5973 | 47.9014 | 43.0495 | 37.9957 | 31.7865 | 25.9961 | 19.0846 | 12.1857 | -4.3502 | -22.4558 | -27.2371 | -30.0037
|  | SHAFTESBURY BSP | ST |  |  | 52.6352 | 51.1852 | 49.5713 | 47.4226 | 45.1659 | 42.1016 | 39.479 | 36.5561 | 33.5531 | 21.7635 | 1.629 | -7.7522 | -13.0743 | 73.8981 | 72.9164 | 71.8432 | 70.552 | 69.2021 | 66.9487 | 65.2471 | 63.3204 | 61.3861 | 53.3745 | 39.7369 | 33.6193 | 29.0419 | 60.2021 | 58.8811 | 57.4406 | 55.516 | 53.505 | 50.5049 | 48.0971 | 45.423 | 42.6476 | 31.8897 | 13.2037 | 4.2084 | -0.8848
|  | SHAFTESBURY BSP | FS |  |  | 53.1282 | 51.8434 | 50.4654 | 47.9745 | 45.4379 | 42.145 | 39.2721 | 36.2836 | 32.7327 | 20.7978 | -5.2456 | -19.4887 | -27.4726 | 74.0623 | 73.1263 | 72.1432 | 70.7999 | 69.4301 | 67.199 | 65.4989 | 63.7037 | 61.6725 | 54.5999 | 37.7657 | 28.087 | 20.5149 | 74.0623 | 73.1263 | 72.1432 | 70.7999 | 69.4301 | 67.199 | 65.4989 | 63.7037 | 61.6725 | 54.5999 | 37.7657 | 28.087 | 20.5149
IVER 132KV | SLOUGH | SLOUGH | MINIMUM HEADROOM | SU 95574 81752 | YES | 33.6079 | 32.2961 | 30.7708 | 20.1131 | 9.1819 | -5.9543 | -9.0966 | -12.9048 | -16.7374 | -27.413 | -42.4003 | -53.3198 | -60.7917 | 39.7577 | 39.1701 | 38.499 | 27.2278 | 15.7672 | -0.86279 | -2.2972 | -4.3351 | -5.801 | -11.6309 | -21.7074 | -30.9925 | -44.0136 | 36.902 | 35.6098 | 34.1119 | 21.5819 | 8.7717 | -9.3166 | -12.3777 | -16.1679 | -19.9657 | -30.0148 | -43.7477 | -52.5976 | -58.7878
|  | SLOUGH | CT |  |  | 34.3549 | 33.4115 | 32.0956 | 22.1657 | 12.0082 | -2.2353 | -4.4393 | -6.9851 | -10.9841 | -21.723 | -39.9138 | -53.3198 | -60.7917 | 39.9529 | 39.4538 | 38.8089 | 27.769 | 16.5679 | 0.24475 | -0.86929 | -2.1547 | -3.9621 | -10.1601 | -21.7074 | -30.8281 | -39.3746 | 37.4861 | 36.524 | 35.1716 | 23.2589 | 11.1127 | -6.1825 | -8.4028 | -10.9882 | -14.7708 | -24.8089 | -41.277 | -52.5976 | -58.7878
|  | SLOUGH | LW |  |  | 33.6079 | 32.2961 | 30.7708 | 20.1131 | 9.1819 | -5.9543 | -9.0966 | -12.9048 | -16.7374 | -27.413 | -42.4003 | -50.0926 | -54.6293 | 39.7577 | 39.1701 | 38.499 | 27.2278 | 15.7672 | -0.86279 | -2.2972 | -4.0356 | -5.801 | -11.6309 | -20.6469 | -24.9221 | -27.5056 | 36.902 | 35.6098 | 34.1119 | 21.5819 | 8.7717 | -9.3166 | -12.3777 | -16.1679 | -19.9657 | -30.0148 | -43.7477 | -50.4817 | -54.3498
|  | SLOUGH | ST |  |  | 35.5591 | 35.1412 | 34.5935 | 25.6762 | 16.5891 | 3.4096 | 2.3843 | 1.1424 | -0.63567 | -8.0139 | -23.2779 | -32.1612 | -37.8497 | 40.4943 | 40.2346 | 39.9253 | 29.315 | 18.5657 | 2.6915 | 2.0703 | 1.3228 | 0.064003 | -4.6284 | -15.6808 | -23.9504 | -31.7518 | 38.7221 | 38.2993 | 37.7509 | 26.7956 | 15.6669 | -0.59885 | -1.6628 | -2.9553 | -4.7469 | -12.1524 | -26.584 | -34.5419 | -39.4103
|  | SLOUGH | FS |  |  | 35.6752 | 35.2956 | 34.8252 | 26.0638 | 15.9559 | 1.7887 | -0.22089 | -3.6655 | -4.9177 | -9.514 | -22.881 | -32.0247 | -36.3402 | 40.5338 | 40.2815 | 39.9934 | 29.4437 | 17.5534 | 0.55322 | -1.191 | -4.3351 | -5.2401 | -8.4793 | -19.0066 | -30.9925 | -44.0136 | 40.5338 | 40.2815 | 39.9934 | 29.4437 | 17.5534 | 0.55322 | -1.191 | -4.3351 | -5.2401 | -8.4793 | -19.0066 | -30.9925 | -44.0136
NURSLING GSP | SOUTHAMPTON (2 X 60) | SOUTHAMPTON (2 X 60) | MINIMUM HEADROOM | SU 41425 11999 | YES | 24.8473 | 23.18 | 21.6329 | 19.6145 | 17.714 | 15.8083 | 13.6271 | 11.1655 | 8.805 | 1.4516 | -9.4269 | -16.0277 | -22.237 | 40.1919 | 39.4735 | 38.8268 | 37.7151 | 36.516 | 35.2714 | 33.7735 | 32.0767 | 30.2828 | 24.2903 | 10.623 | -18.138 | -69.0318 | 29.3531 | 28.1514 | 27.1249 | 25.7809 | 24.4855 | 23.0019 | 21.1827 | 19.1273 | 17.1737 | 10.9791 | 1.729 | -18.138 | -69.0318
|  | SOUTHAMPTON (2 X 60) | CT |  |  | 25.6438 | 24.268 | 22.9265 | 21.3112 | 19.8351 | 18.4406 | 16.7987 | 15.012 | 12.8434 | 6.1847 | -6.5844 | -16.0277 | -22.237 | 40.1919 | 39.4735 | 38.8268 | 37.7151 | 36.516 | 35.2714 | 33.7735 | 32.0767 | 30.2828 | 24.2903 | 11.1182 | -5.6786 | -31.2475 | 29.874 | 28.8655 | 28.0154 | 26.9642 | 25.9798 | 25.0404 | 23.8632 | 22.5666 | 20.8669 | 15.3495 | 4.2943 | -3.6613 | -8.6948
|  | SOUTHAMPTON (2 X 60) | LW |  |  | 24.8473 | 23.18 | 21.6329 | 19.6145 | 17.714 | 15.8083 | 13.6271 | 11.1655 | 8.805 | 1.4516 | -9.4269 | -15.5509 | -20.0594 | 40.3006 | 39.6673 | 39.1319 | 38.3476 | 37.4997 | 36.625 | 35.5063 | 34.1974 | 32.8795 | 28.6646 | 22.7406 | 19.8474 | 17.6109 | 29.3531 | 28.1514 | 27.1249 | 25.7809 | 24.4855 | 23.0019 | 21.1827 | 19.1273 | 17.1737 | 10.9791 | 1.729 | -3.1682 | -6.6261
|  | SOUTHAMPTON (2 X 60) | ST |  |  | 26.7936 | 26.0751 | 25.5576 | 24.8857 | 24.2066 | 23.5455 | 22.6969 | 21.712 | 20.715 | 17.3444 | 8.6864 | 2.0239 | -2.5037 | 40.618 | 40.1141 | 39.6879 | 39.178 | 38.6745 | 37.8297 | 36.7036 | 35.403 | 34.1562 | 29.6407 | 17.213 | 1.1874 | -23.3103 | 30.7276 | 30.1964 | 29.8053 | 29.3425 | 28.9205 | 28.4961 | 27.8667 | 27.1069 | 26.3417 | 23.7 | 17.0731 | 12.2523 | 8.8287
|  | SOUTHAMPTON (2 X 60) | FS |  |  | 26.9409 | 26.2989 | 25.8563 | 25.3659 | 24.8498 | 24.3354 | 23.6609 | 22.9206 | 22.1234 | 19.6321 | 12.8747 | 6.1387 | 1.8723 | 40.6191 | 40.1017 | 39.6582 | 39.0983 | 38.4176 | 37.3082 | 35.9514 | 34.3845 | 32.7824 | 26.9041 | 10.623 | -18.138 | -69.0318 | 40.6191 | 40.1017 | 39.6582 | 39.0983 | 38.4176 | 37.3082 | 35.9514 | 34.3845 | 32.7824 | 26.9041 | 10.623 | -18.138 | -69.0318
NURSLING GSP | SOUTHAMPTON (2 X 90) | SOUTHAMPTON (2 X 90) | MINIMUM HEADROOM | SU 41425 11999 | YES | 40.2736 | 38.2518 | 35.7884 | 32.6455 | 28.6495 | 24.6615 | 20.5058 | 15.7387 | 10.8331 | -4.5903 | -26.0555 | -40.9824 | -52.4621 | 64.651 | 64.0809 | 63.3489 | 62.5624 | 58.9531 | 54.1586 | 49.2996 | 40.103 | 38.3336 | 32.5791 | 15.6218 | -8.1631 | -38.4049 | 51.6169 | 49.7605 | 47.5075 | 44.6537 | 41.008 | 37.3049 | 33.4172 | 28.8762 | 24.1362 | 9.5616 | -10.0192 | -22.3461 | -38.4049
|  | SOUTHAMPTON (2 X 90) | CT |  |  | 41.4799 | 39.9923 | 37.903 | 35.6304 | 32.5887 | 29.7107 | 26.6968 | 23.3272 | 18.6023 | 3.7111 | -21.6644 | -40.9824 | -52.4621 | 64.651 | 64.0809 | 63.3489 | 62.5624 | 61.3094 | 60.0694 | 58.7483 | 57.223 | 54.7516 | 46.0693 | 27.9496 | 10.9986 | -7.4567 | 52.5383 | 51.1615 | 49.1656 | 47.0084 | 44.1434 | 41.3851 | 38.4721 | 35.1811 | 30.7621 | 16.8629 | -5.6412 | -22.3461 | -32.1586
|  | SOUTHAMPTON (2 X 90) | LW |  |  | 40.2736 | 38.2518 | 35.7884 | 32.6455 | 28.6495 | 24.6615 | 20.5058 | 15.7387 | 10.8331 | -4.5903 | -26.0555 | -39.0122 | -47.1031 | 64.7495 | 64.1953 | 63.5159 | 62.749 | 61.4428 | 59.9522 | 57.8089 | 55.3387 | 52.783 | 44.7693 | 31.9321 | 23.9975 | 19.0028 | 51.6169 | 49.7605 | 47.5075 | 44.6537 | 41.008 | 37.3049 | 33.4172 | 28.8762 | 24.1362 | 9.5616 | -10.0192 | -21.2852 | -28.2161
|  | SOUTHAMPTON (2 X 90) | ST |  |  | 42.9889 | 42.2647 | 41.3221 | 40.3524 | 38.7635 | 37.2379 | 35.6361 | 33.7378 | 30.2649 | 18.4106 | -3.9257 | -18.3828 | -27.2634 | 65.0914 | 64.7243 | 64.2724 | 63.7129 | 62.6865 | 61.6788 | 60.6004 | 59.3251 | 56.5561 | 47.4733 | 30.0969 | 13.5061 | -3.4719 | 54.0323 | 53.3924 | 52.5561 | 51.5719 | 50.0102 | 48.4887 | 46.8766 | 44.9725 | 41.5575 | 29.8656 | 8.2386 | -4.7616 | -12.2378
|  | SOUTHAMPTON (2 X 90) | FS |  |  | 43.1467 | 42.4764 | 41.6363 | 40.8938 | 35.7385 | 30.6425 | 25.4785 | 15.9539 | 13.711 | 6.3176 | -10.6613 | -24.7863 | -31.8393 | 65.1027 | 64.7348 | 64.2911 | 63.7764 | 58.9531 | 54.1586 | 49.2996 | 40.103 | 38.3336 | 32.5791 | 15.6218 | -8.1631 | -38.4049 | 65.1027 | 64.7348 | 64.2911 | 63.7764 | 58.9531 | 54.1586 | 49.2996 | 40.103 | 38.3336 | 32.5791 | 15.6218 | -8.1631 | -38.4049
LALEHAM | STAINES | STAINES | MINIMUM HEADROOM | TQ 04585 72135 | YES | 29.6507 | 25.0154 | 20.1495 | 13.5331 | 6.2541 | -1.5295 | -9.6449 | -18.8265 | -28.2655 | -54.7097 | -84.4706 | -100.2161 | -112.3272 | 46.926 | 45.1573 | 43.3526 | 40.4689 | 36.5549 | 32.3108 | 27.8515 | 22.6034 | 17.1057 | 1.6043 | -18.0408 | -34.3831 | -50.5169 | 41.2088 | 37.1648 | 32.9142 | 27.0239 | 20.5721 | 13.655 | 6.4123 | -1.8488 | -10.4047 | -34.5094 | -61.712 | -75.6317 | -85.92
|  | STAINES | CT |  |  | 31.2699 | 27.4786 | 23.0821 | 17.8174 | 11.9776 | 5.9177 | -0.36021 | -7.0587 | -16.0731 | -41.8435 | -77.7762 | -100.2161 | -112.3272 | 47.1033 | 45.4343 | 43.6646 | 41.5247 | 38.0661 | 34.4271 | 30.6166 | 26.407 | 20.9642 | 4.9393 | -18.0408 | -34.3831 | -50.5169 | 42.7493 | 39.4838 | 35.6919 | 31.0752 | 25.978 | 20.6756 | 15.1533 | 9.1872 | 1.0413 | -22.319 | -55.4477 | -75.6317 | -85.92
|  | STAINES | LW |  |  | 29.6507 | 25.0154 | 20.1495 | 13.5331 | 6.2541 | -1.5295 | -9.6449 | -18.8265 | -28.2655 | -54.7097 | -84.4706 | -96.1064 | -103.1187 | 46.926 | 45.1573 | 43.3526 | 40.4689 | 36.5549 | 32.3108 | 27.8515 | 22.6034 | 17.1057 | 1.6043 | -15.8914 | -21.4339 | -24.9141 | 41.2088 | 37.1648 | 32.9142 | 27.0239 | 20.5721 | 13.655 | 6.4123 | -1.8488 | -10.4047 | -34.5094 | -61.712 | -71.9229 | -77.8556
|  | STAINES | ST |  |  | 34.5299 | 32.4062 | 30.2344 | 27.4462 | 24.3157 | 20.9932 | 17.553 | 13.9128 | 10.1628 | -5.4573 | -36.5809 | -53.183 | -62.3502 | 48.3041 | 47.2307 | 46.2116 | 45.0061 | 43.6912 | 42.2671 | 40.2735 | 37.6988 | 35.0003 | 23.968 | 0.12738 | -15.6574 | -30.4719 | 45.6559 | 43.9804 | 42.2133 | 39.895 | 37.3115 | 34.5443 | 31.6434 | 28.4779 | 25.1265 | 11.2617 | -16.9664 | -31.9373 | -39.9448
|  | STAINES | FS |  |  | 34.8347 | 32.865 | 30.9259 | 28.5864 | 25.9906 | 23.192 | 20.3056 | 17.4379 | 14.3577 | 3.0357 | -23.7381 | -42.6259 | -50.6975 | 48.3978 | 47.3596 | 46.3968 | 45.3276 | 44.1806 | 42.9444 | 41.5381 | 39.3683 | 36.9256 | 27.8941 | 5.0646 | -19.455 | -46.6621 | 48.3978 | 47.3596 | 46.3968 | 45.3276 | 44.1806 | 42.9444 | 41.5381 | 39.3683 | 36.9256 | 27.8941 | 5.0646 | -19.455 | -46.6621
MINETY GSP | STRATTON (2 X 60) | STRATTON (2 X 60) | MINIMUM HEADROOM | SU 17028 88748 | NO | -3.8228 | -7.2712 | -10.7807 | -15.5064 | -20.3551 | -25.2573 | -30.6117 | -36.9419 | -43.2181 | -57.6916 | -73.2062 | -78.9349 | -82.6342 | 22.9615 | 21.0859 | 19.1691 | 16.7434 | 14.1769 | 11.4966 | 8.4496 | 4.5961 | 0.85659 | -7.0367 | -15.2654 | -21.873 | -27.943 | 9.1653 | 6.1752 | 3.1027 | -1.0537 | -5.3586 | -9.7509 | -14.5591 | -20.2934 | -26.0126 | -39.0119 | -53.0459 | -58.2084 | -61.3584
|  | STRATTON (2 X 60) | CT |  |  | -1.6179 | -4.2598 | -7.137 | -10.6242 | -14.1972 | -17.7499 | -21.713 | -26.3136 | -32.3431 | -46.5122 | -64.9721 | -77.313 | -82.6342 | 23.4928 | 21.8654 | 20.038 | 18.0396 | 15.9231 | 13.7568 | 11.3193 | 8.3947 | 4.695 | -3.6801 | -14.2694 | -21.873 | -27.943 | 11.1643 | 8.9494 | 6.479 | 3.4023 | 0.21476 | -2.9849 | -6.5616 | -10.7505 | -16.2857 | -29.1074 | -45.686 | -56.6288 | -61.3584
|  | STRATTON (2 X 60) | LW |  |  | -3.8228 | -7.2712 | -10.7807 | -15.5064 | -20.3551 | -25.2573 | -30.6117 | -36.9419 | -43.2181 | -57.6916 | -73.2062 | -78.9349 | -81.8447 | 22.9615 | 21.0859 | 19.1691 | 16.7434 | 14.1769 | 11.4966 | 8.4496 | 4.5961 | 0.85659 | -7.0367 | -15.2654 | -18.3627 | -19.9543 | 9.1653 | 6.1752 | 3.1027 | -1.0537 | -5.3586 | -9.7509 | -14.5591 | -20.2934 | -26.0126 | -39.0119 | -53.0459 | -58.2084 | -60.8153
|  | STRATTON (2 X 60) | ST |  |  | 21.9446 | -1.0851 | -2.6561 | -4.6889 | -6.7988 | -8.8916 | -11.2153 | -13.8024 | -16.7458 | -27.4604 | -43.1294 | -51.2445 | -56.423 | 46.4403 | 23.9836 | 22.9745 | 21.6996 | 20.3235 | 18.9246 | 17.3592 | 15.5894 | 13.5268 | 5.6108 | -6.1398 | -12.8302 | -18.9601 | 34.5515 | 11.8191 | 10.5466 | 8.8656 | 7.0859 | 5.3029 | 3.2564 | 0.95004 | -1.72 | -11.6927 | -26.4397 | -33.8235 | -38.4354
|  | STRATTON (2 X 60) | FS |  |  | 22.2739 | 20.9009 | 19.5685 | 17.5163 | 14.3407 | 11.1834 | 7.7851 | 3.1202 | 0.27738 | -8.8349 | -27.4183 | -37.3411 | -42.3427 | 46.517 | 45.6155 | 44.7226 | 43.58 | 41.2569 | 38.9137 | 36.4 | 32.6347 | 30.7979 | 24.6039 | 10.4977 | 0.88459 | -8.4303 | 46.517 | 45.6155 | 44.7226 | 43.58 | 41.2569 | 38.9137 | 36.4 | 32.6347 | 30.7979 | 24.6039 | 10.4977 | 0.88459 | -8.4303
MINETY GSP | STRATTON (2 X 90) | STRATTON (2 X 90) | MINIMUM HEADROOM | SU 17028 88748 | NO | 45.7923 | 44.4226 | 42.9968 | 40.68 | 37.9998 | 35.1045 | 32.0855 | 28.4397 | 24.5755 | 13.1031 | -2.3602 | -16.0858 | -24.7531 | 57.2205 | 56.6063 | 55.9393 | 55.1105 | 53.3569 | 50.4578 | 47.5541 | 42.2751 | 41.0245 | 36.5149 | 24.3784 | 11.3861 | -3.3249 | 49.753 | 48.537 | 47.2744 | 45.1765 | 42.6966 | 40.0564 | 37.3035 | 33.9873 | 30.4896 | 20.0085 | 6.0556 | -6.0999 | -13.5994
|  | STRATTON (2 X 90) | CT |  |  | 46.2958 | 45.339 | 44.0469 | 42.3087 | 40.2751 | 38.0627 | 35.7503 | 33.1216 | 29.3217 | 17.5907 | -1.4743 | -16.0858 | -24.7531 | 57.2205 | 56.6063 | 55.9393 | 55.1105 | 54.0073 | 52.8381 | 51.6388 | 49.7526 | 47.1765 | 39.1958 | 27.2056 | 17.0644 | 7.8771 | 50.215 | 49.362 | 48.2282 | 46.661 | 44.7759 | 42.7614 | 40.6568 | 38.2683 | 34.8374 | 24.1909 | 6.9079 | -6.0999 | -13.5994
|  | STRATTON (2 X 90) | LW |  |  | 45.7923 | 44.4226 | 42.9968 | 40.68 | 37.9998 | 35.1045 | 32.0855 | 28.4397 | 24.5755 | 13.1031 | -2.3602 | -11.7139 | -17.6099 | 57.2688 | 56.625 | 55.9807 | 55.1365 | 53.9663 | 52.3893 | 50.5167 | 48.0841 | 45.5166 | 38.0219 | 28.6795 | 23.2352 | 19.7407 | 49.753 | 48.537 | 47.2744 | 45.1765 | 42.6966 | 40.0564 | 37.3035 | 33.9873 | 30.4896 | 20.0085 | 6.0556 | -2.1177 | -7.0692
|  | STRATTON (2 X 90) | ST |  |  | 47.3034 | 46.723 | 46.1553 | 45.2435 | 44.0729 | 42.784 | 41.4573 | 39.89 | 37.5467 | 28.7364 | 11.9865 | 1.4359 | -5.3035 | 57.6001 | 57.1522 | 56.743 | 56.1234 | 55.2357 | 54.289 | 53.3217 | 52.1537 | 50.2453 | 43.3432 | 30.1293 | 20.6482 | 12.2122 | 51.1225 | 50.6109 | 50.1156 | 49.2957 | 48.1906 | 47.0105 | 45.7944 | 44.3594 | 42.1479 | 33.9327 | 18.7805 | 9.4646 | 3.7385
|  | STRATTON (2 X 90) | FS |  |  | 47.4594 | 46.8701 | 46.3138 | 45.5533 | 42.4999 | 39.3827 | 36.2178 | 30.6709 | 29.0828 | 23.2665 | 10.6356 | 1.1289 | -3.5759 | 57.6178 | 57.1739 | 56.7764 | 56.2208 | 53.3569 | 50.4578 | 47.5541 | 42.2751 | 41.0245 | 36.5149 | 24.3784 | 11.3861 | -3.3249 | 57.6178 | 57.1739 | 56.7764 | 56.2208 | 53.3569 | 50.4578 | 47.5541 | 42.2751 | 41.0245 | 36.5149 | 24.3784 | 11.3861 | -3.3249
MINETY GSP | SWINDON BSP | SWINDON BSP | MINIMUM HEADROOM | SU 12447 87062 | NO | 37.3893 | 22.0135 | 19.4225 | 15.4017 | 10.9215 | 6.123 | 0.90284 | -5.4681 | -12.1768 | -30.2292 | -53.6707 | -69.97 | -80.6638 | 62.9655 | 48.5195 | 46.892 | 44.7033 | 42.0817 | 39.0989 | 35.7681 | 31.4084 | 26.8523 | 15.3706 | -3.5691 | -20.7522 | -50.0465 | 64.4733 | 51.2092 | 48.6831 | 44.9189 | 40.6919 | 36.1109 | 31.1851 | 24.9511 | 18.4045 | 1.3858 | -20.1153 | -33.5674 | -50.0465
|  | SWINDON BSP | CT |  |  | 38.8722 | 24.2006 | 22.0402 | 19.2863 | 16.1352 | 12.7525 | 9.0752 | 4.7043 | -2.034 | -20.2521 | -49.3279 | -69.97 | -80.6638 | 63.1674 | 48.8803 | 47.1731 | 45.2626 | 42.8972 | 40.3528 | 37.4447 | 33.9617 | 29.2432 | 16.5242 | -3.5691 | -20.7522 | -39.1616 | 67.7166 | 53.0692 | 50.8672 | 48.1924 | 45.0485 | 41.7358 | 38.1163 | 33.8359 | 27.4832 | 10.4571 | -15.7561 | -33.5674 | -42.9018
|  | SWINDON BSP | LW |  |  | 37.3893 | 22.0135 | 19.4225 | 15.4017 | 10.9215 | 6.123 | 0.90284 | -5.4681 | -12.1768 | -30.2292 | -53.6707 | -65.0709 | -71.1729 | 62.9655 | 48.5195 | 46.892 | 44.7033 | 42.0817 | 39.0989 | 35.7681 | 31.4084 | 26.8523 | 15.3706 | 1.2187 | -5.1768 | -8.7717 | 66.5059 | 51.2092 | 48.6831 | 44.9189 | 40.6919 | 36.1109 | 31.1851 | 24.9511 | 18.4045 | 1.3858 | -20.1153 | -29.9742 | -35.2038
|  | SWINDON BSP | ST |  |  | 40.8455 | 39.9717 | 39.0741 | 25.0592 | 23.6046 | 22.0137 | 20.2623 | 18.1489 | 14.7528 | 1.6115 | -24.4405 | -38.9627 | -47.3803 | 64.4451 | 63.625 | 62.7757 | 48.8739 | 47.5462 | 46.0744 | 44.4468 | 42.4123 | 39.3297 | 27.4149 | 4.0155 | -12.6545 | -29.8675 | 69.6968 | 68.843 | 67.9527 | 53.9262 | 52.4591 | 50.8441 | 49.0442 | 46.8027 | 43.4547 | 30.5427 | 5.701 | -7.5553 | -14.9007
|  | SWINDON BSP | FS |  |  | 41.056 | 40.2566 | 39.4863 | 38.5418 | 34.783 | 30.9646 | 26.9868 | 20.0977 | 17.8128 | 9.5869 | -12.4896 | -27.2873 | -33.4635 | 64.4733 | 63.635 | 62.8019 | 61.8823 | 58.1232 | 54.2666 | 50.2395 | 43.2462 | 40.7872 | 31.8929 | 7.9206 | -17.5376 | -50.0465 | 64.4733 | 63.635 | 62.8019 | 61.8823 | 58.1232 | 54.2666 | 50.2395 | 43.2462 | 40.7872 | 31.8929 | 7.9206 | -17.5376 | -50.0465
BRAMLEY (ANDO-THAT) | THATCHAM BSP | THATCHAM BSP | MINIMUM HEADROOM | SU 52824 66435 | YES | -1.855 | -7.9628 | -24.2837 | -32.9968 | -42.6656 | -52.6742 | -63.1143 | -74.1522 | -84.6125 | -109.3109 | -138.1633 | -147.1534 | -151.4449 | 49.3415 | 46.0751 | 32.5604 | 28.1581 | 23.1639 | 17.8477 | 12.0165 | 5.1662 | -1.1928 | -14.9585 | -30.5976 | -39.6729 | -61.1479 | 15.0854 | 9.5191 | -6.2897 | -14.1953 | -22.8985 | -31.9144 | -41.4871 | -51.9881 | -61.751 | -84.2718 | -110.0344 | -117.8159 | -121.4895
|  | THATCHAM BSP | CT |  |  | 5.0748 | 1.2009 | -12.8819 | -18.3863 | -24.721 | -31.0257 | -37.9838 | -45.0502 | -55.0558 | -77.7185 | -111.535 | -130.5252 | -138.4275 | 51.4644 | 48.7891 | 35.8574 | 32.5671 | 28.7307 | 24.7669 | 20.2562 | 15.4558 | 8.8964 | -5.1706 | -25.5076 | -39.2346 | -51.3359 | 20.635 | 17.1058 | 3.3333 | -1.4746 | -7.2035 | -13.0085 | -19.468 | -26.09 | -35.4849 | -56.3125 | -86.8078 | -103.5427 | -110.1543
|  | THATCHAM BSP | LW |  |  | -1.855 | -7.9628 | -24.2837 | -32.9968 | -42.6656 | -52.6742 | -63.1143 | -74.1522 | -84.6125 | -109.3109 | -138.1633 | -147.1534 | -151.4449 | 49.3415 | 46.0751 | 32.5604 | 28.1581 | 23.1639 | 17.8477 | 12.0165 | 5.1662 | -1.1928 | -14.9585 | -30.5976 | -35.3361 | -37.6847 | 15.0854 | 9.5191 | -6.2897 | -14.1953 | -22.8985 | -31.9144 | -41.4871 | -51.9881 | -61.751 | -84.2718 | -110.0344 | -117.8159 | -121.4895
|  | THATCHAM BSP | ST |  |  | 8.7383 | 6.4295 | 4.0945 | 0.95732 | -2.7767 | -6.5572 | -10.6485 | -15.0397 | -20.2074 | -41.1213 | -74.8507 | -90.5475 | -98.9631 | 54.0199 | 52.4217 | 50.7676 | 48.7716 | 46.3417 | 43.8148 | 41.0207 | 37.9256 | 34.3063 | 19.0576 | -5.6867 | -19.3737 | -31.7941 | 24.1425 | 22.1016 | 20.0049 | 17.2624 | 14.0003 | 10.6577 | 6.8886 | 2.8061 | -2.0054 | -21.722 | -53.2611 | -67.5269 | -74.942
|  | THATCHAM BSP | FS |  |  | 9.6606 | 7.8389 | 6.1122 | 2.086 | -3.861 | -9.7929 | -16.109 | -24.189 | -30.1136 | -50.3293 | -94.7661 | -119.8308 | -133.6127 | 54.3331 | 52.9386 | 51.5791 | 49.3814 | 45.3466 | 41.2592 | 36.8336 | 30.6099 | 26.9621 | 13.8447 | -17.5369 | -39.6729 | -61.1479 | 54.3331 | 52.9386 | 51.5791 | 49.3814 | 45.3466 | 41.2592 | 36.8336 | 30.6099 | 26.9621 | 13.8447 | -17.5369 | -39.6729 | -61.1479
MINETY GSP | TOOTHILL BSP | TOOTHILL BSP | MINIMUM HEADROOM | SU 13191 83945 | NO | 56.2616 | 49.7524 | 42.8718 | 39.0643 | 34.8974 | 30.4804 | 25.6454 | 20.166 | 14.8208 | -0.50372 | -15.7443 | -25.0932 | -31.5099 | 68.3232 | 61.7804 | 55.0348 | 52.9337 | 50.643 | 48.1635 | 45.4447 | 42.257 | 39.0967 | 30.2769 | 20.5034 | 12.8953 | 5.7069 | 69.3825 | 63.4797 | 56.6448 | 53.3104 | 49.6683 | 45.7555 | 41.4711 | 36.5125 | 31.6134 | 17.8793 | 4.4074 | -2.9072 | -8.3213
|  | TOOTHILL BSP | CT |  |  | 56.9909 | 50.8314 | 44.1694 | 41.0416 | 37.5728 | 33.989 | 30.0288 | 25.6499 | 20.4164 | 4.946 | -13.6142 | -25.0932 | -31.5099 | 68.4369 | 61.985 | 55.2167 | 53.3162 | 51.2305 | 49.0374 | 46.6211 | 43.9188 | 40.7598 | 31.5506 | 20.5034 | 12.8953 | 5.7069 | 72.0412 | 65.0987 | 57.6868 | 54.9263 | 51.8754 | 48.6914 | 45.1781 | 41.2514 | 36.487 | 22.6947 | 6.5697 | -2.9072 | -8.3213
|  | TOOTHILL BSP | LW |  |  | 56.2616 | 49.7524 | 42.8718 | 39.0643 | 34.8974 | 30.4804 | 25.6454 | 20.166 | 14.8208 | -0.50372 | -15.7443 | -22.143 | -26.0002 | 68.3232 | 61.7804 | 55.0348 | 52.9337 | 50.643 | 48.1635 | 45.4447 | 42.257 | 39.0967 | 30.2769 | 21.8739 | 18.8188 | 16.8789 | 71.4704 | 64.2159 | 56.6448 | 53.3104 | 49.6683 | 45.7555 | 41.4711 | 36.5125 | 31.6134 | 17.8793 | 4.4074 | -0.87309 | -4.0203
|  | TOOTHILL BSP | ST |  |  | 58.397 | 53.122 | 47.6526 | 45.8941 | 43.9405 | 41.8902 | 39.6138 | 37.0938 | 34.6566 | 25.4197 | 10.7107 | 3.18 | -1.5756 | 69.3496 | 63.4178 | 57.3526 | 56.123 | 54.7765 | 53.3415 | 51.7552 | 49.9875 | 48.3195 | 41.9797 | 31.0836 | 24.3133 | 17.7028 | 73.4462 | 67.3496 | 61.087 | 59.5449 | 57.8414 | 56.029 | 54.0164 | 51.7564 | 49.6034 | 41.3873 | 27.9702 | 21.3558 | 17.3702
|  | TOOTHILL BSP | FS |  |  | 58.5259 | 53.3486 | 48.0277 | 46.5751 | 44.9942 | 43.2687 | 41.347 | 39.3231 | 37.3383 | 30.3465 | 17.9317 | 9.9082 | 6.1393 | 69.3825 | 63.4797 | 57.4772 | 56.4545 | 55.3444 | 54.0925 | 52.6927 | 51.1959 | 49.6988 | 44.4306 | 33.9198 | 24.2156 | 13.5207 | 69.3825 | 63.4797 | 57.4772 | 56.4545 | 55.3444 | 54.0925 | 52.6927 | 51.1959 | 49.6988 | 44.4306 | 33.9198 | 24.2156 | 13.5207
IVER 132KV | UPTON BSP | UPTON BSP | MINIMUM HEADROOM | TQ 00838 79445 | YES | 37.6324 | 36.6584 | 35.5588 | 33.8527 | 32.0221 | 29.9843 | 27.7342 | 24.9151 | 22.0951 | 14.7063 | 4.961 | -0.95953 | -5.9343 | 45.7616 | 45.442 | 45.0756 | 44.5361 | 43.8978 | 42.6202 | 41.1864 | 39.3192 | 37.4608 | 32.7153 | 25.237 | 18.5767 | 10.4287 | 41.6434 | 40.7282 | 39.6939 | 38.1142 | 36.4153 | 34.5113 | 32.4001 | 29.7264 | 27.0033 | 19.8463 | 10.5495 | 4.9717 | 0.80084
|  | UPTON BSP | CT |  |  | 38.0423 | 37.2676 | 36.2847 | 35.0357 | 33.6801 | 32.2281 | 30.6289 | 28.6836 | 25.8565 | 18.5761 | 6.9226 | -0.95953 | -5.9343 | 45.785 | 45.4707 | 45.092 | 44.6293 | 44.1236 | 43.1077 | 41.9134 | 40.4577 | 38.4815 | 33.3873 | 25.237 | 18.5767 | 11.5073 | 41.993 | 41.2565 | 40.3183 | 39.1477 | 37.8754 | 36.5041 | 34.9899 | 33.148 | 30.488 | 23.6388 | 12.4117 | 4.9717 | 0.80084
|  | UPTON BSP | LW |  |  | 37.6324 | 36.6584 | 35.5588 | 33.8527 | 32.0221 | 29.9843 | 27.7342 | 24.9151 | 22.0951 | 14.7063 | 4.961 | 0.43046 | -2.4606 | 45.7616 | 45.442 | 45.0756 | 44.5361 | 43.8978 | 42.6202 | 41.1864 | 39.3192 | 37.4608 | 32.7153 | 26.8211 | 24.4904 | 22.9533 | 41.6434 | 40.7282 | 39.6939 | 38.1142 | 36.4153 | 34.5113 | 32.4001 | 29.7264 | 27.0033 | 19.8463 | 10.5495 | 6.4346 | 3.9044
|  | UPTON BSP | ST |  |  | 39.0904 | 38.7526 | 38.3471 | 37.8073 | 37.1978 | 36.5183 | 35.7538 | 34.7706 | 33.711 | 29.1799 | 19.5908 | 13.9573 | 10.368 | 46.1527 | 45.998 | 45.8155 | 45.5782 | 45.3089 | 45.0009 | 44.6539 | 44.1917 | 43.5334 | 39.709 | 31.4632 | 25.3247 | 18.716 | 43.0031 | 42.6877 | 42.3089 | 41.8012 | 41.2268 | 40.584 | 39.858 | 38.9276 | 37.9323 | 33.5978 | 24.5684 | 19.5435 | 16.4866
|  | UPTON BSP | FS |  |  | 39.1618 | 38.8591 | 38.5127 | 38.0906 | 37.6285 | 37.1302 | 36.5472 | 35.822 | 34.9742 | 31.8615 | 23.2519 | 17.19 | 14.2796 | 46.1715 | 46.0241 | 45.8554 | 45.6494 | 45.4198 | 45.1653 | 44.8741 | 44.5064 | 44.046 | 40.9625 | 31.9931 | 22.4011 | 10.4287 | 46.1715 | 46.0241 | 45.8554 | 45.6494 | 45.4198 | 45.1653 | 44.8741 | 44.5064 | 44.046 | 40.9625 | 31.9931 | 22.4011 | 10.4287
NURSLING GSP | VELMORE BSP | VELMORE BSP | MINIMUM HEADROOM | SU 42855 19215 | YES | 20.4303 | 15.8247 | 11.5154 | 5.5397 | -0.66422 | -7.1645 | -13.9094 | -22.0195 | -29.9633 | -48.8297 | -72.8874 | -88.8854 | -100.195 | 50.8121 | 47.6765 | 44.7918 | 41.2614 | 37.5794 | 33.6361 | 29.4636 | 24.0849 | 18.8457 | 7.1343 | -10.9063 | -26.6836 | -45.5951 | 28.1919 | 23.9677 | 19.9542 | 14.5261 | 8.8552 | 2.8891 | -3.3529 | -11.0101 | -18.5205 | -36.1356 | -58.042 | -71.259 | -80.4754
|  | VELMORE BSP | CT |  |  | 21.7795 | 17.7935 | 13.7906 | 9.1368 | 4.2998 | -0.50172 | -5.4941 | -11.0059 | -19.0086 | -38.3116 | -68.4243 | -88.8854 | -100.195 | 50.8829 | 47.8454 | 44.8623 | 41.7174 | 38.4505 | 35.1025 | 31.5215 | 27.4117 | 21.8615 | 8.755 | -10.9063 | -26.6836 | -43.2579 | 29.2314 | 25.5437 | 21.846 | 17.6295 | 13.2362 | 8.8255 | 4.1832 | -1.0247 | -8.5739 | -26.5667 | -53.7006 | -71.259 | -80.4754
|  | VELMORE BSP | LW |  |  | 20.4303 | 15.8247 | 11.5154 | 5.5397 | -0.66422 | -7.1645 | -13.9094 | -22.0195 | -29.9633 | -48.8297 | -72.8874 | -83.5487 | -89.6008 | 50.8121 | 47.6765 | 44.7918 | 41.2614 | 37.5794 | 33.6361 | 29.4636 | 24.0849 | 18.8457 | 7.1343 | -6.5995 | -11.6378 | -14.6606 | 28.1919 | 23.9677 | 19.9542 | 14.5261 | 8.8552 | 2.8891 | -3.3529 | -11.0101 | -18.5205 | -36.1356 | -58.042 | -67.1596 | -72.195
|  | VELMORE BSP | ST |  |  | 24.6502 | 22.1648 | 20.0864 | 17.7043 | 15.2493 | 12.6924 | 10.0976 | 7.2675 | 4.4507 | -7.7845 | -33.1478 | -47.0025 | -55.5337 | 52.9351 | 50.9011 | 49.2077 | 47.3025 | 45.3079 | 43.2512 | 41.0997 | 38.6777 | 36.3348 | 25.9926 | 4.5281 | -10.1592 | -25.8403 | 32.1665 | 29.9669 | 28.0771 | 25.8638 | 23.5837 | 21.2634 | 18.8683 | 16.1987 | 13.547 | 1.7865 | -22.1159 | -34.4189 | -41.6292
|  | VELMORE BSP | FS |  |  | 24.8882 | 22.583 | 20.7743 | 18.8514 | 16.9238 | 15.0021 | 12.9667 | 10.8523 | 8.6035 | 0.44222 | -22.8728 | -37.3263 | -43.7477 | 52.9797 | 51.0043 | 49.428 | 47.8357 | 46.223 | 44.5259 | 42.7021 | 40.7222 | 38.53 | 30.2692 | 6.5264 | -16.6193 | -45.5951 | 52.9797 | 51.0043 | 49.428 | 47.8357 | 46.223 | 44.5259 | 42.7021 | 40.7222 | 38.53 | 30.2692 | 6.5264 | -16.6193 | -45.5951
MANNINGTON GSP | WAREHAM | WAREHAM | MINIMUM HEADROOM | SY 91548 88451 | YES | 8.1633 | 6.9637 | 5.6063 | 3.5894 | 1.1997 | -1.3315 | -4.0198 | -8.2469 | -10.1246 | -18.0359 | -27.5264 | -33.3354 | -37.4829 | 10.9793 | 10.631 | 10.121 | 9.0258 | 7.4473 | 4.5913 | 1.6834 | -3.978 | -5.2084 | -9.2522 | -17.5549 | -23.7355 | -29.1409 | 6.8523 | 5.7522 | 4.5103 | 2.6902 | 0.51261 | -1.8014 | -4.2618 | -7.0717 | -9.8978 | -17.1353 | -25.85 | -31.0514 | -34.8096
|  | WAREHAM | CT |  |  | 8.9677 | 8.511 | 7.4661 | 6.0654 | 4.3511 | 2.4709 | 0.4485 | -1.6795 | -4.5912 | -12.4068 | -24.4328 | -33.3354 | -37.4829 | 10.9793 | 10.6417 | 10.2171 | 9.7675 | 8.6811 | 7.4199 | 6.0626 | 4.6137 | 2.795 | -1.9585 | -8.8495 | -14.4841 | -18.5044 | 7.7714 | 7.125 | 6.1485 | 4.8729 | 3.2989 | 1.5722 | -0.28646 | -2.2534 | -4.9442 | -12.1085 | -23.0022 | -31.0514 | -34.8096
|  | WAREHAM | LW |  |  | 8.1633 | 6.9637 | 5.6063 | 3.5894 | 1.1997 | -1.3315 | -4.0198 | -7.07 | -10.1246 | -18.0359 | -27.5264 | -32.1638 | -34.6901 | 10.9904 | 10.631 | 10.121 | 9.0258 | 7.6118 | 6.0863 | 4.4599 | 2.5919 | 0.73209 | -3.8344 | -9.3621 | -12.4719 | -14.1457 | 6.8523 | 5.7522 | 4.5103 | 2.6902 | 0.51261 | -1.8014 | -4.2618 | -7.0717 | -9.8978 | -17.1353 | -25.85 | -30.1806 | -32.5317
|  | WAREHAM | ST |  |  | 9.2777 | 8.9727 | 8.609 | 7.8955 | 6.8095 | 5.6485 | 4.4178 | 3.1562 | 1.1123 | -5.7719 | -16.1657 | -21.8454 | -25.3429 | 11.1391 | 10.8786 | 10.5769 | 10.2254 | 9.6564 | 9.0326 | 8.3484 | 7.3779 | 5.6646 | -0.11591 | -8.51 | -13.2765 | -17.0395 | 8.2421 | 7.8246 | 7.328 | 6.6071 | 5.6111 | 4.5446 | 3.414 | 2.25 | 0.30299 | -6.2946 | -16.2329 | -21.5292 | -24.7154
|  | WAREHAM | FS |  |  | 9.3034 | 9.0075 | 8.6589 | 8.0437 | 4.6776 | 1.2407 | -2.2686 | -8.2469 | -9.8571 | -15.0132 | -25.1515 | -31.1752 | -33.9055 | 11.1422 | 10.881 | 10.5818 | 10.2562 | 7.4473 | 4.5913 | 1.6834 | -3.978 | -5.2084 | -9.2522 | -17.5549 | -23.7355 | -29.1409 | 11.1422 | 10.881 | 10.5818 | 10.2562 | 7.4473 | 4.5913 | 1.6834 | -3.978 | -5.2084 | -9.2522 | -17.5549 | -23.7355 | -29.1409
MELKSHAM GSP | WEST GRAFTON | WEST GRAFTON | MINIMUM HEADROOM | SU 24302 59215 | YES | 18.1629 | 16.6691 | 15.1073 | 13.042 | 10.9263 | 8.6886 | 6.2956 | 3.4037 | 0.50624 | -6.4791 | -14.087 | -16.1451 | -17.1854 | 30.4472 | 29.6773 | 28.8618 | 27.8352 | 26.7699 | 25.6116 | 24.3546 | 22.7581 | 21.1506 | 17.5334 | 13.8115 | 10.9574 | 7.8898 | 22.4934 | 21.1438 | 19.727 | 17.8479 | 15.9138 | 13.8568 | 11.6498 | 8.9502 | 6.2438 | -0.16764 | -7.0578 | -8.8739 | -9.7053
|  | WEST GRAFTON | CT |  |  | 19.7496 | 18.8616 | 17.7886 | 16.4698 | 15.1265 | 13.7177 | 12.1733 | 10.4132 | 7.7703 | 1.2895 | -8.4725 | -14.7691 | -17.1854 | 30.9932 | 30.4425 | 29.76 | 29.0013 | 28.2174 | 27.3757 | 26.4394 | 25.3423 | 23.7823 | 20.0743 | 14.8027 | 10.9574 | 7.8898 | 23.8791 | 23.0688 | 22.0745 | 20.8567 | 19.6097 | 18.2963 | 16.8516 | 15.1913 | 12.7096 | 6.7128 | -2.0441 | -7.5894 | -9.7053
|  | WEST GRAFTON | LW |  |  | 18.1629 | 16.6691 | 15.1073 | 13.042 | 10.9263 | 8.6886 | 6.2956 | 3.4037 | 0.50624 | -6.4791 | -14.087 | -16.1451 | -17.0716 | 30.4472 | 29.6773 | 28.8618 | 27.8352 | 26.7699 | 25.6116 | 24.3546 | 22.7581 | 21.1506 | 17.5334 | 13.8115 | 12.9315 | 12.5459 | 22.4934 | 21.1438 | 19.727 | 17.8479 | 15.9138 | 13.8568 | 11.6498 | 8.9502 | 6.2438 | -0.16764 | -7.0578 | -8.8739 | -9.683
|  | WEST GRAFTON | ST |  |  | 20.6861 | 20.2018 | 19.6724 | 18.9903 | 18.2987 | 17.5601 | 16.76 | 15.8561 | 14.8836 | 10.8464 | 3.6027 | 0.1185 | -2.1157 | 31.557 | 31.2469 | 30.8998 | 30.4773 | 30.0416 | 29.5621 | 29.0343 | 28.4269 | 27.8101 | 25.1255 | 20.0739 | 17.2013 | 14.2097 | 24.7715 | 24.3447 | 23.8719 | 23.2429 | 22.6001 | 21.9099 | 21.16 | 20.3081 | 19.3997 | 15.5603 | 8.7274 | 5.5981 | 3.6416
|  | WEST GRAFTON | FS |  |  | 20.8937 | 20.4941 | 20.0767 | 19.3231 | 18.5578 | 17.7879 | 16.9476 | 16.0592 | 14.9238 | 10.993 | 1.5732 | -3.7002 | -6.427 | 31.6222 | 31.3382 | 31.0335 | 30.6055 | 30.1618 | 29.7022 | 29.1835 | 28.6191 | 27.9359 | 25.4372 | 18.9735 | 14.2139 | 9.3161 | 31.6222 | 31.3382 | 31.0335 | 30.6055 | 30.1618 | 29.7022 | 29.1835 | 28.6191 | 27.9359 | 25.4372 | 18.9735 | 14.2139 | 9.3161
NURSLING GSP | WINCHESTER | WINCHESTER | MINIMUM HEADROOM | SU 44965 26671 | YES | 24.9273 | 22.4999 | 19.7256 | 15.4341 | 10.9037 | 6.1002 | 1.0613 | -4.5993 | -10.218 | -25.6244 | -42.7058 | -47.5545 | -52.8694 | 48.0804 | 47.3943 | 46.4259 | 45.3399 | 43.7944 | 40.9848 | 37.9779 | 34.2751 | 30.6485 | 21.6691 | 10.6364 | 0.97408 | -11.8469 | 27.676 | 25.4867 | 22.9721 | 19.309 | 15.4083 | 11.1671 | 6.6279 | 1.2254 | -4.0844 | -17.6165 | -31.9727 | -35.9699 | -40.0921
|  | WINCHESTER | CT |  |  | 27.1731 | 25.537 | 23.5222 | 20.5975 | 17.4641 | 14.2342 | 10.8242 | 7.2011 | 1.8071 | -12.8913 | -34.8553 | -47.5545 | -52.8694 | 48.0804 | 47.3943 | 46.4259 | 45.3399 | 44.1747 | 42.7198 | 40.2035 | 37.4265 | 33.6034 | 24.0305 | 10.6364 | 0.97408 | -9.2762 | 29.1124 | 27.4642 | 25.4385 | 22.7948 | 19.9446 | 16.9436 | 13.698 | 10.1645 | 4.9611 | -8.0252 | -25.57 | -35.6081 | -40.0921
|  | WINCHESTER | LW |  |  | 24.9273 | 22.4999 | 19.7256 | 15.4341 | 10.9037 | 6.1002 | 1.0613 | -4.5993 | -10.218 | -25.6244 | -42.7058 | -47.5229 | -49.3217 | 48.1547 | 47.4811 | 46.5141 | 45.3669 | 43.7944 | 40.9848 | 37.9779 | 34.2751 | 30.6485 | 21.6691 | 12.5749 | 10.6204 | 9.8857 | 27.676 | 25.4867 | 22.9721 | 19.309 | 15.4083 | 11.1671 | 6.6279 | 1.2254 | -4.0844 | -17.6165 | -31.9727 | -35.9699 | -37.5015
|  | WINCHESTER | ST |  |  | 39.7089 | 38.8712 | 27.0216 | 25.4654 | 23.8038 | 22.0373 | 20.2293 | 18.2573 | 16.1378 | 7.6624 | -9.206 | -17.3369 | -21.8921 | 59.5123 | 59.1437 | 47.7884 | 47.0227 | 46.1974 | 45.3027 | 44.4527 | 43.4426 | 42.3262 | 35.2894 | 21.1429 | 11.8692 | 1.7007 | 41.797 | 40.9956 | 29.1927 | 27.7316 | 26.163 | 24.4701 | 22.6949 | 20.7149 | 18.6844 | 9.9229 | -5.662 | -12.6956 | -16.4338
|  | WINCHESTER | FS |  |  | 40.0217 | 39.3307 | 38.419 | 36.8523 | 35.2391 | 22.7898 | 21.0819 | 19.3098 | 17.2111 | 10.0209 | -6.5934 | -16.7148 | -20.9384 | 59.5439 | 59.1996 | 58.6247 | 57.938 | 57.2208 | 45.7143 | 45.0181 | 44.2595 | 43.4378 | 37.0553 | 20.8968 | 6.12 | -11.8469 | 59.5439 | 59.1996 | 58.6247 | 57.938 | 57.2208 | 45.7143 | 45.0181 | 44.2595 | 43.4378 | 37.0553 | 20.8968 | 6.12 | -11.8469
MANNINGTON GSP | WINFRITH HEATH | WINFRITH HEATH | MINIMUM HEADROOM | SY 80748 86538 | YES | 31.6798 | 30.8957 | 30.1226 | 29.262 | 28.4923 | 27.7063 | 26.6803 | 25.6076 | 24.6293 | 22.3391 | 20.2775 | 19.8062 | 19.492 | 28.1431 | 27.417 | 26.7009 | 25.9653 | 25.3515 | 24.8325 | 24.3596 | 23.8604 | 23.4242 | 22.4732 | 21.9361 | 21.8644 | 21.7747 | 28.2186 | 27.5326 | 26.8569 | 26.1653 | 25.6028 | 25.1398 | 24.2858 | 23.3403 | 22.474 | 20.4418 | 18.6465 | 18.2343 | 17.9583
|  | WINFRITH HEATH | CT |  |  | 31.902 | 31.1966 | 30.5007 | 29.7413 | 29.0756 | 28.4606 | 27.8507 | 27.1576 | 26.2345 | 24.1014 | 21.5187 | 20.1365 | 19.9357 | 28.1745 | 27.4633 | 26.7556 | 26.0373 | 25.442 | 24.9446 | 24.4949 | 24.0344 | 23.6085 | 22.6848 | 22.0742 | 21.869 | 21.7747 | 30.0417 | 29.2927 | 28.5451 | 27.7041 | 26.9318 | 26.1929 | 25.446 | 24.7005 | 23.8877 | 21.9997 | 19.748 | 18.5362 | 18.3597
|  | WINFRITH HEATH | LW |  |  | 31.6798 | 30.8957 | 30.1226 | 29.262 | 28.4923 | 27.7063 | 26.6803 | 25.6076 | 24.6293 | 22.3391 | 20.2775 | 19.8062 | 19.492 | 28.1431 | 27.417 | 26.7009 | 25.9653 | 25.3515 | 24.8325 | 24.3596 | 23.8604 | 23.4242 | 22.4732 | 21.9361 | 21.8644 | 21.8213 | 29.7081 | 28.8328 | 27.9786 | 26.9915 | 26.07 | 25.1841 | 24.2858 | 23.3403 | 22.474 | 20.4418 | 18.6465 | 18.2343 | 17.9583
|  | WINFRITH HEATH | ST |  |  | 31.9976 | 31.3541 | 30.7166 | 30.0488 | 29.4944 | 29.0138 | 28.5503 | 28.06 | 27.6087 | 26.3822 | 24.6673 | 23.8382 | 23.3175 | 28.2127 | 27.5237 | 26.8437 | 26.1509 | 25.585 | 25.12 | 24.7081 | 24.2845 | 23.9221 | 23.042 | 22.3371 | 22.0777 | 21.944 | 30.1477 | 29.4801 | 28.826 | 28.1148 | 27.4968 | 26.9375 | 26.4041 | 25.8618 | 25.3736 | 24.0281 | 22.5098 | 21.7505 | 21.2674
|  | WINFRITH HEATH | FS |  |  | 32.0296 | 31.3867 | 30.7608 | 30.0769 | 29.5067 | 28.9938 | 28.5129 | 28.0168 | 27.5483 | 26.149 | 23.7666 | 22.5317 | 21.7851 | 28.2186 | 27.5326 | 26.8569 | 26.1653 | 25.6028 | 25.1398 | 24.7301 | 24.3134 | 23.9548 | 23.1202 | 22.3871 | 21.9961 | 21.777 | 28.2186 | 27.5326 | 26.8569 | 26.1653 | 25.6028 | 25.1398 | 24.7301 | 24.3134 | 23.9548 | 23.1202 | 22.3871 | 21.9961 | 21.777
COWLEY GSP | WITNEY BSP | WITNEY BSP | MINIMUM HEADROOM | SP 35605 08274 | NO | 17.9757 | 14.094 | 9.9103 | 4.2046 | -1.9521 | -8.0088 | -14.4409 | -21.8179 | -29.1995 | -46.4393 | -65.6255 | -72.3247 | -76.2381 | 51.0213 | 49.0908 | 46.987 | 44.2603 | 41.1876 | 38.1059 | 34.7962 | 30.8257 | 26.8818 | 18.1405 | 6.3725 | -6.776 | -19.2798 | 32.8841 | 29.4373 | 25.7205 | 20.6496 | 15.1511 | 9.6836 | 3.8608 | -2.9067 | -9.6821 | -25.3197 | -42.7259 | -48.8005 | -52.3121
|  | WITNEY BSP | CT |  |  | 21.8437 | 19.4411 | 16.4872 | 12.7094 | 8.503 | 4.482 | 0.081976 | -4.8435 | -11.6833 | -27.292 | -49.7935 | -63.3158 | -68.5133 | 52.4376 | 51.0468 | 49.334 | 47.3017 | 44.9505 | 42.6601 | 40.1425 | 37.285 | 33.5031 | 24.8206 | 11.8407 | 2.6349 | -4.5324 | 36.4023 | 34.253 | 31.5837 | 28.1994 | 24.4107 | 20.742 | 16.7135 | 12.1578 | 5.8165 | -8.5058 | -28.6243 | -40.6911 | -45.3238
|  | WITNEY BSP | LW |  |  | 17.9757 | 14.094 | 9.9103 | 4.2046 | -1.9521 | -8.0088 | -14.4409 | -21.8179 | -29.1995 | -46.4393 | -65.6255 | -72.3247 | -76.2381 | 51.0213 | 49.0908 | 46.987 | 44.2603 | 41.1876 | 38.1059 | 34.7962 | 30.8257 | 26.8818 | 18.1405 | 8.1423 | 4.2213 | 1.9828 | 32.8841 | 29.4373 | 25.7205 | 20.6496 | 15.1511 | 9.6836 | 3.8608 | -2.9067 | -9.6821 | -25.3197 | -42.7259 | -48.8005 | -52.3121
|  | WITNEY BSP | ST |  |  | 23.7625 | 22.2711 | 20.578 | 18.2993 | 15.6985 | 13.2002 | 10.5281 | 7.6331 | 3.9932 | -8.9427 | -29.8127 | -40.9967 | -47.729 | 53.0444 | 52.6558 | 51.6453 | 50.3598 | 48.8084 | 47.2882 | 45.6509 | 43.8499 | 41.3709 | 32.5698 | 18.1272 | 9.0783 | 1.1764 | 38.2242 | 36.9557 | 35.5174 | 33.513 | 31.2035 | 28.9454 | 26.5241 | 23.8778 | 20.4968 | 8.2163 | -11.4455 | -21.6206 | -27.601
|  | WITNEY BSP | FS |  |  | 24.2503 | 22.9936 | 21.617 | 18.8443 | 13.9389 | 9.1341 | 4.1216 | -3.0336 | -7.0881 | -19.7608 | -46.759 | -62.6469 | -71.3477 | 53.0594 | 52.7069 | 52.0321 | 50.5874 | 47.0362 | 43.52 | 39.8734 | 34.1089 | 31.7249 | 23.995 | 6.3725 | -6.776 | -19.2798 | 53.0594 | 52.7069 | 52.0321 | 50.5874 | 47.0362 | 43.52 | 39.8734 | 34.1089 | 31.7249 | 23.995 | 6.3725 | -6.776 | -19.2798
BRAMLEY (FLEE) | WOKINGHAM BSP | WOKINGHAM BSP | MINIMUM HEADROOM | SU 79589 67665 | YES | 51.415 | 49.107 | 45.581 | 42.8533 | 39.9346 | 36.8824 | 33.5492 | 29.5379 | 25.8294 | 16.8392 | 6.1924 | 0.64043 | -3.5492 | 58.7358 | 56.7883 | 53.4847 | 51.9796 | 50.314 | 48.5246 | 46.5363 | 43.9667 | 41.622 | 36.3491 | 29.4731 | 23.3822 | 17.9434 | 53.8353 | 51.5175 | 47.7696 | 45.5042 | 43.0505 | 40.4447 | 37.5675 | 33.9595 | 30.6485 | 22.4923 | 12.7842 | 8.0206 | 4.3497
|  | WOKINGHAM BSP | CT |  |  | 52.0978 | 49.9477 | 46.6738 | 44.606 | 42.3862 | 40.1945 | 37.7975 | 34.9435 | 31.2103 | 22.2091 | 9.176 | 0.64043 | -3.5492 | 58.8067 | 56.7965 | 53.4994 | 52.207 | 50.7787 | 49.3092 | 47.685 | 45.7136 | 43.2542 | 37.6165 | 29.4731 | 23.3822 | 17.9434 | 54.2658 | 52.0172 | 48.4385 | 46.6792 | 44.77 | 42.8471 | 40.7282 | 38.1641 | 34.8263 | 27.2155 | 15.5869 | 8.0206 | 4.3497
|  | WOKINGHAM BSP | LW |  |  | 51.415 | 49.107 | 45.581 | 42.8533 | 39.9346 | 36.8824 | 33.5492 | 29.5379 | 25.8294 | 16.8392 | 6.1924 | 1.7456 | -0.57606 | 58.7358 | 56.7883 | 53.4847 | 51.9796 | 50.314 | 48.5246 | 46.5363 | 43.9667 | 41.622 | 36.3491 | 30.1436 | 27.6395 | 26.2937 | 53.8353 | 51.5175 | 47.7696 | 45.5042 | 43.0505 | 40.4447 | 37.5675 | 33.9595 | 30.6485 | 22.4923 | 12.7842 | 8.8191 | 6.7837
|  | WOKINGHAM BSP | ST |  |  | 84.0247 | 82.5052 | 49.2452 | 48.1104 | 46.8618 | 45.5858 | 44.2052 | 42.6316 | 40.77 | 33.3643 | 22.1224 | 16.2605 | 12.8243 | 90.3687 | 88.7965 | 55.2903 | 54.484 | 53.5657 | 52.6044 | 51.5552 | 50.3464 | 48.8699 | 42.9153 | 33.6627 | 28.0447 | 22.8984 | 86.1611 | 84.5137 | 50.8915 | 49.8922 | 48.7778 | 47.6259 | 46.3733 | 44.9371 | 43.22 | 36.187 | 25.782 | 20.7664 | 17.9889
|  | WOKINGHAM BSP | FS |  |  | 84.1597 | 82.7566 | 80.2878 | 79.2731 | 77.2437 | 75.198 | 73.029 | 69.7154 | 68.1891 | 62.9037 | 51.438 | 45.2273 | 42.5154 | 90.4123 | 88.8974 | 86.1044 | 85.4138 | 83.6965 | 81.9335 | 80.0621 | 77.0634 | 75.8489 | 71.5056 | 61.293 | 53.6665 | 45.9467 | 90.4123 | 88.8974 | 86.1044 | 85.4138 | 83.6965 | 81.9335 | 80.0621 | 77.0634 | 75.8489 | 71.5056 | 61.293 | 53.6665 | 45.9467
LOVEDEAN GSP | WYMERING BSP | WYMERING BSP | MINIMUM HEADROOM | SU 64948 05441 | YES | 47.9372 | 45.3004 | 42.0071 | 36.9669 | 31.2676 | 25.3133 | 18.9821 | 11.6534 | 3.8781 | -19.5984 | -50.5035 | -73.9497 | -88.5609 | 72.582 | 71.5645 | 70.2202 | 68.7701 | 65.6534 | 62.332 | 58.7402 | 54.752 | 49.6106 | 33.2364 | 4.0612 | -33.6464 | -103.951 | 52.5029 | 50.031 | 46.974 | 42.4506 | 37.3274 | 31.8902 | 26.0793 | 19.2207 | 11.882 | -9.9288 | -37.5746 | -56.0207 | -103.951
|  | WYMERING BSP | CT |  |  | 49.1379 | 47.2526 | 44.2892 | 40.4829 | 36.0789 | 31.5005 | 26.5955 | 21.255 | 13.6112 | -9.9887 | -48.1392 | -73.9497 | -88.5609 | 72.582 | 71.5645 | 70.2202 | 68.7701 | 65.6534 | 62.332 | 58.7402 | 54.752 | 49.6106 | 33.2364 | 4.0612 | -25.1326 | -61.841 | 53.4635 | 51.7076 | 48.8774 | 45.3836 | 41.3519 | 37.1213 | 32.5674 | 27.5251 | 20.4011 | -1.3711 | -34.6094 | -56.0207 | -67.9938
|  | WYMERING BSP | LW |  |  | 47.9372 | 45.3004 | 42.0071 | 36.9669 | 31.2676 | 25.3133 | 18.9821 | 11.6534 | 3.8781 | -19.5984 | -50.5035 | -65.4286 | -74.8099 | 72.6854 | 71.6449 | 70.3471 | 68.9648 | 65.9625 | 62.5958 | 59.0048 | 54.7675 | 50.2301 | 36.5885 | 19.4622 | 11.8145 | 6.8993 | 52.5029 | 50.031 | 46.974 | 42.4506 | 37.3274 | 31.8902 | 26.0793 | 19.2207 | 11.882 | -9.9288 | -37.5746 | -50.039 | -57.778
|  | WYMERING BSP | ST |  |  | 50.4225 | 49.6317 | 48.5963 | 46.8399 | 44.5858 | 42.2525 | 39.7387 | 36.9543 | 33.5779 | 20.8196 | -6.8772 | -23.6514 | -34.5206 | 73.2997 | 72.6037 | 71.725 | 70.7523 | 69.5817 | 68.1668 | 65.7854 | 63.1153 | 59.9289 | 47.9566 | 20.5693 | -6.495 | -41.6993 | 55.4178 | 54.5063 | 53.2754 | 51.5662 | 49.5055 | 47.3378 | 44.9867 | 42.3363 | 39.1632 | 26.9261 | 0.53561 | -14.1292 | -23.0155
|  | WYMERING BSP | FS |  |  | 50.4795 | 49.7103 | 48.7215 | 47.4875 | 44.6793 | 41.785 | 38.7589 | 34.4754 | 31.9596 | 23.0143 | 2.207 | -13.2707 | -20.8527 | 73.3232 | 72.6274 | 71.7654 | 70.8754 | 68.764 | 65.906 | 62.4405 | 57.571 | 54.3172 | 42.2701 | 11.4188 | -33.6464 | -103.951 | 73.3232 | 72.6274 | 71.7654 | 70.8754 | 68.764 | 65.906 | 62.4405 | 57.571 | 54.3172 | 42.2701 | 11.4188 | -33.6464 | -103.951
COWLEY GSP | YARNTON BSP | YARNTON BSP | MINIMUM HEADROOM | SP 35605 08274 | NO | 28.2441 | 22.8795 | 16.9913 | 8.8308 | 0.17323 | -8.4566 | -17.4816 | -27.4568 | -37.7507 | -61.5624 | -86.7946 | -95.0617 | -99.8182 | 58.6843 | 55.8127 | 52.6769 | 48.5531 | 44.0997 | 39.5916 | 34.8426 | 29.4376 | 23.8869 | 11.5645 | -0.98654 | -8.7993 | -20.5722 | 40.9649 | 36.2986 | 31.1802 | 24.1685 | 16.6863 | 9.1258 | 1.159 | -7.8668 | -17.1952 | -38.2328 | -60.137 | -67.4691 | -71.6608
|  | YARNTON BSP | CT |  |  | 33.4707 | 29.7301 | 25.2352 | 19.1757 | 12.6606 | 6.2967 | -0.3994 | -7.5399 | -17.036 | -39.2684 | -71.4916 | -90.7236 | -95.4673 | 60.501 | 58.2076 | 55.4842 | 52.119 | 48.4532 | 44.8155 | 40.962 | 36.7804 | 31.4786 | 19.2602 | 2.5705 | -8.4244 | -15.0349 | 45.1539 | 41.8548 | 37.8349 | 32.572 | 26.8845 | 21.2631 | 15.301 | 8.8389 | 0.18213 | -19.7962 | -47.2383 | -63.4557 | -67.6354
|  | YARNTON BSP | LW |  |  | 28.2441 | 22.8795 | 16.9913 | 8.8308 | 0.17323 | -8.4566 | -17.4816 | -27.4568 | -37.7507 | -61.5624 | -86.7946 | -95.0617 | -99.8182 | 58.6843 | 55.8127 | 52.6769 | 48.5531 | 44.0997 | 39.5916 | 34.8426 | 29.4376 | 23.8869 | 11.5645 | -0.98654 | -5.1076 | -7.4401 | 40.9649 | 36.2986 | 31.1802 | 24.1685 | 16.6863 | 9.1258 | 1.159 | -7.8668 | -17.1952 | -38.2328 | -60.137 | -67.4691 | -71.6608
|  | YARNTON BSP | ST |  |  | 35.1946 | 32.4435 | 29.435 | 25.2594 | 20.8068 | 16.6858 | 12.449 | 7.9705 | 3.0192 | -11.8403 | -35.8652 | -49.0483 | -57.3617 | 61.6311 | 59.941 | 58.0922 | 55.6358 | 52.9623 | 50.3992 | 47.7351 | 44.8766 | 41.6565 | 31.7402 | 15.722 | 6.3592 | -1.6165 | 46.9981 | 44.7136 | 42.1983 | 38.6269 | 34.7919 | 31.1839 | 27.4459 | 23.442 | 19.014 | 4.9524 | -17.7586 | -29.1409 | -35.9965
|  | YARNTON BSP | FS |  |  | 35.8264 | 33.4167 | 30.8381 | 25.5678 | 18.9334 | 12.2926 | 5.5292 | -2.5002 | -8.9264 | -27.1272 | -58.5145 | -76.3252 | -85.8381 | 61.8473 | 60.2781 | 58.6017 | 55.8445 | 51.7807 | 47.6626 | 43.4348 | 37.9253 | 34.3238 | 24.0275 | 4.7236 | -8.7993 | -20.5722 | 61.8473 | 60.2781 | 58.6017 | 55.8445 | 51.7807 | 47.6626 | 43.4348 | 37.9253 | 34.3238 | 24.0275 | 4.7236 | -8.7993 | -20.5722
AXMINSTER | YEOVIL BSP | YEOVIL BSP | MINIMUM HEADROOM | ST 57586 16894 | YES | -2.5167 | -7.5911 | -12.8317 | -20.1435 | -27.7165 | -35.1986 | -42.5342 | -50.9677 | -59.5419 | -81.5406 | -105.2583 | -113.6807 | -119.5829 | 40.9131 | 38.864 | 36.0994 | 32.5377 | 28.7849 | 24.8667 | 20.8172 | 15.842 | 10.7387 | -0.99105 | -12.443 | -20.0086 | -35.1119 | 11.1985 | 6.7062 | 2.0739 | -4.4349 | -11.1625 | -17.801 | -24.2938 | -31.7153 | -39.4643 | -59.2262 | -80.2939 | -87.521 | -92.5236
|  | YEOVIL BSP | CT |  |  | 3.3326 | 0.58478 | -2.8322 | -7.5606 | -12.5397 | -17.7022 | -22.9225 | -28.6719 | -36.6202 | -57.5251 | -87.7155 | -106.9056 | -116.251 | 41.7956 | 40.8748 | 39.2823 | 36.5745 | 33.6868 | 30.6179 | 27.3516 | 23.5726 | 18.5559 | 6.2368 | -9.197 | -20.0086 | -29.421 | 16.5829 | 14.2017 | 11.2587 | 7.1199 | 2.7574 | -1.888 | -6.6191 | -11.8585 | -19.1292 | -37.991 | -64.7004 | -81.4049 | -89.4323
|  | YEOVIL BSP | LW |  |  | -2.5167 | -7.5911 | -12.8317 | -20.1435 | -27.7165 | -35.1986 | -42.5342 | -50.9677 | -59.5419 | -81.5406 | -105.2583 | -113.6807 | -119.5829 | 40.9131 | 38.864 | 36.0994 | 32.5377 | 28.7849 | 24.8667 | 20.8172 | 15.842 | 10.7387 | -0.99105 | -12.443 | -16.0969 | -18.677 | 11.1985 | 6.7062 | 2.0739 | -4.4349 | -11.1625 | -17.801 | -24.2938 | -31.7153 | -39.4643 | -59.2262 | -80.2939 | -87.521 | -92.5236
|  | YEOVIL BSP | ST |  |  | 4.9512 | 3.0588 | 1.1241 | -1.7899 | -4.8533 | -8.0359 | -11.4557 | -15.2182 | -19.247 | -33.7633 | -57.8448 | -70.0322 | -78.1762 | 42.3215 | 41.6874 | 40.9978 | 40.0344 | 38.6344 | 36.6601 | 34.4859 | 32.0352 | 29.5577 | 19.8782 | 3.1247 | -6.0356 | -15.0066 | 18.0206 | 16.4037 | 14.7608 | 12.2609 | 9.6422 | 6.9086 | 3.9608 | 0.73021 | -2.8561 | -16.0229 | -38.0818 | -48.8101 | -55.7823
|  | YEOVIL BSP | FS |  |  | 5.6587 | 4.0324 | 2.4069 | -1.3451 | -5.1979 | -9.1599 | -13.3211 | -17.667 | -22.8802 | -39.4966 | -73.144 | -93.8878 | -103.2907 | 42.3123 | 41.6691 | 41.088 | 40.1418 | 38.7017 | 36.6469 | 34.3847 | 31.9634 | 29.1265 | 19.4545 | -2.3099 | -18.8172 | -35.1119 | 42.3123 | 41.6691 | 41.088 | 40.1418 | 38.7017 | 36.6469 | 34.3847 | 31.9634 | 29.1265 | 19.4545 | -2.3099 | -18.8172 | -35.1119

## BSP Headroom Gen
Grid Supply Point | Bulk Supply Point |  | Scenario | Grid Reference | Upstream Constraint (YES / NO) | Generation Headroom Winter (MVA) | [12 empty] | Generation Headroom Summer (MVA) | [12 empty] | Generation Headroom Spring/Autumn (MVA)
[6 empty] | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2035 | 2040 | 2045 | 2050 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2035 | 2040 | 2045 | 2050 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2035 | 2040 | 2045 | 2050
BRAMLEY (FLEE) | ALDERSHOT BSP | ALDERSHOT BSP | MINIMUM HEADROOM | SU 85922 48779 | YES | 199.5197 | 199.5197 | 199.5197 | 199.5152 | 199.5107 | 199.506 | 199.5013 | 199.4939 | 199.4914 | 199.4559 | 199.3568 | 199.2251 | 199.5742 | 195.2125 | 195.1788 | 195.1497 | 195.1095 | 195.0616 | 194.9989 | 194.9394 | 194.8822 | 194.8277 | 194.6519 | 188.3685 | 175.1945 | 164.658 | 196.7572 | 196.7432 | 196.7311 | 196.7118 | 196.6892 | 196.6604 | 196.627 | 196.5836 | 196.5437 | 196.3955 | 195.3106 | 184.8786 | 174.8466
|  | ALDERSHOT BSP | CT |  |  | 227.9791 | 227.9772 | 227.9743 | 227.928 | 227.7905 | 228.6619 | 227.9033 | 227.2982 | 226.8652 | 225.4809 | 222.9061 | 217.6239 | 206.83 | 217.7572 | 217.6954 | 217.5716 | 217.3907 | 217.129 | 217.8365 | 216.9392 | 215.927 | 213.3635 | 205.276 | 192.4541 | 180.0322 | 167.8072 | 219.9893 | 219.9873 | 219.9845 | 219.9381 | 219.8007 | 220.6503 | 219.7932 | 219.0806 | 218.5259 | 213.1943 | 201.092 | 189.3619 | 177.8628
|  | ALDERSHOT BSP | LW |  |  | 227.9693 | 227.9633 | 228.9659 | 228.9371 | 228.7983 | 228.3348 | 227.8536 | 227.347 | 226.8818 | 225.017 | 222.9833 | 213.485 | 204.1437 | 217.7547 | 217.6927 | 218.5828 | 218.4052 | 218.125 | 217.4996 | 216.8489 | 215.0616 | 212.2202 | 202.5565 | 188.3685 | 175.1945 | 164.658 | 219.9795 | 219.9735 | 220.9761 | 220.9473 | 220.8085 | 220.3163 | 219.7147 | 219.0771 | 218.4762 | 210.6332 | 197.2986 | 184.8786 | 174.8466
|  | ALDERSHOT BSP | ST |  |  | 199.5197 | 199.5197 | 199.5197 | 199.5152 | 199.5107 | 199.506 | 199.5013 | 199.4939 | 199.4914 | 199.4559 | 199.3568 | 199.2251 | 199.5742 | 195.2125 | 195.1788 | 195.1497 | 195.1095 | 195.0616 | 194.9989 | 194.9394 | 194.8822 | 194.8277 | 194.6519 | 194.2302 | 193.7205 | 193.9173 | 196.7572 | 196.7432 | 196.7311 | 196.7118 | 196.6892 | 196.6604 | 196.627 | 196.5836 | 196.5437 | 196.3955 | 195.3106 | 193.9681 | 193.944
|  | ALDERSHOT BSP | FS |  |  | 227.9815 | 227.9813 | 227.9812 | 227.9571 | 226.8061 | 225.6551 | 224.4082 | 222.0012 | 221.6143 | 220.353 | 219.7777 | 218.411 | 217.6368 | 217.8452 | 217.8369 | 217.8271 | 217.7784 | 216.602 | 215.4237 | 214.1496 | 211.7086 | 211.2873 | 209.9076 | 209.1486 | 207.5619 | 206.582 | 219.9917 | 219.9915 | 219.9914 | 219.9673 | 218.8163 | 217.6653 | 216.4184 | 214.0114 | 213.6245 | 212.3632 | 211.7879 | 210.3825 | 209.4624
BRAMLEY (FLEE) | ALTON | ALTON | MINIMUM HEADROOM | SU 72730 39772 | YES | 127.6508 | 127.0765 | 125.3353 | 120.3796 | 84.7099 | 81.6134 | 78.4518 | 73.3948 | 69.9933 | 55.3056 | 9.308 | -13.0992 | -21.6665 | 78.8354 | 78.1602 | 76.2296 | 69.2898 | 29.7206 | 26.3074 | 22.8324 | 17.361 | 13.4082 | -3.0204 | -60.1299 | -85.7941 | -95.3404 | 78.7795 | 78.1525 | 76.3126 | 68.3468 | 27.9672 | 24.7057 | 21.3807 | 16.1076 | 12.4187 | -2.8927 | -56.3848 | -82.0562 | -91.6047
|  | ALTON | CT |  |  | 127.6508 | 127.0765 | 125.3353 | 120.3796 | 116.1238 | 111.8361 | 106.3077 | 101.865 | 96.6814 | 87.3388 | 63.9987 | 47.3705 | 30.6521 | 78.8354 | 78.1602 | 76.2296 | 70.4356 | 65.4479 | 60.4243 | 54.05 | 48.9441 | 42.9225 | 34.9131 | 8.2542 | -10.5768 | -29.6929 | 78.7795 | 78.1525 | 76.3126 | 70.9199 | 66.2825 | 61.6111 | 55.6417 | 50.8533 | 45.2328 | 39.6376 | 13.5594 | -4.886 | -23.5826
|  | ALTON | LW |  |  | 135.7834 | 135.2892 | 133.2785 | 123.729 | 114.0153 | 103.9267 | 93.7199 | 86.5754 | 79.8733 | 55.3056 | 9.308 | -13.0992 | -21.6665 | 91.2812 | 90.6907 | 88.5031 | 77.0955 | 65.7164 | 54.0047 | 42.1642 | 33.9627 | 26.1982 | -2.237 | -60.1299 | -85.7941 | -95.3404 | 92.4645 | 91.9152 | 89.8034 | 79.1919 | 68.6109 | 57.6976 | 46.6608 | 38.7199 | 31.1413 | 3.3829 | -56.3848 | -82.0562 | -91.6047
|  | ALTON | ST |  |  | 155.9916 | 155.9915 | 155.9914 | 155.9685 | 155.8522 | 155.5765 | 156.2905 | 155.9334 | 155.3383 | 153.5246 | 151.3729 | 149.9328 | 149.1171 | 144.003 | 143.9713 | 143.9186 | 143.8186 | 143.6198 | 143.2711 | 143.9077 | 143.4686 | 142.7541 | 139.2851 | 129.3977 | 121.02 | 112.7773 | 148.0018 | 148.0017 | 148.0016 | 147.9787 | 147.8624 | 147.5867 | 148.3007 | 147.9436 | 147.3485 | 145.2466 | 139.1232 | 131.2327 | 123.5114
|  | ALTON | FS |  |  | 128.7052 | 128.5664 | 128.2636 | 121.112 | 84.7099 | 81.6134 | 78.4518 | 73.3948 | 69.9933 | 55.8987 | 37.4784 | 23.4714 | 16.25 | 80.0613 | 79.8982 | 79.5821 | 69.2898 | 29.7206 | 26.3074 | 22.8324 | 17.361 | 13.4082 | -3.0204 | -24.4451 | -40.7386 | -49.1324 | 79.9232 | 79.7718 | 79.4621 | 68.3468 | 27.9672 | 24.7057 | 21.3807 | 16.1076 | 12.4187 | -2.8927 | -23.3648 | -39.269 | -47.4632
MELKSHAM GSP | AMESBURY | AMESBURY | MINIMUM HEADROOM | SU 15842 42724 | YES | 124.4566 | 242.0655 | 241.1538 | 237.3432 | 233.4897 | 229.535 | 224.5859 | 220.7464 | 215.672 | 206.7251 | 186.3002 | 164.8987 | 151.2326 | 73.3026 | 191.4746 | 190.4811 | 185.9936 | 181.4761 | 176.8656 | 171.0869 | 166.6341 | 160.7726 | 153.2839 | 129.7557 | 102.081 | 86.1881 | 75.6381 | 193.2017 | 192.2474 | 188.0839 | 183.8842 | 179.5876 | 174.206 | 170.0468 | 164.562 | 159.6174 | 136.6777 | 107.9072 | 92.3958
|  | AMESBURY | CT |  |  | 124.6703 | 242.6667 | 242.4465 | 241.141 | 239.9981 | 238.8459 | 237.3128 | 235.151 | 232.3294 | 222.6075 | 211.24 | 203.4806 | 193.6533 | 110.2154 | 228.8565 | 228.6257 | 227.2539 | 226.0533 | 224.763 | 222.9427 | 220.3767 | 217.1059 | 205.8181 | 192.5931 | 183.5762 | 172.114 | 111.8613 | 229.8382 | 229.5791 | 228.0306 | 226.6762 | 225.3114 | 223.4947 | 220.9337 | 217.6695 | 206.4219 | 193.3184 | 184.3837 | 173.0285
|  | AMESBURY | LW |  |  | 124.6397 | 242.6197 | 242.3644 | 239.601 | 236.81 | 233.8506 | 230.8296 | 227.0237 | 223.2769 | 209.4395 | 191.0169 | 179.8444 | 176.4107 | 110.1834 | 228.8073 | 228.5398 | 225.6356 | 222.3396 | 218.8653 | 215.3692 | 210.9701 | 206.6161 | 190.4582 | 168.9786 | 155.9929 | 151.9973 | 111.8256 | 229.7833 | 229.4833 | 226.2033 | 222.8929 | 219.4254 | 215.9362 | 211.5457 | 207.2115 | 191.2054 | 169.9257 | 157.0586 | 153.0997
|  | AMESBURY | ST |  |  | 124.4566 | 242.0655 | 241.1538 | 237.3432 | 233.4897 | 229.535 | 224.5859 | 220.7464 | 215.672 | 206.7251 | 186.3002 | 164.8987 | 151.2326 | 73.3026 | 191.4746 | 190.4811 | 185.9936 | 181.4761 | 176.8656 | 171.0869 | 166.6341 | 160.7726 | 153.2839 | 129.7557 | 102.081 | 86.1881 | 75.6381 | 193.2017 | 192.2474 | 188.0839 | 183.8842 | 179.5876 | 174.206 | 170.0468 | 164.562 | 159.6174 | 136.6777 | 107.9072 | 92.3958
|  | AMESBURY | FS |  |  | 124.8146 | 242.9004 | 242.8837 | 242.5741 | 242.2217 | 241.7159 | 241.2159 | 240.5543 | 239.5877 | 235.6458 | 230.6819 | 226.4031 | 223.9324 | 110.3671 | 229.1022 | 229.0847 | 228.7605 | 228.3914 | 227.8609 | 227.3365 | 226.6428 | 225.6321 | 221.0509 | 215.2906 | 210.417 | 207.6288 | 112.0327 | 230.1158 | 230.0964 | 229.7333 | 229.3193 | 228.7229 | 228.1335 | 227.3545 | 226.2261 | 221.6057 | 215.8566 | 210.9916 | 208.208
BRAMLEY (ANDO-THAT) | ANDOVER BSP | ANDOVER BSP | MINIMUM HEADROOM | SU 35334 46598 | YES | 50.2626 | 48.6901 | 47.009 | 44.9416 | 41.0786 | 36.2426 | 31.3936 | 25.3356 | 20.0805 | 1.0581 | -41.9637 | -80.9793 | -88.647 | 19.913 | 17.5576 | 15.7792 | 13.3713 | 10.1745 | 4.6542 | -0.87946 | -7.7848 | -13.8956 | -36.0498 | -86.8875 | -132.0359 | -140.6942 | 26.8269 | 24.2464 | 22.4788 | 20.1085 | 16.7546 | 11.2979 | 5.778 | -1.1102 | -7.2038 | -29.2948 | -80.2508 | -125.2757 | -133.9141
|  | ANDOVER BSP | CT |  |  | 63.2529 | 48.6901 | 47.009 | 44.9416 | 42.7998 | 42.1908 | 39.6285 | 37.6956 | 34.9072 | 21.4092 | -4.554 | -28.7458 | -44.1879 | 34.6528 | 17.5576 | 15.7792 | 13.3713 | 10.9275 | 10.4976 | 7.5607 | 5.5718 | 2.8707 | -12.8704 | -42.7322 | -70.5768 | -88.3952 | 41.0617 | 24.2464 | 22.4788 | 20.1085 | 17.6981 | 17.0461 | 14.1506 | 11.9751 | 9.5235 | -6.1725 | -35.9557 | -63.7267 | -81.4972
|  | ANDOVER BSP | LW |  |  | 50.2626 | 49.6193 | 50.1309 | 45.7935 | 41.0786 | 36.2426 | 31.3936 | 25.3356 | 20.0805 | 1.0581 | -41.9637 | -80.9793 | -88.647 | 19.913 | 19.2185 | 20.5632 | 15.5589 | 10.1745 | 4.6542 | -0.87946 | -7.7848 | -13.8956 | -36.0498 | -86.8875 | -132.0359 | -140.6942 | 26.8269 | 26.1381 | 26.9956 | 22.065 | 16.7546 | 11.2979 | 5.778 | -1.1102 | -7.2038 | -29.2948 | -80.2508 | -125.2757 | -133.9141
|  | ANDOVER BSP | ST |  |  | 128.5092 | 128.4326 | 128.298 | 127.1473 | 126.009 | 124.8761 | 123.4551 | 121.3746 | 118.6742 | 109.2623 | 98.7242 | 91.5334 | 82.3479 | 116.4957 | 116.4151 | 116.2741 | 115.0659 | 113.8709 | 112.6517 | 110.9675 | 108.5027 | 105.3562 | 94.4423 | 82.1441 | 73.8023 | 63.0843 | 115.7054 | 115.6143 | 115.4559 | 114.0945 | 112.7484 | 111.4092 | 109.7284 | 107.2683 | 104.128 | 93.2444 | 81.0612 | 72.7947 | 62.177
|  | ANDOVER BSP | FS |  |  | 103.4925 | 103.3253 | 71.9015 | 57.4927 | 53.3843 | 50.1218 | 45.5021 | 37.3823 | 35.4407 | 28.3084 | 20.9311 | 13.2579 | 9.2015 | 80.5137 | 80.3177 | 43.3671 | 26.4007 | 22.2086 | 18.8258 | 14.0877 | 5.8117 | 3.6661 | -4.3076 | -11.8607 | -20.4113 | -24.967 | 86.2933 | 86.1005 | 49.7607 | 33.077 | 28.8942 | 25.5246 | 20.7997 | 12.5409 | 10.4179 | 2.5372 | -5.3917 | -13.9143 | -18.4599
MANNINGTON GSP | ARNEWOOD | ARNEWOOD | MINIMUM HEADROOM | SZ 26094 97294 | YES | 27.3419 | 12.9281 | 11.8358 | 9.8185 | 7.7919 | 7.379 | 5.0761 | 3.4722 | -0.31109 | -16.794 | -42.7425 | -66.3632 | -79.9981 | -2.3921 | -19.3696 | -20.5223 | -22.831 | -25.1538 | -25.3679 | -28.0151 | -29.6387 | -33.2957 | -51.9033 | -81.5442 | -109.3297 | -125.1147 | 5.2007 | -11.4935 | -12.6395 | -14.916 | -17.2061 | -17.6445 | -20.2536 | -22.0678 | -25.4578 | -44.0226 | -73.5891 | -101.4746 | -117.2163
|  | ARNEWOOD | CT |  |  | 98.0966 | 98.0812 | 97.1376 | 97.0601 | 96.7807 | 96.5012 | 96.2214 | 95.9408 | 95.7482 | 95.1699 | 89.6703 | 84.2949 | 79.7985 | 78.3083 | 78.1575 | 76.9059 | 76.3885 | 75.6632 | 74.9185 | 73.7201 | 72.507 | 71.3217 | 67.7878 | 58.3677 | 51.633 | 45.7545 | 86.7413 | 86.6004 | 85.3712 | 84.886 | 84.1931 | 83.4824 | 82.351 | 81.2058 | 80.0929 | 76.7746 | 67.8225 | 61.2062 | 55.4479
|  | ARNEWOOD | LW |  |  | 97.9626 | 97.9368 | 96.3642 | 96.2185 | 95.8362 | 95.4526 | 95.0675 | 94.6704 | 94.4258 | 93.6884 | 86.0659 | 80.4249 | 76.0707 | 78.1903 | 78.0379 | 76.1756 | 75.5091 | 74.5869 | 73.1737 | 71.7732 | 70.3398 | 69.0406 | 65.0705 | 53.6085 | 46.5414 | 40.9331 | 86.6222 | 86.479 | 84.6378 | 84.0093 | 83.1265 | 81.7884 | 80.4619 | 79.104 | 77.8817 | 74.1474 | 63.1638 | 56.2208 | 50.661
|  | ARNEWOOD | ST |  |  | 27.3419 | 12.9281 | 11.8358 | 9.8185 | 7.7919 | 7.379 | 5.0761 | 3.4722 | -0.31109 | -16.794 | -42.7425 | -66.3632 | -79.9981 | -2.3921 | -19.3696 | -20.5223 | -22.831 | -25.1538 | -25.3679 | -28.0151 | -29.6387 | -33.2957 | -51.9033 | -81.5442 | -109.3297 | -125.1147 | 5.2007 | -11.4935 | -12.6395 | -14.916 | -17.2061 | -17.6445 | -20.2536 | -22.0678 | -25.4578 | -44.0226 | -73.5891 | -101.4746 | -117.2163
|  | ARNEWOOD | FS |  |  | 98.2307 | 98.2255 | 97.6403 | 97.6145 | 95.0471 | 92.4796 | 89.9121 | 84.8029 | 84.2738 | 82.686 | 79.8332 | 77.9725 | 77.2683 | 78.6537 | 78.6377 | 77.5891 | 77.4731 | 74.8019 | 72.0271 | 69.2596 | 63.9073 | 63.1059 | 60.666 | 56.4972 | 53.3982 | 51.615 | 86.9664 | 86.9613 | 85.9369 | 85.8274 | 83.1638 | 80.4041 | 77.6511 | 72.3166 | 71.5351 | 69.1573 | 65.0845 | 62.0758 | 60.3712
BRAMLEY (BASI) | BASINGSTOKE T1A & T2A | BASINGSTOKE T1A & T2A | MINIMUM HEADROOM | SU 65132 52710 | YES | 94.3093 | 130.4791 | 129.5057 | 129.0198 | 128.3774 | 127.1382 | 125.3524 | 121.8585 | 121.3811 | 119.8785 | 117.3333 | 115.5189 | 111.1209 | 68.4612 | 105.8171 | 104.8142 | 104.2782 | 103.5856 | 102.4841 | 100.6872 | 97.1789 | 96.6863 | 95.1297 | 92.5055 | 89.9139 | 83.1373 | 72.3023 | 108.4616 | 107.4661 | 106.9426 | 106.2625 | 105.1267 | 103.3325 | 99.8278 | 99.339 | 97.7959 | 95.1914 | 93.325 | 86.4107
|  | BASINGSTOKE T1A & T2A | CT |  |  | 94.3637 | 130.5342 | 129.8418 | 129.4753 | 128.9884 | 128.5043 | 127.988 | 127.4272 | 126.8524 | 125.0452 | 121.4393 | 118.1914 | 120.3385 | 68.5147 | 105.8708 | 105.1481 | 104.7425 | 104.2182 | 103.697 | 103.1399 | 102.5331 | 101.905 | 99.8486 | 95.8828 | 92.3072 | 96.7721 | 72.356 | 108.5157 | 107.8005 | 107.4047 | 106.8897 | 106.3778 | 105.8309 | 105.2355 | 104.6207 | 102.6859 | 98.8971 | 95.4827 | 100.8901
|  | BASINGSTOKE T1A & T2A | LW |  |  | 94.3093 | 130.4791 | 129.5057 | 129.0198 | 128.3774 | 127.7116 | 127.0464 | 126.3268 | 125.6592 | 123.4776 | 124.5389 | 120.9653 | 111.1209 | 68.4612 | 105.8171 | 104.8142 | 104.2782 | 103.5856 | 102.867 | 102.149 | 101.3687 | 100.6108 | 98.128 | 101.4116 | 97.4697 | 83.1373 | 72.3023 | 108.4616 | 107.4661 | 106.9426 | 106.2625 | 105.5571 | 104.8523 | 104.0886 | 103.3752 | 101.0406 | 105.3136 | 101.5529 | 86.4107
|  | BASINGSTOKE T1A & T2A | ST |  |  | 98.1637 | 134.4533 | 133.8243 | 133.7726 | 133.5123 | 133.2518 | 132.9911 | 132.7298 | 131.6714 | 128.4949 | 124.2296 | 119.9971 | 116.7165 | 78.4331 | 115.8317 | 115.0311 | 114.6639 | 114.0393 | 113.1412 | 112.2351 | 111.2987 | 109.5102 | 104.1459 | 95.0656 | 89.9139 | 85.6804 | 86.8619 | 123.0671 | 122.2791 | 121.9348 | 121.3368 | 120.4852 | 119.6262 | 118.739 | 117.0038 | 111.799 | 103.1159 | 98.1671 | 94.0165
|  | BASINGSTOKE T1A & T2A | FS |  |  | 94.5139 | 130.8115 | 130.6668 | 130.6549 | 128.9249 | 127.1382 | 125.3524 | 121.8585 | 121.3811 | 119.8785 | 117.3333 | 115.5189 | 119.5445 | 68.9378 | 106.2818 | 106.1271 | 106.0504 | 104.282 | 102.4841 | 100.6872 | 97.1789 | 96.6863 | 95.1297 | 92.5055 | 90.6219 | 97.2645 | 72.7696 | 108.9176 | 108.7632 | 108.6881 | 106.9217 | 105.1267 | 103.3325 | 99.8278 | 99.339 | 97.7959 | 95.1914 | 93.325 | 100.7497
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | BASINGSTOKE T1B & T2B | MINIMUM HEADROOM | SU 65132 52711 | YES | 123.1906 | 107.1802 | 105.2471 | 101.9319 | 98.4431 | 95.087 | 91.7256 | 87.6003 | 83.7724 | 69.9636 | 51.2758 | 32.5376 | 25.3699 | 82.2989 | 63.7332 | 61.6213 | 57.7998 | 53.7692 | 49.9348 | 46.0982 | 41.3931 | 36.9782 | 21.0706 | -0.46137 | -21.9276 | -29.935 | 108.9172 | 108.694 | 107.059 | 103.2393 | 99.2431 | 95.4392 | 91.6328 | 86.9645 | 82.587 | 66.8128 | 45.4617 | 24.169 | 16.215
|  | BASINGSTOKE T1B & T2B | CT |  |  | 123.2915 | 122.7402 | 105.725 | 103.7443 | 101.7698 | 99.7885 | 97.528 | 94.8086 | 91.7494 | 81.5858 | 67.4866 | 53.7179 | 41.6402 | 82.4036 | 81.7657 | 62.1097 | 59.8236 | 57.5415 | 55.2475 | 52.7062 | 49.616 | 46.0951 | 34.3897 | 18.4173 | 2.8045 | -10.9817 | 118.7068 | 118.6588 | 107.5477 | 105.2536 | 102.9871 | 100.713 | 98.1895 | 95.1229 | 91.6314 | 80.024 | 64.1707 | 48.6752 | 34.9976
|  | BASINGSTOKE T1B & T2B | LW |  |  | 123.1906 | 107.1802 | 105.2471 | 101.9319 | 98.4431 | 95.087 | 91.7256 | 87.6003 | 83.7724 | 69.9636 | 51.2758 | 32.5376 | 25.3699 | 82.2989 | 63.7332 | 61.6213 | 57.7998 | 53.7692 | 49.9348 | 46.0982 | 41.3931 | 36.9782 | 21.0706 | -0.46137 | -21.9276 | -29.935 | 118.6284 | 109.1756 | 107.059 | 103.2393 | 99.2431 | 95.4392 | 91.6328 | 86.9645 | 82.587 | 66.8128 | 45.4617 | 24.169 | 16.215
|  | BASINGSTOKE T1B & T2B | ST |  |  | 130.7931 | 130.7015 | 130.2882 | 130.0415 | 129.6283 | 129.2085 | 128.7703 | 128.2997 | 127.2396 | 123.9793 | 119.9964 | 117.2759 | 120.0361 | 106.2719 | 106.0428 | 105.6149 | 105.3419 | 104.8991 | 104.449 | 103.9782 | 103.4714 | 102.3684 | 98.9473 | 94.6861 | 91.7294 | 96.8965 | 108.9172 | 108.694 | 108.2697 | 108.0033 | 107.5678 | 107.1253 | 106.6627 | 106.1649 | 105.0726 | 101.7087 | 97.5844 | 94.7439 | 100.8096
|  | BASINGSTOKE T1B & T2B | FS |  |  | 126.5805 | 124.0438 | 123.8055 | 123.408 | 121.4204 | 119.369 | 117.269 | 113.4753 | 112.3123 | 107.967 | 101.7995 | 99.2406 | 96.6112 | 86.5281 | 83.2653 | 83.0148 | 82.5559 | 80.4972 | 78.3646 | 76.1857 | 72.2889 | 70.9968 | 66.1369 | 59.2789 | 56.1639 | 53.1967 | 119.0262 | 118.8235 | 118.6563 | 118.6155 | 117.041 | 115.4619 | 113.8206 | 110.6262 | 110.2139 | 108.8598 | 104.7455 | 101.616 | 98.64
BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | BASINGSTOKE T3 & T4 | MINIMUM HEADROOM | SU 65132 52712 | YES | 123.5829 | 103.0918 | 103.0269 | 102.8884 | 102.7457 | 102.1868 | 100.4686 | 98.1981 | 95.0471 | 84.637 | 72.3965 | 61.2708 | 51.7084 | 82.7358 | 82.3289 | 63.4376 | 61.7109 | 59.7421 | 58.0394 | 56.073 | 53.4699 | 49.8976 | 38.0624 | 24.1471 | 11.4008 | 0.34952 | 118.7614 | 100.2561 | 100.1621 | 99.9621 | 99.7568 | 99.5099 | 99.2405 | 98.916 | 95.4017 | 83.6572 | 69.8484 | 57.2051 | 46.2485
|  | BASINGSTOKE T3 & T4 | CT |  |  | 130.9156 | 103.0918 | 103.0269 | 102.8971 | 102.7794 | 102.6579 | 102.4937 | 102.285 | 102.0826 | 100.5204 | 96.5538 | 93.1294 | 89.5247 | 125.9179 | 98.0595 | 97.9291 | 97.6898 | 97.4759 | 97.2551 | 96.9501 | 96.5706 | 96.1691 | 94.0079 | 89.7572 | 85.7239 | 81.4775 | 128.0953 | 100.2561 | 100.1621 | 99.9836 | 99.8232 | 99.6575 | 99.4307 | 99.1461 | 98.8552 | 96.7967 | 92.3005 | 88.4221 | 84.3507
|  | BASINGSTOKE T3 & T4 | LW |  |  | 130.9192 | 103.0975 | 103.0368 | 102.8884 | 102.7457 | 102.5736 | 102.3853 | 102.1568 | 101.9303 | 98.6012 | 93.616 | 89.719 | 87.111 | 125.9251 | 98.0707 | 97.9488 | 97.6522 | 97.3688 | 97.0284 | 96.6575 | 96.2131 | 95.463 | 92.1309 | 86.2618 | 81.6602 | 78.5738 | 128.1005 | 100.2642 | 100.1763 | 99.9621 | 99.7568 | 99.5099 | 99.2405 | 98.916 | 98.4495 | 94.5998 | 88.9587 | 84.5362 | 81.5715
|  | BASINGSTOKE T3 & T4 | ST |  |  | 123.5829 | 123.2314 | 106.8981 | 105.4024 | 103.6804 | 102.1868 | 100.4686 | 98.1981 | 95.0471 | 84.637 | 72.3965 | 61.2708 | 51.7084 | 82.7358 | 82.3289 | 63.4376 | 61.7109 | 59.7421 | 58.0394 | 56.073 | 53.4699 | 49.8976 | 38.0624 | 24.1471 | 11.4008 | 0.34952 | 118.7614 | 118.7314 | 108.8796 | 107.1469 | 105.1717 | 103.4798 | 101.5292 | 98.9472 | 95.4017 | 83.6572 | 69.8484 | 57.2051 | 46.2485
|  | BASINGSTOKE T3 & T4 | FS |  |  | 130.9646 | 130.9376 | 130.9249 | 130.8933 | 130.8637 | 130.8256 | 130.7843 | 130.731 | 130.6506 | 130.3718 | 130.0854 | 129.7457 | 129.5144 | 126.0162 | 125.962 | 125.9365 | 125.8783 | 125.8241 | 125.7528 | 125.6754 | 125.5767 | 125.4388 | 124.9554 | 124.4173 | 123.8571 | 123.3496 | 128.1662 | 128.1271 | 128.1087 | 128.0653 | 128.0247 | 127.9719 | 127.9146 | 127.8411 | 127.7351 | 127.3654 | 126.9671 | 126.5294 | 126.2543
EAST CLAYDON GSP | BICESTER NORTH BSP | BICESTER NORTH BSP | MINIMUM HEADROOM | SP5972023735 | YES | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31
|  | BICESTER NORTH BSP | CT |  |  | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31
|  | BICESTER NORTH BSP | LW |  |  | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31
|  | BICESTER NORTH BSP | ST |  |  | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31
|  | BICESTER NORTH BSP | FS |  |  | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31
BOTLEY WOOD GSP | BOTLEY WOOD BSP | BOTLEY WOOD BSP | MINIMUM HEADROOM | SU 54073 09759 | YES | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 103.2148 | 103.1641 | 103.1031 | 102.9119 | 103.2247 | 103.2052 | 103.185 | 103.1615 | 103.1411 | 103.0805 | 112.5 | 112.5 | 112.5 | 108.4247 | 108.401 | 108.3725 | 108.2239 | 108.4288 | 108.4195 | 108.4098 | 108.3984 | 108.3877 | 108.3559 | 113.1883 | 112.808 | 112.6498
|  | BOTLEY WOOD BSP | CT |  |  | 116.7577 | 116.7577 | 116.7577 | 116.6465 | 130.7188 | 130.6038 | 130.4836 | 130.2984 | 130.2749 | 130.1995 | 129.8514 | 129.4594 | 129.3591 | 103.2268 | 103.1827 | 103.1031 | 102.9119 | 119.1379 | 118.936 | 118.7475 | 118.4933 | 118.4014 | 118.127 | 117.4916 | 116.8409 | 116.4895 | 108.4303 | 108.4097 | 108.3725 | 108.2239 | 122.9791 | 122.8235 | 122.6714 | 122.4539 | 122.3985 | 122.2301 | 121.7477 | 121.2349 | 121.0172
|  | BOTLEY WOOD BSP | LW |  |  | 116.7577 | 116.7577 | 130.9433 | 130.8104 | 130.6732 | 130.5299 | 130.3814 | 130.1558 | 130.1246 | 130.0175 | 129.8573 | 129.5685 | 129.5517 | 103.2148 | 103.1641 | 119.4921 | 119.2657 | 119.0327 | 118.8251 | 118.6082 | 118.3136 | 118.214 | 117.9078 | 117.4604 | 116.9129 | 116.6449 | 108.4247 | 108.401 | 123.2642 | 123.0876 | 122.9056 | 122.7322 | 122.5518 | 122.294 | 122.2308 | 122.0307 | 121.7363 | 121.3266 | 121.1924
|  | BOTLEY WOOD BSP | ST |  |  | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 114.2539 | 114.2496 | 113.9862 | 113.9062 | 113.8249 | 113.7413 | 113.6546 | 113.5298 | 113.4852 | 113.3384 | 113.1883 | 112.808 | 112.6498
|  | BOTLEY WOOD BSP | FS |  |  | 116.7577 | 116.7577 | 116.7577 | 116.7573 | 116.7568 | 116.7563 | 116.7559 | 116.7551 | 116.753 | 116.7465 | 130.9289 | 130.9191 | 130.9108 | 103.2886 | 103.2734 | 103.2647 | 103.2461 | 103.2247 | 103.2052 | 103.185 | 103.1615 | 103.1411 | 103.0805 | 119.4213 | 119.3449 | 119.2726 | 108.4592 | 108.4521 | 108.448 | 108.4391 | 108.4288 | 108.4195 | 108.4098 | 108.3984 | 108.3877 | 108.3559 | 123.2234 | 123.1825 | 123.1443
MANNINGTON GSP | BOURNEMOUTH | BOURNEMOUTH | MINIMUM HEADROOM | SZ 06265 92437 | YES | 158.4477 | 116.7577 | 116.7577 | 116.6035 | 130.6323 | 130.4723 | 130.3071 | 130.0514 | 129.9647 | 129.6878 | 129.4653 | 127.7659 | 116.5407 | 140.7463 | 103.2078 | 103.1587 | 102.945 | 119.1385 | 118.9276 | 118.7089 | 118.4066 | 118.273 | 115.1367 | 102.499 | 89.0964 | 75.9385 | 150.1294 | 108.4215 | 108.3985 | 108.2165 | 122.9333 | 122.7495 | 122.5593 | 122.2818 | 122.1732 | 121.8319 | 118.7352 | 106.9168 | 93.7112
|  | BOURNEMOUTH | CT |  |  | 211.8951 | 170.1874 | 169.5223 | 169.4231 | 169.2305 | 169.0364 | 166.6442 | 165.3722 | 164.4204 | 161.3482 | 155.3223 | 149.2051 | 138.0169 | 187.0831 | 149.5653 | 148.9002 | 148.801 | 148.6085 | 148.4144 | 146.0222 | 144.7501 | 143.7983 | 139.2919 | 124.384 | 110.4671 | 97.3464 | 197.568 | 155.8602 | 155.1951 | 155.0959 | 154.9034 | 154.7093 | 152.3171 | 151.045 | 150.0932 | 147.021 | 140.9952 | 128.2858 | 115.1174
|  | BOURNEMOUTH | LW |  |  | 188.9891 | 147.2593 | 146.1391 | 145.9857 | 145.715 | 144.3478 | 142.9346 | 141.8696 | 140.874 | 136.818 | 133.0624 | 127.7659 | 116.5407 | 164.1771 | 126.6372 | 125.5171 | 125.3636 | 125.093 | 123.7257 | 122.3126 | 121.2475 | 120.2519 | 115.1367 | 102.499 | 89.0964 | 75.9385 | 174.662 | 132.9321 | 131.812 | 131.6585 | 131.3879 | 130.0206 | 128.6074 | 127.5424 | 126.5468 | 122.4908 | 118.7352 | 106.9168 | 93.7112
|  | BOURNEMOUTH | ST |  |  | 158.4477 | 116.7577 | 116.7577 | 116.6035 | 130.6323 | 130.4723 | 130.3071 | 130.0514 | 129.9647 | 129.6878 | 129.4653 | 128.7872 | 128.5752 | 140.7463 | 103.2078 | 103.1587 | 102.945 | 119.1385 | 118.9276 | 118.7089 | 118.4066 | 118.273 | 117.8583 | 117.4389 | 116.5928 | 116.2186 | 150.1294 | 108.4215 | 108.3985 | 108.2165 | 122.9333 | 122.7495 | 122.5593 | 122.2818 | 122.1732 | 121.8319 | 121.5174 | 120.7608 | 120.473
|  | BOURNEMOUTH | FS |  |  | 211.997 | 170.3029 | 170.0842 | 170.064 | 168.8879 | 167.7117 | 166.21 | 163.486 | 163.0576 | 161.4972 | 159.5522 | 158.5619 | 158.0683 | 187.1849 | 149.6808 | 149.4621 | 149.442 | 148.2658 | 147.0896 | 145.5879 | 142.8639 | 142.4355 | 140.8752 | 138.9302 | 137.9398 | 137.4463 | 197.6698 | 155.9757 | 155.757 | 155.7368 | 154.5607 | 153.3845 | 151.8828 | 149.1588 | 148.7304 | 147.17 | 145.2251 | 144.2347 | 143.7412
BRAMLEY (FLEE) | BRACKNELL MAIN | BRACKNELL MAIN | MINIMUM HEADROOM | SU 86026 69422 | YES | 142.3403 | 142.2808 | 142.1838 | 141.879 | 141.5709 | 142.3118 | 142.2764 | 142.2322 | 142.1831 | 141.9999 | 147.5932 | 142.5461 | 131.6579 | 125.6901 | 124.9599 | 123.769 | 121.7655 | 119.759 | 125.3423 | 124.9084 | 124.3684 | 123.7761 | 119.68 | 114.4077 | 108.5622 | 94.4223 | 132.9615 | 132.9615 | 132.9615 | 132.8073 | 132.6498 | 132.9614 | 132.9612 | 132.961 | 132.96 | 132.9546 | 136.5645 | 130.7173 | 115.8729
|  | BRACKNELL MAIN | CT |  |  | 142.3494 | 142.2949 | 142.1838 | 141.879 | 141.5709 | 156.22 | 156.051 | 155.7882 | 155.7545 | 154.8167 | 147.5932 | 142.5461 | 143.8399 | 125.8016 | 125.133 | 123.769 | 121.7655 | 119.759 | 135.26 | 133.6735 | 131.6867 | 129.615 | 122.8325 | 114.4077 | 108.5622 | 112.0726 | 132.9615 | 132.9615 | 132.9615 | 132.8073 | 132.6498 | 151.134 | 150.965 | 150.7022 | 150.6685 | 144.9919 | 136.5645 | 130.7173 | 135.6274
|  | BRACKNELL MAIN | LW |  |  | 142.3403 | 142.2808 | 156.6925 | 156.6735 | 156.651 | 156.6245 | 156.5938 | 156.541 | 156.5328 | 152.2746 | 149.987 | 144.4949 | 131.6579 | 125.6901 | 124.9599 | 140.9299 | 138.4952 | 135.9989 | 134.2211 | 132.3142 | 130.0336 | 127.6938 | 119.68 | 118.951 | 112.4996 | 94.4223 | 132.9615 | 132.9615 | 151.6066 | 151.5876 | 151.565 | 151.5385 | 151.5078 | 151.455 | 149.8024 | 141.8381 | 142.5075 | 136.054 | 115.8729
|  | BRACKNELL MAIN | ST |  |  | 170.261 | 170.2535 | 169.8167 | 169.7639 | 169.616 | 168.928 | 168.1732 | 167.2182 | 166.2927 | 163.4418 | 160.4931 | 158.5275 | 157.3613 | 149.6389 | 149.6314 | 149.1946 | 149.1419 | 148.9939 | 148.3059 | 147.5511 | 146.5961 | 145.6706 | 142.8198 | 137.2019 | 128.2899 | 120.5767 | 155.9338 | 155.9263 | 155.4895 | 155.4367 | 155.2888 | 154.6008 | 153.846 | 152.891 | 151.9655 | 149.1147 | 146.1659 | 144.2003 | 138.4158
|  | BRACKNELL MAIN | FS |  |  | 142.4465 | 142.4246 | 142.4158 | 142.3831 | 142.3454 | 142.3118 | 142.2764 | 142.2322 | 142.1831 | 141.9999 | 156.6813 | 156.6604 | 160.7725 | 126.994 | 126.7257 | 126.6172 | 126.2162 | 125.7537 | 125.3423 | 124.9084 | 124.3684 | 123.7761 | 121.589 | 136.3296 | 134.3967 | 142.9796 | 132.9615 | 132.9615 | 132.9615 | 132.9615 | 132.9614 | 132.9614 | 132.9612 | 132.961 | 132.96 | 132.9546 | 151.5953 | 151.5744 | 159.5669
BRAMLEY (FLEE) | BRACKNELL RESERVE | BRACKNELL RESERVE | MINIMUM HEADROOM | SU 86026 69422 | YES | 125.9343 | 125.893 | 125.8836 | 125.8215 | 124.8347 | 123.0805 | 121.3088 | 119.1969 | 117.2514 | 110.4462 | 99.7223 | 92.4651 | 88.345 | 116.5526 | 116.5526 | 116.5526 | 115.8153 | 113.7514 | 111.7685 | 109.7669 | 107.3871 | 105.1759 | 97.4419 | 85.1073 | 76.7351 | 71.9563 | 115.2634 | 115.2001 | 115.1857 | 115.0935 | 114.9863 | 114.5541 | 113.2693 | 111.4088 | 109.7129 | 103.7794 | 94.4265 | 88.0714 | 84.4841
|  | BRACKNELL RESERVE | CT |  |  | 128.1962 | 128.1006 | 127.9072 | 127.1726 | 125.8636 | 124.5217 | 123.1505 | 121.4077 | 119.7851 | 114.4574 | 106.3149 | 99.761 | 93.024 | 118.9947 | 118.7467 | 117.934 | 116.4192 | 114.961 | 113.4661 | 111.9395 | 110.0088 | 108.1685 | 102.1256 | 92.9654 | 85.5252 | 77.7433 | 117.4291 | 117.2825 | 116.9858 | 116.2888 | 115.6092 | 114.9132 | 114.1982 | 113.2339 | 111.8158 | 107.1593 | 99.9723 | 94.1584 | 88.2669
|  | BRACKNELL RESERVE | LW |  |  | 128.1891 | 128.0896 | 127.8879 | 126.6591 | 124.8347 | 123.0805 | 121.3088 | 119.1969 | 117.2514 | 110.4462 | 99.7223 | 92.4651 | 88.345 | 118.9947 | 118.7004 | 117.8528 | 115.8153 | 113.7514 | 111.7685 | 109.7669 | 107.3871 | 105.1759 | 97.4419 | 85.1073 | 76.7351 | 71.9563 | 117.4182 | 117.2656 | 116.9562 | 116.1567 | 115.3433 | 114.5541 | 113.2693 | 111.4088 | 109.7129 | 103.7794 | 94.4265 | 88.0714 | 84.4841
|  | BRACKNELL RESERVE | ST |  |  | 142.3916 | 142.342 | 142.2833 | 142.1633 | 142.0276 | 156.6446 | 156.6264 | 156.5964 | 156.5855 | 156.5442 | 154.6681 | 151.1056 | 153.4936 | 126.3199 | 125.711 | 124.9902 | 123.6876 | 122.201 | 138.6672 | 137.488 | 136.1102 | 134.4747 | 128.9412 | 122.5027 | 118.3243 | 123.1063 | 132.9615 | 132.9615 | 132.9615 | 132.9464 | 132.9304 | 151.5586 | 151.5404 | 151.5105 | 151.4995 | 151.0332 | 144.6617 | 140.482 | 146.6642
|  | BRACKNELL RESERVE | FS |  |  | 125.9343 | 125.893 | 125.8836 | 125.8215 | 125.7495 | 128.0966 | 128.0021 | 127.8802 | 127.726 | 126.1397 | 123.5683 | 121.2763 | 119.6734 | 116.5526 | 116.5526 | 116.5526 | 116.5466 | 116.5408 | 118.7862 | 118.4085 | 117.9268 | 117.365 | 115.2325 | 112.3111 | 109.7227 | 107.9159 | 115.2634 | 115.2001 | 115.1857 | 115.0935 | 114.9863 | 117.2857 | 117.144 | 116.9621 | 116.7399 | 115.9051 | 114.8102 | 113.2478 | 111.8363
BRAMLEY (FLEE) | BURGHFIELD MAIN | BURGHFIELD MAIN | MINIMUM HEADROOM | SU 69442 70509 | YES | 106.164 | 105.4416 | 105.4369 | 105.4243 | 105.4115 | 105.3872 | 105.363 | 103.5407 | 103.417 | 103.0297 | 102.2853 | 101.3688 | 100.6278 | 100.1684 | 99.536 | 99.5183 | 99.4803 | 99.4019 | 98.9498 | 98.494 | 96.2971 | 95.8869 | 94.6206 | 92.1033 | 88.2217 | 83.2131 | 113.8404 | 113.0979 | 113.09 | 113.0712 | 113.0519 | 113.0133 | 112.9055 | 110.9112 | 110.7172 | 110.1144 | 105.6457 | 101.5913 | 96.9458
|  | BURGHFIELD MAIN | CT |  |  | 106.164 | 106.1374 | 106.0867 | 106.0033 | 105.9214 | 105.8399 | 105.7063 | 103.8616 | 103.7502 | 103.4071 | 102.6477 | 101.777 | 101.0156 | 100.1684 | 100.0682 | 99.8769 | 99.6563 | 99.443 | 99.2326 | 98.8305 | 96.7175 | 96.3196 | 95.0976 | 92.565 | 88.8213 | 83.8139 | 113.8404 | 113.7958 | 113.7106 | 113.5936 | 113.4795 | 113.3663 | 113.167 | 111.2565 | 111.0748 | 110.5163 | 109.3221 | 107.9551 | 106.6995
|  | BURGHFIELD MAIN | LW |  |  | 106.1669 | 106.142 | 106.0947 | 105.9677 | 105.8402 | 105.6564 | 105.4693 | 103.5407 | 103.417 | 103.0297 | 102.2853 | 101.3688 | 100.6278 | 100.1794 | 100.0852 | 99.9068 | 99.6518 | 99.4019 | 98.9498 | 98.494 | 96.2971 | 95.8869 | 94.6206 | 92.1033 | 88.2217 | 83.2131 | 113.8453 | 113.8034 | 113.724 | 113.5656 | 113.4081 | 113.1585 | 112.9055 | 110.9112 | 110.7172 | 110.1144 | 108.9354 | 107.5225 | 106.287
|  | BURGHFIELD MAIN | ST |  |  | 128.2716 | 128.2229 | 128.1435 | 127.9241 | 127.6633 | 126.9725 | 126.0081 | 124.8245 | 123.4426 | 118.838 | 112.5236 | 107.8913 | 102.561 | 118.9947 | 118.9947 | 118.9266 | 118.0658 | 117.1333 | 116.1683 | 115.0736 | 113.7314 | 112.1602 | 106.9255 | 99.7443 | 94.4963 | 88.341 | 117.5447 | 117.4701 | 117.3482 | 117.0219 | 116.6686 | 116.3028 | 115.8885 | 115.3741 | 114.7915 | 111.1464 | 105.6457 | 101.5913 | 96.9458
|  | BURGHFIELD MAIN | FS |  |  | 106.2257 | 105.4416 | 105.4369 | 105.4243 | 105.4115 | 105.3872 | 105.363 | 108.1944 | 108.1523 | 108.7761 | 108.581 | 108.3113 | 108.0497 | 100.4008 | 99.536 | 99.5183 | 99.4803 | 99.441 | 99.3586 | 99.2764 | 102.0343 | 101.916 | 102.3041 | 101.6294 | 100.8044 | 99.9781 | 113.944 | 113.0979 | 113.09 | 113.0712 | 113.0519 | 113.0133 | 112.9749 | 115.7882 | 115.7275 | 116.3357 | 116.023 | 115.6172 | 115.2171
BRAMLEY (FLEE) | BURGHFIELD RESERVE | BURGHFIELD RESERVE | MINIMUM HEADROOM | SU 69442 70509 | YES | 106.178 | 106.1615 | 106.1356 | 106.0931 | 106.0464 | 105.9717 | 105.8968 | 104.9661 | 104.8878 | 104.6478 | 88.4687 | 63.2218 | 57.7994 | 100.221 | 100.1589 | 100.061 | 99.9337 | 99.791 | 99.5437 | 99.2963 | 98.1825 | 97.9084 | 85.3432 | 64.4082 | 36.0088 | 29.6776 | 113.8639 | 113.8362 | 113.7926 | 113.7293 | 113.6591 | 113.5421 | 113.4249 | 112.4493 | 108.386 | 93.2106 | 71.3346 | 42.5436 | 36.351
|  | BURGHFIELD RESERVE | CT |  |  | 137.6658 | 137.6651 | 137.664 | 137.5783 | 136.1736 | 134.5283 | 132.875 | 130.5888 | 127.8706 | 118.5515 | 105.984 | 89.9864 | 78.7029 | 122.4387 | 121.9757 | 121.0689 | 118.9813 | 117.0795 | 115.2438 | 113.4002 | 110.8534 | 107.8047 | 97.353 | 83.5587 | 66.1185 | 53.7969 | 131.3599 | 131.0314 | 130.3881 | 128.345 | 126.3605 | 124.4453 | 122.5222 | 119.8668 | 116.6802 | 105.7558 | 91.3552 | 73.1472 | 60.2732
|  | BURGHFIELD RESERVE | LW |  |  | 137.6623 | 137.6602 | 137.6573 | 136.9288 | 133.8596 | 130.9408 | 128.0029 | 124.3076 | 120.7744 | 107.6352 | 88.4687 | 63.2218 | 57.7994 | 122.5376 | 122.1298 | 121.3408 | 117.9191 | 114.4873 | 111.2265 | 107.9455 | 103.8255 | 99.8633 | 85.3432 | 64.4082 | 36.0088 | 29.6776 | 131.3863 | 131.1392 | 130.5789 | 127.2353 | 123.6523 | 120.2487 | 116.8244 | 112.5272 | 108.386 | 93.2106 | 71.3346 | 42.5436 | 36.351
|  | BURGHFIELD RESERVE | ST |  |  | 106.178 | 106.1615 | 106.1356 | 106.0931 | 106.0464 | 105.9717 | 105.8968 | 104.9661 | 104.8878 | 104.6478 | 104.192 | 106.513 | 106.0272 | 100.221 | 100.1589 | 100.061 | 99.9337 | 99.791 | 99.5437 | 99.2963 | 98.1825 | 97.9084 | 97.0708 | 95.4077 | 96.4063 | 94.3026 | 113.8639 | 113.8362 | 113.7926 | 113.7293 | 113.6591 | 113.5421 | 113.4249 | 112.4493 | 112.3231 | 111.9365 | 111.1847 | 113.1815 | 112.3785
|  | BURGHFIELD RESERVE | FS |  |  | 137.6666 | 137.6666 | 136.4488 | 136.4268 | 136.4052 | 136.3834 | 136.3611 | 136.3262 | 135.9468 | 132.1858 | 127.2663 | 122.7932 | 119.8759 | 123.2148 | 123.0809 | 119.9018 | 119.4827 | 119.0155 | 118.4166 | 117.8248 | 117.0408 | 116.005 | 111.8217 | 106.3181 | 101.3601 | 98.1395 | 131.3907 | 131.3906 | 128.2537 | 127.9502 | 127.6127 | 127.1817 | 126.7556 | 125.9843 | 124.9057 | 120.5462 | 114.7988 | 109.6386 | 106.2914
BRAMLEY (FLEE) | CAMBERLEY MAIN | CAMBERLEY MAIN | MINIMUM HEADROOM | SU 86530 59483 | YES | 129.7119 | 129.7119 | 129.7119 | 129.7 | 129.686 | 128.9422 | 127.4679 | 124.4746 | 122.9399 | 114.1783 | 103.2218 | 88.9215 | 79.1541 | 10.1577 | 9.4699 | 6.506 | 4.0951 | 1.3455 | -0.94301 | -3.223 | -8.0966 | -9.3179 | -16.4727 | -29.4889 | -40.1937 | -46.8393 | 109.5691 | 108.6579 | 105.2502 | 102.0712 | 98.5424 | 95.6324 | 92.7356 | 89.4454 | 86.3292 | 75.5793 | 59.0474 | 45.7229 | 37.4159
|  | CAMBERLEY MAIN | CT |  |  | 141.5905 | 141.5183 | 140.4171 | 139.9722 | 139.2658 | 138.5479 | 137.8475 | 136.9927 | 136.5354 | 134.1612 | 122.0619 | 111.6652 | 101.7619 | 10.4124 | 9.7983 | 7.628 | 5.7355 | 3.6165 | 1.4632 | -0.40308 | -2.64 | -4.6862 | -11.3794 | -23.0134 | -33.0184 | -42.0212 | 109.8623 | 109.046 | 106.477 | 104.0444 | 101.3976 | 98.7066 | 96.4035 | 93.6488 | 91.0073 | 82.3456 | 68.0945 | 55.8864 | 44.4185
|  | CAMBERLEY MAIN | LW |  |  | 141.439 | 141.3502 | 139.5759 | 139.2237 | 138.5542 | 137.9246 | 137.2909 | 136.6102 | 136.1036 | 128.7704 | 115.1246 | 103.3823 | 96.0787 | 10.1577 | 9.4699 | 6.506 | 4.0951 | 1.3455 | -0.94301 | -3.223 | -5.8021 | -8.207 | -16.4727 | -29.4889 | -40.1937 | -46.8393 | 109.5691 | 108.6579 | 105.2502 | 102.0712 | 98.5424 | 95.6324 | 92.7356 | 89.4454 | 86.3292 | 75.5793 | 59.0474 | 45.7229 | 37.4159
|  | CAMBERLEY MAIN | ST |  |  | 129.7119 | 129.7119 | 129.7119 | 129.7 | 129.686 | 128.9422 | 127.4679 | 125.4735 | 122.9399 | 114.1783 | 103.2218 | 88.9215 | 79.1541 | 16.7576 | 16.3969 | 16.0185 | 14.5695 | 13.095 | 11.7301 | 10.0773 | 7.8427 | 5.0001 | -4.828 | -16.9896 | -32.6039 | -43.2772 | 123.436 | 123.4359 | 123.2101 | 122.1792 | 120.6576 | 119.2312 | 117.5039 | 115.169 | 112.1975 | 101.9243 | 89.2118 | 72.8983 | 61.7428
|  | CAMBERLEY MAIN | FS |  |  | 141.4809 | 141.4319 | 141.0938 | 141.0306 | 137.7097 | 134.3859 | 131.063 | 124.4746 | 123.7244 | 121.7943 | 117.8433 | 115.0892 | 113.9059 | 11.2289 | 10.758 | 10.3444 | 9.9883 | 6.3243 | 2.629 | -1.0549 | -8.0966 | -9.3179 | -12.8265 | -19.2866 | -24.1843 | -26.9165 | 111.1988 | 110.5704 | 110.1287 | 109.6634 | 105.8713 | 102.0374 | 98.2188 | 91.008 | 89.6109 | 85.339 | 77.9399 | 72.2391 | 68.9265
BRAMLEY (FLEE) | CAMBERLEY RESERVE | CAMBERLEY RESERVE | MINIMUM HEADROOM | SU 86530 59483 | YES | 102.1904 | 85.0074 | 85.0074 | 84.8997 | 84.7886 | 84.6725 | 84.5522 | 84.3694 | 84.3441 | 84.504 | 84.3505 | 80.3554 | 69.5757 | 80.6207 | 78.9059 | 78.6057 | 77.4713 | 75.9367 | 74.5696 | 73.1069 | 71.5071 | 68.658 | 59.575 | 48.5456 | 40.8169 | 33.7186 | 80.3303 | 78.5578 | 77.861 | 76.3635 | 74.421 | 72.7031 | 70.8576 | 68.8316 | 65.4777 | 54.7028 | 41.5194 | 32.1073 | 23.062
|  | CAMBERLEY RESERVE | CT |  |  | 102.3058 | 102.0205 | 102.0205 | 102.0091 | 85.1555 | 85.1437 | 85.1314 | 85.1125 | 85.1101 | 85.1024 | 84.3505 | 80.3554 | 85.9248 | 96.2044 | 95.9191 | 95.9191 | 95.9077 | 79.054 | 78.9622 | 78.802 | 78.6281 | 78.4653 | 76.2981 | 71.543 | 67.1496 | 77.2007 | 95.8562 | 95.5709 | 95.5709 | 95.5595 | 78.7058 | 78.6941 | 78.6818 | 78.6629 | 78.6605 | 78.5017 | 73.954 | 69.6934 | 81.9343
|  | CAMBERLEY RESERVE | LW |  |  | 102.1904 | 85.0074 | 85.0074 | 84.8997 | 84.7886 | 84.6725 | 84.5522 | 84.3694 | 84.3441 | 84.504 | 90.1352 | 88.6907 | 69.5757 | 96.0889 | 78.9059 | 78.9059 | 78.7982 | 78.6871 | 78.4336 | 78.1654 | 77.8277 | 77.642 | 75.6613 | 83.8753 | 80.5083 | 52.4891 | 95.7408 | 78.5578 | 78.5578 | 78.4501 | 78.339 | 78.2229 | 78.1026 | 77.9198 | 77.8945 | 77.9613 | 84.9496 | 84.6927 | 54.3075
|  | CAMBERLEY RESERVE | ST |  |  | 111.1027 | 111.0195 | 110.3056 | 110.1445 | 109.7032 | 109.2766 | 108.8374 | 108.3753 | 106.8736 | 102.3064 | 93.9526 | 85.9246 | 78.4802 | 80.6207 | 79.8357 | 78.6057 | 77.4713 | 75.9367 | 74.5696 | 73.1069 | 71.5071 | 68.658 | 59.575 | 48.5456 | 40.8169 | 33.7186 | 80.3303 | 79.2836 | 77.861 | 76.3635 | 74.421 | 72.7031 | 70.8576 | 68.8316 | 65.4777 | 54.7028 | 41.5194 | 32.1073 | 23.062
|  | CAMBERLEY RESERVE | FS |  |  | 102.71 | 102.651 | 102.651 | 98.8813 | 98.8813 | 98.8813 | 98.8813 | 98.8813 | 98.8813 | 98.8813 | 98.8813 | 99.1531 | 105.238 | 96.6085 | 96.5495 | 96.5495 | 89.8458 | 89.7715 | 89.6784 | 89.5841 | 89.4722 | 89.3382 | 88.9849 | 88.4229 | 88.56 | 99.0683 | 96.2604 | 96.2014 | 96.2014 | 91.921 | 91.921 | 91.921 | 91.921 | 91.7771 | 91.6297 | 91.2635 | 90.6812 | 91.1219 | 99.3327
IVER 132KV | CHALVEY BSP | CHALVEY BSP | MINIMUM HEADROOM | SU 96669 79364 | YES | 137.7891 | 137.5965 | 120.7544 | 120.7544 | 120.7544 | 120.7544 | 120.7544 | 120.7544 | 120.7544 | 120.7544 | 120.7544 | 121.0011 | 124.196 | 123.3923 | 123.3422 | 110.153 | 110.153 | 110.153 | 110.153 | 110.153 | 110.061 | 109.9512 | 109.6771 | 107.728 | 102.6606 | 97.3758 | 129.8958 | 129.857 | 114.3048 | 114.3048 | 114.3048 | 114.3048 | 114.3048 | 114.3048 | 114.3048 | 114.3048 | 114.3048 | 112.0261 | 116.6091
|  | CHALVEY BSP | CT |  |  | 140.0524 | 140.0122 | 139.5523 | 139.4576 | 139.2654 | 139.0742 | 138.8606 | 138.6395 | 138.463 | 137.9751 | 136.2067 | 130.8421 | 125.9108 | 123.4519 | 123.4071 | 122.9403 | 122.8372 | 122.6361 | 122.4363 | 122.211 | 121.7342 | 120.4199 | 117.0693 | 110.9091 | 104.8735 | 99.2703 | 129.9551 | 129.9213 | 129.471 | 129.3881 | 129.2081 | 129.0289 | 128.8315 | 128.628 | 128.4683 | 128.0224 | 125.8983 | 121.7331 | 118.0025
|  | CHALVEY BSP | LW |  |  | 139.9929 | 139.9475 | 139.213 | 139.0793 | 138.8306 | 138.5678 | 138.2986 | 138.0148 | 137.8102 | 137.2298 | 134.4604 | 128.8614 | 124.196 | 123.3923 | 123.3422 | 122.6005 | 122.4573 | 122.1987 | 121.924 | 121.6422 | 120.3788 | 118.9839 | 115.3067 | 108.9579 | 102.6606 | 97.3758 | 129.8958 | 129.857 | 129.1324 | 129.0119 | 128.7772 | 128.5308 | 128.279 | 128.0141 | 127.8269 | 127.2921 | 124.5183 | 120.1673 | 116.6091
|  | CHALVEY BSP | ST |  |  | 137.7891 | 137.5965 | 120.7544 | 120.7544 | 120.7544 | 120.7544 | 120.7544 | 120.7544 | 120.7544 | 120.7544 | 120.7544 | 121.0011 | 126.762 | 127.1876 | 126.9951 | 110.153 | 110.153 | 110.153 | 110.153 | 110.153 | 110.061 | 109.9512 | 109.6771 | 107.728 | 105.1142 | 116.0021 | 131.3395 | 131.1469 | 114.3048 | 114.3048 | 114.3048 | 114.3048 | 114.3048 | 114.3048 | 114.3048 | 114.3048 | 114.3048 | 112.0261 | 121.5764
|  | CHALVEY BSP | FS |  |  | 140.1449 | 140.128 | 139.9805 | 139.95 | 138.7266 | 137.5006 | 136.2737 | 133.8499 | 133.5654 | 132.7175 | 131.2574 | 131.2278 | 130.7496 | 123.5492 | 123.5303 | 123.3813 | 123.3485 | 122.1227 | 120.8939 | 119.6641 | 117.237 | 116.9492 | 116.0925 | 114.6178 | 114.5735 | 113.3203 | 130.041 | 130.027 | 129.8815 | 129.8542 | 128.6341 | 127.412 | 126.1891 | 123.7699 | 123.4901 | 122.6544 | 121.2144 | 121.2053 | 120.7458
LOVEDEAN GSP | CHICHESTER & HUNSTON | CHICHESTER & HUNSTON | MINIMUM HEADROOM | SU 92282 07416 | YES | 217.2088 | 215.6168 | 212.0421 | 209.1308 | 205.8868 | 202.0379 | 198.0677 | 193.6776 | 189.7979 | 177.1067 | 149.9009 | 112.4264 | 95.0566 | 166.0884 | 164.2899 | 160.4277 | 157.1049 | 153.4316 | 149.0539 | 144.5362 | 139.5597 | 135.0792 | 120.4125 | 90.852 | 47.5602 | 24.7675 | 170.8335 | 169.0289 | 165.1583 | 161.8233 | 158.1374 | 153.744 | 149.2101 | 144.2163 | 139.718 | 124.993 | 95.4266 | 51.963 | 28.9144
|  | CHICHESTER & HUNSTON | CT |  |  | 217.5719 | 216.0962 | 213.3675 | 211.1592 | 208.7018 | 206.2341 | 202.9187 | 199.3297 | 195.7686 | 184.3833 | 160.9495 | 135.4476 | 124.8267 | 166.4661 | 164.7919 | 161.7925 | 159.2483 | 156.4446 | 153.6294 | 149.8243 | 145.711 | 141.586 | 128.3909 | 101.5523 | 72.1722 | 61.8153 | 171.2117 | 169.5316 | 166.5242 | 163.9701 | 161.1562 | 158.3307 | 154.5112 | 150.3823 | 146.2407 | 132.9921 | 106.0529 | 76.5582 | 66.2729
|  | CHICHESTER & HUNSTON | LW |  |  | 217.2088 | 215.6168 | 212.0421 | 209.1308 | 205.8868 | 202.0379 | 198.0677 | 193.6776 | 189.7979 | 177.1067 | 149.9009 | 112.4264 | 95.0566 | 166.0884 | 164.2899 | 160.4277 | 157.1049 | 153.4316 | 149.0539 | 144.5362 | 139.5597 | 135.0792 | 120.4125 | 90.852 | 47.5602 | 24.7675 | 170.8335 | 169.0289 | 165.1583 | 161.8233 | 158.1374 | 153.744 | 149.2101 | 144.2163 | 139.718 | 124.993 | 95.4266 | 51.963 | 28.9144
|  | CHICHESTER & HUNSTON | ST |  |  | 237.6039 | 237.5713 | 237.272 | 237.1495 | 236.9235 | 236.6868 | 236.4431 | 236.153 | 235.5586 | 233.7939 | 231.7448 | 230.2428 | 227.6687 | 217.2566 | 217.2201 | 216.9172 | 216.7896 | 216.5578 | 216.3141 | 216.0627 | 215.7637 | 215.1607 | 212.3618 | 206.9938 | 202.3266 | 198.3588 | 227.5023 | 227.4751 | 227.1808 | 227.0654 | 226.8473 | 226.6205 | 226.3874 | 226.1096 | 225.5273 | 223.7938 | 221.7935 | 220.338 | 217.8291
|  | CHICHESTER & HUNSTON | FS |  |  | 234.8016 | 233.5027 | 218.5273 | 213.7893 | 210.9094 | 207.903 | 204.882 | 199.4264 | 198.0128 | 193.3874 | 183.6457 | 178.3586 | 177.9121 | 186.5194 | 185.0114 | 167.5623 | 159.6739 | 156.7025 | 153.5831 | 150.4467 | 144.8537 | 143.2838 | 138.1239 | 125.542 | 119.654 | 121.0733 | 191.1853 | 189.7772 | 172.3121 | 164.2482 | 161.2742 | 158.1514 | 155.0116 | 149.4145 | 147.84 | 142.6643 | 129.9413 | 124.0356 | 125.5738
CHICKERELL GSP | CHICKERELL BSP | CHICKERELL BSP | MINIMUM HEADROOM | SY 65479 80511 | YES | 118.6901 | 107.8633 | 104.7149 | 88.4468 | 86.4708 | 84.3071 | 82.0026 | 79.4236 | 75.9587 | 64.918 | 45.1036 | 17.6595 | 7.4821 | 74.7837 | 71.4154 | 68.1319 | 43.3098 | 41.0512 | 38.5735 | 35.9314 | 32.9734 | 29.0916 | 16.6902 | -5.8964 | -37.0026 | -48.9379 | 73.0974 | 70.5788 | 68.6838 | 41.6015 | 39.3346 | 36.8475 | 34.1954 | 31.2262 | 27.3321 | 14.8905 | -7.7779 | -32.3648 | -37.9133
|  | CHICKERELL BSP | CT |  |  | 133.8693 | 108.1081 | 106.0007 | 91.8731 | 90.373 | 88.867 | 85.9714 | 82.7471 | 79.3945 | 68.3723 | 48.2724 | 27.986 | 27.5409 | 101.2157 | 71.6582 | 69.4141 | 54.9864 | 53.209 | 51.4251 | 48.053 | 44.2262 | 40.1687 | 26.8031 | 2.9992 | -21.3461 | -24.4068 | 111.6845 | 94.0824 | 92.2686 | 78.7861 | 77.882 | 76.9734 | 75.1016 | 73.1724 | 71.3347 | 65.349 | 45.7673 | 21.6019 | 18.3447
|  | CHICKERELL BSP | LW |  |  | 119.4471 | 107.8633 | 104.7149 | 102.3665 | 99.6956 | 96.0516 | 92.3557 | 87.9728 | 84.0041 | 70.0367 | 46.4174 | 17.6595 | 7.4821 | 83.0867 | 71.4154 | 68.1319 | 65.2877 | 62.1186 | 57.8118 | 53.4475 | 48.2555 | 43.4583 | 26.5971 | -2.0403 | -37.0026 | -48.9379 | 105.229 | 93.8333 | 90.9754 | 89.6924 | 88.0923 | 85.8727 | 83.6135 | 80.9692 | 78.7813 | 69.2838 | 40.869 | 5.5191 | -6.5651
|  | CHICKERELL BSP | ST |  |  | 119.1766 | 117.0017 | 115.2763 | 88.4468 | 86.4708 | 84.3071 | 82.0026 | 79.4236 | 75.9587 | 64.918 | 45.1036 | 23.8435 | 17.3075 | 74.7837 | 72.275 | 70.3849 | 43.3098 | 41.0512 | 38.5735 | 35.9314 | 32.9734 | 29.0916 | 16.6902 | -5.8964 | -30.3877 | -36.0265 | 73.0974 | 70.5788 | 68.6838 | 41.6015 | 39.3346 | 36.8475 | 34.1954 | 31.2262 | 27.3321 | 14.8905 | -7.7779 | -32.3648 | -37.9133
|  | CHICKERELL BSP | FS |  |  | 118.6901 | 118.318 | 117.6876 | 117.3745 | 117.1175 | 113.4111 | 98.4096 | 91.2262 | 89.6897 | 84.3821 | 76.0546 | 70.2903 | 66.932 | 80.9698 | 80.5028 | 79.8284 | 79.4468 | 84.3594 | 80.5346 | 65.4155 | 58.0729 | 56.33 | 50.2421 | 40.7441 | 34.1336 | 30.1795 | 90.4143 | 90.2462 | 89.6029 | 89.4369 | 95.0501 | 91.598 | 76.8493 | 70.0082 | 68.9151 | 65.2845 | 59.4729 | 55.5271 | 53.4494
MELKSHAM GSP | CHIPPENHAM | CHIPPENHAM | MINIMUM HEADROOM | ST 92629 74275 | YES | 104.9354 | 104.9354 | 104.9354 | 93.236 | 91.8942 | 90.1421 | 88.2068 | 85.6656 | 81.9118 | 69.7956 | 52.8092 | 36.0553 | 39.0974 | 39.7563 | 16.6129 | -2.5174 | -5.9514 | -10.8208 | -15.713 | -25.3696 | -36.7127 | -42.7757 | -83.4746 | -175.0831 | -210.897 | -226.8776 | 47.455 | 22.1184 | 5.0414 | 1.5881 | -3.2983 | -8.7073 | -19.8405 | -31.2207 | -37.2371 | -77.5683 | -168.627 | -204.3955 | -220.52
|  | CHIPPENHAM | CT |  |  | 104.9354 | 104.9354 | 104.9354 | 104.9354 | 104.9354 | 104.9354 | 104.9354 | 104.9354 | 104.9354 | 114.31 | 114.31 | 114.3226 | 114.3226 | 73.627 | 34.1 | -2.5174 | -5.9514 | -10.8208 | -15.713 | -7.5805 | -14.474 | -22.7714 | -41.1969 | -92.984 | -118.3027 | -145.0489 | 81.4626 | 41.7933 | 5.0414 | 1.5881 | -3.2983 | -8.2074 | -2.1526 | -9.068 | -17.3936 | -35.6738 | -87.0051 | -112.1143 | -138.6304
|  | CHIPPENHAM | LW |  |  | 104.9354 | 104.9354 | 104.9354 | 104.9354 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.3226 | 105.6873 | 105.6873 | 97.631 | 39.7563 | 16.6129 | 13.4021 | 2.4794 | -3.2691 | -14.2736 | -25.3696 | -36.7127 | -42.7757 | -83.4746 | -175.0831 | -210.897 | -226.8776 | 47.455 | 22.1184 | 18.902 | 7.9412 | 2.3343 | -8.7073 | -19.8405 | -31.2207 | -37.2371 | -77.5683 | -168.627 | -204.3955 | -220.52
|  | CHIPPENHAM | ST |  |  | 134.2173 | 119.6446 | 118.2832 | 93.236 | 91.8942 | 90.1421 | 88.2068 | 85.6656 | 81.9118 | 69.7956 | 52.8092 | 36.0553 | 39.0974 | 101.625 | 83.2503 | 81.8084 | 56.5249 | 54.939 | 52.8785 | 50.5929 | 47.5633 | 43.2232 | 29.1292 | 9.0924 | -11.1608 | -10.1895 | 111.9007 | 105.4995 | 104.311 | 79.7719 | 78.9545 | 77.8652 | 76.6828 | 75.1913 | 72.6977 | 64.832 | 51.7915 | 31.6934 | 32.7565
|  | CHIPPENHAM | FS |  |  | 104.9354 | 104.9354 | 104.9354 | 104.9354 | 104.9354 | 104.9354 | 104.9354 | 104.9354 | 104.9354 | 104.9354 | 104.9354 | 105.0038 | 105.0038 | 75.072 | 74.949 | 74.7018 | 35.4601 | 34.0441 | 32.0558 | 30.0106 | 27.3095 | 23.7683 | 27.3069 | 8.2947 | -1.7955 | -9.9571 | 82.9122 | 82.7888 | 82.5411 | 43.1583 | 41.7373 | 39.7419 | 37.6898 | 34.9795 | 31.4261 | 32.8544 | 13.7751 | 3.6348 | -4.5538
MANNINGTON GSP | CHRISTCHURCH BSP | CHRISTCHURCH BSP | MINIMUM HEADROOM | SZ 15716 93165 | YES | 104.9354 | 104.9354 | 104.9354 | 104.9354 | 104.9354 | 104.9354 | 104.9354 | 104.9354 | 104.9354 | 114.31 | 114.31 | 102.9749 | 96.2482 | 74.3314 | 35.6595 | -1.2193 | -3.5657 | -5.889 | -10.1596 | -1.2718 | -7.3318 | -14.9648 | -36.1676 | -78.3513 | -104.4422 | -127.5634 | 82.169 | 43.3578 | 6.3473 | 3.985 | 1.6459 | -2.6394 | 4.1713 | -1.9094 | -9.5693 | -30.6854 | -72.4471 | -98.6198 | -121.529
|  | CHRISTCHURCH BSP | CT |  |  | 137.9535 | 137.9368 | 136.8242 | 136.9482 | 136.1505 | 135.3408 | 134.1675 | 132.9353 | 131.8604 | 128.4969 | 120.5624 | 108.4266 | 101.2668 | 125.3507 | 125.3215 | 124.2814 | 124.9758 | 124.6476 | 124.3168 | 123.1833 | 121.926 | 120.8237 | 117.3739 | 109.1248 | 95.4888 | 87.2035 | 117.4763 | 117.1861 | 115.6672 | 115.8645 | 114.9988 | 114.1199 | 112.8283 | 111.479 | 110.276 | 106.5102 | 97.813 | 84.2529 | 76.2352
|  | CHRISTCHURCH BSP | LW |  |  | 137.809 | 138.4859 | 136.7909 | 135.9928 | 135.079 | 133.8442 | 132.587 | 131.3094 | 130.1535 | 126.4579 | 119.1804 | 102.9749 | 96.2482 | 125.2055 | 126.0827 | 124.3638 | 124.159 | 123.8318 | 122.8648 | 121.5794 | 120.2737 | 119.0886 | 115.2988 | 107.5333 | 88.9258 | 81.149 | 117.3169 | 117.9869 | 115.7729 | 114.889 | 113.8904 | 112.5271 | 111.1387 | 109.73 | 108.4378 | 104.3029 | 96.1982 | 77.9541 | 70.427
|  | CHRISTCHURCH BSP | ST |  |  | 104.9354 | 104.9354 | 104.9354 | 104.9354 | 104.9354 | 104.9354 | 104.9354 | 104.9354 | 104.9354 | 114.31 | 114.31 | 105.0038 | 105.0038 | 74.3314 | 35.6595 | -1.2193 | -3.5657 | -5.889 | -10.1596 | -1.2718 | -7.3318 | -14.9648 | -36.1676 | -78.3513 | -104.4422 | -127.5634 | 82.169 | 43.3578 | 6.3473 | 3.985 | 1.6459 | -2.6394 | 4.1713 | -1.9094 | -9.5693 | -30.6854 | -72.4471 | -98.6198 | -121.529
|  | CHRISTCHURCH BSP | FS |  |  | 138.098 | 138.0924 | 137.7534 | 137.7161 | 136.3722 | 135.0283 | 133.6842 | 130.7955 | 130.2197 | 129.2385 | 126.0357 | 123.9146 | 121.591 | 125.5231 | 125.5014 | 125.1596 | 125.1164 | 123.7662 | 122.41 | 121.0534 | 118.3824 | 118.0496 | 117.9571 | 115.0366 | 112.8616 | 110.4862 | 118.2268 | 117.8694 | 117.47 | 117.3053 | 115.8255 | 114.2135 | 112.5987 | 109.6197 | 109.0088 | 108.0548 | 104.6268 | 102.2544 | 99.6894
IVER 132KV | CIPPENHAM | CIPPENHAM | MINIMUM HEADROOM | SU 96266 79634 | YES | 70.9588 | 70.9479 | 70.2605 | 70.1135 | 69.9397 | 69.8091 | 64.0226 | 64.0042 | 63.9788 | 63.8984 | 63.8439 | 57.6935 | 52.6579 | 67.9734 | 67.9416 | 67.2101 | 67.0079 | 66.7782 | 66.6174 | 60.9199 | 60.7659 | 60.6172 | 60.1126 | 58.6479 | 47.4406 | 41.7324 | 63.6354 | 63.1465 | 62.1882 | 62.5428 | 61.7649 | 60.6274 | 57.1813 | 57.1355 | 56.8848 | 52.4464 | 45.7343 | 34.2491 | 28.6384
|  | CIPPENHAM | CT |  |  | 71.0154 | 71.0089 | 70.5869 | 70.5304 | 70.4501 | 70.4167 | 70.3357 | 70.3006 | 70.2635 | 70.1748 | 69.0963 | 66.8146 | 64.3729 | 68.0306 | 68.0035 | 67.5384 | 67.4344 | 67.3068 | 67.2259 | 67.1212 | 67.0588 | 66.7123 | 64.586 | 61.2631 | 58.6271 | 55.8092 | 66.6689 | 66.6374 | 66.1628 | 66.0486 | 65.9107 | 65.8194 | 65.7096 | 65.6412 | 65.5655 | 64.7221 | 61.4869 | 58.9288 | 56.195
|  | CIPPENHAM | LW |  |  | 70.9588 | 70.9479 | 70.2605 | 70.1135 | 69.9397 | 69.8091 | 69.6274 | 69.4495 | 69.3867 | 69.2123 | 67.1135 | 64.472 | 62.571 | 67.9734 | 67.9416 | 67.2101 | 67.0079 | 66.7782 | 66.6174 | 66.4052 | 66.1925 | 65.4275 | 62.8038 | 59.0511 | 56.0137 | 53.8294 | 66.6115 | 66.5752 | 65.8342 | 65.62 | 65.3781 | 65.2108 | 64.9919 | 64.7716 | 64.6649 | 62.9664 | 59.3248 | 56.3759 | 54.255
|  | CIPPENHAM | ST |  |  | 83.7157 | 83.7046 | 83.0266 | 83.5149 | 82.8319 | 81.7916 | 80.7172 | 79.6654 | 78.3298 | 74.1902 | 68.0264 | 57.6935 | 52.6579 | 72.9412 | 72.9081 | 72.2172 | 72.8999 | 72.5528 | 72.1858 | 71.5588 | 70.4888 | 69.133 | 64.9293 | 58.6479 | 47.4406 | 41.7324 | 63.6354 | 63.1465 | 62.1882 | 62.5428 | 61.7649 | 60.6274 | 59.4517 | 58.3149 | 56.8848 | 52.4464 | 45.7343 | 34.2491 | 28.6384
|  | CIPPENHAM | FS |  |  | 71.072 | 71.0698 | 70.9371 | 70.9214 | 70.9058 | 70.8902 | 64.0226 | 64.0042 | 63.9788 | 63.8984 | 63.8439 | 63.7258 | 63.6131 | 68.119 | 68.1152 | 67.9807 | 67.9569 | 67.9314 | 67.9081 | 60.9199 | 60.7659 | 60.6172 | 60.1126 | 59.4753 | 58.8532 | 58.3605 | 66.7642 | 66.76 | 66.6252 | 66.5997 | 66.572 | 66.5469 | 57.1813 | 57.1355 | 57.0853 | 56.9193 | 56.7473 | 56.5275 | 56.3381
MINETY GSP | CIRENCESTER BSP | CIRENCESTER BSP | MINIMUM HEADROOM | SP 02701 00368 | NO | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | -216.4661 | -272.7468 | -273.8619 | -283.0516 | -292.3429 | -301.4572 | -310.6534 | -319.2668 | -327.1765 | -356.375 | -402.7768 | -466.4673 | -473.6359 | -210.4006 | -266.6457 | -267.7214 | -276.5952 | -285.5683 | -294.3727 | -303.2574 | -311.5928 | -319.2219 | -347.3369 | -393.167 | -456.6688 | -463.8161
|  | CIRENCESTER BSP | CT |  |  | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | -137.8408 | -213.2033 | -214.291 | -218.8544 | -222.931 | -227.0376 | -231.6459 | -236.5807 | -242.5534 | -263.1522 | -291.313 | -327.556 | -345.0889 | -133.6464 | -207.1032 | -208.1523 | -212.5568 | -216.4926 | -220.4578 | -224.907 | -229.6752 | -235.4342 | -255.2956 | -282.442 | -317.9901 | -335.4707
|  | CIRENCESTER BSP | LW |  |  | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | -216.4661 | -272.7468 | -273.8619 | -283.0516 | -292.3429 | -301.4572 | -310.6534 | -319.2668 | -327.1765 | -356.375 | -402.7768 | -466.4673 | -473.6359 | -210.4006 | -266.6457 | -267.7214 | -276.5952 | -285.5683 | -294.3727 | -303.2574 | -311.5928 | -319.2219 | -347.3369 | -393.167 | -456.6688 | -463.8161
|  | CIRENCESTER BSP | ST |  |  | 125.3537 | 125.3494 | 125.0602 | 125.0146 | 124.9925 | 124.923 | 124.9004 | 124.8767 | 124.8435 | 124.8126 | 124.7156 | 124.6437 | 124.287 | 120.5779 | 120.5648 | 120.2606 | 120.1919 | 120.1423 | 120.0527 | 120.0083 | 119.9633 | 119.9047 | 119.7941 | 118.5878 | 116.7627 | 114.7173 | 121.0304 | 121.0153 | 120.7079 | 120.6341 | 120.5786 | 120.4846 | 120.4355 | 120.3858 | 120.3216 | 120.1937 | 119.9729 | 118.7244 | 116.7427
|  | CIRENCESTER BSP | FS |  |  | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 46.2718 | 46.2138 | 34.6326 | -13.7875 | -14.9837 | -16.6429 | -18.2807 | -20.4454 | -23.3688 | -35.7112 | -51.6803 | -64.3169 | -71.1631 | 50.3368 | 50.2817 | 38.8114 | -8.393 | -9.5596 | -11.1774 | -12.7745 | -14.8854 | -17.7368 | -29.7743 | -45.2229 | -57.4176 | -64.0302
FAWLEY GSP | COWES & WOOTTON COMMON BSP | COWES & WOOTTON COMMON BSP | MINIMUM HEADROOM | SZ 50519 94250 | YES | 114.31 | 88.7207 | -10.1613 | -39.8587 | -42.0803 | -49.3463 | -52.3304 | -55.7886 | -58.7494 | -67.9636 | -100.2569 | -127.3341 | -151.5185 | 34.1843 | -157.1385 | -213.0697 | -217.0193 | -220.9971 | -224.6064 | -229.1013 | -233.8265 | -239.5737 | -259.5099 | -285.6029 | -320.6581 | -336.7532 | 38.3745 | -151.0663 | -206.9747 | -210.7897 | -214.6321 | -218.1198 | -222.4615 | -227.0306 | -232.5753 | -251.808 | -276.9589 | -311.1145 | -327.1621
|  | COWES & WOOTTON COMMON BSP | CT |  |  | 124.1108 | 123.6155 | 122.5337 | 121.6197 | 103.6823 | 102.5788 | 100.6809 | 94.3394 | 91.8863 | 83.9771 | 63.9835 | 50.8737 | 50.6653 | 96.7302 | 96.1093 | 94.9118 | 93.7747 | 75.6298 | 74.3171 | 72.0026 | 65.1841 | 62.2978 | 53.0895 | 30.0016 | 15.2129 | 18.4637 | 101.4551 | 100.9251 | 99.8114 | 98.8358 | 80.8412 | 79.6799 | 77.6671 | 71.1939 | 68.7077 | 60.7805 | 40.7442 | 28.1619 | 35.9784
|  | COWES & WOOTTON COMMON BSP | LW |  |  | 122.116 | 88.7207 | -10.1613 | -39.8587 | -42.0803 | -49.3463 | -52.3304 | -55.7886 | -58.7494 | -67.9636 | -100.2569 | -127.3341 | -151.5185 | 94.7343 | 54.7539 | -54.8964 | -89.858 | -92.3515 | -100.0346 | -103.427 | -107.3454 | -110.7778 | -121.2428 | -153.3484 | -183.1764 | -216.2601 | 99.46 | 65.4816 | -38.4589 | -72.1689 | -74.5978 | -82.1817 | -85.477 | -89.286 | -92.6063 | -102.5203 | -131.3023 | -160.8888 | -198.1142
|  | COWES & WOOTTON COMMON BSP | ST |  |  | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 34.1843 | -157.1385 | -213.0697 | -217.0193 | -220.9971 | -224.6064 | -229.1013 | -233.8265 | -239.5737 | -259.5099 | -285.6029 | -320.6581 | -336.7532 | 38.3745 | -151.0663 | -206.9747 | -210.7897 | -214.6321 | -218.1198 | -222.4615 | -227.0306 | -232.5753 | -251.808 | -276.9589 | -311.1145 | -327.1621
|  | COWES & WOOTTON COMMON BSP | FS |  |  | 122.5873 | 122.2908 | 122.0194 | 121.8074 | 118.5635 | 115.1944 | 111.8435 | 105.3906 | 104.1553 | 96.8814 | 90.4307 | 86.2423 | 93.9348 | 95.273 | 94.8998 | 94.6126 | 94.3498 | 91.0491 | 87.5904 | 84.1546 | 77.5926 | 76.1973 | 67.0209 | 59.7622 | 55.2851 | 67.7402 | 99.9499 | 99.6322 | 99.3565 | 99.1305 | 95.8709 | 92.477 | 89.1027 | 82.6197 | 81.3403 | 71.6593 | 64.9856 | 61.2175 | 77.2359
COWLEY GSP | COWLEY LOCAL (2 X 45) | COWLEY LOCAL (2 X 45) | MINIMUM HEADROOM | SP 56113 03074 | NO | 122.6584 | 122.6328 | 122.4573 | 122.3041 | 122.1059 | 120.9006 | 119.5429 | 117.7917 | 114.8049 | 105.0497 | 85.5804 | 74.7447 | 76.9593 | 94.9772 | 94.4476 | 93.6804 | 92.7747 | 91.5754 | 90.0321 | 88.3937 | 86.2601 | 82.8295 | 71.9949 | 49.7949 | 37.6778 | 43.7351 | 102.3819 | 101.9308 | 101.2156 | 100.4405 | 99.3788 | 98.0247 | 96.5895 | 94.7328 | 91.6304 | 81.8604 | 62.3533 | 52.0506 | 62.5783
|  | COWLEY LOCAL (2 X 45) | CT |  |  | 133.4243 | 133.3203 | 132.7088 | 132.0776 | 131.374 | 130.616 | 129.6494 | 128.4329 | 127.0146 | 121.8893 | 114.4995 | 110.6242 | 107.3594 | 111.9445 | 111.8243 | 111.178 | 110.4487 | 109.6353 | 108.7586 | 107.6389 | 106.2285 | 104.5784 | 98.6131 | 90.0969 | 85.6193 | 81.8378 | 122.1242 | 122.0068 | 121.3667 | 120.6547 | 119.8606 | 119.0048 | 117.9121 | 116.5359 | 114.9265 | 109.1092 | 100.7914 | 96.4199 | 92.7294
|  | COWLEY LOCAL (2 X 45) | LW |  |  | 133.3943 | 133.3002 | 132.4546 | 131.4275 | 130.2744 | 128.9671 | 127.5794 | 125.9025 | 124.2197 | 117.9312 | 108.5431 | 102.9669 | 101.4439 | 111.9188 | 111.8109 | 110.9356 | 109.7485 | 108.4152 | 106.9026 | 105.2969 | 103.3561 | 101.3996 | 94.0849 | 83.1783 | 76.7095 | 74.9603 | 122.0977 | 121.9923 | 121.1222 | 119.9633 | 118.6617 | 117.1853 | 115.618 | 113.7237 | 111.8154 | 104.6814 | 94.0423 | 87.7307 | 86.0213
|  | COWLEY LOCAL (2 X 45) | ST |  |  | 125.0337 | 124.6125 | 123.9171 | 123.1919 | 122.1826 | 120.9006 | 119.5429 | 117.7917 | 114.8049 | 105.0497 | 85.5804 | 74.7447 | 76.9593 | 94.9772 | 94.4476 | 93.6804 | 92.7747 | 91.5754 | 90.0321 | 88.3937 | 86.2601 | 82.8295 | 71.9949 | 49.7949 | 37.6778 | 43.7351 | 102.3819 | 101.9308 | 101.2156 | 100.4405 | 99.3788 | 98.0247 | 96.5895 | 94.7328 | 91.6304 | 81.8604 | 62.3533 | 52.0506 | 62.5783
|  | COWLEY LOCAL (2 X 45) | FS |  |  | 122.6584 | 122.6328 | 122.4573 | 122.3041 | 122.1059 | 121.8336 | 132.4959 | 132.15 | 131.7306 | 130.0098 | 127.6324 | 126.3696 | 125.673 | 101.1994 | 101.1699 | 100.9873 | 100.8108 | 100.5816 | 100.266 | 110.883 | 110.4816 | 109.9935 | 107.9898 | 105.2222 | 103.7555 | 102.9507 | 111.3755 | 111.3466 | 111.1653 | 110.9929 | 110.7691 | 110.4612 | 121.0861 | 120.6945 | 120.2185 | 118.2646 | 115.5658 | 114.135 | 113.3493
COWLEY GSP | COWLEY LOCAL (2 X 90) | COWLEY LOCAL (2 X 90) | MINIMUM HEADROOM | SP 56113 03074 | NO | 133.5423 | 133.4934 | 133.1373 | 132.6772 | 132.1444 | 131.4971 | 130.7193 | 129.71 | 128.5166 | 124.1536 | 118.3571 | 111.4909 | 95.3176 | 112.0774 | 112.0211 | 111.6504 | 111.1211 | 110.5071 | 109.7598 | 108.8605 | 107.6935 | 106.306 | 101.2309 | 94.4886 | 90.5742 | 73.4848 | 122.2545 | 122.1994 | 121.8314 | 121.3142 | 120.7146 | 119.9848 | 119.107 | 117.9678 | 116.6144 | 108.5651 | 101.8339 | 92.3099 | 71.0356
|  | COWLEY LOCAL (2 X 90) | CT |  |  | 142.4756 | 142.4485 | 140.8522 | 140.6278 | 140.4009 | 140.4777 | 140.2425 | 139.9484 | 138.7403 | 132.2228 | 120.7512 | 112.2376 | 110.4198 | 130.7272 | 130.6311 | 128.9519 | 128.6105 | 128.2665 | 128.3638 | 127.8744 | 126.3006 | 124.0954 | 116.6738 | 103.8826 | 94.3072 | 94.4206 | 130.5714 | 130.4954 | 128.8403 | 128.5328 | 128.2227 | 127.9663 | 126.2449 | 124.1313 | 121.939 | 114.5612 | 101.8339 | 92.3099 | 94.2841
|  | COWLEY LOCAL (2 X 90) | LW |  |  | 142.5508 | 142.5045 | 139.8426 | 139.6003 | 139.3527 | 139.0989 | 138.8466 | 136.9927 | 134.7264 | 126.7721 | 120.7088 | 111.4909 | 95.3176 | 130.9513 | 130.8384 | 128.0988 | 127.6985 | 127.2868 | 126.7289 | 124.9787 | 122.2838 | 119.7054 | 110.65 | 105.8866 | 95.4081 | 73.4848 | 130.7421 | 130.6485 | 127.9314 | 127.577 | 127.2129 | 125.0919 | 122.8107 | 120.1305 | 117.5672 | 108.5651 | 105.6931 | 95.2757 | 71.0356
|  | COWLEY LOCAL (2 X 90) | ST |  |  | 133.5423 | 133.4934 | 133.1373 | 132.6772 | 132.1444 | 131.4971 | 130.7193 | 129.71 | 128.5166 | 124.1536 | 118.3571 | 114.975 | 112.089 | 112.0774 | 112.0211 | 111.6504 | 111.1211 | 110.5071 | 109.7598 | 108.8605 | 107.6935 | 106.306 | 101.2309 | 94.4886 | 90.5742 | 87.2254 | 122.2545 | 122.1994 | 121.8314 | 121.3142 | 120.7146 | 119.9848 | 119.107 | 117.9678 | 116.6144 | 111.6648 | 105.089 | 101.2684 | 98.0011
|  | COWLEY LOCAL (2 X 90) | FS |  |  | 142.604 | 142.5952 | 142.0635 | 142.0196 | 141.9756 | 141.9316 | 141.8875 | 141.8431 | 141.8234 | 142.0687 | 141.9734 | 141.5073 | 148.1573 | 130.8907 | 130.8458 | 130.3062 | 130.2396 | 130.1686 | 130.0884 | 130.0102 | 129.9215 | 129.8508 | 130.0445 | 129.4859 | 126.903 | 136.7996 | 130.7085 | 130.6837 | 130.1464 | 130.0864 | 130.0232 | 129.9535 | 129.8852 | 129.8094 | 129.7534 | 129.9513 | 127.6532 | 124.695 | 136.4117
BRAMLEY (FLEE) | COXMOOR WOOD BSP | COXMOOR WOOD BSP | MINIMUM HEADROOM | SU 78324 50817 | YES | 28.6481 | -25.4444 | -26.8937 | -35.8625 | -44.8822 | -53.2794 | -61.7452 | -67.9138 | -73.8454 | -95.6143 | -124.6693 | -147.3316 | -153.5923 | 8.8174 | -51.7458 | -53.4966 | -64.3207 | -75.1986 | -85.3151 | -95.509 | -102.8955 | -110.0565 | -136.3312 | -171.3654 | -198.5828 | -206.1315 | 21.1156 | -38.9176 | -40.6631 | -51.4545 | -62.2997 | -72.386 | -82.5495 | -89.9145 | -97.0539 | -123.2493 | -158.1783 | -185.3155 | -192.8415
|  | COXMOOR WOOD BSP | CT |  |  | 34.7008 | 4.8158 | -26.8351 | -31.4845 | -35.6124 | -39.7456 | -43.9401 | -47.5278 | -52.0355 | -67.4864 | -85.7932 | -100.8761 | -116.0448 | 26.1393 | -15.1577 | -53.4297 | -59.0493 | -64.0364 | -69.0282 | -74.0917 | -78.4143 | -83.8616 | -102.5303 | -124.5709 | -142.696 | -160.9844 | 29.8664 | -2.8353 | -40.5964 | -46.1988 | -51.1709 | -56.1475 | -61.1957 | -65.5054 | -70.9362 | -89.5482 | -111.5232 | -129.5947 | -147.8282
|  | COXMOOR WOOD BSP | LW |  |  | 28.6481 | -25.4444 | -26.8937 | -35.8625 | -44.8822 | -53.2794 | -61.7452 | -67.9138 | -73.8454 | -95.6143 | -124.6693 | -147.3316 | -153.5923 | 8.8174 | -51.7458 | -53.4966 | -64.3207 | -75.1986 | -85.3151 | -95.509 | -102.8955 | -110.0565 | -136.3312 | -171.3654 | -198.5828 | -206.1315 | 21.1156 | -38.9176 | -40.6631 | -51.4545 | -62.2997 | -72.386 | -82.5495 | -89.9145 | -97.0539 | -123.2493 | -158.1783 | -185.3155 | -192.8415
|  | COXMOOR WOOD BSP | ST |  |  | 139.9 | 139.8826 | 138.8192 | 138.7158 | 138.6113 | 138.8121 | 138.705 | 138.5847 | 138.5375 | 136.4004 | 128.6908 | 122.8478 | 123.2954 | 130.9157 | 130.8612 | 129.7768 | 129.6179 | 129.4526 | 129.7104 | 129.5097 | 129.269 | 129.0779 | 124.3226 | 115.5352 | 108.8896 | 111.5329 | 128.0253 | 128.0047 | 126.9265 | 126.7836 | 126.636 | 126.867 | 126.6934 | 126.4876 | 125.5936 | 119.4822 | 110.7469 | 104.1402 | 108.6315
|  | COXMOOR WOOD BSP | FS |  |  | 139.8686 | 116.7106 | 116.7104 | 116.7046 | 116.6985 | 116.6921 | 116.6851 | 116.6736 | 116.7365 | 104.136 | 89.4666 | 77.8774 | 71.6251 | 131.354 | 108.1822 | 108.1774 | 108.1028 | 108.018 | 107.4664 | 105.6518 | 103.2248 | 100.139 | 81.661 | 63.9411 | 50.0021 | 42.5115 | 135.0197 | 111.8617 | 111.8615 | 111.8557 | 111.8497 | 111.8432 | 111.7609 | 111.6126 | 111.5154 | 93.8079 | 76.3053 | 62.4076 | 54.9388
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IVER 132KV | DENHAM | DENHAM | MINIMUM HEADROOM | TQ 01785 87618 | YES | 77.4969 | 58.6273 | 49.2545 | 45.4635 | 41.6381 | 91.0215 | 86.8766 | 83.528 | 79.2598 | 64.5035 | 47.7582 | 34.1262 | 20.4377 | 74.0056 | 40.3963 | 24.7418 | 20.1612 | 15.5406 | 58.9927 | 53.9891 | 49.9551 | 44.8001 | 26.9836 | 6.7662 | -9.6119 | -26.1272 | 74.2857 | 41.7469 | 35.7604 | 31.1937 | 26.587 | 75.3012 | 70.3126 | 66.2907 | 61.1513 | 43.3887 | 23.2324 | 6.9026 | -9.5629
|  | DENHAM | CT |  |  | 99.6575 | 99.6575 | 80.069 | 78.8233 | 77.6455 | 129.126 | 128.2432 | 127.0751 | 125.7165 | 121.0992 | 115.0896 | 110.3934 | 105.0376 | 96.1689 | 96.1478 | 61.71 | 60.2507 | 58.8716 | 104.8992 | 103.8685 | 102.5077 | 100.9092 | 95.4771 | 88.4398 | 82.9549 | 76.6582 | 96.4464 | 96.4464 | 63.0632 | 61.6081 | 60.2331 | 111.5148 | 110.4871 | 109.1301 | 107.5365 | 102.1208 | 95.1042 | 89.6352 | 83.3575
|  | DENHAM | LW |  |  | 77.4969 | 58.6273 | 57.7825 | 55.963 | 54.1367 | 105.4206 | 104.0239 | 102.3151 | 100.6079 | 94.4263 | 85.835 | 79.9847 | 77.1414 | 74.0056 | 40.3963 | 39.401 | 37.2584 | 35.1085 | 80.8979 | 79.2557 | 77.249 | 75.2391 | 67.9626 | 57.8555 | 50.9903 | 47.6427 | 74.2857 | 41.7469 | 40.7547 | 38.6185 | 36.4751 | 87.5194 | 85.8822 | 83.8815 | 81.8777 | 74.6233 | 64.5468 | 57.702 | 54.3645
|  | DENHAM | ST |  |  | 109.4865 | 80.2144 | 49.2545 | 45.4635 | 41.6381 | 91.0215 | 86.8766 | 83.528 | 79.2598 | 64.5035 | 47.7582 | 34.1262 | 20.4377 | 102.7681 | 62.1788 | 24.7418 | 20.1612 | 15.5406 | 58.9927 | 53.9891 | 49.9551 | 44.8001 | 26.9836 | 6.7662 | -9.6119 | -26.1272 | 104.6521 | 72.6695 | 35.7604 | 31.1937 | 26.587 | 75.3012 | 70.3126 | 66.2907 | 61.1513 | 43.3887 | 23.2324 | 6.9026 | -9.5629
|  | DENHAM | FS |  |  | 99.6575 | 99.6575 | 99.6575 | 99.6496 | 99.6418 | 152.3039 | 152.2958 | 152.2831 | 152.2474 | 152.1305 | 152.0724 | 151.8794 | 151.7139 | 96.2015 | 96.1997 | 96.198 | 96.1773 | 96.1545 | 143.5513 | 143.528 | 143.4953 | 143.4366 | 143.2273 | 143.042 | 142.7456 | 141.8026 | 96.4464 | 96.4464 | 96.4464 | 96.4384 | 96.4306 | 149.0927 | 149.0846 | 149.0719 | 149.0362 | 148.8346 | 148.6257 | 148.3102 | 148.0664
COWLEY GSP | DRAYTON BSP | DRAYTON BSP | MINIMUM HEADROOM | SU 46684 92706 | YES | 160.3709 | 158.9521 | 153.3405 | 154.4108 | 152.6833 | 150.8737 | 149.0603 | 145.9283 | 144.2763 | 138.4749 | 79.1403 | 60.6213 | 54.8885 | 119.2356 | 117.5232 | 109.0224 | 110.4101 | 108.5896 | 106.6728 | 104.7514 | 101.4872 | 100.2931 | 95.0654 | 17.7844 | -3.7411 | -10.35 | 118.0009 | 116.3729 | 106.5414 | 107.8172 | 106.0194 | 104.1288 | 102.2338 | 99.0018 | 97.8255 | 94.7491 | 13.1459 | -8.1083 | -14.6382
|  | DRAYTON BSP | CT |  |  | 160.8175 | 161.3046 | 159.3964 | 157.2415 | 154.8699 | 152.4143 | 150.0122 | 147.1454 | 144.2763 | 138.4749 | 141.959 | 129.012 | 127.2596 | 119.9626 | 120.6478 | 118.4768 | 115.971 | 113.2278 | 110.3866 | 107.6093 | 104.2971 | 100.9503 | 95.0654 | 110.1998 | 95.2476 | 92.1438 | 118.6076 | 119.2143 | 117.1075 | 114.6874 | 111.9854 | 109.179 | 106.4356 | 103.1635 | 99.8598 | 94.7491 | 117.2934 | 102.3369 | 99.23
|  | DRAYTON BSP | LW |  |  | 171.2065 | 170.3935 | 168.3019 | 165.6581 | 162.6999 | 159.8216 | 156.8547 | 153.4144 | 150.1432 | 169.5215 | 79.1403 | 60.6213 | 54.8885 | 131.9754 | 131.0227 | 128.6816 | 125.5905 | 122.1503 | 118.8047 | 115.3563 | 111.3562 | 107.5388 | 141.1128 | 17.7844 | -3.7411 | -10.35 | 131.0986 | 130.1801 | 127.8999 | 124.9181 | 121.576 | 118.2726 | 114.8676 | 110.9179 | 107.1498 | 148.003 | 13.1459 | -8.1083 | -14.6382
|  | DRAYTON BSP | ST |  |  | 202.1275 | 202.1275 | 183.4332 | 182.5584 | 181.6121 | 180.8649 | 180.0021 | 178.9107 | 177.6471 | 173.3179 | 168.1202 | 164.0794 | 159.4581 | 198.6539 | 198.6427 | 165.2334 | 164.2158 | 163.1143 | 162.2479 | 161.2459 | 159.9829 | 158.5023 | 153.4292 | 147.3298 | 142.6402 | 137.2179 | 198.9164 | 198.9164 | 166.5833 | 165.5687 | 164.4703 | 163.6063 | 162.6071 | 161.3476 | 159.8713 | 154.8132 | 148.7319 | 144.0554 | 138.6493
|  | DRAYTON BSP | FS |  |  | 160.3709 | 158.9521 | 153.3405 | 154.4108 | 152.6833 | 150.8737 | 149.0603 | 145.9283 | 144.8726 | 143.51 | 139.4255 | 135.8813 | 133.7766 | 119.2356 | 117.5232 | 109.0224 | 110.4101 | 108.5896 | 106.6728 | 104.7514 | 101.4872 | 100.2931 | 98.9977 | 94.4936 | 90.4988 | 88.0985 | 118.0009 | 116.3729 | 106.5414 | 107.8172 | 106.0194 | 104.1288 | 102.2338 | 99.0018 | 97.8255 | 96.348 | 91.8231 | 87.8689 | 85.4953
EALING GSP | EALING 22kV | EALING 22kV | MINIMUM HEADROOM | TQ 18371 79475 | YES | 79.7769 | 79.8118 | 78.7896 | 77.3513 | 75.5806 | 73.8724 | 71.986 | 69.737 | 66.98 | 61.1638 | 36.9437 | 23.2956 | 23.1209 | 35.1363 | 35.2903 | 34.1363 | 32.4666 | 30.424 | 28.4552 | 26.2778 | 23.6838 | 20.542 | 14.8603 | -13.2521 | -29.8832 | -31.1438 | 37.729 | 37.8237 | 36.7019 | 35.0888 | 33.1126 | 31.1925 | 29.0414 | 26.4785 | 23.3714 | 18.4442 | -9.317 | -26.4456 | -27.6082
|  | EALING 22kV | CT |  |  | 122.5249 | 122.5249 | 122.4698 | 122.334 | 122.1966 | 122.0588 | 121.9863 | 121.8972 | 121.8541 | 121.7149 | 119.3746 | 114.7879 | 110.7642 | 115.0266 | 114.9889 | 114.9161 | 114.8133 | 114.7093 | 114.327 | 113.7737 | 113.2295 | 112.727 | 111.1039 | 106.9445 | 101.8051 | 97.5972 | 119.81 | 119.7594 | 119.6616 | 119.5345 | 119.406 | 118.1373 | 117.6019 | 117.0747 | 116.5893 | 115.0217 | 110.8658 | 105.6647 | 101.2542
|  | EALING 22kV | LW |  |  | 122.5249 | 122.5249 | 122.487 | 121.9649 | 121.4282 | 120.9332 | 120.42 | 119.6625 | 119.5261 | 119.0659 | 117.9324 | 112.3495 | 107.0001 | 115.0309 | 114.9956 | 114.9278 | 114.4365 | 113.931 | 113.4476 | 112.9465 | 112.2004 | 111.6558 | 109.7117 | 106.0231 | 99.8874 | 93.4239 | 119.8158 | 119.7684 | 119.6773 | 119.1634 | 118.635 | 118.143 | 117.2453 | 116.0497 | 115.4712 | 113.5825 | 109.9629 | 103.7656 | 97.1663
|  | EALING 22kV | ST |  |  | 79.7769 | 79.8118 | 78.7896 | 77.3513 | 75.5806 | 73.8724 | 71.986 | 69.737 | 66.98 | 61.1638 | 36.9437 | 23.2956 | 23.1209 | 35.1363 | 35.2903 | 34.1363 | 32.4666 | 30.424 | 28.4552 | 26.2778 | 23.6838 | 20.542 | 14.8603 | -13.2521 | -29.8832 | -31.1438 | 37.729 | 37.8237 | 36.7019 | 35.0888 | 33.1126 | 31.1925 | 29.0414 | 26.4785 | 23.3714 | 18.4442 | -9.317 | -26.4456 | -27.6082
|  | EALING 22kV | FS |  |  | 122.5249 | 122.5249 | 122.5249 | 122.5249 | 122.5249 | 122.5249 | 122.5249 | 122.5249 | 122.5249 | 122.5249 | 122.49 | 122.3771 | 122.5924 | 115.1038 | 115.0768 | 115.073 | 115.0618 | 115.0486 | 115.0385 | 115.0282 | 115.016 | 115.0094 | 114.988 | 114.9298 | 114.8528 | 115.1163 | 119.9138 | 119.8775 | 119.8724 | 119.8574 | 119.8396 | 119.826 | 119.8122 | 119.7958 | 119.787 | 119.7582 | 119.6801 | 119.5766 | 119.9704
LALEHAM | EAST BEDFONT B | EAST BEDFONT B | MINIMUM HEADROOM | TQ 08394 73826 | YES | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
|  | EAST BEDFONT B | CT |  |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
|  | EAST BEDFONT B | LW |  |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
|  | EAST BEDFONT B | ST |  |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
|  | EAST BEDFONT B | FS |  |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
LALEHAM | EAST BEDFONT A | EAST BEDFONT A | MINIMUM HEADROOM | TQ 08394 73826 | YES | 96.5249 | 96.5249 | 96.5249 | 96.3276 | 96.1271 | 111.8987 | 111.6474 | 111.2959 | 111.1601 | 110.7251 | 110.2317 | 109.0988 | 107.3203 | 90.0855 | 90.0477 | 90.0249 | 89.8002 | 89.5663 | 105.335 | 105.0963 | 104.7526 | 104.6247 | 104.2154 | 103.0952 | 98.8799 | 96.2827 | 93.8892 | 93.8384 | 93.8078 | 93.5736 | 93.3284 | 109.0879 | 108.8399 | 108.4905 | 108.3567 | 107.9285 | 105.9205 | 101.8203 | 99.2081
|  | EAST BEDFONT A | CT |  |  | 105.8091 | 105.8091 | 105.8091 | 105.7983 | 105.7872 | 121.776 | 121.7643 | 121.7462 | 121.7439 | 121.7366 | 121.7026 | 121.2991 | 116.8591 | 98.6512 | 98.64 | 98.6191 | 98.5856 | 98.5527 | 114.5186 | 114.468 | 114.4149 | 114.379 | 114.2656 | 110.9383 | 105.5639 | 100.2152 | 102.7924 | 102.7924 | 102.7924 | 102.7815 | 102.7705 | 118.7592 | 118.7475 | 118.7294 | 118.7272 | 118.6909 | 116.2696 | 111.0122 | 105.6618
|  | EAST BEDFONT A | LW |  |  | 105.8091 | 105.8091 | 105.8091 | 105.6924 | 105.572 | 121.4461 | 121.3157 | 121.1177 | 121.0902 | 120.9962 | 120.8406 | 119.896 | 115.4452 | 98.6506 | 98.6391 | 98.6174 | 98.4775 | 98.3345 | 114.1735 | 114.0042 | 113.7711 | 113.7101 | 113.51 | 109.8068 | 104.1147 | 98.7552 | 102.7924 | 102.7924 | 102.7924 | 102.6756 | 102.5552 | 118.4294 | 118.299 | 118.1009 | 118.0735 | 117.9352 | 115.2018 | 109.5629 | 104.2016
|  | EAST BEDFONT A | ST |  |  | 96.5249 | 96.5249 | 96.5249 | 96.3276 | 96.1271 | 111.8987 | 111.6474 | 111.2959 | 111.1601 | 110.7251 | 110.2317 | 109.0988 | 107.3203 | 90.0855 | 90.0477 | 90.0249 | 89.8002 | 89.5663 | 105.335 | 105.0963 | 104.7526 | 104.6247 | 104.2154 | 103.0952 | 98.8799 | 96.2827 | 93.8892 | 93.8384 | 93.8078 | 93.5736 | 93.3284 | 109.0879 | 108.8399 | 108.4905 | 108.3567 | 107.9285 | 105.9205 | 101.8203 | 99.2081
|  | EAST BEDFONT A | FS |  |  | 105.8091 | 105.8091 | 105.8091 | 105.8091 | 105.8091 | 121.8091 | 121.8091 | 121.8091 | 121.8091 | 121.8091 | 121.8091 | 121.8091 | 121.8091 | 98.6679 | 98.6646 | 98.6599 | 98.6536 | 98.6477 | 114.6396 | 114.6308 | 114.6219 | 114.6129 | 114.5843 | 114.5138 | 114.4217 | 114.3247 | 102.7924 | 102.7924 | 102.7924 | 102.7924 | 102.7924 | 118.7924 | 118.7924 | 118.7924 | 118.7924 | 118.7924 | 118.7924 | 118.7924 | 118.7499
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | FAREHAM T1A T2A (90MVAS) | MINIMUM HEADROOM | SU 56534 04031 | YES | 68.9222 | 66.8082 | 50.15 | 49.5502 | 48.7172 | 47.8604 | 46.7118 | 45.4753 | 44.2465 | 40.0199 | 21.7534 | 13.8673 | 7.5867 | 48.2801 | 44.127 | 27.2808 | 26.4638 | 25.4065 | 24.316 | 22.8152 | 21.1995 | 19.547 | 14.1572 | -9.528 | -19.6507 | -27.8035 | 58.4686 | 54.3553 | 37.4396 | 36.5421 | 35.4018 | 34.2248 | 32.5935 | 30.8375 | 29.0281 | 23.1078 | -5.3668 | -16.9431 | -26.3854
|  | FAREHAM T1A T2A (90MVAS) | CT |  |  | 69.0019 | 66.8082 | 50.15 | 49.5502 | 48.7172 | 47.8604 | 46.7118 | 45.4753 | 44.2465 | 40.2527 | 27.4512 | 20.0995 | 13.5836 | 48.3687 | 44.127 | 27.2808 | 26.4638 | 25.4065 | 24.316 | 22.8152 | 21.1995 | 19.547 | 14.1572 | -2.9667 | -12.3929 | -21.0924 | 58.5605 | 54.3553 | 37.4396 | 36.5421 | 35.4018 | 34.2248 | 32.5935 | 30.8375 | 29.0281 | 23.1078 | 3.1748 | -7.6412 | -17.7599
|  | FAREHAM T1A T2A (90MVAS) | LW |  |  | 68.9222 | 68.6264 | 51.6699 | 50.8999 | 49.8447 | 48.5151 | 47.1821 | 45.7434 | 44.4019 | 40.0199 | 21.7534 | 13.8673 | 7.5867 | 48.2801 | 47.8679 | 30.7131 | 29.6699 | 28.3287 | 26.6021 | 24.8721 | 23.006 | 21.212 | 15.3637 | -9.528 | -19.6507 | -27.8035 | 58.4686 | 58.0133 | 40.7851 | 39.6408 | 38.1937 | 36.3201 | 34.4431 | 32.4188 | 30.4572 | 23.8309 | -5.3668 | -16.9431 | -26.3854
|  | FAREHAM T1A T2A (90MVAS) | ST |  |  | 142.1191 | 142.1191 | 142.1191 | 142.0313 | 141.942 | 141.8509 | 141.7568 | 141.6112 | 141.5619 | 141.4042 | 141.2775 | 140.864 | 140.5016 | 136.1631 | 136.1481 | 136.1363 | 136.0344 | 135.9304 | 135.8173 | 135.6987 | 135.5294 | 135.457 | 135.226 | 134.4521 | 130.9188 | 127.4048 | 139.1024 | 139.1024 | 139.1024 | 139.0145 | 138.9253 | 138.8342 | 138.7401 | 138.5945 | 138.5451 | 138.3874 | 138.1636 | 135.1495 | 131.6637
|  | FAREHAM T1A T2A (90MVAS) | FS |  |  | 122.1395 | 119.8148 | 119.6099 | 119.475 | 116.607 | 113.667 | 110.731 | 105.0312 | 104.176 | 101.4626 | 96.7809 | 93.2489 | 91.0355 | 101.646 | 97.2179 | 96.985 | 96.8004 | 93.8748 | 90.8478 | 87.8264 | 82.0213 | 81.0486 | 77.9234 | 72.5651 | 68.4473 | 65.638 | 111.9493 | 107.5372 | 107.294 | 107.0909 | 104.144 | 101.0848 | 98.0318 | 92.1877 | 91.1716 | 87.8939 | 82.285 | 77.9265 | 74.8966
LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | FAREHAM T1B T2B (1X90, 1X60MVA) | MINIMUM HEADROOM | SU 56534 04031 | YES | 85.5938 | 83.2131 | 30.1299 | 29.6678 | 28.9163 | 28.0288 | 27.1191 | 26.1318 | 24.2245 | 18.2363 | 5.2844 | -0.60179 | -5.3406 | 63.9124 | 59.4062 | 6.2069 | 5.5812 | 4.6389 | 3.5055 | 2.3416 | 1.0783 | -1.1432 | -8.18 | -24.847 | -32.1313 | -38.3604 | 75.3468 | 70.8484 | 17.6061 | 16.9197 | 15.9069 | 14.6825 | 13.4245 | 12.059 | 9.7211 | 2.2961 | -16.556 | -24.7904 | -31.9881
|  | FAREHAM T1B T2B (1X90, 1X60MVA) | CT |  |  | 93.2849 | 93.276 | 92.7357 | 92.6914 | 92.6471 | 92.6028 | 92.5585 | 92.5142 | 92.4965 | 92.4434 | 90.9096 | 86.5732 | 82.3236 | 84.9042 | 84.8954 | 84.355 | 84.3107 | 84.2665 | 84.2222 | 84.1779 | 84.1336 | 84.1159 | 84.0627 | 81.9531 | 76.8783 | 71.8941 | 90.1604 | 90.1436 | 89.5851 | 89.5207 | 89.4544 | 89.3896 | 89.3073 | 89.222 | 89.1607 | 88.9831 | 84.6632 | 79.6532 | 74.7335
|  | FAREHAM T1B T2B (1X90, 1X60MVA) | LW |  |  | 93.2081 | 93.1933 | 92.2928 | 92.219 | 92.1451 | 92.0713 | 91.9975 | 91.9237 | 91.8942 | 91.8056 | 90.6111 | 86.4137 | 82.163 | 84.8275 | 84.8127 | 83.9121 | 83.8383 | 83.7645 | 83.6907 | 83.6169 | 83.543 | 83.5135 | 83.4249 | 81.6261 | 76.6901 | 71.7046 | 90.0849 | 90.0629 | 89.1458 | 89.0533 | 88.959 | 88.8475 | 88.7357 | 88.6208 | 88.5477 | 88.3347 | 84.3387 | 79.4676 | 74.5466
|  | FAREHAM T1B T2B (1X90, 1X60MVA) | ST |  |  | 85.5938 | 83.2131 | 30.1299 | 29.6678 | 28.9163 | 28.0288 | 27.1191 | 26.1318 | 24.2245 | 18.2363 | 5.2844 | -0.60179 | -5.3406 | 63.9124 | 59.4062 | 6.2069 | 5.5812 | 4.6389 | 3.5055 | 2.3416 | 1.0783 | -1.1432 | -8.18 | -24.847 | -32.1313 | -38.3604 | 75.3468 | 70.8484 | 17.6061 | 16.9197 | 15.9069 | 14.6825 | 13.4245 | 12.059 | 9.7211 | 2.2961 | -16.556 | -24.7904 | -31.9881
|  | FAREHAM T1B T2B (1X90, 1X60MVA) | FS |  |  | 93.3617 | 93.3587 | 93.1786 | 93.1614 | 93.1443 | 93.1272 | 93.1101 | 93.0916 | 93.0753 | 93.0248 | 92.9796 | 92.9127 | 92.839 | 84.981 | 84.9781 | 84.7979 | 84.7808 | 84.7637 | 84.7466 | 84.7294 | 84.711 | 84.6947 | 84.6441 | 84.599 | 84.532 | 84.4584 | 90.2479 | 90.2438 | 90.0613 | 90.0397 | 90.0174 | 89.9925 | 89.9676 | 89.9391 | 89.9112 | 89.8273 | 89.7166 | 89.5719 | 89.4186
BRAMLEY (FLEE) | FERNHURST | FERNHURST | MINIMUM HEADROOM | SU 72730 39772 | YES | 112.357 | 112.357 | 112.357 | 112.357 | 112.357 | 112.357 | 112.357 | 112.357 | 112.357 | 112.357 | 112.357 | 106.0926 | 106.0926 | 111.2856 | 111.2856 | 111.2856 | 111.2856 | 111.2856 | 111.2856 | 111.2856 | 111.2856 | 111.2856 | 111.2856 | 111.2856 | 107.3905 | 107.3905 | 114.31 | 114.31 | 114.31 | 114.2214 | 114.1236 | 114.0125 | 113.8885 | 113.6828 | 113.6519 | 113.5255 | 113.2144 | 112.7319 | 112.6044
|  | FERNHURST | CT |  |  | 112.357 | 112.357 | 112.357 | 112.357 | 112.357 | 112.357 | 112.357 | 112.357 | 112.357 | 114.31 | 115.4046 | 115.4046 | 115.4046 | 111.2856 | 111.2856 | 111.2856 | 111.2856 | 111.2856 | 111.2856 | 111.2856 | 111.2856 | 111.2856 | 112.5 | 113.4941 | 113.4941 | 113.4941 | 114.31 | 114.31 | 114.31 | 114.2214 | 114.1294 | 114.034 | 113.9307 | 113.7639 | 113.7417 | 113.6617 | 113.2144 | 112.7319 | 112.6044
|  | FERNHURST | LW |  |  | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 114.31 | 115.4046 | 115.4046 | 115.4046 | 115.7196 | 106.0926 | 106.0926 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 112.5 | 113.4941 | 113.4941 | 113.4941 | 113.7802 | 107.3905 | 107.3905 | 114.31 | 114.31 | 114.31 | 114.2219 | 114.1236 | 114.0125 | 113.8885 | 113.6828 | 113.6519 | 113.5255 | 113.2795 | 112.7416 | 112.7072
|  | FERNHURST | ST |  |  | 129.6333 | 129.6274 | 129.2671 | 129.2376 | 129.2081 | 129.1786 | 129.149 | 129.1195 | 129.1077 | 129.0723 | 129.0132 | 128.3398 | 125.6605 | 122.4426 | 122.4367 | 122.0765 | 122.047 | 122.0174 | 121.9879 | 121.9584 | 121.9289 | 121.917 | 121.8816 | 121.8226 | 120.6182 | 117.4691 | 126.5161 | 126.5068 | 126.1396 | 126.1006 | 126.0594 | 126.0065 | 125.9533 | 125.896 | 125.8543 | 125.7335 | 125.3051 | 122.1344 | 119.0265
|  | FERNHURST | FS |  |  | 112.357 | 112.357 | 112.357 | 112.357 | 112.357 | 112.357 | 112.357 | 112.357 | 112.357 | 112.357 | 112.357 | 112.357 | 115.0445 | 111.2856 | 111.2856 | 111.2856 | 111.2856 | 111.2856 | 111.2856 | 111.2856 | 111.2856 | 111.2856 | 111.2856 | 111.2856 | 111.2856 | 113.1671 | 114.31 | 114.31 | 114.31 | 114.3004 | 114.2909 | 114.2813 | 114.2714 | 114.2558 | 114.2117 | 114.065 | 113.9906 | 113.7378 | 113.519
LOVEDEAN GSP | FORT WIDLEY | FORT WIDLEY | MINIMUM HEADROOM | SU 64948 05441 | YES | 55.8743 | 55.6903 | 54.615 | 53.5999 | 52.4288 | 50.9653 | 49.4286 | 47.6734 | 45.9883 | 40.1489 | 32.2298 | 9.1723 | 4.3413 | 51.413 | 51.2032 | 50.0793 | 48.923 | 47.602 | 45.9697 | 44.2546 | 42.2954 | 40.4014 | 33.8573 | 24.9659 | -1.3417 | -6.6504 | 55.3631 | 55.1551 | 54.0346 | 52.888 | 51.5773 | 49.9566 | 48.2538 | 46.3086 | 44.4289 | 37.9333 | 29.1087 | 3.0245 | -2.2514
|  | FORT WIDLEY | CT |  |  | 55.9633 | 55.7972 | 55.0492 | 54.4305 | 53.7144 | 52.9851 | 51.6561 | 50.2455 | 48.7852 | 44.1078 | 36.8769 | 22.457 | 16.2885 | 51.5049 | 51.3145 | 50.5215 | 49.8139 | 49.0066 | 48.1843 | 46.7246 | 45.1615 | 43.5231 | 38.2783 | 30.3143 | 14.0141 | 7.1539 | 55.4549 | 55.2661 | 54.4762 | 53.7747 | 52.9737 | 52.1578 | 50.7071 | 49.1544 | 47.5283 | 42.3225 | 34.409 | 18.2379 | 11.4253
|  | FORT WIDLEY | LW |  |  | 55.8743 | 55.6903 | 54.615 | 53.5999 | 52.4288 | 50.9653 | 49.4286 | 47.6734 | 45.9883 | 40.1489 | 32.2298 | 9.1723 | 4.3413 | 51.413 | 51.2032 | 50.0793 | 48.923 | 47.602 | 45.9697 | 44.2546 | 42.2954 | 40.4014 | 33.8573 | 24.9659 | -1.3417 | -6.6504 | 55.3631 | 55.1551 | 54.0346 | 52.888 | 51.5773 | 49.9566 | 48.2538 | 46.3086 | 44.4289 | 37.9333 | 29.1087 | 3.0245 | -2.2514
|  | FORT WIDLEY | ST |  |  | 76.047 | 76.047 | 76.047 | 76.047 | 76.047 | 76.047 | 76.047 | 76.047 | 76.047 | 78 | 79.0946 | 78.7345 | 78.7345 | 73.7856 | 73.7856 | 73.7856 | 73.7856 | 73.7856 | 73.7856 | 73.7856 | 73.7856 | 73.7856 | 75 | 75.9941 | 75.6671 | 75.6671 | 78 | 78 | 78 | 77.9152 | 77.8277 | 77.7366 | 77.6403 | 77.4862 | 77.4317 | 77.2415 | 77.0672 | 76.518 | 76.3423
|  | FORT WIDLEY | FS |  |  | 56.2131 | 56.177 | 55.9867 | 55.8418 | 54.6353 | 53.3674 | 52.0379 | 49.6167 | 49.0295 | 47.0031 | 44.0246 | 41.711 | 40.231 | 51.783 | 51.7417 | 51.5454 | 51.3803 | 50.1493 | 48.8474 | 47.482 | 45.0176 | 44.3781 | 42.1609 | 38.9188 | 36.3748 | 34.7211 | 55.731 | 55.6901 | 55.4942 | 55.3305 | 54.1012 | 52.8016 | 51.4387 | 48.9773 | 48.3414 | 46.1372 | 42.9132 | 40.3851 | 38.7434
MELKSHAM GSP | FROME BSP | FROME BSP | MINIMUM HEADROOM | ST 78803 48019 | YES | 65.5206 | 63.3214 | 60.4345 | 50.7193 | 40.53 | 30.0598 | 20.3208 | 10.3502 | 1.2198 | -32.2138 | -86.1806 | -130.8249 | -145.5821 | 26.1256 | 23.1505 | 19.3447 | 8.8173 | -2.9779 | -15.0932 | -25.9432 | -37.4054 | -48.0389 | -87.0212 | -148.1079 | -199.6106 | -219.5865 | 25.3201 | 22.2881 | 18.54 | 8.0649 | -3.6281 | -15.6389 | -26.3119 | -37.6793 | -48.2172 | -87.292 | -148.5254 | -200.2252 | -220.475
|  | FROME BSP | CT |  |  | 95.6582 | 63.6472 | 61.7063 | 57.2813 | 53.0903 | 48.9124 | 43.6145 | 37.9887 | 31.1147 | 8.3388 | -27.9145 | -55.7808 | -70.5316 | 56.2774 | 23.4983 | 21.444 | 16.2685 | 11.4299 | 6.6086 | 0.47376 | -6.0393 | -14.0537 | -40.2272 | -81.8219 | -113.8291 | -128.872 | 55.4709 | 22.6344 | 20.5873 | 15.4596 | 10.6622 | 5.8818 | -0.19984 | -6.6565 | -14.5984 | -40.4495 | -82.0668 | -114.193 | -129.1616
|  | FROME BSP | LW |  |  | 65.5206 | 63.3214 | 60.4345 | 50.7193 | 40.53 | 30.0598 | 20.3208 | 10.3502 | 1.2198 | -32.2138 | -86.1806 | -130.8249 | -145.5821 | 26.1256 | 23.1505 | 20.1335 | 8.8173 | -2.9779 | -15.0932 | -25.9432 | -37.4054 | -48.0389 | -87.0212 | -148.1079 | -199.6106 | -219.5865 | 25.3201 | 22.2881 | 19.2793 | 8.0649 | -3.6281 | -15.6389 | -26.3119 | -37.6793 | -48.2172 | -87.292 | -148.5254 | -200.2252 | -220.475
|  | FROME BSP | ST |  |  | 92.3707 | 92.2615 | 91.7954 | 91.3056 | 90.6766 | 89.9012 | 89.0105 | 87.9205 | 86.4414 | 81.7304 | 75.9702 | 63.4678 | 59.2204 | 89.1121 | 88.9868 | 88.4955 | 87.9385 | 87.2341 | 86.3733 | 85.3814 | 84.1683 | 82.5413 | 77.3475 | 70.9852 | 56.7511 | 51.9642 | 91.8714 | 91.7472 | 91.2576 | 90.7053 | 90.006 | 89.1512 | 88.1662 | 86.9615 | 85.3447 | 80.1841 | 73.8631 | 59.7481 | 54.9983
|  | FROME BSP | FS |  |  | 76.0433 | 71.0799 | 61.3078 | 60.1641 | 54.5707 | 48.3884 | 36.1552 | 25.1077 | 20.8983 | 5.5489 | -17.3853 | -34.5657 | -39.0912 | 38.2067 | 30.753 | 19.3447 | 18.0085 | 12.1965 | 5.6927 | -10.8997 | -22.367 | -27.1505 | -44.4393 | -70.5283 | -90.098 | -93.1609 | 37.4332 | 29.8443 | 18.54 | 17.2161 | 11.418 | 4.9346 | -12.1769 | -23.6175 | -28.3644 | -45.7923 | -71.6807 | -91.0984 | -93.7237
MINETY GSP | GALILEO | GALILEO | MINIMUM HEADROOM | SU 10596 83733 | NO | 62.9892 | 62.9892 | 62.9892 | 62.9892 | 62.9892 | 62.9892 | 62.9892 | 62.9892 | 62.9892 | 62.9892 | 62.9375 | 62.3182 | 61.7142 | 58.9215 | 58.9215 | 58.9215 | 58.9215 | 58.9215 | 58.9215 | 58.9215 | 58.9215 | 58.9215 | 58.7398 | 58.0017 | 57.2712 | 56.5586 | 61.3023 | 61.298 | 61.2917 | 61.2861 | 61.2791 | 61.2689 | 61.2582 | 61.2488 | 61.2389 | 61.2128 | 60.4988 | 59.768 | 59.0552
|  | GALILEO | CT |  |  | 66.5664 | 66.5664 | 66.5664 | 66.5357 | 66.5045 | 66.4727 | 66.4395 | 66.3884 | 66.3819 | 66.3611 | 66.265 | 66.1616 | 65.593 | 64.1222 | 64.1112 | 64.0898 | 64.0377 | 63.9847 | 63.931 | 63.8584 | 63.7676 | 63.7191 | 63.564 | 63.1577 | 62.3348 | 61.4981 | 67.0172 | 67.0113 | 67 | 66.958 | 66.9151 | 66.8717 | 66.8176 | 66.7455 | 66.7167 | 66.5707 | 65.9345 | 65.0847 | 64.2035
|  | GALILEO | LW |  |  | 66.5664 | 66.5664 | 66.5664 | 66.5664 | 66.5664 | 66.5664 | 66.5664 | 66.5664 | 66.5664 | 66.5664 | 66.5664 | 66.5664 | 65.9664 | 64.1198 | 64.1075 | 64.0834 | 64.0594 | 64.0349 | 63.9956 | 63.9561 | 63.9165 | 63.8745 | 63.7402 | 63.4156 | 62.683 | 61.8621 | 67.0159 | 67.0094 | 66.9966 | 66.9838 | 66.9708 | 66.95 | 66.9291 | 66.908 | 66.8857 | 66.7253 | 66.1853 | 65.4238 | 64.5693
|  | GALILEO | ST |  |  | 62.9892 | 62.9892 | 62.9892 | 62.9892 | 62.9892 | 62.9892 | 62.9892 | 62.9892 | 62.9892 | 62.9892 | 62.9375 | 62.3182 | 61.7142 | 58.9215 | 58.9215 | 58.9215 | 58.9215 | 58.9215 | 58.9215 | 58.9215 | 58.9215 | 58.9215 | 58.7398 | 58.0017 | 57.2712 | 56.5586 | 61.3023 | 61.298 | 61.2917 | 61.2861 | 61.2791 | 61.2689 | 61.2582 | 61.2488 | 61.2389 | 61.2128 | 60.4988 | 59.768 | 59.0552
|  | GALILEO | FS |  |  | 66.5664 | 66.5664 | 66.5664 | 66.5634 | 66.5605 | 66.5575 | 66.5545 | 66.5499 | 66.5368 | 66.4954 | 66.4757 | 66.4137 | 66.3618 | 64.2125 | 64.1337 | 64.1316 | 64.1227 | 64.1127 | 64.1014 | 64.09 | 64.0749 | 64.0506 | 63.9736 | 63.8671 | 63.695 | 63.528 | 67.0651 | 67.0233 | 67.0222 | 67.016 | 67.0093 | 67.002 | 66.9945 | 66.9843 | 66.9653 | 66.905 | 66.8392 | 66.7188 | 66.5074
COWLEY GSP | HARWELL | HARWELL | MINIMUM HEADROOM |  |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
|  | HARWELL | CT |  |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
|  | HARWELL | LW |  |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
|  | HARWELL | ST |  |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
|  | HARWELL | FS |  |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
LOVEDEAN GSP | HAVANT | HAVANT | MINIMUM HEADROOM | SU 70625 05720 | YES | 33.5721 | 64.7523 | 63.417 | 59.5277 | 55.3502 | 51.2861 | 46.2628 | 40.9852 | 32.9576 | 6.7204 | -29.046 | -56.0876 | -69.5704 | -3.9313 | 24.7913 | 23.3728 | 18.8188 | 13.9893 | 9.2943 | 3.474 | -2.6391 | -11.7523 | -41.2193 | -82.0602 | -113.5173 | -127.0388 | -6.5521 | 23.9061 | 22.4929 | 17.9812 | 13.1931 | 8.5383 | 2.7687 | -3.2913 | -12.3355 | -41.4908 | -82.2898 | -113.8903 | -127.3302
|  | HAVANT | CT |  |  | 107.8496 | 140.5282 | 140.5259 | 151.822 | 151.7823 | 151.7416 | 151.2681 | 150.8539 | 150.5629 | 149.6242 | 147.9378 | 142.2837 | 126.7353 | 102.0737 | 132.88 | 132.8469 | 147.7771 | 147.7374 | 147.6967 | 147.2233 | 146.8091 | 146.5181 | 145.387 | 135.2724 | 124.3516 | 103.305 | 101.4305 | 134.0108 | 133.9666 | 147.6813 | 147.6416 | 147.6009 | 147.1275 | 146.7133 | 146.4223 | 145.2524 | 134.4744 | 123.6967 | 101.8924
|  | HAVANT | LW |  |  | 119.1771 | 151.8527 | 151.8467 | 151.6372 | 151.4187 | 150.9914 | 150.5485 | 149.9479 | 149.6309 | 148.3271 | 147.2205 | 126.7684 | 120.473 | 116.9323 | 147.8078 | 147.8019 | 147.5923 | 147.3738 | 146.9466 | 146.5037 | 145.9031 | 145.5692 | 143.7385 | 131.4461 | 104.9029 | 94.6356 | 115.0365 | 147.712 | 147.7061 | 147.4965 | 147.278 | 146.8508 | 146.4079 | 145.8073 | 145.4828 | 142.8148 | 130.6964 | 102.9472 | 92.8171
|  | HAVANT | ST |  |  | 33.5721 | 64.7523 | 63.417 | 59.5277 | 55.3502 | 51.2861 | 46.2628 | 40.9852 | 32.9576 | 6.7204 | -29.046 | -56.0876 | -69.5704 | -3.9313 | 24.7913 | 23.3728 | 18.8188 | 13.9893 | 9.2943 | 3.474 | -2.6391 | -11.7523 | -41.2193 | -82.0602 | -113.5173 | -127.0388 | -6.5521 | 23.9061 | 22.4929 | 17.9812 | 13.1931 | 8.5383 | 2.7687 | -3.2913 | -12.3355 | -41.4908 | -82.2898 | -113.8903 | -127.3302
|  | HAVANT | FS |  |  | 107.8514 | 138.2905 | 138.2816 | 138.1493 | 138.1129 | 138.0651 | 137.9584 | 139.2543 | 151.939 | 151.5211 | 151.278 | 150.8389 | 150.4578 | 102.1125 | 131.7937 | 131.7875 | 131.69 | 131.6588 | 131.6198 | 131.5216 | 132.8281 | 147.9897 | 147.5717 | 147.3287 | 146.7771 | 146.2839 | 101.4828 | 131.6929 | 131.6928 | 131.673 | 131.6536 | 131.6342 | 131.5554 | 132.8854 | 147.6315 | 147.2135 | 146.9135 | 146.3257 | 145.8016
COWLEY GSP | HEADINGTON BSP | HEADINGTON BSP | MINIMUM HEADROOM | SP 54454 08145 | NO | 104.2268 | 102.2559 | 102.1593 | 99.3863 | 94.6141 | 89.7208 | 84.7673 | 80.0236 | 75.4148 | 59.1666 | 32.386 | 14.2394 | 6.7545 | 75.8558 | 73.0456 | 72.9274 | 70.2107 | 64.6052 | 58.9417 | 53.2139 | 47.7681 | 42.4479 | 23.9688 | -6.8024 | -28.327 | -36.5673 | 72.281 | 68.8493 | 68.7318 | 67.1589 | 61.8037 | 56.3233 | 50.7796 | 45.5007 | 40.3496 | 22.6314 | -6.6983 | -28.241 | -36.3017
|  | HEADINGTON BSP | CT |  |  | 104.2268 | 103.5223 | 102.3124 | 99.9349 | 97.7978 | 95.6843 | 92.4028 | 89.1266 | 85.4122 | 74.6524 | 55.3783 | 43.3869 | 32.79 | 75.8558 | 74.9945 | 73.6095 | 70.6228 | 67.9329 | 65.3666 | 61.6767 | 57.9667 | 53.7019 | 41.8541 | 19.7996 | 6.5491 | -4.9293 | 72.281 | 71.4249 | 70.0457 | 67.1589 | 64.5655 | 62.091 | 58.4982 | 54.8914 | 50.7574 | 39.7157 | 18.3222 | 5.6016 | -5.1744
|  | HEADINGTON BSP | LW |  |  | 105.7885 | 105.0678 | 103.8298 | 99.3863 | 94.6141 | 89.7208 | 84.7673 | 80.0236 | 75.4148 | 59.1666 | 32.386 | 14.2394 | 6.7545 | 78.0359 | 77.1563 | 75.7386 | 70.2107 | 64.6052 | 58.9417 | 53.2139 | 47.7681 | 42.4479 | 23.9688 | -6.8024 | -28.327 | -36.5673 | 74.8737 | 73.9994 | 72.5877 | 67.2111 | 61.8037 | 56.3233 | 50.7796 | 45.5007 | 40.3496 | 22.6314 | -6.6983 | -28.241 | -36.3017
|  | HEADINGTON BSP | ST |  |  | 140.5415 | 140.5414 | 140.5413 | 151.7687 | 151.6594 | 151.4499 | 151.2246 | 150.8901 | 150.7452 | 150.2833 | 149.7382 | 141.6613 | 140.6835 | 132.9825 | 132.8983 | 132.8821 | 147.7139 | 147.6046 | 147.3951 | 147.1697 | 146.8353 | 146.6904 | 146.214 | 143.649 | 127.8025 | 121.1737 | 134.159 | 134.0445 | 134.0225 | 147.6281 | 147.5188 | 147.3093 | 147.0839 | 146.7494 | 146.6046 | 146.1382 | 142.7585 | 126.1058 | 119.5727
|  | HEADINGTON BSP | FS |  |  | 104.712 | 102.2559 | 102.1593 | 101.5648 | 100.9068 | 100.0657 | 99.1025 | 97.8464 | 96.3066 | 89.7814 | 81.2252 | 74.9758 | 72.362 | 76.4487 | 73.0456 | 72.9274 | 72.1966 | 71.3694 | 70.3114 | 69.1344 | 67.5966 | 65.6879 | 57.7983 | 47.7693 | 40.6714 | 38.0809 | 72.8703 | 68.8493 | 68.7318 | 68.0114 | 67.2138 | 66.1937 | 65.054 | 63.5654 | 61.721 | 54.0981 | 44.4193 | 37.7536 | 35.6502
COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE BSP | MINIMUM HEADROOM | SU 84773 92191 | YES | 104.4607 | 104.2475 | 103.8705 | 101.9558 | 100.043 | 98.0819 | 95.6391 | 92.8983 | 89.7951 | 80.8713 | 65.2343 | 55.3428 | 48.2677 | 76.1412 | 75.8803 | 75.419 | 73.0779 | 70.6897 | 68.2999 | 65.3781 | 62.2397 | 58.6243 | 48.7096 | 30.457 | 18.7661 | 11.0096 | 72.5646 | 72.3053 | 71.8468 | 69.5383 | 67.233 | 64.9181 | 62.0891 | 59.0452 | 55.5516 | 46.4199 | 28.7892 | 17.2091 | 10.1073
|  | HIGH WYCOMBE BSP | CT |  |  | 122.7001 | 122.2045 | 119.6002 | 118.0736 | 116.414 | 114.759 | 113.1311 | 111.2422 | 109.4499 | 103.7108 | 92.497 | 78.9518 | 70.2645 | 92.0743 | 91.5037 | 88.7467 | 87.0219 | 85.1738 | 83.3317 | 81.5222 | 79.4238 | 77.3851 | 70.85 | 58.3557 | 42.8972 | 32.9331 | 101.846 | 101.3964 | 98.8862 | 97.4816 | 95.938 | 94.3982 | 92.8819 | 91.1221 | 89.4814 | 84.2321 | 73.728 | 59.5498 | 49.8089
|  | HIGH WYCOMBE BSP | LW |  |  | 122.5578 | 122.0942 | 118.5025 | 116.6257 | 114.5286 | 112.4281 | 110.322 | 107.942 | 105.836 | 98.777 | 87.1858 | 68.9855 | 61.9848 | 91.9464 | 91.4159 | 87.6882 | 85.5644 | 83.2214 | 80.8757 | 78.5247 | 75.8668 | 73.4736 | 65.3933 | 52.1591 | 31.1499 | 23.1804 | 101.6948 | 101.2724 | 97.7643 | 96.0395 | 94.0938 | 92.1442 | 90.1889 | 87.9799 | 86.0506 | 79.5935 | 68.6425 | 48.1116 | 40.307
|  | HIGH WYCOMBE BSP | ST |  |  | 104.4607 | 104.2475 | 103.8705 | 101.9558 | 100.043 | 98.0819 | 95.6391 | 92.8983 | 89.7951 | 80.8713 | 65.2343 | 55.3428 | 48.2677 | 76.1412 | 75.8803 | 75.419 | 73.0779 | 70.6897 | 68.2999 | 65.3781 | 62.2397 | 58.6243 | 48.7096 | 30.457 | 18.7661 | 11.0096 | 72.5646 | 72.3053 | 71.8468 | 69.5383 | 67.233 | 64.9181 | 62.0891 | 59.0452 | 55.5516 | 46.4199 | 28.7892 | 17.2091 | 10.1073
|  | HIGH WYCOMBE BSP | FS |  |  | 123.7525 | 123.7029 | 123.1184 | 122.8721 | 120.2116 | 117.4561 | 114.7041 | 109.4727 | 108.5191 | 105.3711 | 100.2167 | 96.2439 | 93.856 | 93.2433 | 93.1872 | 92.5969 | 92.3187 | 89.6214 | 86.814 | 84.0107 | 78.7125 | 77.6876 | 74.2794 | 68.7373 | 64.4157 | 61.7742 | 102.8266 | 102.781 | 102.2001 | 101.9734 | 99.3355 | 96.612 | 93.8916 | 88.7012 | 87.7915 | 84.8037 | 79.8879 | 76.1297 | 73.921
FAWLEY GSP | LANGLEY BSP | LANGLEY BSP | MINIMUM HEADROOM | SU 45185 01376 | YES | 65.9328 | 65.2646 | 65.2612 | 64.8527 | 63.6871 | 62.4753 | 61.1852 | 59.7305 | 57.4095 | 50.102 | 40.7798 | 29.5735 | 23.0107 | 36.4654 | 36.1797 | 34.6427 | 33.6317 | 32.3363 | 30.9878 | 29.5487 | 27.925 | 25.4012 | 17.4311 | 7.1797 | -5.6242 | -13.1497 | 46.5803 | 46.3541 | 44.9148 | 44.0941 | 43.0083 | 41.8808 | 40.6822 | 39.3316 | 37.1354 | 30.2357 | 21.474 | 11.1417 | 3.8918
|  | LANGLEY BSP | CT |  |  | 65.9569 | 65.9262 | 65.8619 | 65.7164 | 65.5548 | 65.39 | 64.9551 | 64.4583 | 63.8816 | 61.9596 | 57.8276 | 55.793 | 53.6757 | 57.4325 | 57.3965 | 57.321 | 57.1501 | 56.9605 | 56.7671 | 56.2566 | 55.6736 | 54.9966 | 52.7404 | 47.8914 | 45.5051 | 43.02 | 61.5927 | 61.558 | 61.4852 | 61.3205 | 61.1378 | 60.9513 | 60.4593 | 59.8974 | 59.2449 | 57.0704 | 52.3965 | 50.0962 | 47.7009
|  | LANGLEY BSP | LW |  |  | 65.9328 | 65.8889 | 65.7965 | 65.5413 | 65.2594 | 64.7508 | 64.234 | 63.6476 | 63.0189 | 60.8646 | 54.8041 | 52.5761 | 50.8182 | 57.4042 | 57.3527 | 57.2442 | 56.9447 | 56.6139 | 56.0172 | 55.4109 | 54.7233 | 53.9854 | 51.4569 | 44.3435 | 41.7316 | 39.6679 | 61.5654 | 61.5157 | 61.4112 | 61.1225 | 60.8037 | 60.2285 | 59.6441 | 58.9812 | 58.27 | 55.8329 | 48.9768 | 46.4316 | 44.3955
|  | LANGLEY BSP | ST |  |  | 67.4713 | 67.2225 | 65.7459 | 64.8527 | 63.6871 | 62.4753 | 61.1852 | 59.7305 | 57.4095 | 50.102 | 40.7798 | 29.5735 | 23.0107 | 36.4654 | 36.1797 | 34.6427 | 33.6317 | 32.3363 | 30.9878 | 29.5487 | 27.925 | 25.4012 | 17.4311 | 7.1797 | -5.6242 | -13.1497 | 46.5803 | 46.3541 | 44.9148 | 44.0941 | 43.0083 | 41.8808 | 40.6822 | 39.3316 | 37.1354 | 30.2357 | 21.474 | 11.1417 | 3.8918
|  | LANGLEY BSP | FS |  |  | 66.0705 | 65.2646 | 65.2612 | 65.2255 | 65.1772 | 65.089 | 64.9999 | 64.8819 | 64.7201 | 64.8714 | 64.0772 | 63.4839 | 63.0095 | 57.5659 | 56.558 | 56.554 | 56.5121 | 56.4554 | 56.3518 | 56.2472 | 56.1087 | 55.9188 | 56.1584 | 55.2261 | 54.5303 | 53.974 | 61.7212 | 60.7793 | 60.7754 | 60.735 | 60.6804 | 60.5805 | 60.4798 | 60.3462 | 60.1632 | 60.3646 | 59.4661 | 58.7953 | 58.2591
IVER 132KV | LONGFORD | LONGFORD | MINIMUM HEADROOM | TQ 03910 76751 | YES | 73.951 | 73.951 | 73.951 | 73.9498 | 73.9486 | 73.9474 | 73.9462 | 73.9444 | 73.9392 | 73.9228 | 75.4009 | 75.3763 | 75.3557 | 76.889 | 76.8056 | 76.8019 | 76.7866 | 76.7688 | 76.7404 | 76.7122 | 76.6751 | 76.6302 | 76.4685 | 77.6112 | 77.3525 | 77.1002 | 72.1844 | 72.1688 | 72.1681 | 72.1643 | 72.16 | 72.1537 | 72.1475 | 72.139 | 72.1264 | 72.0828 | 73.4599 | 73.3915 | 73.3275
|  | LONGFORD | CT |  |  | 100.4188 | 100.4188 | 100.3984 | 100.378 | 100.3372 | 100.3372 | 100.2963 | 101.1404 | 101.12 | 101.0792 | 100.9771 | 100.9363 | 100.8546 | 94.6081 | 94.6058 | 94.5805 | 94.5554 | 94.5099 | 94.5052 | 94.4562 | 95.5487 | 95.5196 | 95.4473 | 95.2965 | 94.7199 | 93.5599 | 96.0667 | 96.0557 | 96.0124 | 95.9697 | 95.9065 | 95.8843 | 95.8048 | 96.9645 | 96.9029 | 96.7128 | 96.3798 | 96.0892 | 95.7597
|  | LONGFORD | LW |  |  | 100.4188 | 100.4188 | 101.2425 | 101.1903 | 101.1168 | 101.0826 | 101.0064 | 100.9526 | 100.9247 | 100.8583 | 100.7162 | 100.596 | 100.5088 | 94.6079 | 94.6055 | 95.6807 | 95.6237 | 95.5452 | 95.5029 | 95.4185 | 95.3566 | 95.32 | 95.2221 | 95.0313 | 94.2903 | 93.1244 | 96.0658 | 96.0544 | 97.2083 | 97.1329 | 97.0361 | 96.9632 | 96.8483 | 96.7561 | 96.687 | 96.4714 | 96.0984 | 95.7284 | 95.3933
|  | LONGFORD | ST |  |  | 121.7613 | 121.7317 | 121.6813 | 121.5504 | 121.3922 | 121.1251 | 120.8374 | 120.4663 | 120.0282 | 118.5497 | 115.0836 | 113.6526 | 112.1171 | 113.6759 | 113.6412 | 113.582 | 113.4284 | 113.2426 | 112.9291 | 112.5914 | 112.156 | 111.6417 | 109.9064 | 105.8378 | 104.1603 | 102.3585 | 117.3963 | 117.3629 | 117.3059 | 117.1578 | 116.9787 | 116.6765 | 116.3511 | 115.9314 | 115.4357 | 113.7631 | 109.8418 | 108.2245 | 106.4877
|  | LONGFORD | FS |  |  | 73.951 | 73.951 | 73.951 | 73.9498 | 73.9486 | 73.9474 | 73.9462 | 73.9444 | 73.9392 | 73.9228 | 75.4009 | 75.3763 | 75.3557 | 76.889 | 76.8056 | 76.8019 | 76.7866 | 76.7688 | 76.7404 | 76.7122 | 76.6751 | 76.6302 | 76.4685 | 77.6112 | 77.3525 | 77.1002 | 72.1844 | 72.1688 | 72.1681 | 72.1643 | 72.16 | 72.1537 | 72.1475 | 72.139 | 72.1264 | 72.0828 | 73.4599 | 73.3915 | 73.3275
AMERSHAM | LOUDWATER BSP | LOUDWATER BSP | MINIMUM HEADROOM | SU 90644 91247 | YES | 91.1967 | 48.3594 | 48.2782 | 48.0115 | 47.7418 | 47.4691 | 47.2083 | 46.8384 | 46.7418 | 46.4417 | 45.5538 | 42.7909 | 39.0922 | 82.0645 | 39.7975 | 39.6476 | 39.3155 | 38.9806 | 38.6428 | 38.3344 | 37.9183 | 37.6487 | 36.7805 | 33.8414 | 28.9784 | 24.6812 | 85.2677 | 42.8724 | 42.805 | 42.5514 | 42.2947 | 42.0351 | 41.7839 | 41.4233 | 41.3364 | 41.071 | 37.2028 | 32.3218 | 28.007
|  | LOUDWATER BSP | CT |  |  | 92.725 | 48.3594 | 48.2782 | 48.0115 | 47.7418 | 47.4691 | 47.2083 | 46.8384 | 46.7418 | 46.4417 | 45.5538 | 42.7909 | 39.0922 | 84.2004 | 39.7975 | 39.6476 | 39.3155 | 38.9806 | 38.6428 | 38.3344 | 37.9183 | 37.6487 | 36.7805 | 33.8414 | 28.9784 | 24.6812 | 87.2304 | 42.8724 | 42.805 | 42.5514 | 42.2947 | 42.0351 | 41.7839 | 41.4233 | 41.3364 | 41.071 | 37.2028 | 32.3218 | 28.007
|  | LOUDWATER BSP | LW |  |  | 92.7276 | 48.3635 | 48.2854 | 48.1948 | 48.1039 | 48.0296 | 47.9551 | 47.873 | 47.8126 | 47.629 | 47.3139 | 45.5325 | 41.9953 | 84.2052 | 39.805 | 39.6608 | 39.5073 | 39.3537 | 39.2314 | 39.1092 | 38.9809 | 38.8349 | 38.0817 | 36.0393 | 31.7884 | 27.6523 | 87.2326 | 42.8758 | 42.8109 | 42.7329 | 42.6546 | 42.59 | 42.5251 | 42.4522 | 42.4015 | 42.2513 | 39.4027 | 35.1338 | 30.9801
|  | LOUDWATER BSP | ST |  |  | 100.4188 | 100.4188 | 100.3984 | 100.378 | 100.378 | 100.3372 | 100.3372 | 101.1812 | 101.1608 | 101.1608 | 101.12 | 101.0996 | 101.0792 | 94.6145 | 94.6088 | 94.5864 | 94.5637 | 94.5608 | 94.5146 | 94.5093 | 95.6044 | 95.578 | 95.5565 | 95.4828 | 95.4282 | 95.3658 | 96.097 | 96.0699 | 96.0404 | 96.0088 | 95.9953 | 95.9289 | 95.9037 | 97.0756 | 97.0271 | 96.9248 | 96.7285 | 96.5461 | 96.3658
|  | LOUDWATER BSP | FS |  |  | 91.1967 | 91.1893 | 91.1834 | 91.1688 | 91.152 | 91.1358 | 91.1199 | 91.1005 | 91.0849 | 91.0397 | 90.9631 | 90.8872 | 90.8141 | 82.0645 | 82.0515 | 82.0409 | 82.0151 | 81.9853 | 81.9566 | 81.9283 | 81.8939 | 81.8445 | 81.6502 | 81.3203 | 80.993 | 80.6786 | 85.2677 | 85.2618 | 85.2571 | 85.2455 | 85.2321 | 85.2191 | 85.2064 | 85.191 | 85.1785 | 85.1425 | 85.0814 | 85.0207 | 84.9625
MANNINGTON GSP | LYTCHETT | LYTCHETT | MINIMUM HEADROOM | SY 97796 94214 | YES | 47.6145 | 38.8727 | 37.4868 | 28.6978 | 19.3824 | 8.6867 | -2.1207 | -11.3029 | -19.9808 | -52.5258 | -101.7789 | -140.3249 | -152.5027 | 18.6453 | 9.5688 | 8.1333 | -1.4376 | -12.079 | -24.1519 | -36.3424 | -46.6189 | -56.3986 | -93.0169 | -148.7704 | -192.0039 | -205.1048 | 20.7392 | 11.6548 | 10.2128 | 0.33982 | -10.4757 | -22.7293 | -35.1014 | -45.5216 | -55.446 | -92.599 | -149.2059 | -193.0549 | -206.2769
|  | LYTCHETT | CT |  |  | 58.01 | 38.8727 | 37.4868 | 33.1788 | 29.2011 | 25.1898 | 18.8498 | 12.4489 | 5.6637 | -17.4349 | -52.6547 | -80.4415 | -102.2689 | 30.3715 | 9.5688 | 8.1333 | 3.2201 | -1.2743 | -5.8054 | -12.6008 | -19.6437 | -27.2595 | -53.225 | -92.292 | -122.9784 | -147.1842 | 32.6761 | 11.6548 | 10.2128 | 5.2201 | 0.65783 | -3.9415 | -10.96 | -18.0872 | -25.812 | -52.1539 | -91.726 | -122.793 | -147.3111
|  | LYTCHETT | LW |  |  | 47.6145 | 39.0856 | 37.6647 | 28.6978 | 19.3824 | 8.6867 | -2.1207 | -11.3029 | -19.9808 | -52.5258 | -101.7789 | -140.3249 | -152.5027 | 18.6453 | 10.0913 | 8.8507 | -1.4376 | -12.079 | -24.1519 | -36.3424 | -46.6189 | -56.3986 | -93.0169 | -148.7704 | -192.0039 | -205.1048 | 20.7392 | 12.1818 | 10.8016 | 0.33982 | -10.4757 | -22.7293 | -35.1014 | -45.5216 | -55.446 | -92.599 | -149.2059 | -193.0549 | -206.2769
|  | LYTCHETT | ST |  |  | 92.7442 | 92.715 | 92.6711 | 48.2594 | 48.1585 | 48.0739 | 47.9884 | 47.887 | 47.8267 | 47.6454 | 47.3943 | 47.0043 | 46.7508 | 84.2359 | 84.1819 | 84.1009 | 39.6456 | 39.4926 | 39.3702 | 39.2475 | 39.1146 | 39.0216 | 38.7457 | 37.9226 | 36.8739 | 34.5082 | 87.2464 | 87.2221 | 87.1857 | 42.7828 | 42.6923 | 42.6153 | 42.5373 | 42.4422 | 42.3884 | 42.2261 | 42.0119 | 40.6134 | 37.8673
|  | LYTCHETT | FS |  |  | 59.5521 | 50.2304 | 49.4518 | 48.4329 | 44.4065 | 46.0772 | 38.2287 | 30.9879 | 27.0903 | 11.2446 | -8.955 | -24.8052 | -33.1045 | 32.2273 | 22.7507 | 21.6639 | 20.4954 | 16.2984 | 17.7033 | 7.3701 | -0.21871 | -4.5856 | -22.4333 | -45.0108 | -62.8568 | -72.1937 | 34.5581 | 25.0612 | 23.97 | 22.7818 | 18.5624 | 19.9324 | 9.5365 | 1.9019 | -2.5266 | -20.6372 | -43.6901 | -61.7982 | -71.2713
BRAMLEY (FLEE) | MAIDENHEAD BSP | MAIDENHEAD BSP | MINIMUM HEADROOM | SU 86592 79883 | YES | 59.0951 | 37.1929 | 37.1929 | 34.657 | 30.9144 | 26.4582 | 21.653 | 16.3441 | 9.4777 | -13.6946 | -43.9181 | -65.1857 | -82.06 | 31.6106 | 9.8657 | 8.9821 | 4.8338 | 0.59005 | -4.3997 | -9.6569 | -15.576 | -23.2391 | -49.1781 | -83.072 | -107.0412 | -126.0953 | 33.9355 | 11.9551 | 11.0683 | 6.8516 | 2.542 | -2.5178 | -7.9976 | -13.9969 | -21.7645 | -48.0667 | -82.4425 | -106.7663 | -126.1067
|  | MAIDENHEAD BSP | CT |  |  | 142.0262 | 142.0262 | 142.0262 | 141.8359 | 141.6414 | 141.443 | 141.2348 | 140.9113 | 140.8699 | 139.9984 | 133.1752 | 127.5566 | 121.8707 | 134.3062 | 134.2723 | 134.2048 | 133.9295 | 133.6507 | 133.3303 | 131.8445 | 129.9448 | 128.0034 | 121.7965 | 113.948 | 107.511 | 100.9101 | 136.645 | 136.6047 | 136.5247 | 136.2338 | 135.9394 | 135.6414 | 135.3587 | 134.9434 | 134.7927 | 133.4353 | 125.7674 | 119.4745 | 112.8693
|  | MAIDENHEAD BSP | LW |  |  | 142.0262 | 142.0262 | 142.0262 | 141.7939 | 141.551 | 141.294 | 141.0243 | 140.6081 | 140.5496 | 136.3165 | 127.7448 | 121.2499 | 117.5559 | 134.3049 | 134.2701 | 134.201 | 133.8583 | 133.5026 | 132.0591 | 130.0393 | 127.5091 | 125.2289 | 117.5677 | 107.6274 | 100.1549 | 95.8529 | 136.6433 | 136.6022 | 136.5203 | 136.1572 | 135.7806 | 135.427 | 135.0553 | 134.5177 | 134.3322 | 129.3028 | 119.6035 | 112.103 | 107.7505
|  | MAIDENHEAD BSP | ST |  |  | 59.0951 | 39.1433 | 38.2841 | 34.657 | 30.9144 | 26.4582 | 21.653 | 16.3441 | 9.4777 | -13.6946 | -43.9181 | -65.1857 | -82.06 | 31.6106 | 9.8657 | 8.9821 | 4.8338 | 0.59005 | -4.3997 | -9.6569 | -15.576 | -23.2391 | -49.1781 | -83.072 | -107.0412 | -126.0953 | 33.9355 | 11.9551 | 11.0683 | 6.8516 | 2.542 | -2.5178 | -7.9976 | -13.9969 | -21.7645 | -48.0667 | -82.4425 | -106.7663 | -126.1067
|  | MAIDENHEAD BSP | FS |  |  | 142.0262 | 37.1929 | 37.1929 | 37.1925 | 37.1922 | 37.1918 | 37.1913 | 37.1906 | 37.1882 | 37.178 | 37.1713 | 37.1425 | 37.1153 | 134.3575 | 64.6441 | 64.5762 | 64.3549 | 64.0931 | 63.8336 | 63.5616 | 63.2126 | 62.8456 | 61.5167 | 59.828 | 58.4248 | 57.4213 | 136.7058 | 39.6702 | 39.6539 | 39.6004 | 39.5371 | 39.4744 | 39.4086 | 39.3241 | 39.234 | 38.9066 | 38.4952 | 38.1357 | 37.8737
MANNINGTON GSP | MANNINGTON BSP | MANNINGTON BSP | MINIMUM HEADROOM | SU 07523 05221 | YES | 66.3518 | 65.9816 | 63.135 | 58.7522 | 53.7115 | 48.1366 | 42.4522 | 30.8948 | 25.1921 | 7.9331 | -23.1605 | -67.0697 | -76.6591 | 62.1899 | 61.7621 | 58.8153 | 53.7818 | 48.0784 | 41.7539 | 35.3052 | 25.0951 | 17.1437 | -4.4979 | -40.0918 | -90.5179 | -101.2284 | 50.5393 | 50.1152 | 47.1747 | 42.1826 | 36.5213 | 30.2445 | 23.8445 | 13.3401 | 5.1336 | -15.6227 | -50.9304 | -100.942 | -111.5812
|  | MANNINGTON BSP | CT |  |  | 66.5248 | 66.1572 | 64.1905 | 61.9849 | 59.4598 | 56.8294 | 53.4551 | 49.1442 | 44.4376 | 28.5945 | 5.6978 | -22.2927 | -39.5548 | 62.3582 | 61.9303 | 59.858 | 57.3142 | 54.4797 | 51.5226 | 47.6936 | 42.7833 | 37.3348 | 18.9684 | -6.8821 | -38.7876 | -58.5544 | 50.7079 | 50.2839 | 48.2182 | 45.6959 | 42.8811 | 39.9448 | 36.1447 | 31.2725 | 25.8712 | 7.6653 | -17.9973 | -49.6539 | -69.2615
|  | MANNINGTON BSP | LW |  |  | 66.3518 | 65.9816 | 63.135 | 58.7522 | 53.7115 | 48.1366 | 42.4522 | 35.4834 | 29.4553 | 7.9331 | -23.1605 | -67.0697 | -76.6591 | 62.1899 | 61.7621 | 58.8153 | 53.7818 | 48.0784 | 41.7539 | 35.3052 | 27.4043 | 20.4348 | -4.4979 | -40.0918 | -90.5179 | -101.2284 | 50.5393 | 50.1152 | 47.1747 | 42.1826 | 36.5213 | 30.2445 | 23.8445 | 16.0028 | 9.0932 | -15.6227 | -50.9304 | -100.942 | -111.5812
|  | MANNINGTON BSP | ST |  |  | 105.7162 | 105.7162 | 105.7162 | 105.6169 | 105.5153 | 105.411 | 105.3024 | 105.1325 | 105.074 | 104.8805 | 103.6412 | 99.2993 | 1.4511 | 96.8359 | 96.814 | 96.7861 | 96.6368 | 96.4783 | 96.3264 | 96.1626 | 95.9306 | 95.5097 | 90.2709 | 84.1934 | 79.2236 | 7.1892 | 100.3701 | 100.3442 | 100.3111 | 100.1525 | 99.9836 | 99.8228 | 99.6488 | 99.4053 | 99.2571 | 98.7717 | 97.0321 | 92.1728 | -1.9041
|  | MANNINGTON BSP | FS |  |  | 84.0659 | 66.9973 | 66.4777 | 64.4697 | 57.8985 | 50.9967 | 44.0876 | 30.8948 | 25.1921 | 15.815 | 2.0378 | -8.1671 | -13.3252 | 81.2152 | 62.8555 | 62.3245 | 59.221 | 52.5664 | 45.5233 | 38.4718 | 25.0951 | 17.1437 | 6.8474 | -8.1314 | -19.2439 | -24.9268 | 72.084 | 51.1969 | 50.6666 | 47.431 | 40.7817 | 33.7476 | 26.7051 | 13.3401 | 5.1336 | -5.1043 | -20.0067 | -31.0615 | -36.711
BOTLEY WOOD GSP | NETLEY COMMON BSP | NETLEY COMMON BSP | MINIMUM HEADROOM | SU 47559 12003 | YES | 103.0641 | 102.819 | 215.8644 | 214.0559 | 211.7073 | 209.0293 | 205.9358 | 202.057 | 195.6179 | 174.5695 | 150.6035 | 124.0187 | 108.6005 | 100.1105 | 99.8251 | 211.0215 | 208.9338 | 206.299 | 203.278 | 199.7704 | 195.3566 | 188.2419 | 164.8718 | 138.2515 | 108.0335 | 90.382 | 87.2688 | 86.9859 | 199.9761 | 197.9061 | 195.2895 | 192.2903 | 188.8091 | 184.4292 | 177.3576 | 154.1351 | 127.6836 | 97.6966 | 80.1872
|  | NETLEY COMMON BSP | CT |  |  | 170.6517 | 170.6404 | 284.3132 | 284.0803 | 282.9438 | 281.6181 | 279.5096 | 277.217 | 275.0579 | 267.8932 | 253.0873 | 232.0572 | 218.0984 | 147.5904 | 147.5249 | 259.3591 | 259.0625 | 258.7635 | 258.4605 | 257.7774 | 257.0503 | 256.6686 | 251.1875 | 234.3083 | 210.0789 | 194.0028 | 150.4874 | 149.4197 | 262.1488 | 260.6784 | 259.2328 | 257.7799 | 255.4941 | 253.0067 | 250.635 | 242.9166 | 227.0285 | 204.0871 | 188.1495
|  | NETLEY COMMON BSP | LW |  |  | 170.5585 | 170.5381 | 283.7977 | 277.5433 | 275.3531 | 272.549 | 269.7338 | 266.3683 | 263.8341 | 255.1029 | 238.5864 | 209.6028 | 197.2952 | 147.4967 | 147.4217 | 258.8422 | 257.9025 | 257.1227 | 256.1313 | 253.4132 | 249.6956 | 246.797 | 236.8364 | 217.7891 | 184.2943 | 170.1317 | 150.3839 | 149.3017 | 261.6054 | 253.2676 | 250.9153 | 247.9414 | 244.9582 | 241.4089 | 238.6845 | 229.3117 | 211.4743 | 178.5203 | 164.4791
|  | NETLEY COMMON BSP | ST |  |  | 103.0641 | 102.819 | 215.8644 | 214.0559 | 211.7073 | 209.0293 | 205.9358 | 202.057 | 195.6179 | 174.5695 | 150.6035 | 124.0187 | 108.6005 | 100.1105 | 99.8251 | 211.0215 | 208.9338 | 206.299 | 203.278 | 199.7704 | 195.3566 | 188.2419 | 164.8718 | 138.2515 | 108.0335 | 90.382 | 87.2688 | 86.9859 | 199.9761 | 197.9061 | 195.2895 | 192.2903 | 188.8091 | 184.4292 | 177.3576 | 154.1351 | 127.6836 | 97.6966 | 80.1872
|  | NETLEY COMMON BSP | FS |  |  | 169.73 | 169.7266 | 283.1122 | 283.0847 | 284.0639 | 284.0325 | 283.9535 | 283.8565 | 283.7595 | 282.819 | 279.9702 | 275.8678 | 272.0333 | 146.7199 | 146.6976 | 258.0714 | 258.0314 | 258.9961 | 258.9442 | 258.8452 | 258.7228 | 258.5952 | 258.1424 | 258.6362 | 258.0589 | 255.6918 | 150.3379 | 150.1894 | 263.2705 | 262.9995 | 263.6976 | 263.2666 | 262.7996 | 262.2094 | 261.5182 | 259.0644 | 255.9051 | 251.3906 | 247.2468
MELKSHAM GSP | NORRINGTON | NORRINGTON | MINIMUM HEADROOM | ST 88273 64983 | YES | 84.3877 | -74.5404 | -71.9063 | -81.0257 | -90.4223 | -100.2557 | -110.137 | -120.6889 | -130.8637 | -169.2094 | -231.8236 | -323.4469 | -338.6608 | 44.7978 | -114.2892 | -109.9706 | -121.6041 | -133.5162 | -145.977 | -158.4918 | -171.825 | -184.8057 | -232.1862 | -304.5411 | -411.7223 | -430.4958 | 54.4755 | -104.2453 | -99.9277 | -105.7645 | -111.8771 | -119.6631 | -129.0901 | -140.0145 | -151.0745 | -197.1971 | -268.1972 | -373.7652 | -392.687
|  | NORRINGTON | CT |  |  | 84.7216 | 83.7486 | 80.97 | 76.414 | 72.2157 | 68.0092 | 62.606 | 62.7952 | 55.0128 | 28.4799 | -11.3976 | -65.6472 | -92.2298 | 45.1504 | 44.0288 | 40.9763 | 35.1984 | 29.941 | 24.6765 | 17.8789 | 18.3677 | 8.4397 | -25.4294 | -73.9829 | -137.1659 | -167.318 | 54.7848 | 54.0059 | 51.5849 | 48.6243 | 45.8087 | 42.9835 | 39.4011 | 43.0817 | 35.7523 | 8.2794 | -39.0344 | -101.2911 | -130.7283
|  | NORRINGTON | LW |  |  | 84.3877 | -74.5404 | -71.9063 | -81.0257 | -90.4223 | -100.2557 | -110.137 | -120.6889 | -130.8637 | -169.2094 | -231.8236 | -323.4469 | -338.6608 | 44.7978 | -114.2892 | -109.9706 | -121.6041 | -133.5162 | -145.977 | -158.4918 | -171.825 | -184.8057 | -232.1862 | -304.5411 | -411.7223 | -430.4958 | 54.4755 | -104.2453 | -99.9277 | -105.7645 | -111.8771 | -119.6631 | -129.0901 | -140.0145 | -151.0745 | -197.1971 | -268.1972 | -373.7652 | -392.687
|  | NORRINGTON | ST |  |  | 242.6869 | 242.6801 | 242.2698 | 242.21 | 242.1492 | 241.7402 | 240.5134 | 239.0363 | 237.4717 | 232.291 | 222.4616 | 206.7382 | 197.6674 | 221.4613 | 221.4216 | 220.9841 | 220.8777 | 220.7644 | 220.5651 | 220.3516 | 220.0727 | 219.8908 | 219.3014 | 208.5001 | 190.1931 | 179.65 | 223.0207 | 222.3741 | 221.4372 | 220.4708 | 219.3864 | 218.1032 | 216.7503 | 215.1242 | 213.3876 | 207.6995 | 197.0383 | 179.9664 | 170.0346
|  | NORRINGTON | FS |  |  | 86.1488 | 83.8216 | 80.866 | 79.8171 | 79.2656 | 72.1141 | 67.4385 | 60.1175 | 56.5285 | 48.9097 | 29.5813 | 17.7743 | 11.2666 | 46.8025 | 43.1762 | 38.5936 | 37.2609 | 36.3862 | 26.7181 | 21.5639 | 13.6088 | 9.1676 | -0.030788 | -24.0178 | -39.4253 | -46.7726 | 55.4269 | 51.9181 | 46.7705 | 46.092 | 45.9625 | 36.6292 | 32.5784 | 26.0855 | 23.6089 | 21.9353 | 4.1939 | -8.0968 | -13.8199
NORTH HYDE GSP | NORTH HYDE 22kV | NORTH HYDE 22kV | MINIMUM HEADROOM | TQ 10367 79001 | YES | -35.6607 | -36.7389 | -38.5582 | -43.0522 | -47.3062 | -51.5677 | -56.7282 | -56.316 | -64.6455 | -92.8674 | -129.5118 | -181.4397 | -205.3414 | -78.0072 | -79.3879 | -81.3809 | -86.933 | -92.2346 | -97.5422 | -104.0002 | -103.1745 | -113.5275 | -148.7189 | -193.9604 | -254.3605 | -281.3866 | -65.8908 | -66.5742 | -68.1665 | -71.279 | -74.1652 | -77.061 | -80.5275 | -76.7726 | -84.0253 | -112.7342 | -156.1298 | -215.6514 | -242.0087
|  | NORTH HYDE 22kV | CT |  |  | 77.0107 | 77.0107 | 77.0107 | 77.0043 | 76.9978 | 76.9912 | 76.9844 | 76.9738 | 76.9724 | 76.9681 | 76.9469 | 76.2253 | 72.3433 | 71.5463 | 71.5373 | 71.5227 | 71.5006 | 71.4767 | 71.452 | 71.4089 | 71.3635 | 71.3264 | 70.9478 | 67.8219 | 63.4519 | 58.9723 | 74.5808 | 74.5736 | 74.5618 | 74.5428 | 74.5222 | 74.5011 | 74.4651 | 74.4264 | 74.3964 | 74.2991 | 71.3692 | 66.9373 | 62.4321
|  | NORTH HYDE 22kV | LW |  |  | 77.0107 | 77.0107 | 77.0107 | 77.0026 | 76.9942 | 76.9855 | 76.9764 | 76.9627 | 76.9608 | 76.9542 | 76.9445 | 76.0311 | 72.1536 | 71.5463 | 71.5373 | 71.5227 | 71.4989 | 71.473 | 71.4274 | 71.3822 | 71.3336 | 71.296 | 70.7554 | 67.6063 | 63.2267 | 58.7515 | 74.5808 | 74.5736 | 74.5618 | 74.5411 | 74.5186 | 74.4802 | 74.442 | 74.4002 | 74.3696 | 74.2701 | 71.1393 | 66.7113 | 62.2072
|  | NORTH HYDE 22kV | ST |  |  | -35.6607 | -36.7389 | -38.5582 | -43.0522 | -47.3062 | -51.5677 | -56.7282 | -56.316 | -64.6455 | -92.8674 | -129.5118 | -181.4397 | -205.3414 | -78.0072 | -79.3879 | -81.3809 | -86.933 | -92.2346 | -97.5422 | -104.0002 | -103.1745 | -113.5275 | -148.7189 | -193.9604 | -254.3605 | -281.3866 | -65.8908 | -66.5742 | -68.1665 | -71.279 | -74.1652 | -77.061 | -80.5275 | -76.7726 | -84.0253 | -112.7342 | -156.1298 | -215.6514 | -242.0087
|  | NORTH HYDE 22kV | FS |  |  | 77.0107 | 77.0107 | 77.0107 | 76.9828 | 76.9813 | 76.9798 | 76.9782 | 76.9757 | 76.9689 | 76.9472 | 76.9369 | 76.9044 | 76.8772 | 71.5636 | 71.5534 | 71.5508 | 71.5049 | 71.4988 | 71.4922 | 71.4858 | 71.4785 | 71.4622 | 71.4096 | 71.3163 | 71.0216 | 70.0844 | 74.5947 | 74.5865 | 74.5844 | 74.5222 | 74.517 | 74.5114 | 74.506 | 74.4996 | 74.4851 | 74.4386 | 74.3615 | 74.2409 | 73.8315
COWLEY GSP | OXFORD BSP | OXFORD BSP | MINIMUM HEADROOM | SP 50054 05983 | NO | 69.1223 | 68.3401 | 53.859 | 51.4104 | 48.8966 | 47.0991 | 45.2055 | 43.0848 | 41.2858 | 35.4035 | 26.4904 | 18.7256 | 13.3115 | 81.0085 | 80.9952 | 80.3387 | 79.2408 | 78.1067 | 77.2528 | 76.3409 | 74.1542 | 72.0982 | 65.3694 | 55.2323 | 46.0712 | 39.9228 | 68.8352 | 67.9257 | 53.2909 | 50.4695 | 47.5751 | 45.5172 | 43.3526 | 40.9213 | 38.8315 | 31.9916 | 21.6874 | 12.3847 | 6.14
|  | OXFORD BSP | CT |  |  | 69.3066 | 68.4968 | 54.4903 | 52.4161 | 50.3297 | 48.2583 | 47.5379 | 45.9136 | 44.3985 | 39.7255 | 30.7286 | 23.7622 | 16.3854 | 94.2717 | 93.9539 | 80.9239 | 80.0196 | 79.0999 | 78.2044 | 78.4259 | 77.1056 | 75.3708 | 70.0175 | 60.0324 | 52.1563 | 43.6051 | 69.004 | 68.0585 | 53.7825 | 51.3856 | 48.9772 | 46.5812 | 45.7533 | 43.8888 | 42.1252 | 36.6825 | 26.5676 | 18.5721 | 9.8882
|  | OXFORD BSP | LW |  |  | 69.1223 | 68.3401 | 53.859 | 51.4104 | 48.8966 | 47.0991 | 45.2055 | 43.0848 | 41.2858 | 35.4035 | 26.4904 | 18.7256 | 13.3115 | 94.0315 | 93.7106 | 80.3387 | 79.2408 | 78.1067 | 77.2528 | 76.3409 | 74.1542 | 72.0982 | 65.3694 | 55.2323 | 46.0712 | 39.9228 | 68.8352 | 67.9257 | 53.2909 | 50.4695 | 47.5751 | 45.5172 | 43.3526 | 40.9213 | 38.8315 | 31.9916 | 21.6874 | 12.3847 | 6.14
|  | OXFORD BSP | ST |  |  | 83.4607 | 83.4607 | 83.4607 | 83.4535 | 83.4463 | 83.4389 | 83.4312 | 83.4194 | 83.4154 | 83.4026 | 83.3923 | 83.3583 | 83.3476 | 81.0085 | 80.9952 | 80.9873 | 80.9705 | 80.9514 | 80.93 | 80.9088 | 80.8733 | 80.8449 | 80.7528 | 79.4507 | 76.8069 | 74.0231 | 81.0406 | 81.0298 | 81.0235 | 81.0086 | 80.9918 | 80.9732 | 80.9546 | 80.9238 | 80.9001 | 80.8235 | 80.2207 | 77.3257 | 74.5127
|  | OXFORD BSP | FS |  |  | 71.0717 | 70.6324 | 69.8988 | 69.4939 | 69.0314 | 68.5878 | 68.1352 | 57.0517 | 56.5053 | 54.6195 | 52.8166 | 50.1357 | 48.0043 | 95.0935 | 94.9252 | 94.2509 | 94.0528 | 93.8338 | 93.6217 | 93.4061 | 82.6166 | 82.3326 | 81.3762 | 81.1812 | 79.8132 | 78.754 | 71.0295 | 70.5154 | 69.7655 | 69.3035 | 68.7738 | 68.2662 | 67.7483 | 56.5837 | 55.9649 | 53.8226 | 51.7284 | 48.6851 | 46.3236
MANNINGTON GSP | POOLE PS (HAMWORTHY) | POOLE PS (HAMWORTHY) | MINIMUM HEADROOM | SZ 00203 90789 | YES | 77.0879 | 76.3602 | 74.5453 | 73.3977 | 61.6047 | 60.467 | 59.946 | 58.5644 | 57.2638 | 53.1892 | 47.6174 | 42.2579 | 37.0369 | 71.8648 | 71.8537 | 74.7309 | 74.6734 | 74.4859 | 74.2961 | 74.1038 | 73.315 | 73.0286 | 72.1675 | 56.4275 | 51.7116 | 49.2457 | 76.9764 | 76.1254 | 74.2199 | 72.9125 | 60.9366 | 59.6445 | 59.0472 | 57.4759 | 55.9697 | 51.2434 | 44.7731 | 38.4126 | 32.3938
|  | POOLE PS (HAMWORTHY) | CT |  |  | 89.7079 | 89.7012 | 89.2947 | 89.2608 | 89.1169 | 88.9725 | 88.8273 | 91.5874 | 91.4856 | 91.1778 | 84.37 | 80.8746 | 77.5019 | 80.3436 | 80.3369 | 79.9305 | 79.8965 | 79.7526 | 79.6082 | 79.463 | 82.8694 | 82.7676 | 82.4598 | 75.6813 | 71.7949 | 67.9638 | 87.2559 | 87.2492 | 86.8427 | 86.8088 | 86.6622 | 86.4901 | 86.3062 | 89.5679 | 89.461 | 86.9008 | 76.1441 | 72.2454 | 68.4
|  | POOLE PS (HAMWORTHY) | LW |  |  | 81.2291 | 81.218 | 83.4489 | 83.3913 | 83.2039 | 83.0141 | 82.8218 | 82.6201 | 82.4926 | 82.0914 | 66.6198 | 62.4027 | 60.1871 | 71.8648 | 71.8537 | 74.7309 | 74.6734 | 74.4859 | 74.2961 | 74.1038 | 73.9022 | 73.7746 | 73.3854 | 56.4275 | 51.7116 | 49.2457 | 78.777 | 78.7659 | 81.4294 | 81.3718 | 81.1844 | 80.9946 | 80.8022 | 80.5454 | 79.2289 | 74.8119 | 56.8433 | 52.1118 | 49.6381
|  | POOLE PS (HAMWORTHY) | ST |  |  | 77.0879 | 76.3602 | 74.5453 | 73.3977 | 61.6047 | 60.467 | 59.946 | 58.5644 | 57.2638 | 53.1892 | 47.6174 | 42.2579 | 37.0369 | 98.3609 | 98.0799 | 96.5934 | 96.0249 | 84.8946 | 84.3166 | 84.6239 | 83.9301 | 83.3742 | 81.4511 | 75.085 | 68.8161 | 62.8955 | 76.9764 | 76.1254 | 74.2199 | 72.9125 | 60.9366 | 59.6445 | 59.0472 | 57.4759 | 55.9697 | 51.2434 | 44.7731 | 38.4126 | 32.3938
|  | POOLE PS (HAMWORTHY) | FS |  |  | 89.7656 | 89.7634 | 89.6279 | 89.6168 | 88.2271 | 86.8374 | 85.4477 | 82.6793 | 82.3929 | 81.5318 | 82.896 | 81.8775 | 81.4894 | 80.4014 | 80.3991 | 80.2636 | 80.2525 | 78.8628 | 77.4731 | 76.0834 | 73.315 | 73.0286 | 72.1675 | 74.1781 | 73.1595 | 72.7714 | 87.3136 | 87.3114 | 87.1759 | 87.1648 | 85.7751 | 84.3854 | 82.9957 | 80.2273 | 79.9394 | 79.0151 | 80.8765 | 79.8174 | 78.9557
LOVEDEAN GSP | PORTSMOUTH BSP | PORTSMOUTH BSP | MINIMUM HEADROOM | SZ 63405 99685 | YES | 89.7368 | 89.7323 | 89.4613 | 89.4387 | 89.3025 | 89.1659 | 89.0287 | 91.7975 | 91.224 | 89.4987 | 83.3285 | 80.2731 | 77.4111 | 80.3725 | 80.368 | 80.097 | 80.0744 | 79.9382 | 79.8016 | 79.6644 | 83.0795 | 82.506 | 80.7807 | 74.8517 | 71.4764 | 68.227 | 87.2847 | 87.2803 | 87.0093 | 86.9867 | 86.8505 | 86.6993 | 86.5303 | 89.7779 | 89.2044 | 86.2433 | 75.321 | 71.9357 | 68.6743
|  | PORTSMOUTH BSP | CT |  |  | 117.5899 | 117.5815 | 117.1471 | 117.0035 | 116.8579 | 116.7104 | 116.5579 | 116.343 | 116.3033 | 116.1769 | 111.3549 | 104.1468 | 97.4254 | 105.3216 | 105.2946 | 104.8273 | 104.6456 | 104.4576 | 104.2713 | 104.0541 | 103.7674 | 103.6505 | 99.9701 | 90.6512 | 82.4929 | 74.8471 | 109.2567 | 109.2483 | 108.8139 | 108.6703 | 108.5248 | 108.3773 | 108.2247 | 108.0098 | 107.9701 | 107.8437 | 106.729 | 98.8761 | 91.1573
|  | PORTSMOUTH BSP | LW |  |  | 117.522 | 117.5063 | 116.7801 | 116.6796 | 116.5764 | 116.4698 | 116.3707 | 116.2513 | 116.2178 | 116.1122 | 111.5143 | 104.7263 | 98.1379 | 105.252 | 105.2167 | 104.4555 | 104.3149 | 104.1672 | 103.9981 | 103.8344 | 103.6431 | 103.5325 | 99.3457 | 90.7402 | 83.0018 | 75.4889 | 109.1889 | 109.1731 | 108.4469 | 108.3465 | 108.2432 | 108.1366 | 108.0375 | 107.9181 | 107.8846 | 107.7791 | 107.0808 | 99.3885 | 91.7813
|  | PORTSMOUTH BSP | ST |  |  | 89.7368 | 89.7323 | 89.4613 | 89.4387 | 89.3025 | 89.1659 | 89.0287 | 91.7975 | 91.224 | 89.4987 | 83.3285 | 80.2731 | 77.4111 | 80.3725 | 80.368 | 80.097 | 80.0744 | 79.9382 | 79.8016 | 79.6644 | 83.0795 | 82.506 | 80.7807 | 74.8517 | 71.4764 | 68.227 | 87.2847 | 87.2803 | 87.0093 | 86.9867 | 86.8505 | 86.6993 | 86.5303 | 89.7779 | 89.2044 | 86.2433 | 75.321 | 71.9357 | 68.6743
|  | PORTSMOUTH BSP | FS |  |  | 117.6529 | 114.6268 | 113.9686 | 113.9529 | 113.9372 | 113.9216 | 113.9059 | 113.8881 | 113.867 | 113.8009 | 113.7512 | 113.6454 | 113.3942 | 105.4348 | 100.9461 | 100.0389 | 100.013 | 99.9855 | 99.9532 | 99.9205 | 99.8809 | 99.8391 | 99.7017 | 97.902 | 95.6204 | 93.3306 | 109.3197 | 105.3427 | 104.007 | 103.9768 | 103.9444 | 103.9051 | 103.8654 | 103.8167 | 103.7663 | 103.5992 | 103.3507 | 103.0774 | 102.8039
BRAMLEY (FLEE) | PYESTOCK BSP | PYESTOCK BSP | MINIMUM HEADROOM | SU 82940 54553 | YES | 60.707 | 60.707 | 60.707 | 60.6932 | 60.6789 | 60.6643 | 60.6488 | 60.6245 | 60.6213 | 60.6105 | 60.555 | 60.4122 | 59.42 | 55.8287 | 55.8176 | 55.7943 | 55.7535 | 55.7132 | 55.6728 | 55.6434 | 55.4887 | 55.0812 | 53.6768 | 51.5715 | 49.8679 | 48.6977 | 57.2352 | 57.2352 | 57.2352 | 57.2201 | 57.179 | 57.1377 | 57.1079 | 57.0667 | 57.0436 | 56.5188 | 54.4127 | 52.7087 | 51.5381
|  | PYESTOCK BSP | CT |  |  | 60.707 | 60.707 | 60.707 | 60.6932 | 60.6789 | 60.6643 | 60.6488 | 60.6245 | 60.6213 | 60.6105 | 60.555 | 60.4941 | 59.8595 | 55.8287 | 55.8176 | 55.7943 | 55.7535 | 55.7132 | 55.6728 | 55.6434 | 55.5295 | 55.1821 | 54.0496 | 52.3842 | 50.8667 | 49.2481 | 57.2352 | 57.2352 | 57.2352 | 57.2201 | 57.179 | 57.1377 | 57.1079 | 57.0667 | 57.0436 | 56.8917 | 55.2258 | 53.7079 | 52.0886
|  | PYESTOCK BSP | LW |  |  | 60.707 | 60.707 | 60.707 | 60.7064 | 60.7052 | 60.7032 | 60.7006 | 60.6952 | 60.6943 | 60.6895 | 60.678 | 60.4122 | 59.42 | 55.8308 | 55.8209 | 55.8 | 55.7693 | 55.7381 | 55.7167 | 55.6947 | 55.4887 | 55.0812 | 53.6768 | 51.5715 | 49.8679 | 48.6977 | 57.2352 | 57.2352 | 57.2352 | 57.2346 | 57.2038 | 57.1818 | 57.1592 | 57.1309 | 57.1064 | 56.5188 | 54.4127 | 52.7087 | 51.5381
|  | PYESTOCK BSP | ST |  |  | 78.6222 | 78.6175 | 78.329 | 78.2763 | 78.2232 | 78.1694 | 78.1147 | 78.0429 | 78.017 | 77.9361 | 77.8455 | 74.1954 | 69.9982 | 67.5851 | 67.5386 | 67.228 | 67.1462 | 67.0574 | 66.9573 | 66.8549 | 66.7345 | 66.6559 | 65.8622 | 59.8882 | 54.7554 | 49.9681 | 69.6891 | 69.6843 | 69.3958 | 69.3432 | 69.29 | 69.2363 | 69.1815 | 69.1097 | 69.0838 | 69.003 | 68.9123 | 68.5573 | 64.5308
|  | PYESTOCK BSP | FS |  |  | 60.707 | 60.707 | 60.707 | 60.707 | 60.707 | 60.707 | 60.7069 | 60.7069 | 60.7067 | 60.7055 | 60.7046 | 60.7002 | 60.6958 | 55.8465 | 55.8457 | 55.845 | 55.841 | 55.8363 | 55.8317 | 55.8271 | 55.8212 | 55.8153 | 55.7931 | 55.7609 | 55.7283 | 55.7026 | 57.2352 | 57.2352 | 57.2352 | 57.2352 | 57.2352 | 57.2352 | 57.2351 | 57.2351 | 57.2349 | 57.2337 | 57.2273 | 57.1939 | 57.1675
BRAMLEY (FLEE) | READING BSP | READING BSP | MINIMUM HEADROOM | SU 74642 73856 | YES | 208.007 | 138.707 | 138.707 | 138.6694 | 138.631 | 138.5918 | 138.551 | 138.4877 | 138.466 | 138.3954 | 138.3371 | 138.1442 | 131.2093 | 204.9368 | 131.1309 | 131.121 | 131.0674 | 131.0107 | 130.9595 | 130.9058 | 130.829 | 130.7911 | 130.4847 | 122.4782 | 108.9562 | 97.6212 | 205.1352 | 135.8352 | 135.8352 | 135.7976 | 135.7592 | 135.72 | 135.6722 | 135.595 | 135.5566 | 135.4309 | 128.576 | 114.9011 | 103.5626
|  | READING BSP | CT |  |  | 243.4112 | 174.0984 | 173.5396 | 173.473 | 173.311 | 173.1196 | 172.8212 | 172.4992 | 172.2252 | 165.9495 | 154.4934 | 143.3822 | 132.7503 | 230.0419 | 156.1517 | 155.4304 | 154.7203 | 153.6175 | 151.7037 | 149.6924 | 147.4832 | 145.0812 | 137.1995 | 124.317 | 111.6267 | 99.3308 | 231.979 | 162.5886 | 161.8667 | 161.6219 | 161.146 | 157.9512 | 155.9512 | 153.7543 | 151.3663 | 143.5307 | 130.3797 | 117.4911 | 105.2725
|  | READING BSP | LW |  |  | 243.3136 | 173.9869 | 173.0491 | 172.9121 | 172.6571 | 172.3922 | 172.0867 | 171.6407 | 171.324 | 164.7685 | 152.7074 | 140.9293 | 131.2093 | 229.9617 | 156.0671 | 154.9871 | 154.3362 | 153.2133 | 152.2574 | 150.2171 | 147.5581 | 144.9163 | 136.0006 | 122.4782 | 108.9562 | 97.6212 | 231.8989 | 162.5041 | 161.4236 | 161.1086 | 160.6726 | 158.8697 | 156.4676 | 153.8231 | 151.1966 | 142.3327 | 128.576 | 114.9011 | 103.5626
|  | READING BSP | ST |  |  | 208.007 | 138.707 | 138.707 | 138.6694 | 138.631 | 138.5918 | 138.551 | 138.4877 | 138.466 | 138.3954 | 138.3371 | 138.1442 | 138.0827 | 204.9368 | 131.1309 | 131.121 | 131.0674 | 131.0107 | 130.9595 | 130.9058 | 130.829 | 130.7911 | 130.4847 | 129.1354 | 127.8609 | 126.5735 | 205.1352 | 135.8352 | 135.8352 | 135.7976 | 135.7592 | 135.72 | 135.6722 | 135.595 | 135.5566 | 135.4309 | 135.2775 | 134.0027 | 132.7149
|  | READING BSP | FS |  |  | 243.4945 | 174.1912 | 174.0065 | 173.9693 | 172.7637 | 171.5581 | 170.3523 | 167.9587 | 167.6862 | 166.8628 | 165.4839 | 164.4835 | 164.2088 | 230.2764 | 156.4385 | 156.2476 | 156.1751 | 154.9366 | 153.6997 | 152.4625 | 150.029 | 149.7192 | 148.7631 | 146.6861 | 144.5914 | 142.5452 | 232.1837 | 162.876 | 162.6851 | 162.6119 | 161.3733 | 160.1363 | 158.899 | 156.4654 | 156.1555 | 155.1989 | 153.6167 | 151.7586 | 148.889
BRAMLEY (FLEE) | READING TOWN BSP | READING TOWN BSP | MINIMUM HEADROOM | SU 71580 74111 | YES | 135.0729 | 135.061 | 134.3373 | 134.278 | 134.2186 | 134.1593 | 134.1 | 134.0407 | 134.0169 | 133.5162 | 129.5203 | 125.7142 | 122.0114 | 127.8432 | 127.7839 | 126.9709 | 126.8207 | 126.6637 | 126.0387 | 125.2658 | 124.4521 | 123.6395 | 120.93 | 116.3091 | 111.8519 | 107.507 | 130.2862 | 130.2268 | 129.4135 | 129.263 | 129.1109 | 128.3645 | 127.6101 | 126.816 | 126.0248 | 123.4119 | 118.9396 | 114.6372 | 110.4449
|  | READING TOWN BSP | CT |  |  | 135.1346 | 135.1274 | 134.6932 | 134.6576 | 134.622 | 134.5864 | 134.5508 | 134.5152 | 134.501 | 133.5162 | 129.5203 | 125.7142 | 122.0114 | 127.9045 | 127.8498 | 127.3258 | 127.199 | 127.0645 | 126.0387 | 125.2658 | 124.4521 | 123.6395 | 120.93 | 116.3091 | 111.8519 | 107.507 | 130.3476 | 130.2926 | 129.7684 | 129.6413 | 129.5125 | 128.3645 | 127.6101 | 126.816 | 126.0248 | 123.4119 | 118.9396 | 114.6372 | 110.4449
|  | READING TOWN BSP | LW |  |  | 135.0729 | 135.061 | 134.3373 | 134.278 | 134.2186 | 134.1593 | 134.1 | 134.0407 | 134.0169 | 133.7968 | 130.2019 | 126.5073 | 122.8041 | 127.8432 | 127.7839 | 126.9709 | 126.8207 | 126.6637 | 126.4883 | 125.7341 | 124.9027 | 124.0822 | 121.3532 | 117.1334 | 112.7876 | 108.4422 | 130.2862 | 130.2268 | 129.4135 | 129.263 | 129.1109 | 128.8077 | 128.0613 | 127.2434 | 126.4428 | 123.8011 | 119.7299 | 115.539 | 111.3462
|  | READING TOWN BSP | ST |  |  | 171.4655 | 171.4593 | 171.0901 | 170.9842 | 170.7794 | 170.5725 | 170.3623 | 170.1057 | 169.5654 | 167.7254 | 162.1738 | 154.0054 | 146.6034 | 156.3773 | 156.3136 | 155.8849 | 155.6899 | 155.3798 | 154.9413 | 154.4093 | 153.7645 | 152.6592 | 146.7101 | 136.4745 | 127.322 | 119.0588 | 160.1248 | 160.0608 | 159.6319 | 159.4367 | 159.1262 | 158.8375 | 158.5407 | 158.1957 | 157.5535 | 150.2827 | 140.0983 | 130.8963 | 122.4653
|  | READING TOWN BSP | FS |  |  | 135.1963 | 135.1939 | 135.0491 | 135.0373 | 135.0254 | 135.0136 | 135.0017 | 134.9898 | 134.9851 | 134.9708 | 134.9471 | 134.9329 | 134.9068 | 128.0406 | 128.0187 | 127.8667 | 127.8375 | 127.8059 | 127.7803 | 127.7546 | 127.7261 | 127.7092 | 127.6536 | 127.5647 | 127.4803 | 127.3826 | 130.4839 | 130.4619 | 130.3099 | 130.2807 | 130.249 | 130.2233 | 130.1976 | 130.1691 | 130.1521 | 130.0964 | 130.0072 | 129.9226 | 129.8247
MANNINGTON GSP | REDHILL BSP | REDHILL BSP | MINIMUM HEADROOM | SZ 08581 96162 | YES | 101.337 | 101.2063 | 100.9753 | 101.3444 | 101.2725 | 101.1323 | 100.7013 | 99.9854 | 99.2901 | 97.2347 | 64.4589 | 57.5775 | 52.7379 | 78.2048 | 78.0512 | 77.7797 | 78.2137 | 78.1293 | 77.9647 | 77.723 | 76.9549 | 76.1404 | 73.7337 | 35.0658 | 26.9475 | 21.238 | 82.1033 | 81.9511 | 81.6822 | 82.112 | 82.0284 | 81.8654 | 81.3375 | 80.5727 | 79.7659 | 77.3814 | 39.1529 | 31.1432 | 25.51
|  | REDHILL BSP | CT |  |  | 101.337 | 101.2063 | 100.9753 | 102.116 | 101.7738 | 101.4696 | 100.7549 | 99.9854 | 99.2901 | 97.2347 | 78.4635 | 72.3369 | 67.4319 | 78.2048 | 78.0512 | 77.7797 | 79.3981 | 79.0088 | 78.6643 | 77.8381 | 76.9549 | 76.1404 | 73.7337 | 51.7146 | 44.533 | 38.7584 | 82.1033 | 81.9511 | 81.6822 | 82.996 | 82.6097 | 82.2678 | 81.4487 | 80.5727 | 79.7659 | 77.3814 | 55.5696 | 48.4806 | 42.7823
|  | REDHILL BSP | LW |  |  | 102.8048 | 102.6791 | 102.4588 | 102.2234 | 101.9648 | 101.3386 | 100.7013 | 100.0518 | 99.3718 | 97.365 | 64.4589 | 57.5775 | 52.7379 | 80.1948 | 80.0471 | 79.7882 | 79.5116 | 79.2077 | 78.4719 | 77.723 | 76.9597 | 76.1608 | 73.8026 | 35.0658 | 26.9475 | 21.238 | 83.7859 | 83.6396 | 83.3832 | 83.1092 | 82.8081 | 82.0793 | 81.3375 | 80.5815 | 79.7901 | 77.4542 | 39.1529 | 31.1432 | 25.51
|  | REDHILL BSP | ST |  |  | 135.1654 | 135.1607 | 134.8712 | 134.8474 | 134.8237 | 134.8 | 134.7763 | 134.7525 | 134.743 | 134.7146 | 134.6671 | 134.3782 | 132.046 | 127.989 | 127.9514 | 127.6312 | 127.569 | 127.4995 | 127.4409 | 127.3815 | 127.3279 | 127.2873 | 127.144 | 124.7439 | 121.9145 | 119.1725 | 130.4323 | 130.3945 | 130.0742 | 130.0119 | 129.9422 | 129.8835 | 129.824 | 129.7703 | 129.7296 | 129.5958 | 127.1043 | 124.3672 | 121.7227
|  | REDHILL BSP | FS |  |  | 102.9075 | 101.4473 | 101.4073 | 101.3444 | 101.2725 | 101.1323 | 100.991 | 100.8124 | 102.0865 | 101.5438 | 100.3891 | 98.9994 | 97.5765 | 80.0503 | 78.3344 | 78.2874 | 78.2137 | 78.1293 | 77.9647 | 77.7988 | 77.5891 | 79.3521 | 78.7162 | 77.3601 | 75.7299 | 74.0602 | 83.9312 | 82.2316 | 82.185 | 82.112 | 82.0284 | 81.8654 | 81.701 | 81.4933 | 82.9511 | 82.3211 | 80.9779 | 79.3629 | 77.7089
NURSLING GSP | ROWNHAMS | ROWNHAMS | MINIMUM HEADROOM | SU 37168 16854 | YES | 45.0175 | -17.6104 | -19.9411 | -23.0882 | -26.0589 | -29.9138 | -36.8255 | -42.4504 | -46.4169 | -61.6687 | -84.6208 | -108.6434 | -117.9383 | 35.9149 | -31.9976 | -34.5467 | -38.4255 | -41.7141 | -46.3855 | -56.2554 | -63.4954 | -68.4656 | -88.0962 | -117.2568 | -147.1934 | -158.5531 | 7.5295 | -61.1967 | -63.744 | -67.6165 | -70.84 | -75.5045 | -85.661 | -92.9808 | -97.9424 | -117.6409 | -146.9173 | -176.8971 | -188.2391
|  | ROWNHAMS | CT |  |  | 56.403 | -2.9429 | -9.1849 | -10.9766 | -12.3951 | -14.4559 | -15.5566 | -19.268 | -22.4815 | -27.4559 | -44.5419 | -61.7048 | -75.8506 | 47.3152 | -16.4107 | -24.1682 | -26.3918 | -27.7921 | -30.2714 | -31.499 | -36.3153 | -40.3549 | -43.9212 | -64.6804 | -85.6062 | -103.4767 | 18.9297 | -45.3825 | -53.1271 | -55.347 | -56.6851 | -59.1608 | -60.6225 | -65.4917 | -69.5243 | -72.4789 | -93.2068 | -114.1005 | -132.0017
|  | ROWNHAMS | LW |  |  | 45.0175 | -17.6104 | -19.9411 | -23.0882 | -26.0589 | -29.9138 | -36.8255 | -42.4504 | -46.4169 | -61.6687 | -84.6208 | -108.6434 | -117.9383 | 35.9149 | -31.9976 | -34.5467 | -38.4255 | -41.7141 | -46.3855 | -56.2554 | -63.4954 | -68.4656 | -88.0962 | -117.2568 | -147.1934 | -158.5531 | 7.5295 | -61.1967 | -63.744 | -67.6165 | -70.84 | -75.5045 | -85.661 | -92.9808 | -97.9424 | -117.6409 | -146.9173 | -176.8971 | -188.2391
|  | ROWNHAMS | ST |  |  | 102.2207 | 101.3345 | 101.2183 | 102.5349 | 102.362 | 101.9063 | 101.4451 | 101.0033 | 100.5386 | 99.1694 | 81.9424 | 77.7474 | 74.6513 | 79.2432 | 78.2018 | 78.0653 | 79.8776 | 79.6744 | 79.139 | 78.597 | 78.0779 | 77.5318 | 75.9228 | 55.6795 | 50.7426 | 47.0901 | 83.1318 | 82.1003 | 81.9651 | 83.4717 | 83.2705 | 82.7401 | 82.2033 | 81.689 | 81.1481 | 79.5544 | 59.5029 | 54.6201 | 51.0164
|  | ROWNHAMS | FS |  |  | 57.4765 | 50.9812 | 50.63 | 50.2807 | 46.0321 | 35.8981 | 31.5134 | 23.1344 | 21.4569 | 16.963 | 7.894 | 1.69 | -0.11104 | 48.6352 | 37.7548 | 37.3925 | 36.952 | 32.5956 | 17.9347 | 13.416 | 4.8637 | 2.9608 | -1.9739 | -12.2823 | -19.1436 | -20.2692 | 20.2476 | 8.7809 | 8.4187 | 7.979 | 3.6235 | -11.2768 | -15.8069 | -24.3739 | -26.2959 | -31.5889 | -42.0023 | -48.8178 | -49.7389
MANNINGTON GSP | SALISBURY | SALISBURY | MINIMUM HEADROOM | SU 11049 31395 | YES | 78.9232 | 72.088 | 66.4718 | 65.0077 | 63.7376 | 61.8461 | 61.1571 | 57.7991 | 53.5798 | 39.6473 | 23.0652 | 7.1953 | -4.0435 | 66.5346 | 55.2566 | 48.2141 | 46.4089 | 45.1993 | 42.9378 | 42.2391 | 37.8791 | 32.945 | 16.5159 | -3.147 | -22.5814 | -36.4938 | 41.5879 | 29.7242 | 22.6938 | 20.8915 | 19.7438 | 17.4854 | 16.5517 | 12.1378 | 7.2098 | -9.198 | -28.8346 | -48.301 | -62.1906
|  | SALISBURY | CT |  |  | 163.1454 | 163.1337 | 162.4096 | 162.2167 | 162.1203 | 160.5561 | 158.2649 | 154.8667 | 150.7282 | 136.8664 | 117.4855 | 103.3712 | 88.612 | 148.0059 | 147.645 | 146.2166 | 143.7505 | 141.7539 | 139.5345 | 136.8813 | 132.8999 | 128.0324 | 111.7287 | 89.2376 | 72.7291 | 55.4024 | 155.5664 | 155.2158 | 153.808 | 151.4116 | 149.4456 | 147.2884 | 144.6765 | 140.8078 | 136.0813 | 120.2499 | 98.3603 | 82.3148 | 65.0818
|  | SALISBURY | LW |  |  | 163.176 | 163.1565 | 162.131 | 161.7553 | 157.9562 | 153.6095 | 149.1914 | 143.7035 | 138.3477 | 119.089 | 89.8614 | 69.6094 | 63.1454 | 148.1116 | 147.7422 | 146.1125 | 141.377 | 136.6048 | 131.5114 | 126.3369 | 119.9131 | 113.6168 | 90.976 | 56.7591 | 33.0172 | 25.4519 | 155.6409 | 155.2818 | 153.6311 | 149.0304 | 144.3937 | 139.4448 | 134.4165 | 128.1737 | 122.0593 | 100.0726 | 66.4363 | 42.7647 | 35.2217
|  | SALISBURY | ST |  |  | 78.9232 | 72.088 | 66.4718 | 65.0077 | 63.7376 | 61.8461 | 61.1571 | 57.7991 | 53.5798 | 39.6473 | 23.0652 | 7.1953 | -4.0435 | 66.5346 | 55.2566 | 48.2141 | 46.4089 | 45.1993 | 42.9378 | 42.2391 | 37.8791 | 32.945 | 16.5159 | -3.147 | -22.5814 | -36.4938 | 41.5879 | 29.7242 | 22.6938 | 20.8915 | 19.7438 | 17.4854 | 16.5517 | 12.1378 | 7.2098 | -9.198 | -28.8346 | -48.301 | -62.1906
|  | SALISBURY | FS |  |  | 163.247 | 163.2431 | 162.9439 | 162.9209 | 162.8977 | 162.8744 | 162.8118 | 162.7076 | 162.5821 | 158.2904 | 151.7729 | 146.3434 | 143.1695 | 148.9721 | 148.5625 | 148.1872 | 147.6672 | 147.071 | 146.186 | 145.299 | 144.1319 | 142.6199 | 136.7426 | 129.1163 | 122.749 | 119.0406 | 156.5074 | 156.1096 | 155.7493 | 155.2438 | 154.6643 | 153.8046 | 152.9427 | 151.8091 | 150.3406 | 144.6077 | 137.1576 | 130.9717 | 127.3667
MANNINGTON GSP | SHAFTESBURY BSP | SHAFTESBURY BSP | MINIMUM HEADROOM | ST 85442 23791 | YES | 113.0622 | 112.9376 | 112.6476 | 109.8628 | 107.018 | 103.3565 | 99.6666 | 95.089 | 91.0182 | 76.126 | 43.7791 | 19.8727 | 13.95 | 81.8692 | 81.7226 | 81.3869 | 78.1634 | 74.8732 | 70.6726 | 66.4454 | 61.2109 | 56.4758 | 39.1785 | 1.25 | -26.6248 | -33.4078 | 83.5603 | 83.4244 | 83.1112 | 80.1026 | 77.0306 | 73.0942 | 69.1303 | 64.2176 | 59.808 | 43.2926 | 5.5394 | -22.2576 | -29.0237
|  | SHAFTESBURY BSP | CT |  |  | 113.0745 | 112.9556 | 112.6786 | 111.2834 | 109.9973 | 108.6651 | 106.1436 | 103.099 | 99.8749 | 88.961 | 68.2658 | 52.7261 | 41.4445 | 81.8821 | 81.7417 | 81.4199 | 79.8086 | 78.3283 | 76.7947 | 73.952 | 70.4827 | 66.7336 | 54.0341 | 29.9949 | 11.9721 | -1.1357 | 83.5729 | 83.443 | 83.1432 | 81.6378 | 80.2526 | 78.8177 | 76.1323 | 72.8712 | 69.3793 | 57.5547 | 34.2007 | 16.2266 | 3.1547
|  | SHAFTESBURY BSP | LW |  |  | 113.0622 | 112.9376 | 112.6476 | 109.8628 | 107.018 | 103.3565 | 99.6666 | 95.089 | 91.0182 | 76.126 | 43.7791 | 19.8727 | 13.95 | 81.8692 | 81.7226 | 81.3869 | 78.1634 | 74.8732 | 70.6726 | 66.4454 | 61.2109 | 56.4758 | 39.1785 | 1.25 | -26.6248 | -33.4078 | 83.5603 | 83.4244 | 83.1112 | 80.1026 | 77.0306 | 73.0942 | 69.1303 | 64.2176 | 59.808 | 43.2926 | 5.5394 | -22.2576 | -29.0237
|  | SHAFTESBURY BSP | ST |  |  | 141.0062 | 140.9984 | 140.5161 | 140.2714 | 140.0495 | 139.6096 | 137.4513 | 134.0986 | 130.1639 | 116.8277 | 99.9425 | 86.8269 | 73.395 | 129.5986 | 129.3423 | 128.5468 | 126.4401 | 124.5359 | 122.2728 | 119.8025 | 115.9176 | 111.3063 | 95.675 | 75.9226 | 60.6787 | 44.9361 | 133.7106 | 133.4615 | 132.6752 | 130.6236 | 128.7433 | 126.5394 | 124.1006 | 120.3187 | 115.8382 | 100.6508 | 81.4529 | 66.6206 | 51.1491
|  | SHAFTESBURY BSP | FS |  |  | 113.6036 | 113.0015 | 112.9578 | 112.6821 | 112.3652 | 111.8461 | 111.2571 | 110.4946 | 109.5429 | 106.0977 | 101.1201 | 97.3452 | 95.0454 | 82.4473 | 81.7346 | 81.6839 | 81.3597 | 80.9867 | 80.3744 | 79.6947 | 78.813 | 77.7009 | 73.7282 | 67.8775 | 63.4503 | 60.7675 | 84.1241 | 83.4656 | 83.4183 | 83.1179 | 82.7724 | 82.2058 | 81.5705 | 80.7472 | 79.7137 | 75.9854 | 70.5625 | 66.455 | 63.9597
IVER 132KV | SLOUGH | SLOUGH | MINIMUM HEADROOM | SU 95574 81752 | YES | 103.4405 | 103.4318 | 67.3557 | 67.3318 | 65.9439 | 64.5559 | 63.1678 | 60.4107 | 60.0895 | 59.1178 | 57.5264 | 56.3431 | 52.7683 | 82.8948 | 81.8564 | 70.7782 | 70.6754 | 69.1962 | 67.6987 | 66.2033 | 63.3056 | 62.8164 | 58.3227 | 37.6169 | 22.1045 | 11.2428 | 84.5087 | 83.5492 | 67.3475 | 67.3009 | 65.8865 | 64.4669 | 63.0478 | 60.2501 | 59.8803 | 58.7265 | 41.8107 | 26.3425 | 15.5124
|  | SLOUGH | CT |  |  | 147.648 | 147.6224 | 146.9933 | 146.8261 | 146.5268 | 146.2775 | 145.9697 | 145.6722 | 145.4572 | 144.8095 | 142.6184 | 138.4183 | 132.9959 | 138.7014 | 138.6921 | 138.0977 | 137.9813 | 137.7307 | 137.5281 | 137.2736 | 137.0396 | 136.8994 | 136.4995 | 130.0115 | 123.3249 | 116.7993 | 141.8984 | 141.8742 | 141.2481 | 141.0851 | 140.7899 | 140.5445 | 140.2412 | 139.949 | 139.7404 | 139.1134 | 136.3944 | 132.4926 | 125.9465
|  | SLOUGH | LW |  |  | 147.5641 | 147.5307 | 146.5185 | 146.3338 | 145.9956 | 145.7057 | 145.3645 | 145.0496 | 144.8008 | 144.0303 | 140.6282 | 134.5397 | 130.1085 | 138.6205 | 138.6049 | 137.6307 | 137.521 | 137.2582 | 137.0423 | 136.7747 | 136.545 | 136.3841 | 133.9422 | 125.7327 | 118.4983 | 113.211 | 141.8148 | 141.7829 | 140.7739 | 140.5955 | 140.2636 | 139.9799 | 139.6449 | 139.3372 | 139.0958 | 138.2366 | 134.904 | 127.6484 | 122.3452
|  | SLOUGH | ST |  |  | 113.9303 | 113.053 | 112.8985 | 111.8142 | 110.7276 | 109.2591 | 107.5397 | 105.1176 | 102.3462 | 92.8852 | 75.2752 | 62.0203 | 52.7683 | 82.8948 | 81.8564 | 81.677 | 80.4123 | 79.1457 | 77.4532 | 75.4677 | 72.6676 | 69.4199 | 58.3227 | 37.6169 | 22.1045 | 11.2428 | 84.5087 | 83.5492 | 83.382 | 82.2057 | 81.0273 | 79.4446 | 77.5894 | 74.9746 | 71.9602 | 61.6648 | 41.8107 | 26.3425 | 15.5124
|  | SLOUGH | FS |  |  | 103.4405 | 103.4318 | 67.3557 | 67.3318 | 65.9439 | 64.5559 | 63.1678 | 60.4107 | 60.0895 | 59.1178 | 57.5264 | 56.3431 | 55.8071 | 94.461 | 94.4579 | 70.7782 | 70.6754 | 69.1962 | 67.6987 | 66.2033 | 63.3056 | 62.8164 | 61.2145 | 58.5943 | 56.4209 | 55.0678 | 97.6882 | 97.6799 | 67.3475 | 67.3009 | 65.8865 | 64.4669 | 63.0478 | 60.2501 | 59.8803 | 58.7265 | 56.7503 | 55.126 | 54.2262
NURSLING GSP | SOUTHAMPTON (2 X 60) | SOUTHAMPTON (2 X 60) | MINIMUM HEADROOM | SU 41425 11999 | YES | 93.6525 | 93.4085 | 93.7066 | 93.623 | 93.5433 | 93.2824 | 92.9026 | 89.0064 | 88.7041 | 87.6698 | 85.182 | 82.174 | 79.0699 | 71.0689 | 70.6871 | 71.1756 | 71.0514 | 70.9333 | 70.7222 | 70.1923 | 64.9357 | 64.4766 | 63.117 | 60.0438 | 56.3972 | 52.769 | 75.2001 | 74.9098 | 75.2719 | 75.1747 | 75.0821 | 74.9875 | 74.8895 | 69.2359 | 68.8351 | 67.652 | 65.0372 | 61.4228 | 57.7935
|  | SOUTHAMPTON (2 X 60) | CT |  |  | 93.7626 | 93.5388 | 95.0053 | 94.6557 | 94.3238 | 93.9954 | 93.6493 | 90.9469 | 90.6586 | 89.66 | 86.4707 | 83.1894 | 80.1072 | 71.194 | 70.8406 | 72.9569 | 72.4529 | 71.9778 | 71.5089 | 71.0127 | 67.3516 | 66.9065 | 65.5967 | 61.8129 | 57.9319 | 54.3529 | 75.3153 | 75.0479 | 77.4757 | 77.3569 | 77.1074 | 76.6908 | 76.2505 | 71.9653 | 71.5786 | 70.4401 | 67.0604 | 63.1783 | 59.6104
|  | SOUTHAMPTON (2 X 60) | LW |  |  | 93.6525 | 93.4085 | 94.4457 | 94.0359 | 93.6436 | 93.2824 | 92.9026 | 89.0064 | 88.7041 | 87.6698 | 85.182 | 82.174 | 79.0699 | 71.0689 | 70.6871 | 72.3565 | 71.7754 | 71.2231 | 70.7222 | 70.1923 | 64.9357 | 64.4766 | 63.117 | 60.0438 | 56.3972 | 52.769 | 75.2001 | 74.9098 | 76.9769 | 76.8234 | 76.3805 | 75.9316 | 75.4576 | 69.2359 | 68.8351 | 67.652 | 65.0372 | 61.4228 | 57.7935
|  | SOUTHAMPTON (2 X 60) | ST |  |  | 111.4028 | 111.381 | 110.9645 | 110.8389 | 110.6226 | 110.3495 | 110.1201 | 109.8548 | 109.1745 | 107.1769 | 104.7916 | 103.1504 | 100.3628 | 101.2419 | 101.2357 | 100.8312 | 100.7348 | 100.55 | 100.3147 | 100.1267 | 99.913 | 99.2948 | 97.5054 | 94.3057 | 89.1084 | 84.228 | 105.6512 | 105.6307 | 105.2153 | 105.0921 | 104.8784 | 104.6085 | 104.3826 | 104.1217 | 103.4465 | 101.4664 | 99.1071 | 96.8846 | 94.5884
|  | SOUTHAMPTON (2 X 60) | FS |  |  | 94.0302 | 93.9547 | 93.7066 | 93.623 | 93.5433 | 93.462 | 93.3777 | 93.2815 | 93.2061 | 92.9812 | 94.7459 | 94.0715 | 93.2491 | 71.572 | 71.4528 | 71.1756 | 71.0514 | 70.9333 | 70.8127 | 70.6873 | 70.5429 | 70.4258 | 70.0766 | 72.3275 | 71.2566 | 70.1929 | 75.62 | 75.5298 | 75.2719 | 75.1747 | 75.0821 | 74.9875 | 74.8895 | 74.7771 | 74.6876 | 74.421 | 77.4841 | 76.5608 | 75.6709
NURSLING GSP | SOUTHAMPTON (2 X 90) | SOUTHAMPTON (2 X 90) | MINIMUM HEADROOM | SU 41425 11999 | YES | 130.1933 | 130.0421 | 131.817 | 131.6174 | 131.4102 | 127.6582 | 123.2906 | 115.5119 | 114.61 | 111.9035 | 107.0581 | 104.3265 | 103.179 | 108.862 | 108.6231 | 111.1132 | 110.8126 | 110.4999 | 110.1983 | 109.8795 | 103.0355 | 102.1065 | 99.3147 | 94.2948 | 90.9921 | 89.0016 | 111.7619 | 111.5812 | 114.0559 | 114.0074 | 113.9581 | 113.9095 | 113.8056 | 109.7276 | 109.4703 | 108.3389 | 103.4171 | 100.5922 | 98.9727
|  | SOUTHAMPTON (2 X 90) | CT |  |  | 136.639 | 136.6211 | 135.5306 | 135.4412 | 135.0077 | 134.5743 | 134.1408 | 133.7073 | 133.3962 | 132.4631 | 128.5716 | 120.871 | 114.2172 | 124.2524 | 124.1879 | 123.0078 | 122.8427 | 122.3214 | 121.8041 | 121.1799 | 120.4251 | 119.6995 | 117.4444 | 109.0389 | 99.9578 | 92.5126 | 133.1629 | 133.1246 | 131.9949 | 131.8724 | 131.4004 | 130.9303 | 130.4558 | 129.9796 | 129.6239 | 126.8146 | 118.2675 | 109.3683 | 102.1088
|  | SOUTHAMPTON (2 X 90) | LW |  |  | 136.4841 | 136.4543 | 134.6368 | 134.4595 | 133.8797 | 133.2985 | 132.7163 | 132.1177 | 131.7301 | 130.5647 | 127.2487 | 118.9901 | 111.9949 | 124.0907 | 124.0106 | 122.0957 | 121.8351 | 121.1599 | 120.486 | 119.6153 | 118.6692 | 117.8564 | 115.3688 | 107.4592 | 98.0707 | 90.2413 | 133.005 | 132.9532 | 131.0931 | 130.8793 | 130.2577 | 129.636 | 129.0127 | 128.3714 | 127.9392 | 124.5988 | 116.7026 | 107.496 | 99.8481
|  | SOUTHAMPTON (2 X 90) | ST |  |  | 130.1933 | 130.0421 | 131.817 | 131.6174 | 131.4102 | 131.21 | 130.9991 | 128.4722 | 128.2822 | 127.7163 | 126.1419 | 124.2973 | 122.515 | 108.862 | 108.6231 | 111.1132 | 110.8126 | 110.4999 | 110.1983 | 109.8795 | 106.4445 | 106.1473 | 105.2626 | 103.1644 | 100.8563 | 98.687 | 111.7619 | 111.5812 | 114.0559 | 114.0074 | 113.9581 | 113.9095 | 113.8056 | 109.7276 | 109.4703 | 108.7043 | 106.8916 | 104.9139 | 102.7561
|  | SOUTHAMPTON (2 X 90) | FS |  |  | 136.7939 | 136.788 | 136.4245 | 136.3935 | 132.0259 | 127.6582 | 123.2906 | 115.5119 | 114.61 | 111.9035 | 107.0581 | 104.3265 | 103.179 | 124.4725 | 124.4423 | 124.0652 | 124.0171 | 119.6266 | 115.235 | 110.8436 | 103.0355 | 102.1065 | 99.3147 | 94.2948 | 90.9921 | 89.0016 | 133.3464 | 133.3298 | 132.9604 | 132.9219 | 128.5442 | 124.1661 | 119.7881 | 111.9965 | 111.0828 | 108.3389 | 103.4171 | 100.5922 | 98.9727
LALEHAM | STAINES | STAINES | MINIMUM HEADROOM | TQ 04585 72135 | YES | 165.2665 | 165.2545 | 164.5275 | 164.468 | 164.0526 | 163.6372 | 163.2218 | 129.1221 | 127.3287 | 121.9484 | 115.8126 | 113.2697 | 109.4372 | 154.7217 | 154.6653 | 153.8876 | 153.7781 | 153.2963 | 152.816 | 152.3354 | 118.1698 | 116.2825 | 110.1144 | 102.1256 | 95.8902 | 90.7327 | 161.8043 | 161.7729 | 161.0237 | 160.9423 | 160.4978 | 160.054 | 159.6101 | 125.4816 | 123.6576 | 118.1816 | 109.4134 | 103.2976 | 98.26
|  | STAINES | CT |  |  | 194.8137 | 194.8069 | 194.3956 | 194.3616 | 194.3273 | 194.2929 | 194.2581 | 194.2219 | 194.208 | 194.1652 | 193.6543 | 191.5745 | 184.4287 | 178.2598 | 178.253 | 177.8416 | 177.8076 | 177.1139 | 175.7816 | 174.1009 | 172.482 | 170.8415 | 165.2537 | 156.6233 | 147.6146 | 139.2079 | 191.2297 | 191.2229 | 190.8116 | 190.7776 | 190.7434 | 190.7089 | 190.6741 | 190.6379 | 190.624 | 190.5812 | 190.0703 | 184.0527 | 175.9458
|  | STAINES | LW |  |  | 194.7552 | 194.744 | 194.0584 | 193.9298 | 193.798 | 193.6618 | 193.5218 | 193.3363 | 193.2956 | 193.1635 | 192.9478 | 187.844 | 181.2358 | 178.2013 | 178.1901 | 177.5044 | 177.3759 | 176.105 | 174.186 | 172.2599 | 170.3409 | 168.5837 | 162.4501 | 153.3943 | 143.3537 | 135.5827 | 191.1712 | 191.16 | 190.4744 | 190.3458 | 190.214 | 190.0778 | 189.9378 | 189.7523 | 189.7116 | 189.5795 | 189.3638 | 179.9179 | 172.4233
|  | STAINES | ST |  |  | 165.2665 | 165.2545 | 164.5275 | 164.468 | 164.0526 | 163.6372 | 163.2218 | 129.1221 | 127.3287 | 121.9484 | 115.8126 | 113.2697 | 109.4372 | 154.7217 | 154.6653 | 153.8876 | 153.7781 | 153.2963 | 152.816 | 152.3354 | 118.1698 | 116.2825 | 110.1144 | 102.1256 | 95.8902 | 90.7327 | 161.8043 | 161.7729 | 161.0237 | 160.9423 | 160.4978 | 160.054 | 159.6101 | 125.4816 | 123.6576 | 118.1816 | 109.4134 | 103.2976 | 98.26
|  | STAINES | FS |  |  | 194.8721 | 194.8699 | 194.7328 | 194.7076 | 194.6827 | 194.6577 | 194.6326 | 194.5995 | 194.5343 | 194.3275 | 194.2124 | 193.905 | 193.6335 | 178.3182 | 178.316 | 178.1788 | 178.1536 | 178.1288 | 178.1038 | 178.0786 | 178.0456 | 177.9804 | 177.2208 | 174.7596 | 172.0754 | 169.5935 | 191.2881 | 191.2859 | 191.1488 | 191.1236 | 191.0987 | 191.0738 | 191.0486 | 191.0155 | 190.9503 | 190.7435 | 190.6284 | 190.321 | 190.0495
MINETY GSP | STRATTON (2 X 60) | STRATTON (2 X 60) | MINIMUM HEADROOM | SU 17028 88748 | NO | 57.3555 | 44.6873 | 43.321 | 75.3153 | 70.8518 | 66.3206 | 61.7415 | 56.0073 | 50.469 | 27.9925 | -31.5376 | -66.1413 | -72.1584 | 35.4135 | 22.6587 | 21.1534 | 53.4928 | 48.1816 | 42.7945 | 37.3456 | 30.3421 | 23.4689 | -3.6425 | -73.7563 | -114.3976 | -121.3783 | 37.0185 | 24.2815 | 22.8049 | 54.1286 | 48.9922 | 43.7817 | 38.5123 | 31.9163 | 25.3297 | -1.4223 | -71.0718 | -111.5946 | -118.5564
|  | STRATTON (2 X 60) | CT |  |  | 57.4227 | 44.7612 | 43.6518 | 77.6413 | 75.4618 | 73.2801 | 70.6936 | 67.1381 | 62.867 | 45.6735 | 12.5707 | -8.8059 | -24.1793 | 35.4774 | 22.7274 | 21.475 | 56.2019 | 53.6181 | 51.0328 | 47.9626 | 43.7363 | 38.6275 | 18.0481 | -21.5441 | -46.5348 | -64.5554 | 37.083 | 24.3513 | 23.1284 | 56.7586 | 54.2583 | 51.7562 | 48.7858 | 44.6979 | 39.7619 | 19.9552 | -19.016 | -43.9384 | -61.9071
|  | STRATTON (2 X 60) | LW |  |  | 57.3555 | 44.6873 | 43.321 | 75.3153 | 70.8518 | 66.3206 | 61.7415 | 56.0073 | 50.469 | 27.9925 | -31.5376 | -66.1413 | -72.1584 | 35.4135 | 22.6587 | 21.1534 | 53.4928 | 48.1816 | 42.7945 | 37.3456 | 30.3421 | 23.4689 | -3.6425 | -73.7563 | -114.3976 | -121.3783 | 37.0185 | 24.2815 | 22.8049 | 54.1286 | 48.9922 | 43.7817 | 38.5123 | 31.9163 | 25.3297 | -1.4223 | -71.0718 | -111.5946 | -118.5564
|  | STRATTON (2 X 60) | ST |  |  | 129.9829 | 129.9784 | 129.7042 | 165.9776 | 165.9406 | 165.9031 | 165.8648 | 165.8174 | 165.7997 | 165.7429 | 165.6713 | 165.5502 | 165.4718 | 110.429 | 110.4245 | 110.1502 | 147.6136 | 147.5766 | 147.2643 | 146.0296 | 144.8523 | 143.6458 | 139.5121 | 133.6605 | 127.3566 | 121.6833 | 126.3989 | 126.3944 | 126.1202 | 162.3936 | 162.3566 | 162.3191 | 162.2808 | 162.2334 | 162.2157 | 162.1589 | 162.0873 | 161.9662 | 159.7913
|  | STRATTON (2 X 60) | FS |  |  | 68.6186 | 67.7983 | 67.4621 | 103.2474 | 101.4829 | 99.5014 | 97.518 | 90.9166 | 89.3109 | 83.062 | 73.6238 | 67.1891 | 63.6996 | 46.9116 | 45.9266 | 45.5343 | 82.4092 | 80.5329 | 78.3962 | 76.2572 | 67.395 | 65.5291 | 58.2158 | 47.4588 | 39.9869 | 35.9342 | 48.4681 | 47.5171 | 47.1472 | 82.8528 | 80.9996 | 78.8949 | 76.788 | 67.8263 | 66.0141 | 58.9204 | 48.4246 | 41.1667 | 37.2301
MINETY GSP | STRATTON (2 X 90) | STRATTON (2 X 90) | MINIMUM HEADROOM | SU 17028 88748 | NO | 104.7725 | 81.495 | 80.8688 | 78.9597 | 76.9576 | 74.9632 | 72.5327 | 69.1584 | 64.7069 | 48.2659 | 16.2584 | -4.1713 | -18.3093 | 91.193 | 60.728 | 60.0284 | 57.7605 | 55.4016 | 53.0529 | 50.1819 | 46.1927 | 40.9584 | 21.4323 | -17.0493 | -40.8757 | -57.4702 | 95.4255 | 61.1461 | 60.4616 | 58.2677 | 55.9824 | 53.7068 | 50.9267 | 47.0643 | 41.9915 | 23.2806 | -14.5867 | -38.2994 | -54.8457
|  | STRATTON (2 X 90) | CT |  |  | 104.8791 | 104.7854 | 103.9746 | 103.7597 | 103.3505 | 102.9433 | 102.221 | 101.5004 | 100.817 | 98.6962 | 93.0353 | 87.0373 | 81.8488 | 91.302 | 91.1936 | 90.3547 | 90.1111 | 89.6712 | 89.2337 | 88.425 | 87.6183 | 86.8432 | 84.4347 | 78.1506 | 71.4191 | 65.4964 | 95.5344 | 95.4263 | 94.588 | 94.3449 | 93.9056 | 93.4688 | 92.6619 | 91.8569 | 91.0835 | 88.6809 | 82.4094 | 75.6927 | 69.7847
|  | STRATTON (2 X 90) | LW |  |  | 104.7725 | 104.6642 | 103.402 | 103.1358 | 102.6448 | 101.8565 | 101.0677 | 100.2807 | 99.5586 | 97.3212 | 92.0328 | 85.935 | 80.6005 | 91.193 | 91.0686 | 89.7754 | 89.4777 | 88.9533 | 88.0786 | 87.2035 | 86.3303 | 85.5166 | 82.9914 | 77.0799 | 70.2486 | 64.1796 | 95.4255 | 95.3014 | 94.0088 | 93.7117 | 93.188 | 92.3151 | 91.4417 | 90.5702 | 89.7584 | 87.2389 | 81.34 | 74.5235 | 68.4693
|  | STRATTON (2 X 90) | ST |  |  | 116.815 | 81.495 | 80.8688 | 78.9597 | 76.9576 | 74.9632 | 72.5327 | 69.1584 | 64.7069 | 48.2659 | 16.2584 | -4.1713 | -18.3093 | 96.2383 | 60.728 | 60.0284 | 57.7605 | 55.4016 | 53.0529 | 50.1819 | 46.1927 | 40.9584 | 21.4323 | -17.0493 | -40.8757 | -57.4702 | 96.6171 | 61.1461 | 60.4616 | 58.2677 | 55.9824 | 53.7068 | 50.9267 | 47.0643 | 41.9915 | 23.2806 | -14.5867 | -38.2994 | -54.8457
|  | STRATTON (2 X 90) | FS |  |  | 105.097 | 105.0791 | 104.8468 | 104.7941 | 102.4222 | 100.0293 | 97.6362 | 92.9164 | 92.3005 | 90.4355 | 86.8889 | 84.0346 | 82.1972 | 91.5422 | 91.5218 | 91.2869 | 91.228 | 88.8486 | 86.4444 | 84.04 | 79.3064 | 78.6661 | 76.7248 | 73.0067 | 69.9436 | 67.8902 | 95.7741 | 95.7538 | 95.519 | 95.4602 | 93.081 | 90.677 | 88.2728 | 83.5394 | 82.8997 | 80.9599 | 77.2452 | 74.1863 | 72.1373
MINETY GSP | SWINDON BSP | SWINDON BSP | MINIMUM HEADROOM | SU 12447 87062 | NO | 104.968 | 104.3972 | 101.162 | 99.6644 | 97.7755 | 95.5399 | 97.8493 | 95.4043 | 93.0261 | 85.054 | 64.1772 | 30.9178 | 22.9607 | 91.3985 | 79.491 | 76.1009 | 74.2297 | 72.0773 | 69.5105 | 71.9511 | 69.8759 | 67.5811 | 59.4661 | 31.7387 | -6.8148 | -15.8418 | 95.6308 | 80.624 | 77.2113 | 75.2855 | 73.0783 | 70.4544 | 72.9089 | 70.829 | 68.5535 | 61.0749 | 32.6581 | -5.5587 | -14.5177
|  | SWINDON BSP | CT |  |  | 135.9026 | 104.6635 | 102.5385 | 101.6508 | 100.5582 | 99.4056 | 97.8493 | 96.1012 | 94.2238 | 92.5835 | 80.5779 | 58.8092 | 48.9712 | 113.9642 | 79.7599 | 77.4818 | 76.3512 | 75.0509 | 73.7432 | 71.9511 | 69.8759 | 67.5811 | 67.8046 | 54.3103 | 28.8518 | 17.5212 | 114.9002 | 80.8932 | 78.5927 | 77.4267 | 76.0931 | 74.752 | 72.9089 | 70.829 | 68.5535 | 69.3264 | 55.9922 | 30.7898 | 19.6198
|  | SWINDON BSP | LW |  |  | 135.6588 | 104.3972 | 101.162 | 99.6644 | 97.7755 | 95.5399 | 98.0793 | 95.4043 | 93.0261 | 85.054 | 64.1772 | 30.9178 | 22.9607 | 113.7185 | 79.491 | 76.1009 | 74.2297 | 72.0773 | 69.5105 | 74.4874 | 71.4572 | 68.7063 | 59.4661 | 31.7387 | -6.8148 | -15.8418 | 114.655 | 80.624 | 77.2113 | 75.2855 | 73.0783 | 70.4544 | 75.8814 | 72.8895 | 70.1786 | 61.0749 | 32.6581 | -5.5587 | -14.5177
|  | SWINDON BSP | ST |  |  | 104.968 | 104.9047 | 104.3805 | 104.2345 | 103.8723 | 103.429 | 102.9851 | 102.4295 | 101.1198 | 97.1453 | 91.4667 | 86.9106 | 83.3597 | 91.3985 | 91.3252 | 90.7853 | 90.6196 | 90.2331 | 89.751 | 89.2681 | 88.6538 | 87.2814 | 83.1108 | 77.005 | 71.968 | 67.9474 | 95.6308 | 95.5577 | 95.018 | 94.8527 | 94.4667 | 93.9854 | 93.5033 | 92.8902 | 91.5191 | 87.3524 | 81.2553 | 76.2279 | 72.2168
|  | SWINDON BSP | FS |  |  | 135.2783 | 130.1439 | 129.5556 | 129.3619 | 126.2883 | 124.3704 | 108.5811 | 102.4935 | 101.4548 | 97.9617 | 92.1212 | 87.5829 | 84.7937 | 113.0474 | 104.9984 | 104.3982 | 104.1566 | 101.0277 | 99.4463 | 83.574 | 77.3798 | 76.2003 | 72.2917 | 65.873 | 60.7278 | 57.5174 | 114.237 | 106.3971 | 105.7951 | 105.5466 | 102.4096 | 100.5767 | 84.6922 | 78.4825 | 77.2825 | 73.2989 | 66.8271 | 61.71 | 58.5217
BRAMLEY (ANDO-THAT) | THATCHAM BSP | THATCHAM BSP | MINIMUM HEADROOM | SU 52824 66435 | YES | 177.1203 | 94.603 | 93.2459 | 66.6676 | 65.7374 | 64.7087 | 63.5382 | 62.1039 | 59.5528 | 56.0756 | 44.8796 | 21.4948 | 14.0979 | 157.0541 | 68.5731 | 67.1333 | 40.372 | 39.2441 | 38.0121 | 36.673 | 35.0178 | 32.144 | 30.6006 | 17.7643 | -11.3492 | -19.8193 | 156.1648 | 70.9057 | 69.4539 | 42.6659 | 41.5091 | 40.2445 | 38.869 | 37.1661 | 34.2867 | 33.2592 | 20.5789 | -8.9512 | -17.353
|  | THATCHAM BSP | CT |  |  | 213.3942 | 135.8414 | 123.2587 | 120.3558 | 117.3412 | 114.3388 | 111.8506 | 108.7976 | 105.6312 | 100.9175 | 84.1064 | 71.0319 | 57.7897 | 186.5855 | 105.1926 | 91.3946 | 87.8497 | 84.2013 | 80.5697 | 77.5829 | 73.9245 | 70.0268 | 66.1181 | 47.0432 | 32.2261 | 17.0029 | 188.3791 | 110.1444 | 96.6672 | 93.5768 | 90.3772 | 87.191 | 84.5571 | 81.3274 | 77.9474 | 75.3734 | 56.1103 | 41.1484 | 25.7721
|  | THATCHAM BSP | LW |  |  | 219.6945 | 142.1203 | 128.8414 | 124.9881 | 120.8678 | 117.533 | 114.1681 | 110.1513 | 106.0826 | 91.6856 | 61.596 | 46.7107 | 38.2759 | 195.5337 | 114.0879 | 99.5499 | 94.7827 | 89.7241 | 85.6475 | 81.536 | 76.7541 | 72.0449 | 55.3652 | 17.7643 | 0.72338 | -8.9237 | 199.193 | 120.9031 | 106.6817 | 102.5289 | 98.101 | 94.5231 | 90.9135 | 86.126 | 81.3636 | 64.4941 | 24.4359 | 7.2158 | -2.5321
|  | THATCHAM BSP | ST |  |  | 177.1203 | 94.603 | 93.2459 | 66.6676 | 65.7374 | 64.7087 | 63.5382 | 62.1039 | 59.5528 | 56.0756 | 44.8796 | 21.4948 | 14.0979 | 157.0541 | 68.5731 | 67.1333 | 40.372 | 39.2441 | 38.0121 | 36.673 | 35.0178 | 32.144 | 30.6006 | 17.8993 | -11.3492 | -19.8193 | 156.1648 | 70.9057 | 69.4539 | 42.6659 | 41.5091 | 40.2445 | 38.869 | 37.1661 | 34.2867 | 33.2592 | 20.5789 | -8.9512 | -17.353
|  | THATCHAM BSP | FS |  |  | 214.0511 | 136.688 | 136.3364 | 136.1326 | 134.1771 | 132.2128 | 130.2494 | 126.5062 | 125.2372 | 120.445 | 113.6503 | 108.215 | 104.9366 | 188.7617 | 108.0831 | 107.6595 | 106.9988 | 104.4808 | 101.9289 | 99.3821 | 94.8959 | 93.3522 | 87.7075 | 79.7476 | 73.3877 | 69.5215 | 190.269 | 112.6499 | 112.2398 | 111.6652 | 109.2532 | 106.812 | 104.3751 | 100.0289 | 98.6396 | 93.5985 | 86.4635 | 80.7582 | 77.3446
MINETY GSP | TOOTHILL BSP | TOOTHILL BSP | MINIMUM HEADROOM | SU 13191 83945 | NO | 86.3114 | 85.9096 | 84.5225 | 83.1404 | 81.6585 | 80.089 | 78.4182 | 76.4466 | 74.7263 | 67.2367 | 55.6893 | 44.6416 | 40.662 | 68.1095 | 67.6454 | 66.1533 | 64.5799 | 62.8917 | 61.1032 | 59.1983 | 56.9574 | 54.9711 | 45.4923 | 32.1486 | 19.3986 | 14.8072 | 73.7109 | 73.3049 | 71.895 | 70.4008 | 68.7979 | 67.0999 | 65.2918 | 63.1623 | 61.286 | 51.696 | 38.1236 | 25.1568 | 20.4876
|  | TOOTHILL BSP | CT |  |  | 86.4084 | 86.0306 | 84.976 | 84.0281 | 83.0201 | 81.9637 | 80.6983 | 79.2141 | 77.6998 | 72.6273 | 64.0911 | 59.4622 | 54.2794 | 68.2122 | 67.7752 | 66.6219 | 65.5325 | 64.3735 | 63.1586 | 61.7015 | 59.9935 | 58.2406 | 52.368 | 42.5717 | 38.9011 | 32.9173 | 73.8084 | 73.4266 | 72.3574 | 71.3265 | 70.23 | 69.0806 | 67.7028 | 66.0874 | 64.4331 | 58.6392 | 48.6824 | 44.8907 | 38.8048
|  | TOOTHILL BSP | LW |  |  | 86.3114 | 85.9096 | 84.5225 | 83.1404 | 81.6585 | 80.089 | 78.4182 | 76.4466 | 74.7263 | 67.2367 | 55.6893 | 44.6416 | 40.662 | 68.1095 | 67.6454 | 66.1533 | 64.5799 | 62.8917 | 61.1032 | 59.1983 | 56.9574 | 54.9711 | 45.4923 | 32.1486 | 19.3986 | 14.8072 | 73.7109 | 73.3049 | 71.895 | 70.4008 | 68.7979 | 67.0999 | 65.2918 | 63.1623 | 61.286 | 51.696 | 38.1236 | 25.1568 | 20.4876
|  | TOOTHILL BSP | ST |  |  | 172.7157 | 172.427 | 171.4406 | 169.6948 | 167.0229 | 165.034 | 162.8274 | 160.215 | 156.8043 | 151.7845 | 137.4496 | 120.4524 | 109.4912 | 144.6607 | 143.5576 | 141.61 | 138.8844 | 135.6502 | 133.2696 | 130.6194 | 127.4928 | 123.4475 | 119.1538 | 102.911 | 81.6126 | 69.0262 | 148.1581 | 147.2084 | 145.4419 | 143.0635 | 140.2274 | 138.1241 | 135.7879 | 133.0254 | 129.4294 | 127.3005 | 110.8991 | 88.0135 | 75.3036
|  | TOOTHILL BSP | FS |  |  | 87.0842 | 86.2999 | 86.0376 | 85.7983 | 85.5195 | 85.1911 | 84.8462 | 84.4342 | 84.0012 | 82.3993 | 80.3932 | 81.802 | 80.4555 | 68.7802 | 67.871 | 67.5902 | 67.3145 | 66.993 | 66.6141 | 66.216 | 65.7401 | 65.2388 | 63.3838 | 61.0615 | 64.3445 | 62.7893 | 74.2606 | 73.468 | 73.2045 | 72.9626 | 72.681 | 72.3492 | 71.978 | 71.5285 | 71.0555 | 69.3052 | 67.1137 | 70.3221 | 68.8533
IVER 132KV | UPTON BSP | UPTON BSP | MINIMUM HEADROOM | TQ 00838 79445 | YES | 50.8997 | 50.0451 | 49.4243 | 48.6689 | 47.8167 | 46.8805 | 45.8243 | 44.5196 | 43.2655 | 38.9847 | 32.0933 | 25.3124 | 21.3272 | 31.6365 | 30.6461 | 29.9727 | 29.1219 | 28.1593 | 27.0997 | 25.9018 | 24.4287 | 22.9881 | 18.068 | 10.1162 | 2.3586 | -2.2249 | 38.3079 | 37.4441 | 36.8198 | 36.0486 | 35.1317 | 34.1231 | 32.9838 | 31.5803 | 30.2168 | 25.5611 | 17.5101 | 9.6282 | 4.9685
|  | UPTON BSP | CT |  |  | 90.6444 | 90.6444 | 90.6444 | 90.6225 | 90.6002 | 91.5879 | 91.5639 | 91.5265 | 91.5217 | 91.4018 | 91.0841 | 90.7354 | 90.4537 | 86.8904 | 86.8904 | 86.8904 | 86.8685 | 86.8462 | 87.8339 | 87.8098 | 87.7724 | 87.7676 | 87.7517 | 84.4836 | 80.8218 | 77.1203 | 89.6793 | 89.6636 | 89.6313 | 89.5745 | 89.5173 | 90.4697 | 90.4175 | 90.3479 | 90.307 | 90.1789 | 89.9072 | 86.9319 | 83.2653
|  | UPTON BSP | LW |  |  | 90.6444 | 90.6444 | 91.6549 | 91.4104 | 91.1577 | 90.8932 | 90.6186 | 90.2004 | 90.1337 | 89.7795 | 89.2056 | 88.2739 | 87.263 | 86.8904 | 86.8904 | 87.9009 | 87.6564 | 87.4037 | 87.1392 | 86.8646 | 86.4464 | 86.3884 | 85.5779 | 81.4793 | 77.0729 | 73.6862 | 89.6757 | 89.6581 | 90.6322 | 90.3443 | 90.0479 | 89.7514 | 89.4443 | 88.9894 | 88.8925 | 88.5678 | 87.5671 | 83.1961 | 79.8411
|  | UPTON BSP | ST |  |  | 50.8997 | 50.0451 | 49.4243 | 48.6689 | 47.8167 | 46.8805 | 45.8243 | 44.5196 | 43.2655 | 38.9847 | 32.0933 | 25.3124 | 21.3272 | 31.6365 | 30.6461 | 29.9727 | 29.1219 | 28.1593 | 27.0997 | 25.9018 | 24.4287 | 22.9881 | 18.068 | 10.1162 | 2.3586 | -2.2249 | 38.3079 | 37.4441 | 36.8198 | 36.0486 | 35.1317 | 34.1231 | 32.9838 | 31.5803 | 30.2168 | 25.5611 | 17.5101 | 9.6282 | 4.9685
|  | UPTON BSP | FS |  |  | 90.6444 | 90.6444 | 90.6444 | 90.6243 | 90.6047 | 90.585 | 90.5649 | 90.5336 | 90.4465 | 90.1699 | 91.0483 | 90.6313 | 90.282 | 86.8904 | 86.8904 | 86.8904 | 86.8703 | 86.8507 | 86.831 | 86.8109 | 86.7796 | 86.6925 | 86.4159 | 87.2943 | 86.8773 | 86.528 | 89.701 | 89.7009 | 89.699 | 89.6718 | 89.6438 | 89.6164 | 89.5886 | 89.547 | 89.4499 | 89.1398 | 89.9595 | 89.4805 | 89.073
NURSLING GSP | VELMORE BSP | VELMORE BSP | MINIMUM HEADROOM | SU 42855 19215 | YES | 126.9544 | 126.9544 | 126.9544 | 126.8836 | 126.8117 | 126.7381 | 127.6725 | 127.5545 | 127.5143 | 127.385 | 127.1148 | 122.0518 | 123.5608 | 124.3904 | 124.3904 | 124.3904 | 124.3196 | 124.2477 | 124.1741 | 125.1085 | 124.9905 | 124.9503 | 124.4633 | 114.1774 | 103.4485 | 102.9687 | 126.0023 | 125.9807 | 125.9602 | 125.8614 | 125.7562 | 125.6615 | 126.5738 | 126.4321 | 126.3649 | 122.2522 | 112.4514 | 101.7194 | 101.2353
|  | VELMORE BSP | CT |  |  | 135.3073 | 135.3073 | 135.3073 | 135.0241 | 134.7358 | 134.4425 | 134.1357 | 133.6619 | 133.6017 | 133.4072 | 131.3113 | 122.0518 | 124.8539 | 127.5014 | 127.5014 | 127.5014 | 127.2182 | 126.9298 | 126.586 | 126.2177 | 125.6822 | 125.5554 | 124.4633 | 114.1774 | 103.4485 | 104.9841 | 131.9275 | 131.9275 | 131.9275 | 131.6444 | 131.356 | 131.0627 | 129.8978 | 128.1344 | 126.6783 | 122.2522 | 112.4514 | 101.7194 | 103.2522
|  | VELMORE BSP | LW |  |  | 145.4126 | 145.4126 | 145.4126 | 145.2892 | 145.1608 | 145.0254 | 144.8839 | 144.6665 | 144.636 | 144.5287 | 140.1098 | 129.9469 | 123.5608 | 137.6066 | 137.6066 | 137.6066 | 137.4833 | 137.3548 | 137.1605 | 136.9494 | 136.6616 | 136.5593 | 134.3801 | 122.4247 | 110.4983 | 102.9687 | 142.0328 | 142.0328 | 142.0328 | 141.9095 | 141.781 | 141.6457 | 140.2998 | 138.6121 | 137.0775 | 132.2569 | 120.6976 | 108.7674 | 101.2353
|  | VELMORE BSP | ST |  |  | 126.9544 | 126.9544 | 126.9544 | 126.8836 | 126.8117 | 126.7381 | 127.6725 | 127.5545 | 127.5143 | 127.385 | 127.1148 | 126.6246 | 126.3517 | 124.3904 | 124.3904 | 124.3904 | 124.3196 | 124.2477 | 124.1741 | 125.1085 | 124.9905 | 124.9503 | 124.821 | 124.0724 | 121.3161 | 118.7141 | 126.0023 | 125.9807 | 125.9602 | 125.8614 | 125.7562 | 125.6615 | 126.5738 | 126.4321 | 126.3649 | 126.1505 | 125.9036 | 125.4462 | 123.6231
|  | VELMORE BSP | FS |  |  | 135.3073 | 135.3073 | 134.0759 | 134.0705 | 134.0651 | 134.0598 | 134.0543 | 134.0457 | 134.0217 | 133.9447 | 133.9073 | 133.7867 | 133.6848 | 127.5014 | 127.5014 | 126.3024 | 126.297 | 126.2916 | 126.2862 | 126.2808 | 126.2722 | 126.2482 | 126.1574 | 126.0153 | 125.7867 | 125.5863 | 131.9275 | 131.9275 | 130.3892 | 130.363 | 130.3341 | 130.3052 | 130.2776 | 130.2433 | 130.194 | 130.0353 | 129.8553 | 128.3994 | 126.2383
MANNINGTON GSP | WAREHAM | WAREHAM | MINIMUM HEADROOM | SY 91548 88451 | YES | 25.3379 | 25.322 | 24.9084 | 44.2139 | 41.4365 | 38.5576 | 35.6791 | 30.1571 | 29.1084 | 25.41 | 7.8735 | -3.1124 | -6.9394 | 7.1513 | 7.1329 | 6.7156 | 25.2292 | 22.4027 | 19.4478 | 16.4935 | 10.873 | 9.6923 | 5.4536 | -14.5796 | -27.1282 | -31.3799 | 12.0323 | 12.0206 | 11.613 | 30.9644 | 28.1555 | 25.2279 | 22.3008 | 16.7155 | 15.5822 | 11.537 | -6.7553 | -19.2849 | -23.5314
|  | WAREHAM | CT |  |  | 31.8721 | 31.7892 | 30.4565 | 49.0814 | 48.076 | 47.0549 | 45.719 | 44.0083 | 42.1099 | 35.7244 | 22.8295 | 14.8248 | 7.7419 | 17.6206 | 17.5245 | 16.1642 | 33.8832 | 32.7372 | 31.5727 | 30.0287 | 28.0368 | 25.7875 | 18.207 | 3.2887 | -5.8614 | -14.1294 | 22.7487 | 22.6584 | 21.3101 | 39.8471 | 38.7623 | 37.6603 | 36.207 | 34.3377 | 32.2413 | 25.1816 | 11.0809 | 1.9434 | -6.3115
|  | WAREHAM | LW |  |  | 31.7017 | 31.6056 | 29.473 | 47.2344 | 45.2248 | 43.0238 | 40.794 | 38.1099 | 35.6557 | 26.8753 | 7.8735 | -3.1124 | -6.9394 | 17.4501 | 17.3409 | 15.1807 | 31.8728 | 29.5384 | 26.9745 | 24.3774 | 21.2411 | 18.3333 | 7.9019 | -14.5796 | -27.1282 | -31.3799 | 22.5783 | 22.4748 | 20.3266 | 37.9079 | 35.715 | 33.3093 | 30.8722 | 27.933 | 25.2229 | 15.511 | -6.7553 | -19.2849 | -23.5314
|  | WAREHAM | ST |  |  | 59.9973 | 59.9973 | 59.9973 | 79.4971 | 79.4966 | 79.4959 | 79.4949 | 79.4925 | 79.4914 | 79.4854 | 79.4775 | 78.4291 | 83.6908 | 52.5014 | 52.5014 | 52.5014 | 71.2511 | 71.2506 | 71.2499 | 71.2489 | 71.2346 | 71.1835 | 71.0241 | 67.9844 | 60.8838 | 65.2767 | 56.6175 | 56.6175 | 56.6175 | 76.1173 | 76.1168 | 76.1161 | 76.1151 | 76.1127 | 76.1116 | 73.0868 | 66.3672 | 59.5979 | 63.989
|  | WAREHAM | FS |  |  | 25.3379 | 25.322 | 24.9084 | 44.2139 | 41.4365 | 38.5576 | 35.6791 | 30.1571 | 29.1084 | 25.41 | 19.8615 | 15.8575 | 13.9209 | 7.1513 | 7.1329 | 6.7156 | 25.2292 | 22.4027 | 19.4478 | 16.4935 | 10.873 | 9.6923 | 5.4536 | -0.79326 | -5.3329 | -7.5671 | 12.0323 | 12.0206 | 11.613 | 30.9644 | 28.1555 | 25.2279 | 22.3008 | 16.7155 | 15.5822 | 11.537 | 5.5404 | 1.1927 | -0.93496
MELKSHAM GSP | WEST GRAFTON | WEST GRAFTON | MINIMUM HEADROOM | SU 24302 59215 | YES | 46.9905 | 46.9403 | 46.0748 | 45.3475 | 44.409 | 43.3769 | 42.1754 | 40.5895 | 37.9221 | 29.216 | 16.217 | 8.8213 | 2.4467 | 34.2459 | 34.188 | 33.3088 | 32.4521 | 31.3843 | 30.204 | 28.8197 | 26.977 | 23.9831 | 14.155 | -0.7614 | -9.1944 | -16.6506 | 37.871 | 37.8165 | 36.9432 | 36.1429 | 35.1315 | 34.0158 | 32.7111 | 30.9803 | 28.1287 | 18.7896 | 4.7088 | -3.6442 | -11.0885
|  | WEST GRAFTON | CT |  |  | 69.2622 | 69.0991 | 68.7744 | 68.1365 | 67.5542 | 66.9702 | 66.2739 | 65.3782 | 64.3323 | 60.8528 | 54.3174 | 50.8185 | 46.8204 | 56.9129 | 56.745 | 56.411 | 55.7553 | 55.1571 | 54.5571 | 53.8416 | 52.9214 | 51.8453 | 48.2653 | 41.5454 | 37.9505 | 33.8386 | 64.9055 | 64.7628 | 64.4779 | 63.9157 | 63.3681 | 62.7382 | 61.9452 | 60.9252 | 59.7261 | 55.6924 | 48.0256 | 43.9383 | 39.2426
|  | WEST GRAFTON | LW |  |  | 69.2589 | 69.0942 | 68.7668 | 67.7247 | 66.6829 | 65.5915 | 64.4992 | 63.1741 | 61.8697 | 57.2361 | 46.7548 | 42.3614 | 40.2089 | 56.9095 | 56.7401 | 56.4033 | 55.3315 | 54.2601 | 53.1378 | 52.0145 | 50.6523 | 49.3102 | 44.5424 | 33.7582 | 29.2416 | 27.0278 | 64.9021 | 64.7579 | 64.4703 | 63.5499 | 62.4025 | 61.1542 | 59.9047 | 58.3913 | 56.8808 | 51.4245 | 39.0861 | 33.9375 | 31.4093
|  | WEST GRAFTON | ST |  |  | 46.9905 | 46.9403 | 46.0748 | 45.3475 | 44.409 | 43.3769 | 42.1754 | 40.5895 | 37.9221 | 29.216 | 16.217 | 8.8213 | 2.4467 | 34.2459 | 34.188 | 33.3088 | 32.4521 | 31.3843 | 30.204 | 28.8197 | 26.977 | 23.9831 | 14.155 | -0.7614 | -9.1944 | -16.6506 | 37.871 | 37.8165 | 36.9432 | 36.1429 | 35.1315 | 34.0158 | 32.7111 | 30.9803 | 28.1287 | 18.7896 | 4.7088 | -3.6442 | -11.0885
|  | WEST GRAFTON | FS |  |  | 69.5718 | 69.4715 | 69.4474 | 69.3252 | 69.1866 | 68.9977 | 68.8108 | 68.5662 | 68.2476 | 67.0022 | 65.3359 | 63.9687 | 63.1097 | 57.2315 | 57.1282 | 57.1035 | 56.9778 | 56.8352 | 56.6408 | 56.4485 | 56.1968 | 55.8691 | 54.5878 | 52.873 | 51.4671 | 50.5841 | 65.1762 | 65.0885 | 65.0673 | 64.9601 | 64.8386 | 64.6731 | 64.5094 | 64.2952 | 64.0157 | 62.7641 | 60.852 | 59.2883 | 58.3078
NURSLING GSP | WINCHESTER | WINCHESTER | MINIMUM HEADROOM | SU 44965 26671 | YES | 108.7234 | 79.1601 | 77.7385 | 66.1162 | 54.3884 | 42.9878 | 31.4831 | 21.5603 | 11.9441 | -23.9661 | -70.3051 | -112.6951 | -120.6582 | 79.2866 | 45.5545 | 43.8787 | 30.2613 | 16.5198 | 3.2132 | -10.2058 | -21.7273 | -32.9481 | -74.8143 | -128.9258 | -178.3876 | -187.4392 | 84.0921 | 50.3508 | 48.6743 | 35.0526 | 21.3067 | 7.9958 | -5.4275 | -16.9524 | -28.1768 | -70.0561 | -124.1848 | -173.5114 | -182.5412
|  | WINCHESTER | CT |  |  | 108.7878 | 102.518 | 77.76 | 71.8647 | 66.64 | 61.3793 | 55.3612 | 49.4502 | 42.1593 | 16.9165 | -12.5532 | -38.936 | -58.4 | 79.3399 | 72.945 | 43.8787 | 36.9621 | 30.8348 | 24.6671 | 17.7043 | 10.8597 | 2.3632 | -27.0622 | -61.2127 | -91.7187 | -114.22 | 84.1454 | 77.7502 | 48.6743 | 41.7555 | 35.6262 | 29.4565 | 22.4915 | 15.6449 | 7.1457 | -22.2889 | -56.4497 | -86.9648 | -109.4728
|  | WINCHESTER | LW |  |  | 108.7234 | 79.1601 | 77.7385 | 66.1162 | 54.3884 | 42.9878 | 31.4831 | 21.5603 | 11.9441 | -23.9661 | -70.3051 | -112.6951 | -120.6582 | 79.2866 | 45.5545 | 43.8873 | 30.2613 | 16.5198 | 3.2132 | -10.2058 | -21.7273 | -32.9481 | -74.8143 | -128.9258 | -178.3876 | -187.4392 | 84.0921 | 50.3508 | 48.683 | 35.0526 | 21.3067 | 7.9958 | -5.4275 | -16.9524 | -28.1768 | -70.0561 | -124.1848 | -173.5114 | -182.5412
|  | WINCHESTER | ST |  |  | 128.7527 | 128.6526 | 128.4887 | 128.0151 | 127.5235 | 127.0486 | 126.4918 | 125.7272 | 124.7929 | 121.6499 | 115.8575 | 113.0439 | 109.6919 | 112.8059 | 112.7029 | 112.5343 | 112.0473 | 111.5419 | 111.0536 | 110.481 | 109.6949 | 108.7336 | 105.4996 | 99.5388 | 96.6467 | 93.1977 | 122.5846 | 122.4971 | 122.3533 | 121.937 | 121.5049 | 121.0685 | 120.4665 | 119.5985 | 118.5271 | 114.9177 | 108.0927 | 104.7977 | 100.8512
|  | WINCHESTER | FS |  |  | 118.5448 | 118.3566 | 118.288 | 116.8992 | 115.3005 | 102.0085 | 94.4935 | 91.5246 | 87.6286 | 73.9203 | 52.6388 | 36.2495 | 27.7446 | 88.5458 | 88.3351 | 88.2546 | 86.6251 | 84.7491 | 71.0734 | 63.1802 | 59.7116 | 55.1509 | 39.3659 | 14.4231 | -4.7333 | -14.6358 | 93.7051 | 93.4944 | 93.4139 | 91.7839 | 89.9073 | 76.2307 | 68.3367 | 64.867 | 60.3049 | 44.1601 | 19.2091 | 0.046641 | -9.8589
MANNINGTON GSP | WINFRITH HEATH | WINFRITH HEATH | MINIMUM HEADROOM | SY 80748 86538 | YES | 23.9873 | 23.9483 | 23.8955 | 23.8299 | 23.7456 | 23.6267 | 23.4848 | 23.3393 | 23.221 | 22.8816 | 22.4244 | 22.0396 | 21.7715 | 22.574 | 22.5242 | 22.4567 | 22.3737 | 22.2677 | 22.1183 | 21.9405 | 21.7619 | 21.612 | 21.1847 | 20.616 | 20.1545 | 19.814 | 22.0231 | 21.9749 | 21.9096 | 21.8292 | 21.7264 | 21.5816 | 21.4092 | 21.2355 | 21.0903 | 20.6761 | 20.124 | 19.6739 | 19.3442
|  | WINFRITH HEATH | CT |  |  | 23.9914 | 23.9546 | 23.9066 | 23.8477 | 23.7723 | 23.6803 | 23.5478 | 23.4206 | 23.3054 | 22.9814 | 22.5179 | 22.1728 | 21.8908 | 22.5792 | 22.5323 | 22.4709 | 22.3959 | 22.3 | 22.1831 | 22.0148 | 21.8544 | 21.7076 | 21.2958 | 20.7207 | 20.2989 | 19.9445 | 22.0281 | 21.9827 | 21.9234 | 21.8507 | 21.7579 | 21.6447 | 21.4818 | 21.3263 | 21.1842 | 20.7855 | 20.2271 | 19.8167 | 19.473
|  | WINFRITH HEATH | LW |  |  | 23.9873 | 23.9483 | 23.8955 | 23.8299 | 23.7456 | 23.6267 | 23.4848 | 23.3393 | 23.221 | 22.8816 | 22.4244 | 22.0396 | 21.7715 | 22.574 | 22.5242 | 22.4567 | 22.3737 | 22.2677 | 22.1183 | 21.9405 | 21.7619 | 21.612 | 21.1847 | 20.616 | 20.1545 | 19.814 | 22.0231 | 21.9749 | 21.9096 | 21.8292 | 21.7264 | 21.5816 | 21.4092 | 21.2355 | 21.0903 | 20.6761 | 20.124 | 19.6739 | 19.3442
|  | WINFRITH HEATH | ST |  |  | 43.0149 | 43.0145 | 43.0117 | 43.008 | 43.0031 | 42.998 | 42.9929 | 42.9868 | 42.9812 | 42.9628 | 42.9322 | 42.8891 | 42.7705 | 40.9216 | 40.9203 | 40.9182 | 40.9153 | 40.9114 | 40.9074 | 40.9033 | 40.8982 | 40.8937 | 40.8786 | 40.7192 | 40.3534 | 40.0034 | 42.6477 | 42.6477 | 42.6477 | 42.6475 | 42.6472 | 42.6468 | 42.6461 | 42.6446 | 42.6439 | 42.6401 | 42.6351 | 42.5901 | 42.29
|  | WINFRITH HEATH | FS |  |  | 24.0199 | 24.0084 | 24.0001 | 23.9843 | 23.9632 | 23.9371 | 23.9065 | 23.8772 | 23.8455 | 23.753 | 23.6388 | 23.5513 | 23.4714 | 22.6158 | 22.601 | 22.5904 | 22.5702 | 22.5433 | 22.5099 | 22.4708 | 22.4335 | 22.3933 | 22.2767 | 22.132 | 22.0261 | 21.9298 | 22.0635 | 22.0492 | 22.039 | 22.0194 | 21.9934 | 21.9611 | 21.9233 | 21.8871 | 21.8482 | 21.7352 | 21.595 | 21.4919 | 21.3981
COWLEY GSP | WITNEY BSP | WITNEY BSP | MINIMUM HEADROOM | SP 35605 08274 | NO | 104.2162 | 69.8484 | 68.1135 | 64.5218 | 60.6586 | 56.7248 | 52.7462 | 47.8101 | 43.5171 | 25.3794 | -1.031 | -24.7325 | -41.713 | 63.3119 | 22.7713 | 20.9068 | 16.7517 | 12.3154 | 7.8015 | 3.2362 | -2.4148 | -7.4261 | -25.0507 | -49.4648 | -74.2619 | -94.08 | 65.4826 | 25.993 | 24.1505 | 20.0914 | 15.7526 | 11.3375 | 6.8722 | 1.3429 | -3.5461 | -21.1389 | -45.5603 | -69.4947 | -89.3191
|  | WITNEY BSP | CT |  |  | 128.279 | 103.8972 | 68.5899 | 66.6881 | 64.738 | 62.8343 | 60.603 | 57.7158 | 54.3927 | 43.5051 | 28.816 | 15.3413 | 3.2251 | 93.1982 | 62.9204 | 21.3763 | 19.1527 | 16.9028 | 14.7084 | 12.1287 | 8.7827 | 4.8951 | -7.8491 | -24.7371 | -40.2713 | -54.3524 | 94.3846 | 65.1034 | 24.6212 | 22.4524 | 20.2536 | 18.1086 | 15.5883 | 12.3204 | 8.5289 | -3.9327 | -20.8254 | -36.3641 | -50.4494
|  | WITNEY BSP | LW |  |  | 104.2162 | 69.8484 | 68.1135 | 64.5218 | 60.6586 | 56.7248 | 52.7462 | 47.8101 | 43.5171 | 28.4319 | 7.4072 | -12.7917 | -19.0394 | 63.3119 | 22.7713 | 20.9068 | 16.7517 | 12.3154 | 7.8015 | 3.2362 | -2.4148 | -7.4261 | -25.0507 | -49.4648 | -72.7314 | -79.8788 | 65.4826 | 25.993 | 24.1505 | 20.0914 | 15.7526 | 11.3375 | 6.8722 | 1.3429 | -3.5461 | -21.1389 | -45.5603 | -68.8334 | -75.9828
|  | WITNEY BSP | ST |  |  | 121.5558 | 120.9427 | 86.0198 | 76.107 | 71.4924 | 67.0448 | 61.4242 | 55.9922 | 49.1694 | 25.3794 | -1.031 | -24.7325 | -41.713 | 94.0148 | 93.3286 | 54.256 | 43.5411 | 38.1321 | 32.9412 | 26.3783 | 20.0562 | 12.0726 | -15.7634 | -46.6452 | -74.2619 | -94.08 | 98.8305 | 98.1441 | 59.0623 | 48.3456 | 42.9349 | 37.7424 | 31.1774 | 24.8533 | 16.8672 | -10.9778 | -41.8694 | -69.4947 | -89.3191
|  | WITNEY BSP | FS |  |  | 129.4801 | 128.7584 | 128.4851 | 104.1347 | 101.589 | 92.8069 | 90.1074 | 85.1439 | 83.7129 | 78.5014 | 71.083 | 65.3827 | 62.4845 | 94.5761 | 93.7403 | 93.4556 | 63.2238 | 60.6005 | 48.7613 | 45.9566 | 40.8573 | 39.2531 | 33.3591 | 25.0393 | 18.6272 | 15.3128 | 95.7965 | 94.9388 | 94.6518 | 65.3955 | 62.7855 | 49.9126 | 47.1257 | 42.0496 | 40.4749 | 34.6971 | 26.5308 | 20.2399 | 16.9963
BRAMLEY (FLEE) | WOKINGHAM BSP | WOKINGHAM BSP | MINIMUM HEADROOM | SU 79589 67665 | YES | 92.0982 | 92.0851 | 69.6819 | 68.0129 | 66.1223 | 64.1996 | 61.9753 | 58.963 | 55.0435 | 42.2462 | 27.6992 | 14.4658 | 3.4675 | 87.9603 | 63.4802 | 22.6186 | 20.711 | 18.5741 | 16.401 | 13.8743 | 10.4518 | 6.0168 | -8.5052 | -25.0393 | -40.1017 | -52.8422 | 90.1372 | 65.65 | 25.8379 | 23.9709 | 21.876 | 19.7455 | 17.2703 | 13.9177 | 9.5704 | -4.6579 | -21.1259 | -36.1923 | -48.9364
|  | WOKINGHAM BSP | CT |  |  | 92.1664 | 92.1585 | 91.6786 | 91.599 | 91.4365 | 91.2732 | 91.0967 | 90.8514 | 90.7038 | 88.4724 | 84.2441 | 80.6351 | 77.4487 | 88.0285 | 87.9668 | 87.41 | 87.2468 | 85.717 | 84.1229 | 83.2753 | 82.3151 | 81.4272 | 78.5935 | 73.9339 | 69.92 | 66.3161 | 90.2054 | 90.1975 | 89.7176 | 89.638 | 89.4755 | 87.9806 | 87.1114 | 86.1269 | 85.2138 | 82.2992 | 77.5488 | 73.4833 | 69.8262
|  | WOKINGHAM BSP | LW |  |  | 92.0982 | 92.0851 | 91.2852 | 91.1782 | 90.9734 | 90.766 | 90.5563 | 90.2717 | 90.0962 | 87.6983 | 83.4563 | 79.6768 | 76.8419 | 87.9603 | 87.8933 | 87.0164 | 86.792 | 85.0361 | 84.0743 | 83.0839 | 81.9715 | 80.9971 | 77.8079 | 73.065 | 68.8486 | 65.6576 | 90.1372 | 90.1241 | 89.3242 | 89.2172 | 88.9321 | 87.9465 | 86.9315 | 85.7914 | 84.7898 | 81.5107 | 76.6695 | 72.3975 | 69.1612
|  | WOKINGHAM BSP | ST |  |  | 129.1032 | 104.3795 | 69.6819 | 68.0129 | 66.1223 | 64.1996 | 61.9753 | 58.963 | 55.0435 | 42.2462 | 27.6992 | 14.4658 | 3.4675 | 94.1461 | 63.4802 | 22.6186 | 20.711 | 18.5741 | 16.401 | 13.8743 | 10.4518 | 6.0168 | -8.5052 | -25.0393 | -40.1017 | -52.8422 | 95.3563 | 65.65 | 25.8379 | 23.9709 | 21.876 | 19.7455 | 17.2703 | 13.9177 | 9.5704 | -4.6579 | -21.1259 | -36.1923 | -48.9364
|  | WOKINGHAM BSP | FS |  |  | 123.8135 | 123.8109 | 123.6509 | 123.6378 | 122.5908 | 121.5438 | 120.4967 | 118.4157 | 118.1993 | 117.5495 | 116.3832 | 115.6203 | 115.3253 | 119.7375 | 119.7227 | 119.5579 | 119.5288 | 118.4635 | 117.4041 | 116.3446 | 114.2481 | 114.0187 | 113.3242 | 112.0984 | 111.2845 | 110.5878 | 121.8526 | 121.8499 | 121.6899 | 121.6768 | 120.6298 | 119.5828 | 118.5357 | 116.4547 | 116.2383 | 115.5886 | 114.4223 | 113.6594 | 113.3644
LOVEDEAN GSP | WYMERING BSP | WYMERING BSP | MINIMUM HEADROOM | SU 64948 05441 | YES | 164.7195 | 81.4642 | 49.5653 | 49.5389 | 49.4276 | 49.3162 | 49.2045 | 49.0922 | 48.6592 | 47.3586 | 45.6351 | 43.1253 | 40.8335 | 162.4232 | 79.1391 | 47.2048 | 47.1289 | 46.9595 | 46.8167 | 46.6716 | 46.2182 | 45.1858 | 41.9262 | 37.9636 | 35.0848 | 32.5259 | 162.7585 | 79.5032 | 47.6043 | 47.5779 | 47.4666 | 47.3552 | 47.2435 | 47.1312 | 46.6982 | 43.971 | 39.9304 | 36.9877 | 34.3616
|  | WYMERING BSP | CT |  |  | 186.8679 | 103.5396 | 102.8636 | 102.5808 | 102.1788 | 112.8641 | 111.775 | 127.6147 | 126.7444 | 123.9112 | 113.8734 | 104.5146 | 91.0718 | 164.9924 | 81.4619 | 80.3748 | 79.4988 | 78.4305 | 91.4011 | 89.0949 | 103.6268 | 101.3089 | 93.6939 | 80.0809 | 67.7985 | 48.5059 | 168.7935 | 85.3036 | 84.299 | 83.5421 | 82.6077 | 94.4525 | 92.3907 | 107.1852 | 105.1579 | 98.503 | 86.501 | 75.6924 | 56.3334
|  | WYMERING BSP | LW |  |  | 186.7683 | 103.4222 | 113.4563 | 112.7173 | 111.8218 | 110.5019 | 109.1414 | 124.3577 | 123.3251 | 118.6536 | 107.9355 | 90.6399 | 82.5318 | 164.8463 | 81.2725 | 93.7956 | 92.2374 | 90.4276 | 87.7588 | 85.012 | 98.7385 | 96.1493 | 87.1703 | 72.9201 | 48.1955 | 37.4379 | 168.6568 | 85.1287 | 96.4851 | 95.0914 | 93.4652 | 91.0673 | 88.5988 | 102.6244 | 100.3478 | 92.4263 | 79.9567 | 54.4541 | 45.032
|  | WYMERING BSP | ST |  |  | 164.7195 | 81.4642 | 49.5653 | 49.5389 | 49.4276 | 49.3162 | 49.2045 | 49.0922 | 48.6592 | 47.3586 | 45.6351 | 43.1253 | 40.8335 | 162.4232 | 79.1391 | 47.2048 | 47.1289 | 46.9595 | 46.8167 | 46.6716 | 46.2182 | 45.1858 | 41.9262 | 37.9636 | 35.0848 | 32.5259 | 162.7585 | 79.5032 | 47.6043 | 47.5779 | 47.4666 | 47.3552 | 47.2435 | 47.1312 | 46.6982 | 43.971 | 39.9304 | 36.9877 | 34.3616
|  | WYMERING BSP | FS |  |  | 187.1846 | 103.7601 | 103.5587 | 103.4774 | 102.206 | 100.9134 | 99.542 | 113.794 | 113.2996 | 111.6656 | 120.344 | 118.3371 | 116.982 | 166.0186 | 82.0845 | 81.815 | 81.5838 | 80.1242 | 78.5806 | 76.9538 | 90.9007 | 90.0028 | 86.9425 | 96.1109 | 91.8319 | 88.426 | 169.6772 | 85.8455 | 85.5896 | 85.3885 | 83.9667 | 82.4735 | 80.898 | 94.9062 | 94.0893 | 91.3154 | 99.7185 | 95.8957 | 92.9015
COWLEY GSP | YARNTON BSP | YARNTON BSP | MINIMUM HEADROOM | SP 35605 08274 | NO | 79.8433 | 74.4268 | 72.8316 | 70.4729 | 67.8754 | 65.0826 | 62.2174 | 58.8389 | 55.9686 | 47.2852 | 31.2498 | 5.8581 | 0.67127 | 56.2848 | 50.0349 | 48.2666 | 45.6403 | 42.7205 | 39.5783 | 36.3551 | 32.5705 | 29.2876 | 19.3621 | 1.4474 | -27.5577 | -33.433 | 56.2747 | 49.9154 | 48.1225 | 45.4629 | 42.5009 | 39.3128 | 36.0425 | 32.2046 | 28.8676 | 18.779 | 0.56211 | -28.9174 | -34.883
|  | YARNTON BSP | CT |  |  | 115.3804 | 79.1981 | 72.8461 | 71.1447 | 69.3037 | 67.4757 | 65.4503 | 63.0951 | 60.6474 | 53.7607 | 41.9878 | 26.3401 | 19.4384 | 97.2919 | 55.5319 | 48.2666 | 46.3221 | 44.2316 | 42.1567 | 39.8547 | 37.1808 | 34.373 | 26.4775 | 13.1364 | -4.7009 | -12.1865 | 97.9999 | 55.5076 | 48.1225 | 46.146 | 44.0228 | 41.9154 | 39.5771 | 36.8614 | 34.0063 | 25.9784 | 12.4315 | -5.6933 | -13.3111
|  | YARNTON BSP | LW |  |  | 79.8433 | 74.4268 | 72.8316 | 70.4729 | 67.8754 | 65.0826 | 62.2174 | 58.8389 | 55.9686 | 47.2852 | 31.2498 | 5.8581 | 0.67127 | 56.2848 | 50.0349 | 48.3041 | 45.6403 | 42.7205 | 39.5783 | 36.3551 | 32.5705 | 29.2876 | 19.3621 | 1.4474 | -27.5577 | -33.433 | 56.2747 | 49.9154 | 48.1668 | 45.4629 | 42.5009 | 39.3128 | 36.0425 | 32.2046 | 28.8676 | 18.779 | 0.56211 | -28.9174 | -34.883
|  | YARNTON BSP | ST |  |  | 148.8356 | 148.6413 | 148.2072 | 148.0082 | 147.681 | 158.2461 | 157.6851 | 173.8463 | 172.8744 | 169.8075 | 164.2612 | 153.3808 | 147.7804 | 122.9881 | 122.2334 | 121.5705 | 120.9566 | 120.1226 | 132.9317 | 131.6023 | 146.8065 | 144.7522 | 138.0577 | 127.997 | 112.2077 | 104.5829 | 131.1832 | 130.541 | 129.924 | 129.3934 | 128.6612 | 140.3529 | 139.1778 | 154.5741 | 152.7371 | 146.771 | 137.8946 | 121.5646 | 114.9603
|  | YARNTON BSP | FS |  |  | 116.3983 | 116.0548 | 115.7505 | 79.1422 | 77.5097 | 75.7627 | 74.0163 | 70.9471 | 70.0034 | 64.0939 | 60.5803 | 57.3745 | 56.0738 | 98.43 | 98.0338 | 97.7047 | 55.3341 | 53.6402 | 51.8143 | 49.9891 | 46.8256 | 45.7775 | 37.3102 | 33.5893 | 30.0394 | 28.9739 | 99.1579 | 98.7548 | 98.4224 | 55.4537 | 53.7518 | 51.9155 | 50.08 | 46.904 | 45.8423 | 37.3025 | 33.3961 | 29.801 | 28.7108
AXMINSTER | YEOVIL BSP | YEOVIL BSP | MINIMUM HEADROOM | ST 57586 16894 | YES | 94.6273 | 41.7021 | 41.2974 | 29.0069 | 16.5594 | 2.4839 | -11.7589 | -21.9612 | -31.5753 | -67.2988 | -115.2779 | -154.978 | -166.6088 | 66.9381 | 3.159 | 2.6805 | -12.0549 | -26.9592 | -43.2959 | -59.8138 | -71.5218 | -82.6555 | -123.9631 | -179.7055 | -225.5084 | -238.5575 | 67.9091 | 7.7507 | 7.2835 | -7.0793 | -21.6083 | -37.5493 | -53.6691 | -65.1136 | -75.9814 | -116.3118 | -170.6957 | -215.4307 | -228.2316
|  | YEOVIL BSP | CT |  |  | 94.6474 | 94.1049 | 41.3364 | 35.4837 | 30.3632 | 25.1886 | 17.1089 | 10.2116 | 2.6663 | -23.153 | -56.5766 | -84.7262 | -107.1228 | 66.9575 | 66.3047 | 2.7178 | -4.2444 | -10.3195 | -16.4553 | -25.8452 | -33.7263 | -42.4374 | -72.2676 | -110.503 | -142.5351 | -168.1555 | 67.9288 | 67.3233 | 7.3211 | 0.52791 | -5.4017 | -11.391 | -20.5812 | -28.302 | -36.8092 | -65.9375 | -103.3309 | -134.6836 | -159.7398
|  | YEOVIL BSP | LW |  |  | 94.6273 | 41.7021 | 41.2974 | 29.0069 | 16.5594 | 2.4839 | -11.7589 | -21.9612 | -31.5753 | -67.2988 | -115.2779 | -154.978 | -166.6088 | 66.9381 | 3.159 | 2.6805 | -12.0549 | -26.9592 | -43.2959 | -59.8138 | -71.5218 | -82.6555 | -123.9631 | -179.7055 | -225.5084 | -238.5575 | 67.9091 | 7.7507 | 7.2835 | -7.0793 | -21.6083 | -37.5493 | -53.6691 | -65.1136 | -75.9814 | -116.3118 | -170.6957 | -215.4307 | -228.2316
|  | YEOVIL BSP | ST |  |  | 113.5198 | 77.2374 | 71.633 | 70.6754 | 69.5161 | 68.1464 | 66.6352 | 64.8877 | 62.4907 | 55.4413 | 44.8967 | 31.0552 | 25.6839 | 98.2445 | 56.3686 | 49.9441 | 48.8426 | 47.5239 | 45.9624 | 44.2379 | 42.2412 | 39.5534 | 31.655 | 19.757 | 3.9478 | -1.7977 | 96.2787 | 53.6684 | 47.1363 | 46.0159 | 44.6762 | 43.0896 | 41.337 | 39.3077 | 36.5817 | 28.5718 | 16.4962 | 0.42866 | -5.4215
|  | YEOVIL BSP | FS |  |  | 95.475 | 95.0204 | 94.7212 | 93.329 | 91.5274 | 89.1063 | 86.5424 | 83.1589 | 78.6269 | 59.3954 | 35.2606 | 16.1748 | 5.6413 | 67.9537 | 67.406 | 67.0364 | 65.3637 | 63.2413 | 60.3288 | 57.2796 | 53.2523 | 47.8321 | 24.8209 | -4.1411 | -26.9581 | -39.2307 | 68.8528 | 68.345 | 68.012 | 66.4595 | 64.4745 | 61.7726 | 58.9313 | 55.1798 | 50.1401 | 28.7482 | 0.58146 | -21.6669 | -33.643

## LEP Reference
LEP | Local Authority | Grid Supply Point | Bulk Supply Point | Primary Substation
Buckinghamshire Thames Valley | Chiltern | AMERSHAM | LOUDWATER BSP | BOWERDEAN
Buckinghamshire Thames Valley | Chiltern | AMERSHAM | LOUDWATER BSP | FLACKWELL HEATH
Buckinghamshire Thames Valley | Chiltern | IVER 132KV | DENHAM | COKES LANE
Buckinghamshire Thames Valley | Chiltern | IVER 132KV | DENHAM | GERRARDS CROSS
Buckinghamshire Thames Valley | Chiltern | IVER 132KV | DENHAM | GRASSINGHAM ROAD
Buckinghamshire Thames Valley | Chiltern | IVER 132KV | UPTON BSP | BEACONSFIELD (END BB)
Buckinghamshire Thames Valley | South Bucks | AMERSHAM | LOUDWATER BSP | FLACKWELL HEATH
Buckinghamshire Thames Valley | South Bucks | AMERSHAM | LOUDWATER BSP | WELL END
Buckinghamshire Thames Valley | South Bucks | BRAMLEY (FLEE) | MAIDENHEAD BSP | BRAYWICK ROAD
Buckinghamshire Thames Valley | South Bucks | BRAMLEY (FLEE) | MAIDENHEAD BSP | CORDWALLIS
Buckinghamshire Thames Valley | South Bucks | IVER 132KV | CHALVEY BSP | CHALVEY
Buckinghamshire Thames Valley | South Bucks | IVER 132KV | CHALVEY BSP | PETERSFIELD AVENUE
Buckinghamshire Thames Valley | South Bucks | IVER 132KV | CIPPENHAM | CLARENCE ROAD
Buckinghamshire Thames Valley | South Bucks | IVER 132KV | DENHAM | DENHAM AVENUE
Buckinghamshire Thames Valley | South Bucks | IVER 132KV | DENHAM | GERRARDS CROSS
Buckinghamshire Thames Valley | South Bucks | IVER 132KV | DENHAM | GRASSINGHAM ROAD
Buckinghamshire Thames Valley | South Bucks | IVER 132KV | LONGFORD | POYLE
Buckinghamshire Thames Valley | South Bucks | IVER 132KV | SLOUGH | FARNHAM ROYAL
Buckinghamshire Thames Valley | South Bucks | IVER 132KV | SLOUGH | TAPLOW
Buckinghamshire Thames Valley | South Bucks | IVER 132KV | UPTON BSP | BEACONSFIELD (END BB)
Buckinghamshire Thames Valley | South Bucks | IVER 132KV | UPTON BSP | SUTTON LANE
Buckinghamshire Thames Valley | South Bucks | IVER 132KV | UPTON BSP | UPTON
Buckinghamshire Thames Valley | Wycombe | AMERSHAM | LOUDWATER BSP | BOWERDEAN
Buckinghamshire Thames Valley | Wycombe | AMERSHAM | LOUDWATER BSP | FLACKWELL HEATH
Buckinghamshire Thames Valley | Wycombe | AMERSHAM | LOUDWATER BSP | WELL END
Buckinghamshire Thames Valley | Wycombe | AMERSHAM | LOUDWATER BSP | WYCOMBE MARSH
Buckinghamshire Thames Valley | Wycombe | BRAMLEY (FLEE) | MAIDENHEAD BSP | TEMPLE FARM
Buckinghamshire Thames Valley | Wycombe | BRAMLEY (FLEE) | READING BSP | HENLEY
Buckinghamshire Thames Valley | Wycombe | COWLEY GSP | HIGH WYCOMBE BSP | CHISBRIDGE
Buckinghamshire Thames Valley | Wycombe | COWLEY GSP | HIGH WYCOMBE BSP | FRYERS LANE
Buckinghamshire Thames Valley | Wycombe | COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE
Buckinghamshire Thames Valley | Wycombe | COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE TOWN
Buckinghamshire Thames Valley | Wycombe | COWLEY GSP | HIGH WYCOMBE BSP | LITTLE MARLOW
Buckinghamshire Thames Valley | Wycombe | COWLEY GSP | HIGH WYCOMBE BSP | NUFFIELD
Buckinghamshire Thames Valley | Wycombe | COWLEY GSP | HIGH WYCOMBE BSP | STOKENCHURCH
Buckinghamshire Thames Valley | Wycombe | COWLEY GSP | HIGH WYCOMBE BSP | WATLINGTON
Buckinghamshire Thames Valley | Wycombe | IVER 132KV | SLOUGH | TAPLOW
Buckinghamshire Thames Valley | Wycombe | IVER 132KV | UPTON BSP | BEACONSFIELD (END BB)
Coast to Capital | Arun | BRAMLEY (FLEE) | FERNHURST | HASLINGBOURNE
Coast to Capital | Arun | LOVEDEAN GSP | CHICHESTER & HUNSTON | ARGYLE ROAD
Coast to Capital | Arun | LOVEDEAN GSP | CHICHESTER & HUNSTON | ASHLING ROAD
Coast to Capital | Arun | LOVEDEAN GSP | CHICHESTER & HUNSTON | BILSHAM
Coast to Capital | Arun | LOVEDEAN GSP | CHICHESTER & HUNSTON | CHICHESTER
Coast to Capital | Arun | LOVEDEAN GSP | CHICHESTER & HUNSTON | HUNSTON
Coast to Capital | Arun | LOVEDEAN GSP | CHICHESTER & HUNSTON | ROSE GREEN
Coast to Capital | Arun | LOVEDEAN GSP | CHICHESTER & HUNSTON | SOUTH BERSTED
Coast to Capital | Chichester | BRAMLEY (FLEE) | FERNHURST | FIVE OAKS
Coast to Capital | Chichester | BRAMLEY (FLEE) | FERNHURST | HASLEMERE
Coast to Capital | Chichester | BRAMLEY (FLEE) | FERNHURST | HASLINGBOURNE
Coast to Capital | Chichester | BRAMLEY (FLEE) | FERNHURST | LANGLEY COURT
Coast to Capital | Chichester | BRAMLEY (FLEE) | FERNHURST | MIDHURST
Coast to Capital | Chichester | BRAMLEY (FLEE) | FERNHURST | PETERSFIELD
Coast to Capital | Chichester | BRAMLEY (FLEE) | FERNHURST | PLAISTOW
Coast to Capital | Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON | ASHLING ROAD
Coast to Capital | Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON | BILLINGSHURST
Coast to Capital | Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON | BIRDHAM
Coast to Capital | Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON | CHICHESTER
Coast to Capital | Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON | HUNSTON
Coast to Capital | Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON | MARKET
Coast to Capital | Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON | ROSE GREEN
Coast to Capital | Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON | SELSEY
Coast to Capital | Chichester | LOVEDEAN GSP | HAVANT | EMSWORTH
Coast to Capital | Chichester | LOVEDEAN GSP | HAVANT | GABLE HEAD
Coast to Capital | Chichester | LOVEDEAN GSP | HAVANT | HORNDEAN
Coast to Capital | Chichester | LOVEDEAN GSP | HAVANT | LEIGH PARK
Coast to Capital | Chichester | LOVEDEAN GSP | HAVANT | MEYRICK ROAD
Coast to Capital | Horsham | BRAMLEY (FLEE) | FERNHURST | FIVE OAKS
Coast to Capital | Horsham | BRAMLEY (FLEE) | FERNHURST | HASLINGBOURNE
Coast to Capital | Horsham | BRAMLEY (FLEE) | FERNHURST | PLAISTOW
Coast to Capital | Horsham | LOVEDEAN GSP | CHICHESTER & HUNSTON | BILLINGSHURST
Coast to Capital | Mole Valley | BRAMLEY (FLEE) | FERNHURST | FIVE OAKS
Coventry and Warwickshire | Stratford-on-Avon | COWLEY GSP | WITNEY BSP | BLEDDINGTON
Coventry and Warwickshire | Stratford-on-Avon | COWLEY GSP | YARNTON BSP | CHIPPING NORTON
Dorset | Bournemouth | MANNINGTON GSP | BOURNEMOUTH | ALDERNEY
Dorset | Bournemouth | MANNINGTON GSP | BOURNEMOUTH | BOURNE VALLEY
Dorset | Bournemouth | MANNINGTON GSP | BOURNEMOUTH | CENTRAL
Dorset | Bournemouth | MANNINGTON GSP | BOURNEMOUTH | ELECTRIC HOUSE
Dorset | Bournemouth | MANNINGTON GSP | BOURNEMOUTH | WESTBOURNE
Dorset | Bournemouth | MANNINGTON GSP | CHRISTCHURCH BSP | BOSCOMBE EAST
Dorset | Bournemouth | MANNINGTON GSP | CHRISTCHURCH BSP | CHRISTCHURCH
Dorset | Bournemouth | MANNINGTON GSP | CHRISTCHURCH BSP | SOMERFORD
Dorset | Bournemouth | MANNINGTON GSP | CHRISTCHURCH BSP | SOUTHBOURNE
Dorset | Bournemouth | MANNINGTON GSP | MANNINGTON BSP | FERNDOWN
Dorset | Bournemouth | MANNINGTON GSP | REDHILL BSP | EAST HOWE
Dorset | Bournemouth | MANNINGTON GSP | REDHILL BSP | REDHILL
Dorset | Bournemouth | MANNINGTON GSP | REDHILL BSP | WINTON
Dorset | Christchurch | MANNINGTON GSP | ARNEWOOD | NEW MILTON
Dorset | Christchurch | MANNINGTON GSP | CHRISTCHURCH BSP | CHRISTCHURCH
Dorset | Christchurch | MANNINGTON GSP | CHRISTCHURCH BSP | SOMERFORD
Dorset | Christchurch | MANNINGTON GSP | CHRISTCHURCH BSP | SOUTHBOURNE
Dorset | Christchurch | MANNINGTON GSP | MANNINGTON BSP | FERNDOWN
Dorset | Christchurch | MANNINGTON GSP | MANNINGTON BSP | Mill Lane, Ringwood
Dorset | Christchurch | MANNINGTON GSP | REDHILL BSP | REDHILL
Dorset | Christchurch | MANNINGTON GSP | REDHILL BSP | WINTON
Dorset | East Dorset | MANNINGTON GSP | CHRISTCHURCH BSP | CHRISTCHURCH
Dorset | East Dorset | MANNINGTON GSP | LYTCHETT | BLANDFORD
Dorset | East Dorset | MANNINGTON GSP | LYTCHETT | CORFE MULLEN
Dorset | East Dorset | MANNINGTON GSP | LYTCHETT | CREEKMOOR
Dorset | East Dorset | MANNINGTON GSP | LYTCHETT | WINTERBORNE KINGSTON
Dorset | East Dorset | MANNINGTON GSP | MANNINGTON BSP | FERNDOWN
Dorset | East Dorset | MANNINGTON GSP | MANNINGTON BSP | FORDINGBRIDGE
Dorset | East Dorset | MANNINGTON GSP | MANNINGTON BSP | HINTON MARTELL
Dorset | East Dorset | MANNINGTON GSP | MANNINGTON BSP | MANNINGTON
Dorset | East Dorset | MANNINGTON GSP | MANNINGTON BSP | Mill Lane, Ringwood
Dorset | East Dorset | MANNINGTON GSP | MANNINGTON BSP | ROCKBOURNE
Dorset | East Dorset | MANNINGTON GSP | MANNINGTON BSP | VERWOOD
Dorset | East Dorset | MANNINGTON GSP | MANNINGTON BSP | WIMBORNE
Dorset | East Dorset | MANNINGTON GSP | MANNINGTON BSP | WIMBORNE ST GILES
Dorset | East Dorset | MANNINGTON GSP | POOLE PS (HAMWORTHY) | HAMWORTHY
Dorset | East Dorset | MANNINGTON GSP | REDHILL BSP | EAST HOWE
Dorset | East Dorset | MANNINGTON GSP | REDHILL BSP | REDHILL
Dorset | East Dorset | MANNINGTON GSP | SALISBURY | HOMINGTON
Dorset | East Dorset | MANNINGTON GSP | SHAFTESBURY BSP | GUSSAGE ST MICHAEL
Dorset | East Dorset | MANNINGTON GSP | SHAFTESBURY BSP | MINCHINGTON
Dorset | East Dorset | MANNINGTON GSP | SHAFTESBURY BSP | TARRANT RUSHTON
Dorset | North Dorset | AXMINSTER | YEOVIL BSP | HENSTRIDGE
Dorset | North Dorset | AXMINSTER | YEOVIL BSP | PULHAM
Dorset | North Dorset | AXMINSTER | YEOVIL BSP | SHERBORNE
Dorset | North Dorset | AXMINSTER | YEOVIL BSP | YETMINSTER
Dorset | North Dorset | CHICKERELL GSP | CHICKERELL BSP | PIDDLETRENTHIDE
Dorset | North Dorset | CHICKERELL GSP | CHICKERELL BSP | PUDDLETOWN
Dorset | North Dorset | MANNINGTON GSP | LYTCHETT | BLANDFORD
Dorset | North Dorset | MANNINGTON GSP | LYTCHETT | WINTERBORNE KINGSTON
Dorset | North Dorset | MANNINGTON GSP | MANNINGTON BSP | WIMBORNE
Dorset | North Dorset | MANNINGTON GSP | SHAFTESBURY BSP | BOURTON
Dorset | North Dorset | MANNINGTON GSP | SHAFTESBURY BSP | GILLINGHAM
Dorset | North Dorset | MANNINGTON GSP | SHAFTESBURY BSP | GUSSAGE ST MICHAEL
Dorset | North Dorset | MANNINGTON GSP | SHAFTESBURY BSP | MINCHINGTON
Dorset | North Dorset | MANNINGTON GSP | SHAFTESBURY BSP | SHAFTESBURY
Dorset | North Dorset | MANNINGTON GSP | SHAFTESBURY BSP | SHROTON
Dorset | North Dorset | MANNINGTON GSP | SHAFTESBURY BSP | TARRANT RUSHTON
Dorset | North Dorset | MANNINGTON GSP | SHAFTESBURY BSP | WEST STOUR
Dorset | North Dorset | MANNINGTON GSP | SHAFTESBURY BSP | WINCANTON
Dorset | Poole | MANNINGTON GSP | BOURNEMOUTH | ALDERNEY
Dorset | Poole | MANNINGTON GSP | BOURNEMOUTH | BOURNE VALLEY
Dorset | Poole | MANNINGTON GSP | BOURNEMOUTH | PARKSTONE NORTH
Dorset | Poole | MANNINGTON GSP | BOURNEMOUTH | PARKSTONE SOUTH
Dorset | Poole | MANNINGTON GSP | BOURNEMOUTH | WESTBOURNE
Dorset | Poole | MANNINGTON GSP | LYTCHETT | CORFE MULLEN
Dorset | Poole | MANNINGTON GSP | LYTCHETT | CREEKMOOR
Dorset | Poole | MANNINGTON GSP | LYTCHETT | HOLES BAY
Dorset | Poole | MANNINGTON GSP | MANNINGTON BSP | FERNDOWN
Dorset | Poole | MANNINGTON GSP | MANNINGTON BSP | WIMBORNE
Dorset | Poole | MANNINGTON GSP | POOLE PS (HAMWORTHY) | HAMWORTHY
Dorset | Poole | MANNINGTON GSP | REDHILL BSP | EAST HOWE
Dorset | Poole | MANNINGTON GSP | REDHILL BSP | WINTON
Dorset | Purbeck | CHICKERELL GSP | CHICKERELL BSP | PUDDLETOWN
Dorset | Purbeck | MANNINGTON GSP | BOURNEMOUTH | PARKSTONE SOUTH
Dorset | Purbeck | MANNINGTON GSP | LYTCHETT | BLANDFORD
Dorset | Purbeck | MANNINGTON GSP | LYTCHETT | CORFE MULLEN
Dorset | Purbeck | MANNINGTON GSP | LYTCHETT | CREEKMOOR
Dorset | Purbeck | MANNINGTON GSP | LYTCHETT | WINTERBORNE KINGSTON
Dorset | Purbeck | MANNINGTON GSP | POOLE PS (HAMWORTHY) | HAMWORTHY
Dorset | Purbeck | MANNINGTON GSP | WAREHAM | BOVINGTON
Dorset | Purbeck | MANNINGTON GSP | WAREHAM | BUSHEY
Dorset | Purbeck | MANNINGTON GSP | WAREHAM | SWANAGE
Dorset | Purbeck | MANNINGTON GSP | WAREHAM | WAREHAM TOWN
Dorset | West Dorset | AXMINSTER | YEOVIL BSP | CHILTON CANTELO
Dorset | West Dorset | AXMINSTER | YEOVIL BSP | HENSTRIDGE
Dorset | West Dorset | AXMINSTER | YEOVIL BSP | MILBORNE PORT
Dorset | West Dorset | AXMINSTER | YEOVIL BSP | PULHAM
Dorset | West Dorset | AXMINSTER | YEOVIL BSP | SHERBORNE
Dorset | West Dorset | AXMINSTER | YEOVIL BSP | WEST HENDFORD
Dorset | West Dorset | AXMINSTER | YEOVIL BSP | YEOVIL
Dorset | West Dorset | AXMINSTER | YEOVIL BSP | YETMINSTER
Dorset | West Dorset | CHICKERELL GSP | CHICKERELL BSP | CERNE ABBAS
Dorset | West Dorset | CHICKERELL GSP | CHICKERELL BSP | CHARMINSTER
Dorset | West Dorset | CHICKERELL GSP | CHICKERELL BSP | CHICKERELL
Dorset | West Dorset | CHICKERELL GSP | CHICKERELL BSP | DORCHESTER
Dorset | West Dorset | CHICKERELL GSP | CHICKERELL BSP | MAIDEN NEWTON
Dorset | West Dorset | CHICKERELL GSP | CHICKERELL BSP | PIDDLETRENTHIDE
Dorset | West Dorset | CHICKERELL GSP | CHICKERELL BSP | PUDDLETOWN
Dorset | West Dorset | CHICKERELL GSP | CHICKERELL BSP | REDLANDS
Dorset | West Dorset | CHICKERELL GSP | CHICKERELL BSP | WEYMOUTH
Dorset | West Dorset | MANNINGTON GSP | LYTCHETT | WINTERBORNE KINGSTON
Dorset | West Dorset | MANNINGTON GSP | WAREHAM | BOVINGTON
Dorset | Weymouth and Portland | CHICKERELL GSP | CHICKERELL BSP | CHICKERELL
Dorset | Weymouth and Portland | CHICKERELL GSP | CHICKERELL BSP | DORCHESTER
Dorset | Weymouth and Portland | CHICKERELL GSP | CHICKERELL BSP | PORTLAND
Dorset | Weymouth and Portland | CHICKERELL GSP | CHICKERELL BSP | REDLANDS
Dorset | Weymouth and Portland | CHICKERELL GSP | CHICKERELL BSP | WEYMOUTH
Enterprise M3 | Basingstoke and Deane | BRAMLEY (ANDO-THAT) | ANDOVER BSP | ANDOVER EAST
Enterprise M3 | Basingstoke and Deane | BRAMLEY (ANDO-THAT) | ANDOVER BSP | BARTON STACEY
Enterprise M3 | Basingstoke and Deane | BRAMLEY (ANDO-THAT) | ANDOVER BSP | HURSTBOURNE TARRANT
Enterprise M3 | Basingstoke and Deane | BRAMLEY (ANDO-THAT) | ANDOVER BSP | WHITCHURCH
Enterprise M3 | Basingstoke and Deane | BRAMLEY (ANDO-THAT) | THATCHAM BSP | BALL HILL
Enterprise M3 | Basingstoke and Deane | BRAMLEY (ANDO-THAT) | THATCHAM BSP | KINGSCLERE
Enterprise M3 | Basingstoke and Deane | BRAMLEY (ANDO-THAT) | THATCHAM BSP | ST JOHNS
Enterprise M3 | Basingstoke and Deane | BRAMLEY (ANDO-THAT) | THATCHAM BSP | TADLEY
Enterprise M3 | Basingstoke and Deane | BRAMLEY (ANDO-THAT) | THATCHAM BSP | THATCHAM
Enterprise M3 | Basingstoke and Deane | BRAMLEY (BASI) | BASINGSTOKE T1A & T2A | BASINGSTOKE
Enterprise M3 | Basingstoke and Deane | BRAMLEY (BASI) | BASINGSTOKE T1A & T2A | JAYS CLOSE
Enterprise M3 | Basingstoke and Deane | BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | BRAMLEY GREEN
Enterprise M3 | Basingstoke and Deane | BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | CHINEHAM
Enterprise M3 | Basingstoke and Deane | BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | DOWN GRANGE
Enterprise M3 | Basingstoke and Deane | BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | OVERTON
Enterprise M3 | Basingstoke and Deane | BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | BROOK STREET
Enterprise M3 | Basingstoke and Deane | BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | HOUNDMILLS
Enterprise M3 | Basingstoke and Deane | BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | OAKRIDGE
Enterprise M3 | Basingstoke and Deane | BRAMLEY (FLEE) | ALTON | ALRESFORD
Enterprise M3 | Basingstoke and Deane | BRAMLEY (FLEE) | ALTON | ALTON LOCAL
Enterprise M3 | Basingstoke and Deane | BRAMLEY (FLEE) | ALTON | HERRIARD
Enterprise M3 | Basingstoke and Deane | BRAMLEY (FLEE) | BURGHFIELD RESERVE | MORTIMER
Enterprise M3 | Basingstoke and Deane | BRAMLEY (FLEE) | BURGHFIELD RESERVE | PADWORTH
Enterprise M3 | Basingstoke and Deane | BRAMLEY (FLEE) | BURGHFIELD RESERVE | TRASH GREEN
Enterprise M3 | Basingstoke and Deane | BRAMLEY (FLEE) | COXMOOR WOOD BSP | HOOK
Enterprise M3 | Basingstoke and Deane | BRAMLEY (FLEE) | FERNHURST | PRESTON CANDOVER
Enterprise M3 | Elmbridge | LALEHAM | STAINES | SUNBURY CROSS
Enterprise M3 | Guildford | BRAMLEY (FLEE) | ALDERSHOT BSP | FARNHAM
Enterprise M3 | Guildford | BRAMLEY (FLEE) | ALDERSHOT BSP | GODALMING
Enterprise M3 | Guildford | BRAMLEY (FLEE) | ALDERSHOT BSP | MILFORD
Enterprise M3 | Guildford | BRAMLEY (FLEE) | ALDERSHOT BSP | NORMANDY
Enterprise M3 | Guildford | BRAMLEY (FLEE) | ALDERSHOT BSP | TONGHAM
Enterprise M3 | Guildford | BRAMLEY (FLEE) | CAMBERLEY RESERVE | FARNBOROUGH
Enterprise M3 | Guildford | BRAMLEY (FLEE) | CAMBERLEY RESERVE | FRIMLEY
Enterprise M3 | Hart | BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | ARBORFIELD
Enterprise M3 | Hart | BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | BRAMLEY GREEN
Enterprise M3 | Hart | BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | CHINEHAM
Enterprise M3 | Hart | BRAMLEY (FLEE) | ALDERSHOT BSP | ALDERSHOT
Enterprise M3 | Hart | BRAMLEY (FLEE) | ALDERSHOT BSP | FARNHAM
Enterprise M3 | Hart | BRAMLEY (FLEE) | ALTON | ALTON LOCAL
Enterprise M3 | Hart | BRAMLEY (FLEE) | BURGHFIELD RESERVE | MORTIMER
Enterprise M3 | Hart | BRAMLEY (FLEE) | BURGHFIELD RESERVE | TRASH GREEN
Enterprise M3 | Hart | BRAMLEY (FLEE) | CAMBERLEY MAIN | CAMBERLEY
Enterprise M3 | Hart | BRAMLEY (FLEE) | CAMBERLEY MAIN | CROWTHORNE
Enterprise M3 | Hart | BRAMLEY (FLEE) | CAMBERLEY MAIN | SANDHURST
Enterprise M3 | Hart | BRAMLEY (FLEE) | CAMBERLEY RESERVE | COVE
Enterprise M3 | Hart | BRAMLEY (FLEE) | COXMOOR WOOD BSP | COXMOOR WOOD
Enterprise M3 | Hart | BRAMLEY (FLEE) | COXMOOR WOOD BSP | HAWLEY
Enterprise M3 | Hart | BRAMLEY (FLEE) | COXMOOR WOOD BSP | HITCHES LANE
Enterprise M3 | Hart | BRAMLEY (FLEE) | COXMOOR WOOD BSP | HOOK
Enterprise M3 | Hart | BRAMLEY (FLEE) | COXMOOR WOOD BSP | WRECCLESHAM
Enterprise M3 | Hart | BRAMLEY (FLEE) | PYESTOCK BSP | Crookham
Enterprise M3 | Runnymede | BRAMLEY (FLEE) | BRACKNELL RESERVE | CHOBHAM
Enterprise M3 | Runnymede | BRAMLEY (FLEE) | BRACKNELL RESERVE | M V E E
Enterprise M3 | Runnymede | IVER 132KV | CHALVEY BSP | CHALVEY
Enterprise M3 | Runnymede | IVER 132KV | CIPPENHAM | CLARENCE ROAD
Enterprise M3 | Runnymede | LALEHAM | STAINES | CAUSEWAY
Enterprise M3 | Runnymede | LALEHAM | STAINES | EGHAM
Enterprise M3 | Runnymede | LALEHAM | STAINES | SIDNEY ROAD
Enterprise M3 | Rushmoor | BRAMLEY (FLEE) | ALDERSHOT BSP | ALDERSHOT
Enterprise M3 | Rushmoor | BRAMLEY (FLEE) | ALDERSHOT BSP | LABURNAM ROAD
Enterprise M3 | Rushmoor | BRAMLEY (FLEE) | ALDERSHOT BSP | TONGHAM
Enterprise M3 | Rushmoor | BRAMLEY (FLEE) | CAMBERLEY RESERVE | COVE
Enterprise M3 | Rushmoor | BRAMLEY (FLEE) | CAMBERLEY RESERVE | FARNBOROUGH
Enterprise M3 | Rushmoor | BRAMLEY (FLEE) | CAMBERLEY RESERVE | FRIMLEY
Enterprise M3 | Rushmoor | BRAMLEY (FLEE) | CAMBERLEY RESERVE | QUEENSMEAD
Enterprise M3 | Rushmoor | BRAMLEY (FLEE) | COXMOOR WOOD BSP | HAWLEY
Enterprise M3 | Rushmoor | BRAMLEY (FLEE) | COXMOOR WOOD BSP | HITCHES LANE
Enterprise M3 | Rushmoor | BRAMLEY (FLEE) | PYESTOCK BSP | Crookham
Enterprise M3 | Spelthorne | IVER 132KV | CHALVEY BSP | CHALVEY
Enterprise M3 | Spelthorne | IVER 132KV | LONGFORD | POYLE
Enterprise M3 | Spelthorne | LALEHAM | EAST BEDFONT A | CHURCH ROAD
Enterprise M3 | Spelthorne | LALEHAM | STAINES | CAUSEWAY
Enterprise M3 | Spelthorne | LALEHAM | STAINES | SIDNEY ROAD
Enterprise M3 | Spelthorne | LALEHAM | STAINES | STANWELL
Enterprise M3 | Spelthorne | LALEHAM | STAINES | SUNBURY CROSS
Enterprise M3 | Surrey Heath | BRAMLEY (FLEE) | BRACKNELL MAIN | ASCOT
Enterprise M3 | Surrey Heath | BRAMLEY (FLEE) | BRACKNELL RESERVE | BAGSHOT
Enterprise M3 | Surrey Heath | BRAMLEY (FLEE) | BRACKNELL RESERVE | CHOBHAM
Enterprise M3 | Surrey Heath | BRAMLEY (FLEE) | BRACKNELL RESERVE | M V E E
Enterprise M3 | Surrey Heath | BRAMLEY (FLEE) | BRACKNELL RESERVE | SUNNINGHILL
Enterprise M3 | Surrey Heath | BRAMLEY (FLEE) | CAMBERLEY MAIN | CAMBERLEY
Enterprise M3 | Surrey Heath | BRAMLEY (FLEE) | CAMBERLEY MAIN | KINGS RIDE
Enterprise M3 | Surrey Heath | BRAMLEY (FLEE) | CAMBERLEY RESERVE | FARNBOROUGH
Enterprise M3 | Surrey Heath | BRAMLEY (FLEE) | CAMBERLEY RESERVE | FRIMLEY
Enterprise M3 | Surrey Heath | BRAMLEY (FLEE) | CAMBERLEY RESERVE | QUEENSMEAD
Enterprise M3 | Surrey Heath | BRAMLEY (FLEE) | COXMOOR WOOD BSP | HAWLEY
Enterprise M3 | Waverley | BRAMLEY (FLEE) | ALDERSHOT BSP | ALDERSHOT
Enterprise M3 | Waverley | BRAMLEY (FLEE) | ALDERSHOT BSP | FARNHAM
Enterprise M3 | Waverley | BRAMLEY (FLEE) | ALDERSHOT BSP | GODALMING
Enterprise M3 | Waverley | BRAMLEY (FLEE) | ALDERSHOT BSP | HINDHEAD
Enterprise M3 | Waverley | BRAMLEY (FLEE) | ALDERSHOT BSP | LABURNAM ROAD
Enterprise M3 | Waverley | BRAMLEY (FLEE) | ALDERSHOT BSP | MILFORD
Enterprise M3 | Waverley | BRAMLEY (FLEE) | ALDERSHOT BSP | TONGHAM
Enterprise M3 | Waverley | BRAMLEY (FLEE) | ALTON | BORDON
Enterprise M3 | Waverley | BRAMLEY (FLEE) | BURGHFIELD RESERVE | SOUTHCOTE
Enterprise M3 | Waverley | BRAMLEY (FLEE) | COXMOOR WOOD BSP | WRECCLESHAM
Enterprise M3 | Waverley | BRAMLEY (FLEE) | FERNHURST | HASLEMERE
Enterprise M3 | Waverley | BRAMLEY (FLEE) | FERNHURST | PLAISTOW
Enterprise M3 | Woking | BRAMLEY (FLEE) | BRACKNELL RESERVE | CHOBHAM
Gloucestershire | Cheltenham | MINETY GSP | CIRENCESTER BSP | SHIPTON OLIFFE
Gloucestershire | Cotswold | BRAMLEY (FLEE) | BURGHFIELD MAIN | WHITELEY WOOD
Gloucestershire | Cotswold | COWLEY GSP | WITNEY BSP | BLEDDINGTON
Gloucestershire | Cotswold | COWLEY GSP | WITNEY BSP | RISSINGTON
Gloucestershire | Cotswold | MELKSHAM GSP | CHIPPENHAM | ALDERTON
Gloucestershire | Cotswold | MELKSHAM GSP | CHIPPENHAM | MALMESBURY
Gloucestershire | Cotswold | MELKSHAM GSP | CHIPPENHAM | TETBURY
Gloucestershire | Cotswold | MINETY GSP | CIRENCESTER BSP | CIRENCESTER TOWN
Gloucestershire | Cotswold | MINETY GSP | CIRENCESTER BSP | CRICKLADE
Gloucestershire | Cotswold | MINETY GSP | CIRENCESTER BSP | FAIRFORD
Gloucestershire | Cotswold | MINETY GSP | CIRENCESTER BSP | KEMBLE RAF
Gloucestershire | Cotswold | MINETY GSP | CIRENCESTER BSP | MINETY VILLAGE
Gloucestershire | Cotswold | MINETY GSP | CIRENCESTER BSP | NORTHLEACH
Gloucestershire | Cotswold | MINETY GSP | CIRENCESTER BSP | SHIPTON OLIFFE
Gloucestershire | Cotswold | MINETY GSP | STRATTON (2 X 60) | LECHLADE
Gloucestershire | Cotswold | MINETY GSP | STRATTON (2 X 60) | STANTON FITZWARREN
Gloucestershire | Tewkesbury | MINETY GSP | CIRENCESTER BSP | NORTHLEACH
Gloucestershire | Tewkesbury | MINETY GSP | CIRENCESTER BSP | SHIPTON OLIFFE
Heart of the South West | Mendip | AXMINSTER | YEOVIL BSP | SPARKFORD
Heart of the South West | Mendip | MANNINGTON GSP | SHAFTESBURY BSP | BOURTON
Heart of the South West | Mendip | MELKSHAM GSP | FROME BSP | BRUTON
Heart of the South West | Mendip | MELKSHAM GSP | FROME BSP | CROCKERTON
Heart of the South West | Mendip | MELKSHAM GSP | FROME BSP | FROME
Heart of the South West | Mendip | MELKSHAM GSP | FROME BSP | HAWKERIDGE
Heart of the South West | Mendip | MELKSHAM GSP | FROME BSP | HOLWELL
Heart of the South West | Mendip | MELKSHAM GSP | FROME BSP | WESTBURY
Heart of the South West | Mendip | MELKSHAM GSP | NORRINGTON | BRADFORD-ON-AVON
Heart of the South West | Mendip | MELKSHAM GSP | NORRINGTON | TROWBRIDGE TOWN
Heart of the South West | South Somerset | AXMINSTER | YEOVIL BSP | CASTLE CARY
Heart of the South West | South Somerset | AXMINSTER | YEOVIL BSP | CHILTON CANTELO
Heart of the South West | South Somerset | AXMINSTER | YEOVIL BSP | HENSTRIDGE
Heart of the South West | South Somerset | AXMINSTER | YEOVIL BSP | LARKHILL
Heart of the South West | South Somerset | AXMINSTER | YEOVIL BSP | MILBORNE PORT
Heart of the South West | South Somerset | AXMINSTER | YEOVIL BSP | SHERBORNE
Heart of the South West | South Somerset | AXMINSTER | YEOVIL BSP | SPARKFORD
Heart of the South West | South Somerset | AXMINSTER | YEOVIL BSP | WEST HENDFORD
Heart of the South West | South Somerset | AXMINSTER | YEOVIL BSP | YEOVIL
Heart of the South West | South Somerset | AXMINSTER | YEOVIL BSP | YETMINSTER
Heart of the South West | South Somerset | MANNINGTON GSP | SHAFTESBURY BSP | BOURTON
Heart of the South West | South Somerset | MANNINGTON GSP | SHAFTESBURY BSP | WEST STOUR
Heart of the South West | South Somerset | MANNINGTON GSP | SHAFTESBURY BSP | WINCANTON
Heart of the South West | South Somerset | MELKSHAM GSP | FROME BSP | BRUTON
Heart of the South West | South Somerset | MELKSHAM GSP | FROME BSP | HOLWELL
Hertfordshire | Three Rivers | IVER 132KV | DENHAM | COKES LANE
Hertfordshire | Three Rivers | IVER 132KV | DENHAM | DENHAM AVENUE
Hertfordshire | Three Rivers | IVER 132KV | DENHAM | GRASSINGHAM ROAD
Hertfordshire | Three Rivers | IVER 132KV | DENHAM | HAREFIELD
London | Brent | WILLESDEN GSP | ACTON LANE | PARK ROYAL
London | Brent | WILLESDEN GSP | CANAL BANK | CANAL BANK 11kV
London | Ealing | EALING GSP | EALING 22kV | EALING 11kV
London | Ealing | EALING GSP | EALING 22kV | BRENTFORD
London | Ealing | EALING GSP | EALING 22kV | DEAN GARDENS
London | Ealing | EALING GSP | EALING 22kV | HARVARD LANE
London | Ealing | NORTH HYDE GSP | NORTH HYDE 22kV | SPRINGFIELD ROAD
London | Ealing | NORTH HYDE GSP | NORTH HYDE 22kV | THE GREEN
London | Ealing | WILLESDEN GSP | ACTON LANE | GOLDSMITHS
London | Ealing | WILLESDEN GSP |  | GREENFORD
London | Ealing | WILLESDEN GSP | ACTON LANE | LEAMINGTON PARK
London | Ealing | WILLESDEN GSP | ACTON LANE | PARK ROYAL
London | Ealing | WILLESDEN GSP | CANAL BANK | CANAL BANK 11kV
London | Hammersmith and Fulham | EALING GSP | EALING 22kV | HARVARD LANE
London | Hammersmith and Fulham | WILLESDEN GSP | ACTON LANE | GOLDSMITHS
London | Hammersmith and Fulham | WILLESDEN GSP | ACTON LANE | LEAMINGTON PARK
London | Hammersmith and Fulham | WILLESDEN GSP | CANAL BANK | CANAL BANK 11kV
London | Hillingdon | IVER 132KV | DENHAM | DENHAM AVENUE
London | Hillingdon | IVER 132KV | DENHAM | HAREFIELD
London | Hillingdon | IVER 132KV | LONGFORD | BATH ROAD WEST
London | Hillingdon | IVER 132KV | LONGFORD | POYLE
London | Hillingdon | IVER 132KV | UPTON BSP | UPTON
London | Hillingdon | LALEHAM | EAST BEDFONT A | NORTH FELTHAM
London | Hillingdon | NORTH HYDE GSP | NORTH HYDE 22kV | BATH ROAD EAST
London | Hillingdon | NORTH HYDE GSP |  | HAYES
London | Hillingdon | NORTH HYDE GSP | NORTH HYDE 22kV | SPRINGFIELD ROAD
London | Hounslow | EALING GSP | EALING 22kV | BRENTFORD
London | Hounslow | EALING GSP | EALING 22kV | HARVARD LANE
London | Hounslow | LALEHAM | EAST BEDFONT A | CHURCH ROAD
London | Hounslow | LALEHAM | EAST BEDFONT A | FELTHAM
London | Hounslow | LALEHAM | EAST BEDFONT A | HOPE AND ANCHOR
London | Hounslow | LALEHAM | EAST BEDFONT A | NORTH FELTHAM
London | Hounslow | LALEHAM | STAINES | STANWELL
London | Hounslow | LALEHAM | STAINES | SUNBURY CROSS
London | Hounslow | NORTH HYDE GSP | NORTH HYDE 22kV | BATH ROAD EAST
London | Hounslow | NORTH HYDE GSP |  | NORTH HYDE 11kV
London | Hounslow | NORTH HYDE GSP | NORTH HYDE 22kV | THE GREEN
London | Hounslow | WILLESDEN GSP | ACTON LANE | GOLDSMITHS
London | Richmond upon Thames | EALING GSP | EALING 22kV | BRENTFORD
London | Richmond upon Thames | EALING GSP | EALING 22kV | HARVARD LANE
London | Richmond upon Thames | LALEHAM | EAST BEDFONT A | FELTHAM
London | Richmond upon Thames | LALEHAM | EAST BEDFONT A | HOPE AND ANCHOR
London | Richmond upon Thames | LALEHAM | EAST BEDFONT A | NORTH FELTHAM
London | Richmond upon Thames | LALEHAM | STAINES | SUNBURY CROSS
Oxfordshire LEP | Cherwell | COWLEY GSP | HEADINGTON BSP | ARNCOTT
Oxfordshire LEP | Cherwell | COWLEY GSP | HEADINGTON BSP | HEADINGTON
Oxfordshire LEP | Cherwell | COWLEY GSP | HEADINGTON BSP | WHEATLEY
Oxfordshire LEP | Cherwell | COWLEY GSP | YARNTON BSP | CHIPPING NORTON
Oxfordshire LEP | Cherwell | COWLEY GSP | YARNTON BSP | DEDDINGTON
Oxfordshire LEP | Cherwell | COWLEY GSP | YARNTON BSP | KIDDINGTON
Oxfordshire LEP | Cherwell | COWLEY GSP | YARNTON BSP | LOVELACE ROAD
Oxfordshire LEP | Cherwell | COWLEY GSP | YARNTON BSP | WOODSTOCK
Oxfordshire LEP | Cherwell | COWLEY GSP | YARNTON BSP | YARNTON
Oxfordshire LEP | Cherwell | EAST CLAYDON GSP | BICESTER NORTH BSP | BICESTER
Oxfordshire LEP | Cherwell | EAST CLAYDON GSP | BICESTER NORTH BSP | BICESTER NORTH
Oxfordshire LEP | Cherwell | EAST CLAYDON GSP | BICESTER NORTH BSP | COTTISFORD
Oxfordshire LEP | Cherwell | EAST CLAYDON GSP | BICESTER NORTH BSP | UPPER HEYFORD
Oxfordshire LEP | Oxford | COWLEY GSP | COWLEY LOCAL (2 X 90) | COWLEY LOCAL
Oxfordshire LEP | Oxford | COWLEY GSP | COWLEY LOCAL (2 X 90) | ROSE HILL
Oxfordshire LEP | Oxford | COWLEY GSP | COWLEY LOCAL (2 X 90) | UNION STREET
Oxfordshire LEP | Oxford | COWLEY GSP | HEADINGTON BSP | HEADINGTON
Oxfordshire LEP | Oxford | COWLEY GSP | HEADINGTON BSP | OLD ROAD
Oxfordshire LEP | Oxford | COWLEY GSP | HEADINGTON BSP | WHEATLEY
Oxfordshire LEP | Oxford | COWLEY GSP | OXFORD BSP | FRENCHAY ROAD
Oxfordshire LEP | Oxford | COWLEY GSP | OXFORD BSP | NORTH HINKSEY
Oxfordshire LEP | Oxford | COWLEY GSP | OXFORD BSP | OXFORD
Oxfordshire LEP | Oxford | COWLEY GSP | OXFORD BSP | ST EBBES
Oxfordshire LEP | Oxford | COWLEY GSP | YARNTON BSP | LOVELACE ROAD
Oxfordshire LEP | Oxford | COWLEY GSP | YARNTON BSP | YARNTON
Oxfordshire LEP | South Oxfordshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | YATTENDON
Oxfordshire LEP | South Oxfordshire | BRAMLEY (FLEE) | BURGHFIELD MAIN | KENTWOOD HILL
Oxfordshire LEP | South Oxfordshire | BRAMLEY (FLEE) | BURGHFIELD RESERVE | GORING
Oxfordshire LEP | South Oxfordshire | BRAMLEY (FLEE) | BURGHFIELD RESERVE | PANGBOURNE
Oxfordshire LEP | South Oxfordshire | BRAMLEY (FLEE) | BURGHFIELD RESERVE | WOODCOTE
Oxfordshire LEP | South Oxfordshire | BRAMLEY (FLEE) | READING BSP | HENLEY
Oxfordshire LEP | South Oxfordshire | BRAMLEY (FLEE) | READING BSP | KIDMORE END
Oxfordshire LEP | South Oxfordshire | BRAMLEY (FLEE) | READING BSP | READING
Oxfordshire LEP | South Oxfordshire | BRAMLEY (FLEE) | READING BSP | TWYFORD
Oxfordshire LEP | South Oxfordshire | BRAMLEY (FLEE) | READING TOWN BSP | CAVERSHAM
Oxfordshire LEP | South Oxfordshire | BRAMLEY (FLEE) | READING TOWN BSP | READING TOWN
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | COWLEY LOCAL (2 X 45) | BERINSFIELD
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | COWLEY LOCAL (2 X 45) | KENNINGTON
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | COWLEY LOCAL (2 X 90) | COWLEY LOCAL
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | COWLEY LOCAL (2 X 90) | ROSE HILL
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | COWLEY LOCAL (2 X 90) | WALLINGFORD
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | DRAYTON BSP | CHOLSEY
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | DRAYTON BSP | FULSCOT
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | DRAYTON BSP | MILTON
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | DRAYTON BSP | WINSMORE LANE
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | HEADINGTON BSP | ARNCOTT
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | HEADINGTON BSP | HEADINGTON
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | HEADINGTON BSP | OLD ROAD
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | HEADINGTON BSP | WHEATLEY
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | HIGH WYCOMBE BSP | NUFFIELD
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | HIGH WYCOMBE BSP | STOKENCHURCH
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | HIGH WYCOMBE BSP | WATLINGTON
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | YARNTON BSP | LOVELACE ROAD
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | YARNTON BSP | YARNTON
Oxfordshire LEP | Vale of White Horse | BRAMLEY (ANDO-THAT) | THATCHAM BSP | LAMBOURN
Oxfordshire LEP | Vale of White Horse | BRAMLEY (ANDO-THAT) | THATCHAM BSP | LECKHAMPSTEAD
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | COWLEY LOCAL (2 X 45) | BERINSFIELD
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | COWLEY LOCAL (2 X 45) | KENNINGTON
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | COWLEY LOCAL (2 X 90) | COWLEY LOCAL
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | COWLEY LOCAL (2 X 90) | ROSE HILL
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | COWLEY LOCAL (2 X 90) | WALLINGFORD
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | DRAYTON BSP | CHOLSEY
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | DRAYTON BSP | FULSCOT
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | DRAYTON BSP | GROVE
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | DRAYTON BSP | MILTON
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | DRAYTON BSP | WANTAGE
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | DRAYTON BSP | WINSMORE LANE
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | OXFORD BSP | NORTH HINKSEY
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | OXFORD BSP | OXFORD
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | OXFORD BSP | ST EBBES
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | OXFORD BSP | WOOTTON ROAD
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | WITNEY BSP | FYFIELD
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | WITNEY BSP | STANDLAKE
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | YARNTON BSP | EYNSHAM
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | YARNTON BSP | YARNTON
Oxfordshire LEP | Vale of White Horse | MINETY GSP | STRATTON (2 X 60) | BLACK BOURTON
Oxfordshire LEP | Vale of White Horse | MINETY GSP | STRATTON (2 X 60) | FARINGDON
Oxfordshire LEP | Vale of White Horse | MINETY GSP | STRATTON (2 X 60) | LECHLADE
Oxfordshire LEP | Vale of White Horse | MINETY GSP | STRATTON (2 X 60) | SHRIVENHAM
Oxfordshire LEP | Vale of White Horse | MINETY GSP | STRATTON (2 X 60) | STANTON FITZWARREN
Oxfordshire LEP | Vale of White Horse | MINETY GSP | TOOTHILL BSP | CHISLEDON
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | WITNEY BSP | BLEDINGTON
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | WITNEY BSP | BURFORD
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | WITNEY BSP | CARTERTON
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | WITNEY BSP | FYFIELD
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | WITNEY BSP | LEAFIELD
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | WITNEY BSP | RISSINGTON
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | WITNEY BSP | STANDLAKE
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | WITNEY BSP | WINDRUSH PARK
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | WITNEY BSP | WITNEY TOWN
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | YARNTON BSP | CHARLBURY
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | YARNTON BSP | CHIPPING NORTON
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | YARNTON BSP | DEDDINGTON
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | YARNTON BSP | EYNSHAM
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | YARNTON BSP | KIDDINGTON
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | YARNTON BSP | WOODSTOCK
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | YARNTON BSP | YARNTON
Oxfordshire LEP | West Oxfordshire | EAST CLAYDON GSP | BICESTER NORTH BSP | UPPER HEYFORD
Oxfordshire LEP | West Oxfordshire | MINETY GSP | CIRENCESTER BSP | NORTHLEACH
Oxfordshire LEP | West Oxfordshire | MINETY GSP | STRATTON (2 X 60) | BLACK BOURTON
Oxfordshire LEP | West Oxfordshire | MINETY GSP | STRATTON (2 X 60) | FARINGDON
Oxfordshire LEP | West Oxfordshire | MINETY GSP | STRATTON (2 X 60) | LECHLADE
Solent | East Hampshire | BRAMLEY (FLEE) | ALDERSHOT BSP | FARNHAM
Solent | East Hampshire | BRAMLEY (FLEE) | ALDERSHOT BSP | HINDHEAD
Solent | East Hampshire | BRAMLEY (FLEE) | ALTON | ALRESFORD
Solent | East Hampshire | BRAMLEY (FLEE) | ALTON | ALTON LOCAL
Solent | East Hampshire | BRAMLEY (FLEE) | ALTON | BORDON
Solent | East Hampshire | BRAMLEY (FLEE) | ALTON | HERRIARD
Solent | East Hampshire | BRAMLEY (FLEE) | COXMOOR WOOD BSP | COXMOOR WOOD
Solent | East Hampshire | BRAMLEY (FLEE) | COXMOOR WOOD BSP | HOOK
Solent | East Hampshire | BRAMLEY (FLEE) | COXMOOR WOOD BSP | WRECCLESHAM
Solent | East Hampshire | BRAMLEY (FLEE) | FERNHURST | HASLEMERE
Solent | East Hampshire | BRAMLEY (FLEE) | FERNHURST | LANGLEY COURT
Solent | East Hampshire | BRAMLEY (FLEE) | FERNHURST | PETERSFIELD
Solent | East Hampshire | BRAMLEY (FLEE) | FERNHURST | PRESTON CANDOVER
Solent | East Hampshire | LOVEDEAN GSP | CHICHESTER & HUNSTON | ASHLING ROAD
Solent | East Hampshire | LOVEDEAN GSP | FORT WIDLEY | WATERLOOVILLE
Solent | East Hampshire | LOVEDEAN GSP | HAVANT | EMSWORTH
Solent | East Hampshire | LOVEDEAN GSP | HAVANT | HORNDEAN
Solent | East Hampshire | LOVEDEAN GSP | HAVANT | LEIGH PARK
Solent | Eastleigh | BOTLEY WOOD GSP | BOTLEY WOOD BSP | WHITELEY
Solent | Eastleigh | BOTLEY WOOD GSP | NETLEY COMMON BSP | BISHOPS WALTHAM
Solent | Eastleigh | BOTLEY WOOD GSP | NETLEY COMMON BSP | BITTERNE
Solent | Eastleigh | BOTLEY WOOD GSP | NETLEY COMMON BSP | HAMBLE
Solent | Eastleigh | BOTLEY WOOD GSP | NETLEY COMMON BSP | NETLEY COMMON
Solent | Eastleigh | BOTLEY WOOD GSP | NETLEY COMMON BSP | TOWNHILL PARK
Solent | Eastleigh | BOTLEY WOOD GSP | NETLEY COMMON BSP | WESTON
Solent | Eastleigh | NURSLING GSP | ROWNHAMS | NORTH BADDESLEY
Solent | Eastleigh | NURSLING GSP | ROWNHAMS | SILKSTEAD
Solent | Eastleigh | NURSLING GSP | VELMORE BSP | BASSETT
Solent | Eastleigh | NURSLING GSP | VELMORE BSP | BISHOPSTOKE
Solent | Eastleigh | NURSLING GSP | VELMORE BSP | CHANDLERS FORD
Solent | Eastleigh | NURSLING GSP | VELMORE BSP | EASTLEIGH NORTH
Solent | Eastleigh | NURSLING GSP | VELMORE BSP | HEDGE END
Solent | Eastleigh | NURSLING GSP | VELMORE BSP | VELMORE
Solent | Fareham | BOTLEY WOOD GSP | BOTLEY WOOD BSP | PARK GATE
Solent | Fareham | BOTLEY WOOD GSP | BOTLEY WOOD BSP | WHITLEY
Solent | Fareham | BOTLEY WOOD GSP | NETLEY COMMON BSP | NETLEY COMMON
Solent | Fareham | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | BROCKHURST
Solent | Fareham | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | HOEFORD
Solent | Fareham | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | NORTH FAREHAM
Solent | Fareham | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | PLESSEY TITCHFIELD
Solent | Fareham | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | TITCHFIELD
Solent | Fareham | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | WEST END
Solent | Fareham | LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | LEE-ON-SOLENT
Solent | Fareham | LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | ROWNER PARK
Solent | Fareham | LOVEDEAN GSP | WYMERING BSP | PORTCHESTER
Solent | Fareham | LOVEDEAN GSP | WYMERING BSP | WYMERING
Solent | Gosport | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | BROCKHURST
Solent | Gosport | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | HOEFORD
Solent | Gosport | LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | LEE-ON-SOLENT
Solent | Gosport | LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | ROWNER PARK
Solent | Gosport | LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | ZETLAND ROAD
Solent | Havant | LOVEDEAN GSP | CHICHESTER & HUNSTON | ASHLING ROAD
Solent | Havant | LOVEDEAN GSP | FORT WIDLEY | PURBROOK
Solent | Havant | LOVEDEAN GSP | FORT WIDLEY | WATERLOOVILLE
Solent | Havant | LOVEDEAN GSP | HAVANT | BROCKHAMPTON
Solent | Havant | LOVEDEAN GSP | HAVANT | EMSWORTH
Solent | Havant | LOVEDEAN GSP | HAVANT | GABLE HEAD
Solent | Havant | LOVEDEAN GSP | HAVANT | HORNDEAN
Solent | Havant | LOVEDEAN GSP | HAVANT | LEIGH PARK
Solent | Havant | LOVEDEAN GSP | HAVANT | MEYRICK ROAD
Solent | Havant | LOVEDEAN GSP | PORTSMOUTH BSP | FRATTON PARK
Solent | Havant | LOVEDEAN GSP | WYMERING BSP | FARLINGTON
Solent | Havant | LOVEDEAN GSP | WYMERING BSP | WYMERING
Solent | Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | BINSTEAD
Solent | Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | FRESHWATER
Solent | Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | NEWPORT
Solent | Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | RYDE
Solent | Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | SANDOWN
Solent | Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | SHALFLEET
Solent | Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | SHANKLIN
Solent | Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | VENTNOR
Solent | Isle of Wight | LOVEDEAN GSP | PORTSMOUTH BSP | GREETHAM STREET
Solent | New Forest | BOTLEY WOOD GSP | NETLEY COMMON BSP | HAMBLE
Solent | New Forest | FAWLEY GSP | COWES & WOOTTON COMMON BSP | FRESHWATER
Solent | New Forest | FAWLEY GSP | LANGLEY BSP | BUTTS ASH
Solent | New Forest | FAWLEY GSP | LANGLEY BSP | LANGLEY
Solent | New Forest | MANNINGTON GSP | ARNEWOOD | HINCHESLEA
Solent | New Forest | MANNINGTON GSP | ARNEWOOD | LYMINGTON
Solent | New Forest | MANNINGTON GSP | ARNEWOOD | MILFORD-ON-SEA
Solent | New Forest | MANNINGTON GSP | ARNEWOOD | NEW MILTON
Solent | New Forest | MANNINGTON GSP | CHRISTCHURCH BSP | CHRISTCHURCH
Solent | New Forest | MANNINGTON GSP | CHRISTCHURCH BSP | SOMERFORD
Solent | New Forest | MANNINGTON GSP | MANNINGTON BSP | FORDINGBRIDGE
Solent | New Forest | MANNINGTON GSP | MANNINGTON BSP | MANNINGTON
Solent | New Forest | MANNINGTON GSP | MANNINGTON BSP | Mill Lane
Solent | New Forest | MANNINGTON GSP | MANNINGTON BSP | ROCKBOURNE
Solent | New Forest | MANNINGTON GSP | MANNINGTON BSP | VERWOOD
Solent | New Forest | MANNINGTON GSP | MANNINGTON BSP | WIMBORNE ST GILES
Solent | New Forest | MANNINGTON GSP | SALISBURY | HOMINGTON
Solent | New Forest | MANNINGTON GSP | SALISBURY | REDLYNCH
Solent | New Forest | MANNINGTON GSP | SHAFTESBURY BSP | MINCHINGTON
Solent | New Forest | NURSLING GSP | ROWNHAMS | FLETCHWOOD
Solent | New Forest | NURSLING GSP | ROWNHAMS | LORDSHILL
Solent | New Forest | NURSLING GSP | ROWNHAMS | ROMSEY
Solent | New Forest | NURSLING GSP | ROWNHAMS | TOTTON
Solent | New Forest | NURSLING GSP | SOUTHAMPTON (2 X 60) | CENTRAL BRIDGE
Solent | New Forest | NURSLING GSP | WINCHESTER | DUNBRIDGE
Solent | Portsmouth | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | HOEFORD
Solent | Portsmouth | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | WEST END
Solent | Portsmouth | LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | ZETLAND ROAD
Solent | Portsmouth | LOVEDEAN GSP | FORT WIDLEY | PURBROOK
Solent | Portsmouth | LOVEDEAN GSP | HAVANT | MEYRICK ROAD
Solent | Portsmouth | LOVEDEAN GSP | PORTSMOUTH BSP | BRANDON ROAD
Solent | Portsmouth | LOVEDEAN GSP | PORTSMOUTH BSP | EASTNEY
Solent | Portsmouth | LOVEDEAN GSP | PORTSMOUTH BSP | FRATTON PARK
Solent | Portsmouth | LOVEDEAN GSP | PORTSMOUTH BSP | GREETHAM STREET
Solent | Portsmouth | LOVEDEAN GSP | PORTSMOUTH BSP | PORTSMOUTH
Solent | Portsmouth | LOVEDEAN GSP | WYMERING BSP | COLLEGE PARK
Solent | Portsmouth | LOVEDEAN GSP | WYMERING BSP | FARLINGTON
Solent | Portsmouth | LOVEDEAN GSP | WYMERING BSP | GAMBLE ROAD
Solent | Portsmouth | LOVEDEAN GSP | WYMERING BSP | HILSEA
Solent | Portsmouth | LOVEDEAN GSP | WYMERING BSP | PORTCHESTER
Solent | Portsmouth | LOVEDEAN GSP | WYMERING BSP | WYMERING
Solent | Southampton | BOTLEY WOOD GSP | NETLEY COMMON BSP | BITTERNE
Solent | Southampton | BOTLEY WOOD GSP | NETLEY COMMON BSP | NETLEY COMMON
Solent | Southampton | BOTLEY WOOD GSP | NETLEY COMMON BSP | TOWNHILL PARK
Solent | Southampton | BOTLEY WOOD GSP | NETLEY COMMON BSP | WESTON
Solent | Southampton | BOTLEY WOOD GSP | NETLEY COMMON BSP | WOOLSTON
Solent | Southampton | NURSLING GSP | ROWNHAMS | LORDSHILL
Solent | Southampton | NURSLING GSP | ROWNHAMS | MAYBUSH
Solent | Southampton | NURSLING GSP | ROWNHAMS | NORTH BADDESLEY
Solent | Southampton | NURSLING GSP | SOUTHAMPTON (2 X 60) | BEVOIS VALLEY
Solent | Southampton | NURSLING GSP | SOUTHAMPTON (2 X 60) | CENTRAL BRIDGE
Solent | Southampton | NURSLING GSP | SOUTHAMPTON (2 X 60) | CHAPEL
Solent | Southampton | NURSLING GSP | SOUTHAMPTON (2 X 90) | REGENTS PARK
Solent | Southampton | NURSLING GSP | SOUTHAMPTON (2 X 90) | SHIRLEY
Solent | Southampton | NURSLING GSP | SOUTHAMPTON (2 X 90) | WESTERN ESPLANADE
Solent | Southampton | NURSLING GSP | SOUTHAMPTON (2 X 90) | WOODMILL LANE
Solent | Southampton | NURSLING GSP |  | SOUTHFIELD ROAD
Solent | Southampton | NURSLING GSP | VELMORE BSP | BASSETT
Solent | Southampton | NURSLING GSP | VELMORE BSP | EASTLEIGH NORTH
Solent | Southampton | NURSLING GSP | VELMORE BSP | VELMORE
Solent | Test Valley | BRAMLEY (ANDO-THAT) | ANDOVER BSP | ANDOVER
Solent | Test Valley | BRAMLEY (ANDO-THAT) | ANDOVER BSP | ANDOVER EAST
Solent | Test Valley | BRAMLEY (ANDO-THAT) | ANDOVER BSP | ANDOVER TOWN
Solent | Test Valley | BRAMLEY (ANDO-THAT) | ANDOVER BSP | BARTON STACEY
Solent | Test Valley | BRAMLEY (ANDO-THAT) | ANDOVER BSP | HURSTBOURNE TARRANT
Solent | Test Valley | BRAMLEY (ANDO-THAT) | ANDOVER BSP | MIDDLE WALLOP
Solent | Test Valley | BRAMLEY (ANDO-THAT) | ANDOVER BSP | PORTWAY
Solent | Test Valley | BRAMLEY (ANDO-THAT) | ANDOVER BSP | THRUXTON
Solent | Test Valley | BRAMLEY (ANDO-THAT) | ANDOVER BSP | WHITCHURCH
Solent | Test Valley | BRAMLEY (ANDO-THAT) | THATCHAM BSP | BALL HILL
Solent | Test Valley | BRAMLEY (ANDO-THAT) | THATCHAM BSP | KINTBURY
Solent | Test Valley | MANNINGTON GSP | SALISBURY | PETERSFINGER
Solent | Test Valley | MELKSHAM GSP | AMESBURY | PARK HOUSE
Solent | Test Valley | MELKSHAM GSP | WEST GRAFTON | TIDWORTH
Solent | Test Valley | MELKSHAM GSP | WEST GRAFTON | WEST GRAFTON VILLAGE
Solent | Test Valley | NURSLING GSP | ROWNHAMS | FLETCHWOOD
Solent | Test Valley | NURSLING GSP | ROWNHAMS | LORDSHILL
Solent | Test Valley | NURSLING GSP | ROWNHAMS | MAYBUSH
Solent | Test Valley | NURSLING GSP | ROWNHAMS | NORTH BADDESLEY
Solent | Test Valley | NURSLING GSP | ROWNHAMS | ROMSEY
Solent | Test Valley | NURSLING GSP | ROWNHAMS | SILKSTEAD
Solent | Test Valley | NURSLING GSP | ROWNHAMS | TOTTON
Solent | Test Valley | NURSLING GSP | SOUTHAMPTON (2 X 90) | REGENTS PARK
Solent | Test Valley | NURSLING GSP | VELMORE BSP | BASSETT
Solent | Test Valley | NURSLING GSP | VELMORE BSP | CHANDLERS FORD
Solent | Test Valley | NURSLING GSP | VELMORE BSP | VELMORE
Solent | Test Valley | NURSLING GSP | WINCHESTER | DUNBRIDGE
Solent | Test Valley | NURSLING GSP | WINCHESTER | HARESTOCK
Solent | Test Valley | NURSLING GSP | WINCHESTER | HOUGHTON
Solent | Winchester | BOTLEY WOOD GSP | BOTLEY WOOD BSP | PARK GATE
Solent | Winchester | BOTLEY WOOD GSP | BOTLEY WOOD BSP | WHITLEY
Solent | Winchester | BOTLEY WOOD GSP | NETLEY COMMON BSP | BISHOPS WALTHAM
Solent | Winchester | BOTLEY WOOD GSP | NETLEY COMMON BSP | NETLEY COMMON
Solent | Winchester | BRAMLEY (ANDO-THAT) | ANDOVER BSP | BARTON STACEY
Solent | Winchester | BRAMLEY (ANDO-THAT) | ANDOVER BSP | WHITCHURCH
Solent | Winchester | BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | OVERTON
Solent | Winchester | BRAMLEY (FLEE) | ALTON | ALRESFORD
Solent | Winchester | BRAMLEY (FLEE) | FERNHURST | PETERSFIELD
Solent | Winchester | BRAMLEY (FLEE) | FERNHURST | PRESTON CANDOVER
Solent | Winchester | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | NORTH FAREHAM
Solent | Winchester | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | PLESSEY TITCHFIELD
Solent | Winchester | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | TITCHFIELD
Solent | Winchester | LOVEDEAN GSP | FORT WIDLEY | PURBROOK
Solent | Winchester | LOVEDEAN GSP | FORT WIDLEY | WATERLOOVILLE
Solent | Winchester | LOVEDEAN GSP | HAVANT | HORNDEAN
Solent | Winchester | LOVEDEAN GSP | WYMERING BSP | PORTCHESTER
Solent | Winchester | LOVEDEAN GSP | WYMERING BSP | WYMERING
Solent | Winchester | NURSLING GSP | ROWNHAMS | NORTH BADDESLEY
Solent | Winchester | NURSLING GSP | ROWNHAMS | SILKSTEAD
Solent | Winchester | NURSLING GSP | VELMORE BSP | CHANDLERS FORD
Solent | Winchester | NURSLING GSP | VELMORE BSP | EASTLEIGH NORTH
Solent | Winchester | NURSLING GSP | VELMORE BSP | HEDGE END
Solent | Winchester | NURSLING GSP | WINCHESTER | DUNBRIDGE
Solent | Winchester | NURSLING GSP | WINCHESTER | GORDON ROAD
Solent | Winchester | NURSLING GSP | WINCHESTER | HARESTOCK
Solent | Winchester | NURSLING GSP | WINCHESTER | HOUGHTON
Solent | Winchester | NURSLING GSP | WINCHESTER | ST CROSS
South East Midlands | Aylesbury Vale | COWLEY GSP | HEADINGTON BSP | ARNCOTT
South East Midlands | Aylesbury Vale | COWLEY GSP | HEADINGTON BSP | WHEATLEY
South East Midlands | Aylesbury Vale | EAST CLAYDON GSP | BICESTER NORTH BSP | BICESTER
South East Midlands | Aylesbury Vale | EAST CLAYDON GSP | BICESTER NORTH BSP | COTTISFORD
South East Midlands | South Northamptonshire | COWLEY GSP | YARNTON BSP | DEDDINGTON
South East Midlands | South Northamptonshire | EAST CLAYDON GSP | BICESTER NORTH BSP | COTTISFORD
Swindon and Wiltshire | Swindon | BRAMLEY (ANDO-THAT) | THATCHAM BSP | LAMBOURN
Swindon and Wiltshire | Swindon | MELKSHAM GSP | WEST GRAFTON | RAMSBURY
Swindon and Wiltshire | Swindon | MINETY GSP | CIRENCESTER BSP | CRICKLADE
Swindon and Wiltshire | Swindon | MINETY GSP | CIRENCESTER BSP | FAIRFORD
Swindon and Wiltshire | Swindon | MINETY GSP | STRATTON (2 X 60) | FARINGDON
Swindon and Wiltshire | Swindon | MINETY GSP | STRATTON (2 X 60) | LECHLADE
Swindon and Wiltshire | Swindon | MINETY GSP | STRATTON (2 X 60) | SHRIVENHAM
Swindon and Wiltshire | Swindon | MINETY GSP | STRATTON (2 X 60) | STANTON FITZWARREN
Swindon and Wiltshire | Swindon | MINETY GSP | STRATTON (2 X 60) | STRATTON
Swindon and Wiltshire | Swindon | MINETY GSP | STRATTON (2 X 90) | DRAKES WAY
Swindon and Wiltshire | Swindon | MINETY GSP | STRATTON (2 X 90) | PARK NORTH
Swindon and Wiltshire | Swindon | MINETY GSP | STRATTON (2 X 90) | PLESSEY
Swindon and Wiltshire | Swindon | MINETY GSP | STRATTON (2 X 90) | PRESSED STEEL SWINDON
Swindon and Wiltshire | Swindon | MINETY GSP | SWINDON BSP | MANCHESTER ROAD
Swindon and Wiltshire | Swindon | MINETY GSP | SWINDON BSP | SWINDON
Swindon and Wiltshire | Swindon | MINETY GSP | SWINDON BSP | TRADING ESTATE
Swindon and Wiltshire | Swindon | MINETY GSP | SWINDON BSP | WOOTTON BASSETT
Swindon and Wiltshire | Swindon | MINETY GSP | TOOTHILL BSP | CHISLEDON
Swindon and Wiltshire | Swindon | MINETY GSP | TOOTHILL BSP | DORCAN SOUTH
Swindon and Wiltshire | Swindon | MINETY GSP | TOOTHILL BSP | QUARRY ROAD
Swindon and Wiltshire | Swindon | MINETY GSP | TOOTHILL BSP | TOOTHILL
Swindon and Wiltshire | Swindon | MINETY GSP | TOOTHILL BSP | WROUGHTON
Swindon and Wiltshire | Wiltshire | BRAMLEY (ANDO-THAT) | ANDOVER BSP | HURSTBOURNE TARRANT
Swindon and Wiltshire | Wiltshire | BRAMLEY (ANDO-THAT) | ANDOVER BSP | MIDDLE WALLOP
Swindon and Wiltshire | Wiltshire | BRAMLEY (ANDO-THAT) | ANDOVER BSP | THRUXTON
Swindon and Wiltshire | Wiltshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | HUNGERFORD
Swindon and Wiltshire | Wiltshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | KINTBURY
Swindon and Wiltshire | Wiltshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | LAMBOURN
Swindon and Wiltshire | Wiltshire | MANNINGTON GSP | MANNINGTON BSP | ROCKBOURNE
Swindon and Wiltshire | Wiltshire | MANNINGTON GSP | SALISBURY | BEMERTON
Swindon and Wiltshire | Wiltshire | MANNINGTON GSP | SALISBURY | HOMINGTON
Swindon and Wiltshire | Wiltshire | MANNINGTON GSP | SALISBURY | NETHERHAMPTON
Swindon and Wiltshire | Wiltshire | MANNINGTON GSP | SALISBURY | PETERSFINGER
Swindon and Wiltshire | Wiltshire | MANNINGTON GSP | SALISBURY | REDLYNCH
Swindon and Wiltshire | Wiltshire | MANNINGTON GSP | SALISBURY | SALISBURY CENTRAL
Swindon and Wiltshire | Wiltshire | MANNINGTON GSP | SALISBURY | STAPLEFORD
Swindon and Wiltshire | Wiltshire | MANNINGTON GSP | SALISBURY | TEFFONT
Swindon and Wiltshire | Wiltshire | MANNINGTON GSP | SHAFTESBURY BSP | BOURTON
Swindon and Wiltshire | Wiltshire | MANNINGTON GSP | SHAFTESBURY BSP | MINCHINGTON
Swindon and Wiltshire | Wiltshire | MANNINGTON GSP | SHAFTESBURY BSP | SHAFTESBURY
Swindon and Wiltshire | Wiltshire | MANNINGTON GSP | SHAFTESBURY BSP | SHROTON
Swindon and Wiltshire | Wiltshire | MANNINGTON GSP | SHAFTESBURY BSP | TISBURY
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | AMESBURY | BOSCOMBE DOWN
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | AMESBURY | ENFORD
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | AMESBURY | PARK HOUSE
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | AMESBURY | PEWSEY
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | CHIPPENHAM | ALDERTON
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | CHIPPENHAM | CALNE
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | CHIPPENHAM | COCKLEBURY
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | CHIPPENHAM | LYNEHAM
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | CHIPPENHAM | MALMESBURY
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | CHIPPENHAM | ROWDEN
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | CHIPPENHAM | SUTTON BENGER
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | CHIPPENHAM | TETBURY
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | CHIPPENHAM | YATTON KEYNELL
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | FROME BSP | BRUTON
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | FROME BSP | CODFORD
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | FROME BSP | CROCKERTON
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | FROME BSP | FROME
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | FROME BSP | HAWKERIDGE
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | FROME BSP | HOLWELL
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | FROME BSP | WARMINSTER
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | FROME BSP | WESTBURY
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | NORRINGTON | ASHTON PARK
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | NORRINGTON | BRADFORD-ON-AVON
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | NORRINGTON | BROMHAM
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | NORRINGTON | CORSHAM
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | NORRINGTON | DEVIZES
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | NORRINGTON | EASTERTON
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | NORRINGTON | MELKSHAM TOWN
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | NORRINGTON | SPRING QUARRY WEST
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | NORRINGTON | TROWBRIDGE TOWN
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | WEST GRAFTON | MARLBOROUGH SOUTH
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | WEST GRAFTON | RAMSBURY
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | WEST GRAFTON | TIDWORTH
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | WEST GRAFTON | WEST GRAFTON VILLAGE
Swindon and Wiltshire | Wiltshire | MINETY GSP | CIRENCESTER BSP | CIRENCESTER TOWN
Swindon and Wiltshire | Wiltshire | MINETY GSP | CIRENCESTER BSP | CRICKLADE
Swindon and Wiltshire | Wiltshire | MINETY GSP | CIRENCESTER BSP | FAIRFORD
Swindon and Wiltshire | Wiltshire | MINETY GSP | CIRENCESTER BSP | MINETY VILLAGE
Swindon and Wiltshire | Wiltshire | MINETY GSP | STRATTON (2 X 60) | SHRIVENHAM
Swindon and Wiltshire | Wiltshire | MINETY GSP | STRATTON (2 X 60) | STANTON FITZWARREN
Swindon and Wiltshire | Wiltshire | MINETY GSP | SWINDON BSP | SWINDON
Swindon and Wiltshire | Wiltshire | MINETY GSP | SWINDON BSP | WOOTTON BASSETT
Swindon and Wiltshire | Wiltshire | MINETY GSP | TOOTHILL BSP | CHISLEDON
Swindon and Wiltshire | Wiltshire | MINETY GSP | TOOTHILL BSP | TOOTHILL
Swindon and Wiltshire | Wiltshire | MINETY GSP | TOOTHILL BSP | WROUGHTON
Swindon and Wiltshire | Wiltshire | NURSLING GSP | ROWNHAMS | ROMSEY
Swindon and Wiltshire | Wiltshire | NURSLING GSP | WINCHESTER | DUNBRIDGE
Thames Valley Berkshire | Bracknell Forest | BRAMLEY (FLEE) | BRACKNELL MAIN | ASCOT
Thames Valley Berkshire | Bracknell Forest | BRAMLEY (FLEE) | BRACKNELL MAIN | BRACKNELL
Thames Valley Berkshire | Bracknell Forest | BRAMLEY (FLEE) | BRACKNELL MAIN | WARFIELD
Thames Valley Berkshire | Bracknell Forest | BRAMLEY (FLEE) | BRACKNELL RESERVE | BAGSHOT
Thames Valley Berkshire | Bracknell Forest | BRAMLEY (FLEE) | BRACKNELL RESERVE | EASTHAMPSTEAD
Thames Valley Berkshire | Bracknell Forest | BRAMLEY (FLEE) | BRACKNELL RESERVE | SUNNINGHILL
Thames Valley Berkshire | Bracknell Forest | BRAMLEY (FLEE) | CAMBERLEY MAIN | CAMBERLEY
Thames Valley Berkshire | Bracknell Forest | BRAMLEY (FLEE) | CAMBERLEY MAIN | CROWTHORNE
Thames Valley Berkshire | Bracknell Forest | BRAMLEY (FLEE) | CAMBERLEY MAIN | KINGS RIDE
Thames Valley Berkshire | Bracknell Forest | BRAMLEY (FLEE) | CAMBERLEY MAIN | SANDHURST
Thames Valley Berkshire | Bracknell Forest | BRAMLEY (FLEE) | MAIDENHEAD BSP | KNOWL HILL
Thames Valley Berkshire | Bracknell Forest | BRAMLEY (FLEE) | MAIDENHEAD BSP | MAIDENHEAD
Thames Valley Berkshire | Bracknell Forest | BRAMLEY (FLEE) | WOKINGHAM BSP | ELMS ROAD
Thames Valley Berkshire | Bracknell Forest | BRAMLEY (FLEE) | WOKINGHAM BSP | PEACOCK FARM
Thames Valley Berkshire | Bracknell Forest | IVER 132KV | CIPPENHAM | CLARENCE ROAD
Thames Valley Berkshire | Bracknell Forest | LALEHAM | STAINES | EGHAM
Thames Valley Berkshire | Reading | BRAMLEY (FLEE) | BURGHFIELD MAIN | COURAGES
Thames Valley Berkshire | Reading | BRAMLEY (FLEE) | BURGHFIELD MAIN | GREEN PARK
Thames Valley Berkshire | Reading | BRAMLEY (FLEE) | BURGHFIELD MAIN | KENTWOOD HILL
Thames Valley Berkshire | Reading | BRAMLEY (FLEE) | BURGHFIELD MAIN | WILSON ROAD
Thames Valley Berkshire | Reading | BRAMLEY (FLEE) | BURGHFIELD RESERVE | SOUTHCOTE
Thames Valley Berkshire | Reading | BRAMLEY (FLEE) | BURGHFIELD RESERVE | TRASH GREEN
Thames Valley Berkshire | Reading | BRAMLEY (FLEE) | READING BSP | KIDMORE END
Thames Valley Berkshire | Reading | BRAMLEY (FLEE) | READING BSP | LITTLE HUNGERFORD
Thames Valley Berkshire | Reading | BRAMLEY (FLEE) | READING BSP | NORTHUMBERLAND AVENUE
Thames Valley Berkshire | Reading | BRAMLEY (FLEE) | READING BSP | READING
Thames Valley Berkshire | Reading | BRAMLEY (FLEE) | READING BSP | SILVER STREET
Thames Valley Berkshire | Reading | BRAMLEY (FLEE) | READING TOWN BSP | CAVERSHAM
Thames Valley Berkshire | Reading | BRAMLEY (FLEE) | READING TOWN BSP | READING TOWN
Thames Valley Berkshire | Reading | BRAMLEY (FLEE) | READING TOWN BSP | THE MALL
Thames Valley Berkshire | Reading | MELKSHAM GSP | AMESBURY | BOSCOMBE DOWN
Thames Valley Berkshire | Reading | MINETY GSP | CIRENCESTER BSP | WHITEWAY
Thames Valley Berkshire | Slough | IVER 132KV | CHALVEY BSP | CHALVEY
Thames Valley Berkshire | Slough | IVER 132KV | CHALVEY BSP | PETERSFIELD AVENUE
Thames Valley Berkshire | Slough | IVER 132KV | LONGFORD | POYLE
Thames Valley Berkshire | Slough | IVER 132KV | SLOUGH | FARNHAM ROYAL
Thames Valley Berkshire | Slough | IVER 132KV | SLOUGH | TAPLOW
Thames Valley Berkshire | Slough | IVER 132KV | UPTON BSP | SUTTON LANE
Thames Valley Berkshire | Slough | IVER 132KV | UPTON BSP | UPTON
Thames Valley Berkshire | West Berkshire | BRAMLEY (ANDO-THAT) | ANDOVER BSP | HURSTBOURNE TARRANT
Thames Valley Berkshire | West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | BALL HILL
Thames Valley Berkshire | West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | BEENHAM
Thames Valley Berkshire | West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | HUNGERFORD
Thames Valley Berkshire | West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | KINGSCLERE
Thames Valley Berkshire | West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | KINTBURY
Thames Valley Berkshire | West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | LAMBOURN
Thames Valley Berkshire | West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | LECKHAMPSTEAD
Thames Valley Berkshire | West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | LOVE LANE
Thames Valley Berkshire | West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | RIVERSIDE
Thames Valley Berkshire | West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | ST JOHNS
Thames Valley Berkshire | West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | TADLEY
Thames Valley Berkshire | West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | THATCHAM
Thames Valley Berkshire | West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | YATTENDON
Thames Valley Berkshire | West Berkshire | BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | ARBORFIELD
Thames Valley Berkshire | West Berkshire | BRAMLEY (FLEE) | BURGHFIELD MAIN | KENTWOOD HILL
Thames Valley Berkshire | West Berkshire | BRAMLEY (FLEE) | BURGHFIELD MAIN | WILSON ROAD
Thames Valley Berkshire | West Berkshire | BRAMLEY (FLEE) | BURGHFIELD RESERVE | GORING
Thames Valley Berkshire | West Berkshire | BRAMLEY (FLEE) | BURGHFIELD RESERVE | MORTIMER
Thames Valley Berkshire | West Berkshire | BRAMLEY (FLEE) | BURGHFIELD RESERVE | PADWORTH
Thames Valley Berkshire | West Berkshire | BRAMLEY (FLEE) | BURGHFIELD RESERVE | PANGBOURNE
Thames Valley Berkshire | West Berkshire | BRAMLEY (FLEE) | BURGHFIELD RESERVE | SOUTHCOTE
Thames Valley Berkshire | West Berkshire | BRAMLEY (FLEE) | BURGHFIELD RESERVE | THEALE
Thames Valley Berkshire | West Berkshire | BRAMLEY (FLEE) | BURGHFIELD RESERVE | TRASH GREEN
Thames Valley Berkshire | West Berkshire | BRAMLEY (FLEE) | BURGHFIELD RESERVE | WOODCOTE
Thames Valley Berkshire | West Berkshire | BRAMLEY (FLEE) | READING TOWN BSP | READING TOWN
Thames Valley Berkshire | West Berkshire | COWLEY GSP | DRAYTON BSP | CHOLSEY
Thames Valley Berkshire | West Berkshire | COWLEY GSP | DRAYTON BSP | WANTAGE
Thames Valley Berkshire | West Berkshire | MELKSHAM GSP | WEST GRAFTON | RAMSBURY
Thames Valley Berkshire | West Berkshire | MINETY GSP | CIRENCESTER BSP | WHITEWAY
Thames Valley Berkshire | Windsor and Maidenhead | AMERSHAM | LOUDWATER BSP | WELL END
Thames Valley Berkshire | Windsor and Maidenhead | BRAMLEY (FLEE) | BRACKNELL MAIN | ASCOT
Thames Valley Berkshire | Windsor and Maidenhead | BRAMLEY (FLEE) | BRACKNELL MAIN | BRACKNELL
Thames Valley Berkshire | Windsor and Maidenhead | BRAMLEY (FLEE) | BRACKNELL MAIN | WARFIELD
Thames Valley Berkshire | Windsor and Maidenhead | BRAMLEY (FLEE) | BRACKNELL RESERVE | BAGSHOT
Thames Valley Berkshire | Windsor and Maidenhead | BRAMLEY (FLEE) | BRACKNELL RESERVE | CHOBHAM
Thames Valley Berkshire | Windsor and Maidenhead | BRAMLEY (FLEE) | BRACKNELL RESERVE | M V E E
Thames Valley Berkshire | Windsor and Maidenhead | BRAMLEY (FLEE) | BRACKNELL RESERVE | SUNNINGHILL
Thames Valley Berkshire | Windsor and Maidenhead | BRAMLEY (FLEE) | MAIDENHEAD BSP | BRAYWICK ROAD
Thames Valley Berkshire | Windsor and Maidenhead | BRAMLEY (FLEE) | MAIDENHEAD BSP | CORDWALLIS
Thames Valley Berkshire | Windsor and Maidenhead | BRAMLEY (FLEE) | MAIDENHEAD BSP | KNOWL HILL
Thames Valley Berkshire | Windsor and Maidenhead | BRAMLEY (FLEE) | MAIDENHEAD BSP | MAIDENHEAD
Thames Valley Berkshire | Windsor and Maidenhead | BRAMLEY (FLEE) | MAIDENHEAD BSP | TEMPLE FARM
Thames Valley Berkshire | Windsor and Maidenhead | BRAMLEY (FLEE) | READING BSP | HENLEY
Thames Valley Berkshire | Windsor and Maidenhead | BRAMLEY (FLEE) | READING BSP | TWYFORD
Thames Valley Berkshire | Windsor and Maidenhead | COWLEY GSP | HIGH WYCOMBE BSP | CHISBRIDGE
Thames Valley Berkshire | Windsor and Maidenhead | COWLEY GSP | HIGH WYCOMBE BSP | LITTLE MARLOW
Thames Valley Berkshire | Windsor and Maidenhead | IVER 132KV | CHALVEY BSP | CHALVEY
Thames Valley Berkshire | Windsor and Maidenhead | IVER 132KV | CIPPENHAM | CLARENCE ROAD
Thames Valley Berkshire | Windsor and Maidenhead | IVER 132KV | LONGFORD | POYLE
Thames Valley Berkshire | Windsor and Maidenhead | IVER 132KV | SLOUGH | TAPLOW
Thames Valley Berkshire | Windsor and Maidenhead | IVER 132KV | UPTON BSP | SUTTON LANE
Thames Valley Berkshire | Windsor and Maidenhead | IVER 132KV | UPTON BSP | UPTON
Thames Valley Berkshire | Windsor and Maidenhead | LALEHAM | STAINES | CAUSEWAY
Thames Valley Berkshire | Windsor and Maidenhead | LALEHAM | STAINES | EGHAM
Thames Valley Berkshire | Wokingham | BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | ARBORFIELD
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | BRACKNELL MAIN | BRACKNELL
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | BURGHFIELD MAIN | COURAGES
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | BURGHFIELD RESERVE | TRASH GREEN
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | CAMBERLEY MAIN | CROWTHORNE
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | CAMBERLEY MAIN | SANDHURST
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | COXMOOR WOOD BSP | HITCHES LANE
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | MAIDENHEAD BSP | KNOWL HILL
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | MAIDENHEAD BSP | TEMPLE FARM
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | READING BSP | HENLEY
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | READING BSP | LITTLE HUNGERFORD
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | READING BSP | NORTHUMBERLAND AVENUE
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | READING BSP | READING
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | READING BSP | SILVER STREET
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | READING BSP | TWYFORD
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | WOKINGHAM BSP | ELMS ROAD
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | WOKINGHAM BSP | WOKINGHAM
Thames Valley Berkshire | Wokingham | COWLEY GSP | HIGH WYCOMBE BSP | CHISBRIDGE
Thames Valley Berkshire | Wokingham | MINETY GSP | CIRENCESTER BSP | WHITEWAY
West of England | Bath and North East Somerset | MELKSHAM GSP | NORRINGTON | BRADFORD-ON-AVON
West of England | Bath and North East Somerset | MELKSHAM GSP | NORRINGTON | SPRING QUARRY WEST
West of England | South Gloucestershire | MELKSHAM GSP | CHIPPENHAM | ALDERTON
West of England | South Gloucestershire | MELKSHAM GSP | NORRINGTON | SPRING QUARRY WEST
| Data Centre ESA | BRAMLEY (FLEE) | READING BSP | HENLEY
Solent | Portsmouth | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | BROCKHURST
Solent | Southampton | FAWLEY GSP | LANGLEY BSP | BUTTS ASH
| BSP ESA | MELKSHAM GSP | FROME BSP | FROME
| BSP ESA | COWLEY GSP | HEADINGTON BSP | HEADINGTON
Oxfordshire LEP | Cherwell | LALEHAM | EAST BEDFONT A | NORTH FELTHAM
Oxfordshire LEP | Cherwell | COWLEY GSP | COWLEY LOCAL (2 X 90) | ROSE HILL
Oxfordshire LEP | Cherwell | COWLEY GSP | WITNEY BSP | WINDRUSH PARK

## EISD
| GSPs in November 2022 LTDS | Demand |  | Generation |  | Comments (optional)
|  | EISD | Under review at freeze date? | EISD | Under review at freeze date?
| Acton Lane | 2037 | Under active review | 2037 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Amersham Main | 2037 | Under active review | 2037 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Axminster | 2036 | Under active review | 2036 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Botley Wood | 2036 | Under active review | 2036 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Bramley | 2036 | Under active review | 2036 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Chickerell | 2036 | Under active review | 2036 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Cowley | 2029 | Under active review | 2029 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Ealing | 2037 | Under active review | 2037 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| East Claydon | 2034 | Under active review | 2034 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Fawley | 2036 | Under active review | 2036 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Fleet | 2036 | Under active review | 2036 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Iver | 2037 | Under active review | 2037 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Laleham | 2037 | Under active review | 2037 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Lovedean | 2036 | Under active review | 2036 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Mannington | 2036 | Under active review | 2036 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Melksham | 2036 | Under active review | 2036 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Minety | 2036 | Under active review | 2036 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| North Hyde | 2037 | Under active review | 2037 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Nursling | 2036 | Under active review | 2036 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Tynemouth | 2032 | Under active review | 2032 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Willesden | 2037 | Under active review | 2037 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
Links to additional public-domain information related to the EISDs, provided by the Transmission Owner
https://www.nationalgrid.com/electricity-transmission/connections/regional-customer-connections-update
2023-01-31 | Transmission Owner's freeze date
Southern Electric Power Distribution | DNO Licence area
NGET | Transmision Owner providing
2023-03-01 | Last update (version, date)
Notes
1 Earliest in service dates (EISDs) represent a snapshot of the Transmission Owner's view at the 'freeze date' of the earliest date for connection for NEW applications for demand and generation of significant size (>1MW)
For customers which already have accepted connections with a DNO, DNOs may already have agreed with transmission for earlier connection dates for demand and generation customers
2 For storage, both the demand and generation EISDs may be relevant.
3 Where an EISD has not been established for a GSP, this is shown as N/A.
There is likely to be some headroom for connection because there is no constraint yet defined with defined construction works affecting connnection, this is shown as "no date restriction identified".
4 Where the tranmission owner is actively reviewing construction works and earliest in service dates for new applications may be revised e.g. due to an application for capacity affecting that GSP, this is shown as "under active review"
5 The EISDs reflect both works at a Grid Supply Point and in wider tranmission network.
6 Unlike the rest of the DNO Network Scenario Headroom Reports, this is a snapshot of current status based on connection applications, not a scenario based output.
7 The list of GSPs includes at a minimum the GSPs associated with the primary substations and Bulk Supply Points in the DNO's last Long Term Development Statement Table 3. Future new GSPs may not be included.