## Contents
SHEPD Network Scenario Headroom Report 2024 Summary
Our Network Scenario Headroom Report (NSHR) is published to enable customers, developers, generators, local authorities and other interested third parties to view the possible headroom capacity at our Primary Substations up to 2050. SHEPD have used the latest Distribution Future Energy Scenarios (DFES) data to inform four scenarios of demand and generation forecasts. SSEN's best view of the future demand and generation needs on our network is aligned to the Customer Transformation scenario. Although the NSHR provides a view of the future in terms of our potential available capacity and constraints on our network, we would encourage any party using this information in their decision-making process to engage with us ahead of making an application to connect or offer flexible services. Please note version 1.0 of the 2024 Network Scenario Headroom Report is subject to change before the final version is released. Updated DFES projections have yet to be finalised so the headroom calculations in version 1.0 have been based on last year's DFES. Headroom estimations, including new additions to the DFES, will be updated in the final release on the 1st of May.
Network Headroom Report Contents
Tab | Description
Key Information | This tab provides some additional detail to assist users with how to read the data presented within this report.
Primary Headroom Dem | This tab provides the demand headroom capacity at each of our Primary substations, grid references, connectivity upto the Grid Supply Point and upstream constraints.
Primary Headroom Gen | This tab provides the generation headroom capacity at each of our Primary substations, grid references, connectivity upto the Grid Supply Point and upstream constraints.
Local Authority Reference | This tab provides information on the local authorities and the Primaries that support those areas
EISD | To indicate potential transmission constraints by 'Earliest in Service Date' per Grid Supply Point (GSP)
March 2024
Version 1.0

## Key Information
SHEPD Network Scenario Headroom Report 2024 Key Information
Our Network Scenario Headroom Report (NSHR) has been developed to be used in conjunction with our others documents that combine to make the full Network Development Plan; the other documents to reference are the Network Development Plan Methodology & Assumptions and Network Development Report. The capacity that demand and generation growth is measured against is the firm capacity of the primary substation or BSP as per our Load Indices submission to Ofgem and as indicated by our Long Term Development Statement. Firm capacity means the available capacity on the network with a single feed on outage; for instance a twin transformer sites firm capacity would be the lowest capacity available on a single transformer. For single transformer sites, the firm capacity is based on the backfeed supply available to restore supplies; this may be limited by the backfeed circuit capacity rather than the transformer providing the backfeed. Where the capacity is shown as 0 MVA, this signifies that there may be no alternative supplies to restore power to these sites. When reviewing the headroom reports for demand and generation the following applies: GREEN and POSTIVE VALUES = Capacity is forecast to be available RED and NEGATIVE VALUES = There are constraints forecast It must be noted that forecasts in RED do not mean that connections cannot be made; there are opportunities through flexible services that can enable connections without triggering network reinforcement. We would encourage any developer, generator or customer to contact us to discuss their connection and available opportuinites to connect. The data shown within this NSHR is used by us to identify long term investment opportunities where there are constraints highlighted. As the forecast is scenario based, these constraints are subject to change and will be reviewed and published annually by SHEPD.
`
March 2024
Version 1.0

## Primary Headroom Dem
#VALUE! | Grid Supply Point | Primary Substation | Scenario | Grid Reference | Single Transformer Site (YES/NO) | Upstream Constraint (YES / NO) | Demand Headroom Winter MVA | [13 empty] | Demand Headroom Summer MVA | [13 empty] | Demand Headroom Spring/Autumn MVA
[7 empty] | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050
| FORT AUGUSTUS | ABERCHALDER | MINIMUM HEADROOM | NH 33843 03575 | YES | YES | 0.1855 | 0.18071 | 0.15412 | 0.12592 | 0.10867 | 0.057268 | 0.042322 | -0.00031123 | -0.020938 | -0.035363 | -0.057256 | -0.16494 | -0.30179 | -0.43598 | 0.18744 | 0.1853 | 0.14649 | 0.11624 | 0.096626 | 0.032614 | 0.014239 | -0.035566 | -0.055628 | -0.072094 | -0.098505 | -0.22412 | -0.38775 | -0.55072 | 0.17128 | 0.16709 | 0.13131 | 0.098386 | 0.077749 | 0.013637 | -0.0048639 | -0.056511 | -0.0797 | -0.096918 | -0.12423 | -0.25591 | -0.42284 | -0.58767
|  | ABERCHALDER | CT |  |  |  | 0.1894 | 0.18669 | 0.17729 | 0.16658 | 0.11976 | 0.077779 | 0.066941 | 0.048154 | 0.023169 | 0.0063237 | -0.013937 | -0.10955 | -0.2006 | -0.29228 | 0.18879 | 0.18744 | 0.17965 | 0.1684 | 0.1185 | 0.068092 | 0.054881 | 0.031492 | 0.0065363 | -0.014199 | -0.038182 | -0.15647 | -0.26198 | -0.37428 | 0.17456 | 0.17215 | 0.16227 | 0.14986 | 0.095274 | 0.043757 | 0.030455 | 0.0070583 | -0.021244 | -0.042035 | -0.066388 | -0.18709 | -0.29588 | -0.40914
|  | ABERCHALDER | LW |  |  |  | 0.1855 | 0.18071 | 0.17653 | 0.17371 | 0.17101 | 0.16372 | 0.16047 | 0.14975 | 0.14054 | 0.13057 | 0.11941 | 0.074091 | -0.082677 | -0.30966 | 0.18744 | 0.1853 | 0.18346 | 0.18203 | 0.18071 | 0.17742 | 0.17541 | 0.16357 | 0.15101 | 0.13938 | 0.12714 | 0.076351 | -0.11678 | -0.39892 | 0.17128 | 0.16709 | 0.16343 | 0.16088 | 0.15844 | 0.15189 | 0.14887 | 0.13653 | 0.12407 | 0.11112 | 0.097478 | 0.043769 | -0.15053 | -0.43324
|  | ABERCHALDER | ST |  |  |  | 0.19166 | 0.18752 | 0.15412 | 0.12592 | 0.10867 | 0.057268 | 0.042322 | -0.00031123 | -0.020938 | -0.035363 | -0.057256 | -0.16494 | -0.30179 | -0.43598 | 0.18972 | 0.18811 | 0.14649 | 0.11624 | 0.096626 | 0.032614 | 0.014239 | -0.035566 | -0.055628 | -0.072094 | -0.098505 | -0.22412 | -0.38775 | -0.55072 | 0.1765 | 0.17298 | 0.13131 | 0.098386 | 0.077749 | 0.013637 | -0.0048639 | -0.056511 | -0.0797 | -0.096918 | -0.12423 | -0.25591 | -0.42284 | -0.58767
|  | ABERCHALDER | FS |  |  |  | 0.19362 | 0.18956 | 0.18253 | 0.17347 | 0.16326 | 0.15491 | 0.14415 | 0.12773 | 0.11564 | 0.10151 | 0.089215 | 0.054424 | 0.036629 | 0.01199 | 0.19044 | 0.18886 | 0.18016 | 0.17071 | 0.15982 | 0.14954 | 0.13937 | 0.12082 | 0.10773 | 0.09387 | 0.08059 | 0.052823 | 0.032189 | 0.0071648 | 0.17817 | 0.17471 | 0.16597 | 0.15553 | 0.14365 | 0.13332 | 0.12141 | 0.10182 | 0.08767 | 0.071794 | 0.057427 | 0.021008 | -0.0010546 | -0.02886
| TUMMEL BRIDGE | ABERFELDY | MINIMUM HEADROOM | NN 84889 48876 | NO | YES | 3.8234 | 3.6043 | 3.2826 | 2.9508 | 2.6134 | 2.2038 | 1.8034 | 1.4481 | 1.0729 | 0.74258 | 0.50745 | -0.05773 | -0.35979 | -0.56529 | 4.3219 | 4.1786 | 4.0139 | 3.836 | 3.6384 | 3.3965 | 3.1623 | 2.9392 | 2.6985 | 2.5055 | 2.3594 | 2.021 | 1.7772 | 1.5681 | 3.3616 | 3.1563 | 2.8906 | 2.5989 | 2.3007 | 1.9356 | 1.576 | 1.2534 | 0.91137 | 0.61126 | 0.38892 | -0.13363 | -0.40487 | -0.5916
|  | ABERFELDY | CT |  |  |  | 3.8461 | 3.68 | 3.4455 | 3.0796 | 2.7383 | 2.3752 | 2.0264 | 1.6873 | 1.3043 | 0.97511 | 0.7255 | 0.03291 | -0.35979 | -0.56529 | 4.3702 | 4.2463 | 4.0587 | 3.8496 | 3.6608 | 3.4422 | 3.2415 | 3.0316 | 2.7876 | 2.5979 | 2.4461 | 2.021 | 1.7772 | 1.5681 | 3.4583 | 3.2959 | 3.0134 | 2.7001 | 2.3947 | 2.0715 | 1.7626 | 1.4581 | 1.1109 | 0.81421 | 0.58209 | -0.053963 | -0.40487 | -0.5916
|  | ABERFELDY | LW |  |  |  | 3.8234 | 3.6043 | 3.2826 | 2.9508 | 2.6134 | 2.2038 | 1.8034 | 1.4481 | 1.0729 | 0.74258 | 0.50745 | -0.05773 | -0.27739 | -0.39649 | 4.3219 | 4.1786 | 4.0139 | 3.836 | 3.6384 | 3.3965 | 3.1623 | 2.9392 | 2.6985 | 2.5055 | 2.3594 | 2.0278 | 1.9053 | 1.8161 | 3.3616 | 3.1563 | 2.8906 | 2.5989 | 2.3007 | 1.9356 | 1.576 | 1.2534 | 0.91137 | 0.61126 | 0.38892 | -0.13363 | -0.33595 | -0.4559
|  | ABERFELDY | ST |  |  |  | 3.8857 | 3.7834 | 3.6645 | 3.5244 | 3.3763 | 3.2145 | 3.0674 | 2.8632 | 2.6266 | 2.4373 | 2.2813 | 1.4345 | 1.0433 | 0.69382 | 4.405 | 4.3196 | 4.2186 | 4.1015 | 3.9797 | 3.8431 | 3.7208 | 3.578 | 3.4126 | 3.2866 | 3.1695 | 2.5572 | 2.306 | 2.0536 | 3.5247 | 3.4164 | 3.2903 | 3.1495 | 3.0013 | 2.8334 | 2.6788 | 2.4982 | 2.289 | 2.1204 | 1.9725 | 1.1742 | 0.82119 | 0.50855
|  | ABERFELDY | FS |  |  |  | 3.9222 | 3.8423 | 3.7481 | 3.6349 | 3.5191 | 3.3983 | 3.2526 | 3.0724 | 2.8745 | 2.7056 | 2.572 | 1.7366 | 1.0161 | 0.62507 | 4.4313 | 4.3634 | 4.2813 | 4.1843 | 4.0846 | 3.9801 | 3.8756 | 3.7569 | 3.6237 | 3.5149 | 3.4222 | 2.8552 | 2.2972 | 1.8874 | 3.5562 | 3.4715 | 3.3642 | 3.2443 | 3.1181 | 2.9858 | 2.8523 | 2.6999 | 2.5293 | 2.3835 | 2.2627 | 1.4966 | 0.81946 | 0.46691
| STRATHLEVEN | ABERFOYLE | MINIMUM HEADROOM | NS 53215 99705 | YES | YES | 3.6026 | 3.5527 | 3.4819 | 3.4058 | 3.3115 | 3.2108 | 3.1078 | 3.0411 | 2.9795 | 2.8623 | 2.7417 | 2.4268 | 2.249 | 2.1033 | 3.9522 | 3.9054 | 3.858 | 3.7902 | 3.7315 | 3.6691 | 3.5939 | 3.5147 | 3.4285 | 3.3402 | 3.2566 | 3.0687 | 2.9608 | 2.8289 | 3.6421 | 3.5804 | 3.5093 | 3.4365 | 3.3595 | 3.2622 | 3.1677 | 3.1037 | 3.0205 | 2.911 | 2.8047 | 2.5282 | 2.3741 | 2.2513
|  | ABERFOYLE | CT |  |  |  | 3.6026 | 3.5556 | 3.4985 | 3.4058 | 3.3115 | 3.2108 | 3.1078 | 3.0411 | 2.9795 | 2.9178 | 2.8441 | 2.5476 | 2.3109 | 2.1759 | 3.9706 | 3.9302 | 3.8629 | 3.7902 | 3.7315 | 3.6691 | 3.6058 | 3.544 | 3.4669 | 3.3885 | 3.313 | 3.104 | 2.9608 | 2.8289 | 3.6895 | 3.6368 | 3.5464 | 3.453 | 3.3634 | 3.2687 | 3.1729 | 3.1176 | 3.0575 | 2.9847 | 2.8911 | 2.6308 | 2.4199 | 2.3045
|  | ABERFOYLE | LW |  |  |  | 3.6054 | 3.5527 | 3.4819 | 3.4097 | 3.3323 | 3.2342 | 3.1362 | 3.0661 | 2.9868 | 2.8623 | 2.7417 | 2.4268 | 2.249 | 2.1033 | 3.9522 | 3.9054 | 3.858 | 3.8057 | 3.7547 | 3.6775 | 3.5939 | 3.5147 | 3.4285 | 3.3402 | 3.2566 | 3.0687 | 2.9884 | 2.9149 | 3.6421 | 3.5804 | 3.5093 | 3.4365 | 3.3595 | 3.2622 | 3.1677 | 3.1037 | 3.0205 | 2.911 | 2.8047 | 2.5282 | 2.3741 | 2.2513
|  | ABERFOYLE | ST |  |  |  | 3.6248 | 3.6104 | 3.5903 | 3.5657 | 3.5362 | 3.4884 | 3.4331 | 3.3714 | 3.3046 | 3.23 | 3.1507 | 2.7128 | 2.5237 | 2.4354 | 3.9871 | 3.9695 | 3.9444 | 3.9145 | 3.8816 | 3.8446 | 3.8023 | 3.7533 | 3.6971 | 3.6342 | 3.5657 | 3.21 | 3.0611 | 2.9388 | 3.7192 | 3.6949 | 3.6579 | 3.6179 | 3.5754 | 3.5314 | 3.4829 | 3.4273 | 3.3694 | 3.3057 | 3.2394 | 2.8454 | 2.6676 | 2.564
|  | ABERFOYLE | FS |  |  |  | 3.6307 | 3.6202 | 3.6048 | 3.5864 | 3.5649 | 3.5401 | 3.5102 | 3.461 | 3.4119 | 3.3557 | 3.2958 | 2.9031 | 2.5895 | 2.4199 | 3.995 | 3.9803 | 3.9608 | 3.9368 | 3.9109 | 3.8818 | 3.8492 | 3.8112 | 3.7703 | 3.724 | 3.6736 | 3.3451 | 3.0429 | 2.8322 | 3.7379 | 3.7188 | 3.6921 | 3.6602 | 3.6268 | 3.5913 | 3.5527 | 3.5071 | 3.4634 | 3.4128 | 3.3596 | 2.997 | 2.6751 | 2.5379
| KEITH | ABERLOUR | MINIMUM HEADROOM | NJ 24809 40878 | NO | YES | 2.0018 | 1.878 | 1.3241 | 0.73085 | -0.35574 | -1.5215 | -2.3281 | -2.5758 | -2.8395 | -3.0809 | -3.3235 | -4.2891 | -4.6411 | -4.8388 | 2.3242 | 2.2864 | 1.7179 | 1.0861 | -0.16401 | -1.5017 | -2.3753 | -2.6067 | -2.8509 | -3.0695 | -3.301 | -4.3443 | -4.6861 | -4.89 | 2.0488 | 2.0009 | 1.4205 | 0.77888 | -0.48124 | -1.8325 | -2.7196 | -2.9751 | -3.2463 | -3.4916 | -3.747 | -4.8647 | -5.2418 | -5.4586
|  | ABERLOUR | CT |  |  |  | 2.0831 | 1.9914 | 1.7925 | 1.5624 | 0.97658 | 0.35685 | 0.037109 | -0.13069 | -0.31456 | -0.49105 | -0.66389 | -1.257 | -1.5682 | -1.7232 | 2.3273 | 2.2864 | 2.1727 | 2.0138 | 1.3984 | 0.74166 | 0.47917 | 0.35399 | 0.22936 | 0.11549 | -0.012265 | -0.54763 | -0.72044 | -0.8638 | 2.0567 | 2.0043 | 1.8754 | 1.7033 | 1.0762 | 0.40724 | 0.13175 | -0.0046753 | -0.13864 | -0.27536 | -0.42973 | -1.0416 | -1.288 | -1.4168
|  | ABERLOUR | LW |  |  |  | 2.0018 | 1.878 | 1.3241 | 0.73085 | -0.35574 | -1.5215 | -2.3281 | -2.5758 | -2.8395 | -3.0809 | -3.3235 | -4.2891 | -4.6411 | -4.8388 | 2.3242 | 2.288 | 1.7179 | 1.0861 | -0.16401 | -1.5017 | -2.3753 | -2.6067 | -2.8509 | -3.0695 | -3.301 | -4.3443 | -4.6861 | -4.89 | 2.0488 | 2.0009 | 1.4205 | 0.77888 | -0.48124 | -1.8325 | -2.7196 | -2.9751 | -3.2463 | -3.4916 | -3.747 | -4.8647 | -5.2418 | -5.4586
|  | ABERLOUR | ST |  |  |  | 2.1222 | 2.0597 | 1.5842 | 1.2571 | 1.0213 | 0.32161 | 0.010029 | -0.19849 | -0.32834 | -0.45457 | -0.60902 | -1.3915 | -1.7656 | -2.0143 | 2.3389 | 2.3221 | 1.7814 | 1.4122 | 1.1604 | 0.33176 | 0.013349 | -0.19853 | -0.30238 | -0.40192 | -0.53709 | -1.1918 | -1.4707 | -1.6093 | 2.0739 | 2.0503 | 1.5046 | 1.1309 | 0.87375 | 0.038845 | -0.28701 | -0.50684 | -0.62036 | -0.73061 | -0.87774 | -1.598 | -1.909 | -2.1084
|  | ABERLOUR | FS |  |  |  | 2.1466 | 2.1008 | 1.9689 | 1.8414 | 1.7011 | 1.5548 | 1.3761 | 1.2627 | 1.1582 | 1.0534 | 0.94363 | 0.42039 | 0.026849 | -0.15449 | 2.3419 | 2.3289 | 2.2088 | 2.0906 | 1.9529 | 1.8133 | 1.6383 | 1.5529 | 1.4831 | 1.4107 | 1.3376 | 1.0903 | 0.86935 | 0.74156 | 2.0809 | 2.0608 | 1.936 | 1.814 | 1.6722 | 1.5279 | 1.3483 | 1.2567 | 1.1801 | 1.1005 | 1.0193 | 0.71889 | 0.42644 | 0.22818
| ABERNETHY | ABERNETHY | MINIMUM HEADROOM | NO 20094 17132 | YES | YES | 1.1728 | 1.1066 | 1.043 | 0.93763 | 0.86092 | 0.74238 | 0.65847 | 0.58567 | 0.51001 | 0.43887 | 0.35935 | 0.058623 | -0.42806 | -1.2417 | 1.2723 | 1.2349 | 1.1948 | 1.1297 | 1.0517 | 0.96326 | 0.91789 | 0.83818 | 0.77852 | 0.72274 | 0.64175 | 0.26276 | -0.30895 | -1.1847 | 1.2412 | 1.1871 | 1.1306 | 1.0357 | 0.94577 | 0.82372 | 0.74506 | 0.66489 | 0.58167 | 0.50448 | 0.41854 | 0.075557 | -0.51644 | -1.4942
|  | ABERNETHY | CT |  |  |  | 1.2165 | 1.1658 | 1.076 | 0.97744 | 0.86092 | 0.74238 | 0.65847 | 0.58567 | 0.51001 | 0.43887 | 0.35935 | 0.058623 | -0.32153 | -0.67457 | 1.28 | 1.2447 | 1.195 | 1.1366 | 1.0517 | 0.96326 | 0.91789 | 0.84922 | 0.78275 | 0.72274 | 0.64872 | 0.32876 | -0.047241 | -0.45135 | 1.261 | 1.2157 | 1.1457 | 1.0647 | 0.94577 | 0.82372 | 0.74506 | 0.66489 | 0.58167 | 0.50448 | 0.41854 | 0.075557 | -0.35721 | -0.78206
|  | ABERNETHY | LW |  |  |  | 1.1728 | 1.1066 | 1.043 | 0.93763 | 0.88044 | 0.81192 | 0.74347 | 0.67149 | 0.59625 | 0.52609 | 0.45419 | 0.1756 | -0.42806 | -1.2417 | 1.2723 | 1.2349 | 1.2047 | 1.1297 | 1.1054 | 1.0749 | 1.043 | 0.97817 | 0.91001 | 0.84852 | 0.78381 | 0.50818 | -0.19596 | -1.1847 | 1.2412 | 1.1871 | 1.1306 | 1.0357 | 0.98527 | 0.92396 | 0.86238 | 0.78477 | 0.70355 | 0.62909 | 0.55204 | 0.24247 | -0.48887 | -1.4942
|  | ABERNETHY | ST |  |  |  | 1.2482 | 1.2111 | 1.1321 | 1.0623 | 1.0119 | 0.91946 | 0.86976 | 0.74739 | 0.67714 | 0.6109 | 0.52371 | 0.11801 | -0.40174 | -0.9174 | 1.2942 | 1.2673 | 1.1948 | 1.1314 | 1.0947 | 1.0039 | 0.96666 | 0.83818 | 0.77852 | 0.72339 | 0.64175 | 0.26276 | -0.30895 | -0.89541 | 1.2841 | 1.2523 | 1.1723 | 1.1021 | 1.0568 | 0.95671 | 0.90979 | 0.77144 | 0.69997 | 0.63221 | 0.53777 | 0.089905 | -0.51644 | -1.1282
|  | ABERNETHY | FS |  |  |  | 1.3325 | 1.3021 | 1.2563 | 1.215 | 1.1728 | 1.1304 | 1.0836 | 1.0102 | 0.94793 | 0.88298 | 0.8081 | 0.51391 | 0.34672 | 0.22961 | 1.3734 | 1.3491 | 1.3182 | 1.2885 | 1.2568 | 1.2248 | 1.1921 | 1.128 | 1.0765 | 1.0238 | 0.96076 | 0.78419 | 0.67476 | 0.56539 | 1.3656 | 1.338 | 1.3001 | 1.2641 | 1.226 | 1.1871 | 1.1462 | 1.0734 | 1.0113 | 0.94518 | 0.86997 | 0.59602 | 0.43578 | 0.31387
| TARLAND | ABOYNE | MINIMUM HEADROOM | NO 52048 98716 | NO | YES | 7.1468 | 6.735 | 6.2918 | 5.8233 | 5.3685 | 4.7423 | 4.0553 | 3.6886 | 3.356 | 3.0184 | 2.6721 | 1.802 | 1.0348 | 0.63615 | 9.1903 | 9.0062 | 8.8154 | 8.6027 | 8.3087 | 7.9678 | 7.599 | 7.3353 | 7.1153 | 6.8954 | 6.6747 | 6.0259 | 5.448 | 4.9834 | 8.1447 | 7.828 | 7.4981 | 7.1511 | 6.712 | 6.1783 | 5.6028 | 5.2546 | 4.9997 | 4.7453 | 4.4468 | 3.6302 | 2.9014 | 2.5399
|  | ABOYNE | CT |  |  |  | 7.4903 | 7.1908 | 6.5995 | 5.9867 | 5.3867 | 4.7423 | 4.0553 | 3.6886 | 3.356 | 3.0211 | 2.6909 | 1.9237 | 1.0348 | 0.63615 | 9.3083 | 9.1582 | 8.8871 | 8.6027 | 8.3087 | 7.9678 | 7.599 | 7.3353 | 7.1153 | 6.8954 | 6.6747 | 6.0259 | 5.448 | 4.9834 | 8.3771 | 8.1176 | 7.6594 | 7.2004 | 6.712 | 6.1783 | 5.6028 | 5.2546 | 4.9997 | 4.7453 | 4.4468 | 3.6302 | 2.9014 | 2.5399
|  | ABOYNE | LW |  |  |  | 7.1468 | 6.735 | 6.2918 | 5.8233 | 5.3685 | 4.7948 | 4.1292 | 3.7199 | 3.3799 | 3.0184 | 2.6721 | 1.802 | 1.2364 | 0.81909 | 9.1903 | 9.0062 | 8.8154 | 8.6101 | 8.4123 | 8.12 | 7.7456 | 7.4665 | 7.2539 | 7.0273 | 6.8091 | 6.2272 | 5.8315 | 5.4619 | 8.1447 | 7.828 | 7.4981 | 7.1511 | 6.8045 | 6.3616 | 5.8279 | 5.4734 | 5.1875 | 4.8499 | 4.5192 | 3.6988 | 3.1421 | 2.6949
|  | ABOYNE | ST |  |  |  | 7.7724 | 7.6187 | 7.3841 | 7.1414 | 6.8984 | 6.5737 | 6.2029 | 5.7923 | 5.4519 | 5.0854 | 4.6962 | 2.8477 | 1.8998 | 1.2974 | 9.4307 | 9.3597 | 9.226 | 9.0936 | 8.9638 | 8.7409 | 8.4931 | 8.2102 | 8.0059 | 7.785 | 7.5426 | 6.2998 | 5.6375 | 5.0982 | 8.6119 | 8.4882 | 8.2858 | 8.0822 | 7.8761 | 7.5785 | 7.2438 | 6.8678 | 6.5666 | 6.2395 | 5.8839 | 4.1017 | 3.1488 | 2.6
|  | ABOYNE | FS |  |  |  | 7.8877 | 7.7798 | 7.6004 | 7.4093 | 7.2102 | 6.9842 | 6.7032 | 6.3734 | 6.0908 | 5.7874 | 5.4822 | 3.4604 | 2.0728 | 1.3871 | 9.4763 | 9.4246 | 9.3388 | 9.2451 | 9.1454 | 9.0174 | 8.8356 | 8.6324 | 8.4751 | 8.3038 | 8.1282 | 7.0119 | 5.9786 | 5.1978 | 8.7 | 8.6135 | 8.4672 | 8.3128 | 8.1486 | 7.9586 | 7.7119 | 7.4266 | 7.1895 | 6.9343 | 6.6744 | 4.9772 | 3.7155 | 2.9279
| GRUDIE BRIDGE | ACHILTIBUIE | MINIMUM HEADROOM | NC 01618 09557 | YES | YES | 0.27909 | 0.25843 | 0.23847 | 0.2138 | 0.19218 | 0.16467 | 0.13433 | 0.11225 | 0.085364 | 0.061136 | 0.036131 | -0.0032242 | -0.024093 | -0.036259 | 0.33014 | 0.31862 | 0.3081 | 0.29308 | 0.28128 | 0.26765 | 0.24861 | 0.2308 | 0.21061 | 0.19106 | 0.17238 | 0.14621 | 0.13173 | 0.1191 | 0.66682 | 0.65252 | 0.63883 | 0.62221 | 0.60603 | 0.58834 | 0.56521 | 0.54611 | 0.51995 | 0.49523 | 0.47064 | 0.43476 | 0.41747 | 0.40635
|  | ACHILTIBUIE | CT |  |  |  | 0.29129 | 0.27655 | 0.24956 | 0.21816 | 0.19553 | 0.17156 | 0.14506 | 0.12348 | 0.10022 | 0.076415 | 0.054388 | 0.010071 | -0.024093 | -0.036259 | 0.3345 | 0.32584 | 0.31048 | 0.29308 | 0.28128 | 0.26879 | 0.25547 | 0.24046 | 0.22137 | 0.20181 | 0.18468 | 0.14939 | 0.13173 | 0.1191 | 0.67558 | 0.66491 | 0.64675 | 0.62733 | 0.61109 | 0.59407 | 0.57433 | 0.55648 | 0.53549 | 0.51091 | 0.48903 | 0.44563 | 0.41747 | 0.40635
|  | ACHILTIBUIE | LW |  |  |  | 0.27909 | 0.25843 | 0.23847 | 0.2138 | 0.19218 | 0.16467 | 0.13433 | 0.11225 | 0.085364 | 0.061136 | 0.036131 | -0.0032242 | -0.02158 | -0.025575 | 0.33014 | 0.31862 | 0.3081 | 0.29521 | 0.28437 | 0.26765 | 0.24861 | 0.2308 | 0.21061 | 0.19106 | 0.17238 | 0.14621 | 0.13917 | 0.13782 | 0.66682 | 0.65252 | 0.63883 | 0.62221 | 0.60603 | 0.58834 | 0.56521 | 0.54611 | 0.51995 | 0.49523 | 0.47064 | 0.43476 | 0.41944 | 0.41598
|  | ACHILTIBUIE | ST |  |  |  | 0.29998 | 0.29142 | 0.28264 | 0.2738 | 0.26274 | 0.24898 | 0.23505 | 0.2211 | 0.20301 | 0.18168 | 0.1613 | 0.05115 | 0.015728 | -0.0020222 | 0.33839 | 0.33412 | 0.32927 | 0.32374 | 0.31717 | 0.30903 | 0.3001 | 0.29008 | 0.27752 | 0.2629 | 0.24774 | 0.16748 | 0.14547 | 0.1329 | 0.68333 | 0.67666 | 0.67047 | 0.66465 | 0.65681 | 0.64731 | 0.63787 | 0.62917 | 0.61779 | 0.60085 | 0.58321 | 0.47812 | 0.4497 | 0.43706
|  | ACHILTIBUIE | FS |  |  |  | 0.30522 | 0.29921 | 0.29043 | 0.28143 | 0.27182 | 0.26272 | 0.2483 | 0.23563 | 0.22488 | 0.20822 | 0.19255 | 0.081701 | 0.0020021 | -0.013023 | 0.34033 | 0.33708 | 0.33265 | 0.3276 | 0.32227 | 0.31666 | 0.30878 | 0.3009 | 0.29302 | 0.28264 | 0.27196 | 0.19999 | 0.14073 | 0.1251 | 0.68444 | 0.68295 | 0.67624 | 0.67016 | 0.66332 | 0.65694 | 0.64684 | 0.63858 | 0.63198 | 0.6212 | 0.60945 | 0.51488 | 0.43956 | 0.42738
| BEAULY | AIGAS | MINIMUM HEADROOM | NH 45362 40529 | YES | YES | 0.45662 | 0.44815 | 0.43675 | 0.42535 | 0.40529 | 0.38428 | 0.37053 | 0.35625 | 0.34556 | 0.32569 | 0.31031 | 0.27143 | 0.234 | 0.19952 | 0.47332 | 0.46826 | 0.46244 | 0.4532 | 0.43683 | 0.42025 | 0.41125 | 0.39909 | 0.38638 | 0.37113 | 0.35799 | 0.31392 | 0.26963 | 0.22851 | 0.44817 | 0.44023 | 0.42982 | 0.41932 | 0.3973 | 0.37567 | 0.36234 | 0.34707 | 0.33372 | 0.31381 | 0.29795 | 0.25521 | 0.20942 | 0.16981
|  | AIGAS | CT |  |  |  | 0.46592 | 0.46053 | 0.44118 | 0.4275 | 0.40529 | 0.38428 | 0.37053 | 0.35625 | 0.34556 | 0.32569 | 0.31031 | 0.27143 | 0.23445 | 0.21101 | 0.47669 | 0.47303 | 0.46244 | 0.4532 | 0.43683 | 0.42025 | 0.41125 | 0.39909 | 0.38638 | 0.37113 | 0.35799 | 0.31814 | 0.2856 | 0.25457 | 0.45637 | 0.45124 | 0.43329 | 0.41964 | 0.3973 | 0.37567 | 0.36234 | 0.34707 | 0.33372 | 0.31381 | 0.29795 | 0.25521 | 0.21648 | 0.18922
|  | AIGAS | LW |  |  |  | 0.45662 | 0.44815 | 0.43675 | 0.42535 | 0.41259 | 0.39846 | 0.38568 | 0.37088 | 0.35792 | 0.343 | 0.32912 | 0.30077 | 0.26199 | 0.21446 | 0.47332 | 0.46826 | 0.46246 | 0.45635 | 0.45013 | 0.44172 | 0.43259 | 0.42085 | 0.40948 | 0.39774 | 0.38676 | 0.36433 | 0.32316 | 0.26692 | 0.44817 | 0.44023 | 0.42982 | 0.41932 | 0.40773 | 0.39453 | 0.38166 | 0.36609 | 0.35229 | 0.33738 | 0.32347 | 0.29454 | 0.2493 | 0.1913
|  | AIGAS | ST |  |  |  | 0.46891 | 0.46774 | 0.45406 | 0.44336 | 0.43461 | 0.41782 | 0.41237 | 0.39308 | 0.38455 | 0.36848 | 0.35173 | 0.27764 | 0.234 | 0.19952 | 0.47828 | 0.47716 | 0.46558 | 0.45665 | 0.44961 | 0.43315 | 0.42682 | 0.41066 | 0.40182 | 0.39028 | 0.37696 | 0.31392 | 0.26963 | 0.22851 | 0.45911 | 0.45795 | 0.44336 | 0.43209 | 0.42306 | 0.40424 | 0.39735 | 0.37699 | 0.36708 | 0.35101 | 0.3339 | 0.25761 | 0.20942 | 0.16981
|  | AIGAS | FS |  |  |  | 0.46947 | 0.46963 | 0.46511 | 0.45798 | 0.44756 | 0.44342 | 0.43568 | 0.42752 | 0.41826 | 0.4047 | 0.39771 | 0.33713 | 0.29442 | 0.28445 | 0.47854 | 0.47797 | 0.47443 | 0.46973 | 0.46356 | 0.4595 | 0.4541 | 0.44711 | 0.44009 | 0.43115 | 0.42409 | 0.38246 | 0.34819 | 0.3326 | 0.45963 | 0.45966 | 0.45505 | 0.44809 | 0.4382 | 0.43363 | 0.42597 | 0.41712 | 0.40759 | 0.39448 | 0.38649 | 0.328 | 0.28658 | 0.27665
| ARDMORE | AIRD | MINIMUM HEADROOM | NF 79163 53853 | NO | YES | 4.7631 | 4.7065 | 4.6335 | 4.5566 | 4.4729 | 4.3822 | 4.2679 | 4.1725 | 4.0654 | 3.9563 | 3.8573 | 3.6808 | 3.6481 | 3.6004 | 5.7177 | 5.6855 | 5.6422 | 5.5975 | 5.5514 | 5.49 | 5.429 | 5.3698 | 5.2917 | 5.2104 | 5.1351 | 4.982 | 4.8868 | 4.8661 | 4.4218 | 4.3746 | 4.3092 | 4.2437 | 4.1709 | 4.0837 | 4.0012 | 3.9335 | 3.856 | 3.7768 | 3.6864 | 3.4932 | 3.3952 | 3.3588
|  | AIRD | CT |  |  |  | 4.807 | 4.757 | 4.657 | 4.5572 | 4.4729 | 4.3822 | 4.3025 | 4.2363 | 4.1547 | 4.0685 | 3.9864 | 3.7893 | 3.7267 | 3.702 | 5.7488 | 5.7099 | 5.6502 | 5.6028 | 5.5514 | 5.49 | 5.445 | 5.4051 | 5.3665 | 5.3224 | 5.264 | 5.0875 | 5.0663 | 5.0582 | 4.4644 | 4.4146 | 4.325 | 4.2498 | 4.1709 | 4.0837 | 4.0098 | 3.961 | 3.9198 | 3.8767 | 3.82 | 3.6264 | 3.5856 | 3.5699
|  | AIRD | LW |  |  |  | 4.7631 | 4.7065 | 4.6335 | 4.5566 | 4.4907 | 4.3824 | 4.2679 | 4.1725 | 4.0654 | 3.9563 | 3.8573 | 3.6808 | 3.6481 | 3.6004 | 5.7177 | 5.6855 | 5.6422 | 5.5975 | 5.5613 | 5.4909 | 5.429 | 5.3698 | 5.2917 | 5.2104 | 5.1351 | 4.982 | 4.9693 | 4.9584 | 4.4218 | 4.3746 | 4.3092 | 4.2437 | 4.1844 | 4.092 | 4.0012 | 3.9335 | 3.856 | 3.7768 | 3.6864 | 3.4932 | 3.468 | 3.4524
|  | AIRD | ST |  |  |  | 4.8342 | 4.8071 | 4.7786 | 4.7414 | 4.701 | 4.6529 | 4.6062 | 4.5507 | 4.4833 | 4.4072 | 4.3231 | 3.8969 | 3.7938 | 3.7614 | 5.7689 | 5.7475 | 5.7244 | 5.6998 | 5.6689 | 5.6275 | 5.597 | 5.5602 | 5.5148 | 5.4522 | 5.3816 | 5.002 | 4.8868 | 4.8661 | 4.4956 | 4.4687 | 4.4406 | 4.4067 | 4.3677 | 4.3206 | 4.2789 | 4.2297 | 4.1709 | 4.1039 | 4.028 | 3.549 | 3.3952 | 3.3588
|  | AIRD | FS |  |  |  | 4.8766 | 4.8518 | 4.8231 | 4.7971 | 4.7643 | 4.7222 | 4.6848 | 4.6385 | 4.5883 | 4.5363 | 4.4753 | 4.0919 | 3.8034 | 3.7157 | 5.8145 | 5.7949 | 5.7731 | 5.7551 | 5.7336 | 5.7 | 5.6746 | 5.6444 | 5.6114 | 5.5771 | 5.5379 | 5.2492 | 5.0131 | 4.8767 | 4.5431 | 4.5183 | 4.4901 | 4.4659 | 4.4352 | 4.3939 | 4.3605 | 4.3196 | 4.2756 | 4.2312 | 4.1789 | 3.84 | 3.5401 | 3.3659
| PORT ANN | AIRIGH-NA-BRODAIG | MINIMUM HEADROOM | NR 85849 74792 | YES | YES | 0.31782 | 0.31858 | 0.31544 | 0.30983 | 0.29914 | 0.29209 | 0.28939 | 0.28123 | 0.27794 | 0.27481 | 0.27043 | 0.24705 | 0.22519 | 0.20071 | 0.30957 | 0.30947 | 0.30398 | 0.29848 | 0.29425 | 0.28391 | 0.27902 | 0.2701 | 0.26649 | 0.26316 | 0.25833 | 0.23385 | 0.20735 | 0.18017 | 0.28745 | 0.28798 | 0.2834 | 0.27701 | 0.26772 | 0.2591 | 0.25439 | 0.24457 | 0.24075 | 0.23718 | 0.23208 | 0.20515 | 0.17752 | 0.14922
|  | AIRIGH-NA-BRODAIG | CT |  |  |  | 0.32213 | 0.32042 | 0.31553 | 0.31132 | 0.29914 | 0.29209 | 0.28939 | 0.28528 | 0.28067 | 0.27825 | 0.27396 | 0.24913 | 0.23508 | 0.22042 | 0.31154 | 0.31036 | 0.30737 | 0.30425 | 0.29425 | 0.28578 | 0.28304 | 0.2785 | 0.27354 | 0.26936 | 0.26456 | 0.24166 | 0.22451 | 0.20628 | 0.29111 | 0.2897 | 0.28495 | 0.28067 | 0.26772 | 0.2591 | 0.25604 | 0.25125 | 0.24596 | 0.24249 | 0.23737 | 0.21015 | 0.19273 | 0.17444
|  | AIRIGH-NA-BRODAIG | LW |  |  |  | 0.31782 | 0.31858 | 0.31791 | 0.31525 | 0.30936 | 0.3029 | 0.30101 | 0.29811 | 0.29501 | 0.29207 | 0.28919 | 0.27936 | 0.2542 | 0.21619 | 0.30957 | 0.30947 | 0.30893 | 0.3076 | 0.30515 | 0.30219 | 0.30082 | 0.298 | 0.29501 | 0.29208 | 0.28917 | 0.27952 | 0.2484 | 0.20256 | 0.28745 | 0.28798 | 0.28731 | 0.28489 | 0.27965 | 0.27384 | 0.27201 | 0.26885 | 0.26549 | 0.26233 | 0.25907 | 0.24806 | 0.21672 | 0.17001
|  | AIRIGH-NA-BRODAIG | ST |  |  |  | 0.32148 | 0.32109 | 0.31544 | 0.30983 | 0.30546 | 0.29672 | 0.2897 | 0.28123 | 0.27794 | 0.27481 | 0.27043 | 0.24705 | 0.22519 | 0.20071 | 0.31117 | 0.31086 | 0.30398 | 0.29848 | 0.29457 | 0.28391 | 0.27902 | 0.2701 | 0.26649 | 0.26316 | 0.25833 | 0.23385 | 0.20735 | 0.18017 | 0.29078 | 0.29037 | 0.2834 | 0.27701 | 0.27224 | 0.26147 | 0.25439 | 0.24457 | 0.24075 | 0.23718 | 0.23208 | 0.20515 | 0.17752 | 0.14922
|  | AIRIGH-NA-BRODAIG | FS |  |  |  | 0.32151 | 0.32227 | 0.31982 | 0.31837 | 0.31549 | 0.31198 | 0.30855 | 0.30572 | 0.30319 | 0.30088 | 0.29848 | 0.28543 | 0.27737 | 0.27114 | 0.3112 | 0.31159 | 0.30938 | 0.30776 | 0.30534 | 0.30274 | 0.3003 | 0.29704 | 0.29448 | 0.29195 | 0.28935 | 0.28022 | 0.27367 | 0.26926 | 0.29083 | 0.29145 | 0.28883 | 0.28712 | 0.28402 | 0.2804 | 0.27692 | 0.27355 | 0.27069 | 0.26802 | 0.26525 | 0.25236 | 0.24389 | 0.23781
| COUPAR ANGUS | ALYTH | MINIMUM HEADROOM | NO 23579 48311 | NO | YES | 3.5115 | 3.2473 | 2.8949 | 2.5149 | 2.0991 | 1.5957 | 1.045 | 0.66465 | 0.3146 | -0.045017 | -0.3323 | -1.2998 | -1.9234 | -2.2905 | 4.2212 | 4.0688 | 3.8868 | 3.6974 | 3.4579 | 3.1751 | 2.9173 | 2.6817 | 2.4256 | 2.169 | 1.9499 | 1.2499 | 0.7923 | 0.35178 | 3.9357 | 3.7168 | 3.4391 | 3.1352 | 2.8109 | 2.3993 | 1.9403 | 1.5942 | 1.2644 | 0.92666 | 0.64729 | -0.28722 | -0.83859 | -1.2099
|  | ALYTH | CT |  |  |  | 3.6517 | 3.452 | 3.0904 | 2.6927 | 2.2504 | 1.7722 | 1.3005 | 0.90671 | 0.49788 | 0.085285 | -0.25299 | -1.2998 | -1.9234 | -2.2905 | 4.2737 | 4.1497 | 3.9432 | 3.7212 | 3.4579 | 3.1751 | 2.9173 | 2.6817 | 2.4256 | 2.169 | 1.9499 | 1.2499 | 0.7923 | 0.35178 | 4.0403 | 3.8735 | 3.5709 | 3.234 | 2.8588 | 2.4542 | 2.0729 | 1.7276 | 1.3524 | 0.97491 | 0.6593 | -0.28722 | -0.83859 | -1.2099
|  | ALYTH | LW |  |  |  | 3.5115 | 3.2473 | 2.8949 | 2.5149 | 2.0991 | 1.5957 | 1.045 | 0.66465 | 0.3146 | -0.045017 | -0.3323 | -1.0888 | -1.5764 | -2.0179 | 4.2212 | 4.0688 | 3.8868 | 3.6974 | 3.4955 | 3.2357 | 2.9348 | 2.7055 | 2.4846 | 2.2586 | 2.0695 | 1.6186 | 1.223 | 0.75278 | 3.9357 | 3.7168 | 3.4391 | 3.1352 | 2.8109 | 2.3993 | 1.9403 | 1.5942 | 1.2644 | 0.92666 | 0.64729 | -0.027226 | -0.51072 | -1.018
|  | ALYTH | ST |  |  |  | 3.705 | 3.5629 | 3.3492 | 3.1412 | 2.9199 | 2.6258 | 2.3579 | 2.1147 | 1.8927 | 1.6653 | 1.4383 | 0.24245 | -0.44506 | -1.0545 | 4.3024 | 4.2179 | 4.0593 | 3.9179 | 3.7757 | 3.5547 | 3.3705 | 3.1784 | 3.0196 | 2.8537 | 2.6779 | 1.778 | 1.1932 | 0.61267 | 4.0853 | 3.9751 | 3.7846 | 3.6012 | 3.4122 | 3.1383 | 2.9034 | 2.665 | 2.4536 | 2.2339 | 2.0042 | 0.82573 | 0.16456 | -0.39682
|  | ALYTH | FS |  |  |  | 3.746 | 3.6322 | 3.4762 | 3.3144 | 3.1327 | 2.9316 | 2.7185 | 2.524 | 2.3447 | 2.1587 | 1.9878 | 0.99336 | 0.12903 | -0.34874 | 4.3203 | 4.2504 | 4.1524 | 4.0515 | 3.9384 | 3.8126 | 3.6711 | 3.539 | 3.4142 | 3.2826 | 3.1566 | 2.4501 | 1.7364 | 1.1257 | 4.1168 | 4.0284 | 3.9022 | 3.768 | 3.6178 | 3.4509 | 3.2703 | 3.097 | 2.9349 | 2.7643 | 2.6014 | 1.6684 | 0.86892 | 0.48041
| FORT WILLIAM | ANNAT | MINIMUM HEADROOM | NN 08452 76751 | YES | YES | 5.9945 | 5.8915 | 5.7655 | 5.6324 | 5.4678 | 5.2879 | 5.1153 | 5.0463 | 4.9615 | 4.8817 | 4.8006 | 4.6175 | 4.3566 | 4.2321 | 6.2602 | 6.2108 | 6.1541 | 6.079 | 5.9796 | 5.8794 | 5.7953 | 5.7421 | 5.6781 | 5.6165 | 5.5547 | 5.3758 | 5.1824 | 5.004 | 5.5747 | 5.5071 | 5.4303 | 5.3264 | 5.1958 | 5.0643 | 4.9456 | 4.88 | 4.8212 | 4.766 | 4.694 | 4.4881 | 4.2857 | 4.1221
|  | ANNAT | CT |  |  |  | 6.0807 | 6.0098 | 5.8336 | 5.6504 | 5.4678 | 5.2879 | 5.1153 | 5.0463 | 4.9615 | 4.8817 | 4.8006 | 4.6175 | 4.3566 | 4.2321 | 6.2928 | 6.255 | 6.1697 | 6.079 | 5.9796 | 5.8794 | 5.7953 | 5.7421 | 5.6781 | 5.6165 | 5.5547 | 5.3758 | 5.1824 | 5.004 | 5.6166 | 5.558 | 5.4412 | 5.3264 | 5.1958 | 5.0643 | 4.9456 | 4.88 | 4.8212 | 4.766 | 4.694 | 4.4881 | 4.3095 | 4.2011
|  | ANNAT | LW |  |  |  | 5.9945 | 5.8915 | 5.7655 | 5.6324 | 5.5045 | 5.3501 | 5.186 | 5.105 | 5.0192 | 4.9294 | 4.8465 | 4.6312 | 4.4186 | 4.242 | 6.2602 | 6.2108 | 6.1541 | 6.0931 | 6.0353 | 5.9597 | 5.8772 | 5.8206 | 5.76 | 5.6976 | 5.6395 | 5.4995 | 5.3369 | 5.1562 | 5.5747 | 5.5071 | 5.4303 | 5.3492 | 5.268 | 5.1673 | 5.0584 | 4.9894 | 4.9147 | 4.8357 | 4.7613 | 4.5484 | 4.36 | 4.1786
|  | ANNAT | ST |  |  |  | 6.1384 | 6.1045 | 6.0372 | 5.9685 | 5.9053 | 5.8175 | 5.7413 | 5.6512 | 5.5671 | 5.4729 | 5.3716 | 4.8959 | 4.6462 | 4.4639 | 6.3183 | 6.3017 | 6.2551 | 6.2117 | 6.1731 | 6.1061 | 6.0593 | 5.9928 | 5.9377 | 5.8772 | 5.8083 | 5.4667 | 5.2441 | 5.0275 | 5.6565 | 5.6321 | 5.5752 | 5.5213 | 5.4706 | 5.39 | 5.3276 | 5.2461 | 5.1737 | 5.0936 | 5.0022 | 4.5439 | 4.2857 | 4.1221
|  | ANNAT | FS |  |  |  | 6.1656 | 6.1409 | 6.0921 | 6.0409 | 5.9896 | 5.9336 | 5.8722 | 5.8078 | 5.7304 | 5.6583 | 5.5734 | 5.0606 | 4.7289 | 4.5886 | 6.3292 | 6.3166 | 6.2904 | 6.2621 | 6.2327 | 6.2003 | 6.1651 | 6.1229 | 6.076 | 6.0295 | 5.9761 | 5.6614 | 5.3722 | 5.1086 | 5.6735 | 5.6556 | 5.6208 | 5.5844 | 5.5459 | 5.5038 | 5.4585 | 5.4069 | 5.3492 | 5.2927 | 5.2274 | 4.8417 | 4.5547 | 4.3764
| KILLIN | ARDCHYLE | MINIMUM HEADROOM | NN 52734 29223 | YES | YES | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11
|  | ARDCHYLE | CT |  |  |  | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11
|  | ARDCHYLE | LW |  |  |  | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11
|  | ARDCHYLE | ST |  |  |  | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11
|  | ARDCHYLE | FS |  |  |  | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11
| NAIRN | ARDERSIER | MINIMUM HEADROOM | NH 80475 55905 | NO | YES | 4.5725 | 4.4478 | 4.2258 | 3.9873 | 3.6954 | 3.3602 | 3.0474 | 2.8566 | 2.6497 | 2.4356 | 2.2258 | 1.5754 | 1.4079 | 1.2683 | 5.0846 | 5.0064 | 4.8666 | 4.7125 | 4.4974 | 4.243 | 4.0318 | 3.9 | 3.7604 | 3.6191 | 3.4835 | 3.1241 | 3.0112 | 2.8853 | 4.4809 | 4.3646 | 4.1711 | 3.9603 | 3.6873 | 3.357 | 3.0549 | 2.8676 | 2.6703 | 2.4696 | 2.2744 | 1.7105 | 1.5468 | 1.3956
|  | ARDERSIER | CT |  |  |  | 4.6351 | 4.5538 | 4.3576 | 4.1306 | 3.8537 | 3.5594 | 3.3108 | 3.1412 | 2.9511 | 2.7429 | 2.5477 | 2.1536 | 1.9247 | 1.8138 | 5.1133 | 5.0526 | 4.942 | 4.8166 | 4.6392 | 4.4514 | 4.3265 | 4.2189 | 4.0889 | 3.9541 | 3.8298 | 3.5486 | 3.4031 | 3.2697 | 4.506 | 4.4442 | 4.2811 | 4.0914 | 3.849 | 3.5843 | 3.3694 | 3.2105 | 3.0246 | 2.8293 | 2.6501 | 2.2785 | 2.0745 | 1.9665
|  | ARDERSIER | LW |  |  |  | 4.5725 | 4.4478 | 4.2258 | 3.9873 | 3.6954 | 3.3602 | 3.0474 | 2.8566 | 2.6497 | 2.4356 | 2.2258 | 1.5754 | 1.4079 | 1.2683 | 5.0846 | 5.0064 | 4.8666 | 4.7125 | 4.4974 | 4.243 | 4.0318 | 3.9 | 3.7604 | 3.6191 | 3.4835 | 3.1241 | 3.0112 | 2.8853 | 4.4809 | 4.3646 | 4.1711 | 3.9603 | 3.6873 | 3.357 | 3.0549 | 2.8676 | 2.6703 | 2.4696 | 2.2744 | 1.7105 | 1.5468 | 1.3956
|  | ARDERSIER | ST |  |  |  | 4.6498 | 4.6145 | 4.5037 | 4.3702 | 4.2442 | 4.0473 | 3.9105 | 3.7729 | 3.6245 | 3.4657 | 3.2988 | 2.6962 | 2.4755 | 2.3285 | 5.1348 | 5.0945 | 4.9748 | 4.874 | 4.7862 | 4.6119 | 4.5141 | 4.4221 | 4.3291 | 4.2287 | 4.1199 | 3.6712 | 3.4937 | 3.3448 | 4.5344 | 4.4961 | 4.3769 | 4.2518 | 4.1385 | 3.9373 | 3.8122 | 3.6899 | 3.5629 | 3.4276 | 3.2829 | 2.7017 | 2.4874 | 2.3483
|  | ARDERSIER | FS |  |  |  | 4.6584 | 4.6244 | 4.5761 | 4.5085 | 4.4074 | 4.2991 | 4.1882 | 4.075 | 3.9591 | 3.8373 | 3.7055 | 2.9903 | 2.5927 | 2.4645 | 5.1483 | 5.1146 | 5.056 | 4.9954 | 4.9304 | 4.8607 | 4.7893 | 4.7201 | 4.6482 | 4.5721 | 4.4902 | 4.0392 | 3.7029 | 3.5114 | 4.5487 | 4.5177 | 4.4614 | 4.393 | 4.306 | 4.2124 | 4.1164 | 4.021 | 3.9224 | 3.8199 | 3.7093 | 3.0989 | 2.7134 | 2.603
| FORT AUGUSTUS | ARDOCHY | MINIMUM HEADROOM | NH 47714 12561 | YES | YES | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11
|  | ARDOCHY | CT |  |  |  | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11
|  | ARDOCHY | LW |  |  |  | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11
|  | ARDOCHY | ST |  |  |  | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11
|  | ARDOCHY | FS |  |  |  | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11
| FORT WILLIAM | ARISAIG | MINIMUM HEADROOM | NM 66564 86619 | YES | YES | 2.2317 | 2.2212 | 2.2068 | 2.1776 | 2.145 | 2.1101 | 2.0722 | 2.0442 | 2.0157 | 1.985 | 1.9573 | 1.9151 | 1.8898 | 1.8722 | 2.1162 | 2.1021 | 2.0874 | 2.0658 | 2.0488 | 2.0306 | 2.0089 | 1.9869 | 1.9638 | 1.9396 | 1.9178 | 1.8873 | 1.8624 | 1.8401 | 2.0514 | 2.0292 | 2.0034 | 1.9738 | 1.9439 | 1.912 | 1.8763 | 1.8486 | 1.8203 | 1.7899 | 1.7625 | 1.7218 | 1.6995 | 1.6837
|  | ARISAIG | CT |  |  |  | 2.2344 | 2.2265 | 2.2068 | 2.1776 | 2.145 | 2.1101 | 2.0786 | 2.054 | 2.0261 | 1.9988 | 1.971 | 1.9289 | 1.8898 | 1.8722 | 2.1205 | 2.1102 | 2.0882 | 2.0658 | 2.0488 | 2.0306 | 2.0136 | 1.9955 | 1.9726 | 1.9495 | 1.928 | 1.8875 | 1.8624 | 1.8401 | 2.0616 | 2.0469 | 2.0102 | 1.9738 | 1.9439 | 1.912 | 1.8831 | 1.8592 | 1.8314 | 1.8041 | 1.7769 | 1.7344 | 1.6995 | 1.6837
|  | ARISAIG | LW |  |  |  | 2.2317 | 2.2212 | 2.2078 | 2.1788 | 2.1513 | 2.1154 | 2.0722 | 2.0442 | 2.0157 | 1.985 | 1.9573 | 1.9151 | 1.8969 | 1.887 | 2.1162 | 2.1021 | 2.0874 | 2.071 | 2.0567 | 2.0349 | 2.0089 | 1.9869 | 1.9638 | 1.9396 | 1.9178 | 1.8873 | 1.8793 | 1.8755 | 2.0514 | 2.0292 | 2.0034 | 1.9757 | 1.9505 | 1.9169 | 1.8763 | 1.8486 | 1.8203 | 1.7899 | 1.7625 | 1.7218 | 1.7058 | 1.6973
|  | ARISAIG | ST |  |  |  | 2.249 | 2.2463 | 2.244 | 2.2404 | 2.237 | 2.234 | 2.2278 | 2.2174 | 2.1936 | 2.1692 | 2.1473 | 2.0242 | 1.9943 | 1.9751 | 2.1297 | 2.125 | 2.1201 | 2.1128 | 2.1059 | 2.0979 | 2.0874 | 2.0759 | 2.0596 | 2.0419 | 2.0242 | 1.9279 | 1.9015 | 1.8805 | 2.0804 | 2.073 | 2.0662 | 2.0555 | 2.0463 | 2.0362 | 2.0218 | 2.0078 | 1.9851 | 1.9615 | 1.9399 | 1.8195 | 1.7914 | 1.7747
|  | ARISAIG | FS |  |  |  | 2.25 | 2.2473 | 2.2436 | 2.2407 | 2.2375 | 2.2349 | 2.2274 | 2.22 | 2.2048 | 2.1883 | 2.1703 | 2.0496 | 1.9596 | 1.9391 | 2.1308 | 2.1266 | 2.1211 | 2.1152 | 2.1089 | 2.1023 | 2.0924 | 2.0834 | 2.0727 | 2.0608 | 2.0476 | 1.9605 | 1.8839 | 1.8503 | 2.0825 | 2.076 | 2.0669 | 2.058 | 2.0485 | 2.0394 | 2.0238 | 2.0119 | 1.9974 | 1.9815 | 1.9643 | 1.8485 | 1.7613 | 1.743
| STORNOWAY | ARNISH | MINIMUM HEADROOM | NB 42300 30440 | YES | YES | 12 | 12 | 11.9887 | 11.981 | 11.9759 | 11.9586 | 11.9537 | 11.8971 | 11.8771 | 11.8601 | 11.833 | 11.7057 | 11.3357 | 10.7447 | 11.9997 | 11.9994 | 11.9855 | 11.9758 | 11.9693 | 11.9473 | 11.9409 | 11.8699 | 11.8444 | 11.8227 | 11.7882 | 11.6261 | 11.1625 | 10.4237 | 11.9996 | 11.9992 | 11.9854 | 11.9757 | 11.9691 | 11.9471 | 11.9407 | 11.8696 | 11.844 | 11.8222 | 11.7876 | 11.6246 | 11.1599 | 10.4212
|  | ARNISH | CT |  |  |  | 12 | 12 | 11.9985 | 11.9959 | 11.9833 | 11.9699 | 11.9665 | 11.9408 | 11.9149 | 11.8926 | 11.8681 | 11.7378 | 11.5393 | 11.3047 | 11.9997 | 11.9994 | 11.9971 | 11.9936 | 11.9771 | 11.96 | 11.9554 | 11.9228 | 11.8899 | 11.8614 | 11.8302 | 11.6656 | 11.4172 | 11.1244 | 11.9996 | 11.9992 | 11.9969 | 11.9933 | 11.9758 | 11.9587 | 11.9542 | 11.9215 | 11.8881 | 11.8595 | 11.8281 | 11.6624 | 11.414 | 11.1219
|  | ARNISH | LW |  |  |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 11.9719 | 11.9428 | 11.9188 | 11.8918 | 11.7498 | 11.3357 | 10.7447 | 11.9997 | 11.9994 | 11.9986 | 11.9984 | 11.9982 | 11.9977 | 11.9972 | 11.9617 | 11.9246 | 11.8934 | 11.859 | 11.68 | 11.1625 | 10.4237 | 11.9997 | 11.9993 | 11.9976 | 11.9973 | 11.997 | 11.9965 | 11.9958 | 11.9607 | 11.9234 | 11.8916 | 11.857 | 11.6771 | 11.1599 | 10.4212
|  | ARNISH | ST |  |  |  | 12 | 12 | 11.9887 | 11.981 | 11.9759 | 11.9586 | 11.9537 | 11.8971 | 11.8771 | 11.8601 | 11.833 | 11.7057 | 11.3995 | 11.0605 | 11.9999 | 11.9998 | 11.9855 | 11.9758 | 11.9693 | 11.9473 | 11.9409 | 11.8699 | 11.8444 | 11.8227 | 11.7882 | 11.6261 | 11.2422 | 10.8186 | 11.9998 | 11.9997 | 11.9854 | 11.9757 | 11.9691 | 11.9471 | 11.9407 | 11.8696 | 11.844 | 11.8222 | 11.7876 | 11.6246 | 11.2401 | 10.8167
|  | ARNISH | FS |  |  |  | 12 | 12 | 11.9977 | 11.9954 | 11.9927 | 11.99 | 11.9876 | 11.9672 | 11.9533 | 11.9394 | 11.9255 | 11.9087 | 11.8916 | 11.8537 | 11.9999 | 11.9998 | 11.9968 | 11.9938 | 11.9903 | 11.9868 | 11.9837 | 11.9579 | 11.9403 | 11.9225 | 11.9048 | 11.8808 | 11.8578 | 11.8099 | 11.9999 | 11.9998 | 11.9968 | 11.9937 | 11.9902 | 11.9866 | 11.9836 | 11.9577 | 11.94 | 11.9218 | 11.9041 | 11.878 | 11.8553 | 11.8078
| ELGIN | ASHGROVE | MINIMUM HEADROOM | NJ 22458 62130 | YES | YES | 13.2196 | 11.7982 | 10.1024 | 8.7411 | 7.3327 | 5.9057 | 4.0663 | 2.5564 | 0.8612 | -0.54237 | -1.9344 | -6.2409 | -7.1334 | -7.7016 | 15.5213 | 14.3643 | 13.0164 | 12.0341 | 10.9849 | 9.9353 | 8.5265 | 7.4795 | 6.2345 | 5.3117 | 4.3965 | 1.8033 | 1.194 | 0.53732 | 14.7915 | 13.5046 | 11.9326 | 10.6663 | 9.3313 | 7.9708 | 6.2495 | 4.8802 | 3.3208 | 2.0306 | 0.75808 | -3.0071 | -3.852 | -4.4744
|  | ASHGROVE | CT |  |  |  | 13.6696 | 12.4706 | 10.9045 | 9.6058 | 8.2745 | 6.9503 | 5.2984 | 3.7985 | 2.0492 | 0.64839 | -0.7664 | -4.4234 | -5.8204 | -6.5967 | 15.6716 | 14.6067 | 13.4861 | 12.5883 | 11.6147 | 10.6483 | 9.3912 | 8.3235 | 7.0048 | 6.0617 | 5.105 | 2.5706 | 1.5446 | 0.53732 | 15.1891 | 14.1001 | 12.658 | 11.4599 | 10.2074 | 8.9638 | 7.4494 | 6.1026 | 4.5094 | 3.2306 | 1.9479 | -1.3772 | -2.6132 | -3.3205
|  | ASHGROVE | LW |  |  |  | 13.2196 | 11.7982 | 10.1024 | 8.7411 | 7.3327 | 5.9057 | 4.0663 | 2.5564 | 0.8612 | -0.54237 | -1.9344 | -6.2409 | -7.1334 | -7.7016 | 15.5213 | 14.3643 | 13.0164 | 12.0341 | 10.9849 | 9.9353 | 8.5265 | 7.4795 | 6.2345 | 5.3117 | 4.3965 | 1.8033 | 1.194 | 0.69809 | 14.7915 | 13.5046 | 11.9326 | 10.6663 | 9.3313 | 7.9708 | 6.2495 | 4.8802 | 3.3208 | 2.0306 | 0.75808 | -3.0071 | -3.852 | -4.4744
|  | ASHGROVE | ST |  |  |  | 13.8376 | 12.7542 | 11.5823 | 10.7304 | 9.9119 | 8.9939 | 7.7668 | 6.702 | 5.4542 | 4.5307 | 3.5572 | 0.1693 | -1.1912 | -2.5887 | 15.6912 | 14.6665 | 13.4749 | 12.6734 | 11.9383 | 11.0634 | 9.8834 | 8.9756 | 7.8491 | 7.1585 | 6.4324 | 4.1681 | 3.043 | 1.7674 | 15.3402 | 14.3607 | 13.2404 | 12.4292 | 11.6612 | 10.7623 | 9.6139 | 8.631 | 7.4852 | 6.6362 | 5.7356 | 2.4669 | 1.2002 | -0.03279
|  | ASHGROVE | FS |  |  |  | 14.2752 | 13.4295 | 12.5716 | 11.8595 | 11.2066 | 10.5433 | 9.5555 | 8.6022 | 7.4517 | 6.5458 | 5.67 | 1.5632 | -1.1463 | -2.4951 | 16.1379 | 15.3387 | 14.5026 | 13.8596 | 13.2889 | 12.7106 | 11.7763 | 10.9769 | 9.9506 | 9.2175 | 8.5338 | 5.5408 | 3.0705 | 1.0805 | 15.742 | 14.9886 | 14.1947 | 13.5361 | 12.9336 | 12.317 | 11.395 | 10.536 | 9.4973 | 8.6796 | 7.8883 | 4.1439 | 1.5945 | 0.41898
| MILTON OF CRAIGIE | ASHLUDIE | MINIMUM HEADROOM | NO 49222 33584 | NO | YES | 2.0851 | 1.1304 | -0.28538 | -1.9185 | -3.9133 | -5.8227 | -7.4152 | -8.6469 | -9.9958 | -11.361 | -12.7079 | -15.4634 | -16.6876 | -17.6372 | 4.1926 | 3.4754 | 2.404 | 1.1221 | -0.5698 | -2.1762 | -3.4152 | -4.3589 | -5.4092 | -6.4693 | -7.5195 | -9.5501 | -10.5457 | -11.5518 | 2.6458 | 1.7617 | 0.3914 | -1.1935 | -3.1939 | -5.1283 | -6.7009 | -7.8847 | -9.1813 | -10.4891 | -11.7804 | -14.4582 | -15.7351 | -16.8295
|  | ASHLUDIE | CT |  |  |  | 2.6407 | 1.8981 | 0.6798 | -0.76086 | -2.492 | -4.0024 | -5.1481 | -6.3397 | -7.7542 | -9.1506 | -10.5259 | -13.8012 | -15.3745 | -16.3443 | 4.4559 | 3.8387 | 2.973 | 1.8976 | 0.4792 | -0.74144 | -1.5655 | -2.4505 | -3.5304 | -4.5967 | -5.6537 | -8.1187 | -9.4845 | -11.0082 | 3.1398 | 2.4475 | 1.311 | -0.042415 | -1.7286 | -3.2107 | -4.2879 | -5.4115 | -6.7494 | -8.0692 | -9.3684 | -12.4631 | -13.9448 | -14.8996
|  | ASHLUDIE | LW |  |  |  | 2.0851 | 1.1304 | -0.28538 | -1.9185 | -3.9133 | -5.8227 | -7.4152 | -8.6469 | -9.9958 | -11.361 | -12.7079 | -15.4634 | -16.6876 | -17.6372 | 4.1926 | 3.4754 | 2.404 | 1.1221 | -0.5698 | -2.1762 | -3.4152 | -4.3589 | -5.4092 | -6.4693 | -7.5195 | -9.5501 | -10.5457 | -11.5518 | 2.6458 | 1.7617 | 0.3914 | -1.1935 | -3.1939 | -5.1283 | -6.7009 | -7.8847 | -9.1813 | -10.4891 | -11.7804 | -14.4582 | -15.7351 | -16.8295
|  | ASHLUDIE | ST |  |  |  | 2.8259 | 2.2171 | 1.3423 | 0.34773 | -0.77688 | -1.9288 | -2.7058 | -3.5421 | -4.4707 | -5.4266 | -6.4385 | -9.8959 | -11.6728 | -13.4055 | 4.545 | 4.0146 | 3.168 | 2.2349 | 1.2011 | 0.059919 | -0.64744 | -1.413 | -2.2441 | -3.1018 | -4.03 | -6.8818 | -8.5235 | -10.4156 | 3.3075 | 2.7424 | 1.8504 | 0.86808 | -0.22207 | -1.4153 | -2.1785 | -3.0013 | -3.8926 | -4.809 | -5.7861 | -9.1318 | -10.8619 | -12.5245
|  | ASHLUDIE | FS |  |  |  | 3.2485 | 2.774 | 2.2019 | 1.4696 | 0.60337 | -0.099144 | -0.77135 | -1.5429 | -2.4033 | -3.2549 | -4.1247 | -7.7702 | -10.6637 | -12.2358 | 4.8921 | 4.4722 | 3.9648 | 3.3084 | 2.5298 | 1.895 | 1.2904 | 0.62197 | -0.12628 | -0.8716 | -1.6341 | -4.6779 | -7.4972 | -10.039 | 3.698 | 3.2587 | 2.7109 | 2.0109 | 1.1813 | 0.50519 | -0.14106 | -0.87475 | -1.689 | -2.4964 | -3.3217 | -6.7491 | -9.4566 | -10.8729
| GRUDIE BRIDGE | AULTBEA | MINIMUM HEADROOM | NG 87458 88885 | YES | YES | -0.72154 | -0.78662 | -0.85954 | -0.93982 | -1.0217 | -1.1108 | -1.2205 | -1.2994 | -1.3869 | -1.473 | -1.5542 | -1.6807 | -1.7503 | -1.8042 | -0.24287 | -0.28408 | -0.32687 | -0.38318 | -0.43345 | -0.48487 | -0.55183 | -0.61249 | -0.67907 | -0.74664 | -0.81779 | -0.91596 | -0.9703 | -1.0205 | -0.86264 | -0.90778 | -0.95633 | -1.0087 | -1.0652 | -1.1268 | -1.2002 | -1.252 | -1.3343 | -1.4196 | -1.4997 | -1.6375 | -1.703 | -1.7519
|  | AULTBEA | CT |  |  |  | -0.6806 | -0.72675 | -0.82865 | -0.93562 | -1.0217 | -1.1089 | -1.1951 | -1.2599 | -1.3431 | -1.4307 | -1.5066 | -1.6415 | -1.7503 | -1.8042 | -0.22447 | -0.25547 | -0.31792 | -0.38318 | -0.43345 | -0.48487 | -0.53601 | -0.58463 | -0.64841 | -0.71488 | -0.77559 | -0.90771 | -0.9703 | -1.0205 | -0.83979 | -0.87497 | -0.94412 | -1.0057 | -1.0652 | -1.1264 | -1.1882 | -1.2305 | -1.2897 | -1.3764 | -1.4512 | -1.5927 | -1.703 | -1.7519
|  | AULTBEA | LW |  |  |  | -0.72154 | -0.78662 | -0.85954 | -0.93982 | -1.011 | -1.1108 | -1.2205 | -1.2994 | -1.3869 | -1.473 | -1.5542 | -1.6807 | -1.7393 | -1.7589 | -0.24287 | -0.28408 | -0.32687 | -0.37482 | -0.41652 | -0.48033 | -0.55183 | -0.61249 | -0.67907 | -0.74664 | -0.81779 | -0.91596 | -0.93884 | -0.9448 | -0.86264 | -0.90778 | -0.95633 | -1.0087 | -1.0596 | -1.1268 | -1.2002 | -1.252 | -1.3343 | -1.4196 | -1.4997 | -1.6375 | -1.6939 | -1.7108
|  | AULTBEA | ST |  |  |  | -0.64905 | -0.66682 | -0.69352 | -0.72536 | -0.75882 | -0.79725 | -0.84332 | -0.89461 | -0.95546 | -1.0235 | -1.0969 | -1.4622 | -1.564 | -1.6163 | -0.20486 | -0.21706 | -0.23442 | -0.25579 | -0.27866 | -0.30549 | -0.33766 | -0.37462 | -0.41886 | -0.46866 | -0.52312 | -0.82608 | -0.90345 | -0.94719 | -0.80736 | -0.82133 | -0.84118 | -0.86409 | -0.88908 | -0.91801 | -0.95205 | -0.98925 | -1.033 | -1.0821 | -1.1352 | -1.4232 | -1.5308 | -1.5838
|  | AULTBEA | FS |  |  |  | -0.639 | -0.65235 | -0.67852 | -0.70672 | -0.73515 | -0.77022 | -0.80694 | -0.84631 | -0.89561 | -0.94603 | -1.0004 | -1.3643 | -1.6261 | -1.6824 | -0.19943 | -0.20915 | -0.22536 | -0.24366 | -0.2625 | -0.28546 | -0.31033 | -0.33775 | -0.37114 | -0.40648 | -0.44506 | -0.70019 | -0.92446 | -0.98488 | -0.79921 | -0.80983 | -0.82944 | -0.84967 | -0.87088 | -0.89689 | -0.92356 | -0.95121 | -0.98502 | -1.0197 | -1.057 | -1.3183 | -1.5843 | -1.6419
| BOAT OF GARTEN | AVIEMORE | MINIMUM HEADROOM | NH 89856 11394 | NO | YES | 5.787 | 5.6227 | 5.5042 | 5.3956 | 5.2726 | 5.0282 | 4.8511 | 4.668 | 4.4361 | 4.1733 | 4.0031 | 3.1686 | 2.4476 | 2.273 | 9.8895 | 9.7072 | 9.5158 | 9.3671 | 9.2214 | 9.0214 | 8.8584 | 8.666 | 8.4626 | 8.2039 | 7.9748 | 6.8635 | 6.3471 | 6.213 | 7.8017 | 7.6252 | 7.4862 | 7.3493 | 7.2104 | 6.9708 | 6.7998 | 6.5884 | 6.3789 | 6.1605 | 5.9197 | 4.4425 | 3.7471 | 3.5794
|  | AVIEMORE | CT |  |  |  | 5.7944 | 5.6449 | 5.5159 | 5.3972 | 5.2726 | 5.0394 | 4.8848 | 4.7135 | 4.4921 | 4.2623 | 4.1129 | 3.5769 | 3.4943 | 3.4529 | 9.8895 | 9.7072 | 9.5158 | 9.3671 | 9.2214 | 9.0214 | 8.8584 | 8.666 | 8.4829 | 8.3068 | 8.1362 | 7.4665 | 7.4065 | 7.3852 | 7.8026 | 7.6381 | 7.4862 | 7.3493 | 7.2104 | 6.9708 | 6.8033 | 6.613 | 6.4255 | 6.2371 | 6.1089 | 5.2286 | 5.1538 | 5.1381
|  | AVIEMORE | LW |  |  |  | 5.787 | 5.6227 | 5.5042 | 5.3956 | 5.2831 | 5.0282 | 4.8511 | 4.668 | 4.4361 | 4.1733 | 4.0031 | 3.585 | 3.4946 | 3.4111 | 9.9095 | 9.7265 | 9.5833 | 9.4742 | 9.361 | 9.153 | 8.9429 | 8.711 | 8.4626 | 8.2039 | 7.9748 | 7.4103 | 7.3357 | 7.261 | 7.8017 | 7.6252 | 7.4963 | 7.3795 | 7.2598 | 6.9999 | 6.7998 | 6.5884 | 6.3789 | 6.1605 | 5.9197 | 5.1468 | 5.0439 | 4.941
|  | AVIEMORE | ST |  |  |  | 5.8186 | 5.7011 | 5.6142 | 5.5389 | 5.4526 | 5.2985 | 5.1848 | 5.0612 | 4.9254 | 4.7736 | 4.5763 | 3.1686 | 2.4476 | 2.273 | 9.9522 | 9.8466 | 9.741 | 9.6535 | 9.5463 | 9.3969 | 9.2393 | 9.0555 | 8.8379 | 8.5862 | 8.315 | 6.8635 | 6.3471 | 6.213 | 7.8386 | 7.7209 | 7.6273 | 7.544 | 7.4468 | 7.2846 | 7.1515 | 7.0028 | 6.8346 | 6.6441 | 6.4175 | 4.4425 | 3.7471 | 3.5794
|  | AVIEMORE | FS |  |  |  | 5.8399 | 5.7445 | 5.6711 | 5.6065 | 5.5341 | 5.41 | 5.3249 | 5.2375 | 5.1454 | 5.0467 | 4.9759 | 4.3995 | 3.5125 | 2.6926 | 9.9696 | 9.8854 | 9.8049 | 9.7373 | 9.663 | 9.5551 | 9.4583 | 9.3479 | 9.2196 | 9.0793 | 8.9388 | 8.0006 | 7.0808 | 6.4783 | 7.8602 | 7.7651 | 7.6882 | 7.6193 | 7.5421 | 7.4156 | 7.3217 | 7.2223 | 7.1145 | 6.9978 | 6.9021 | 6.0127 | 4.7742 | 3.9827
| ALNESS | BALALDIE | MINIMUM HEADROOM | NH 87017 79720 | YES | YES | -2.3558 | -2.4979 | -2.6642 | -2.8339 | -3.0307 | -3.2444 | -3.4557 | -3.5891 | -3.7558 | -3.9272 | -4.0989 | -4.6297 | -5.167 | -5.7759 | -0.83457 | -0.93302 | -1.0299 | -1.1778 | -1.2999 | -1.4294 | -1.5569 | -1.7363 | -1.94 | -2.142 | -2.3369 | -2.8466 | -3.385 | -4.0946 | -1.4213 | -1.5331 | -1.6639 | -1.7968 | -1.9844 | -2.1958 | -2.4052 | -2.6185 | -2.8554 | -3.089 | -3.3167 | -3.9331 | -4.5649 | -5.2905
|  | BALALDIE | CT |  |  |  | -2.2625 | -2.3794 | -2.5957 | -2.8213 | -3.0307 | -3.2444 | -3.4557 | -3.5891 | -3.7296 | -3.8631 | -3.9936 | -4.439 | -4.8759 | -5.1788 | -0.80222 | -0.88755 | -1.0276 | -1.1778 | -1.2999 | -1.4294 | -1.5569 | -1.7029 | -1.8743 | -2.0417 | -2.199 | -2.7045 | -3.0842 | -3.4744 | -1.3442 | -1.4372 | -1.6088 | -1.7847 | -1.9844 | -2.1958 | -2.4052 | -2.5776 | -2.7757 | -2.968 | -3.1493 | -3.706 | -4.1661 | -4.5197
|  | BALALDIE | LW |  |  |  | -2.3558 | -2.4979 | -2.6642 | -2.8339 | -2.9996 | -3.2008 | -3.4154 | -3.5801 | -3.7558 | -3.9272 | -4.0989 | -4.6297 | -5.167 | -5.7759 | -0.83457 | -0.93302 | -1.0299 | -1.1358 | -1.2333 | -1.3804 | -1.5474 | -1.7363 | -1.94 | -2.142 | -2.3369 | -2.8466 | -3.385 | -4.0946 | -1.4213 | -1.5331 | -1.6639 | -1.7968 | -1.9354 | -2.1558 | -2.3975 | -2.6185 | -2.8554 | -3.089 | -3.3167 | -3.9331 | -4.5461 | -5.2905
|  | BALALDIE | ST |  |  |  | -2.1871 | -2.2425 | -2.318 | -2.4031 | -2.4934 | -2.587 | -2.6992 | -2.8702 | -3.0352 | -3.2105 | -3.4096 | -4.3925 | -5.0379 | -5.5088 | -0.76341 | -0.80021 | -0.84872 | -0.90731 | -0.97224 | -1.0456 | -1.1347 | -1.2939 | -1.4394 | -1.5982 | -1.7834 | -2.7378 | -3.3709 | -3.9037 | -1.282 | -1.3256 | -1.3855 | -1.4516 | -1.5231 | -1.5973 | -1.6862 | -1.8704 | -2.0579 | -2.2655 | -2.5074 | -3.7789 | -4.5649 | -5.0865
|  | BALALDIE | FS |  |  |  | -2.1477 | -2.19 | -2.254 | -2.3266 | -2.3982 | -2.4717 | -2.5553 | -2.6628 | -2.7803 | -2.8957 | -3.0286 | -3.8581 | -4.505 | -4.9056 | -0.74717 | -0.77656 | -0.8164 | -0.86399 | -0.91314 | -0.96703 | -1.0297 | -1.1214 | -1.2183 | -1.3212 | -1.4367 | -2.132 | -2.7871 | -3.2298 | -1.2511 | -1.2845 | -1.3355 | -1.3931 | -1.4499 | -1.5093 | -1.5762 | -1.6684 | -1.7767 | -1.9012 | -2.0517 | -2.973 | -3.7111 | -4.1793
| ABERNETHY | BALBEGGIE | MINIMUM HEADROOM | NO 17499 29606 | YES | YES | 4.431 | 4.2473 | 4.024 | 3.7486 | 3.4193 | 3.0019 | 2.6957 | 2.3955 | 2.0562 | 1.7233 | 1.2726 | 0.14984 | -0.44259 | -0.81142 | 5.126 | 5.0178 | 4.8837 | 4.7361 | 4.5008 | 4.2421 | 4.0653 | 3.8473 | 3.6265 | 3.4142 | 2.999 | 1.7485 | 1.0009 | 0.56163 | 4.7251 | 4.5966 | 4.4104 | 4.2035 | 3.9085 | 3.5815 | 3.3406 | 3.0594 | 2.7214 | 2.3899 | 1.9606 | 0.77828 | 0.013931 | -0.47851
|  | BALBEGGIE | CT |  |  |  | 4.5272 | 4.3784 | 4.11 | 3.7872 | 3.4193 | 3.0019 | 2.6957 | 2.3955 | 2.0562 | 1.7233 | 1.2726 | 0.14984 | -0.44259 | -0.81142 | 5.126 | 5.0178 | 4.8837 | 4.7361 | 4.5008 | 4.2421 | 4.0653 | 3.8473 | 3.6265 | 3.4142 | 2.999 | 1.8709 | 1.3963 | 1.0775 | 4.7389 | 4.6002 | 4.4104 | 4.2035 | 3.9085 | 3.5815 | 3.3406 | 3.0594 | 2.7214 | 2.3899 | 1.9606 | 0.77828 | 0.20261 | -0.16549
|  | BALBEGGIE | LW |  |  |  | 4.431 | 4.2473 | 4.024 | 3.7486 | 3.4829 | 3.1216 | 2.8033 | 2.5198 | 2.2175 | 1.908 | 1.4832 | 0.60246 | -0.066155 | -0.71328 | 5.1359 | 5.0451 | 4.9624 | 4.8601 | 4.7556 | 4.5967 | 4.4274 | 4.2187 | 3.9869 | 3.741 | 3.3275 | 2.3818 | 1.6417 | 0.89708 | 4.7251 | 4.5966 | 4.4668 | 4.3087 | 4.1374 | 3.8319 | 3.5481 | 3.2684 | 2.9687 | 2.6625 | 2.2583 | 1.2498 | 0.45189 | -0.30348
|  | BALBEGGIE | ST |  |  |  | 4.6466 | 4.5618 | 4.3695 | 4.18 | 4.0104 | 3.7195 | 3.5378 | 3.2821 | 3.0588 | 2.8228 | 2.4131 | 0.98977 | 0.25691 | -0.30125 | 5.2321 | 5.1914 | 5.0327 | 4.8919 | 4.7676 | 4.5071 | 4.3573 | 4.1086 | 3.9117 | 3.6958 | 3.2712 | 1.7485 | 1.0009 | 0.56163 | 4.8744 | 4.8183 | 4.6397 | 4.4759 | 4.327 | 4.0376 | 3.858 | 3.5776 | 3.3425 | 3.0843 | 2.6214 | 0.86924 | 0.013931 | -0.47851
|  | BALBEGGIE | FS |  |  |  | 4.679 | 4.6175 | 4.5101 | 4.3826 | 4.2555 | 4.1026 | 3.9759 | 3.8163 | 3.6589 | 3.4957 | 3.2427 | 2.16 | 1.267 | 0.7563 | 5.2526 | 5.2224 | 5.1626 | 5.0917 | 5.0142 | 4.924 | 4.8397 | 4.7247 | 4.6137 | 4.492 | 4.2664 | 3.363 | 2.4747 | 1.8935 | 4.9031 | 4.8632 | 4.7871 | 4.6988 | 4.6031 | 4.4914 | 4.3868 | 4.2477 | 4.1109 | 3.9622 | 3.7109 | 2.6177 | 1.5529 | 0.84385
| MILTON OF CRAIGIE | BALDOVIE | MINIMUM HEADROOM | NO 45279 32147 | NO | YES | 13.2742 | 12.9676 | 10.7454 | 8.3447 | 4.045 | -0.77777 | -3.9947 | -5.38 | -6.8656 | -7.9384 | -9.0505 | -13.3625 | -14.6854 | -15.3601 | 15.2265 | 15.1295 | 12.9428 | 10.5087 | 5.6034 | 0.11926 | -3.3278 | -4.5654 | -5.9045 | -6.8813 | -7.9166 | -12.2211 | -13.5356 | -14.3121 | 15.078 | 14.9746 | 12.8324 | 10.1489 | 5.0891 | -0.49332 | -4.0346 | -5.3698 | -6.8576 | -7.921 | -9.0449 | -13.8654 | -15.3525 | -16.1699
|  | BALDOVIE | CT |  |  |  | 13.5845 | 13.3925 | 12.6133 | 11.6932 | 9.4644 | 6.9273 | 5.7101 | 4.6711 | 3.4719 | 2.6456 | 1.8079 | -1.2474 | -2.5516 | -3.2457 | 15.2738 | 15.1801 | 14.7636 | 14.1601 | 11.8581 | 9.1044 | 8.0001 | 7.1899 | 6.2284 | 5.6278 | 4.9585 | 2.3166 | 1.0265 | -0.24493 | 15.0869 | 14.9746 | 14.6005 | 14.0447 | 11.5832 | 8.7473 | 7.5634 | 6.6514 | 5.6445 | 4.9518 | 4.1825 | 1.2038 | -0.053725 | -0.73253
|  | BALDOVIE | LW |  |  |  | 13.2742 | 12.9676 | 10.7454 | 8.3447 | 4.045 | -0.77777 | -3.9947 | -5.38 | -6.8656 | -7.9384 | -9.0505 | -13.3625 | -14.6854 | -15.3601 | 15.2265 | 15.1295 | 12.9428 | 10.5087 | 5.6034 | 0.11926 | -3.3278 | -4.5654 | -5.9045 | -6.8813 | -7.9166 | -12.2211 | -13.5356 | -14.3121 | 15.078 | 14.9797 | 12.8324 | 10.1489 | 5.0891 | -0.49332 | -4.0346 | -5.3698 | -6.8576 | -7.921 | -9.0449 | -13.8654 | -15.3525 | -16.1699
|  | BALDOVIE | ST |  |  |  | 13.7012 | 13.6186 | 12.0357 | 10.9601 | 10.1663 | 7.5274 | 6.5336 | 5.6451 | 4.9176 | 4.544 | 4.0591 | 1.2905 | -0.26807 | -1.5762 | 15.3101 | 15.269 | 13.3467 | 12.0368 | 11.086 | 7.8106 | 6.6075 | 5.6316 | 4.9079 | 4.5885 | 4.1492 | 1.6429 | 0.054489 | -1.4915 | 15.1107 | 15.0597 | 13.1289 | 11.8135 | 10.8677 | 7.641 | 6.486 | 5.5336 | 4.8387 | 4.5067 | 4.0535 | 1.8649 | 0.76648 | -0.3265
|  | BALDOVIE | FS |  |  |  | 13.7319 | 13.6628 | 13.268 | 12.8873 | 12.4151 | 11.8241 | 11.2218 | 10.6664 | 10.1281 | 9.7691 | 9.3935 | 7.5658 | 5.5419 | 4.089 | 15.3423 | 15.3052 | 14.8811 | 14.4613 | 13.9233 | 13.2321 | 12.5243 | 11.9871 | 11.4916 | 11.194 | 10.8886 | 9.3496 | 7.1682 | 4.7395 | 15.1457 | 15.1008 | 14.6745 | 14.259 | 13.7336 | 13.0818 | 12.426 | 11.9318 | 11.4821 | 11.2097 | 10.9309 | 9.9762 | 8.5117 | 7.2731
| TARLAND | BALLATER | MINIMUM HEADROOM | NO 37542 97131 | NO | YES | 7.4876 | 7.3898 | 7.1785 | 6.9505 | 6.7379 | 6.4516 | 6.1424 | 5.9098 | 5.6615 | 5.4035 | 5.1723 | 4.7432 | 4.5184 | 4.3646 | 8.6089 | 8.4998 | 8.3927 | 8.2654 | 8.1342 | 8.0009 | 7.8331 | 7.6802 | 7.5164 | 7.3356 | 7.1679 | 6.8926 | 6.7208 | 6.5695 | 8.1799 | 7.9926 | 7.7985 | 7.59 | 7.3949 | 7.1345 | 6.8539 | 6.6477 | 6.4272 | 6.1932 | 5.9697 | 5.5679 | 5.3704 | 5.2344
|  | BALLATER | CT |  |  |  | 7.4876 | 7.4359 | 7.3025 | 7.0047 | 6.7465 | 6.4878 | 6.2254 | 6.0327 | 5.7929 | 5.5467 | 5.3247 | 4.8669 | 4.5184 | 4.3646 | 8.6625 | 8.578 | 8.4255 | 8.2654 | 8.1342 | 8.0009 | 7.8656 | 7.7399 | 7.5819 | 7.4194 | 7.2622 | 6.914 | 6.7208 | 6.575 | 8.3104 | 8.1752 | 7.9127 | 7.6404 | 7.4018 | 7.163 | 6.9205 | 6.7476 | 6.5354 | 6.3175 | 6.1173 | 5.6785 | 5.3704 | 5.2344
|  | BALLATER | LW |  |  |  | 7.4995 | 7.3898 | 7.1785 | 6.9505 | 6.7379 | 6.4516 | 6.1424 | 5.9098 | 5.6615 | 5.4035 | 5.1723 | 4.7432 | 4.5762 | 4.473 | 8.6089 | 8.4998 | 8.3927 | 8.2747 | 8.1675 | 8.0088 | 7.8331 | 7.6802 | 7.5164 | 7.3356 | 7.1679 | 6.8926 | 6.8186 | 6.7695 | 8.1799 | 7.9926 | 7.7985 | 7.59 | 7.3949 | 7.1345 | 6.8539 | 6.6477 | 6.4272 | 6.1932 | 5.9697 | 5.5679 | 5.423 | 5.3335
|  | BALLATER | ST |  |  |  | 7.5151 | 7.498 | 7.4755 | 7.4464 | 7.4119 | 7.3256 | 7.1814 | 7.0189 | 6.8344 | 6.6364 | 6.4164 | 5.3499 | 4.9697 | 4.7637 | 8.7174 | 8.6785 | 8.6279 | 8.5681 | 8.5028 | 8.4279 | 8.3425 | 8.2437 | 8.129 | 8.0028 | 7.8623 | 7.1289 | 6.8865 | 6.7322 | 8.4187 | 8.3521 | 8.2648 | 8.1666 | 8.0608 | 7.9434 | 7.8127 | 7.6655 | 7.4981 | 7.3191 | 7.1198 | 6.1127 | 5.7674 | 5.5888
|  | BALLATER | FS |  |  |  | 7.5202 | 7.5078 | 7.4902 | 7.4682 | 7.4432 | 7.4134 | 7.3463 | 7.2097 | 7.0621 | 6.9071 | 6.7378 | 5.6449 | 4.8757 | 4.6379 | 8.7355 | 8.7062 | 8.6614 | 8.6111 | 8.5599 | 8.501 | 8.4362 | 8.3576 | 8.2709 | 8.1775 | 8.0745 | 7.407 | 6.8272 | 6.5695 | 8.458 | 8.4104 | 8.3307 | 8.2456 | 8.1614 | 8.0664 | 7.9643 | 7.8403 | 7.7061 | 7.5655 | 7.4117 | 6.4153 | 5.6867 | 5.474
| CARRADALE | BALLIEKINE | MINIMUM HEADROOM | NR 87179 38819 | YES | YES | 0.48699 | 0.48559 | 0.47203 | 0.4613 | 0.45082 | 0.4098 | 0.38318 | 0.36133 | 0.33562 | 0.314 | 0.29202 | 0.23322 | 0.17283 | 0.11401 | 0.60041 | 0.59854 | 0.58157 | 0.56812 | 0.55879 | 0.52906 | 0.51951 | 0.49615 | 0.48608 | 0.47421 | 0.45226 | 0.37983 | 0.31842 | 0.23878 | 0.47331 | 0.46777 | 0.45387 | 0.43945 | 0.40232 | 0.36396 | 0.34156 | 0.32473 | 0.30662 | 0.2929 | 0.27538 | 0.21048 | 0.14338 | 0.074731
|  | BALLIEKINE | CT |  |  |  | 0.48729 | 0.48614 | 0.4823 | 0.47678 | 0.45082 | 0.4098 | 0.38318 | 0.36133 | 0.33562 | 0.314 | 0.29202 | 0.23322 | 0.17283 | 0.12092 | 0.60062 | 0.59905 | 0.59412 | 0.58741 | 0.56508 | 0.54049 | 0.53211 | 0.51584 | 0.49483 | 0.47421 | 0.45226 | 0.37983 | 0.32116 | 0.26182 | 0.47556 | 0.47395 | 0.45714 | 0.43945 | 0.40232 | 0.36396 | 0.34156 | 0.32473 | 0.30662 | 0.2929 | 0.27538 | 0.21048 | 0.14338 | 0.083133
|  | BALLIEKINE | LW |  |  |  | 0.48699 | 0.48559 | 0.48429 | 0.48281 | 0.47074 | 0.44783 | 0.41965 | 0.40242 | 0.38385 | 0.3621 | 0.34486 | 0.30412 | 0.22151 | 0.11401 | 0.60041 | 0.59854 | 0.59693 | 0.59505 | 0.59339 | 0.59034 | 0.58468 | 0.57111 | 0.55493 | 0.53583 | 0.51879 | 0.47896 | 0.3873 | 0.25745 | 0.47331 | 0.46777 | 0.45387 | 0.44066 | 0.42685 | 0.41311 | 0.39365 | 0.38449 | 0.37465 | 0.36109 | 0.34544 | 0.30475 | 0.2066 | 0.074731
|  | BALLIEKINE | ST |  |  |  | 0.48767 | 0.4873 | 0.47203 | 0.4613 | 0.45395 | 0.43029 | 0.42275 | 0.40417 | 0.39624 | 0.38896 | 0.37836 | 0.30602 | 0.24371 | 0.17872 | 0.60131 | 0.60076 | 0.58157 | 0.56812 | 0.55879 | 0.52906 | 0.51951 | 0.49615 | 0.48608 | 0.47679 | 0.46332 | 0.39868 | 0.31842 | 0.23878 | 0.47604 | 0.47545 | 0.4562 | 0.44263 | 0.43316 | 0.40284 | 0.39182 | 0.3666 | 0.35425 | 0.34236 | 0.326 | 0.24667 | 0.17124 | 0.098922
|  | BALLIEKINE | FS |  |  |  | 0.48776 | 0.48746 | 0.48401 | 0.48044 | 0.47629 | 0.47205 | 0.46818 | 0.46095 | 0.4556 | 0.45004 | 0.44432 | 0.40524 | 0.35663 | 0.33963 | 0.6014 | 0.60094 | 0.59653 | 0.59198 | 0.58674 | 0.58133 | 0.57636 | 0.56726 | 0.56046 | 0.5534 | 0.54618 | 0.52687 | 0.48515 | 0.46618 | 0.47615 | 0.47566 | 0.47126 | 0.46664 | 0.46135 | 0.45586 | 0.45036 | 0.43998 | 0.43165 | 0.42291 | 0.41375 | 0.38235 | 0.3494 | 0.33284
| BOAT OF GARTEN | BALLINDALLOCH | MINIMUM HEADROOM | NJ 19279 34652 | NO | YES | 7.822 | 7.725 | 6.9914 | 6.1802 | 4.6578 | 3.0179 | 2.0194 | 1.712 | 1.3905 | 1.1122 | 0.80521 | -0.45941 | -0.95606 | -1.2868 | 8.0538 | 8.0038 | 7.1664 | 6.2326 | 4.4061 | 2.4484 | 1.2875 | 0.95307 | 0.60322 | 0.30142 | -0.024519 | -1.4701 | -2.0248 | -2.4172 | 7.3108 | 7.2281 | 6.3508 | 5.3797 | 3.5143 | 1.5205 | 0.3312 | -0.00068558 | -0.34696 | -0.63883 | -0.96332 | -2.5221 | -3.1026 | -3.4969
|  | BALLINDALLOCH | CT |  |  |  | 7.8828 | 7.813 | 7.6008 | 7.3116 | 6.4982 | 5.6279 | 5.3158 | 5.1352 | 4.9343 | 4.7532 | 4.5639 | 3.8616 | 3.5125 | 3.33 | 8.0758 | 8.0329 | 7.8595 | 7.6026 | 6.6796 | 5.6947 | 5.3996 | 5.2159 | 5.0142 | 4.83 | 4.6406 | 3.86 | 3.5477 | 3.3385 | 7.3728 | 7.3075 | 7.0889 | 6.7878 | 5.8168 | 4.7779 | 4.4339 | 4.2473 | 4.0526 | 3.8815 | 3.6688 | 2.7516 | 2.4135 | 2.2259
|  | BALLINDALLOCH | LW |  |  |  | 7.822 | 7.725 | 6.9914 | 6.1802 | 4.6578 | 3.0179 | 2.0194 | 1.712 | 1.3905 | 1.1122 | 0.80521 | -0.45941 | -0.95606 | -1.2868 | 8.0538 | 8.0038 | 7.1664 | 6.2326 | 4.4061 | 2.4484 | 1.2875 | 0.95307 | 0.60322 | 0.30142 | -0.024519 | -1.4701 | -2.0248 | -2.4172 | 7.3108 | 7.2281 | 6.3508 | 5.3797 | 3.5143 | 1.5205 | 0.3312 | -0.00068558 | -0.34696 | -0.63883 | -0.96332 | -2.5221 | -3.1026 | -3.4969
|  | BALLINDALLOCH | ST |  |  |  | 7.9269 | 7.8916 | 7.2243 | 6.7535 | 6.4207 | 5.4045 | 5.0661 | 4.7727 | 4.6034 | 4.4465 | 4.2375 | 3.2225 | 2.7108 | 2.448 | 8.097 | 8.0784 | 7.2766 | 6.7224 | 6.3436 | 5.1138 | 4.7398 | 4.4197 | 4.2652 | 4.1213 | 3.9201 | 2.9487 | 2.502 | 2.2204 | 7.4214 | 7.3872 | 6.5656 | 5.9929 | 5.594 | 4.3457 | 3.9517 | 3.6147 | 3.44 | 3.2814 | 3.0197 | 1.7308 | 1.1522 | 0.85463
|  | BALLINDALLOCH | FS |  |  |  | 7.9516 | 7.928 | 7.762 | 7.591 | 7.4022 | 7.2066 | 7.0299 | 6.888 | 6.766 | 6.6322 | 6.4971 | 5.8942 | 5.4916 | 5.2932 | 8.1071 | 8.0937 | 7.9146 | 7.732 | 7.5236 | 7.311 | 7.1222 | 6.9874 | 6.8807 | 6.7679 | 6.652 | 6.2488 | 5.9487 | 5.8102 | 7.449 | 7.4273 | 7.2305 | 7.0301 | 6.807 | 6.578 | 6.3745 | 6.2212 | 6.0967 | 5.9623 | 5.8277 | 5.2376 | 4.7409 | 4.4315
| CARRADALE | BALLURE | MINIMUM HEADROOM | NR 71425 49944 | YES | YES | 1.7226 | 1.694 | 1.6594 | 1.6232 | 1.5523 | 1.4711 | 1.4208 | 1.3847 | 1.3515 | 1.3124 | 1.2723 | 1.1461 | 1.0051 | 0.87606 | 1.8258 | 1.8108 | 1.7867 | 1.751 | 1.7013 | 1.6348 | 1.6053 | 1.5612 | 1.5197 | 1.475 | 1.4315 | 1.2449 | 1.0631 | 0.89012 | 1.711 | 1.6871 | 1.6619 | 1.6227 | 1.5505 | 1.4715 | 1.4299 | 1.3834 | 1.3323 | 1.2793 | 1.2284 | 1.0593 | 0.86578 | 0.68535
|  | BALLURE | CT |  |  |  | 1.7424 | 1.7231 | 1.6777 | 1.6232 | 1.5523 | 1.4711 | 1.4208 | 1.3847 | 1.3515 | 1.3124 | 1.2723 | 1.1461 | 1.0051 | 0.90087 | 1.8317 | 1.8209 | 1.7953 | 1.7628 | 1.7013 | 1.6348 | 1.6053 | 1.5651 | 1.5197 | 1.475 | 1.4315 | 1.2759 | 1.1518 | 1.0287 | 1.7241 | 1.7076 | 1.6696 | 1.6227 | 1.5505 | 1.4715 | 1.4299 | 1.3834 | 1.3323 | 1.2793 | 1.2284 | 1.0613 | 0.9204 | 0.79372
|  | BALLURE | LW |  |  |  | 1.7226 | 1.694 | 1.6594 | 1.6272 | 1.5941 | 1.5525 | 1.5099 | 1.4829 | 1.4502 | 1.4201 | 1.3926 | 1.3028 | 1.1217 | 0.88645 | 1.8258 | 1.8108 | 1.7962 | 1.7804 | 1.7661 | 1.7431 | 1.7171 | 1.6846 | 1.6492 | 1.6152 | 1.5827 | 1.4997 | 1.2981 | 1.0093 | 1.711 | 1.6871 | 1.6619 | 1.6362 | 1.6118 | 1.5763 | 1.5375 | 1.4985 | 1.4552 | 1.4137 | 1.3744 | 1.2744 | 1.0635 | 0.77118
|  | BALLURE | ST |  |  |  | 1.7705 | 1.7597 | 1.715 | 1.6796 | 1.655 | 1.5875 | 1.5572 | 1.5008 | 1.4634 | 1.4321 | 1.3919 | 1.192 | 1.0323 | 0.87606 | 1.8392 | 1.8341 | 1.7867 | 1.751 | 1.725 | 1.6514 | 1.6225 | 1.5612 | 1.5278 | 1.4962 | 1.4538 | 1.2449 | 1.0631 | 0.89012 | 1.7378 | 1.7292 | 1.678 | 1.6379 | 1.6086 | 1.5298 | 1.496 | 1.4292 | 1.3889 | 1.3517 | 1.3029 | 1.0593 | 0.86578 | 0.68535
|  | BALLURE | FS |  |  |  | 1.7757 | 1.7713 | 1.7515 | 1.7329 | 1.7109 | 1.6901 | 1.6715 | 1.6392 | 1.6159 | 1.586 | 1.5568 | 1.4141 | 1.3228 | 1.2694 | 1.8408 | 1.8376 | 1.8233 | 1.8084 | 1.7914 | 1.7739 | 1.7572 | 1.7293 | 1.7068 | 1.682 | 1.6563 | 1.5529 | 1.4727 | 1.4389 | 1.7408 | 1.736 | 1.7173 | 1.6985 | 1.6767 | 1.655 | 1.6343 | 1.6007 | 1.5736 | 1.5425 | 1.5106 | 1.3679 | 1.2649 | 1.226
| DYCE | BALMEDIE | MINIMUM HEADROOM | NJ 95546 18627 | YES | YES | 2.5875 | 2.3988 | 2.0539 | 1.6607 | 1.1541 | 0.36145 | -0.50456 | -0.90545 | -1.2503 | -1.6157 | -1.9634 | -2.9361 | -3.3793 | -3.6417 | 3.8846 | 3.8209 | 3.6785 | 3.4873 | 3.162 | 2.5179 | 1.8367 | 1.6364 | 1.508 | 1.2983 | 1.0521 | 0.43464 | 0.17935 | -0.089125 | 3.062 | 2.8843 | 2.558 | 2.1828 | 1.6862 | 0.91475 | 0.086806 | -0.30453 | -0.64709 | -1.0093 | -1.3522 | -2.2627 | -2.68 | -2.9507
|  | BALMEDIE | CT |  |  |  | 2.763 | 2.6288 | 2.3118 | 1.9687 | 1.5195 | 0.85193 | 0.16057 | -0.25777 | -0.64437 | -1.0208 | -1.3852 | -2.4833 | -3.1906 | -3.5697 | 3.9071 | 3.8378 | 3.7228 | 3.5893 | 3.3081 | 2.7499 | 2.1984 | 1.9825 | 1.8286 | 1.6854 | 1.4839 | 0.79198 | 0.34188 | -0.089125 | 3.1065 | 3.0262 | 2.7839 | 2.4582 | 2.0231 | 1.3871 | 0.74798 | 0.35447 | -0.019556 | -0.38494 | -0.73454 | -1.7546 | -2.3735 | -2.7149
|  | BALMEDIE | LW |  |  |  | 2.5875 | 2.3988 | 2.0539 | 1.6607 | 1.1541 | 0.36145 | -0.50456 | -0.90545 | -1.2503 | -1.6157 | -1.9634 | -2.9361 | -3.3793 | -3.6417 | 3.8846 | 3.8209 | 3.6785 | 3.4873 | 3.162 | 2.5179 | 1.8367 | 1.6364 | 1.508 | 1.2983 | 1.0521 | 0.43464 | 0.17935 | -0.037699 | 3.062 | 2.8843 | 2.558 | 2.1828 | 1.6862 | 0.91475 | 0.086806 | -0.30453 | -0.64709 | -1.0093 | -1.3522 | -2.2627 | -2.68 | -2.9507
|  | BALMEDIE | ST |  |  |  | 2.8346 | 2.7663 | 2.6119 | 2.4634 | 2.2514 | 1.7368 | 1.2097 | 0.96997 | 0.77845 | 0.58891 | 0.37907 | -0.81891 | -1.5362 | -2.2131 | 3.9291 | 3.8957 | 3.7725 | 3.6672 | 3.4942 | 2.9491 | 2.4298 | 2.2433 | 2.129 | 2.0186 | 1.9013 | 1.3363 | 0.81834 | 0.29626 | 3.1346 | 3.1007 | 2.9746 | 2.8661 | 2.6809 | 2.1682 | 1.666 | 1.4283 | 1.236 | 1.0425 | 0.82732 | -0.32134 | -0.98484 | -1.5977
|  | BALMEDIE | FS |  |  |  | 2.9196 | 2.8669 | 2.7834 | 2.6892 | 2.5242 | 2.2372 | 1.8299 | 1.6086 | 1.4173 | 1.225 | 1.0368 | -0.13775 | -1.2813 | -1.9568 | 3.9967 | 3.9676 | 3.9221 | 3.8726 | 3.7454 | 3.4687 | 3.0661 | 2.9134 | 2.7989 | 2.6853 | 2.5797 | 2.0224 | 1.1008 | 0.35944 | 3.1957 | 3.1679 | 3.1209 | 3.0691 | 2.945 | 2.6913 | 2.3142 | 2.1049 | 1.9223 | 1.737 | 1.5534 | 0.43076 | -0.63652 | -1.2413
| CLAYHILLS | BALNAGASK | MINIMUM HEADROOM | NJ 96055 05234 | YES | NO | 9.7174 | 9.5936 | 9.3955 | 9.1753 | 8.9446 | 8.6815 | 8.3724 | 8.0815 | 7.7692 | 7.4499 | 7.1334 | 6.2516 | 5.5506 | 4.6122 | 9.0991 | 9.03 | 8.8921 | 8.7193 | 8.5349 | 8.3421 | 8.1844 | 7.9952 | 7.7898 | 7.5881 | 7.3737 | 6.427 | 5.484 | 3.9398 | 9.1755 | 9.1021 | 8.9925 | 8.8082 | 8.5691 | 8.321 | 8.0994 | 7.8107 | 7.4997 | 7.1836 | 6.8714 | 5.9991 | 5.1838 | 4.051
|  | BALNAGASK | CT |  |  |  | 9.7405 | 9.6464 | 9.4754 | 9.2015 | 8.9446 | 8.6815 | 8.4447 | 8.198 | 7.9259 | 7.6604 | 7.385 | 6.3571 | 5.699 | 5.2359 | 9.1241 | 9.0449 | 8.8921 | 8.7193 | 8.5349 | 8.3421 | 8.1844 | 7.9952 | 7.7898 | 7.5881 | 7.3737 | 6.427 | 5.484 | 4.2716 | 9.1797 | 9.1021 | 8.9925 | 8.8082 | 8.5691 | 8.321 | 8.1083 | 7.8672 | 7.6002 | 7.3403 | 7.07 | 6.0801 | 5.4288 | 4.916
|  | BALNAGASK | LW |  |  |  | 9.7174 | 9.5936 | 9.3955 | 9.1753 | 8.9631 | 8.6839 | 8.3724 | 8.0815 | 7.7692 | 7.4499 | 7.1334 | 6.2516 | 5.5506 | 4.6122 | 9.0991 | 9.03 | 8.9321 | 8.8218 | 8.7144 | 8.5658 | 8.3967 | 8.2022 | 7.9924 | 7.7814 | 7.5702 | 6.9283 | 6.1545 | 5.0848 | 9.1755 | 9.1358 | 9.0071 | 8.8166 | 8.6332 | 8.3825 | 8.0994 | 7.8107 | 7.4997 | 7.1836 | 6.8714 | 5.9991 | 5.1838 | 4.051
|  | BALNAGASK | ST |  |  |  | 9.7576 | 9.7414 | 9.6817 | 9.6279 | 9.5769 | 9.4753 | 9.4078 | 9.2559 | 9.1183 | 8.9597 | 8.7679 | 7.5753 | 6.7114 | 5.9008 | 9.1521 | 9.1249 | 9.0426 | 8.9679 | 8.8971 | 8.7627 | 8.6725 | 8.4783 | 8.3395 | 8.1915 | 8.0075 | 6.8967 | 5.7122 | 4.2476 | 9.1937 | 9.1794 | 9.1124 | 9.0551 | 9.004 | 8.8926 | 8.8277 | 8.6622 | 8.5477 | 8.3993 | 8.2114 | 7.018 | 6.1005 | 5.2484
|  | BALNAGASK | FS |  |  |  | 9.7684 | 9.7557 | 9.7317 | 9.7067 | 9.6775 | 9.644 | 9.5949 | 9.4817 | 9.3728 | 9.2508 | 9.1181 | 8.2815 | 7.3697 | 6.7187 | 9.1547 | 9.1279 | 9.0781 | 9.0231 | 8.9617 | 8.8899 | 8.8131 | 8.6893 | 8.5685 | 8.4337 | 8.2848 | 7.3524 | 5.9716 | 3.9398 | 9.2029 | 9.1915 | 9.1673 | 9.1422 | 9.1129 | 9.0799 | 9.0445 | 8.9743 | 8.9116 | 8.7887 | 8.6553 | 7.8606 | 7.0188 | 6.4467
| KINTORE | BANCHORY | MINIMUM HEADROOM | NO 69262 96297 | NO | YES | 2.7463 | 2.2781 | 1.5928 | 0.86735 | 0.15038 | -0.73761 | -1.9665 | -2.8336 | -3.5978 | -4.4334 | -5.2373 | -7.4224 | -8.6968 | -9.5471 | 6.2808 | 6.0062 | 5.6715 | 5.3033 | 4.9029 | 4.4319 | 3.5992 | 2.9494 | 2.4104 | 1.8354 | 1.2903 | -0.16074 | -1.303 | -2.3994 | 4.6768 | 4.2116 | 3.5958 | 2.9308 | 2.2883 | 1.4279 | 0.23646 | -0.6859 | -1.515 | -2.3894 | -3.2198 | -5.2549 | -6.2574 | -6.9791
|  | BANCHORY | CT |  |  |  | 3.2059 | 2.883 | 2.1239 | 1.3308 | 0.59547 | -0.20031 | -1.2547 | -2.1131 | -2.8865 | -3.7163 | -4.5331 | -7.0029 | -8.6968 | -9.5471 | 6.4335 | 6.2076 | 5.7745 | 5.309 | 4.9029 | 4.4462 | 3.7623 | 3.1569 | 2.6001 | 2.0324 | 1.4859 | -0.16074 | -1.303 | -2.3994 | 5.0488 | 4.7157 | 3.9894 | 3.217 | 2.5395 | 1.8073 | 0.84876 | -0.0044635 | -0.84328 | -1.6977 | -2.5148 | -4.852 | -6.2574 | -6.9791
|  | BANCHORY | LW |  |  |  | 2.7463 | 2.2781 | 1.5928 | 0.86735 | 0.15038 | -0.73761 | -1.9665 | -2.8336 | -3.5978 | -4.4334 | -5.2373 | -7.4224 | -8.4562 | -9.036 | 6.2808 | 6.0062 | 5.6715 | 5.3033 | 4.9508 | 4.4319 | 3.5992 | 2.9494 | 2.4104 | 1.8354 | 1.2903 | -0.021005 | -0.57589 | -0.98265 | 4.6768 | 4.2116 | 3.5958 | 2.9308 | 2.2883 | 1.4279 | 0.23646 | -0.6859 | -1.515 | -2.3894 | -3.2198 | -5.2549 | -6.1653 | -6.7336
|  | BANCHORY | ST |  |  |  | 3.477 | 3.334 | 3.1226 | 2.8934 | 2.6468 | 2.3217 | 1.7263 | 1.2124 | 0.79943 | 0.35156 | -0.12795 | -3.1652 | -4.7643 | -6.1599 | 6.5641 | 6.4679 | 6.318 | 6.151 | 5.9715 | 5.7066 | 5.2045 | 4.7661 | 4.4216 | 4.0398 | 3.623 | 1.3512 | 0.10134 | -1.2097 | 5.2809 | 5.1391 | 4.9248 | 4.6859 | 4.429 | 4.0838 | 3.494 | 2.9589 | 2.4951 | 1.9844 | 1.429 | -1.5988 | -3.0678 | -4.268
|  | BANCHORY | FS |  |  |  | 3.565 | 3.4616 | 3.2821 | 3.0876 | 2.8806 | 2.6377 | 2.178 | 1.7394 | 1.3811 | 0.99514 | 0.60146 | -2.1163 | -4.7412 | -6.337 | 6.5999 | 6.522 | 6.4074 | 6.2752 | 6.132 | 5.9525 | 5.5721 | 5.234 | 4.9624 | 4.6611 | 4.3449 | 2.2684 | -0.030625 | -2.14 | 5.3552 | 5.2497 | 5.0758 | 4.8805 | 4.6722 | 4.426 | 3.9787 | 3.5486 | 3.1773 | 2.7726 | 2.3511 | -0.43468 | -2.9539 | -4.3296
| TAYNUILT | BARCALDINE | MINIMUM HEADROOM | NM 96356 42181 | YES | YES | -2.4344 | -2.4994 | -2.5822 | -2.6786 | -2.7786 | -2.8907 | -2.9922 | -3.0404 | -3.1112 | -3.1877 | -3.2503 | -3.3977 | -3.5006 | -3.5665 | -2.3549 | -2.3811 | -2.4302 | -2.5039 | -2.5692 | -2.641 | -2.7029 | -2.7498 | -2.8139 | -2.8786 | -2.9342 | -3.0686 | -3.1583 | -3.2396 | -2.8188 | -2.8828 | -2.9625 | -3.0638 | -3.1642 | -3.279 | -3.3865 | -3.4388 | -3.5138 | -3.5893 | -3.6514 | -3.7911 | -3.9091 | -3.9819
|  | BARCALDINE | CT |  |  |  | -2.3943 | -2.4462 | -2.563 | -2.6786 | -2.7786 | -2.8907 | -2.9922 | -3.0404 | -3.1112 | -3.1877 | -3.2503 | -3.3852 | -3.5006 | -3.5664 | -2.3549 | -2.3774 | -2.4302 | -2.5039 | -2.5692 | -2.641 | -2.7029 | -2.7498 | -2.8139 | -2.8786 | -2.9342 | -3.0686 | -3.1583 | -3.2396 | -2.7808 | -2.8339 | -2.9485 | -3.0638 | -3.1642 | -3.279 | -3.3865 | -3.4388 | -3.5138 | -3.5893 | -3.6514 | -3.7911 | -3.9091 | -3.9802
|  | BARCALDINE | LW |  |  |  | -2.4344 | -2.4994 | -2.5822 | -2.6588 | -2.735 | -2.8296 | -2.9418 | -3.0114 | -3.0854 | -3.1682 | -3.2437 | -3.3977 | -3.4909 | -3.5665 | -2.3549 | -2.3811 | -2.4288 | -2.4751 | -2.5192 | -2.5816 | -2.6555 | -2.7168 | -2.7826 | -2.8506 | -2.9127 | -3.032 | -3.1106 | -3.1923 | -2.8188 | -2.8828 | -2.9625 | -3.0378 | -3.1121 | -3.2072 | -3.3228 | -3.3976 | -3.477 | -3.5606 | -3.6363 | -3.7893 | -3.8921 | -3.9819
|  | BARCALDINE | ST |  |  |  | -2.3742 | -2.3961 | -2.4342 | -2.4747 | -2.5075 | -2.5598 | -2.6047 | -2.6662 | -2.7256 | -2.7909 | -2.8663 | -3.2555 | -3.3967 | -3.4808 | -2.3486 | -2.3551 | -2.3738 | -2.3891 | -2.4105 | -2.4548 | -2.4903 | -2.5409 | -2.5887 | -2.6416 | -2.7031 | -3.0127 | -3.137 | -3.2292 | -2.7618 | -2.7834 | -2.8234 | -2.8654 | -2.9004 | -2.9572 | -3.0043 | -3.0705 | -3.1338 | -3.2036 | -3.2844 | -3.678 | -3.8202 | -3.9065
|  | BARCALDINE | FS |  |  |  | -2.358 | -2.3753 | -2.4054 | -2.4332 | -2.4667 | -2.4986 | -2.535 | -2.5761 | -2.6189 | -2.6692 | -2.7206 | -3.0661 | -3.3416 | -3.4208 | -2.3467 | -2.352 | -2.3606 | -2.3685 | -2.3777 | -2.3993 | -2.4256 | -2.457 | -2.49 | -2.5279 | -2.5679 | -2.8223 | -3.0402 | -3.1318 | -2.7465 | -2.7631 | -2.793 | -2.8214 | -2.8552 | -2.8882 | -2.9254 | -2.9685 | -3.0132 | -3.0656 | -3.1193 | -3.4715 | -3.7383 | -3.8145
| STORNOWAY | BARVAS | MINIMUM HEADROOM | NB 35613 48891 | NO | YES | 0.6207 | 0.47863 | 0.31536 | 0.13855 | -0.02485 | -0.21325 | -0.41277 | -0.51613 | -0.62404 | -0.73754 | -0.83619 | -1.0578 | -1.252 | -1.3426 | 1.3737 | 1.3337 | 1.2966 | 1.2526 | 1.2141 | 1.1651 | 1.1059 | 1.0072 | 0.90197 | 0.79368 | 0.69726 | 0.54135 | 0.41994 | 0.33201 | 0.3542 | 0.31101 | 0.26735 | 0.16907 | 0.045269 | -0.13686 | -0.33193 | -0.44722 | -0.56828 | -0.69804 | -0.83883 | -1.0916 | -1.2509 | -1.3378
|  | BARVAS | CT |  |  |  | 0.7574 | 0.65856 | 0.44327 | 0.22087 | 0.020777 | -0.17823 | -0.36993 | -0.4536 | -0.55907 | -0.6704 | -0.76724 | -0.96247 | -1.252 | -1.3426 | 1.3957 | 1.365 | 1.3141 | 1.2637 | 1.2169 | 1.1715 | 1.1296 | 1.0667 | 0.9611 | 0.85161 | 0.75846 | 0.56269 | 0.41994 | 0.33201 | 0.38348 | 0.34453 | 0.28422 | 0.21509 | 0.077849 | -0.10672 | -0.28474 | -0.37655 | -0.4962 | -0.62162 | -0.74047 | -1.007 | -1.2509 | -1.3378
|  | BARVAS | LW |  |  |  | 0.6207 | 0.47863 | 0.31536 | 0.13855 | -0.02485 | -0.21325 | -0.41277 | -0.51613 | -0.62404 | -0.73754 | -0.83619 | -1.0578 | -1.1978 | -1.2396 | 1.3737 | 1.3337 | 1.2966 | 1.2526 | 1.2141 | 1.1651 | 1.1059 | 1.0072 | 0.90197 | 0.79368 | 0.69726 | 0.54135 | 0.48544 | 0.47052 | 0.3542 | 0.31101 | 0.26735 | 0.16907 | 0.045269 | -0.13686 | -0.33193 | -0.44722 | -0.56828 | -0.69804 | -0.83883 | -1.0916 | -1.2089 | -1.2419
|  | BARVAS | ST |  |  |  | 0.81707 | 0.7586 | 0.67752 | 0.5944 | 0.5058 | 0.4196 | 0.33159 | 0.22854 | 0.11989 | 0.0039365 | -0.1192 | -0.70824 | -0.96265 | -1.1181 | 1.4095 | 1.3928 | 1.3733 | 1.3526 | 1.3248 | 1.2969 | 1.2697 | 1.238 | 1.2014 | 1.1604 | 1.1151 | 0.68584 | 0.53167 | 0.43197 | 0.40245 | 0.38156 | 0.35635 | 0.3296 | 0.3003 | 0.26982 | 0.23909 | 0.19595 | 0.13144 | 0.037286 | -0.088079 | -0.77032 | -1.0126 | -1.138
|  | BARVAS | FS |  |  |  | 0.89064 | 0.84551 | 0.77411 | 0.7031 | 0.63309 | 0.55801 | 0.48295 | 0.38626 | 0.2869 | 0.18126 | 0.073163 | -0.65729 | -1.0891 | -1.2296 | 1.4441 | 1.4311 | 1.4135 | 1.3965 | 1.3804 | 1.3585 | 1.3343 | 1.306 | 1.2754 | 1.2424 | 1.2072 | 0.83007 | 0.47902 | 0.35779 | 0.43933 | 0.42302 | 0.40024 | 0.37781 | 0.35603 | 0.33195 | 0.3056 | 0.27497 | 0.23819 | 0.17528 | 0.10597 | -0.61016 | -1.1053 | -1.2137
| STORNOWAY | BATTERY POINT | MINIMUM HEADROOM | NB 43147 32182 | NO | YES | 4.1389 | 3.1348 | 1.9577 | 14.2182 | 12.8366 | 11.3223 | 9.9831 | 8.9553 | 7.8813 | 6.5223 | 5.1934 | 3.3525 | 2.3389 | 1.593 | 8.1746 | 7.3271 | 6.3649 | 18.1422 | 16.8796 | 15.5013 | 14.3569 | 13.3608 | 12.3612 | 11.1049 | 9.6826 | 7.3992 | 5.862 | 5.2474 | 5.646 | 4.573 | 3.3207 | 14.7882 | 13.2715 | 11.6178 | 10.1824 | 9.0272 | 7.8466 | 6.5174 | 5.2179 | 3.3133 | 2.275 | 1.4102
|  | BATTERY POINT | CT |  |  |  | 4.4666 | 3.6403 | 2.3972 | 14.5308 | 13.1361 | 11.7132 | 10.5067 | 9.5561 | 8.5281 | 7.2509 | 6.0021 | 4.1869 | 3.0258 | 2.4715 | 8.3041 | 7.5717 | 6.6266 | 18.3361 | 17.1622 | 15.9329 | 14.96 | 14.016 | 13.0035 | 11.8287 | 10.5059 | 8.4456 | 7.9013 | 7.5616 | 5.9377 | 5.0439 | 3.761 | 15.1073 | 13.613 | 12.1051 | 10.857 | 9.785 | 8.6183 | 7.3776 | 6.1642 | 4.3069 | 3.219 | 2.647
|  | BATTERY POINT | LW |  |  |  | 4.1389 | 3.1348 | 1.9577 | 14.2182 | 12.8366 | 11.3223 | 9.9831 | 8.9553 | 7.8813 | 6.5223 | 5.1934 | 3.3525 | 2.3389 | 1.593 | 8.1746 | 7.3271 | 6.3649 | 18.1422 | 16.8796 | 15.5013 | 14.3569 | 13.3608 | 12.3612 | 11.1049 | 9.6826 | 7.75 | 6.9128 | 6.1715 | 5.646 | 4.573 | 3.3207 | 14.7882 | 13.2715 | 11.6178 | 10.1824 | 9.0272 | 7.8466 | 6.5174 | 5.2179 | 3.3133 | 2.275 | 1.4102
|  | BATTERY POINT | ST |  |  |  | 4.7548 | 4.1404 | 3.3929 | 16.0458 | 15.1442 | 14.1451 | 13.3287 | 12.4078 | 11.4366 | 10.1786 | 8.8513 | 4.2545 | 2.3534 | 1.6057 | 8.4538 | 7.8633 | 7.1343 | 19.0918 | 18.1297 | 16.9934 | 16.1225 | 15.1612 | 14.0926 | 12.7104 | 11.2394 | 7.3992 | 5.862 | 5.2474 | 6.2006 | 5.5082 | 4.6582 | 16.4692 | 15.4261 | 14.2764 | 13.3563 | 12.3234 | 11.2466 | 10.0324 | 8.748 | 4.3652 | 2.5333 | 1.6932
|  | BATTERY POINT | FS |  |  |  | 4.8928 | 4.4258 | 3.8647 | 16.7115 | 16.0055 | 15.3153 | 14.6499 | 13.9112 | 13.1244 | 12.2026 | 11.2489 | 7.6388 | 4.5613 | 2.532 | 8.5418 | 8.0913 | 7.579 | 19.7491 | 19.0598 | 18.3741 | 17.7038 | 16.9467 | 16.1464 | 15.2622 | 14.3528 | 11.1151 | 8.1009 | 6.488 | 6.2874 | 5.8116 | 5.1925 | 17.2382 | 16.4277 | 15.6438 | 14.8949 | 14.0667 | 13.1868 | 12.2638 | 11.3299 | 7.7814 | 4.7569 | 2.8101
| MYBSTER | BETTYHILL | MINIMUM HEADROOM | NC 70763 61645 | YES | YES | 0.15969 | 0.12709 | 0.092767 | 0.055667 | -0.014382 | -0.088311 | -0.13902 | -0.17745 | -0.22419 | -0.27091 | -0.31142 | -0.43724 | -0.58092 | -0.71339 | 0.38866 | 0.36807 | 0.34787 | 0.3118 | 0.25208 | 0.18883 | 0.15416 | 0.11554 | 0.06908 | 0.023706 | -0.018053 | -0.17728 | -0.34152 | -0.49226 | 0.19027 | 0.1591 | 0.1267 | 0.084843 | 0.010548 | -0.067974 | -0.1179 | -0.16128 | -0.21416 | -0.26657 | -0.31256 | -0.45978 | -0.63254 | -0.78462
|  | BETTYHILL | CT |  |  |  | 0.18142 | 0.16056 | 0.1089 | 0.055667 | -0.014382 | -0.088311 | -0.13902 | -0.17745 | -0.22419 | -0.27091 | -0.31142 | -0.43724 | -0.55721 | -0.64845 | 0.39787 | 0.38329 | 0.34911 | 0.3118 | 0.25208 | 0.18883 | 0.15416 | 0.11554 | 0.06908 | 0.023706 | -0.018053 | -0.15802 | -0.27228 | -0.38223 | 0.20875 | 0.18823 | 0.13772 | 0.084843 | 0.010548 | -0.067974 | -0.1179 | -0.16128 | -0.21416 | -0.26657 | -0.31256 | -0.45978 | -0.58959 | -0.69548
|  | BETTYHILL | LW |  |  |  | 0.15969 | 0.12709 | 0.092767 | 0.056189 | 0.020955 | -0.02301 | -0.070118 | -0.10733 | -0.14891 | -0.18711 | -0.22321 | -0.30519 | -0.45379 | -0.63886 | 0.38866 | 0.36807 | 0.34787 | 0.32566 | 0.30537 | 0.27581 | 0.24307 | 0.20817 | 0.17015 | 0.13408 | 0.10007 | 0.024495 | -0.13889 | -0.3627 | 0.19027 | 0.1591 | 0.1267 | 0.09204 | 0.059261 | 0.015888 | -0.03084 | -0.072175 | -0.11767 | -0.15999 | -0.19985 | -0.28861 | -0.46307 | -0.6909
|  | BETTYHILL | ST |  |  |  | 0.19119 | 0.18075 | 0.14118 | 0.10215 | 0.074842 | 0.01814 | -0.017407 | -0.071275 | -0.11121 | -0.14998 | -0.19738 | -0.42229 | -0.58092 | -0.71339 | 0.40408 | 0.3976 | 0.35673 | 0.32203 | 0.29686 | 0.23502 | 0.20457 | 0.14945 | 0.11429 | 0.079703 | 0.03571 | -0.17728 | -0.34152 | -0.49226 | 0.21864 | 0.20919 | 0.16395 | 0.12212 | 0.092885 | 0.026683 | -0.011062 | -0.072381 | -0.11542 | -0.15715 | -0.20928 | -0.45563 | -0.63254 | -0.78462
|  | BETTYHILL | FS |  |  |  | 0.19989 | 0.19201 | 0.17347 | 0.15322 | 0.13076 | 0.10817 | 0.08566 | 0.053003 | 0.022716 | -0.008034 | -0.040261 | -0.21786 | -0.34127 | -0.37733 | 0.40813 | 0.40295 | 0.38854 | 0.37272 | 0.35502 | 0.3367 | 0.31837 | 0.29036 | 0.26529 | 0.23928 | 0.21181 | 0.07861 | -0.026522 | -0.070331 | 0.22646 | 0.21913 | 0.20052 | 0.18012 | 0.15736 | 0.13448 | 0.11141 | 0.076969 | 0.045232 | 0.013006 | -0.020882 | -0.19974 | -0.32771 | -0.36397
| GRUDIE BRIDGE | BIDEN CLAN RAONAILD | MINIMUM HEADROOM | NH 06927 58342 | YES | YES | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075
|  | BIDEN CLAN RAONAILD | CT |  |  |  | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075
|  | BIDEN CLAN RAONAILD | LW |  |  |  | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075
|  | BIDEN CLAN RAONAILD | ST |  |  |  | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075
|  | BIDEN CLAN RAONAILD | FS |  |  |  | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.11619 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.10774 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075 | 0.1075
| ELGIN | BILBOHALL | MINIMUM HEADROOM | NJ 20782 61556 | YES | YES | 19.1178 | 19.0221 | 18.3961 | 17.6746 | 16.3907 | 15.0031 | 14.1012 | 13.7489 | 13.3754 | 13.0193 | 12.7038 | 11.5288 | 11.1002 | 10.8775 | 18.5049 | 18.4526 | 17.767 | 16.989 | 15.5063 | 13.9144 | 12.9434 | 12.6312 | 12.3026 | 12.0045 | 11.7141 | 10.5028 | 10.0902 | 9.8537 | 17.905 | 17.8823 | 17.2398 | 16.5121 | 15.0761 | 13.5416 | 12.6339 | 12.3727 | 12.0991 | 11.8579 | 11.6108 | 10.2819 | 9.7946 | 9.5357
|  | BILBOHALL | CT |  |  |  | 19.2041 | 19.143 | 18.9384 | 18.6548 | 17.9702 | 17.2456 | 16.9401 | 16.6896 | 16.4034 | 16.1163 | 15.8734 | 15.0091 | 14.5892 | 14.3881 | 18.5388 | 18.5015 | 18.3458 | 18.1137 | 17.3685 | 16.5765 | 16.3126 | 16.1216 | 15.9077 | 15.7001 | 15.5095 | 14.7449 | 14.3832 | 14.0881 | 17.9055 | 17.8828 | 17.772 | 17.5953 | 16.8956 | 16.1508 | 15.9354 | 15.7997 | 15.6603 | 15.5306 | 15.3984 | 14.6118 | 14.1824 | 13.9749
|  | BILBOHALL | LW |  |  |  | 19.1178 | 19.0221 | 18.3961 | 17.6746 | 16.3907 | 15.0031 | 14.1012 | 13.7489 | 13.3754 | 13.0193 | 12.7038 | 11.5288 | 11.1002 | 10.8775 | 18.5049 | 18.4526 | 17.767 | 16.989 | 15.5063 | 13.9144 | 12.9434 | 12.6312 | 12.3026 | 12.0045 | 11.7141 | 10.5028 | 10.0902 | 9.8537 | 17.905 | 17.8823 | 17.2398 | 16.5121 | 15.0761 | 13.5416 | 12.6339 | 12.3727 | 12.0991 | 11.8579 | 11.6108 | 10.2819 | 9.7946 | 9.5357
|  | BILBOHALL | ST |  |  |  | 19.2348 | 19.2092 | 18.6874 | 18.3014 | 18.0213 | 17.2129 | 16.9296 | 16.6784 | 16.5168 | 16.3512 | 16.1716 | 15.2275 | 14.7615 | 14.4028 | 18.5549 | 18.5396 | 17.9155 | 17.4735 | 17.1664 | 16.2013 | 15.8962 | 15.6376 | 15.4982 | 15.3606 | 15.1922 | 14.3326 | 13.8964 | 13.518 | 17.9153 | 17.9083 | 17.2984 | 16.8719 | 16.5809 | 15.6337 | 15.348 | 15.1128 | 14.9993 | 14.8896 | 14.7492 | 14.0726 | 13.8016 | 13.6714
|  | BILBOHALL | FS |  |  |  | 19.252 | 19.2304 | 19.1005 | 18.9497 | 18.7805 | 18.6088 | 18.4435 | 18.3016 | 18.1727 | 18.0349 | 17.9105 | 17.2907 | 16.7947 | 16.5301 | 18.5623 | 18.5491 | 18.407 | 18.2527 | 18.0765 | 17.8973 | 17.7326 | 17.6071 | 17.4998 | 17.3859 | 17.2768 | 16.8107 | 16.3424 | 15.8724 | 17.9173 | 17.9116 | 17.7816 | 17.6422 | 17.4811 | 17.3179 | 17.1723 | 17.0739 | 16.9959 | 16.9142 | 16.8383 | 16.609 | 16.4403 | 16.3598
| RANNOCH | BLACKMOUNT | MINIMUM HEADROOM | NN 30077 41404 | YES | YES | 0.033813 | 0.030931 | 0.028191 | 0.023903 | 0.022873 | 0.020427 | 0.012564 | 0.011279 | 0.007665 | 0.0023687 | -0.003196 | -0.013717 | -0.016924 | -0.018693 | 0.0077902 | 0.0063205 | 0.0049141 | 0.0022782 | 0.0014026 | 0.0001082 | -0.0033475 | -0.0050438 | -0.0088588 | -0.01292 | -0.016807 | -0.02496 | -0.027283 | -0.028395 | 0.0016714 | -0.0009596 | -0.0034169 | -0.0074329 | -0.0084937 | -0.0098986 | -0.017568 | -0.017611 | -0.019634 | -0.022733 | -0.02804 | -0.038171 | -0.04124 | -0.042895
|  | BLACKMOUNT | CT |  |  |  | 0.033813 | 0.032718 | 0.029256 | 0.023903 | 0.022873 | 0.020427 | 0.012564 | 0.011279 | 0.0087074 | 0.0061292 | 0.0029028 | -0.005759 | -0.0073804 | -0.0070348 | 0.0077902 | 0.0068797 | 0.0049141 | 0.0022782 | 0.0014026 | 0.0001082 | -0.0033475 | -0.0050438 | -0.0070468 | -0.009056 | -0.011778 | -0.018999 | -0.019657 | -0.01983 | 0.0016714 | 0.00056258 | -0.0026316 | -0.0074329 | -0.0084937 | -0.0098986 | -0.017568 | -0.017611 | -0.019634 | -0.021696 | -0.023426 | -0.030521 | -0.031986 | -0.031707
|  | BLACKMOUNT | LW |  |  |  | 0.033842 | 0.030931 | 0.028191 | 0.02724 | 0.024437 | 0.02346 | 0.018321 | 0.012669 | 0.007665 | 0.0023687 | -0.003196 | -0.013717 | -0.015079 | -0.015079 | 0.0078211 | 0.0063205 | 0.0049629 | 0.0041548 | 0.0027584 | 0.0019708 | -0.0013201 | -0.0050229 | -0.0088588 | -0.01292 | -0.016807 | -0.02496 | -0.025841 | -0.025841 | 0.0016741 | -0.0009596 | -0.0034169 | -0.004416 | -0.0069215 | -0.0072528 | -0.010856 | -0.014765 | -0.017632 | -0.022733 | -0.02804 | -0.038171 | -0.039439 | -0.039439
|  | BLACKMOUNT | ST |  |  |  | 0.034214 | 0.033932 | 0.033545 | 0.03303 | 0.032426 | 0.031709 | 0.02851 | 0.026082 | 0.022253 | 0.018618 | 0.014466 | -0.010736 | -0.016924 | -0.017028 | 0.0081025 | 0.0078481 | 0.0075087 | 0.0070568 | 0.0065325 | 0.0064416 | 0.004284 | 0.0033019 | 0.00085233 | -0.0019298 | -0.0051095 | -0.022535 | -0.027283 | -0.027389 | 0.0020577 | 0.0017647 | 0.0013638 | 0.00082637 | 0.00020236 | 0.00075911 | -0.0034366 | -0.0046253 | -0.0073463 | -0.0090374 | -0.011436 | -0.035284 | -0.04124 | -0.04134
|  | BLACKMOUNT | FS |  |  |  | 0.03429 | 0.034068 | 0.033778 | 0.033405 | 0.03299 | 0.032488 | 0.02995 | 0.030729 | 0.028105 | 0.026174 | 0.022805 | 0.0048033 | -0.010093 | -0.018693 | 0.0081578 | 0.0079494 | 0.0076896 | 0.007355 | 0.0069859 | 0.006541 | 0.005332 | 0.0052663 | 0.0038536 | 0.0030216 | 0.0013996 | -0.010637 | -0.021768 | -0.028395 | 0.0021335 | 0.0019029 | 0.0016002 | 0.0012078 | 0.00077531 | 0.00025319 | -0.0019892 | -0.001401 | -0.0038954 | -0.0048881 | -0.0076316 | -0.020326 | -0.034622 | -0.042895
| BEAULY | BLACKSTAND | MINIMUM HEADROOM | NH 71036 59151 | YES | YES | 3.9816 | 3.8378 | 3.6911 | 3.5343 | 3.3622 | 3.1432 | 2.9304 | 2.7952 | 2.6295 | 2.4659 | 2.3092 | 1.8787 | 1.2361 | 0.42027 | 4.6634 | 4.5892 | 4.5181 | 4.4292 | 4.2987 | 4.1621 | 4.0515 | 3.9381 | 3.7979 | 3.6567 | 3.5228 | 3.0794 | 2.4687 | 1.5671 | 3.9976 | 3.8816 | 3.7645 | 3.6382 | 3.4714 | 3.2795 | 3.1089 | 2.9737 | 2.8118 | 2.6535 | 2.506 | 2.0531 | 1.3723 | 0.389
|  | BLACKSTAND | CT |  |  |  | 4.0823 | 3.9814 | 3.7809 | 3.5737 | 3.3622 | 3.1432 | 2.9304 | 2.7952 | 2.6295 | 2.4659 | 2.3144 | 1.8787 | 1.365 | 0.96382 | 4.7018 | 4.6466 | 4.5415 | 4.4292 | 4.2987 | 4.1621 | 4.0515 | 3.9381 | 3.7979 | 3.6567 | 3.5228 | 3.0794 | 2.5988 | 2.0842 | 4.0743 | 3.9928 | 3.8286 | 3.6561 | 3.4714 | 3.2795 | 3.1089 | 2.9737 | 2.8118 | 2.6535 | 2.506 | 2.0531 | 1.5356 | 1.0871
|  | BLACKSTAND | LW |  |  |  | 3.9816 | 3.8378 | 3.6911 | 3.5343 | 3.3849 | 3.1997 | 2.9708 | 2.8095 | 2.6394 | 2.4676 | 2.3092 | 1.8828 | 1.2361 | 0.42027 | 4.6634 | 4.5892 | 4.5181 | 4.4405 | 4.3696 | 4.2697 | 4.1471 | 4.016 | 3.871 | 3.7294 | 3.5946 | 3.2228 | 2.5266 | 1.5671 | 3.9976 | 3.8816 | 3.7645 | 3.6382 | 3.5212 | 3.3661 | 3.1779 | 3.0221 | 2.8575 | 2.6941 | 2.5412 | 2.1144 | 1.3723 | 0.389
|  | BLACKSTAND | ST |  |  |  | 4.1329 | 4.0701 | 3.9715 | 3.8769 | 3.7907 | 3.6544 | 3.537 | 3.3564 | 3.2139 | 3.068 | 2.898 | 2.087 | 1.459 | 0.89867 | 4.7259 | 4.6932 | 4.6191 | 4.5532 | 4.4958 | 4.3859 | 4.3099 | 4.15 | 4.0457 | 3.9385 | 3.8017 | 3.1283 | 2.4687 | 1.7886 | 4.1152 | 4.0663 | 3.9739 | 3.8883 | 3.8125 | 3.6801 | 3.5789 | 3.3952 | 3.2642 | 3.1313 | 2.9714 | 2.2051 | 1.5337 | 0.90429
|  | BLACKSTAND | FS |  |  |  | 4.1668 | 4.1189 | 4.0572 | 3.9868 | 3.9142 | 3.8402 | 3.748 | 3.6308 | 3.5151 | 3.3987 | 3.2707 | 2.5577 | 2.0792 | 1.891 | 4.7396 | 4.7132 | 4.6767 | 4.6351 | 4.591 | 4.5445 | 4.4886 | 4.4022 | 4.3222 | 4.2395 | 4.1499 | 3.6811 | 3.2686 | 2.9629 | 4.1407 | 4.1032 | 4.0518 | 3.9929 | 3.9317 | 3.8688 | 3.7918 | 3.6838 | 3.5805 | 3.4759 | 3.3615 | 2.7582 | 2.3417 | 2.1767
| COUPAR ANGUS | BLAIRGOWRIE | MINIMUM HEADROOM | NO 18741 44551 | NO | YES | 13.7366 | 13.1898 | 12.3286 | 11.4154 | 10.3639 | 9.166 | 7.9833 | 6.7039 | 5.3262 | 3.9526 | 3.0566 | 0.54835 | -0.52971 | -1.0269 | 15.5785 | 15.2292 | 14.7335 | 14.1902 | 13.5329 | 12.7583 | 12.0372 | 11.1644 | 10.2022 | 9.237 | 8.6424 | 7.1984 | 6.5859 | 5.7862 | 14.5948 | 14.0988 | 13.3214 | 12.4881 | 11.5178 | 10.3916 | 9.2947 | 8.1079 | 6.8238 | 5.5395 | 4.6858 | 2.4193 | 1.4437 | 0.92427
|  | BLAIRGOWRIE | CT |  |  |  | 14.112 | 13.7216 | 12.9256 | 12.0614 | 11.1161 | 10.1202 | 9.1963 | 7.9461 | 6.5052 | 5.0677 | 4.0916 | 1.2734 | -0.22482 | -1.0269 | 15.7173 | 15.437 | 14.9693 | 14.4399 | 13.8411 | 13.2134 | 12.697 | 11.8864 | 10.9001 | 9.9141 | 9.2905 | 7.5864 | 6.6507 | 5.7862 | 14.9134 | 14.5554 | 13.8321 | 13.0372 | 12.1654 | 11.2479 | 10.4279 | 9.2928 | 7.9636 | 6.6361 | 5.7274 | 3.1647 | 1.8577 | 1.1396
|  | BLAIRGOWRIE | LW |  |  |  | 13.7366 | 13.1898 | 12.3286 | 11.4154 | 10.3639 | 9.166 | 7.9833 | 6.7039 | 5.3262 | 3.9526 | 3.0566 | 0.54835 | -0.52971 | -1.0234 | 15.5785 | 15.2292 | 14.7335 | 14.1902 | 13.5329 | 12.7583 | 12.0372 | 11.1644 | 10.2022 | 9.237 | 8.6424 | 7.1984 | 6.5859 | 6.1699 | 14.5948 | 14.0988 | 13.3214 | 12.4881 | 11.5178 | 10.3916 | 9.2947 | 8.1079 | 6.8238 | 5.5395 | 4.6858 | 2.4193 | 1.4437 | 0.92427
|  | BLAIRGOWRIE | ST |  |  |  | 14.3136 | 14.0599 | 13.707 | 13.3337 | 12.9412 | 12.4143 | 11.9891 | 11.2583 | 10.3782 | 9.4731 | 8.9355 | 6.4903 | 5.1179 | 3.6588 | 15.8121 | 15.6258 | 15.3143 | 14.9952 | 14.678 | 14.2069 | 13.8685 | 13.2642 | 12.5384 | 11.7895 | 11.3389 | 9.4031 | 8.3903 | 7.2877 | 15.091 | 14.8681 | 14.5184 | 14.1554 | 13.7864 | 13.2571 | 12.8543 | 12.1671 | 11.3436 | 10.4917 | 9.9618 | 7.5278 | 6.2688 | 4.9991
|  | BLAIRGOWRIE | FS |  |  |  | 14.3635 | 14.1589 | 13.898 | 13.5952 | 13.2651 | 12.9117 | 12.5564 | 11.9327 | 11.265 | 10.5844 | 10.0871 | 7.5135 | 5.2045 | 3.6862 | 15.8458 | 15.694 | 15.5015 | 15.2697 | 15.0192 | 14.7537 | 14.4852 | 13.9996 | 13.476 | 12.9309 | 12.5303 | 10.5355 | 8.5315 | 6.8007 | 15.1358 | 14.9584 | 14.7229 | 14.4451 | 14.1454 | 13.8249 | 13.5013 | 12.9335 | 12.3238 | 11.6963 | 11.2269 | 8.7864 | 6.5972 | 5.282
| STRATHLEVEN | BLAIRLINNANS | MINIMUM HEADROOM | NS 40709 85121 | YES | YES | 0.45418 | 0.44685 | 0.43746 | 0.43134 | 0.42516 | 0.4187 | 0.41265 | 0.40143 | 0.37312 | 0.34469 | 0.31759 | 0.26421 | 0.23876 | 0.2301 | 0.59568 | 0.58485 | 0.57046 | 0.56159 | 0.55217 | 0.54231 | 0.53235 | 0.51375 | 0.49277 | 0.47136 | 0.45182 | 0.41729 | 0.40051 | 0.39881 | 0.52906 | 0.51913 | 0.50627 | 0.49838 | 0.49023 | 0.48162 | 0.47316 | 0.45855 | 0.44041 | 0.42192 | 0.40521 | 0.37672 | 0.36262 | 0.3613
|  | BLAIRLINNANS | CT |  |  |  | 0.45418 | 0.44685 | 0.43746 | 0.43134 | 0.42516 | 0.4187 | 0.41265 | 0.40311 | 0.39533 | 0.38134 | 0.35565 | 0.29454 | 0.28065 | 0.27819 | 0.59568 | 0.58485 | 0.57046 | 0.56159 | 0.55217 | 0.54231 | 0.53235 | 0.51783 | 0.50673 | 0.49553 | 0.47708 | 0.43291 | 0.43033 | 0.42993 | 0.52906 | 0.51913 | 0.50627 | 0.49838 | 0.49023 | 0.48162 | 0.47316 | 0.4603 | 0.45038 | 0.44041 | 0.42392 | 0.3855 | 0.3836 | 0.38329
|  | BLAIRLINNANS | LW |  |  |  | 0.45681 | 0.45067 | 0.44565 | 0.44054 | 0.43519 | 0.42543 | 0.41398 | 0.40143 | 0.37312 | 0.34469 | 0.31759 | 0.26421 | 0.25972 | 0.25787 | 0.59953 | 0.58964 | 0.58198 | 0.57376 | 0.56533 | 0.5506 | 0.53299 | 0.51375 | 0.49277 | 0.47136 | 0.45182 | 0.41729 | 0.41679 | 0.41669 | 0.53298 | 0.52426 | 0.51769 | 0.5105 | 0.50343 | 0.49052 | 0.4753 | 0.45855 | 0.44041 | 0.42192 | 0.40521 | 0.37672 | 0.3765 | 0.37644
|  | BLAIRLINNANS | ST |  |  |  | 0.45988 | 0.45793 | 0.45627 | 0.45307 | 0.44901 | 0.44417 | 0.4383 | 0.43105 | 0.42234 | 0.41235 | 0.40109 | 0.27891 | 0.23876 | 0.2301 | 0.60402 | 0.6012 | 0.59734 | 0.59243 | 0.58636 | 0.57888 | 0.56978 | 0.55872 | 0.54543 | 0.53009 | 0.51268 | 0.42465 | 0.40051 | 0.399 | 0.53686 | 0.53442 | 0.53113 | 0.52689 | 0.52164 | 0.51518 | 0.50732 | 0.49776 | 0.48618 | 0.47289 | 0.45794 | 0.38267 | 0.36262 | 0.36147
|  | BLAIRLINNANS | FS |  |  |  | 0.46036 | 0.45889 | 0.45746 | 0.45552 | 0.45261 | 0.44927 | 0.44544 | 0.441 | 0.43566 | 0.42985 | 0.42346 | 0.35471 | 0.27666 | 0.23029 | 0.60478 | 0.60252 | 0.59971 | 0.5961 | 0.59183 | 0.58669 | 0.58085 | 0.57408 | 0.56609 | 0.55718 | 0.54739 | 0.4834 | 0.42929 | 0.39881 | 0.53749 | 0.53555 | 0.53307 | 0.52999 | 0.52628 | 0.52188 | 0.51678 | 0.51086 | 0.50395 | 0.49626 | 0.48774 | 0.43266 | 0.38642 | 0.3613
| BOAT OF GARTEN | BOAT OF GARTEN | MINIMUM HEADROOM | NH 95609 19427 | NO | YES | 7.8615 | 7.8431 | 7.8205 | 7.7957 | 7.7433 | 7.6209 | 7.5086 | 7.46 | 7.3894 | 7.2629 | 7.1482 | 6.9386 | 6.7557 | 6.6453 | 8.0394 | 8.0083 | 7.9696 | 7.9308 | 7.8719 | 7.8059 | 7.7531 | 7.7235 | 7.6947 | 7.6655 | 7.593 | 7.375 | 7.2391 | 7.1063 | 6.8966 | 6.8349 | 6.7569 | 6.6788 | 6.5902 | 6.4758 | 6.3741 | 6.3264 | 6.28 | 6.2325 | 6.1797 | 6.0394 | 5.8758 | 5.7712
|  | BOAT OF GARTEN | CT |  |  |  | 7.8623 | 7.8462 | 7.8205 | 7.7957 | 7.7433 | 7.6209 | 7.5086 | 7.46 | 7.4129 | 7.2922 | 7.1843 | 6.955 | 6.7557 | 6.6453 | 8.0641 | 8.0401 | 7.9874 | 7.9353 | 7.8719 | 7.8059 | 7.7531 | 7.7235 | 7.6947 | 7.6655 | 7.593 | 7.375 | 7.2391 | 7.1063 | 6.9513 | 6.9053 | 6.8023 | 6.7008 | 6.5902 | 6.4758 | 6.3741 | 6.3264 | 6.28 | 6.2325 | 6.1797 | 6.0394 | 5.8758 | 5.7781
|  | BOAT OF GARTEN | LW |  |  |  | 7.8615 | 7.8431 | 7.8283 | 7.8111 | 7.7455 | 7.644 | 7.536 | 7.4808 | 7.3894 | 7.2629 | 7.1482 | 6.9386 | 6.7962 | 6.6701 | 8.0394 | 8.0083 | 7.9696 | 7.9308 | 7.8918 | 7.8446 | 7.7939 | 7.7626 | 7.7239 | 7.6792 | 7.5955 | 7.4469 | 7.3453 | 7.2207 | 6.8966 | 6.8349 | 6.7569 | 6.6788 | 6.6003 | 6.5085 | 6.4104 | 6.3573 | 6.2992 | 6.2395 | 6.1841 | 6.0401 | 5.9016 | 5.7712
|  | BOAT OF GARTEN | ST |  |  |  | 7.8702 | 7.8646 | 7.8453 | 7.8275 | 7.8107 | 7.7779 | 7.7563 | 7.7219 | 7.6925 | 7.6603 | 7.6223 | 7.2591 | 7.0675 | 6.9317 | 8.0877 | 8.0777 | 8.0499 | 8.025 | 8.001 | 7.9603 | 7.9342 | 7.8937 | 7.8616 | 7.8223 | 7.7766 | 7.4797 | 7.3128 | 7.1681 | 6.9955 | 6.9749 | 6.9333 | 6.893 | 6.8522 | 6.7949 | 6.7502 | 6.6898 | 6.6359 | 6.5789 | 6.5147 | 6.1823 | 6.0021 | 5.8765
|  | BOAT OF GARTEN | FS |  |  |  | 7.8727 | 7.8677 | 7.859 | 7.849 | 7.8379 | 7.8254 | 7.8116 | 7.7932 | 7.7745 | 7.7541 | 7.7318 | 7.4336 | 7.0695 | 6.9752 | 8.0937 | 8.0867 | 8.0695 | 8.0501 | 8.0304 | 8.0117 | 7.9915 | 7.9653 | 7.9394 | 7.9142 | 7.8878 | 7.7048 | 7.4041 | 7.2566 | 7.0078 | 6.9933 | 6.9602 | 6.923 | 6.886 | 6.8512 | 6.8133 | 6.7673 | 6.7203 | 6.6751 | 6.6277 | 6.3199 | 6.1224 | 6.0061
| PETERHEAD SHELL | BODDAM | MINIMUM HEADROOM | NK 12219 42512 | YES | NO | 1.768 | 1.6992 | 1.5659 | 1.4432 | 1.3317 | 0.7412 | 0.16015 | -0.4198 | -1.1285 | -1.6573 | -2.0414 | -3.2545 | -3.8867 | -4.5267 | 1.757 | 1.7055 | 1.6032 | 1.5107 | 1.4283 | 0.82477 | 0.24344 | -0.33246 | -1.0589 | -1.5754 | -1.9145 | -3.0332 | -3.7006 | -4.4861 | 0.90813 | 0.86448 | 0.77403 | 0.69013 | 0.61505 | 0.052365 | -0.48964 | -1.0287 | -1.7122 | -2.1939 | -2.5127 | -3.5475 | -4.213 | -5.0003
|  | BODDAM | CT |  |  |  | 1.8043 | 1.7042 | 1.5659 | 1.4432 | 1.3317 | 0.7412 | 0.16015 | -0.41806 | -1.1285 | -1.6391 | -2.008 | -3.1239 | -3.4629 | -3.775 | 1.7905 | 1.707 | 1.6032 | 1.5107 | 1.4283 | 0.82477 | 0.24344 | -0.33246 | -1.0589 | -1.5754 | -1.9145 | -2.9489 | -3.2772 | -3.6237 | 0.9389 | 0.86611 | 0.77403 | 0.69013 | 0.61505 | 0.052365 | -0.48964 | -1.0287 | -1.7122 | -2.1939 | -2.5127 | -3.4904 | -3.8164 | -4.159
|  | BODDAM | LW |  |  |  | 1.768 | 1.6992 | 1.6169 | 1.5197 | 1.4383 | 0.83017 | 0.18374 | -0.4198 | -1.1155 | -1.6573 | -2.0414 | -3.2545 | -3.8867 | -4.5267 | 1.757 | 1.7055 | 1.6509 | 1.5742 | 1.5276 | 0.92134 | 0.28222 | -0.31389 | -1.0035 | -1.5309 | -1.8744 | -2.9985 | -3.7006 | -4.4861 | 0.90813 | 0.86448 | 0.81549 | 0.74872 | 0.70805 | 0.14539 | -0.4477 | -1.0034 | -1.6464 | -2.1312 | -2.4521 | -3.5161 | -4.213 | -5.0003
|  | BODDAM | ST |  |  |  | 1.8325 | 1.7958 | 1.7296 | 1.6724 | 1.6187 | 1.0652 | 0.52569 | -0.053094 | -0.75443 | -1.2663 | -1.6413 | -3.0539 | -3.6358 | -4.0642 | 1.8058 | 1.7684 | 1.6995 | 1.6445 | 1.5982 | 1.0097 | 0.44844 | -0.15787 | -0.88218 | -1.4064 | -1.7628 | -3.0332 | -3.603 | -4.0715 | 0.95054 | 0.91817 | 0.85493 | 0.80571 | 0.76482 | 0.21557 | -0.30768 | -0.87793 | -1.5554 | -2.0389 | -2.3723 | -3.5475 | -4.0951 | -4.5615
|  | BODDAM | FS |  |  |  | 1.9072 | 1.8787 | 1.8338 | 1.7966 | 1.7596 | 1.439 | 1.0195 | 0.59796 | 0.14908 | -0.21291 | -0.52048 | -1.8579 | -2.8901 | -3.3379 | 1.9133 | 1.8834 | 1.8375 | 1.802 | 1.7695 | 1.4305 | 0.98657 | 0.54458 | 0.077323 | -0.29851 | -0.60588 | -1.8503 | -2.7571 | -3.102 | 1.0435 | 1.0176 | 0.97652 | 0.94519 | 0.91659 | 0.60151 | 0.18811 | -0.22579 | -0.66254 | -1.0103 | -1.2971 | -2.4457 | -3.2749 | -3.575
| TUMMEL BRIDGE | BONSKEID | MINIMUM HEADROOM | NN 90919 60658 | YES | YES | -2.4256 | -2.514 | -2.6323 | -2.7641 | -2.9451 | -3.136 | -3.3046 | -3.4794 | -3.6614 | -3.8445 | -3.996 | -4.4837 | -5.0023 | -5.2693 | -1.4164 | -1.4653 | -1.5402 | -1.6308 | -1.7555 | -1.889 | -1.9856 | -2.1096 | -2.2488 | -2.3892 | -2.5226 | -3.3247 | -3.7922 | -4.0513 | -2.3709 | -2.4603 | -2.5695 | -2.712 | -2.8901 | -3.0776 | -3.2318 | -3.4051 | -3.5964 | -3.7879 | -3.9487 | -4.4492 | -4.8016 | -5.0964
|  | BONSKEID | CT |  |  |  | -2.3933 | -2.4663 | -2.6067 | -2.7641 | -2.9451 | -3.136 | -3.3046 | -3.4794 | -3.6614 | -3.8445 | -3.996 | -4.4837 | -4.7543 | -4.9322 | -1.4052 | -1.4572 | -1.5402 | -1.6308 | -1.7555 | -1.889 | -1.9856 | -2.1096 | -2.2488 | -2.3892 | -2.5226 | -3.0665 | -3.2432 | -3.3904 | -2.3303 | -2.4092 | -2.554 | -2.712 | -2.8901 | -3.0776 | -3.2318 | -3.4051 | -3.5964 | -3.7879 | -3.9487 | -4.4492 | -4.7147 | -4.9093
|  | BONSKEID | LW |  |  |  | -2.4256 | -2.514 | -2.6323 | -2.7564 | -2.8878 | -3.052 | -3.2335 | -3.3953 | -3.5738 | -3.761 | -3.8998 | -4.2558 | -4.5326 | -4.8326 | -1.4164 | -1.4653 | -1.5223 | -1.5832 | -1.6451 | -1.7336 | -1.8466 | -1.9704 | -2.1057 | -2.2448 | -2.3597 | -2.6262 | -2.8933 | -3.2362 | -2.3709 | -2.4603 | -2.5695 | -2.687 | -2.8034 | -2.9595 | -3.1346 | -3.3038 | -3.4895 | -3.6823 | -3.8346 | -4.195 | -4.5006 | -4.8597
|  | BONSKEID | ST |  |  |  | -2.3528 | -2.38 | -2.4579 | -2.5375 | -2.6186 | -2.7452 | -2.8428 | -2.9853 | -3.1173 | -3.2567 | -3.4027 | -4.4739 | -5.0023 | -5.2693 | -1.3778 | -1.3978 | -1.4736 | -1.5381 | -1.5975 | -1.7125 | -1.7844 | -1.9002 | -1.9961 | -2.1316 | -2.3243 | -3.3247 | -3.7922 | -4.0513 | -2.2903 | -2.3233 | -2.4194 | -2.5066 | -2.59 | -2.7307 | -2.8327 | -2.9842 | -3.1184 | -3.2611 | -3.4103 | -4.2482 | -4.8016 | -5.0964
|  | BONSKEID | FS |  |  |  | -2.3457 | -2.365 | -2.4043 | -2.4484 | -2.5079 | -2.5748 | -2.6441 | -2.7318 | -2.8263 | -2.9251 | -3.0155 | -3.5779 | -4.2374 | -4.7571 | -1.3697 | -1.3859 | -1.4192 | -1.454 | -1.4941 | -1.5387 | -1.5851 | -1.647 | -1.7089 | -1.7814 | -1.8556 | -2.4137 | -3.0156 | -3.4138 | -2.2767 | -2.3045 | -2.3555 | -2.4086 | -2.4686 | -2.5357 | -2.6061 | -2.696 | -2.7896 | -2.8885 | -2.9835 | -3.5523 | -4.0447 | -4.4578
| PORT ANN | BOWMORE | MINIMUM HEADROOM | NR 32021 60211 | YES | YES | 1.7946 | 1.6863 | 0.89184 | 0.17394 | -0.57936 | -0.76487 | -0.96481 | -1.0639 | -1.1653 | -1.2751 | -1.3738 | -1.6868 | -2.1592 | -2.7188 | 2.3143 | 2.2582 | 1.4763 | 0.72193 | -0.076369 | -0.16912 | -0.27934 | -0.35026 | -0.4241 | -0.49909 | -0.57091 | -0.83103 | -1.3287 | -1.9883 | 1.0096 | 0.91134 | 0.10679 | -0.65712 | -1.4598 | -1.6253 | -1.8057 | -1.9019 | -2.0209 | -2.1457 | -2.2605 | -2.6038 | -3.1547 | -3.8392
|  | BOWMORE | CT |  |  |  | 1.8399 | 1.7947 | 1.0315 | 0.26087 | -0.49125 | -0.71809 | -0.9483 | -1.0563 | -1.1431 | -1.2244 | -1.3037 | -1.5162 | -1.8886 | -2.1668 | 2.3467 | 2.3014 | 1.5802 | 0.80238 | 0.033718 | -0.088456 | -0.22366 | -0.32275 | -0.38346 | -0.44001 | -0.49787 | -0.7146 | -1.0399 | -1.3617 | 1.085 | 1.0114 | 0.23926 | -0.57054 | -1.3642 | -1.5695 | -1.7806 | -1.8886 | -1.9742 | -2.0709 | -2.1641 | -2.424 | -2.8187 | -3.141
|  | BOWMORE | LW |  |  |  | 1.7946 | 1.6863 | 0.89184 | 0.17394 | -0.57936 | -0.76487 | -0.96481 | -1.0639 | -1.1653 | -1.2751 | -1.3738 | -1.6868 | -2.1592 | -2.7188 | 2.3143 | 2.2582 | 1.4763 | 0.72193 | -0.076369 | -0.16912 | -0.27934 | -0.35026 | -0.4241 | -0.49909 | -0.57091 | -0.83103 | -1.3287 | -1.9883 | 1.0096 | 0.91134 | 0.10679 | -0.65712 | -1.4598 | -1.6253 | -1.8057 | -1.9019 | -2.0209 | -2.1457 | -2.2605 | -2.6038 | -3.1547 | -3.8392
|  | BOWMORE | ST |  |  |  | 1.8984 | 1.8827 | 1.2734 | 0.64022 | 0.0043265 | -0.055064 | -0.12658 | -0.27771 | -0.36882 | -0.46522 | -0.57558 | -1.1253 | -1.5692 | -1.9645 | 2.3846 | 2.3644 | 1.7012 | 0.9684 | 0.2336 | 0.16933 | 0.089492 | -0.037671 | -0.084952 | -0.14301 | -0.21596 | -0.57919 | -1.0202 | -1.4663 | 1.1576 | 1.125 | 0.48929 | -0.18624 | -0.86451 | -0.95534 | -1.0545 | -1.2126 | -1.2985 | -1.3899 | -1.507 | -2.0733 | -2.5684 | -3.0295
|  | BOWMORE | FS |  |  |  | 1.912 | 1.8986 | 1.4314 | 0.91722 | 0.43716 | 0.28323 | 0.17429 | 0.03422 | -0.18542 | -0.35223 | -0.42998 | -0.93974 | -1.3324 | -1.4999 | 2.3956 | 2.3777 | 1.8738 | 1.2818 | 0.72504 | 0.54934 | 0.44351 | 0.32833 | 0.11686 | -0.03193 | -0.078862 | -0.34678 | -0.61925 | -0.80873 | 1.179 | 1.1512 | 0.65904 | 0.10143 | -0.42071 | -0.60908 | -0.73202 | -0.87381 | -1.0983 | -1.2654 | -1.3367 | -1.8333 | -2.2267 | -2.3907
| SHETLAND | BRAE | MINIMUM HEADROOM | HU3604068816 | YES | YES | -2.8475 | -3.2224 | -3.6564 | -4.2154 | -4.7354 | -5.5334 | -6.1762 | -6.8587 | -7.6841 | -8.5487 | -8.7253 | -9.337 | -9.8941 | -10.5886 | -1.4769 | -1.9024 | -2.3589 | -2.967 | -3.5331 | -4.4208 | -5.1197 | -5.8541 | -6.7736 | -7.7628 | -7.9323 | -8.5456 | -9.1575 | -10.0311 | -2.7621 | -3.176 | -3.6152 | -4.1845 | -4.7142 | -5.5328 | -6.1854 | -6.847 | -7.6699 | -8.4966 | -8.6643 | -9.2851 | -9.9411 | -10.8474
|  | BRAE | CT |  |  |  | -2.7532 | -3.0904 | -3.521 | -4.0818 | -4.6539 | -5.4892 | -6.1137 | -6.7701 | -7.6712 | -8.5487 | -8.7253 | -9.2782 | -9.6304 | -9.9772 | -1.3833 | -1.7774 | -2.2259 | -2.8233 | -3.4382 | -4.3578 | -5.0324 | -5.7866 | -6.7736 | -7.7628 | -7.9323 | -8.4995 | -8.9214 | -9.3571 | -2.6626 | -3.0428 | -3.4833 | -4.0526 | -4.6413 | -5.5019 | -6.1387 | -6.8193 | -7.6699 | -8.4966 | -8.6643 | -9.2465 | -9.6692 | -10.0942
|  | BRAE | LW |  |  |  | -2.8475 | -3.2224 | -3.6564 | -4.2154 | -4.7354 | -5.5334 | -6.1762 | -6.8587 | -7.6841 | -8.5361 | -8.6731 | -9.1851 | -9.8146 | -10.5886 | -1.4769 | -1.9024 | -2.3589 | -2.967 | -3.5331 | -4.4208 | -5.1197 | -5.8541 | -6.739 | -7.6757 | -7.7931 | -8.3063 | -9.0674 | -10.0311 | -2.7621 | -3.176 | -3.6152 | -4.1845 | -4.7142 | -5.5328 | -6.1854 | -6.847 | -7.624 | -8.4328 | -8.5731 | -9.1158 | -9.8796 | -10.8474
|  | BRAE | ST |  |  |  | -2.7142 | -3.0251 | -3.4194 | -3.9321 | -4.4216 | -5.2605 | -5.8966 | -6.6531 | -7.552 | -8.4333 | -8.6166 | -9.337 | -9.8941 | -10.3828 | -1.3632 | -1.7437 | -2.1992 | -2.795 | -3.3601 | -4.279 | -4.9455 | -5.757 | -6.7626 | -7.743 | -7.9174 | -8.5456 | -9.1575 | -9.7562 | -2.6259 | -2.9819 | -3.4052 | -3.9424 | -4.4528 | -5.2835 | -5.8848 | -6.6193 | -7.4875 | -8.3413 | -8.5304 | -9.2851 | -9.9411 | -10.5431
|  | BRAE | FS |  |  |  | -2.5467 | -2.7496 | -3.0265 | -3.4197 | -3.8002 | -4.334 | -4.8472 | -5.4594 | -6.1557 | -6.8397 | -7.1402 | -8.2214 | -8.99 | -9.2524 | -1.1156 | -1.4092 | -1.7304 | -2.1784 | -2.6159 | -3.2229 | -3.805 | -4.4611 | -5.1922 | -5.937 | -6.2601 | -7.3516 | -8.1244 | -8.3901 | -2.3965 | -2.6712 | -2.981 | -3.3969 | -3.7932 | -4.3451 | -4.8723 | -5.468 | -6.1291 | -6.7781 | -7.0658 | -8.12 | -8.8712 | -9.1466
| BRIDGE OF DUN | BRECHIN | MINIMUM HEADROOM | NO 60998 59682 | NO | YES | 4.6729 | 4.3098 | 3.6862 | 3.0192 | 2.3194 | 1.4588 | 0.20089 | -0.58903 | -1.421 | -2.2842 | -3.0924 | -5.2823 | -6.3708 | -7.4654 | 6.371 | 6.161 | 5.8041 | 5.4154 | 4.9542 | 4.3474 | 3.4159 | 2.8502 | 2.2508 | 1.6072 | 0.98983 | -0.65774 | -1.6238 | -2.8511 | 5.7779 | 5.4596 | 4.8897 | 4.2761 | 3.5996 | 2.7598 | 1.5692 | 0.82169 | 0.032963 | -0.80763 | -1.6096 | -3.7572 | -4.9245 | -6.2322
|  | BRECHIN | CT |  |  |  | 4.8754 | 4.6948 | 4.1119 | 3.4931 | 2.8442 | 2.1195 | 1.1171 | 0.33039 | -0.52266 | -1.3681 | -2.1858 | -4.8107 | -6.0432 | -6.8263 | 6.46 | 6.303 | 5.9784 | 5.6244 | 5.1924 | 4.6862 | 3.9703 | 3.4251 | 2.8217 | 2.225 | 1.635 | -0.37082 | -1.4019 | -2.5 | 6.0045 | 5.7953 | 5.2722 | 4.7112 | 4.0865 | 3.3854 | 2.4595 | 1.727 | 0.93028 | 0.14184 | -0.62687 | -3.153 | -4.3248 | -5.124
|  | BRECHIN | LW |  |  |  | 4.6729 | 4.3098 | 3.6862 | 3.0192 | 2.3194 | 1.4588 | 0.20089 | -0.58903 | -1.421 | -2.2842 | -3.0924 | -5.2823 | -6.3708 | -7.4654 | 6.371 | 6.161 | 5.8041 | 5.4154 | 4.9542 | 4.3474 | 3.4159 | 2.8502 | 2.2508 | 1.6072 | 0.98983 | -0.65774 | -1.6238 | -2.8511 | 5.7779 | 5.4596 | 4.8897 | 4.2761 | 3.5996 | 2.7598 | 1.5692 | 0.82169 | 0.032963 | -0.80763 | -1.6096 | -3.7572 | -4.9245 | -6.2322
|  | BRECHIN | ST |  |  |  | 4.934 | 4.85 | 4.6371 | 4.449 | 4.2886 | 3.9258 | 3.293 | 2.7815 | 2.2564 | 1.7131 | 1.1376 | -1.5252 | -2.9327 | -4.365 | 6.559 | 6.4796 | 6.2389 | 6.0298 | 5.8577 | 5.4558 | 4.86 | 4.3963 | 3.9449 | 3.4769 | 2.9737 | 0.63821 | -0.7228 | -2.1831 | 6.1903 | 6.0974 | 5.8399 | 5.6098 | 5.4224 | 4.9994 | 4.3695 | 3.8659 | 3.3668 | 2.8481 | 2.265 | -0.44966 | -1.8865 | -3.2867
|  | BRECHIN | FS |  |  |  | 4.9482 | 4.8764 | 4.7721 | 4.6574 | 4.5195 | 4.3116 | 3.7975 | 3.4252 | 3.0385 | 2.6248 | 2.1986 | -0.10242 | -2.0838 | -3.3367 | 6.5631 | 6.4936 | 6.3714 | 6.2368 | 6.0999 | 5.9271 | 5.4796 | 5.1654 | 4.8417 | 4.4928 | 4.1252 | 2.1738 | 0.19811 | -1.6385 | 6.1903 | 6.1119 | 5.9655 | 5.8058 | 5.6451 | 5.4495 | 4.9687 | 4.6182 | 4.2567 | 3.8693 | 3.4664 | 1.238 | -0.68964 | -1.828
| PERSLEY | BRIDGE OF DON | MINIMUM HEADROOM | NJ 94130 10184 | NO | YES | 7.6282 | 6.3142 | 4.0657 | 1.7339 | -0.45862 | -2.0566 | -3.688 | -4.6769 | -5.7742 | -6.937 | -8.0658 | -11.2341 | -13.8441 | -14.7546 | 11.7021 | 10.3615 | 8.1893 | 5.9842 | 3.858 | 2.5027 | 1.0662 | 0.19385 | -0.75928 | -1.7602 | -2.7099 | -5.1881 | -7.4062 | -8.3234 | 10.3936 | 9.1 | 6.6408 | 4.2586 | 1.9613 | 0.35745 | -1.1947 | -2.0577 | -2.9802 | -3.9282 | -4.8531 | -7.9264 | -10.5366 | -11.5138
|  | BRIDGE OF DON | CT |  |  |  | 7.7219 | 6.5217 | 4.638 | 2.5978 | 0.65408 | -0.73704 | -2.0418 | -3.1037 | -4.001 | -4.8638 | -5.8331 | -9.4207 | -10.5752 | -11.404 | 11.8072 | 10.591 | 8.6238 | 6.4354 | 4.4992 | 3.3007 | 2.2132 | 1.3905 | 0.71861 | 0.076393 | -0.6508 | -3.3941 | -4.0588 | -4.5487 | 10.4899 | 9.3134 | 7.4335 | 5.285 | 3.2441 | 1.8574 | 0.61912 | -0.28065 | -1.0773 | -1.8492 | -2.6441 | -5.6985 | -6.9465 | -7.7603
|  | BRIDGE OF DON | LW |  |  |  | 7.6282 | 6.3142 | 4.0657 | 1.7339 | -0.45862 | -2.0566 | -3.688 | -4.6769 | -5.7742 | -6.937 | -8.0658 | -11.1039 | -11.9907 | -13.2493 | 11.7021 | 10.3615 | 8.1893 | 5.9842 | 3.858 | 2.5027 | 1.0662 | 0.19385 | -0.75928 | -1.7602 | -2.7099 | -5.1565 | -6.0111 | -7.0913 | 10.3936 | 9.1 | 6.6408 | 4.2586 | 1.9613 | 0.35745 | -1.1947 | -2.0577 | -2.9802 | -3.9282 | -4.8531 | -7.6136 | -8.5279 | -9.7041
|  | BRIDGE OF DON | ST |  |  |  | 7.882 | 6.8896 | 5.0903 | 3.2314 | 1.7854 | 0.78246 | -0.22354 | -1.137 | -2.1021 | -3.2025 | -4.4558 | -11.2341 | -13.8441 | -14.7546 | 11.9357 | 10.886 | 8.9096 | 6.7986 | 5.1291 | 4.077 | 3.1567 | 2.4728 | 1.777 | 0.99121 | 0.093937 | -5.1881 | -7.4062 | -8.3234 | 10.6387 | 9.6553 | 7.8241 | 5.9015 | 4.4048 | 3.3382 | 2.386 | 1.726 | 0.94483 | -0.12342 | -1.3433 | -7.9264 | -10.5366 | -11.5138
|  | BRIDGE OF DON | FS |  |  |  | 8.1963 | 7.4254 | 6.1412 | 4.7093 | 3.6187 | 2.8965 | 2.1629 | 1.6585 | 0.86491 | 0.03829 | -0.69608 | -5.4431 | -9.8784 | -12.6178 | 12.2693 | 11.4688 | 10.0931 | 8.4726 | 7.2253 | 6.4544 | 5.6996 | 5.1969 | 4.4473 | 3.8031 | 3.2517 | -0.29665 | -3.808 | -6.0324 | 10.9488 | 10.1882 | 8.9118 | 7.4617 | 6.3386 | 5.6065 | 4.8696 | 4.3646 | 3.6362 | 3.0103 | 2.4671 | -2.1081 | -6.384 | -9.0259
| BRIDGE OF DUN | BRIDGE OF DUN | MINIMUM HEADROOM | NO 66018 58883 | YES | YES | -0.22991 | -0.25409 | -0.28199 | -0.30945 | -0.34733 | -0.39484 | -0.43439 | -0.47754 | -0.52836 | -0.57242 | -0.61672 | -0.80772 | -1.2548 | -1.8728 | -0.015078 | -0.02727 | -0.039776 | -0.058641 | -0.091636 | -0.12622 | -0.14725 | -0.20242 | -0.2449 | -0.29117 | -0.3384 | -0.57654 | -1.0593 | -1.8209 | -0.35059 | -0.37072 | -0.39272 | -0.41514 | -0.45733 | -0.50207 | -0.53469 | -0.58523 | -0.64425 | -0.69726 | -0.7498 | -0.98421 | -1.51 | -2.2769
|  | BRIDGE OF DUN | CT |  |  |  | -0.20869 | -0.22589 | -0.26142 | -0.30128 | -0.34733 | -0.39484 | -0.43439 | -0.47754 | -0.52836 | -0.57242 | -0.61672 | -0.80059 | -1.0623 | -1.3261 | -0.0081829 | -0.017426 | -0.036568 | -0.058641 | -0.091636 | -0.12622 | -0.14725 | -0.19344 | -0.2449 | -0.29117 | -0.3384 | -0.54487 | -0.82759 | -1.1491 | -0.33532 | -0.34967 | -0.37975 | -0.41414 | -0.45733 | -0.50207 | -0.53469 | -0.58523 | -0.64425 | -0.69726 | -0.7498 | -0.96788 | -1.2696 | -1.5899
|  | BRIDGE OF DUN | LW |  |  |  | -0.22991 | -0.25409 | -0.28199 | -0.30945 | -0.33951 | -0.37313 | -0.40848 | -0.4553 | -0.50811 | -0.56025 | -0.60631 | -0.80242 | -1.2548 | -1.8728 | -0.015078 | -0.02727 | -0.039776 | -0.052949 | -0.066029 | -0.08385 | -0.10342 | -0.15455 | -0.20931 | -0.25927 | -0.30911 | -0.51889 | -1.0593 | -1.8209 | -0.35059 | -0.37072 | -0.39272 | -0.41514 | -0.43835 | -0.46705 | -0.4978 | -0.55379 | -0.61526 | -0.67427 | -0.72933 | -0.9571 | -1.51 | -2.2769
|  | BRIDGE OF DUN | ST |  |  |  | -0.19284 | -0.20605 | -0.23559 | -0.25943 | -0.28094 | -0.31813 | -0.3412 | -0.41894 | -0.46163 | -0.50108 | -0.55579 | -0.80772 | -1.1879 | -1.5768 | -0.0020124 | -0.0077279 | -0.031726 | -0.05039 | -0.065777 | -0.10053 | -0.11746 | -0.20242 | -0.2417 | -0.27796 | -0.32973 | -0.57654 | -1.0042 | -1.464 | -0.32402 | -0.33402 | -0.3633 | -0.38661 | -0.40682 | -0.44657 | -0.46857 | -0.55903 | -0.60465 | -0.647 | -0.70628 | -0.98421 | -1.4316 | -1.8984
|  | BRIDGE OF DUN | FS |  |  |  | -0.185 | -0.1943 | -0.20668 | -0.22363 | -0.23925 | -0.25381 | -0.27189 | -0.31154 | -0.34119 | -0.38108 | -0.41611 | -0.57129 | -0.67948 | -0.76315 | 0.00062728 | -0.0037147 | -0.011838 | -0.021872 | -0.032065 | -0.042379 | -0.053764 | -0.089961 | -0.11711 | -0.14806 | -0.17807 | -0.27847 | -0.36352 | -0.44521 | -0.31849 | -0.32565 | -0.33685 | -0.35143 | -0.36552 | -0.37919 | -0.39522 | -0.43715 | -0.46876 | -0.50766 | -0.54375 | -0.68596 | -0.79449 | -0.87635
| ABERNETHY | BRIDGE OF EARN | MINIMUM HEADROOM | NO 13343 17764 | NO | YES | 9.5707 | 8.9588 | 8.1956 | 7.3025 | 6.3608 | 5.3664 | 4.4852 | 3.7639 | 2.9787 | 2.1729 | 1.465 | -0.40442 | -1.0919 | -1.5526 | 10.6476 | 10.1959 | 9.6484 | 8.9818 | 8.2597 | 7.5064 | 6.8929 | 6.388 | 5.8222 | 5.2426 | 4.7097 | 3.432 | 2.9058 | 2.4149 | 9.3903 | 8.833 | 8.1328 | 7.3034 | 6.4133 | 5.4632 | 4.6379 | 3.9699 | 3.2402 | 2.493 | 1.8257 | 0.12952 | -0.54829 | -1.0806
|  | BRIDGE OF EARN | CT |  |  |  | 9.8163 | 9.3136 | 8.609 | 7.7802 | 6.872 | 5.9554 | 5.1974 | 4.4676 | 3.6171 | 2.7667 | 2.0081 | 0.11121 | -0.56784 | -0.96077 | 10.7711 | 10.3781 | 9.8949 | 9.2975 | 8.6034 | 7.912 | 7.4158 | 6.9143 | 6.3046 | 5.6966 | 5.1323 | 3.7001 | 3.2052 | 2.7401 | 9.6019 | 9.142 | 8.5024 | 7.7399 | 6.8829 | 6.0183 | 5.3382 | 4.6722 | 3.8857 | 3.1011 | 2.3928 | 0.61668 | -0.013441 | -0.40493
|  | BRIDGE OF EARN | LW |  |  |  | 9.5707 | 8.9588 | 8.1956 | 7.3025 | 6.3608 | 5.3664 | 4.4852 | 3.7639 | 2.9787 | 2.1729 | 1.465 | -0.40442 | -1.0919 | -1.5526 | 10.6476 | 10.1959 | 9.6484 | 8.9818 | 8.2597 | 7.5064 | 6.8929 | 6.388 | 5.8222 | 5.2426 | 4.7097 | 3.432 | 2.9058 | 2.4149 | 9.3903 | 8.833 | 8.1328 | 7.3034 | 6.4133 | 5.4632 | 4.6379 | 3.9699 | 3.2402 | 2.493 | 1.8257 | 0.12952 | -0.54829 | -1.0806
|  | BRIDGE OF EARN | ST |  |  |  | 9.9253 | 9.4851 | 8.9263 | 8.2951 | 7.7048 | 6.9937 | 6.4865 | 5.9368 | 5.3321 | 4.7166 | 4.1246 | 2.1677 | 1.4907 | 0.8531 | 10.8181 | 10.4621 | 9.9669 | 9.421 | 8.9236 | 8.2774 | 7.8629 | 7.4153 | 6.934 | 6.4446 | 5.9483 | 4.3431 | 3.7588 | 3.162 | 9.6965 | 9.2982 | 8.7559 | 8.1556 | 7.6038 | 6.898 | 6.4227 | 5.9054 | 5.3464 | 4.7772 | 4.2141 | 2.3304 | 1.6588 | 1.0308
|  | BRIDGE OF EARN | FS |  |  |  | 10.1647 | 9.8181 | 9.4262 | 8.9441 | 8.4688 | 8.0027 | 7.551 | 7.068 | 6.5284 | 5.9972 | 5.4944 | 3.3164 | 1.9423 | 1.4197 | 11.0178 | 10.7384 | 10.4261 | 10.0322 | 9.643 | 9.2654 | 8.9054 | 8.5227 | 8.0953 | 7.6754 | 7.2662 | 5.5605 | 4.4097 | 3.7744 | 9.9206 | 9.6086 | 9.253 | 8.8116 | 8.3758 | 7.9493 | 7.5369 | 7.0962 | 6.6045 | 6.1194 | 5.6507 | 3.6264 | 2.3555 | 1.8859
| RANNOCH | BRIDGE OF GAUR | MINIMUM HEADROOM | NN 50676 57767 | YES | YES | 0.77227 | 0.75883 | 0.75335 | 0.73745 | 0.71961 | 0.69522 | 0.67862 | 0.66476 | 0.64878 | 0.63763 | 0.62218 | 0.57959 | 0.53788 | 0.50015 | 0.60271 | 0.596 | 0.58992 | 0.57874 | 0.56344 | 0.54526 | 0.53491 | 0.5234 | 0.50994 | 0.4988 | 0.48644 | 0.44189 | 0.39553 | 0.35559 | 0.54217 | 0.52998 | 0.52451 | 0.50793 | 0.48893 | 0.4642 | 0.44837 | 0.43369 | 0.41649 | 0.40419 | 0.38847 | 0.34266 | 0.29224 | 0.24942
|  | BRIDGE OF GAUR | CT |  |  |  | 0.78032 | 0.77313 | 0.7544 | 0.73745 | 0.71961 | 0.69522 | 0.67862 | 0.66476 | 0.64878 | 0.63763 | 0.62218 | 0.57959 | 0.5481 | 0.52017 | 0.60571 | 0.6007 | 0.58992 | 0.57874 | 0.56344 | 0.54526 | 0.53491 | 0.5234 | 0.50994 | 0.4988 | 0.48644 | 0.44676 | 0.4175 | 0.38729 | 0.5491 | 0.54205 | 0.52451 | 0.50793 | 0.48893 | 0.4642 | 0.44837 | 0.43369 | 0.41649 | 0.40419 | 0.38847 | 0.34266 | 0.30852 | 0.27706
|  | BRIDGE OF GAUR | LW |  |  |  | 0.77227 | 0.75883 | 0.75335 | 0.74013 | 0.72685 | 0.71663 | 0.69918 | 0.68876 | 0.67329 | 0.66026 | 0.64256 | 0.60589 | 0.56255 | 0.51329 | 0.60271 | 0.596 | 0.59234 | 0.58561 | 0.57913 | 0.57212 | 0.56193 | 0.55229 | 0.54042 | 0.52967 | 0.5174 | 0.48868 | 0.44353 | 0.38528 | 0.54217 | 0.52998 | 0.52454 | 0.51249 | 0.50057 | 0.49037 | 0.47386 | 0.46232 | 0.44647 | 0.43336 | 0.4162 | 0.37931 | 0.32935 | 0.26921
|  | BRIDGE OF GAUR | ST |  |  |  | 0.78486 | 0.77999 | 0.76982 | 0.75739 | 0.74854 | 0.73303 | 0.7187 | 0.70484 | 0.69292 | 0.67823 | 0.66341 | 0.58715 | 0.53788 | 0.50015 | 0.60775 | 0.60535 | 0.59492 | 0.58533 | 0.57821 | 0.5619 | 0.55229 | 0.53801 | 0.52831 | 0.5175 | 0.50492 | 0.44189 | 0.39553 | 0.35559 | 0.55304 | 0.54865 | 0.53702 | 0.52424 | 0.51502 | 0.49706 | 0.48302 | 0.46712 | 0.45464 | 0.43977 | 0.42404 | 0.34589 | 0.29224 | 0.24942
|  | BRIDGE OF GAUR | FS |  |  |  | 0.78716 | 0.78435 | 0.78156 | 0.77482 | 0.76428 | 0.75849 | 0.75478 | 0.74527 | 0.73078 | 0.72312 | 0.71268 | 0.65136 | 0.60137 | 0.58282 | 0.6087 | 0.60717 | 0.60428 | 0.59983 | 0.59376 | 0.58916 | 0.58529 | 0.57785 | 0.5692 | 0.56267 | 0.55486 | 0.51504 | 0.47937 | 0.46165 | 0.55503 | 0.55247 | 0.54924 | 0.54266 | 0.53278 | 0.52675 | 0.5225 | 0.51267 | 0.49892 | 0.49077 | 0.48013 | 0.42113 | 0.37328 | 0.35504
| BROADFORD | BROADFORD | MINIMUM HEADROOM | NG 62656 24360 | YES | YES | 4.2089 | 4.1706 | 4.1184 | 4.0496 | 3.8793 | 3.7843 | 3.7081 | 3.6772 | 3.6352 | 3.5847 | 3.5469 | 3.4668 | 3.3567 | 3.2696 | 4.2289 | 4.2067 | 4.1796 | 4.1313 | 4.0225 | 3.9515 | 3.905 | 3.8717 | 3.8303 | 3.7855 | 3.7471 | 3.6319 | 3.5159 | 3.3933 | 3.7572 | 3.7189 | 3.6673 | 3.5992 | 3.435 | 3.3341 | 3.2572 | 3.2224 | 3.1775 | 3.1253 | 3.0843 | 2.9865 | 2.8622 | 2.7581
|  | BROADFORD | CT |  |  |  | 4.2326 | 4.208 | 4.1293 | 4.0496 | 3.8793 | 3.7843 | 3.7081 | 3.6772 | 3.6352 | 3.5847 | 3.5469 | 3.4668 | 3.3567 | 3.2696 | 4.239 | 4.2232 | 4.1796 | 4.1313 | 4.0225 | 3.9515 | 3.905 | 3.8717 | 3.8303 | 3.7855 | 3.7471 | 3.6319 | 3.5159 | 3.3942 | 3.7818 | 3.7576 | 3.6792 | 3.5992 | 3.435 | 3.3341 | 3.2572 | 3.2224 | 3.1775 | 3.1253 | 3.0843 | 2.9865 | 2.8622 | 2.7581
|  | BROADFORD | LW |  |  |  | 4.2089 | 4.1706 | 4.1184 | 4.0633 | 3.9267 | 3.8607 | 3.7892 | 3.7524 | 3.7141 | 3.6773 | 3.6437 | 3.5802 | 3.4463 | 3.278 | 4.2289 | 4.2067 | 4.1798 | 4.1491 | 4.0767 | 4.0375 | 3.9946 | 3.9624 | 3.9284 | 3.8956 | 3.8649 | 3.8002 | 3.6526 | 3.4525 | 3.7572 | 3.7189 | 3.6673 | 3.6127 | 3.4898 | 3.4247 | 3.3546 | 3.3163 | 3.2765 | 3.2384 | 3.2031 | 3.1311 | 2.9699 | 2.7637
|  | BROADFORD | ST |  |  |  | 4.2708 | 4.266 | 4.2358 | 4.2089 | 4.1324 | 4.0848 | 4.0585 | 4.0101 | 3.9711 | 3.9279 | 3.8811 | 3.6746 | 3.5555 | 3.4359 | 4.2558 | 4.2511 | 4.2164 | 4.1882 | 4.1373 | 4.083 | 4.0576 | 4.0081 | 3.9747 | 3.9391 | 3.8976 | 3.6991 | 3.5496 | 3.3933 | 3.8178 | 3.8124 | 3.7756 | 3.7441 | 3.6751 | 3.618 | 3.5887 | 3.5334 | 3.4925 | 3.4485 | 3.3988 | 3.1735 | 3.0274 | 2.8835
|  | BROADFORD | FS |  |  |  | 4.2719 | 4.2661 | 4.2473 | 4.2276 | 4.1631 | 4.1396 | 4.1155 | 4.086 | 4.0555 | 4.0245 | 3.9955 | 3.8243 | 3.7003 | 3.6569 | 4.2567 | 4.2517 | 4.2371 | 4.2216 | 4.1812 | 4.1624 | 4.1434 | 4.1171 | 4.0923 | 4.0665 | 4.0408 | 3.9082 | 3.7922 | 3.7122 | 3.8191 | 3.8127 | 3.7921 | 3.7704 | 3.7136 | 3.6883 | 3.6627 | 3.6308 | 3.5989 | 3.5662 | 3.5353 | 3.3624 | 3.2376 | 3.1915
| CARRADALE | BRODICK | MINIMUM HEADROOM | NS 01976 35459 | NO | YES | 6.0236 | 5.8935 | 5.7347 | 5.511 | 5.3163 | 5.1119 | 4.9094 | 4.7455 | 4.5428 | 4.3325 | 4.1416 | 3.8178 | 3.7138 | 3.6754 | 7.2876 | 7.2062 | 7.1113 | 6.9578 | 6.8408 | 6.7176 | 6.594 | 6.494 | 6.3535 | 6.2067 | 6.0723 | 5.8335 | 5.7561 | 5.6418 | 5.6585 | 5.5771 | 5.4412 | 5.2873 | 5.1563 | 5.017 | 4.8708 | 4.758 | 4.6574 | 4.553 | 4.4346 | 4.1214 | 4.009 | 3.8584
|  | BRODICK | CT |  |  |  | 6.0972 | 5.9922 | 5.7597 | 5.511 | 5.3163 | 5.1119 | 4.9094 | 4.7691 | 4.5819 | 4.384 | 4.2184 | 3.9458 | 3.7794 | 3.6929 | 7.3259 | 7.2538 | 7.1113 | 6.9578 | 6.8408 | 6.7176 | 6.594 | 6.494 | 6.3638 | 6.2274 | 6.1094 | 5.8852 | 5.7561 | 5.6418 | 5.6927 | 5.5913 | 5.4412 | 5.2873 | 5.1563 | 5.017 | 4.8708 | 4.758 | 4.6574 | 4.553 | 4.4346 | 4.1646 | 4.0597 | 3.9885
|  | BRODICK | LW |  |  |  | 6.0236 | 5.8935 | 5.7347 | 5.5634 | 5.4024 | 5.1803 | 4.9301 | 4.7455 | 4.5428 | 4.3325 | 4.1416 | 3.8178 | 3.7138 | 3.6754 | 7.2876 | 7.2062 | 7.1133 | 7.0117 | 6.917 | 6.7797 | 6.6237 | 6.4948 | 6.3535 | 6.2067 | 6.0723 | 5.8335 | 5.7658 | 5.7433 | 5.6585 | 5.5771 | 5.4891 | 5.3948 | 5.2984 | 5.1696 | 5.0237 | 4.9003 | 4.7637 | 4.6187 | 4.4804 | 4.1214 | 4.009 | 3.9948
|  | BRODICK | ST |  |  |  | 6.2306 | 6.2125 | 6.1867 | 6.1493 | 6.1012 | 6.0425 | 5.9724 | 5.872 | 5.7508 | 5.6109 | 5.4568 | 4.7146 | 4.5926 | 4.5226 | 7.373 | 7.3575 | 7.3361 | 7.3087 | 7.2746 | 7.232 | 7.1808 | 7.1182 | 7.0384 | 6.9394 | 6.8292 | 6.2741 | 6.1341 | 6.0346 | 5.7582 | 5.7329 | 5.7 | 5.6601 | 5.6104 | 5.5512 | 5.4818 | 5.397 | 5.295 | 5.1776 | 5.0444 | 4.3326 | 4.0837 | 3.9993
|  | BRODICK | FS |  |  |  | 6.2226 | 6.2038 | 6.162 | 6.1074 | 6.0546 | 5.995 | 5.9247 | 5.8542 | 5.7723 | 5.6819 | 5.5842 | 4.8869 | 4.3037 | 4.1514 | 7.3788 | 7.3684 | 7.3497 | 7.3136 | 7.2776 | 7.2366 | 7.1886 | 7.138 | 7.0796 | 7.0145 | 6.9432 | 6.4463 | 5.98 | 5.7503 | 5.7633 | 5.7429 | 5.7054 | 5.6617 | 5.6156 | 5.5646 | 5.5069 | 5.4488 | 5.383 | 5.3103 | 5.2297 | 4.6872 | 4.1701 | 3.8584
| BRORA | BRORA | MINIMUM HEADROOM | NC 90482 04236 | NO | YES | 4.7664 | 4.7623 | 4.7582 | 4.7082 | 4.6221 | 4.5311 | 4.4213 | 4.3852 | 4.3031 | 4.2251 | 4.1532 | 4.014 | 3.9211 | 3.862 | 5.1158 | 5.0708 | 5.0214 | 4.9682 | 4.9086 | 4.8492 | 4.7754 | 4.7205 | 4.6598 | 4.6004 | 4.5461 | 4.4524 | 4.3547 | 4.2367 | 4.8816 | 4.8057 | 4.7189 | 4.6267 | 4.5365 | 4.4257 | 4.3012 | 4.2207 | 4.131 | 4.0446 | 3.9649 | 3.8191 | 3.7399 | 3.6824
|  | BRORA | CT |  |  |  | 4.7673 | 4.7642 | 4.7583 | 4.7455 | 4.6353 | 4.5311 | 4.4213 | 4.3926 | 4.3412 | 4.258 | 4.192 | 4.0663 | 3.9211 | 3.862 | 5.1418 | 5.1101 | 5.0417 | 4.9694 | 4.9086 | 4.8492 | 4.7877 | 4.7442 | 4.6851 | 4.623 | 4.5711 | 4.4578 | 4.3547 | 4.2683 | 4.9336 | 4.8824 | 4.7661 | 4.643 | 4.5365 | 4.4337 | 4.3272 | 4.2646 | 4.179 | 4.0886 | 4.0153 | 3.8745 | 3.7399 | 3.6824
|  | BRORA | LW |  |  |  | 4.7664 | 4.7623 | 4.7582 | 4.7082 | 4.6221 | 4.5315 | 4.423 | 4.3852 | 4.3031 | 4.2251 | 4.1532 | 4.014 | 3.9336 | 3.9007 | 5.1158 | 5.0708 | 5.0214 | 4.9682 | 4.9191 | 4.8508 | 4.7754 | 4.7205 | 4.6598 | 4.6004 | 4.5461 | 4.4524 | 4.4118 | 4.3946 | 4.8816 | 4.8057 | 4.7189 | 4.6267 | 4.54 | 4.4257 | 4.3012 | 4.2207 | 4.131 | 4.0446 | 3.9649 | 3.8191 | 3.7446 | 3.7147
|  | BRORA | ST |  |  |  | 4.7694 | 4.7683 | 4.7669 | 4.7649 | 4.7628 | 4.7604 | 4.7572 | 4.7531 | 4.7482 | 4.7415 | 4.6695 | 4.3146 | 4.192 | 4.1186 | 5.1647 | 5.1498 | 5.1303 | 5.1069 | 5.0826 | 5.0569 | 5.0249 | 4.9867 | 4.9428 | 4.8941 | 4.8411 | 4.5748 | 4.4708 | 4.3808 | 4.9745 | 4.9496 | 4.9173 | 4.879 | 4.8401 | 4.8003 | 4.7502 | 4.6913 | 4.6243 | 4.5507 | 4.4716 | 4.0888 | 3.964 | 3.8952
|  | BRORA | FS |  |  |  | 4.7699 | 4.7692 | 4.768 | 4.7665 | 4.7651 | 4.7632 | 4.761 | 4.7583 | 4.7551 | 4.7517 | 4.7306 | 4.3619 | 4.0987 | 4.0291 | 5.1711 | 5.1598 | 5.1418 | 5.1199 | 5.0992 | 5.0749 | 5.0476 | 5.0161 | 4.9809 | 4.9425 | 4.9019 | 4.6297 | 4.3924 | 4.2367 | 4.9871 | 4.9691 | 4.9391 | 4.9028 | 4.8695 | 4.8308 | 4.7877 | 4.7391 | 4.6854 | 4.6277 | 4.5678 | 4.1687 | 3.8895 | 3.821
| MILTON OF CRAIGIE | BROUGHTY FERRY | MINIMUM HEADROOM | NO 46658 30758 | NO | YES | 6.6166 | 6.4624 | 6.16 | 5.8484 | 5.5296 | 5.1172 | 4.6714 | 4.2448 | 3.7879 | 3.3245 | 2.8842 | 1.7507 | 1.1299 | 0.45192 | 7.8889 | 7.7704 | 7.621 | 7.4143 | 7.2461 | 7.059 | 6.7842 | 6.4697 | 6.1292 | 5.7857 | 5.4613 | 4.5787 | 3.6649 | 1.8632 | 7.4235 | 7.2664 | 6.9902 | 6.7046 | 6.4157 | 6.0355 | 5.6214 | 5.2119 | 4.774 | 4.3314 | 3.9102 | 2.8355 | 2.1607 | 1.3647
|  | BROUGHTY FERRY | CT |  |  |  | 6.7767 | 6.6757 | 6.3548 | 6.0206 | 5.7275 | 5.4423 | 5.1508 | 4.7855 | 4.3561 | 3.9199 | 3.4946 | 2.1349 | 1.4313 | 0.94166 | 7.9224 | 7.8249 | 7.6274 | 7.4143 | 7.2461 | 7.0743 | 6.8976 | 6.6373 | 6.3194 | 5.9959 | 5.6781 | 4.5787 | 3.6649 | 2.4407 | 7.5551 | 7.4414 | 7.1581 | 6.8476 | 6.5797 | 6.3171 | 6.0488 | 5.7017 | 5.295 | 4.8835 | 4.4819 | 3.2094 | 2.5284 | 2.0223
|  | BROUGHTY FERRY | LW |  |  |  | 6.6166 | 6.4624 | 6.16 | 5.8484 | 5.5296 | 5.1172 | 4.6714 | 4.2448 | 3.7879 | 3.3245 | 2.8842 | 1.7507 | 1.1299 | 0.45192 | 7.8889 | 7.7704 | 7.621 | 7.4587 | 7.3015 | 7.059 | 6.7842 | 6.4697 | 6.1292 | 5.7857 | 5.4613 | 4.6985 | 4.136 | 3.3644 | 7.4235 | 7.2664 | 6.9902 | 6.7046 | 6.4157 | 6.0355 | 5.6214 | 5.2119 | 4.774 | 4.3314 | 3.9102 | 2.8355 | 2.1607 | 1.3647
|  | BROUGHTY FERRY | ST |  |  |  | 6.8448 | 6.8159 | 6.7775 | 6.7152 | 6.6478 | 6.569 | 6.4685 | 6.3041 | 6.1197 | 5.9115 | 5.6772 | 4.2577 | 3.3649 | 2.5484 | 7.9616 | 7.9198 | 7.8684 | 7.8007 | 7.7242 | 7.6331 | 7.5226 | 7.3348 | 7.1453 | 6.9338 | 6.6911 | 5.3022 | 4.194 | 2.8269 | 7.6146 | 7.5767 | 7.5277 | 7.4585 | 7.3819 | 7.29 | 7.175 | 6.981 | 6.7753 | 6.5443 | 6.2816 | 4.7824 | 3.9264 | 3.1959
|  | BROUGHTY FERRY | FS |  |  |  | 6.8442 | 6.8231 | 6.7799 | 6.7298 | 6.6677 | 6.6024 | 6.5218 | 6.3825 | 6.2341 | 6.073 | 5.8962 | 4.7461 | 3.5628 | 2.8009 | 7.9621 | 7.9238 | 7.8738 | 7.8144 | 7.7473 | 7.6699 | 7.5782 | 7.435 | 7.2796 | 7.1068 | 6.9147 | 5.6671 | 4.0148 | 1.8632 | 7.618 | 7.5886 | 7.5414 | 7.4856 | 7.4216 | 7.3505 | 7.2637 | 7.1223 | 6.9707 | 6.8044 | 6.6214 | 5.4711 | 4.3594 | 3.7854
| DUNOON | BRUCHAG | MINIMUM HEADROOM | NS 11372 57191 | NO | YES | 11.2258 | 11.1182 | 10.9923 | 10.8342 | 10.6556 | 10.464 | 10.2834 | 10.0756 | 9.8493 | 9.6113 | 9.3854 | 8.9115 | 8.6908 | 8.2438 | 12.2034 | 12.1289 | 12.0497 | 11.9298 | 11.794 | 11.6483 | 11.5357 | 11.4133 | 11.2371 | 11.0535 | 10.8796 | 10.5026 | 10.2722 | 9.8314 | 11.973 | 11.8694 | 11.7511 | 11.5949 | 11.416 | 11.2242 | 11.0656 | 10.8647 | 10.6379 | 10.4 | 10.1745 | 9.696 | 9.4439 | 8.9452
|  | BRUCHAG | CT |  |  |  | 11.2656 | 11.1935 | 11.0246 | 10.8342 | 10.6556 | 10.464 | 10.2988 | 10.1512 | 9.9917 | 9.8298 | 9.6463 | 9.1416 | 8.9311 | 8.788 | 12.2226 | 12.1709 | 12.0586 | 11.9298 | 11.794 | 11.6483 | 11.5357 | 11.4135 | 11.282 | 11.1506 | 11.0005 | 10.5455 | 10.3285 | 10.1159 | 11.9852 | 11.9384 | 11.7775 | 11.5949 | 11.416 | 11.2242 | 11.0656 | 10.9153 | 10.7528 | 10.5889 | 10.4028 | 9.8763 | 9.6555 | 9.4957
|  | BRUCHAG | LW |  |  |  | 11.2258 | 11.1182 | 10.9923 | 10.8523 | 10.7188 | 10.5138 | 10.2834 | 10.0756 | 9.8493 | 9.6113 | 9.3854 | 8.9115 | 8.6908 | 8.2438 | 12.2034 | 12.1289 | 12.0497 | 11.9598 | 11.8736 | 11.7347 | 11.5744 | 11.4133 | 11.2371 | 11.0535 | 10.8796 | 10.5026 | 10.2722 | 9.8314 | 11.973 | 11.8694 | 11.7511 | 11.6188 | 11.4924 | 11.2956 | 11.0726 | 10.8647 | 10.6379 | 10.4 | 10.1745 | 9.696 | 9.4439 | 8.9452
|  | BRUCHAG | ST |  |  |  | 11.3757 | 11.3644 | 11.3119 | 11.2595 | 11.209 | 11.1081 | 11.0349 | 10.9151 | 10.801 | 10.6796 | 10.5303 | 9.8536 | 9.6649 | 9.4925 | 12.2797 | 12.2654 | 12.2047 | 12.1494 | 12.0983 | 11.9927 | 11.9237 | 11.8113 | 11.7147 | 11.6116 | 11.4861 | 10.8815 | 10.6085 | 10.3536 | 11.9936 | 11.9934 | 11.9526 | 11.9239 | 11.9042 | 11.8061 | 11.7283 | 11.5997 | 11.4828 | 11.3585 | 11.2057 | 10.5046 | 10.2776 | 10.0791
|  | BRUCHAG | FS |  |  |  | 11.3693 | 11.357 | 11.3171 | 11.2733 | 11.2265 | 11.1684 | 11.103 | 11.0354 | 10.962 | 10.8793 | 10.7914 | 10.2195 | 9.7551 | 9.5396 | 12.2784 | 12.2649 | 12.232 | 12.1951 | 12.1544 | 12.1062 | 12.0528 | 11.9897 | 11.9243 | 11.8518 | 11.7735 | 11.3036 | 10.8711 | 10.5596 | 11.9929 | 11.9927 | 11.9833 | 11.9736 | 11.9571 | 11.8984 | 11.8328 | 11.7619 | 11.6865 | 11.602 | 11.512 | 10.9446 | 10.4826 | 10.2701
| KEITH | BUCKIE | MINIMUM HEADROOM | NJ 43291 64802 | NO | YES | 7.2841 | 6.6652 | 5.584 | 4.3715 | 3.0796 | 1.861 | 0.55151 | -0.53209 | -1.646 | -2.7035 | -3.5243 | -5.9718 | -7.4441 | -8.371 | 9.6151 | 9.2189 | 8.5693 | 7.8149 | 6.9586 | 6.1839 | 5.3291 | 4.6315 | 3.8933 | 3.1798 | 2.6669 | 1.1716 | 0.12203 | -0.80725 | 8.2062 | 7.651 | 6.6569 | 5.5409 | 4.3192 | 3.1561 | 1.9237 | 0.91918 | -0.12129 | -1.1176 | -1.8962 | -4.224 | -5.7036 | -6.7206
|  | BUCKIE | CT |  |  |  | 7.8272 | 7.3555 | 6.3805 | 5.2723 | 4.1464 | 3.1998 | 2.1954 | 1.0874 | -0.13653 | -1.2949 | -2.1949 | -5.25 | -7.2783 | -8.371 | 9.826 | 9.4654 | 8.9259 | 8.2449 | 7.5117 | 6.9449 | 6.3311 | 5.6604 | 4.8883 | 4.1466 | 3.6171 | 1.8215 | 0.50363 | -0.70558 | 8.6848 | 8.2566 | 7.3738 | 6.3678 | 5.3214 | 4.4395 | 3.5238 | 2.5136 | 1.3883 | 0.31622 | -0.5184 | -3.3413 | -5.2129 | -6.2708
|  | BUCKIE | LW |  |  |  | 7.2841 | 6.6652 | 5.584 | 4.3715 | 3.0796 | 1.861 | 0.55151 | -0.53209 | -1.646 | -2.7035 | -3.5243 | -5.9718 | -7.4441 | -8.3258 | 9.6151 | 9.2189 | 8.5693 | 7.8149 | 6.9586 | 6.1839 | 5.3291 | 4.6315 | 3.8933 | 3.1798 | 2.6669 | 1.1716 | 0.12203 | -0.80725 | 8.2062 | 7.651 | 6.6569 | 5.5409 | 4.3192 | 3.1561 | 1.9237 | 0.91918 | -0.12129 | -1.1176 | -1.8962 | -4.224 | -5.7036 | -6.7206
|  | BUCKIE | ST |  |  |  | 7.9904 | 7.6703 | 7.2114 | 6.6824 | 6.174 | 5.7366 | 5.2578 | 4.6894 | 4.101 | 3.5206 | 3.1101 | 0.47958 | -1.5744 | -3.7479 | 9.8803 | 9.6406 | 9.2478 | 8.8184 | 8.4122 | 8.037 | 7.6213 | 7.1354 | 6.6527 | 6.1672 | 5.823 | 3.8532 | 2.335 | 0.65036 | 8.8324 | 8.5486 | 8.1005 | 7.6021 | 7.1309 | 6.6865 | 6.2303 | 5.6822 | 5.1305 | 4.5787 | 4.1743 | 1.528 | -0.34579 | -2.3627
|  | BUCKIE | FS |  |  |  | 8.196 | 7.948 | 7.6196 | 7.2112 | 6.8023 | 6.5011 | 6.0995 | 5.5785 | 5.0357 | 4.5128 | 4.0894 | 1.5412 | -0.91619 | -2.7805 | 10.0549 | 9.8656 | 9.6349 | 9.324 | 9.0032 | 8.7778 | 8.439 | 8.0439 | 7.6249 | 7.2095 | 6.8818 | 5.0228 | 2.9527 | 0.81416 | 9.0205 | 8.8027 | 8.5053 | 8.1367 | 7.767 | 7.4972 | 7.1255 | 6.6486 | 6.1503 | 5.6621 | 5.2644 | 2.8989 | 0.61872 | -1.0565
| FORT AUGUSTUS | BUNOICH | MINIMUM HEADROOM | NH 37662 09672 | YES | YES | 1.7566 | 1.7353 | 1.7148 | 1.6899 | 1.6714 | 1.6479 | 1.3234 | 1.2987 | 1.2822 | 1.2605 | 1.2439 | 1.1982 | 1.1575 | 1.1423 | 1.8431 | 1.8333 | 1.8242 | 1.8133 | 1.8026 | 1.7889 | 1.6356 | 1.6208 | 1.6079 | 1.592 | 1.5786 | 1.5492 | 1.5291 | 1.5139 | 1.8217 | 1.8094 | 1.793 | 1.7729 | 1.7572 | 1.7338 | 1.4603 | 1.437 | 1.4201 | 1.3986 | 1.3817 | 1.3404 | 1.3059 | 1.2925
|  | BUNOICH | CT |  |  |  | 1.7684 | 1.7571 | 1.7324 | 1.7061 | 1.6793 | 1.6488 | 1.3762 | 1.3598 | 1.3349 | 1.3029 | 1.2698 | 1.1982 | 1.1575 | 1.1423 | 1.8466 | 1.8399 | 1.8272 | 1.8137 | 1.8026 | 1.7889 | 1.6608 | 1.6501 | 1.6343 | 1.6135 | 1.5934 | 1.5492 | 1.5291 | 1.5139 | 1.8231 | 1.8186 | 1.804 | 1.7811 | 1.7601 | 1.7339 | 1.5015 | 1.4869 | 1.4631 | 1.4336 | 1.4039 | 1.3406 | 1.3059 | 1.2925
|  | BUNOICH | LW |  |  |  | 1.7566 | 1.7353 | 1.7148 | 1.6899 | 1.6714 | 1.6479 | 1.3234 | 1.2987 | 1.2822 | 1.2605 | 1.2439 | 1.1984 | 1.178 | 1.1674 | 1.8431 | 1.8333 | 1.8242 | 1.8133 | 1.8047 | 1.7905 | 1.6356 | 1.6208 | 1.6079 | 1.592 | 1.5786 | 1.5528 | 1.545 | 1.5413 | 1.8217 | 1.8094 | 1.793 | 1.7729 | 1.7572 | 1.7338 | 1.4603 | 1.437 | 1.4201 | 1.3986 | 1.3817 | 1.3404 | 1.3231 | 1.3143
|  | BUNOICH | ST |  |  |  | 1.7757 | 1.7724 | 1.7629 | 1.7493 | 1.743 | 1.7342 | 1.5887 | 1.5712 | 1.5489 | 1.5235 | 1.4967 | 1.3873 | 1.3552 | 1.3337 | 1.8495 | 1.8473 | 1.843 | 1.8369 | 1.8325 | 1.8268 | 1.7461 | 1.7356 | 1.7228 | 1.7075 | 1.6911 | 1.6205 | 1.5997 | 1.583 | 1.8265 | 1.8254 | 1.8231 | 1.8192 | 1.8132 | 1.8047 | 1.6783 | 1.6634 | 1.6447 | 1.623 | 1.6 | 1.5045 | 1.48 | 1.4637
|  | BUNOICH | FS |  |  |  | 1.7816 | 1.7804 | 1.7677 | 1.762 | 1.7544 | 1.7444 | 1.6269 | 1.6064 | 1.5931 | 1.5679 | 1.545 | 1.4264 | 1.3641 | 1.3457 | 1.8512 | 1.8497 | 1.8448 | 1.8414 | 1.8373 | 1.8322 | 1.7621 | 1.7521 | 1.7437 | 1.73 | 1.7168 | 1.6475 | 1.6013 | 1.5795 | 1.828 | 1.8276 | 1.824 | 1.8226 | 1.8202 | 1.8137 | 1.7065 | 1.6904 | 1.6791 | 1.6588 | 1.6399 | 1.5408 | 1.4847 | 1.4711
| THURSO | BURGARHILL | MINIMUM HEADROOM | HY 34441 26078 | YES | YES | 2.8264 | 2.7738 | 2.6979 | 2.596 | 2.4769 | 2.3557 | 2.251 | 2.2012 | 2.1424 | 2.0768 | 2.0211 | 1.8856 | 1.7446 | 1.6453 | 3.295 | 3.2641 | 3.2233 | 3.1575 | 3.0804 | 3.0006 | 2.9435 | 2.8951 | 2.8362 | 2.7714 | 2.7112 | 2.5442 | 2.3827 | 2.2245 | 3.0528 | 3.0038 | 2.9348 | 2.8373 | 2.7212 | 2.6023 | 2.5052 | 2.4525 | 2.3837 | 2.3068 | 2.2408 | 2.0788 | 1.9331 | 1.8201
|  | BURGARHILL | CT |  |  |  | 2.8635 | 2.82 | 2.7139 | 2.596 | 2.4769 | 2.3557 | 2.251 | 2.2012 | 2.1424 | 2.0768 | 2.0211 | 1.8856 | 1.7446 | 1.6453 | 3.3085 | 3.2817 | 3.2233 | 3.1575 | 3.0804 | 3.0006 | 2.9435 | 2.8951 | 2.8362 | 2.7714 | 2.7112 | 2.5442 | 2.4166 | 2.2873 | 3.0857 | 3.045 | 2.9469 | 2.8373 | 2.7212 | 2.6023 | 2.5052 | 2.4525 | 2.3837 | 2.3068 | 2.2408 | 2.0788 | 1.9331 | 1.823
|  | BURGARHILL | LW |  |  |  | 2.8264 | 2.7738 | 2.6979 | 2.6185 | 2.5461 | 2.4523 | 2.3454 | 2.2848 | 2.2212 | 2.1553 | 2.0906 | 1.9664 | 1.8164 | 1.6477 | 3.295 | 3.2641 | 3.2265 | 3.1857 | 3.1495 | 3.0963 | 3.0348 | 2.9827 | 2.9252 | 2.863 | 2.804 | 2.6959 | 2.5463 | 2.3519 | 3.0528 | 3.0038 | 2.9348 | 2.8624 | 2.7966 | 2.7096 | 2.6102 | 2.5437 | 2.4712 | 2.397 | 2.3253 | 2.1946 | 2.0246 | 1.8214
|  | BURGARHILL | ST |  |  |  | 2.888 | 2.87 | 2.8238 | 2.7826 | 2.7409 | 2.6756 | 2.6266 | 2.5579 | 2.496 | 2.4335 | 2.3593 | 1.988 | 1.806 | 1.6781 | 3.3205 | 3.3097 | 3.2681 | 3.2329 | 3.2011 | 3.1378 | 3.1001 | 3.0385 | 2.9908 | 2.9417 | 2.8817 | 2.5634 | 2.3827 | 2.2245 | 3.1022 | 3.0913 | 3.0416 | 2.9985 | 2.9566 | 2.8837 | 2.833 | 2.7576 | 2.693 | 2.6269 | 2.5479 | 2.1593 | 1.9639 | 1.8201
|  | BURGARHILL | FS |  |  |  | 2.8968 | 2.8817 | 2.8549 | 2.8252 | 2.7977 | 2.7626 | 2.729 | 2.6823 | 2.6386 | 2.5868 | 2.5371 | 2.2239 | 1.9894 | 1.9288 | 3.3241 | 3.3148 | 3.2967 | 3.2763 | 3.2557 | 3.2311 | 3.2065 | 3.1715 | 3.1388 | 3.1015 | 3.0634 | 2.841 | 2.6433 | 2.5548 | 3.1035 | 3.0997 | 3.0759 | 3.0471 | 3.0199 | 2.9857 | 2.9518 | 2.9041 | 2.8591 | 2.8065 | 2.7548 | 2.4425 | 2.2077 | 2.1496
| ELGIN | BURGHEAD | MINIMUM HEADROOM | NJ 12666 68781 | NO | YES | 7.2626 | 6.9708 | 5.6866 | 4.2669 | 1.7343 | -0.96832 | -2.69 | -3.2754 | -3.8894 | -4.4534 | -5.0358 | -7.1687 | -7.8771 | -8.2878 | 8.0423 | 7.8861 | 6.5053 | 4.967 | 2.0386 | -1.0976 | -3.0032 | -3.5948 | -4.216 | -4.7709 | -5.3538 | -7.7197 | -8.4545 | -8.8787 | 6.7413 | 6.4803 | 4.9843 | 3.3252 | 0.2745 | -2.9872 | -5.0203 | -5.6761 | -6.3636 | -6.9865 | -7.6359 | -10.1525 | -10.9622 | -11.4336
|  | BURGHEAD | CT |  |  |  | 7.4442 | 7.2224 | 6.703 | 6.0761 | 4.6572 | 3.1961 | 2.5682 | 2.2127 | 1.8075 | 1.4212 | 1.05 | -0.16309 | -0.77165 | -1.0407 | 8.1073 | 7.9795 | 7.6138 | 7.1199 | 5.6244 | 4.0512 | 3.518 | 3.1866 | 2.8157 | 2.4668 | 2.1199 | 0.78917 | 0.22599 | -0.20943 | 6.9005 | 6.7016 | 6.1905 | 5.5485 | 3.9087 | 2.2015 | 1.5348 | 1.1542 | 0.72433 | 0.31746 | -0.079102 | -1.4559 | -2.0738 | -2.3532
|  | BURGHEAD | LW |  |  |  | 7.2626 | 6.9708 | 5.6866 | 4.2669 | 1.7343 | -0.96832 | -2.69 | -3.2754 | -3.8894 | -4.4534 | -5.0358 | -7.1687 | -7.8771 | -8.2878 | 8.0423 | 7.8861 | 6.5053 | 4.967 | 2.0386 | -1.0976 | -3.0032 | -3.5948 | -4.216 | -4.7709 | -5.3538 | -7.7197 | -8.4545 | -8.8787 | 6.7413 | 6.4803 | 4.9843 | 3.3252 | 0.2745 | -2.9872 | -5.0203 | -5.6761 | -6.3636 | -6.9865 | -7.6359 | -10.1525 | -10.9622 | -11.4336
|  | BURGHEAD | ST |  |  |  | 7.5854 | 7.4622 | 6.3689 | 5.5689 | 4.9719 | 3.3648 | 2.7824 | 2.268 | 1.9258 | 1.5756 | 1.1568 | -0.87391 | -1.6884 | -2.0938 | 8.1724 | 8.1064 | 6.8498 | 5.9633 | 5.3375 | 3.4337 | 2.8184 | 2.3005 | 2.0082 | 1.7177 | 1.3438 | -0.49782 | -1.2813 | -1.8054 | 7.0275 | 6.9215 | 5.6127 | 4.6731 | 3.9913 | 2.0367 | 1.3669 | 0.78976 | 0.43466 | 0.076029 | -0.36625 | -2.5205 | -3.3658 | -3.7734
|  | BURGHEAD | FS |  |  |  | 7.649 | 7.5542 | 7.2335 | 6.9017 | 6.5304 | 6.1718 | 5.8406 | 5.5596 | 5.3051 | 5.0396 | 4.7584 | 3.3249 | 2.3433 | 1.9528 | 8.1984 | 8.1453 | 7.8364 | 7.5189 | 7.1563 | 6.7969 | 6.4716 | 6.2272 | 6.0176 | 5.7975 | 5.5646 | 4.5343 | 3.6276 | 2.9228 | 7.0837 | 7.0028 | 6.6516 | 6.2895 | 5.8809 | 5.4791 | 5.1112 | 4.8162 | 4.5565 | 4.2854 | 3.9992 | 2.629 | 1.6843 | 1.3189
| BURGHMUIR | BURGHMUIR | MINIMUM HEADROOM | NO 08256 23702 | NO | YES | 1.2229 | 0.47695 | -0.80199 | -2.3247 | -3.7543 | -5.474 | -7.1518 | -8.5294 | -9.9597 | -11.4623 | -13.1525 | -18.2884 | -20.3192 | -20.9188 | 3.9096 | 3.3777 | 2.4929 | 1.4303 | 0.40638 | -0.8252 | -1.9319 | -2.7984 | -3.718 | -4.6843 | -5.8253 | -8.9941 | -10.5814 | -11.1706 | 2.1489 | 1.4802 | 0.35106 | -1.0334 | -2.4224 | -4.1023 | -5.6941 | -6.9819 | -8.3399 | -9.7641 | -11.3457 | -15.9864 | -17.8192 | -18.4357
|  | BURGHMUIR | CT |  |  |  | 1.6095 | 1.0305 | -0.09349 | -1.4547 | -2.671 | -3.982 | -5.2115 | -6.5591 | -8.0003 | -9.4703 | -11.1892 | -16.5211 | -19.028 | -19.9946 | 4.042 | 3.5803 | 2.8316 | 1.9031 | 1.0549 | 0.14544 | -0.60452 | -1.4325 | -2.3352 | -3.2541 | -4.4034 | -8.3632 | -9.866 | -11.1706 | 2.4293 | 1.8993 | 0.9198 | -0.26866 | -1.4048 | -2.6471 | -3.7574 | -4.9874 | -6.3286 | -7.6924 | -9.2726 | -14.152 | -16.4186 | -17.2937
|  | BURGHMUIR | LW |  |  |  | 1.2229 | 0.47695 | -0.80199 | -2.3247 | -3.7543 | -5.474 | -7.1518 | -8.5294 | -9.9597 | -11.4623 | -13.1525 | -18.2884 | -20.3192 | -20.9188 | 3.9096 | 3.3777 | 2.4929 | 1.4303 | 0.40638 | -0.8252 | -1.9319 | -2.7984 | -3.718 | -4.6843 | -5.8253 | -8.9941 | -10.5814 | -10.887 | 2.1489 | 1.4802 | 0.35106 | -1.0334 | -2.4224 | -4.1023 | -5.6941 | -6.9819 | -8.3399 | -9.7641 | -11.3457 | -15.9864 | -17.8192 | -18.4357
|  | BURGHMUIR | ST |  |  |  | 2.2418 | 1.8828 | 1.1875 | 0.34509 | -0.19409 | -1.0215 | -1.6872 | -2.3811 | -3.1445 | -4.0291 | -5.1856 | -11.2549 | -13.8234 | -14.847 | 4.486 | 4.1845 | 3.5321 | 2.8012 | 2.3676 | 1.614 | 1.0897 | 0.56288 | -0.0099212 | -0.71227 | -2.0325 | -8.0657 | -10.0953 | -10.426 | 2.9942 | 2.6754 | 1.9913 | 1.208 | 0.69714 | -0.15178 | -0.78553 | -1.4361 | -2.1537 | -2.9845 | -4.057 | -10.4649 | -12.9655 | -13.3432
|  | BURGHMUIR | FS |  |  |  | 2.4858 | 2.2195 | 1.7777 | 1.1769 | 0.772 | 0.29003 | -0.19402 | -0.74298 | -1.3524 | -1.9904 | -2.7583 | -7.3337 | -11.8763 | -14.9456 | 4.6741 | 4.446 | 4.0757 | 3.5808 | 3.2659 | 2.8934 | 2.5234 | 2.1261 | 1.6679 | 1.1889 | 0.58529 | -2.9259 | -6.9931 | -10.6903 | 3.2057 | 2.9692 | 2.5723 | 2.0405 | 1.672 | 1.2363 | 0.79585 | 0.31138 | -0.23239 | -0.80602 | -1.4951 | -5.7035 | -9.9899 | -13.2001
| CLACHAN | BUTTERBRIDGE | MINIMUM HEADROOM | NN 19306 09936 | YES | YES | 0.094185 | 0.086121 | 0.081977 | 0.068265 | 0.049906 | 0.028442 | 0.014558 | 0.0058542 | -0.0095621 | -0.021092 | -0.03622 | -0.095524 | -0.15327 | -0.19874 | 0.096729 | 0.092495 | 0.083305 | 0.072376 | 0.059519 | 0.039101 | 0.02963 | 0.013627 | 0.0027502 | -0.0071731 | -0.022356 | -0.092184 | -0.15387 | -0.20717 | 0.08754 | 0.080182 | 0.075651 | 0.062041 | 0.041252 | 0.017436 | 0.0038384 | -0.0064871 | -0.022962 | -0.03593 | -0.051884 | -0.1227 | -0.18936 | -0.24465
|  | BUTTERBRIDGE | CT |  |  |  | 0.098349 | 0.093611 | 0.084291 | 0.068265 | 0.049906 | 0.028442 | 0.014558 | 0.0058542 | -0.0095621 | -0.021092 | -0.03622 | -0.077604 | -0.11783 | -0.14673 | 0.09809 | 0.094905 | 0.087547 | 0.078063 | 0.059519 | 0.039101 | 0.02963 | 0.017987 | 0.005191 | -0.00659 | -0.019754 | -0.067722 | -0.10797 | -0.14867 | 0.091198 | 0.086757 | 0.077518 | 0.062041 | 0.041252 | 0.017436 | 0.0038384 | -0.0064871 | -0.022962 | -0.03593 | -0.051884 | -0.10006 | -0.14541 | -0.18156
|  | BUTTERBRIDGE | LW |  |  |  | 0.094185 | 0.086121 | 0.081977 | 0.073526 | 0.065138 | 0.05704 | 0.045852 | 0.037144 | 0.024079 | 0.015738 | 0.0030459 | -0.032084 | -0.085671 | -0.15875 | 0.096729 | 0.092495 | 0.089882 | 0.085529 | 0.081408 | 0.076028 | 0.069234 | 0.059888 | 0.048543 | 0.038335 | 0.027725 | -0.0032252 | -0.066911 | -0.15725 | 0.08754 | 0.080182 | 0.07631 | 0.068615 | 0.061021 | 0.053203 | 0.042758 | 0.033585 | 0.020138 | 0.010759 | -0.0021709 | -0.038812 | -0.10427 | -0.19519
|  | BUTTERBRIDGE | ST |  |  |  | 0.10296 | 0.10025 | 0.085215 | 0.074733 | 0.069918 | 0.045655 | 0.035183 | 0.019658 | 0.0079414 | -0.00134 | -0.019416 | -0.095524 | -0.15327 | -0.19874 | 0.10015 | 0.098701 | 0.083305 | 0.072376 | 0.065459 | 0.041178 | 0.031984 | 0.013627 | 0.0027502 | -0.0071731 | -0.022356 | -0.092184 | -0.15387 | -0.20717 | 0.095338 | 0.092883 | 0.075651 | 0.063647 | 0.057356 | 0.029802 | 0.01865 | 0.00012817 | -0.012427 | -0.023317 | -0.042052 | -0.1227 | -0.18936 | -0.24465
|  | BUTTERBRIDGE | FS |  |  |  | 0.10344 | 0.10254 | 0.097641 | 0.0944 | 0.086614 | 0.079283 | 0.073517 | 0.066624 | 0.058941 | 0.047544 | 0.039899 | -0.0033587 | -0.035308 | -0.061469 | 0.10039 | 0.099613 | 0.095447 | 0.091733 | 0.086 | 0.080314 | 0.075311 | 0.067664 | 0.06083 | 0.05255 | 0.045339 | 0.014863 | -0.011487 | -0.032017 | 0.095779 | 0.094881 | 0.089698 | 0.085868 | 0.077969 | 0.070463 | 0.064382 | 0.056454 | 0.048306 | 0.036904 | 0.028638 | -0.01336 | -0.045313 | -0.07136
| BRACO | CALLANDER | MINIMUM HEADROOM | NN 62995 07081 | NO | YES | 2.6375 | 2.5332 | 2.387 | 2.0596 | 1.7265 | 1.3606 | 0.97679 | 0.67889 | 0.3549 | 0.023856 | -0.30656 | -1.5429 | -2.3926 | -2.9785 | 3.3903 | 3.324 | 3.2258 | 3.0993 | 2.9892 | 2.8159 | 2.6085 | 2.4223 | 2.2178 | 2.0067 | 1.7997 | 1.1233 | 0.68812 | 0.20929 | 2.7534 | 2.6344 | 2.4705 | 2.2776 | 2.0758 | 1.8558 | 1.5907 | 1.3075 | 0.95687 | 0.55191 | 0.15797 | -1.064 | -1.7836 | -2.364
|  | CALLANDER | CT |  |  |  | 2.7387 | 2.6027 | 2.4077 | 2.2038 | 1.884 | 1.5309 | 1.1916 | 0.90335 | 0.602 | 0.3048 | -0.0060015 | -1.225 | -2.2526 | -2.9388 | 3.4563 | 3.349 | 3.2258 | 3.0993 | 2.9892 | 2.8179 | 2.642 | 2.4753 | 2.2951 | 2.1159 | 1.9292 | 1.2291 | 0.68812 | 0.20929 | 2.8469 | 2.7158 | 2.5258 | 2.2919 | 2.0758 | 1.8558 | 1.6516 | 1.4716 | 1.2216 | 0.90526 | 0.54959 | -0.6833 | -1.5532 | -2.1396
|  | CALLANDER | LW |  |  |  | 2.6375 | 2.5332 | 2.387 | 2.0596 | 1.7265 | 1.3606 | 0.97679 | 0.67889 | 0.3549 | 0.023856 | -0.30656 | -1.5429 | -2.3926 | -2.9785 | 3.3903 | 3.324 | 3.2646 | 3.1727 | 3.0073 | 2.8159 | 2.6085 | 2.4223 | 2.2178 | 2.0067 | 1.7997 | 1.1233 | 0.70565 | 0.37084 | 2.7534 | 2.6344 | 2.4705 | 2.2776 | 2.0872 | 1.8726 | 1.5907 | 1.3075 | 0.95687 | 0.55191 | 0.15797 | -1.064 | -1.7836 | -2.364
|  | CALLANDER | ST |  |  |  | 2.7806 | 2.7201 | 2.6363 | 2.5501 | 2.4538 | 2.3476 | 2.2552 | 2.1452 | 2.0216 | 1.8855 | 1.7102 | 0.39142 | -0.33584 | -1.1037 | 3.477 | 3.4281 | 3.3606 | 3.2955 | 3.2251 | 3.1441 | 3.0829 | 3.003 | 2.9167 | 2.8196 | 2.7067 | 1.7873 | 1.3651 | 0.86077 | 2.8747 | 2.8217 | 2.7474 | 2.6729 | 2.5897 | 2.4791 | 2.3824 | 2.2693 | 2.145 | 2.009 | 1.8561 | 0.77166 | 0.053872 | -0.55241
|  | CALLANDER | FS |  |  |  | 2.9032 | 2.859 | 2.7901 | 2.7232 | 2.6532 | 2.58 | 2.5033 | 2.413 | 2.314 | 2.2096 | 2.0626 | 0.92094 | -0.11557 | -0.9831 | 3.5967 | 3.5596 | 3.5073 | 3.458 | 3.411 | 3.3593 | 3.305 | 3.2428 | 3.1746 | 3.101 | 3.0202 | 2.2453 | 1.4594 | 0.66242 | 2.9912 | 2.9519 | 2.8951 | 2.8394 | 2.7844 | 2.721 | 2.6404 | 2.5422 | 2.4365 | 2.326 | 2.2064 | 1.3344 | 0.24375 | -0.51071
| STORNOWAY | CALLANISH | MINIMUM HEADROOM | NB 22040 33554 | YES | YES | 2.5434 | 2.45 | 2.3481 | 2.238 | 2.1369 | 2.0109 | 1.8807 | 1.81 | 1.736 | 1.6556 | 1.5675 | 1.4106 | 1.3145 | 1.2597 | 2.841 | 2.8229 | 2.8079 | 2.7537 | 2.6996 | 2.6409 | 2.5699 | 2.5172 | 2.4611 | 2.3974 | 2.3302 | 2.2266 | 2.1465 | 2.0857 | 2.6022 | 2.5538 | 2.4741 | 2.3868 | 2.3092 | 2.2045 | 2.0931 | 2.0169 | 1.9362 | 1.8511 | 1.7683 | 1.6143 | 1.5185 | 1.4657
|  | CALLANISH | CT |  |  |  | 2.621 | 2.556 | 2.4173 | 2.2751 | 2.1492 | 2.0253 | 1.8976 | 1.8405 | 1.7665 | 1.6931 | 1.6262 | 1.4635 | 1.3145 | 1.2597 | 2.846 | 2.8275 | 2.8084 | 2.7594 | 2.6996 | 2.6417 | 2.5821 | 2.5404 | 2.4842 | 2.4274 | 2.368 | 2.2348 | 2.1465 | 2.0857 | 2.6062 | 2.5847 | 2.5221 | 2.407 | 2.3109 | 2.2162 | 2.1191 | 2.0593 | 1.9769 | 1.8944 | 1.823 | 1.6653 | 1.5185 | 1.4657
|  | CALLANISH | LW |  |  |  | 2.5434 | 2.45 | 2.3481 | 2.238 | 2.1369 | 2.0109 | 1.8807 | 1.81 | 1.736 | 1.6556 | 1.5675 | 1.4106 | 1.3376 | 1.3198 | 2.841 | 2.8229 | 2.8079 | 2.7537 | 2.7068 | 2.6409 | 2.5699 | 2.5172 | 2.4611 | 2.3974 | 2.3302 | 2.2266 | 2.1934 | 2.1859 | 2.6022 | 2.5538 | 2.4741 | 2.3868 | 2.3092 | 2.2045 | 2.0931 | 2.0169 | 1.9362 | 1.8511 | 1.7683 | 1.6143 | 1.5422 | 1.5245
|  | CALLANISH | ST |  |  |  | 2.6505 | 2.6167 | 2.5728 | 2.5219 | 2.4707 | 2.4138 | 2.3538 | 2.2941 | 2.2215 | 2.1441 | 2.0585 | 1.6124 | 1.4636 | 1.3883 | 2.8516 | 2.8403 | 2.8326 | 2.8244 | 2.8141 | 2.8045 | 2.7889 | 2.7527 | 2.7085 | 2.6601 | 2.6079 | 2.3121 | 2.212 | 2.1473 | 2.6133 | 2.6008 | 2.5924 | 2.5828 | 2.5593 | 2.5118 | 2.4603 | 2.4065 | 2.341 | 2.2702 | 2.1943 | 1.8149 | 1.6682 | 1.5934
|  | CALLANISH | FS |  |  |  | 2.6751 | 2.6467 | 2.614 | 2.5738 | 2.5309 | 2.4874 | 2.4414 | 2.3827 | 2.3187 | 2.2535 | 2.1866 | 1.7221 | 1.4091 | 1.3368 | 2.8618 | 2.8524 | 2.8461 | 2.8396 | 2.8327 | 2.8248 | 2.8158 | 2.8054 | 2.7697 | 2.7317 | 2.6915 | 2.4201 | 2.1864 | 2.1062 | 2.6212 | 2.6112 | 2.6044 | 2.597 | 2.5889 | 2.5709 | 2.5312 | 2.4817 | 2.427 | 2.3701 | 2.3104 | 1.9085 | 1.6151 | 1.544
| TUMMEL BRIDGE | CALVINE | MINIMUM HEADROOM | NN 80186 65270 | YES | YES | -0.86385 | -0.88531 | -0.90658 | -0.93354 | -0.96441 | -0.99686 | -1.0264 | -1.0508 | -1.0748 | -1.1032 | -1.1365 | -1.2186 | -1.301 | -1.3426 | 0.14641 | 0.12978 | 0.1146 | 0.095958 | 0.068974 | 0.040491 | 0.017304 | -0.000807 | -0.025022 | -0.046702 | -0.067817 | -0.12809 | -0.18558 | -0.23879 | -0.00010888 | -0.031673 | -0.06114 | -0.092404 | -0.1264 | -0.17236 | -0.21497 | -0.23875 | -0.27304 | -0.30162 | -0.3297 | -0.40581 | -0.48189 | -0.53111
|  | CALVINE | CT |  |  |  | -0.85607 | -0.87565 | -0.90658 | -0.93354 | -0.96441 | -0.99686 | -1.0264 | -1.0508 | -1.0748 | -1.0971 | -1.125 | -1.2062 | -1.2479 | -1.2751 | 0.15611 | 0.14355 | 0.11972 | 0.095958 | 0.068974 | 0.040491 | 0.017304 | -0.000807 | -0.025022 | -0.046702 | -0.067817 | -0.12809 | -0.17752 | -0.21568 | 0.023219 | 0.0016755 | -0.041386 | -0.08276 | -0.1264 | -0.17236 | -0.21497 | -0.23875 | -0.27304 | -0.30162 | -0.3297 | -0.40581 | -0.48189 | -0.52285
|  | CALVINE | LW |  |  |  | -0.86385 | -0.88531 | -0.90366 | -0.92388 | -0.94414 | -0.97207 | -1.0053 | -1.0352 | -1.0691 | -1.1032 | -1.1365 | -1.2162 | -1.2632 | -1.3123 | 0.14641 | 0.12978 | 0.1146 | 0.0981 | 0.082788 | 0.062553 | 0.038284 | 0.018685 | -0.0037479 | -0.02504 | -0.046308 | -0.092101 | -0.14309 | -0.20274 | -0.00010888 | -0.031673 | -0.06114 | -0.092404 | -0.12202 | -0.15709 | -0.19935 | -0.22582 | -0.25736 | -0.28598 | -0.31595 | -0.38322 | -0.4497 | -0.51706
|  | CALVINE | ST |  |  |  | -0.84575 | -0.85305 | -0.86825 | -0.88424 | -0.89947 | -0.92393 | -0.94224 | -0.9694 | -0.9948 | -1.0221 | -1.0539 | -1.2186 | -1.301 | -1.3426 | 0.16234 | 0.15661 | 0.14175 | 0.12711 | 0.11439 | 0.091919 | 0.078391 | 0.05526 | 0.036329 | 0.017442 | -0.0051263 | -0.11719 | -0.18558 | -0.23879 | 0.035501 | 0.024595 | 0.0036251 | -0.019157 | -0.039241 | -0.069449 | -0.089087 | -0.12192 | -0.15074 | -0.17835 | -0.21072 | -0.36813 | -0.46449 | -0.53111
|  | CALVINE | FS |  |  |  | -0.84179 | -0.84675 | -0.85545 | -0.86683 | -0.87667 | -0.88951 | -0.90159 | -0.91914 | -0.9367 | -0.9558 | -0.97488 | -1.1021 | -1.2039 | -1.2664 | 0.16542 | 0.16198 | 0.15459 | 0.14445 | 0.13653 | 0.12595 | 0.11682 | 0.10148 | 0.087418 | 0.071932 | 0.057459 | -0.037761 | -0.10891 | -0.14561 | 0.042421 | 0.036598 | 0.024029 | 0.0057051 | -0.0066241 | -0.024553 | -0.038548 | -0.064051 | -0.086946 | -0.1122 | -0.13395 | -0.29348 | -0.39602 | -0.44312
| CARRADALE | CAMPBELTOWN | MINIMUM HEADROOM | NR 71509 20746 | NO | YES | 6.9204 | 6.7135 | 6.4251 | 6.1446 | 5.8209 | 5.4324 | 5.1142 | 4.8065 | 4.4643 | 4.1361 | 3.8111 | 2.6903 | 1.734 | 0.5355 | 8.907 | 8.7964 | 8.662 | 8.4774 | 8.2201 | 7.9483 | 7.7714 | 7.5429 | 7.2844 | 7.0373 | 6.7908 | 5.8831 | 5.0565 | 3.8205 | 7.438 | 7.2611 | 6.9868 | 6.7182 | 6.3814 | 5.973 | 5.6547 | 5.3654 | 5.0599 | 4.7727 | 4.4766 | 3.3385 | 2.2472 | 0.88128
|  | CAMPBELTOWN | CT |  |  |  | 7.0678 | 6.9053 | 6.5533 | 6.1934 | 5.8209 | 5.4324 | 5.1142 | 4.8065 | 4.4643 | 4.1361 | 3.8111 | 2.6903 | 1.734 | 1.0057 | 8.9589 | 8.8665 | 8.6791 | 8.4774 | 8.2201 | 7.9483 | 7.7714 | 7.5429 | 7.2844 | 7.0373 | 6.7908 | 5.8831 | 5.0565 | 4.1854 | 7.586 | 7.4468 | 7.1147 | 6.7737 | 6.3814 | 5.973 | 5.6547 | 5.3654 | 5.0599 | 4.7727 | 4.4766 | 3.3385 | 2.2472 | 1.4049
|  | CAMPBELTOWN | LW |  |  |  | 6.9204 | 6.7135 | 6.4251 | 6.1446 | 5.8956 | 5.5714 | 5.2181 | 4.9023 | 4.5596 | 4.2194 | 3.8898 | 2.9099 | 1.7928 | 0.5355 | 8.907 | 8.7964 | 8.662 | 8.5278 | 8.4111 | 8.2405 | 8.0483 | 7.8198 | 7.573 | 7.3314 | 7.0963 | 6.4136 | 5.3059 | 3.8205 | 7.438 | 7.2611 | 6.9868 | 6.7182 | 6.4731 | 6.1733 | 5.8526 | 5.5799 | 5.2842 | 4.9949 | 4.7092 | 3.7299 | 2.4001 | 0.88128
|  | CAMPBELTOWN | ST |  |  |  | 7.1942 | 7.1286 | 6.9613 | 6.8316 | 6.7198 | 6.499 | 6.3605 | 6.084 | 5.8878 | 5.6786 | 5.4256 | 4.0563 | 3.0125 | 1.9295 | 9.0157 | 8.9778 | 8.8195 | 8.6986 | 8.6009 | 8.3707 | 8.2538 | 7.9814 | 7.8145 | 7.643 | 7.4248 | 6.2943 | 5.223 | 4.0625 | 7.7251 | 7.6788 | 7.5097 | 7.3843 | 7.2795 | 7.0461 | 6.9232 | 6.6376 | 6.4546 | 6.2385 | 5.9718 | 4.5517 | 3.3899 | 2.1975
|  | CAMPBELTOWN | FS |  |  |  | 7.2103 | 7.15 | 7.047 | 6.9475 | 6.8528 | 6.7515 | 6.6434 | 6.4808 | 6.3256 | 6.1639 | 5.989 | 4.9739 | 4.0493 | 3.4713 | 9.0239 | 8.9889 | 8.9195 | 8.8504 | 8.7799 | 8.7035 | 8.6236 | 8.4856 | 8.3606 | 8.228 | 8.0851 | 7.3554 | 6.5632 | 5.7788 | 7.7354 | 7.6926 | 7.6043 | 7.5152 | 7.4282 | 7.3369 | 7.2415 | 7.0838 | 6.9402 | 6.7934 | 6.6351 | 5.6793 | 4.788 | 4.2362
| COUPAR ANGUS | CAPUTH | MINIMUM HEADROOM | NO 09277 40265 | NO | YES | 6.3641 | 6.1124 | 5.7623 | 5.3974 | 4.9839 | 4.4812 | 4.0437 | 3.7905 | 3.5243 | 3.0376 | 2.6788 | 1.7715 | 1.1103 | 0.47129 | 8.6605 | 8.5645 | 8.4009 | 8.2288 | 7.9424 | 7.5909 | 7.4015 | 7.2079 | 6.987 | 6.5654 | 6.311 | 5.5394 | 4.8821 | 4.4581 | 6.8187 | 6.5674 | 6.2245 | 5.8596 | 5.4422 | 4.9135 | 4.4437 | 4.1284 | 3.7934 | 3.2821 | 2.9514 | 2.0875 | 1.3699 | 0.63104
|  | CAPUTH | CT |  |  |  | 6.6013 | 6.42 | 6.0235 | 5.6165 | 5.1268 | 4.5845 | 4.1784 | 3.9248 | 3.66 | 3.1938 | 2.9122 | 1.9199 | 1.1396 | 0.69947 | 8.6805 | 8.568 | 8.4009 | 8.2288 | 7.9424 | 7.5909 | 7.4015 | 7.2079 | 7.0286 | 6.6161 | 6.4044 | 5.6282 | 5.0945 | 4.6223 | 7.025 | 6.8426 | 6.4511 | 6.0374 | 5.5384 | 4.9899 | 4.596 | 4.3009 | 3.9685 | 3.4647 | 3.1361 | 2.1699 | 1.388 | 0.92272
|  | CAPUTH | LW |  |  |  | 6.3641 | 6.1124 | 5.7623 | 5.3974 | 4.9839 | 4.4812 | 4.0437 | 3.7905 | 3.5243 | 3.0376 | 2.6788 | 1.7715 | 1.1103 | 0.47129 | 8.6605 | 8.5645 | 8.4207 | 8.2612 | 8.0412 | 7.7164 | 7.4738 | 7.2485 | 6.987 | 6.5654 | 6.311 | 5.7006 | 5.1404 | 4.4637 | 6.8187 | 6.5674 | 6.2245 | 5.8596 | 5.4422 | 4.9135 | 4.4437 | 4.1284 | 3.7934 | 3.2821 | 2.9514 | 2.0875 | 1.3699 | 0.63104
|  | CAPUTH | ST |  |  |  | 6.7742 | 6.693 | 6.4665 | 6.2728 | 6.0919 | 5.7434 | 5.5474 | 5.2958 | 5.0803 | 4.6497 | 4.3933 | 2.9214 | 2.0308 | 1.3436 | 8.7489 | 8.7129 | 8.5238 | 8.3723 | 8.2416 | 7.8968 | 7.7428 | 7.5308 | 7.3604 | 6.9369 | 6.7143 | 5.5394 | 4.8821 | 4.4581 | 7.1767 | 7.0966 | 6.8451 | 6.6306 | 6.4353 | 6.0426 | 5.8237 | 5.5408 | 5.2992 | 4.8695 | 4.575 | 3.0615 | 2.1529 | 1.4263
|  | CAPUTH | FS |  |  |  | 6.8435 | 6.7851 | 6.659 | 6.5319 | 6.3918 | 6.2283 | 6.0781 | 5.893 | 5.7138 | 5.4025 | 5.1831 | 3.8375 | 2.7013 | 2.1234 | 8.7724 | 8.7461 | 8.6793 | 8.6081 | 8.526 | 8.4096 | 8.3168 | 8.2049 | 8.0958 | 7.8391 | 7.6855 | 6.8739 | 6.1339 | 5.5963 | 7.2357 | 7.1761 | 7.0481 | 6.9151 | 6.7688 | 6.5991 | 6.4384 | 6.2421 | 6.0497 | 5.741 | 5.5056 | 4.0949 | 3.0346 | 2.4781
| ARBROATH | CARNOUSTIE | MINIMUM HEADROOM | NO 55631 35403 | NO | YES | 3.6889 | 2.9631 | 1.8783 | 0.63315 | -0.31162 | -1.3271 | -2.124 | -2.7836 | -3.4642 | -4.1562 | -4.8119 | -6.546 | -8.0079 | -8.8023 | 6.1752 | 5.6662 | 5.0256 | 4.2204 | 3.6501 | 3.0109 | 2.5642 | 2.153 | 1.7189 | 1.2762 | 0.86297 | -0.48541 | -1.5799 | -2.7885 | 5.11 | 4.4596 | 3.5395 | 2.4643 | 1.6469 | 0.71906 | -0.040979 | -0.71565 | -1.421 | -2.1394 | -2.8145 | -4.4216 | -5.5755 | -6.2561
|  | CARNOUSTIE | CT |  |  |  | 4.2372 | 3.6528 | 2.6308 | 1.5519 | 0.62777 | -0.25236 | -0.88923 | -1.6403 | -2.4268 | -3.1962 | -3.9551 | -6.5458 | -8.0079 | -8.8023 | 6.4421 | 5.9766 | 5.3174 | 4.5851 | 3.9524 | 3.3649 | 3.0136 | 2.5768 | 2.0928 | 1.6156 | 1.1407 | -0.48541 | -1.5799 | -2.7885 | 5.5543 | 5.0283 | 4.123 | 3.1513 | 2.3264 | 1.5374 | 0.96884 | 0.26674 | -0.50368 | -1.263 | -2.0021 | -4.3635 | -5.5755 | -6.2561
|  | CARNOUSTIE | LW |  |  |  | 3.6889 | 2.9631 | 1.8783 | 0.63315 | -0.31162 | -1.3271 | -2.124 | -2.7836 | -3.4642 | -4.1562 | -4.8119 | -6.546 | -7.3396 | -7.7975 | 6.1752 | 5.6662 | 5.0256 | 4.2204 | 3.6501 | 3.0109 | 2.5642 | 2.153 | 1.7189 | 1.2762 | 0.86297 | -0.054504 | -0.48214 | -0.9007 | 5.11 | 4.4596 | 3.5395 | 2.4643 | 1.6469 | 0.71906 | -0.040979 | -0.71565 | -1.421 | -2.1394 | -2.8145 | -4.4216 | -5.1207 | -5.6373
|  | CARNOUSTIE | ST |  |  |  | 4.368 | 3.8742 | 3.3438 | 2.768 | 2.2898 | 1.8215 | 1.5959 | 1.3451 | 1.1098 | 0.87033 | 0.58431 | -1.4471 | -2.8808 | -4.5049 | 6.5077 | 6.1091 | 5.668 | 5.1693 | 4.7362 | 4.3015 | 4.0987 | 3.8602 | 3.6356 | 3.3993 | 3.1156 | 1.3748 | 0.18543 | -1.3256 | 5.6706 | 5.2456 | 4.7716 | 4.2484 | 3.8008 | 3.3414 | 3.0958 | 2.8088 | 2.5288 | 2.2334 | 1.8855 | -0.33114 | -1.5999 | -2.9168
|  | CARNOUSTIE | FS |  |  |  | 4.9173 | 4.5112 | 4.068 | 3.6025 | 3.1886 | 2.7854 | 2.5178 | 2.1758 | 1.8032 | 1.4402 | 1.0732 | -1.0873 | -3.0704 | -4.5812 | 6.9823 | 6.646 | 6.2916 | 5.9 | 5.5373 | 5.1794 | 4.9401 | 4.6536 | 4.3316 | 4.0138 | 3.6824 | 1.7932 | -0.28388 | -2.6881 | 6.1431 | 5.794 | 5.4099 | 4.9956 | 4.6174 | 4.2429 | 3.9793 | 3.6479 | 3.284 | 2.9222 | 2.5497 | 0.36429 | -1.5823 | -2.8019
| KILLIN | CASHLIE | MINIMUM HEADROOM | NN 50711 42144 | YES | YES | 0.81131 | 0.79316 | 0.77692 | 0.76027 | 0.7458 | 0.7249 | 0.70366 | 0.69237 | 0.67834 | 0.66713 | 0.65114 | 0.6142 | 0.59248 | 0.57904 | 0.88277 | 0.8748 | 0.86774 | 0.85868 | 0.8504 | 0.84017 | 0.83206 | 0.82468 | 0.81597 | 0.80761 | 0.79787 | 0.77627 | 0.76678 | 0.75953 | 0.84577 | 0.82986 | 0.81565 | 0.80092 | 0.78814 | 0.7684 | 0.75013 | 0.73894 | 0.7253 | 0.71386 | 0.69865 | 0.66433 | 0.64554 | 0.6346
|  | CASHLIE | CT |  |  |  | 0.82337 | 0.81296 | 0.78962 | 0.76598 | 0.74809 | 0.7249 | 0.70831 | 0.6952 | 0.68257 | 0.67176 | 0.65944 | 0.63201 | 0.59258 | 0.58204 | 0.88709 | 0.88125 | 0.87016 | 0.85868 | 0.8504 | 0.84017 | 0.83206 | 0.82468 | 0.81666 | 0.80921 | 0.80159 | 0.78495 | 0.76932 | 0.76351 | 0.85598 | 0.84641 | 0.82566 | 0.80447 | 0.78865 | 0.7684 | 0.75357 | 0.74133 | 0.72897 | 0.71809 | 0.70621 | 0.68026 | 0.64676 | 0.63741
|  | CASHLIE | LW |  |  |  | 0.81131 | 0.79316 | 0.77692 | 0.76027 | 0.7458 | 0.72734 | 0.70366 | 0.69237 | 0.67834 | 0.66713 | 0.65114 | 0.6142 | 0.59248 | 0.58437 | 0.88277 | 0.8748 | 0.86774 | 0.86021 | 0.85363 | 0.84443 | 0.83284 | 0.82508 | 0.81597 | 0.80761 | 0.79787 | 0.77627 | 0.76678 | 0.76391 | 0.84577 | 0.82986 | 0.81565 | 0.80092 | 0.78814 | 0.77145 | 0.75013 | 0.73894 | 0.7253 | 0.71386 | 0.69865 | 0.66433 | 0.64554 | 0.63873
|  | CASHLIE | ST |  |  |  | 0.83219 | 0.82514 | 0.81653 | 0.80869 | 0.79907 | 0.78923 | 0.77808 | 0.76734 | 0.75346 | 0.73863 | 0.72894 | 0.65767 | 0.61559 | 0.59196 | 0.89067 | 0.88768 | 0.88398 | 0.8803 | 0.87586 | 0.8711 | 0.86558 | 0.85983 | 0.8525 | 0.84445 | 0.83779 | 0.79549 | 0.77617 | 0.76665 | 0.86353 | 0.85738 | 0.84989 | 0.8429 | 0.83435 | 0.82556 | 0.81551 | 0.80564 | 0.79291 | 0.77927 | 0.7697 | 0.7025 | 0.6657 | 0.64586
|  | CASHLIE | FS |  |  |  | 0.83789 | 0.83138 | 0.82628 | 0.81582 | 0.81033 | 0.8065 | 0.79503 | 0.78691 | 0.77464 | 0.76032 | 0.75064 | 0.66891 | 0.60765 | 0.57904 | 0.89281 | 0.89014 | 0.88783 | 0.88351 | 0.88085 | 0.87863 | 0.87357 | 0.86949 | 0.86372 | 0.85704 | 0.85175 | 0.81024 | 0.77535 | 0.75953 | 0.86836 | 0.86275 | 0.85822 | 0.84919 | 0.84424 | 0.84061 | 0.83054 | 0.82319 | 0.81224 | 0.79952 | 0.79055 | 0.71649 | 0.65976 | 0.6346
| KILLIN | CHAORACH | MINIMUM HEADROOM | NN 45400 27553 | YES | YES | 0.71794 | 0.70925 | 0.71015 | 0.70388 | 0.70117 | 0.6958 | 0.69094 | 0.68947 | 0.68575 | 0.68336 | 0.68182 | 0.674 | 0.66805 | 0.66805 | 0.80613 | 0.80262 | 0.80254 | 0.79989 | 0.79856 | 0.79593 | 0.79375 | 0.79202 | 0.78946 | 0.78742 | 0.78622 | 0.78163 | 0.77947 | 0.77947 | 0.75468 | 0.74723 | 0.74778 | 0.74234 | 0.73992 | 0.73512 | 0.73086 | 0.72932 | 0.72558 | 0.72292 | 0.72153 | 0.71409 | 0.70908 | 0.70908
|  | CHAORACH | CT |  |  |  | 0.72182 | 0.71327 | 0.71204 | 0.70701 | 0.70229 | 0.69797 | 0.69094 | 0.68947 | 0.68575 | 0.68558 | 0.68182 | 0.67909 | 0.669 | 0.66845 | 0.80751 | 0.80413 | 0.80308 | 0.80071 | 0.79864 | 0.79668 | 0.79375 | 0.79249 | 0.79023 | 0.78916 | 0.78693 | 0.78404 | 0.78028 | 0.77992 | 0.75795 | 0.75066 | 0.74937 | 0.74487 | 0.74076 | 0.73696 | 0.73086 | 0.72932 | 0.72573 | 0.72507 | 0.72153 | 0.71844 | 0.7099 | 0.70931
|  | CHAORACH | LW |  |  |  | 0.71794 | 0.70925 | 0.71015 | 0.70388 | 0.70117 | 0.6958 | 0.69403 | 0.69007 | 0.68592 | 0.68336 | 0.68293 | 0.674 | 0.66805 | 0.66805 | 0.80613 | 0.80262 | 0.80254 | 0.79989 | 0.79856 | 0.79593 | 0.79443 | 0.79202 | 0.78946 | 0.78742 | 0.78622 | 0.78163 | 0.77947 | 0.77947 | 0.75468 | 0.74723 | 0.74778 | 0.74234 | 0.73992 | 0.73512 | 0.73327 | 0.72952 | 0.72558 | 0.72292 | 0.72209 | 0.71409 | 0.70908 | 0.70908
|  | CHAORACH | ST |  |  |  | 0.72216 | 0.71996 | 0.71572 | 0.71345 | 0.71289 | 0.70832 | 0.70747 | 0.70642 | 0.70362 | 0.70378 | 0.69599 | 0.68362 | 0.67572 | 0.67315 | 0.80778 | 0.80688 | 0.80521 | 0.80415 | 0.80369 | 0.80174 | 0.80103 | 0.80014 | 0.79852 | 0.79783 | 0.79426 | 0.78567 | 0.78207 | 0.78112 | 0.75828 | 0.75639 | 0.75277 | 0.75072 | 0.75015 | 0.74619 | 0.74531 | 0.74421 | 0.74161 | 0.7414 | 0.73452 | 0.72241 | 0.7155 | 0.71327
|  | CHAORACH | FS |  |  |  | 0.72222 | 0.722 | 0.71784 | 0.71719 | 0.71485 | 0.71438 | 0.71187 | 0.70775 | 0.70695 | 0.70576 | 0.70282 | 0.68646 | 0.675 | 0.66983 | 0.80782 | 0.80764 | 0.80604 | 0.80562 | 0.8046 | 0.80419 | 0.80303 | 0.80124 | 0.80057 | 0.79968 | 0.79814 | 0.78912 | 0.78231 | 0.77998 | 0.75834 | 0.75811 | 0.75458 | 0.75391 | 0.75188 | 0.75138 | 0.74916 | 0.74557 | 0.74474 | 0.74351 | 0.74083 | 0.72571 | 0.71497 | 0.71058
| ARBROATH | CHARLES AVENUE | MINIMUM HEADROOM | NO 62954 41097 | NO | YES | 3.991 | 3.6927 | 3.025 | 2.3247 | 1.5852 | 0.5961 | -0.52265 | -1.4789 | -2.3532 | -3.1026 | -3.8284 | -5.9455 | -6.6816 | -7.4052 | 5.4395 | 5.251 | 4.9008 | 4.5206 | 4.0812 | 3.4183 | 2.6589 | 1.9791 | 1.3429 | 0.84874 | 0.37415 | -0.8402 | -1.659 | -3.6118 | 5.0783 | 4.7872 | 4.1729 | 3.5216 | 2.8176 | 1.8573 | 0.78454 | -0.14023 | -0.99364 | -1.735 | -2.4492 | -4.4273 | -5.0303 | -5.4322
|  | CHARLES AVENUE | CT |  |  |  | 4.3511 | 4.1986 | 3.6008 | 2.9789 | 2.3728 | 1.6287 | 0.82514 | -0.12428 | -1.0413 | -1.8045 | -2.5643 | -5.2102 | -6.6816 | -7.4052 | 5.5554 | 5.425 | 5.0893 | 4.7282 | 4.363 | 3.8744 | 3.3461 | 2.7127 | 2.0693 | 1.5882 | 1.1067 | -0.55842 | -1.659 | -2.8738 | 5.3835 | 5.2241 | 4.6679 | 4.0826 | 3.5102 | 2.8069 | 2.0636 | 1.1791 | 0.31285 | -0.41385 | -1.1349 | -3.5563 | -4.8138 | -5.4322
|  | CHARLES AVENUE | LW |  |  |  | 3.991 | 3.6927 | 3.025 | 2.3247 | 1.5852 | 0.5961 | -0.52265 | -1.4789 | -2.3532 | -3.1026 | -3.8284 | -5.9455 | -6.6436 | -6.9492 | 5.4395 | 5.251 | 4.9008 | 4.5206 | 4.0812 | 3.4183 | 2.6589 | 1.9791 | 1.3429 | 0.84874 | 0.37415 | -0.8402 | -1.133 | -1.3481 | 5.0783 | 4.7872 | 4.1729 | 3.5216 | 2.8176 | 1.8573 | 0.78454 | -0.14023 | -0.99364 | -1.735 | -2.4492 | -4.4273 | -5.0303 | -5.3408
|  | CHARLES AVENUE | ST |  |  |  | 4.5398 | 4.5106 | 4.42 | 4.3201 | 4.2194 | 3.9232 | 3.5465 | 3.1069 | 2.7074 | 2.4249 | 2.1091 | -0.028859 | -1.4375 | -2.995 | 5.6472 | 5.6025 | 5.4755 | 5.3489 | 5.2237 | 4.9008 | 4.5272 | 4.1087 | 3.6902 | 3.4042 | 3.0855 | 1.218 | 4.295e-05 | -1.5072 | 5.5516 | 5.5144 | 5.3989 | 5.2775 | 5.157 | 4.8317 | 4.4475 | 4.009 | 3.6018 | 3.2961 | 2.9548 | 0.77682 | -0.48995 | -1.8027
|  | CHARLES AVENUE | FS |  |  |  | 4.5171 | 4.4872 | 4.4084 | 4.3135 | 4.2102 | 4.0244 | 3.7221 | 3.3268 | 2.999 | 2.7348 | 2.4529 | 0.47984 | -1.7547 | -3.5136 | 5.6425 | 5.6007 | 5.5196 | 5.4231 | 5.3154 | 5.1325 | 4.84 | 4.4887 | 4.1712 | 3.9178 | 3.6408 | 1.7804 | -0.6796 | -3.6118 | 5.5356 | 5.5004 | 5.4165 | 5.3153 | 5.2046 | 5.015 | 4.7149 | 4.3351 | 4.0151 | 3.7496 | 3.4646 | 1.5094 | -0.62731 | -2.1682
| CHARLESTON | CHARLESTON | MINIMUM HEADROOM | NO 35734 31818 | NO | YES | 8.1987 | 8.0527 | 7.8378 | 7.5964 | 7.2554 | 6.8124 | 6.4025 | 6.0599 | 5.5714 | 5.0676 | 4.4608 | 2.8252 | 1.5816 | 1.0499 | 2.6102 | 2.4965 | 2.3506 | 2.1937 | 1.9437 | 1.6086 | 1.3199 | 1.0205 | 0.60397 | 0.17521 | -0.38047 | -1.6904 | -2.7965 | -3.3746 | 4.2768 | 4.1499 | 3.8945 | 3.6066 | 3.2419 | 2.7894 | 2.3873 | 2.0764 | 1.7354 | 1.3931 | 0.78533 | -0.82875 | -2.111 | -2.7138
|  | CHARLESTON | CT |  |  |  | 8.2254 | 8.0527 | 7.8378 | 7.6153 | 7.3533 | 7.0085 | 6.7281 | 6.3824 | 6.042 | 5.7187 | 5.2383 | 3.8713 | 3.4742 | 3.1728 | 2.6102 | 2.4965 | 2.3506 | 2.1937 | 1.9744 | 1.7199 | 1.5512 | 1.3087 | 1.0322 | 0.76871 | 0.34297 | -0.77631 | -1.1065 | -1.4324 | 4.3213 | 4.154 | 3.9435 | 3.7233 | 3.4229 | 3.0818 | 2.831 | 2.5785 | 2.3117 | 2.0611 | 1.5929 | 0.22568 | -0.1236 | -0.43726
|  | CHARLESTON | LW |  |  |  | 8.1987 | 8.0756 | 7.851 | 7.5964 | 7.2554 | 6.8124 | 6.4025 | 6.0599 | 5.5714 | 5.0676 | 4.4608 | 3.1054 | 2.5237 | 1.8403 | 2.6297 | 2.5337 | 2.3824 | 2.2026 | 1.9437 | 1.6086 | 1.3199 | 1.0205 | 0.60397 | 0.17521 | -0.38047 | -1.5499 | -2.1896 | -2.9851 | 4.2768 | 4.1499 | 3.8945 | 3.6066 | 3.2419 | 2.7894 | 2.3873 | 2.0764 | 1.7354 | 1.3931 | 0.78533 | -0.63112 | -1.3061 | -2.1257
|  | CHARLESTON | ST |  |  |  | 8.2994 | 8.2439 | 8.0988 | 7.955 | 7.8062 | 7.5472 | 7.3328 | 7.0577 | 6.6964 | 6.2781 | 5.6611 | 2.8252 | 1.5816 | 1.0499 | 2.6567 | 2.6174 | 2.4766 | 2.3501 | 2.2319 | 1.9943 | 1.8343 | 1.6228 | 1.4165 | 1.1591 | 0.59138 | -1.6904 | -2.7965 | -3.3746 | 4.3928 | 4.3388 | 4.1777 | 4.0243 | 3.8712 | 3.5891 | 3.3728 | 3.0923 | 2.8001 | 2.465 | 1.9403 | -0.82875 | -2.111 | -2.7138
|  | CHARLESTON | FS |  |  |  | 8.3322 | 8.2915 | 8.2276 | 8.1529 | 8.0631 | 7.9578 | 7.8375 | 7.6958 | 7.5382 | 7.3601 | 7.0568 | 5.3534 | 3.4959 | 2.2814 | 2.6832 | 2.6527 | 2.5985 | 2.5368 | 2.4634 | 2.3794 | 2.2866 | 2.1767 | 2.0591 | 1.9273 | 1.6884 | 0.45082 | -1.0134 | -2.0067 | 4.426 | 4.3863 | 4.3202 | 4.2435 | 4.1515 | 4.0446 | 3.9239 | 3.7816 | 3.6257 | 3.4501 | 3.1746 | 1.7223 | -0.073778 | -1.254
| ARDMORE | CLACHAN | MINIMUM HEADROOM | NF 81863 64360 | YES | YES | 1.0206 | 0.92672 | 0.84222 | 0.73952 | -1.3979 | -3.4991 | -5.2454 | -6.953 | -9.0979 | -11.7055 | -14.3329 | -17.512 | -17.6996 | -17.8467 | 1.6598 | 1.5942 | 1.5477 | 1.4775 | -1.2114 | -4.3779 | -6.952 | -9.5303 | -12.6115 | -15.9808 | -19.3692 | -23.4706 | -23.722 | -23.8628 | 1.0588 | 0.97794 | 0.88632 | 0.79 | -1.6629 | -4.3572 | -6.5753 | -8.8168 | -11.4986 | -14.4242 | -17.3599 | -20.896 | -21.1536 | -21.2702
|  | CLACHAN | CT |  |  |  | 1.0615 | 0.98622 | 0.86752 | 0.73952 | -1.3979 | -3.4369 | -5.0149 | -6.7023 | -9.0979 | -11.7055 | -14.3329 | -17.512 | -17.6914 | -17.774 | 1.6827 | 1.6211 | 1.5511 | 1.4775 | -1.2114 | -4.2561 | -6.5889 | -9.1636 | -12.6115 | -15.9808 | -19.3692 | -23.4538 | -23.6622 | -23.7746 | 1.0764 | 0.98499 | 0.88632 | 0.79 | -1.6629 | -4.2612 | -6.2734 | -8.5041 | -11.4986 | -14.4242 | -17.3599 | -20.896 | -21.1536 | -21.2702
|  | CLACHAN | LW |  |  |  | 1.0206 | 0.92672 | 0.84222 | 0.7546 | -1.3592 | -3.4991 | -5.2454 | -6.953 | -9.0621 | -11.5376 | -14.06 | -17.118 | -17.6321 | -17.7216 | 1.6598 | 1.5942 | 1.5477 | 1.4987 | -1.1709 | -4.3779 | -6.952 | -9.5303 | -12.5891 | -15.777 | -19.0259 | -22.9403 | -23.5907 | -23.702 | 1.0588 | 0.97794 | 0.91595 | 0.85238 | -1.6254 | -4.3572 | -6.5753 | -8.8168 | -11.479 | -14.2477 | -17.067 | -20.4878 | -21.0868 | -21.1982
|  | CLACHAN | ST |  |  |  | 1.091 | 1.0475 | 1.0162 | 0.9781 | -1.0961 | -3.0694 | -4.5952 | -6.2794 | -8.8968 | -11.5166 | -14.1544 | -17.486 | -17.6996 | -17.7861 | 1.699 | 1.6603 | 1.6376 | 1.6111 | -1.1336 | -4.17 | -6.4958 | -9.0622 | -12.508 | -15.8792 | -19.2711 | -23.4706 | -23.722 | -23.8343 | 1.1173 | 1.07 | 1.0368 | 0.99814 | -1.3839 | -3.9234 | -5.8979 | -8.1339 | -11.1316 | -14.0666 | -17.0192 | -20.7724 | -21.0428 | -21.1755
|  | CLACHAN | FS |  |  |  | 1.1183 | 1.082 | 1.0545 | 1.0242 | -0.47934 | -1.7364 | -3.0459 | -4.4671 | -5.9569 | -7.6931 | -9.686 | -14.385 | -17.3821 | -17.8467 | 1.7207 | 1.6889 | 1.6696 | 1.6484 | -0.21172 | -2.1329 | -4.1354 | -6.2991 | -8.5606 | -10.9674 | -13.5359 | -19.5059 | -23.2974 | -23.8628 | 1.1466 | 1.1093 | 1.0812 | 1.051 | -0.59999 | -2.2142 | -3.896 | -5.7283 | -7.7052 | -9.8068 | -12.0421 | -17.3709 | -20.745 | -21.2547
| CARRADALE | CLAONAIG | MINIMUM HEADROOM | NR 86915 56467 | YES | YES | 0.2059 | 0.198 | 0.18616 | 0.17973 | 0.16001 | 0.14058 | 0.12963 | 0.11628 | 0.10123 | 0.092235 | 0.076495 | 0.033049 | -0.008951 | -0.056212 | 0.22776 | 0.22365 | 0.2166 | 0.20741 | 0.19315 | 0.17508 | 0.16734 | 0.15372 | 0.14344 | 0.13281 | 0.12001 | 0.067728 | 0.014107 | -0.039432 | 0.19219 | 0.18496 | 0.17432 | 0.16731 | 0.14551 | 0.12408 | 0.11315 | 0.09912 | 0.08338 | 0.072837 | 0.0564 | 0.0071953 | -0.047262 | -0.10349
|  | CLAONAIG | CT |  |  |  | 0.21014 | 0.2061 | 0.19018 | 0.18017 | 0.16001 | 0.14058 | 0.12963 | 0.11628 | 0.10123 | 0.092235 | 0.076495 | 0.033049 | -0.008951 | -0.041292 | 0.2293 | 0.22676 | 0.21815 | 0.21081 | 0.19315 | 0.17508 | 0.16734 | 0.15609 | 0.14344 | 0.13281 | 0.12001 | 0.075655 | 0.037305 | -0.00077997 | 0.19597 | 0.19216 | 0.17733 | 0.16731 | 0.14551 | 0.12408 | 0.11315 | 0.09912 | 0.08338 | 0.072837 | 0.0564 | 0.0071953 | -0.037648 | -0.075349
|  | CLAONAIG | LW |  |  |  | 0.2059 | 0.198 | 0.18616 | 0.17973 | 0.17207 | 0.16209 | 0.14768 | 0.136 | 0.12897 | 0.11805 | 0.11014 | 0.080691 | 0.028999 | -0.038221 | 0.22776 | 0.22365 | 0.21831 | 0.21476 | 0.21098 | 0.20538 | 0.1978 | 0.18918 | 0.18166 | 0.17274 | 0.16505 | 0.14192 | 0.084748 | 0.00436 | 0.19219 | 0.18496 | 0.17432 | 0.16837 | 0.16141 | 0.15215 | 0.13892 | 0.12727 | 0.11963 | 0.10836 | 0.099393 | 0.069025 | 0.0078943 | -0.074414
|  | CLAONAIG | ST |  |  |  | 0.21276 | 0.2136 | 0.19959 | 0.19156 | 0.18026 | 0.16075 | 0.15404 | 0.13668 | 0.12512 | 0.11618 | 0.10448 | 0.043193 | -0.0070638 | -0.056212 | 0.23057 | 0.23046 | 0.2166 | 0.20741 | 0.1988 | 0.1781 | 0.17096 | 0.15372 | 0.14438 | 0.13624 | 0.12479 | 0.067728 | 0.014107 | -0.039432 | 0.19832 | 0.19897 | 0.18311 | 0.17357 | 0.16194 | 0.1393 | 0.13166 | 0.1121 | 0.10013 | 0.0906 | 0.077524 | 0.010497 | -0.047262 | -0.10349
|  | CLAONAIG | FS |  |  |  | 0.21661 | 0.21227 | 0.2126 | 0.20405 | 0.20035 | 0.18974 | 0.18431 | 0.1796 | 0.16905 | 0.16012 | 0.15416 | 0.1075 | 0.075644 | 0.062932 | 0.23202 | 0.23004 | 0.22806 | 0.22268 | 0.21876 | 0.21218 | 0.20766 | 0.20151 | 0.19415 | 0.18724 | 0.18126 | 0.15098 | 0.1265 | 0.11276 | 0.20171 | 0.19784 | 0.19732 | 0.189 | 0.18479 | 0.17451 | 0.16885 | 0.16304 | 0.15254 | 0.14342 | 0.13687 | 0.092179 | 0.060537 | 0.048324
| CLAYHILLS | CLAYHILLS | MINIMUM HEADROOM | NJ 94047 05518 | NO | NO | 8.5684 | 7.9591 | 6.8661 | 5.6678 | 4.2904 | 2.3889 | 0.35512 | -1.4118 | -3.3523 | -5.3722 | -7.3118 | -12.0038 | -13.0114 | -15.6531 | 12.5499 | 12.1596 | 11.5316 | 10.8087 | 9.9178 | 8.6401 | 7.1434 | 5.792 | 4.3007 | 2.7488 | 1.2654 | -2.2907 | -4.2522 | -14.0087 | 10.7871 | 10.0588 | 8.979 | 7.779 | 6.391 | 4.4848 | 2.4791 | 0.73697 | -1.1782 | -3.1705 | -5.0801 | -9.7009 | -10.7502 | -13.4915
|  | CLAYHILLS | CT |  |  |  | 8.9213 | 8.5642 | 7.444 | 6.1704 | 4.9782 | 3.6983 | 2.5124 | 1.2769 | 0.050229 | -1.1735 | -2.6744 | -7.9297 | -9.7688 | -10.6701 | 12.5519 | 12.2142 | 11.5484 | 10.8087 | 9.9626 | 9.0417 | 8.1926 | 7.1956 | 6.1921 | 5.1769 | 3.918 | -1.024 | -4.2054 | -8.5485 | 11.0659 | 10.6022 | 9.4938 | 8.2635 | 7.0931 | 5.8336 | 4.6984 | 3.4991 | 2.3082 | 1.1208 | -0.3428 | -5.4111 | -7.1281 | -7.9986
|  | CLAYHILLS | LW |  |  |  | 8.5684 | 7.9591 | 6.8661 | 5.6678 | 4.2904 | 2.3889 | 0.35512 | -1.4118 | -3.3523 | -5.3722 | -7.3118 | -12.0038 | -13.0114 | -15.6531 | 12.5499 | 12.1596 | 11.5316 | 10.8331 | 9.9178 | 8.6401 | 7.1434 | 5.792 | 4.3007 | 2.7488 | 1.2654 | -2.2907 | -3.1251 | -5.4298 | 10.7871 | 10.0588 | 8.979 | 7.779 | 6.391 | 4.4848 | 2.4791 | 0.73697 | -1.1782 | -3.1705 | -5.0801 | -9.7009 | -10.7502 | -13.4915
|  | CLAYHILLS | ST |  |  |  | 9.1256 | 9.0307 | 8.7726 | 8.5239 | 8.2548 | 7.6001 | 6.9907 | 6.2891 | 5.4764 | 4.5429 | 3.4911 | -2.5226 | -4.936 | -6.7055 | 12.7719 | 12.6124 | 12.2567 | 11.9091 | 11.5495 | 10.9344 | 10.4289 | 9.8315 | 9.0898 | 8.1855 | 7.1608 | 1.2582 | -2.6238 | -7.3959 | 11.4064 | 11.3038 | 10.9309 | 10.5446 | 10.1277 | 9.4223 | 8.8011 | 8.0915 | 7.2801 | 6.3504 | 5.3007 | -0.60384 | -2.9634 | -4.636
|  | CLAYHILLS | FS |  |  |  | 9.1536 | 9.0813 | 8.964 | 8.8261 | 8.5234 | 8.1437 | 7.6911 | 7.1833 | 6.6101 | 5.9749 | 5.2705 | 0.44423 | -4.2193 | -7.4338 | 12.7576 | 12.5956 | 12.3605 | 12.0879 | 11.7718 | 11.4029 | 10.9862 | 10.518 | 9.9612 | 9.3349 | 8.556 | 2.9689 | -4.2522 | -14.0087 | 11.4328 | 11.3376 | 11.0991 | 10.8164 | 10.4843 | 10.0924 | 9.641 | 9.1403 | 8.5763 | 7.9507 | 7.2563 | 2.5522 | -1.9395 | -4.9629
| MYBSTER | COLDBACKIE | MINIMUM HEADROOM | NC 62182 59590 | YES | YES | 0.19286 | 0.14863 | 0.10143 | 0.053354 | 0.0034722 | -0.05018 | -0.10372 | -0.12854 | -0.15093 | -0.18094 | -0.20375 | -0.27681 | -0.37806 | -0.42853 | 0.32307 | 0.30271 | 0.28263 | 0.26089 | 0.24003 | 0.2131 | 0.18174 | 0.15517 | 0.12769 | 0.097777 | 0.07199 | 0.022416 | -0.017831 | -0.042576 | 0.10975 | 0.076127 | 0.038489 | -0.0021888 | -0.044675 | -0.091753 | -0.14643 | -0.18039 | -0.21102 | -0.24403 | -0.28473 | -0.41792 | -0.51812 | -0.58232
|  | COLDBACKIE | CT |  |  |  | 0.23217 | 0.20158 | 0.14028 | 0.083091 | 0.023452 | -0.030442 | -0.09023 | -0.12089 | -0.1461 | -0.17383 | -0.20071 | -0.27601 | -0.37806 | -0.40631 | 0.3361 | 0.3209 | 0.29258 | 0.26419 | 0.24003 | 0.21735 | 0.19139 | 0.16763 | 0.13887 | 0.10875 | 0.082479 | 0.022416 | -0.017831 | -0.039008 | 0.12384 | 0.091705 | 0.045344 | 0.0021586 | -0.044178 | -0.091125 | -0.14643 | -0.18039 | -0.21102 | -0.24403 | -0.28473 | -0.40181 | -0.46364 | -0.48075
|  | COLDBACKIE | LW |  |  |  | 0.19286 | 0.14863 | 0.10143 | 0.053354 | 0.0034722 | -0.05018 | -0.10372 | -0.12854 | -0.15093 | -0.18094 | -0.20375 | -0.27681 | -0.32514 | -0.33891 | 0.32307 | 0.30271 | 0.28263 | 0.26089 | 0.24095 | 0.2131 | 0.18174 | 0.15517 | 0.12769 | 0.097777 | 0.07199 | 0.026629 | 0.010263 | 0.0061137 | 0.10975 | 0.076127 | 0.038489 | -0.0021888 | -0.044675 | -0.091753 | -0.13876 | -0.16288 | -0.19541 | -0.23308 | -0.26419 | -0.3324 | -0.36732 | -0.37678
|  | COLDBACKIE | ST |  |  |  | 0.2555 | 0.2305 | 0.20441 | 0.17959 | 0.15167 | 0.12301 | 0.093201 | 0.056239 | 0.024228 | -0.013353 | -0.054541 | -0.23713 | -0.34159 | -0.40118 | 0.34421 | 0.33451 | 0.32384 | 0.31238 | 0.29959 | 0.28588 | 0.27061 | 0.25186 | 0.23117 | 0.20655 | 0.17932 | 0.044783 | -0.0042551 | -0.028345 | 0.14616 | 0.12782 | 0.1072 | 0.085794 | 0.060839 | 0.032742 | 0.00198 | -0.03435 | -0.07298 | -0.1176 | -0.16713 | -0.41792 | -0.51812 | -0.56236
|  | COLDBACKIE | FS |  |  |  | 0.27565 | 0.25907 | 0.23943 | 0.21377 | 0.19168 | 0.16677 | 0.14276 | 0.11021 | 0.082257 | 0.047711 | 0.011885 | -0.21931 | -0.35657 | -0.42853 | 0.35154 | 0.34444 | 0.33609 | 0.32539 | 0.31553 | 0.30425 | 0.29232 | 0.27694 | 0.26194 | 0.24414 | 0.22351 | 0.090428 | -0.0080139 | -0.042576 | 0.15969 | 0.14737 | 0.13127 | 0.11123 | 0.092201 | 0.070249 | 0.046884 | 0.017922 | -0.010566 | -0.043811 | -0.080012 | -0.31257 | -0.48196 | -0.58232
| DUNOON | COLINTRAIVE | MINIMUM HEADROOM | NS 03209 74814 | YES | YES | 0.45739 | 0.45068 | 0.44089 | 0.43237 | 0.42601 | 0.41608 | 0.40487 | 0.39612 | 0.38868 | 0.38049 | 0.37276 | 0.35598 | 0.34811 | 0.34117 | 0.4623 | 0.45852 | 0.45384 | 0.44896 | 0.44539 | 0.4403 | 0.43332 | 0.42655 | 0.4199 | 0.41314 | 0.40694 | 0.3969 | 0.39094 | 0.38524 | 0.44356 | 0.43734 | 0.42846 | 0.42064 | 0.4148 | 0.40553 | 0.39499 | 0.38574 | 0.37741 | 0.36927 | 0.36162 | 0.34583 | 0.33886 | 0.3326
|  | COLINTRAIVE | CT |  |  |  | 0.45984 | 0.45558 | 0.44596 | 0.43432 | 0.42796 | 0.4193 | 0.41098 | 0.40578 | 0.39666 | 0.38543 | 0.37985 | 0.35935 | 0.34811 | 0.34117 | 0.46323 | 0.46056 | 0.45519 | 0.44896 | 0.44539 | 0.44092 | 0.43644 | 0.43178 | 0.42451 | 0.41655 | 0.41119 | 0.39715 | 0.39094 | 0.38524 | 0.44575 | 0.44174 | 0.43283 | 0.42212 | 0.41623 | 0.40832 | 0.4007 | 0.39503 | 0.3853 | 0.37418 | 0.36847 | 0.34894 | 0.33886 | 0.3326
|  | COLINTRAIVE | LW |  |  |  | 0.45739 | 0.45068 | 0.44089 | 0.43237 | 0.42601 | 0.41608 | 0.40487 | 0.39612 | 0.38868 | 0.38049 | 0.37276 | 0.35598 | 0.34978 | 0.34807 | 0.4623 | 0.45852 | 0.45384 | 0.4494 | 0.44605 | 0.4403 | 0.43332 | 0.42655 | 0.4199 | 0.41314 | 0.40694 | 0.3969 | 0.39452 | 0.39389 | 0.44356 | 0.43734 | 0.42846 | 0.42064 | 0.4148 | 0.40553 | 0.39499 | 0.38574 | 0.37741 | 0.36927 | 0.36162 | 0.34583 | 0.34032 | 0.33882
|  | COLINTRAIVE | ST |  |  |  | 0.46582 | 0.46133 | 0.45691 | 0.45502 | 0.4533 | 0.44898 | 0.44236 | 0.43767 | 0.43191 | 0.42549 | 0.41827 | 0.37766 | 0.36809 | 0.36037 | 0.4659 | 0.46369 | 0.46152 | 0.46008 | 0.45863 | 0.45596 | 0.45223 | 0.44865 | 0.44427 | 0.43934 | 0.4339 | 0.4051 | 0.39832 | 0.39332 | 0.4514 | 0.44705 | 0.44304 | 0.44121 | 0.43949 | 0.43546 | 0.42928 | 0.42445 | 0.41847 | 0.41181 | 0.40458 | 0.36549 | 0.35655 | 0.34977
|  | COLINTRAIVE | FS |  |  |  | 0.46737 | 0.46196 | 0.46073 | 0.45735 | 0.45423 | 0.44909 | 0.44879 | 0.44103 | 0.43628 | 0.43337 | 0.42608 | 0.38633 | 0.36091 | 0.35493 | 0.46669 | 0.46402 | 0.46312 | 0.46129 | 0.45953 | 0.45689 | 0.45585 | 0.452 | 0.44886 | 0.44604 | 0.44165 | 0.41575 | 0.39576 | 0.38993 | 0.45284 | 0.44763 | 0.44645 | 0.44335 | 0.44047 | 0.43578 | 0.43531 | 0.42824 | 0.42362 | 0.42033 | 0.41333 | 0.37495 | 0.35032 | 0.345
| STORNOWAY | COLL | MINIMUM HEADROOM | NB 47510 40182 | YES | YES | 1.703 | 1.592 | 1.4553 | 1.3123 | 1.1584 | 0.98474 | 0.81588 | 0.67593 | 0.51856 | 0.35156 | 0.20365 | -0.14524 | -0.59775 | -1.15 | 2.2973 | 2.2354 | 2.1675 | 2.0747 | 1.9919 | 1.9047 | 1.8017 | 1.6685 | 1.5289 | 1.389 | 1.2592 | 0.94291 | 0.4519 | -0.21001 | 2.3221 | 2.2327 | 2.1086 | 1.9768 | 1.8295 | 1.6737 | 1.5059 | 1.3461 | 1.1818 | 1.0113 | 0.8579 | 0.48388 | -0.04925 | -0.72669
|  | COLL | CT |  |  |  | 1.7841 | 1.7071 | 1.5214 | 1.3238 | 1.1584 | 0.98474 | 0.81806 | 0.7198 | 0.58667 | 0.4361 | 0.30418 | -0.0059143 | -0.35997 | -0.6368 | 2.3278 | 2.282 | 2.1839 | 2.0747 | 1.9919 | 1.9047 | 1.8198 | 1.7216 | 1.5924 | 1.4633 | 1.3479 | 1.0315 | 0.70922 | 0.36846 | 2.3809 | 2.3327 | 2.1613 | 1.9779 | 1.8295 | 1.6737 | 1.5235 | 1.4095 | 1.257 | 1.1031 | 0.96736 | 0.63153 | 0.25376 | -0.067715
|  | COLL | LW |  |  |  | 1.703 | 1.592 | 1.4553 | 1.3123 | 1.1772 | 1.0021 | 0.81588 | 0.67593 | 0.51856 | 0.35156 | 0.20365 | -0.14524 | -0.59775 | -1.15 | 2.2973 | 2.2354 | 2.1675 | 2.0918 | 2.0236 | 1.9187 | 1.8017 | 1.6685 | 1.5289 | 1.389 | 1.2592 | 0.94291 | 0.4519 | -0.21001 | 2.3221 | 2.2327 | 2.1086 | 1.9768 | 1.8546 | 1.6871 | 1.5059 | 1.3461 | 1.1818 | 1.0113 | 0.8579 | 0.48388 | -0.04925 | -0.72669
|  | COLL | ST |  |  |  | 1.8338 | 1.7977 | 1.7447 | 1.688 | 1.6251 | 1.5563 | 1.4824 | 1.3527 | 1.2318 | 1.1009 | 0.95194 | 0.22385 | -0.2386 | -0.62798 | 2.3509 | 2.3304 | 2.3018 | 2.2686 | 2.2309 | 2.1856 | 2.1341 | 2.0182 | 1.9247 | 1.8258 | 1.7088 | 1.124 | 0.65693 | 0.20211 | 2.4155 | 2.392 | 2.3577 | 2.3124 | 2.2521 | 2.1847 | 2.1107 | 1.9691 | 1.8457 | 1.7159 | 1.5663 | 0.8336 | 0.3202 | -0.13172
|  | COLL | FS |  |  |  | 1.8576 | 1.8298 | 1.7815 | 1.7301 | 1.6776 | 1.6207 | 1.5609 | 1.4703 | 1.3795 | 1.2842 | 1.1802 | 0.5287 | 0.069229 | -0.06777 | 2.3604 | 2.3438 | 2.3186 | 2.2901 | 2.2604 | 2.2257 | 2.1865 | 2.1189 | 2.0524 | 1.9808 | 1.9038 | 1.4666 | 1.1033 | 0.9384 | 2.4299 | 2.4152 | 2.3826 | 2.3501 | 2.3017 | 2.2472 | 2.1888 | 2.0964 | 2.0043 | 1.9067 | 1.8027 | 1.1812 | 0.73402 | 0.59862
| CLAYHILLS | COMMERCE STREET | MINIMUM HEADROOM | NJ 94816 06282 | NO | NO | 9.2425 | 8.9309 | 8.5906 | 8.2447 | 7.9707 | 7.658 | 7.3098 | 6.7458 | 6.2619 | 5.7212 | 4.8704 | 1.896 | 0.087803 | -0.43054 | 11.1473 | 10.9105 | 10.6525 | 10.3913 | 10.1809 | 9.9053 | 9.4426 | 8.9306 | 8.4944 | 8.0644 | 7.3869 | 4.9885 | 3.4529 | 2.8972 | 9.6827 | 9.4209 | 9.1087 | 8.7934 | 8.5387 | 8.1004 | 7.5202 | 6.8895 | 6.352 | 5.8218 | 4.9904 | 2.0902 | 0.27198 | -0.31003
|  | COMMERCE STREET | CT |  |  |  | 9.2425 | 8.9309 | 8.5906 | 8.2447 | 7.9707 | 7.658 | 7.3098 | 6.7458 | 6.2619 | 5.7212 | 5.0533 | 2.9655 | 2.5801 | 2.2554 | 11.1473 | 10.9105 | 10.6525 | 10.3913 | 10.1809 | 9.9053 | 9.4426 | 8.9306 | 8.4944 | 8.0644 | 7.537 | 5.8639 | 5.478 | 5.1147 | 9.6827 | 9.4209 | 9.1087 | 8.7934 | 8.5387 | 8.1004 | 7.5202 | 6.8895 | 6.352 | 5.8218 | 5.173 | 3.1325 | 2.7138 | 2.344
|  | COMMERCE STREET | LW |  |  |  | 9.2836 | 9.1022 | 8.9537 | 8.7802 | 8.5948 | 8.2852 | 7.9126 | 7.4637 | 6.7089 | 5.7861 | 4.8704 | 2.35 | 1.5419 | 0.92275 | 11.1892 | 11.0532 | 10.9422 | 10.8122 | 10.6729 | 10.4346 | 10.1479 | 9.5559 | 8.852 | 8.1073 | 7.3869 | 5.3799 | 4.5887 | 3.8663 | 9.7116 | 9.5539 | 9.4065 | 9.2388 | 9.0593 | 8.7757 | 8.4352 | 7.6693 | 6.8012 | 5.8806 | 4.9904 | 2.5213 | 1.6389 | 0.89512
|  | COMMERCE STREET | ST |  |  |  | 9.3508 | 9.2846 | 9.1954 | 9.0803 | 8.9341 | 8.7488 | 8.5182 | 8.1922 | 7.8273 | 7.4024 | 6.6123 | 1.896 | 0.087803 | -0.43054 | 11.2349 | 11.1841 | 11.116 | 11.0278 | 10.9155 | 10.7688 | 10.5869 | 10.3105 | 10.0172 | 9.4699 | 8.7626 | 4.9885 | 3.4529 | 2.8972 | 9.8309 | 9.7939 | 9.74 | 9.6625 | 9.5615 | 9.4246 | 9.2019 | 8.8747 | 8.3644 | 7.6174 | 6.7458 | 2.0902 | 0.27198 | -0.31003
|  | COMMERCE STREET | FS |  |  |  | 9.3786 | 9.3341 | 9.2743 | 9.2009 | 9.1118 | 9.0034 | 8.8733 | 8.7056 | 8.5157 | 8.2989 | 8.0501 | 5.5778 | 2.2442 | 0.0036947 | 11.2532 | 11.2175 | 11.1706 | 11.1125 | 11.042 | 10.9554 | 10.8496 | 10.7052 | 10.545 | 10.3627 | 10.1544 | 7.9059 | 5.296 | 3.5043 | 9.8369 | 9.813 | 9.7714 | 9.7187 | 9.6525 | 9.571 | 9.4688 | 9.337 | 9.1884 | 8.9797 | 8.703 | 5.681 | 2.4618 | 0.29243
| ST FILLANS | COMRIE | MINIMUM HEADROOM | NN 76887 22417 | YES | NO | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535
|  | COMRIE | CT |  |  |  | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535
|  | COMRIE | LW |  |  |  | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535
|  | COMRIE | ST |  |  |  | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535
|  | COMRIE | FS |  |  |  | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.042141 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.040629 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535 | 0.038535
| TAYNUILT | CONNEL | MINIMUM HEADROOM | NM 91213 33970 | YES | YES | -0.81847 | -0.87959 | -0.95316 | -1.047 | -1.1616 | -1.2797 | -1.3796 | -1.444 | -1.5289 | -1.6111 | -1.6901 | -1.8822 | -2.0254 | -2.1811 | -0.13948 | -0.17616 | -0.21801 | -0.28545 | -0.36976 | -0.45761 | -0.52025 | -0.57246 | -0.6375 | -0.70028 | -0.76181 | -0.94839 | -1.0925 | -1.2575 | -0.47278 | -0.51177 | -0.56597 | -0.6307 | -0.74246 | -0.8704 | -0.9752 | -1.0405 | -1.1249 | -1.206 | -1.2851 | -1.4863 | -1.6509 | -1.822
|  | CONNEL | CT |  |  |  | -0.78713 | -0.83368 | -0.93516 | -1.047 | -1.1616 | -1.2797 | -1.3796 | -1.444 | -1.5289 | -1.6111 | -1.6901 | -1.8822 | -2.0254 | -2.1221 | -0.12489 | -0.15415 | -0.21596 | -0.28545 | -0.36976 | -0.45761 | -0.52025 | -0.57246 | -0.6375 | -0.70028 | -0.76181 | -0.94839 | -1.0841 | -1.2208 | -0.44407 | -0.47577 | -0.5514 | -0.6307 | -0.74246 | -0.8704 | -0.9752 | -1.0405 | -1.1249 | -1.206 | -1.2851 | -1.4863 | -1.6509 | -1.7673
|  | CONNEL | LW |  |  |  | -0.81847 | -0.87959 | -0.95316 | -1.0322 | -1.1092 | -1.2116 | -1.3228 | -1.4023 | -1.4887 | -1.5767 | -1.6606 | -1.8227 | -1.9746 | -2.1811 | -0.13948 | -0.17616 | -0.21801 | -0.26348 | -0.30724 | -0.36828 | -0.4354 | -0.49208 | -0.55367 | -0.61582 | -0.67766 | -0.81299 | -0.97363 | -1.2087 | -0.47278 | -0.51177 | -0.56597 | -0.62131 | -0.68104 | -0.78327 | -0.89424 | -0.97143 | -1.0555 | -1.1408 | -1.2225 | -1.3895 | -1.5743 | -1.822
|  | CONNEL | ST |  |  |  | -0.75016 | -0.77509 | -0.82605 | -0.87908 | -0.92624 | -1.0033 | -1.0585 | -1.1352 | -1.2017 | -1.2754 | -1.3541 | -1.7465 | -1.9232 | -2.0543 | -0.10166 | -0.11688 | -0.16391 | -0.20686 | -0.24322 | -0.31545 | -0.35734 | -0.42394 | -0.47331 | -0.5264 | -0.587 | -0.90586 | -1.0925 | -1.2575 | -0.40729 | -0.4246 | -0.47275 | -0.51802 | -0.55486 | -0.62534 | -0.66549 | -0.72772 | -0.79437 | -0.86873 | -0.94885 | -1.3516 | -1.5576 | -1.7187
|  | CONNEL | FS |  |  |  | -0.7378 | -0.75839 | -0.78904 | -0.8242 | -0.8615 | -0.90183 | -0.94167 | -0.99086 | -1.0378 | -1.0922 | -1.1462 | -1.4762 | -1.7171 | -1.7879 | -0.094815 | -0.1078 | -0.12967 | -0.1544 | -0.18114 | -0.21004 | -0.23861 | -0.27634 | -0.31137 | -0.35088 | -0.39107 | -0.6156 | -0.8089 | -0.9167 | -0.39502 | -0.40922 | -0.43382 | -0.46067 | -0.48934 | -0.51905 | -0.54688 | -0.58446 | -0.61639 | -0.66659 | -0.7218 | -1.0527 | -1.2904 | -1.3668
| BEAULY | CONON BRIDGE | MINIMUM HEADROOM | NH 54996 55499 | NO | YES | 1.6652 | 1.2045 | 0.91206 | 0.53404 | 0.26597 | -0.070881 | -0.55876 | -0.85023 | -1.1647 | -1.4749 | -1.7655 | -2.4427 | -2.9185 | -3.1793 | 3.2218 | 2.9735 | 2.8274 | 2.6349 | 2.5012 | 2.3028 | 2.0267 | 1.8126 | 1.5808 | 1.348 | 1.133 | 0.68773 | 0.32091 | -0.036446 | 2.9635 | 2.5855 | 2.3277 | 2.0003 | 1.761 | 1.443 | 1.0002 | 0.70193 | 0.37979 | 0.059175 | -0.23942 | -0.87711 | -1.2503 | -1.4736
|  | CONON BRIDGE | CT |  |  |  | 1.8516 | 1.4829 | 1.1589 | 0.75205 | 0.46976 | 0.16181 | -0.2708 | -0.56124 | -0.90209 | -1.2338 | -1.5347 | -2.3358 | -2.9185 | -3.1793 | 3.2883 | 3.0798 | 2.8929 | 2.6614 | 2.5112 | 2.3466 | 2.1275 | 1.937 | 1.695 | 1.4544 | 1.24 | 0.68773 | 0.32091 | -0.032984 | 3.1173 | 2.8166 | 2.5174 | 2.151 | 1.8974 | 1.6231 | 1.2529 | 0.97371 | 0.63377 | 0.29877 | -0.001081 | -0.76138 | -1.2503 | -1.4736
|  | CONON BRIDGE | LW |  |  |  | 1.6652 | 1.2045 | 0.91206 | 0.53404 | 0.26597 | -0.070881 | -0.55876 | -0.85023 | -1.1647 | -1.4749 | -1.7655 | -2.4427 | -2.7692 | -2.882 | 3.2218 | 2.9735 | 2.8274 | 2.6349 | 2.5012 | 2.3028 | 2.0267 | 1.8126 | 1.5808 | 1.348 | 1.133 | 0.72849 | 0.59465 | 0.54043 | 2.9635 | 2.5855 | 2.3277 | 2.0003 | 1.761 | 1.443 | 1.0002 | 0.70193 | 0.37979 | 0.059175 | -0.23942 | -0.87711 | -1.1493 | -1.2464
|  | CONON BRIDGE | ST |  |  |  | 1.918 | 1.6231 | 1.5231 | 1.3546 | 1.2412 | 1.1 | 0.88 | 0.71098 | 0.52001 | 0.32234 | 0.11556 | -1.0375 | -1.5669 | -2.0088 | 3.3217 | 3.1661 | 3.106 | 3.0067 | 2.9318 | 2.837 | 2.6968 | 2.5743 | 2.4311 | 2.2764 | 2.1081 | 1.1892 | 0.79292 | 0.3977 | 3.1762 | 2.9496 | 2.8592 | 2.714 | 2.6066 | 2.4745 | 2.2795 | 2.1139 | 1.9236 | 1.7214 | 1.5067 | 0.32753 | -0.14205 | -0.50081
|  | CONON BRIDGE | FS |  |  |  | 1.9825 | 1.7456 | 1.6423 | 1.4921 | 1.3826 | 1.268 | 1.0972 | 0.94576 | 0.78742 | 0.61848 | 0.44149 | -0.70268 | -1.6345 | -2.0868 | 3.3478 | 3.2158 | 3.1558 | 3.0673 | 2.9987 | 2.9231 | 2.8145 | 2.7131 | 2.6024 | 2.4804 | 2.3485 | 1.4907 | 0.62512 | -0.036446 | 3.2287 | 3.0496 | 2.96 | 2.8335 | 2.7349 | 2.6296 | 2.4807 | 2.3389 | 2.1878 | 2.0252 | 1.8524 | 0.7317 | -0.19118 | -0.57004
| GRUDIE BRIDGE | CONON FALLS | MINIMUM HEADROOM | NH 38745 57593 | YES | YES | 0.21603 | 0.20083 | 0.19195 | 0.17489 | 0.16085 | 0.14681 | 0.13083 | 0.12371 | 0.10872 | 0.096919 | 0.087893 | 0.064125 | 0.053219 | 0.045105 | 0.264 | 0.25666 | 0.25172 | 0.2438 | 0.23725 | 0.22889 | 0.21916 | 0.21173 | 0.20143 | 0.19208 | 0.18421 | 0.16989 | 0.16375 | 0.15786 | 0.19595 | 0.18227 | 0.17395 | 0.15871 | 0.14622 | 0.13284 | 0.11762 | 0.11001 | 0.095799 | 0.084353 | 0.075448 | 0.053337 | 0.043854 | 0.036578
|  | CONON FALLS | CT |  |  |  | 0.22366 | 0.21359 | 0.1988 | 0.18232 | 0.16691 | 0.15043 | 0.13707 | 0.12718 | 0.11823 | 0.10366 | 0.094989 | 0.07608 | 0.053219 | 0.045105 | 0.26687 | 0.26146 | 0.25335 | 0.24451 | 0.23725 | 0.22962 | 0.22294 | 0.21574 | 0.20752 | 0.19735 | 0.18983 | 0.17401 | 0.16375 | 0.15786 | 0.20293 | 0.19332 | 0.17961 | 0.16439 | 0.15057 | 0.13589 | 0.12378 | 0.11388 | 0.10484 | 0.091012 | 0.082496 | 0.064124 | 0.043854 | 0.036578
|  | CONON FALLS | LW |  |  |  | 0.21603 | 0.20083 | 0.19195 | 0.17489 | 0.16085 | 0.14681 | 0.13083 | 0.12371 | 0.10872 | 0.096919 | 0.087893 | 0.064125 | 0.054905 | 0.051116 | 0.264 | 0.25666 | 0.25172 | 0.2438 | 0.23737 | 0.22889 | 0.21916 | 0.21173 | 0.20143 | 0.19208 | 0.18421 | 0.16989 | 0.16622 | 0.16491 | 0.19595 | 0.18227 | 0.17395 | 0.15871 | 0.14622 | 0.13284 | 0.11762 | 0.11001 | 0.095799 | 0.084353 | 0.075448 | 0.053337 | 0.04519 | 0.041888
|  | CONON FALLS | ST |  |  |  | 0.22486 | 0.22408 | 0.21661 | 0.21297 | 0.20701 | 0.19996 | 0.19144 | 0.18168 | 0.17454 | 0.16475 | 0.15272 | 0.10249 | 0.078061 | 0.064211 | 0.2691 | 0.26666 | 0.26325 | 0.26073 | 0.25735 | 0.25321 | 0.24828 | 0.24246 | 0.237 | 0.2302 | 0.22225 | 0.18501 | 0.17213 | 0.1651 | 0.20738 | 0.20275 | 0.1961 | 0.1925 | 0.18696 | 0.18029 | 0.17232 | 0.16319 | 0.15632 | 0.14704 | 0.13571 | 0.087675 | 0.065603 | 0.053461
|  | CONON FALLS | FS |  |  |  | 0.22505 | 0.2245 | 0.22265 | 0.21901 | 0.21017 | 0.20805 | 0.20142 | 0.19148 | 0.18601 | 0.17964 | 0.16832 | 0.10872 | 0.069025 | 0.057336 | 0.26976 | 0.26825 | 0.26561 | 0.26338 | 0.25944 | 0.25742 | 0.25366 | 0.2486 | 0.24471 | 0.24028 | 0.23395 | 0.19761 | 0.16956 | 0.16156 | 0.20885 | 0.20632 | 0.20132 | 0.19784 | 0.19004 | 0.18773 | 0.18151 | 0.17247 | 0.16718 | 0.16115 | 0.15074 | 0.095341 | 0.05787 | 0.047418
| DUDHOPE | CONSTABLE STREET | MINIMUM HEADROOM | NO 40903 30821 | NO | NO | 15.4041 | 14.9085 | 13.9477 | 12.9701 | 11.7511 | 10.2734 | 8.904 | 7.9738 | 6.9616 | 5.9222 | 4.9275 | 2.3758 | 1.5949 | 0.35106 | 18.3464 | 18.1404 | 17.5091 | 16.8259 | 15.8388 | 14.6534 | 13.6637 | 13.0274 | 12.2775 | 11.5051 | 10.7645 | 8.8451 | 7.3488 | -0.12837 | 16.9928 | 16.4793 | 15.5114 | 14.5343 | 13.2545 | 11.736 | 10.3931 | 9.5433 | 8.621 | 7.6779 | 6.7716 | 4.3851 | 3.5462 | 2.2321
|  | CONSTABLE STREET | CT |  |  |  | 15.6317 | 15.3358 | 14.5939 | 13.7139 | 12.7335 | 11.6808 | 10.8194 | 10.104 | 9.3525 | 8.6073 | 7.7945 | 4.9808 | 3.6647 | 2.9552 | 18.3464 | 18.1404 | 17.6936 | 17.105 | 16.3311 | 15.4927 | 14.8905 | 14.3565 | 13.7881 | 13.2119 | 12.544 | 9.727 | 7.3596 | 3.9247 | 17.0275 | 16.7764 | 16.153 | 15.3309 | 14.3467 | 13.2934 | 12.4835 | 11.8331 | 11.1528 | 10.4789 | 9.7443 | 7.1653 | 5.8915 | 5.1729
|  | CONSTABLE STREET | LW |  |  |  | 15.4041 | 14.9085 | 13.9477 | 12.9701 | 11.7511 | 10.2734 | 8.904 | 7.9738 | 6.9616 | 5.9222 | 4.9275 | 2.3758 | 1.5949 | 0.35106 | 18.3642 | 18.1702 | 17.5091 | 16.8259 | 15.8388 | 14.6534 | 13.6637 | 13.0274 | 12.2775 | 11.5051 | 10.7645 | 8.8451 | 8.1449 | 6.9471 | 16.9928 | 16.4793 | 15.5114 | 14.5343 | 13.2545 | 11.736 | 10.3931 | 9.5433 | 8.621 | 7.6779 | 6.7716 | 4.3851 | 3.5462 | 2.2321
|  | CONSTABLE STREET | ST |  |  |  | 15.8663 | 15.7371 | 15.4546 | 15.2722 | 15.1219 | 14.6162 | 14.2652 | 13.9219 | 13.5359 | 13.0962 | 12.5936 | 9.5446 | 8.1803 | 6.7994 | 18.4322 | 18.3263 | 17.9613 | 17.6913 | 17.4636 | 16.7869 | 16.3853 | 16.0171 | 15.622 | 15.1765 | 14.6464 | 11.3249 | 8.6691 | 4.9933 | 17.0931 | 16.9582 | 16.5803 | 16.3082 | 16.0779 | 15.5025 | 15.217 | 14.9739 | 14.724 | 14.4421 | 14.1139 | 11.3343 | 9.9776 | 8.6551
|  | CONSTABLE STREET | FS |  |  |  | 15.8752 | 15.7658 | 15.6418 | 15.5447 | 15.4284 | 15.2305 | 14.9643 | 14.6963 | 14.3969 | 14.0668 | 13.7088 | 11.181 | 8.5796 | 6.6665 | 18.4414 | 18.3398 | 18.1978 | 18.0608 | 17.8201 | 17.51 | 17.1762 | 16.8447 | 16.4726 | 16.0539 | 15.5853 | 12.2384 | 7.3488 | -0.12837 | 17.1243 | 17.0036 | 16.8646 | 16.7453 | 16.6034 | 16.45 | 16.2938 | 16.1614 | 15.9673 | 15.6746 | 15.3556 | 13.0898 | 10.7224 | 8.9323
| ALNESS | CONTULLICH | MINIMUM HEADROOM | NN 59226 32752 | YES | YES | 0.094789 | 0.094789 | 0.082968 | 0.074977 | 0.069697 | 0.051551 | 0.046504 | 0.032856 | 0.028016 | 0.023918 | 0.017369 | -0.013334 | -0.058397 | -0.10465 | 0.092935 | 0.092935 | 0.078159 | 0.068169 | 0.061569 | 0.038888 | 0.032579 | 0.015518 | 0.0094684 | 0.0043459 | -0.0038398 | -0.042218 | -0.098548 | -0.15636 | 0.089613 | 0.089613 | 0.074838 | 0.064848 | 0.058248 | 0.035566 | 0.029257 | 0.012197 | 0.0061469 | 0.0010245 | -0.0071612 | -0.04554 | -0.10187 | -0.15968
|  | CONTULLICH | CT |  |  |  | 0.094789 | 0.094789 | 0.093249 | 0.090516 | 0.077376 | 0.063363 | 0.059809 | 0.053604 | 0.047378 | 0.041993 | 0.036074 | 0.0046508 | -0.024991 | -0.056989 | 0.092935 | 0.092935 | 0.09101 | 0.087594 | 0.071168 | 0.053652 | 0.04921 | 0.041454 | 0.033671 | 0.02694 | 0.019542 | -0.019738 | -0.05679 | -0.096787 | 0.089613 | 0.089613 | 0.087689 | 0.084272 | 0.067847 | 0.050331 | 0.045889 | 0.038133 | 0.03035 | 0.023618 | 0.01622 | -0.023059 | -0.060111 | -0.10011
|  | CONTULLICH | LW |  |  |  | 0.094789 | 0.094789 | 0.094789 | 0.094789 | 0.094789 | 0.094789 | 0.094789 | 0.092362 | 0.089845 | 0.087775 | 0.085443 | 0.073185 | 0.018166 | -0.062452 | 0.092935 | 0.092935 | 0.092935 | 0.092935 | 0.092935 | 0.092935 | 0.092935 | 0.089901 | 0.086755 | 0.084167 | 0.081252 | 0.06593 | -0.0028434 | -0.10362 | 0.089613 | 0.089613 | 0.089613 | 0.089613 | 0.089613 | 0.089613 | 0.089613 | 0.08658 | 0.083434 | 0.080846 | 0.077931 | 0.062608 | -0.0061648 | -0.10694
|  | CONTULLICH | ST |  |  |  | 0.094789 | 0.094789 | 0.082968 | 0.074977 | 0.069697 | 0.051551 | 0.046504 | 0.032856 | 0.028016 | 0.023918 | 0.017369 | -0.013334 | -0.058397 | -0.10465 | 0.092935 | 0.092935 | 0.078159 | 0.068169 | 0.061569 | 0.038888 | 0.032579 | 0.015518 | 0.0094684 | 0.0043459 | -0.0038398 | -0.042218 | -0.098548 | -0.15636 | 0.089613 | 0.089613 | 0.074838 | 0.064848 | 0.058248 | 0.035566 | 0.029257 | 0.012197 | 0.0061469 | 0.0010245 | -0.0071612 | -0.04554 | -0.10187 | -0.15968
|  | CONTULLICH | FS |  |  |  | 0.094789 | 0.094789 | 0.092372 | 0.089954 | 0.087137 | 0.08432 | 0.081903 | 0.076963 | 0.073613 | 0.070262 | 0.066912 | 0.062852 | 0.060036 | 0.054868 | 0.092935 | 0.092935 | 0.089913 | 0.086892 | 0.08337 | 0.079849 | 0.076828 | 0.070653 | 0.066465 | 0.062277 | 0.058089 | 0.053013 | 0.049494 | 0.043034 | 0.089613 | 0.089613 | 0.086592 | 0.08357 | 0.080049 | 0.076528 | 0.073506 | 0.067332 | 0.063144 | 0.058955 | 0.054767 | 0.049692 | 0.046172 | 0.039713
| FORT WILLIAM | CORRAN | MINIMUM HEADROOM | NN 02545 63126 | YES | YES | -0.42222 | -0.46868 | -0.5188 | -0.59189 | -0.70034 | -0.81527 | -0.90206 | -0.95928 | -1.0233 | -1.081 | -1.1416 | -1.3766 | -1.6346 | -1.825 | -0.030725 | -0.059285 | -0.099617 | -0.15816 | -0.24807 | -0.34361 | -0.40134 | -0.46362 | -0.53627 | -0.60509 | -0.67335 | -0.952 | -1.2194 | -1.4357 | -0.2063 | -0.25086 | -0.29663 | -0.37871 | -0.48954 | -0.6069 | -0.68715 | -0.75963 | -0.84624 | -0.92787 | -1.0072 | -1.2837 | -1.577 | -1.7926
|  | CORRAN | CT |  |  |  | -0.38968 | -0.43164 | -0.50976 | -0.59189 | -0.70034 | -0.81527 | -0.90206 | -0.95928 | -1.0233 | -1.081 | -1.1416 | -1.3766 | -1.585 | -1.7189 | -0.020446 | -0.048558 | -0.099617 | -0.15816 | -0.24807 | -0.34361 | -0.40134 | -0.46362 | -0.53627 | -0.60509 | -0.67335 | -0.9226 | -1.1073 | -1.2694 | -0.18166 | -0.22214 | -0.29663 | -0.37871 | -0.48954 | -0.6069 | -0.68715 | -0.75963 | -0.84624 | -0.92787 | -1.0072 | -1.2831 | -1.4936 | -1.6505
|  | CORRAN | LW |  |  |  | -0.42222 | -0.46868 | -0.5188 | -0.56977 | -0.62717 | -0.69119 | -0.76458 | -0.81513 | -0.86918 | -0.9294 | -0.99288 | -1.217 | -1.4823 | -1.7495 | -0.030725 | -0.059285 | -0.087178 | -0.11779 | -0.14883 | -0.19248 | -0.24346 | -0.29911 | -0.3594 | -0.42213 | -0.48511 | -0.67183 | -0.94234 | -1.2671 | -0.2063 | -0.25086 | -0.29595 | -0.34388 | -0.39379 | -0.45833 | -0.53297 | -0.60081 | -0.67372 | -0.75096 | -0.82873 | -1.0562 | -1.3495 | -1.6781
|  | CORRAN | ST |  |  |  | -0.36584 | -0.38315 | -0.44577 | -0.49661 | -0.54464 | -0.63316 | -0.68513 | -0.77122 | -0.83084 | -0.89737 | -0.97505 | -1.3618 | -1.6346 | -1.825 | -0.0074711 | -0.017288 | -0.07788 | -0.12547 | -0.16577 | -0.25975 | -0.30568 | -0.39139 | -0.44658 | -0.50549 | -0.57867 | -0.952 | -1.2194 | -1.4357 | -0.16189 | -0.1776 | -0.24695 | -0.30317 | -0.35326 | -0.45632 | -0.5125 | -0.61049 | -0.67771 | -0.75119 | -0.83927 | -1.2837 | -1.577 | -1.7926
|  | CORRAN | FS |  |  |  | -0.34794 | -0.36131 | -0.38932 | -0.41849 | -0.45008 | -0.48119 | -0.51446 | -0.5599 | -0.60432 | -0.6472 | -0.70021 | -0.9843 | -1.2261 | -1.3813 | -0.0010406 | -0.0086674 | -0.028791 | -0.050624 | -0.074939 | -0.10062 | -0.12764 | -0.16787 | -0.20486 | -0.24327 | -0.28686 | -0.50504 | -0.71583 | -0.84429 | -0.14885 | -0.16104 | -0.18854 | -0.21811 | -0.25044 | -0.28354 | -0.31853 | -0.36825 | -0.41587 | -0.46397 | -0.52048 | -0.81613 | -1.0748 | -1.2055
| KILLIN | COSHIEVILLE | MINIMUM HEADROOM | NN 77193 48683 | YES | YES | 1.4662 | 1.3963 | 1.3205 | 1.2279 | 1.1373 | 1.0315 | 0.90997 | 0.82658 | 0.73631 | 0.64609 | 0.57427 | 0.44101 | 0.37575 | 0.32971 | 1.5303 | 1.4921 | 1.4545 | 1.3991 | 1.3469 | 1.2952 | 1.2367 | 1.179 | 1.1166 | 1.0539 | 1.0012 | 0.91301 | 0.85932 | 0.8106 | 1.3579 | 1.2994 | 1.2404 | 1.1675 | 1.0884 | 1.0094 | 0.90746 | 0.82583 | 0.73757 | 0.64892 | 0.57558 | 0.45644 | 0.41301 | 0.3791
|  | COSHIEVILLE | CT |  |  |  | 1.4972 | 1.4665 | 1.3615 | 1.2441 | 1.1373 | 1.0331 | 0.92959 | 0.8593 | 0.77384 | 0.6859 | 0.62093 | 0.48873 | 0.37575 | 0.32971 | 1.5498 | 1.5181 | 1.462 | 1.3991 | 1.3469 | 1.2952 | 1.2434 | 1.1967 | 1.1369 | 1.0756 | 1.0269 | 0.923 | 0.85932 | 0.8106 | 1.3934 | 1.3481 | 1.2639 | 1.1689 | 1.0884 | 1.0094 | 0.93083 | 0.86486 | 0.7797 | 0.69179 | 0.62489 | 0.49247 | 0.41301 | 0.3791
|  | COSHIEVILLE | LW |  |  |  | 1.4662 | 1.3963 | 1.3205 | 1.2279 | 1.1435 | 1.0315 | 0.90997 | 0.82658 | 0.73631 | 0.64609 | 0.57427 | 0.44101 | 0.38999 | 0.37334 | 1.5303 | 1.4921 | 1.4545 | 1.4077 | 1.366 | 1.3048 | 1.2367 | 1.179 | 1.1166 | 1.0539 | 1.0012 | 0.91301 | 0.8891 | 0.88278 | 1.3579 | 1.2994 | 1.2404 | 1.1675 | 1.1028 | 1.0101 | 0.90746 | 0.82583 | 0.73757 | 0.64892 | 0.57558 | 0.45644 | 0.42132 | 0.41093
|  | COSHIEVILLE | ST |  |  |  | 1.508 | 1.5026 | 1.4951 | 1.4673 | 1.4188 | 1.3722 | 1.3211 | 1.2616 | 1.1961 | 1.1213 | 1.0494 | 0.70206 | 0.57969 | 0.50784 | 1.5678 | 1.5558 | 1.5399 | 1.5163 | 1.49 | 1.4626 | 1.4317 | 1.3951 | 1.3532 | 1.3055 | 1.2572 | 1.0146 | 0.9354 | 0.88187 | 1.4223 | 1.4054 | 1.3821 | 1.3475 | 1.3089 | 1.2698 | 1.226 | 1.1737 | 1.1142 | 1.0463 | 0.97859 | 0.64825 | 0.55622 | 0.51186
|  | COSHIEVILLE | FS |  |  |  | 1.5099 | 1.5058 | 1.5002 | 1.4906 | 1.4622 | 1.4229 | 1.3805 | 1.3277 | 1.2729 | 1.2184 | 1.1579 | 0.7948 | 0.5384 | 0.45826 | 1.5755 | 1.5664 | 1.551 | 1.533 | 1.5115 | 1.4894 | 1.4648 | 1.4349 | 1.4028 | 1.3696 | 1.3331 | 1.1073 | 0.92096 | 0.8442 | 1.4355 | 1.4235 | 1.4002 | 1.3743 | 1.3427 | 1.3109 | 1.2759 | 1.2322 | 1.1859 | 1.1385 | 1.0861 | 0.76579 | 0.52613 | 0.47278
| COUPAR ANGUS | COUPAR ANGUS | MINIMUM HEADROOM | NO 21784 39212 | NO | YES | 0.61793 | 0.41985 | 0.10071 | -0.24675 | -0.65204 | -1.1547 | -1.7203 | -2.085 | -2.4644 | -3.2574 | -3.9913 | -4.8996 | -5.6093 | -6.2449 | 0.23791 | 0.13351 | -0.052328 | -0.25998 | -0.53951 | -0.89108 | -1.2761 | -1.5069 | -1.7515 | -2.345 | -2.9084 | -3.5656 | -4.1026 | -4.8062 | 0.010536 | -0.16261 | -0.44794 | -0.77014 | -1.1756 | -1.6739 | -2.2178 | -2.5607 | -2.919 | -3.669 | -4.3708 | -5.2467 | -6.0099 | -6.7638
|  | COUPAR ANGUS | CT |  |  |  | 0.73703 | 0.59804 | 0.31314 | -0.023119 | -0.45249 | -0.92107 | -1.3669 | -1.7193 | -2.1126 | -2.9117 | -3.6597 | -4.8379 | -5.5856 | -6.0312 | 0.28382 | 0.20098 | 0.033611 | -0.16148 | -0.47665 | -0.81765 | -1.0905 | -1.3124 | -1.571 | -2.1709 | -2.7462 | -3.5656 | -4.1026 | -4.6227 | 0.12377 | -0.0081413 | -0.28069 | -0.58515 | -1.0035 | -1.4693 | -1.8869 | -2.2204 | -2.5939 | -3.3506 | -4.067 | -5.2146 | -5.9458 | -6.4144
|  | COUPAR ANGUS | LW |  |  |  | 0.61793 | 0.41985 | 0.10071 | -0.24675 | -0.65204 | -1.1547 | -1.7203 | -2.085 | -2.4644 | -3.2574 | -3.9913 | -4.8996 | -5.6093 | -6.2449 | 0.23791 | 0.13351 | -0.052328 | -0.25998 | -0.53951 | -0.89108 | -1.2761 | -1.5069 | -1.7515 | -2.345 | -2.9084 | -3.4823 | -4.0889 | -4.8062 | 0.010536 | -0.16261 | -0.44794 | -0.77014 | -1.1756 | -1.6739 | -2.2178 | -2.5607 | -2.919 | -3.669 | -4.3708 | -5.2467 | -6.0099 | -6.7638
|  | COUPAR ANGUS | ST |  |  |  | 0.80114 | 0.72995 | 0.51302 | 0.32845 | 0.16702 | -0.16851 | -0.45311 | -0.71099 | -0.93252 | -1.5779 | -2.2227 | -3.6229 | -4.4526 | -5.1719 | 0.31794 | 0.277 | 0.06012 | -0.11077 | -0.24834 | -0.5869 | -0.82726 | -1.0455 | -1.2099 | -1.7286 | -2.2646 | -3.3393 | -4.0537 | -4.7316 | 0.18645 | 0.12137 | -0.12418 | -0.32621 | -0.49683 | -0.876 | -1.1615 | -1.4292 | -1.6483 | -2.2292 | -2.8264 | -4.1999 | -5.0383 | -5.7968
|  | COUPAR ANGUS | FS |  |  |  | 0.82586 | 0.7717 | 0.67548 | 0.57026 | 0.44742 | 0.31783 | 0.11969 | -0.05868 | -0.24056 | -0.66592 | -1.1223 | -2.4314 | -3.515 | -4.0832 | 0.3288 | 0.29601 | 0.22124 | 0.13958 | 0.045596 | -0.055728 | -0.21955 | -0.34661 | -0.47149 | -0.80412 | -1.1696 | -2.0733 | -2.9582 | -3.5917 | 0.21051 | 0.16186 | 0.063342 | -0.043574 | -0.16843 | -0.29794 | -0.4961 | -0.66719 | -0.83684 | -1.2159 | -1.6258 | -2.8538 | -3.8646 | -4.4006
| CRAIGIEBUCKLER | CRAIGIEBUCKLER | MINIMUM HEADROOM | NJ 90775 04519 | NO | YES | 16.4516 | 16.1623 | 15.6616 | 15.062 | 14.6016 | 14.0341 | 13.4163 | 12.8198 | 12.1995 | 11.5652 | 10.9406 | 9.3902 | 8.6466 | 7.7762 | 17.9103 | 17.7235 | 17.475 | 17.1701 | 16.9388 | 16.6069 | 16.2325 | 15.8334 | 15.397 | 14.9283 | 14.4762 | 13.4532 | 12.6801 | 11.5745 | 16.8014 | 16.5234 | 16.0752 | 15.5423 | 15.1215 | 14.5767 | 13.9784 | 13.3973 | 12.7579 | 12.105 | 11.4705 | 9.9741 | 9.1961 | 8.2259
|  | CRAIGIEBUCKLER | CT |  |  |  | 16.6904 | 16.5155 | 16.0194 | 15.4359 | 15.0202 | 14.5895 | 14.1531 | 13.6036 | 12.9891 | 12.388 | 11.7906 | 9.9035 | 8.9563 | 8.2477 | 17.9856 | 17.8509 | 17.5638 | 17.2253 | 16.9948 | 16.7507 | 16.5019 | 16.1568 | 15.7577 | 15.3599 | 14.9395 | 13.5824 | 12.6801 | 11.5745 | 17.0036 | 16.8321 | 16.3697 | 15.8318 | 15.447 | 15.047 | 14.6416 | 14.1266 | 13.5279 | 12.9321 | 12.3417 | 10.5407 | 9.6751 | 9.0026
|  | CRAIGIEBUCKLER | LW |  |  |  | 16.4516 | 16.1623 | 15.6616 | 15.062 | 14.6016 | 14.0341 | 13.4163 | 12.8198 | 12.1995 | 11.5652 | 10.9406 | 9.3902 | 8.6466 | 7.7762 | 17.9103 | 17.7235 | 17.475 | 17.1701 | 16.9388 | 16.6069 | 16.2325 | 15.8334 | 15.397 | 14.9283 | 14.4762 | 13.4532 | 12.828 | 11.94 | 16.8014 | 16.5234 | 16.0752 | 15.5423 | 15.1215 | 14.5767 | 13.9784 | 13.3973 | 12.7579 | 12.105 | 11.4705 | 9.9741 | 9.1961 | 8.2259
|  | CRAIGIEBUCKLER | ST |  |  |  | 16.7818 | 16.6856 | 16.5756 | 16.4073 | 16.309 | 16.1877 | 16.037 | 15.8009 | 15.5512 | 15.2845 | 14.9817 | 12.8762 | 11.6665 | 10.6286 | 18.0389 | 17.9656 | 17.8811 | 17.7567 | 17.6633 | 17.5483 | 17.4099 | 17.1918 | 16.9747 | 16.7394 | 16.4655 | 14.7391 | 13.5598 | 12.2571 | 17.0904 | 17.0023 | 16.8989 | 16.7457 | 16.64 | 16.5093 | 16.3461 | 16.0843 | 15.8121 | 15.5169 | 15.1803 | 13.129 | 11.9494 | 10.9384
|  | CRAIGIEBUCKLER | FS |  |  |  | 16.8113 | 16.7339 | 16.6332 | 16.4797 | 16.3893 | 16.2832 | 16.1627 | 15.9779 | 15.7774 | 15.5499 | 15.3109 | 13.7117 | 11.9279 | 10.7983 | 18.052 | 17.9873 | 17.9109 | 17.8001 | 17.7193 | 17.6237 | 17.513 | 17.3497 | 17.1774 | 16.9845 | 16.775 | 15.3808 | 13.6183 | 11.7795 | 17.1167 | 17.0465 | 16.9542 | 16.8182 | 16.726 | 16.6169 | 16.4917 | 16.3019 | 16.0955 | 15.8606 | 15.6106 | 13.9984 | 12.3162 | 11.2954
| CLAYHILLS | CRAIGINCHES | MINIMUM HEADROOM | NJ 94694 04089 | NO | NO | 10.6604 | 10.4496 | 10.1784 | 9.8726 | 9.2935 | 8.435 | 7.5881 | 6.8996 | 6.1399 | 5.352 | 4.578 | 2.333 | 1.5528 | 0.88128 | 12.6011 | 12.3569 | 12.0396 | 11.6612 | 10.9603 | 10.0799 | 9.3534 | 8.7936 | 8.1756 | 7.5409 | 6.9132 | 4.9993 | 4.1937 | 3.3992 | 11.127 | 10.9095 | 10.3556 | 9.7441 | 8.8582 | 7.863 | 7.0619 | 6.5081 | 5.7532 | 4.9754 | 4.209 | 1.9328 | 1.0569 | 0.25027
|  | CRAIGINCHES | CT |  |  |  | 10.6604 | 10.4496 | 10.1784 | 9.8757 | 9.4725 | 8.8884 | 8.3736 | 7.8711 | 7.4168 | 6.9733 | 6.4425 | 4.6145 | 3.9969 | 3.5813 | 12.6011 | 12.3569 | 12.0396 | 11.7089 | 11.23 | 10.6693 | 10.2866 | 9.902 | 9.5521 | 9.2138 | 8.8088 | 7.4024 | 6.9689 | 6.095 | 11.2519 | 10.9095 | 10.4545 | 9.995 | 9.4024 | 8.7251 | 8.2207 | 7.7279 | 7.2812 | 6.8467 | 6.3272 | 4.523 | 3.9534 | 3.5379
|  | CRAIGINCHES | LW |  |  |  | 10.673 | 10.5313 | 10.2255 | 9.8726 | 9.2935 | 8.435 | 7.5881 | 6.8996 | 6.1399 | 5.352 | 4.578 | 2.333 | 1.5528 | 0.88128 | 12.6228 | 12.456 | 12.0842 | 11.6612 | 10.9603 | 10.0799 | 9.3534 | 8.7936 | 8.1756 | 7.5409 | 6.9132 | 4.9993 | 4.1937 | 3.3992 | 11.127 | 10.9229 | 10.3556 | 9.7441 | 8.8582 | 7.863 | 7.0619 | 6.5081 | 5.7532 | 4.9754 | 4.209 | 1.9328 | 1.0569 | 0.25027
|  | CRAIGINCHES | ST |  |  |  | 10.7278 | 10.6785 | 10.4346 | 10.2296 | 10.0433 | 9.6345 | 9.3903 | 9.0784 | 8.7806 | 8.389 | 7.7608 | 4.3372 | 2.8767 | 2.2537 | 12.6853 | 12.627 | 12.3261 | 12.0752 | 11.8488 | 11.3464 | 11.052 | 10.6819 | 10.3265 | 9.889 | 9.3662 | 6.5806 | 5.3291 | 4.7481 | 11.3219 | 11.2757 | 10.9619 | 10.6702 | 10.3921 | 9.8253 | 9.4509 | 8.9833 | 8.5174 | 7.9858 | 7.3538 | 3.9832 | 2.5626 | 1.9648
|  | CRAIGINCHES | FS |  |  |  | 10.7466 | 10.7111 | 10.63 | 10.5389 | 10.4305 | 10.3081 | 10.1759 | 10.0277 | 9.8717 | 9.6911 | 9.4868 | 7.3746 | 5.0166 | 3.3744 | 12.706 | 12.6629 | 12.5629 | 12.4508 | 12.3175 | 12.1672 | 12.0054 | 11.8242 | 11.6337 | 11.4199 | 11.1783 | 9.4638 | 7.617 | 4.3583 | 11.3396 | 11.3063 | 11.2187 | 11.0865 | 10.9203 | 10.7315 | 10.5239 | 10.287 | 10.0319 | 9.7453 | 9.421 | 7.3032 | 5.0416 | 3.4686
| CRAIGIEBUCKLER | CRAIGTON | MINIMUM HEADROOM | NJ 89195 03438 | YES | YES | 8.0552 | 7.2986 | 5.6116 | 4.5506 | 3.4576 | 2.2909 | 0.75445 | -0.40241 | -1.6302 | -2.8941 | -3.7324 | -5.4108 | -6.4117 | -7.6835 | 9.6071 | 9.1245 | 8.1054 | 7.4693 | 6.8222 | 6.1239 | 5.096 | 4.3549 | 3.546 | 2.7095 | 2.0875 | 0.52141 | -0.56446 | -1.7955 | 8.5114 | 7.8524 | 6.4825 | 5.5675 | 4.6367 | 3.6024 | 2.2206 | 1.1704 | 0.065791 | -1.0695 | -1.8714 | -3.5023 | -4.6223 | -6.1175
|  | CRAIGTON | CT |  |  |  | 8.362 | 7.757 | 6.1665 | 5.1098 | 4.0255 | 2.9163 | 1.5454 | 0.36507 | -0.89555 | -2.1674 | -3.0466 | -5.3298 | -6.4011 | -7.1974 | 9.7318 | 9.3224 | 8.3295 | 7.649 | 6.9473 | 6.2287 | 5.3075 | 4.5471 | 3.7222 | 2.8869 | 2.237 | 0.52141 | -0.56446 | -1.7955 | 8.7675 | 8.243 | 6.9182 | 5.9766 | 5.0135 | 4.0255 | 2.8238 | 1.763 | 0.62717 | -0.5072 | -1.3368 | -3.5023 | -4.568 | -5.4106
|  | CRAIGTON | LW |  |  |  | 8.0552 | 7.2986 | 5.6116 | 4.5506 | 3.4576 | 2.2909 | 0.75445 | -0.40241 | -1.6302 | -2.8941 | -3.7324 | -5.4108 | -6.4117 | -7.6835 | 9.6071 | 9.1245 | 8.1054 | 7.4693 | 6.8222 | 6.1239 | 5.096 | 4.3549 | 3.546 | 2.7095 | 2.0875 | 0.89057 | -0.1224 | -1.5459 | 8.5114 | 7.8524 | 6.4825 | 5.5675 | 4.6367 | 3.6024 | 2.2206 | 1.1704 | 0.065791 | -1.0695 | -1.8714 | -3.493 | -4.6223 | -6.1175
|  | CRAIGTON | ST |  |  |  | 8.4785 | 7.976 | 6.7164 | 6.0519 | 5.3904 | 4.6585 | 3.6906 | 2.8717 | 2.0685 | 1.2234 | 0.57893 | -2.1296 | -3.5795 | -4.7315 | 9.7979 | 9.4685 | 8.6022 | 8.1052 | 7.6171 | 7.0345 | 6.2634 | 5.6121 | 5.016 | 4.3954 | 3.8608 | 1.6727 | 0.18297 | -1.33 | 8.8763 | 8.4587 | 7.4277 | 6.8446 | 6.2692 | 5.5989 | 4.736 | 3.9795 | 3.2696 | 2.524 | 1.9029 | -0.77743 | -2.2708 | -3.4774
|  | CRAIGTON | FS |  |  |  | 8.7138 | 8.3279 | 7.3658 | 6.7768 | 6.2357 | 5.6212 | 4.8386 | 4.1797 | 3.3797 | 2.6072 | 2.0992 | -0.20819 | -2.2376 | -3.3089 | 9.9384 | 9.6694 | 9.0386 | 8.614 | 8.223 | 7.7813 | 7.1658 | 6.6786 | 6.0972 | 5.5348 | 5.1237 | 3.3039 | 1.4441 | -0.14627 | 9.0775 | 8.762 | 7.9845 | 7.5032 | 7.0436 | 6.5254 | 5.8407 | 5.2629 | 4.581 | 3.9169 | 3.4422 | 1.2814 | -0.68968 | -1.6679
| BRACO | CRIEFF | MINIMUM HEADROOM | NN 85626 22119 | NO | YES | 5.1538 | 13.4435 | 12.849 | 12.2015 | 11.58 | 10.8928 | 10.1627 | 9.4689 | 8.7221 | 7.8249 | 6.9512 | 4.9784 | 4.0727 | 3.4217 | 8.548 | 16.5306 | 16.2033 | 15.8321 | 15.4273 | 15.0031 | 14.5593 | 14.0688 | 13.5388 | 12.8794 | 12.2441 | 10.8618 | 9.9898 | 9.1012 | 5.984 | 13.845 | 13.337 | 12.7728 | 12.2427 | 11.5703 | 10.8293 | 10.1435 | 9.4088 | 8.541 | 7.702 | 5.8969 | 5.0477 | 4.3273
|  | CRIEFF | CT |  |  |  | 5.4422 | 13.8488 | 13.2211 | 12.5465 | 11.8852 | 11.232 | 10.6104 | 9.9781 | 9.226 | 8.3381 | 7.4539 | 5.3087 | 4.1537 | 3.5101 | 8.6503 | 16.6891 | 16.2921 | 15.8491 | 15.4273 | 15.0031 | 14.6293 | 14.1784 | 13.6536 | 13.0107 | 12.3717 | 10.8618 | 9.9898 | 9.1012 | 6.2005 | 14.1682 | 13.591 | 12.958 | 12.3655 | 11.7734 | 11.2081 | 10.5675 | 9.8408 | 8.9958 | 8.1591 | 6.1359 | 5.1125 | 4.5158
|  | CRIEFF | LW |  |  |  | 5.1538 | 13.4435 | 12.849 | 12.2015 | 11.58 | 10.8928 | 10.1627 | 9.4689 | 8.7221 | 7.8249 | 6.9512 | 4.9784 | 4.0727 | 3.4217 | 8.548 | 16.5306 | 16.2033 | 15.8321 | 15.4882 | 15.0449 | 14.5593 | 14.0688 | 13.5388 | 12.8794 | 12.2441 | 11.0512 | 10.4578 | 9.8373 | 5.984 | 13.845 | 13.337 | 12.7728 | 12.2427 | 11.5703 | 10.8293 | 10.1435 | 9.4088 | 8.541 | 7.702 | 5.8969 | 5.0477 | 4.3273
|  | CRIEFF | ST |  |  |  | 5.6427 | 14.1768 | 13.9323 | 13.6642 | 13.407 | 13.096 | 12.8275 | 12.4855 | 12.1135 | 11.5458 | 10.936 | 8.609 | 7.4611 | 6.4002 | 8.7467 | 16.8817 | 16.6686 | 16.4383 | 16.2156 | 15.9156 | 15.6674 | 15.338 | 15.0057 | 14.5293 | 14.0095 | 12.0504 | 11.0274 | 9.969 | 6.3596 | 14.4595 | 14.2108 | 13.9389 | 13.675 | 13.3326 | 13.0362 | 12.6501 | 12.2529 | 11.7092 | 11.1177 | 8.7539 | 7.697 | 6.8123
|  | CRIEFF | FS |  |  |  | 5.7121 | 14.2801 | 14.0835 | 13.8546 | 13.627 | 13.4113 | 13.1875 | 12.9072 | 12.61 | 12.2182 | 11.7663 | 9.5257 | 7.6053 | 6.5264 | 8.7922 | 16.9491 | 16.8002 | 16.6221 | 16.4405 | 16.2574 | 16.0629 | 15.8201 | 15.5588 | 15.2117 | 14.8301 | 13.0238 | 11.1799 | 9.5774 | 6.4195 | 14.5505 | 14.3657 | 14.1473 | 13.9265 | 13.7074 | 13.4746 | 13.1859 | 12.8768 | 12.4836 | 12.0554 | 9.9394 | 8.1295 | 7.2005
| PORT ANN | CRINAN | MINIMUM HEADROOM | NR 79620 92347 | YES | YES | 0.19214 | 0.18488 | 0.17669 | 0.16431 | 0.14372 | 0.10176 | 0.068815 | 0.043441 | 0.0055162 | -0.031051 | -0.0627 | -0.13202 | -0.18613 | -0.21774 | 0.376 | 0.36351 | 0.35001 | 0.32114 | 0.29164 | 0.26155 | 0.23974 | 0.21489 | 0.18022 | 0.14606 | 0.11595 | 0.041956 | -0.0062285 | -0.052781 | 0.17848 | 0.16705 | 0.14638 | 0.12718 | 0.09423 | 0.059253 | 0.030622 | 0.014726 | -0.0081429 | -0.036412 | -0.071935 | -0.14956 | -0.20995 | -0.24795
|  | CRINAN | CT |  |  |  | 0.19317 | 0.18742 | 0.17669 | 0.16431 | 0.14372 | 0.10176 | 0.068815 | 0.043441 | 0.0055162 | -0.031051 | -0.0627 | -0.13202 | -0.18613 | -0.21774 | 0.38103 | 0.37131 | 0.3503 | 0.32114 | 0.29164 | 0.26155 | 0.23974 | 0.21489 | 0.18022 | 0.14606 | 0.11595 | 0.041956 | -0.0062285 | -0.052781 | 0.18344 | 0.17925 | 0.15759 | 0.12941 | 0.09423 | 0.059253 | 0.030622 | 0.014726 | -0.0081429 | -0.036412 | -0.071935 | -0.14956 | -0.20995 | -0.24795
|  | CRINAN | LW |  |  |  | 0.19214 | 0.18488 | 0.17884 | 0.17153 | 0.16322 | 0.1244 | 0.083466 | 0.050058 | 0.016787 | -0.02011 | -0.054457 | -0.11217 | -0.15853 | -0.20896 | 0.376 | 0.36351 | 0.35001 | 0.33143 | 0.31587 | 0.2892 | 0.25993 | 0.23013 | 0.19895 | 0.16636 | 0.13652 | 0.087241 | 0.040029 | -0.019032 | 0.17848 | 0.16705 | 0.14638 | 0.12718 | 0.10953 | 0.087279 | 0.057784 | 0.037106 | 0.017889 | -0.021569 | -0.058732 | -0.12311 | -0.17936 | -0.24185
|  | CRINAN | ST |  |  |  | 0.1947 | 0.19267 | 0.18322 | 0.17489 | 0.1677 | 0.15221 | 0.14302 | 0.12733 | 0.11481 | 0.10035 | 0.07776 | -0.059913 | -0.11797 | -0.16194 | 0.38539 | 0.38204 | 0.36867 | 0.35578 | 0.34512 | 0.32386 | 0.30813 | 0.28384 | 0.26041 | 0.23666 | 0.20828 | 0.065807 | 0.0024656 | -0.051782 | 0.18456 | 0.1831 | 0.17274 | 0.16433 | 0.15755 | 0.14094 | 0.13277 | 0.11735 | 0.10684 | 0.095811 | 0.074131 | -0.082556 | -0.14971 | -0.19878
|  | CRINAN | FS |  |  |  | 0.19508 | 0.19341 | 0.18986 | 0.18556 | 0.18089 | 0.17557 | 0.16978 | 0.16159 | 0.1534 | 0.14438 | 0.13296 | 0.019238 | -0.079393 | -0.099902 | 0.38716 | 0.38426 | 0.37752 | 0.36996 | 0.36155 | 0.35305 | 0.34312 | 0.32973 | 0.31265 | 0.29679 | 0.27825 | 0.1687 | 0.074867 | 0.038904 | 0.18484 | 0.18364 | 0.18035 | 0.17652 | 0.1723 | 0.16762 | 0.1627 | 0.15531 | 0.14331 | 0.1368 | 0.12745 | 0.016412 | -0.09297 | -0.11781
| PORT ANN | CROMALT | MINIMUM HEADROOM | NN 08395 07755 | YES | YES | -2.157 | -2.5925 | -2.6707 | -2.7916 | -2.8533 | -2.9118 | -2.9777 | -3.0268 | -3.0672 | -3.1062 | -3.1623 | -3.4108 | -3.5685 | -3.6775 | -1.7039 | -2.1812 | -2.2623 | -2.3917 | -2.4501 | -2.4889 | -2.5226 | -2.5656 | -2.6018 | -2.6363 | -2.6863 | -2.9567 | -3.1178 | -3.2403 | -1.6648 | -2.098 | -2.1845 | -2.3133 | -2.38 | -2.4359 | -2.4969 | -2.5383 | -2.5795 | -2.6175 | -2.6651 | -2.8658 | -3.0277 | -3.1611
|  | CROMALT | CT |  |  |  | -2.071 | -2.4871 | -2.5949 | -2.7054 | -2.8146 | -2.9118 | -2.9777 | -3.0268 | -3.0672 | -3.1062 | -3.1623 | -3.3899 | -3.4721 | -3.5432 | -1.6168 | -2.0488 | -2.1558 | -2.267 | -2.3763 | -2.4664 | -2.5226 | -2.5656 | -2.6018 | -2.6363 | -2.6863 | -2.91 | -2.9972 | -3.0784 | -1.5703 | -1.9682 | -2.0811 | -2.2017 | -2.3223 | -2.428 | -2.4969 | -2.5383 | -2.5795 | -2.6175 | -2.6651 | -2.8658 | -2.9713 | -3.0621
|  | CROMALT | LW |  |  |  | -2.157 | -2.5925 | -2.6707 | -2.7916 | -2.8533 | -2.9049 | -2.9405 | -2.978 | -3.0174 | -3.0575 | -3.0959 | -3.1923 | -3.3112 | -3.4689 | -1.7039 | -2.1812 | -2.2623 | -2.3917 | -2.4501 | -2.4889 | -2.5054 | -2.5268 | -2.5485 | -2.5806 | -2.6118 | -2.695 | -2.833 | -3.0269 | -1.6648 | -2.098 | -2.1845 | -2.3133 | -2.38 | -2.4359 | -2.4775 | -2.5157 | -2.5522 | -2.5904 | -2.6298 | -2.7233 | -2.8717 | -3.0795
|  | CROMALT | ST |  |  |  | -2.0381 | -2.4409 | -2.5505 | -2.6554 | -2.7374 | -2.8263 | -2.8805 | -2.9321 | -2.9724 | -3.0147 | -3.0731 | -3.4108 | -3.5685 | -3.6775 | -1.5946 | -2.026 | -2.1471 | -2.2593 | -2.3428 | -2.4341 | -2.4802 | -2.5232 | -2.5569 | -2.5943 | -2.6485 | -2.9567 | -3.1178 | -3.2403 | -1.5391 | -1.9283 | -2.0391 | -2.141 | -2.2181 | -2.3072 | -2.3563 | -2.408 | -2.4451 | -2.4749 | -2.5239 | -2.8504 | -3.0277 | -3.1611
|  | CROMALT | FS |  |  |  | -1.7981 | -2.0926 | -2.1716 | -2.2517 | -2.3233 | -2.3857 | -2.4486 | -2.5184 | -2.588 | -2.6588 | -2.7434 | -3.1318 | -3.2942 | -3.3959 | -1.3276 | -1.6479 | -1.7291 | -1.8113 | -1.8842 | -1.9472 | -2.0103 | -2.0811 | -2.1506 | -2.2206 | -2.3047 | -2.6662 | -2.7971 | -2.8803 | -1.2961 | -1.5928 | -1.6716 | -1.7512 | -1.8194 | -1.8813 | -1.94 | -2.0076 | -2.0777 | -2.1395 | -2.2194 | -2.5579 | -2.7056 | -2.8114
| ALNESS | CROSSHILLS | MINIMUM HEADROOM | NH 65470 70156 | NO | YES | 6.0328 | 5.2011 | 3.9545 | 3.2696 | 2.6059 | 1.6911 | 0.78763 | 0.1176 | -0.48836 | -1.1133 | -1.6065 | -3.015 | -4.0364 | -4.5767 | 7.1842 | 6.3736 | 5.3004 | 4.8705 | 4.4717 | 4.043 | 3.5938 | 3.2801 | 2.985 | 2.6766 | 2.3875 | 1.5997 | 0.9409 | 0.42034 | 6.5476 | 5.7615 | 4.6301 | 4.0283 | 3.4478 | 2.6963 | 1.8982 | 1.3007 | 0.74772 | 0.17711 | -0.28527 | -1.5746 | -2.4819 | -2.9629
|  | CROSSHILLS | CT |  |  |  | 6.4264 | 5.7354 | 4.5212 | 3.8527 | 3.2428 | 2.4165 | 1.6338 | 0.93439 | 0.29293 | -0.36086 | -0.90775 | -2.8602 | -4.0364 | -4.5767 | 7.4449 | 6.7217 | 5.6719 | 5.255 | 4.8806 | 4.4298 | 3.9969 | 3.6461 | 3.3526 | 3.0561 | 2.7577 | 1.5997 | 0.9409 | 0.42034 | 6.7448 | 6.0304 | 4.9747 | 4.5094 | 4.0442 | 3.3225 | 2.6323 | 2.0106 | 1.4321 | 0.84436 | 0.34216 | -1.4403 | -2.4819 | -2.9629
|  | CROSSHILLS | LW |  |  |  | 6.0328 | 5.2011 | 3.9545 | 3.2696 | 2.6059 | 1.6911 | 0.78763 | 0.1176 | -0.48836 | -1.1133 | -1.6065 | -3.015 | -3.682 | -3.9998 | 7.1842 | 6.3736 | 5.3004 | 4.8705 | 4.4717 | 4.043 | 3.5938 | 3.2801 | 2.985 | 2.6766 | 2.3875 | 1.6305 | 1.3109 | 1.0984 | 6.5476 | 5.7615 | 4.6301 | 4.0283 | 3.4478 | 2.6963 | 1.8982 | 1.3007 | 0.74772 | 0.17711 | -0.28527 | -1.5746 | -2.1731 | -2.4785
|  | CROSSHILLS | ST |  |  |  | 6.5613 | 5.982 | 5.1052 | 4.7795 | 4.4736 | 4.021 | 3.5836 | 3.2068 | 2.8777 | 2.5044 | 2.1516 | -0.014831 | -1.1344 | -2.1294 | 7.5111 | 6.8515 | 5.9433 | 5.6659 | 5.4198 | 5.1159 | 4.8119 | 4.5752 | 4.3846 | 4.1682 | 3.9444 | 2.2119 | 1.5389 | 1.0374 | 6.8398 | 6.2503 | 5.3847 | 5.1019 | 4.8214 | 4.451 | 4.0564 | 3.7031 | 3.3634 | 2.9725 | 2.5493 | 0.19246 | -0.71851 | -1.1519
|  | CROSSHILLS | FS |  |  |  | 6.9481 | 6.5042 | 5.8115 | 5.4788 | 5.2255 | 4.7939 | 4.4195 | 4.0498 | 3.6117 | 3.1942 | 2.8583 | 0.76689 | -0.90454 | -2.0366 | 7.9683 | 7.4657 | 6.7614 | 6.4718 | 6.2759 | 5.9705 | 5.7079 | 5.4615 | 5.1217 | 4.8158 | 4.5748 | 3.1372 | 1.8581 | 0.63326 | 7.2157 | 6.7707 | 6.1156 | 5.84 | 5.6241 | 5.292 | 4.9894 | 4.699 | 4.3146 | 3.9506 | 3.6356 | 1.717 | 0.17511 | -0.854
| KEITH | CULLEN | MINIMUM HEADROOM | NJ 51590 65032 | YES | YES | 6.0912 | 5.9503 | 5.726 | 5.4947 | 5.2819 | 5.0225 | 4.7066 | 4.4464 | 4.1694 | 3.8631 | 3.5708 | 2.6201 | 1.8812 | 0.9343 | 6.2065 | 6.1304 | 6.0234 | 5.9116 | 5.716 | 5.5078 | 5.3337 | 5.1401 | 4.9208 | 4.6973 | 4.4756 | 3.7175 | 3.053 | 1.9284 | 6.0373 | 5.9139 | 5.7192 | 5.5171 | 5.329 | 5.0546 | 4.8018 | 4.5316 | 4.2291 | 3.9367 | 3.658 | 2.7044 | 1.916 | 0.72642
|  | CULLEN | CT |  |  |  | 6.2177 | 6.123 | 5.8716 | 5.6123 | 5.3382 | 5.0471 | 4.7765 | 4.4949 | 4.1747 | 3.8631 | 3.5708 | 2.6201 | 1.8812 | 1.3115 | 6.2545 | 6.1972 | 6.06 | 5.912 | 5.716 | 5.5078 | 5.3337 | 5.1401 | 4.9208 | 4.6973 | 4.4756 | 3.7175 | 3.053 | 2.3499 | 6.1495 | 6.0687 | 5.8462 | 5.6135 | 5.3426 | 5.0546 | 4.8018 | 4.5316 | 4.2291 | 3.9367 | 3.658 | 2.7044 | 1.916 | 1.2665
|  | CULLEN | LW |  |  |  | 6.0912 | 5.9503 | 5.726 | 5.4947 | 5.2819 | 5.0225 | 4.7066 | 4.4464 | 4.1694 | 3.8981 | 3.6345 | 2.9201 | 2.0023 | 0.9343 | 6.2065 | 6.1304 | 6.0234 | 5.9116 | 5.8113 | 5.6785 | 5.4893 | 5.3128 | 5.1239 | 4.9154 | 4.7136 | 4.1652 | 3.2085 | 1.9284 | 6.0373 | 5.9139 | 5.7192 | 5.5171 | 5.329 | 5.1008 | 4.8162 | 4.5723 | 4.3128 | 4.0609 | 3.8139 | 3.1001 | 2.033 | 0.72642
|  | CULLEN | ST |  |  |  | 6.2685 | 6.2187 | 6.071 | 5.9491 | 5.8475 | 5.6616 | 5.4978 | 5.275 | 5.1149 | 4.9568 | 4.7677 | 3.7419 | 2.8062 | 1.8616 | 6.2789 | 6.2507 | 6.1195 | 6.0163 | 5.9346 | 5.751 | 5.6137 | 5.3932 | 5.2617 | 5.1329 | 4.9688 | 4.0295 | 3.0984 | 2.121 | 6.1961 | 6.1555 | 6.0051 | 5.8853 | 5.7877 | 5.5877 | 5.4302 | 5.1897 | 5.034 | 4.8827 | 4.6954 | 3.6742 | 2.6625 | 1.6092
|  | CULLEN | FS |  |  |  | 6.2888 | 6.2476 | 6.1671 | 6.0855 | 6.0056 | 5.9246 | 5.8014 | 5.6671 | 5.5382 | 5.4053 | 5.2638 | 4.5088 | 3.8124 | 3.3799 | 6.2879 | 6.2637 | 6.2085 | 6.1516 | 6.0935 | 6.033 | 5.9363 | 5.8246 | 5.7237 | 5.6183 | 5.5075 | 4.9485 | 4.3272 | 3.802 | 6.2139 | 6.1809 | 6.1105 | 6.0383 | 5.9653 | 5.8919 | 5.7768 | 5.6427 | 5.5185 | 5.3908 | 5.2556 | 4.5753 | 3.9438 | 3.5247
| INVERNESS | CULLODEN | MINIMUM HEADROOM | NH 71240 45502 | NO | YES | 7.3634 | 8.4846 | 7.2852 | 5.8799 | 4.5952 | 3.1836 | 1.7426 | 0.48088 | -0.83611 | -2.1153 | -3.0158 | -5.4602 | -6.9438 | -8.137 | 9.848 | 11.5628 | 10.8855 | 10.042 | 9.2941 | 8.4449 | 7.6176 | 6.8674 | 6.0746 | 5.2967 | 4.7032 | 3.2302 | 2.2857 | 1.0485 | 9.5529 | 11.1032 | 10.051 | 8.8063 | 7.6485 | 6.3532 | 5.0463 | 3.9051 | 2.7095 | 1.5432 | 0.68354 | -1.6191 | -3.0623 | -4.3459
|  | CULLODEN | CT |  |  |  | 7.9628 | 9.3066 | 8.1718 | 6.9468 | 5.7966 | 4.6754 | 3.5792 | 2.3379 | 0.9991 | -0.30569 | -1.3046 | -4.6333 | -6.6257 | -7.7042 | 10.1744 | 12.0014 | 11.3285 | 10.6009 | 9.9192 | 9.265 | 8.6843 | 8.004 | 7.2478 | 6.5044 | 5.887 | 3.7926 | 2.4121 | 1.0485 | 10.08 | 11.8279 | 10.8312 | 9.75 | 8.7232 | 7.7162 | 6.7563 | 5.6582 | 4.4658 | 3.3009 | 2.3755 | -0.68715 | -2.5054 | -3.531
|  | CULLODEN | LW |  |  |  | 7.3634 | 8.4846 | 7.2852 | 5.8799 | 4.5952 | 3.1836 | 1.7426 | 0.48088 | -0.83611 | -2.1153 | -3.0158 | -5.4602 | -6.9438 | -8.137 | 9.848 | 11.5628 | 10.8855 | 10.042 | 9.2941 | 8.4449 | 7.6176 | 6.8674 | 6.0746 | 5.2967 | 4.7032 | 3.2302 | 2.2857 | 1.1945 | 9.5529 | 11.1032 | 10.051 | 8.8063 | 7.6485 | 6.3532 | 5.0463 | 3.9051 | 2.7095 | 1.5432 | 0.68354 | -1.6191 | -3.0623 | -4.3459
|  | CULLODEN | ST |  |  |  | 8.2101 | 9.7102 | 9.1465 | 8.5719 | 8.0585 | 7.5103 | 7.0166 | 6.4553 | 5.8619 | 5.2509 | 4.7731 | 1.9272 | 0.26753 | -1.6156 | 10.2915 | 12.2162 | 11.782 | 11.3492 | 10.973 | 10.5332 | 10.1786 | 9.7692 | 9.352 | 8.9133 | 8.5142 | 6.2706 | 4.8141 | 3.0724 | 10.3036 | 12.1992 | 11.7027 | 11.2025 | 10.7592 | 10.2521 | 9.8203 | 9.3198 | 8.7995 | 8.2571 | 7.7957 | 4.9725 | 3.3759 | 1.6789
|  | CULLODEN | FS |  |  |  | 8.7891 | 10.432 | 9.9412 | 9.4365 | 8.9541 | 8.4866 | 7.9915 | 7.4199 | 6.8362 | 6.2492 | 5.75 | 2.9099 | 0.59602 | -1.0625 | 10.8237 | 12.87 | 12.5258 | 12.1724 | 11.8336 | 11.5001 | 11.1458 | 10.7368 | 10.3135 | 9.8777 | 9.4658 | 7.1649 | 4.9645 | 2.6178 | 10.8317 | 12.8585 | 12.4494 | 12.0272 | 11.6212 | 11.2237 | 10.8016 | 10.3085 | 9.8043 | 9.2906 | 8.8276 | 6.1773 | 3.939 | 2.4983
| CRAIGIEBUCKLER | CULTER | MINIMUM HEADROOM | NJ 84009 00884 | NO | YES | 16.6327 | 16.2264 | 15.6835 | 15.1042 | 14.4876 | 13.7298 | 12.9448 | 12.2903 | 11.646 | 10.9722 | 10.3154 | 8.7233 | 8.1633 | 7.5282 | 17.8814 | 17.6439 | 17.3392 | 17.0052 | 16.6218 | 16.1248 | 15.6274 | 15.1954 | 14.7559 | 14.3179 | 13.893 | 12.8793 | 12.2629 | 11.4134 | 17.0914 | 16.7222 | 16.2277 | 15.6926 | 15.1112 | 14.3714 | 13.6087 | 12.9564 | 12.2997 | 11.6468 | 11.0132 | 9.4918 | 8.9354 | 8.2643
|  | CULTER | CT |  |  |  | 16.864 | 16.5783 | 16.0437 | 15.47 | 14.8846 | 14.2652 | 13.6919 | 13.1062 | 12.5082 | 11.9343 | 11.3309 | 9.3944 | 8.5448 | 8.0886 | 17.9563 | 17.7733 | 17.4653 | 17.1245 | 16.7458 | 16.3418 | 16.0061 | 15.6323 | 15.2332 | 14.8442 | 14.4375 | 13.0663 | 12.2629 | 11.4134 | 17.2802 | 17.021 | 16.5264 | 15.9881 | 15.4337 | 14.846 | 14.3222 | 13.7632 | 13.1734 | 12.601 | 12.0129 | 10.1734 | 9.3853 | 8.9536
|  | CULTER | LW |  |  |  | 16.6327 | 16.2264 | 15.6835 | 15.1042 | 14.4876 | 13.7298 | 12.9448 | 12.2903 | 11.646 | 10.9722 | 10.3154 | 8.7233 | 8.1633 | 7.5282 | 17.8814 | 17.6439 | 17.3392 | 17.0052 | 16.6218 | 16.1248 | 15.6274 | 15.1954 | 14.7559 | 14.3179 | 13.893 | 12.8793 | 12.4599 | 11.9115 | 17.0914 | 16.7222 | 16.2277 | 15.6926 | 15.1112 | 14.3714 | 13.6087 | 12.9564 | 12.2997 | 11.6468 | 11.0132 | 9.4918 | 8.9354 | 8.2643
|  | CULTER | ST |  |  |  | 17.0059 | 16.818 | 16.5887 | 16.3646 | 16.1387 | 15.8042 | 15.5251 | 15.2081 | 14.8982 | 14.548 | 14.1632 | 11.8953 | 10.8537 | 10.1108 | 18.0411 | 17.9264 | 17.7304 | 17.5477 | 17.371 | 17.0681 | 16.8459 | 16.5898 | 16.3428 | 16.0792 | 15.7828 | 14.0848 | 13.113 | 12.1257 | 17.4135 | 17.2553 | 17.0214 | 16.7963 | 16.5734 | 16.2188 | 15.9382 | 15.6146 | 15.2932 | 14.9514 | 14.5718 | 12.3713 | 11.3789 | 10.6853
|  | CULTER | FS |  |  |  | 17.0641 | 16.9253 | 16.7706 | 16.6104 | 16.4234 | 16.2289 | 16.0154 | 15.758 | 15.5096 | 15.2618 | 14.9967 | 13.1615 | 11.3504 | 10.2333 | 18.0671 | 17.9736 | 17.8637 | 17.7442 | 17.6069 | 17.4582 | 17.2956 | 17.1058 | 16.9159 | 16.7172 | 16.5001 | 15.0934 | 13.4372 | 11.7405 | 17.4632 | 17.3475 | 17.2057 | 17.0549 | 16.8795 | 16.6933 | 16.4878 | 16.2425 | 15.998 | 15.7468 | 15.4755 | 13.7172 | 11.9977 | 10.9746
| ELGIN | CUMMING STREET | MINIMUM HEADROOM | NJ 21542 63007 | NO | YES | 8.6687 | 8.4468 | 8.1607 | 7.8686 | 7.3429 | 6.6488 | 6.0423 | 5.5711 | 5.0651 | 4.5437 | 3.8747 | 1.9153 | 0.58094 | 0.2206 | 9.8171 | 9.6582 | 9.4461 | 9.2047 | 8.796 | 8.2282 | 7.602 | 7.0867 | 6.5203 | 5.9304 | 5.3709 | 3.8793 | 2.8138 | 2.5124 | 9.4644 | 9.1923 | 8.8472 | 8.5019 | 8.0404 | 7.4569 | 6.8628 | 6.3808 | 5.6973 | 4.9619 | 4.2647 | 2.4357 | 1.131 | 0.76899
|  | CUMMING STREET | CT |  |  |  | 8.6687 | 8.4468 | 8.1607 | 7.8686 | 7.4871 | 7.058 | 6.7136 | 6.3003 | 5.8674 | 5.3943 | 4.8254 | 2.9394 | 2.3059 | 1.771 | 9.8171 | 9.6582 | 9.4461 | 9.2047 | 8.8231 | 8.3006 | 7.914 | 7.4962 | 7.1285 | 6.768 | 6.3311 | 4.8898 | 4.6761 | 4.5369 | 9.4644 | 9.1923 | 8.8472 | 8.5019 | 8.0404 | 7.5198 | 7.1545 | 6.7701 | 6.3254 | 5.8691 | 5.3201 | 3.5019 | 2.9674 | 2.6255
|  | CUMMING STREET | LW |  |  |  | 8.705 | 8.5259 | 8.2692 | 7.9201 | 7.3429 | 6.6488 | 6.0423 | 5.5711 | 5.0651 | 4.5437 | 3.8747 | 2.1027 | 1.6857 | 1.4162 | 9.8477 | 9.7201 | 9.485 | 9.216 | 8.796 | 8.2282 | 7.602 | 7.0867 | 6.5203 | 5.9304 | 5.3709 | 3.9818 | 3.6811 | 3.4246 | 9.5148 | 9.2972 | 8.9884 | 8.634 | 8.1278 | 7.4569 | 6.8628 | 6.3808 | 5.6973 | 4.9619 | 4.2647 | 2.5337 | 2.1507 | 1.8443
|  | CUMMING STREET | ST |  |  |  | 8.7714 | 8.7054 | 8.4805 | 8.267 | 8.0556 | 7.6681 | 7.394 | 7.1116 | 6.7824 | 6.4022 | 5.7656 | 1.9153 | 0.58094 | 0.2206 | 9.8906 | 9.843 | 9.6127 | 9.4141 | 9.2328 | 8.8488 | 8.615 | 8.3575 | 7.9554 | 7.4605 | 6.892 | 3.8793 | 2.8138 | 2.5124 | 9.5943 | 9.5154 | 9.2418 | 8.9863 | 8.7335 | 8.2604 | 7.9249 | 7.5774 | 7.1729 | 6.7049 | 6.1634 | 2.4357 | 1.131 | 0.76899
|  | CUMMING STREET | FS |  |  |  | 8.7929 | 8.7447 | 8.6494 | 8.5339 | 8.3988 | 8.2449 | 8.0848 | 7.9286 | 7.7503 | 7.5493 | 7.3218 | 5.1407 | 2.5857 | 0.92227 | 9.9054 | 9.8702 | 9.7879 | 9.6918 | 9.5792 | 9.4528 | 9.3221 | 9.201 | 9.0646 | 8.8872 | 8.6225 | 6.6236 | 4.6468 | 3.3483 | 9.6206 | 9.5638 | 9.4515 | 9.3176 | 9.1595 | 8.9787 | 8.7856 | 8.595 | 8.3771 | 8.1308 | 7.8516 | 5.6856 | 3.2248 | 1.6259
| ST FILLANS | DALCHONZIE | MINIMUM HEADROOM | NN 74079 21921 | YES | NO | 5.0909 | 4.9834 | 4.8205 | 4.6426 | 4.4702 | 4.2766 | 4.0747 | 3.89 | 3.7007 | 3.5072 | 3.321 | 2.8244 | 2.4841 | 2.2807 | 5.4209 | 5.357 | 5.2728 | 5.1792 | 5.068 | 4.9549 | 4.8628 | 4.7433 | 4.6105 | 4.4718 | 4.3433 | 3.964 | 3.7245 | 3.506 | 4.9524 | 4.8549 | 4.7099 | 4.5509 | 4.3979 | 4.2206 | 4.0338 | 3.8588 | 3.6786 | 3.4946 | 3.3182 | 2.8213 | 2.5029 | 2.3033
|  | DALCHONZIE | CT |  |  |  | 5.1751 | 5.0989 | 4.9185 | 4.7284 | 4.5403 | 4.3649 | 4.2101 | 4.0276 | 3.8158 | 3.6031 | 3.4052 | 2.8244 | 2.4841 | 2.2807 | 5.4483 | 5.4045 | 5.299 | 5.1852 | 5.068 | 4.9549 | 4.8645 | 4.749 | 4.6105 | 4.4718 | 4.3433 | 3.964 | 3.7245 | 3.506 | 5.0267 | 4.957 | 4.7922 | 4.6173 | 4.4412 | 4.2742 | 4.1315 | 3.9596 | 3.7584 | 3.5568 | 3.3692 | 2.8213 | 2.5029 | 2.3033
|  | DALCHONZIE | LW |  |  |  | 5.0909 | 4.9834 | 4.8205 | 4.6426 | 4.4702 | 4.2766 | 4.0747 | 3.89 | 3.7007 | 3.5072 | 3.321 | 2.8724 | 2.605 | 2.4181 | 5.4209 | 5.357 | 5.2728 | 5.1792 | 5.0906 | 4.9807 | 4.8628 | 4.7433 | 4.6185 | 4.4911 | 4.37 | 4.1003 | 3.9027 | 3.7082 | 4.9524 | 4.8549 | 4.7099 | 4.5509 | 4.3979 | 4.2206 | 4.0338 | 3.8588 | 3.6786 | 3.4946 | 3.3182 | 2.9013 | 2.6322 | 2.4182
|  | DALCHONZIE | ST |  |  |  | 5.2202 | 5.1894 | 5.1233 | 5.0609 | 4.9992 | 4.9182 | 4.8555 | 4.765 | 4.6793 | 4.582 | 4.4727 | 3.8297 | 3.4434 | 3.072 | 5.4651 | 5.4519 | 5.4048 | 5.3553 | 5.3084 | 5.234 | 5.1829 | 5.1043 | 5.0354 | 4.9589 | 4.8704 | 4.3807 | 4.0855 | 3.7874 | 5.0677 | 5.0411 | 4.9757 | 4.9151 | 4.8567 | 4.7715 | 4.7093 | 4.6163 | 4.5317 | 4.4362 | 4.3274 | 3.6982 | 3.3245 | 2.9711
|  | DALCHONZIE | FS |  |  |  | 5.2269 | 5.1975 | 5.1518 | 5.1037 | 5.0493 | 5.0001 | 4.9488 | 4.8771 | 4.8046 | 4.7262 | 4.6392 | 4.0984 | 3.5716 | 3.267 | 5.4683 | 5.4574 | 5.4331 | 5.3995 | 5.362 | 5.3258 | 5.2878 | 5.2348 | 5.1812 | 5.1227 | 5.0578 | 4.6682 | 4.2534 | 3.9393 | 5.0739 | 5.0486 | 5.0073 | 4.9633 | 4.9138 | 4.8673 | 4.8183 | 4.7491 | 4.6794 | 4.6039 | 4.5204 | 4.0081 | 3.5121 | 3.2384
| NAIRN | DALCROSS | MINIMUM HEADROOM | NH 76333 51847 | NO | YES | 9.1327 | 8.7188 | 8.0627 | 7.1886 | 6.1156 | 4.8983 | 3.9451 | 3.3423 | 2.7214 | 2.0841 | 1.7842 | 0.8165 | 0.54088 | 0.44631 | 9.5586 | 9.3165 | 8.7619 | 8.0236 | 6.9891 | 5.8486 | 5.0763 | 4.7051 | 4.3186 | 3.94 | 3.6888 | 2.7996 | 2.5256 | 2.4543 | 8.5159 | 8.1365 | 7.6373 | 6.8297 | 5.7549 | 4.5606 | 3.7241 | 3.2824 | 2.8151 | 2.3463 | 2.0009 | 0.75975 | 0.44037 | 0.36497
|  | DALCROSS | CT |  |  |  | 9.2161 | 8.8135 | 8.3689 | 7.8325 | 7.1121 | 6.3103 | 5.7181 | 5.2032 | 4.6451 | 4.065 | 3.7719 | 2.9411 | 2.647 | 2.5093 | 9.5826 | 9.3446 | 9.0838 | 8.748 | 8.1692 | 7.5404 | 7.216 | 6.9343 | 6.6366 | 6.3246 | 6.1047 | 5.2843 | 5.1155 | 5.0433 | 8.5159 | 8.1365 | 7.7818 | 7.3413 | 6.677 | 5.9524 | 5.5176 | 5.1484 | 4.8077 | 4.4598 | 4.1679 | 3.2456 | 3.0446 | 2.9527
|  | DALCROSS | LW |  |  |  | 9.1327 | 8.7188 | 8.0627 | 7.1886 | 6.1156 | 4.8983 | 3.9451 | 3.3423 | 2.7214 | 2.0841 | 1.7842 | 0.8165 | 0.54088 | 0.44631 | 9.5586 | 9.3165 | 8.7619 | 8.0236 | 6.9891 | 5.8486 | 5.0763 | 4.7051 | 4.3186 | 3.94 | 3.6888 | 2.7996 | 2.5256 | 2.4543 | 8.5301 | 8.2208 | 7.6373 | 6.8297 | 5.7549 | 4.5606 | 3.7241 | 3.2824 | 2.8151 | 2.3463 | 2.0009 | 0.75975 | 0.44037 | 0.36497
|  | DALCROSS | ST |  |  |  | 9.264 | 8.9433 | 8.4017 | 7.9161 | 7.546 | 6.8306 | 6.4174 | 6.0141 | 5.6412 | 5.2342 | 4.9594 | 3.7295 | 3.3698 | 3.219 | 9.6033 | 9.411 | 8.9157 | 8.5075 | 8.2274 | 7.5378 | 7.2381 | 6.9669 | 6.75 | 6.5184 | 6.3113 | 4.9292 | 4.5008 | 4.3931 | 8.5702 | 8.3351 | 7.8084 | 7.3554 | 7.0355 | 6.2952 | 5.934 | 5.5897 | 5.2815 | 4.9411 | 4.607 | 2.9747 | 2.4592 | 2.3334
|  | DALCROSS | FS |  |  |  | 9.6219 | 9.3505 | 9.0679 | 8.7772 | 8.4741 | 8.1436 | 7.8079 | 7.4829 | 7.1594 | 6.817 | 6.5737 | 5.5223 | 4.8474 | 4.5338 | 9.8605 | 9.6931 | 9.4982 | 9.297 | 9.0823 | 8.8534 | 8.6283 | 8.427 | 8.2315 | 8.0259 | 7.8541 | 7.0979 | 6.3249 | 5.8248 | 8.908 | 8.7046 | 8.501 | 8.2796 | 8.0375 | 7.7773 | 7.5157 | 7.2722 | 7.0276 | 6.7656 | 6.513 | 5.3486 | 4.3788 | 3.7499
| TAYNUILT | DALMALLY | MINIMUM HEADROOM | NN 15538 26930 | YES | YES | 0.75231 | 0.7193 | 0.6892 | 0.66764 | 0.6495 | 0.62991 | 0.60812 | 0.59737 | 0.58747 | 0.57309 | 0.56516 | 0.53937 | 0.51131 | 0.50133 | 0.83025 | 0.81422 | 0.79953 | 0.78963 | 0.78156 | 0.77166 | 0.76048 | 0.75286 | 0.74525 | 0.73647 | 0.72931 | 0.71272 | 0.69564 | 0.6803 | 0.79151 | 0.7644 | 0.73992 | 0.72092 | 0.70476 | 0.68695 | 0.66707 | 0.65674 | 0.64707 | 0.63405 | 0.62571 | 0.6016 | 0.57707 | 0.56813
|  | DALMALLY | CT |  |  |  | 0.76485 | 0.74302 | 0.70651 | 0.68308 | 0.66219 | 0.63802 | 0.61207 | 0.59984 | 0.58802 | 0.57309 | 0.56516 | 0.54372 | 0.51131 | 0.50133 | 0.83528 | 0.82376 | 0.80602 | 0.79459 | 0.78505 | 0.77405 | 0.76228 | 0.75455 | 0.7461 | 0.73647 | 0.72996 | 0.71272 | 0.69564 | 0.68252 | 0.80207 | 0.78454 | 0.75384 | 0.73291 | 0.71438 | 0.69314 | 0.67038 | 0.65932 | 0.6481 | 0.63405 | 0.62623 | 0.60572 | 0.57707 | 0.56813
|  | DALMALLY | LW |  |  |  | 0.75231 | 0.7193 | 0.6892 | 0.66764 | 0.6495 | 0.62991 | 0.60812 | 0.59737 | 0.58747 | 0.57594 | 0.56538 | 0.53937 | 0.52274 | 0.51719 | 0.83025 | 0.81422 | 0.79953 | 0.78963 | 0.78156 | 0.77166 | 0.76048 | 0.75286 | 0.74525 | 0.73698 | 0.72931 | 0.71404 | 0.70771 | 0.70582 | 0.79151 | 0.7644 | 0.73992 | 0.72092 | 0.70476 | 0.68695 | 0.66707 | 0.65674 | 0.64707 | 0.63593 | 0.62571 | 0.6016 | 0.58689 | 0.58203
|  | DALMALLY | ST |  |  |  | 0.77289 | 0.75324 | 0.73391 | 0.72303 | 0.71268 | 0.70423 | 0.69347 | 0.68024 | 0.66908 | 0.65777 | 0.64426 | 0.58784 | 0.56002 | 0.54192 | 0.83866 | 0.82887 | 0.81911 | 0.81386 | 0.80877 | 0.80394 | 0.79793 | 0.79069 | 0.784 | 0.77696 | 0.76884 | 0.7299 | 0.71251 | 0.69772 | 0.80923 | 0.79385 | 0.77864 | 0.76913 | 0.75998 | 0.75261 | 0.74322 | 0.73152 | 0.72129 | 0.71076 | 0.69818 | 0.64289 | 0.61845 | 0.60352
|  | DALMALLY | FS |  |  |  | 0.78358 | 0.76468 | 0.74491 | 0.73772 | 0.7287 | 0.71935 | 0.71183 | 0.69879 | 0.68922 | 0.67701 | 0.66875 | 0.59541 | 0.55039 | 0.53346 | 0.84298 | 0.83357 | 0.82371 | 0.81984 | 0.81535 | 0.81057 | 0.80634 | 0.79979 | 0.7943 | 0.7876 | 0.78217 | 0.73983 | 0.70428 | 0.6803 | 0.81695 | 0.8029 | 0.78803 | 0.782 | 0.77424 | 0.76615 | 0.75957 | 0.74803 | 0.73945 | 0.7285 | 0.7209 | 0.65362 | 0.61111 | 0.59644
| TAYNUILT | DALMALLY SCHOOL | MINIMUM HEADROOM | NN 17249 27128 | YES | YES | 0.3717 | 0.3717 | 0.35888 | 0.35022 | 0.34449 | 0.32482 | 0.31934 | 0.30454 | 0.2993 | 0.29485 | 0.28775 | 0.25446 | 0.2056 | 0.15545 | 0.34335 | 0.34335 | 0.32733 | 0.3165 | 0.30934 | 0.28475 | 0.27791 | 0.25941 | 0.25285 | 0.24729 | 0.23842 | 0.1968 | 0.13572 | 0.073038 | 0.34335 | 0.34335 | 0.32733 | 0.3165 | 0.30934 | 0.28475 | 0.27791 | 0.25941 | 0.25285 | 0.24729 | 0.23842 | 0.1968 | 0.13572 | 0.073038
|  | DALMALLY SCHOOL | CT |  |  |  | 0.3717 | 0.3717 | 0.37003 | 0.36707 | 0.35282 | 0.33762 | 0.33377 | 0.32704 | 0.32029 | 0.31445 | 0.30804 | 0.27396 | 0.24182 | 0.20713 | 0.34335 | 0.34335 | 0.34126 | 0.33756 | 0.31975 | 0.30076 | 0.29594 | 0.28753 | 0.27909 | 0.27179 | 0.26377 | 0.22118 | 0.181 | 0.13763 | 0.34335 | 0.34335 | 0.34126 | 0.33756 | 0.31975 | 0.30076 | 0.29594 | 0.28753 | 0.27909 | 0.27179 | 0.26377 | 0.22118 | 0.181 | 0.13763
|  | DALMALLY SCHOOL | LW |  |  |  | 0.3717 | 0.3717 | 0.3717 | 0.3717 | 0.3717 | 0.3717 | 0.3717 | 0.36907 | 0.36634 | 0.36409 | 0.36157 | 0.34827 | 0.28862 | 0.2012 | 0.34335 | 0.34335 | 0.34335 | 0.34335 | 0.34335 | 0.34335 | 0.34335 | 0.34006 | 0.33665 | 0.33384 | 0.33068 | 0.31407 | 0.2395 | 0.13023 | 0.34335 | 0.34335 | 0.34335 | 0.34335 | 0.34335 | 0.34335 | 0.34335 | 0.34006 | 0.33665 | 0.33384 | 0.33068 | 0.31407 | 0.2395 | 0.13023
|  | DALMALLY SCHOOL | ST |  |  |  | 0.3717 | 0.3717 | 0.35888 | 0.35022 | 0.34449 | 0.32482 | 0.31934 | 0.30454 | 0.2993 | 0.29485 | 0.28775 | 0.25446 | 0.2056 | 0.15545 | 0.34335 | 0.34335 | 0.32733 | 0.3165 | 0.30934 | 0.28475 | 0.27791 | 0.25941 | 0.25285 | 0.24729 | 0.23842 | 0.1968 | 0.13572 | 0.073038 | 0.34335 | 0.34335 | 0.32733 | 0.3165 | 0.30934 | 0.28475 | 0.27791 | 0.25941 | 0.25285 | 0.24729 | 0.23842 | 0.1968 | 0.13572 | 0.073038
|  | DALMALLY SCHOOL | FS |  |  |  | 0.3717 | 0.3717 | 0.36908 | 0.36646 | 0.3634 | 0.36035 | 0.35773 | 0.35237 | 0.34874 | 0.34511 | 0.34147 | 0.33707 | 0.33402 | 0.32841 | 0.34335 | 0.34335 | 0.34007 | 0.3368 | 0.33298 | 0.32916 | 0.32589 | 0.31919 | 0.31465 | 0.31011 | 0.30557 | 0.30006 | 0.29625 | 0.28924 | 0.34335 | 0.34335 | 0.34007 | 0.3368 | 0.33298 | 0.32916 | 0.32589 | 0.31919 | 0.31465 | 0.31011 | 0.30557 | 0.30006 | 0.29625 | 0.28924
| INVERNESS | DALNEIGH | MINIMUM HEADROOM | NH 65564 44955 | YES | YES | 4.2306 | 3.7747 | 2.9379 | 2.0916 | 1.2177 | 0.13179 | -0.97418 | -1.915 | -2.91 | -3.9235 | -4.8828 | -7.7032 | -9.2976 | -10.3923 | 6.4655 | 6.2037 | 5.7419 | 5.2614 | 4.7251 | 4.0358 | 3.3664 | 2.784 | 2.1617 | 1.5204 | 0.87719 | -0.79441 | -1.9659 | -3.7643 | 5.9137 | 5.505 | 4.7757 | 3.9803 | 3.1379 | 2.0834 | 1.0255 | 0.12279 | -0.83446 | -1.8083 | -2.7308 | -5.3838 | -6.916 | -8.0866
|  | DALNEIGH | CT |  |  |  | 4.6743 | 4.3698 | 3.5719 | 2.7652 | 2.019 | 1.2562 | 0.53373 | -0.34004 | -1.3167 | -2.2934 | -3.2415 | -6.5659 | -8.9008 | -10.268 | 6.6469 | 6.4351 | 5.9805 | 5.5092 | 5.0466 | 4.5713 | 4.1571 | 3.6402 | 3.0471 | 2.4501 | 1.8659 | -0.259 | -1.9659 | -3.7643 | 6.2659 | 5.9846 | 5.2848 | 4.5641 | 3.8791 | 3.1534 | 2.4845 | 1.6678 | 0.74671 | -0.17455 | -1.0687 | -4.1497 | -6.2659 | -7.4972
|  | DALNEIGH | LW |  |  |  | 4.2306 | 3.7747 | 2.9379 | 2.0916 | 1.2177 | 0.13179 | -0.97418 | -1.915 | -2.91 | -3.9235 | -4.8828 | -7.7032 | -9.2976 | -10.3923 | 6.4655 | 6.2037 | 5.7419 | 5.2614 | 4.7251 | 4.0358 | 3.3664 | 2.784 | 2.1617 | 1.5204 | 0.87719 | -0.79441 | -1.7698 | -2.754 | 5.9137 | 5.505 | 4.7757 | 3.9803 | 3.1379 | 2.0834 | 1.0255 | 0.12279 | -0.83446 | -1.8083 | -2.7308 | -5.3838 | -6.916 | -8.0866
|  | DALNEIGH | ST |  |  |  | 4.903 | 4.7943 | 4.5941 | 4.4124 | 4.2261 | 3.9338 | 3.672 | 3.3413 | 2.9786 | 2.5709 | 2.1084 | -0.89412 | -2.7569 | -4.9118 | 6.76 | 6.6707 | 6.4795 | 6.3085 | 6.1366 | 5.8539 | 5.6307 | 5.3456 | 5.049 | 4.7164 | 4.3354 | 1.8655 | 0.15814 | -1.9485 | 6.4589 | 6.3588 | 6.1508 | 5.959 | 5.766 | 5.4492 | 5.1817 | 4.8418 | 4.4756 | 4.0641 | 3.5952 | 0.66666 | -1.0483 | -2.9394
|  | DALNEIGH | FS |  |  |  | 4.9547 | 4.8529 | 4.6764 | 4.5092 | 4.3244 | 4.1215 | 3.8945 | 3.5918 | 3.2653 | 2.9097 | 2.532 | -0.12293 | -2.8255 | -4.7471 | 6.8126 | 6.7277 | 6.5923 | 6.4578 | 6.3082 | 6.14 | 5.9526 | 5.7095 | 5.445 | 5.1518 | 4.8313 | 2.6283 | -0.21846 | -3.5 | 6.5072 | 6.4156 | 6.256 | 6.0979 | 5.9228 | 5.7285 | 5.5106 | 5.2263 | 4.919 | 4.5825 | 4.222 | 1.7505 | -0.77579 | -2.5056
| COUPAR ANGUS | DALRULZION | MINIMUM HEADROOM | NO 13498 58153 | YES | YES | 0.77454 | 0.70842 | 0.64767 | 0.57492 | 0.4886 | 0.39058 | 0.30705 | 0.24249 | 0.15789 | 0.076981 | 0.0058932 | -0.15578 | -0.28197 | -0.36139 | 1.3695 | 1.3364 | 1.3065 | 1.2513 | 1.194 | 1.1328 | 1.0873 | 1.0365 | 0.96993 | 0.90464 | 0.84631 | 0.6969 | 0.59917 | 0.4918 | 0.84837 | 0.79996 | 0.75508 | 0.70108 | 0.63719 | 0.55147 | 0.48197 | 0.43875 | 0.39123 | 0.34847 | 0.29719 | 0.15155 | 0.031514 | -0.079178
|  | DALRULZION | CT |  |  |  | 0.81921 | 0.77228 | 0.67771 | 0.57955 | 0.4886 | 0.39058 | 0.30705 | 0.24249 | 0.15789 | 0.076981 | 0.0058932 | -0.15578 | -0.28197 | -0.36139 | 1.3858 | 1.3601 | 1.3076 | 1.2513 | 1.194 | 1.1328 | 1.0873 | 1.0365 | 0.96993 | 0.90464 | 0.84631 | 0.6969 | 0.59917 | 0.50345 | 0.89008 | 0.85673 | 0.78692 | 0.71712 | 0.63719 | 0.55147 | 0.48197 | 0.43875 | 0.39123 | 0.34847 | 0.29719 | 0.15155 | 0.031514 | -0.048274
|  | DALRULZION | LW |  |  |  | 0.77454 | 0.70842 | 0.64767 | 0.57492 | 0.50907 | 0.42589 | 0.32748 | 0.25153 | 0.17169 | 0.089587 | 0.014772 | -0.12151 | -0.22581 | -0.33869 | 1.3695 | 1.3364 | 1.3065 | 1.2689 | 1.2363 | 1.1869 | 1.1285 | 1.0709 | 1.0095 | 0.9471 | 0.89001 | 0.79132 | 0.69486 | 0.57239 | 0.84837 | 0.79996 | 0.75508 | 0.70108 | 0.64875 | 0.59605 | 0.53276 | 0.48129 | 0.42398 | 0.36427 | 0.30834 | 0.17213 | 0.05582 | -0.079178
|  | DALRULZION | ST |  |  |  | 0.85867 | 0.83652 | 0.79577 | 0.75663 | 0.71758 | 0.65955 | 0.61396 | 0.55025 | 0.48803 | 0.41947 | 0.34851 | -0.010527 | -0.16812 | -0.27389 | 1.4024 | 1.3915 | 1.361 | 1.3324 | 1.3053 | 1.2564 | 1.2232 | 1.1719 | 1.1269 | 1.0777 | 1.0226 | 0.74187 | 0.60569 | 0.4918 | 0.93008 | 0.9137 | 0.87737 | 0.84688 | 0.81773 | 0.76849 | 0.73817 | 0.68827 | 0.6375 | 0.58215 | 0.52408 | 0.21957 | 0.04178 | -0.076755
|  | DALRULZION | FS |  |  |  | 0.86861 | 0.85596 | 0.82962 | 0.79744 | 0.76549 | 0.7312 | 0.69587 | 0.6527 | 0.60372 | 0.55117 | 0.50165 | 0.16461 | -0.076325 | -0.14834 | 1.406 | 1.3989 | 1.3839 | 1.3656 | 1.3457 | 1.3236 | 1.3003 | 1.27 | 1.2376 | 1.2024 | 1.1664 | 0.94553 | 0.75911 | 0.67934 | 0.93813 | 0.93013 | 0.90909 | 0.88413 | 0.8602 | 0.83491 | 0.81074 | 0.7811 | 0.74797 | 0.71068 | 0.67181 | 0.40802 | 0.22206 | 0.10809
| BOAT OF GARTEN | DALWHINNIE | MINIMUM HEADROOM | NN 63711 84671 | YES | YES | 0.27488 | 0.26928 | 0.26116 | 0.22997 | 0.20176 | 0.16728 | 0.12443 | 0.10165 | 0.078155 | 0.050243 | 0.028276 | -0.025861 | -0.071818 | -0.091472 | 0.42481 | 0.4127 | 0.40082 | 0.38638 | 0.37282 | 0.35697 | 0.33608 | 0.31929 | 0.30137 | 0.28211 | 0.26555 | 0.23766 | 0.21803 | 0.20503 | 0.32483 | 0.30234 | 0.27857 | 0.24981 | 0.22637 | 0.19466 | 0.15766 | 0.13431 | 0.10986 | 0.082077 | 0.059363 | 0.01187 | -0.021549 | -0.037224
|  | DALWHINNIE | CT |  |  |  | 0.27488 | 0.26928 | 0.26116 | 0.24378 | 0.21371 | 0.17274 | 0.13541 | 0.11734 | 0.091816 | 0.067095 | 0.042783 | -0.0090138 | -0.071818 | -0.091472 | 0.43222 | 0.4228 | 0.40554 | 0.38682 | 0.37282 | 0.35702 | 0.34219 | 0.32933 | 0.31092 | 0.29255 | 0.27586 | 0.24104 | 0.21803 | 0.20503 | 0.34468 | 0.32767 | 0.29506 | 0.25963 | 0.23124 | 0.19874 | 0.16887 | 0.15072 | 0.12477 | 0.099153 | 0.075169 | 0.025592 | -0.021549 | -0.037224
|  | DALWHINNIE | LW |  |  |  | 0.27527 | 0.26937 | 0.2623 | 0.22997 | 0.20176 | 0.16728 | 0.12443 | 0.10165 | 0.078155 | 0.050243 | 0.028276 | -0.025861 | -0.060099 | -0.073674 | 0.42481 | 0.4127 | 0.40082 | 0.38638 | 0.37478 | 0.35697 | 0.33608 | 0.31929 | 0.30137 | 0.28211 | 0.26555 | 0.23766 | 0.22747 | 0.22378 | 0.32483 | 0.30234 | 0.27857 | 0.24981 | 0.22637 | 0.19466 | 0.15766 | 0.13431 | 0.10986 | 0.082077 | 0.059363 | 0.01187 | -0.013521 | -0.023316
|  | DALWHINNIE | ST |  |  |  | 0.27815 | 0.27639 | 0.27395 | 0.27084 | 0.26725 | 0.26278 | 0.25456 | 0.23874 | 0.21803 | 0.19425 | 0.16791 | 0.040328 | -0.023708 | -0.055582 | 0.4357 | 0.43202 | 0.42573 | 0.41792 | 0.41164 | 0.40297 | 0.39208 | 0.38182 | 0.36878 | 0.3543 | 0.33854 | 0.25982 | 0.23269 | 0.21822 | 0.35101 | 0.34393 | 0.33111 | 0.31568 | 0.3045 | 0.28879 | 0.26879 | 0.25229 | 0.23113 | 0.20792 | 0.18334 | 0.063471 | 0.01283 | -0.010366
|  | DALWHINNIE | FS |  |  |  | 0.27871 | 0.27735 | 0.27543 | 0.27311 | 0.27047 | 0.26739 | 0.2638 | 0.25958 | 0.24576 | 0.22635 | 0.20629 | 0.053457 | -0.040035 | -0.075134 | 0.43837 | 0.43555 | 0.43079 | 0.42475 | 0.4186 | 0.41229 | 0.40471 | 0.39629 | 0.38598 | 0.37495 | 0.36346 | 0.28625 | 0.2279 | 0.20852 | 0.3577 | 0.35294 | 0.34297 | 0.33107 | 0.31891 | 0.30728 | 0.29348 | 0.27847 | 0.25971 | 0.2404 | 0.2209 | 0.088359 | 0.0018446 | -0.024303
| WILLOWDALE | DENBURN | MINIMUM HEADROOM | NJ 93484 06342 | NO | NO | 7.128 | 6.9024 | 6.471 | 6.029 | 5.5789 | 5.0387 | 4.4536 | 4.0275 | 3.5686 | 3.046 | 2.4609 | 0.87683 | -0.018997 | -1.3477 | 10.5639 | 10.4267 | 10.2625 | 9.9963 | 9.6688 | 9.3089 | 8.9631 | 8.598 | 8.2349 | 7.868 | 7.4309 | 5.2857 | 3.1291 | -2.5216 | 8.1136 | 7.9603 | 7.774 | 7.4976 | 7.0957 | 6.5837 | 5.9174 | 5.3439 | 4.7194 | 4.0795 | 3.4571 | 1.8192 | 0.86692 | -0.61151
|  | DENBURN | CT |  |  |  | 7.201 | 7.0423 | 6.698 | 6.205 | 5.7163 | 5.2123 | 4.7276 | 4.3278 | 3.946 | 3.5688 | 3.1285 | 1.2244 | -0.018997 | -0.72887 | 10.5639 | 10.4267 | 10.2625 | 9.9963 | 9.6688 | 9.3089 | 8.9631 | 8.598 | 8.2349 | 7.868 | 7.4309 | 5.2857 | 3.2293 | 0.37813 | 8.1136 | 7.9603 | 7.774 | 7.5874 | 7.1752 | 6.7016 | 6.2497 | 5.7896 | 5.3245 | 4.8642 | 4.3215 | 2.2863 | 1.1119 | 0.38621
|  | DENBURN | LW |  |  |  | 7.128 | 6.9024 | 6.471 | 6.029 | 5.5789 | 5.0387 | 4.4536 | 4.0275 | 3.5686 | 3.046 | 2.4609 | 0.87683 | 0.024506 | -1.3477 | 10.613 | 10.5215 | 10.4121 | 10.192 | 9.9673 | 9.6634 | 9.298 | 8.9341 | 8.5373 | 8.1179 | 7.6427 | 6.4072 | 5.5785 | 4.2241 | 8.1464 | 8.0326 | 7.8839 | 7.4976 | 7.0957 | 6.5837 | 5.9174 | 5.3439 | 4.7194 | 4.0795 | 3.4571 | 1.8192 | 0.86692 | -0.61151
|  | DENBURN | ST |  |  |  | 7.277 | 7.2361 | 7.1472 | 7.0556 | 6.9559 | 6.7952 | 6.6509 | 6.4099 | 6.1895 | 5.9435 | 5.6506 | 4.1129 | 2.9927 | 1.6235 | 10.6232 | 10.5777 | 10.4776 | 10.379 | 10.2758 | 10.1042 | 9.9621 | 9.7118 | 9.5006 | 9.2266 | 8.8738 | 6.5604 | 4.2333 | 1.0367 | 8.1884 | 8.1491 | 8.0531 | 7.9576 | 7.8563 | 7.6846 | 7.5399 | 7.2817 | 7.0585 | 6.8117 | 6.5155 | 4.4648 | 3.2388 | 2.4935
|  | DENBURN | FS |  |  |  | 7.2905 | 7.2612 | 7.2147 | 7.1595 | 7.0938 | 7.0164 | 6.9272 | 6.8023 | 6.672 | 6.527 | 6.3656 | 5.0216 | 3.4509 | 1.9817 | 10.6291 | 10.5893 | 10.5318 | 10.4647 | 10.3863 | 10.2947 | 10.1519 | 9.9159 | 9.6592 | 9.3705 | 9.0482 | 6.772 | 3.1291 | -2.5216 | 8.2011 | 8.1729 | 8.1262 | 8.0709 | 8.005 | 7.9275 | 7.8387 | 7.7087 | 7.5761 | 7.4292 | 7.266 | 6.0511 | 4.3171 | 2.9632
| TAYNUILT | DERVAIG | MINIMUM HEADROOM | NM 42441 51227 | YES | YES | 1.2478 | 1.1968 | 1.1229 | 1.0523 | 0.97574 | 0.8902 | 0.80169 | 0.77091 | 0.72796 | 0.66688 | 0.60721 | 0.4892 | 0.44226 | 0.41041 | 1.9596 | 1.924 | 1.8854 | 1.842 | 1.7996 | 1.7553 | 1.6925 | 1.6369 | 1.5758 | 1.5133 | 1.4549 | 1.3537 | 1.3343 | 1.306 | 1.7745 | 1.7532 | 1.7168 | 1.6632 | 1.604 | 1.5361 | 1.4657 | 1.4455 | 1.4063 | 1.3117 | 1.2226 | 1.0649 | 1.03 | 0.98605
|  | DERVAIG | CT |  |  |  | 1.2915 | 1.2488 | 1.1599 | 1.0622 | 0.97574 | 0.8902 | 0.80169 | 0.77091 | 0.737 | 0.70055 | 0.65276 | 0.5601 | 0.47834 | 0.44176 | 1.976 | 1.9486 | 1.8976 | 1.842 | 1.7996 | 1.7559 | 1.7114 | 1.6713 | 1.6204 | 1.5684 | 1.5189 | 1.4087 | 1.3653 | 1.3326 | 1.794 | 1.7786 | 1.7355 | 1.6726 | 1.604 | 1.5361 | 1.4657 | 1.4455 | 1.4267 | 1.3923 | 1.3187 | 1.1611 | 1.0969 | 1.0669
|  | DERVAIG | LW |  |  |  | 1.2478 | 1.1968 | 1.1229 | 1.0523 | 0.98774 | 0.90322 | 0.81624 | 0.77586 | 0.72796 | 0.66688 | 0.60721 | 0.4892 | 0.44226 | 0.41041 | 1.9596 | 1.924 | 1.8854 | 1.8458 | 1.811 | 1.7553 | 1.6925 | 1.6369 | 1.5758 | 1.5133 | 1.4549 | 1.3537 | 1.3343 | 1.306 | 1.7745 | 1.7532 | 1.7168 | 1.6632 | 1.6123 | 1.5491 | 1.4851 | 1.4589 | 1.4063 | 1.3117 | 1.2226 | 1.0649 | 1.03 | 0.98605
|  | DERVAIG | ST |  |  |  | 1.3331 | 1.3174 | 1.3019 | 1.276 | 1.2613 | 1.2378 | 1.2078 | 1.1705 | 1.1323 | 1.0884 | 1.0406 | 0.80351 | 0.73262 | 0.68704 | 1.9911 | 1.9789 | 1.9652 | 1.9471 | 1.9306 | 1.909 | 1.8829 | 1.8516 | 1.8157 | 1.7748 | 1.7296 | 1.5014 | 1.4428 | 1.4118 | 1.7966 | 1.7949 | 1.7932 | 1.7911 | 1.7894 | 1.7869 | 1.7795 | 1.7473 | 1.713 | 1.6739 | 1.6308 | 1.3438 | 1.2658 | 1.236
|  | DERVAIG | FS |  |  |  | 1.3423 | 1.3277 | 1.3033 | 1.2829 | 1.2564 | 1.2342 | 1.21 | 1.1819 | 1.152 | 1.1201 | 1.0895 | 0.85251 | 0.65298 | 0.57392 | 1.9956 | 1.9845 | 1.9692 | 1.9542 | 1.9372 | 1.9198 | 1.8999 | 1.8768 | 1.8512 | 1.823 | 1.7928 | 1.591 | 1.4215 | 1.3567 | 1.7975 | 1.7958 | 1.7938 | 1.7922 | 1.7903 | 1.7885 | 1.784 | 1.7603 | 1.7342 | 1.7066 | 1.6785 | 1.4761 | 1.2261 | 1.1558
| BEAULY | DINGWALL | MINIMUM HEADROOM | NH 53956 59680 | NO | YES | 5.7142 | 5.4337 | 4.9483 | 4.3884 | 3.7499 | 2.9166 | 2.1048 | 1.57 | 1.0473 | 0.51603 | 0.0021297 | -1.5355 | -2.1858 | -2.5735 | 7.5823 | 7.3895 | 7.0637 | 6.6816 | 6.196 | 5.5503 | 4.957 | 4.5331 | 4.0969 | 3.6496 | 3.2234 | 2.1815 | 1.8275 | 1.5743 | 7.2312 | 7.0269 | 6.7235 | 6.3473 | 5.8098 | 5.0899 | 4.416 | 3.9352 | 3.4354 | 2.9141 | 2.4062 | 0.94911 | 0.37911 | 0.026148
|  | DINGWALL | CT |  |  |  | 5.9037 | 5.7149 | 5.2394 | 4.7057 | 4.151 | 3.5214 | 2.9462 | 2.4598 | 1.9669 | 1.4775 | 0.97962 | -0.56679 | -1.5789 | -2.0378 | 7.6575 | 7.4944 | 7.1846 | 6.826 | 6.4309 | 5.9895 | 5.6342 | 5.2911 | 4.9107 | 4.5273 | 4.1417 | 2.9967 | 2.3302 | 1.743 | 7.2312 | 7.0269 | 6.7235 | 6.3653 | 5.9322 | 5.45 | 4.9819 | 4.5566 | 4.1805 | 3.8065 | 3.3534 | 1.9287 | 1.1967 | 0.78199
|  | DINGWALL | LW |  |  |  | 5.7142 | 5.4337 | 4.9483 | 4.3884 | 3.7499 | 2.9166 | 2.1048 | 1.57 | 1.0473 | 0.51603 | 0.0021297 | -1.5355 | -2.1858 | -2.5735 | 7.5823 | 7.3895 | 7.0637 | 6.6816 | 6.196 | 5.5503 | 4.957 | 4.5331 | 4.0969 | 3.6496 | 3.2234 | 2.1815 | 1.8275 | 1.5743 | 7.2442 | 7.0582 | 6.7287 | 6.3473 | 5.8098 | 5.0899 | 4.416 | 3.9352 | 3.4354 | 2.9141 | 2.4062 | 0.94911 | 0.37911 | 0.026148
|  | DINGWALL | ST |  |  |  | 5.9781 | 5.935 | 5.7852 | 5.6372 | 5.4715 | 5.1246 | 4.8551 | 4.6114 | 4.3478 | 4.051 | 3.7319 | 1.8298 | 0.93731 | 0.25885 | 7.7567 | 7.6983 | 7.5023 | 7.3115 | 7.1402 | 6.7969 | 6.5589 | 6.346 | 6.1084 | 5.8383 | 5.5399 | 3.9024 | 3.178 | 2.5113 | 7.3175 | 7.2727 | 7.0958 | 6.9142 | 6.7419 | 6.3975 | 6.1188 | 5.8527 | 5.5459 | 5.1914 | 4.792 | 2.6142 | 1.8145 | 1.4847
|  | DINGWALL | FS |  |  |  | 5.9935 | 5.9616 | 5.9028 | 5.8203 | 5.6618 | 5.4638 | 5.2491 | 5.043 | 4.839 | 4.6194 | 4.3834 | 2.7326 | 1.1217 | 0.13716 | 7.7706 | 7.7227 | 7.6279 | 7.5087 | 7.3796 | 7.2202 | 7.0469 | 6.8829 | 6.711 | 6.5201 | 6.31 | 4.885 | 3.3305 | 1.9828 | 7.3344 | 7.302 | 7.2365 | 7.152 | 7.0451 | 6.9082 | 6.7264 | 6.554 | 6.3687 | 6.1623 | 5.9324 | 4.3532 | 2.7328 | 1.5544
| CARRADALE | DIPPEN | MINIMUM HEADROOM | NR 80026 37592 | YES | YES | 0.29618 | 0.25648 | 0.21591 | 0.1765 | 0.11928 | 0.051523 | 0.0045134 | -0.033873 | -0.083372 | -0.12636 | -0.16501 | -0.29033 | -0.39119 | -0.48765 | 0.52972 | 0.50823 | 0.48806 | 0.46017 | 0.4125 | 0.36211 | 0.3336 | 0.30131 | 0.25977 | 0.22021 | 0.18365 | 0.055093 | -0.071919 | -0.18033 | 0.36334 | 0.32815 | 0.29182 | 0.25581 | 0.19264 | 0.1238 | 0.079176 | 0.039575 | -0.011396 | -0.059466 | -0.10299 | -0.23927 | -0.36377 | -0.47757
|  | DIPPEN | CT |  |  |  | 0.31995 | 0.29069 | 0.23826 | 0.18445 | 0.11928 | 0.051523 | 0.0045134 | -0.033873 | -0.083372 | -0.12636 | -0.16501 | -0.29033 | -0.39119 | -0.46078 | 0.53888 | 0.5221 | 0.49237 | 0.46017 | 0.4125 | 0.36211 | 0.3336 | 0.30131 | 0.25977 | 0.22021 | 0.18365 | 0.063918 | -0.02182 | -0.10138 | 0.38408 | 0.35816 | 0.30964 | 0.25869 | 0.19264 | 0.1238 | 0.079176 | 0.039575 | -0.011396 | -0.059466 | -0.10299 | -0.23927 | -0.34578 | -0.4259
|  | DIPPEN | LW |  |  |  | 0.29618 | 0.25648 | 0.21591 | 0.1765 | 0.14301 | 0.092087 | 0.04528 | 0.0073194 | -0.037058 | -0.074822 | -0.1174 | -0.2122 | -0.32496 | -0.4614 | 0.52972 | 0.50823 | 0.48806 | 0.46782 | 0.45075 | 0.4226 | 0.39422 | 0.36298 | 0.32628 | 0.29198 | 0.25802 | 0.18402 | 0.065444 | -0.096582 | 0.36334 | 0.32815 | 0.29182 | 0.25581 | 0.22523 | 0.17814 | 0.13418 | 0.096114 | 0.048708 | 0.0065466 | -0.037094 | -0.13308 | -0.26418 | -0.43079
|  | DIPPEN | ST |  |  |  | 0.33738 | 0.31933 | 0.28419 | 0.25506 | 0.22697 | 0.17808 | 0.14715 | 0.097709 | 0.058608 | 0.019735 | -0.024078 | -0.25388 | -0.38852 | -0.48765 | 0.54683 | 0.53734 | 0.5055 | 0.4806 | 0.45925 | 0.41175 | 0.3877 | 0.34393 | 0.31447 | 0.28348 | 0.24557 | 0.055093 | -0.071919 | -0.18033 | 0.39975 | 0.38446 | 0.34664 | 0.31571 | 0.28721 | 0.23293 | 0.20169 | 0.14884 | 0.10949 | 0.068785 | 0.021599 | -0.21671 | -0.36377 | -0.47757
|  | DIPPEN | FS |  |  |  | 0.34638 | 0.33435 | 0.30932 | 0.29319 | 0.27255 | 0.24894 | 0.22464 | 0.19338 | 0.16786 | 0.13589 | 0.1024 | -0.084919 | -0.21581 | -0.26271 | 0.55062 | 0.54365 | 0.52877 | 0.51694 | 0.50267 | 0.48675 | 0.47054 | 0.44766 | 0.42831 | 0.40587 | 0.38215 | 0.25762 | 0.15806 | 0.11545 | 0.40756 | 0.39762 | 0.37429 | 0.35826 | 0.33803 | 0.31504 | 0.29149 | 0.26019 | 0.23462 | 0.20322 | 0.17018 | -0.013413 | -0.14258 | -0.18833
| BRORA | DORNOCH | MINIMUM HEADROOM | NH 79721 89953 | YES | YES | -0.14316 | -0.27146 | -0.45204 | -0.67181 | -0.90846 | -1.2279 | -1.4593 | -1.5608 | -1.6665 | -1.7781 | -1.8833 | -2.1933 | -2.3399 | -2.3854 | 1.2276 | 1.142 | 1.0066 | 0.8335 | 0.63323 | 0.36102 | 0.16929 | 0.065337 | -0.04477 | -0.15702 | -0.26137 | -0.48173 | -0.55957 | -0.57976 | -0.264 | -0.38277 | -0.56142 | -0.78082 | -1.0289 | -1.3521 | -1.5834 | -1.6818 | -1.7847 | -1.8927 | -1.9951 | -2.2957 | -2.4297 | -2.4694
|  | DORNOCH | CT |  |  |  | -0.037296 | -0.14839 | -0.34593 | -0.54174 | -0.76998 | -1.0611 | -1.2515 | -1.341 | -1.4264 | -1.5083 | -1.6112 | -1.9145 | -2.1492 | -2.2307 | 1.2912 | 1.2173 | 1.0893 | 0.95116 | 0.78846 | 0.58532 | 0.47475 | 0.39667 | 0.2911 | 0.1851 | 0.087981 | -0.15598 | -0.30514 | -0.41079 | -0.16746 | -0.2723 | -0.45517 | -0.63761 | -0.86251 | -1.1431 | -1.3198 | -1.4047 | -1.4854 | -1.5631 | -1.6614 | -1.9532 | -2.1628 | -2.2344
|  | DORNOCH | LW |  |  |  | -0.14316 | -0.27146 | -0.45204 | -0.67181 | -0.90846 | -1.2279 | -1.4593 | -1.5608 | -1.6665 | -1.7781 | -1.8833 | -2.1933 | -2.3399 | -2.3854 | 1.2276 | 1.142 | 1.0066 | 0.8335 | 0.63323 | 0.36102 | 0.16929 | 0.065337 | -0.04477 | -0.15702 | -0.26137 | -0.48173 | -0.55957 | -0.57976 | -0.264 | -0.38277 | -0.56142 | -0.78082 | -1.0289 | -1.3521 | -1.5834 | -1.6818 | -1.7847 | -1.8927 | -1.9951 | -2.2957 | -2.4297 | -2.4694
|  | DORNOCH | ST |  |  |  | 0.048972 | -0.016721 | -0.1392 | -0.2504 | -0.34928 | -0.52684 | -0.62662 | -0.71752 | -0.82132 | -0.93691 | -1.0658 | -1.719 | -1.9829 | -2.1185 | 1.3296 | 1.2844 | 1.1767 | 1.0822 | 1.0044 | 0.83706 | 0.75842 | 0.69412 | 0.61828 | 0.53291 | 0.43726 | -0.055438 | -0.21302 | -0.32291 | -0.088835 | -0.15128 | -0.28063 | -0.39499 | -0.49386 | -0.67994 | -0.7787 | -0.86325 | -0.96023 | -1.0685 | -1.1898 | -1.8073 | -2.0504 | -2.1703
|  | DORNOCH | FS |  |  |  | 0.17287 | 0.12417 | 0.04131 | -0.037656 | -0.11867 | -0.22297 | -0.30677 | -0.39426 | -0.48503 | -0.58469 | -0.68783 | -1.3516 | -1.8016 | -2.0851 | 1.4253 | 1.3894 | 1.3308 | 1.2725 | 1.2141 | 1.1308 | 1.0676 | 1.0066 | 0.94076 | 0.86827 | 0.78995 | 0.3055 | -0.074077 | -0.27412 | 0.034117 | -0.012378 | -0.092732 | -0.16936 | -0.24797 | -0.34686 | -0.42806 | -0.5094 | -0.59408 | -0.68702 | -0.78412 | -1.4037 | -1.8264 | -2.0914
| CLACHAN | DOUGLAS PIER | MINIMUM HEADROOM | NS 19396 99616 | YES | YES | 1.9428 | 1.9258 | 1.9057 | 1.8865 | 1.8655 | 1.8386 | 1.8083 | 1.7833 | 1.7537 | 1.7262 | 1.6987 | 1.6579 | 1.6411 | 1.6286 | 1.9785 | 1.9738 | 1.9673 | 1.9614 | 1.9565 | 1.9511 | 1.9438 | 1.9341 | 1.9233 | 1.9122 | 1.9018 | 1.8827 | 1.8769 | 1.8632 | 1.056 | 1.0398 | 1.0212 | 1.003 | 0.98263 | 0.95789 | 0.92884 | 0.90409 | 0.87499 | 0.84779 | 0.82075 | 0.78136 | 0.7666 | 0.75512
|  | DOUGLAS PIER | CT |  |  |  | 1.9529 | 1.9397 | 1.9136 | 1.8876 | 1.8655 | 1.8425 | 1.8209 | 1.7997 | 1.77 | 1.7412 | 1.7168 | 1.6682 | 1.6411 | 1.6286 | 1.9787 | 1.9741 | 1.9673 | 1.9614 | 1.9565 | 1.9511 | 1.9455 | 1.9384 | 1.931 | 1.9235 | 1.9149 | 1.8931 | 1.8769 | 1.8632 | 1.0651 | 1.0524 | 1.0278 | 1.0031 | 0.98263 | 0.96125 | 0.94111 | 0.92036 | 0.89126 | 0.86285 | 0.83884 | 0.79115 | 0.7666 | 0.75512
|  | DOUGLAS PIER | LW |  |  |  | 1.9428 | 1.9258 | 1.9057 | 1.8865 | 1.8657 | 1.8386 | 1.8083 | 1.7833 | 1.7537 | 1.7262 | 1.6987 | 1.6579 | 1.6451 | 1.6418 | 1.9785 | 1.9738 | 1.9697 | 1.965 | 1.9604 | 1.9528 | 1.9438 | 1.9341 | 1.9233 | 1.9122 | 1.9018 | 1.8827 | 1.8809 | 1.8806 | 1.056 | 1.0398 | 1.0212 | 1.003 | 0.98377 | 0.95789 | 0.92884 | 0.90409 | 0.87499 | 0.84779 | 0.82075 | 0.78136 | 0.76983 | 0.76691
|  | DOUGLAS PIER | ST |  |  |  | 1.9622 | 1.9588 | 1.9513 | 1.9407 | 1.9322 | 1.9225 | 1.9081 | 1.8942 | 1.8749 | 1.8549 | 1.8356 | 1.7247 | 1.6969 | 1.6855 | 1.9811 | 1.9797 | 1.9777 | 1.9751 | 1.9722 | 1.9686 | 1.9641 | 1.9588 | 1.9521 | 1.9446 | 1.9362 | 1.8914 | 1.8793 | 1.8777 | 1.0734 | 1.0701 | 1.0631 | 1.0531 | 1.0449 | 1.0355 | 1.0217 | 1.0082 | 0.98943 | 0.9699 | 0.9508 | 0.84211 | 0.81596 | 0.80596
|  | DOUGLAS PIER | FS |  |  |  | 1.9658 | 1.963 | 1.9561 | 1.9468 | 1.9388 | 1.9296 | 1.9208 | 1.9093 | 1.8949 | 1.8808 | 1.8636 | 1.7608 | 1.682 | 1.6661 | 1.9815 | 1.9804 | 1.9788 | 1.9768 | 1.9747 | 1.9721 | 1.9692 | 1.9657 | 1.9617 | 1.9572 | 1.952 | 1.9188 | 1.8893 | 1.875 | 1.0767 | 1.074 | 1.0675 | 1.0588 | 1.0513 | 1.0425 | 1.034 | 1.023 | 1.0093 | 0.99563 | 0.97915 | 0.87994 | 0.8031 | 0.78885
| DOUNREAY | DOUNREAY | MINIMUM HEADROOM | NC 9815 6665 | NO | YES | 21 | 21 | 20.9687 | 20.9476 | 20.9336 | 20.8856 | 20.8722 | 20.8361 | 20.8233 | 20.8124 | 20.7951 | 20.7138 | 20.5946 | 20.4722 | 19.5 | 19.5 | 19.4609 | 19.4345 | 19.417 | 19.357 | 19.3403 | 19.2951 | 19.2791 | 19.2655 | 19.2439 | 19.1423 | 18.9932 | 18.8402 | 19.5 | 19.5 | 19.4609 | 19.4345 | 19.417 | 19.357 | 19.3403 | 19.2951 | 19.2791 | 19.2655 | 19.2439 | 19.1423 | 18.9932 | 18.8402
|  | DOUNREAY | CT |  |  |  | 21 | 21 | 20.9959 | 20.9887 | 20.9539 | 20.9168 | 20.9074 | 20.891 | 20.8745 | 20.8603 | 20.8446 | 20.7614 | 20.683 | 20.5983 | 19.5 | 19.5 | 19.4949 | 19.4859 | 19.4424 | 19.396 | 19.3843 | 19.3638 | 19.3432 | 19.3253 | 19.3058 | 19.2018 | 19.1037 | 18.9979 | 19.5 | 19.5 | 19.4949 | 19.4859 | 19.4424 | 19.396 | 19.3843 | 19.3638 | 19.3432 | 19.3253 | 19.3058 | 19.2018 | 19.1037 | 18.9979
|  | DOUNREAY | LW |  |  |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20.9936 | 20.9869 | 20.9814 | 20.9753 | 20.9428 | 20.7972 | 20.5839 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.492 | 19.4836 | 19.4768 | 19.4691 | 19.4285 | 19.2465 | 18.9798 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.492 | 19.4836 | 19.4768 | 19.4691 | 19.4285 | 19.2465 | 18.9798
|  | DOUNREAY | ST |  |  |  | 21 | 21 | 20.9687 | 20.9476 | 20.9336 | 20.8856 | 20.8722 | 20.8361 | 20.8233 | 20.8124 | 20.7951 | 20.7138 | 20.5946 | 20.4722 | 19.5 | 19.5 | 19.4609 | 19.4345 | 19.417 | 19.357 | 19.3403 | 19.2951 | 19.2791 | 19.2655 | 19.2439 | 19.1423 | 18.9932 | 18.8402 | 19.5 | 19.5 | 19.4609 | 19.4345 | 19.417 | 19.357 | 19.3403 | 19.2951 | 19.2791 | 19.2655 | 19.2439 | 19.1423 | 18.9932 | 18.8402
|  | DOUNREAY | FS |  |  |  | 21 | 21 | 20.9936 | 20.9872 | 20.9798 | 20.9723 | 20.9659 | 20.9528 | 20.944 | 20.9351 | 20.9262 | 20.9155 | 20.908 | 20.8943 | 19.5 | 19.5 | 19.492 | 19.484 | 19.4747 | 19.4654 | 19.4574 | 19.441 | 19.4299 | 19.4189 | 19.4078 | 19.3943 | 19.385 | 19.3679 | 19.5 | 19.5 | 19.492 | 19.484 | 19.4747 | 19.4654 | 19.4574 | 19.441 | 19.4299 | 19.4189 | 19.4078 | 19.3943 | 19.385 | 19.3679
| ARDMORE | DRIMORE | MINIMUM HEADROOM | NF 77377 40049 | YES | YES | 1.8401 | 1.8147 | 1.7826 | 1.7436 | 1.699 | 1.6544 | 1.6062 | 1.5781 | 1.5429 | 1.5088 | 1.4759 | 1.4269 | 1.3963 | 1.3764 | 1.8941 | 1.8851 | 1.871 | 1.8502 | 1.8283 | 1.8065 | 1.7826 | 1.7616 | 1.7303 | 1.6989 | 1.67 | 1.6313 | 1.6043 | 1.5803 | 1.5302 | 1.507 | 1.4779 | 1.4446 | 1.4096 | 1.3749 | 1.3335 | 1.3054 | 1.2719 | 1.2391 | 1.2078 | 1.1632 | 1.1404 | 1.124
|  | DRIMORE | CT |  |  |  | 1.8567 | 1.8348 | 1.7905 | 1.7442 | 1.699 | 1.6544 | 1.6063 | 1.5863 | 1.5556 | 1.5207 | 1.4918 | 1.4428 | 1.3963 | 1.3764 | 1.8991 | 1.8904 | 1.8733 | 1.8502 | 1.8283 | 1.8065 | 1.7833 | 1.7681 | 1.7437 | 1.7117 | 1.6847 | 1.6324 | 1.6043 | 1.5803 | 1.5465 | 1.5272 | 1.4869 | 1.4446 | 1.4096 | 1.3749 | 1.338 | 1.3176 | 1.2865 | 1.2524 | 1.2245 | 1.1778 | 1.1404 | 1.124
|  | DRIMORE | LW |  |  |  | 1.8401 | 1.8147 | 1.7826 | 1.7436 | 1.7046 | 1.6598 | 1.6062 | 1.5781 | 1.5429 | 1.5088 | 1.4759 | 1.4269 | 1.4028 | 1.397 | 1.8941 | 1.8851 | 1.871 | 1.8533 | 1.8359 | 1.8116 | 1.7826 | 1.7616 | 1.7303 | 1.6989 | 1.67 | 1.6313 | 1.6222 | 1.6204 | 1.5302 | 1.507 | 1.4779 | 1.4455 | 1.4152 | 1.3779 | 1.3335 | 1.3054 | 1.2719 | 1.2391 | 1.2078 | 1.1632 | 1.145 | 1.1407
|  | DRIMORE | ST |  |  |  | 1.8698 | 1.8588 | 1.8447 | 1.8298 | 1.8165 | 1.7985 | 1.7782 | 1.7534 | 1.7232 | 1.6941 | 1.6593 | 1.4947 | 1.4502 | 1.427 | 1.9063 | 1.902 | 1.8967 | 1.8911 | 1.8862 | 1.8776 | 1.8672 | 1.8526 | 1.8342 | 1.8157 | 1.7898 | 1.6603 | 1.624 | 1.6019 | 1.5571 | 1.5469 | 1.5337 | 1.5202 | 1.5078 | 1.4914 | 1.4733 | 1.4513 | 1.4248 | 1.3994 | 1.3691 | 1.2234 | 1.1802 | 1.1618
|  | DRIMORE | FS |  |  |  | 1.8735 | 1.867 | 1.8542 | 1.845 | 1.8303 | 1.818 | 1.8004 | 1.7819 | 1.7614 | 1.7393 | 1.714 | 1.5491 | 1.432 | 1.4081 | 1.9077 | 1.9053 | 1.9004 | 1.8972 | 1.8916 | 1.8871 | 1.8783 | 1.869 | 1.8568 | 1.8431 | 1.8275 | 1.7141 | 1.6171 | 1.5876 | 1.561 | 1.5545 | 1.5427 | 1.5335 | 1.5201 | 1.5086 | 1.4927 | 1.4755 | 1.4571 | 1.4372 | 1.4144 | 1.2704 | 1.1667 | 1.151
| CEANNACROC | DRUMNADROCHIT | MINIMUM HEADROOM | NH 50306 29824 | YES | YES | 2.4819 | 2.4732 | 2.4629 | 2.4504 | 2.4203 | 2.2749 | 2.1204 | 2.0126 | 1.8981 | 1.7827 | 1.6761 | 1.4752 | 1.3709 | 1.3 | 3.7055 | 3.6858 | 3.6664 | 3.6381 | 3.6214 | 3.6029 | 3.5703 | 3.5326 | 3.492 | 3.4504 | 3.4084 | 3.2814 | 3.1896 | 3.1034 | 2.5511 | 2.5276 | 2.5051 | 2.4423 | 2.3511 | 2.2283 | 2.0978 | 2.0063 | 1.9091 | 1.8111 | 1.7204 | 1.5476 | 1.461 | 1.397
|  | DRUMNADROCHIT | CT |  |  |  | 2.4827 | 2.4738 | 2.4629 | 2.4504 | 2.4228 | 2.288 | 2.1532 | 2.0726 | 1.9635 | 1.8531 | 1.7529 | 1.5507 | 1.3709 | 1.3 | 3.7084 | 3.6912 | 3.6664 | 3.6381 | 3.6214 | 3.6045 | 3.5877 | 3.5597 | 3.5212 | 3.4818 | 3.4462 | 3.2919 | 3.1896 | 3.1034 | 2.5548 | 2.5348 | 2.5051 | 2.468 | 2.3559 | 2.2419 | 2.1277 | 2.0591 | 1.9657 | 1.8708 | 1.786 | 1.6156 | 1.461 | 1.397
|  | DRUMNADROCHIT | LW |  |  |  | 2.4819 | 2.4732 | 2.4661 | 2.4511 | 2.4203 | 2.2749 | 2.1204 | 2.0126 | 1.8981 | 1.7827 | 1.6761 | 1.4752 | 1.3817 | 1.33 | 3.7055 | 3.6858 | 3.6698 | 3.644 | 3.6304 | 3.6029 | 3.5703 | 3.5326 | 3.492 | 3.4504 | 3.4084 | 3.2814 | 3.2467 | 3.2213 | 2.5511 | 2.5276 | 2.5083 | 2.4423 | 2.3511 | 2.2283 | 2.0978 | 2.0063 | 1.9091 | 1.8111 | 1.7204 | 1.5476 | 1.4658 | 1.4215
|  | DRUMNADROCHIT | ST |  |  |  | 2.4859 | 2.4806 | 2.4764 | 2.4703 | 2.4661 | 2.4618 | 2.4566 | 2.45 | 2.4417 | 2.4053 | 2.3023 | 1.7976 | 1.6329 | 1.5414 | 3.7125 | 3.7034 | 3.6942 | 3.6815 | 3.6701 | 3.657 | 3.6416 | 3.6227 | 3.5998 | 3.5735 | 3.5434 | 3.3825 | 3.2914 | 3.2056 | 2.5599 | 2.5499 | 2.5395 | 2.525 | 2.5116 | 2.496 | 2.4774 | 2.4545 | 2.4179 | 2.3401 | 2.2547 | 1.8275 | 1.6819 | 1.6002
|  | DRUMNADROCHIT | FS |  |  |  | 2.5014 | 2.4962 | 2.4924 | 2.4885 | 2.4846 | 2.4799 | 2.4748 | 2.4688 | 2.462 | 2.4547 | 2.4451 | 1.9183 | 1.5513 | 1.4477 | 3.7291 | 3.7204 | 3.7121 | 3.7029 | 3.6931 | 3.6819 | 3.669 | 3.654 | 3.637 | 3.6181 | 3.5959 | 3.4681 | 3.2447 | 3.108 | 2.5765 | 2.5673 | 2.5581 | 2.5475 | 2.5363 | 2.5234 | 2.5084 | 2.4909 | 2.4709 | 2.4386 | 2.3681 | 1.9227 | 1.6156 | 1.5324
| GRUDIE BRIDGE | DRUMRUNIE | MINIMUM HEADROOM | NC 16664 05298 | YES | YES | 0.78689 | 0.77845 | 0.7739 | 0.76142 | 0.75552 | 0.74471 | 0.73479 | 0.72912 | 0.71581 | 0.70788 | 0.69888 | 0.68121 | 0.67085 | 0.66553 | 0.83073 | 0.8262 | 0.82335 | 0.81736 | 0.81306 | 0.8078 | 0.80146 | 0.79626 | 0.78799 | 0.78164 | 0.77473 | 0.7636 | 0.75806 | 0.7537 | 0.8042 | 0.79643 | 0.79214 | 0.78084 | 0.77537 | 0.7653 | 0.7559 | 0.74962 | 0.7366 | 0.72792 | 0.71858 | 0.70164 | 0.69309 | 0.68832
|  | DRUMRUNIE | CT |  |  |  | 0.7911 | 0.78653 | 0.77652 | 0.76501 | 0.75652 | 0.74756 | 0.7389 | 0.73142 | 0.72424 | 0.71319 | 0.70472 | 0.68745 | 0.67085 | 0.66553 | 0.8323 | 0.82941 | 0.82376 | 0.81751 | 0.81306 | 0.80838 | 0.80379 | 0.79868 | 0.79286 | 0.78553 | 0.77931 | 0.76573 | 0.75806 | 0.7537 | 0.80791 | 0.80361 | 0.79434 | 0.78372 | 0.77595 | 0.76775 | 0.75982 | 0.75266 | 0.7448 | 0.73355 | 0.72478 | 0.70709 | 0.69309 | 0.68832
|  | DRUMRUNIE | LW |  |  |  | 0.78689 | 0.77845 | 0.7739 | 0.76142 | 0.75552 | 0.74471 | 0.73479 | 0.72912 | 0.71581 | 0.70788 | 0.69888 | 0.68121 | 0.6731 | 0.67149 | 0.83073 | 0.8262 | 0.82335 | 0.81736 | 0.81406 | 0.8078 | 0.80146 | 0.79626 | 0.78799 | 0.78164 | 0.77473 | 0.7636 | 0.76047 | 0.75991 | 0.8042 | 0.79643 | 0.79214 | 0.78084 | 0.77537 | 0.7653 | 0.7559 | 0.74962 | 0.7366 | 0.72792 | 0.71858 | 0.70164 | 0.69489 | 0.69364
|  | DRUMRUNIE | ST |  |  |  | 0.79396 | 0.79271 | 0.78816 | 0.7846 | 0.77898 | 0.77105 | 0.76671 | 0.76276 | 0.75688 | 0.74295 | 0.73693 | 0.69301 | 0.68005 | 0.67209 | 0.83378 | 0.83288 | 0.83062 | 0.82853 | 0.82558 | 0.82158 | 0.81866 | 0.81559 | 0.81145 | 0.80405 | 0.7993 | 0.76931 | 0.7612 | 0.75657 | 0.81053 | 0.80933 | 0.80521 | 0.80189 | 0.79675 | 0.78953 | 0.7854 | 0.78154 | 0.77582 | 0.7631 | 0.75658 | 0.71277 | 0.70096 | 0.69443
|  | DRUMRUNIE | FS |  |  |  | 0.79599 | 0.79338 | 0.79206 | 0.79074 | 0.78379 | 0.77882 | 0.77496 | 0.76883 | 0.76231 | 0.76032 | 0.74977 | 0.70704 | 0.67851 | 0.66915 | 0.83459 | 0.83325 | 0.83229 | 0.8312 | 0.82799 | 0.82537 | 0.82302 | 0.81966 | 0.81598 | 0.81379 | 0.80828 | 0.78205 | 0.76107 | 0.75449 | 0.81233 | 0.80995 | 0.80869 | 0.80739 | 0.80114 | 0.79659 | 0.79298 | 0.78734 | 0.78131 | 0.7792 | 0.76955 | 0.72852 | 0.69979 | 0.69208
| STRATHLEVEN | DRYMEN | MINIMUM HEADROOM | NS 48494 88026 | YES | YES | -2.9586 | -3.0628 | -3.2065 | -3.3606 | -3.51 | -3.7055 | -3.9005 | -4.0614 | -4.2327 | -4.4038 | -4.5709 | -5.1422 | -5.6323 | -5.9627 | -0.80196 | -0.85758 | -0.92662 | -1.0085 | -1.1306 | -1.2585 | -1.3502 | -1.4543 | -1.5752 | -1.6936 | -1.8131 | -2.2459 | -2.6348 | -3.0518 | -1.0149 | -1.0627 | -1.1855 | -1.3197 | -1.4562 | -1.638 | -1.8119 | -1.9582 | -2.1135 | -2.2734 | -2.4376 | -3.0064 | -3.4758 | -3.7965
|  | DRYMEN | CT |  |  |  | -2.8822 | -2.9482 | -3.1207 | -3.2908 | -3.4822 | -3.6805 | -3.8452 | -4.0022 | -4.1856 | -4.3646 | -4.5412 | -5.1422 | -5.6323 | -5.9627 | -0.77693 | -0.81844 | -0.91293 | -1.0085 | -1.1306 | -1.2585 | -1.3502 | -1.4543 | -1.5752 | -1.6936 | -1.8131 | -2.2459 | -2.6348 | -3.0518 | -1.0149 | -1.0433 | -1.1073 | -1.2575 | -1.4442 | -1.638 | -1.7919 | -1.9392 | -2.1087 | -2.2734 | -2.4376 | -3.0064 | -3.4758 | -3.7965
|  | DRYMEN | LW |  |  |  | -2.9586 | -3.0628 | -3.2065 | -3.3606 | -3.51 | -3.7055 | -3.9005 | -4.0614 | -4.2327 | -4.4038 | -4.5709 | -5.0441 | -5.4653 | -5.8537 | -0.80196 | -0.85758 | -0.92662 | -1.002 | -1.0736 | -1.1743 | -1.2782 | -1.3776 | -1.4837 | -1.5892 | -1.6907 | -1.955 | -2.2556 | -2.5987 | -1.0076 | -1.0627 | -1.1855 | -1.3197 | -1.4562 | -1.6345 | -1.8119 | -1.9582 | -2.1135 | -2.2684 | -2.4201 | -2.8527 | -3.275 | -3.6872
|  | DRYMEN | ST |  |  |  | -2.8344 | -2.8679 | -2.9465 | -3.0184 | -3.0945 | -3.2116 | -3.2902 | -3.4083 | -3.5082 | -3.6189 | -3.7456 | -4.4162 | -4.8581 | -5.2681 | -0.75166 | -0.7718 | -0.83778 | -0.89509 | -0.94981 | -1.0514 | -1.1113 | -1.2093 | -1.2849 | -1.3663 | -1.4628 | -1.9802 | -2.3977 | -2.8743 | -0.99659 | -1.0059 | -1.0572 | -1.0999 | -1.1373 | -1.2198 | -1.2825 | -1.4 | -1.4924 | -1.5941 | -1.7126 | -2.3457 | -2.772 | -3.1789
|  | DRYMEN | FS |  |  |  | -2.8149 | -2.8372 | -2.8864 | -2.9437 | -3.0026 | -3.0673 | -3.1295 | -3.2165 | -3.3021 | -3.3982 | -3.4986 | -4.0891 | -4.5919 | -4.9028 | -0.74394 | -0.75958 | -0.79288 | -0.83136 | -0.87267 | -0.91827 | -0.96377 | -1.0286 | -1.0925 | -1.1633 | -1.2391 | -1.6791 | -2.1804 | -2.7601 | -0.99451 | -1.0022 | -1.0207 | -1.0419 | -1.0666 | -1.0937 | -1.1208 | -1.1887 | -1.2676 | -1.3563 | -1.4489 | -1.9815 | -2.4333 | -2.7199
| DUNVEGAN | DRYNOCH | MINIMUM HEADROOM | NG 41080 31292 | YES | YES | 1.5818 | 1.5188 | 1.4457 | 1.3503 | 1.2621 | 1.1667 | 1.075 | 1.0109 | 0.924 | 0.8359 | 0.75398 | 0.58471 | 0.51932 | 0.50101 | 1.6066 | 1.5705 | 1.5289 | 1.4637 | 1.4179 | 1.369 | 1.3203 | 1.2697 | 1.2025 | 1.1337 | 1.0701 | 0.95454 | 0.91649 | 0.86045 | 1.3161 | 1.2674 | 1.2082 | 1.1259 | 1.0494 | 0.96637 | 0.88479 | 0.84553 | 0.80898 | 0.75274 | 0.68341 | 0.482 | 0.42069 | 0.40305
|  | DRYNOCH | CT |  |  |  | 1.6236 | 1.5708 | 1.4662 | 1.3503 | 1.2621 | 1.1667 | 1.075 | 1.016 | 0.93576 | 0.85561 | 0.78563 | 0.6516 | 0.54483 | 0.50101 | 1.6212 | 1.5876 | 1.5289 | 1.4637 | 1.4179 | 1.369 | 1.3203 | 1.2745 | 1.211 | 1.1467 | 1.0914 | 0.97732 | 0.91649 | 0.8667 | 1.3502 | 1.3026 | 1.2155 | 1.1259 | 1.0494 | 0.96637 | 0.88479 | 0.84553 | 0.80898 | 0.77409 | 0.73035 | 0.60781 | 0.52185 | 0.48168
|  | DRYNOCH | LW |  |  |  | 1.5818 | 1.5188 | 1.4457 | 1.3698 | 1.295 | 1.1956 | 1.088 | 1.0109 | 0.924 | 0.8359 | 0.75398 | 0.58471 | 0.51932 | 0.50404 | 1.6066 | 1.5705 | 1.5333 | 1.4924 | 1.4547 | 1.3963 | 1.3304 | 1.2697 | 1.2025 | 1.1337 | 1.0701 | 0.95454 | 0.92324 | 0.91804 | 1.3161 | 1.2674 | 1.2082 | 1.1486 | 1.0843 | 1.0072 | 0.92511 | 0.87399 | 0.81438 | 0.75274 | 0.68341 | 0.482 | 0.42069 | 0.4103
|  | DRYNOCH | ST |  |  |  | 1.6513 | 1.6292 | 1.5991 | 1.5614 | 1.5257 | 1.4828 | 1.4369 | 1.3818 | 1.315 | 1.2441 | 1.166 | 0.77717 | 0.65337 | 0.59823 | 1.6346 | 1.6223 | 1.6059 | 1.5846 | 1.563 | 1.5365 | 1.5065 | 1.4698 | 1.4251 | 1.3756 | 1.3203 | 1.0365 | 0.9531 | 0.9071 | 1.3787 | 1.3602 | 1.3352 | 1.3049 | 1.2756 | 1.241 | 1.2042 | 1.1619 | 1.1106 | 1.0549 | 0.98707 | 0.63273 | 0.49703 | 0.45633
|  | DRYNOCH | FS |  |  |  | 1.6676 | 1.6487 | 1.6227 | 1.595 | 1.5639 | 1.5295 | 1.4949 | 1.4505 | 1.4021 | 1.3506 | 1.2941 | 0.91733 | 0.62651 | 0.53827 | 1.6409 | 1.6305 | 1.6168 | 1.601 | 1.5836 | 1.5636 | 1.542 | 1.5151 | 1.4847 | 1.4515 | 1.4144 | 1.1675 | 0.94689 | 0.86045 | 1.394 | 1.3781 | 1.356 | 1.334 | 1.3088 | 1.2808 | 1.2537 | 1.2196 | 1.1829 | 1.1441 | 1.102 | 0.81296 | 0.55973 | 0.40305
| KEITH | DUFFTOWN | MINIMUM HEADROOM | NJ 32060 39722 | NO | YES | 1.2749 | 1.1697 | -0.71746 | -2.8355 | -6.9379 | -11.3028 | -13.9127 | -14.6198 | -15.3559 | -15.992 | -16.6896 | -19.9665 | -20.9957 | -21.4185 | 1.615 | 1.5399 | -0.71501 | -3.2458 | -8.25 | -13.571 | -16.6909 | -17.4915 | -18.3245 | -19.0314 | -19.8108 | -23.5942 | -24.7366 | -25.2468 | -3.6209 | -3.7468 | -6.0799 | -8.6993 | -13.7935 | -19.2143 | -22.4385 | -23.298 | -24.1909 | -24.9558 | -25.795 | -29.7557 | -30.9949 | -31.5335
|  | DUFFTOWN | CT |  |  |  | 1.3114 | 1.2277 | 0.89767 | 0.36263 | -1.6482 | -3.7837 | -4.4766 | -4.8682 | -5.2632 | -5.6276 | -6.0219 | -7.7767 | -8.4608 | -8.7487 | 1.6579 | 1.5994 | 1.2366 | 0.64815 | -1.7439 | -4.2896 | -5.0217 | -5.417 | -5.8302 | -6.2052 | -6.6012 | -8.4491 | -9.0857 | -9.4196 | -3.5153 | -3.6024 | -4.043 | -4.7177 | -7.1967 | -9.829 | -10.6533 | -11.1126 | -11.5956 | -12.0421 | -12.5039 | -14.5579 | -15.3395 | -15.6751
|  | DUFFTOWN | LW |  |  |  | 1.2749 | 1.1697 | -0.71746 | -2.8355 | -6.9379 | -11.3028 | -13.9127 | -14.6198 | -15.3559 | -15.992 | -16.6896 | -19.9665 | -20.9957 | -21.4185 | 1.615 | 1.5399 | -0.71501 | -3.2458 | -8.25 | -13.571 | -16.6909 | -17.4915 | -18.3245 | -19.0314 | -19.8108 | -23.5942 | -24.7366 | -25.2468 | -3.6209 | -3.7468 | -6.0799 | -8.6993 | -13.7935 | -19.2143 | -22.4385 | -23.298 | -24.1909 | -24.9558 | -25.795 | -29.7557 | -30.9949 | -31.5335
|  | DUFFTOWN | ST |  |  |  | 1.4364 | 1.3984 | -0.28286 | -1.4487 | -2.2435 | -4.8401 | -5.6224 | -6.226 | -6.5089 | -6.7771 | -7.151 | -9.015 | -9.8237 | -10.2436 | 1.7219 | 1.6896 | -0.39506 | -1.8295 | -2.7946 | -6.0067 | -6.9428 | -7.6526 | -7.9507 | -8.2206 | -8.6136 | -10.5348 | -11.3555 | -11.8382 | -3.4115 | -3.4602 | -5.5623 | -7.0179 | -8.005 | -11.2409 | -12.2006 | -12.9344 | -13.2586 | -13.5555 | -13.9758 | -16.0773 | -17.0281 | -17.6126
|  | DUFFTOWN | FS |  |  |  | 1.4487 | 1.4191 | 1.056 | 0.67774 | 0.24047 | -0.20348 | -0.59507 | -0.84112 | -1.0317 | -1.2357 | -1.4485 | -2.191 | -2.7963 | -3.2503 | 1.7303 | 1.7045 | 1.2624 | 0.80498 | 0.27745 | -0.25677 | -0.72233 | -1.0062 | -1.2176 | -1.4342 | -1.6552 | -2.2609 | -2.7486 | -3.1462 | -3.3942 | -3.431 | -3.8877 | -4.365 | -4.9101 | -5.4668 | -5.9519 | -6.2623 | -6.5 | -6.7442 | -6.9934 | -7.7973 | -8.4035 | -8.8102
| BRACO | DUNBLANE | MINIMUM HEADROOM | NN 77907 01544 | NO | YES | 1.7338 | 1.3228 | 0.35357 | -0.73518 | -2.2724 | -3.9124 | -5.3361 | -6.3278 | -7.398 | -8.4692 | -9.5626 | -13.3366 | -16.1309 | -18.4015 | 4.1888 | 3.946 | 3.2714 | 2.5101 | 1.2778 | -0.04532 | -1.0758 | -1.7036 | -2.3846 | -3.0636 | -3.7483 | -5.8456 | -7.3396 | -8.7736 | 3.2802 | 2.9081 | 1.9556 | 0.89442 | -0.65515 | -2.3355 | -3.7393 | -4.6704 | -5.6749 | -6.6776 | -7.6841 | -11.0036 | -13.3818 | -15.4078
|  | DUNBLANE | CT |  |  |  | 2.0764 | 1.7936 | 1.0324 | 0.16873 | -1.0541 | -2.2495 | -3.1451 | -4.0747 | -5.1137 | -6.1567 | -7.2149 | -11.2918 | -14.4315 | -16.7136 | 4.3057 | 4.1088 | 3.6504 | 3.1061 | 2.1407 | 1.204 | 0.65591 | 0.11166 | -0.52263 | -1.1582 | -1.8075 | -4.1612 | -6.0183 | -7.8981 | 3.5813 | 3.3232 | 2.622 | 1.817 | 0.59047 | -0.61752 | -1.4415 | -2.2826 | -3.2389 | -4.1962 | -5.1611 | -8.717 | -11.3125 | -13.2051
|  | DUNBLANE | LW |  |  |  | 1.7338 | 1.3228 | 0.35357 | -0.73518 | -2.2724 | -3.9124 | -5.3361 | -6.3278 | -7.398 | -8.4692 | -9.5626 | -13.3366 | -16.1309 | -18.4015 | 4.1888 | 3.946 | 3.2714 | 2.5101 | 1.2778 | -0.04532 | -1.0758 | -1.7036 | -2.3846 | -3.0636 | -3.7483 | -5.8456 | -7.3396 | -8.7736 | 3.2802 | 2.9081 | 1.9556 | 0.89442 | -0.65515 | -2.3355 | -3.7393 | -4.6704 | -5.6749 | -6.6776 | -7.6841 | -11.0036 | -13.3818 | -15.4078
|  | DUNBLANE | ST |  |  |  | 2.2064 | 2.0673 | 1.4962 | 0.99754 | 0.44489 | -0.43413 | -0.93395 | -1.4043 | -1.8906 | -2.4088 | -3.014 | -6.4934 | -8.9021 | -11.2338 | 4.3783 | 4.2823 | 3.7001 | 3.2315 | 2.7544 | 1.8483 | 1.4196 | 1.0443 | 0.68495 | 0.29872 | -0.16592 | -2.6959 | -4.5097 | -6.4915 | 3.7015 | 3.5815 | 2.952 | 2.4291 | 1.8871 | 0.916 | 0.41975 | -0.029167 | -0.47441 | -0.9511 | -1.5142 | -4.7155 | -6.8558 | -8.8984
|  | DUNBLANE | FS |  |  |  | 2.2969 | 2.1885 | 1.9327 | 1.6405 | 1.2459 | 0.89181 | 0.54017 | 0.15936 | -0.25487 | -0.6851 | -1.1528 | -4.0545 | -6.9709 | -9.1533 | 4.4294 | 4.3482 | 4.1412 | 3.9091 | 3.5852 | 3.2991 | 3.016 | 2.7433 | 2.4515 | 2.1393 | 1.7924 | -0.3022 | -2.7323 | -5.223 | 3.7838 | 3.6911 | 3.4443 | 3.1663 | 2.7932 | 2.4577 | 2.1249 | 1.7801 | 1.4099 | 1.0225 | 0.59978 | -2.0038 | -4.6054 | -6.4669
| DUNOON | DUNOON | MINIMUM HEADROOM | NS 17135 77531 | NO | YES | 15.9424 | 15.7698 | 15.3993 | 15.0185 | 14.645 | 14.1974 | 13.711 | 13.2842 | 12.838 | 12.3764 | 11.9303 | 10.5814 | 9.3845 | 8.7436 | 18.0292 | 17.9168 | 17.7434 | 17.5575 | 17.3722 | 17.1349 | 16.8614 | 16.5927 | 16.3062 | 16.0101 | 15.7272 | 14.6874 | 13.8318 | 12.9777 | 17.7422 | 17.5715 | 17.2395 | 16.8942 | 16.5586 | 16.1395 | 15.685 | 15.2808 | 14.8567 | 14.4183 | 13.9954 | 12.7434 | 11.6244 | 11.0293
|  | DUNOON | CT |  |  |  | 16.1527 | 16.0512 | 15.6841 | 15.3042 | 14.9443 | 14.5721 | 14.2278 | 13.8046 | 13.3389 | 12.8733 | 12.4069 | 10.6184 | 9.3845 | 8.7436 | 18.0992 | 18.0135 | 17.8072 | 17.5868 | 17.3722 | 17.1475 | 16.951 | 16.6919 | 16.3962 | 16.0988 | 15.7992 | 14.6874 | 13.8318 | 12.9777 | 17.9208 | 17.8154 | 17.4761 | 17.1232 | 16.7843 | 16.4326 | 16.1142 | 15.7176 | 15.2784 | 14.8395 | 14.4001 | 12.7434 | 11.6244 | 11.0293
|  | DUNOON | LW |  |  |  | 15.9424 | 15.7698 | 15.3993 | 15.0185 | 14.645 | 14.1974 | 13.711 | 13.2842 | 12.838 | 12.3764 | 11.9303 | 10.5814 | 9.7725 | 9.3665 | 18.0292 | 17.9168 | 17.7434 | 17.5575 | 17.3799 | 17.1349 | 16.8614 | 16.5927 | 16.3062 | 16.0101 | 15.7272 | 14.9871 | 14.5373 | 14.1755 | 17.7422 | 17.5715 | 17.2395 | 16.8942 | 16.5586 | 16.1395 | 15.685 | 15.2808 | 14.8567 | 14.4183 | 13.9954 | 12.7466 | 11.9795 | 11.5394
|  | DUNOON | ST |  |  |  | 16.2627 | 16.2482 | 16.1885 | 16.1281 | 16.0596 | 15.9472 | 15.8432 | 15.6974 | 15.5385 | 15.3572 | 15.1589 | 13.7197 | 12.7522 | 11.5989 | 18.1564 | 18.1308 | 18.0591 | 17.9884 | 17.9157 | 17.7915 | 17.6897 | 17.5405 | 17.3917 | 17.2245 | 17.034 | 15.8492 | 15.0066 | 13.9463 | 18.0199 | 17.9998 | 17.9314 | 17.8652 | 17.7934 | 17.6692 | 17.5623 | 17.4072 | 17.2308 | 17.0305 | 16.8081 | 15.3264 | 14.4374 | 13.4502
|  | DUNOON | FS |  |  |  | 16.2576 | 16.2428 | 16.191 | 16.1341 | 16.0695 | 15.9913 | 15.9059 | 15.7655 | 15.6221 | 15.4659 | 15.2903 | 14.0557 | 12.6978 | 11.6563 | 18.1582 | 18.1343 | 18.0861 | 18.0326 | 17.9722 | 17.9009 | 17.8216 | 17.7013 | 17.5744 | 17.4333 | 17.2747 | 16.202 | 14.7754 | 13.0556 | 18.0169 | 17.9985 | 17.945 | 17.8883 | 17.8242 | 17.747 | 17.6626 | 17.5263 | 17.3873 | 17.2357 | 17.0651 | 15.8398 | 14.5404 | 13.6473
| DUNVEGAN | DUNVEGAN | MINIMUM HEADROOM | NG 27646 47150 | YES | YES | 3.3 | 3.3 | 3.2915 | 3.2857 | 3.2819 | 3.2687 | 3.2651 | 3.2552 | 3.2517 | 3.2488 | 3.244 | 3.2218 | 3.1892 | 3.1558 | 3.3 | 3.3 | 3.2893 | 3.2821 | 3.2773 | 3.2609 | 3.2564 | 3.244 | 3.2396 | 3.2359 | 3.23 | 3.2023 | 3.1615 | 3.1197 | 3.3 | 3.3 | 3.2893 | 3.2821 | 3.2773 | 3.2609 | 3.2564 | 3.244 | 3.2396 | 3.2359 | 3.23 | 3.2023 | 3.1615 | 3.1197
|  | DUNVEGAN | CT |  |  |  | 3.3 | 3.3 | 3.2989 | 3.2969 | 3.2874 | 3.2773 | 3.2747 | 3.2702 | 3.2657 | 3.2618 | 3.2575 | 3.2348 | 3.2134 | 3.1902 | 3.3 | 3.3 | 3.2986 | 3.2961 | 3.2843 | 3.2716 | 3.2684 | 3.2628 | 3.2571 | 3.2523 | 3.2469 | 3.2185 | 3.1917 | 3.1628 | 3.3 | 3.3 | 3.2986 | 3.2961 | 3.2843 | 3.2716 | 3.2684 | 3.2628 | 3.2571 | 3.2523 | 3.2469 | 3.2185 | 3.1917 | 3.1628
|  | DUNVEGAN | LW |  |  |  | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.2982 | 3.2964 | 3.2949 | 3.2932 | 3.2844 | 3.2446 | 3.1863 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.2978 | 3.2955 | 3.2937 | 3.2916 | 3.2805 | 3.2307 | 3.1579 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.2978 | 3.2955 | 3.2937 | 3.2916 | 3.2805 | 3.2307 | 3.1579
|  | DUNVEGAN | ST |  |  |  | 3.3 | 3.3 | 3.2915 | 3.2857 | 3.2819 | 3.2687 | 3.2651 | 3.2552 | 3.2517 | 3.2488 | 3.244 | 3.2218 | 3.1892 | 3.1558 | 3.3 | 3.3 | 3.2893 | 3.2821 | 3.2773 | 3.2609 | 3.2564 | 3.244 | 3.2396 | 3.2359 | 3.23 | 3.2023 | 3.1615 | 3.1197 | 3.3 | 3.3 | 3.2893 | 3.2821 | 3.2773 | 3.2609 | 3.2564 | 3.244 | 3.2396 | 3.2359 | 3.23 | 3.2023 | 3.1615 | 3.1197
|  | DUNVEGAN | FS |  |  |  | 3.3 | 3.3 | 3.2983 | 3.2965 | 3.2945 | 3.2924 | 3.2907 | 3.2871 | 3.2847 | 3.2823 | 3.2798 | 3.2769 | 3.2749 | 3.2711 | 3.3 | 3.3 | 3.2978 | 3.2956 | 3.2931 | 3.2905 | 3.2884 | 3.2839 | 3.2809 | 3.2778 | 3.2748 | 3.2711 | 3.2686 | 3.2639 | 3.3 | 3.3 | 3.2978 | 3.2956 | 3.2931 | 3.2905 | 3.2884 | 3.2839 | 3.2809 | 3.2778 | 3.2748 | 3.2711 | 3.2686 | 3.2639
| DYCE | DYCE NORTH | MINIMUM HEADROOM | NJ 89092 12705 | NO | YES | 8.8491 | 8.6724 | 8.3799 | 7.6354 | 6.8676 | 5.9766 | 5.1111 | 4.5289 | 3.7039 | 2.8074 | 1.9564 | -0.035727 | -0.40982 | -0.89165 | 11.1127 | 10.8365 | 10.474 | 9.9338 | 9.2841 | 8.4468 | 7.6446 | 7.0689 | 6.4382 | 5.7844 | 5.165 | 3.6995 | 3.1984 | 2.897 | 8.3582 | 8.0715 | 7.701 | 7.1876 | 6.4053 | 5.3947 | 4.4039 | 3.6807 | 2.8939 | 2.0773 | 1.3029 | -0.51798 | -1.0099 | -1.4213
|  | DYCE NORTH | CT |  |  |  | 8.8491 | 8.6724 | 8.3843 | 7.8839 | 7.2626 | 6.576 | 5.9443 | 5.2981 | 4.7622 | 4.2289 | 3.4821 | 1.1135 | 0.58018 | 0.30995 | 11.1127 | 10.8365 | 10.474 | 9.9531 | 9.437 | 8.8717 | 8.4027 | 7.9476 | 7.5629 | 7.1664 | 6.6385 | 5.0241 | 4.7628 | 4.6108 | 8.3582 | 8.0715 | 7.701 | 7.2011 | 6.57 | 5.859 | 5.2441 | 4.6229 | 4.1074 | 3.5948 | 2.9215 | 0.85734 | 0.47921 | 0.28137
|  | DYCE NORTH | LW |  |  |  | 8.8849 | 8.7288 | 8.3799 | 7.6354 | 6.8676 | 5.9766 | 5.1111 | 4.5289 | 3.7039 | 2.8074 | 1.9564 | -0.035727 | -0.36988 | -0.60191 | 11.1744 | 10.9341 | 10.5514 | 9.9338 | 9.2841 | 8.4468 | 7.6446 | 7.0689 | 6.4382 | 5.7844 | 5.165 | 3.6995 | 3.4371 | 3.1937 | 8.3931 | 8.1803 | 7.7977 | 7.1876 | 6.4053 | 5.3947 | 4.4039 | 3.6807 | 2.8939 | 2.0773 | 1.3029 | -0.51798 | -0.83028 | -1.0934
|  | DYCE NORTH | ST |  |  |  | 8.9407 | 8.886 | 8.6446 | 8.2743 | 8.084 | 7.644 | 7.2133 | 6.805 | 6.295 | 5.6467 | 4.9056 | 0.96028 | -0.40982 | -0.89165 | 11.2689 | 11.185 | 10.8617 | 10.39 | 10.1173 | 9.5684 | 9.1268 | 8.7343 | 8.2994 | 7.8016 | 7.2304 | 4.244 | 3.1984 | 2.897 | 8.4474 | 8.3945 | 8.1043 | 7.6589 | 7.3798 | 6.8225 | 6.3686 | 5.9626 | 5.4766 | 4.8495 | 4.131 | 0.31743 | -1.0099 | -1.4213
|  | DYCE NORTH | FS |  |  |  | 8.9577 | 8.9176 | 8.8301 | 8.6119 | 8.4863 | 8.3449 | 8.1264 | 7.9156 | 7.6432 | 7.3335 | 6.9102 | 4.1001 | 1.4352 | -0.49577 | 11.2956 | 11.2349 | 11.1093 | 10.8303 | 10.6501 | 10.4456 | 10.1633 | 9.9356 | 9.6748 | 9.3926 | 9.0783 | 7.0375 | 5.049 | 3.7558 | 8.4636 | 8.4248 | 8.3303 | 8.0962 | 7.9143 | 7.7072 | 7.4201 | 7.1881 | 6.9222 | 6.6322 | 6.2253 | 3.5328 | 0.98546 | -0.67204
| THURSO | EDAY | MINIMUM HEADROOM | HY 56341 33422 | YES | YES | 0.80899 | 0.80468 | 0.79395 | 0.78415 | 0.77066 | 0.76027 | 0.74993 | 0.71721 | 0.68344 | 0.64707 | 0.61172 | 0.46182 | 0.092944 | -0.42424 | 0.87761 | 0.87431 | 0.86785 | 0.86088 | 0.85401 | 0.84818 | 0.84223 | 0.80441 | 0.7632 | 0.72535 | 0.68598 | 0.50767 | 0.051554 | -0.59112 | 0.84217 | 0.83796 | 0.8282 | 0.81857 | 0.80635 | 0.79678 | 0.78721 | 0.74666 | 0.70473 | 0.66298 | 0.62159 | 0.43646 | -0.022148 | -0.66601
|  | EDAY | CT |  |  |  | 0.81527 | 0.80873 | 0.795 | 0.78415 | 0.77066 | 0.76027 | 0.74993 | 0.72495 | 0.6941 | 0.6676 | 0.63849 | 0.52396 | 0.34181 | 0.13297 | 0.87997 | 0.87565 | 0.86785 | 0.86088 | 0.85401 | 0.84818 | 0.84223 | 0.81264 | 0.77949 | 0.74972 | 0.71833 | 0.57917 | 0.35898 | 0.09806 | 0.84772 | 0.84155 | 0.82885 | 0.81857 | 0.80635 | 0.79678 | 0.78721 | 0.75655 | 0.72014 | 0.68837 | 0.65456 | 0.51487 | 0.2914 | 0.032018
|  | EDAY | LW |  |  |  | 0.80899 | 0.80468 | 0.79395 | 0.78766 | 0.77855 | 0.76418 | 0.75411 | 0.71721 | 0.68344 | 0.64707 | 0.61172 | 0.46182 | 0.092944 | -0.42424 | 0.87761 | 0.87431 | 0.86891 | 0.86484 | 0.85999 | 0.85185 | 0.84476 | 0.80441 | 0.7632 | 0.72535 | 0.68598 | 0.50767 | 0.051554 | -0.59112 | 0.84217 | 0.83796 | 0.8282 | 0.82226 | 0.81392 | 0.8006 | 0.79038 | 0.74666 | 0.70473 | 0.66298 | 0.62159 | 0.43646 | -0.022148 | -0.66601
|  | EDAY | ST |  |  |  | 0.82154 | 0.82002 | 0.8162 | 0.81071 | 0.80787 | 0.80447 | 0.80225 | 0.75031 | 0.72887 | 0.70913 | 0.67521 | 0.53415 | 0.25456 | -0.044442 | 0.88273 | 0.88159 | 0.87942 | 0.87639 | 0.8742 | 0.87154 | 0.86902 | 0.80944 | 0.78537 | 0.76355 | 0.7289 | 0.56781 | 0.22609 | -0.14373 | 0.8516 | 0.85075 | 0.84838 | 0.84334 | 0.84046 | 0.83685 | 0.83402 | 0.77159 | 0.74582 | 0.72122 | 0.68259 | 0.50789 | 0.16156 | -0.2106
|  | EDAY | FS |  |  |  | 0.8237 | 0.82091 | 0.81716 | 0.81183 | 0.8116 | 0.80734 | 0.80456 | 0.78216 | 0.76613 | 0.75115 | 0.73377 | 0.68032 | 0.63119 | 0.58805 | 0.88362 | 0.8821 | 0.88013 | 0.8774 | 0.87649 | 0.87394 | 0.87175 | 0.84823 | 0.8313 | 0.81454 | 0.79665 | 0.75048 | 0.70438 | 0.6522 | 0.85193 | 0.85128 | 0.84931 | 0.84448 | 0.84402 | 0.83997 | 0.83699 | 0.81107 | 0.79243 | 0.77447 | 0.75442 | 0.69809 | 0.64577 | 0.58249
| THURSO | EDAY TIDAL | MINIMUM HEADROOM | HY 54226 31320 | YES | YES | 0.15102 | 0.15102 | 0.14125 | 0.13464 | 0.13027 | 0.11527 | 0.11109 | 0.056318 | 0.036895 | 0.020449 | -0.005831 | -0.12905 | -0.50319 | -1.0836 | 0.11837 | 0.11837 | 0.10615 | 0.097888 | 0.092431 | 0.073673 | 0.068457 | -1.1247e-05 | -0.024289 | -0.044847 | -0.077697 | -0.23172 | -0.6994 | -1.4249 | -0.012245 | -0.012245 | -0.024463 | -0.032724 | -0.038182 | -0.056939 | -0.062155 | -0.13062 | -0.1549 | -0.17546 | -0.20831 | -0.36233 | -0.83001 | -1.5555
|  | EDAY TIDAL | CT |  |  |  | 0.15102 | 0.15102 | 0.14975 | 0.14749 | 0.13662 | 0.12503 | 0.12209 | 0.097194 | 0.072207 | 0.050594 | 0.026843 | -0.099267 | -0.29396 | -0.52433 | 0.11837 | 0.11837 | 0.11678 | 0.11395 | 0.10037 | 0.085883 | 0.08221 | 0.051085 | 0.019851 | -0.0071653 | -0.036854 | -0.19449 | -0.43786 | -0.72582 | -0.012245 | -0.012245 | -0.013836 | -0.016661 | -0.030245 | -0.04473 | -0.048402 | -0.079528 | -0.11076 | -0.13778 | -0.16747 | -0.3251 | -0.56847 | -0.85643
|  | EDAY TIDAL | LW |  |  |  | 0.15102 | 0.15102 | 0.15102 | 0.15102 | 0.15102 | 0.15102 | 0.15102 | 0.12324 | 0.094428 | 0.070724 | 0.044032 | -0.096296 | -0.50319 | -1.0836 | 0.11837 | 0.11837 | 0.11837 | 0.11837 | 0.11837 | 0.11837 | 0.11837 | 0.083638 | 0.047627 | 0.017997 | -0.015368 | -0.19078 | -0.6994 | -1.4249 | -0.012245 | -0.012245 | -0.012245 | -0.012245 | -0.012245 | -0.012245 | -0.012245 | -0.046974 | -0.082986 | -0.11262 | -0.14598 | -0.32139 | -0.83001 | -1.5555
|  | EDAY TIDAL | ST |  |  |  | 0.15102 | 0.15102 | 0.14125 | 0.13464 | 0.13027 | 0.11527 | 0.11109 | 0.056318 | 0.036895 | 0.020449 | -0.005831 | -0.12905 | -0.42929 | -0.76226 | 0.11837 | 0.11837 | 0.10615 | 0.097888 | 0.092431 | 0.073673 | 0.068457 | -1.1247e-05 | -0.024289 | -0.044847 | -0.077697 | -0.23172 | -0.60703 | -1.0232 | -0.012245 | -0.012245 | -0.024463 | -0.032724 | -0.038182 | -0.056939 | -0.062155 | -0.13062 | -0.1549 | -0.17546 | -0.20831 | -0.36233 | -0.73764 | -1.1538
|  | EDAY TIDAL | FS |  |  |  | 0.15102 | 0.15102 | 0.14902 | 0.14702 | 0.14469 | 0.14236 | 0.14036 | 0.12054 | 0.10709 | 0.093648 | 0.080202 | 0.063906 | 0.047159 | 0.0099558 | 0.11837 | 0.11837 | 0.11587 | 0.11337 | 0.11046 | 0.10755 | 0.10505 | 0.080265 | 0.063458 | 0.046652 | 0.029845 | 0.0094741 | -0.011459 | -0.057963 | -0.012245 | -0.012245 | -0.014743 | -0.017242 | -0.020154 | -0.023066 | -0.025564 | -0.050347 | -0.067154 | -0.08396 | -0.10077 | -0.12114 | -0.14207 | -0.18858
| FIDDES | EDZELL | MINIMUM HEADROOM | NO 63500 70513 | YES | YES | 1.8578 | 1.6847 | 1.442 | 1.2251 | 0.54027 | -0.19674 | -0.81988 | -1.3316 | -1.9141 | -2.5109 | -3.1163 | -4.0777 | -4.5604 | -4.9967 | 2.3403 | 2.2991 | 2.199 | 2.09 | 1.5204 | 0.87381 | 0.3603 | -0.10266 | -0.63802 | -1.1915 | -1.7786 | -2.8107 | -3.1773 | -3.4769 | 2.2978 | 2.1475 | 1.9232 | 1.7137 | 1.0495 | 0.33354 | -0.26406 | -0.75157 | -1.3063 | -1.874 | -2.4495 | -3.3988 | -3.8788 | -4.4206
|  | EDZELL | CT |  |  |  | 1.9964 | 1.8718 | 1.6355 | 1.4173 | 0.69346 | -0.031962 | -0.58075 | -1.1055 | -1.7499 | -2.3864 | -3.0205 | -4.0777 | -4.5604 | -4.8396 | 2.3426 | 2.3058 | 2.2394 | 2.1698 | 1.5416 | 0.9054 | 0.47757 | 0.01215 | -0.57575 | -1.1471 | -1.7347 | -2.6446 | -2.9318 | -3.2627 | 2.419 | 2.3115 | 2.0994 | 1.8942 | 1.188 | 0.47885 | -0.037427 | -0.53731 | -1.1528 | -1.7594 | -2.3645 | -3.3988 | -3.876 | -4.177
|  | EDZELL | LW |  |  |  | 1.8578 | 1.6847 | 1.442 | 1.2251 | 0.54027 | -0.19674 | -0.81988 | -1.3316 | -1.9141 | -2.5109 | -3.1163 | -4.0569 | -4.5396 | -4.9967 | 2.3403 | 2.2991 | 2.214 | 2.09 | 1.5204 | 0.87381 | 0.3603 | -0.10266 | -0.63802 | -1.1915 | -1.7516 | -2.5446 | -2.9742 | -3.465 | 2.2978 | 2.1475 | 1.9232 | 1.7137 | 1.0495 | 0.33354 | -0.26406 | -0.75157 | -1.3063 | -1.874 | -2.4495 | -3.3535 | -3.8788 | -4.4206
|  | EDZELL | ST |  |  |  | 2.0559 | 1.9821 | 1.7882 | 1.6477 | 1.0962 | 0.44295 | -0.016995 | -0.53038 | -1.1274 | -1.7121 | -2.3179 | -3.6084 | -4.1712 | -4.6352 | 2.3593 | 2.3405 | 2.199 | 2.1025 | 1.5563 | 0.88829 | 0.45213 | -0.044947 | -0.62314 | -1.1902 | -1.7786 | -2.8107 | -3.1773 | -3.4769 | 2.4724 | 2.4115 | 2.2097 | 2.0607 | 1.5306 | 0.87321 | 0.43069 | -0.069848 | -0.63787 | -1.194 | -1.774 | -3.0303 | -3.6084 | -4.0947
|  | EDZELL | FS |  |  |  | 2.0977 | 2.0405 | 1.9353 | 1.855 | 1.4466 | 1.0915 | 0.71746 | 0.30237 | -0.11363 | -0.56029 | -1.0271 | -2.5347 | -3.5308 | -3.8645 | 2.363 | 2.3468 | 2.303 | 2.2656 | 1.8784 | 1.5419 | 1.1918 | 0.8166 | 0.43621 | 0.031685 | -0.3988 | -1.4907 | -2.2251 | -2.498 | 2.509 | 2.4626 | 2.3668 | 2.2883 | 1.9 | 1.5614 | 1.2058 | 0.81114 | 0.41719 | -0.005394 | -0.4477 | -1.8574 | -2.7928 | -3.1011
| MILTON OF CRAIGIE | EDZELL STREET | MINIMUM HEADROOM | NO 47103 32070 | YES | YES | 8.8518 | 8.699 | 8.4409 | 8.166 | 7.9045 | 7.5464 | 7.154 | 6.7497 | 6.3183 | 5.8884 | 5.479 | 4.5403 | 3.8732 | 3.1303 | 8.8575 | 8.7506 | 8.6139 | 8.4621 | 8.2927 | 8.1114 | 7.8694 | 7.5805 | 7.2708 | 6.9638 | 6.6731 | 5.9266 | 5.3065 | 4.4649 | 8.4572 | 8.3078 | 8.0706 | 7.8161 | 7.5765 | 7.2414 | 6.872 | 6.4768 | 6.0556 | 5.637 | 5.2381 | 4.3234 | 3.5633 | 2.6569
|  | EDZELL STREET | CT |  |  |  | 8.9772 | 8.8831 | 8.5969 | 8.2937 | 8.027 | 7.759 | 7.5115 | 7.1499 | 6.7049 | 6.2555 | 5.8373 | 4.6405 | 4.0044 | 3.4889 | 8.9058 | 8.8316 | 8.6551 | 8.4621 | 8.2927 | 8.1189 | 7.9699 | 7.7213 | 7.4054 | 7.088 | 6.7953 | 5.9266 | 5.3065 | 4.5856 | 8.5665 | 8.4743 | 8.2048 | 7.9173 | 7.662 | 7.4042 | 7.1718 | 6.8213 | 6.389 | 5.9541 | 5.5499 | 4.3913 | 3.743 | 3.1872
|  | EDZELL STREET | LW |  |  |  | 8.8518 | 8.699 | 8.4409 | 8.166 | 7.9045 | 7.5464 | 7.154 | 6.7497 | 6.3183 | 5.8884 | 5.479 | 4.5403 | 3.8732 | 3.1303 | 8.8575 | 8.7506 | 8.6139 | 8.4626 | 8.3256 | 8.1114 | 7.8694 | 7.5805 | 7.2708 | 6.9638 | 6.6731 | 6.0293 | 5.3539 | 4.4649 | 8.4572 | 8.3078 | 8.0706 | 7.8161 | 7.5765 | 7.2414 | 6.872 | 6.4768 | 6.0556 | 5.637 | 5.2381 | 4.3234 | 3.5633 | 2.6569
|  | EDZELL STREET | ST |  |  |  | 9.0194 | 8.9885 | 8.9201 | 8.8497 | 8.7742 | 8.6621 | 8.5539 | 8.3622 | 8.181 | 7.979 | 7.7481 | 6.3714 | 5.5205 | 4.7344 | 8.9317 | 8.9039 | 8.8363 | 8.7673 | 8.6978 | 8.5853 | 8.489 | 8.2959 | 8.1329 | 7.9551 | 7.7456 | 6.5891 | 5.743 | 4.8363 | 8.6064 | 8.5758 | 8.5023 | 8.4279 | 8.3505 | 8.2293 | 8.119 | 7.9103 | 7.7256 | 7.5216 | 7.2852 | 5.9088 | 5.0157 | 4.1834
|  | EDZELL STREET | FS |  |  |  | 9.02 | 8.9956 | 8.949 | 8.8953 | 8.8315 | 8.7621 | 8.6843 | 8.5455 | 8.3995 | 8.2448 | 8.0726 | 7.0143 | 5.9286 | 5.3827 | 8.9336 | 8.9101 | 8.8699 | 8.8218 | 8.7675 | 8.706 | 8.6364 | 8.5141 | 8.3882 | 8.2516 | 8.1006 | 7.2092 | 6.1946 | 5.3245 | 8.6075 | 8.5834 | 8.537 | 8.4827 | 8.4191 | 8.3493 | 8.2712 | 8.1306 | 7.9855 | 7.8315 | 7.6603 | 6.6369 | 5.6009 | 5.1028
| ELGIN | ELGIN | MINIMUM HEADROOM | NJ 21256 64664 | NO | YES | 7.5108 | 6.7118 | 6.0315 | 5.3324 | 4.6397 | 3.8056 | 2.699 | 1.7833 | 0.81892 | -0.18169 | -1.1534 | -3.6703 | -4.7293 | -5.2554 | 8.779 | 8.2129 | 7.849 | 7.4734 | 7.1118 | 6.6427 | 5.9282 | 5.3438 | 4.717 | 4.0637 | 3.4376 | 1.5039 | 0.72828 | -0.067505 | 8.9096 | 8.3018 | 7.7844 | 7.2457 | 6.7102 | 5.9637 | 4.9465 | 4.0859 | 3.1727 | 2.2259 | 1.3109 | -1.0454 | -1.9787 | -2.4584
|  | ELGIN | CT |  |  |  | 7.8417 | 7.1936 | 6.5116 | 5.8165 | 5.1153 | 4.3611 | 3.4213 | 2.5011 | 1.4965 | 0.48142 | -0.48994 | -3.6701 | -4.7293 | -5.2554 | 8.9376 | 8.454 | 8.0433 | 7.6224 | 7.2085 | 6.7671 | 6.1696 | 5.6079 | 4.967 | 4.3207 | 3.7029 | 1.5039 | 0.72828 | -0.052295 | 9.1402 | 8.6513 | 8.1075 | 7.5431 | 6.9965 | 6.3793 | 5.5363 | 4.6938 | 3.7548 | 2.808 | 1.9044 | -1.0454 | -1.9787 | -2.4584
|  | ELGIN | LW |  |  |  | 7.5108 | 6.7118 | 6.0315 | 5.3324 | 4.6397 | 3.8056 | 2.699 | 1.7833 | 0.81892 | -0.18169 | -1.1534 | -3.6703 | -4.3365 | -4.795 | 8.779 | 8.2129 | 7.849 | 7.4734 | 7.1118 | 6.6427 | 5.9282 | 5.3438 | 4.717 | 4.0637 | 3.4376 | 1.7836 | 1.3771 | 0.97475 | 8.9096 | 8.3018 | 7.7844 | 7.2457 | 6.7102 | 5.9637 | 4.9465 | 4.0859 | 3.1727 | 2.2259 | 1.3109 | -1.0259 | -1.6532 | -2.1427
|  | ELGIN | ST |  |  |  | 7.9493 | 7.4098 | 7.0543 | 6.7057 | 6.3412 | 5.9261 | 5.3183 | 4.7866 | 4.1968 | 3.5564 | 2.8802 | -0.59482 | -1.886 | -2.8822 | 9.0036 | 8.6019 | 8.3568 | 8.1145 | 7.8622 | 7.5587 | 7.0804 | 6.67 | 6.2153 | 5.7204 | 5.1897 | 2.4389 | 1.3743 | 0.35294 | 9.2232 | 8.8317 | 8.5445 | 8.2599 | 7.965 | 7.6113 | 7.1161 | 6.6462 | 6.127 | 5.532 | 4.8533 | 1.4748 | 0.25614 | -0.64509
|  | ELGIN | FS |  |  |  | 8.1479 | 7.7203 | 7.4358 | 7.1361 | 6.8328 | 6.5198 | 6.0429 | 5.6008 | 5.1285 | 4.6291 | 4.1097 | 1.1716 | -1.0139 | -2.1942 | 9.1503 | 8.8302 | 8.6394 | 8.4354 | 8.2283 | 8.0117 | 7.6365 | 7.3081 | 6.9523 | 6.5699 | 6.1631 | 3.7578 | 1.7201 | -0.067505 | 9.3591 | 9.0446 | 8.8203 | 8.5806 | 8.3366 | 8.0807 | 7.6947 | 7.3202 | 6.9192 | 6.492 | 6.0422 | 3.2885 | 1.1824 | 0.097633
| ARBROATH | ELLIOT DEPOT | MINIMUM HEADROOM | NO 62251 40381 | YES | YES | -7.1216 | -7.518 | -7.9896 | -8.3414 | -8.5482 | -8.7157 | -8.8636 | -9.0312 | -9.2216 | -9.4343 | -9.6342 | -10.1959 | -10.6679 | -11.1275 | -7.528 | -7.9545 | -8.4707 | -8.8562 | -9.0982 | -9.323 | -9.4771 | -9.5773 | -9.6823 | -9.7882 | -9.8911 | -10.3323 | -10.7257 | -11.2121 | -8.0474 | -8.4472 | -8.9327 | -9.3006 | -9.5242 | -9.7249 | -9.922 | -10.0544 | -10.1916 | -10.3327 | -10.4675 | -10.9818 | -11.4731 | -12.0535
|  | ELLIOT DEPOT | CT |  |  |  | -6.9706 | -7.4059 | -7.8603 | -8.1059 | -8.3767 | -8.5843 | -8.6917 | -8.7904 | -8.8794 | -9.0998 | -9.3295 | -10.1736 | -10.6679 | -11.0168 | -7.3534 | -7.8225 | -8.308 | -8.555 | -8.8514 | -9.0827 | -9.2155 | -9.3513 | -9.4762 | -9.5934 | -9.7302 | -10.3323 | -10.7257 | -11.1217 | -7.8912 | -8.3288 | -8.7866 | -9.0335 | -9.329 | -9.5616 | -9.6693 | -9.7705 | -9.9305 | -10.0808 | -10.2473 | -10.9818 | -11.4731 | -11.8399
|  | ELLIOT DEPOT | LW |  |  |  | -7.1216 | -7.518 | -7.9896 | -8.3414 | -8.5482 | -8.7157 | -8.8636 | -9.0312 | -9.2216 | -9.4343 | -9.6342 | -10.1959 | -10.6336 | -11.1275 | -7.528 | -7.9545 | -8.4707 | -8.8562 | -9.0982 | -9.323 | -9.4771 | -9.5773 | -9.6823 | -9.7882 | -9.8911 | -10.2247 | -10.6581 | -11.2121 | -8.0474 | -8.4472 | -8.9327 | -9.3006 | -9.5242 | -9.7249 | -9.922 | -10.0544 | -10.1916 | -10.3327 | -10.4675 | -10.9685 | -11.4655 | -12.0535
|  | ELLIOT DEPOT | ST |  |  |  | -6.9614 | -7.3641 | -7.8693 | -8.1208 | -8.3021 | -8.528 | -8.6298 | -8.7559 | -8.827 | -8.899 | -9.0057 | -9.584 | -9.9216 | -10.1882 | -7.3475 | -7.7946 | -8.3665 | -8.6442 | -8.8413 | -9.1068 | -9.2145 | -9.3497 | -9.4142 | -9.4777 | -9.5815 | -10.1438 | -10.5738 | -11.1272 | -7.8836 | -8.2945 | -8.8323 | -9.1033 | -9.2965 | -9.5606 | -9.6705 | -9.8105 | -9.8827 | -9.9541 | -10.0635 | -10.6472 | -11.0256 | -11.3712
|  | ELLIOT DEPOT | FS |  |  |  | -6.4473 | -6.7802 | -7.1277 | -7.3077 | -7.4528 | -7.6015 | -7.7162 | -7.8462 | -8.0032 | -8.1463 | -8.2963 | -8.8503 | -9.1023 | -9.4131 | -6.7386 | -7.108 | -7.4923 | -7.6837 | -7.8393 | -8.0073 | -8.1351 | -8.2807 | -8.4556 | -8.6141 | -8.7809 | -9.3665 | -9.7542 | -10.2322 | -7.3449 | -7.6851 | -8.0435 | -8.2298 | -8.3819 | -8.539 | -8.6603 | -8.7979 | -8.9609 | -9.1094 | -9.2653 | -9.8138 | -10.0356 | -10.2528
| DYCE | ELLON | MINIMUM HEADROOM | NJ 95510 30054 | NO | YES | -0.35224 | 10.2017 | 9.3062 | 8.2904 | 7.2848 | 5.7851 | 4.2087 | 2.9086 | 1.5704 | 0.37899 | -0.75321 | -3.6003 | -4.9652 | -6.0465 | 2.506 | 12.7322 | 12.2318 | 11.6247 | 11.0154 | 9.9628 | 8.9027 | 8.0501 | 7.1569 | 6.4086 | 5.6661 | 3.9404 | 2.5393 | 1.0614 | 0.81838 | 10.8642 | 10.0168 | 9.0503 | 8.0783 | 6.6197 | 5.1489 | 4.0019 | 2.8215 | 1.7912 | 0.80178 | -1.8375 | -3.2007 | -4.2385
|  | ELLON | CT |  |  |  | 0.090447 | 10.8289 | 9.886 | 8.8762 | 7.9101 | 6.6591 | 5.4884 | 4.2631 | 2.901 | 1.7148 | 0.58325 | -2.9947 | -4.9652 | -6.0465 | 2.6566 | 12.9516 | 12.4064 | 11.8064 | 11.1919 | 10.288 | 9.5092 | 8.7093 | 7.7942 | 7.051 | 6.3352 | 3.9954 | 2.5393 | 1.0614 | 1.2431 | 11.4545 | 10.5959 | 9.6792 | 8.7518 | 7.5037 | 6.3901 | 5.2728 | 4.0544 | 3.0153 | 2.0084 | -1.2923 | -3.2007 | -4.2385
|  | ELLON | LW |  |  |  | -0.35224 | 10.2017 | 9.3062 | 8.2904 | 7.2848 | 5.7851 | 4.2087 | 2.9086 | 1.5704 | 0.37899 | -0.75321 | -3.6003 | -4.9628 | -5.8666 | 2.506 | 12.7322 | 12.2318 | 11.6247 | 11.0154 | 9.9628 | 8.9027 | 8.0501 | 7.1569 | 6.4086 | 5.6661 | 3.9404 | 3.1545 | 2.4361 | 0.81838 | 10.8642 | 10.0168 | 9.0503 | 8.0783 | 6.6197 | 5.1489 | 4.0019 | 2.8215 | 1.7912 | 0.80178 | -1.8375 | -3.1582 | -4.0717
|  | ELLON | ST |  |  |  | 0.32452 | 11.2802 | 10.9141 | 10.529 | 10.1581 | 9.382 | 8.6566 | 7.9046 | 7.0964 | 6.4065 | 5.6326 | 1.3363 | -0.94256 | -2.8839 | 2.7843 | 13.225 | 12.9158 | 12.6079 | 12.331 | 11.6149 | 11.0127 | 10.4154 | 9.7753 | 9.2614 | 8.6761 | 5.4041 | 3.5888 | 1.7841 | 1.4674 | 11.8703 | 11.5073 | 11.1434 | 10.8091 | 10.0093 | 9.33 | 8.6458 | 7.9234 | 7.3312 | 6.6606 | 2.5429 | 0.4232 | -1.3395
|  | ELLON | FS |  |  |  | 0.48747 | 11.4896 | 11.2503 | 10.9747 | 10.6803 | 10.226 | 9.68 | 9.0739 | 8.4523 | 7.8925 | 7.2934 | 3.5136 | 0.0091379 | -2.0437 | 2.9154 | 13.3793 | 13.2079 | 13.01 | 12.794 | 12.4124 | 11.958 | 11.497 | 11.0169 | 10.5991 | 10.1408 | 7.3358 | 4.1734 | 1.2917 | 1.6417 | 12.0867 | 11.8678 | 11.6205 | 11.3558 | 10.9153 | 10.4037 | 9.8488 | 9.2818 | 8.7843 | 8.2515 | 4.85 | 1.5556 | -0.29672
| TAYNUILT | EREDINE | MINIMUM HEADROOM | NM 97142 09376 | YES | YES | 0.13667 | 0.12982 | 0.11918 | 0.10502 | 0.091203 | 0.067334 | 0.058822 | 0.028608 | 0.019793 | 0.011892 | -0.0017683 | -0.067403 | -0.14153 | -0.21478 | 0.14617 | 0.1431 | 0.12413 | 0.10826 | 0.097275 | 0.0633 | 0.053106 | 0.023712 | 0.013414 | 0.0042897 | -0.010227 | -0.079605 | -0.16688 | -0.25538 | 0.13259 | 0.12646 | 0.11067 | 0.09378 | 0.081766 | 0.047671 | 0.037325 | 0.0032257 | -0.0073418 | -0.016732 | -0.032536 | -0.10814 | -0.19795 | -0.28742
|  | EREDINE | CT |  |  |  | 0.14061 | 0.13753 | 0.12987 | 0.12225 | 0.091203 | 0.067662 | 0.061252 | 0.04826 | 0.034137 | 0.023353 | 0.010279 | -0.04791 | -0.097816 | -0.14696 | 0.14755 | 0.14589 | 0.14031 | 0.13316 | 0.10423 | 0.07692 | 0.069391 | 0.055656 | 0.04113 | 0.028883 | 0.015248 | -0.049626 | -0.10748 | -0.1689 | 0.13595 | 0.13303 | 0.12528 | 0.1169 | 0.082381 | 0.053956 | 0.046258 | 0.031245 | 0.015132 | 0.002398 | -0.012589 | -0.08134 | -0.14136 | -0.20197
|  | EREDINE | LW |  |  |  | 0.13667 | 0.12982 | 0.12715 | 0.12601 | 0.12129 | 0.11369 | 0.10612 | 0.099745 | 0.092687 | 0.086539 | 0.080305 | 0.052628 | -0.031783 | -0.1497 | 0.14617 | 0.1431 | 0.14161 | 0.1406 | 0.13841 | 0.13472 | 0.13088 | 0.12418 | 0.11701 | 0.11072 | 0.10411 | 0.07637 | -0.025706 | -0.17311 | 0.13259 | 0.12646 | 0.12388 | 0.12262 | 0.11837 | 0.11147 | 0.10456 | 0.097324 | 0.089414 | 0.082539 | 0.07548 | 0.044103 | -0.059969 | -0.20737
|  | EREDINE | ST |  |  |  | 0.14287 | 0.1387 | 0.11918 | 0.10502 | 0.094747 | 0.067334 | 0.058822 | 0.028608 | 0.019793 | 0.011892 | -0.0017683 | -0.067403 | -0.14153 | -0.21478 | 0.14851 | 0.14682 | 0.12413 | 0.10826 | 0.097275 | 0.0633 | 0.053106 | 0.023712 | 0.013414 | 0.0042897 | -0.010227 | -0.079605 | -0.16688 | -0.25538 | 0.13791 | 0.13431 | 0.11067 | 0.09378 | 0.081766 | 0.047671 | 0.037325 | 0.0032257 | -0.0073418 | -0.016732 | -0.032536 | -0.10814 | -0.19795 | -0.28742
|  | EREDINE | FS |  |  |  | 0.14468 | 0.14075 | 0.1366 | 0.13071 | 0.12604 | 0.12127 | 0.11182 | 0.10179 | 0.093943 | 0.084096 | 0.07595 | 0.048204 | 0.034671 | 0.019265 | 0.14923 | 0.14758 | 0.14269 | 0.13714 | 0.13151 | 0.12578 | 0.11878 | 0.10825 | 0.1005 | 0.091936 | 0.083927 | 0.063962 | 0.050597 | 0.035391 | 0.1396 | 0.13606 | 0.13098 | 0.12443 | 0.11874 | 0.11294 | 0.10325 | 0.091659 | 0.082821 | 0.072218 | 0.063088 | 0.03553 | 0.021259 | 0.0048589
| INVERNESS | ERROGIE | MINIMUM HEADROOM | NH 56674 22810 | YES | YES | 0.86045 | 0.85252 | 0.83435 | 0.81751 | 0.80453 | 0.78538 | 0.7632 | 0.75402 | 0.74028 | 0.72971 | 0.71677 | 0.68896 | 0.66855 | 0.65865 | 0.90898 | 0.90409 | 0.89599 | 0.88802 | 0.88054 | 0.87174 | 0.86 | 0.85242 | 0.84219 | 0.83288 | 0.82334 | 0.80668 | 0.78788 | 0.77004 | 0.87884 | 0.8711 | 0.85503 | 0.8399 | 0.82819 | 0.81047 | 0.78991 | 0.78041 | 0.76721 | 0.75607 | 0.74283 | 0.71686 | 0.70007 | 0.69141
|  | ERROGIE | CT |  |  |  | 0.87416 | 0.86543 | 0.8468 | 0.8261 | 0.80931 | 0.79221 | 0.77164 | 0.76292 | 0.75159 | 0.73784 | 0.72746 | 0.70249 | 0.66855 | 0.65865 | 0.9136 | 0.90861 | 0.89905 | 0.88858 | 0.88054 | 0.87228 | 0.86276 | 0.85601 | 0.84707 | 0.83643 | 0.82773 | 0.80668 | 0.78788 | 0.77303 | 0.89049 | 0.88232 | 0.86533 | 0.84645 | 0.83144 | 0.81618 | 0.79801 | 0.78895 | 0.77788 | 0.7645 | 0.75353 | 0.72832 | 0.70007 | 0.69141
|  | ERROGIE | LW |  |  |  | 0.86045 | 0.85252 | 0.83435 | 0.81751 | 0.80453 | 0.78538 | 0.7632 | 0.75402 | 0.74028 | 0.72971 | 0.71677 | 0.68896 | 0.67645 | 0.66738 | 0.90898 | 0.90409 | 0.89599 | 0.88802 | 0.8818 | 0.87174 | 0.86 | 0.85242 | 0.84219 | 0.83288 | 0.82334 | 0.80723 | 0.8024 | 0.79926 | 0.87884 | 0.8711 | 0.85503 | 0.8399 | 0.82819 | 0.81047 | 0.78991 | 0.78041 | 0.76721 | 0.75607 | 0.74283 | 0.71686 | 0.70643 | 0.69911
|  | ERROGIE | ST |  |  |  | 0.87734 | 0.87045 | 0.86333 | 0.85555 | 0.84604 | 0.8372 | 0.8285 | 0.8167 | 0.8077 | 0.79088 | 0.78182 | 0.71638 | 0.68508 | 0.66925 | 0.91523 | 0.91198 | 0.90845 | 0.90439 | 0.89955 | 0.89462 | 0.88939 | 0.88267 | 0.87655 | 0.86715 | 0.86001 | 0.81373 | 0.79374 | 0.77774 | 0.89332 | 0.88727 | 0.88088 | 0.87382 | 0.86526 | 0.85708 | 0.84889 | 0.83788 | 0.82934 | 0.81386 | 0.80508 | 0.74112 | 0.71398 | 0.70102
|  | ERROGIE | FS |  |  |  | 0.88289 | 0.87816 | 0.87314 | 0.86402 | 0.85466 | 0.85243 | 0.84474 | 0.83388 | 0.8214 | 0.81325 | 0.80166 | 0.72659 | 0.68015 | 0.66519 | 0.91722 | 0.91475 | 0.91215 | 0.90784 | 0.90339 | 0.9012 | 0.89687 | 0.8912 | 0.88466 | 0.87946 | 0.87271 | 0.82789 | 0.79075 | 0.77004 | 0.89804 | 0.89382 | 0.88931 | 0.88122 | 0.87294 | 0.8705 | 0.86343 | 0.85356 | 0.84221 | 0.83459 | 0.82391 | 0.75473 | 0.71014 | 0.69786
| ABERNETHY | ERROL | MINIMUM HEADROOM | NO 23206 23038 | NO | YES | 4.0416 | 3.8579 | 3.4679 | 3.0349 | 2.4459 | 1.7993 | 1.2667 | 0.96353 | 0.63986 | 0.31812 | 0.0040874 | -0.82934 | -1.2071 | -1.4465 | 4.5339 | 4.4441 | 4.1602 | 3.8414 | 3.33 | 2.7688 | 2.3649 | 2.1581 | 1.9253 | 1.6934 | 1.4706 | 0.92952 | 0.70844 | 0.51246 | 4.904 | 4.7356 | 4.3373 | 3.8963 | 3.2626 | 2.5624 | 2.0109 | 1.7188 | 1.4066 | 1.0971 | 0.79537 | -0.0034087 | -0.36501 | -0.61234
|  | ERROL | CT |  |  |  | 4.2078 | 4.0826 | 3.775 | 3.423 | 2.9629 | 2.5089 | 2.1877 | 1.9196 | 1.6189 | 1.3135 | 1.0132 | 0.14261 | -0.43451 | -0.73187 | 4.591 | 4.5189 | 4.3507 | 4.1492 | 3.792 | 3.427 | 3.2327 | 3.083 | 2.8802 | 2.6739 | 2.476 | 1.9069 | 1.5311 | 1.1226 | 5.0502 | 4.9339 | 4.6459 | 4.314 | 3.84 | 3.3643 | 3.0571 | 2.807 | 2.524 | 2.237 | 1.9557 | 1.1481 | 0.62844 | 0.35328
|  | ERROL | LW |  |  |  | 4.0416 | 3.8579 | 3.4679 | 3.0349 | 2.4459 | 1.7993 | 1.2667 | 0.96353 | 0.63986 | 0.31812 | 0.0040874 | -0.82934 | -1.2071 | -1.4465 | 4.5339 | 4.4441 | 4.1602 | 3.8414 | 3.33 | 2.7688 | 2.3649 | 2.1581 | 1.9253 | 1.6934 | 1.4706 | 0.92952 | 0.70844 | 0.51246 | 4.904 | 4.7356 | 4.3373 | 3.8963 | 3.2626 | 2.5624 | 2.0109 | 1.7188 | 1.4066 | 1.0971 | 0.79537 | -0.0034087 | -0.36501 | -0.61234
|  | ERROL | ST |  |  |  | 4.2907 | 4.2327 | 3.9975 | 3.785 | 3.6001 | 3.254 | 3.0667 | 2.9132 | 2.7504 | 2.575 | 2.3771 | 1.2693 | 0.68929 | 0.17528 | 4.6313 | 4.5985 | 4.3586 | 4.1674 | 4.0156 | 3.6506 | 3.4951 | 3.3885 | 3.2647 | 3.1281 | 2.9731 | 2.1307 | 1.6787 | 1.2196 | 5.1266 | 5.0727 | 4.805 | 4.5773 | 4.3871 | 3.9876 | 3.7917 | 3.6429 | 3.4879 | 3.3206 | 3.1331 | 2.0801 | 1.5343 | 1.0687
|  | ERROL | FS |  |  |  | 4.3204 | 4.2797 | 4.1813 | 4.0603 | 3.9321 | 3.8067 | 3.6813 | 3.5458 | 3.4079 | 3.2592 | 3.104 | 2.0536 | 1.1653 | 0.6469 | 4.6448 | 4.619 | 4.5413 | 4.4526 | 4.3548 | 4.2572 | 4.1615 | 4.0806 | 3.9969 | 3.8952 | 3.7812 | 3.0378 | 2.2612 | 1.5939 | 5.1567 | 5.1184 | 5.0147 | 4.8959 | 4.7689 | 4.6416 | 4.5155 | 4.3897 | 4.2612 | 4.1224 | 3.977 | 3.0009 | 2.1724 | 1.7074
| FASNAKYLE | FASNAKYLE | MINIMUM HEADROOM | NH 31948 29998 | YES | NO | 0.48794 | 0.4838 | 0.45969 | 0.43671 | 0.41108 | 0.38145 | 0.3457 | 0.32631 | 0.30586 | 0.28475 | 0.26184 | 0.22098 | 0.19077 | 0.17631 | 0.59173 | 0.57957 | 0.56667 | 0.55247 | 0.53838 | 0.52389 | 0.50231 | 0.48361 | 0.46359 | 0.44311 | 0.42355 | 0.3962 | 0.37856 | 0.36511 | 0.48117 | 0.46598 | 0.4467 | 0.43104 | 0.41212 | 0.39175 | 0.36708 | 0.35435 | 0.34113 | 0.3209 | 0.29461 | 0.25435 | 0.22791 | 0.21481
|  | FASNAKYLE | CT |  |  |  | 0.48794 | 0.4843 | 0.47864 | 0.4455 | 0.41554 | 0.38646 | 0.35416 | 0.34117 | 0.32087 | 0.29673 | 0.27714 | 0.2328 | 0.19077 | 0.17631 | 0.59777 | 0.58895 | 0.57122 | 0.55247 | 0.53838 | 0.52431 | 0.50925 | 0.49565 | 0.47554 | 0.45391 | 0.43598 | 0.39884 | 0.37856 | 0.36511 | 0.49413 | 0.4835 | 0.46023 | 0.43809 | 0.41674 | 0.39547 | 0.37206 | 0.36371 | 0.35407 | 0.33584 | 0.31268 | 0.26535 | 0.22791 | 0.21481
|  | FASNAKYLE | LW |  |  |  | 0.48802 | 0.4838 | 0.45969 | 0.43671 | 0.41108 | 0.38145 | 0.3457 | 0.32631 | 0.30586 | 0.28475 | 0.26184 | 0.22098 | 0.19688 | 0.1893 | 0.59173 | 0.57957 | 0.56667 | 0.55407 | 0.54199 | 0.52389 | 0.50231 | 0.48361 | 0.46359 | 0.44311 | 0.42355 | 0.3962 | 0.38722 | 0.38467 | 0.48117 | 0.46598 | 0.4467 | 0.43104 | 0.41212 | 0.39175 | 0.36708 | 0.35435 | 0.34113 | 0.3209 | 0.29461 | 0.25435 | 0.23308 | 0.22651
|  | FASNAKYLE | ST |  |  |  | 0.48969 | 0.48852 | 0.4868 | 0.48459 | 0.48201 | 0.47883 | 0.46718 | 0.44963 | 0.42674 | 0.40965 | 0.387 | 0.27551 | 0.23521 | 0.21216 | 0.60116 | 0.59907 | 0.59248 | 0.58572 | 0.57805 | 0.56968 | 0.5605 | 0.54874 | 0.53391 | 0.51961 | 0.50261 | 0.41757 | 0.39384 | 0.3795 | 0.50047 | 0.49945 | 0.48906 | 0.48041 | 0.47031 | 0.46036 | 0.45049 | 0.43817 | 0.42221 | 0.41034 | 0.39409 | 0.30401 | 0.26714 | 0.24697
|  | FASNAKYLE | FS |  |  |  | 0.49006 | 0.48907 | 0.4878 | 0.48612 | 0.48431 | 0.48207 | 0.47955 | 0.46524 | 0.45297 | 0.4337 | 0.4173 | 0.29422 | 0.21677 | 0.19722 | 0.60423 | 0.60093 | 0.59645 | 0.59121 | 0.58469 | 0.57741 | 0.5709 | 0.56064 | 0.55172 | 0.54005 | 0.52855 | 0.44934 | 0.38756 | 0.37064 | 0.50738 | 0.50292 | 0.49623 | 0.48965 | 0.48002 | 0.46991 | 0.4631 | 0.4492 | 0.44088 | 0.42731 | 0.41603 | 0.3303 | 0.25118 | 0.23436
| TUMMEL BRIDGE | FINCASTLE | MINIMUM HEADROOM | NN 87976 61147 | YES | YES | 0.058653 | 0.055732 | 0.037842 | 0.022147 | 0.011542 | -0.023647 | -0.036046 | -0.063064 | -0.075563 | -0.086503 | -0.099341 | -0.17349 | -0.2613 | -0.34923 | 0.062897 | 0.06133 | 0.035239 | 0.015795 | 0.0027402 | -0.040996 | -0.054444 | -0.087836 | -0.10121 | -0.11289 | -0.12965 | -0.21323 | -0.32185 | -0.43173 | 0.053695 | 0.050979 | 0.026914 | 0.0073618 | -0.0058146 | -0.049702 | -0.064274 | -0.097896 | -0.11249 | -0.12523 | -0.14171 | -0.22996 | -0.33912 | -0.44901
|  | FINCASTLE | CT |  |  |  | 0.060668 | 0.057934 | 0.053694 | 0.043272 | 0.015489 | -0.013996 | -0.02362 | -0.038931 | -0.053118 | -0.065883 | -0.079353 | -0.14073 | -0.19773 | -0.25902 | 0.063661 | 0.062273 | 0.057428 | 0.048332 | 0.015652 | -0.019136 | -0.029093 | -0.045944 | -0.062911 | -0.078011 | -0.094061 | -0.17149 | -0.24243 | -0.31883 | 0.055419 | 0.052924 | 0.047799 | 0.036529 | 0.0027236 | -0.0332 | -0.044293 | -0.062423 | -0.079671 | -0.095311 | -0.11183 | -0.18863 | -0.2597 | -0.33619
|  | FINCASTLE | LW |  |  |  | 0.058653 | 0.055732 | 0.054928 | 0.052023 | 0.051238 | 0.045779 | 0.043915 | 0.036884 | 0.02577 | 0.022493 | 0.015361 | -0.011452 | -0.11623 | -0.2694 | 0.062897 | 0.06133 | 0.0606 | 0.059042 | 0.058337 | 0.055549 | 0.053864 | 0.045961 | 0.036369 | 0.030179 | 0.022471 | -0.0094665 | -0.14033 | -0.3318 | 0.053695 | 0.050979 | 0.050077 | 0.047373 | 0.046502 | 0.041499 | 0.039416 | 0.031133 | 0.019247 | 0.014047 | 0.0058281 | -0.026774 | -0.15768 | -0.34915
|  | FINCASTLE | ST |  |  |  | 0.060948 | 0.060674 | 0.037842 | 0.022147 | 0.011542 | -0.023647 | -0.036046 | -0.063064 | -0.075563 | -0.086503 | -0.099341 | -0.17349 | -0.2613 | -0.34923 | 0.063896 | 0.063648 | 0.035239 | 0.015795 | 0.0027402 | -0.040996 | -0.054444 | -0.087836 | -0.10121 | -0.11289 | -0.12965 | -0.21323 | -0.32185 | -0.43173 | 0.055709 | 0.055403 | 0.026914 | 0.0073618 | -0.0058146 | -0.049702 | -0.064274 | -0.097896 | -0.11249 | -0.12523 | -0.14171 | -0.22996 | -0.33912 | -0.44901
|  | FINCASTLE | FS |  |  |  | 0.061001 | 0.060776 | 0.055889 | 0.050907 | 0.045137 | 0.03734 | 0.030209 | 0.020098 | 0.01289 | 0.0071402 | -0.00043125 | -0.021413 | -0.037103 | -0.047518 | 0.063943 | 0.063739 | 0.057733 | 0.051638 | 0.044571 | 0.036744 | 0.029783 | 0.017393 | 0.008674 | 0.00041406 | -0.0085521 | -0.026979 | -0.040659 | -0.053401 | 0.055767 | 0.055515 | 0.049446 | 0.043268 | 0.036112 | 0.027238 | 0.01921 | 0.0066658 | -0.0022334 | -0.0099584 | -0.019248 | -0.04191 | -0.058517 | -0.071365
| SHETLAND | FIRTH | MINIMUM HEADROOM | HU4396874166 | YES | YES | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.95651 | 0.94109 | 0.9255 | 0.90074 | 0.77055 | 0.40915 | -0.1046 | -1.0496 | -1.5504 | -2.062 | -2.7637 | -3.4317 | -4.0468 | -4.5178 | -5.0198 | -5.6066 | -6.2111 | -6.2955 | -6.6563 | -7.162 | -7.8051 | -1.3686 | -1.837 | -2.3165 | -2.9468 | -3.5361 | -4.0965 | -4.5415 | -5.0151 | -5.5631 | -6.127 | -6.2495 | -6.6688 | -7.1732 | -7.8159
|  | FIRTH | CT |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.98023 | 0.96039 | 0.94323 | 0.92438 | 0.82425 | 0.65407 | 0.45016 | -0.95407 | -1.4239 | -1.9159 | -2.5663 | -3.2251 | -3.8356 | -4.3016 | -4.8198 | -5.4601 | -6.0847 | -6.1952 | -6.5849 | -6.8542 | -7.1326 | -1.2787 | -1.7179 | -2.1865 | -2.7963 | -3.3878 | -3.9405 | -4.3711 | -4.8545 | -5.4264 | -5.9867 | -6.1303 | -6.5973 | -6.8688 | -7.1487
|  | FIRTH | LW |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.97422 | 0.9475 | 0.9255 | 0.90074 | 0.77055 | 0.40915 | -0.1046 | -1.0496 | -1.5504 | -2.062 | -2.7637 | -3.4317 | -4.0468 | -4.5178 | -5.0198 | -5.6066 | -6.2111 | -6.2955 | -6.6563 | -7.162 | -7.8051 | -1.3686 | -1.837 | -2.3165 | -2.9468 | -3.5361 | -4.0965 | -4.5415 | -5.0151 | -5.5631 | -6.127 | -6.2495 | -6.6688 | -7.1732 | -7.8159
|  | FIRTH | ST |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.95651 | 0.94109 | 0.92803 | 0.90717 | 0.80934 | 0.54636 | 0.25164 | -0.93388 | -1.3852 | -1.8554 | -2.5227 | -3.1753 | -3.778 | -4.2326 | -4.7702 | -5.3985 | -6.0158 | -6.1294 | -6.6178 | -7.0525 | -7.4444 | -1.2433 | -1.6589 | -2.0921 | -2.678 | -3.2447 | -3.7889 | -4.2038 | -4.6991 | -5.2736 | -5.8377 | -5.9595 | -6.5959 | -7.0651 | -7.4675
|  | FIRTH | FS |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.98426 | 0.97358 | 0.96291 | 0.95223 | 0.9393 | 0.92488 | 0.89195 | -0.64193 | -0.98995 | -1.3543 | -1.8588 | -2.3553 | -2.8297 | -3.2648 | -3.7502 | -4.3134 | -4.8476 | -5.0797 | -5.9029 | -6.4535 | -6.6517 | -0.97938 | -1.2986 | -1.6369 | -2.1027 | -2.5488 | -2.9674 | -3.3552 | -3.7878 | -4.2881 | -4.7702 | -4.9916 | -5.8591 | -6.4467 | -6.6889
| FORT WILLIAM | FISHNISH | MINIMUM HEADROOM | NM 66623 42191 | YES | YES | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456
|  | FISHNISH | CT |  |  |  | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456
|  | FISHNISH | LW |  |  |  | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456
|  | FISHNISH | ST |  |  |  | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456
|  | FISHNISH | FS |  |  |  | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.2311 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21493 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456 | 0.21456
| THURSO | FLOTTA | MINIMUM HEADROOM | NC 94318 95432 | YES | YES | 0.8745 | 0.86685 | 0.85494 | 0.84682 | 0.84105 | 0.82874 | 0.81896 | 0.78599 | 0.75461 | 0.72404 | 0.69334 | 0.54431 | 0.17705 | -0.33723 | 0.92112 | 0.91727 | 0.91208 | 0.90743 | 0.90328 | 0.89754 | 0.893 | 0.85521 | 0.81784 | 0.78446 | 0.74804 | 0.56748 | 0.11289 | -0.52959 | 0.89615 | 0.88922 | 0.87878 | 0.87146 | 0.86577 | 0.85466 | 0.84573 | 0.80632 | 0.76817 | 0.73248 | 0.69468 | 0.50759 | 0.051123 | -0.59162
|  | FLOTTA | CT |  |  |  | 0.87876 | 0.87608 | 0.85943 | 0.84961 | 0.84131 | 0.82874 | 0.82016 | 0.79244 | 0.7692 | 0.74452 | 0.71887 | 0.60587 | 0.42266 | 0.21496 | 0.92269 | 0.92054 | 0.91283 | 0.90743 | 0.90328 | 0.89754 | 0.89316 | 0.86367 | 0.83522 | 0.80867 | 0.78046 | 0.64539 | 0.42698 | 0.16939 | 0.89982 | 0.89717 | 0.88236 | 0.87322 | 0.86577 | 0.85466 | 0.84692 | 0.81464 | 0.78599 | 0.75735 | 0.7273 | 0.58926 | 0.36552 | 0.10715
|  | FLOTTA | LW |  |  |  | 0.8745 | 0.86685 | 0.85494 | 0.84682 | 0.84105 | 0.82953 | 0.81896 | 0.78599 | 0.75461 | 0.72404 | 0.69334 | 0.54431 | 0.17705 | -0.33723 | 0.92112 | 0.91727 | 0.91208 | 0.90805 | 0.90499 | 0.89902 | 0.893 | 0.85559 | 0.81784 | 0.78446 | 0.74804 | 0.56748 | 0.11289 | -0.52959 | 0.89615 | 0.88922 | 0.87878 | 0.87146 | 0.86615 | 0.85565 | 0.84573 | 0.80632 | 0.76817 | 0.73248 | 0.69468 | 0.50759 | 0.051123 | -0.59162
|  | FLOTTA | ST |  |  |  | 0.88141 | 0.8822 | 0.87605 | 0.87437 | 0.8688 | 0.86505 | 0.86097 | 0.8127 | 0.78825 | 0.76779 | 0.74376 | 0.60531 | 0.32546 | 0.02481 | 0.92398 | 0.92395 | 0.92124 | 0.92004 | 0.91731 | 0.9151 | 0.91259 | 0.85521 | 0.83107 | 0.81024 | 0.78098 | 0.62549 | 0.28587 | -0.084847 | 0.90219 | 0.90281 | 0.89733 | 0.89572 | 0.89068 | 0.8872 | 0.88338 | 0.82453 | 0.79696 | 0.77372 | 0.74128 | 0.5728 | 0.22832 | -0.14529
|  | FLOTTA | FS |  |  |  | 0.8853 | 0.88102 | 0.88178 | 0.87675 | 0.8735 | 0.86893 | 0.86523 | 0.8436 | 0.82892 | 0.81547 | 0.79656 | 0.74664 | 0.70737 | 0.6605 | 0.92549 | 0.92364 | 0.92359 | 0.9213 | 0.91962 | 0.91737 | 0.91534 | 0.89268 | 0.87692 | 0.86149 | 0.8439 | 0.80608 | 0.76788 | 0.71273 | 0.90562 | 0.90181 | 0.9024 | 0.8979 | 0.89494 | 0.8908 | 0.8874 | 0.86237 | 0.84529 | 0.82926 | 0.80841 | 0.75789 | 0.7109 | 0.65079
| ELGIN | FOCHABERS | MINIMUM HEADROOM | NC 94318 95432 | NO | YES | 7.6384 | 7.3699 | 6.9441 | 6.5169 | 5.0663 | 3.3487 | 2.6499 | 1.9628 | 1.2033 | 0.42931 | -0.34068 | -1.7619 | -2.8455 | -3.5298 | 8.5823 | 8.4205 | 8.177 | 7.9188 | 6.5173 | 4.8173 | 4.2539 | 3.585 | 2.8281 | 2.0563 | 1.2844 | -0.0085104 | -1.0375 | -1.6434 | 8.1248 | 7.8865 | 7.5173 | 7.1362 | 5.7213 | 4.0198 | 3.3381 | 2.629 | 1.8374 | 1.03 | 0.22498 | -1.346 | -2.2209 | -3.1151
|  | FOCHABERS | CT |  |  |  | 7.64 | 7.4928 | 7.2289 | 6.8096 | 5.3854 | 3.8024 | 3.237 | 2.5537 | 1.7622 | 1.007 | 0.25384 | -1.2464 | -2.1148 | -2.6127 | 8.6117 | 8.4531 | 8.205 | 7.9654 | 6.5953 | 5.0459 | 4.6397 | 4.0226 | 3.3016 | 2.623 | 1.9185 | 0.61728 | 0.15309 | -0.23516 | 8.2368 | 8.074 | 7.7034 | 7.3415 | 5.9592 | 4.4034 | 3.8762 | 3.1951 | 2.4178 | 1.6796 | 0.91927 | -0.6606 | -1.3747 | -1.8717
|  | FOCHABERS | LW |  |  |  | 7.6384 | 7.3699 | 6.9441 | 6.5169 | 5.0663 | 3.3487 | 2.6499 | 1.9628 | 1.2033 | 0.42931 | -0.34068 | -1.7619 | -2.6328 | -3.3996 | 8.5823 | 8.4205 | 8.177 | 7.9188 | 6.5173 | 4.8173 | 4.2539 | 3.585 | 2.8281 | 2.0563 | 1.2844 | -0.0085104 | -0.78288 | -1.6424 | 8.1248 | 7.8865 | 7.5173 | 7.1362 | 5.7213 | 4.0198 | 3.3381 | 2.629 | 1.8374 | 1.03 | 0.22498 | -1.346 | -2.2209 | -3.1151
|  | FOCHABERS | ST |  |  |  | 7.6998 | 7.6452 | 7.4786 | 7.3326 | 6.1984 | 4.8101 | 4.3993 | 3.719 | 2.911 | 2.0849 | 1.1923 | -1.6078 | -2.8455 | -3.5298 | 8.6897 | 8.6289 | 8.4354 | 8.2662 | 7.0518 | 5.5571 | 5.1947 | 4.5743 | 3.8502 | 3.1249 | 2.3345 | 0.020827 | -1.0375 | -1.6434 | 8.2917 | 8.2429 | 8.0565 | 7.849 | 6.713 | 5.2976 | 4.907 | 4.2712 | 3.5182 | 2.7226 | 1.8641 | -0.79222 | -2.1318 | -2.9765
|  | FOCHABERS | FS |  |  |  | 7.7168 | 7.6743 | 7.5932 | 7.5118 | 6.701 | 5.8911 | 5.587 | 5.1065 | 4.5569 | 3.9744 | 3.3703 | 1.0196 | -1.1221 | -2.2481 | 8.7165 | 8.6703 | 8.5812 | 8.4893 | 7.6214 | 6.759 | 6.4348 | 5.9325 | 5.43 | 4.901 | 4.3595 | 2.4841 | 0.75652 | -0.11658 | 8.3067 | 8.269 | 8.1918 | 8.113 | 7.2843 | 6.4598 | 6.1434 | 5.6162 | 5.0881 | 4.5336 | 3.9648 | 1.6928 | -0.3668 | -1.481
| NAIRN | FORRES | MINIMUM HEADROOM | NJ 03362 59425 | NO | YES | 2.9311 | 1.8639 | 0.22314 | -1.4855 | -3.4535 | -5.672 | -7.687 | -9.3106 | -10.8665 | -12.4253 | -14.0076 | -18.5745 | -20.4697 | -22.0382 | 6.3812 | 5.665 | 4.5854 | 3.4015 | 1.9331 | 0.20273 | -1.3099 | -2.5536 | -3.7108 | -4.8652 | -6.0164 | -10.7623 | -13.4992 | -14.776 | 5.5925 | 4.6344 | 3.1536 | 1.5787 | -0.29702 | -2.4764 | -4.4346 | -6.0229 | -7.557 | -9.0746 | -10.5978 | -14.8887 | -18.1241 | -19.5524
|  | FORRES | CT |  |  |  | 3.4553 | 2.5987 | 1.0542 | -0.56201 | -2.4657 | -4.4626 | -6.0547 | -7.6686 | -9.2318 | -10.721 | -12.2229 | -17.203 | -19.4089 | -20.6923 | 6.5761 | 5.9552 | 4.9782 | 3.8894 | 2.4779 | 0.96131 | -0.10676 | -1.2767 | -2.4122 | -3.497 | -4.5719 | -8.2547 | -9.8415 | -11.3269 | 5.7759 | 4.8907 | 3.7118 | 2.3456 | 0.56369 | -1.3502 | -2.7951 | -4.3116 | -5.8214 | -7.2588 | -8.6834 | -13.4187 | -15.4191 | -16.6451
|  | FORRES | LW |  |  |  | 2.9311 | 1.8639 | 0.22314 | -1.4855 | -3.4535 | -5.672 | -7.687 | -9.3106 | -10.8665 | -12.4253 | -14.0076 | -18.5745 | -20.4697 | -22.0382 | 6.3812 | 5.665 | 4.5854 | 3.4015 | 1.9331 | 0.20273 | -1.3099 | -2.5536 | -3.7108 | -4.8652 | -6.0164 | -9.2915 | -10.6968 | -12.3381 | 5.5925 | 4.6344 | 3.1536 | 1.5787 | -0.29702 | -2.4764 | -4.4346 | -6.0229 | -7.557 | -9.0746 | -10.5978 | -14.8887 | -16.8017 | -18.6006
|  | FORRES | ST |  |  |  | 3.7939 | 3.208 | 2.1436 | 1.1293 | 0.13593 | -1.309 | -2.3844 | -3.654 | -4.759 | -6.1083 | -7.8282 | -16.2728 | -19.4625 | -20.78 | 6.7538 | 6.33 | 5.3813 | 4.4929 | 3.6667 | 2.2846 | 1.3168 | -0.048472 | -1.1995 | -2.4434 | -3.8682 | -10.7623 | -13.4992 | -14.776 | 6.0543 | 5.5304 | 4.4618 | 3.3992 | 2.3572 | 0.69757 | -0.56415 | -2.0675 | -3.418 | -4.8919 | -6.5809 | -14.8797 | -18.1241 | -19.5524
|  | FORRES | FS |  |  |  | 4.0741 | 3.6144 | 2.9539 | 2.2436 | 1.4827 | 0.71441 | -0.094439 | -1.0355 | -1.9175 | -2.8008 | -3.7405 | -9.0413 | -13.9507 | -17.0639 | 6.9552 | 6.6185 | 6.1194 | 5.5556 | 4.9543 | 4.3279 | 3.6594 | 2.8995 | 2.2076 | 1.5015 | 0.75199 | -3.9398 | -8.1007 | -10.5482 | 6.3089 | 5.906 | 5.3391 | 4.6757 | 3.9569 | 3.1837 | 2.3337 | 1.3904 | 0.50938 | -0.4114 | -1.4019 | -7.0454 | -12.1192 | -15.1303
| THURSO | FORSS | MINIMUM HEADROOM | ND 02614 69148 | YES | YES | 0.019545 | -0.024443 | -0.065386 | -0.11016 | -0.16063 | -0.21343 | -0.2723 | -0.33235 | -0.42241 | -0.52942 | -0.63401 | -0.92767 | -1.3124 | -1.8349 | 0.42961 | 0.40806 | 0.38868 | 0.36612 | 0.3433 | 0.31582 | 0.28344 | 0.20212 | 0.10724 | 0.014729 | -0.076913 | -0.35912 | -0.81972 | -1.4652 | 0.078787 | 0.039587 | 0.0032846 | -0.041835 | -0.089906 | -0.14685 | -0.22438 | -0.32706 | -0.43703 | -0.54591 | -0.65322 | -0.97123 | -1.4434 | -2.0933
|  | FORSS | CT |  |  |  | 0.049359 | 0.019567 | -0.036147 | -0.097804 | -0.14628 | -0.20489 | -0.25851 | -0.30437 | -0.35282 | -0.40216 | -0.46799 | -0.73711 | -0.95735 | -1.1768 | 0.43971 | 0.42382 | 0.3959 | 0.36612 | 0.3433 | 0.3166 | 0.2914 | 0.24528 | 0.1885 | 0.13454 | 0.063772 | -0.18877 | -0.42193 | -0.68306 | 0.10431 | 0.069861 | 0.0093046 | -0.041835 | -0.089906 | -0.14497 | -0.20029 | -0.27496 | -0.34071 | -0.40432 | -0.48702 | -0.77353 | -1.0305 | -1.2991
|  | FORSS | LW |  |  |  | 0.019545 | -0.024443 | -0.065386 | -0.11016 | -0.16063 | -0.21343 | -0.2723 | -0.33235 | -0.42241 | -0.52942 | -0.63401 | -0.92767 | -1.3124 | -1.8349 | 0.42961 | 0.40806 | 0.38868 | 0.367 | 0.34421 | 0.31582 | 0.28344 | 0.20212 | 0.10724 | 0.014729 | -0.076913 | -0.35912 | -0.81972 | -1.4652 | 0.078787 | 0.039587 | 0.0032846 | -0.03664 | -0.080737 | -0.14685 | -0.22438 | -0.32706 | -0.43703 | -0.54591 | -0.65322 | -0.97123 | -1.4434 | -2.0933
|  | FORSS | ST |  |  |  | 0.068097 | 0.052959 | 0.031272 | 0.0076436 | -0.015711 | -0.044113 | -0.071511 | -0.1475 | -0.19515 | -0.24869 | -0.33686 | -0.81157 | -1.2038 | -1.5273 | 0.45061 | 0.44316 | 0.43276 | 0.42096 | 0.4088 | 0.39395 | 0.37841 | 0.3054 | 0.26595 | 0.21133 | 0.13265 | -0.26658 | -0.68117 | -1.0611 | 0.12164 | 0.10799 | 0.088446 | 0.067258 | 0.046275 | 0.015546 | -0.023619 | -0.12455 | -0.19746 | -0.2773 | -0.37097 | -0.8517 | -1.3014 | -1.6952
|  | FORSS | FS |  |  |  | 0.0854 | 0.069019 | 0.055536 | 0.033798 | 0.014919 | -0.0036912 | -0.027115 | -0.074884 | -0.11402 | -0.15233 | -0.19618 | -0.46641 | -0.72238 | -0.89529 | 0.45751 | 0.44984 | 0.44295 | 0.43248 | 0.42281 | 0.41269 | 0.4003 | 0.36453 | 0.33555 | 0.30613 | 0.27395 | 0.072247 | -0.12074 | -0.26381 | 0.13124 | 0.12227 | 0.11004 | 0.090449 | 0.073309 | 0.056284 | 0.030215 | -0.023516 | -0.072465 | -0.12327 | -0.18051 | -0.48091 | -0.72814 | -0.90204
| BRACO | FORTEVIOT | MINIMUM HEADROOM | NO 04539 18092 | YES | YES | 5.3423 | 5.2067 | 4.9486 | 4.7148 | 4.3548 | 3.9559 | 3.6583 | 3.5144 | 3.3668 | 3.2091 | 3.055 | 2.632 | 2.4234 | 2.2655 | 5.5045 | 5.4279 | 5.2157 | 5.0007 | 4.6295 | 4.2128 | 3.9281 | 3.8104 | 3.6858 | 3.5619 | 3.4424 | 3.1283 | 2.9718 | 2.8149 | 5.1386 | 5.0208 | 4.7557 | 4.4989 | 4.0859 | 3.6225 | 3.2874 | 3.1306 | 2.9674 | 2.8024 | 2.6435 | 2.2179 | 2.0085 | 1.8313
|  | FORTEVIOT | CT |  |  |  | 5.4101 | 5.3052 | 5.1403 | 4.9884 | 4.7277 | 4.449 | 4.2822 | 4.1523 | 4.0128 | 3.8792 | 3.7411 | 3.3376 | 3.0955 | 2.9577 | 5.5269 | 5.4627 | 5.356 | 5.2419 | 4.9952 | 4.7314 | 4.6135 | 4.5244 | 4.4192 | 4.3154 | 4.2169 | 3.9313 | 3.7554 | 3.572 | 5.193 | 5.1014 | 4.9453 | 4.7886 | 4.5009 | 4.1939 | 4.03 | 3.9005 | 3.7533 | 3.6102 | 3.4729 | 3.0833 | 2.8648 | 2.7317
|  | FORTEVIOT | LW |  |  |  | 5.3423 | 5.2067 | 4.9486 | 4.7148 | 4.3548 | 3.9559 | 3.6583 | 3.5144 | 3.3668 | 3.2091 | 3.055 | 2.632 | 2.4234 | 2.2655 | 5.5045 | 5.4279 | 5.2157 | 5.0007 | 4.6295 | 4.2128 | 3.9281 | 3.8104 | 3.6858 | 3.5619 | 3.4424 | 3.1283 | 2.9718 | 2.8149 | 5.1386 | 5.0208 | 4.7557 | 4.4989 | 4.0859 | 3.6225 | 3.2874 | 3.1306 | 2.9674 | 2.8024 | 2.6435 | 2.2179 | 2.0085 | 1.8313
|  | FORTEVIOT | ST |  |  |  | 5.4404 | 5.3645 | 5.168 | 5.0429 | 4.9411 | 4.6839 | 4.5688 | 4.492 | 4.4193 | 4.34 | 4.2546 | 3.7404 | 3.4633 | 3.2368 | 5.5414 | 5.4995 | 5.2953 | 5.1562 | 5.0509 | 4.7546 | 4.6391 | 4.5693 | 4.5058 | 4.4361 | 4.3573 | 3.9325 | 3.7015 | 3.4821 | 5.2195 | 5.1585 | 4.9376 | 4.789 | 4.6726 | 4.3639 | 4.2339 | 4.1496 | 4.0697 | 3.9821 | 3.8867 | 3.3606 | 3.0915 | 2.8831
|  | FORTEVIOT | FS |  |  |  | 5.4665 | 5.401 | 5.3194 | 5.2583 | 5.1901 | 5.1162 | 5.0501 | 4.9876 | 4.9269 | 4.8642 | 4.7999 | 4.3607 | 3.9681 | 3.7575 | 5.5514 | 5.5141 | 5.448 | 5.3907 | 5.3255 | 5.2564 | 5.1917 | 5.1448 | 5.097 | 5.0453 | 4.9897 | 4.6461 | 4.2916 | 4.0173 | 5.2404 | 5.1885 | 5.1087 | 5.0423 | 4.9679 | 4.8875 | 4.8139 | 4.7513 | 4.6891 | 4.6236 | 4.5549 | 4.1128 | 3.7264 | 3.5441
| INVERNESS | FOYERS | MINIMUM HEADROOM | NH 49740 21044 | YES | YES | 0.61717 | 0.60414 | 0.58684 | 0.56343 | 0.51301 | 0.45844 | 0.42431 | 0.39035 | 0.35711 | 0.33051 | 0.29816 | 0.17569 | 0.049033 | -0.083154 | 0.69333 | 0.68503 | 0.65823 | 0.62949 | 0.60163 | 0.54512 | 0.52178 | 0.4715 | 0.44619 | 0.42352 | 0.39054 | 0.23496 | 0.078574 | -0.073245 | 0.6045 | 0.59096 | 0.57265 | 0.54594 | 0.48794 | 0.42633 | 0.39235 | 0.3556 | 0.3191 | 0.28916 | 0.25376 | 0.10592 | -0.057458 | -0.21504
|  | FOYERS | CT |  |  |  | 0.62744 | 0.61634 | 0.59443 | 0.56343 | 0.51301 | 0.45844 | 0.42431 | 0.39035 | 0.35711 | 0.33051 | 0.29816 | 0.17569 | 0.070495 | -0.016897 | 0.69698 | 0.69027 | 0.67429 | 0.65193 | 0.60163 | 0.54831 | 0.52591 | 0.49449 | 0.46096 | 0.43118 | 0.39894 | 0.26798 | 0.16275 | 0.056618 | 0.61448 | 0.60388 | 0.58042 | 0.54674 | 0.48794 | 0.42633 | 0.39235 | 0.3556 | 0.3191 | 0.28916 | 0.25376 | 0.11367 | -0.0065419 | -0.11314
|  | FOYERS | LW |  |  |  | 0.61717 | 0.60414 | 0.58684 | 0.57113 | 0.54852 | 0.5227 | 0.49797 | 0.47426 | 0.44709 | 0.4205 | 0.39655 | 0.32408 | 0.17418 | -0.041212 | 0.69333 | 0.68503 | 0.67583 | 0.66652 | 0.65654 | 0.64201 | 0.62633 | 0.60379 | 0.57915 | 0.55542 | 0.53273 | 0.46636 | 0.2904 | 0.03029 | 0.6045 | 0.59096 | 0.57265 | 0.55619 | 0.53571 | 0.5118 | 0.48858 | 0.46378 | 0.4357 | 0.40849 | 0.38351 | 0.30568 | 0.12294 | -0.1417
|  | FOYERS | ST |  |  |  | 0.63907 | 0.63248 | 0.59739 | 0.5722 | 0.55093 | 0.49599 | 0.4716 | 0.42762 | 0.40127 | 0.37997 | 0.34597 | 0.18716 | 0.049033 | -0.083154 | 0.70198 | 0.69857 | 0.65823 | 0.62949 | 0.60787 | 0.54512 | 0.52178 | 0.4715 | 0.44619 | 0.42352 | 0.39054 | 0.23496 | 0.078574 | -0.073245 | 0.6245 | 0.61857 | 0.5762 | 0.54594 | 0.52147 | 0.4555 | 0.42775 | 0.37496 | 0.34499 | 0.3196 | 0.28143 | 0.10592 | -0.057458 | -0.21504
|  | FOYERS | FS |  |  |  | 0.64216 | 0.63591 | 0.62305 | 0.60981 | 0.59807 | 0.58274 | 0.56817 | 0.54464 | 0.52771 | 0.50812 | 0.4851 | 0.39008 | 0.32278 | 0.28961 | 0.70329 | 0.70017 | 0.68912 | 0.67749 | 0.66538 | 0.65169 | 0.63868 | 0.61658 | 0.59976 | 0.58169 | 0.56202 | 0.49541 | 0.44277 | 0.41275 | 0.62729 | 0.62175 | 0.60807 | 0.5937 | 0.58019 | 0.56333 | 0.54672 | 0.51954 | 0.50017 | 0.4781 | 0.4527 | 0.36047 | 0.2945 | 0.25987
| FRASERBURGH | FRASERBURGH | MINIMUM HEADROOM | NH 51502 69028 | NO | YES | 19.377 | 18.7069 | 17.6052 | 16.4296 | 15.1434 | 13.6818 | 11.8438 | 9.886 | 8.3494 | 6.879 | 5.4359 | 1.8104 | -0.20717 | -1.7752 | 23.4288 | 23.2105 | 22.9279 | 22.6218 | 22.1946 | 21.4919 | 20.2987 | 18.8089 | 17.7163 | 16.7148 | 15.7242 | 13.4603 | 11.7657 | 9.7845 | 21.6768 | 21.0827 | 20.1008 | 19.0529 | 17.8784 | 16.5504 | 14.8844 | 13.0451 | 11.6558 | 10.2654 | 8.9003 | 5.5123 | 3.5191 | 1.8135
|  | FRASERBURGH | CT |  |  |  | 20.044 | 19.583 | 18.4207 | 17.1874 | 15.9306 | 14.6669 | 13.1657 | 11.3056 | 9.7445 | 8.2812 | 6.8416 | 2.8134 | 0.014335 | -1.7009 | 23.4288 | 23.2105 | 22.9279 | 22.6218 | 22.1946 | 21.7498 | 20.8286 | 19.4641 | 18.3525 | 17.3615 | 16.3806 | 13.731 | 11.7657 | 9.7845 | 22.2607 | 21.8357 | 20.811 | 19.7309 | 18.5703 | 17.4079 | 16.0527 | 14.3078 | 12.8843 | 11.5877 | 10.2368 | 6.4908 | 3.9291 | 2.3325
|  | FRASERBURGH | LW |  |  |  | 19.377 | 18.7069 | 17.6052 | 16.4296 | 15.1434 | 13.6818 | 11.8438 | 9.886 | 8.3494 | 6.879 | 5.4359 | 1.8104 | -0.20717 | -1.7752 | 23.4512 | 23.2946 | 23.0826 | 22.8348 | 22.3731 | 21.4919 | 20.2987 | 18.8089 | 17.7163 | 16.7148 | 15.7242 | 13.4603 | 12.0416 | 10.5668 | 21.6768 | 21.0827 | 20.1008 | 19.0529 | 17.8784 | 16.5504 | 14.8844 | 13.0451 | 11.6558 | 10.2654 | 8.9003 | 5.5123 | 3.5191 | 1.8135
|  | FRASERBURGH | ST |  |  |  | 20.4651 | 20.2949 | 19.9189 | 19.5343 | 19.0994 | 18.5196 | 17.7191 | 16.4068 | 15.4257 | 14.4982 | 13.4917 | 8.9375 | 6.2654 | 3.6852 | 23.5026 | 23.4405 | 23.2074 | 22.9995 | 22.7576 | 22.3691 | 21.7744 | 20.5129 | 19.7255 | 19.0978 | 18.4015 | 15.9727 | 13.683 | 11.2003 | 22.638 | 22.4902 | 22.1339 | 21.7925 | 21.4144 | 20.8714 | 20.1477 | 18.8556 | 17.9561 | 17.154 | 16.2678 | 12.0396 | 9.4231 | 6.8592
|  | FRASERBURGH | FS |  |  |  | 20.5501 | 20.4198 | 20.1448 | 19.8391 | 19.475 | 19.1114 | 18.4869 | 17.4664 | 16.7404 | 16.0105 | 15.2325 | 11.0051 | 7.086 | 4.5943 | 23.525 | 23.4773 | 23.3833 | 23.2745 | 23.1139 | 22.9679 | 22.5512 | 21.6767 | 21.2006 | 20.7733 | 20.3057 | 17.8448 | 14.2496 | 10.6468 | 22.7142 | 22.602 | 22.3642 | 22.106 | 21.7919 | 21.487 | 20.9252 | 19.9307 | 19.2675 | 18.6232 | 17.938 | 14.1458 | 10.5269 | 8.1658
| LUNANHEAD | FRIOCKHEIM | MINIMUM HEADROOM | NO 58834 49317 | YES | YES | 2.3622 | 2.2607 | 2.1288 | 1.9943 | 1.8076 | 1.5593 | 1.3911 | 1.1958 | 1.0129 | 0.83474 | 0.62935 | -0.0941 | -0.68167 | -1.7441 | 3.199 | 3.1266 | 3.0361 | 2.938 | 2.7254 | 2.5013 | 2.3748 | 2.1947 | 1.9928 | 1.7969 | 1.604 | 0.90809 | 0.20356 | -0.9317 | 2.9528 | 2.8329 | 2.6724 | 2.4915 | 2.2829 | 1.9701 | 1.7592 | 1.5222 | 1.262 | 0.98905 | 0.72527 | -0.14306 | -0.90427 | -2.1535
|  | FRIOCKHEIM | CT |  |  |  | 2.4408 | 2.3659 | 2.199 | 2.0429 | 1.8076 | 1.5593 | 1.3911 | 1.1958 | 1.0129 | 0.83474 | 0.62935 | -0.0941 | -0.68167 | -1.2664 | 3.2499 | 3.1985 | 3.0738 | 2.938 | 2.7254 | 2.5013 | 2.3748 | 2.1947 | 1.9928 | 1.7969 | 1.604 | 0.90809 | 0.25076 | -0.4363 | 3.0569 | 2.9774 | 2.7772 | 2.5656 | 2.2829 | 1.9701 | 1.7592 | 1.5222 | 1.262 | 0.98905 | 0.72527 | -0.14306 | -0.90427 | -1.5707
|  | FRIOCKHEIM | LW |  |  |  | 2.3622 | 2.2607 | 2.1288 | 1.9943 | 1.8473 | 1.6694 | 1.4861 | 1.3014 | 1.104 | 0.91046 | 0.71926 | 0.16795 | -0.6547 | -1.7441 | 3.199 | 3.1266 | 3.0361 | 2.941 | 2.8423 | 2.7111 | 2.5759 | 2.4068 | 2.2276 | 2.0559 | 1.8868 | 1.4019 | 0.42412 | -0.9317 | 2.9528 | 2.8329 | 2.6724 | 2.4915 | 2.3001 | 2.0737 | 1.8461 | 1.6298 | 1.3903 | 1.1477 | 0.91011 | 0.27136 | -0.77217 | -2.1535
|  | FRIOCKHEIM | ST |  |  |  | 2.5016 | 2.4724 | 2.3506 | 2.2484 | 2.1539 | 1.9662 | 1.8639 | 1.6513 | 1.5131 | 1.3709 | 1.1966 | 0.27875 | -0.58752 | -1.3962 | 3.283 | 3.2617 | 3.1321 | 3.0287 | 2.9396 | 2.7367 | 2.6435 | 2.4148 | 2.285 | 2.1549 | 1.989 | 1.128 | 0.20356 | -0.7628 | 3.1141 | 3.0818 | 2.9347 | 2.811 | 2.6991 | 2.4719 | 2.3541 | 2.0971 | 1.935 | 1.7687 | 1.566 | 0.50501 | -0.5005 | -1.506
|  | FRIOCKHEIM | FS |  |  |  | 2.5178 | 2.4963 | 2.441 | 2.3814 | 2.3126 | 2.2397 | 2.1721 | 2.055 | 1.9481 | 1.8359 | 1.7212 | 1.1161 | 0.61156 | 0.20717 | 3.292 | 3.2755 | 3.2279 | 3.1761 | 3.1144 | 3.0492 | 2.9898 | 2.8759 | 2.776 | 2.671 | 2.5628 | 2.0557 | 1.5801 | 1.1768 | 3.1319 | 3.1086 | 3.0441 | 2.9735 | 2.8914 | 2.805 | 2.7262 | 2.5849 | 2.4555 | 2.3198 | 2.1816 | 1.4652 | 0.87054 | 0.50751
| KINTORE | FYVIE | MINIMUM HEADROOM | NJ 76759 37635 | NO | YES | 4.728 | 4.5569 | 4.3741 | 4.186 | 4.0027 | 3.6513 | 3.4113 | 3.2634 | 3.0869 | 2.9135 | 2.7309 | 2.258 | 1.7951 | 1.5219 | 5.5024 | 5.4136 | 5.3258 | 5.2188 | 5.0379 | 4.7852 | 4.6549 | 4.5314 | 4.3864 | 4.2454 | 4.1109 | 3.6977 | 3.2502 | 2.8059 | 2.9116 | 2.7466 | 2.5755 | 2.3966 | 2.1853 | 1.83 | 1.6 | 1.4449 | 1.2696 | 1.0986 | 0.93462 | 0.47739 | -0.0034421 | -0.3582
|  | FYVIE | CT |  |  |  | 4.887 | 4.773 | 4.5344 | 4.289 | 4.0079 | 3.6513 | 3.4113 | 3.2634 | 3.0869 | 2.9135 | 2.7309 | 2.258 | 1.7951 | 1.5219 | 5.5584 | 5.4924 | 5.3612 | 5.2188 | 5.0379 | 4.7852 | 4.6549 | 4.5314 | 4.3864 | 4.2454 | 4.1109 | 3.6977 | 3.3303 | 2.9861 | 3.0531 | 2.9418 | 2.71 | 2.4666 | 2.1853 | 1.83 | 1.6 | 1.4449 | 1.2696 | 1.0986 | 0.93462 | 0.47739 | -0.0034421 | -0.3004
|  | FYVIE | LW |  |  |  | 4.728 | 4.5569 | 4.3741 | 4.186 | 4.0027 | 3.7162 | 3.4937 | 3.3332 | 3.1681 | 2.9857 | 2.8065 | 2.3976 | 1.9922 | 1.5556 | 5.5024 | 5.4136 | 5.3258 | 5.2309 | 5.143 | 4.9536 | 4.8205 | 4.699 | 4.572 | 4.4426 | 4.3217 | 4.0477 | 3.6677 | 3.1811 | 2.9116 | 2.7466 | 2.5755 | 2.3966 | 2.2261 | 1.9457 | 1.7227 | 1.5659 | 1.4059 | 1.24 | 1.0851 | 0.70269 | 0.24681 | -0.27232
|  | FYVIE | ST |  |  |  | 4.9782 | 4.9086 | 4.7632 | 4.6269 | 4.4959 | 4.2381 | 4.1057 | 3.92 | 3.768 | 3.614 | 3.4341 | 2.4831 | 1.9364 | 1.5327 | 5.5968 | 5.5619 | 5.4502 | 5.3527 | 5.2661 | 5.0384 | 4.9432 | 4.7886 | 4.6742 | 4.557 | 4.4189 | 3.7302 | 3.2502 | 2.8059 | 3.1355 | 3.0706 | 2.919 | 2.7794 | 2.6484 | 2.3765 | 2.2401 | 2.0419 | 1.884 | 1.7228 | 1.5414 | 0.6621 | 0.08952 | -0.3582
|  | FYVIE | FS |  |  |  | 5.0418 | 4.9916 | 4.905 | 4.8132 | 4.7202 | 4.5787 | 4.4816 | 4.3447 | 4.2096 | 4.0765 | 3.9379 | 3.0203 | 2.4058 | 2.1758 | 5.6193 | 5.5921 | 5.541 | 5.485 | 5.4258 | 5.3234 | 5.2573 | 5.1622 | 5.0704 | 4.9765 | 4.8767 | 4.3183 | 3.855 | 3.5402 | 3.1898 | 3.1421 | 3.0581 | 2.968 | 2.8759 | 2.7365 | 2.6381 | 2.4994 | 2.3627 | 2.2264 | 2.0833 | 1.234 | 0.68935 | 0.45613
| GRUDIE BRIDGE | GARBAT FOREST | MINIMUM HEADROOM | NH 41255 67993 | YES | YES | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106
|  | GARBAT FOREST | CT |  |  |  | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106
|  | GARBAT FOREST | LW |  |  |  | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106
|  | GARBAT FOREST | ST |  |  |  | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106
|  | GARBAT FOREST | FS |  |  |  | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.11439 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.10648 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106 | 0.106
| STORNOWAY | GISLA | MINIMUM HEADROOM | NB 12846 25823 | YES | YES | -0.6733 | -0.71161 | -0.72872 | -0.75353 | -0.78636 | -0.82882 | -0.87785 | -0.90815 | -0.93724 | -0.96575 | -1.0052 | -1.1646 | -1.211 | -1.2385 | -0.31758 | -0.34116 | -0.34909 | -0.36043 | -0.37158 | -0.39032 | -0.4127 | -0.42792 | -0.44452 | -0.46117 | -0.47655 | -0.5539 | -0.57472 | -0.59886 | -0.23183 | -0.27117 | -0.28901 | -0.32203 | -0.35634 | -0.38535 | -0.41878 | -0.43116 | -0.44392 | -0.45588 | -0.46911 | -0.53654 | -0.56283 | -0.58123
|  | GISLA | CT |  |  |  | -0.65629 | -0.69051 | -0.7197 | -0.75219 | -0.78636 | -0.82882 | -0.87785 | -0.90815 | -0.93724 | -0.96575 | -0.9956 | -1.0808 | -1.117 | -1.1359 | -0.31688 | -0.33888 | -0.34909 | -0.36043 | -0.37158 | -0.39032 | -0.4127 | -0.42792 | -0.44452 | -0.46117 | -0.47655 | -0.5204 | -0.54002 | -0.55406 | -0.21689 | -0.25482 | -0.28684 | -0.32203 | -0.35634 | -0.38535 | -0.41878 | -0.43116 | -0.44392 | -0.45588 | -0.46703 | -0.4994 | -0.53679 | -0.55083
|  | GISLA | LW |  |  |  | -0.6733 | -0.71161 | -0.72872 | -0.75353 | -0.77453 | -0.80319 | -0.82656 | -0.85612 | -0.90367 | -0.95605 | -1.0052 | -1.1646 | -1.211 | -1.2186 | -0.31758 | -0.34116 | -0.34764 | -0.35353 | -0.35957 | -0.37021 | -0.38159 | -0.40223 | -0.42591 | -0.45219 | -0.47619 | -0.5539 | -0.57472 | -0.57669 | -0.23183 | -0.27117 | -0.28901 | -0.3139 | -0.33588 | -0.36651 | -0.3934 | -0.41154 | -0.43021 | -0.4518 | -0.46911 | -0.53654 | -0.56283 | -0.57078
|  | GISLA | ST |  |  |  | -0.64611 | -0.66943 | -0.67925 | -0.68916 | -0.7016 | -0.70965 | -0.72175 | -0.73613 | -0.75475 | -0.79431 | -0.84283 | -1.0849 | -1.1802 | -1.199 | -0.3156 | -0.33304 | -0.33647 | -0.34074 | -0.34543 | -0.35058 | -0.35718 | -0.36406 | -0.37255 | -0.38238 | -0.40364 | -0.52531 | -0.56667 | -0.57424 | -0.20665 | -0.23053 | -0.24079 | -0.25147 | -0.26486 | -0.27483 | -0.28916 | -0.30618 | -0.31897 | -0.33698 | -0.36185 | -0.46215 | -0.52555 | -0.54525
|  | GISLA | FS |  |  |  | -0.64101 | -0.65954 | -0.66707 | -0.67456 | -0.6867 | -0.6943 | -0.70468 | -0.71676 | -0.72713 | -0.73912 | -0.75263 | -0.92483 | -1.1153 | -1.2385 | -0.31516 | -0.32845 | -0.33075 | -0.33417 | -0.33775 | -0.34132 | -0.34547 | -0.35039 | -0.35606 | -0.36246 | -0.36963 | -0.43627 | -0.5356 | -0.59886 | -0.20167 | -0.22046 | -0.2281 | -0.23601 | -0.24818 | -0.25664 | -0.26776 | -0.28082 | -0.29273 | -0.30647 | -0.32211 | -0.42408 | -0.50928 | -0.58123
| ALNESS | GLASTULLICH | MINIMUM HEADROOM | NH 78509 76508 | YES | YES | 3.0606 | 3.0065 | 2.9122 | 2.8128 | 2.668 | 2.5272 | 2.3938 | 2.3698 | 2.3407 | 2.3115 | 2.2871 | 2.1671 | 1.6776 | 1.034 | 3.2616 | 3.232 | 3.1905 | 3.1319 | 3.0563 | 2.9807 | 2.9194 | 2.868 | 2.8069 | 2.7486 | 2.6918 | 2.4679 | 1.9445 | 1.1654 | 2.7834 | 2.7292 | 2.6467 | 2.5492 | 2.4188 | 2.2904 | 2.1741 | 2.122 | 2.0559 | 1.9914 | 1.9349 | 1.7356 | 1.1522 | 0.36092
|  | GLASTULLICH | CT |  |  |  | 3.1137 | 3.0795 | 2.9452 | 2.8128 | 2.668 | 2.5272 | 2.3938 | 2.3698 | 2.3407 | 2.3115 | 2.2871 | 2.1755 | 1.8503 | 1.5597 | 3.2812 | 3.2606 | 3.1974 | 3.1319 | 3.0563 | 2.9807 | 2.9194 | 2.868 | 2.8069 | 2.7486 | 2.6918 | 2.4679 | 2.1439 | 1.7843 | 2.8277 | 2.7922 | 2.6717 | 2.5492 | 2.4188 | 2.2904 | 2.1741 | 2.122 | 2.0559 | 1.9914 | 1.9349 | 1.7356 | 1.3773 | 1.029
|  | GLASTULLICH | LW |  |  |  | 3.0606 | 3.0065 | 2.9122 | 2.8143 | 2.7241 | 2.6199 | 2.5149 | 2.4726 | 2.4315 | 2.3891 | 2.3536 | 2.1671 | 1.6776 | 1.034 | 3.2616 | 3.232 | 3.1905 | 3.1457 | 3.1061 | 3.053 | 2.9965 | 2.9326 | 2.8664 | 2.8022 | 2.7376 | 2.5067 | 1.9445 | 1.1654 | 2.7834 | 2.7292 | 2.6467 | 2.559 | 2.4803 | 2.3811 | 2.2777 | 2.2046 | 2.1297 | 2.0562 | 1.9891 | 1.7416 | 1.1522 | 0.36092
|  | GLASTULLICH | ST |  |  |  | 3.1326 | 3.1291 | 3.0969 | 3.0571 | 3.0238 | 2.9712 | 2.9389 | 2.8396 | 2.7809 | 2.7234 | 2.6533 | 2.3416 | 1.9311 | 1.5063 | 3.2966 | 3.2874 | 3.2558 | 3.2267 | 3.2024 | 3.1553 | 3.1283 | 3.0271 | 2.9729 | 2.9197 | 2.8502 | 2.5029 | 2.0355 | 1.5358 | 2.8583 | 2.8422 | 2.8001 | 2.7579 | 2.7219 | 2.6618 | 2.6232 | 2.5055 | 2.4354 | 2.3652 | 2.2781 | 1.8661 | 1.3752 | 0.87427
|  | GLASTULLICH | FS |  |  |  | 3.1335 | 3.1306 | 3.1239 | 3.096 | 3.0654 | 3.0375 | 3.0016 | 2.9458 | 2.8978 | 2.8506 | 2.7966 | 2.5283 | 2.3662 | 2.2527 | 3.3018 | 3.2939 | 3.2771 | 3.2594 | 3.2401 | 3.2207 | 3.1979 | 3.1495 | 3.1088 | 3.0671 | 3.0215 | 2.822 | 2.6488 | 2.5121 | 2.8698 | 2.8561 | 2.828 | 2.7992 | 2.7681 | 2.7381 | 2.7011 | 2.6383 | 2.5835 | 2.5281 | 2.466 | 2.168 | 1.9657 | 1.8613
| SHIN | GLEDFIELD | MINIMUM HEADROOM | NH 58876 90837 | YES | YES | 1.353 | 1.2947 | 1.2364 | 1.1695 | 1.1096 | 1.0357 | 0.90317 | 0.85555 | 0.79821 | 0.74221 | 0.69288 | 0.58975 | 0.52381 | 0.48151 | 1.852 | 1.8219 | 1.7935 | 1.7605 | 1.7284 | 1.6904 | 1.6207 | 1.5844 | 1.5433 | 1.5023 | 1.4657 | 1.4027 | 1.3576 | 1.3171 | 1.403 | 1.3619 | 1.3193 | 1.2709 | 1.2259 | 1.1753 | 1.0882 | 1.0676 | 1.0346 | 0.98039 | 0.93224 | 0.84317 | 0.79587 | 0.76388
|  | GLEDFIELD | CT |  |  |  | 1.39 | 1.36 | 1.2753 | 1.2003 | 1.1249 | 1.052 | 0.93084 | 0.89349 | 0.83887 | 0.78226 | 0.73136 | 0.63176 | 0.52381 | 0.48151 | 1.8668 | 1.8471 | 1.8043 | 1.7638 | 1.7284 | 1.6933 | 1.6373 | 1.6081 | 1.5685 | 1.5275 | 1.491 | 1.4141 | 1.3576 | 1.3171 | 1.4324 | 1.4076 | 1.3485 | 1.3001 | 1.2432 | 1.1882 | 1.1014 | 1.0817 | 1.0614 | 1.0172 | 0.96916 | 0.87547 | 0.79587 | 0.76388
|  | GLEDFIELD | LW |  |  |  | 1.353 | 1.2947 | 1.2364 | 1.1695 | 1.1096 | 1.0357 | 0.90317 | 0.85555 | 0.79821 | 0.74221 | 0.69288 | 0.58975 | 0.53252 | 0.51078 | 1.852 | 1.8219 | 1.7935 | 1.7605 | 1.7318 | 1.6904 | 1.6207 | 1.5844 | 1.5433 | 1.5023 | 1.4657 | 1.4027 | 1.3794 | 1.3696 | 1.403 | 1.3619 | 1.3193 | 1.2709 | 1.2259 | 1.1753 | 1.0882 | 1.0676 | 1.0346 | 0.98039 | 0.93224 | 0.84317 | 0.80186 | 0.78523
|  | GLEDFIELD | ST |  |  |  | 1.4197 | 1.4018 | 1.3818 | 1.3531 | 1.3292 | 1.2935 | 1.2344 | 1.1949 | 1.1492 | 1.101 | 1.0477 | 0.79392 | 0.69772 | 0.6353 | 1.8803 | 1.8697 | 1.8576 | 1.842 | 1.8276 | 1.8077 | 1.7744 | 1.7501 | 1.7215 | 1.6901 | 1.6553 | 1.4825 | 1.4229 | 1.378 | 1.4563 | 1.4405 | 1.4233 | 1.4026 | 1.385 | 1.3594 | 1.3234 | 1.2974 | 1.268 | 1.2376 | 1.2037 | 1.0041 | 0.93052 | 0.88717
|  | GLEDFIELD | FS |  |  |  | 1.4319 | 1.4183 | 1.3995 | 1.3756 | 1.3499 | 1.3208 | 1.2731 | 1.2353 | 1.1972 | 1.1582 | 1.1152 | 0.82913 | 0.64448 | 0.58887 | 1.8854 | 1.8769 | 1.8658 | 1.8526 | 1.839 | 1.8232 | 1.796 | 1.7751 | 1.753 | 1.7294 | 1.7033 | 1.5318 | 1.3967 | 1.3354 | 1.4659 | 1.4541 | 1.4373 | 1.4184 | 1.3993 | 1.3781 | 1.3496 | 1.3238 | 1.2983 | 1.273 | 1.2451 | 1.054 | 0.88949 | 0.85152
| FORT AUGUSTUS | GLEN LAOGH | MINIMUM HEADROOM | NH 27430 00910 | YES | YES | 0.11193 | 0.11191 | 0.1119 | 0.11189 | 0.11187 | 0.11186 | 0.11184 | 0.11181 | 0.11179 | 0.11177 | 0.11176 | 0.11168 | 0.11157 | 0.11148 | 0.10484 | 0.10476 | 0.1047 | 0.10464 | 0.10456 | 0.10448 | 0.10438 | 0.1043 | 0.1042 | 0.10409 | 0.10397 | 0.10305 | 0.10114 | 0.097434 | 0.10314 | 0.10313 | 0.10312 | 0.10311 | 0.10311 | 0.1031 | 0.10309 | 0.10308 | 0.10307 | 0.10307 | 0.10306 | 0.10302 | 0.10295 | 0.10289
|  | GLEN LAOGH | CT |  |  |  | 0.11194 | 0.11192 | 0.11191 | 0.11189 | 0.11188 | 0.11186 | 0.11185 | 0.11183 | 0.11181 | 0.11179 | 0.11177 | 0.11172 | 0.11163 | 0.11155 | 0.10486 | 0.10479 | 0.10473 | 0.10466 | 0.10458 | 0.10449 | 0.1044 | 0.10431 | 0.10422 | 0.10411 | 0.104 | 0.10315 | 0.10164 | 0.098991 | 0.10314 | 0.10313 | 0.10312 | 0.10312 | 0.10311 | 0.1031 | 0.1031 | 0.10309 | 0.10308 | 0.10307 | 0.10307 | 0.10304 | 0.10299 | 0.10294
|  | GLEN LAOGH | LW |  |  |  | 0.11193 | 0.11191 | 0.1119 | 0.11189 | 0.11187 | 0.11186 | 0.11184 | 0.11181 | 0.11179 | 0.11177 | 0.11176 | 0.11168 | 0.11157 | 0.11148 | 0.10496 | 0.10495 | 0.10494 | 0.10493 | 0.10492 | 0.10491 | 0.10489 | 0.10488 | 0.10486 | 0.10485 | 0.10483 | 0.10478 | 0.10472 | 0.10466 | 0.10314 | 0.10313 | 0.10312 | 0.10311 | 0.10311 | 0.1031 | 0.10309 | 0.10308 | 0.10307 | 0.10307 | 0.10306 | 0.10302 | 0.10295 | 0.10289
|  | GLEN LAOGH | ST |  |  |  | 0.11194 | 0.11192 | 0.11191 | 0.1119 | 0.11189 | 0.11188 | 0.11187 | 0.11185 | 0.11184 | 0.11182 | 0.11181 | 0.11173 | 0.11163 | 0.11156 | 0.10486 | 0.10479 | 0.10473 | 0.10467 | 0.10459 | 0.10451 | 0.10441 | 0.10433 | 0.10424 | 0.10414 | 0.10403 | 0.10316 | 0.10164 | 0.098996 | 0.10314 | 0.10313 | 0.10313 | 0.10312 | 0.10311 | 0.10311 | 0.1031 | 0.10309 | 0.10309 | 0.10308 | 0.10308 | 0.10305 | 0.10299 | 0.10294
|  | GLEN LAOGH | FS |  |  |  | 0.11194 | 0.11193 | 0.11192 | 0.11191 | 0.1119 | 0.11189 | 0.11187 | 0.11186 | 0.11185 | 0.11184 | 0.11183 | 0.11177 | 0.11168 | 0.11161 | 0.10484 | 0.10476 | 0.1047 | 0.10464 | 0.10456 | 0.10448 | 0.10438 | 0.1043 | 0.1042 | 0.10409 | 0.10397 | 0.10305 | 0.10114 | 0.097434 | 0.10314 | 0.10313 | 0.10313 | 0.10312 | 0.10312 | 0.10311 | 0.1031 | 0.1031 | 0.10309 | 0.10309 | 0.10308 | 0.10306 | 0.10302 | 0.10298
| KINLOCHLEVEN | GLENCOE | MINIMUM HEADROOM | NN 10658 58797 | YES | YES | 1.1026 | 1.0777 | 1.0652 | 1.0068 | 0.93179 | 0.83359 | 0.72711 | 0.66466 | 0.59641 | 0.52903 | 0.46732 | 0.33796 | 0.23579 | 0.18253 | 1.7888 | 1.7406 | 1.7046 | 1.6643 | 1.6234 | 1.5793 | 1.522 | 1.4758 | 1.4256 | 1.3752 | 1.3294 | 1.2535 | 1.1873 | 1.1345 | 1.3844 | 1.3003 | 1.2283 | 1.1495 | 1.0816 | 0.99121 | 0.89272 | 0.83198 | 0.76566 | 0.69993 | 0.63979 | 0.51885 | 0.42979 | 0.38242
|  | GLENCOE | CT |  |  |  | 1.1039 | 1.0833 | 1.0652 | 1.0422 | 0.94584 | 0.85 | 0.74508 | 0.69578 | 0.62925 | 0.56206 | 0.50724 | 0.3859 | 0.23579 | 0.18253 | 1.8063 | 1.7691 | 1.7189 | 1.666 | 1.6234 | 1.5802 | 1.5337 | 1.4978 | 1.4482 | 1.3977 | 1.3551 | 1.2603 | 1.1873 | 1.1345 | 1.4325 | 1.3714 | 1.2766 | 1.1778 | 1.091 | 1.0047 | 0.91068 | 0.86316 | 0.79864 | 0.73327 | 0.67964 | 0.56247 | 0.42979 | 0.38242
|  | GLENCOE | LW |  |  |  | 1.1026 | 1.0777 | 1.066 | 1.0068 | 0.93179 | 0.83359 | 0.72711 | 0.66466 | 0.59641 | 0.52903 | 0.46732 | 0.33796 | 0.26209 | 0.2318 | 1.7888 | 1.7406 | 1.7046 | 1.6643 | 1.6304 | 1.5793 | 1.522 | 1.4758 | 1.4256 | 1.3752 | 1.3294 | 1.2535 | 1.2257 | 1.2137 | 1.3844 | 1.3003 | 1.2283 | 1.1495 | 1.0816 | 0.99121 | 0.89272 | 0.83198 | 0.76566 | 0.69993 | 0.63979 | 0.51885 | 0.45243 | 0.42603
|  | GLENCOE | ST |  |  |  | 1.1098 | 1.0958 | 1.0906 | 1.0835 | 1.0757 | 1.0653 | 1.0522 | 1.0371 | 0.97898 | 0.91544 | 0.84785 | 0.51454 | 0.37775 | 0.29498 | 1.8268 | 1.8011 | 1.7836 | 1.7638 | 1.7438 | 1.7183 | 1.6892 | 1.6584 | 1.6217 | 1.5819 | 1.5387 | 1.3195 | 1.2413 | 1.1832 | 1.4695 | 1.4248 | 1.3904 | 1.3539 | 1.3188 | 1.2739 | 1.2249 | 1.1765 | 1.1193 | 1.0595 | 0.99555 | 0.6796 | 0.55633 | 0.48411
|  | GLENCOE | FS |  |  |  | 1.1109 | 1.0985 | 1.094 | 1.0882 | 1.0817 | 1.0741 | 1.0654 | 1.055 | 1.043 | 1.0099 | 0.95276 | 0.57977 | 0.33705 | 0.26483 | 1.835 | 1.8142 | 1.8 | 1.7825 | 1.7649 | 1.7464 | 1.7253 | 1.6988 | 1.6704 | 1.6397 | 1.6067 | 1.3919 | 1.2178 | 1.1377 | 1.4885 | 1.4547 | 1.4271 | 1.3938 | 1.3614 | 1.3296 | 1.2933 | 1.2468 | 1.199 | 1.1486 | 1.0956 | 0.74974 | 0.52116 | 0.45729
| DUNOON | GLENDARUEL | MINIMUM HEADROOM | NN 03067 59147 | YES | YES | 0.25253 | 0.24002 | 0.22506 | 0.20847 | 0.1812 | 0.1531 | 0.13074 | 0.11873 | 0.10538 | 0.087028 | 0.071458 | 0.030621 | -0.021893 | -0.058435 | 0.29539 | 0.28843 | 0.28099 | 0.26786 | 0.24889 | 0.22905 | 0.21649 | 0.20515 | 0.19128 | 0.17557 | 0.16137 | 0.1113 | 0.062429 | 0.02076 | 0.26569 | 0.25384 | 0.24024 | 0.22367 | 0.19641 | 0.1682 | 0.14724 | 0.13444 | 0.12009 | 0.101 | 0.083976 | 0.03453 | -0.022204 | -0.062983
|  | GLENDARUEL | CT |  |  |  | 0.26213 | 0.25218 | 0.23086 | 0.20847 | 0.1812 | 0.1531 | 0.13074 | 0.11873 | 0.10538 | 0.087028 | 0.071458 | 0.031205 | -0.012543 | -0.037061 | 0.29881 | 0.29294 | 0.28099 | 0.26786 | 0.24889 | 0.22905 | 0.21649 | 0.20515 | 0.19128 | 0.17557 | 0.16137 | 0.11875 | 0.083786 | 0.052509 | 0.27389 | 0.26461 | 0.24476 | 0.22367 | 0.19641 | 0.1682 | 0.14724 | 0.13444 | 0.12009 | 0.101 | 0.083976 | 0.038205 | -0.0060466 | -0.034696
|  | GLENDARUEL | LW |  |  |  | 0.25253 | 0.24002 | 0.22506 | 0.20881 | 0.19381 | 0.17621 | 0.15511 | 0.14025 | 0.12583 | 0.1116 | 0.094615 | 0.059186 | 0.012532 | -0.03758 | 0.29539 | 0.28843 | 0.28107 | 0.27286 | 0.26548 | 0.25536 | 0.24327 | 0.23119 | 0.21816 | 0.20525 | 0.19189 | 0.16393 | 0.11832 | 0.059312 | 0.26569 | 0.25384 | 0.24024 | 0.22542 | 0.21179 | 0.19542 | 0.1758 | 0.16095 | 0.1462 | 0.13059 | 0.11301 | 0.076724 | 0.024555 | -0.036368
|  | GLENDARUEL | ST |  |  |  | 0.2638 | 0.26065 | 0.24447 | 0.23395 | 0.22349 | 0.20414 | 0.19101 | 0.17034 | 0.15747 | 0.13947 | 0.12304 | 0.030621 | -0.021893 | -0.058435 | 0.30009 | 0.29811 | 0.28523 | 0.27601 | 0.26803 | 0.24995 | 0.24038 | 0.22321 | 0.21275 | 0.20029 | 0.18612 | 0.1113 | 0.062429 | 0.02076 | 0.27564 | 0.27257 | 0.25566 | 0.24438 | 0.23374 | 0.21247 | 0.19936 | 0.17768 | 0.16456 | 0.14698 | 0.13014 | 0.03453 | -0.022204 | -0.062983
|  | GLENDARUEL | FS |  |  |  | 0.26947 | 0.26644 | 0.25982 | 0.25126 | 0.24158 | 0.23547 | 0.22691 | 0.21698 | 0.1995 | 0.18923 | 0.17606 | 0.099815 | 0.041411 | 0.021691 | 0.3022 | 0.30043 | 0.296 | 0.29063 | 0.28456 | 0.27959 | 0.27368 | 0.26573 | 0.2555 | 0.24764 | 0.2384 | 0.18894 | 0.14627 | 0.12719 | 0.28047 | 0.27768 | 0.27119 | 0.26294 | 0.25361 | 0.24736 | 0.23898 | 0.22879 | 0.21226 | 0.20197 | 0.18906 | 0.11681 | 0.059855 | 0.041906
| ABERNETHY | GLENDEVON | MINIMUM HEADROOM | NO 00101 02760 | YES | YES | 2.7085 | 2.5698 | 2.4765 | 2.3653 | 2.1869 | 1.984 | 1.8311 | 1.7186 | 1.5883 | 1.4619 | 1.3619 | 0.9042 | 0.59284 | 0.25921 | 2.8325 | 2.7396 | 2.6924 | 2.6078 | 2.4582 | 2.3017 | 2.2121 | 2.1184 | 2.0108 | 1.9074 | 1.8159 | 1.2971 | 0.88081 | 0.47187 | 2.658 | 2.5337 | 2.4513 | 2.3534 | 2.1575 | 1.9524 | 1.8125 | 1.6967 | 1.5616 | 1.4315 | 1.3233 | 0.8397 | 0.437 | 0.053562
|  | GLENDEVON | CT |  |  |  | 2.7703 | 2.6649 | 2.5373 | 2.39 | 2.1869 | 1.984 | 1.8311 | 1.7186 | 1.5883 | 1.4619 | 1.3619 | 0.9042 | 0.59284 | 0.37251 | 2.8524 | 2.7747 | 2.7008 | 2.6114 | 2.4582 | 2.3017 | 2.2121 | 2.1184 | 2.0108 | 1.9074 | 1.8159 | 1.346 | 1.048 | 0.744 | 2.7104 | 2.6152 | 2.4974 | 2.3603 | 2.1575 | 1.9524 | 1.8125 | 1.6967 | 1.5616 | 1.4315 | 1.3233 | 0.8397 | 0.50974 | 0.2512
|  | GLENDEVON | LW |  |  |  | 2.7085 | 2.5698 | 2.4765 | 2.3653 | 2.2484 | 2.1166 | 1.981 | 1.8689 | 1.7587 | 1.6445 | 1.5665 | 1.2274 | 0.85749 | 0.38833 | 2.8325 | 2.7396 | 2.6924 | 2.635 | 2.5787 | 2.5082 | 2.4346 | 2.3538 | 2.2713 | 2.1886 | 2.1229 | 1.8289 | 1.4235 | 0.8641 | 2.658 | 2.5337 | 2.4513 | 2.3534 | 2.2531 | 2.1351 | 2.0125 | 1.9023 | 1.7923 | 1.6798 | 1.5967 | 1.261 | 0.82645 | 0.25363
|  | GLENDEVON | ST |  |  |  | 2.809 | 2.722 | 2.6078 | 2.5008 | 2.4042 | 2.2393 | 2.1423 | 1.9955 | 1.8881 | 1.7772 | 1.6675 | 0.99109 | 0.59366 | 0.25921 | 2.869 | 2.8047 | 2.6975 | 2.6078 | 2.5343 | 2.3739 | 2.298 | 2.1621 | 2.0795 | 1.9962 | 1.901 | 1.2971 | 0.88081 | 0.47187 | 2.7438 | 2.667 | 2.5432 | 2.4337 | 2.3395 | 2.1582 | 2.062 | 1.9041 | 1.7974 | 1.6884 | 1.5724 | 0.87851 | 0.437 | 0.053562
|  | GLENDEVON | FS |  |  |  | 2.8414 | 2.779 | 2.7215 | 2.6542 | 2.5892 | 2.5145 | 2.4466 | 2.3506 | 2.259 | 2.1728 | 2.0886 | 1.5345 | 1.2338 | 1.11 | 2.8864 | 2.8373 | 2.7977 | 2.7514 | 2.7023 | 2.6499 | 2.6004 | 2.5273 | 2.4618 | 2.3966 | 2.3316 | 1.9357 | 1.6756 | 1.5032 | 2.7718 | 2.7165 | 2.6617 | 2.5987 | 2.5371 | 2.4667 | 2.4025 | 2.3083 | 2.2207 | 2.137 | 2.0529 | 1.5335 | 1.2386 | 1.1218
| FORT AUGUSTUS | GLENDOE | MINIMUM HEADROOM | NH 40060 08894 | YES | YES | 1.1171 | 1.0907 | 1.064 | 1.0347 | 1.0054 | 0.96601 | 0.91983 | 0.88007 | 0.8395 | 0.79593 | 0.75307 | 0.67268 | 0.65457 | 0.62096 | 1.2797 | 1.2631 | 1.2474 | 1.2277 | 1.2101 | 1.1859 | 1.1549 | 1.1248 | 1.093 | 1.0595 | 1.0275 | 0.9692 | 0.96025 | 0.93716 | 1.1726 | 1.1484 | 1.1212 | 1.0915 | 1.0615 | 1.0223 | 0.97668 | 0.93845 | 0.89989 | 0.8581 | 0.81674 | 0.73825 | 0.71872 | 0.68594
|  | GLENDOE | CT |  |  |  | 1.1296 | 1.1115 | 1.0756 | 1.0374 | 1.0079 | 0.9762 | 0.94273 | 0.91514 | 0.88295 | 0.849 | 0.81452 | 0.73236 | 0.69318 | 0.67982 | 1.2852 | 1.2735 | 1.2515 | 1.2277 | 1.2101 | 1.1913 | 1.1716 | 1.151 | 1.1263 | 1.1007 | 1.0746 | 1.0113 | 0.98956 | 0.97883 | 1.1833 | 1.1667 | 1.1338 | 1.0957 | 1.0653 | 1.0327 | 0.99842 | 0.97146 | 0.94051 | 0.90787 | 0.87459 | 0.79523 | 0.75336 | 0.73877
|  | GLENDOE | LW |  |  |  | 1.1171 | 1.0907 | 1.064 | 1.0347 | 1.0054 | 0.96601 | 0.91983 | 0.88007 | 0.8395 | 0.79593 | 0.75307 | 0.67268 | 0.65457 | 0.62096 | 1.2797 | 1.2631 | 1.2474 | 1.2295 | 1.2122 | 1.1859 | 1.1549 | 1.1248 | 1.093 | 1.0595 | 1.0275 | 0.9692 | 0.96025 | 0.93716 | 1.1726 | 1.1484 | 1.1212 | 1.0915 | 1.0615 | 1.0223 | 0.97668 | 0.93845 | 0.89989 | 0.8581 | 0.81674 | 0.73825 | 0.71872 | 0.68594
|  | GLENDOE | ST |  |  |  | 1.1404 | 1.1344 | 1.1218 | 1.1073 | 1.0966 | 1.0799 | 1.0607 | 1.0418 | 1.0137 | 0.98664 | 0.95727 | 0.80491 | 0.76017 | 0.74097 | 1.2912 | 1.287 | 1.2795 | 1.2706 | 1.2627 | 1.2515 | 1.2384 | 1.2245 | 1.2054 | 1.1856 | 1.1639 | 1.0515 | 1.0218 | 1.01 | 1.1933 | 1.1878 | 1.1765 | 1.1634 | 1.1535 | 1.1382 | 1.1196 | 1.1015 | 1.0737 | 1.0474 | 1.0192 | 0.87017 | 0.82341 | 0.8018
|  | GLENDOE | FS |  |  |  | 1.1439 | 1.1388 | 1.1271 | 1.117 | 1.106 | 1.0936 | 1.0783 | 1.0631 | 1.0431 | 1.0232 | 1.0012 | 0.85616 | 0.74576 | 0.70946 | 1.2929 | 1.2893 | 1.2827 | 1.2762 | 1.2691 | 1.2608 | 1.2508 | 1.2403 | 1.2271 | 1.2134 | 1.1981 | 1.0985 | 1.0182 | 0.99083 | 1.1963 | 1.1916 | 1.1812 | 1.1721 | 1.1621 | 1.1509 | 1.1363 | 1.1211 | 1.1009 | 1.0813 | 1.0594 | 0.91564 | 0.80793 | 0.77087
| BRACO | GLENEAGLES | MINIMUM HEADROOM | NN 91540 11582 | NO | YES | -0.80319 | -11.2345 | -12.2385 | -12.9765 | -13.9976 | -15.1711 | -16.1624 | -17.1221 | -18.1566 | -18.9048 | -19.5191 | -21.1762 | -22.0566 | -22.8156 | -0.92551 | -13.5628 | -14.2838 | -14.8078 | -15.6218 | -16.5542 | -17.272 | -17.9477 | -18.6907 | -19.1935 | -19.6388 | -20.7865 | -21.4974 | -22.2878 | -3.2426 | -16.0488 | -17.0194 | -17.7495 | -18.7987 | -19.9949 | -20.971 | -21.8685 | -22.8397 | -23.5351 | -24.1244 | -25.7176 | -26.6367 | -27.5002
|  | GLENEAGLES | CT |  |  |  | 8.2282 | 6.6002 | 5.7184 | 5.058 | 4.1779 | 3.2124 | 2.4926 | 1.5956 | 0.57274 | -0.16817 | -0.80202 | -2.7589 | -3.881 | -4.5297 | 10.1146 | 8.3703 | 7.794 | 7.3749 | 6.7057 | 5.9817 | 5.5566 | 4.9522 | 4.2322 | 3.7528 | 3.3142 | 1.9387 | 1.1494 | 0.42878 | 7.9431 | 6.088 | 5.2702 | 4.6496 | 3.7619 | 2.7945 | 2.1275 | 1.295 | 0.33989 | -0.34216 | -0.94186 | -2.8039 | -3.8686 | -4.5139
|  | GLENEAGLES | LW |  |  |  | -0.80319 | -11.2345 | -12.2385 | -12.9765 | -13.9976 | -15.1711 | -16.1624 | -17.1221 | -18.1566 | -18.9048 | -19.5191 | -21.1762 | -22.0566 | -22.8156 | -0.92551 | -13.5628 | -14.2838 | -14.8078 | -15.6218 | -16.5542 | -17.272 | -17.9477 | -18.6907 | -19.1935 | -19.6388 | -20.7865 | -21.4974 | -22.2878 | -3.2426 | -16.0488 | -17.0194 | -17.7495 | -18.7987 | -19.9949 | -20.971 | -21.8685 | -22.8397 | -23.5351 | -24.1244 | -25.7176 | -26.6367 | -27.5002
|  | GLENEAGLES | ST |  |  |  | 3.9513 | -2.3187 | -3.0594 | -3.4673 | -3.8589 | -4.5818 | -5.0053 | -5.6674 | -6.3851 | -6.8387 | -7.2738 | -9.5396 | -10.7027 | -11.7103 | 4.6048 | -3.0179 | -3.6924 | -4.0704 | -4.3958 | -5.1104 | -5.4622 | -5.9955 | -6.5524 | -6.8902 | -7.2474 | -9.077 | -10.0593 | -10.9543 | 2.5256 | -5.1709 | -5.936 | -6.3649 | -6.7532 | -7.5379 | -7.9546 | -8.5903 | -9.2633 | -9.6822 | -10.1046 | -12.305 | -13.4586 | -14.4479
|  | GLENEAGLES | FS |  |  |  | 9.7287 | 9.1978 | 8.7575 | 8.47 | 8.1772 | 7.8295 | 7.5248 | 7.0162 | 6.4587 | 6.052 | 5.7068 | 3.6554 | 1.9162 | 0.8386 | 11.7552 | 11.2546 | 10.914 | 10.6923 | 10.4697 | 10.2077 | 9.9792 | 9.601 | 9.1829 | 8.8892 | 8.6216 | 7.1039 | 5.6299 | 4.482 | 9.7087 | 9.155 | 8.738 | 8.4621 | 8.1845 | 7.8602 | 7.5752 | 7.1047 | 6.59 | 6.2194 | 5.8936 | 3.9777 | 2.3375 | 1.347
| RANNOCH | GLENETIVE | MINIMUM HEADROOM | NN 25850 54886 | YES | YES | 0.29528 | 0.27952 | 0.26595 | 0.25002 | 0.22501 | 0.19528 | 0.17554 | 0.14588 | 0.12487 | 0.10409 | 0.075036 | -0.069007 | -0.14541 | -0.19083 | 0.22919 | 0.21745 | 0.20699 | 0.19475 | 0.17209 | 0.14642 | 0.12974 | 0.1044 | 0.085847 | 0.067508 | 0.042738 | -0.086611 | -0.1609 | -0.21195 | 0.21782 | 0.20826 | 0.19555 | 0.18004 | 0.15343 | 0.1223 | 0.10261 | 0.072842 | 0.051381 | 0.03027 | 0.0011399 | -0.14728 | -0.22976 | -0.28285
|  | GLENETIVE | CT |  |  |  | 0.29528 | 0.27952 | 0.26595 | 0.25002 | 0.22501 | 0.19528 | 0.17554 | 0.14588 | 0.12487 | 0.10409 | 0.075036 | -0.020206 | -0.050376 | -0.074466 | 0.22919 | 0.21745 | 0.20699 | 0.19475 | 0.17209 | 0.14642 | 0.12974 | 0.1044 | 0.085847 | 0.067508 | 0.042738 | -0.042385 | -0.075298 | -0.1042 | 0.21814 | 0.20826 | 0.19555 | 0.18004 | 0.15343 | 0.1223 | 0.10261 | 0.072842 | 0.051381 | 0.03027 | 0.0011399 | -0.096768 | -0.13169 | -0.16125
|  | GLENETIVE | LW |  |  |  | 0.29933 | 0.29449 | 0.28839 | 0.28196 | 0.27398 | 0.26233 | 0.249 | 0.2308 | 0.2141 | 0.19851 | 0.18393 | 0.15396 | 0.1141 | 0.056847 | 0.23206 | 0.2294 | 0.22483 | 0.22002 | 0.21527 | 0.20656 | 0.19658 | 0.18332 | 0.16986 | 0.15668 | 0.14446 | 0.1169 | 0.06809 | -0.0029906 | 0.21782 | 0.21554 | 0.21387 | 0.21091 | 0.20411 | 0.19292 | 0.1801 | 0.1623 | 0.14574 | 0.13028 | 0.11579 | 0.084487 | 0.035088 | -0.03627
|  | GLENETIVE | ST |  |  |  | 0.30374 | 0.3014 | 0.28774 | 0.27455 | 0.26117 | 0.23407 | 0.21574 | 0.18831 | 0.16237 | 0.13379 | 0.098555 | -0.069007 | -0.14541 | -0.19083 | 0.23386 | 0.23305 | 0.2191 | 0.20639 | 0.19457 | 0.16917 | 0.15376 | 0.12852 | 0.10737 | 0.083798 | 0.054915 | -0.086611 | -0.1609 | -0.21195 | 0.2216 | 0.2206 | 0.20894 | 0.19872 | 0.1853 | 0.15679 | 0.13816 | 0.10902 | 0.083173 | 0.054925 | 0.019927 | -0.14728 | -0.22976 | -0.28285
|  | GLENETIVE | FS |  |  |  | 0.30415 | 0.30349 | 0.29928 | 0.29257 | 0.28278 | 0.27145 | 0.26 | 0.24526 | 0.22979 | 0.2115 | 0.19247 | 0.076442 | -0.022978 | -0.089667 | 0.23415 | 0.23365 | 0.23073 | 0.22517 | 0.21742 | 0.20861 | 0.19924 | 0.18653 | 0.17385 | 0.15967 | 0.14391 | 0.052844 | -0.026015 | -0.080131 | 0.22195 | 0.22134 | 0.21824 | 0.21489 | 0.20935 | 0.19903 | 0.18788 | 0.17271 | 0.15717 | 0.139 | 0.12004 | 0.0080187 | -0.088039 | -0.15315
| FORT WILLIAM | GLENUIG | MINIMUM HEADROOM | NM 67224 77119 | YES | YES | 0.041081 | 0.039927 | 0.030634 | 0.022132 | 0.015615 | 0.0041756 | -0.0058244 | -0.010353 | -0.014462 | -0.021035 | -0.026095 | -0.036501 | -0.041047 | -0.04586 | 0.058175 | 0.056487 | 0.052003 | 0.046743 | 0.043157 | 0.037765 | 0.032858 | 0.027252 | 0.021925 | 0.016348 | 0.011216 | 0.003567 | 0.00036229 | -0.0035108 | 0.043885 | 0.042438 | 0.034029 | 0.026038 | 0.020041 | 0.0097169 | 0.00065521 | -0.003913 | -0.0097817 | -0.016088 | -0.021652 | -0.031757 | -0.035788 | -0.040129
|  | GLENUIG | CT |  |  |  | 0.048823 | 0.042844 | 0.031645 | 0.022132 | 0.015615 | 0.0041756 | -0.0058244 | -0.010353 | -0.011575 | -0.021035 | -0.025702 | -0.031976 | -0.040694 | -0.04586 | 0.061019 | 0.057801 | 0.052003 | 0.046743 | 0.043157 | 0.037765 | 0.032858 | 0.028723 | 0.024634 | 0.017881 | 0.013335 | 0.0049019 | 0.00036229 | -0.0035108 | 0.050587 | 0.04509 | 0.034839 | 0.026038 | 0.020041 | 0.0097169 | 0.00065521 | -0.0038368 | -0.0067126 | -0.015878 | -0.020713 | -0.027636 | -0.035467 | -0.040129
|  | GLENUIG | LW |  |  |  | 0.041081 | 0.039927 | 0.030634 | 0.024174 | 0.018289 | 0.010123 | -0.0010214 | -0.0089765 | -0.014462 | -0.020653 | -0.026095 | -0.036501 | -0.041047 | -0.041518 | 0.058175 | 0.056487 | 0.052065 | 0.048489 | 0.045376 | 0.040192 | 0.033407 | 0.027252 | 0.021925 | 0.016348 | 0.011216 | 0.003567 | 0.001742 | 0.0015709 | 0.043885 | 0.042438 | 0.034029 | 0.028048 | 0.022641 | 0.014967 | 0.0044221 | -0.003913 | -0.0097817 | -0.016088 | -0.021652 | -0.031757 | -0.035788 | -0.036178
|  | GLENUIG | ST |  |  |  | 0.053204 | 0.050682 | 0.047443 | 0.0427 | 0.039232 | 0.035375 | 0.034462 | 0.031417 | 0.024335 | 0.015749 | 0.011745 | -0.021167 | -0.029888 | -0.034268 | 0.063012 | 0.061668 | 0.059985 | 0.057574 | 0.055558 | 0.053225 | 0.051438 | 0.048597 | 0.044092 | 0.038878 | 0.034881 | 0.010142 | 0.0043351 | 0.0014442 | 0.054612 | 0.052214 | 0.049254 | 0.044931 | 0.041707 | 0.038097 | 0.036731 | 0.033338 | 0.026516 | 0.018433 | 0.014301 | -0.017736 | -0.02587 | -0.029704
|  | GLENUIG | FS |  |  |  | 0.053375 | 0.052615 | 0.047947 | 0.044973 | 0.043784 | 0.040174 | 0.038472 | 0.034971 | 0.027025 | 0.025838 | 0.020878 | -0.011439 | -0.035386 | -0.038282 | 0.063119 | 0.062557 | 0.060368 | 0.058754 | 0.057763 | 0.05577 | 0.054235 | 0.051822 | 0.047883 | 0.045771 | 0.042351 | 0.020567 | 0.0026543 | -0.0007397 | 0.054758 | 0.054089 | 0.049753 | 0.047019 | 0.045842 | 0.042515 | 0.040745 | 0.037279 | 0.0301 | 0.028253 | 0.023367 | -0.007491 | -0.030618 | -0.033241
| BRORA | GOLSPIE | MINIMUM HEADROOM | NC 82996 00240 | YES | YES | 2.7648 | 2.6824 | 2.5351 | 2.4266 | 2.3181 | 2.2024 | 2.0843 | 2.0125 | 1.9433 | 1.8656 | 1.8013 | 1.6571 | 1.5327 | 1.4572 | 3.1384 | 3.032 | 2.9326 | 2.8763 | 2.8183 | 2.7455 | 2.6716 | 2.6199 | 2.5672 | 2.5108 | 2.4619 | 2.3745 | 2.2765 | 2.1929 | 2.6736 | 2.5583 | 2.4281 | 2.3317 | 2.2349 | 2.1312 | 2.0287 | 1.9613 | 1.8946 | 1.8217 | 1.7595 | 1.6331 | 1.5455 | 1.4835
|  | GOLSPIE | CT |  |  |  | 2.7685 | 2.7299 | 2.6189 | 2.4867 | 2.3518 | 2.2204 | 2.0913 | 2.0452 | 1.9726 | 1.8975 | 1.8333 | 1.7215 | 1.5327 | 1.4572 | 3.1679 | 3.0817 | 2.9739 | 2.8937 | 2.8245 | 2.7568 | 2.6896 | 2.6452 | 2.5911 | 2.5355 | 2.487 | 2.3824 | 2.2765 | 2.1929 | 2.724 | 2.6472 | 2.5022 | 2.3813 | 2.2645 | 2.1477 | 2.0328 | 1.9957 | 1.9286 | 1.8564 | 1.7953 | 1.6859 | 1.5455 | 1.4835
|  | GOLSPIE | LW |  |  |  | 2.7648 | 2.6824 | 2.5351 | 2.4266 | 2.3181 | 2.2024 | 2.0843 | 2.0125 | 1.9433 | 1.8656 | 1.8013 | 1.6571 | 1.5531 | 1.5112 | 3.1384 | 3.032 | 2.9326 | 2.8763 | 2.8183 | 2.7455 | 2.6716 | 2.6199 | 2.5672 | 2.5108 | 2.4619 | 2.3745 | 2.3324 | 2.3143 | 2.6736 | 2.5583 | 2.4281 | 2.3317 | 2.2349 | 2.1312 | 2.0287 | 1.9613 | 1.8946 | 1.8217 | 1.7595 | 1.6331 | 1.5538 | 1.5226
|  | GOLSPIE | ST |  |  |  | 2.7731 | 2.737 | 2.7125 | 2.7059 | 2.6996 | 2.6894 | 2.6428 | 2.5905 | 2.5369 | 2.4786 | 2.4203 | 2.0916 | 1.9518 | 1.8503 | 3.1972 | 3.1281 | 3.0661 | 3.0401 | 3.013 | 2.9852 | 2.9513 | 2.9125 | 2.871 | 2.825 | 2.7769 | 2.5306 | 2.4325 | 2.3413 | 2.7343 | 2.698 | 2.6625 | 2.6238 | 2.5838 | 2.5425 | 2.4977 | 2.4449 | 2.3884 | 2.3265 | 2.2636 | 1.9485 | 1.8301 | 1.7483
|  | GOLSPIE | FS |  |  |  | 2.7753 | 2.7478 | 2.729 | 2.7211 | 2.716 | 2.7095 | 2.675 | 2.6286 | 2.5738 | 2.5216 | 2.4656 | 2.0714 | 1.8033 | 1.7036 | 3.2052 | 3.1522 | 3.1044 | 3.0742 | 3.0477 | 3.0166 | 2.9884 | 2.9558 | 2.9157 | 2.8757 | 2.8341 | 2.5636 | 2.3435 | 2.1947 | 2.7356 | 2.7083 | 2.6917 | 2.6498 | 2.6117 | 2.5683 | 2.5269 | 2.482 | 2.43 | 2.3781 | 2.3217 | 1.9639 | 1.733 | 1.6636
| BURGHMUIR | GOODLYBURN | MINIMUM HEADROOM | NO 10084 24586 | NO | YES | 2.5259 | 2.2707 | 1.684 | 1.0537 | 0.31239 | -0.53651 | -1.344 | -1.962 | -2.605 | -3.2737 | -3.9256 | -5.8861 | -6.6326 | -7.0448 | 4.6782 | 4.5348 | 4.2392 | 3.9106 | 3.4391 | 2.8779 | 2.3943 | 2.0448 | 1.6656 | 1.2667 | 0.87978 | -0.19468 | -0.53708 | -1.6268 | 3.7336 | 3.6066 | 3.2582 | 2.8779 | 2.1993 | 1.3316 | 0.5188 | -0.11118 | -0.77587 | -1.4658 | -2.1319 | -3.9825 | -4.613 | -5.0624
|  | GOODLYBURN | CT |  |  |  | 2.6709 | 2.55 | 2.1416 | 1.5972 | 1.0159 | 0.41691 | -0.098834 | -0.67619 | -1.2751 | -1.8844 | -2.5132 | -4.7475 | -6.0857 | -6.7948 | 4.6807 | 4.5679 | 4.302 | 4.0372 | 3.6796 | 3.3028 | 3.0265 | 2.7554 | 2.5121 | 2.2668 | 1.9656 | 0.60478 | -0.36819 | -1.4284 | 3.8424 | 3.7267 | 3.4459 | 3.1457 | 2.7612 | 2.2314 | 1.7503 | 1.2064 | 0.62298 | 0.02974 | -0.57975 | -2.6117 | -3.6966 | -4.2768
|  | GOODLYBURN | LW |  |  |  | 2.5259 | 2.2707 | 1.684 | 1.0537 | 0.31239 | -0.53651 | -1.344 | -1.962 | -2.605 | -3.2737 | -3.9256 | -5.8861 | -6.6326 | -7.0448 | 4.6782 | 4.5348 | 4.2392 | 3.9106 | 3.4391 | 2.8779 | 2.3943 | 2.0448 | 1.6656 | 1.2667 | 0.87978 | -0.19468 | -0.53708 | -0.85046 | 3.7336 | 3.6066 | 3.2582 | 2.8779 | 2.1993 | 1.3316 | 0.5188 | -0.11118 | -0.77587 | -1.4658 | -2.1319 | -3.9825 | -4.613 | -5.0624
|  | GOODLYBURN | ST |  |  |  | 2.7442 | 2.724 | 2.5859 | 2.4731 | 2.3685 | 2.1388 | 2.0116 | 1.8955 | 1.7194 | 1.5002 | 1.2497 | -0.59792 | -1.6905 | -2.8997 | 4.7139 | 4.686 | 4.5147 | 4.3766 | 4.2577 | 3.9675 | 3.7856 | 3.6208 | 3.4312 | 3.2109 | 2.9558 | 1.5507 | 0.95989 | -0.16213 | 3.9333 | 3.9194 | 3.7601 | 3.6366 | 3.5274 | 3.2656 | 3.1365 | 2.996 | 2.7944 | 2.5594 | 2.2865 | 0.63805 | -0.27274 | -1.2695
|  | GOODLYBURN | FS |  |  |  | 2.7434 | 2.7271 | 2.6785 | 2.6216 | 2.5542 | 2.4816 | 2.345 | 2.1814 | 1.9997 | 1.8049 | 1.5939 | 0.038674 | -1.6797 | -3.0933 | 4.7221 | 4.7005 | 4.6449 | 4.583 | 4.5099 | 4.4311 | 4.3198 | 4.2126 | 4.0921 | 3.9577 | 3.8067 | 2.7013 | 0.76591 | -1.6268 | 3.9272 | 3.915 | 3.8592 | 3.7955 | 3.7218 | 3.6426 | 3.5592 | 3.4748 | 3.3801 | 3.2764 | 3.1617 | 1.598 | -0.090753 | -1.2843
| CHARLESTON | GOURDIE | MINIMUM HEADROOM | NO 34573 32203 | YES | YES | 4.213 | 3.807 | 3.2059 | 2.9408 | 2.5671 | 2.1685 | 1.5591 | 1.0738 | 0.82168 | 0.56497 | 0.29055 | -0.58747 | -1.2929 | -2.0097 | 4.7279 | 4.3984 | 3.9253 | 3.7147 | 3.3853 | 3.0205 | 2.4984 | 2.064 | 1.8349 | 1.5988 | 1.3549 | 0.59833 | -0.12339 | -0.98921 | 4.1369 | 3.7849 | 3.2609 | 2.9884 | 2.6024 | 2.1598 | 1.5766 | 1.0938 | 0.78255 | 0.46692 | 0.14448 | -0.77806 | -1.5618 | -2.4542
|  | GOURDIE | CT |  |  |  | 4.3006 | 3.9739 | 3.4676 | 3.2341 | 2.9277 | 2.6163 | 2.0999 | 1.6165 | 1.34 | 1.0766 | 0.80048 | -0.11227 | -0.75258 | -1.1573 | 4.7606 | 4.4754 | 4.0891 | 3.9126 | 3.6523 | 3.3837 | 2.9799 | 2.5656 | 2.3253 | 2.0916 | 1.8564 | 1.0705 | 0.48671 | -0.050289 | 4.2123 | 3.9179 | 3.475 | 3.2342 | 2.9198 | 2.5957 | 2.1537 | 1.7026 | 1.3869 | 1.0804 | 0.77278 | -0.18812 | -0.81107 | -1.2624
|  | GOURDIE | LW |  |  |  | 4.213 | 3.807 | 3.2059 | 2.9408 | 2.5671 | 2.1685 | 1.5591 | 1.0738 | 0.82168 | 0.56497 | 0.29055 | -0.58747 | -1.2929 | -2.0097 | 4.7279 | 4.3984 | 3.9253 | 3.7147 | 3.3853 | 3.0205 | 2.4984 | 2.064 | 1.8349 | 1.5988 | 1.3549 | 0.59833 | -0.12339 | -0.98921 | 4.1369 | 3.7849 | 3.2609 | 2.9884 | 2.6024 | 2.1598 | 1.5766 | 1.0938 | 0.78255 | 0.46692 | 0.14448 | -0.77806 | -1.5618 | -2.4542
|  | GOURDIE | ST |  |  |  | 4.3836 | 4.0996 | 3.6573 | 3.5082 | 3.3626 | 3.1208 | 2.6972 | 2.2649 | 2.0841 | 1.9016 | 1.6921 | 0.61407 | -0.18061 | -0.85479 | 4.8205 | 4.5738 | 4.166 | 4.0151 | 3.8804 | 3.618 | 3.2441 | 2.8376 | 2.6694 | 2.4938 | 2.2923 | 1.2837 | 0.50933 | -0.21249 | 4.2952 | 4.0564 | 3.6416 | 3.4764 | 3.3224 | 3.0395 | 2.6614 | 2.2505 | 2.0459 | 1.8324 | 1.5854 | 0.32595 | -0.49707 | -1.1728
|  | GOURDIE | FS |  |  |  | 4.4059 | 4.1937 | 3.9162 | 3.8062 | 3.7088 | 3.5846 | 3.2927 | 2.993 | 2.814 | 2.6299 | 2.4837 | 1.5947 | 0.75186 | 0.18969 | 4.8366 | 4.6487 | 4.4026 | 4.2983 | 4.2097 | 4.0989 | 3.8455 | 3.5773 | 3.4194 | 3.2581 | 3.121 | 2.3587 | 1.5653 | 0.96648 | 4.3226 | 4.1437 | 3.8913 | 3.7745 | 3.6726 | 3.5466 | 3.291 | 3.0198 | 2.8414 | 2.6548 | 2.4914 | 1.5283 | 0.62878 | 0.14901
| BOAT OF GARTEN | GRANTOWN | MINIMUM HEADROOM | NJ 03670 26311 | NO | YES | 7.8183 | 7.6389 | 7.3755 | 7.1119 | 6.7797 | 6.4081 | 6.076 | 5.9251 | 5.7634 | 5.5022 | 5.2299 | 4.639 | 4.2509 | 3.9168 | 10.2682 | 10.1358 | 9.9294 | 9.7122 | 9.4218 | 9.0648 | 8.758 | 8.5679 | 8.3629 | 8.1559 | 7.9623 | 7.5438 | 7.2437 | 6.9174 | 8.4663 | 8.3047 | 8.0484 | 7.7885 | 7.4435 | 7.0578 | 6.7278 | 6.5803 | 6.422 | 6.1844 | 5.9116 | 5.3369 | 4.9573 | 4.5883
|  | GRANTOWN | CT |  |  |  | 7.9525 | 7.8166 | 7.5444 | 7.2816 | 6.9337 | 6.5733 | 6.2864 | 6.1349 | 5.9934 | 5.8545 | 5.6195 | 5.0312 | 4.549 | 4.3053 | 10.3305 | 10.2305 | 10.0361 | 9.8288 | 9.5504 | 9.2581 | 9.0649 | 8.9055 | 8.707 | 8.508 | 8.3216 | 7.8262 | 7.4634 | 7.1439 | 8.5825 | 8.4589 | 8.21 | 7.9666 | 7.618 | 7.2554 | 6.9877 | 6.8406 | 6.7028 | 6.5679 | 6.3648 | 5.765 | 5.3382 | 5.1027
|  | GRANTOWN | LW |  |  |  | 7.8183 | 7.6389 | 7.3755 | 7.1119 | 6.7797 | 6.4081 | 6.076 | 5.9251 | 5.7634 | 5.5022 | 5.2299 | 4.639 | 4.2509 | 3.9168 | 10.2682 | 10.1358 | 9.9294 | 9.7122 | 9.4218 | 9.0648 | 8.758 | 8.5679 | 8.3629 | 8.1559 | 7.9623 | 7.5438 | 7.2437 | 6.9174 | 8.4663 | 8.3047 | 8.0484 | 7.7885 | 7.4435 | 7.0578 | 6.7278 | 6.5803 | 6.422 | 6.1844 | 5.9116 | 5.3369 | 4.9573 | 4.5883
|  | GRANTOWN | ST |  |  |  | 8.0069 | 7.9993 | 7.8547 | 7.7153 | 7.5871 | 7.3458 | 7.1987 | 7.0406 | 6.8825 | 6.7087 | 6.5134 | 5.512 | 5.0264 | 4.7418 | 10.4008 | 10.3529 | 10.1823 | 10.0458 | 9.9284 | 9.6707 | 9.5316 | 9.3806 | 9.2406 | 9.0877 | 8.9133 | 8.0368 | 7.6208 | 7.2537 | 8.6247 | 8.6177 | 8.4621 | 8.3137 | 8.1825 | 7.9133 | 7.7645 | 7.6074 | 7.4652 | 7.3119 | 7.1393 | 6.2705 | 5.8061 | 5.4785
|  | GRANTOWN | FS |  |  |  | 8.01 | 8.0032 | 7.97 | 7.8685 | 7.7574 | 7.6427 | 7.529 | 7.4107 | 7.2937 | 7.1698 | 7.038 | 6.2047 | 5.5169 | 5.1972 | 10.4181 | 10.3776 | 10.2999 | 10.2208 | 10.1336 | 10.0402 | 9.9449 | 9.8445 | 9.7414 | 9.629 | 9.5071 | 8.7541 | 8.0675 | 7.6118 | 8.6275 | 8.6212 | 8.5909 | 8.4946 | 8.3868 | 8.2753 | 8.1654 | 8.0533 | 7.9432 | 7.8266 | 7.7023 | 6.9309 | 6.268 | 6.0288
| SHETLAND | GREMISTA | MINIMUM HEADROOM | HU4646842756 | NO | YES | 27.0734 | 25.9064 | 24.1072 | 21.7726 | 19.2792 | 16.7334 | 14.8073 | 13.6034 | 12.2567 | 10.8759 | 10.1805 | 8.1367 | 7.5914 | 7.4307 | 28.758 | 27.6863 | 25.9285 | 23.6158 | 21.0122 | 18.433 | 16.6217 | 15.5184 | 14.2707 | 13.001 | 12.4299 | 10.5864 | 10.1523 | 10.0478 | 27.3205 | 26.174 | 24.3213 | 21.9226 | 19.2108 | 16.4834 | 14.4998 | 13.2976 | 11.9435 | 10.5572 | 9.8487 | 7.3344 | 6.6985 | 6.638
|  | GREMISTA | CT |  |  |  | 27.5631 | 26.3975 | 24.893 | 23.0367 | 20.9602 | 19.017 | 17.6514 | 16.5982 | 15.3515 | 14.1079 | 13.5038 | 11.9737 | 11.3806 | 11.1805 | 29.1422 | 28.0383 | 26.7329 | 25.0633 | 23.0506 | 21.2309 | 20.1055 | 19.1359 | 17.9721 | 16.8213 | 16.3295 | 14.8302 | 14.2346 | 13.7009 | 27.7639 | 26.5728 | 25.1097 | 23.3254 | 21.17 | 19.1737 | 17.8486 | 16.7865 | 15.6068 | 14.4402 | 13.8458 | 12.0118 | 11.4911 | 11.3023
|  | GREMISTA | LW |  |  |  | 27.0734 | 25.9064 | 24.1072 | 21.7726 | 19.2792 | 16.7334 | 14.8073 | 13.6034 | 12.2567 | 10.8759 | 10.1805 | 8.1367 | 7.5914 | 7.4307 | 28.758 | 27.6863 | 25.9285 | 23.6158 | 21.0122 | 18.433 | 16.6217 | 15.5184 | 14.2707 | 13.001 | 12.4299 | 10.5864 | 10.1523 | 10.0478 | 27.3205 | 26.174 | 24.3213 | 21.9226 | 19.2108 | 16.4834 | 14.4998 | 13.2976 | 11.9435 | 10.5572 | 9.8487 | 7.3344 | 6.6985 | 6.638
|  | GREMISTA | ST |  |  |  | 27.8568 | 26.8916 | 25.464 | 23.8763 | 22.4758 | 20.8063 | 19.7845 | 18.7907 | 17.6468 | 16.4779 | 15.9068 | 12.7492 | 11.6998 | 11.5061 | 29.2881 | 28.3141 | 26.7132 | 24.9109 | 23.3299 | 21.4255 | 20.3666 | 19.3829 | 18.2536 | 17.1184 | 16.6888 | 14.7172 | 14.1731 | 13.7693 | 28.0342 | 27.064 | 25.4947 | 23.8146 | 22.3315 | 20.4555 | 19.3742 | 18.3507 | 17.1834 | 15.9878 | 15.3016 | 11.9125 | 10.9089 | 10.691
|  | GREMISTA | FS |  |  |  | 28.9632 | 28.1852 | 27.2632 | 26.1288 | 25.031 | 23.9974 | 23.032 | 22.0865 | 21.0125 | 19.9633 | 19.2687 | 16.2437 | 14.1698 | 12.7662 | 30.4043 | 29.6132 | 28.6904 | 27.5498 | 26.4355 | 25.4096 | 24.4453 | 23.4965 | 22.4045 | 21.355 | 20.7253 | 18.1004 | 16.0428 | 14.5489 | 29.1363 | 28.3494 | 27.401 | 26.2435 | 25.1061 | 24.0595 | 23.0832 | 22.1401 | 21.0667 | 20.0189 | 19.323 | 16.1451 | 13.6315 | 12.2851
| WILLOWDALE | GREYFRIARS | MINIMUM HEADROOM | NJ 94327 07070 | NO | NO | 14.7933 | 14.126 | 13.1809 | 12.2693 | 11.2276 | 9.8419 | 8.3676 | 7.1687 | 5.8566 | 4.4934 | 3.1782 | 0.03409 | -0.72376 | -2.6191 | 17.1668 | 16.7538 | 16.1759 | 15.5848 | 14.8705 | 13.8826 | 12.8595 | 11.9462 | 10.9394 | 9.8935 | 8.8908 | 6.4803 | 4.984 | -1.6663 | 14.0477 | 13.4458 | 12.5226 | 11.6203 | 10.5894 | 9.2512 | 7.8148 | 6.6354 | 5.3432 | 4.0017 | 2.7094 | -0.3958 | -1.2225 | -3.2346
|  | GREYFRIARS | CT |  |  |  | 15.1086 | 14.6657 | 13.702 | 12.7554 | 11.879 | 10.9387 | 9.9996 | 9.1188 | 8.2441 | 7.3791 | 6.3455 | 2.658 | 1.0827 | 0.31176 | 17.2159 | 16.8703 | 16.2419 | 15.5848 | 14.939 | 14.2359 | 13.5945 | 12.9095 | 12.2176 | 11.5214 | 10.6741 | 7.3059 | 4.984 | 1.9307 | 14.3825 | 13.9888 | 13.0779 | 12.1748 | 11.2867 | 10.3357 | 9.4526 | 8.6047 | 7.7605 | 6.9253 | 5.9211 | 2.3777 | 0.90303 | 0.14411
|  | GREYFRIARS | LW |  |  |  | 14.7933 | 14.126 | 13.1809 | 12.2693 | 11.2276 | 9.8419 | 8.3676 | 7.1687 | 5.8566 | 4.4934 | 3.1782 | 0.03409 | -0.72376 | -2.6191 | 17.1668 | 16.7538 | 16.1759 | 15.586 | 14.8705 | 13.8826 | 12.8595 | 11.9462 | 10.9394 | 9.8935 | 8.8908 | 6.4803 | 5.7773 | 4.0153 | 14.0477 | 13.4458 | 12.5226 | 11.6203 | 10.5894 | 9.2512 | 7.8148 | 6.6354 | 5.3432 | 4.0017 | 2.7094 | -0.3958 | -1.2225 | -3.2346
|  | GREYFRIARS | ST |  |  |  | 15.4244 | 15.2009 | 14.8533 | 14.578 | 14.28 | 13.8144 | 13.3706 | 12.8633 | 12.3025 | 11.6736 | 10.9591 | 6.8115 | 5.0001 | 3.5219 | 17.3936 | 17.1992 | 16.8657 | 16.5718 | 16.261 | 15.7639 | 15.3267 | 14.8305 | 14.2959 | 13.6956 | 13.0113 | 9.0519 | 6.356 | 2.9268 | 14.6938 | 14.5064 | 14.1744 | 13.9085 | 13.6234 | 13.1279 | 12.6833 | 12.1714 | 11.6135 | 10.9879 | 10.2752 | 6.2104 | 4.4248 | 2.9504
|  | GREYFRIARS | FS |  |  |  | 15.453 | 15.2832 | 15.0147 | 14.7909 | 14.5298 | 14.2298 | 13.8915 | 13.5188 | 13.1031 | 12.6477 | 12.1461 | 8.7439 | 5.5242 | 3.1251 | 17.395 | 17.2237 | 16.9839 | 16.7488 | 16.4755 | 16.1572 | 15.7974 | 15.403 | 14.9613 | 14.467 | 13.9134 | 10.1117 | 5.1437 | -1.6663 | 14.719 | 14.582 | 14.3403 | 14.13 | 13.8859 | 13.6088 | 13.2784 | 12.9102 | 12.5015 | 12.0541 | 11.5616 | 8.2304 | 5.073 | 2.8163
| GRUDIE BRIDGE | GRUDIE BRIDGE | MINIMUM HEADROOM | NH 309 623 | NO | YES | 23.28 | 23.28 | 23.2091 | 23.1611 | 23.1294 | 23.0205 | 22.9902 | 22.9083 | 22.8792 | 22.8546 | 22.8153 | 22.631 | 22.3606 | 22.083 | 22.08 | 22.08 | 21.9913 | 21.9314 | 21.8917 | 21.7556 | 21.7177 | 21.6153 | 21.579 | 21.5483 | 21.4992 | 21.2688 | 20.9307 | 20.5837 | 22.08 | 22.08 | 21.9913 | 21.9314 | 21.8917 | 21.7556 | 21.7177 | 21.6153 | 21.579 | 21.5483 | 21.4992 | 21.2688 | 20.9307 | 20.5837
|  | GRUDIE BRIDGE | CT |  |  |  | 23.28 | 23.28 | 23.2708 | 23.2544 | 23.1755 | 23.0914 | 23.0701 | 23.0328 | 22.9954 | 22.9631 | 22.9276 | 22.739 | 22.5611 | 22.369 | 22.08 | 22.08 | 22.0685 | 22.0479 | 21.9494 | 21.8442 | 21.8176 | 21.771 | 21.7243 | 21.6839 | 21.6395 | 21.4037 | 21.1814 | 20.9413 | 22.08 | 22.08 | 22.0685 | 22.0479 | 21.9494 | 21.8442 | 21.8176 | 21.771 | 21.7243 | 21.6839 | 21.6395 | 21.4037 | 21.1814 | 20.9413
|  | GRUDIE BRIDGE | LW |  |  |  | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.2654 | 23.2503 | 23.2379 | 23.2239 | 23.1503 | 22.8201 | 22.3362 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.0618 | 22.0429 | 22.0274 | 22.0099 | 21.9179 | 21.5051 | 20.9003 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.0618 | 22.0429 | 22.0274 | 22.0099 | 21.9179 | 21.5051 | 20.9003
|  | GRUDIE BRIDGE | ST |  |  |  | 23.28 | 23.28 | 23.2091 | 23.1611 | 23.1294 | 23.0205 | 22.9902 | 22.9083 | 22.8792 | 22.8546 | 22.8153 | 22.631 | 22.3606 | 22.083 | 22.08 | 22.08 | 21.9913 | 21.9314 | 21.8917 | 21.7556 | 21.7177 | 21.6153 | 21.579 | 21.5483 | 21.4992 | 21.2688 | 20.9307 | 20.5837 | 22.08 | 22.08 | 21.9913 | 21.9314 | 21.8917 | 21.7556 | 21.7177 | 21.6153 | 21.579 | 21.5483 | 21.4992 | 21.2688 | 20.9307 | 20.5837
|  | GRUDIE BRIDGE | FS |  |  |  | 23.28 | 23.28 | 23.2655 | 23.251 | 23.2341 | 23.2172 | 23.2027 | 23.173 | 23.1529 | 23.1328 | 23.1127 | 23.0883 | 23.0714 | 23.0404 | 22.08 | 22.08 | 22.0619 | 22.0437 | 22.0226 | 22.0015 | 21.9833 | 21.9463 | 21.9211 | 21.896 | 21.8709 | 21.8404 | 21.8193 | 21.7805 | 22.08 | 22.08 | 22.0619 | 22.0437 | 22.0226 | 22.0015 | 21.9833 | 21.9463 | 21.9211 | 21.896 | 21.8709 | 21.8404 | 21.8193 | 21.7805
| SHETLAND | GUTCHER | MINIMUM HEADROOM | HU5453899599 | YES | YES | 0.26678 | 0.2507 | 0.23178 | 0.21569 | 0.19301 | 0.17157 | 0.14436 | 0.12886 | 0.11786 | 0.099136 | 0.085354 | 0.063485 | 0.049727 | 0.043908 | 0.51662 | 0.50567 | 0.49465 | 0.4805 | 0.4682 | 0.45484 | 0.43612 | 0.41903 | 0.40253 | 0.38128 | 0.36296 | 0.3384 | 0.32859 | 0.319 | 0.35431 | 0.3495 | 0.34377 | 0.3383 | 0.33146 | 0.32326 | 0.31115 | 0.29442 | 0.27134 | 0.24412 | 0.22026 | 0.17446 | 0.16533 | 0.16232
|  | GUTCHER | CT |  |  |  | 0.2776 | 0.26273 | 0.2403 | 0.21696 | 0.19558 | 0.17201 | 0.14826 | 0.138 | 0.12581 | 0.11363 | 0.099458 | 0.080181 | 0.051417 | 0.046081 | 0.52101 | 0.51163 | 0.49647 | 0.4805 | 0.4682 | 0.45484 | 0.44138 | 0.42898 | 0.41222 | 0.39407 | 0.37645 | 0.34365 | 0.32859 | 0.319 | 0.35684 | 0.35237 | 0.34597 | 0.3383 | 0.33161 | 0.32326 | 0.31115 | 0.30914 | 0.29453 | 0.28034 | 0.25982 | 0.21318 | 0.19606 | 0.19072
|  | GUTCHER | LW |  |  |  | 0.26678 | 0.2507 | 0.23178 | 0.21569 | 0.19301 | 0.17157 | 0.14436 | 0.12886 | 0.11786 | 0.099136 | 0.085354 | 0.063485 | 0.049727 | 0.043908 | 0.51662 | 0.50567 | 0.49465 | 0.48364 | 0.47159 | 0.45568 | 0.43612 | 0.41903 | 0.40253 | 0.38128 | 0.36296 | 0.3384 | 0.33279 | 0.33111 | 0.35431 | 0.3495 | 0.34377 | 0.33923 | 0.33146 | 0.32575 | 0.3137 | 0.29442 | 0.27134 | 0.24412 | 0.22026 | 0.17446 | 0.16533 | 0.16232
|  | GUTCHER | ST |  |  |  | 0.29077 | 0.28861 | 0.28561 | 0.28174 | 0.27386 | 0.26696 | 0.25894 | 0.24999 | 0.24311 | 0.2256 | 0.21445 | 0.14979 | 0.13249 | 0.11881 | 0.52678 | 0.52435 | 0.52107 | 0.51677 | 0.51077 | 0.50441 | 0.49675 | 0.48778 | 0.47824 | 0.46329 | 0.4487 | 0.37079 | 0.3533 | 0.34388 | 0.36398 | 0.36422 | 0.36461 | 0.36562 | 0.36382 | 0.36352 | 0.36259 | 0.36173 | 0.36342 | 0.3529 | 0.33294 | 0.22287 | 0.18705 | 0.17674
|  | GUTCHER | FS |  |  |  | 0.29508 | 0.2913 | 0.28299 | 0.27429 | 0.27086 | 0.26301 | 0.25676 | 0.24802 | 0.24037 | 0.22856 | 0.21934 | 0.14865 | 0.10177 | 0.080664 | 0.52846 | 0.52569 | 0.52095 | 0.51563 | 0.51191 | 0.50615 | 0.50047 | 0.49336 | 0.48588 | 0.47645 | 0.46712 | 0.4008 | 0.34515 | 0.33083 | 0.3651 | 0.36449 | 0.36227 | 0.36046 | 0.36107 | 0.35982 | 0.35914 | 0.35796 | 0.3571 | 0.3546 | 0.3538 | 0.27358 | 0.20404 | 0.16429
| THURSO | HALKIRK | MINIMUM HEADROOM | ND 13246 58223 | YES | YES | 0.43218 | 0.31674 | 0.18182 | 0.58177 | 0.45542 | 0.28805 | 0.12682 | 0.013823 | -0.12045 | -0.25169 | -0.37903 | -0.77746 | -1.3911 | -2.1188 | 1.0607 | 1.0016 | 0.93577 | 1.3796 | 1.2775 | 1.1721 | 1.0898 | 0.99524 | 0.88409 | 0.77702 | 0.67273 | 0.31264 | -0.26328 | -1.1306 | 0.56193 | 0.45694 | 0.33529 | 0.72414 | 0.60108 | 0.43278 | 0.28495 | 0.16778 | 0.02953 | -0.10463 | -0.23321 | -0.641 | -1.3489 | -2.239
|  | HALKIRK | CT |  |  |  | 0.54088 | 0.4505 | 0.27671 | 0.64243 | 0.46384 | 0.28805 | 0.12682 | 0.013823 | -0.12045 | -0.25169 | -0.37658 | -0.75461 | -1.2397 | -1.5978 | 1.1065 | 1.0531 | 0.96032 | 1.3845 | 1.2775 | 1.1721 | 1.0898 | 0.99524 | 0.88409 | 0.77702 | 0.67273 | 0.31264 | -0.10482 | -0.5286 | 0.65807 | 0.57514 | 0.41601 | 0.77126 | 0.60108 | 0.43278 | 0.28495 | 0.16778 | 0.02953 | -0.10463 | -0.23321 | -0.641 | -1.1535 | -1.5685
|  | HALKIRK | LW |  |  |  | 0.43218 | 0.31674 | 0.18182 | 0.58177 | 0.45542 | 0.30447 | 0.14483 | 0.015563 | -0.11814 | -0.24877 | -0.37903 | -0.77746 | -1.3911 | -2.1188 | 1.0607 | 1.0016 | 0.93577 | 1.3796 | 1.3212 | 1.2422 | 1.1557 | 1.0489 | 0.93661 | 0.82935 | 0.72235 | 0.38624 | -0.26328 | -1.1306 | 0.56193 | 0.45694 | 0.33529 | 0.72414 | 0.61034 | 0.47194 | 0.32478 | 0.19159 | 0.053334 | -0.080395 | -0.21426 | -0.63417 | -1.3489 | -2.239
|  | HALKIRK | ST |  |  |  | 0.58713 | 0.52956 | 0.43483 | 0.89132 | 0.80747 | 0.69851 | 0.60517 | 0.44829 | 0.32909 | 0.20496 | 0.061966 | -0.63005 | -1.2244 | -1.7423 | 1.1285 | 1.0961 | 1.029 | 1.4921 | 1.4392 | 1.3552 | 1.2976 | 1.1601 | 1.073 | 0.9844 | 0.87366 | 0.32822 | -0.25459 | -0.83688 | 0.69983 | 0.64791 | 0.55425 | 0.989 | 0.90915 | 0.79736 | 0.70849 | 0.54039 | 0.42143 | 0.29881 | 0.15405 | -0.54664 | -1.2051 | -1.8032
|  | HALKIRK | FS |  |  |  | 0.66453 | 0.61943 | 0.55686 | 1.0399 | 0.97137 | 0.9005 | 0.82798 | 0.71543 | 0.61044 | 0.50379 | 0.38704 | -0.25969 | -0.67376 | -0.86124 | 1.1822 | 1.1549 | 1.1179 | 1.6042 | 1.5638 | 1.521 | 1.4768 | 1.3976 | 1.3265 | 1.2529 | 1.172 | 0.78361 | 0.48117 | 0.27582 | 0.7699 | 0.72912 | 0.67104 | 1.1339 | 1.0699 | 1.0036 | 0.93577 | 0.82459 | 0.72264 | 0.6188 | 0.5055 | -0.09687 | -0.49071 | -0.67417
| ABERNETHY | HARBOUR | MINIMUM HEADROOM | NO 11948 22049 | NO | YES | 18.86 | 18.2617 | 17.1178 | 15.7361 | 14.371 | 12.8924 | 11.6801 | 10.9186 | 10.1224 | 9.3018 | 8.531 | 6.36 | 5.4572 | 4.9069 | 19.4568 | 19.0593 | 18.2687 | 17.3033 | 16.2946 | 15.21 | 14.4244 | 13.9985 | 13.5349 | 12.98 | 12.4529 | 11.0425 | 10.5268 | 10.0645 | 17.6494 | 17.218 | 16.2519 | 14.8983 | 13.4636 | 11.8989 | 10.6685 | 9.9542 | 9.2042 | 8.4348 | 7.7086 | 5.6593 | 4.8121 | 4.2503
|  | HARBOUR | CT |  |  |  | 18.8885 | 18.4531 | 17.7526 | 16.624 | 15.6101 | 14.5812 | 13.8341 | 13.1313 | 12.3925 | 11.6499 | 10.9228 | 8.5385 | 7.2466 | 6.5118 | 19.4568 | 19.0593 | 18.5449 | 17.8541 | 17.1846 | 16.415 | 16.0003 | 15.6655 | 15.3717 | 15.0803 | 14.6023 | 12.9333 | 11.7933 | 10.4139 | 17.6494 | 17.218 | 16.6833 | 15.8372 | 14.8091 | 13.7532 | 13.0513 | 12.4126 | 11.7395 | 11.0637 | 10.3972 | 8.214 | 7.0569 | 6.3885
|  | HARBOUR | LW |  |  |  | 18.86 | 18.2617 | 17.1178 | 15.7361 | 14.371 | 12.8924 | 11.6801 | 10.9186 | 10.1224 | 9.3018 | 8.531 | 6.36 | 5.4572 | 4.9069 | 19.4698 | 19.0614 | 18.2687 | 17.3033 | 16.2946 | 15.21 | 14.4244 | 13.9985 | 13.5349 | 12.98 | 12.4529 | 11.0425 | 10.5268 | 10.0645 | 17.6671 | 17.2368 | 16.2519 | 14.8983 | 13.4636 | 11.8989 | 10.6685 | 9.9542 | 9.2042 | 8.4348 | 7.7086 | 5.6593 | 4.8121 | 4.2503
|  | HARBOUR | ST |  |  |  | 18.9462 | 18.6179 | 17.9312 | 17.1971 | 16.8642 | 16.1761 | 15.8289 | 15.5748 | 15.2776 | 14.9031 | 14.498 | 12.1737 | 10.9696 | 9.7321 | 19.5147 | 19.2 | 18.4527 | 17.6946 | 17.3739 | 16.6062 | 16.2732 | 16.0282 | 15.7203 | 15.3688 | 14.9652 | 12.894 | 12.1091 | 11.0271 | 17.7093 | 17.3884 | 16.6291 | 15.8547 | 15.5021 | 14.7 | 14.3285 | 14.0769 | 13.7994 | 13.4122 | 12.9708 | 10.4998 | 9.5737 | 9.0229
|  | HARBOUR | FS |  |  |  | 19.0393 | 18.78 | 18.4373 | 17.964 | 17.713 | 17.4476 | 17.2072 | 16.9179 | 16.5804 | 16.2522 | 15.9227 | 13.9487 | 12.0065 | 10.599 | 19.6036 | 19.3541 | 19.0095 | 18.5431 | 18.307 | 18.0502 | 17.8314 | 17.6669 | 17.4528 | 17.2564 | 17.0602 | 15.5775 | 13.2832 | 10.4341 | 17.8027 | 17.5511 | 17.2011 | 16.7267 | 16.4731 | 16.2012 | 15.9657 | 15.7891 | 15.5635 | 15.3532 | 15.144 | 13.3297 | 11.5211 | 10.2445
| STORNOWAY | HARRIS GRID | MINIMUM HEADROOM | NG 13495 94249 | YES | YES | 34.9454 | 34.9265 | 34.8905 | 34.8372 | 34.7931 | 34.7001 | 34.6703 | 34.5908 | 34.5618 | 34.5317 | 34.4863 | 34.2472 | 33.9915 | 33.7552 | 32.3579 | 32.3401 | 32.2853 | 32.223 | 32.1811 | 32.0533 | 32.0167 | 31.9245 | 31.8866 | 31.852 | 31.8003 | 31.5359 | 31.2304 | 30.9374 | 32.2632 | 32.2444 | 32.1912 | 32.1283 | 32.0857 | 31.957 | 31.9192 | 31.8256 | 31.7859 | 31.7492 | 31.695 | 31.4144 | 31.1035 | 30.8102
|  | HARRIS GRID | CT |  |  |  | 34.9692 | 34.9519 | 34.9196 | 34.8855 | 34.7931 | 34.7053 | 34.671 | 34.6325 | 34.5948 | 34.5589 | 34.5245 | 34.3343 | 34.1775 | 34.0094 | 32.3759 | 32.3577 | 32.3289 | 32.292 | 32.1963 | 32.0909 | 32.0597 | 32.0128 | 31.966 | 31.9244 | 31.8783 | 31.6493 | 31.4581 | 31.2522 | 32.2811 | 32.2607 | 32.2294 | 32.1898 | 32.0923 | 31.9851 | 31.9479 | 31.8986 | 31.8518 | 31.8087 | 31.7609 | 31.5266 | 31.3324 | 31.1241
|  | HARRIS GRID | LW |  |  |  | 34.9454 | 34.9265 | 34.9175 | 34.9006 | 34.8853 | 34.8688 | 34.8552 | 34.833 | 34.8055 | 34.7866 | 34.7666 | 34.649 | 34.3549 | 33.9468 | 32.3579 | 32.3401 | 32.3365 | 32.3229 | 32.3087 | 32.3012 | 32.2921 | 32.2656 | 32.2359 | 32.2084 | 32.1794 | 32.0569 | 31.6977 | 31.188 | 32.2632 | 32.2444 | 32.24 | 32.2252 | 32.2099 | 32.1979 | 32.1832 | 32.1533 | 32.1195 | 32.0901 | 32.0592 | 31.9279 | 31.5652 | 31.0554
|  | HARRIS GRID | ST |  |  |  | 34.9785 | 34.9646 | 34.8905 | 34.8372 | 34.8059 | 34.7001 | 34.6703 | 34.5908 | 34.5618 | 34.5317 | 34.4863 | 34.2472 | 33.9915 | 33.7552 | 32.3819 | 32.3712 | 32.2853 | 32.223 | 32.1811 | 32.0533 | 32.0167 | 31.9245 | 31.8866 | 31.852 | 31.8003 | 31.5359 | 31.2304 | 30.9374 | 32.2886 | 32.2776 | 32.1912 | 32.1283 | 32.0857 | 31.957 | 31.9192 | 31.8256 | 31.7859 | 31.7492 | 31.695 | 31.4144 | 31.1035 | 30.8102
|  | HARRIS GRID | FS |  |  |  | 35.0108 | 35.0033 | 34.9772 | 34.9544 | 34.9338 | 34.9109 | 34.8916 | 34.8559 | 34.8288 | 34.8013 | 34.7754 | 34.6838 | 34.6141 | 34.5447 | 32.416 | 32.4105 | 32.3846 | 32.3586 | 32.3344 | 32.3098 | 32.2874 | 32.2484 | 32.219 | 32.1889 | 32.1581 | 32.0661 | 31.9987 | 31.9325 | 32.3232 | 32.3174 | 32.2913 | 32.2649 | 32.2403 | 32.2152 | 32.1921 | 32.1524 | 32.1221 | 32.091 | 32.059 | 31.9541 | 31.8765 | 31.8019
| DYCE | HARVEST AVENUE | MINIMUM HEADROOM | NJ 86978 11769 | NO | YES | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08
|  | HARVEST AVENUE | CT |  |  |  | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08
|  | HARVEST AVENUE | LW |  |  |  | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08
|  | HARVEST AVENUE | ST |  |  |  | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08
|  | HARVEST AVENUE | FS |  |  |  | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08
| THURSO | HASTIGROW | MINIMUM HEADROOM | ND 26576 60773 | YES | YES | 2.7619 | 2.5998 | 2.414 | 2.2175 | 1.9092 | 1.579 | 1.3189 | 1.1406 | 0.92609 | 0.72061 | 0.52497 | -0.093247 | -0.95753 | -1.8606 | 2.777 | 2.6968 | 2.6104 | 2.4666 | 2.2434 | 2.0098 | 1.8654 | 1.7103 | 1.533 | 1.3655 | 1.1998 | 0.50707 | -0.42025 | -1.3173 | 2.9688 | 2.8221 | 2.6533 | 2.4745 | 2.1513 | 1.8167 | 1.5707 | 1.3891 | 1.1774 | 0.97693 | 0.78142 | 0.11336 | -0.9234 | -1.9696
|  | HASTIGROW | CT |  |  |  | 2.8936 | 2.7725 | 2.5126 | 2.2291 | 1.9092 | 1.579 | 1.3189 | 1.1406 | 0.92609 | 0.72061 | 0.52497 | -0.093247 | -0.81527 | -1.3661 | 2.826 | 2.7594 | 2.622 | 2.4666 | 2.2434 | 2.0098 | 1.8654 | 1.7103 | 1.533 | 1.3655 | 1.1998 | 0.59197 | -0.052627 | -0.69313 | 3.0884 | 2.9779 | 2.7379 | 2.4745 | 2.1513 | 1.8167 | 1.5707 | 1.3891 | 1.1774 | 0.97693 | 0.78142 | 0.11336 | -0.6728 | -1.3182
|  | HASTIGROW | LW |  |  |  | 2.7619 | 2.5998 | 2.414 | 2.2175 | 2.0315 | 1.804 | 1.5564 | 1.369 | 1.1674 | 0.96653 | 0.77368 | 0.20874 | -0.72426 | -1.8606 | 2.777 | 2.6968 | 2.6104 | 2.517 | 2.4302 | 2.3134 | 2.1834 | 2.0343 | 1.8747 | 1.7208 | 1.5695 | 1.0942 | 0.078088 | -1.2946 | 2.9688 | 2.8221 | 2.6533 | 2.4751 | 2.3057 | 2.1 | 1.8765 | 1.6948 | 1.4999 | 1.3081 | 1.1216 | 0.53421 | -0.56915 | -1.9696
|  | HASTIGROW | ST |  |  |  | 2.9526 | 2.8876 | 2.7134 | 2.5563 | 2.4162 | 2.1743 | 2.0219 | 1.7501 | 1.5527 | 1.3539 | 1.1159 | -0.020403 | -0.95753 | -1.7605 | 2.8556 | 2.8241 | 2.677 | 2.5571 | 2.4587 | 2.24 | 2.132 | 1.8843 | 1.7379 | 1.5933 | 1.4078 | 0.50707 | -0.42025 | -1.3173 | 3.1435 | 3.0845 | 2.8978 | 2.7361 | 2.5963 | 2.3332 | 2.183 | 1.8892 | 1.6937 | 1.4998 | 1.2616 | 0.12775 | -0.9234 | -1.8652
|  | HASTIGROW | FS |  |  |  | 3.0077 | 2.962 | 2.8669 | 2.7733 | 2.6701 | 2.5622 | 2.4513 | 2.286 | 2.1248 | 1.9639 | 1.795 | 0.83641 | 0.19321 | -0.10101 | 2.8779 | 2.8547 | 2.797 | 2.7379 | 2.672 | 2.6023 | 2.532 | 2.4096 | 2.3004 | 2.1889 | 2.0717 | 1.5158 | 1.0795 | 0.80232 | 3.194 | 3.1527 | 3.0605 | 2.97 | 2.8696 | 2.7651 | 2.6589 | 2.492 | 2.3344 | 2.1773 | 2.0129 | 1.1306 | 0.53773 | 0.23849
| STRICHEN | HATTON | MINIMUM HEADROOM | NK 06441 37348 | NO | YES | 5.124 | 4.9454 | 4.6554 | 4.3372 | 3.9506 | 3.4071 | 2.9258 | 2.6125 | 2.2879 | 1.9619 | 1.6509 | 0.80584 | -0.089611 | -1.133 | 5.8737 | 5.7714 | 5.5688 | 5.343 | 5.0263 | 4.5695 | 4.1935 | 3.9598 | 3.7145 | 3.472 | 3.2384 | 2.5751 | 1.6564 | 0.44819 | 5.4373 | 5.2669 | 4.9596 | 4.6253 | 4.1991 | 3.621 | 3.1279 | 2.8365 | 2.5361 | 2.2376 | 1.9487 | 1.0792 | 0.019975 | -1.2356
|  | HATTON | CT |  |  |  | 5.269 | 5.1546 | 4.8771 | 4.575 | 4.1953 | 3.7208 | 3.3762 | 3.0857 | 2.7561 | 2.4283 | 2.1161 | 1.1544 | 0.38653 | -0.18516 | 5.9326 | 5.8593 | 5.6893 | 5.4945 | 5.1842 | 4.7822 | 4.5366 | 4.3209 | 4.0737 | 3.8319 | 3.5987 | 2.8184 | 2.1257 | 1.4117 | 5.5942 | 5.4881 | 5.2137 | 4.9158 | 4.4998 | 3.9804 | 3.6199 | 3.3351 | 3.0246 | 2.7186 | 2.4204 | 1.4357 | 0.5659 | -0.097646
|  | HATTON | LW |  |  |  | 5.124 | 4.9454 | 4.6554 | 4.3372 | 3.9506 | 3.4071 | 2.9258 | 2.6125 | 2.2879 | 1.9619 | 1.6509 | 0.80584 | -0.089611 | -1.133 | 5.8737 | 5.7714 | 5.5688 | 5.343 | 5.0263 | 4.5695 | 4.1935 | 3.9598 | 3.7145 | 3.472 | 3.2384 | 2.5751 | 1.6564 | 0.44819 | 5.4373 | 5.2669 | 4.9596 | 4.6253 | 4.1991 | 3.621 | 3.1279 | 2.8365 | 2.5361 | 2.2376 | 1.9487 | 1.0792 | 0.019975 | -1.2356
|  | HATTON | ST |  |  |  | 5.3397 | 5.2796 | 5.0713 | 4.8887 | 4.7294 | 4.3438 | 4.1024 | 3.8497 | 3.6537 | 3.4492 | 3.2113 | 1.9771 | 1.0099 | 0.11141 | 5.9694 | 5.9337 | 5.7232 | 5.555 | 5.4195 | 5.0227 | 4.8095 | 4.574 | 4.4144 | 4.2512 | 4.0529 | 3.0407 | 2.0995 | 1.1278 | 5.6689 | 5.612 | 5.3754 | 5.1775 | 5.0113 | 4.5792 | 4.3298 | 4.0661 | 3.8805 | 3.6917 | 3.4671 | 2.3029 | 1.2169 | 0.16374
|  | HATTON | FS |  |  |  | 5.374 | 5.3303 | 5.2367 | 5.1303 | 5.0198 | 4.8569 | 4.6866 | 4.517 | 4.3561 | 4.1853 | 4.0069 | 2.9815 | 2.1425 | 1.7021 | 5.9843 | 5.9564 | 5.8836 | 5.8024 | 5.7144 | 5.577 | 5.4328 | 5.2983 | 5.1729 | 5.0402 | 4.9012 | 4.1697 | 3.4523 | 2.8642 | 5.705 | 5.6645 | 5.5675 | 5.4593 | 5.3469 | 5.1798 | 5.0064 | 4.8351 | 4.6774 | 4.5121 | 4.3409 | 3.3864 | 2.6114 | 2.1307
| PERSLEY | HAUDAGAIN | MINIMUM HEADROOM | NJ 91425 09066 | NO | YES | 19.4 | 19.4 | 19.2339 | 19.0706 | 18.7197 | 18.3482 | 18.135 | 18.0865 | 18.0362 | 17.9948 | 17.9482 | 17.7032 | 17.318 | 16.8042 | 13.4095 | 13.0688 | 12.5091 | 11.917 | 11.1085 | 10.0908 | 9.1847 | 8.5031 | 7.7608 | 7.0024 | 6.2668 | 4.4067 | 3.7269 | 1.0157 | 12.4333 | 11.9302 | 11.1087 | 10.26 | 9.1955 | 7.8786 | 6.6519 | 5.7405 | 4.7534 | 3.745 | 2.7624 | 0.28086 | -0.50239 | -1.775
|  | HAUDAGAIN | CT |  |  |  | 19.4 | 19.4 | 19.3784 | 19.34 | 19.1553 | 18.9584 | 18.9084 | 18.8887 | 18.8688 | 18.8517 | 18.8328 | 18.7327 | 18.5625 | 18.3586 | 13.5185 | 13.2451 | 12.761 | 12.2349 | 11.5928 | 10.8829 | 10.369 | 9.8339 | 9.2716 | 8.7088 | 8.1065 | 5.7812 | 4.3863 | 2.7035 | 12.732 | 12.3756 | 11.6534 | 10.8896 | 10.0268 | 9.0828 | 8.3453 | 7.6217 | 6.8759 | 6.1313 | 5.3494 | 2.5338 | 1.3892 | 0.78078
|  | HAUDAGAIN | LW |  |  |  | 19.4 | 19.4 | 19.2443 | 19.0706 | 18.7197 | 18.3482 | 18.135 | 18.0865 | 18.0362 | 17.9948 | 17.9482 | 17.7032 | 17.318 | 16.8042 | 13.4095 | 13.0688 | 12.5091 | 11.917 | 11.1085 | 10.0908 | 9.1847 | 8.5031 | 7.7608 | 7.0024 | 6.2668 | 4.4067 | 3.7269 | 2.5863 | 12.4333 | 11.9302 | 11.1087 | 10.26 | 9.1955 | 7.8786 | 6.6519 | 5.7405 | 4.7534 | 3.745 | 2.7624 | 0.28086 | -0.50239 | -1.775
|  | HAUDAGAIN | ST |  |  |  | 19.4 | 19.4 | 19.2339 | 19.1216 | 19.0474 | 18.7924 | 18.7215 | 18.678 | 18.6626 | 18.6495 | 18.6287 | 18.5308 | 18.2678 | 17.9731 | 13.6466 | 13.5101 | 13.157 | 12.8519 | 12.5553 | 11.983 | 11.6003 | 11.2031 | 10.7759 | 10.2907 | 9.7355 | 6.5221 | 4.5264 | 2.4542 | 12.9375 | 12.7688 | 12.3854 | 12.0514 | 11.719 | 11.1011 | 10.6688 | 10.2214 | 9.7344 | 9.179 | 8.5468 | 4.8313 | 3.0253 | 1.7233
|  | HAUDAGAIN | FS |  |  |  | 19.4 | 19.4 | 19.366 | 19.3321 | 19.2925 | 19.2529 | 19.2189 | 19.2032 | 19.1925 | 19.1818 | 19.1712 | 19.1582 | 19.1438 | 19.1109 | 13.7106 | 13.589 | 13.4024 | 13.2078 | 12.9852 | 12.7382 | 12.4665 | 12.1736 | 11.8505 | 11.4908 | 11.0928 | 8.3787 | 5.0116 | 1.0157 | 13.0584 | 12.9196 | 12.7052 | 12.4865 | 12.2392 | 11.9704 | 11.674 | 11.3533 | 11.0043 | 10.6228 | 10.2081 | 7.3873 | 4.5909 | 2.6778
| WILLOWDALE | HAYTON | MINIMUM HEADROOM | NJ 92753 08909 | NO | NO | 14.8905 | 14.4534 | 13.7722 | 13.0487 | 12.3301 | 11.4144 | 10.4058 | 9.5711 | 8.6521 | 7.6459 | 6.6625 | 4.2853 | 3.3887 | 1.7684 | 16.9004 | 16.6377 | 16.2995 | 15.928 | 15.5435 | 15.0331 | 14.3905 | 13.7321 | 13.0139 | 12.276 | 11.5636 | 9.878 | 8.2175 | 4.9017 | 15.6068 | 15.1854 | 14.6018 | 13.9351 | 13.2733 | 12.3864 | 11.3917 | 10.5039 | 9.5426 | 8.5568 | 7.5979 | 5.2843 | 4.305 | 2.5205
|  | HAYTON | CT |  |  |  | 15.2863 | 15.0517 | 14.338 | 13.5751 | 12.878 | 12.1602 | 11.4573 | 10.7699 | 10.0493 | 9.3257 | 8.5021 | 5.505 | 4.0021 | 3.239 | 17.011 | 16.8335 | 16.4207 | 15.964 | 15.5435 | 15.1007 | 14.6795 | 14.155 | 13.5936 | 13.0274 | 12.3778 | 9.9369 | 8.2175 | 6.1484 | 15.8952 | 15.6553 | 15.0124 | 14.3103 | 13.6764 | 12.9962 | 12.3371 | 11.6423 | 10.9084 | 10.1727 | 9.3442 | 6.475 | 5.0516 | 4.275
|  | HAYTON | LW |  |  |  | 14.8905 | 14.4534 | 13.7722 | 13.0487 | 12.3301 | 11.4144 | 10.4058 | 9.5711 | 8.6521 | 7.6459 | 6.6625 | 4.2853 | 3.3887 | 1.7684 | 16.9004 | 16.6377 | 16.2995 | 15.928 | 15.5596 | 15.0331 | 14.3905 | 13.7321 | 13.0139 | 12.276 | 11.5636 | 9.878 | 9.0391 | 7.4274 | 15.6068 | 15.1854 | 14.6018 | 13.9351 | 13.2733 | 12.3864 | 11.3917 | 10.5039 | 9.5426 | 8.5568 | 7.5979 | 5.2843 | 4.305 | 2.5205
|  | HAYTON | ST |  |  |  | 15.4623 | 15.3561 | 15.1794 | 14.9928 | 14.7931 | 14.5125 | 14.2424 | 13.8713 | 13.4993 | 13.0711 | 12.5552 | 9.4159 | 7.6398 | 6.1081 | 17.1083 | 17.0161 | 16.8569 | 16.6893 | 16.5102 | 16.2478 | 16.0038 | 15.6409 | 15.2715 | 14.858 | 14.3815 | 11.6127 | 9.552 | 7.0972 | 16.0548 | 15.9464 | 15.7611 | 15.5622 | 15.3478 | 15.0385 | 14.7379 | 14.3087 | 13.8822 | 13.4116 | 12.8734 | 9.7495 | 8.0675 | 6.6697
|  | HAYTON | FS |  |  |  | 15.5123 | 15.4295 | 15.282 | 15.1149 | 14.9346 | 14.7289 | 14.5088 | 14.1905 | 13.8607 | 13.512 | 13.1334 | 10.4866 | 7.9639 | 6.2367 | 17.125 | 17.0411 | 16.9159 | 16.7704 | 16.6079 | 16.4189 | 16.2086 | 15.92 | 15.614 | 15.2784 | 14.8966 | 12.3053 | 9.0704 | 4.9017 | 16.0948 | 16.0093 | 15.8703 | 15.7064 | 15.526 | 15.3172 | 15.0875 | 14.7669 | 14.4312 | 14.0711 | 13.6777 | 11.1321 | 8.7723 | 7.1836
| BRORA | HELMSDALE | MINIMUM HEADROOM | ND 02372 15376 | YES | YES | 3.6854 | 3.6552 | 3.5826 | 3.5349 | 3.4841 | 3.423 | 3.3558 | 3.3299 | 3.2985 | 3.2486 | 3.2015 | 3.1108 | 3.0622 | 3.0276 | 3.6597 | 3.6327 | 3.5792 | 3.5475 | 3.5168 | 3.4749 | 3.43 | 3.3928 | 3.3517 | 3.3098 | 3.2722 | 3.2096 | 3.1786 | 3.1458 | 3.2176 | 3.1804 | 3.1051 | 3.0579 | 3.0079 | 2.9548 | 2.9043 | 2.8873 | 2.8666 | 2.8349 | 2.7919 | 2.7067 | 2.6608 | 2.6294
|  | HELMSDALE | CT |  |  |  | 3.7009 | 3.6829 | 3.6162 | 3.5717 | 3.5064 | 3.4445 | 3.3726 | 3.3476 | 3.3168 | 3.284 | 3.2363 | 3.1509 | 3.0622 | 3.0276 | 3.6735 | 3.6555 | 3.5937 | 3.5522 | 3.5168 | 3.4827 | 3.4481 | 3.4178 | 3.3782 | 3.3382 | 3.3014 | 3.2273 | 3.1786 | 3.1458 | 3.2529 | 3.2316 | 3.1471 | 3.091 | 3.0283 | 2.971 | 2.9115 | 2.8928 | 2.8739 | 2.8564 | 2.8245 | 2.7451 | 2.6638 | 2.6294
|  | HELMSDALE | LW |  |  |  | 3.6854 | 3.6552 | 3.5826 | 3.5349 | 3.4841 | 3.423 | 3.3558 | 3.3299 | 3.2985 | 3.2486 | 3.2015 | 3.1108 | 3.0624 | 3.0414 | 3.6597 | 3.6327 | 3.5792 | 3.5475 | 3.5169 | 3.4749 | 3.43 | 3.3928 | 3.3517 | 3.3098 | 3.2722 | 3.2096 | 3.188 | 3.1763 | 3.2176 | 3.1804 | 3.1051 | 3.0579 | 3.0079 | 2.9548 | 2.9043 | 2.8873 | 2.8666 | 2.8349 | 2.7919 | 2.7067 | 2.6608 | 2.6418
|  | HELMSDALE | ST |  |  |  | 3.7153 | 3.7074 | 3.6637 | 3.6487 | 3.631 | 3.6135 | 3.5942 | 3.5726 | 3.5508 | 3.5255 | 3.499 | 3.2951 | 3.2216 | 3.1746 | 3.6859 | 3.6784 | 3.6433 | 3.6283 | 3.6107 | 3.5929 | 3.5723 | 3.5475 | 3.5208 | 3.4895 | 3.4561 | 3.2905 | 3.2386 | 3.2041 | 3.2802 | 3.2706 | 3.2246 | 3.2058 | 3.1818 | 3.1626 | 3.1403 | 3.1162 | 3.0937 | 3.0659 | 3.0366 | 2.8644 | 2.7896 | 2.7439
|  | HELMSDALE | FS |  |  |  | 3.7194 | 3.7128 | 3.678 | 3.6615 | 3.6456 | 3.6282 | 3.612 | 3.5947 | 3.5708 | 3.5489 | 3.5282 | 3.3232 | 3.1637 | 3.1191 | 3.6895 | 3.6828 | 3.6553 | 3.6404 | 3.6254 | 3.6091 | 3.5927 | 3.574 | 3.5487 | 3.5241 | 3.4999 | 3.3387 | 3.2105 | 3.1575 | 3.288 | 3.2791 | 3.2424 | 3.2217 | 3.1977 | 3.1777 | 3.156 | 3.1348 | 3.1052 | 3.0796 | 3.0554 | 2.8863 | 2.7467 | 2.7065
| INVERNESS | HILTON | MINIMUM HEADROOM | NH 67326 43262 | NO | YES | 10.3183 | 9.7963 | 8.8621 | 7.8859 | 6.9395 | 5.6613 | 4.2699 | 3.0395 | 1.705 | 0.32618 | -0.98626 | -4.3651 | -6.0926 | -7.6126 | 13.983 | 13.6446 | 13.1907 | 12.6964 | 12.228 | 11.5054 | 10.687 | 9.8546 | 8.9693 | 8.064 | 7.2094 | 5.2193 | 3.438 | 1.3236 | 12.2585 | 11.7471 | 10.9146 | 10.0317 | 9.1819 | 7.9948 | 6.684 | 5.4668 | 4.1875 | 2.8804 | 1.6376 | -1.5082 | -3.1666 | -4.7648
|  | HILTON | CT |  |  |  | 10.8262 | 10.5438 | 9.6408 | 8.6946 | 7.8698 | 6.9433 | 5.9949 | 4.839 | 3.573 | 2.2701 | 0.95404 | -3.2383 | -5.9368 | -7.5846 | 14.1428 | 13.9152 | 13.3891 | 12.8199 | 12.358 | 11.8397 | 11.3133 | 10.6024 | 9.7935 | 8.9703 | 8.1307 | 5.4002 | 3.438 | 1.3236 | 12.6806 | 12.3904 | 11.5467 | 10.6514 | 9.8952 | 9.055 | 8.1982 | 7.113 | 5.9134 | 4.699 | 3.4712 | -0.41053 | -2.8078 | -4.2701
|  | HILTON | LW |  |  |  | 10.3183 | 9.7963 | 8.8621 | 7.8859 | 6.9395 | 5.6613 | 4.2699 | 3.0395 | 1.705 | 0.32618 | -0.98626 | -4.3651 | -6.0926 | -7.6126 | 13.983 | 13.6446 | 13.1907 | 12.6964 | 12.228 | 11.5054 | 10.687 | 9.8546 | 8.9693 | 8.064 | 7.2094 | 5.2193 | 4.1715 | 2.8571 | 12.2585 | 11.7471 | 10.9146 | 10.0317 | 9.1819 | 7.9948 | 6.684 | 5.4668 | 4.1875 | 2.8804 | 1.6376 | -1.5082 | -3.1666 | -4.7648
|  | HILTON | ST |  |  |  | 11.1753 | 11.0989 | 10.9856 | 10.8377 | 10.6525 | 10.3526 | 10.0151 | 9.5641 | 9.0792 | 8.5287 | 7.9179 | 4.3379 | 2.3271 | -0.21009 | 14.3036 | 14.212 | 14.0842 | 13.926 | 13.75 | 13.493 | 13.2077 | 12.8061 | 12.3886 | 11.9186 | 11.3887 | 8.4285 | 6.4716 | 3.943 | 12.9839 | 12.8964 | 12.7662 | 12.5977 | 12.4125 | 12.1261 | 11.8058 | 11.3603 | 10.8818 | 10.3367 | 9.7269 | 6.2301 | 4.3447 | 2.0343
|  | HILTON | FS |  |  |  | 11.1647 | 11.094 | 10.9288 | 10.7442 | 10.5561 | 10.2851 | 9.9694 | 9.5619 | 9.132 | 8.6698 | 8.1696 | 4.9507 | 1.8142 | -0.4782 | 14.3049 | 14.2189 | 14.0868 | 13.9319 | 13.7655 | 13.5445 | 13.2937 | 12.965 | 12.6105 | 12.2199 | 11.7898 | 9.0187 | 5.7057 | 1.9177 | 12.9801 | 12.9022 | 12.7407 | 12.5543 | 12.3613 | 12.1014 | 11.8108 | 11.4294 | 11.0258 | 10.5904 | 10.1173 | 7.0696 | 4.1192 | 2.0607
| ARBROATH | HUME STREET | MINIMUM HEADROOM | NO 64067 41180 | NO | YES | 13.356 | 12.6158 | 12.016 | 11.4196 | 10.7951 | 10.0328 | 9.2576 | 8.6542 | 8.0154 | 7.3722 | 6.7538 | 4.9582 | 3.5335 | 2.6862 | 15.8853 | 15.4705 | 15.1475 | 14.816 | 14.4133 | 13.8839 | 13.4631 | 13.0549 | 12.6231 | 12.1297 | 11.6494 | 9.9117 | 8.5881 | 6.6781 | 14.8002 | 14.2005 | 13.6511 | 13.0928 | 12.4926 | 11.7417 | 10.9829 | 10.3709 | 9.7192 | 9.0607 | 8.4313 | 6.6965 | 5.4192 | 4.5707
|  | HUME STREET | CT |  |  |  | 13.6348 | 13.0446 | 12.4506 | 11.8511 | 11.1708 | 10.4213 | 9.7473 | 9.129 | 8.5158 | 7.925 | 7.2871 | 4.9582 | 3.5335 | 2.6862 | 15.9609 | 15.6016 | 15.257 | 14.8933 | 14.4133 | 13.8839 | 13.4807 | 13.0549 | 12.6261 | 12.2074 | 11.7438 | 9.9117 | 8.5881 | 7.0175 | 15.0314 | 14.5659 | 14.0133 | 13.4417 | 12.7714 | 12.038 | 11.4179 | 10.8183 | 10.2117 | 9.6245 | 8.9905 | 6.7306 | 5.4192 | 4.5988
|  | HUME STREET | LW |  |  |  | 13.356 | 12.6158 | 12.016 | 11.4196 | 10.7951 | 10.0328 | 9.2576 | 8.6542 | 8.0154 | 7.3722 | 6.7538 | 4.969 | 4.067 | 3.0515 | 15.8853 | 15.4705 | 15.1475 | 14.816 | 14.4359 | 13.9447 | 13.4631 | 13.0579 | 12.6231 | 12.1297 | 11.6494 | 10.4611 | 9.7309 | 8.6535 | 14.8002 | 14.2005 | 13.6511 | 13.0928 | 12.4926 | 11.7417 | 10.9829 | 10.3709 | 9.7192 | 9.0607 | 8.4313 | 6.6965 | 5.7592 | 4.5707
|  | HUME STREET | ST |  |  |  | 13.908 | 13.4877 | 13.2696 | 13.099 | 12.9334 | 12.5659 | 12.2971 | 11.9701 | 11.6666 | 11.3429 | 10.9643 | 8.0584 | 6.4121 | 5.1849 | 16.0962 | 15.8436 | 15.5946 | 15.3943 | 15.2119 | 14.806 | 14.5502 | 14.2166 | 13.9283 | 13.6191 | 13.2526 | 10.3951 | 9.0555 | 7.582 | 15.2812 | 14.9651 | 14.7123 | 14.5105 | 14.3222 | 13.9003 | 13.6182 | 13.2584 | 12.936 | 12.5901 | 11.9671 | 8.2224 | 6.565 | 5.3373
|  | HUME STREET | FS |  |  |  | 13.9065 | 13.5646 | 13.414 | 13.2685 | 13.098 | 12.9095 | 12.7222 | 12.4803 | 12.2311 | 11.9656 | 11.6753 | 9.7708 | 7.8698 | 6.0122 | 16.1003 | 15.8847 | 15.754 | 15.6194 | 15.4618 | 15.2861 | 15.1049 | 14.8744 | 14.6357 | 14.3741 | 14.0854 | 12.2453 | 9.7921 | 6.6781 | 15.2783 | 15.0314 | 14.8847 | 14.7368 | 14.5649 | 14.3741 | 14.1808 | 13.9343 | 13.6819 | 13.4115 | 13.1154 | 11.1221 | 8.4838 | 6.5599
| KEITH | HUNTLY | MINIMUM HEADROOM | NJ 52762 39217 | NO | YES | 7.8753 | 7.6451 | 7.2298 | 6.7884 | 6.2571 | 5.5673 | 4.7097 | 4.0862 | 3.6772 | 3.2493 | 2.8207 | 1.4826 | 0.41912 | -0.37469 | 9.337 | 9.2118 | 8.9602 | 8.6842 | 8.3035 | 7.7815 | 7.1337 | 6.6667 | 6.3859 | 6.0906 | 5.7976 | 4.8098 | 3.9521 | 3.1486 | 7.6931 | 7.4847 | 7.0879 | 6.664 | 6.1305 | 5.4434 | 4.6169 | 4.029 | 3.6393 | 3.2336 | 2.827 | 1.5606 | 0.50919 | -0.48161
|  | HUNTLY | CT |  |  |  | 8.0967 | 7.9452 | 7.5605 | 7.1536 | 6.6029 | 5.9559 | 5.2692 | 4.6313 | 4.1557 | 3.6926 | 3.2265 | 1.5934 | 0.41912 | -0.28402 | 9.4002 | 9.3088 | 9.094 | 8.8467 | 8.4246 | 7.9119 | 7.414 | 6.9401 | 6.6078 | 6.2842 | 5.9591 | 4.8098 | 3.9521 | 3.1486 | 7.8866 | 7.7474 | 7.392 | 7.0104 | 6.4478 | 5.7914 | 5.142 | 4.538 | 4.0835 | 3.6427 | 3.1979 | 1.6306 | 0.50919 | -0.20118
|  | HUNTLY | LW |  |  |  | 7.8753 | 7.6451 | 7.2298 | 6.7884 | 6.2571 | 5.5673 | 4.7097 | 4.0862 | 3.6772 | 3.2493 | 2.8207 | 1.4826 | 0.49705 | -0.37469 | 9.337 | 9.2118 | 8.9602 | 8.6842 | 8.3035 | 7.7815 | 7.1337 | 6.6667 | 6.3859 | 6.0906 | 5.7976 | 4.9245 | 4.114 | 3.1759 | 7.6931 | 7.4847 | 7.0879 | 6.664 | 6.1305 | 5.4434 | 4.6169 | 4.029 | 3.6393 | 3.2336 | 2.827 | 1.5606 | 0.52669 | -0.48161
|  | HUNTLY | ST |  |  |  | 8.212 | 8.1417 | 7.8639 | 7.6328 | 7.4297 | 6.9504 | 6.4545 | 5.9557 | 5.6926 | 5.4197 | 5.1196 | 3.473 | 2.2527 | 1.0928 | 9.4434 | 9.4174 | 9.1381 | 8.9193 | 8.7428 | 8.2509 | 7.8078 | 7.3497 | 7.1295 | 6.9014 | 6.6396 | 5.2928 | 4.2523 | 3.1923 | 7.9919 | 7.9293 | 7.6179 | 7.3684 | 7.1581 | 6.6279 | 6.1391 | 5.6386 | 5.3799 | 5.1135 | 4.814 | 3.1699 | 1.9753 | 0.82246
|  | HUNTLY | FS |  |  |  | 8.2864 | 8.2347 | 8.1115 | 7.9841 | 7.843 | 7.651 | 7.2927 | 6.9256 | 6.7041 | 6.4626 | 6.224 | 4.7923 | 3.4649 | 2.5482 | 9.4869 | 9.4663 | 9.3725 | 9.2713 | 9.1574 | 9.0005 | 8.6924 | 8.3897 | 8.217 | 8.0271 | 7.8358 | 6.7827 | 5.6136 | 4.4977 | 8.0606 | 8.0149 | 7.8926 | 7.7663 | 7.6256 | 7.4374 | 7.0914 | 6.7403 | 6.5281 | 6.2973 | 6.0684 | 4.7388 | 3.506 | 2.6709
| BRIDGE OF DUN | INCHBARE | MINIMUM HEADROOM | NO 60684 65379 | YES | YES | 1.6591 | 1.6272 | 1.5759 | 1.4896 | 1.3484 | 1.1655 | 1.0573 | 0.92058 | 0.78795 | 0.66273 | 0.50842 | -0.25941 | -0.83542 | -1.24 | 1.794 | 1.7712 | 1.6808 | 1.5841 | 1.5138 | 1.3089 | 1.2327 | 1.0652 | 0.98135 | 0.88476 | 0.73969 | -0.036762 | -0.65508 | -1.1323 | 1.6464 | 1.6019 | 1.5397 | 1.4343 | 1.2915 | 1.0976 | 0.99809 | 0.83185 | 0.71044 | 0.58309 | 0.41862 | -0.43881 | -1.0742 | -1.5494
|  | INCHBARE | CT |  |  |  | 1.6653 | 1.6344 | 1.5838 | 1.5162 | 1.3484 | 1.1655 | 1.0573 | 0.92058 | 0.78795 | 0.66273 | 0.50842 | -0.11879 | -0.49474 | -0.7704 | 1.7986 | 1.7766 | 1.7329 | 1.6759 | 1.5138 | 1.3393 | 1.2674 | 1.1666 | 1.0426 | 0.92781 | 0.7895 | 0.15971 | -0.24277 | -0.57536 | 1.6464 | 1.6019 | 1.5404 | 1.4712 | 1.2915 | 1.0976 | 0.99809 | 0.8586 | 0.71953 | 0.58978 | 0.4321 | -0.24503 | -0.66138 | -0.99318
|  | INCHBARE | LW |  |  |  | 1.6591 | 1.6272 | 1.5858 | 1.5467 | 1.5027 | 1.436 | 1.3435 | 1.2248 | 1.0946 | 0.95774 | 0.81778 | 0.35868 | -0.2156 | -0.88089 | 1.794 | 1.7712 | 1.7491 | 1.7267 | 1.702 | 1.6661 | 1.6276 | 1.563 | 1.464 | 1.3573 | 1.2411 | 0.81039 | 0.14326 | -0.68281 | 1.6542 | 1.6167 | 1.5858 | 1.5497 | 1.5102 | 1.4476 | 1.3725 | 1.2615 | 1.1383 | 1.0104 | 0.87725 | 0.40664 | -0.27702 | -1.1029
|  | INCHBARE | ST |  |  |  | 1.6979 | 1.6861 | 1.5759 | 1.4896 | 1.4257 | 1.2497 | 1.1704 | 0.9927 | 0.8719 | 0.74516 | 0.58303 | -0.25941 | -0.83542 | -1.24 | 1.8207 | 1.8119 | 1.6808 | 1.5841 | 1.5146 | 1.3089 | 1.2327 | 1.0652 | 0.98135 | 0.88476 | 0.73969 | -0.036762 | -0.65508 | -1.1323 | 1.6929 | 1.679 | 1.5397 | 1.4343 | 1.3507 | 1.1278 | 1.0295 | 0.83185 | 0.71044 | 0.58309 | 0.41862 | -0.43881 | -1.0742 | -1.5494
|  | INCHBARE | FS |  |  |  | 1.7058 | 1.6983 | 1.667 | 1.6365 | 1.6001 | 1.5618 | 1.522 | 1.4608 | 1.4018 | 1.3291 | 1.2455 | 0.8104 | 0.35387 | 0.01323 | 1.8265 | 1.8202 | 1.7871 | 1.7541 | 1.7153 | 1.6749 | 1.6356 | 1.5698 | 1.5161 | 1.4612 | 1.4026 | 1.1331 | 0.75685 | 0.45418 | 1.7001 | 1.6913 | 1.6552 | 1.6168 | 1.5714 | 1.5227 | 1.4738 | 1.3947 | 1.3265 | 1.2528 | 1.1734 | 0.79473 | 0.3632 | 0.030031
| DUNOON | INNELLAN | MINIMUM HEADROOM | NS 15129 70875 | YES | YES | 1.6304 | 1.6088 | 1.5486 | 1.4537 | 1.3427 | 1.1649 | 1.0582 | 0.92092 | 0.77976 | 0.644 | 0.50491 | -0.11669 | -0.61661 | -0.97804 | 1.8796 | 1.8488 | 1.795 | 1.7093 | 1.5683 | 1.3967 | 1.3175 | 1.2005 | 1.0731 | 0.95215 | 0.82862 | 0.32286 | -0.07817 | -0.61762 | 1.6345 | 1.5866 | 1.511 | 1.4281 | 1.245 | 1.0479 | 0.9419 | 0.79053 | 0.62343 | 0.46237 | 0.30066 | -0.33855 | -0.83607 | -1.2312
|  | INNELLAN | CT |  |  |  | 1.6556 | 1.6409 | 1.5829 | 1.5155 | 1.3427 | 1.1649 | 1.0582 | 0.92092 | 0.77976 | 0.644 | 0.50491 | -0.11669 | -0.61661 | -0.97804 | 1.8997 | 1.8779 | 1.8116 | 1.7314 | 1.5683 | 1.3967 | 1.3175 | 1.2005 | 1.0731 | 0.95215 | 0.82862 | 0.32286 | -0.07817 | -0.4615 | 1.6722 | 1.6412 | 1.5452 | 1.4338 | 1.245 | 1.0479 | 0.9419 | 0.79053 | 0.62343 | 0.46237 | 0.30066 | -0.33855 | -0.83607 | -1.2312
|  | INNELLAN | LW |  |  |  | 1.6304 | 1.6088 | 1.5486 | 1.4537 | 1.3621 | 1.2589 | 1.1506 | 1.0499 | 0.94322 | 0.83819 | 0.73204 | 0.32179 | -0.23674 | -0.8799 | 1.8796 | 1.8488 | 1.803 | 1.7524 | 1.7052 | 1.6399 | 1.5669 | 1.4762 | 1.379 | 1.2839 | 1.189 | 0.90308 | 0.34584 | -0.42229 | 1.6345 | 1.5866 | 1.511 | 1.4281 | 1.3507 | 1.2463 | 1.1304 | 1.0014 | 0.8631 | 0.72602 | 0.59372 | 0.20707 | -0.42233 | -1.2126
|  | INNELLAN | ST |  |  |  | 1.6828 | 1.6804 | 1.5909 | 1.5274 | 1.4813 | 1.3429 | 1.2964 | 1.1853 | 1.1338 | 1.0852 | 1.0179 | 0.51378 | -0.021417 | -0.61791 | 1.9197 | 1.912 | 1.795 | 1.7093 | 1.646 | 1.4643 | 1.3968 | 1.2472 | 1.1713 | 1.0975 | 0.998 | 0.46262 | -0.068582 | -0.61762 | 1.7008 | 1.6908 | 1.57 | 1.4791 | 1.4094 | 1.2209 | 1.1446 | 0.98406 | 0.89429 | 0.80468 | 0.68817 | 0.053513 | -0.52779 | -1.1215
|  | INNELLAN | FS |  |  |  | 1.6866 | 1.6846 | 1.6615 | 1.6371 | 1.6103 | 1.5835 | 1.5545 | 1.5061 | 1.4639 | 1.4235 | 1.3724 | 1.0946 | 0.74953 | 0.48621 | 1.9229 | 1.916 | 1.8842 | 1.8499 | 1.8115 | 1.7717 | 1.7306 | 1.6637 | 1.606 | 1.5473 | 1.4834 | 1.2255 | 0.95614 | 0.7356 | 1.7057 | 1.6972 | 1.6612 | 1.6213 | 1.5777 | 1.5323 | 1.4826 | 1.4063 | 1.3358 | 1.2652 | 1.1862 | 0.83368 | 0.5024 | 0.28707
| KEITH | INSCH | MINIMUM HEADROOM | NJ 63100 28651 | NO | YES | 6.0809 | 5.688 | 5.2154 | 4.7156 | 4.162 | 3.2596 | 2.4042 | 2.0753 | 1.728 | 1.3648 | 1.0245 | 0.14012 | -0.53964 | -1.185 | 9.2488 | 9.0587 | 8.7969 | 8.5103 | 8.1544 | 7.4824 | 6.8762 | 6.6214 | 6.3492 | 6.0642 | 5.7991 | 5.1569 | 4.3861 | 3.6272 | 7.1938 | 6.8401 | 6.4003 | 5.9306 | 5.3941 | 4.5199 | 3.7024 | 3.3597 | 2.9959 | 2.6179 | 2.2642 | 1.3869 | 0.67456 | -0.065212
|  | INSCH | CT |  |  |  | 6.4195 | 6.1381 | 5.5639 | 4.9619 | 4.2962 | 3.3612 | 2.568 | 2.2664 | 1.9211 | 1.5806 | 1.2646 | 0.50781 | -0.40559 | -0.86726 | 9.3649 | 9.2127 | 8.9159 | 8.5898 | 8.1679 | 7.5013 | 7.0031 | 6.7603 | 6.472 | 6.1898 | 5.9287 | 5.195 | 4.5333 | 3.9193 | 7.4806 | 7.2239 | 6.7011 | 6.1452 | 5.5052 | 4.6144 | 3.8912 | 3.5804 | 3.2147 | 2.8543 | 2.5226 | 1.7092 | 0.85953 | 0.38595
|  | INSCH | LW |  |  |  | 6.0809 | 5.688 | 5.2154 | 4.7156 | 4.162 | 3.2596 | 2.4042 | 2.0753 | 1.728 | 1.3648 | 1.0245 | 0.14012 | -0.53964 | -1.185 | 9.2488 | 9.0587 | 8.7969 | 8.5103 | 8.1544 | 7.4824 | 6.8762 | 6.6214 | 6.3492 | 6.0642 | 5.7991 | 5.1569 | 4.5884 | 3.9171 | 7.1938 | 6.8401 | 6.4003 | 5.9306 | 5.3941 | 4.5199 | 3.7024 | 3.3597 | 2.9959 | 2.6179 | 2.2642 | 1.3869 | 0.67456 | -0.065212
|  | INSCH | ST |  |  |  | 6.6222 | 6.4612 | 6.1199 | 5.8047 | 5.5153 | 4.8144 | 4.2787 | 3.8965 | 3.5477 | 3.1841 | 2.7961 | 0.94983 | -0.13727 | -0.85623 | 9.4517 | 9.3745 | 9.112 | 8.8885 | 8.6965 | 8.0864 | 7.6732 | 7.3893 | 7.1499 | 6.9009 | 6.6226 | 5.2489 | 4.3861 | 3.6272 | 7.6559 | 7.5144 | 7.1659 | 6.853 | 6.5726 | 5.8656 | 5.3543 | 4.9721 | 4.6323 | 4.2773 | 3.8915 | 2.0406 | 0.98306 | 0.27063
|  | INSCH | FS |  |  |  | 6.7531 | 6.6388 | 6.442 | 6.2375 | 6.0173 | 5.6481 | 5.2473 | 4.9414 | 4.6328 | 4.3153 | 3.9925 | 1.9828 | 0.65889 | 0.11018 | 9.5 | 9.441 | 9.3268 | 9.2041 | 9.0696 | 8.7972 | 8.4973 | 8.3046 | 8.1081 | 7.9045 | 7.6954 | 6.4605 | 5.3847 | 4.6665 | 7.7671 | 7.666 | 7.4831 | 7.2912 | 7.084 | 6.7381 | 6.3625 | 6.0744 | 5.784 | 5.4838 | 5.1766 | 3.2994 | 2.0188 | 1.531
| BURGHMUIR | INVERALMOND | MINIMUM HEADROOM | NO 08721 25807 | NO | YES | 25.5389 | 25.3174 | 25.1308 | 24.5647 | 24.3554 | 24.093 | 23.6123 | 23.1373 | 22.6462 | 22.1264 | 21.6186 | 19.4951 | 18.9966 | 18.8872 | 24.5903 | 24.4211 | 24.2868 | 23.7584 | 23.6206 | 23.4556 | 23.308 | 23.1242 | 22.9244 | 22.6593 | 22.3923 | 21.3656 | 21.1376 | 21.0691 | 23.1142 | 22.9164 | 22.7533 | 22.192 | 22.0262 | 21.829 | 21.5929 | 21.1849 | 20.7618 | 20.3137 | 19.8763 | 18.0684 | 17.6433 | 17.5502
|  | INVERALMOND | CT |  |  |  | 25.6559 | 25.3968 | 25.1308 | 24.5811 | 24.3554 | 24.1274 | 23.9196 | 23.5099 | 23.0286 | 22.531 | 22.0209 | 20.6199 | 20.1299 | 19.9167 | 24.705 | 24.4991 | 24.2909 | 23.7885 | 23.6206 | 23.4556 | 23.3145 | 23.1657 | 23.0183 | 22.8693 | 22.6197 | 21.8427 | 21.5525 | 21.3042 | 23.235 | 23.0009 | 22.7621 | 22.2251 | 22.0265 | 21.829 | 21.6542 | 21.4699 | 21.0814 | 20.6583 | 20.2222 | 19.0013 | 18.5762 | 18.391
|  | INVERALMOND | LW |  |  |  | 25.5389 | 25.3174 | 25.1312 | 24.5647 | 24.3728 | 24.093 | 23.6123 | 23.1373 | 22.6462 | 22.1264 | 21.6186 | 19.4951 | 18.9966 | 18.8872 | 24.5903 | 24.4211 | 24.2868 | 23.7584 | 23.6233 | 23.4759 | 23.308 | 23.1242 | 22.9244 | 22.6593 | 22.3923 | 21.3656 | 21.1376 | 21.0691 | 23.1142 | 22.9164 | 22.7533 | 22.192 | 22.0262 | 21.8428 | 21.5929 | 21.1849 | 20.7618 | 20.3137 | 19.8763 | 18.0684 | 17.6433 | 17.5502
|  | INVERALMOND | ST |  |  |  | 25.6927 | 25.5119 | 25.3346 | 24.8661 | 24.6856 | 24.506 | 24.3308 | 24.1311 | 23.9011 | 23.6407 | 23.3512 | 22.1036 | 21.641 | 21.4675 | 24.7333 | 24.5879 | 24.4474 | 24.0069 | 23.8728 | 23.7437 | 23.6261 | 23.4903 | 23.3319 | 23.1513 | 22.9451 | 21.9945 | 21.6661 | 21.5906 | 23.2664 | 23.0997 | 22.9379 | 22.4723 | 22.3132 | 22.1578 | 22.0116 | 21.8446 | 21.6516 | 21.4327 | 21.1787 | 19.898 | 19.5206 | 19.4569
|  | INVERALMOND | FS |  |  |  | 26.0231 | 25.8656 | 25.7006 | 25.3401 | 25.1698 | 24.9903 | 24.8002 | 24.6048 | 24.3921 | 24.1808 | 23.9438 | 22.6843 | 21.7884 | 21.1588 | 25.0694 | 24.945 | 24.815 | 24.483 | 24.3536 | 24.2174 | 24.0733 | 23.9266 | 23.7651 | 23.6087 | 23.4286 | 22.4777 | 21.7901 | 21.2345 | 23.6091 | 23.4651 | 23.3147 | 22.96 | 22.8078 | 22.6478 | 22.4786 | 22.306 | 22.1175 | 21.9331 | 21.7238 | 20.578 | 19.674 | 19.1643
| CLACHAN | INVERARAY | MINIMUM HEADROOM | NN 09172 09746 | YES | YES | 2.1959 | 2.1901 | 2.1646 | 2.143 | 2.1241 | 2.0744 | 2.0583 | 2.0194 | 2.0003 | 1.984 | 1.9624 | 1.8546 | 1.7245 | 1.5953 | 2.1474 | 2.1441 | 2.1084 | 2.0816 | 2.0614 | 2.0004 | 1.982 | 1.9353 | 1.9153 | 1.8983 | 1.8737 | 1.7537 | 1.5977 | 1.4406 | 1.9317 | 1.9278 | 1.8928 | 1.8659 | 1.8455 | 1.7846 | 1.7658 | 1.7187 | 1.6983 | 1.6806 | 1.6553 | 1.5246 | 1.3628 | 1.2019
|  | INVERARAY | CT |  |  |  | 2.1985 | 2.1947 | 2.1823 | 2.1664 | 2.1258 | 2.0815 | 2.0658 | 2.0442 | 2.0253 | 2.0057 | 1.9862 | 1.8906 | 1.8023 | 1.7157 | 2.1489 | 2.1463 | 2.1361 | 2.1219 | 2.0754 | 2.0251 | 2.0094 | 1.9856 | 1.9628 | 1.9413 | 1.9188 | 1.8069 | 1.7032 | 1.5947 | 1.9331 | 1.9299 | 1.9189 | 1.9037 | 1.8564 | 1.8055 | 1.7865 | 1.7601 | 1.7365 | 1.7123 | 1.6879 | 1.5701 | 1.4605 | 1.3517
|  | INVERARAY | LW |  |  |  | 2.1959 | 2.1901 | 2.183 | 2.1757 | 2.1715 | 2.1678 | 2.1575 | 2.1477 | 2.1375 | 2.1265 | 2.1135 | 2.0662 | 1.9138 | 1.7022 | 2.1474 | 2.1441 | 2.1403 | 2.1362 | 2.1335 | 2.1306 | 2.1245 | 2.1137 | 2.1022 | 2.0913 | 2.0791 | 2.0288 | 1.8443 | 1.5809 | 1.9317 | 1.9278 | 1.9231 | 1.9182 | 1.9154 | 1.9115 | 1.8998 | 1.888 | 1.8754 | 1.8625 | 1.8472 | 1.7911 | 1.6013 | 1.3369
|  | INVERARAY | ST |  |  |  | 2.2023 | 2.2004 | 2.1646 | 2.143 | 2.1241 | 2.0744 | 2.0583 | 2.0194 | 2.0003 | 1.984 | 1.9624 | 1.8546 | 1.7245 | 1.5953 | 2.1507 | 2.1496 | 2.1084 | 2.0816 | 2.0614 | 2.0004 | 1.982 | 1.9353 | 1.9153 | 1.8983 | 1.8737 | 1.7537 | 1.5977 | 1.4406 | 1.9358 | 1.9345 | 1.8928 | 1.8659 | 1.8455 | 1.7846 | 1.7658 | 1.7187 | 1.6983 | 1.6806 | 1.6553 | 1.5246 | 1.3628 | 1.2019
|  | INVERARAY | FS |  |  |  | 2.204 | 2.2022 | 2.194 | 2.1857 | 2.175 | 2.1655 | 2.1539 | 2.1405 | 2.1275 | 2.1159 | 2.1011 | 2.0619 | 2.0335 | 2.0034 | 2.1515 | 2.1505 | 2.1415 | 2.1324 | 2.1211 | 2.1106 | 2.0997 | 2.0825 | 2.069 | 2.0562 | 2.0416 | 2.0094 | 1.9844 | 1.9553 | 1.9368 | 1.9356 | 1.9265 | 1.9172 | 1.906 | 1.8952 | 1.8839 | 1.8673 | 1.8535 | 1.8403 | 1.8251 | 1.7806 | 1.7485 | 1.7147
| LUNANHEAD | INVERARITY | MINIMUM HEADROOM | NO 44549 44200 | YES | YES | 0.1551 | 0.12247 | 0.036886 | -0.060995 | -0.20886 | -0.39692 | -0.49857 | -0.56462 | -0.66345 | -0.77131 | -0.87867 | -1.3563 | -1.7646 | -2.1051 | 0.36762 | 0.35014 | 0.21079 | 0.096723 | 0.015317 | -0.23731 | -0.32 | -0.44093 | -0.49982 | -0.55471 | -0.63319 | -1.0168 | -1.4333 | -1.8187 | 0.082476 | 0.062065 | -0.072638 | -0.18732 | -0.28397 | -0.52598 | -0.61161 | -0.7363 | -0.80045 | -0.85991 | -0.94536 | -1.3613 | -1.769 | -2.1847
|  | INVERARITY | CT |  |  |  | 0.17533 | 0.1468 | 0.072843 | -0.016444 | -0.19784 | -0.39692 | -0.48433 | -0.56462 | -0.6483 | -0.72603 | -0.8198 | -1.1633 | -1.3852 | -1.5994 | 0.37488 | 0.35482 | 0.30162 | 0.23016 | 0.032625 | -0.17993 | -0.25526 | -0.3237 | -0.39695 | -0.46363 | -0.53303 | -0.82993 | -1.0874 | -1.3565 | 0.090783 | 0.06429 | 0.0027016 | -0.075555 | -0.27871 | -0.49815 | -0.58168 | -0.65214 | -0.72398 | -0.78856 | -0.85971 | -1.1639 | -1.4171 | -1.6713
|  | INVERARITY | LW |  |  |  | 0.1551 | 0.12247 | 0.039188 | -0.055976 | -0.20886 | -0.37642 | -0.49857 | -0.56018 | -0.66345 | -0.77131 | -0.87867 | -1.2245 | -1.6153 | -2.1051 | 0.36762 | 0.35014 | 0.27001 | 0.17925 | 0.016492 | -0.16199 | -0.28063 | -0.33774 | -0.3996 | -0.45806 | -0.5182 | -0.75605 | -1.2127 | -1.8187 | 0.082476 | 0.062065 | -0.021162 | -0.11583 | -0.28397 | -0.46777 | -0.59321 | -0.65468 | -0.72296 | -0.78844 | -0.85605 | -1.1192 | -1.5763 | -2.1847
|  | INVERARITY | ST |  |  |  | 0.19271 | 0.18096 | 0.036886 | -0.060995 | -0.13696 | -0.3495 | -0.4284 | -0.53886 | -0.602 | -0.67366 | -0.78613 | -1.3563 | -1.7646 | -2.0686 | 0.383 | 0.37658 | 0.21079 | 0.096723 | 0.015317 | -0.23731 | -0.32 | -0.44093 | -0.49982 | -0.55471 | -0.63319 | -1.0168 | -1.4333 | -1.7924 | 0.10213 | 0.094936 | -0.072638 | -0.18732 | -0.27112 | -0.52598 | -0.61161 | -0.7363 | -0.80045 | -0.85991 | -0.94536 | -1.3613 | -1.769 | -2.1335
|  | INVERARITY | FS |  |  |  | 0.20362 | 0.19096 | 0.15586 | 0.11731 | 0.074317 | 0.026071 | -0.013639 | -0.066739 | -0.112 | -0.15522 | -0.20419 | -0.48438 | -0.7868 | -1.0059 | 0.38756 | 0.38121 | 0.34377 | 0.3045 | 0.25955 | 0.21213 | 0.17075 | 0.1203 | 0.080204 | 0.039872 | -0.0035408 | -0.16111 | -0.31061 | -0.43374 | 0.10825 | 0.10117 | 0.063328 | 0.023761 | -0.021921 | -0.070774 | -0.1125 | -0.16484 | -0.20677 | -0.24876 | -0.29495 | -0.47205 | -0.64214 | -0.77721
| INVERNESS | INVERARNIE | MINIMUM HEADROOM | NH 68830 34971 | YES | YES | 1.7154 | 1.6879 | 1.6589 | 1.6189 | 1.5485 | 1.4699 | 1.4161 | 1.379 | 1.3404 | 1.3083 | 1.2636 | 1.053 | 0.86423 | 0.7171 | 1.844 | 1.8279 | 1.8045 | 1.7689 | 1.716 | 1.6497 | 1.6174 | 1.5765 | 1.5412 | 1.5055 | 1.4589 | 1.2298 | 1.0388 | 0.87583 | 1.6515 | 1.6216 | 1.5856 | 1.5448 | 1.459 | 1.3681 | 1.3117 | 1.271 | 1.2199 | 1.176 | 1.1305 | 0.95253 | 0.73923 | 0.56453
|  | INVERARNIE | CT |  |  |  | 1.7306 | 1.7078 | 1.6625 | 1.6189 | 1.5485 | 1.4699 | 1.4161 | 1.379 | 1.3404 | 1.3083 | 1.2636 | 1.1065 | 0.98814 | 0.88423 | 1.8485 | 1.8344 | 1.8062 | 1.7781 | 1.716 | 1.6497 | 1.6174 | 1.5786 | 1.5413 | 1.5077 | 1.4659 | 1.3061 | 1.1919 | 1.0792 | 1.6777 | 1.6551 | 1.6027 | 1.5448 | 1.459 | 1.3681 | 1.3117 | 1.271 | 1.2199 | 1.176 | 1.1305 | 0.97508 | 0.81795 | 0.68852
|  | INVERARNIE | LW |  |  |  | 1.7154 | 1.6879 | 1.6589 | 1.6264 | 1.5914 | 1.5479 | 1.5002 | 1.4648 | 1.4248 | 1.3815 | 1.3385 | 1.2309 | 1.0647 | 0.84425 | 1.844 | 1.8279 | 1.8126 | 1.7952 | 1.7781 | 1.7534 | 1.725 | 1.6914 | 1.6555 | 1.6198 | 1.5847 | 1.4913 | 1.3014 | 1.032 | 1.6515 | 1.6216 | 1.5856 | 1.546 | 1.5099 | 1.4652 | 1.417 | 1.3809 | 1.3441 | 1.3082 | 1.2707 | 1.1776 | 0.96561 | 0.68848
|  | INVERARNIE | ST |  |  |  | 1.7422 | 1.7323 | 1.6879 | 1.6501 | 1.6189 | 1.5508 | 1.5148 | 1.4537 | 1.4125 | 1.3695 | 1.3161 | 1.053 | 0.86423 | 0.7171 | 1.8562 | 1.8508 | 1.8045 | 1.7689 | 1.7412 | 1.669 | 1.6381 | 1.5765 | 1.5412 | 1.5055 | 1.4589 | 1.2298 | 1.0388 | 0.87583 | 1.6864 | 1.6761 | 1.6224 | 1.5767 | 1.541 | 1.4595 | 1.4209 | 1.352 | 1.3095 | 1.2671 | 1.213 | 0.95253 | 0.73923 | 0.56453
|  | INVERARNIE | FS |  |  |  | 1.7486 | 1.7418 | 1.723 | 1.7045 | 1.6845 | 1.6609 | 1.6393 | 1.6061 | 1.574 | 1.544 | 1.5116 | 1.3375 | 1.2112 | 1.13 | 1.859 | 1.8551 | 1.8407 | 1.826 | 1.8094 | 1.791 | 1.7737 | 1.7455 | 1.7208 | 1.6962 | 1.67 | 1.5536 | 1.4623 | 1.3995 | 1.6943 | 1.688 | 1.6656 | 1.6443 | 1.6217 | 1.5946 | 1.5712 | 1.5329 | 1.4957 | 1.4635 | 1.4285 | 1.2479 | 1.1303 | 1.0729
| FIDDES | INVERBERVIE | MINIMUM HEADROOM | NO 82850 72935 | NO | YES | 3.564 | 3.4401 | 3.2464 | 3.0496 | 2.8492 | 2.5059 | 2.1676 | 1.9887 | 1.8263 | 1.6541 | 1.4893 | 0.97722 | 0.46339 | 0.18103 | 4.5805 | 4.5224 | 4.4416 | 4.3572 | 4.2706 | 4.0507 | 3.859 | 3.7379 | 3.6196 | 3.5022 | 3.3876 | 2.9942 | 2.6342 | 2.2667 | 3.9845 | 3.877 | 3.7158 | 3.5454 | 3.3732 | 3.0674 | 2.7622 | 2.5948 | 2.4407 | 2.2779 | 2.1227 | 1.6193 | 1.1643 | 0.90198
|  | INVERBERVIE | CT |  |  |  | 3.7071 | 3.6376 | 3.4356 | 3.225 | 3.001 | 2.6669 | 2.3573 | 2.1557 | 1.9651 | 1.7729 | 1.5848 | 0.97722 | 0.46339 | 0.18103 | 4.6278 | 4.5885 | 4.4927 | 4.3898 | 4.2706 | 4.0507 | 3.8624 | 3.7379 | 3.6196 | 3.5022 | 3.3876 | 2.9942 | 2.6342 | 2.2667 | 4.0977 | 4.035 | 3.8621 | 3.6794 | 3.4812 | 3.1769 | 2.9003 | 2.7148 | 2.5353 | 2.3549 | 2.1793 | 1.6193 | 1.1643 | 0.90198
|  | INVERBERVIE | LW |  |  |  | 3.564 | 3.4401 | 3.2464 | 3.0496 | 2.8492 | 2.5059 | 2.1676 | 1.9887 | 1.8263 | 1.6541 | 1.4893 | 1.0021 | 0.64929 | 0.38631 | 4.5805 | 4.5224 | 4.4416 | 4.3572 | 4.2731 | 4.0657 | 3.859 | 3.749 | 3.6528 | 3.5496 | 3.4526 | 3.1886 | 2.9582 | 2.7116 | 3.9845 | 3.877 | 3.7158 | 3.5454 | 3.3732 | 3.0674 | 2.7622 | 2.5948 | 2.4407 | 2.2779 | 2.1227 | 1.6821 | 1.3443 | 1.0581
|  | INVERBERVIE | ST |  |  |  | 3.7915 | 3.7574 | 3.6873 | 3.6221 | 3.5596 | 3.3599 | 3.1863 | 3.07 | 2.9795 | 2.8855 | 2.7856 | 2.224 | 1.7622 | 1.2594 | 4.6611 | 4.6416 | 4.5873 | 4.539 | 4.4948 | 4.3185 | 4.1772 | 4.0766 | 4.0057 | 3.9328 | 3.852 | 3.4163 | 3.0327 | 2.5671 | 4.1646 | 4.1346 | 4.0648 | 4.0008 | 3.9407 | 3.7519 | 3.5929 | 3.4759 | 3.3852 | 3.2906 | 3.1873 | 2.6227 | 2.2036 | 1.7668
|  | INVERBERVIE | FS |  |  |  | 3.8086 | 3.7819 | 3.7279 | 3.6746 | 3.6186 | 3.4967 | 3.355 | 3.2482 | 3.1566 | 3.0588 | 2.9619 | 2.3507 | 1.8294 | 1.4366 | 4.6673 | 4.6506 | 4.6191 | 4.586 | 4.5502 | 4.455 | 4.3439 | 4.2663 | 4.1995 | 4.1287 | 4.0571 | 3.6268 | 3.1248 | 2.5406 | 4.1787 | 4.1552 | 4.1072 | 4.0587 | 4.0075 | 3.899 | 3.7721 | 3.6745 | 3.5891 | 3.4981 | 3.4067 | 2.8477 | 2.3707 | 2.0404
| GRUDIE BRIDGE | INVERBROOM | MINIMUM HEADROOM | NH 17885 84667 | YES | YES | 0.081217 | 0.077337 | 0.17418 | 0.16659 | 0.15994 | 0.14849 | 0.14244 | 0.14113 | 0.13407 | 0.12786 | 0.12602 | 0.11414 | 0.11172 | 0.10643 | 0.095147 | 0.092834 | 0.21146 | 0.20778 | 0.20364 | 0.19853 | 0.19509 | 0.19272 | 0.18855 | 0.183 | 0.17989 | 0.17274 | 0.16829 | 0.16299 | 0.075818 | 0.07218 | 0.18771 | 0.18082 | 0.17463 | 0.16438 | 0.15862 | 0.15639 | 0.14992 | 0.14222 | 0.13951 | 0.12836 | 0.12623 | 0.12148
|  | INVERBROOM | CT |  |  |  | 0.085565 | 0.083695 | 0.17759 | 0.16904 | 0.15994 | 0.14849 | 0.14292 | 0.14113 | 0.13407 | 0.13091 | 0.12647 | 0.11873 | 0.11172 | 0.10643 | 0.096773 | 0.095344 | 0.21238 | 0.20785 | 0.20364 | 0.19853 | 0.19556 | 0.19338 | 0.18855 | 0.18497 | 0.18092 | 0.17312 | 0.16829 | 0.16299 | 0.079666 | 0.077848 | 0.19067 | 0.18282 | 0.17463 | 0.16438 | 0.15927 | 0.15732 | 0.14992 | 0.14568 | 0.14065 | 0.13252 | 0.12623 | 0.12148
|  | INVERBROOM | LW |  |  |  | 0.081217 | 0.077337 | 0.17418 | 0.16659 | 0.16283 | 0.1537 | 0.14244 | 0.14132 | 0.13648 | 0.12786 | 0.12602 | 0.11414 | 0.11276 | 0.11092 | 0.095147 | 0.092834 | 0.21146 | 0.20778 | 0.2057 | 0.20091 | 0.19509 | 0.19272 | 0.18881 | 0.183 | 0.17989 | 0.17274 | 0.17198 | 0.17128 | 0.075818 | 0.07218 | 0.18771 | 0.18082 | 0.17734 | 0.16894 | 0.15862 | 0.15639 | 0.15085 | 0.14222 | 0.13951 | 0.12836 | 0.12712 | 0.12554
|  | INVERBROOM | ST |  |  |  | 0.091173 | 0.088749 | 0.19165 | 0.18545 | 0.18396 | 0.18403 | 0.18042 | 0.17637 | 0.17158 | 0.16848 | 0.16174 | 0.14005 | 0.13503 | 0.12763 | 0.099006 | 0.097797 | 0.219 | 0.21618 | 0.21505 | 0.21435 | 0.21216 | 0.20963 | 0.20659 | 0.20399 | 0.19989 | 0.18218 | 0.17734 | 0.17168 | 0.08197 | 0.081764 | 0.20339 | 0.19783 | 0.19638 | 0.19595 | 0.19244 | 0.18842 | 0.18354 | 0.18 | 0.1734 | 0.15154 | 0.14679 | 0.14032
|  | INVERBROOM | FS |  |  |  | 0.091601 | 0.0908 | 0.19201 | 0.18933 | 0.18629 | 0.18525 | 0.17998 | 0.17856 | 0.17495 | 0.17264 | 0.16825 | 0.14264 | 0.12333 | 0.124 | 0.099185 | 0.098599 | 0.21924 | 0.21783 | 0.21626 | 0.21533 | 0.21275 | 0.21148 | 0.20929 | 0.20746 | 0.20474 | 0.18769 | 0.17251 | 0.16859 | 0.08203 | 0.08186 | 0.20362 | 0.2013 | 0.19853 | 0.19741 | 0.19268 | 0.19098 | 0.18748 | 0.18489 | 0.18054 | 0.15509 | 0.13653 | 0.13711
| FORT AUGUSTUS | INVERGARRY | MINIMUM HEADROOM | NH 29862 01000 | YES | YES | 0.61792 | 0.60477 | 0.58288 | 0.54958 | 0.50698 | 0.45991 | 0.4292 | 0.40649 | 0.3828 | 0.36057 | 0.337 | 0.26266 | 0.16658 | 0.08086 | 0.75356 | 0.74628 | 0.729 | 0.70711 | 0.66888 | 0.62755 | 0.60689 | 0.58502 | 0.56166 | 0.53991 | 0.51739 | 0.39469 | 0.27445 | 0.17827 | 0.64123 | 0.6291 | 0.60512 | 0.5752 | 0.52899 | 0.47829 | 0.44823 | 0.42341 | 0.39744 | 0.37275 | 0.34627 | 0.23357 | 0.10401 | 0.00059818
|  | INVERGARRY | CT |  |  |  | 0.6289 | 0.61206 | 0.58288 | 0.54958 | 0.50698 | 0.45991 | 0.4292 | 0.40649 | 0.3828 | 0.36057 | 0.337 | 0.26266 | 0.18298 | 0.12126 | 0.75727 | 0.74702 | 0.729 | 0.70711 | 0.66888 | 0.62755 | 0.60689 | 0.58502 | 0.56166 | 0.53991 | 0.51739 | 0.42384 | 0.35446 | 0.27821 | 0.64696 | 0.63015 | 0.60512 | 0.5752 | 0.52899 | 0.47829 | 0.44823 | 0.42341 | 0.39744 | 0.37275 | 0.34627 | 0.24979 | 0.16975 | 0.09581
|  | INVERGARRY | LW |  |  |  | 0.61792 | 0.60477 | 0.58648 | 0.57065 | 0.55188 | 0.5287 | 0.50671 | 0.48413 | 0.4631 | 0.44017 | 0.42125 | 0.35002 | 0.23749 | 0.1012 | 0.75356 | 0.74628 | 0.73738 | 0.7289 | 0.71952 | 0.70661 | 0.69327 | 0.6753 | 0.65706 | 0.63832 | 0.61747 | 0.53152 | 0.40251 | 0.23712 | 0.64123 | 0.6291 | 0.61252 | 0.59798 | 0.58092 | 0.5595 | 0.53891 | 0.5161 | 0.4944 | 0.47032 | 0.44622 | 0.34832 | 0.21259 | 0.044976
|  | INVERGARRY | ST |  |  |  | 0.64067 | 0.64006 | 0.61235 | 0.59232 | 0.57392 | 0.53569 | 0.51704 | 0.48535 | 0.46445 | 0.44138 | 0.41432 | 0.28004 | 0.16658 | 0.08086 | 0.76482 | 0.76371 | 0.73528 | 0.71483 | 0.69864 | 0.65614 | 0.63926 | 0.60454 | 0.58574 | 0.56651 | 0.54153 | 0.39469 | 0.27445 | 0.17827 | 0.66065 | 0.65909 | 0.6294 | 0.60661 | 0.58684 | 0.54173 | 0.52167 | 0.48475 | 0.46214 | 0.43587 | 0.40278 | 0.23357 | 0.10401 | 0.00059818
|  | INVERGARRY | FS |  |  |  | 0.64739 | 0.64424 | 0.63419 | 0.62067 | 0.61325 | 0.60126 | 0.58966 | 0.57355 | 0.55667 | 0.54005 | 0.52515 | 0.43779 | 0.3651 | 0.31693 | 0.7679 | 0.76602 | 0.75798 | 0.74843 | 0.74043 | 0.7305 | 0.72101 | 0.70592 | 0.69247 | 0.67875 | 0.66525 | 0.60501 | 0.54275 | 0.48689 | 0.66288 | 0.66185 | 0.65457 | 0.641 | 0.63251 | 0.61996 | 0.60793 | 0.59032 | 0.57292 | 0.55566 | 0.53959 | 0.4538 | 0.36829 | 0.30341
| ALNESS | INVERGORDON | MINIMUM HEADROOM | NH 70756 69177 | NO | YES | -20.7426 | -21.123 | -22.7107 | -24.6103 | -27.0647 | -29.2724 | -31.0107 | -31.8612 | -32.7698 | -33.6498 | -34.4628 | -36.9656 | -38.2596 | -39.1684 | -28.78 | -28.9661 | -30.4143 | -32.1789 | -34.7507 | -37.0406 | -38.6665 | -39.3954 | -40.2444 | -41.0544 | -41.8417 | -44.2312 | -45.3491 | -46.398 | -21.9143 | -21.9143 | -22.7447 | -23.6717 | -25.5435 | -27.5255 | -28.6627 | -28.9633 | -29.275 | -29.5315 | -29.8202 | -31.3385 | -32.2539 | -33.1769
|  | INVERGORDON | CT |  |  |  | 8.1494 | 7.8193 | 6.8162 | -23.0009 | -24.643 | -26.001 | -26.9311 | -27.7177 | -28.5468 | -29.343 | -30.0715 | -32.2024 | -33.4636 | -34.1525 | 7.0509 | 6.8312 | 6.1508 | -30.5489 | -32.1627 | -33.4263 | -34.1008 | -34.6973 | -35.3193 | -35.9142 | -36.5462 | -38.3393 | -39.2493 | -40.0102 | 13.8 | 13.8 | 13.6957 | -22.2037 | -23.0939 | -24.0431 | -24.2838 | -24.4298 | -24.5763 | -24.7031 | -24.8423 | -25.5817 | -25.992 | -26.3584
|  | INVERGORDON | LW |  |  |  | -20.7426 | -21.123 | -22.7107 | -24.6103 | -27.0647 | -29.2724 | -31.0107 | -31.8612 | -32.7698 | -33.6498 | -34.4628 | -36.9656 | -38.2596 | -39.1684 | -28.78 | -28.9661 | -30.4143 | -32.1789 | -34.7507 | -37.0406 | -38.6665 | -39.3954 | -40.2444 | -41.0544 | -41.8417 | -44.2312 | -45.3491 | -46.398 | -21.9143 | -21.9143 | -22.7447 | -23.6717 | -25.5435 | -27.5255 | -28.6627 | -28.9633 | -29.275 | -29.5315 | -29.8202 | -31.3385 | -32.2539 | -33.1769
|  | INVERGORDON | ST |  |  |  | 8.2649 | 8.0414 | 6.7944 | 5.6081 | 4.6646 | -25.1672 | -25.8561 | -26.5273 | -27.1007 | -27.6757 | -28.2871 | -30.5973 | -32.028 | -33.2644 | 7.088 | 6.9388 | 5.6455 | 4.4558 | 3.4968 | -33.6164 | -34.2907 | -35.0089 | -35.5971 | -36.2004 | -36.8898 | -39.4266 | -40.6343 | -41.3145 | 13.8 | 13.8 | 12.9993 | 12.4579 | 12.1003 | -24.8432 | -25.1851 | -25.5063 | -25.6202 | -25.7166 | -25.8707 | -26.5931 | -27.2008 | -27.7303
|  | INVERGORDON | FS |  |  |  | 8.6328 | 8.4466 | 7.8158 | 7.0691 | 6.3845 | 5.9116 | 5.3778 | 4.8872 | 4.3657 | 3.8556 | 3.3798 | 1.5305 | 0.013186 | -1.0526 | 7.4364 | 7.3096 | 6.7454 | 6.0661 | 5.406 | 4.9917 | 4.5216 | 4.1023 | 3.6305 | 3.1473 | 2.679 | 1.0516 | -0.30707 | -1.2278 | 13.8 | 13.8 | 13.6363 | 13.4726 | 13.2817 | 13.0909 | 12.9271 | 12.8109 | 12.7321 | 12.6532 | 12.5744 | 12.4788 | 12.4332 | 12.3741
| FORT WILLIAM | INVERLOCHY | MINIMUM HEADROOM | NN 11653 74987 | NO | YES | 5.3531 | 5.0871 | 4.7844 | 4.4747 | 4.0962 | 3.6763 | 3.2472 | 3.0785 | 2.9104 | 2.6977 | 2.4303 | 1.5997 | 1.1408 | 0.88944 | 6.6076 | 6.4511 | 6.2947 | 6.0636 | 5.8374 | 5.598 | 5.3567 | 5.1691 | 4.9508 | 4.7052 | 4.4564 | 3.8304 | 3.3569 | 2.7102 | 4.2112 | 4.0539 | 3.8844 | 3.6485 | 3.4156 | 3.1674 | 2.751 | 2.5383 | 2.2859 | 1.9607 | 1.6471 | 0.82568 | 0.39428 | 0.14239
|  | INVERLOCHY | CT |  |  |  | 5.5266 | 5.3069 | 4.9103 | 4.4988 | 4.0962 | 3.6763 | 3.2472 | 3.0785 | 2.9104 | 2.7026 | 2.4676 | 1.8414 | 1.2285 | 1.0022 | 6.6728 | 6.5326 | 6.3134 | 6.0636 | 5.8374 | 5.598 | 5.3567 | 5.1691 | 4.9508 | 4.7287 | 4.5002 | 3.8304 | 3.3569 | 2.9615 | 4.267 | 4.1114 | 3.8844 | 3.6485 | 3.4156 | 3.1674 | 2.751 | 2.5383 | 2.2936 | 2.024 | 1.7481 | 1.0367 | 0.47629 | 0.26667
|  | INVERLOCHY | LW |  |  |  | 5.3531 | 5.0871 | 4.7844 | 4.4747 | 4.1667 | 3.8054 | 3.4122 | 3.2245 | 2.972 | 2.6977 | 2.4303 | 1.5997 | 1.1408 | 0.88944 | 6.6076 | 6.4511 | 6.2947 | 6.1181 | 5.9488 | 5.7091 | 5.4361 | 5.2128 | 4.9639 | 4.7052 | 4.4564 | 3.8381 | 3.5514 | 3.3586 | 4.2112 | 4.0539 | 3.8923 | 3.7211 | 3.5494 | 3.2867 | 2.866 | 2.6014 | 2.2859 | 1.9607 | 1.6471 | 0.82568 | 0.39428 | 0.14239
|  | INVERLOCHY | ST |  |  |  | 5.7416 | 5.6596 | 5.5563 | 5.4406 | 5.3189 | 5.1643 | 5.0056 | 4.8115 | 4.6031 | 4.376 | 4.1219 | 2.8164 | 2.0918 | 1.9087 | 6.7919 | 6.7278 | 6.6576 | 6.5783 | 6.4861 | 6.3577 | 6.2267 | 6.062 | 5.8811 | 5.678 | 5.4486 | 4.2424 | 3.7131 | 3.2979 | 4.4357 | 4.377 | 4.3136 | 4.2413 | 4.1621 | 4.0501 | 3.9363 | 3.7873 | 3.6237 | 3.3389 | 2.9957 | 1.1112 | 0.44789 | 0.33276
|  | INVERLOCHY | FS |  |  |  | 5.7916 | 5.729 | 5.6435 | 5.5365 | 5.4242 | 5.3074 | 5.1848 | 5.0424 | 4.8916 | 4.7304 | 4.5614 | 3.3372 | 2.2496 | 1.6542 | 6.8232 | 6.7711 | 6.7106 | 6.6447 | 6.5727 | 6.4862 | 6.3908 | 6.2746 | 6.1472 | 6.0064 | 5.8529 | 4.8034 | 3.6862 | 2.7102 | 4.4714 | 4.4264 | 4.3759 | 4.3218 | 4.2617 | 4.196 | 4.1242 | 4.0353 | 3.9382 | 3.8309 | 3.7138 | 2.553 | 1.2269 | 0.31999
| PORT ANN | INVERNEIL | MINIMUM HEADROOM | NR 84790 80580 | YES | YES | 6.8453 | 6.833 | 6.8032 | 6.7528 | 6.6839 | 6.6139 | 6.5647 | 6.4925 | 6.4098 | 6.3322 | 6.2386 | 5.9559 | 5.4463 | 4.6907 | 6.336 | 6.3245 | 6.3015 | 6.274 | 6.2164 | 6.156 | 6.125 | 6.0473 | 5.9806 | 5.9092 | 5.8283 | 5.5035 | 4.9441 | 4.025 | 5.1414 | 5.1393 | 5.1077 | 5.0835 | 5.0557 | 4.9793 | 4.9301 | 4.8496 | 4.7591 | 4.6784 | 4.5881 | 4.2492 | 3.6448 | 2.7141
|  | INVERNEIL | CT |  |  |  | 6.8456 | 6.8441 | 6.807 | 6.7528 | 6.6839 | 6.6139 | 6.5647 | 6.4925 | 6.4098 | 6.3364 | 6.2538 | 5.9576 | 5.6822 | 5.3901 | 6.3361 | 6.3346 | 6.3072 | 6.274 | 6.2164 | 6.156 | 6.125 | 6.056 | 5.9806 | 5.9092 | 5.8283 | 5.5069 | 5.1755 | 4.7976 | 5.1417 | 5.1402 | 5.1327 | 5.1214 | 5.0557 | 4.9793 | 4.9301 | 4.8496 | 4.7591 | 4.6784 | 4.5881 | 4.2492 | 3.9164 | 3.5556
|  | INVERNEIL | LW |  |  |  | 6.8453 | 6.833 | 6.8032 | 6.7679 | 6.7314 | 6.6782 | 6.6156 | 6.5261 | 6.4297 | 6.3322 | 6.2386 | 5.9559 | 5.4463 | 4.6907 | 6.336 | 6.3245 | 6.3089 | 6.2902 | 6.2718 | 6.2422 | 6.2068 | 6.1314 | 6.0396 | 5.9513 | 5.8634 | 5.5677 | 4.9441 | 4.025 | 5.1414 | 5.1393 | 5.1374 | 5.135 | 5.1141 | 5.0624 | 5.0016 | 4.9046 | 4.8004 | 4.6971 | 4.5966 | 4.2756 | 3.6448 | 2.7141
|  | INVERNEIL | ST |  |  |  | 6.8473 | 6.8469 | 6.8187 | 6.7993 | 6.7859 | 6.7309 | 6.7003 | 6.5943 | 6.5351 | 6.4774 | 6.3976 | 6.0269 | 5.6158 | 5.2027 | 6.337 | 6.3366 | 6.3015 | 6.2767 | 6.2521 | 6.1868 | 6.159 | 6.0473 | 5.9938 | 5.9437 | 5.8725 | 5.5035 | 4.9977 | 4.4679 | 5.1432 | 5.1428 | 5.1077 | 5.0835 | 5.0671 | 5.0125 | 4.9964 | 4.8998 | 4.8572 | 4.7941 | 4.706 | 4.2945 | 3.7919 | 3.2791
|  | INVERNEIL | FS |  |  |  | 6.8475 | 6.847 | 6.8411 | 6.8346 | 6.8273 | 6.8135 | 6.79 | 6.7441 | 6.7043 | 6.6619 | 6.6129 | 6.4113 | 6.2438 | 6.1476 | 6.3371 | 6.3367 | 6.3293 | 6.3216 | 6.307 | 6.2889 | 6.2711 | 6.2253 | 6.1888 | 6.1505 | 6.1097 | 5.96 | 5.8006 | 5.6664 | 5.1434 | 5.143 | 5.1356 | 5.1277 | 5.1187 | 5.1095 | 5.1012 | 5.0659 | 5.0413 | 5.0158 | 4.9631 | 4.7595 | 4.5889 | 4.483
| INVERNESS | INVERNESS | MINIMUM HEADROOM | NH 65302 42625 | NO | YES | 5.3337 | 4.8348 | 4.2025 | 3.5176 | 2.8027 | 2.0133 | 1.1565 | 0.38123 | -0.31346 | -1.0246 | -1.467 | -2.8189 | -4.1833 | -5.0327 | 7.6471 | 7.4539 | 7.2561 | 7.0638 | 6.817 | 6.492 | 6.1303 | 5.7454 | 5.3709 | 4.9885 | 4.6998 | 3.9119 | 3.1977 | 1.9124 | 6.4763 | 6.0469 | 5.5414 | 4.9718 | 4.3764 | 3.6806 | 2.9163 | 2.1874 | 1.5098 | 0.81863 | 0.34531 | -0.94394 | -2.0418 | -3.0007
|  | INVERNESS | CT |  |  |  | 5.5991 | 5.2167 | 4.6286 | 3.9992 | 3.3447 | 2.6641 | 1.9224 | 1.1207 | 0.35314 | -0.42942 | -0.95673 | -2.8157 | -4.1833 | -5.0327 | 7.6551 | 7.462 | 7.2561 | 7.0638 | 6.8447 | 6.5606 | 6.2605 | 5.9005 | 5.5855 | 5.269 | 4.9845 | 4.0485 | 3.1977 | 1.9124 | 6.6726 | 6.341 | 5.8399 | 5.298 | 4.7564 | 4.1753 | 3.5498 | 2.8356 | 2.1148 | 1.3815 | 0.85863 | -0.85758 | -2.0418 | -2.8319
|  | INVERNESS | LW |  |  |  | 5.3337 | 4.8348 | 4.2025 | 3.5176 | 2.8027 | 2.0133 | 1.1565 | 0.38123 | -0.31346 | -1.0246 | -1.467 | -2.8189 | -3.9356 | -4.8076 | 7.6471 | 7.4539 | 7.2921 | 7.0821 | 6.817 | 6.492 | 6.1303 | 5.7454 | 5.3709 | 4.9885 | 4.6998 | 3.9119 | 3.2196 | 2.4243 | 6.4763 | 6.0469 | 5.5414 | 4.9718 | 4.3764 | 3.6806 | 2.9163 | 2.1874 | 1.5098 | 0.81863 | 0.34531 | -0.94394 | -2.0121 | -3.0007
|  | INVERNESS | ST |  |  |  | 5.6972 | 5.3917 | 5.1296 | 4.8516 | 4.5551 | 4.2422 | 3.9192 | 3.522 | 3.1735 | 2.7994 | 2.5457 | 1.0459 | -0.15299 | -1.5532 | 7.7075 | 7.5876 | 7.4696 | 7.3427 | 7.2031 | 7.0381 | 6.8646 | 6.6094 | 6.3849 | 6.1403 | 5.9085 | 4.6426 | 3.8326 | 2.9112 | 6.7508 | 6.4996 | 6.2731 | 6.0287 | 5.768 | 5.4825 | 5.1851 | 4.7973 | 4.4518 | 4.0787 | 3.7848 | 2.1586 | 1.0697 | -0.13776
|  | INVERNESS | FS |  |  |  | 5.7725 | 5.5174 | 5.2709 | 5.0157 | 4.7421 | 4.4696 | 4.1845 | 3.8529 | 3.5452 | 3.2339 | 3.0065 | 1.6741 | 0.42735 | -0.62 | 7.7298 | 7.6223 | 7.5207 | 7.4119 | 7.2919 | 7.1664 | 7.0308 | 6.8642 | 6.7082 | 6.5413 | 6.3995 | 5.5396 | 4.4477 | 2.4261 | 6.8099 | 6.5983 | 6.3911 | 6.1719 | 5.9372 | 5.6985 | 5.4451 | 5.1434 | 4.8585 | 4.5643 | 4.3306 | 2.9815 | 1.7432 | 0.88675
| KINTORE | INVERURIE | MINIMUM HEADROOM | NJ 75665 21688 | NO | YES | 13.056 | 12.3712 | 11.3854 | 10.34 | 9.3025 | 8.002 | 6.4958 | 5.262 | 4.0056 | 2.6376 | 1.3363 | -1.9351 | -3.6645 | -5.0502 | 17.1699 | 16.7613 | 16.2748 | 15.7409 | 15.1507 | 14.4786 | 13.5554 | 12.7202 | 11.8523 | 10.9478 | 10.098 | 7.9088 | 6.2668 | 4.493 | 16.2738 | 15.6262 | 14.7411 | 13.7942 | 12.8627 | 11.6484 | 10.2254 | 9.0112 | 7.7611 | 6.4608 | 5.2312 | 2.1947 | 0.58028 | -0.67749
|  | INVERURIE | CT |  |  |  | 13.6337 | 13.1725 | 12.1061 | 10.9927 | 9.9358 | 8.8045 | 7.632 | 6.4808 | 5.2766 | 4.0658 | 2.8236 | -1.3014 | -3.6645 | -5.0502 | 17.3565 | 17.0374 | 16.4238 | 15.7679 | 15.1507 | 14.4786 | 13.7834 | 13.0439 | 12.2398 | 11.4312 | 10.6278 | 7.9088 | 6.2668 | 4.6001 | 16.5852 | 16.2688 | 15.3224 | 14.277 | 13.2952 | 12.2413 | 11.1647 | 10.0662 | 8.8916 | 7.7124 | 6.5461 | 2.7057 | 0.58028 | -0.67749
|  | INVERURIE | LW |  |  |  | 13.056 | 12.3712 | 11.3854 | 10.34 | 9.3025 | 8.002 | 6.4958 | 5.262 | 4.0056 | 2.6376 | 1.3363 | -1.9351 | -3.3701 | -4.5542 | 17.1699 | 16.7613 | 16.2748 | 15.7409 | 15.2231 | 14.4823 | 13.5554 | 12.7202 | 11.8523 | 10.9478 | 10.098 | 8.1142 | 7.2653 | 6.3133 | 16.2738 | 15.6262 | 14.7411 | 13.7942 | 12.8627 | 11.6484 | 10.2254 | 9.0112 | 7.7611 | 6.4608 | 5.2312 | 2.1947 | 0.84724 | -0.35561
|  | INVERURIE | ST |  |  |  | 13.9746 | 13.774 | 13.4375 | 13.071 | 12.6754 | 12.1655 | 11.5559 | 10.9284 | 10.2734 | 9.5143 | 8.6533 | 3.701 | 1.1079 | -1.2474 | 17.5311 | 17.3945 | 17.1406 | 16.8674 | 16.5759 | 16.1592 | 15.6774 | 15.1546 | 14.6215 | 14.022 | 13.3451 | 9.5755 | 7.4843 | 5.3821 | 16.704 | 16.6086 | 16.4104 | 16.1766 | 15.7998 | 15.2811 | 14.6819 | 14.0413 | 13.3749 | 12.629 | 11.7419 | 6.6669 | 4.5113 | 2.4781
|  | INVERURIE | FS |  |  |  | 14.0788 | 13.9294 | 13.6703 | 13.3724 | 13.0524 | 12.6991 | 12.2421 | 11.732 | 11.2054 | 10.6422 | 10.0379 | 5.856 | 1.9655 | -0.68926 | 17.5773 | 17.4673 | 17.2951 | 17.0913 | 16.8666 | 16.6103 | 16.2583 | 15.879 | 15.4804 | 15.0415 | 14.5619 | 11.4075 | 7.9188 | 4.493 | 16.7331 | 16.6609 | 16.5544 | 16.4253 | 16.19 | 15.8511 | 15.4111 | 14.9186 | 14.4056 | 13.8533 | 13.2571 | 9.3027 | 5.6523 | 3.2408
| BROADFORD | KALNAKIL | MINIMUM HEADROOM | NG 69146 53941 | YES | YES | [14 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: Demand Headroom Winter MVA 2025 to Demand Headroom Winter MVA 2050
|  | KALNAKIL | CT | [17 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: Demand Headroom Winter MVA 2025 to Demand Headroom Winter MVA 2050
|  | KALNAKIL | LW | [17 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: Demand Headroom Winter MVA 2025 to Demand Headroom Winter MVA 2050
|  | KALNAKIL | ST | [17 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: Demand Headroom Winter MVA 2025 to Demand Headroom Winter MVA 2050
|  | KALNAKIL | FS | [17 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: Demand Headroom Winter MVA 2025 to Demand Headroom Winter MVA 2050
| DUNOON | KAMES | MINIMUM HEADROOM | NR 96305 71237 | YES | YES | 2.2056 | 2.1442 | 2.0735 | 1.9976 | 1.9262 | 1.8445 | 1.7502 | 1.6918 | 1.6283 | 1.56 | 1.4982 | 1.3793 | 1.3334 | 1.2933 | 2.3262 | 2.2919 | 2.2558 | 2.2133 | 2.1705 | 2.127 | 2.0705 | 2.0244 | 1.9743 | 1.9215 | 1.8732 | 1.7849 | 1.762 | 1.7364 | 2.1984 | 2.1421 | 2.078 | 2.0087 | 1.9413 | 1.8668 | 1.7783 | 1.7202 | 1.6571 | 1.5895 | 1.5282 | 1.4122 | 1.3705 | 1.3314
|  | KAMES | CT |  |  |  | 2.2426 | 2.2007 | 2.1048 | 2.009 | 1.9262 | 1.8445 | 1.7579 | 1.718 | 1.6618 | 1.6072 | 1.5541 | 1.455 | 1.3688 | 1.3326 | 2.341 | 2.316 | 2.2654 | 2.2133 | 2.1705 | 2.127 | 2.0812 | 2.049 | 2.0055 | 1.9622 | 1.9209 | 1.834 | 1.7868 | 1.7587 | 2.231 | 2.1923 | 2.1047 | 2.0165 | 1.9413 | 1.8668 | 1.788 | 1.7483 | 1.6928 | 1.6386 | 1.5861 | 1.4859 | 1.4043 | 1.3681
|  | KAMES | LW |  |  |  | 2.2056 | 2.1442 | 2.0735 | 1.9976 | 1.935 | 1.8481 | 1.7502 | 1.6918 | 1.6283 | 1.56 | 1.4982 | 1.3793 | 1.3334 | 1.2933 | 2.3262 | 2.2919 | 2.2558 | 2.2155 | 2.1814 | 2.1297 | 2.0705 | 2.0244 | 1.9743 | 1.9215 | 1.8732 | 1.7849 | 1.762 | 1.7364 | 2.1984 | 2.1421 | 2.078 | 2.0087 | 1.9513 | 1.8701 | 1.7783 | 1.7202 | 1.6571 | 1.5895 | 1.5282 | 1.4122 | 1.3705 | 1.3314
|  | KAMES | ST |  |  |  | 2.2813 | 2.2612 | 2.2371 | 2.2114 | 2.1878 | 2.1624 | 2.1301 | 2.0895 | 2.0473 | 1.9979 | 1.9439 | 1.6933 | 1.6335 | 1.5915 | 2.3579 | 2.3463 | 2.3324 | 2.3169 | 2.3015 | 2.284 | 2.2621 | 2.2351 | 2.2048 | 2.1698 | 2.1311 | 1.9416 | 1.8957 | 1.8656 | 2.2533 | 2.2475 | 2.2256 | 2.2017 | 2.1794 | 2.1551 | 2.1242 | 2.0856 | 2.0448 | 1.997 | 1.9447 | 1.6995 | 1.6424 | 1.6056
|  | KAMES | FS |  |  |  | 2.2881 | 2.2731 | 2.248 | 2.2249 | 2.1984 | 2.1725 | 2.144 | 2.1131 | 2.0796 | 2.0433 | 2.0054 | 1.7377 | 1.5461 | 1.4856 | 2.3613 | 2.3521 | 2.3385 | 2.3252 | 2.3105 | 2.295 | 2.2775 | 2.2578 | 2.2358 | 2.2116 | 2.1854 | 2.006 | 1.8606 | 1.8046 | 2.2531 | 2.2533 | 2.2356 | 2.2145 | 2.19 | 2.1659 | 2.1392 | 2.1101 | 2.0782 | 2.0436 | 2.0073 | 1.7524 | 1.567 | 1.5109
| KEITH | KEITH | MINIMUM HEADROOM | NJ 43925 50405 | NO | YES | 6.082 | 6.0048 | 5.4262 | 4.4167 | 3.5366 | 2.563 | 1.7071 | 1.2474 | 0.77958 | 0.30704 | -0.38017 | -1.8538 | -2.9018 | -3.7972 | 8.3601 | 8.2295 | 7.756 | 6.909 | 6.094 | 5.1861 | 4.4617 | 4.126 | 3.776 | 3.4328 | 2.8924 | 1.8067 | 0.88633 | -0.13156 | 4.9596 | 4.8237 | 4.3003 | 3.3429 | 2.4197 | 1.4143 | 0.58796 | 0.2006 | -0.19722 | -0.59535 | -1.2175 | -2.6004 | -3.6568 | -4.6726
|  | KEITH | CT |  |  |  | 6.0834 | 6.0048 | 5.8639 | 5.1403 | 4.4504 | 3.725 | 3.1924 | 2.7176 | 2.2107 | 1.7159 | 0.9939 | -0.76009 | -1.9537 | -2.6569 | 8.4466 | 8.3484 | 8.0897 | 7.453 | 6.8346 | 6.1785 | 5.8012 | 5.4826 | 5.1302 | 4.7891 | 4.2468 | 2.9955 | 2.1266 | 1.3201 | 4.9596 | 4.8698 | 4.6471 | 3.9405 | 3.2684 | 2.5558 | 2.0966 | 1.6989 | 1.3153 | 0.94764 | 0.31263 | -1.2414 | -2.2499 | -2.9054
|  | KEITH | LW |  |  |  | 6.082 | 6.0095 | 5.4262 | 4.4167 | 3.5366 | 2.563 | 1.7071 | 1.2474 | 0.77958 | 0.30704 | -0.38017 | -1.8538 | -2.9018 | -3.7972 | 8.3601 | 8.2295 | 7.756 | 6.909 | 6.094 | 5.1861 | 4.4617 | 4.126 | 3.776 | 3.4328 | 2.8924 | 1.8067 | 0.88633 | -0.13156 | 4.9605 | 4.8237 | 4.3003 | 3.3429 | 2.4197 | 1.4143 | 0.58796 | 0.2006 | -0.19722 | -0.59535 | -1.2175 | -2.6004 | -3.6568 | -4.6726
|  | KEITH | ST |  |  |  | 6.1062 | 6.0703 | 5.6985 | 5.0423 | 4.8603 | 4.3086 | 4.0199 | 3.7717 | 3.6263 | 3.4715 | 2.9769 | 1.3796 | 0.083816 | -1.2204 | 8.4853 | 8.4342 | 7.9597 | 7.2752 | 7.0331 | 6.3245 | 5.981 | 5.6526 | 5.4521 | 5.2485 | 4.7889 | 3.4009 | 2.313 | 1.1893 | 4.9898 | 4.9568 | 4.504 | 3.7843 | 3.5594 | 2.8572 | 2.5 | 2.1679 | 1.9535 | 1.7284 | 1.206 | -0.37297 | -1.5048 | -2.4772
|  | KEITH | FS |  |  |  | 6.1138 | 6.0822 | 5.9785 | 5.5951 | 5.4704 | 5.3412 | 5.1479 | 5.0286 | 4.9128 | 4.7527 | 4.4034 | 3.0809 | 1.841 | 0.94083 | 8.5013 | 8.4585 | 8.3193 | 7.932 | 7.7646 | 7.5882 | 7.3562 | 7.1688 | 6.9892 | 6.8147 | 6.515 | 5.5212 | 4.4476 | 3.4202 | 4.9979 | 4.9698 | 4.8522 | 4.4474 | 4.2997 | 4.1467 | 3.9188 | 3.7551 | 3.5828 | 3.3992 | 3.0746 | 1.9999 | 0.98692 | 0.22657
| KINTORE | KEMNAY | MINIMUM HEADROOM | NJ 73180 16804 | NO | YES | 10.2808 | 10.2461 | 10.0486 | 9.8081 | 9.574 | 9.0901 | 8.6837 | 8.3163 | 8.0459 | 7.7624 | 7.4899 | 6.8001 | 6.2763 | 5.9488 | 11.1471 | 11.116 | 11.069 | 10.9529 | 10.8428 | 10.5151 | 10.2558 | 10.003 | 9.8358 | 9.6596 | 9.4917 | 8.9782 | 8.5684 | 8.1486 | 10.5359 | 10.399 | 10.2009 | 9.9892 | 9.7859 | 9.3491 | 8.9787 | 8.6326 | 8.3686 | 8.0931 | 7.83 | 7.2072 | 6.7389 | 6.4392
|  | KEMNAY | CT |  |  |  | 10.2811 | 10.2511 | 10.2042 | 10.0021 | 9.7698 | 9.3403 | 9.0293 | 8.6605 | 8.3571 | 8.0472 | 7.7574 | 6.8573 | 6.2763 | 5.9488 | 11.1471 | 11.1162 | 11.069 | 10.9921 | 10.8621 | 10.5572 | 10.3551 | 10.1074 | 9.9153 | 9.722 | 9.541 | 8.9782 | 8.5684 | 8.1486 | 10.5781 | 10.5314 | 10.3591 | 10.1338 | 9.9229 | 9.5355 | 9.2601 | 8.9212 | 8.6303 | 8.3344 | 8.0595 | 7.2385 | 6.7389 | 6.4392
|  | KEMNAY | LW |  |  |  | 10.2808 | 10.2461 | 10.0486 | 9.8081 | 9.574 | 9.0901 | 8.6837 | 8.3163 | 8.0459 | 7.7624 | 7.4899 | 6.8001 | 6.4355 | 6.1784 | 11.1499 | 11.116 | 11.0693 | 10.9529 | 10.8428 | 10.5151 | 10.2558 | 10.003 | 9.8358 | 9.6596 | 9.4917 | 9.1066 | 8.8941 | 8.6838 | 10.5359 | 10.399 | 10.2009 | 9.9892 | 9.7859 | 9.3491 | 8.9787 | 8.6326 | 8.3686 | 8.0931 | 7.83 | 7.2072 | 6.8801 | 6.6178
|  | KEMNAY | ST |  |  |  | 10.2935 | 10.2798 | 10.2461 | 10.2124 | 10.179 | 9.9338 | 9.7896 | 9.6204 | 9.4808 | 9.3338 | 9.1748 | 8.2768 | 7.7137 | 7.1484 | 11.163 | 11.1511 | 11.1156 | 11.082 | 11.0492 | 10.7909 | 10.6307 | 10.4551 | 10.3793 | 10.3025 | 10.1823 | 9.5083 | 9.0625 | 8.5464 | 10.6045 | 10.5862 | 10.5419 | 10.4977 | 10.4237 | 10.1471 | 9.9721 | 9.7542 | 9.6142 | 9.4657 | 9.303 | 8.406 | 7.9015 | 7.4187
|  | KEMNAY | FS |  |  |  | 10.2964 | 10.285 | 10.2671 | 10.2456 | 10.2215 | 10.0844 | 9.9732 | 9.8531 | 9.7618 | 9.6217 | 9.4828 | 8.6055 | 7.8018 | 7.3149 | 11.1655 | 11.1556 | 11.1389 | 11.1193 | 11.0968 | 10.9561 | 10.834 | 10.7093 | 10.652 | 10.5697 | 10.4629 | 9.8084 | 9.0624 | 8.3343 | 10.6101 | 10.5951 | 10.5709 | 10.5427 | 10.5107 | 10.3466 | 10.208 | 10.0304 | 9.9069 | 9.7737 | 9.6394 | 8.8019 | 8.0426 | 7.6384
| TAYNUILT | KENMORE | MINIMUM HEADROOM | NN 00325 34042 | YES | YES | 0.37311 | 0.36971 | 0.36204 | 0.3533 | 0.34694 | 0.33295 | 0.32655 | 0.31975 | 0.31393 | 0.30453 | 0.29923 | 0.28594 | 0.28136 | 0.27972 | 0.38431 | 0.38172 | 0.3778 | 0.37208 | 0.36846 | 0.36196 | 0.35764 | 0.35219 | 0.34661 | 0.33876 | 0.33311 | 0.32387 | 0.32033 | 0.31477 | 0.35817 | 0.35484 | 0.34783 | 0.33961 | 0.33372 | 0.32114 | 0.31487 | 0.30814 | 0.30278 | 0.29179 | 0.28554 | 0.27237 | 0.26842 | 0.26683
|  | KENMORE | CT |  |  |  | 0.37736 | 0.37308 | 0.36494 | 0.3533 | 0.34694 | 0.33295 | 0.32784 | 0.32102 | 0.31393 | 0.30885 | 0.30235 | 0.29117 | 0.28518 | 0.27972 | 0.38587 | 0.38314 | 0.37829 | 0.37208 | 0.36846 | 0.36196 | 0.3587 | 0.35394 | 0.34823 | 0.34226 | 0.33646 | 0.32491 | 0.32033 | 0.31477 | 0.36196 | 0.3579 | 0.3503 | 0.33961 | 0.33372 | 0.32114 | 0.31633 | 0.30978 | 0.30278 | 0.29663 | 0.28954 | 0.27724 | 0.27177 | 0.26683
|  | KENMORE | LW |  |  |  | 0.37311 | 0.36971 | 0.36204 | 0.35346 | 0.34881 | 0.33829 | 0.32655 | 0.31975 | 0.31576 | 0.30453 | 0.29923 | 0.28594 | 0.28136 | 0.28103 | 0.38431 | 0.38172 | 0.3778 | 0.37332 | 0.37053 | 0.36451 | 0.35764 | 0.35219 | 0.34661 | 0.33876 | 0.33311 | 0.32387 | 0.3221 | 0.32199 | 0.35817 | 0.35484 | 0.34783 | 0.33996 | 0.33561 | 0.32583 | 0.31487 | 0.30814 | 0.303 | 0.29179 | 0.28554 | 0.27237 | 0.26842 | 0.2681
|  | KENMORE | ST |  |  |  | 0.38265 | 0.38167 | 0.37883 | 0.37251 | 0.37038 | 0.36814 | 0.36654 | 0.35837 | 0.35199 | 0.34714 | 0.33991 | 0.30689 | 0.29703 | 0.29275 | 0.38847 | 0.3877 | 0.38589 | 0.38263 | 0.38098 | 0.37908 | 0.37734 | 0.37262 | 0.36824 | 0.36384 | 0.35846 | 0.33184 | 0.32389 | 0.31933 | 0.36725 | 0.36629 | 0.36345 | 0.35736 | 0.35529 | 0.35307 | 0.35131 | 0.34379 | 0.33758 | 0.33228 | 0.32525 | 0.2896 | 0.27515 | 0.27202
|  | KENMORE | FS |  |  |  | 0.3842 | 0.3834 | 0.37645 | 0.37669 | 0.37326 | 0.37168 | 0.36762 | 0.36206 | 0.35723 | 0.35422 | 0.34868 | 0.31575 | 0.29144 | 0.28727 | 0.38926 | 0.38859 | 0.38506 | 0.38456 | 0.38262 | 0.38125 | 0.37883 | 0.37569 | 0.37265 | 0.37011 | 0.36639 | 0.34253 | 0.32212 | 0.31558 | 0.36863 | 0.36784 | 0.36106 | 0.36118 | 0.35797 | 0.35641 | 0.35264 | 0.3475 | 0.34297 | 0.33999 | 0.33475 | 0.30197 | 0.27737 | 0.26978
| STRATHLEVEN | KEPCULLOCH | MINIMUM HEADROOM | NS 53864 91598 | NO | YES | 2.7843 | 2.5661 | 2.182 | 1.7714 | 1.3019 | 0.77118 | 0.26863 | -0.044056 | -0.37792 | -0.70869 | -1.0331 | -2.149 | -3.0692 | -3.8586 | 4.3001 | 4.2239 | 4.0708 | 3.903 | 3.6692 | 3.4006 | 3.1765 | 3.0368 | 2.8853 | 2.724 | 2.5199 | 1.9192 | 1.4009 | 0.84201 | 3.9372 | 3.7422 | 3.3885 | 3.0095 | 2.5629 | 2.0556 | 1.5863 | 1.2985 | 0.99154 | 0.68752 | 0.39022 | -0.59935 | -1.4352 | -2.1893
|  | KEPCULLOCH | CT |  |  |  | 2.9962 | 2.8599 | 2.4793 | 2.0724 | 1.608 | 1.1225 | 0.708 | 0.41397 | 0.08391 | -0.24518 | -0.56978 | -1.7874 | -2.9392 | -3.7082 | 4.3429 | 4.2848 | 4.1521 | 4.0179 | 3.7915 | 3.5519 | 3.4006 | 3.2733 | 3.1501 | 3.0231 | 2.8201 | 2.0952 | 1.4762 | 0.91658 | 4.1229 | 4.001 | 3.6587 | 3.2904 | 2.8493 | 2.3873 | 2.0137 | 1.7439 | 1.4402 | 1.1379 | 0.83973 | -0.25935 | -1.2745 | -1.9564
|  | KEPCULLOCH | LW |  |  |  | 2.7843 | 2.5661 | 2.182 | 1.7714 | 1.3019 | 0.77118 | 0.26863 | -0.044056 | -0.37792 | -0.70869 | -1.0331 | -2.149 | -3.0692 | -3.8586 | 4.3001 | 4.2239 | 4.0708 | 3.903 | 3.6692 | 3.4006 | 3.1765 | 3.0368 | 2.8853 | 2.724 | 2.5199 | 1.9192 | 1.4009 | 0.84201 | 3.9372 | 3.7422 | 3.3885 | 3.0095 | 2.5629 | 2.0556 | 1.5863 | 1.2985 | 0.99154 | 0.68752 | 0.39022 | -0.59935 | -1.4352 | -2.1893
|  | KEPCULLOCH | ST |  |  |  | 3.0896 | 3.0109 | 2.816 | 2.6358 | 2.4611 | 2.185 | 1.9939 | 1.7919 | 1.5957 | 1.3901 | 1.1661 | -0.076676 | -0.97592 | -1.8709 | 4.3799 | 4.3517 | 4.2099 | 4.0951 | 3.9965 | 3.7797 | 3.671 | 3.5481 | 3.4467 | 3.3401 | 3.216 | 2.5599 | 2.0205 | 1.3876 | 4.2066 | 4.1381 | 3.9382 | 3.7609 | 3.5959 | 3.3083 | 3.1274 | 2.9332 | 2.7534 | 2.5646 | 2.3562 | 1.2095 | 0.39204 | -0.41472
|  | KEPCULLOCH | FS |  |  |  | 3.1427 | 3.086 | 2.9657 | 2.8398 | 2.6968 | 2.5487 | 2.4019 | 2.229 | 2.0491 | 1.8622 | 1.6733 | 0.44065 | -0.56737 | -1.3242 | 4.3942 | 4.3727 | 4.3171 | 4.2578 | 4.1894 | 4.1173 | 4.0467 | 3.9696 | 3.8924 | 3.8115 | 3.7269 | 3.2367 | 2.5346 | 1.8834 | 4.2532 | 4.204 | 4.0937 | 3.9785 | 3.848 | 3.7127 | 3.5784 | 3.4212 | 3.2597 | 3.0911 | 2.9202 | 1.8202 | 0.92426 | 0.27543
| TAYNUILT | KERRERA | MINIMUM HEADROOM | NM 82340 27997 | YES | YES | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138
|  | KERRERA | CT |  |  |  | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138
|  | KERRERA | LW |  |  |  | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138
|  | KERRERA | ST |  |  |  | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138
|  | KERRERA | FS |  |  |  | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.27706 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26905 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138 | 0.26138
| GRUDIE BRIDGE | KERRY FALLS | MINIMUM HEADROOM | NG 82909 71978 | YES | YES | 5.3684 | 5.3032 | 5.2299 | 5.1525 | 5.0784 | 4.9844 | 4.8826 | 4.8177 | 4.7537 | 4.6853 | 4.6263 | 4.5084 | 4.436 | 4.3881 | 5.1833 | 5.1482 | 5.1121 | 5.0679 | 5.025 | 4.9798 | 4.926 | 4.8778 | 4.8281 | 4.7719 | 4.7203 | 4.6419 | 4.5844 | 4.5352 | 4.9677 | 4.9076 | 4.8409 | 4.7701 | 4.7006 | 4.6158 | 4.521 | 4.4541 | 4.3831 | 4.3083 | 4.2429 | 4.1296 | 4.066 | 4.0229
|  | KERRY FALLS | CT |  |  |  | 5.4134 | 5.3702 | 5.2722 | 5.1665 | 5.0784 | 4.9854 | 4.8961 | 4.8507 | 4.7866 | 4.7174 | 4.6637 | 4.5472 | 4.436 | 4.3881 | 5.1998 | 5.1746 | 5.1232 | 5.0679 | 5.025 | 4.9798 | 4.9358 | 4.9005 | 4.8507 | 4.7977 | 4.7491 | 4.6473 | 4.5844 | 4.5352 | 5.0074 | 4.9672 | 4.8774 | 4.7805 | 4.7006 | 4.6165 | 4.5355 | 4.4909 | 4.4217 | 4.3458 | 4.2859 | 4.1651 | 4.066 | 4.0229
|  | KERRY FALLS | LW |  |  |  | 5.3684 | 5.3032 | 5.2299 | 5.1525 | 5.0807 | 4.9844 | 4.8826 | 4.8177 | 4.7537 | 4.6853 | 4.6263 | 4.5084 | 4.4534 | 4.432 | 5.1833 | 5.1482 | 5.1121 | 5.0726 | 5.0375 | 4.9843 | 4.926 | 4.8778 | 4.8281 | 4.7719 | 4.7203 | 4.6419 | 4.6188 | 4.6106 | 4.9677 | 4.9076 | 4.8409 | 4.7701 | 4.7049 | 4.6158 | 4.521 | 4.4541 | 4.3831 | 4.3083 | 4.2429 | 4.1296 | 4.0812 | 4.0627
|  | KERRY FALLS | ST |  |  |  | 5.447 | 5.4278 | 5.3988 | 5.3643 | 5.3321 | 5.2927 | 5.253 | 5.2072 | 5.1518 | 5.0914 | 5.0265 | 4.7125 | 4.607 | 4.5453 | 5.216 | 5.2053 | 5.1899 | 5.1709 | 5.1521 | 5.1289 | 5.1039 | 5.0743 | 5.0383 | 4.9983 | 4.9545 | 4.7228 | 4.6516 | 4.6021 | 5.0377 | 5.0201 | 4.9936 | 4.9619 | 4.932 | 4.8954 | 4.8577 | 4.8118 | 4.7561 | 4.695 | 4.6288 | 4.3141 | 4.2173 | 4.1633
|  | KERRY FALLS | FS |  |  |  | 5.4647 | 5.4448 | 5.4207 | 5.3907 | 5.3621 | 5.3289 | 5.2937 | 5.2515 | 5.2066 | 5.1607 | 5.1116 | 4.7809 | 4.5475 | 4.4948 | 5.2231 | 5.2125 | 5.1998 | 5.1838 | 5.1679 | 5.1493 | 5.1288 | 5.1042 | 5.0772 | 5.0484 | 5.0171 | 4.8066 | 4.6237 | 4.559 | 5.0419 | 5.0354 | 5.0134 | 4.9859 | 4.9596 | 4.9291 | 4.8964 | 4.8573 | 4.814 | 4.7688 | 4.7201 | 4.396 | 4.1656 | 4.1189
| TAYNUILT | KILCHRENAN | MINIMUM HEADROOM | NN 03495 23835 | YES | YES | 0.32667 | 0.30325 | 0.27635 | 0.24227 | 0.20783 | 0.17201 | 0.13415 | 0.11618 | 0.094572 | 0.068842 | 0.045635 | -0.010168 | -0.034159 | -0.049295 | 0.35121 | 0.33426 | 0.31501 | 0.29545 | 0.28052 | 0.26469 | 0.24685 | 0.23017 | 0.21542 | 0.20044 | 0.18236 | 0.12166 | 0.10613 | 0.088059 | 0.11328 | 0.094928 | 0.074592 | 0.053696 | 0.038495 | 0.022219 | 0.0037461 | -0.014181 | -0.030325 | -0.046767 | -0.066111 | -0.1322 | -0.14916 | -0.16311
|  | KILCHRENAN | CT |  |  |  | 0.34316 | 0.32254 | 0.28396 | 0.24227 | 0.20783 | 0.17201 | 0.13415 | 0.11618 | 0.094572 | 0.070069 | 0.047308 | 0.0086704 | -0.034159 | -0.049295 | 0.35121 | 0.33426 | 0.31501 | 0.29545 | 0.28052 | 0.26469 | 0.24685 | 0.23017 | 0.21542 | 0.20044 | 0.18236 | 0.13698 | 0.12714 | 0.10881 | 0.11328 | 0.094928 | 0.074592 | 0.053696 | 0.038495 | 0.022219 | 0.0037461 | -0.014181 | -0.030325 | -0.046767 | -0.066111 | -0.11419 | -0.12571 | -0.14103
|  | KILCHRENAN | LW |  |  |  | 0.32667 | 0.30325 | 0.27635 | 0.24585 | 0.2185 | 0.18241 | 0.14444 | 0.11951 | 0.09523 | 0.068842 | 0.045635 | -0.010168 | -0.033876 | -0.040203 | 0.35478 | 0.34525 | 0.33695 | 0.32712 | 0.31692 | 0.3008 | 0.28166 | 0.26051 | 0.23738 | 0.2122 | 0.18797 | 0.12166 | 0.10613 | 0.10563 | 0.11796 | 0.10845 | 0.10021 | 0.090405 | 0.080146 | 0.063404 | 0.043341 | 0.020569 | -0.0049673 | -0.032529 | -0.059171 | -0.1322 | -0.14916 | -0.14927
|  | KILCHRENAN | ST |  |  |  | 0.36078 | 0.35064 | 0.34229 | 0.32976 | 0.31527 | 0.30198 | 0.28429 | 0.26627 | 0.24745 | 0.22625 | 0.20044 | 0.079243 | 0.044704 | 0.023112 | 0.37252 | 0.369 | 0.36452 | 0.35874 | 0.35167 | 0.3429 | 0.33207 | 0.31896 | 0.30297 | 0.28424 | 0.26245 | 0.14601 | 0.10933 | 0.10496 | 0.13727 | 0.13389 | 0.1294 | 0.12355 | 0.11629 | 0.10721 | 0.095953 | 0.082064 | 0.06497 | 0.044875 | 0.021472 | -0.10316 | -0.14092 | -0.14342
|  | KILCHRENAN | FS |  |  |  | 0.36796 | 0.36097 | 0.3494 | 0.34057 | 0.3278 | 0.31786 | 0.30758 | 0.29005 | 0.27561 | 0.25701 | 0.23605 | 0.11311 | 0.020022 | -0.011369 | 0.37648 | 0.37406 | 0.37075 | 0.36681 | 0.36218 | 0.35672 | 0.35043 | 0.3427 | 0.33388 | 0.32363 | 0.31195 | 0.23035 | 0.14277 | 0.088059 | 0.14153 | 0.13929 | 0.13613 | 0.13232 | 0.12774 | 0.1223 | 0.11582 | 0.10801 | 0.098917 | 0.088386 | 0.076192 | -0.0096987 | -0.10468 | -0.16311
| STRATHLEVEN | KILLEARN | MINIMUM HEADROOM | NS 51313 86758 | YES | YES | -1.2131 | -1.3311 | -1.5529 | -1.7982 | -2.0534 | -2.3462 | -2.6539 | -2.9065 | -3.1692 | -3.4202 | -3.6714 | -4.7277 | -5.6836 | -6.4106 | -0.37839 | -0.43731 | -0.52328 | -0.62911 | -0.79388 | -0.97421 | -1.1083 | -1.2625 | -1.4365 | -1.6061 | -1.7714 | -2.4368 | -3.0468 | -3.6946 | -0.70622 | -0.80459 | -0.97568 | -1.1661 | -1.3609 | -1.5936 | -1.8409 | -2.0578 | -2.2844 | -2.5054 | -2.7413 | -3.6609 | -4.4848 | -5.1325
|  | KILLEARN | CT |  |  |  | -1.1039 | -1.1829 | -1.4077 | -1.656 | -1.9371 | -2.2393 | -2.5034 | -2.7689 | -3.0552 | -3.3318 | -3.6063 | -4.7277 | -5.6836 | -6.4106 | -0.35171 | -0.40035 | -0.5071 | -0.62911 | -0.79388 | -0.97421 | -1.1083 | -1.2625 | -1.4365 | -1.6061 | -1.7714 | -2.4368 | -3.0468 | -3.6946 | -0.62548 | -0.69342 | -0.8768 | -1.0815 | -1.3213 | -1.5784 | -1.7885 | -2.0134 | -2.2633 | -2.5054 | -2.7413 | -3.6609 | -4.4848 | -5.1325
|  | KILLEARN | LW |  |  |  | -1.2131 | -1.3311 | -1.5529 | -1.7982 | -2.0534 | -2.3462 | -2.6539 | -2.9065 | -3.1692 | -3.4202 | -3.6714 | -4.633 | -5.5344 | -6.3283 | -0.37839 | -0.43731 | -0.52328 | -0.62683 | -0.73753 | -0.87608 | -1.0242 | -1.1671 | -1.3168 | -1.4617 | -1.6039 | -2.0754 | -2.611 | -3.1837 | -0.70622 | -0.80459 | -0.97568 | -1.1661 | -1.3609 | -1.5936 | -1.8409 | -2.0578 | -2.2844 | -2.5025 | -2.7183 | -3.4793 | -4.2784 | -5.0422
|  | KILLEARN | ST |  |  |  | -1.074 | -1.1226 | -1.2335 | -1.3404 | -1.4517 | -1.614 | -1.7273 | -1.8816 | -2.0132 | -2.1449 | -2.2951 | -3.1886 | -3.9593 | -4.7481 | -0.33906 | -0.36729 | -0.45715 | -0.53728 | -0.61251 | -0.75033 | -0.83242 | -0.96039 | -1.0575 | -1.1566 | -1.2751 | -1.9528 | -2.5673 | -3.2746 | -0.60154 | -0.64052 | -0.74804 | -0.84737 | -0.94566 | -1.1066 | -1.2097 | -1.3616 | -1.4839 | -1.6075 | -1.7514 | -2.5798 | -3.2503 | -3.9152
|  | KILLEARN | FS |  |  |  | -1.053 | -1.0919 | -1.1589 | -1.2345 | -1.314 | -1.4068 | -1.4971 | -1.6178 | -1.7298 | -1.8483 | -1.9712 | -2.712 | -3.4483 | -4.0669 | -0.33273 | -0.35787 | -0.40083 | -0.44991 | -0.50366 | -0.56434 | -0.625 | -0.707 | -0.78443 | -0.86715 | -0.95723 | -1.4845 | -2.113 | -2.8332 | -0.58551 | -0.61668 | -0.67376 | -0.73844 | -0.80689 | -0.88616 | -0.96414 | -1.0705 | -1.1693 | -1.2743 | -1.3839 | -2.0199 | -2.638 | -3.0992
| KILLIN | KILLIN TOWN | MINIMUM HEADROOM | NN 56931 32662 | YES | YES | 1.8755 | 1.8723 | 1.8528 | 1.7957 | 1.7018 | 1.6048 | 1.5258 | 1.4673 | 1.4057 | 1.3429 | 1.2637 | 1.0025 | 0.76637 | 0.54295 | 2.0518 | 2.0238 | 1.9903 | 1.9343 | 1.8649 | 1.792 | 1.742 | 1.6856 | 1.6193 | 1.5565 | 1.4939 | 1.2877 | 1.1288 | 0.9747 | 1.7409 | 1.7178 | 1.6754 | 1.6149 | 1.5252 | 1.4318 | 1.3605 | 1.303 | 1.2494 | 1.2033 | 1.1381 | 0.901 | 0.70179 | 0.49517
|  | KILLIN TOWN | CT |  |  |  | 1.8759 | 1.8728 | 1.8652 | 1.7957 | 1.7018 | 1.6048 | 1.5258 | 1.4673 | 1.4057 | 1.3429 | 1.2637 | 1.0025 | 0.76637 | 0.58186 | 2.0629 | 2.0373 | 1.9903 | 1.9343 | 1.8649 | 1.792 | 1.742 | 1.6856 | 1.6193 | 1.5565 | 1.4939 | 1.2877 | 1.1288 | 0.9747 | 1.7465 | 1.7399 | 1.6825 | 1.6149 | 1.5252 | 1.4318 | 1.3605 | 1.303 | 1.2494 | 1.2033 | 1.1381 | 0.901 | 0.70179 | 0.53809
|  | KILLIN TOWN | LW |  |  |  | 1.8755 | 1.8723 | 1.8566 | 1.798 | 1.7394 | 1.6641 | 1.5911 | 1.5371 | 1.4625 | 1.3826 | 1.3014 | 1.0572 | 0.80867 | 0.54295 | 2.0518 | 2.0238 | 1.9928 | 1.9568 | 1.9227 | 1.8713 | 1.8161 | 1.7584 | 1.6949 | 1.6332 | 1.573 | 1.4145 | 1.2248 | 0.98839 | 1.7409 | 1.7178 | 1.6754 | 1.6282 | 1.581 | 1.5205 | 1.4613 | 1.4156 | 1.3389 | 1.2669 | 1.1948 | 0.9953 | 0.76574 | 0.49517
|  | KILLIN TOWN | ST |  |  |  | 1.8774 | 1.876 | 1.8528 | 1.836 | 1.8234 | 1.7877 | 1.7643 | 1.7036 | 1.6561 | 1.6048 | 1.5424 | 1.1905 | 0.97552 | 0.80978 | 2.0775 | 2.0652 | 2.0246 | 1.9885 | 1.9558 | 1.893 | 1.8531 | 1.7921 | 1.7457 | 1.6964 | 1.6381 | 1.3395 | 1.1482 | 0.9779 | 1.7479 | 1.7466 | 1.7183 | 1.6981 | 1.6659 | 1.6023 | 1.5567 | 1.4944 | 1.4486 | 1.3995 | 1.343 | 0.96853 | 0.73853 | 0.57306
|  | KILLIN TOWN | FS |  |  |  | 1.8778 | 1.8767 | 1.8707 | 1.8643 | 1.8568 | 1.849 | 1.8419 | 1.8221 | 1.7858 | 1.748 | 1.7063 | 1.4405 | 1.202 | 1.0716 | 2.0814 | 2.0723 | 2.054 | 2.0331 | 2.0102 | 1.9841 | 1.9584 | 1.9238 | 1.8905 | 1.8549 | 1.8161 | 1.6036 | 1.4098 | 1.2821 | 1.7483 | 1.7473 | 1.7403 | 1.7331 | 1.7245 | 1.6948 | 1.6662 | 1.6287 | 1.5947 | 1.5591 | 1.5199 | 1.299 | 1.0719 | 0.90899
| TAYNUILT | KILMELFORD | MINIMUM HEADROOM | NM 84056 14437 | YES | YES | -1.2798 | -1.3213 | -1.3715 | -1.4153 | -1.4662 | -1.5157 | -1.568 | -1.6067 | -1.6486 | -1.6934 | -1.7309 | -1.7966 | -1.8163 | -1.8289 | 0.025922 | 0.0010044 | -0.023748 | -0.054882 | -0.08049 | -0.10534 | -0.14059 | -0.17651 | -0.21545 | -0.25581 | -0.2916 | -0.3453 | -0.35506 | -0.37764 | -1.5105 | -1.5236 | -1.546 | -1.5629 | -1.586 | -1.6088 | -1.6311 | -1.6338 | -1.6354 | -1.641 | -1.6415 | -1.6509 | -1.6676 | -1.6788
|  | KILMELFORD | CT |  |  |  | -1.2581 | -1.293 | -1.3512 | -1.4144 | -1.4662 | -1.5157 | -1.5641 | -1.5936 | -1.6307 | -1.6734 | -1.7048 | -1.7671 | -1.807 | -1.8277 | 0.032995 | 0.012425 | -0.019926 | -0.054882 | -0.08049 | -0.10534 | -0.13012 | -0.1569 | -0.19298 | -0.23118 | -0.26297 | -0.33046 | -0.35506 | -0.37764 | -1.4996 | -1.5119 | -1.5357 | -1.5621 | -1.586 | -1.6088 | -1.6311 | -1.6338 | -1.6354 | -1.641 | -1.6415 | -1.6418 | -1.6622 | -1.6788
|  | KILMELFORD | LW |  |  |  | -1.2798 | -1.3213 | -1.3715 | -1.4153 | -1.4615 | -1.5138 | -1.568 | -1.6067 | -1.6486 | -1.6934 | -1.7309 | -1.7966 | -1.8163 | -1.8289 | 0.025922 | 0.0010044 | -0.023748 | -0.048113 | -0.071049 | -0.10386 | -0.14059 | -0.17651 | -0.21545 | -0.25581 | -0.2916 | -0.3453 | -0.35329 | -0.36141 | -1.5105 | -1.5236 | -1.546 | -1.5629 | -1.5836 | -1.6022 | -1.6196 | -1.6234 | -1.6276 | -1.6332 | -1.6357 | -1.6509 | -1.6676 | -1.6765
|  | KILMELFORD | ST |  |  |  | -1.2422 | -1.2592 | -1.2773 | -1.2976 | -1.318 | -1.3377 | -1.3603 | -1.3837 | -1.4128 | -1.4484 | -1.4795 | -1.6551 | -1.6979 | -1.7134 | 0.040035 | 0.029832 | 0.01908 | 0.0065455 | -0.006834 | -0.020943 | -0.037655 | -0.056891 | -0.080388 | -0.10782 | -0.13591 | -0.28128 | -0.31553 | -0.3332 | -1.4929 | -1.4955 | -1.4984 | -1.5041 | -1.5096 | -1.514 | -1.5187 | -1.5218 | -1.5276 | -1.5353 | -1.5381 | -1.5836 | -1.5987 | -1.6057
|  | KILMELFORD | FS |  |  |  | -1.2344 | -1.2502 | -1.2674 | -1.2866 | -1.3081 | -1.3245 | -1.3408 | -1.364 | -1.3823 | -1.4071 | -1.4321 | -1.5937 | -1.722 | -1.7492 | 0.042941 | 0.033623 | 0.023933 | 0.012935 | 0.0008258 | -0.01003 | -0.021956 | -0.037137 | -0.052277 | -0.070564 | -0.090161 | -0.21606 | -0.32434 | -0.35687 | -1.4926 | -1.495 | -1.4969 | -1.5012 | -1.5091 | -1.5129 | -1.5163 | -1.5231 | -1.5256 | -1.5315 | -1.5362 | -1.5739 | -1.5969 | -1.6087
| TAYNUILT | KILNINVER | MINIMUM HEADROOM | NM 83049 22251 | YES | YES | -0.9822 | -1.0224 | -1.0601 | -1.1079 | -1.1563 | -1.2035 | -1.2692 | -1.3271 | -1.3915 | -1.4579 | -1.5215 | -1.6238 | -1.6447 | -1.6687 | -0.30458 | -0.3302 | -0.3543 | -0.39131 | -0.4197 | -0.44822 | -0.49008 | -0.53629 | -0.58711 | -0.63949 | -0.68845 | -0.76633 | -0.7776 | -0.79416 | -0.43984 | -0.47927 | -0.51637 | -0.56288 | -0.61035 | -0.65668 | -0.72126 | -0.77813 | -0.84134 | -0.90667 | -0.96912 | -1.071 | -1.0926 | -1.1161
|  | KILNINVER | CT |  |  |  | -0.96791 | -0.9958 | -1.0522 | -1.1079 | -1.1563 | -1.2035 | -1.2502 | -1.2926 | -1.3503 | -1.4064 | -1.458 | -1.5679 | -1.6131 | -1.6355 | -0.2989 | -0.31845 | -0.3543 | -0.39131 | -0.4197 | -0.44822 | -0.47697 | -0.51056 | -0.55587 | -0.60118 | -0.64279 | -0.73499 | -0.7667 | -0.79416 | -0.42526 | -0.45281 | -0.50824 | -0.56288 | -0.61035 | -0.65668 | -0.7027 | -0.74447 | -0.80102 | -0.85605 | -0.90692 | -1.0154 | -1.0604 | -1.0834
|  | KILNINVER | LW |  |  |  | -0.9822 | -1.0224 | -1.0601 | -1.102 | -1.1413 | -1.2027 | -1.2692 | -1.3271 | -1.3915 | -1.4579 | -1.5215 | -1.6238 | -1.6447 | -1.6687 | -0.30458 | -0.3302 | -0.35315 | -0.3795 | -0.40321 | -0.44394 | -0.49008 | -0.53629 | -0.58711 | -0.63949 | -0.68845 | -0.76633 | -0.7776 | -0.79323 | -0.43984 | -0.47927 | -0.51637 | -0.55739 | -0.59604 | -0.65618 | -0.72126 | -0.77813 | -0.84134 | -0.90667 | -0.96912 | -1.071 | -1.0926 | -1.1161
|  | KILNINVER | ST |  |  |  | -0.9469 | -0.95716 | -0.9713 | -0.98733 | -1.0052 | -1.0279 | -1.0532 | -1.0863 | -1.1254 | -1.1683 | -1.2145 | -1.4497 | -1.5022 | -1.5192 | -0.28834 | -0.29554 | -0.30515 | -0.31698 | -0.33028 | -0.34696 | -0.36638 | -0.39084 | -0.42026 | -0.45329 | -0.48961 | -0.67689 | -0.72202 | -0.74376 | -0.40516 | -0.41554 | -0.42977 | -0.44578 | -0.46374 | -0.48627 | -0.51137 | -0.54398 | -0.58243 | -0.62464 | -0.67007 | -0.90312 | -0.95773 | -0.97612
|  | KILNINVER | FS |  |  |  | -0.94411 | -0.95291 | -0.96501 | -0.98088 | -0.99617 | -1.0152 | -1.0364 | -1.0581 | -1.0853 | -1.1155 | -1.1484 | -1.3629 | -1.5333 | -1.5764 | -0.28681 | -0.29299 | -0.30097 | -0.31141 | -0.32202 | -0.33505 | -0.35 | -0.36638 | -0.38612 | -0.40827 | -0.43279 | -0.5924 | -0.73153 | -0.77926 | -0.40238 | -0.41117 | -0.42345 | -0.43934 | -0.45473 | -0.47384 | -0.49486 | -0.51661 | -0.54347 | -0.57333 | -0.60581 | -0.81688 | -0.98458 | -1.028
| BEAULY | KILTARLITY | MINIMUM HEADROOM | NH 50271 41265 | YES | YES | 5.358 | 5.2959 | 5.215 | 5.1379 | 5.0552 | 4.9687 | 4.8701 | 4.8446 | 4.8139 | 4.7768 | 4.7461 | 4.6438 | 4.5571 | 4.5022 | 5.6177 | 5.5809 | 5.5419 | 5.4949 | 5.4497 | 5.4024 | 5.3446 | 5.2928 | 5.2386 | 5.1818 | 5.1312 | 5.0513 | 4.9897 | 4.9248 | 5.3049 | 5.256 | 5.19 | 5.1272 | 5.0589 | 4.987 | 4.903 | 4.8853 | 4.8295 | 4.7636 | 4.7058 | 4.6002 | 4.5381 | 4.495
|  | KILTARLITY | CT |  |  |  | 5.4187 | 5.3743 | 5.2737 | 5.166 | 5.0705 | 4.9705 | 4.8701 | 4.8486 | 4.8223 | 4.7955 | 4.7679 | 4.7017 | 4.5571 | 4.5022 | 5.637 | 5.6093 | 5.5545 | 5.4949 | 5.4497 | 5.4024 | 5.3547 | 5.3169 | 5.2636 | 5.2089 | 5.1613 | 5.0614 | 4.9897 | 4.9314 | 5.3537 | 5.3189 | 5.2359 | 5.1497 | 5.0703 | 4.987 | 4.903 | 4.8853 | 4.8577 | 4.7969 | 4.7438 | 4.6437 | 4.5381 | 4.495
|  | KILTARLITY | LW |  |  |  | 5.358 | 5.2959 | 5.215 | 5.1379 | 5.0552 | 4.9687 | 4.8787 | 4.8446 | 4.8139 | 4.7768 | 4.7461 | 4.6438 | 4.5726 | 4.5429 | 5.6177 | 5.5809 | 5.5419 | 5.5007 | 5.462 | 5.4065 | 5.3446 | 5.2928 | 5.2386 | 5.1818 | 5.1312 | 5.0513 | 5.026 | 5.0143 | 5.3049 | 5.256 | 5.19 | 5.1272 | 5.0589 | 4.988 | 4.9147 | 4.887 | 4.8295 | 4.7636 | 4.7058 | 4.6002 | 4.5489 | 4.5267
|  | KILTARLITY | ST |  |  |  | 5.4395 | 5.4126 | 5.375 | 5.3435 | 5.3035 | 5.2656 | 5.222 | 5.1801 | 5.1334 | 5.0843 | 5.031 | 4.7971 | 4.6723 | 4.592 | 5.6467 | 5.6329 | 5.6142 | 5.5945 | 5.5714 | 5.5461 | 5.5162 | 5.4831 | 5.4439 | 5.4003 | 5.352 | 5.1103 | 5.0285 | 4.9693 | 5.3725 | 5.3515 | 5.322 | 5.2963 | 5.2635 | 5.2319 | 5.1959 | 5.1624 | 5.1253 | 5.086 | 5.0383 | 4.7389 | 4.6346 | 4.5798
|  | KILTARLITY | FS |  |  |  | 5.4629 | 5.4462 | 5.4132 | 5.3852 | 5.3526 | 5.3191 | 5.2863 | 5.2465 | 5.2053 | 5.1589 | 5.117 | 4.8092 | 4.6262 | 4.5485 | 5.6541 | 5.6439 | 5.6279 | 5.6114 | 5.5931 | 5.5728 | 5.5507 | 5.5241 | 5.4947 | 5.4615 | 5.4273 | 5.1956 | 5.0067 | 4.9248 | 5.3895 | 5.3762 | 5.3507 | 5.3291 | 5.3022 | 5.2742 | 5.2471 | 5.2144 | 5.1807 | 5.1428 | 5.1086 | 4.8139 | 4.6008 | 4.551
| REDMOSS | KINCORTH | MINIMUM HEADROOM | NJ 94445 03252 | NO | YES | 4.7343 | 4.4593 | 3.6555 | 2.7506 | 1.5669 | 0.66966 | -0.21373 | -0.81132 | -1.4492 | -2.113 | -2.7557 | -4.555 | -5.4148 | -6.4581 | 5.6415 | 5.5377 | 5.0458 | 4.4491 | 3.4302 | 2.8134 | 2.3134 | 2.0165 | 1.6451 | 1.1943 | 0.74093 | -0.56981 | -1.6935 | -3.2243 | 5.1511 | 4.9736 | 4.3223 | 3.5745 | 2.4827 | 1.6534 | 0.83316 | 0.25721 | -0.35881 | -0.99796 | -1.6148 | -3.3446 | -4.2726 | -5.5057
|  | KINCORTH | CT |  |  |  | 5.0375 | 4.8759 | 4.0989 | 3.1679 | 1.9831 | 1.1496 | 0.44971 | -0.15079 | -0.74797 | -1.3363 | -1.9405 | -4.173 | -5.3249 | -5.9805 | 5.6948 | 5.6016 | 5.1114 | 4.4739 | 3.4302 | 2.8134 | 2.3368 | 2.048 | 1.7823 | 1.4242 | 1.0299 | -0.56981 | -1.6935 | -2.963 | 5.3452 | 5.2275 | 4.6004 | 3.8352 | 2.7271 | 1.9945 | 1.3967 | 0.82902 | 0.26026 | -0.29886 | -0.87424 | -2.9815 | -4.084 | -4.7608
|  | KINCORTH | LW |  |  |  | 4.7343 | 4.4593 | 3.6555 | 2.7506 | 1.5669 | 0.66966 | -0.21373 | -0.81132 | -1.4492 | -2.113 | -2.7557 | -4.555 | -5.4148 | -6.4581 | 5.6415 | 5.5377 | 5.0458 | 4.4491 | 3.445 | 2.8477 | 2.3134 | 2.0165 | 1.6451 | 1.1943 | 0.74093 | -0.4787 | -1.2746 | -2.4306 | 5.1511 | 4.9736 | 4.3223 | 3.5745 | 2.4827 | 1.6534 | 0.83316 | 0.25721 | -0.35881 | -0.99796 | -1.6148 | -3.3446 | -4.2726 | -5.5057
|  | KINCORTH | ST |  |  |  | 5.1254 | 5.0629 | 4.6778 | 4.154 | 3.3356 | 2.8454 | 2.4498 | 2.1231 | 1.8376 | 1.4612 | 1.0208 | -1.4118 | -2.7368 | -4.0552 | 5.7382 | 5.7052 | 5.3119 | 4.7776 | 3.8483 | 3.3112 | 2.901 | 2.6297 | 2.4211 | 2.2028 | 1.9507 | 0.096743 | -1.0644 | -2.6754 | 5.4142 | 5.3747 | 5.0009 | 4.4959 | 3.6533 | 3.1568 | 2.7747 | 2.489 | 2.2653 | 2.0241 | 1.7008 | -0.66742 | -1.9966 | -3.2489
|  | KINCORTH | FS |  |  |  | 5.2295 | 5.1728 | 4.8649 | 4.4396 | 3.8182 | 3.452 | 3.1047 | 2.8091 | 2.4633 | 2.1357 | 1.8602 | 0.02294 | -2.0315 | -3.5041 | 5.7672 | 5.737 | 5.4486 | 5.0341 | 4.3419 | 3.951 | 3.585 | 3.3605 | 3.089 | 2.8425 | 2.6658 | 1.417 | -0.7375 | -3.2243 | 5.4815 | 5.4476 | 5.1658 | 4.7694 | 4.1385 | 3.7794 | 3.4433 | 3.1996 | 2.9123 | 2.6495 | 2.4478 | 0.86868 | -1.0775 | -2.3818
| FORT WILLIAM | KINGAIRLOCH | MINIMUM HEADROOM | NM 76917 56652 | YES | YES | 0.05245 | 0.051465 | 0.050095 | 0.04912 | 0.048147 | 0.045701 | 0.040693 | 0.034611 | 0.027882 | 0.020794 | 0.014209 | 0.0016387 | -0.0038154 | -0.0040558 | 0.062508 | 0.061893 | 0.060986 | 0.060174 | 0.059416 | 0.057316 | 0.053379 | 0.048857 | 0.043854 | 0.038422 | 0.033241 | 0.023349 | 0.019036 | 0.018817 | 0.053784 | 0.051511 | 0.04833 | 0.046113 | 0.043754 | 0.04119 | 0.036373 | 0.030632 | 0.024163 | 0.01735 | 0.01102 | -0.0010587 | -0.0062952 | -0.0065257
|  | KINGAIRLOCH | CT |  |  |  | 0.05245 | 0.051465 | 0.050095 | 0.04912 | 0.048147 | 0.045701 | 0.042906 | 0.038673 | 0.035347 | 0.032019 | 0.026913 | 0.013201 | 0.012835 | 0.012788 | 0.062508 | 0.061899 | 0.060986 | 0.060174 | 0.059416 | 0.057316 | 0.05502 | 0.05187 | 0.049377 | 0.046881 | 0.043081 | 0.032432 | 0.03213 | 0.032072 | 0.053784 | 0.051511 | 0.04833 | 0.046113 | 0.043754 | 0.04119 | 0.038386 | 0.034536 | 0.031337 | 0.028135 | 0.023226 | 0.010047 | 0.0096973 | 0.0096533
|  | KINGAIRLOCH | LW |  |  |  | 0.052618 | 0.05157 | 0.050753 | 0.049801 | 0.048831 | 0.045804 | 0.040693 | 0.034611 | 0.027882 | 0.020794 | 0.014209 | 0.0016387 | 0.0015977 | 0.0015758 | 0.062569 | 0.061893 | 0.061351 | 0.060709 | 0.060125 | 0.057408 | 0.053379 | 0.048857 | 0.043854 | 0.038422 | 0.033241 | 0.023349 | 0.023313 | 0.023292 | 0.054235 | 0.051858 | 0.050015 | 0.047781 | 0.045405 | 0.041296 | 0.036373 | 0.030632 | 0.024163 | 0.01735 | 0.01102 | -0.0010587 | -0.0010953 | -0.0011137
|  | KINGAIRLOCH | ST |  |  |  | 0.053034 | 0.052721 | 0.052301 | 0.05176 | 0.051086 | 0.050242 | 0.049201 | 0.047589 | 0.043831 | 0.038965 | 0.033393 | 0.0042927 | -0.0038154 | -0.0039515 | 0.06278 | 0.062557 | 0.06227 | 0.061893 | 0.061449 | 0.060898 | 0.060227 | 0.058887 | 0.055741 | 0.052095 | 0.047957 | 0.025428 | 0.019036 | 0.018908 | 0.05505 | 0.054481 | 0.053525 | 0.052298 | 0.050756 | 0.04878 | 0.046239 | 0.043113 | 0.039272 | 0.034819 | 0.029464 | 0.0014934 | -0.0062952 | -0.0064237
|  | KINGAIRLOCH | FS |  |  |  | 0.053108 | 0.052856 | 0.05254 | 0.05215 | 0.051688 | 0.051134 | 0.050476 | 0.049707 | 0.048812 | 0.047424 | 0.044726 | 0.024757 | 0.006682 | -0.0040558 | 0.062814 | 0.062621 | 0.062394 | 0.062107 | 0.061785 | 0.061399 | 0.060942 | 0.06041 | 0.059792 | 0.058754 | 0.056497 | 0.041507 | 0.02729 | 0.018817 | 0.055096 | 0.054793 | 0.054077 | 0.053202 | 0.052153 | 0.050894 | 0.049398 | 0.047547 | 0.045389 | 0.042955 | 0.040199 | 0.02116 | 0.0037864 | -0.0065257
| DYCE | KINGSEAT | MINIMUM HEADROOM | NJ 89545 19709 | NO | YES | 2.7345 | 2.5322 | 2.2233 | 9.4831 | 9.1964 | 8.7653 | 8.2988 | 7.7607 | 7.4469 | 7.1142 | 6.7952 | 6.0159 | 5.3583 | 4.9641 | 3.7854 | 3.6814 | 3.5286 | 10.6888 | 10.5002 | 10.2102 | 9.9664 | 9.5805 | 9.3357 | 9.092 | 8.8625 | 8.1749 | 7.6576 | 7.1159 | 3.0748 | 2.8896 | 2.6165 | 9.6549 | 9.3985 | 9.0037 | 8.5724 | 8.0616 | 7.7621 | 7.4456 | 7.1256 | 6.329 | 5.7319 | 5.3484
|  | KINGSEAT | CT |  |  |  | 2.912 | 2.7783 | 2.4269 | 9.6375 | 9.3081 | 8.8886 | 8.4974 | 7.989 | 7.6379 | 7.2881 | 6.9578 | 6.0159 | 5.3583 | 4.9641 | 3.8509 | 3.772 | 3.5815 | 10.6978 | 10.5002 | 10.2102 | 9.9664 | 9.5805 | 9.3357 | 9.092 | 8.8625 | 8.1749 | 7.6576 | 7.1159 | 3.2314 | 3.1076 | 2.7897 | 9.7768 | 9.4655 | 9.0702 | 8.7099 | 8.2277 | 7.8916 | 7.5576 | 7.2404 | 6.329 | 5.7319 | 5.3484
|  | KINGSEAT | LW |  |  |  | 2.7345 | 2.5322 | 2.2233 | 9.4831 | 9.1964 | 8.7653 | 8.2988 | 7.7607 | 7.4469 | 7.1142 | 6.7952 | 6.0194 | 5.5456 | 5.1253 | 3.7854 | 3.6814 | 3.5286 | 10.6888 | 10.5533 | 10.2835 | 9.9997 | 9.5881 | 9.3781 | 9.157 | 8.9426 | 8.4511 | 8.0996 | 7.6926 | 3.0748 | 2.8896 | 2.6165 | 9.6549 | 9.3985 | 9.0037 | 8.5724 | 8.0616 | 7.7621 | 7.4456 | 7.1256 | 6.3914 | 5.9246 | 5.4596
|  | KINGSEAT | ST |  |  |  | 3.0085 | 2.939 | 2.7742 | 10.1944 | 10.0641 | 9.8005 | 9.5685 | 9.1545 | 8.9499 | 8.7344 | 8.4993 | 7.2785 | 6.5749 | 5.9363 | 3.8946 | 3.8554 | 3.7337 | 10.9413 | 10.8538 | 10.6178 | 10.4356 | 10.0829 | 9.935 | 9.7691 | 9.5822 | 8.6311 | 8.018 | 7.3586 | 3.3181 | 3.2556 | 3.098 | 10.2718 | 10.1478 | 9.8867 | 9.6653 | 9.2618 | 9.064 | 8.8561 | 8.6136 | 7.3634 | 6.6937 | 6.1112
|  | KINGSEAT | FS |  |  |  | 3.049 | 2.9986 | 2.8882 | 10.3346 | 10.234 | 10.0749 | 9.8966 | 9.5756 | 9.4013 | 9.2107 | 9.014 | 7.8524 | 6.8737 | 6.3484 | 3.9122 | 3.881 | 3.8107 | 11.046 | 10.981 | 10.8561 | 10.7183 | 10.4598 | 10.3374 | 10.2021 | 10.056 | 9.2133 | 8.3196 | 7.5291 | 3.3541 | 3.3088 | 3.21 | 10.4145 | 10.3208 | 10.1733 | 10.0057 | 9.701 | 9.537 | 9.3571 | 9.1705 | 8.0588 | 7.1086 | 6.6601
| BOAT OF GARTEN | KINGUSSIE | MINIMUM HEADROOM | NH 75429 00426 | NO | YES | 1.6558 | 1.4485 | 1.168 | 0.8714 | 0.51621 | 0.074228 | -0.34295 | -0.61211 | -0.88171 | -1.1782 | -1.4213 | -2.0011 | -2.2251 | -2.3462 | 3.7321 | 3.5963 | 3.3897 | 3.1657 | 2.867 | 2.4921 | 2.1637 | 1.9458 | 1.7211 | 1.4928 | 1.2949 | 0.86612 | 0.75938 | 0.68855 | 2.3062 | 2.1268 | 1.8636 | 1.586 | 1.2225 | 0.79118 | 0.40546 | 0.18739 | -0.034312 | -0.27721 | -0.51192 | -1.1257 | -1.3639 | -1.5542
|  | KINGUSSIE | CT |  |  |  | 1.7657 | 1.6102 | 1.3227 | 1.0138 | 0.6865 | 0.33226 | 0.026512 | -0.19493 | -0.45254 | -0.7156 | -0.93041 | -1.4852 | -1.8558 | -1.9898 | 3.7788 | 3.6683 | 3.4775 | 3.2695 | 3.0233 | 2.754 | 2.5521 | 2.3809 | 2.1859 | 1.9899 | 1.822 | 1.3687 | 1.1515 | 0.97854 | 2.3891 | 2.2324 | 1.986 | 1.7241 | 1.3929 | 1.0295 | 0.73117 | 0.53681 | 0.36404 | 0.19371 | 0.00036517 | -0.61655 | -0.83925 | -0.91798
|  | KINGUSSIE | LW |  |  |  | 1.6558 | 1.4485 | 1.168 | 0.8714 | 0.51621 | 0.074228 | -0.34295 | -0.61211 | -0.88171 | -1.1782 | -1.4213 | -2.0011 | -2.2251 | -2.3462 | 3.7321 | 3.5963 | 3.3897 | 3.1657 | 2.867 | 2.4921 | 2.1637 | 1.9458 | 1.7211 | 1.4928 | 1.2949 | 0.86612 | 0.75938 | 0.68855 | 2.3062 | 2.1268 | 1.8636 | 1.586 | 1.2225 | 0.79118 | 0.40546 | 0.18739 | -0.034312 | -0.27721 | -0.51192 | -1.1257 | -1.2866 | -1.3658
|  | KINGUSSIE | ST |  |  |  | 1.8592 | 1.7729 | 1.6035 | 1.4472 | 1.2976 | 1.0608 | 0.87509 | 0.68934 | 0.49511 | 0.27747 | 0.057486 | -1.1016 | -1.5698 | -1.7903 | 3.8326 | 3.7759 | 3.6283 | 3.4971 | 3.3754 | 3.153 | 3.0001 | 2.8589 | 2.7026 | 2.5254 | 2.3394 | 1.391 | 1.0465 | 0.83927 | 2.4835 | 2.4102 | 2.2387 | 2.0822 | 1.9284 | 1.6683 | 1.4707 | 1.2797 | 1.0646 | 0.81884 | 0.55297 | -0.82795 | -1.3639 | -1.5542
|  | KINGUSSIE | FS |  |  |  | 1.8977 | 1.8302 | 1.7195 | 1.606 | 1.4844 | 1.3552 | 1.2145 | 1.068 | 0.92047 | 0.76236 | 0.60568 | -0.42764 | -1.2896 | -1.6616 | 3.8535 | 3.8078 | 3.73 | 3.6476 | 3.5572 | 3.4585 | 3.3518 | 3.2468 | 3.1366 | 3.016 | 2.8917 | 2.0792 | 1.3505 | 0.8994 | 2.5172 | 2.463 | 2.3665 | 2.2653 | 2.1521 | 2.0301 | 1.8971 | 1.7647 | 1.6236 | 1.4698 | 1.3068 | 0.22852 | -0.67273 | -1.2197
| TAYNUILT | KINLOCH | MINIMUM HEADROOM | NM 52465 27215 | YES | YES | -0.41582 | -0.4381 | -0.46757 | -0.51197 | -0.55381 | -0.59475 | -0.63827 | -0.6541 | -0.6679 | -0.68537 | -0.7023 | -0.73643 | -0.77471 | -0.7847 | -0.18725 | -0.20797 | -0.23198 | -0.26764 | -0.29436 | -0.32139 | -0.34935 | -0.38281 | -0.42081 | -0.46019 | -0.49641 | -0.55072 | -0.58118 | -0.60623 | -0.59719 | -0.61352 | -0.63941 | -0.67106 | -0.69983 | -0.7283 | -0.75881 | -0.77447 | -0.78877 | -0.80554 | -0.82273 | -0.85933 | -0.88393 | -0.89468
|  | KINLOCH | CT |  |  |  | -0.40285 | -0.42225 | -0.46757 | -0.51197 | -0.55381 | -0.59475 | -0.63827 | -0.6541 | -0.6679 | -0.68537 | -0.7023 | -0.73511 | -0.77471 | -0.7847 | -0.18047 | -0.19802 | -0.23198 | -0.26764 | -0.29436 | -0.32139 | -0.34935 | -0.37658 | -0.41336 | -0.45207 | -0.48485 | -0.55072 | -0.58118 | -0.60623 | -0.59123 | -0.60737 | -0.63941 | -0.67106 | -0.69983 | -0.7283 | -0.75881 | -0.77447 | -0.78877 | -0.80554 | -0.82273 | -0.85933 | -0.88393 | -0.88971
|  | KINLOCH | LW |  |  |  | -0.41582 | -0.4381 | -0.46704 | -0.49767 | -0.52884 | -0.56565 | -0.60713 | -0.62932 | -0.6486 | -0.67077 | -0.69255 | -0.73643 | -0.75992 | -0.76531 | -0.18725 | -0.20797 | -0.22899 | -0.25274 | -0.2738 | -0.30746 | -0.34637 | -0.38281 | -0.42081 | -0.46019 | -0.49641 | -0.55059 | -0.56379 | -0.56592 | -0.59719 | -0.61352 | -0.63296 | -0.65402 | -0.67515 | -0.70215 | -0.73311 | -0.75366 | -0.773 | -0.79465 | -0.81546 | -0.85639 | -0.87178 | -0.87467
|  | KINLOCH | ST |  |  |  | -0.38067 | -0.38907 | -0.39833 | -0.40754 | -0.41785 | -0.42842 | -0.44241 | -0.4606 | -0.48299 | -0.50821 | -0.53273 | -0.65587 | -0.69187 | -0.71701 | -0.17105 | -0.17814 | -0.18691 | -0.19755 | -0.20925 | -0.22284 | -0.2396 | -0.26036 | -0.28587 | -0.31482 | -0.346 | -0.50826 | -0.54944 | -0.57174 | -0.57553 | -0.58133 | -0.58791 | -0.595 | -0.60318 | -0.61217 | -0.62394 | -0.63928 | -0.65814 | -0.67976 | -0.70184 | -0.8134 | -0.84238 | -0.85172
|  | KINLOCH | FS |  |  |  | -0.37844 | -0.38323 | -0.39285 | -0.40048 | -0.41157 | -0.42049 | -0.4322 | -0.44668 | -0.46253 | -0.47969 | -0.49243 | -0.62268 | -0.72168 | -0.76861 | -0.16963 | -0.17485 | -0.18275 | -0.19136 | -0.20137 | -0.21201 | -0.22469 | -0.23997 | -0.25734 | -0.27669 | -0.29616 | -0.43662 | -0.55902 | -0.59825 | -0.57391 | -0.57733 | -0.5837 | -0.58921 | -0.597 | -0.60374 | -0.61269 | -0.62375 | -0.63614 | -0.64979 | -0.66138 | -0.76698 | -0.85359 | -0.89468
| TUMMEL BRIDGE | KINLOCH RANNOCH | MINIMUM HEADROOM | NN 65927 58500 | YES | YES | -0.057943 | -0.08553 | -0.10997 | -0.1415 | -0.17634 | -0.21383 | -0.25548 | -0.26788 | -0.28373 | -0.30164 | -0.3214 | -0.36633 | -0.38109 | -0.39371 | 0.37799 | 0.36399 | 0.35185 | 0.33151 | 0.31464 | 0.29633 | 0.27662 | 0.26502 | 0.2498 | 0.23087 | 0.21398 | 0.18036 | 0.17251 | 0.15413 | 0.14171 | 0.13862 | 0.13488 | 0.13019 | 0.12711 | 0.12376 | 0.11952 | 0.11268 | 0.10527 | 0.097648 | 0.090657 | 0.079252 | 0.074746 | 0.073903
|  | KINLOCH RANNOCH | CT |  |  |  | -0.039737 | -0.059948 | -0.09976 | -0.14149 | -0.17634 | -0.21383 | -0.25548 | -0.26788 | -0.28373 | -0.30164 | -0.31587 | -0.34402 | -0.37926 | -0.39371 | 0.38446 | 0.37308 | 0.35286 | 0.33151 | 0.31464 | 0.29633 | 0.27662 | 0.26502 | 0.25003 | 0.2342 | 0.22081 | 0.18965 | 0.17251 | 0.16154 | 0.14199 | 0.1392 | 0.13488 | 0.13019 | 0.12711 | 0.12376 | 0.12044 | 0.11535 | 0.10844 | 0.1014 | 0.095373 | 0.081835 | 0.07981 | 0.078428
|  | KINLOCH RANNOCH | LW |  |  |  | -0.057943 | -0.08553 | -0.10997 | -0.1415 | -0.16821 | -0.1978 | -0.23691 | -0.25946 | -0.27815 | -0.30149 | -0.3214 | -0.36633 | -0.38109 | -0.38745 | 0.37799 | 0.36399 | 0.35185 | 0.33655 | 0.32354 | 0.30617 | 0.28419 | 0.26675 | 0.2498 | 0.23087 | 0.21398 | 0.18036 | 0.17255 | 0.16953 | 0.14171 | 0.13862 | 0.13605 | 0.13298 | 0.13042 | 0.12542 | 0.11952 | 0.11268 | 0.10527 | 0.097648 | 0.090657 | 0.079252 | 0.077649 | 0.077128
|  | KINLOCH RANNOCH | ST |  |  |  | -0.021708 | -0.028823 | -0.040329 | -0.05081 | -0.059314 | -0.070394 | -0.0886 | -0.10525 | -0.12391 | -0.14827 | -0.17157 | -0.29091 | -0.33856 | -0.36413 | 0.39208 | 0.38813 | 0.38217 | 0.37596 | 0.36999 | 0.36243 | 0.35158 | 0.34024 | 0.32695 | 0.31061 | 0.29361 | 0.20452 | 0.17413 | 0.1598 | 0.1428 | 0.14186 | 0.14058 | 0.13886 | 0.13688 | 0.13444 | 0.13148 | 0.12779 | 0.12327 | 0.11805 | 0.11216 | 0.081455 | 0.074746 | 0.073903
|  | KINLOCH RANNOCH | FS |  |  |  | -0.015587 | -0.021799 | -0.030853 | -0.042181 | -0.048544 | -0.06298 | -0.072609 | -0.085378 | -0.10131 | -0.11756 | -0.13212 | -0.25205 | -0.33837 | -0.38011 | 0.39454 | 0.3912 | 0.38657 | 0.38071 | 0.37641 | 0.36886 | 0.36256 | 0.35458 | 0.34495 | 0.33465 | 0.32432 | 0.2478 | 0.18342 | 0.15413 | 0.14302 | 0.14227 | 0.14129 | 0.14001 | 0.13862 | 0.13696 | 0.13499 | 0.13262 | 0.12986 | 0.12673 | 0.12319 | 0.10023 | 0.079442 | 0.074893
| GRUDIE BRIDGE | KINLOCHEWE | MINIMUM HEADROOM | NH 03723 62321 | YES | YES | 0.40741 | 0.38735 | 0.36924 | 0.34798 | 0.32465 | 0.30051 | 0.26959 | 0.25105 | 0.22774 | 0.20378 | 0.18396 | 0.14683 | 0.12142 | 0.10866 | 0.52654 | 0.51557 | 0.50597 | 0.49244 | 0.48065 | 0.46732 | 0.45062 | 0.43605 | 0.41911 | 0.40156 | 0.38495 | 0.35986 | 0.34117 | 0.32724 | 0.45528 | 0.43677 | 0.42013 | 0.40057 | 0.37939 | 0.35674 | 0.32787 | 0.30753 | 0.2828 | 0.25741 | 0.236 | 0.1996 | 0.17772 | 0.16604
|  | KINLOCHEWE | CT |  |  |  | 0.4194 | 0.40661 | 0.37801 | 0.35149 | 0.32866 | 0.30213 | 0.27724 | 0.26175 | 0.23735 | 0.21951 | 0.19849 | 0.15752 | 0.12142 | 0.10866 | 0.53079 | 0.52293 | 0.50737 | 0.49244 | 0.48065 | 0.46732 | 0.45458 | 0.4429 | 0.42576 | 0.41083 | 0.39476 | 0.36073 | 0.34117 | 0.32724 | 0.46585 | 0.45388 | 0.42753 | 0.40295 | 0.38211 | 0.35798 | 0.3353 | 0.31981 | 0.29413 | 0.27363 | 0.25149 | 0.20938 | 0.17772 | 0.16604
|  | KINLOCHEWE | LW |  |  |  | 0.40741 | 0.38735 | 0.36924 | 0.34798 | 0.32465 | 0.30051 | 0.26959 | 0.25105 | 0.22774 | 0.20378 | 0.18396 | 0.14683 | 0.12764 | 0.12298 | 0.52654 | 0.51557 | 0.50597 | 0.49465 | 0.48327 | 0.4687 | 0.45062 | 0.43605 | 0.41911 | 0.40156 | 0.38495 | 0.35986 | 0.35202 | 0.35032 | 0.45528 | 0.43677 | 0.42013 | 0.40057 | 0.37939 | 0.35674 | 0.32787 | 0.30753 | 0.2828 | 0.25741 | 0.236 | 0.1996 | 0.18283 | 0.17899
|  | KINLOCHEWE | ST |  |  |  | 0.43465 | 0.42645 | 0.41937 | 0.41074 | 0.40202 | 0.38837 | 0.3806 | 0.36584 | 0.34794 | 0.33181 | 0.31198 | 0.21754 | 0.18893 | 0.17542 | 0.53776 | 0.53357 | 0.52945 | 0.52424 | 0.51876 | 0.51095 | 0.50473 | 0.4952 | 0.48361 | 0.47195 | 0.45826 | 0.3875 | 0.36689 | 0.35413 | 0.47244 | 0.47107 | 0.46555 | 0.4575 | 0.44932 | 0.43668 | 0.42815 | 0.41345 | 0.39566 | 0.37878 | 0.35847 | 0.26327 | 0.23675 | 0.22491
|  | KINLOCHEWE | FS |  |  |  | 0.43728 | 0.43287 | 0.42265 | 0.41726 | 0.40756 | 0.39898 | 0.38818 | 0.37591 | 0.36493 | 0.35078 | 0.33796 | 0.24238 | 0.17111 | 0.15169 | 0.5389 | 0.53623 | 0.53124 | 0.52766 | 0.52237 | 0.51715 | 0.51075 | 0.50338 | 0.49603 | 0.48708 | 0.47817 | 0.41583 | 0.36038 | 0.3408 | 0.47296 | 0.47186 | 0.4686 | 0.46351 | 0.45461 | 0.44661 | 0.43658 | 0.42475 | 0.41365 | 0.39969 | 0.38655 | 0.29166 | 0.22142 | 0.20407
| KINLOCHLEVEN | KINLOCHLEVEN | MINIMUM HEADROOM | NN 19285 62002 | NO | YES | 2.3154 | 2.3132 | 2.2901 | 2.2256 | 2.1307 | 2.0357 | 1.9449 | 1.9227 | 1.899 | 1.8769 | 1.853 | 1.8014 | 1.6977 | 1.6158 | 2.4481 | 2.4257 | 2.3653 | 2.3288 | 2.275 | 2.221 | 2.1771 | 2.1514 | 2.1194 | 2.0825 | 2.047 | 1.9533 | 1.8674 | 1.7768 | 2.1285 | 2.1264 | 2.0768 | 2.029 | 1.9558 | 1.8745 | 1.7903 | 1.763 | 1.7325 | 1.7033 | 1.6734 | 1.6221 | 1.5158 | 1.4409
|  | KINLOCHLEVEN | CT |  |  |  | 2.3163 | 2.3145 | 2.2914 | 2.2281 | 2.1307 | 2.0357 | 1.9449 | 1.9227 | 1.899 | 1.8769 | 1.853 | 1.8014 | 1.6977 | 1.6264 | 2.4598 | 2.4434 | 2.3777 | 2.3288 | 2.275 | 2.221 | 2.1771 | 2.1514 | 2.1194 | 2.0825 | 2.047 | 1.9533 | 1.8674 | 1.7768 | 2.1293 | 2.1276 | 2.1051 | 2.0348 | 1.9558 | 1.8745 | 1.7903 | 1.763 | 1.7325 | 1.7033 | 1.6734 | 1.6221 | 1.5158 | 1.4435
|  | KINLOCHLEVEN | LW |  |  |  | 2.3154 | 2.3132 | 2.2901 | 2.2256 | 2.1548 | 2.0782 | 2.001 | 1.9761 | 1.9509 | 1.9273 | 1.8945 | 1.8156 | 1.7191 | 1.6158 | 2.4481 | 2.4257 | 2.3653 | 2.3331 | 2.2991 | 2.2597 | 2.2189 | 2.1881 | 2.1518 | 2.1156 | 2.0814 | 2.017 | 1.9372 | 1.8312 | 2.1285 | 2.1264 | 2.0768 | 2.029 | 1.9762 | 1.9205 | 1.8465 | 1.8162 | 1.7849 | 1.7549 | 1.7245 | 1.6612 | 1.5567 | 1.4409
|  | KINLOCHLEVEN | ST |  |  |  | 2.3195 | 2.3193 | 2.2917 | 2.2831 | 2.2767 | 2.2586 | 2.2525 | 2.2376 | 2.2315 | 2.2255 | 2.2174 | 2.0342 | 1.9541 | 1.8697 | 2.4766 | 2.4707 | 2.4282 | 2.4091 | 2.3909 | 2.3567 | 2.3356 | 2.3002 | 2.2731 | 2.243 | 2.2093 | 2.036 | 1.9387 | 1.8329 | 2.1322 | 2.1319 | 2.1023 | 2.0919 | 2.0844 | 2.0623 | 2.0551 | 2.0373 | 2.0301 | 2.0232 | 2.0022 | 1.8715 | 1.7803 | 1.6818
|  | KINLOCHLEVEN | FS |  |  |  | 2.3197 | 2.3194 | 2.3038 | 2.2987 | 2.295 | 2.2894 | 2.2864 | 2.2804 | 2.2733 | 2.2674 | 2.2627 | 2.0894 | 1.9542 | 1.9066 | 2.478 | 2.4724 | 2.4431 | 2.4271 | 2.4124 | 2.3941 | 2.3778 | 2.3558 | 2.331 | 2.3065 | 2.2809 | 2.1351 | 1.9951 | 1.8791 | 2.1323 | 2.132 | 2.1163 | 2.1108 | 2.1066 | 2.1004 | 2.0969 | 2.0898 | 2.0763 | 2.0543 | 2.0309 | 1.9082 | 1.805 | 1.7572
| FORT WILLIAM | KINLOCHMOIDART | MINIMUM HEADROOM | NM 71407 72091 | YES | YES | 0.94352 | 0.9421 | 0.94067 | 0.93861 | 0.93735 | 0.93603 | 0.93341 | 0.93027 | 0.92688 | 0.92344 | 0.92033 | 0.9164 | 0.91611 | 0.91576 | 0.95971 | 0.95865 | 0.95752 | 0.9559 | 0.95491 | 0.95388 | 0.95182 | 0.94935 | 0.94669 | 0.94398 | 0.94154 | 0.93843 | 0.9382 | 0.93796 | 0.95271 | 0.95129 | 0.94988 | 0.94782 | 0.94657 | 0.94526 | 0.94265 | 0.93953 | 0.93617 | 0.93274 | 0.92965 | 0.92575 | 0.92545 | 0.9251
|  | KINLOCHMOIDART | CT |  |  |  | 0.94369 | 0.94258 | 0.94067 | 0.93861 | 0.93735 | 0.93603 | 0.93471 | 0.9324 | 0.92906 | 0.92564 | 0.92276 | 0.91719 | 0.91637 | 0.91576 | 0.95981 | 0.95903 | 0.95752 | 0.9559 | 0.95491 | 0.95388 | 0.95284 | 0.95102 | 0.94841 | 0.94573 | 0.94346 | 0.93908 | 0.93843 | 0.93796 | 0.95288 | 0.95178 | 0.94988 | 0.94782 | 0.94657 | 0.94526 | 0.94395 | 0.94165 | 0.93833 | 0.93493 | 0.93206 | 0.92652 | 0.9257 | 0.9251
|  | KINLOCHMOIDART | LW |  |  |  | 0.94352 | 0.9421 | 0.94092 | 0.9395 | 0.93839 | 0.93611 | 0.93341 | 0.93027 | 0.92688 | 0.92344 | 0.92033 | 0.9164 | 0.91611 | 0.91611 | 0.95971 | 0.95865 | 0.95772 | 0.95661 | 0.95574 | 0.95394 | 0.95182 | 0.94935 | 0.94669 | 0.94398 | 0.94154 | 0.93843 | 0.9382 | 0.9382 | 0.95271 | 0.95129 | 0.95012 | 0.94871 | 0.94761 | 0.94534 | 0.94265 | 0.93953 | 0.93617 | 0.93274 | 0.92965 | 0.92575 | 0.92545 | 0.92545
|  | KINLOCHMOIDART | ST |  |  |  | 0.94402 | 0.94363 | 0.94309 | 0.94235 | 0.94153 | 0.94051 | 0.93928 | 0.93773 | 0.93583 | 0.93365 | 0.93121 | 0.91872 | 0.91672 | 0.91666 | 0.96006 | 0.95979 | 0.95942 | 0.95885 | 0.9582 | 0.9574 | 0.95643 | 0.95521 | 0.95371 | 0.952 | 0.95008 | 0.94025 | 0.93866 | 0.93861 | 0.95321 | 0.95281 | 0.95228 | 0.95154 | 0.95073 | 0.94972 | 0.94849 | 0.94695 | 0.94506 | 0.94289 | 0.94047 | 0.92805 | 0.92607 | 0.92601
|  | KINLOCHMOIDART | FS |  |  |  | 0.94409 | 0.94377 | 0.94334 | 0.94277 | 0.94217 | 0.94144 | 0.94058 | 0.93952 | 0.9383 | 0.93691 | 0.93536 | 0.92546 | 0.91705 | 0.91665 | 0.96011 | 0.95989 | 0.9596 | 0.95918 | 0.95871 | 0.95813 | 0.95745 | 0.95663 | 0.95566 | 0.95457 | 0.95335 | 0.94557 | 0.93895 | 0.9386 | 0.95328 | 0.95295 | 0.95253 | 0.95196 | 0.95136 | 0.95064 | 0.94978 | 0.94873 | 0.94751 | 0.94613 | 0.94459 | 0.93475 | 0.92639 | 0.926
| ELGIN | KINLOSS | MINIMUM HEADROOM | NJ 06695 61740 | NO | YES | 11.549 | 11.4636 | 11.3605 | 11.2482 | 11.1155 | 10.9758 | 10.8304 | 10.6931 | 10.5463 | 10.3899 | 10.2408 | 9.8643 | 9.7156 | 9.6089 | 11.3785 | 11.313 | 11.2393 | 11.1453 | 11.0468 | 10.9433 | 10.8414 | 10.7207 | 10.5914 | 10.4567 | 10.3309 | 10.0625 | 9.8623 | 9.6766 | 11.8125 | 11.7774 | 11.7305 | 11.6834 | 11.635 | 11.5835 | 11.4256 | 11.2582 | 11.0816 | 10.8961 | 10.7222 | 10.3291 | 10.129 | 9.9679
|  | KINLOSS | CT |  |  |  | 11.5966 | 11.5213 | 11.3799 | 11.2482 | 11.1155 | 10.9758 | 10.8415 | 10.7235 | 10.616 | 10.5089 | 10.3799 | 9.9896 | 9.7871 | 9.674 | 11.4086 | 11.3573 | 11.2552 | 11.1453 | 11.0468 | 10.9433 | 10.8507 | 10.7507 | 10.6309 | 10.5101 | 10.3933 | 10.0625 | 9.8623 | 9.6766 | 11.8125 | 11.7774 | 11.7305 | 11.6834 | 11.635 | 11.5835 | 11.468 | 11.3552 | 11.1885 | 11.0207 | 10.8591 | 10.4042 | 10.129 | 9.9788
|  | KINLOSS | LW |  |  |  | 11.549 | 11.4636 | 11.3605 | 11.2491 | 11.1354 | 10.9883 | 10.8304 | 10.6931 | 10.5463 | 10.3899 | 10.2408 | 9.8643 | 9.7156 | 9.6089 | 11.3785 | 11.313 | 11.2393 | 11.1571 | 11.0797 | 10.9664 | 10.8414 | 10.7207 | 10.5914 | 10.4567 | 10.3309 | 10.0666 | 9.9414 | 9.7936 | 11.8127 | 11.7838 | 11.7589 | 11.7299 | 11.7009 | 11.5969 | 11.4256 | 11.2582 | 11.0816 | 10.8961 | 10.7222 | 10.3291 | 10.1444 | 9.9679
|  | KINLOSS | ST |  |  |  | 11.6462 | 11.6214 | 11.5758 | 11.5276 | 11.4764 | 11.4068 | 11.3416 | 11.2568 | 11.1683 | 11.0646 | 10.9511 | 10.3233 | 10.0165 | 9.8253 | 11.4347 | 11.4145 | 11.3741 | 11.3317 | 11.2892 | 11.226 | 11.1716 | 11.0979 | 11.0243 | 10.9397 | 10.8464 | 10.3418 | 10.0909 | 9.8597 | 11.8238 | 11.8134 | 11.7868 | 11.7612 | 11.7356 | 11.6909 | 11.6566 | 11.607 | 11.56 | 11.5071 | 11.4451 | 10.9822 | 10.6855 | 10.4693
|  | KINLOSS | FS |  |  |  | 11.6601 | 11.6393 | 11.6086 | 11.5731 | 11.5339 | 11.4922 | 11.4439 | 11.3837 | 11.3204 | 11.2507 | 11.1771 | 10.6695 | 10.2048 | 9.8743 | 11.4426 | 11.4246 | 11.3993 | 11.3691 | 11.3365 | 11.3005 | 11.2595 | 11.2072 | 11.1517 | 11.0901 | 11.0244 | 10.5918 | 10.158 | 9.8291 | 11.8268 | 11.8184 | 11.8054 | 11.7905 | 11.7734 | 11.7539 | 11.7327 | 11.7065 | 11.6788 | 11.648 | 11.6137 | 11.3086 | 10.8085 | 10.5516
| BRACO | KIPPEN | MINIMUM HEADROOM | NS 66376 95628 | NO | YES | 3.0329 | 2.8462 | 2.6263 | 2.3821 | 2.1037 | 1.7847 | 1.4599 | 1.2294 | 0.96233 | 0.63572 | 0.38077 | -0.4021 | -0.98531 | -1.5128 | 4.5999 | 4.4951 | 4.3842 | 4.2116 | 4.0431 | 3.8657 | 3.688 | 3.5354 | 3.3514 | 3.1185 | 2.9312 | 2.3812 | 1.9547 | 1.5308 | 3.5928 | 3.4435 | 3.2783 | 3.0413 | 2.7798 | 2.5039 | 2.22 | 2.0285 | 1.8076 | 1.4889 | 1.2359 | 0.53404 | 0.035823 | -0.44066
|  | KIPPEN | CT |  |  |  | 3.1579 | 3.0139 | 2.7245 | 2.4095 | 2.1037 | 1.7847 | 1.4599 | 1.2565 | 1.0181 | 0.72334 | 0.48769 | -0.25812 | -0.93687 | -1.3867 | 4.6392 | 4.5498 | 4.389 | 4.2116 | 4.0431 | 3.8657 | 3.688 | 3.5354 | 3.3514 | 3.1185 | 2.9378 | 2.3812 | 1.9547 | 1.5308 | 3.6586 | 3.5147 | 3.28 | 3.0413 | 2.7798 | 2.5039 | 2.22 | 2.0285 | 1.8602 | 1.5713 | 1.3377 | 0.63945 | 0.071699 | -0.30796
|  | KIPPEN | LW |  |  |  | 3.0329 | 2.8462 | 2.6263 | 2.3821 | 2.1356 | 1.8278 | 1.4708 | 1.2294 | 0.96233 | 0.63572 | 0.38077 | -0.4021 | -0.98531 | -1.5128 | 4.5999 | 4.4951 | 4.3842 | 4.2577 | 4.135 | 3.9595 | 3.744 | 3.5646 | 3.3675 | 3.119 | 2.9312 | 2.4635 | 2.1467 | 1.8082 | 3.5928 | 3.4435 | 3.2783 | 3.0981 | 2.9113 | 2.6437 | 2.3145 | 2.0733 | 1.8076 | 1.4889 | 1.2359 | 0.53404 | 0.035823 | -0.44066
|  | KIPPEN | ST |  |  |  | 3.2308 | 3.1524 | 3.0288 | 2.8952 | 2.7501 | 2.5741 | 2.392 | 2.1988 | 1.9929 | 1.7206 | 1.4802 | 0.29297 | -0.30654 | -0.71393 | 4.6756 | 4.6317 | 4.5527 | 4.4687 | 4.3798 | 4.2571 | 4.1325 | 3.9946 | 3.8525 | 3.6517 | 3.4786 | 2.5225 | 2.0745 | 1.7053 | 3.7436 | 3.6777 | 3.5695 | 3.4558 | 3.3312 | 3.1702 | 3.0013 | 2.8188 | 2.6267 | 2.3411 | 2.0803 | 0.74375 | 0.15304 | -0.14675
|  | KIPPEN | FS |  |  |  | 3.2847 | 3.2231 | 3.1352 | 3.0279 | 2.9171 | 2.7967 | 2.6552 | 2.5046 | 2.3404 | 2.1421 | 1.9569 | 0.80058 | -0.05111 | -0.47631 | 4.6959 | 4.6595 | 4.6083 | 4.5457 | 4.4787 | 4.4039 | 4.3105 | 4.2128 | 4.1058 | 3.9653 | 3.8369 | 3.0491 | 2.3185 | 1.7663 | 3.7882 | 3.74 | 3.6673 | 3.5812 | 3.4896 | 3.3891 | 3.2659 | 3.1361 | 2.9951 | 2.8167 | 2.652 | 1.5773 | 0.68641 | 0.11716
| THURSO | KIRKWALL | MINIMUM HEADROOM | HY 44669 10987 | NO | YES | -6.3412 | -27.5479 | -28.7878 | -30.3125 | -31.8631 | -34.1321 | -35.1404 | -35.5623 | -36.0355 | -36.6129 | -37.0357 | -38.0801 | -38.9197 | -39.7614 | -7.8285 | -33.8979 | -34.9246 | -36.2285 | -37.5998 | -39.7221 | -40.345 | -40.689 | -41.1081 | -41.646 | -42.0221 | -43.153 | -43.8459 | -44.5486 | -9.6629 | -35.6744 | -36.6336 | -38.1384 | -39.6875 | -41.9074 | -42.9202 | -43.3959 | -43.9282 | -44.5595 | -45.0394 | -46.1722 | -47.0489 | -47.9772
|  | KIRKWALL | CT |  |  |  | 11.5488 | 7.8299 | 6.5058 | 4.9206 | 3.3455 | 1.1662 | 0.19179 | -0.12815 | -0.50863 | -0.9631 | -1.2902 | -2.1336 | -2.909 | -3.4954 | 14.2831 | 9.9747 | 9.025 | 7.8086 | 6.5687 | 4.6706 | 4.1686 | 3.816 | 3.4694 | 3.057 | 2.7234 | 1.4652 | 0.99705 | 0.4169 | 12.4427 | 8.1837 | 7.307 | 5.8078 | 4.2807 | 2.2343 | 1.3387 | 0.98121 | 0.54132 | 0.029685 | -0.35059 | -1.3207 | -2.0737 | -2.6638
|  | KIRKWALL | LW |  |  |  | -6.3412 | -27.5479 | -28.7878 | -30.3125 | -31.8631 | -34.1321 | -35.1404 | -35.5623 | -36.0355 | -36.6129 | -37.0357 | -38.0801 | -38.9197 | -39.7614 | -7.8285 | -33.8979 | -34.9246 | -36.2285 | -37.5998 | -39.7221 | -40.345 | -40.689 | -41.1081 | -41.646 | -42.0221 | -43.153 | -43.8459 | -44.5486 | -9.6629 | -35.6744 | -36.6336 | -38.1384 | -39.6875 | -41.9074 | -42.9202 | -43.3959 | -43.9282 | -44.5595 | -45.0394 | -46.1722 | -47.0489 | -47.9772
|  | KIRKWALL | ST |  |  |  | 2.9103 | -10.1771 | -11.0124 | -12.0582 | -13.0032 | -14.6798 | -15.2115 | -15.6284 | -16.083 | -16.6592 | -17.1633 | -19.942 | -21.0606 | -21.5974 | 3.1222 | -13.0331 | -14.0047 | -15.1945 | -16.2658 | -18.1724 | -18.6165 | -18.8983 | -19.239 | -19.6798 | -20.0292 | -22.0264 | -22.9633 | -23.4457 | 1.2988 | -14.7913 | -15.695 | -16.8205 | -17.8281 | -19.6184 | -20.058 | -20.3526 | -20.6532 | -21.0495 | -21.354 | -23.616 | -24.6946 | -25.2618
|  | KIRKWALL | FS |  |  |  | 14.8885 | 13.4039 | 12.7783 | 11.9322 | 11.1483 | 10.0571 | 9.5897 | 9.1819 | 8.6874 | 8.1734 | 7.7077 | 4.9882 | 2.9629 | 1.8861 | 17.9967 | 16.3043 | 15.644 | 14.7438 | 13.9098 | 12.7181 | 12.2535 | 11.8592 | 11.354 | 10.8771 | 10.5056 | 8.3953 | 6.8344 | 5.9815 | 16.1743 | 14.5322 | 13.923 | 13.0783 | 12.2961 | 11.1872 | 10.7397 | 10.3484 | 9.8619 | 9.3873 | 9.019 | 6.9184 | 5.1685 | 4.1338
| BROADFORD | KISHORNHILL | MINIMUM HEADROOM | NG 88304 40591 | YES | YES | 0.12555 | 0.095176 | 0.056574 | 0.019487 | -0.028913 | -0.089066 | -0.16268 | -0.21563 | -0.2726 | -0.33059 | -0.38302 | -0.46681 | -0.50866 | -0.54439 | 0.0025454 | -0.023078 | -0.049474 | -0.087468 | -0.11854 | -0.14929 | -0.19233 | -0.23508 | -0.28116 | -0.32802 | -0.37035 | -0.42939 | -0.46241 | -0.49504 | -0.21141 | -0.23888 | -0.27339 | -0.30669 | -0.34481 | -0.38611 | -0.43091 | -0.45021 | -0.47397 | -0.49853 | -0.52136 | -0.5755 | -0.60564 | -0.61462
|  | KISHORNHILL | CT |  |  |  | 0.14379 | 0.12384 | 0.075616 | 0.026784 | -0.028913 | -0.089066 | -0.15275 | -0.19091 | -0.24761 | -0.30354 | -0.35571 | -0.43926 | -0.50866 | -0.54439 | 0.012399 | -0.0067765 | -0.045885 | -0.087468 | -0.11854 | -0.14929 | -0.18128 | -0.21292 | -0.25922 | -0.30604 | -0.34706 | -0.42398 | -0.46241 | -0.49504 | -0.19686 | -0.21533 | -0.25729 | -0.30101 | -0.34466 | -0.38611 | -0.43091 | -0.44641 | -0.46276 | -0.47738 | -0.49968 | -0.53769 | -0.58772 | -0.61224
|  | KISHORNHILL | LW |  |  |  | 0.12555 | 0.095176 | 0.056574 | 0.019487 | -0.023153 | -0.085872 | -0.16268 | -0.21563 | -0.2726 | -0.33059 | -0.38302 | -0.46681 | -0.50572 | -0.51649 | 0.0025454 | -0.023078 | -0.049474 | -0.078362 | -0.10517 | -0.1453 | -0.19233 | -0.23508 | -0.28116 | -0.32802 | -0.37035 | -0.42939 | -0.44478 | -0.44853 | -0.21141 | -0.23888 | -0.27339 | -0.30669 | -0.34481 | -0.38383 | -0.42831 | -0.45021 | -0.47397 | -0.49853 | -0.52136 | -0.5755 | -0.60564 | -0.61462
|  | KISHORNHILL | ST |  |  |  | 0.16868 | 0.15995 | 0.15081 | 0.13731 | 0.12207 | 0.10672 | 0.088166 | 0.067368 | 0.036947 | -0.0087502 | -0.057203 | -0.29714 | -0.36193 | -0.39729 | 0.026068 | 0.018235 | 0.0090931 | -0.0044199 | -0.019083 | -0.035785 | -0.056022 | -0.080322 | -0.10985 | -0.14308 | -0.17928 | -0.36345 | -0.40938 | -0.43727 | -0.17356 | -0.18177 | -0.1902 | -0.20259 | -0.21661 | -0.23089 | -0.24817 | -0.26766 | -0.29067 | -0.31581 | -0.34273 | -0.48213 | -0.5363 | -0.5614
|  | KISHORNHILL | FS |  |  |  | 0.17284 | 0.1666 | 0.15512 | 0.14407 | 0.12989 | 0.11584 | 0.10023 | 0.07976 | 0.061477 | 0.038559 | 0.0033034 | -0.23636 | -0.41181 | -0.44333 | 0.02908 | 0.022198 | 0.012855 | 0.0024308 | -0.009889 | -0.023402 | -0.038804 | -0.057852 | -0.078142 | -0.10114 | -0.12597 | -0.29013 | -0.42788 | -0.4648 | -0.16862 | -0.17572 | -0.18611 | -0.19619 | -0.20908 | -0.22195 | -0.23582 | -0.2534 | -0.27015 | -0.28877 | -0.30756 | -0.43882 | -0.53029 | -0.5777
| BROADFORD | KYLE | MINIMUM HEADROOM | NG 76499 27247 | NO | YES | 6.1899 | 6.1354 | 6.0664 | 5.969 | 5.8313 | 5.6938 | 5.594 | 5.5304 | 5.4512 | 5.3789 | 5.3087 | 5.1245 | 4.9442 | 4.7754 | 6.5391 | 6.5088 | 6.4709 | 6.4048 | 6.3008 | 6.1938 | 6.1342 | 6.0752 | 6.0053 | 5.9403 | 5.8758 | 5.6544 | 5.4257 | 5.1704 | 5.6364 | 5.5882 | 5.5294 | 5.4359 | 5.3009 | 5.1643 | 5.0749 | 5.0051 | 4.9189 | 4.8391 | 4.7621 | 4.5404 | 4.3462 | 4.1463
|  | KYLE | CT |  |  |  | 6.2248 | 6.1901 | 6.0827 | 5.969 | 5.8313 | 5.6938 | 5.594 | 5.5304 | 5.4512 | 5.3789 | 5.3087 | 5.1245 | 4.9442 | 4.7882 | 6.5503 | 6.5293 | 6.4709 | 6.4048 | 6.3008 | 6.1938 | 6.1342 | 6.0752 | 6.0053 | 5.9403 | 5.8758 | 5.6544 | 5.467 | 5.2681 | 5.6636 | 5.632 | 5.5378 | 5.4359 | 5.3009 | 5.1643 | 5.0749 | 5.0051 | 4.9189 | 4.8391 | 4.7621 | 4.5404 | 4.3462 | 4.168
|  | KYLE | LW |  |  |  | 6.1899 | 6.1354 | 6.0664 | 5.9916 | 5.9215 | 5.8331 | 5.7343 | 5.6665 | 5.5983 | 5.5287 | 5.4644 | 5.3337 | 5.0912 | 4.7754 | 6.5391 | 6.5088 | 6.4745 | 6.4366 | 6.402 | 6.3532 | 6.2978 | 6.2447 | 6.1896 | 6.135 | 6.0821 | 5.9607 | 5.6921 | 5.3141 | 5.6364 | 5.5882 | 5.5294 | 5.4651 | 5.4057 | 5.3269 | 5.2383 | 5.1678 | 5.0958 | 5.0232 | 4.9556 | 4.8155 | 4.5317 | 4.1463
|  | KYLE | ST |  |  |  | 6.2847 | 6.2757 | 6.2176 | 6.171 | 6.1268 | 6.0409 | 5.9968 | 5.9082 | 5.849 | 5.785 | 5.7099 | 5.3442 | 5.1237 | 4.913 | 6.5751 | 6.5686 | 6.5058 | 6.4574 | 6.4182 | 6.3205 | 6.2785 | 6.1902 | 6.138 | 6.0841 | 6.0161 | 5.6822 | 5.4257 | 5.1704 | 5.7132 | 5.7047 | 5.637 | 5.584 | 5.5371 | 5.435 | 5.3868 | 5.2876 | 5.225 | 5.1587 | 5.0785 | 4.6888 | 4.4325 | 4.1897
|  | KYLE | FS |  |  |  | 6.2926 | 6.2805 | 6.2481 | 6.2134 | 6.1817 | 6.1459 | 6.1058 | 6.0602 | 6.0168 | 5.9701 | 5.9221 | 5.6529 | 5.4561 | 5.3864 | 6.579 | 6.5718 | 6.5496 | 6.526 | 6.5013 | 6.4742 | 6.4458 | 6.4051 | 6.3689 | 6.3301 | 6.2892 | 6.0951 | 5.9235 | 5.8148 | 5.7197 | 5.7091 | 5.6783 | 5.6449 | 5.613 | 5.5774 | 5.5385 | 5.4902 | 5.4455 | 5.3975 | 5.3479 | 5.0891 | 4.8951 | 4.8294
| LAIRG | LAIRG | MINIMUM HEADROOM | NC 58798 07111 | YES | YES | -0.32712 | -0.34436 | -0.4054 | -0.48482 | -0.58907 | -0.7212 | -0.81517 | -0.87935 | -0.95447 | -1.0297 | -1.1064 | -1.3399 | -1.5882 | -1.8084 | 0.13795 | 0.10051 | 0.067737 | 0.014699 | -0.081671 | -0.18359 | -0.23812 | -0.30036 | -0.37513 | -0.44638 | -0.51397 | -0.77482 | -1.0346 | -1.2699 | -0.4285 | -0.4812 | -0.53364 | -0.59574 | -0.71333 | -0.83783 | -0.9161 | -0.98607 | -1.0712 | -1.1516 | -1.2264 | -1.4701 | -1.7559 | -2
|  | LAIRG | CT |  |  |  | -0.3205 | -0.33478 | -0.35877 | -0.46114 | -0.58907 | -0.7212 | -0.81517 | -0.87935 | -0.95447 | -1.0297 | -1.1064 | -1.3399 | -1.5593 | -1.7109 | 0.16093 | 0.13402 | 0.078129 | 0.014699 | -0.081671 | -0.18359 | -0.23812 | -0.30036 | -0.37513 | -0.44638 | -0.51397 | -0.74237 | -0.92643 | -1.0971 | -0.38991 | -0.42602 | -0.50551 | -0.59371 | -0.71333 | -0.83783 | -0.9161 | -0.98607 | -1.0712 | -1.1516 | -1.2264 | -1.469 | -1.6874 | -1.8573
|  | LAIRG | LW |  |  |  | -0.32712 | -0.34436 | -0.4054 | -0.48482 | -0.55543 | -0.63735 | -0.72318 | -0.78501 | -0.84791 | -0.92138 | -0.99183 | -1.1569 | -1.3991 | -1.6982 | 0.13795 | 0.10051 | 0.067737 | 0.026777 | -0.0086471 | -0.056579 | -0.10972 | -0.16671 | -0.22641 | -0.28513 | -0.34111 | -0.46987 | -0.72753 | -1.083 | -0.4285 | -0.4812 | -0.53364 | -0.59574 | -0.64988 | -0.71936 | -0.79413 | -0.86069 | -0.92926 | -0.99674 | -1.0616 | -1.2165 | -1.4931 | -1.8563
|  | LAIRG | ST |  |  |  | -0.3092 | -0.31685 | -0.36601 | -0.40345 | -0.43085 | -0.52889 | -0.58764 | -0.68048 | -0.74755 | -0.81431 | -0.89624 | -1.3148 | -1.5882 | -1.8084 | 0.17507 | 0.15907 | 0.089452 | 0.033112 | -0.010518 | -0.11559 | -0.16255 | -0.25062 | -0.30567 | -0.36089 | -0.43116 | -0.77482 | -1.0346 | -1.2699 | -0.36975 | -0.39268 | -0.47063 | -0.53604 | -0.588 | -0.70408 | -0.76088 | -0.85929 | -0.92518 | -0.99119 | -1.0737 | -1.4701 | -1.7559 | -2
|  | LAIRG | FS |  |  |  | -0.29237 | -0.29717 | -0.31319 | -0.33011 | -0.34673 | -0.3643 | -0.38787 | -0.44782 | -0.50428 | -0.56314 | -0.6277 | -0.97769 | -1.2108 | -1.2873 | 0.19495 | 0.18336 | 0.15543 | 0.12671 | 0.097513 | 0.066429 | 0.034657 | -0.011771 | -0.053646 | -0.097909 | -0.14558 | -0.37406 | -0.54358 | -0.62035 | -0.34512 | -0.36204 | -0.39834 | -0.43413 | -0.47096 | -0.50986 | -0.55009 | -0.6065 | -0.65854 | -0.71318 | -0.77273 | -1.0739 | -1.2741 | -1.339
| MYBSTER | LATHERON | MINIMUM HEADROOM | ND 19924 33627 | YES | YES | 0.7794 | 0.66455 | 0.4729 | 0.33074 | 0.1308 | -0.12687 | -0.30931 | -0.4483 | -0.60906 | -0.75914 | -0.90869 | -1.4168 | -2.2168 | -3.0746 | 1.5375 | 1.4817 | 1.3636 | 1.2778 | 1.092 | 0.89413 | 0.78998 | 0.65789 | 0.51086 | 0.37454 | 0.23703 | -0.41783 | -1.2606 | -2.1438 | 0.97075 | 0.88085 | 0.74148 | 0.63252 | 0.40956 | 0.16592 | 0.015639 | -0.1322 | -0.30416 | -0.46452 | -0.62216 | -1.231 | -2.1349 | -3.1262
|  | LATHERON | CT |  |  |  | 0.88165 | 0.80526 | 0.57233 | 0.38106 | 0.1308 | -0.12687 | -0.30931 | -0.4483 | -0.60906 | -0.75914 | -0.90869 | -1.4168 | -2.0488 | -2.56 | 1.5713 | 1.5328 | 1.3903 | 1.281 | 1.092 | 0.89413 | 0.78998 | 0.65789 | 0.51086 | 0.37454 | 0.23703 | -0.30591 | -0.88931 | -1.4917 | 1.044 | 0.98351 | 0.80371 | 0.64444 | 0.40956 | 0.16592 | 0.015639 | -0.1322 | -0.30416 | -0.46452 | -0.62216 | -1.1911 | -1.8496 | -2.4484
|  | LATHERON | LW |  |  |  | 0.7794 | 0.66455 | 0.4729 | 0.33074 | 0.20144 | 0.045507 | -0.11913 | -0.2494 | -0.39161 | -0.52063 | -0.65031 | -1.0726 | -1.953 | -3.0746 | 1.5375 | 1.4817 | 1.3636 | 1.2957 | 1.233 | 1.1529 | 1.0667 | 0.95122 | 0.82756 | 0.71509 | 0.59613 | 0.20941 | -0.7739 | -2.1438 | 0.97075 | 0.88085 | 0.74148 | 0.63252 | 0.53522 | 0.41095 | 0.27764 | 0.14166 | -0.0053554 | -0.13895 | -0.27329 | -0.71273 | -1.7444 | -3.1262
|  | LATHERON | ST |  |  |  | 0.92053 | 0.87194 | 0.66886 | 0.54054 | 0.43105 | 0.22313 | 0.10797 | -0.12701 | -0.26701 | -0.40881 | -0.57983 | -1.3975 | -2.2168 | -2.9709 | 1.5872 | 1.5664 | 1.3848 | 1.2778 | 1.1939 | 0.99137 | 0.9035 | 0.6757 | 0.56139 | 0.45036 | 0.30384 | -0.41783 | -1.2606 | -2.1122 | 1.0734 | 1.037 | 0.84789 | 0.72258 | 0.62055 | 0.3982 | 0.29038 | 0.039719 | -0.097185 | -0.23295 | -0.40472 | -1.231 | -2.1349 | -3.0049
|  | LATHERON | FS |  |  |  | 0.96403 | 0.92605 | 0.815 | 0.73084 | 0.65203 | 0.56559 | 0.48396 | 0.34953 | 0.22504 | 0.095989 | -0.024286 | -0.67023 | -1.0709 | -1.2593 | 1.6013 | 1.5847 | 1.5063 | 1.4506 | 1.3965 | 1.335 | 1.2808 | 1.1746 | 1.0802 | 0.98473 | 0.89406 | 0.51507 | 0.23369 | 0.049139 | 1.1039 | 1.0751 | 0.98718 | 0.91562 | 0.84582 | 0.77009 | 0.69817 | 0.5695 | 0.45593 | 0.33787 | 0.22464 | -0.31585 | -0.66976 | -0.83597
| FIDDES | LAURENCEKIRK | MINIMUM HEADROOM | NO 70915 71028 | NO | YES | 8.5441 | 8.3141 | 7.879 | 7.4044 | 6.7892 | 5.585 | 4.7605 | 4.3871 | 4.0183 | 3.6324 | 3.2639 | 2.2621 | 1.5302 | 0.79236 | 10.0353 | 9.9098 | 9.5996 | 9.2553 | 8.7324 | 7.6848 | 7.0228 | 6.7597 | 6.4856 | 6.1996 | 5.9303 | 5.2078 | 4.5536 | 3.7506 | 9.5274 | 9.329 | 8.8932 | 8.423 | 7.7711 | 6.5227 | 5.7158 | 5.3895 | 5.0696 | 4.7363 | 4.4211 | 3.4831 | 2.6776 | 1.8267
|  | LAURENCEKIRK | CT |  |  |  | 8.7395 | 8.5753 | 8.1895 | 7.7616 | 7.1863 | 6.1105 | 5.4823 | 5.1035 | 4.7088 | 4.3205 | 3.9492 | 2.8288 | 1.9887 | 1.4614 | 10.1044 | 10.0022 | 9.7727 | 9.5011 | 9.0224 | 8.1051 | 7.6528 | 7.3839 | 7.0999 | 6.815 | 6.5427 | 5.6805 | 5.0419 | 4.4129 | 9.7102 | 9.571 | 9.2185 | 8.825 | 8.2167 | 7.0954 | 6.4937 | 6.1488 | 5.8008 | 5.463 | 5.1333 | 4.0842 | 3.26 | 2.7153
|  | LAURENCEKIRK | LW |  |  |  | 8.5441 | 8.3141 | 7.879 | 7.4044 | 6.7892 | 5.585 | 4.7605 | 4.3871 | 4.0183 | 3.6324 | 3.2639 | 2.2621 | 1.5302 | 0.79236 | 10.0353 | 9.9098 | 9.5996 | 9.2553 | 8.7324 | 7.6848 | 7.0228 | 6.7597 | 6.4856 | 6.1996 | 5.9303 | 5.2078 | 4.5536 | 3.7506 | 9.5274 | 9.329 | 8.8932 | 8.423 | 7.7711 | 6.5227 | 5.7158 | 5.3895 | 5.0696 | 4.7363 | 4.4211 | 3.4831 | 2.6776 | 1.8267
|  | LAURENCEKIRK | ST |  |  |  | 8.8504 | 8.7782 | 8.4524 | 8.1897 | 7.9677 | 7.0328 | 6.5828 | 6.2751 | 6.022 | 5.7644 | 5.474 | 3.968 | 3.0193 | 2.1845 | 10.1567 | 10.1141 | 9.7755 | 9.5182 | 9.3178 | 8.3862 | 7.981 | 7.712 | 7.5169 | 7.3191 | 7.0848 | 5.8891 | 5.0535 | 4.2308 | 9.7361 | 9.7162 | 9.3923 | 9.1102 | 8.8832 | 7.8484 | 7.3989 | 7.0974 | 6.8715 | 6.6489 | 6.3932 | 5.069 | 4.0837 | 3.1744
|  | LAURENCEKIRK | FS |  |  |  | 8.894 | 8.8432 | 8.7041 | 8.5584 | 8.4059 | 7.978 | 7.6477 | 7.4156 | 7.1888 | 6.9647 | 6.735 | 5.3589 | 4.1828 | 3.5762 | 10.1745 | 10.1416 | 10.0332 | 9.9178 | 9.7911 | 9.4197 | 9.1377 | 8.9602 | 8.7916 | 8.623 | 8.4493 | 7.4786 | 6.4944 | 5.7551 | 9.7427 | 9.7281 | 9.6506 | 9.5423 | 9.3928 | 8.9487 | 8.6246 | 8.4057 | 8.1971 | 7.9957 | 7.7915 | 6.601 | 5.5792 | 4.9732
| STORNOWAY | LAXAY | MINIMUM HEADROOM | NB 33424 21925 | YES | YES | -1.055 | -1.148 | -1.2574 | -1.3757 | -1.5434 | -1.7198 | -1.8667 | -1.9731 | -2.1043 | -2.2323 | -2.348 | -2.694 | -3.2477 | -4.0067 | -0.085073 | -0.10824 | -0.14259 | -0.19356 | -0.30173 | -0.41601 | -0.495 | -0.58747 | -0.70234 | -0.82679 | -0.94149 | -1.3183 | -1.8938 | -2.7751 | -0.8377 | -0.91575 | -1.0022 | -1.1195 | -1.2666 | -1.4216 | -1.5405 | -1.6609 | -1.8116 | -1.9585 | -2.091 | -2.4962 | -3.1007 | -4.0339
|  | LAXAY | CT |  |  |  | -0.98314 | -1.052 | -1.2108 | -1.3757 | -1.5434 | -1.7198 | -1.8667 | -1.9731 | -2.1043 | -2.2323 | -2.348 | -2.694 | -3.1215 | -3.4751 | -0.085073 | -0.10824 | -0.14259 | -0.19356 | -0.30173 | -0.41601 | -0.495 | -0.58747 | -0.70234 | -0.82679 | -0.94149 | -1.3183 | -1.7097 | -2.1283 | -0.78881 | -0.84862 | -0.97948 | -1.1195 | -1.2666 | -1.4216 | -1.5405 | -1.6609 | -1.8116 | -1.9585 | -2.091 | -2.4962 | -2.935 | -3.3469
|  | LAXAY | LW |  |  |  | -1.055 | -1.148 | -1.2574 | -1.371 | -1.4808 | -1.6187 | -1.7664 | -1.8913 | -2.0236 | -2.1519 | -2.275 | -2.6414 | -3.2477 | -4.0067 | -0.083366 | -0.099291 | -0.11301 | -0.16375 | -0.21574 | -0.28768 | -0.36693 | -0.47304 | -0.59959 | -0.72079 | -0.83864 | -1.1762 | -1.8512 | -2.7751 | -0.8377 | -0.91575 | -1.0022 | -1.0945 | -1.1802 | -1.2994 | -1.4303 | -1.5712 | -1.7207 | -1.8652 | -2.0041 | -2.3943 | -3.1007 | -4.0339
|  | LAXAY | ST |  |  |  | -0.93538 | -0.96898 | -1.0459 | -1.1204 | -1.1869 | -1.2938 | -1.3709 | -1.5274 | -1.635 | -1.7504 | -1.8866 | -2.5441 | -3.106 | -3.6192 | -0.070387 | -0.075541 | -0.12284 | -0.15922 | -0.18811 | -0.2636 | -0.29753 | -0.42846 | -0.51868 | -0.61252 | -0.73085 | -1.3122 | -1.8938 | -2.4721 | -0.75268 | -0.77935 | -0.85539 | -0.9265 | -0.98867 | -1.1007 | -1.1747 | -1.3456 | -1.4576 | -1.5761 | -1.72 | -2.4168 | -3.0367 | -3.6216
|  | LAXAY | FS |  |  |  | -0.91064 | -0.93558 | -0.98372 | -1.0342 | -1.0863 | -1.1419 | -1.1979 | -1.2899 | -1.3768 | -1.4667 | -1.5643 | -2.0993 | -2.4759 | -2.6397 | -0.067494 | -0.071309 | -0.084624 | -0.099193 | -0.11599 | -0.13424 | -0.15273 | -0.20152 | -0.25332 | -0.31807 | -0.39147 | -0.73986 | -1.0354 | -1.1815 | -0.73519 | -0.75506 | -0.7955 | -0.83918 | -0.88501 | -0.93465 | -0.98565 | -1.0763 | -1.1603 | -1.2482 | -1.3434 | -1.834 | -2.2054 | -2.3478
| COUPAR ANGUS | LEOCH | MINIMUM HEADROOM | NO 35945 36287 | YES | YES | -2.6185 | -2.7539 | -2.9411 | -3.1333 | -3.3594 | -3.661 | -3.8926 | -4.1546 | -4.4539 | -4.7464 | -5.0397 | -6.0355 | -6.8126 | -7.8837 | -1.029 | -1.1033 | -1.195 | -1.3223 | -1.5528 | -1.793 | -1.9376 | -2.141 | -2.37 | -2.5897 | -2.8141 | -3.6784 | -4.5884 | -5.7417 | -1.8342 | -1.9598 | -2.1298 | -2.3055 | -2.5673 | -2.8804 | -3.1018 | -3.3694 | -3.6738 | -3.969 | -4.266 | -5.3046 | -6.1438 | -7.4864
|  | LEOCH | CT |  |  |  | -2.5004 | -2.5959 | -2.8203 | -3.0627 | -3.3594 | -3.661 | -3.8926 | -4.1546 | -4.4539 | -4.7464 | -5.0397 | -6.0355 | -6.8126 | -7.4239 | -0.98532 | -1.0449 | -1.1748 | -1.3223 | -1.5528 | -1.793 | -1.9376 | -2.141 | -2.37 | -2.5897 | -2.8141 | -3.6784 | -4.4713 | -5.3168 | -1.7301 | -1.8199 | -2.0307 | -2.2617 | -2.5673 | -2.8804 | -3.1018 | -3.3694 | -3.6738 | -3.969 | -4.266 | -5.3046 | -6.1438 | -6.8519
|  | LEOCH | LW |  |  |  | -2.6185 | -2.7539 | -2.9411 | -3.1333 | -3.3203 | -3.5575 | -3.8111 | -4.0724 | -4.343 | -4.6184 | -4.8836 | -5.6586 | -6.6686 | -7.8837 | -1.029 | -1.1033 | -1.195 | -1.2919 | -1.3846 | -1.513 | -1.6545 | -1.8436 | -2.0425 | -2.2385 | -2.4316 | -3.0362 | -4.1382 | -5.6092 | -1.8342 | -1.9598 | -2.1298 | -2.3055 | -2.4755 | -2.6953 | -2.9319 | -3.1942 | -3.4668 | -3.7412 | -4.0072 | -4.8021 | -5.9899 | -7.4864
|  | LEOCH | ST |  |  |  | -2.4382 | -2.4811 | -2.6313 | -2.7601 | -2.8696 | -3.0946 | -3.2263 | -3.4803 | -3.6576 | -3.8412 | -4.0639 | -5.277 | -6.3129 | -7.2789 | -0.95087 | -0.97671 | -1.1269 | -1.2461 | -1.3415 | -1.5729 | -1.6834 | -1.943 | -2.0954 | -2.249 | -2.4465 | -3.488 | -4.5884 | -5.7417 | -1.6729 | -1.7124 | -1.8816 | -2.0218 | -2.1377 | -2.3938 | -2.5308 | -2.8182 | -3.0039 | -3.1936 | -3.4293 | -4.689 | -5.8418 | -6.9343
|  | LEOCH | FS |  |  |  | -2.4099 | -2.4415 | -2.508 | -2.5824 | -2.6586 | -2.7453 | -2.8282 | -2.9721 | -3.1125 | -3.2589 | -3.4132 | -4.2665 | -5.0349 | -5.5129 | -0.9386 | -0.95909 | -1.0111 | -1.0685 | -1.1307 | -1.1994 | -1.2667 | -1.3938 | -1.5082 | -1.629 | -1.757 | -2.3819 | -3.0748 | -3.7921 | -1.6476 | -1.6767 | -1.7441 | -1.8192 | -1.8973 | -1.9852 | -2.0694 | -2.2212 | -2.3643 | -2.5135 | -2.6706 | -3.4876 | -4.2239 | -4.6823
| NAIRN | LETHEN | MINIMUM HEADROOM | NH 92307 50795 | YES | YES | 0.080857 | -0.0067266 | -0.099604 | -0.1942 | -0.38102 | -0.58892 | -0.72424 | -0.82543 | -0.93989 | -1.045 | -1.1554 | -1.6001 | -2.1288 | -2.5547 | 0.83781 | 0.79349 | 0.7322 | 0.63701 | 0.49661 | 0.32147 | 0.23602 | 0.13374 | 0.027071 | -0.076395 | -0.18102 | -0.69867 | -1.2104 | -1.6864 | 0.58355 | 0.53157 | 0.46136 | 0.36835 | 0.19285 | 0.0067526 | -0.10965 | -0.22758 | -0.34067 | -0.44384 | -0.57067 | -1.2354 | -1.8183 | -2.2763
|  | LETHEN | CT |  |  |  | 0.15198 | 0.089913 | -0.033489 | -0.17881 | -0.38102 | -0.58892 | -0.72424 | -0.82543 | -0.93989 | -1.045 | -1.1554 | -1.5353 | -1.9423 | -2.2267 | 0.86287 | 0.82735 | 0.75375 | 0.66346 | 0.49661 | 0.32147 | 0.23602 | 0.13826 | 0.027071 | -0.076395 | -0.18102 | -0.5768 | -0.93373 | -1.2772 | 0.6008 | 0.54925 | 0.46136 | 0.36835 | 0.19285 | 0.0067526 | -0.10965 | -0.22758 | -0.34067 | -0.44384 | -0.57067 | -1.0396 | -1.4041 | -1.7156
|  | LETHEN | LW |  |  |  | 0.080857 | -0.0067266 | -0.099604 | -0.1942 | -0.28594 | -0.3971 | -0.51669 | -0.60508 | -0.69213 | -0.78499 | -0.87413 | -1.1537 | -1.6435 | -2.2364 | 0.83781 | 0.79349 | 0.7496 | 0.70275 | 0.65933 | 0.598 | 0.52963 | 0.45257 | 0.37254 | 0.2924 | 0.21474 | -0.0094636 | -0.52992 | -1.2388 | 0.58355 | 0.53157 | 0.48339 | 0.43121 | 0.37823 | 0.28991 | 0.18544 | 0.078387 | -0.035505 | -0.15289 | -0.26764 | -0.60655 | -1.1491 | -1.864
|  | LETHEN | ST |  |  |  | 0.18194 | 0.14274 | 0.010267 | -0.09663 | -0.19253 | -0.37719 | -0.47467 | -0.64264 | -0.74817 | -0.85551 | -0.98431 | -1.6001 | -2.1288 | -2.5547 | 0.87663 | 0.85812 | 0.7322 | 0.63701 | 0.56151 | 0.37277 | 0.29367 | 0.13374 | 0.046656 | -0.039522 | -0.15135 | -0.69867 | -1.2104 | -1.6864 | 0.62448 | 0.60493 | 0.47659 | 0.37842 | 0.2978 | 0.101 | 0.011594 | -0.16036 | -0.26384 | -0.36986 | -0.51121 | -1.2354 | -1.8183 | -2.2763
|  | LETHEN | FS |  |  |  | 0.21348 | 0.18847 | 0.13446 | 0.072211 | 0.0068146 | -0.060443 | -0.1163 | -0.22011 | -0.30671 | -0.39377 | -0.49108 | -0.99445 | -1.3199 | -1.4966 | 0.88816 | 0.87503 | 0.83623 | 0.79301 | 0.74581 | 0.69657 | 0.65221 | 0.57394 | 0.50959 | 0.44331 | 0.37158 | 0.058612 | -0.18912 | -0.35197 | 0.63616 | 0.62187 | 0.5821 | 0.53749 | 0.48805 | 0.43559 | 0.38589 | 0.30371 | 0.23304 | 0.15954 | 0.079541 | -0.35362 | -0.69627 | -0.92812
| GRUDIE BRIDGE | LETTEREWE | MINIMUM HEADROOM | NG 93546 70082 | YES | YES | 0.1112 | 0.10922 | 0.10917 | 0.10912 | 0.10712 | 0.10702 | 0.10681 | 0.10624 | 0.10095 | 0.10084 | 0.10068 | 0.098289 | 0.09668 | 0.096658 | 0.10341 | 0.10269 | 0.10266 | 0.10262 | 0.1019 | 0.10163 | 0.10114 | 0.10057 | 0.099381 | 0.098434 | 0.097817 | 0.096211 | 0.09543 | 0.095407 | 0.10244 | 0.10107 | 0.10103 | 0.10079 | 0.099176 | 0.098755 | 0.098274 | 0.097658 | 0.093559 | 0.093274 | 0.092812 | 0.090493 | 0.089039 | 0.089017
|  | LETTEREWE | CT |  |  |  | 0.1112 | 0.11115 | 0.11094 | 0.11066 | 0.10902 | 0.10702 | 0.10695 | 0.10662 | 0.10095 | 0.10084 | 0.10068 | 0.099402 | 0.097765 | 0.099372 | 0.10341 | 0.10326 | 0.10296 | 0.10277 | 0.10229 | 0.10163 | 0.10134 | 0.10095 | 0.099381 | 0.099077 | 0.098601 | 0.097313 | 0.096863 | 0.097284 | 0.10244 | 0.1022 | 0.10181 | 0.10156 | 0.10028 | 0.098755 | 0.098474 | 0.09809 | 0.093559 | 0.093274 | 0.092812 | 0.091563 | 0.090125 | 0.091534
|  | LETTEREWE | LW |  |  |  | 0.11121 | 0.10922 | 0.10917 | 0.10912 | 0.10712 | 0.10702 | 0.10681 | 0.10624 | 0.10399 | 0.10172 | 0.10109 | 0.098289 | 0.098289 | 0.098289 | 0.10342 | 0.10269 | 0.10266 | 0.10262 | 0.1019 | 0.10164 | 0.10114 | 0.10057 | 0.099518 | 0.098434 | 0.097817 | 0.096211 | 0.096211 | 0.096211 | 0.10249 | 0.10107 | 0.10103 | 0.10079 | 0.099176 | 0.098766 | 0.098274 | 0.097658 | 0.095703 | 0.09365 | 0.093052 | 0.090493 | 0.090493 | 0.090493
|  | LETTEREWE | ST |  |  |  | 0.11123 | 0.11122 | 0.11119 | 0.11117 | 0.11113 | 0.111 | 0.11067 | 0.11026 | 0.10862 | 0.10695 | 0.10484 | 0.099061 | 0.09668 | 0.096669 | 0.10343 | 0.10342 | 0.1034 | 0.10334 | 0.10319 | 0.10301 | 0.10278 | 0.10247 | 0.10185 | 0.10113 | 0.10019 | 0.096616 | 0.09543 | 0.095419 | 0.10256 | 0.10251 | 0.10242 | 0.1023 | 0.10211 | 0.10187 | 0.10157 | 0.1012 | 0.099714 | 0.098535 | 0.096659 | 0.091191 | 0.089039 | 0.089028
|  | LETTEREWE | FS |  |  |  | 0.11124 | 0.11122 | 0.11121 | 0.11119 | 0.11116 | 0.11114 | 0.11108 | 0.11085 | 0.11057 | 0.109 | 0.10699 | 0.10048 | 0.097693 | 0.096658 | 0.10344 | 0.10343 | 0.10341 | 0.1034 | 0.10333 | 0.10321 | 0.10307 | 0.1029 | 0.1027 | 0.10222 | 0.10153 | 0.098384 | 0.096432 | 0.095407 | 0.10257 | 0.10254 | 0.10247 | 0.10239 | 0.10228 | 0.10213 | 0.10194 | 0.10173 | 0.10147 | 0.10018 | 0.098658 | 0.092601 | 0.090012 | 0.089017
| ELGIN | LHANBRYDE | MINIMUM HEADROOM | NJ 27940 61640 | NO | YES | 5.074 | 4.9138 | 4.7441 | 4.572 | 4.4067 | 4.2138 | 4.008 | 3.8523 | 3.6886 | 3.5241 | 3.3659 | 2.8642 | 2.4065 | 2.1613 | 5.4687 | 5.3838 | 5.3074 | 5.2262 | 5.1259 | 4.997 | 4.8994 | 4.7873 | 4.6554 | 4.5262 | 4.3996 | 3.9967 | 3.6865 | 3.3848 | 5.3275 | 5.1912 | 5.0399 | 4.8854 | 4.7374 | 4.5619 | 4.3739 | 4.2192 | 4.0534 | 3.8867 | 3.7272 | 3.2105 | 2.7922 | 2.5515
|  | LHANBRYDE | CT |  |  |  | 5.2044 | 5.0953 | 4.9171 | 4.7296 | 4.527 | 4.3141 | 4.1283 | 3.9614 | 3.7768 | 3.599 | 3.421 | 2.8642 | 2.4065 | 2.1613 | 5.5129 | 5.4493 | 5.3532 | 5.2473 | 5.1259 | 4.997 | 4.8994 | 4.7873 | 4.6554 | 4.5262 | 4.3996 | 3.9967 | 3.6865 | 3.3848 | 5.4405 | 5.3486 | 5.186 | 5.0138 | 4.8215 | 4.6199 | 4.4509 | 4.2907 | 4.1071 | 3.9294 | 3.7533 | 3.2105 | 2.7922 | 2.5515
|  | LHANBRYDE | LW |  |  |  | 5.074 | 4.9138 | 4.7441 | 4.572 | 4.4067 | 4.2138 | 4.008 | 3.8523 | 3.6886 | 3.5241 | 3.3659 | 2.9379 | 2.6163 | 2.3401 | 5.4687 | 5.3838 | 5.3074 | 5.2262 | 5.1511 | 5.0468 | 4.9304 | 4.8173 | 4.6963 | 4.5744 | 4.4593 | 4.2002 | 3.9629 | 3.6713 | 5.3275 | 5.1912 | 5.0399 | 4.8854 | 4.7374 | 4.5619 | 4.3739 | 4.2192 | 4.0534 | 3.8867 | 3.7272 | 3.3197 | 2.992 | 2.6721
|  | LHANBRYDE | ST |  |  |  | 5.2603 | 5.1899 | 5.1129 | 5.0432 | 4.9764 | 4.8689 | 4.789 | 4.6835 | 4.5903 | 4.5003 | 4.3788 | 3.7004 | 3.2512 | 2.8309 | 5.5367 | 5.4977 | 5.4347 | 5.3788 | 5.3275 | 5.2298 | 5.1664 | 5.0707 | 4.9923 | 4.9117 | 4.8136 | 4.288 | 3.9172 | 3.5225 | 5.4905 | 5.4345 | 5.3551 | 5.2851 | 5.2203 | 5.1065 | 5.026 | 4.9131 | 4.8165 | 4.7214 | 4.604 | 3.9672 | 3.5155 | 3.0854
|  | LHANBRYDE | FS |  |  |  | 5.2953 | 5.2332 | 5.1834 | 5.1305 | 5.0728 | 5.0098 | 4.952 | 4.8639 | 4.7723 | 4.681 | 4.5898 | 3.9675 | 3.4448 | 3.1347 | 5.5494 | 5.515 | 5.4822 | 5.4458 | 5.4056 | 5.3611 | 5.3165 | 5.252 | 5.1862 | 5.1168 | 5.0436 | 4.5947 | 4.1312 | 3.6863 | 5.5201 | 5.4715 | 5.4255 | 5.3763 | 5.3227 | 5.2637 | 5.2068 | 5.1208 | 5.0321 | 4.9426 | 4.8518 | 4.2625 | 3.7838 | 3.4882
| FORT WILLIAM | LIDDESDALE | MINIMUM HEADROOM | NM 78116 59480 | YES | YES | 0.092327 | 0.087619 | 0.083019 | 0.078709 | 0.076085 | 0.072688 | 0.068923 | 0.068542 | 0.06276 | 0.059919 | 0.057399 | 0.052518 | 0.047019 | 0.046517 | 0.091717 | 0.089548 | 0.087514 | 0.085493 | 0.084178 | 0.082193 | 0.079866 | 0.078454 | 0.07512 | 0.072742 | 0.070715 | 0.067535 | 0.065449 | 0.065112 | 0.086686 | 0.082446 | 0.078374 | 0.074491 | 0.072085 | 0.068852 | 0.065326 | 0.06465 | 0.059238 | 0.056147 | 0.05364 | 0.048989 | 0.044165 | 0.043665
|  | LIDDESDALE | CT |  |  |  | 0.094321 | 0.091701 | 0.084812 | 0.081495 | 0.078756 | 0.075978 | 0.073605 | 0.070117 | 0.06395 | 0.063035 | 0.060718 | 0.054537 | 0.047019 | 0.046517 | 0.092515 | 0.091214 | 0.088093 | 0.08623 | 0.084834 | 0.083371 | 0.082029 | 0.079897 | 0.076429 | 0.074675 | 0.072805 | 0.068579 | 0.065517 | 0.065112 | 0.088452 | 0.086065 | 0.079869 | 0.076787 | 0.074281 | 0.071737 | 0.069546 | 0.066296 | 0.060607 | 0.059092 | 0.05678 | 0.050835 | 0.044165 | 0.043665
|  | LIDDESDALE | LW |  |  |  | 0.092327 | 0.087619 | 0.083019 | 0.078709 | 0.076085 | 0.072688 | 0.068923 | 0.068542 | 0.06276 | 0.059919 | 0.057399 | 0.052518 | 0.047141 | 0.048493 | 0.091717 | 0.089548 | 0.087514 | 0.085493 | 0.084178 | 0.082193 | 0.079866 | 0.078454 | 0.07512 | 0.072742 | 0.070715 | 0.067535 | 0.065449 | 0.065946 | 0.086686 | 0.082446 | 0.078374 | 0.074491 | 0.072085 | 0.068852 | 0.065326 | 0.06465 | 0.059238 | 0.056147 | 0.05364 | 0.048989 | 0.044246 | 0.045431
|  | LIDDESDALE | ST |  |  |  | 0.094529 | 0.09425 | 0.092019 | 0.087766 | 0.083823 | 0.0832 | 0.082334 | 0.079385 | 0.078035 | 0.074724 | 0.072995 | 0.056525 | 0.048092 | 0.047691 | 0.092682 | 0.092457 | 0.09147 | 0.089685 | 0.088008 | 0.087429 | 0.086725 | 0.08516 | 0.083964 | 0.08193 | 0.08035 | 0.069844 | 0.066047 | 0.065882 | 0.088658 | 0.08838 | 0.08638 | 0.082615 | 0.079159 | 0.078443 | 0.077573 | 0.074859 | 0.073517 | 0.070403 | 0.068449 | 0.052729 | 0.045151 | 0.044796
|  | LIDDESDALE | FS |  |  |  | 0.09458 | 0.09435 | 0.094047 | 0.091792 | 0.087658 | 0.087152 | 0.08654 | 0.085794 | 0.081638 | 0.078803 | 0.075852 | 0.061416 | 0.049995 | 0.048039 | 0.092723 | 0.092537 | 0.092294 | 0.091287 | 0.089582 | 0.089168 | 0.088675 | 0.088075 | 0.086165 | 0.084658 | 0.083018 | 0.074057 | 0.066828 | 0.066004 | 0.088709 | 0.088479 | 0.088179 | 0.086154 | 0.082488 | 0.081976 | 0.081368 | 0.080625 | 0.07688 | 0.074279 | 0.071562 | 0.057772 | 0.046835 | 0.045099
| KEITH | LIMEHILLOCKS | MINIMUM HEADROOM | NJ 52093 50703 | YES | YES | 1.0293 | 0.94188 | 0.85636 | 0.77228 | 0.61409 | 0.42001 | 0.29033 | 0.19373 | 0.084287 | -0.023068 | -0.12576 | -0.47108 | -0.93518 | -1.3309 | 1.6138 | 1.5964 | 1.5208 | 1.4472 | 1.3946 | 1.2376 | 1.1823 | 1.056 | 0.99684 | 0.94006 | 0.86196 | 0.4778 | 0.036808 | -0.40005 | 1.317 | 1.2497 | 1.1855 | 1.1168 | 0.93845 | 0.74908 | 0.64147 | 0.53972 | 0.4209 | 0.306 | 0.19749 | -0.22862 | -0.72786 | -1.1808
|  | LIMEHILLOCKS | CT |  |  |  | 1.104 | 1.0419 | 0.92472 | 0.79694 | 0.61409 | 0.42001 | 0.29033 | 0.19373 | 0.084287 | -0.023068 | -0.12576 | -0.46486 | -0.813 | -1.0745 | 1.6185 | 1.6019 | 1.5654 | 1.5208 | 1.397 | 1.2652 | 1.2151 | 1.1441 | 1.0676 | 0.99699 | 0.92172 | 0.59102 | 0.27414 | -0.038488 | 1.3688 | 1.3212 | 1.2258 | 1.1168 | 0.93845 | 0.74908 | 0.64147 | 0.53972 | 0.4209 | 0.306 | 0.19749 | -0.17804 | -0.53927 | -0.84488
|  | LIMEHILLOCKS | LW |  |  |  | 1.0293 | 0.94188 | 0.85636 | 0.77228 | 0.68585 | 0.58249 | 0.47339 | 0.38997 | 0.30057 | 0.21561 | 0.12653 | -0.10212 | -0.52505 | -1.0648 | 1.6138 | 1.5964 | 1.5807 | 1.5639 | 1.5472 | 1.5219 | 1.4889 | 1.4394 | 1.3861 | 1.3364 | 1.2845 | 1.119 | 0.65175 | 0.0011086 | 1.317 | 1.2497 | 1.1855 | 1.1205 | 1.0564 | 0.97345 | 0.8841 | 0.80017 | 0.71042 | 0.62502 | 0.53809 | 0.31363 | -0.18645 | -0.84975
|  | LIMEHILLOCKS | ST |  |  |  | 1.1453 | 1.1097 | 0.98607 | 0.88609 | 0.80289 | 0.63579 | 0.54424 | 0.39735 | 0.30299 | 0.20107 | 0.087275 | -0.47108 | -0.93518 | -1.3309 | 1.6292 | 1.6232 | 1.5208 | 1.4472 | 1.3946 | 1.2376 | 1.1823 | 1.056 | 0.99684 | 0.94006 | 0.86196 | 0.4778 | 0.036808 | -0.40005 | 1.3975 | 1.3715 | 1.242 | 1.1412 | 1.0614 | 0.87678 | 0.78974 | 0.63243 | 0.54072 | 0.44505 | 0.33111 | -0.22862 | -0.72786 | -1.1808
|  | LIMEHILLOCKS | FS |  |  |  | 1.1742 | 1.1456 | 1.0945 | 1.0398 | 0.98352 | 0.9249 | 0.86561 | 0.77634 | 0.69989 | 0.61021 | 0.52873 | 0.078482 | -0.20957 | -0.34816 | 1.633 | 1.6278 | 1.6025 | 1.5758 | 1.5457 | 1.5145 | 1.485 | 1.433 | 1.3931 | 1.3502 | 1.3073 | 1.1421 | 0.96965 | 0.83515 | 1.417 | 1.3958 | 1.3502 | 1.3012 | 1.2496 | 1.1957 | 1.1419 | 1.0576 | 0.9868 | 0.90598 | 0.82984 | 0.45439 | 0.19183 | 0.060658
| ARDMORE | LOCH CARNAN | MINIMUM HEADROOM | NF 83230 42735 | NO | YES | 9.7142 | 9.702 | 9.6818 | 9.6537 | 9.6323 | 9.6106 | 9.5842 | 9.5719 | 9.5621 | 9.5432 | 9.5329 | 9.4765 | 9.4566 | 9.4514 | 9.3324 | 9.3252 | 9.3097 | 9.2923 | 9.2801 | 9.2676 | 9.2515 | 9.2398 | 9.2289 | 9.2176 | 9.2061 | 9.1359 | 9.1138 | 9.1136 | 9.2254 | 9.214 | 9.1944 | 9.1681 | 9.1484 | 9.1284 | 9.104 | 9.092 | 9.08 | 9.0604 | 9.0477 | 8.9681 | 8.9398 | 8.9392
|  | LOCH CARNAN | CT |  |  |  | 9.7241 | 9.7086 | 9.6818 | 9.6537 | 9.6323 | 9.6106 | 9.5842 | 9.5719 | 9.5621 | 9.5432 | 9.5332 | 9.5027 | 9.4854 | 9.4708 | 9.3363 | 9.3256 | 9.3097 | 9.2923 | 9.2801 | 9.2676 | 9.2515 | 9.2398 | 9.2289 | 9.2176 | 9.2061 | 9.1771 | 9.1698 | 9.1567 | 9.2338 | 9.2166 | 9.1944 | 9.1681 | 9.1484 | 9.1284 | 9.104 | 9.092 | 9.08 | 9.0604 | 9.0486 | 9.0175 | 9.0017 | 8.9883
|  | LOCH CARNAN | LW |  |  |  | 9.7142 | 9.702 | 9.6869 | 9.6708 | 9.6577 | 9.6333 | 9.6153 | 9.5965 | 9.5754 | 9.5567 | 9.5329 | 9.4765 | 9.4566 | 9.4514 | 9.3324 | 9.3252 | 9.3172 | 9.3082 | 9.3005 | 9.2865 | 9.2738 | 9.2598 | 9.2439 | 9.2272 | 9.2091 | 9.1359 | 9.1138 | 9.1136 | 9.2254 | 9.214 | 9.2002 | 9.1853 | 9.1731 | 9.1504 | 9.1331 | 9.1138 | 9.0918 | 9.0718 | 9.0477 | 8.9681 | 8.9398 | 8.9392
|  | LOCH CARNAN | ST |  |  |  | 9.7273 | 9.7201 | 9.717 | 9.7076 | 9.703 | 9.6936 | 9.6793 | 9.6706 | 9.6564 | 9.6366 | 9.6184 | 9.5231 | 9.4894 | 9.4816 | 9.3381 | 9.3344 | 9.332 | 9.3268 | 9.323 | 9.3171 | 9.3087 | 9.3016 | 9.2917 | 9.2788 | 9.2656 | 9.1757 | 9.1436 | 9.1427 | 9.2351 | 9.2307 | 9.2276 | 9.219 | 9.2144 | 9.2056 | 9.1923 | 9.1835 | 9.1693 | 9.1502 | 9.1318 | 9.0194 | 8.9786 | 8.9767
|  | LOCH CARNAN | FS |  |  |  | 9.73 | 9.7268 | 9.7245 | 9.7183 | 9.7082 | 9.7045 | 9.6968 | 9.6897 | 9.6786 | 9.6678 | 9.6561 | 9.5737 | 9.4977 | 9.4583 | 9.3394 | 9.3374 | 9.3356 | 9.3321 | 9.3271 | 9.3242 | 9.3194 | 9.3145 | 9.3078 | 9.3006 | 9.2928 | 9.2361 | 9.1703 | 9.1156 | 9.2361 | 9.2351 | 9.2337 | 9.2287 | 9.2196 | 9.216 | 9.2087 | 9.202 | 9.1916 | 9.1809 | 9.1695 | 9.0886 | 9.0111 | 8.9432
| GRUDIE BRIDGE | LOCH GLASCARNOCH | MINIMUM HEADROOM | NH 31620 71996 | YES | YES | 0.58819 | 0.58819 | 0.57587 | 0.56754 | 0.56204 | 0.54313 | 0.53787 | 0.52365 | 0.5186 | 0.51433 | 0.50751 | 0.47551 | 0.42855 | 0.38035 | 0.54374 | 0.54374 | 0.52834 | 0.51793 | 0.51106 | 0.48742 | 0.48084 | 0.46306 | 0.45676 | 0.45142 | 0.44289 | 0.40289 | 0.34419 | 0.28394 | 0.5435 | 0.5435 | 0.5281 | 0.51769 | 0.51081 | 0.48717 | 0.4806 | 0.46282 | 0.45651 | 0.45118 | 0.44264 | 0.40265 | 0.34394 | 0.2837
|  | LOCH GLASCARNOCH | CT |  |  |  | 0.58819 | 0.58819 | 0.58659 | 0.58374 | 0.57004 | 0.55544 | 0.55174 | 0.54527 | 0.53878 | 0.53317 | 0.527 | 0.49425 | 0.46336 | 0.43002 | 0.54374 | 0.54374 | 0.54174 | 0.53818 | 0.52106 | 0.5028 | 0.49817 | 0.49009 | 0.48198 | 0.47497 | 0.46726 | 0.42632 | 0.38771 | 0.34602 | 0.5435 | 0.5435 | 0.54149 | 0.53793 | 0.52081 | 0.50256 | 0.49793 | 0.48985 | 0.48174 | 0.47472 | 0.46701 | 0.42608 | 0.38746 | 0.34578
|  | LOCH GLASCARNOCH | LW |  |  |  | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58819 | 0.58566 | 0.58304 | 0.58088 | 0.57845 | 0.56568 | 0.50834 | 0.42432 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54374 | 0.54058 | 0.5373 | 0.5346 | 0.53157 | 0.5156 | 0.44393 | 0.33891 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.5435 | 0.54034 | 0.53706 | 0.53436 | 0.53132 | 0.51536 | 0.44368 | 0.33866
|  | LOCH GLASCARNOCH | ST |  |  |  | 0.58819 | 0.58819 | 0.57587 | 0.56754 | 0.56204 | 0.54313 | 0.53787 | 0.52365 | 0.5186 | 0.51433 | 0.50751 | 0.47551 | 0.42855 | 0.38035 | 0.54374 | 0.54374 | 0.52834 | 0.51793 | 0.51106 | 0.48742 | 0.48084 | 0.46306 | 0.45676 | 0.45142 | 0.44289 | 0.40289 | 0.34419 | 0.28394 | 0.5435 | 0.5435 | 0.5281 | 0.51769 | 0.51081 | 0.48717 | 0.4806 | 0.46282 | 0.45651 | 0.45118 | 0.44264 | 0.40265 | 0.34394 | 0.2837
|  | LOCH GLASCARNOCH | FS |  |  |  | 0.58819 | 0.58819 | 0.58567 | 0.58316 | 0.58022 | 0.57728 | 0.57476 | 0.56962 | 0.56612 | 0.56263 | 0.55914 | 0.55491 | 0.55197 | 0.54659 | 0.54374 | 0.54374 | 0.54059 | 0.53745 | 0.53378 | 0.53011 | 0.52696 | 0.52052 | 0.51616 | 0.51179 | 0.50743 | 0.50214 | 0.49847 | 0.49174 | 0.5435 | 0.5435 | 0.54035 | 0.5372 | 0.53353 | 0.52986 | 0.52671 | 0.52028 | 0.51591 | 0.51155 | 0.50718 | 0.50189 | 0.49823 | 0.49149
| FORT WILLIAM | LOCHALINE | MINIMUM HEADROOM | NM 67939 45444 | YES | YES | 0.26223 | 0.2479 | 0.23246 | 0.21425 | 0.19536 | 0.17387 | 0.14984 | 0.14419 | 0.1382 | 0.1279 | 0.11875 | 0.1009 | 0.089386 | 0.080316 | 0.26309 | 0.25605 | 0.24877 | 0.23793 | 0.22912 | 0.21979 | 0.20884 | 0.19928 | 0.18771 | 0.17657 | 0.16609 | 0.15139 | 0.14324 | 0.13469 | 0.1235 | 0.11623 | 0.10869 | 0.099437 | 0.090141 | 0.079531 | 0.068254 | 0.064793 | 0.059581 | 0.053659 | 0.047229 | 0.036035 | 0.031594 | 0.029166
|  | LOCHALINE | CT |  |  |  | 0.27234 | 0.2625 | 0.24089 | 0.21523 | 0.19536 | 0.17387 | 0.14984 | 0.14419 | 0.1382 | 0.1279 | 0.11875 | 0.111 | 0.090551 | 0.080316 | 0.26663 | 0.26127 | 0.25047 | 0.23793 | 0.22912 | 0.21979 | 0.20964 | 0.20222 | 0.19196 | 0.18024 | 0.1704 | 0.15346 | 0.14324 | 0.13469 | 0.1271 | 0.12217 | 0.11158 | 0.099437 | 0.090141 | 0.079531 | 0.068254 | 0.064793 | 0.061209 | 0.056086 | 0.050396 | 0.043529 | 0.034661 | 0.030829
|  | LOCHALINE | LW |  |  |  | 0.26223 | 0.2479 | 0.23246 | 0.21425 | 0.20117 | 0.18021 | 0.15607 | 0.14971 | 0.13854 | 0.12918 | 0.11916 | 0.1009 | 0.089386 | 0.086982 | 0.26309 | 0.25605 | 0.24877 | 0.24015 | 0.2338 | 0.22224 | 0.20884 | 0.19928 | 0.18771 | 0.17657 | 0.16609 | 0.15139 | 0.14714 | 0.1463 | 0.1235 | 0.11623 | 0.10869 | 0.10043 | 0.09365 | 0.082925 | 0.07075 | 0.066444 | 0.059581 | 0.053659 | 0.047229 | 0.036035 | 0.031594 | 0.030454
|  | LOCHALINE | ST |  |  |  | 0.27577 | 0.27034 | 0.26468 | 0.25818 | 0.25169 | 0.24056 | 0.23658 | 0.22598 | 0.21575 | 0.20503 | 0.18765 | 0.13222 | 0.11187 | 0.095515 | 0.26838 | 0.26586 | 0.26291 | 0.25915 | 0.25527 | 0.24953 | 0.24532 | 0.23849 | 0.23089 | 0.22246 | 0.21153 | 0.16423 | 0.15148 | 0.14266 | 0.12952 | 0.12722 | 0.12434 | 0.12138 | 0.11815 | 0.11249 | 0.11007 | 0.10414 | 0.098887 | 0.092461 | 0.082875 | 0.051085 | 0.040942 | 0.033922
|  | LOCHALINE | FS |  |  |  | 0.27766 | 0.27461 | 0.27105 | 0.26337 | 0.25934 | 0.25308 | 0.24615 | 0.2353 | 0.23114 | 0.21891 | 0.21189 | 0.14528 | 0.10446 | 0.089366 | 0.26914 | 0.26736 | 0.26521 | 0.26153 | 0.25887 | 0.25519 | 0.25097 | 0.24524 | 0.24089 | 0.23385 | 0.22791 | 0.18346 | 0.14809 | 0.13705 | 0.13057 | 0.129 | 0.12753 | 0.12379 | 0.12222 | 0.11896 | 0.11571 | 0.1101 | 0.10789 | 0.10162 | 0.098175 | 0.062859 | 0.0397 | 0.029166
| GRUDIE BRIDGE | LOCHCARRON | MINIMUM HEADROOM | NG 91944 41839 | YES | YES | [14 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: Demand Headroom Winter MVA 2025 to Demand Headroom Winter MVA 2050
|  | LOCHCARRON | CT | [17 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: Demand Headroom Winter MVA 2025 to Demand Headroom Winter MVA 2050
|  | LOCHCARRON | LW | [17 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: Demand Headroom Winter MVA 2025 to Demand Headroom Winter MVA 2050
|  | LOCHCARRON | ST | [17 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: Demand Headroom Winter MVA 2025 to Demand Headroom Winter MVA 2050
|  | LOCHCARRON | FS | [17 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: Demand Headroom Winter MVA 2025 to Demand Headroom Winter MVA 2050
| TAYNUILT | LOCHDONHEAD | MINIMUM HEADROOM | NM 72902 34134 | YES | YES | 0.11948 | 0.098408 | 0.07672 | 0.048394 | 0.019499 | -0.011968 | -0.042181 | -0.06693 | -0.096774 | -0.12608 | -0.1526 | -0.20476 | -0.22667 | -0.25331 | 0.418 | 0.40701 | 0.39597 | 0.379 | 0.36374 | 0.34783 | 0.33228 | 0.31989 | 0.30494 | 0.28989 | 0.27475 | 0.24178 | 0.21621 | 0.1948 | 0.18918 | 0.17053 | 0.1479 | 0.12518 | 0.10281 | 0.078539 | 0.053446 | 0.027527 | 0.0069651 | -0.020271 | -0.046834 | -0.13206 | -0.18605 | -0.21673
|  | LOCHDONHEAD | CT |  |  |  | 0.12032 | 0.11157 | 0.08349 | 0.049858 | 0.019499 | -0.011968 | -0.042181 | -0.062478 | -0.089659 | -0.11435 | -0.14013 | -0.19225 | -0.22667 | -0.23797 | 0.42021 | 0.41212 | 0.39597 | 0.379 | 0.36374 | 0.34783 | 0.33228 | 0.31989 | 0.30494 | 0.29101 | 0.27582 | 0.24178 | 0.22348 | 0.21341 | 0.18918 | 0.17053 | 0.1479 | 0.12518 | 0.10281 | 0.078539 | 0.053446 | 0.027527 | 0.0069651 | -0.013613 | -0.041109 | -0.11536 | -0.13332 | -0.13908
|  | LOCHDONHEAD | LW |  |  |  | 0.11948 | 0.098408 | 0.07672 | 0.048394 | 0.028282 | -0.0044466 | -0.040692 | -0.06693 | -0.096774 | -0.12608 | -0.1526 | -0.20476 | -0.22224 | -0.23357 | 0.418 | 0.40701 | 0.39656 | 0.38303 | 0.37313 | 0.35654 | 0.33797 | 0.32318 | 0.30646 | 0.28989 | 0.27475 | 0.24549 | 0.23747 | 0.23247 | 0.19224 | 0.17706 | 0.16391 | 0.14555 | 0.12773 | 0.09804 | 0.064744 | 0.038537 | 0.0089993 | -0.020271 | -0.046834 | -0.096288 | -0.11069 | -0.12085
|  | LOCHDONHEAD | ST |  |  |  | 0.13092 | 0.1273 | 0.12297 | 0.11535 | 0.1032 | 0.091918 | 0.077356 | 0.057198 | 0.036105 | 0.013151 | -0.011027 | -0.157 | -0.21016 | -0.2327 | 0.42721 | 0.42334 | 0.41892 | 0.41348 | 0.4067 | 0.4001 | 0.39166 | 0.38031 | 0.36788 | 0.35429 | 0.33946 | 0.25653 | 0.21621 | 0.20589 | 0.20165 | 0.19493 | 0.18713 | 0.1777 | 0.16561 | 0.15195 | 0.13518 | 0.11435 | 0.09022 | 0.062025 | 0.031415 | -0.13206 | -0.18605 | -0.202
|  | LOCHDONHEAD | FS |  |  |  | 0.13466 | 0.13147 | 0.1279 | 0.12337 | 0.11065 | 0.1051 | 0.089216 | 0.076288 | 0.060582 | 0.043116 | 0.023246 | -0.09907 | -0.19225 | -0.25331 | 0.42979 | 0.42654 | 0.42266 | 0.41823 | 0.41128 | 0.40778 | 0.3995 | 0.39235 | 0.38367 | 0.37401 | 0.3629 | 0.29314 | 0.23474 | 0.1948 | 0.20488 | 0.20033 | 0.1938 | 0.18647 | 0.1764 | 0.16766 | 0.15495 | 0.14171 | 0.12631 | 0.10886 | 0.089557 | -0.037456 | -0.14914 | -0.21673
| KILLIN | LOCHEARNHEAD | MINIMUM HEADROOM | NN 58766 24177 | YES | YES | -0.37771 | -0.44924 | -0.51676 | -0.59517 | -0.66683 | -0.76028 | -0.85389 | -0.91725 | -0.99481 | -1.0723 | -1.1469 | -1.3064 | -1.402 | -1.476 | 0.20229 | 0.16461 | 0.13032 | 0.08806 | 0.044462 | 0.0012276 | -0.055726 | -0.10848 | -0.16906 | -0.23021 | -0.28708 | -0.38609 | -0.46122 | -0.53048 | -0.13527 | -0.14901 | -0.20192 | -0.26741 | -0.32747 | -0.40401 | -0.48004 | -0.52785 | -0.58205 | -0.6559 | -0.72716 | -0.8729 | -0.95505 | -1.019
|  | LOCHEARNHEAD | CT |  |  |  | -0.33273 | -0.37371 | -0.46542 | -0.5656 | -0.65375 | -0.73587 | -0.82873 | -0.88123 | -0.95338 | -1.0198 | -1.0918 | -1.2533 | -1.402 | -1.476 | 0.21781 | 0.19231 | 0.14234 | 0.08806 | 0.044462 | 0.0022591 | -0.043884 | -0.083998 | -0.14234 | -0.19948 | -0.25435 | -0.37975 | -0.46122 | -0.53048 | -0.13363 | -0.14446 | -0.1629 | -0.24045 | -0.31442 | -0.38289 | -0.46121 | -0.50167 | -0.55464 | -0.60571 | -0.67427 | -0.82528 | -0.95505 | -1.019
|  | LOCHEARNHEAD | LW |  |  |  | -0.37771 | -0.44924 | -0.51676 | -0.59517 | -0.66683 | -0.76028 | -0.85389 | -0.91725 | -0.99481 | -1.0723 | -1.1469 | -1.3064 | -1.3987 | -1.4487 | 0.20229 | 0.16461 | 0.13032 | 0.090105 | 0.054551 | 0.0012276 | -0.055726 | -0.10848 | -0.16906 | -0.23021 | -0.28708 | -0.38609 | -0.4237 | -0.44542 | -0.13527 | -0.14901 | -0.20192 | -0.26741 | -0.32747 | -0.40401 | -0.48004 | -0.52785 | -0.58205 | -0.6559 | -0.72716 | -0.8729 | -0.95192 | -0.99377
|  | LOCHEARNHEAD | ST |  |  |  | -0.30166 | -0.32495 | -0.36104 | -0.39581 | -0.43566 | -0.4825 | -0.53253 | -0.58072 | -0.63817 | -0.70197 | -0.76637 | -1.1105 | -1.2523 | -1.3335 | 0.23196 | 0.21918 | 0.20072 | 0.1808 | 0.15811 | 0.13113 | 0.101 | 0.068984 | 0.030443 | -0.013114 | -0.061097 | -0.31552 | -0.40796 | -0.47476 | -0.13051 | -0.13458 | -0.14013 | -0.14771 | -0.15618 | -0.17084 | -0.21212 | -0.25165 | -0.29876 | -0.35094 | -0.39959 | -0.69599 | -0.82349 | -0.89276
|  | LOCHEARNHEAD | FS |  |  |  | -0.27995 | -0.29985 | -0.32545 | -0.35881 | -0.39384 | -0.42838 | -0.4667 | -0.50859 | -0.5561 | -0.61069 | -0.6654 | -1.0301 | -1.2836 | -1.3626 | 0.24002 | 0.22892 | 0.21516 | 0.19728 | 0.17831 | 0.15827 | 0.13557 | 0.11017 | 0.081103 | 0.047953 | 0.013121 | -0.22222 | -0.41974 | -0.5066 | -0.12976 | -0.1331 | -0.13755 | -0.14345 | -0.14977 | -0.15732 | -0.1661 | -0.18932 | -0.22823 | -0.27271 | -0.31717 | -0.61331 | -0.85089 | -0.91995
| LYNDHURST | LOCHEE | MINIMUM HEADROOM | NO 38065 31416 | NO | YES | 16.5442 | 16.356 | 16.1827 | 16.0233 | 15.8343 | 15.6181 | 15.3784 | 15.1485 | 14.8961 | 14.6465 | 14.4061 | 13.7738 | 13.2278 | 12.5508 | 17.6123 | 17.509 | 17.3757 | 17.2517 | 17.0986 | 16.9699 | 16.8401 | 16.6866 | 16.5089 | 16.3307 | 16.1472 | 15.2911 | 14.1851 | 11.6636 | 17.0817 | 16.9217 | 16.763 | 16.6163 | 16.4405 | 16.2431 | 16.0198 | 15.793 | 15.5453 | 15.3014 | 15.0655 | 14.4375 | 13.7985 | 12.9715
|  | LOCHEE | CT |  |  |  | 16.6161 | 16.4604 | 16.2563 | 16.0597 | 15.8531 | 15.6754 | 15.487 | 15.2959 | 15.0623 | 14.8306 | 14.6043 | 13.9097 | 13.469 | 13.1087 | 17.6123 | 17.509 | 17.3757 | 17.2517 | 17.0986 | 16.9699 | 16.8401 | 16.6866 | 16.5089 | 16.3307 | 16.1472 | 15.2911 | 14.3436 | 12.9612 | 17.1452 | 17.0127 | 16.8217 | 16.637 | 16.4405 | 16.2709 | 16.0971 | 15.9081 | 15.68 | 15.4546 | 15.234 | 14.5501 | 14.0856 | 13.6771
|  | LOCHEE | LW |  |  |  | 16.5442 | 16.356 | 16.1827 | 16.0233 | 15.8343 | 15.6181 | 15.3784 | 15.1485 | 14.8961 | 14.6465 | 14.4061 | 13.7738 | 13.2278 | 12.5508 | 17.6143 | 17.517 | 17.4242 | 17.347 | 17.2399 | 17.1296 | 17.0011 | 16.8512 | 16.6877 | 16.5281 | 16.3555 | 15.8479 | 15.2446 | 14.4253 | 17.0817 | 16.9217 | 16.763 | 16.6163 | 16.443 | 16.2431 | 16.0198 | 15.793 | 15.5453 | 15.3014 | 15.0655 | 14.4375 | 13.7985 | 12.9715
|  | LOCHEE | ST |  |  |  | 16.6854 | 16.5904 | 16.5367 | 16.4928 | 16.4221 | 16.3504 | 16.2765 | 16.1444 | 16.0205 | 15.8868 | 15.7308 | 14.8688 | 14.297 | 13.7351 | 17.6457 | 17.579 | 17.51 | 17.4556 | 17.3714 | 17.2851 | 17.2027 | 17.05 | 16.9263 | 16.7943 | 16.6358 | 15.6244 | 14.4869 | 12.9475 | 17.2079 | 17.1333 | 17.0767 | 17.0307 | 16.9601 | 16.8837 | 16.811 | 16.6649 | 16.5405 | 16.4072 | 16.2488 | 15.3848 | 14.7543 | 14.1307
|  | LOCHEE | FS |  |  |  | 16.68 | 16.6072 | 16.5614 | 16.5221 | 16.4553 | 16.4004 | 16.35 | 16.2578 | 16.1609 | 16.0596 | 15.9559 | 15.3265 | 14.7014 | 14.334 | 17.6391 | 17.5783 | 17.5208 | 17.4684 | 17.3886 | 17.3178 | 17.2416 | 17.1253 | 17.0025 | 16.8684 | 16.7244 | 15.7789 | 14.1851 | 11.6636 | 17.2036 | 17.1479 | 17.1041 | 17.0659 | 17.0019 | 16.9491 | 16.8995 | 16.8061 | 16.7109 | 16.6111 | 16.5084 | 15.9068 | 15.3095 | 14.9632
| PORT ANN | LOCHGILPHEAD | MINIMUM HEADROOM | NR 86092 88371 | NO | YES | 15.6892 | 15.0406 | 14.322 | 14.0077 | 13.5429 | 13.0717 | 12.6033 | 12.3207 | 12.0164 | 11.7033 | 11.4049 | 10.5625 | 9.8777 | 9.1447 | 16.8037 | 16.1333 | 15.4216 | 15.1654 | 14.8888 | 14.6299 | 14.3882 | 14.1823 | 13.9593 | 13.7329 | 13.475 | 12.8062 | 12.1738 | 11.3779 | 15.4624 | 14.7348 | 13.9404 | 13.583 | 13.1973 | 12.8302 | 12.4765 | 12.2397 | 11.9845 | 11.7216 | 11.4066 | 10.5603 | 9.863 | 9.0051
|  | LOCHGILPHEAD | CT |  |  |  | 15.8292 | 15.242 | 14.5542 | 14.2157 | 13.7472 | 13.2256 | 12.7199 | 12.4637 | 12.2013 | 11.9454 | 11.6829 | 11.0051 | 10.2907 | 9.9035 | 17.0076 | 16.4107 | 15.6833 | 15.3518 | 15.045 | 14.7576 | 14.4939 | 14.2989 | 14.11 | 13.9251 | 13.7311 | 13.0056 | 12.4181 | 11.8737 | 15.5565 | 15.1101 | 14.2668 | 13.8208 | 13.3763 | 12.9465 | 12.5318 | 12.2924 | 12.0952 | 11.9054 | 11.673 | 10.9574 | 10.2911 | 9.863
|  | LOCHGILPHEAD | LW |  |  |  | 15.6892 | 15.0406 | 14.322 | 14.0077 | 13.5429 | 13.0717 | 12.6033 | 12.3207 | 12.0164 | 11.7033 | 11.4049 | 10.5625 | 9.8777 | 9.1447 | 16.8037 | 16.1333 | 15.4216 | 15.1654 | 14.8888 | 14.6299 | 14.3882 | 14.1823 | 13.9593 | 13.7329 | 13.475 | 12.8062 | 12.1738 | 11.3779 | 15.4624 | 14.7348 | 13.9404 | 13.583 | 13.1973 | 12.8302 | 12.4765 | 12.2397 | 11.9845 | 11.7216 | 11.4066 | 10.5603 | 9.863 | 9.0051
|  | LOCHGILPHEAD | ST |  |  |  | 15.9643 | 15.4578 | 14.9262 | 14.7915 | 14.6548 | 14.5282 | 14.4191 | 14.2569 | 14.1343 | 13.9966 | 13.836 | 12.3889 | 11.7586 | 11.2247 | 17.1322 | 16.6098 | 16.0519 | 15.8868 | 15.7203 | 15.5627 | 15.4243 | 15.2233 | 15.0694 | 14.9021 | 14.7104 | 13.6084 | 12.9021 | 12.2307 | 15.5736 | 15.251 | 14.8806 | 14.687 | 14.4895 | 14.2979 | 14.1188 | 13.8725 | 13.6651 | 13.4395 | 13.1861 | 11.7151 | 10.85 | 10.272
|  | LOCHGILPHEAD | FS |  |  |  | 16.1862 | 15.7991 | 15.3849 | 15.2308 | 15.1342 | 15.0037 | 14.9233 | 14.804 | 14.625 | 14.4675 | 14.2577 | 12.7591 | 11.73 | 11.2506 | 17.3571 | 16.9554 | 16.5072 | 16.3142 | 16.1779 | 16.0068 | 15.8849 | 15.7205 | 15.4973 | 15.2936 | 15.1221 | 14.0653 | 13.1726 | 12.462 | 15.7184 | 15.4726 | 15.2072 | 15.0844 | 14.9038 | 14.6903 | 14.5223 | 14.3192 | 14.0605 | 13.8195 | 13.6074 | 12.2863 | 11.4084 | 10.8103
| CLACHAN | LOCHGOILHEAD | MINIMUM HEADROOM | NN 20159 01862 | YES | YES | -0.96866 | -0.97881 | -0.99718 | -1.0134 | -1.0414 | -1.0722 | -1.0958 | -1.1111 | -1.1314 | -1.1502 | -1.1713 | -1.2246 | -1.2654 | -1.3076 | 0.34995 | 0.34943 | 0.33823 | 0.33006 | 0.32456 | 0.30586 | 0.29595 | 0.28625 | 0.27809 | 0.27119 | 0.2618 | 0.21429 | 0.166 | 0.11574 | -0.95643 | -0.95889 | -0.96886 | -0.97803 | -0.98466 | -1.0044 | -1.0115 | -1.0276 | -1.0357 | -1.0435 | -1.0541 | -1.1058 | -1.1537 | -1.1995
|  | LOCHGOILHEAD | CT |  |  |  | -0.95927 | -0.97023 | -0.98816 | -1.0134 | -1.0414 | -1.0722 | -1.0958 | -1.1111 | -1.1314 | -1.1502 | -1.1713 | -1.2246 | -1.2654 | -1.301 | 0.35006 | 0.34961 | 0.34737 | 0.34381 | 0.32645 | 0.30586 | 0.29595 | 0.28719 | 0.27809 | 0.27119 | 0.2618 | 0.22422 | 0.18826 | 0.15257 | -0.95611 | -0.95796 | -0.96272 | -0.96903 | -0.98422 | -1.0004 | -1.0062 | -1.0164 | -1.0282 | -1.0393 | -1.0502 | -1.0924 | -1.141 | -1.1842
|  | LOCHGOILHEAD | LW |  |  |  | -0.96866 | -0.97881 | -0.99718 | -1.0117 | -1.0271 | -1.0482 | -1.0709 | -1.0872 | -1.1073 | -1.1289 | -1.1487 | -1.1825 | -1.2365 | -1.3076 | 0.34995 | 0.34943 | 0.34887 | 0.34818 | 0.34279 | 0.33674 | 0.33045 | 0.32514 | 0.31886 | 0.31231 | 0.30602 | 0.2871 | 0.22818 | 0.14643 | -0.95643 | -0.95889 | -0.96094 | -0.96343 | -0.96544 | -0.96951 | -0.97434 | -0.98232 | -0.99085 | -0.99909 | -1.007 | -1.0358 | -1.1023 | -1.1894
|  | LOCHGOILHEAD | ST |  |  |  | -0.95401 | -0.9572 | -0.97095 | -0.98389 | -0.99239 | -1.0162 | -1.028 | -1.048 | -1.0669 | -1.08 | -1.103 | -1.1972 | -1.2511 | -1.2958 | 0.35025 | 0.35009 | 0.33823 | 0.33006 | 0.32456 | 0.30623 | 0.30079 | 0.28625 | 0.27883 | 0.27176 | 0.26191 | 0.21429 | 0.166 | 0.11574 | -0.95557 | -0.95626 | -0.96886 | -0.97803 | -0.98466 | -1.0044 | -1.0115 | -1.0276 | -1.0357 | -1.0435 | -1.0541 | -1.1058 | -1.1537 | -1.1995
|  | LOCHGOILHEAD | FS |  |  |  | -0.95421 | -0.95434 | -0.96088 | -0.96873 | -0.97828 | -0.98317 | -0.99378 | -1.0086 | -1.0177 | -1.0318 | -1.0438 | -1.1184 | -1.1719 | -1.1862 | 0.35027 | 0.35017 | 0.34763 | 0.34505 | 0.34202 | 0.33901 | 0.33628 | 0.33098 | 0.32724 | 0.32206 | 0.31658 | 0.29586 | 0.2801 | 0.2685 | -0.95544 | -0.95601 | -0.95913 | -0.9625 | -0.96633 | -0.97038 | -0.97427 | -0.98097 | -0.98639 | -0.99208 | -0.99807 | -1.0191 | -1.0363 | -1.0442
| GRUDIE BRIDGE | LOCHINVER | MINIMUM HEADROOM | NC 09516 22243 | YES | YES | -0.80766 | -0.86985 | -0.92676 | -1.0228 | -1.0885 | -1.1446 | -1.2041 | -1.2612 | -1.3213 | -1.3809 | -1.4382 | -1.5359 | -1.574 | -1.6002 | -0.81652 | -0.8609 | -0.88863 | -0.95672 | -0.98673 | -1.0248 | -1.0755 | -1.1209 | -1.1691 | -1.2179 | -1.2662 | -1.354 | -1.3785 | -1.4136 | -1.2221 | -1.2856 | -1.3445 | -1.4361 | -1.4968 | -1.5634 | -1.6345 | -1.6915 | -1.751 | -1.8146 | -1.8799 | -1.9975 | -2.0412 | -2.0596
|  | LOCHINVER | CT |  |  |  | -0.7417 | -0.81011 | -0.90097 | -0.99126 | -1.0621 | -1.1381 | -1.2041 | -1.2282 | -1.2801 | -1.3357 | -1.3878 | -1.4976 | -1.5682 | -1.6002 | -0.76826 | -0.82466 | -0.88299 | -0.94034 | -0.97947 | -1.0154 | -1.0554 | -1.0875 | -1.1327 | -1.177 | -1.2197 | -1.3307 | -1.3775 | -1.4136 | -1.1608 | -1.2188 | -1.3105 | -1.408 | -1.479 | -1.5498 | -1.6102 | -1.649 | -1.7068 | -1.7658 | -1.8244 | -1.9503 | -2.0242 | -2.0596
|  | LOCHINVER | LW |  |  |  | -0.80766 | -0.86985 | -0.92676 | -1.0228 | -1.0885 | -1.1446 | -1.2033 | -1.2612 | -1.3213 | -1.3809 | -1.4382 | -1.5359 | -1.574 | -1.5896 | -0.81652 | -0.8609 | -0.88863 | -0.95672 | -0.98673 | -1.0248 | -1.0755 | -1.1209 | -1.1691 | -1.2179 | -1.2662 | -1.354 | -1.3785 | -1.3869 | -1.2221 | -1.2856 | -1.3445 | -1.4361 | -1.4968 | -1.5634 | -1.6345 | -1.6915 | -1.751 | -1.8146 | -1.8799 | -1.9975 | -2.0412 | -2.0572
|  | LOCHINVER | ST |  |  |  | -0.72231 | -0.76556 | -0.80909 | -0.85333 | -0.89035 | -0.92381 | -0.94909 | -0.97924 | -1.0144 | -1.052 | -1.0977 | -1.3515 | -1.4349 | -1.4685 | -0.76008 | -0.79923 | -0.83614 | -0.87468 | -0.9036 | -0.93013 | -0.94555 | -0.96447 | -0.98762 | -1.0144 | -1.0482 | -1.2502 | -1.3065 | -1.3381 | -1.1353 | -1.1719 | -1.2121 | -1.2534 | -1.2896 | -1.3215 | -1.3493 | -1.3832 | -1.4232 | -1.4653 | -1.5146 | -1.7864 | -1.856 | -1.8913
|  | LOCHINVER | FS |  |  |  | -0.58618 | -0.62041 | -0.66179 | -0.70012 | -0.73317 | -0.76951 | -0.80522 | -0.84458 | -0.88382 | -0.92743 | -0.97737 | -1.2605 | -1.4449 | -1.5162 | -0.6283 | -0.6592 | -0.69354 | -0.72386 | -0.74795 | -0.77343 | -0.80024 | -0.82878 | -0.85897 | -0.89111 | -0.93027 | -1.163 | -1.3291 | -1.3921 | -1.0257 | -1.0551 | -1.0943 | -1.1308 | -1.1619 | -1.1975 | -1.2319 | -1.2718 | -1.312 | -1.3576 | -1.4088 | -1.7002 | -1.9039 | -1.9585
| LUNANHEAD | LOCHSIDE | MINIMUM HEADROOM | NO 45151 50548 | NO | YES | 5.9784 | 4.9973 | 3.5945 | 2.6344 | 1.5402 | 0.29689 | -0.68766 | -1.5497 | -2.1003 | -2.6955 | -3.2859 | -5.0109 | -5.5564 | -5.8611 | 7.2694 | 6.4075 | 5.2488 | 4.5263 | 3.6297 | 2.6014 | 1.8055 | 1.1076 | 0.75178 | 0.38344 | 0.013949 | -1.0534 | -1.3532 | -1.6163 | 6.6593 | 5.7082 | 4.333 | 3.3728 | 2.2337 | 0.925 | -0.11408 | -0.99184 | -1.5452 | -2.1128 | -2.6756 | -4.3099 | -4.8216 | -5.1294
|  | LOCHSIDE | CT |  |  |  | 6.394 | 5.5433 | 4.3295 | 3.5659 | 2.6872 | 1.6898 | 0.94945 | 0.060654 | -0.48774 | -1.0508 | -1.6378 | -3.7 | -4.7539 | -5.288 | 7.5111 | 6.7213 | 5.7519 | 5.2189 | 4.5394 | 3.7504 | 3.2011 | 2.5175 | 2.1593 | 1.8024 | 1.4431 | 0.10691 | -0.71004 | -1.5828 | 7.0428 | 6.2189 | 5.0493 | 4.3009 | 3.4116 | 2.4042 | 1.6763 | 0.80553 | 0.24605 | -0.31215 | -0.85724 | -2.7545 | -3.6976 | -4.1787
|  | LOCHSIDE | LW |  |  |  | 5.9784 | 4.9973 | 3.5945 | 2.6344 | 1.5402 | 0.29689 | -0.68766 | -1.5497 | -2.1003 | -2.6955 | -3.2859 | -5.0109 | -5.5564 | -5.8611 | 7.2694 | 6.4075 | 5.2488 | 4.5263 | 3.6297 | 2.6014 | 1.8055 | 1.1076 | 0.75178 | 0.38344 | 0.013949 | -1.0534 | -1.3532 | -1.5784 | 6.6593 | 5.7082 | 4.333 | 3.3728 | 2.2337 | 0.925 | -0.11408 | -0.99184 | -1.5452 | -2.1128 | -2.6756 | -4.3099 | -4.8216 | -5.1294
|  | LOCHSIDE | ST |  |  |  | 6.5672 | 5.8396 | 4.8833 | 4.4542 | 4.0902 | 3.4235 | 2.9976 | 2.4344 | 2.1977 | 1.9426 | 1.665 | -0.6202 | -1.444 | -2.4142 | 7.5965 | 6.875 | 5.8775 | 5.4593 | 5.122 | 4.4336 | 3.991 | 3.4446 | 3.2223 | 2.9808 | 2.712 | 1.1342 | 0.17234 | -0.92856 | 7.2019 | 6.5017 | 5.5296 | 5.0789 | 4.7017 | 3.9716 | 3.5171 | 2.9493 | 2.6917 | 2.4112 | 2.1022 | 0.20027 | -0.79441 | -1.7554
|  | LOCHSIDE | FS |  |  |  | 7.0129 | 6.4472 | 5.7701 | 5.4136 | 5.1121 | 4.6965 | 4.3399 | 3.8243 | 3.4585 | 3.1104 | 2.796 | 0.91522 | -0.8722 | -2.1829 | 8.0317 | 7.4819 | 6.8416 | 6.5109 | 6.2346 | 5.8472 | 5.494 | 5.0033 | 4.6603 | 4.3294 | 4.0249 | 2.284 | 0.47872 | -1.6163 | 7.6298 | 7.0865 | 6.4307 | 6.0794 | 5.7793 | 5.3682 | 5.0017 | 4.4924 | 4.1247 | 3.7707 | 3.4452 | 1.5314 | -0.14096 | -1.3295
| BRIDGE OF DUN | LOGIE PERT | MINIMUM HEADROOM | NO 67764 64427 | YES | YES | 4.3368 | 4.3003 | 4.2659 | 4.2261 | 4.1446 | 4.0548 | 3.9981 | 3.9309 | 3.8601 | 3.7927 | 3.7296 | 3.4122 | 2.9203 | 2.2045 | 3.9746 | 3.9575 | 3.9225 | 3.8787 | 3.8303 | 3.7502 | 3.7149 | 3.5887 | 3.5289 | 3.4754 | 3.3997 | 3.034 | 2.4691 | 1.625 | 3.927 | 3.8962 | 3.8682 | 3.8306 | 3.7374 | 3.6413 | 3.588 | 3.507 | 3.4346 | 3.3686 | 3.2836 | 2.8562 | 2.2568 | 1.4156
|  | LOGIE PERT | CT |  |  |  | 4.3682 | 4.3436 | 4.2893 | 4.2341 | 4.1446 | 4.0548 | 3.9981 | 3.9309 | 3.8601 | 3.7927 | 3.7296 | 3.4519 | 3.1136 | 2.7719 | 3.9839 | 3.9715 | 3.9418 | 3.9069 | 3.8303 | 3.7502 | 3.7149 | 3.6446 | 3.5693 | 3.4999 | 3.4297 | 3.1146 | 2.7419 | 2.3237 | 3.9477 | 3.925 | 3.8774 | 3.8306 | 3.7374 | 3.6413 | 3.588 | 3.5109 | 3.437 | 3.3686 | 3.2946 | 2.9577 | 2.569 | 2.1559
|  | LOGIE PERT | LW |  |  |  | 4.3368 | 4.3003 | 4.2659 | 4.2261 | 4.1917 | 4.1473 | 4.1004 | 4.0363 | 3.9692 | 3.9078 | 3.8409 | 3.6024 | 3.0191 | 2.2045 | 3.9746 | 3.9575 | 3.942 | 3.9239 | 3.9084 | 3.8846 | 3.8581 | 3.7916 | 3.7219 | 3.6593 | 3.5931 | 3.3352 | 2.6312 | 1.625 | 3.927 | 3.8962 | 3.8682 | 3.836 | 3.8069 | 3.7676 | 3.7257 | 3.6518 | 3.5743 | 3.5033 | 3.4269 | 3.1373 | 2.4231 | 1.4156
|  | LOGIE PERT | ST |  |  |  | 4.3813 | 4.3702 | 4.3063 | 4.2615 | 4.2163 | 4.1339 | 4.0904 | 3.9773 | 3.9103 | 3.8533 | 3.7786 | 3.4122 | 2.9203 | 2.4202 | 3.9892 | 3.9839 | 3.9225 | 3.8787 | 3.8436 | 3.753 | 3.7172 | 3.5887 | 3.5289 | 3.4754 | 3.3997 | 3.034 | 2.4691 | 1.8716 | 3.9616 | 3.9516 | 3.8818 | 3.8318 | 3.7864 | 3.6888 | 3.6432 | 3.507 | 3.4346 | 3.3704 | 3.2836 | 2.8562 | 2.2568 | 1.6527
|  | LOGIE PERT | FS |  |  |  | 4.3946 | 4.3862 | 4.3594 | 4.3357 | 4.3098 | 4.2834 | 4.2572 | 4.1982 | 4.1502 | 4.1014 | 4.0516 | 3.8419 | 3.7046 | 3.6079 | 3.9934 | 3.9891 | 3.9709 | 3.9529 | 3.9327 | 3.9117 | 3.8915 | 3.8373 | 3.7958 | 3.7532 | 3.7095 | 3.5728 | 3.462 | 3.362 | 3.9713 | 3.9639 | 3.9386 | 3.9153 | 3.889 | 3.8622 | 3.8356 | 3.7724 | 3.722 | 3.6705 | 3.618 | 3.4191 | 3.2767 | 3.1496
| MILTON OF CRAIGIE | LONGHAUGH | MINIMUM HEADROOM | NO 42768 33789 | NO | YES | 11.6279 | 10.6625 | 9.0281 | 7.4156 | 5.1316 | 3.0836 | 1.5368 | 0.76777 | -0.057423 | -0.91266 | -1.8894 | -4.2756 | -5.1828 | -6.0416 | 15.0415 | 14.2466 | 12.9808 | 11.7053 | 9.7412 | 8.0035 | 6.8427 | 6.3493 | 5.8161 | 5.2592 | 4.5864 | 2.9889 | 2.1591 | -0.037256 | 14.6228 | 13.7613 | 12.287 | 10.7295 | 8.3994 | 6.3036 | 4.7932 | 4.1009 | 3.3597 | 2.591 | 1.7021 | -0.56809 | -1.5494 | -2.5709
|  | LONGHAUGH | CT |  |  |  | 12.1994 | 11.401 | 9.9289 | 8.48 | 6.3802 | 4.6452 | 3.4448 | 2.6324 | 1.7945 | 0.96793 | -0.015843 | -2.9925 | -4.4651 | -5.2384 | 15.318 | 14.5902 | 13.4753 | 12.3493 | 10.5401 | 9.0559 | 8.1749 | 7.6408 | 7.0954 | 6.5647 | 5.8823 | 3.7042 | 2.2151 | 0.48499 | 15.0844 | 14.3669 | 13.0751 | 11.7564 | 9.672 | 7.8825 | 6.7227 | 5.9878 | 5.2381 | 4.5049 | 3.6178 | 0.89584 | -0.48776 | -1.2682
|  | LONGHAUGH | LW |  |  |  | 11.6279 | 10.6625 | 9.0281 | 7.4156 | 5.1316 | 3.0836 | 1.5368 | 0.76777 | -0.057423 | -0.91266 | -1.8894 | -4.2756 | -5.1828 | -6.0416 | 15.0415 | 14.2466 | 12.9808 | 11.7053 | 9.7412 | 8.0035 | 6.8427 | 6.3493 | 5.8161 | 5.2592 | 4.5864 | 2.9889 | 2.1591 | 1.1645 | 14.6228 | 13.7613 | 12.287 | 10.7295 | 8.3994 | 6.3036 | 4.7932 | 4.1009 | 3.3597 | 2.591 | 1.7021 | -0.56809 | -1.5494 | -2.5709
|  | LONGHAUGH | ST |  |  |  | 12.4285 | 11.8019 | 10.8418 | 9.972 | 8.5742 | 7.3353 | 6.6622 | 6.2763 | 5.9073 | 5.5272 | 4.9279 | 1.9201 | 0.066018 | -1.6333 | 15.4268 | 14.8083 | 13.8115 | 12.8963 | 11.481 | 10.0254 | 9.227 | 8.8754 | 8.5957 | 8.3185 | 7.8262 | 5.3036 | 3.4299 | 1.2531 | 15.2779 | 14.7297 | 13.8264 | 13.001 | 11.5121 | 10.1292 | 9.4201 | 9.0499 | 8.7259 | 8.4007 | 7.8642 | 4.9251 | 3.173 | 1.5568
|  | LONGHAUGH | FS |  |  |  | 12.8758 | 12.3923 | 11.7068 | 11.0279 | 9.9483 | 9.1138 | 8.4712 | 7.9966 | 7.4273 | 6.8987 | 6.3494 | 3.3992 | 0.60142 | -1.3576 | 15.8615 | 15.3739 | 14.7024 | 14.0156 | 12.9401 | 12.0891 | 11.4393 | 10.9952 | 10.4552 | 9.9521 | 9.4377 | 6.7271 | 3.6106 | -0.037256 | 15.6638 | 15.2394 | 14.6337 | 14.023 | 13.0455 | 12.1519 | 11.4813 | 11.0241 | 10.4708 | 9.9699 | 9.468 | 6.7729 | 4.1862 | 2.4495
| ELGIN | LOSSIEMOUTH | MINIMUM HEADROOM | NJ 23203 69923 | NO | YES | 7.5509 | 7.3447 | 6.8282 | 6.2684 | 5.5059 | 4.6357 | 3.9155 | 3.4168 | 2.8941 | 2.339 | 1.7921 | 0.24052 | -0.34099 | -0.66 | 8.8588 | 8.7336 | 8.3401 | 7.905 | 7.2156 | 6.4285 | 5.8481 | 5.5055 | 5.1429 | 4.7872 | 4.4017 | 3.3159 | 2.9559 | 2.6983 | 8.1233 | 7.9305 | 7.4001 | 6.8198 | 5.9874 | 5.0312 | 4.2686 | 3.7623 | 3.2294 | 2.7006 | 2.1869 | 0.6694 | 0.091638 | -0.23094
|  | LOSSIEMOUTH | CT |  |  |  | 7.7271 | 7.6003 | 7.2366 | 6.8468 | 6.3304 | 5.7842 | 5.3987 | 4.9373 | 4.4335 | 3.923 | 3.4078 | 1.7253 | 0.88671 | 0.43193 | 8.9217 | 8.8308 | 8.6093 | 8.3565 | 7.9315 | 7.4763 | 7.2256 | 6.9405 | 6.6189 | 6.2998 | 5.9887 | 4.8369 | 4.2143 | 3.5777 | 8.1233 | 8.0411 | 7.8019 | 7.4179 | 6.8751 | 6.2989 | 5.9252 | 5.4816 | 4.9869 | 4.4951 | 4.0185 | 2.4195 | 1.6473 | 1.2418
|  | LOSSIEMOUTH | LW |  |  |  | 7.5509 | 7.3447 | 6.8282 | 6.2684 | 5.5059 | 4.6357 | 3.9155 | 3.4168 | 2.8941 | 2.339 | 1.7921 | 0.24052 | -0.34099 | -0.66 | 8.8588 | 8.7336 | 8.3401 | 7.905 | 7.2156 | 6.4285 | 5.8481 | 5.5055 | 5.1429 | 4.7872 | 4.4017 | 3.3159 | 2.9559 | 2.6983 | 8.1287 | 7.9305 | 7.4001 | 6.8198 | 5.9874 | 5.0312 | 4.2686 | 3.7623 | 3.2294 | 2.7006 | 2.1869 | 0.6694 | 0.091638 | -0.23094
|  | LOSSIEMOUTH | ST |  |  |  | 7.8071 | 7.7544 | 7.5044 | 7.3029 | 7.1285 | 6.7344 | 6.5276 | 6.3037 | 6.0623 | 5.7841 | 5.4648 | 3.6421 | 2.7293 | 1.9196 | 8.966 | 8.9273 | 8.6468 | 8.4298 | 8.2548 | 7.8134 | 7.612 | 7.4 | 7.2144 | 7.0109 | 6.7714 | 5.3134 | 4.528 | 3.7309 | 8.1571 | 8.1231 | 7.8502 | 7.6415 | 7.4747 | 7.0422 | 6.8388 | 6.604 | 6.3894 | 6.1462 | 5.8506 | 4.1496 | 3.2745 | 2.4942
|  | LOSSIEMOUTH | FS |  |  |  | 7.82 | 7.7754 | 7.6753 | 7.5655 | 7.4416 | 7.3092 | 7.1712 | 7.0007 | 6.8256 | 6.6385 | 6.4235 | 4.9767 | 3.581 | 2.7153 | 8.9741 | 8.941 | 8.8478 | 8.7459 | 8.63 | 8.5053 | 8.378 | 8.2362 | 8.0909 | 7.9324 | 7.7579 | 6.6662 | 5.2691 | 3.8452 | 8.1665 | 8.1393 | 8.0598 | 7.9741 | 7.8749 | 7.7679 | 7.6604 | 7.5026 | 7.3257 | 7.1352 | 6.9268 | 5.6199 | 4.3452 | 3.5283
| BROADFORD | LOWER OLLACH | MINIMUM HEADROOM | NG 51241 37001 | YES | YES | 0.042529 | 0.013077 | -0.054782 | -0.13737 | -0.25749 | -0.41806 | -0.49516 | -0.58111 | -0.66167 | -0.74382 | -0.8241 | -1.2542 | -1.6962 | -2.1112 | 0.24275 | 0.22685 | 0.11561 | 0.022593 | -0.043134 | -0.24632 | -0.31378 | -0.47409 | -0.54405 | -0.60874 | -0.70124 | -1.1482 | -1.6608 | -2.1679 | 0.1458 | 0.11942 | 0.021737 | -0.076388 | -0.17467 | -0.35943 | -0.43754 | -0.60218 | -0.68158 | -0.75646 | -0.85927 | -1.3604 | -1.8904 | -2.3982
|  | LOWER OLLACH | CT |  |  |  | 0.060084 | 0.036943 | -0.027645 | -0.10082 | -0.25749 | -0.41806 | -0.49516 | -0.57174 | -0.66167 | -0.74382 | -0.8241 | -1.1582 | -1.4605 | -1.7546 | 0.24862 | 0.23517 | 0.193 | 0.13735 | -0.022985 | -0.19172 | -0.25166 | -0.33626 | -0.42935 | -0.51364 | -0.59989 | -0.98629 | -1.3264 | -1.6854 | 0.15995 | 0.13868 | 0.077086 | 0.0034092 | -0.17467 | -0.35943 | -0.43754 | -0.52775 | -0.63054 | -0.72407 | -0.8173 | -1.2182 | -1.5742 | -1.9324
|  | LOWER OLLACH | LW |  |  |  | 0.042529 | 0.013077 | -0.020028 | -0.056656 | -0.090667 | -0.13596 | -0.1878 | -0.2484 | -0.31166 | -0.37327 | -0.4322 | -0.6286 | -1.1272 | -1.8255 | 0.24275 | 0.22685 | 0.2107 | 0.19235 | 0.17583 | 0.15022 | 0.12025 | 0.066173 | 0.0090941 | -0.044446 | -0.097838 | -0.28381 | -0.87986 | -1.7428 | 0.1458 | 0.11942 | 0.09059 | 0.058413 | 0.028706 | -0.012594 | -0.060194 | -0.12535 | -0.19374 | -0.25937 | -0.32324 | -0.53995 | -1.1498 | -2.0176
|  | LOWER OLLACH | ST |  |  |  | 0.071861 | 0.060217 | -0.054782 | -0.13737 | -0.20022 | -0.37267 | -0.43982 | -0.58111 | -0.65177 | -0.71957 | -0.80975 | -1.2542 | -1.6962 | -2.1112 | 0.25389 | 0.24818 | 0.11561 | 0.022593 | -0.043134 | -0.24632 | -0.31378 | -0.47409 | -0.54405 | -0.60874 | -0.70124 | -1.1482 | -1.6608 | -2.1679 | 0.16991 | 0.1598 | 0.021737 | -0.076388 | -0.14852 | -0.35791 | -0.43359 | -0.60218 | -0.68158 | -0.75646 | -0.85927 | -1.3604 | -1.8904 | -2.3982
|  | LOWER OLLACH | FS |  |  |  | 0.081192 | 0.070485 | 0.038684 | 0.0047183 | -0.034118 | -0.06995 | -0.10695 | -0.17063 | -0.21928 | -0.2759 | -0.33006 | -0.5386 | -0.6999 | -0.79138 | 0.25716 | 0.25199 | 0.22068 | 0.18806 | 0.15045 | 0.11318 | 0.078013 | 0.013608 | -0.03427 | -0.085621 | -0.13695 | -0.2858 | -0.40875 | -0.50008 | 0.17748 | 0.16836 | 0.13285 | 0.095412 | 0.052378 | 0.011457 | -0.029205 | -0.10108 | -0.15541 | -0.21638 | -0.27585 | -0.47999 | -0.64016 | -0.73669
| KILLIN | LUBNAIG | MINIMUM HEADROOM | NN 57455 13800 | YES | YES | 0.21886 | 0.21811 | 0.21704 | 0.21577 | 0.21448 | 0.21298 | 0.21015 | 0.20685 | 0.20321 | 0.19938 | 0.19583 | 0.18915 | 0.18633 | 0.1862 | 0.20625 | 0.20541 | 0.20392 | 0.20288 | 0.20182 | 0.20067 | 0.19855 | 0.19606 | 0.1932 | 0.19018 | 0.18738 | 0.18213 | 0.17991 | 0.17981 | 0.204 | 0.2032 | 0.20209 | 0.20083 | 0.19953 | 0.19811 | 0.19539 | 0.19221 | 0.18871 | 0.18502 | 0.1816 | 0.17517 | 0.17246 | 0.17234
|  | LUBNAIG | CT |  |  |  | 0.21888 | 0.21825 | 0.21704 | 0.21577 | 0.21448 | 0.21298 | 0.21132 | 0.20901 | 0.20714 | 0.20526 | 0.20247 | 0.1951 | 0.19488 | 0.19484 | 0.20628 | 0.20541 | 0.20392 | 0.20288 | 0.20182 | 0.20067 | 0.19942 | 0.19768 | 0.19625 | 0.19481 | 0.19261 | 0.18681 | 0.18664 | 0.18661 | 0.20404 | 0.20339 | 0.20209 | 0.20083 | 0.19953 | 0.19811 | 0.19651 | 0.19429 | 0.19249 | 0.19068 | 0.18799 | 0.18089 | 0.18068 | 0.18064
|  | LUBNAIG | LW |  |  |  | 0.21886 | 0.21811 | 0.2175 | 0.21672 | 0.21544 | 0.21309 | 0.21015 | 0.20685 | 0.20321 | 0.19938 | 0.19583 | 0.18915 | 0.18913 | 0.18913 | 0.20625 | 0.20557 | 0.20469 | 0.20366 | 0.2026 | 0.20076 | 0.19855 | 0.19606 | 0.1932 | 0.19018 | 0.18738 | 0.18213 | 0.18211 | 0.18211 | 0.204 | 0.2032 | 0.20255 | 0.20171 | 0.20048 | 0.19822 | 0.19539 | 0.19221 | 0.18871 | 0.18502 | 0.1816 | 0.17517 | 0.17515 | 0.17515
|  | LUBNAIG | ST |  |  |  | 0.21914 | 0.21892 | 0.21863 | 0.21824 | 0.21779 | 0.21723 | 0.21593 | 0.2142 | 0.21192 | 0.20927 | 0.20627 | 0.19061 | 0.18633 | 0.18626 | 0.20648 | 0.2063 | 0.20605 | 0.20572 | 0.20506 | 0.20414 | 0.203 | 0.20161 | 0.19989 | 0.1979 | 0.19561 | 0.18328 | 0.17991 | 0.17986 | 0.20429 | 0.20407 | 0.20376 | 0.20335 | 0.20287 | 0.20227 | 0.20097 | 0.19926 | 0.19709 | 0.19454 | 0.19166 | 0.17659 | 0.17246 | 0.1724
|  | LUBNAIG | FS |  |  |  | 0.21918 | 0.21901 | 0.21878 | 0.21849 | 0.21817 | 0.21778 | 0.21731 | 0.21661 | 0.21543 | 0.21408 | 0.21244 | 0.20153 | 0.19179 | 0.1862 | 0.20652 | 0.20637 | 0.20618 | 0.20592 | 0.20565 | 0.20512 | 0.2044 | 0.20357 | 0.2026 | 0.2015 | 0.20026 | 0.19187 | 0.1842 | 0.17981 | 0.20434 | 0.20415 | 0.20391 | 0.2036 | 0.20326 | 0.20285 | 0.20234 | 0.20166 | 0.20048 | 0.19914 | 0.19759 | 0.18709 | 0.17771 | 0.17234
| LUNANHEAD | LUNANHEAD | MINIMUM HEADROOM | NO 47042 51733 | NO | YES | 5.9771 | 5.6483 | 5.0941 | 4.4493 | 3.7536 | 2.9855 | 2.2919 | 1.8507 | 1.3845 | 0.9182 | 0.46423 | -0.86134 | -1.7663 | -2.6562 | 7.0496 | 6.852 | 6.5269 | 6.1061 | 5.5989 | 5.0168 | 4.5369 | 4.2059 | 3.8464 | 3.4805 | 3.1267 | 2.1602 | 1.4154 | 0.51277 | 6.9963 | 6.6938 | 6.1562 | 5.5268 | 4.8086 | 4.0002 | 3.2907 | 2.8376 | 2.3572 | 1.877 | 1.4106 | 0.085713 | -0.89412 | -1.9588
|  | LUNANHEAD | CT |  |  |  | 6.3183 | 6.0484 | 5.5492 | 4.975 | 4.2664 | 3.551 | 3.0322 | 2.6102 | 2.1602 | 1.7184 | 1.2515 | -0.36104 | -1.5501 | -2.2657 | 7.1673 | 6.9498 | 6.6221 | 6.2948 | 5.7607 | 5.2084 | 4.9006 | 4.5983 | 4.3286 | 4.0673 | 3.7327 | 2.5861 | 2.0286 | 1.5622 | 7.3233 | 7.082 | 6.5827 | 6.039 | 5.3043 | 4.5572 | 4.0546 | 3.6283 | 3.1667 | 2.7141 | 2.2394 | 0.61758 | -0.53433 | -1.2722
|  | LUNANHEAD | LW |  |  |  | 5.9771 | 5.6483 | 5.0941 | 4.4493 | 3.7536 | 2.9855 | 2.2919 | 1.8507 | 1.3845 | 0.9182 | 0.46423 | -0.86134 | -1.7663 | -2.6562 | 7.0496 | 6.852 | 6.5269 | 6.1061 | 5.5989 | 5.0168 | 4.5369 | 4.2059 | 3.8464 | 3.4805 | 3.1267 | 2.1602 | 1.4154 | 0.51277 | 6.9963 | 6.6938 | 6.1562 | 5.5268 | 4.8086 | 4.0002 | 3.2907 | 2.8376 | 2.3572 | 1.877 | 1.4106 | 0.085713 | -0.89412 | -1.9588
|  | LUNANHEAD | ST |  |  |  | 6.442 | 6.3186 | 5.963 | 5.6604 | 5.4072 | 4.9047 | 4.6321 | 4.3044 | 4.0102 | 3.6841 | 3.2924 | 1.0652 | -0.1667 | -1.072 | 7.2621 | 7.1559 | 6.7691 | 6.4565 | 6.2099 | 5.6597 | 5.4062 | 5.0967 | 4.8479 | 4.5769 | 4.2431 | 2.474 | 1.4824 | 0.77794 | 7.3729 | 7.2863 | 6.9203 | 6.5999 | 6.3299 | 5.7623 | 5.4911 | 5.1615 | 4.898 | 4.5583 | 4.1475 | 1.9233 | 0.65961 | -0.28367
|  | LUNANHEAD | FS |  |  |  | 6.6887 | 6.5928 | 6.4248 | 6.2569 | 6.08 | 5.8836 | 5.6746 | 5.4227 | 5.1717 | 4.9075 | 4.6255 | 2.8779 | 1.3877 | 0.2622 | 7.5028 | 7.4193 | 7.2617 | 7.1059 | 6.9416 | 6.7672 | 6.5899 | 6.3956 | 6.2034 | 5.9971 | 5.7662 | 4.5055 | 3.46 | 2.6373 | 7.602 | 7.5326 | 7.4008 | 7.2417 | 7.0422 | 6.8367 | 6.6277 | 6.3766 | 6.1251 | 5.8595 | 5.5751 | 3.8706 | 2.5045 | 1.515
| PORT ANN | LUSSAGIVEN | MINIMUM HEADROOM | NR 63461 86798 | YES | YES | 0.093556 | 0.092956 | 0.090849 | 0.08858 | 0.088156 | 0.088827 | 0.085969 | 0.0848 | 0.083499 | 0.083494 | 0.080598 | 0.075996 | 0.076064 | 0.074308 | 0.093309 | 0.092859 | 0.091774 | 0.090756 | 0.090416 | 0.090177 | 0.088709 | 0.087654 | 0.086513 | 0.085907 | 0.084403 | 0.081903 | 0.081939 | 0.081308 | 0.083415 | 0.082819 | 0.080871 | 0.078833 | 0.078413 | 0.078802 | 0.076233 | 0.07495 | 0.073562 | 0.073527 | 0.070834 | 0.066479 | 0.066548 | 0.065027
|  | LUSSAGIVEN | CT |  |  |  | 0.093633 | 0.093167 | 0.090849 | 0.090116 | 0.089602 | 0.088827 | 0.086474 | 0.08562 | 0.084446 | 0.084531 | 0.080598 | 0.07655 | 0.076232 | 0.077352 | 0.093353 | 0.093019 | 0.091774 | 0.091152 | 0.090729 | 0.090177 | 0.089169 | 0.088397 | 0.087304 | 0.086744 | 0.084776 | 0.082321 | 0.082057 | 0.082313 | 0.083492 | 0.08303 | 0.080871 | 0.080133 | 0.079611 | 0.078803 | 0.076785 | 0.075852 | 0.074534 | 0.07456 | 0.070834 | 0.067019 | 0.066703 | 0.067656
|  | LUSSAGIVEN | LW |  |  |  | 0.093556 | 0.092956 | 0.090952 | 0.08858 | 0.088156 | 0.088828 | 0.085969 | 0.0848 | 0.083499 | 0.083494 | 0.080948 | 0.075996 | 0.077236 | 0.077236 | 0.093309 | 0.092859 | 0.091856 | 0.090756 | 0.090416 | 0.090177 | 0.088709 | 0.087654 | 0.086513 | 0.085907 | 0.084403 | 0.081903 | 0.082258 | 0.082258 | 0.083415 | 0.082819 | 0.080972 | 0.078833 | 0.078413 | 0.078802 | 0.076233 | 0.07495 | 0.073562 | 0.073527 | 0.071156 | 0.066479 | 0.067552 | 0.067552
|  | LUSSAGIVEN | ST |  |  |  | 0.093768 | 0.093601 | 0.093372 | 0.093058 | 0.092709 | 0.09349 | 0.092962 | 0.092301 | 0.091488 | 0.090555 | 0.089512 | 0.080208 | 0.076064 | 0.074308 | 0.09346 | 0.093341 | 0.09318 | 0.09294 | 0.092664 | 0.092769 | 0.09235 | 0.091826 | 0.091181 | 0.090441 | 0.089614 | 0.083772 | 0.081939 | 0.081308 | 0.083626 | 0.08346 | 0.083233 | 0.082921 | 0.082575 | 0.082573 | 0.082024 | 0.081347 | 0.080515 | 0.079551 | 0.07846 | 0.070359 | 0.066548 | 0.065027
|  | LUSSAGIVEN | FS |  |  |  | 0.0938 | 0.093662 | 0.093481 | 0.093239 | 0.092984 | 0.092675 | 0.092308 | 0.093076 | 0.092556 | 0.091968 | 0.089939 | 0.082903 | 0.078045 | 0.074626 | 0.093483 | 0.093385 | 0.093258 | 0.093084 | 0.092882 | 0.092638 | 0.092347 | 0.092443 | 0.092032 | 0.091566 | 0.090485 | 0.086027 | 0.082724 | 0.081434 | 0.083657 | 0.08352 | 0.08334 | 0.0831 | 0.082847 | 0.082541 | 0.082176 | 0.082283 | 0.081806 | 0.081267 | 0.079823 | 0.072971 | 0.06831 | 0.065335
| LYNDHURST | LYNDHURST | MINIMUM HEADROOM | NO 37434 32575 | NO | YES | 9.3986 | 9.0149 | 8.6457 | 8.3142 | 7.8774 | 7.3549 | 6.9547 | 6.6784 | 6.3612 | 6.0613 | 5.7759 | 4.8674 | 4.3503 | 3.7818 | 9.7502 | 9.3477 | 9.0467 | 8.8018 | 8.4243 | 7.9706 | 7.6751 | 7.4851 | 7.2482 | 7.0451 | 6.8044 | 5.9618 | 5.2979 | 4.7002 | 8.7438 | 8.3522 | 7.9774 | 7.6425 | 7.1747 | 6.6219 | 6.215 | 5.9464 | 5.6345 | 5.3457 | 5.0166 | 3.9737 | 3.3938 | 2.675
|  | LYNDHURST | CT |  |  |  | 9.5231 | 9.2071 | 8.8916 | 8.613 | 8.2724 | 7.8793 | 7.6216 | 7.3791 | 7.1042 | 6.849 | 6.6021 | 5.6046 | 5.1388 | 4.818 | 9.8025 | 9.4428 | 9.2095 | 9.0253 | 8.7526 | 8.4225 | 8.2518 | 8.0944 | 7.9018 | 7.7452 | 7.587 | 6.8209 | 6.2919 | 5.5356 | 8.7716 | 8.4336 | 8.2155 | 7.9627 | 7.6133 | 7.2098 | 6.9607 | 6.7148 | 6.4406 | 6.2006 | 5.953 | 4.889 | 4.5369 | 4.2071
|  | LYNDHURST | LW |  |  |  | 9.3986 | 9.0149 | 8.6457 | 8.3142 | 7.8774 | 7.3549 | 6.9547 | 6.6784 | 6.3612 | 6.0613 | 5.7759 | 4.8674 | 4.3503 | 3.7818 | 9.7502 | 9.3477 | 9.0467 | 8.8018 | 8.4243 | 7.9706 | 7.6751 | 7.4851 | 7.2482 | 7.0451 | 6.8044 | 5.9618 | 5.4117 | 4.7002 | 8.7438 | 8.3522 | 7.9774 | 7.6425 | 7.1747 | 6.6219 | 6.215 | 5.9464 | 5.6345 | 5.3457 | 5.0166 | 3.9737 | 3.3938 | 2.675
|  | LYNDHURST | ST |  |  |  | 9.5996 | 9.328 | 9.0942 | 8.9341 | 8.7878 | 8.488 | 8.3199 | 8.137 | 7.9245 | 7.7105 | 7.3465 | 5.3088 | 4.3905 | 3.9293 | 9.8431 | 9.5263 | 9.2695 | 9.1071 | 8.968 | 8.6563 | 8.5081 | 8.3411 | 8.1538 | 7.9314 | 7.6604 | 6.1284 | 5.2979 | 4.785 | 8.8121 | 8.5311 | 8.2781 | 8.1066 | 7.955 | 7.6273 | 7.454 | 7.2118 | 6.9383 | 6.6556 | 6.3257 | 4.4448 | 3.4897 | 2.919
|  | LYNDHURST | FS |  |  |  | 9.6807 | 9.4879 | 9.3716 | 9.2682 | 9.1782 | 9.0558 | 8.9537 | 8.8363 | 8.6835 | 8.5483 | 8.3986 | 7.1602 | 5.9108 | 5.1053 | 9.9349 | 9.6941 | 9.5632 | 9.4585 | 9.3614 | 9.2348 | 9.1353 | 9.0233 | 8.8766 | 8.7465 | 8.6069 | 7.6838 | 6.6808 | 5.1041 | 8.9054 | 8.6948 | 8.5703 | 8.4707 | 8.3735 | 8.248 | 8.145 | 8.0325 | 7.85 | 7.6702 | 7.4738 | 6.1947 | 5.0242 | 4.2339
| THURSO | LYNESS | MINIMUM HEADROOM | ND 30350 94625 | YES | YES | 0.55209 | 0.5328 | 0.50182 | 0.4641 | 0.42182 | 0.38202 | 0.33856 | 0.32747 | 0.31613 | 0.29919 | 0.28368 | 0.24714 | 0.22112 | 0.20634 | 0.71632 | 0.70573 | 0.691 | 0.66901 | 0.64985 | 0.63149 | 0.61165 | 0.60106 | 0.5889 | 0.57376 | 0.55542 | 0.52587 | 0.51409 | 0.50307 | 0.62958 | 0.61171 | 0.58393 | 0.54882 | 0.51124 | 0.47594 | 0.43755 | 0.42495 | 0.41287 | 0.39584 | 0.37553 | 0.33789 | 0.31561 | 0.30393
|  | LYNESS | CT |  |  |  | 0.57038 | 0.55402 | 0.50772 | 0.4641 | 0.42182 | 0.38202 | 0.33856 | 0.32747 | 0.31613 | 0.29919 | 0.2863 | 0.26758 | 0.224 | 0.20634 | 0.72323 | 0.7135 | 0.691 | 0.66901 | 0.64985 | 0.63149 | 0.61165 | 0.60106 | 0.5889 | 0.57444 | 0.561 | 0.53563 | 0.51554 | 0.50307 | 0.64561 | 0.6304 | 0.5885 | 0.54882 | 0.51124 | 0.47594 | 0.43755 | 0.42495 | 0.41287 | 0.39584 | 0.38069 | 0.35637 | 0.31955 | 0.30393
|  | LYNESS | LW |  |  |  | 0.55209 | 0.5328 | 0.50182 | 0.46734 | 0.43937 | 0.40042 | 0.36108 | 0.34548 | 0.32647 | 0.30711 | 0.28368 | 0.24714 | 0.22112 | 0.2123 | 0.71632 | 0.70573 | 0.69141 | 0.67529 | 0.66208 | 0.64195 | 0.62053 | 0.60684 | 0.5912 | 0.57376 | 0.55542 | 0.52587 | 0.51409 | 0.51082 | 0.62958 | 0.61171 | 0.58393 | 0.55312 | 0.52812 | 0.49235 | 0.45576 | 0.44011 | 0.42125 | 0.39985 | 0.37553 | 0.33789 | 0.31561 | 0.30854
|  | LYNESS | ST |  |  |  | 0.58102 | 0.57608 | 0.56356 | 0.54991 | 0.53719 | 0.5233 | 0.51188 | 0.49173 | 0.47479 | 0.45274 | 0.43038 | 0.32315 | 0.28151 | 0.25787 | 0.72802 | 0.72509 | 0.719 | 0.712 | 0.70507 | 0.69722 | 0.6897 | 0.67813 | 0.66684 | 0.6529 | 0.63807 | 0.55943 | 0.53465 | 0.52167 | 0.65515 | 0.6506 | 0.63932 | 0.62693 | 0.61529 | 0.60247 | 0.59167 | 0.57305 | 0.55638 | 0.53484 | 0.51254 | 0.40536 | 0.36726 | 0.3467
|  | LYNESS | FS |  |  |  | 0.58524 | 0.58298 | 0.57235 | 0.56355 | 0.55005 | 0.54039 | 0.52738 | 0.51725 | 0.49914 | 0.48308 | 0.46664 | 0.35086 | 0.26927 | 0.23794 | 0.72979 | 0.72803 | 0.72297 | 0.71824 | 0.71166 | 0.7062 | 0.69915 | 0.69269 | 0.68286 | 0.67336 | 0.66325 | 0.59249 | 0.53227 | 0.51062 | 0.65891 | 0.65675 | 0.64721 | 0.63918 | 0.62702 | 0.61811 | 0.60618 | 0.59669 | 0.58007 | 0.56507 | 0.54917 | 0.43851 | 0.35731 | 0.33029
| STORNOWAY | MAARUIG | MINIMUM HEADROOM | NB 19162 06332 | YES | YES | 0.17318 | 0.16893 | 0.16847 | 0.16757 | 0.16523 | 0.1647 | 0.16047 | 0.15957 | 0.15707 | 0.1557 | 0.15631 | 0.15404 | 0.1517 | 0.15082 | 0.18172 | 0.17991 | 0.17955 | 0.17883 | 0.17775 | 0.17733 | 0.17554 | 0.17471 | 0.17296 | 0.17186 | 0.17155 | 0.1702 | 0.16928 | 0.16875 | 0.16749 | 0.165 | 0.16454 | 0.16366 | 0.16155 | 0.16103 | 0.15726 | 0.15637 | 0.15393 | 0.15246 | 0.15262 | 0.1503 | 0.14796 | 0.14738
|  | MAARUIG | CT |  |  |  | 0.17323 | 0.17278 | 0.17204 | 0.16757 | 0.16523 | 0.1647 | 0.16047 | 0.15957 | 0.15835 | 0.15863 | 0.15752 | 0.15525 | 0.15311 | 0.15106 | 0.18176 | 0.1814 | 0.18081 | 0.17883 | 0.17775 | 0.17733 | 0.17554 | 0.17482 | 0.17384 | 0.17341 | 0.17251 | 0.17068 | 0.16978 | 0.16894 | 0.16749 | 0.16717 | 0.1665 | 0.16366 | 0.16155 | 0.16103 | 0.15726 | 0.15637 | 0.15516 | 0.15507 | 0.15385 | 0.15141 | 0.14959 | 0.14785
|  | MAARUIG | LW |  |  |  | 0.17318 | 0.16893 | 0.16847 | 0.16792 | 0.16747 | 0.16472 | 0.16181 | 0.16025 | 0.15707 | 0.1557 | 0.15631 | 0.15462 | 0.15267 | 0.15082 | 0.18172 | 0.17991 | 0.17955 | 0.17911 | 0.17875 | 0.17735 | 0.17581 | 0.17471 | 0.17296 | 0.17186 | 0.17155 | 0.1702 | 0.16943 | 0.16875 | 0.16753 | 0.165 | 0.16454 | 0.164 | 0.16356 | 0.16105 | 0.15837 | 0.15687 | 0.15393 | 0.15246 | 0.15262 | 0.1503 | 0.14922 | 0.14772
|  | MAARUIG | ST |  |  |  | 0.17338 | 0.17323 | 0.17301 | 0.17272 | 0.1724 | 0.17014 | 0.16779 | 0.1687 | 0.1665 | 0.16562 | 0.16279 | 0.15404 | 0.15281 | 0.15278 | 0.18188 | 0.18176 | 0.18159 | 0.18136 | 0.18109 | 0.18009 | 0.17901 | 0.17907 | 0.17793 | 0.17723 | 0.17576 | 0.17036 | 0.16951 | 0.16949 | 0.16768 | 0.16757 | 0.16743 | 0.16724 | 0.16702 | 0.16599 | 0.16388 | 0.16456 | 0.16258 | 0.16163 | 0.15907 | 0.15038 | 0.14796 | 0.14793
|  | MAARUIG | FS |  |  |  | 0.17341 | 0.17329 | 0.17312 | 0.1729 | 0.17266 | 0.17052 | 0.16833 | 0.16944 | 0.16896 | 0.16842 | 0.16781 | 0.15691 | 0.1517 | 0.15125 | 0.18191 | 0.18181 | 0.18167 | 0.18149 | 0.1813 | 0.18039 | 0.17944 | 0.17967 | 0.17928 | 0.17885 | 0.17836 | 0.17265 | 0.16928 | 0.16892 | 0.1677 | 0.16761 | 0.16751 | 0.16737 | 0.16721 | 0.16637 | 0.16441 | 0.16534 | 0.16483 | 0.16424 | 0.16358 | 0.15367 | 0.14853 | 0.14738
| LYNDHURST | MACALPINE ROAD | MINIMUM HEADROOM | NO 38034 33691 | NO | YES | 13.5055 | 13.1407 | 12.5532 | 12.0767 | 11.6214 | 11.0741 | 10.4535 | 9.8921 | 9.3217 | 8.7429 | 8.1909 | 6.7136 | 5.8405 | 4.9926 | 14.6348 | 14.4626 | 14.2654 | 14.0485 | 13.8466 | 13.5839 | 13.2483 | 12.9182 | 12.5978 | 12.2489 | 11.9057 | 10.5488 | 9.4395 | 7.8652 | 13.9528 | 13.7921 | 13.6439 | 13.5178 | 13.374 | 13.1037 | 12.6155 | 12.139 | 11.5859 | 11.0135 | 10.4687 | 9.0724 | 8.1138 | 7.0655
|  | MACALPINE ROAD | CT |  |  |  | 13.7579 | 13.5033 | 12.9185 | 12.4362 | 11.9737 | 11.5174 | 11.0248 | 10.4719 | 9.8605 | 9.2528 | 8.6791 | 6.8565 | 5.8964 | 5.2235 | 14.6953 | 14.5075 | 14.3074 | 14.1138 | 13.8466 | 13.5839 | 13.2957 | 12.9592 | 12.603 | 12.2489 | 11.9057 | 10.5488 | 9.4395 | 8.0291 | 13.9907 | 13.8089 | 13.6439 | 13.5178 | 13.374 | 13.2356 | 13.0139 | 12.5749 | 12.0195 | 11.4285 | 10.8743 | 9.1612 | 8.2438 | 7.546
|  | MACALPINE ROAD | LW |  |  |  | 13.5055 | 13.1407 | 12.5532 | 12.0767 | 11.6214 | 11.0741 | 10.4535 | 9.8921 | 9.3217 | 8.7429 | 8.1909 | 6.7136 | 5.8405 | 4.9926 | 14.6348 | 14.4626 | 14.2654 | 14.0485 | 13.8471 | 13.5851 | 13.2483 | 12.9182 | 12.5978 | 12.2746 | 11.9339 | 10.994 | 10.1599 | 9.1221 | 13.9528 | 13.7921 | 13.673 | 13.599 | 13.5242 | 13.1037 | 12.6155 | 12.139 | 11.5859 | 11.0135 | 10.4687 | 9.0724 | 8.1138 | 7.0655
|  | MACALPINE ROAD | ST |  |  |  | 13.7763 | 13.6372 | 13.4767 | 13.392 | 13.2943 | 13.1461 | 12.9716 | 12.7126 | 12.4958 | 12.2613 | 11.9944 | 10.2234 | 8.9386 | 7.7452 | 14.7264 | 14.6043 | 14.4764 | 14.3995 | 14.3206 | 14.191 | 14.0415 | 13.8133 | 13.6648 | 13.5035 | 13.2778 | 11.7138 | 10.295 | 8.6081 | 14.0094 | 13.8849 | 13.7532 | 13.6793 | 13.6056 | 13.4822 | 13.346 | 13.1314 | 12.9959 | 12.8533 | 12.6797 | 11.7906 | 10.6328 | 9.4675
|  | MACALPINE ROAD | FS |  |  |  | 13.8318 | 13.714 | 13.6137 | 13.5403 | 13.4494 | 13.3478 | 13.205 | 13.0017 | 12.805 | 12.5862 | 12.3614 | 10.939 | 9.3618 | 8.2842 | 14.7823 | 14.6835 | 14.6063 | 14.5594 | 14.5056 | 14.4478 | 14.3448 | 14.1696 | 13.9982 | 13.8078 | 13.6056 | 12.3299 | 10.3428 | 7.8652 | 14.0655 | 13.9615 | 13.8797 | 13.8373 | 13.7893 | 13.7371 | 13.6433 | 13.5276 | 13.4333 | 13.3311 | 13.2239 | 12.6886 | 11.3233 | 10.4
| MACDUFF | MACDUFF | MINIMUM HEADROOM | NJ 70363 63908 | NO | YES | 13.1325 | 12.6886 | 11.9486 | 11.1651 | 10.2731 | 8.9512 | 7.6189 | 6.4542 | 5.7453 | 5.0017 | 4.2656 | 2.0417 | 0.57507 | -0.49595 | 15.3892 | 15.2169 | 15.0428 | 14.8216 | 14.317 | 13.3965 | 12.5035 | 11.6785 | 11.2076 | 10.7148 | 10.2329 | 8.9617 | 8.0488 | 7.0025 | 16.1128 | 15.724 | 15.0968 | 14.4215 | 13.5834 | 12.3026 | 11.0364 | 9.9394 | 9.2502 | 8.5311 | 7.8228 | 5.7704 | 4.4535 | 3.4103
|  | MACDUFF | CT |  |  |  | 13.5319 | 13.2332 | 12.5547 | 11.8289 | 10.9884 | 9.8353 | 8.7777 | 7.597 | 6.7698 | 5.9444 | 5.1367 | 2.4537 | 0.57507 | -0.49595 | 15.3892 | 15.2169 | 15.0558 | 14.872 | 14.4977 | 13.7546 | 13.1066 | 12.3178 | 11.7817 | 11.2488 | 10.7412 | 9.1531 | 8.0488 | 7.0025 | 16.3984 | 16.1235 | 15.5432 | 14.9073 | 14.1394 | 13.0971 | 12.1266 | 11.0323 | 10.2402 | 9.4514 | 8.6861 | 6.2053 | 4.5287 | 3.5286
|  | MACDUFF | LW |  |  |  | 13.1325 | 12.6886 | 11.9486 | 11.1651 | 10.2731 | 8.9512 | 7.6189 | 6.4542 | 5.7453 | 5.0017 | 4.2656 | 2.0417 | 0.67906 | -0.27374 | 15.4032 | 15.2441 | 15.0428 | 14.8216 | 14.317 | 13.3965 | 12.5035 | 11.6785 | 11.2076 | 10.7148 | 10.2329 | 8.9617 | 8.0819 | 7.1771 | 16.1128 | 15.724 | 15.0968 | 14.4215 | 13.5834 | 12.3026 | 11.0364 | 9.9394 | 9.2502 | 8.5311 | 7.8228 | 5.7704 | 4.4535 | 3.4103
|  | MACDUFF | ST |  |  |  | 13.7604 | 13.6054 | 13.2891 | 13.0087 | 12.7573 | 11.9945 | 11.3651 | 10.5765 | 10.2158 | 9.8326 | 9.4187 | 7.0109 | 5.2747 | 3.4409 | 15.437 | 15.3355 | 15.0474 | 14.825 | 14.6473 | 13.8982 | 13.3381 | 12.5448 | 12.2995 | 12.047 | 11.7633 | 10.3303 | 9.0422 | 7.6951 | 16.5705 | 16.432 | 16.0757 | 15.7686 | 15.5018 | 14.7172 | 14.1241 | 13.3849 | 13.0101 | 12.6094 | 12.1658 | 9.7195 | 8.166 | 6.6377
|  | MACDUFF | FS |  |  |  | 13.7875 | 13.6711 | 13.5027 | 13.3162 | 13.1138 | 12.7402 | 12.2563 | 11.6301 | 11.2961 | 10.9327 | 10.5736 | 8.3325 | 6.1188 | 4.535 | 15.4464 | 15.3693 | 15.2842 | 15.1889 | 15.0795 | 14.7918 | 14.3972 | 13.8503 | 13.6763 | 13.4801 | 13.2857 | 11.9963 | 10.1048 | 8.4216 | 16.5948 | 16.4893 | 16.3271 | 16.1447 | 15.9459 | 15.6009 | 15.1623 | 14.6109 | 14.2966 | 13.9528 | 13.6055 | 11.5151 | 9.4718 | 8.1588
| CARRADALE | MACHRIE | MINIMUM HEADROOM | NR 90092 33864 | YES | YES | 1.0461 | 1.3581 | 1.3148 | 1.2621 | 1.212 | 1.1582 | 1.1 | 1.0428 | 0.98395 | 0.924 | 0.87009 | 0.79816 | 0.77586 | 0.75534 | 1.5826 | 2.084 | 2.0586 | 2.0238 | 1.9943 | 1.9628 | 1.9275 | 1.889 | 1.8488 | 1.8078 | 1.7709 | 1.721 | 1.694 | 1.6668 | 0.70498 | 1.2041 | 1.1711 | 1.1386 | 1.1035 | 1.0599 | 1.0212 | 0.99806 | 0.97197 | 0.94487 | 0.92026 | 0.86846 | 0.84609 | 0.8398
|  | MACHRIE | CT |  |  |  | 1.0619 | 1.3882 | 1.3266 | 1.2621 | 1.212 | 1.1582 | 1.1107 | 1.068 | 1.0108 | 0.95208 | 0.90197 | 0.81852 | 0.77586 | 0.75534 | 1.5907 | 2.0998 | 2.0627 | 2.0238 | 1.9943 | 1.9628 | 1.9341 | 1.905 | 1.8659 | 1.8259 | 1.7911 | 1.7263 | 1.694 | 1.6668 | 0.71996 | 1.2298 | 1.185 | 1.1436 | 1.1035 | 1.0599 | 1.0212 | 1.0012 | 0.98524 | 0.96913 | 0.94794 | 0.90841 | 0.87204 | 0.8541
|  | MACHRIE | LW |  |  |  | 1.0461 | 1.3581 | 1.3148 | 1.2689 | 1.2282 | 1.167 | 1.1 | 1.0428 | 0.98395 | 0.924 | 0.87009 | 0.79816 | 0.77694 | 0.77221 | 1.5826 | 2.084 | 2.0586 | 2.0312 | 2.0073 | 1.9695 | 1.9275 | 1.889 | 1.8488 | 1.8078 | 1.7709 | 1.721 | 1.7089 | 1.7064 | 0.70498 | 1.2041 | 1.1711 | 1.1386 | 1.1059 | 1.066 | 1.0243 | 0.99806 | 0.97197 | 0.94487 | 0.92026 | 0.86846 | 0.84609 | 0.8398
|  | MACHRIE | ST |  |  |  | 1.0921 | 1.4345 | 1.4216 | 1.4089 | 1.3963 | 1.3751 | 1.3539 | 1.3223 | 1.2858 | 1.2472 | 1.2028 | 0.98459 | 0.95135 | 0.93574 | 1.6066 | 2.126 | 2.1174 | 2.1082 | 2.0986 | 2.0842 | 2.069 | 2.0479 | 2.0232 | 1.9964 | 1.9659 | 1.8079 | 1.7715 | 1.7501 | 0.74809 | 1.2675 | 1.2581 | 1.2507 | 1.2436 | 1.2303 | 1.2183 | 1.2004 | 1.1808 | 1.1616 | 1.1388 | 1.0226 | 0.98277 | 0.95861
|  | MACHRIE | FS |  |  |  | 1.0909 | 1.4333 | 1.422 | 1.4082 | 1.3939 | 1.376 | 1.3545 | 1.3349 | 1.3098 | 1.2806 | 1.2498 | 1.0467 | 0.88668 | 0.86645 | 1.6062 | 2.1258 | 2.1182 | 2.109 | 2.0993 | 2.0874 | 2.0733 | 2.0594 | 2.0424 | 2.0227 | 2.0017 | 1.8636 | 1.7464 | 1.7129 | 0.74703 | 1.2662 | 1.2567 | 1.2465 | 1.2357 | 1.2226 | 1.2076 | 1.1961 | 1.1816 | 1.1646 | 1.1478 | 1.0356 | 0.95409 | 0.90781
| FORT WILLIAM | MALLAIG | MINIMUM HEADROOM | NM 67637 94811 | YES | YES | 7.5819 | 7.5343 | 7.4734 | 7.4138 | 7.343 | 7.2589 | 7.1823 | 7.1302 | 7.0646 | 6.9971 | 6.9384 | 6.823 | 6.7768 | 6.7482 | 6.9376 | 6.9092 | 6.8758 | 6.8351 | 6.7921 | 6.7442 | 6.7003 | 6.6556 | 6.6038 | 6.5505 | 6.503 | 6.4159 | 6.3669 | 6.2717 | 6.7329 | 6.7296 | 6.7255 | 6.7081 | 6.6429 | 6.5714 | 6.5022 | 6.4496 | 6.3852 | 6.319 | 6.261 | 6.1321 | 5.9867 | 5.9401
|  | MALLAIG | CT |  |  |  | 7.6175 | 7.5825 | 7.5032 | 7.4195 | 7.343 | 7.2589 | 7.1823 | 7.1316 | 7.0748 | 7.0177 | 6.9659 | 6.8487 | 6.7768 | 6.7482 | 6.9532 | 6.9308 | 6.8846 | 6.8351 | 6.7921 | 6.7442 | 6.7003 | 6.6608 | 6.6149 | 6.5686 | 6.5258 | 6.4178 | 6.3669 | 6.3255 | 6.7354 | 6.7328 | 6.7277 | 6.7081 | 6.6429 | 6.5714 | 6.5022 | 6.4557 | 6.4015 | 6.345 | 6.2941 | 6.1783 | 6.1193 | 6.0965
|  | MALLAIG | LW |  |  |  | 7.5819 | 7.5343 | 7.4734 | 7.4138 | 7.3584 | 7.278 | 7.1906 | 7.1302 | 7.0646 | 6.9971 | 6.9384 | 6.823 | 6.782 | 6.7544 | 6.9376 | 6.9092 | 6.8758 | 6.8411 | 6.8096 | 6.7596 | 6.7034 | 6.6556 | 6.6038 | 6.5505 | 6.503 | 6.4159 | 6.3952 | 6.3776 | 6.7329 | 6.7296 | 6.7255 | 6.7081 | 6.6602 | 6.5882 | 6.509 | 6.4496 | 6.3852 | 6.319 | 6.261 | 6.1526 | 6.1201 | 6.0952
|  | MALLAIG | ST |  |  |  | 7.6496 | 7.6362 | 7.6173 | 7.5939 | 7.5656 | 7.5275 | 7.492 | 7.4475 | 7.3956 | 7.3365 | 7.2754 | 6.9615 | 6.8661 | 6.8245 | 6.9716 | 6.963 | 6.9505 | 6.9345 | 6.915 | 6.8893 | 6.8632 | 6.831 | 6.7928 | 6.7491 | 6.7022 | 6.4564 | 6.3758 | 6.3276 | 6.7378 | 6.7371 | 6.7359 | 6.7344 | 6.7322 | 6.7288 | 6.726 | 6.7223 | 6.68 | 6.6247 | 6.5515 | 6.1321 | 5.9867 | 5.9401
|  | MALLAIG | FS |  |  |  | 7.6633 | 7.6508 | 7.6298 | 7.6045 | 7.5783 | 7.5522 | 7.5216 | 7.4895 | 7.4509 | 7.4122 | 7.3683 | 7.0863 | 6.8696 | 6.7887 | 6.9787 | 6.9708 | 6.9581 | 6.9424 | 6.9258 | 6.9083 | 6.8877 | 6.8649 | 6.8379 | 6.8095 | 6.7775 | 6.5692 | 6.3816 | 6.2717 | 6.7392 | 6.7383 | 6.7369 | 6.7352 | 6.7333 | 6.7315 | 6.7293 | 6.727 | 6.7241 | 6.6997 | 6.6594 | 6.3967 | 6.1278 | 5.9647
| KEITH | MARNOCH | MINIMUM HEADROOM | NJ 61955 53001 | NO | YES | 5.0984 | 4.9252 | 4.751 | 4.5648 | 4.3887 | 4.1285 | 3.8906 | 3.7118 | 3.5351 | 3.3663 | 3.2029 | 2.7664 | 2.3595 | 2.1329 | 5.9051 | 5.8193 | 5.7355 | 5.633 | 5.4796 | 5.3199 | 5.1896 | 5.0454 | 4.9035 | 4.7651 | 4.6335 | 4.248 | 3.9346 | 3.6075 | 5.2196 | 5.0618 | 4.9054 | 4.7367 | 4.5457 | 4.2974 | 4.0804 | 3.8983 | 3.7115 | 3.5317 | 3.3613 | 2.9138 | 2.5265 | 2.2813
|  | MARNOCH | CT |  |  |  | 5.2409 | 5.1273 | 4.8877 | 4.642 | 4.3887 | 4.1285 | 3.8906 | 3.7118 | 3.5351 | 3.3663 | 3.2029 | 2.7664 | 2.3595 | 2.1329 | 5.9574 | 5.8942 | 5.768 | 5.633 | 5.4796 | 5.3199 | 5.1896 | 5.0454 | 4.9035 | 4.7651 | 4.6335 | 4.248 | 3.9595 | 3.6978 | 5.3407 | 5.2355 | 5.0154 | 4.7866 | 4.5457 | 4.2974 | 4.0804 | 3.8983 | 3.7115 | 3.5317 | 3.3613 | 2.9138 | 2.5265 | 2.2899
|  | MARNOCH | LW |  |  |  | 5.0984 | 4.9252 | 4.751 | 4.5648 | 4.3887 | 4.1687 | 3.9192 | 3.7233 | 3.5558 | 3.3814 | 3.204 | 2.8055 | 2.4814 | 2.1361 | 5.9051 | 5.8193 | 5.7355 | 5.6429 | 5.5581 | 5.4365 | 5.2885 | 5.133 | 5.002 | 4.8676 | 4.7355 | 4.4528 | 4.1703 | 3.806 | 5.2196 | 5.0618 | 4.9054 | 4.7367 | 4.579 | 4.3736 | 4.1384 | 3.9382 | 3.7622 | 3.5805 | 3.409 | 3.0213 | 2.6784 | 2.2813
|  | MARNOCH | ST |  |  |  | 5.321 | 5.2545 | 5.1309 | 5.01 | 4.8925 | 4.7255 | 4.5871 | 4.3884 | 4.2396 | 4.0791 | 3.8994 | 3.0402 | 2.5549 | 2.2256 | 5.9924 | 5.9599 | 5.8709 | 5.7899 | 5.7158 | 5.5836 | 5.4873 | 5.3284 | 5.2224 | 5.1086 | 4.9762 | 4.3236 | 3.9346 | 3.6075 | 5.4103 | 5.3511 | 5.2275 | 5.1093 | 4.9968 | 4.8242 | 4.6898 | 4.4885 | 4.3398 | 4.1799 | 3.9982 | 3.1324 | 2.6529 | 2.3176
|  | MARNOCH | FS |  |  |  | 5.3701 | 5.325 | 5.2456 | 5.1579 | 5.0692 | 4.9732 | 4.869 | 4.7219 | 4.5921 | 4.4586 | 4.3205 | 3.4657 | 2.8869 | 2.6627 | 6.0109 | 5.9871 | 5.9425 | 5.8922 | 5.8394 | 5.7813 | 5.7132 | 5.6106 | 5.5279 | 5.4396 | 5.3464 | 4.8097 | 4.354 | 4.0786 | 5.4521 | 5.4115 | 5.3381 | 5.2566 | 5.1734 | 5.0829 | 4.9841 | 4.8428 | 4.7185 | 4.5895 | 4.455 | 3.6423 | 3.0908 | 2.8854
| BEAULY | MARYBANK | MINIMUM HEADROOM | NH 46749 53948 | YES | YES | 3.0346 | 2.9789 | 2.9153 | 2.8338 | 2.6559 | 2.4692 | 2.254 | 2.1416 | 2.0121 | 1.8884 | 1.7618 | 1.3104 | 0.86405 | 0.44352 | 3.3969 | 3.3737 | 3.2912 | 3.1986 | 3.1263 | 2.9322 | 2.8337 | 2.6699 | 2.587 | 2.5053 | 2.3944 | 1.8438 | 1.3146 | 0.84446 | 2.9307 | 2.8979 | 2.8259 | 2.7272 | 2.6195 | 2.4223 | 2.2567 | 2.1523 | 2.0467 | 1.9504 | 1.838 | 1.2051 | 0.64229 | 0.16499
|  | MARYBANK | CT |  |  |  | 3.0767 | 3.0328 | 2.9402 | 2.8338 | 2.6559 | 2.4692 | 2.254 | 2.1416 | 2.0121 | 1.8884 | 1.7618 | 1.3104 | 0.9415 | 0.64741 | 3.4081 | 3.386 | 3.3404 | 3.2855 | 3.1263 | 2.9564 | 2.8451 | 2.7525 | 2.6541 | 2.5638 | 2.4587 | 1.9917 | 1.6341 | 1.3091 | 2.9417 | 2.912 | 2.8556 | 2.7902 | 2.6195 | 2.4223 | 2.2567 | 2.1523 | 2.0467 | 1.9504 | 1.838 | 1.336 | 0.94778 | 0.60343
|  | MARYBANK | LW |  |  |  | 3.0346 | 2.9789 | 2.9153 | 2.8468 | 2.7839 | 2.7006 | 2.4779 | 2.3879 | 2.2888 | 2.1941 | 2.1 | 1.82 | 1.3066 | 0.65355 | 3.3969 | 3.3737 | 3.3489 | 3.3222 | 3.2955 | 3.2606 | 3.1721 | 3.1136 | 3.0433 | 2.9749 | 2.9037 | 2.6389 | 2.045 | 1.2489 | 2.9307 | 2.8979 | 2.8656 | 2.8265 | 2.7776 | 2.7187 | 2.5735 | 2.505 | 2.4294 | 2.3572 | 2.2818 | 1.98 | 1.3626 | 0.56441
|  | MARYBANK | ST |  |  |  | 3.1097 | 3.0881 | 2.9662 | 2.8704 | 2.794 | 2.6103 | 2.4613 | 2.2993 | 2.2 | 2.0984 | 1.9701 | 1.3481 | 0.86405 | 0.44352 | 3.429 | 3.4196 | 3.2912 | 3.1986 | 3.1309 | 2.9322 | 2.8337 | 2.6699 | 2.587 | 2.5053 | 2.3944 | 1.8438 | 1.3146 | 0.84446 | 2.9724 | 2.9592 | 2.8259 | 2.7272 | 2.6521 | 2.4458 | 2.3354 | 2.1615 | 2.0663 | 1.9707 | 1.8442 | 1.2051 | 0.64229 | 0.16499
|  | MARYBANK | FS |  |  |  | 3.1239 | 3.1096 | 3.0659 | 3.0197 | 2.9694 | 2.9164 | 2.8043 | 2.7253 | 2.6541 | 2.5717 | 2.4921 | 2.103 | 1.8021 | 1.6563 | 3.435 | 3.4289 | 3.3953 | 3.3607 | 3.3214 | 3.2806 | 3.219 | 3.1535 | 3.1 | 3.0422 | 2.9833 | 2.7623 | 2.556 | 2.3907 | 2.9801 | 2.9713 | 2.9343 | 2.8958 | 2.8518 | 2.8055 | 2.7361 | 2.663 | 2.6021 | 2.5359 | 2.4681 | 2.1838 | 1.9135 | 1.7083
| LUNANHEAD | MARYTON | MINIMUM HEADROOM | NO 39206 53075 | NO | YES | 6.7174 | 6.3384 | 5.5146 | 4.6478 | 3.3145 | 1.8518 | 0.82665 | 0.15797 | -0.51908 | -1.1892 | -1.8193 | -3.7185 | -4.9191 | -6.0371 | 9.0584 | 8.8398 | 8.2787 | 7.6646 | 6.5458 | 5.2882 | 4.4844 | 3.9618 | 3.4274 | 2.9047 | 2.4061 | 0.99211 | -0.054796 | -1.2973 | 7.4389 | 7.0986 | 6.2879 | 5.4246 | 4.0399 | 2.519 | 1.4768 | 0.81531 | 0.11719 | -0.5705 | -1.2211 | -3.1315 | -4.4378 | -5.7545
|  | MARYTON | CT |  |  |  | 7.0913 | 6.8573 | 6.1787 | 5.4665 | 4.2955 | 3.1003 | 2.4191 | 1.7522 | 1.0552 | 0.3713 | -0.28127 | -2.5018 | -3.9957 | -4.8935 | 9.1848 | 9.0263 | 8.6347 | 8.1893 | 7.2421 | 6.2639 | 5.8444 | 5.3715 | 4.8545 | 4.3519 | 3.8648 | 2.1919 | 1.1053 | 0.053076 | 7.7673 | 7.5554 | 6.9323 | 6.2631 | 5.0717 | 3.8498 | 3.2024 | 2.5604 | 1.8697 | 1.1851 | 0.52867 | -1.6849 | -3.1001 | -4.0078
|  | MARYTON | LW |  |  |  | 6.7174 | 6.3384 | 5.5146 | 4.6478 | 3.3145 | 1.8518 | 0.82665 | 0.15797 | -0.51908 | -1.1892 | -1.8193 | -3.7185 | -4.9191 | -6.0371 | 9.0584 | 8.8398 | 8.2787 | 7.6646 | 6.5458 | 5.2882 | 4.4844 | 3.9618 | 3.4274 | 2.9047 | 2.4061 | 0.99211 | -0.054796 | -1.2973 | 7.4389 | 7.0986 | 6.2879 | 5.4246 | 4.0399 | 2.519 | 1.4768 | 0.81531 | 0.11719 | -0.5705 | -1.2211 | -3.1315 | -4.4378 | -5.7545
|  | MARYTON | ST |  |  |  | 7.2915 | 7.1812 | 6.6891 | 6.3019 | 5.7559 | 4.8293 | 4.4853 | 4.0273 | 3.6896 | 3.3425 | 2.9449 | 0.54929 | -1.0555 | -2.6223 | 9.2763 | 9.2033 | 8.6835 | 8.2887 | 7.7829 | 6.8061 | 6.4693 | 6.0049 | 5.6921 | 5.3718 | 4.9866 | 2.9287 | 1.551 | 0.15041 | 7.9478 | 7.8523 | 7.2968 | 6.8701 | 6.3154 | 5.2888 | 4.9152 | 4.4068 | 4.0471 | 3.6776 | 3.2461 | 0.83073 | -0.79603 | -2.3549
|  | MARYTON | FS |  |  |  | 7.3518 | 7.2652 | 7.0428 | 6.8206 | 6.4117 | 6.0279 | 5.7632 | 5.415 | 5.099 | 4.7655 | 4.4421 | 2.4516 | 0.61878 | -0.57072 | 9.3072 | 9.2469 | 9.0691 | 8.884 | 8.5348 | 8.2005 | 7.9705 | 7.6819 | 7.4243 | 7.1487 | 6.8715 | 5.3537 | 3.7605 | 2.3421 | 8.0026 | 7.9285 | 7.7103 | 7.4895 | 7.0879 | 6.7089 | 6.4437 | 6.0977 | 5.781 | 5.4456 | 5.1146 | 3.1911 | 1.4703 | 0.38825
| STRICHEN | MAUD | MINIMUM HEADROOM | NJ 92528 47491 | NO | YES | 4.5853 | 4.4044 | 4.225 | 4.023 | 3.7486 | 3.4096 | 3.1573 | 2.9839 | 2.7886 | 2.599 | 2.4116 | 1.8556 | 1.2762 | 0.70679 | 5.662 | 5.5755 | 5.4927 | 5.3705 | 5.1148 | 4.8679 | 4.7275 | 4.5849 | 4.424 | 4.263 | 4.0922 | 3.4559 | 2.8052 | 2.1921 | 4.9356 | 4.7723 | 4.6123 | 4.4309 | 4.1231 | 3.7816 | 3.5474 | 3.3617 | 3.1486 | 2.9423 | 2.7406 | 2.1301 | 1.4305 | 0.79309
|  | MAUD | CT |  |  |  | 4.7363 | 4.617 | 4.3702 | 4.0988 | 3.7486 | 3.4096 | 3.1573 | 2.9839 | 2.7886 | 2.599 | 2.4116 | 1.8556 | 1.2876 | 0.90142 | 5.7163 | 5.6547 | 5.5251 | 5.3705 | 5.1148 | 4.8679 | 4.7275 | 4.5849 | 4.424 | 4.263 | 4.0922 | 3.5276 | 3.067 | 2.6053 | 5.0638 | 4.955 | 4.7273 | 4.4728 | 4.1231 | 3.7816 | 3.5474 | 3.3617 | 3.1486 | 2.9423 | 2.7406 | 2.1301 | 1.5419 | 1.1065
|  | MAUD | LW |  |  |  | 4.5853 | 4.4044 | 4.225 | 4.023 | 3.8158 | 3.5892 | 3.3536 | 3.1839 | 3.0134 | 2.8396 | 2.6718 | 2.2454 | 1.648 | 0.9093 | 5.662 | 5.5755 | 5.4927 | 5.3923 | 5.2868 | 5.1707 | 5.0457 | 4.9219 | 4.7937 | 4.6446 | 4.5033 | 4.1853 | 3.5738 | 2.7178 | 4.9356 | 4.7723 | 4.6123 | 4.4309 | 4.2462 | 4.0371 | 3.8165 | 3.639 | 3.458 | 3.2753 | 3.1001 | 2.6753 | 1.9867 | 1.0955
|  | MAUD | ST |  |  |  | 4.822 | 4.7524 | 4.5597 | 4.3864 | 4.2115 | 3.9537 | 3.796 | 3.5578 | 3.383 | 3.2011 | 2.9932 | 1.9916 | 1.2762 | 0.70679 | 5.7534 | 5.72 | 5.5546 | 5.4148 | 5.2861 | 5.0436 | 4.9288 | 4.7186 | 4.5902 | 4.4602 | 4.2913 | 3.4559 | 2.8052 | 2.1921 | 5.1378 | 5.0763 | 4.8709 | 4.6925 | 4.5198 | 4.2347 | 4.0754 | 3.8171 | 3.6385 | 3.4541 | 3.2374 | 2.2002 | 1.4305 | 0.79309
|  | MAUD | FS |  |  |  | 4.8763 | 4.826 | 4.7296 | 4.6217 | 4.4931 | 4.3825 | 4.2665 | 4.1079 | 3.9616 | 3.8097 | 3.6509 | 2.7568 | 2.189 | 1.9525 | 5.7703 | 5.7467 | 5.6876 | 5.616 | 5.5284 | 5.4534 | 5.3773 | 5.2642 | 5.1647 | 5.0602 | 4.9511 | 4.4158 | 3.9574 | 3.664 | 5.1838 | 5.1391 | 5.0468 | 4.9433 | 4.8199 | 4.7118 | 4.5993 | 4.441 | 4.2968 | 4.1466 | 3.9893 | 3.1431 | 2.5913 | 2.3692
| MYBSTER | MELVICH | MINIMUM HEADROOM | NC 88547 64274 | YES | YES | 0.21053 | 0.1703 | 0.12527 | 0.082231 | 0.03534 | -0.025198 | -0.080568 | -0.1209 | -0.14703 | -0.18499 | -0.22536 | -0.38677 | -0.49663 | -0.55472 | -1.0106 | -1.0297 | -1.0489 | -1.0721 | -1.0932 | -1.1177 | -1.1462 | -1.1737 | -1.2022 | -1.2318 | -1.2579 | -1.3004 | -1.3325 | -1.3512 | -2.1127 | -2.1477 | -2.1841 | -2.2288 | -2.2747 | -2.3296 | -2.3801 | -2.4183 | -2.4433 | -2.4758 | -2.5135 | -2.626 | -2.7261 | -2.7878
|  | MELVICH | CT |  |  |  | 0.22718 | 0.1924 | 0.1367 | 0.085775 | 0.03534 | -0.025198 | -0.080568 | -0.1209 | -0.14703 | -0.18151 | -0.22536 | -0.35759 | -0.41312 | -0.42985 | -1.0015 | -1.0156 | -1.0442 | -1.0721 | -1.0932 | -1.1177 | -1.1402 | -1.1623 | -1.1898 | -1.2206 | -1.2461 | -1.3004 | -1.3325 | -1.3512 | -2.0983 | -2.1291 | -2.1826 | -2.2288 | -2.2747 | -2.3296 | -2.3801 | -2.4183 | -2.4433 | -2.4758 | -2.5135 | -2.6185 | -2.6816 | -2.7008
|  | MELVICH | LW |  |  |  | 0.21053 | 0.1703 | 0.12527 | 0.082231 | 0.037874 | -0.015014 | -0.073434 | -0.10878 | -0.14507 | -0.18499 | -0.21903 | -0.29323 | -0.3292 | -0.34309 | -1.0106 | -1.0297 | -1.0489 | -1.0688 | -1.0873 | -1.1148 | -1.1462 | -1.1737 | -1.2022 | -1.2318 | -1.2579 | -1.2997 | -1.3118 | -1.3159 | -2.1127 | -2.1477 | -2.1841 | -2.2189 | -2.2554 | -2.3012 | -2.3522 | -2.3865 | -2.4208 | -2.4577 | -2.4894 | -2.5666 | -2.5932 | -2.6038
|  | MELVICH | ST |  |  |  | 0.25142 | 0.23528 | 0.21371 | 0.18825 | 0.16235 | 0.13431 | 0.099896 | 0.062361 | 0.014966 | -0.036409 | -0.091466 | -0.38677 | -0.49663 | -0.53584 | -0.9945 | -1.0018 | -1.0108 | -1.0221 | -1.0335 | -1.0462 | -1.0618 | -1.0792 | -1.1007 | -1.1235 | -1.1476 | -1.2759 | -1.3147 | -1.3344 | -2.0761 | -2.0921 | -2.1117 | -2.1349 | -2.1587 | -2.1847 | -2.2165 | -2.2507 | -2.2919 | -2.3352 | -2.3804 | -2.626 | -2.7261 | -2.7668
|  | MELVICH | FS |  |  |  | 0.25817 | 0.2504 | 0.23293 | 0.21241 | 0.19257 | 0.16981 | 0.14663 | 0.11654 | 0.084516 | 0.051341 | 0.011708 | -0.24307 | -0.43668 | -0.55472 | -0.99083 | -0.996 | -1.0041 | -1.0134 | -1.0221 | -1.0323 | -1.0431 | -1.0571 | -1.0725 | -1.0888 | -1.1077 | -1.2273 | -1.3187 | -1.3471 | -2.066 | -2.0761 | -2.0938 | -2.1129 | -2.1311 | -2.152 | -2.1734 | -2.2011 | -2.2307 | -2.2614 | -2.2974 | -2.5253 | -2.6877 | -2.7878
| CHARLESTON | MENZIESHILL | MINIMUM HEADROOM | NO 35918 31022 | NO | YES | 8.4082 | 7.9504 | 7.155 | 6.1896 | 5.2083 | 4.3597 | 3.443 | 2.6172 | 1.7857 | 0.93606 | 0.12889 | -1.945 | -2.9406 | -4.1113 | 10.1374 | 9.9858 | 9.7961 | 9.3748 | 8.8705 | 8.6438 | 8.2983 | 7.8404 | 7.4213 | 7.0012 | 6.5419 | 4.6526 | 2.9185 | -1.5502 | 13.6898 | 13.2697 | 12.5855 | 11.7204 | 10.8474 | 10.0593 | 9.1945 | 8.3704 | 7.5312 | 6.6742 | 5.8611 | 3.845 | 2.7801 | 1.3779
|  | MENZIESHILL | CT |  |  |  | 8.7743 | 8.4762 | 7.6683 | 6.6876 | 5.7172 | 5.0246 | 4.3509 | 3.5941 | 2.8161 | 2.0408 | 1.2356 | -1.4476 | -2.8708 | -3.7501 | 10.1374 | 9.9858 | 9.7961 | 9.3748 | 8.8705 | 8.6438 | 8.2983 | 7.8404 | 7.4213 | 7.0012 | 6.5419 | 4.6526 | 2.9185 | 0.64769 | 13.8415 | 13.7141 | 12.9935 | 12.0889 | 11.2038 | 10.5636 | 9.9525 | 9.2282 | 8.4692 | 7.7131 | 6.9272 | 4.3789 | 3.0696 | 2.2006
|  | MENZIESHILL | LW |  |  |  | 8.4082 | 7.9504 | 7.155 | 6.1896 | 5.2083 | 4.3597 | 3.443 | 2.6172 | 1.7857 | 0.93606 | 0.12889 | -1.945 | -2.9406 | -4.1113 | 10.1408 | 10.0081 | 9.8825 | 9.4845 | 9.0638 | 8.722 | 8.33 | 7.8848 | 7.4829 | 7.0769 | 6.6848 | 5.6112 | 4.7316 | 3.59 | 13.6898 | 13.2697 | 12.5855 | 11.7204 | 10.8474 | 10.0593 | 9.1945 | 8.3704 | 7.5312 | 6.6742 | 5.8611 | 3.845 | 2.7801 | 1.3779
|  | MENZIESHILL | ST |  |  |  | 8.9774 | 8.8205 | 8.6035 | 8.2236 | 7.7905 | 7.5887 | 7.392 | 7.0368 | 6.7275 | 6.3835 | 5.9881 | 3.4172 | 1.8248 | 0.22192 | 10.1886 | 10.1062 | 9.9648 | 9.5898 | 9.1595 | 8.9919 | 8.8614 | 8.5511 | 8.3221 | 8.0527 | 7.7309 | 6.0228 | 4.3251 | 1.6084 | 13.8773 | 13.8038 | 13.668 | 13.349 | 13.0072 | 12.8034 | 12.5863 | 12.1959 | 11.8586 | 11.4847 | 11.0517 | 8.4318 | 6.8447 | 5.3307
|  | MENZIESHILL | FS |  |  |  | 9.044 | 8.9158 | 8.723 | 8.416 | 8.0453 | 7.8579 | 7.6575 | 7.3364 | 7.031 | 6.7113 | 6.384 | 4.2372 | 1.9504 | 0.27008 | 10.2784 | 10.203 | 10.1115 | 9.8504 | 9.5216 | 9.4033 | 9.2761 | 9.0589 | 8.8884 | 8.709 | 8.5261 | 6.6705 | 3.8051 | -1.5502 | 13.9213 | 13.8557 | 13.7712 | 13.5508 | 13.2928 | 13.1218 | 12.9174 | 12.5978 | 12.2917 | 11.9685 | 11.6334 | 9.4988 | 7.3062 | 5.8389
| KINTORE | METHLICK | MINIMUM HEADROOM | NJ 85339 36835 | NO | YES | 6.3762 | 6.2636 | 6.146 | 6.0252 | 5.8521 | 5.627 | 5.4654 | 5.3543 | 5.2284 | 5.1037 | 4.981 | 4.6276 | 4.1967 | 3.8027 | 3.9212 | 3.904 | 3.8347 | 3.7702 | 3.7208 | 3.5833 | 3.5323 | 3.4178 | 3.3601 | 3.3039 | 3.2274 | 2.8519 | 2.4884 | 2.1413 | 2.6627 | 2.6523 | 2.5772 | 2.5161 | 2.3466 | 2.152 | 2.0327 | 1.9429 | 1.8493 | 1.7597 | 1.6628 | 1.2742 | 0.80796 | 0.4011
|  | METHLICK | CT |  |  |  | 6.4753 | 6.3995 | 6.2362 | 6.0647 | 5.8521 | 5.627 | 5.4654 | 5.3543 | 5.2284 | 5.1037 | 4.981 | 4.6276 | 4.2456 | 3.9907 | 3.9212 | 3.904 | 3.8695 | 3.8292 | 3.7208 | 3.6054 | 3.5613 | 3.493 | 3.4229 | 3.3582 | 3.2862 | 2.9911 | 2.7636 | 2.5126 | 2.664 | 2.6555 | 2.6306 | 2.5304 | 2.3466 | 2.152 | 2.0327 | 1.9429 | 1.8493 | 1.7597 | 1.6628 | 1.3296 | 0.98599 | 0.71944
|  | METHLICK | LW |  |  |  | 6.3762 | 6.2636 | 6.146 | 6.0252 | 5.9034 | 5.7605 | 5.6115 | 5.5048 | 5.3945 | 5.2828 | 5.1741 | 4.9051 | 4.5042 | 4.0214 | 3.9229 | 3.9069 | 3.8934 | 3.8777 | 3.8626 | 3.8363 | 3.8052 | 3.7538 | 3.6985 | 3.6448 | 3.5919 | 3.4393 | 3.051 | 2.4907 | 2.6627 | 2.6523 | 2.5998 | 2.5208 | 2.4391 | 2.3452 | 2.2471 | 2.172 | 2.0939 | 2.016 | 1.9381 | 1.7158 | 1.2745 | 0.69356
|  | METHLICK | ST |  |  |  | 6.5281 | 6.4825 | 6.3554 | 6.2452 | 6.1447 | 5.974 | 5.8712 | 5.7119 | 5.5966 | 5.4752 | 5.3382 | 4.6812 | 4.1967 | 3.8027 | 3.929 | 3.9237 | 3.8347 | 3.7702 | 3.7226 | 3.5833 | 3.5323 | 3.4178 | 3.3601 | 3.3039 | 3.2274 | 2.8519 | 2.4884 | 2.1413 | 2.6663 | 2.6633 | 2.5772 | 2.5161 | 2.4732 | 2.3396 | 2.2615 | 2.1099 | 2.0156 | 1.92 | 1.8062 | 1.2742 | 0.80796 | 0.4011
|  | METHLICK | FS |  |  |  | 6.5683 | 6.537 | 6.4738 | 6.4056 | 6.3361 | 6.2621 | 6.1875 | 6.0827 | 5.9889 | 5.8862 | 5.782 | 5.1909 | 4.8145 | 4.6493 | 3.9303 | 3.926 | 3.9038 | 3.8804 | 3.8532 | 3.8246 | 3.7971 | 3.7502 | 3.7126 | 3.6729 | 3.6311 | 3.4793 | 3.3363 | 3.2196 | 2.6669 | 2.6644 | 2.6443 | 2.6232 | 2.599 | 2.5739 | 2.5506 | 2.5072 | 2.4355 | 2.3576 | 2.2788 | 1.8773 | 1.6163 | 1.4663
| SHETLAND | MID YELL | MINIMUM HEADROOM | HU4817291442 | YES | YES | -0.050619 | -0.07859 | -0.11705 | -0.15206 | -0.18688 | -0.22838 | -0.27367 | -0.30564 | -0.3357 | -0.36632 | -0.39636 | -0.44765 | -0.48192 | -0.504 | 0.29898 | 0.29299 | 0.28371 | 0.27629 | 0.2699 | 0.26305 | 0.25158 | 0.23701 | 0.22112 | 0.20462 | 0.18947 | 0.16036 | 0.1387 | 0.11988 | 0.0094616 | -0.0094304 | -0.032061 | -0.053298 | -0.075834 | -0.1032 | -0.13386 | -0.15864 | -0.1834 | -0.20915 | -0.23783 | -0.29247 | -0.31723 | -0.33603
|  | MID YELL | CT |  |  |  | -0.027319 | -0.046831 | -0.093562 | -0.14107 | -0.18325 | -0.22521 | -0.26565 | -0.29092 | -0.31636 | -0.34945 | -0.37532 | -0.42544 | -0.48192 | -0.504 | 0.29898 | 0.29299 | 0.28371 | 0.27629 | 0.2699 | 0.26305 | 0.25587 | 0.24537 | 0.23492 | 0.2243 | 0.208 | 0.16705 | 0.1387 | 0.11988 | 0.020589 | 0.0056862 | -0.023482 | -0.049381 | -0.075555 | -0.10156 | -0.12766 | -0.14656 | -0.16096 | -0.17941 | -0.2118 | -0.27383 | -0.31723 | -0.33603
|  | MID YELL | LW |  |  |  | -0.050619 | -0.07859 | -0.11705 | -0.15206 | -0.18688 | -0.22838 | -0.27367 | -0.30564 | -0.3357 | -0.36632 | -0.39636 | -0.44765 | -0.47683 | -0.48518 | 0.29954 | 0.29355 | 0.288 | 0.28156 | 0.27552 | 0.26458 | 0.25158 | 0.23701 | 0.22112 | 0.20462 | 0.18947 | 0.16036 | 0.14865 | 0.14557 | 0.0094616 | -0.0094304 | -0.032061 | -0.053298 | -0.075834 | -0.1032 | -0.13386 | -0.15864 | -0.1834 | -0.20915 | -0.23783 | -0.29247 | -0.3144 | -0.32025
|  | MID YELL | ST |  |  |  | -0.0084758 | -0.019695 | -0.030782 | -0.046814 | -0.063669 | -0.080241 | -0.10054 | -0.1226 | -0.14343 | -0.17252 | -0.20161 | -0.34268 | -0.3945 | -0.42119 | 0.30245 | 0.30088 | 0.2988 | 0.29602 | 0.29212 | 0.28682 | 0.28032 | 0.27236 | 0.26265 | 0.25141 | 0.23876 | 0.17326 | 0.15697 | 0.15173 | 0.03449 | 0.02712 | 0.018799 | 0.0083092 | -0.0036967 | -0.016204 | -0.031422 | -0.047877 | -0.064954 | -0.087096 | -0.11042 | -0.23002 | -0.27783 | -0.2951
|  | MID YELL | FS |  |  |  | -0.0023706 | -0.0092699 | -0.024957 | -0.034779 | -0.053423 | -0.064432 | -0.083579 | -0.10418 | -0.12417 | -0.1471 | -0.16808 | -0.32103 | -0.42571 | -0.45484 | 0.30287 | 0.30156 | 0.29991 | 0.29784 | 0.29555 | 0.29237 | 0.2881 | 0.2831 | 0.27733 | 0.27082 | 0.26352 | 0.21566 | 0.15962 | 0.13405 | 0.037924 | 0.033193 | 0.023256 | 0.015767 | 0.0040724 | -0.0047896 | -0.017714 | -0.031634 | -0.045654 | -0.061218 | -0.076888 | -0.18441 | -0.27608 | -0.30544
| KINTORE | MIDMAR | MINIMUM HEADROOM | NJ 68253 06875 | YES | YES | 0.46131 | 0.36068 | 0.25164 | 0.1373 | -0.043233 | -0.25093 | -0.41753 | -0.51981 | -0.62451 | -0.72732 | -0.83335 | -1.1609 | -1.5716 | -1.9114 | -0.86385 | -0.93266 | -1.001 | -1.1115 | -1.2814 | -1.4586 | -1.5796 | -1.6918 | -1.8211 | -1.948 | -2.0701 | -2.4786 | -2.9692 | -3.4429 | 0.26398 | 0.15369 | 0.042043 | -0.077203 | -0.30001 | -0.53397 | -0.71503 | -0.84354 | -0.96269 | -1.0783 | -1.2133 | -1.6602 | -2.2178 | -2.6414
|  | MIDMAR | CT |  |  |  | 0.55022 | 0.46874 | 0.31631 | 0.1595 | -0.043233 | -0.25093 | -0.41753 | -0.51981 | -0.62451 | -0.72732 | -0.83335 | -1.1609 | -1.5716 | -1.848 | -0.82231 | -0.8809 | -0.99083 | -1.1115 | -1.2814 | -1.4586 | -1.5796 | -1.6918 | -1.8211 | -1.948 | -2.0701 | -2.4697 | -2.8325 | -3.203 | 0.34812 | 0.25624 | 0.089463 | -0.073703 | -0.30001 | -0.53397 | -0.71503 | -0.84354 | -0.96269 | -1.0783 | -1.2133 | -1.6447 | -2.0266 | -2.3101
|  | MIDMAR | LW |  |  |  | 0.46131 | 0.36068 | 0.25164 | 0.1373 | 0.025032 | -0.10708 | -0.26023 | -0.35558 | -0.45827 | -0.56611 | -0.66475 | -0.94923 | -1.3473 | -1.8187 | -0.86385 | -0.93266 | -1.001 | -1.0762 | -1.1457 | -1.2421 | -1.3586 | -1.4614 | -1.572 | -1.6844 | -1.7891 | -2.045 | -2.4498 | -2.9869 | 0.26398 | 0.15369 | 0.042043 | -0.077203 | -0.19606 | -0.34109 | -0.51033 | -0.63277 | -0.76699 | -0.90646 | -1.0372 | -1.4081 | -1.8513 | -2.4057
|  | MIDMAR | ST |  |  |  | 0.60698 | 0.56734 | 0.4548 | 0.35353 | 0.26964 | 0.11137 | 0.0061897 | -0.14151 | -0.24969 | -0.36048 | -0.48934 | -1.0982 | -1.5429 | -1.9114 | -0.79301 | -0.82076 | -0.93119 | -1.0243 | -1.1007 | -1.2656 | -1.3614 | -1.5106 | -1.6118 | -1.716 | -1.8429 | -2.4786 | -2.9692 | -3.4429 | 0.40883 | 0.36556 | 0.23437 | 0.11943 | 0.021142 | -0.16756 | -0.2897 | -0.46398 | -0.59112 | -0.72278 | -0.87953 | -1.6602 | -2.2178 | -2.6414
|  | MIDMAR | FS |  |  |  | 0.63956 | 0.61175 | 0.55585 | 0.49891 | 0.43712 | 0.37002 | 0.30005 | 0.21082 | 0.12508 | 0.034399 | -0.057494 | -0.58839 | -0.95684 | -1.1914 | -0.77787 | -0.79967 | -0.84502 | -0.8933 | -0.94605 | -1.0036 | -1.0665 | -1.1479 | -1.2246 | -1.3065 | -1.3921 | -1.8488 | -2.2548 | -2.5719 | 0.4308 | 0.40867 | 0.3454 | 0.28104 | 0.21071 | 0.13435 | 0.053894 | -0.048223 | -0.14667 | -0.25028 | -0.35702 | -0.96068 | -1.3988 | -1.6905
| BRIDGE OF DUN | MILL RD | MINIMUM HEADROOM | NO 71317 57683 | NO | YES | 5.1887 | 5.0259 | 4.4415 | 3.8124 | 2.8673 | 1.8372 | 1.0513 | 0.628 | 0.18004 | -0.27135 | -0.72093 | -2.4431 | -3.4055 | -4.1627 | 6.4086 | 6.3142 | 5.8271 | 5.2884 | 4.354 | 3.3295 | 2.6323 | 2.2955 | 1.9348 | 1.5827 | 1.2243 | -0.16357 | -1.0121 | -1.8572 | 5.2912 | 5.1228 | 4.6611 | 3.9821 | 2.9083 | 1.7387 | 0.89154 | 0.46134 | 0.0056492 | -0.44739 | -0.90239 | -2.673 | -3.7136 | -4.6046
|  | MILL RD | CT |  |  |  | 5.376 | 5.2125 | 4.8039 | 4.3514 | 3.715 | 3.0483 | 2.6064 | 2.2602 | 1.9148 | 1.5728 | 1.2193 | -0.19548 | -1.2305 | -1.8966 | 6.4603 | 6.3334 | 6.0751 | 5.765 | 5.2025 | 4.6059 | 4.2948 | 4.0401 | 3.783 | 3.5299 | 3.2582 | 2.1016 | 1.0995 | -0.085814 | 5.2912 | 5.1228 | 4.9044 | 4.6153 | 3.9306 | 3.2105 | 2.7753 | 2.4369 | 2.1008 | 1.77 | 1.4258 | 0.047099 | -0.94909 | -1.6225
|  | MILL RD | LW |  |  |  | 5.1887 | 5.0259 | 4.4415 | 3.8124 | 2.8673 | 1.8372 | 1.0513 | 0.628 | 0.18004 | -0.27135 | -0.72093 | -2.4431 | -3.4055 | -4.1627 | 6.4086 | 6.3142 | 5.8271 | 5.2884 | 4.354 | 3.3295 | 2.6323 | 2.2955 | 1.9348 | 1.5827 | 1.2243 | -0.16357 | -1.0121 | -1.8572 | 5.304 | 5.2352 | 4.6611 | 3.9821 | 2.9083 | 1.7387 | 0.89154 | 0.46134 | 0.0056492 | -0.44739 | -0.90239 | -2.673 | -3.7136 | -4.6046
|  | MILL RD | ST |  |  |  | 5.516 | 5.4953 | 5.1884 | 4.966 | 4.7923 | 4.3064 | 4.1135 | 3.895 | 3.7239 | 3.5381 | 3.2017 | 1.0072 | -0.038524 | -0.6753 | 6.5226 | 6.4935 | 6.1148 | 5.8386 | 5.6292 | 5.0366 | 4.808 | 4.5571 | 4.3775 | 4.1871 | 3.9478 | 2.1212 | 1.1855 | -0.046148 | 5.3309 | 5.3039 | 4.9293 | 4.6548 | 4.4466 | 3.8543 | 3.6205 | 3.3638 | 3.1757 | 2.9707 | 2.7111 | 0.92941 | -0.11972 | -0.83419
|  | MILL RD | FS |  |  |  | 5.5177 | 5.5036 | 5.4025 | 5.2947 | 5.1764 | 5.0463 | 4.9195 | 4.7805 | 4.6436 | 4.4943 | 4.3308 | 3.2276 | 1.7741 | 0.5396 | 6.5252 | 6.5 | 6.388 | 6.2687 | 6.133 | 5.9866 | 5.8429 | 5.6937 | 5.5478 | 5.3871 | 5.2106 | 4.1074 | 2.523 | 0.32514 | 5.3445 | 5.3276 | 5.2349 | 5.1373 | 5.0227 | 4.9007 | 4.7823 | 4.671 | 4.566 | 4.4496 | 4.3196 | 3.4226 | 2.0846 | 0.81616
| ABERNETHY | MILNATHORT | MINIMUM HEADROOM | NO 11900 05074 | NO | YES | 0.088605 | -0.69062 | -1.9586 | -3.2882 | -4.9484 | -6.9148 | -8.8544 | -10.7637 | -12.3747 | -13.7362 | -15.1137 | -19.2664 | -21.475 | -23.0882 | 4.5461 | 4.0837 | 3.2175 | 2.277 | 0.93648 | -0.6762 | -2.1542 | -3.6409 | -4.869 | -5.8766 | -7.0051 | -11.7182 | -14.8953 | -16.1562 | 3.0357 | 2.3625 | 1.2004 | -0.05635 | -1.7591 | -3.7916 | -5.7147 | -7.5407 | -9.1142 | -10.4655 | -11.8263 | -15.969 | -19.7475 | -21.1097
|  | MILNATHORT | CT |  |  |  | 0.54825 | -0.060479 | -1.2201 | -2.4339 | -4.0493 | -5.7679 | -7.2256 | -9.0461 | -10.6957 | -12.0256 | -13.3777 | -18.1498 | -20.6625 | -21.8739 | 4.6803 | 4.2754 | 3.5711 | 2.7906 | 1.5174 | 0.14903 | -0.8306 | -2.2151 | -3.4618 | -4.4385 | -5.4986 | -10.1028 | -11.7585 | -12.614 | 3.3666 | 2.828 | 1.8183 | 0.73046 | -0.86901 | -2.6124 | -3.9731 | -5.6887 | -7.2817 | -8.5864 | -9.9061 | -14.6646 | -16.973 | -18.1044
|  | MILNATHORT | LW |  |  |  | 0.088605 | -0.69062 | -1.9586 | -3.2882 | -4.9484 | -6.9148 | -8.8544 | -10.7637 | -12.3747 | -13.7362 | -15.1137 | -19.2664 | -21.475 | -23.0882 | 4.5461 | 4.0837 | 3.2175 | 2.277 | 0.93648 | -0.6762 | -2.1542 | -3.6409 | -4.869 | -5.8766 | -7.0051 | -11.1641 | -13.3601 | -15.0717 | 3.0357 | 2.3625 | 1.2004 | -0.05635 | -1.7591 | -3.7916 | -5.7147 | -7.5407 | -9.1142 | -10.4655 | -11.8263 | -15.8471 | -18.2705 | -20.065
|  | MILNATHORT | ST |  |  |  | 1.1592 | 0.84722 | -0.040687 | -0.79773 | -1.5095 | -2.8156 | -3.8033 | -5.3377 | -6.5789 | -7.6297 | -8.8195 | -17.2931 | -21.0144 | -22.232 | 5.0516 | 4.8651 | 4.0164 | 3.3292 | 2.7264 | 1.4044 | 0.56465 | -0.7488 | -1.806 | -2.9353 | -4.2654 | -11.7182 | -14.8953 | -16.1562 | 3.896 | 3.6332 | 2.6829 | 1.8954 | 1.1881 | -0.24846 | -1.2104 | -2.6535 | -3.8149 | -5.0924 | -6.7973 | -15.969 | -19.7475 | -21.1097
|  | MILNATHORT | FS |  |  |  | 1.3869 | 1.158 | 0.72905 | 0.29238 | -0.18971 | -0.70827 | -1.3578 | -2.4183 | -3.2376 | -3.9639 | -4.7473 | -9.7153 | -14.4935 | -18.6835 | 5.173 | 5.0281 | 4.7137 | 4.3844 | 4.0121 | 3.5996 | 3.0746 | 2.2243 | 1.5911 | 1.0331 | 0.42405 | -3.4294 | -8.3993 | -11.8109 | 4.0832 | 3.8902 | 3.4917 | 3.0783 | 2.618 | 2.121 | 1.5112 | 0.55981 | -0.18505 | -0.85928 | -1.5898 | -6.3333 | -12.5069 | -16.7175
| MILTON OF CRAIGIE | MILTON OF CRAIGIE | MINIMUM HEADROOM | NO 43137 31857 | NO | YES | 12.5401 | 12.1329 | 11.4315 | 10.7292 | 10.0834 | 9.1525 | 8.2129 | 7.5391 | 6.9901 | 6.4211 | 5.5566 | 3.8021 | 3.0974 | 2.4463 | 19.23 | 18.9341 | 18.4841 | 18.0292 | 17.6356 | 16.9688 | 16.324 | 15.8585 | 15.499 | 15.1074 | 14.4441 | 13.2599 | 12.4271 | 10.5849 | 11.5073 | 11.121 | 10.4792 | 9.8306 | 9.2165 | 8.3239 | 7.4319 | 6.7734 | 6.2264 | 5.6616 | 4.8292 | 3.1474 | 2.3943 | 1.5993
|  | MILTON OF CRAIGIE | CT |  |  |  | 12.8487 | 12.5606 | 11.9307 | 11.2775 | 10.7316 | 9.9969 | 9.2879 | 8.6316 | 8.065 | 7.5036 | 6.6324 | 4.4215 | 3.3411 | 2.7725 | 19.3503 | 19.0969 | 18.6934 | 18.2615 | 17.9264 | 17.3996 | 16.9065 | 16.4618 | 16.1024 | 15.7321 | 15.0724 | 13.4893 | 12.4271 | 11.1757 | 11.7697 | 11.4904 | 10.9137 | 10.31 | 9.7986 | 9.1114 | 8.4621 | 7.8434 | 7.3006 | 6.7632 | 5.9442 | 3.8933 | 2.9021 | 2.3331
|  | MILTON OF CRAIGIE | LW |  |  |  | 12.5401 | 12.1329 | 11.4315 | 10.7292 | 10.0834 | 9.1525 | 8.2129 | 7.5391 | 6.9901 | 6.4211 | 5.5566 | 3.8021 | 3.0974 | 2.4463 | 19.23 | 18.9341 | 18.4841 | 18.0292 | 17.6356 | 16.9688 | 16.324 | 15.8585 | 15.499 | 15.1074 | 14.4441 | 13.2599 | 12.634 | 11.8659 | 11.5073 | 11.121 | 10.4792 | 9.8306 | 9.2165 | 8.3239 | 7.4319 | 6.7734 | 6.2264 | 5.6616 | 4.8292 | 3.1474 | 2.3943 | 1.5993
|  | MILTON OF CRAIGIE | ST |  |  |  | 12.9539 | 12.757 | 12.521 | 12.2842 | 12.1673 | 11.7974 | 11.4401 | 11.094 | 10.8781 | 10.6382 | 10.0601 | 7.9449 | 6.6013 | 5.3577 | 19.4049 | 19.2163 | 18.9526 | 18.6827 | 18.5576 | 18.1465 | 17.7656 | 17.436 | 17.2523 | 17.0336 | 16.4086 | 14.6835 | 13.3356 | 11.7509 | 11.8652 | 11.6767 | 11.4364 | 11.1982 | 11.0703 | 10.6891 | 10.3348 | 9.9793 | 9.7498 | 9.4957 | 8.9257 | 6.883 | 5.5823 | 4.3804
|  | MILTON OF CRAIGIE | FS |  |  |  | 13.0028 | 12.8427 | 12.6691 | 12.4731 | 12.364 | 12.1278 | 11.8406 | 11.5302 | 11.2851 | 11.0405 | 10.6138 | 8.7621 | 6.8176 | 5.4487 | 19.4523 | 19.2992 | 19.1251 | 18.9205 | 18.8123 | 18.5631 | 18.2683 | 17.9845 | 17.7568 | 17.5307 | 17.1139 | 15.3643 | 13.1854 | 10.5849 | 11.9116 | 11.7591 | 11.5934 | 11.405 | 11.2932 | 11.0641 | 10.786 | 10.4861 | 10.2471 | 10.006 | 9.5964 | 7.8067 | 5.9939 | 4.7641
| STRICHEN | MINTLAW | MINIMUM HEADROOM | NK 00897 48662 | NO | YES | 8.2357 | 7.9829 | 7.576 | 7.2177 | 6.8666 | 6.3472 | 5.7876 | 5.2877 | 4.925 | 4.5529 | 4.1717 | 3.2271 | 2.3966 | 1.543 | 9.363 | 9.2325 | 9.0094 | 8.8355 | 8.6435 | 8.3188 | 7.9988 | 7.6255 | 7.3538 | 7.0754 | 6.8062 | 6.0375 | 5.3497 | 4.4248 | 9.3555 | 9.1201 | 8.7534 | 8.4296 | 8.117 | 7.6376 | 7.1127 | 6.614 | 6.2377 | 5.8544 | 5.4838 | 4.5671 | 3.66 | 2.6542
|  | MINTLAW | CT |  |  |  | 8.4637 | 8.2921 | 7.83 | 7.4146 | 7.014 | 6.512 | 6.0128 | 5.538 | 5.1418 | 4.751 | 4.3781 | 3.3264 | 2.4567 | 1.8652 | 9.4492 | 9.3493 | 9.0842 | 8.8621 | 8.6435 | 8.3188 | 8.0206 | 7.6703 | 7.3859 | 7.093 | 6.8225 | 6.0375 | 5.3497 | 4.6454 | 9.5504 | 9.3873 | 8.9599 | 8.5722 | 8.2022 | 7.7398 | 7.2861 | 6.8219 | 6.4161 | 6.0157 | 5.6434 | 4.6194 | 3.7675 | 3.1456
|  | MINTLAW | LW |  |  |  | 8.2357 | 7.9829 | 7.576 | 7.2177 | 6.8666 | 6.3472 | 5.7876 | 5.2877 | 4.925 | 4.5529 | 4.1717 | 3.2271 | 2.3966 | 1.543 | 9.363 | 9.2325 | 9.0094 | 8.8355 | 8.6687 | 8.3454 | 7.9988 | 7.6255 | 7.3538 | 7.0754 | 6.8062 | 6.1411 | 5.3749 | 4.4248 | 9.3555 | 9.1201 | 8.7534 | 8.4296 | 8.117 | 7.6376 | 7.1127 | 6.614 | 6.2377 | 5.8544 | 5.4838 | 4.5671 | 3.66 | 2.6542
|  | MINTLAW | ST |  |  |  | 8.6134 | 8.5368 | 8.3307 | 8.1855 | 8.0396 | 7.7507 | 7.4716 | 7.0753 | 6.8409 | 6.5921 | 6.3179 | 4.8227 | 3.8216 | 2.8947 | 9.5173 | 9.4743 | 9.3191 | 9.2219 | 9.1269 | 8.8817 | 8.6667 | 8.3272 | 8.1499 | 7.9643 | 7.7386 | 6.5859 | 5.6941 | 4.7729 | 9.6813 | 9.6107 | 9.4119 | 9.2701 | 9.1291 | 8.8466 | 8.5777 | 8.1756 | 7.9341 | 7.6777 | 7.39 | 5.9227 | 4.8968 | 3.9387
|  | MINTLAW | FS |  |  |  | 8.6733 | 8.6098 | 8.4569 | 8.3313 | 8.2117 | 8.0185 | 7.7979 | 7.4998 | 7.2843 | 7.0573 | 6.8372 | 5.4755 | 4.3362 | 3.7667 | 9.5452 | 9.5086 | 9.4043 | 9.3281 | 9.2554 | 9.11 | 8.9459 | 8.7137 | 8.5589 | 8.3957 | 8.2351 | 7.279 | 6.3096 | 5.5468 | 9.7335 | 9.6751 | 9.5333 | 9.4159 | 9.3032 | 9.1229 | 8.9143 | 8.6262 | 8.415 | 8.1915 | 7.9718 | 6.6669 | 5.5949 | 5.0763
| BRIDGE OF DUN | MONTROSE NORTH | MINIMUM HEADROOM | NO 71226 59070 | NO | YES | -0.90742 | -3.5298 | -5.9949 | -7.2532 | -8.2595 | -9.0458 | -9.6326 | -10.1406 | -10.7069 | -11.2732 | -11.8289 | -13.4166 | -14.5607 | -15.8183 | -0.13759 | -2.995 | -5.4861 | -6.527 | -7.331 | -7.8346 | -8.0722 | -8.2784 | -8.4994 | -8.7156 | -8.9338 | -9.8003 | -10.9019 | -12.2704 | -0.24427 | -2.7569 | -5.141 | -6.3439 | -7.3208 | -8.0756 | -8.6127 | -9.0759 | -9.5951 | -10.1111 | -10.6207 | -12.1352 | -13.4251 | -14.9116
|  | MONTROSE NORTH | CT |  |  |  | -0.14332 | -2.5294 | -4.837 | -5.9049 | -6.8793 | -7.7205 | -8.3306 | -8.9502 | -9.5263 | -10.0904 | -10.6841 | -13.0391 | -14.336 | -15.1807 | 0.48751 | -2.2081 | -4.5665 | -5.371 | -6.1455 | -6.8212 | -7.2152 | -7.5434 | -7.7608 | -7.9681 | -8.2313 | -9.8003 | -10.9019 | -12.1028 | 0.47803 | -1.8151 | -4.0255 | -5.0311 | -5.9937 | -6.8244 | -7.3953 | -7.9683 | -8.4998 | -9.018 | -9.5696 | -11.8236 | -13.133 | -14.0404
|  | MONTROSE NORTH | LW |  |  |  | -0.90742 | -3.5298 | -5.9949 | -7.2532 | -8.2595 | -9.0458 | -9.6326 | -10.1406 | -10.7069 | -11.2732 | -11.8289 | -13.4166 | -14.5607 | -15.8183 | -0.13759 | -2.995 | -5.4861 | -6.527 | -7.331 | -7.8346 | -8.0722 | -8.2784 | -8.4994 | -8.7156 | -8.9338 | -9.7792 | -10.8811 | -12.2704 | -0.24427 | -2.7569 | -5.141 | -6.3439 | -7.3208 | -8.0756 | -8.6127 | -9.0759 | -9.5951 | -10.1111 | -10.6207 | -12.1352 | -13.4251 | -14.9116
|  | MONTROSE NORTH | ST |  |  |  | -0.045812 | -2.3337 | -4.3961 | -5.1583 | -5.7548 | -6.3633 | -6.7215 | -7.1053 | -7.3359 | -7.5784 | -7.9095 | -10.1501 | -11.5999 | -13.0447 | 0.50236 | -2.1436 | -4.5859 | -5.4017 | -6.0326 | -6.6894 | -7.0318 | -7.3785 | -7.5134 | -7.6502 | -7.8745 | -9.3266 | -10.5038 | -11.8051 | 0.56708 | -1.6373 | -3.6816 | -4.4435 | -5.0356 | -5.6789 | -6.0286 | -6.4109 | -6.6083 | -6.8116 | -7.1233 | -9.2459 | -10.7543 | -12.2749
|  | MONTROSE NORTH | FS |  |  |  | 1.4666 | -0.30652 | -1.8655 | -2.5756 | -3.0791 | -3.652 | -4.0401 | -4.5459 | -5.2348 | -5.8398 | -6.3812 | -9.0476 | -10.5667 | -11.6313 | 2.2779 | 0.22903 | -1.5784 | -2.3347 | -2.8461 | -3.4553 | -3.8305 | -4.297 | -4.9838 | -5.5605 | -6.0454 | -8.1618 | -9.073 | -10.8378 | 2.0306 | 0.32517 | -1.1824 | -1.8602 | -2.3412 | -2.8956 | -3.2672 | -3.756 | -4.4184 | -4.9978 | -5.5142 | -7.9956 | -9.3697 | -10.3691
| TARLAND | MOSSAT | MINIMUM HEADROOM | NJ 47470 19897 | NO | YES | 0.91453 | 0.77812 | 0.64369 | 0.49995 | 0.33034 | 0.080694 | -0.14056 | -0.27071 | -0.41704 | -0.55963 | -0.69811 | -1.0583 | -1.4411 | -1.7475 | 1.9265 | 1.8759 | 1.8244 | 1.7468 | 1.6136 | 1.4549 | 1.3221 | 1.2228 | 1.1139 | 1.0091 | 0.90606 | 0.52622 | 0.13822 | -0.23205 | 1.5853 | 1.462 | 1.3411 | 1.2114 | 1.0265 | 0.77958 | 0.57337 | 0.44227 | 0.29452 | 0.15131 | 0.012029 | -0.37177 | -0.76917 | -1.1596
|  | MOSSAT | CT |  |  |  | 1.0305 | 0.93692 | 0.75017 | 0.55641 | 0.33034 | 0.080694 | -0.14056 | -0.27071 | -0.41704 | -0.55963 | -0.69811 | -1.0583 | -1.4411 | -1.6738 | 1.949 | 1.9037 | 1.8244 | 1.7468 | 1.6136 | 1.4549 | 1.3221 | 1.2228 | 1.1139 | 1.0091 | 0.90606 | 0.57496 | 0.26839 | -0.014789 | 1.6874 | 1.602 | 1.4304 | 1.2501 | 1.0265 | 0.77958 | 0.57337 | 0.44227 | 0.29452 | 0.15131 | 0.012029 | -0.37177 | -0.75816 | -1.0164
|  | MOSSAT | LW |  |  |  | 0.91453 | 0.77812 | 0.64369 | 0.49995 | 0.36247 | 0.17575 | -0.043695 | -0.17444 | -0.30832 | -0.43997 | -0.56946 | -0.88264 | -1.2408 | -1.6545 | 1.9265 | 1.8759 | 1.8301 | 1.7794 | 1.7282 | 1.6303 | 1.4995 | 1.4102 | 1.32 | 1.2302 | 1.143 | 0.89843 | 0.55413 | 0.090443 | 1.5853 | 1.462 | 1.3411 | 1.2114 | 1.0879 | 0.91694 | 0.71431 | 0.58669 | 0.45547 | 0.32657 | 0.20005 | -0.10817 | -0.51427 | -1.0112
|  | MOSSAT | ST |  |  |  | 1.0962 | 1.0437 | 0.91896 | 0.80953 | 0.70813 | 0.52608 | 0.38144 | 0.21483 | 0.085994 | -0.046815 | -0.20031 | -0.91727 | -1.3894 | -1.7475 | 1.9763 | 1.9577 | 1.8667 | 1.7943 | 1.7334 | 1.5776 | 1.4681 | 1.3362 | 1.251 | 1.1635 | 1.0557 | 0.52622 | 0.13822 | -0.23205 | 1.746 | 1.6989 | 1.5686 | 1.4576 | 1.3578 | 1.1643 | 1.0233 | 0.84993 | 0.72341 | 0.59388 | 0.44139 | -0.27432 | -0.76917 | -1.1596
|  | MOSSAT | FS |  |  |  | 1.1367 | 1.1008 | 1.0314 | 0.95823 | 0.88213 | 0.79682 | 0.68427 | 0.56867 | 0.45606 | 0.3479 | 0.22981 | -0.46633 | -0.91824 | -1.1054 | 1.9869 | 1.9736 | 1.9402 | 1.9048 | 1.8653 | 1.8135 | 1.7391 | 1.6706 | 1.6096 | 1.5473 | 1.4813 | 1.1006 | 0.78477 | 0.57679 | 1.7817 | 1.7495 | 1.6836 | 1.6141 | 1.5413 | 1.4595 | 1.3527 | 1.2401 | 1.1323 | 1.028 | 0.91458 | 0.26935 | -0.1567 | -0.33239
| THURSO | MOUNT PLEASANT | MINIMUM HEADROOM | ND 12706 67832 | YES | YES | 3.8322 | 3.0032 | 2.1165 | 1.0698 | 0.74107 | 0.47955 | 0.26966 | 0.011342 | -0.25616 | -0.43389 | -0.6061 | -1.2264 | -1.9508 | -2.8113 | 4.6299 | 3.9299 | 3.2115 | 2.3244 | 2.1001 | 1.9486 | 1.8468 | 1.6864 | 1.5161 | 1.377 | 1.2361 | 0.62464 | 0.023384 | -0.96365 | 3.7309 | 2.9524 | 2.1228 | 1.1414 | 0.84176 | 0.609 | 0.42606 | 0.19799 | -0.038481 | -0.20316 | -0.36493 | -1.0305 | -1.8075 | -2.8503
|  | MOUNT PLEASANT | CT |  |  |  | 4.0234 | 3.3326 | 2.4771 | 1.3517 | 1.0236 | 0.69196 | 0.43156 | 0.15367 | -0.11212 | -0.29928 | -0.48557 | -1.2264 | -1.9211 | -2.3935 | 4.7414 | 4.1451 | 3.4541 | 2.5112 | 2.2774 | 2.0388 | 1.8792 | 1.6887 | 1.5174 | 1.377 | 1.2361 | 0.62464 | 0.023384 | -0.58283 | 3.9034 | 3.2525 | 2.4527 | 1.3964 | 1.0852 | 0.76995 | 0.53292 | 0.28066 | 0.043377 | -0.13031 | -0.30551 | -1.0305 | -1.7365 | -2.2621
|  | MOUNT PLEASANT | LW |  |  |  | 3.8322 | 3.0032 | 2.1165 | 1.0698 | 0.74107 | 0.47955 | 0.26966 | 0.011342 | -0.25616 | -0.43389 | -0.6061 | -1.1794 | -1.9508 | -2.8113 | 4.6299 | 3.9299 | 3.2115 | 2.3244 | 2.1001 | 1.9486 | 1.8468 | 1.6864 | 1.5161 | 1.3835 | 1.2534 | 0.82718 | 0.052523 | -0.96365 | 3.7309 | 2.9524 | 2.1228 | 1.1414 | 0.84176 | 0.609 | 0.42606 | 0.19799 | -0.038481 | -0.20316 | -0.36493 | -0.93027 | -1.8075 | -2.8503
|  | MOUNT PLEASANT | ST |  |  |  | 4.0714 | 3.4204 | 2.6743 | 1.6781 | 1.5023 | 1.2746 | 1.1278 | 0.88127 | 0.7176 | 0.59488 | 0.45032 | -0.4112 | -1.1831 | -1.9293 | 4.7636 | 4.1918 | 3.5276 | 2.6236 | 2.4738 | 2.2651 | 2.1454 | 1.9294 | 1.8138 | 1.7203 | 1.6015 | 0.87689 | 0.10204 | -0.72102 | 3.9462 | 3.3309 | 2.6143 | 1.664 | 1.4964 | 1.2673 | 1.1285 | 0.88406 | 0.73697 | 0.62013 | 0.47833 | -0.35473 | -1.1884 | -2.0108
|  | MOUNT PLEASANT | FS |  |  |  | 4.2351 | 3.7549 | 3.2017 | 2.4084 | 2.2325 | 2.0098 | 1.8675 | 1.6345 | 1.3168 | 1.1078 | 0.95345 | 0.045583 | -0.51321 | -0.8517 | 4.898 | 4.4738 | 3.993 | 3.296 | 3.15 | 2.9639 | 2.8485 | 2.6651 | 2.4015 | 2.2273 | 2.105 | 1.4293 | 0.91434 | 0.39733 | 4.1003 | 3.6464 | 3.1224 | 2.3705 | 2.2049 | 1.9953 | 1.8626 | 1.6485 | 1.3574 | 1.1601 | 1.0152 | 0.19744 | -0.30159 | -0.6196
| BEAULY | MUIR OF ORD | MINIMUM HEADROOM | NH 53420 48534 | NO | YES | 8.099 | 7.5869 | 6.7653 | 5.8919 | 4.8772 | 3.7242 | 2.5721 | 1.8541 | 1.1134 | 0.37879 | -0.33087 | -2.3567 | -3.4514 | -4.3008 | 10.9815 | 10.7114 | 10.1728 | 9.5818 | 8.764 | 7.8077 | 6.9931 | 6.4736 | 5.9287 | 5.3935 | 4.8772 | 3.4899 | 2.6381 | 1.7462 | 7.3454 | 6.9127 | 6.1631 | 5.3534 | 4.3365 | 3.1546 | 2.0441 | 1.3332 | 0.59329 | -0.13829 | -0.84344 | -2.7863 | -3.9013 | -4.8796
|  | MUIR OF ORD | CT |  |  |  | 8.503 | 8.1615 | 7.4109 | 6.6106 | 5.7534 | 4.8676 | 4.0263 | 3.3924 | 2.6859 | 1.9812 | 1.2964 | -0.4356 | -1.8101 | -2.4834 | 11.1266 | 10.932 | 10.5305 | 10.0813 | 9.4978 | 8.8855 | 8.4396 | 8.027 | 7.538 | 7.0498 | 6.5843 | 5.3333 | 4.4612 | 3.7323 | 7.6463 | 7.3525 | 6.7149 | 6.0206 | 5.2249 | 4.3975 | 3.6967 | 3.0991 | 2.4094 | 1.7212 | 1.0613 | -0.62264 | -1.8666 | -2.5397
|  | MUIR OF ORD | LW |  |  |  | 8.099 | 7.5869 | 6.7653 | 5.8919 | 4.8772 | 3.7242 | 2.5721 | 1.8541 | 1.1134 | 0.37879 | -0.33087 | -2.3567 | -3.4514 | -4.3008 | 10.9815 | 10.7114 | 10.1728 | 9.5818 | 8.764 | 7.8077 | 6.9931 | 6.4736 | 5.9287 | 5.3935 | 4.8772 | 3.4899 | 2.6381 | 1.7462 | 7.3454 | 6.9127 | 6.1631 | 5.3534 | 4.3365 | 3.1546 | 2.0441 | 1.3332 | 0.59329 | -0.13829 | -0.84344 | -2.7863 | -3.9013 | -4.8796
|  | MUIR OF ORD | ST |  |  |  | 8.7196 | 8.5046 | 8.0381 | 7.6125 | 7.27 | 6.6747 | 6.2129 | 5.7111 | 5.2337 | 4.731 | 4.1836 | 1.6383 | 0.35299 | -0.69231 | 11.2231 | 11.1112 | 10.7199 | 10.3902 | 10.1325 | 9.5726 | 9.2402 | 8.8717 | 8.5453 | 8.1972 | 7.8023 | 5.9349 | 4.91 | 3.9671 | 7.8159 | 7.6418 | 7.1713 | 6.7566 | 6.4232 | 5.7805 | 5.3441 | 4.8618 | 4.4132 | 3.9365 | 3.4078 | 0.96258 | -0.2586 | -1.2492
|  | MUIR OF ORD | FS |  |  |  | 8.8516 | 8.6834 | 8.3935 | 8.0951 | 7.8198 | 7.5312 | 7.1739 | 6.7663 | 6.3629 | 5.9426 | 5.506 | 2.9138 | 1.1538 | 0.38307 | 11.2754 | 11.1827 | 11.0055 | 10.8172 | 10.6338 | 10.4378 | 10.205 | 9.9499 | 9.696 | 9.4254 | 9.1377 | 7.4954 | 6.1363 | 5.2909 | 7.9164 | 7.7798 | 7.5284 | 7.2645 | 7.0123 | 6.745 | 6.4251 | 6.0656 | 5.7073 | 5.3297 | 4.9332 | 2.6062 | 0.96757 | 0.28744
| BEAULY | MUIREND | MINIMUM HEADROOM | NH 64508 54337 | YES | YES | 4.0238 | 3.9287 | 3.8036 | 3.6777 | 3.5505 | 3.396 | 3.2394 | 3.1947 | 3.143 | 3.0949 | 3.0445 | 2.8901 | 2.6802 | 2.5714 | 4.7853 | 4.7274 | 4.6645 | 4.5909 | 4.5006 | 4.4054 | 4.3229 | 4.2577 | 4.1736 | 4.0894 | 4.0106 | 3.8032 | 3.6136 | 3.4065 | 4.1866 | 4.0859 | 3.9643 | 3.8382 | 3.7128 | 3.5434 | 3.3912 | 3.3109 | 3.2124 | 3.1132 | 3.0192 | 2.8131 | 2.6151 | 2.5019
|  | MUIREND | CT |  |  |  | 4.1207 | 4.057 | 3.8969 | 3.7344 | 3.5691 | 3.396 | 3.2394 | 3.1947 | 3.143 | 3.0949 | 3.0445 | 2.934 | 2.6802 | 2.5714 | 4.8191 | 4.7763 | 4.6866 | 4.5909 | 4.5006 | 4.4054 | 4.3229 | 4.2577 | 4.1736 | 4.0894 | 4.0106 | 3.8032 | 3.6136 | 3.4234 | 4.2728 | 4.2044 | 4.0427 | 3.8744 | 3.7128 | 3.5434 | 3.3912 | 3.3175 | 3.2234 | 3.1315 | 3.0447 | 2.8539 | 2.6151 | 2.5019
|  | MUIREND | LW |  |  |  | 4.0238 | 3.9287 | 3.8036 | 3.6777 | 3.5505 | 3.4114 | 3.2667 | 3.2127 | 3.1573 | 3.1024 | 3.0476 | 2.8901 | 2.7262 | 2.6095 | 4.7853 | 4.7274 | 4.6645 | 4.597 | 4.5339 | 4.4453 | 4.3465 | 4.2674 | 4.1827 | 4.0968 | 4.0169 | 3.8668 | 3.7644 | 3.6507 | 4.1866 | 4.0859 | 3.9643 | 3.8382 | 3.7153 | 3.5653 | 3.404 | 3.3109 | 3.2124 | 3.1132 | 3.0192 | 2.8131 | 2.6499 | 2.5121
|  | MUIREND | ST |  |  |  | 4.1749 | 4.1372 | 4.0795 | 4.0239 | 3.9661 | 3.8974 | 3.8372 | 3.7547 | 3.6826 | 3.6093 | 3.5255 | 3.1645 | 2.9486 | 2.7837 | 4.8421 | 4.8196 | 4.7803 | 4.7403 | 4.6991 | 4.6411 | 4.5914 | 4.524 | 4.4597 | 4.3902 | 4.3105 | 3.9083 | 3.6968 | 3.4869 | 4.3213 | 4.2836 | 4.2238 | 4.164 | 4.102 | 4.0241 | 3.9544 | 3.8613 | 3.775 | 3.6839 | 3.58 | 3.0824 | 2.8634 | 2.7057
|  | MUIREND | FS |  |  |  | 4.2114 | 4.187 | 4.1364 | 4.0862 | 4.037 | 3.9847 | 3.9294 | 3.8644 | 3.7989 | 3.7319 | 3.6611 | 3.2023 | 2.9279 | 2.7871 | 4.8556 | 4.8376 | 4.8081 | 4.7758 | 4.7426 | 4.7057 | 4.6651 | 4.6159 | 4.5639 | 4.5079 | 4.4469 | 4.0601 | 3.7014 | 3.4065 | 4.351 | 4.3261 | 4.2762 | 4.2245 | 4.1729 | 4.1171 | 4.0568 | 3.9857 | 3.9121 | 3.8354 | 3.753 | 3.2294 | 2.8849 | 2.7625
| NAIRN | NAIRN CENTRAL | MINIMUM HEADROOM | NH 88496 56295 | NO | YES | 3.836 | 3.1643 | 2.4508 | 1.7122 | 0.91479 | -0.033692 | -0.99245 | -1.7129 | -2.4611 | -3.2196 | -3.9208 | -6.0926 | -7.6869 | -8.6529 | 6.2129 | 5.794 | 5.4102 | 5.0064 | 4.5173 | 3.9126 | 3.3451 | 2.9207 | 2.4721 | 2.0158 | 1.5924 | 0.43119 | -0.47323 | -1.4517 | 6.2212 | 5.6362 | 4.9778 | 4.2881 | 3.5231 | 2.5959 | 1.678 | 0.9773 | 0.24455 | -0.49935 | -1.1896 | -3.1954 | -4.378 | -5.2143
|  | NAIRN CENTRAL | CT |  |  |  | 4.2335 | 3.7444 | 3.1404 | 2.5068 | 1.8456 | 1.1168 | 0.40347 | -0.36272 | -1.1964 | -2.0258 | -2.8135 | -5.6851 | -7.6869 | -8.6529 | 6.3578 | 6.0217 | 5.6957 | 5.3428 | 4.9364 | 4.4908 | 4.1074 | 3.6908 | 3.2176 | 2.7434 | 2.289 | 0.6897 | -0.47323 | -1.4517 | 6.3756 | 6.0603 | 5.5662 | 4.9678 | 4.3366 | 3.6468 | 3.002 | 2.2913 | 1.4983 | 0.707 | -0.041972 | -2.6564 | -4.378 | -5.2143
|  | NAIRN CENTRAL | LW |  |  |  | 3.836 | 3.1643 | 2.4508 | 1.7122 | 0.91479 | -0.033692 | -0.99245 | -1.7129 | -2.4611 | -3.2196 | -3.9208 | -6.0926 | -7.3747 | -7.8566 | 6.2129 | 5.794 | 5.4102 | 5.0064 | 4.5173 | 3.9126 | 3.3451 | 2.9207 | 2.4721 | 2.0158 | 1.5924 | 0.43119 | -0.18629 | -0.49728 | 6.2212 | 5.6362 | 4.9778 | 4.2881 | 3.5231 | 2.5959 | 1.678 | 0.9773 | 0.24455 | -0.49935 | -1.1896 | -3.1954 | -4.3203 | -4.7838
|  | NAIRN CENTRAL | ST |  |  |  | 4.4139 | 4.047 | 3.8734 | 3.6923 | 3.519 | 3.2001 | 2.9245 | 2.6782 | 2.4047 | 2.1038 | 1.7793 | -0.47259 | -2.0519 | -3.8632 | 6.453 | 6.1981 | 6.02 | 5.8541 | 5.7014 | 5.3969 | 5.1764 | 4.9765 | 4.7582 | 4.5149 | 4.247 | 2.5884 | 1.499 | 0.21059 | 6.4769 | 6.2489 | 6.0805 | 5.9311 | 5.7894 | 5.4845 | 5.2061 | 4.9486 | 4.6619 | 4.3438 | 3.9953 | 1.7116 | 0.29476 | -1.2435
|  | NAIRN CENTRAL | FS |  |  |  | 4.4653 | 4.1681 | 4.0344 | 3.8856 | 3.724 | 3.542 | 3.3383 | 3.0839 | 2.8145 | 2.5245 | 2.2319 | 0.178 | -2.0406 | -3.8355 | 6.4791 | 6.2692 | 6.1713 | 6.0592 | 5.9353 | 5.7967 | 5.6428 | 5.4662 | 5.2748 | 5.0641 | 4.8431 | 3.3295 | 1.4518 | -0.57747 | 6.5022 | 6.3145 | 6.2451 | 6.1652 | 6.0718 | 5.904 | 5.7045 | 5.4607 | 5.2001 | 4.9176 | 4.6261 | 2.6109 | 0.49191 | -1.0559
| STRICHEN | NEW PITSLIGO | MINIMUM HEADROOM | NJ 88529 54853 | NO | YES | 7.4719 | 7.4404 | 7.3415 | 7.2344 | 7.1091 | 6.9518 | 6.8215 | 6.7232 | 6.6169 | 6.5141 | 6.4112 | 6.1501 | 5.9025 | 5.7433 | 6.9816 | 6.9343 | 6.887 | 6.825 | 6.7274 | 6.6263 | 6.5562 | 6.4878 | 6.4121 | 6.3388 | 6.2654 | 6.0451 | 5.8262 | 5.6078 | 6.6508 | 6.5648 | 6.4752 | 6.3791 | 6.2513 | 6.098 | 5.9774 | 5.8851 | 5.7869 | 5.6913 | 5.5897 | 5.3222 | 5.0797 | 4.907
|  | NEW PITSLIGO | CT |  |  |  | 7.4719 | 7.4467 | 7.4067 | 7.2637 | 7.1091 | 6.9518 | 6.8215 | 6.7232 | 6.6169 | 6.5141 | 6.4112 | 6.1501 | 5.9025 | 5.7529 | 7.0107 | 6.9726 | 6.9018 | 6.825 | 6.7274 | 6.6263 | 6.5562 | 6.4878 | 6.4121 | 6.3388 | 6.2654 | 6.0451 | 5.858 | 5.6863 | 6.72 | 6.6556 | 6.5323 | 6.4017 | 6.2513 | 6.098 | 5.9774 | 5.8851 | 5.7869 | 5.6913 | 5.5897 | 5.3222 | 5.0797 | 4.9211
|  | NEW PITSLIGO | LW |  |  |  | 7.4725 | 7.4404 | 7.3415 | 7.2344 | 7.1315 | 7.004 | 6.8643 | 6.7625 | 6.658 | 6.5493 | 6.4466 | 6.2069 | 5.9823 | 5.7433 | 6.9816 | 6.9343 | 6.887 | 6.8351 | 6.786 | 6.7195 | 6.6453 | 6.5778 | 6.5072 | 6.4349 | 6.3664 | 6.2062 | 6.0007 | 5.7411 | 6.6508 | 6.5648 | 6.4752 | 6.3791 | 6.2867 | 6.1726 | 6.0476 | 5.9558 | 5.8611 | 5.758 | 5.6589 | 5.4291 | 5.1855 | 4.907
|  | NEW PITSLIGO | ST |  |  |  | 7.4811 | 7.4732 | 7.4349 | 7.4027 | 7.3745 | 7.3084 | 7.2319 | 7.1273 | 7.0346 | 6.9404 | 6.8344 | 6.3189 | 6.0227 | 5.8179 | 7.0332 | 7.0152 | 6.9571 | 6.9061 | 6.8628 | 6.7775 | 6.7271 | 6.6459 | 6.5846 | 6.5219 | 6.4474 | 6.0775 | 5.8262 | 5.6078 | 6.7661 | 6.7331 | 6.6557 | 6.5838 | 6.5213 | 6.4149 | 6.3428 | 6.2382 | 6.1513 | 6.064 | 5.9638 | 5.4573 | 5.1547 | 4.9366
|  | NEW PITSLIGO | FS |  |  |  | 7.4834 | 7.4773 | 7.4635 | 7.4479 | 7.43 | 7.4101 | 7.3895 | 7.3256 | 7.2522 | 7.1766 | 7.0958 | 6.6058 | 6.278 | 6.1424 | 7.0441 | 7.0287 | 7.0022 | 6.9726 | 6.9422 | 6.909 | 6.8749 | 6.8259 | 6.7797 | 6.7311 | 6.6789 | 6.3865 | 6.138 | 5.9578 | 6.7906 | 6.7625 | 6.7197 | 6.6727 | 6.6264 | 6.5763 | 6.5247 | 6.4531 | 6.3847 | 6.3147 | 6.2399 | 5.7923 | 5.4832 | 5.3579
| DUNOON | NEWTON | MINIMUM HEADROOM | NS 04939 98621 | YES | YES | 0.21638 | 0.20761 | 0.2031 | 0.19787 | 0.18947 | 0.18118 | 0.17474 | 0.16724 | 0.15526 | 0.1474 | 0.13904 | 0.127 | 0.12445 | 0.12162 | 0.23999 | 0.23536 | 0.23254 | 0.22781 | 0.22347 | 0.21917 | 0.21337 | 0.20674 | 0.19848 | 0.19165 | 0.18509 | 0.17613 | 0.17473 | 0.17262 | 0.22227 | 0.21421 | 0.20994 | 0.2045 | 0.1968 | 0.18913 | 0.18195 | 0.17396 | 0.16234 | 0.15475 | 0.14683 | 0.13497 | 0.1321 | 0.1295
|  | NEWTON | CT |  |  |  | 0.21874 | 0.2127 | 0.20468 | 0.19787 | 0.18947 | 0.18278 | 0.17802 | 0.16724 | 0.16221 | 0.15464 | 0.14673 | 0.12908 | 0.12654 | 0.12162 | 0.24108 | 0.23768 | 0.23284 | 0.22781 | 0.22347 | 0.21957 | 0.21621 | 0.20964 | 0.20348 | 0.1968 | 0.19059 | 0.17763 | 0.17548 | 0.17262 | 0.22455 | 0.2188 | 0.21126 | 0.2045 | 0.1968 | 0.19045 | 0.18562 | 0.17523 | 0.1691 | 0.16191 | 0.15426 | 0.13707 | 0.13436 | 0.1295
|  | NEWTON | LW |  |  |  | 0.21638 | 0.20761 | 0.2031 | 0.19813 | 0.19006 | 0.18118 | 0.17474 | 0.16729 | 0.15526 | 0.1474 | 0.13904 | 0.127 | 0.12445 | 0.12274 | 0.23999 | 0.23536 | 0.23254 | 0.22912 | 0.2251 | 0.21917 | 0.21337 | 0.20674 | 0.19848 | 0.19165 | 0.18509 | 0.17613 | 0.17473 | 0.17417 | 0.22227 | 0.21421 | 0.20994 | 0.20521 | 0.19784 | 0.18913 | 0.18195 | 0.17396 | 0.16234 | 0.15475 | 0.14683 | 0.13497 | 0.1321 | 0.1306
|  | NEWTON | ST |  |  |  | 0.22095 | 0.21973 | 0.21829 | 0.21478 | 0.21001 | 0.20729 | 0.20382 | 0.19966 | 0.19319 | 0.18735 | 0.17808 | 0.14272 | 0.13558 | 0.13117 | 0.24238 | 0.24153 | 0.24054 | 0.23835 | 0.23559 | 0.23344 | 0.23071 | 0.22744 | 0.22286 | 0.21823 | 0.21196 | 0.18461 | 0.17933 | 0.17708 | 0.22681 | 0.22561 | 0.22419 | 0.22068 | 0.21611 | 0.21346 | 0.20998 | 0.20594 | 0.19965 | 0.19393 | 0.18492 | 0.15021 | 0.1429 | 0.13851
|  | NEWTON | FS |  |  |  | 0.22114 | 0.22148 | 0.21897 | 0.21606 | 0.21292 | 0.20765 | 0.20713 | 0.2043 | 0.19965 | 0.19592 | 0.19038 | 0.15662 | 0.13266 | 0.12887 | 0.24251 | 0.24247 | 0.241 | 0.23927 | 0.23737 | 0.23467 | 0.23335 | 0.23112 | 0.22794 | 0.225 | 0.22115 | 0.19713 | 0.17855 | 0.17603 | 0.22701 | 0.2272 | 0.22486 | 0.22204 | 0.21888 | 0.21407 | 0.21314 | 0.2104 | 0.20583 | 0.20221 | 0.19683 | 0.16376 | 0.14049 | 0.13651
| REDMOSS | NEWTONHILL | MINIMUM HEADROOM | NO 90190 93653 | NO | YES | 2.8262 | 2.4295 | 1.4215 | 0.32506 | -1.1648 | -3.5768 | -5.2777 | -6.7627 | -7.9259 | -8.9504 | -9.9581 | -12.801 | -13.9244 | -14.6167 | 5.9748 | 5.8392 | 5.2343 | 4.5593 | 3.3686 | 1.1949 | -0.14721 | -1.2834 | -2.1321 | -2.8396 | -3.5424 | -5.5492 | -6.2263 | -6.752 | 4.3499 | 4.2448 | 3.2113 | 2.0813 | 0.45704 | -2.0502 | -3.7891 | -5.2198 | -6.3504 | -7.3422 | -8.3206 | -11.1219 | -12.1698 | -12.8558
|  | NEWTONHILL | CT |  |  |  | 3.1942 | 2.9498 | 2.2506 | 1.4728 | 0.47192 | -1.2362 | -2.2273 | -3.5932 | -4.7748 | -5.7809 | -6.7605 | -9.8487 | -11.4885 | -12.3477 | 6.0099 | 5.8772 | 5.6061 | 5.3063 | 4.6253 | 3.0965 | 2.4955 | 1.651 | 0.83291 | 0.17688 | -0.4666 | -2.5355 | -3.761 | -4.9908 | 4.3511 | 4.2454 | 4.0368 | 3.3047 | 2.2586 | 0.54582 | -0.40236 | -1.689 | -2.8069 | -3.7556 | -4.6804 | -7.5806 | -9.0577 | -9.8348
|  | NEWTONHILL | LW |  |  |  | 2.8262 | 2.4295 | 1.4215 | 0.32506 | -1.1648 | -3.5768 | -5.2777 | -6.7627 | -7.9259 | -8.9504 | -9.9581 | -12.801 | -13.9244 | -14.6167 | 5.9748 | 5.8392 | 5.2343 | 4.5593 | 3.3686 | 1.1949 | -0.14721 | -1.2834 | -2.1321 | -2.8396 | -3.5424 | -5.5492 | -6.2263 | -6.752 | 4.3499 | 4.2448 | 3.2113 | 2.0813 | 0.45704 | -2.0502 | -3.7891 | -5.2198 | -6.3504 | -7.3422 | -8.3206 | -11.1219 | -12.1698 | -12.8558
|  | NEWTONHILL | ST |  |  |  | 3.3347 | 3.2254 | 2.7157 | 2.2915 | 1.9299 | 0.47984 | -0.19313 | -1.105 | -1.718 | -2.1878 | -2.7105 | -5.6336 | -7.2858 | -8.8647 | 6.0739 | 6.0299 | 5.5149 | 5.133 | 4.8418 | 3.2315 | 2.6431 | 1.8228 | 1.3523 | 1.0554 | 0.71082 | -1.2544 | -2.6186 | -4.1154 | 4.3882 | 4.3507 | 3.8451 | 3.4729 | 3.1947 | 1.6495 | 1.0901 | 0.3117 | -0.18713 | -0.64714 | -1.1784 | -4.2028 | -5.6987 | -7.0216
|  | NEWTONHILL | FS |  |  |  | 3.3747 | 3.294 | 3.088 | 2.8617 | 2.606 | 1.9506 | 1.4626 | 0.7403 | 0.25021 | -0.17932 | -0.62653 | -3.2873 | -5.9019 | -7.4822 | 6.0874 | 6.0533 | 5.9127 | 5.7631 | 5.5894 | 4.9403 | 4.5375 | 3.9583 | 3.632 | 3.3905 | 3.1405 | 1.2468 | -1.26 | -3.6645 | 4.3968 | 4.3666 | 4.2346 | 4.0926 | 3.9291 | 3.3192 | 2.9371 | 2.3953 | 2.0485 | 1.6378 | 1.2088 | -1.3587 | -3.8722 | -5.2171
| ALNESS | NIGG | MINIMUM HEADROOM | NH 79490 69773 | YES | YES | -2.4035 | -2.4505 | -2.5325 | -2.7549 | -2.7551 | -2.7554 | -2.7558 | -2.782 | -2.8092 | -2.8317 | -2.8569 | -2.9879 | -3.3493 | -3.8631 | -2.5057 | -2.5548 | -2.6405 | -2.8728 | -2.8731 | -2.8735 | -2.8741 | -2.9069 | -2.941 | -2.9692 | -3.0008 | -3.1649 | -3.6166 | -4.2588 | -3.1969 | -3.2444 | -3.3274 | -3.5524 | -3.5526 | -3.5529 | -3.5533 | -3.5859 | -3.6197 | -3.6477 | -3.679 | -3.8426 | -4.2943 | -4.9365
|  | NIGG | CT |  |  |  | -2.2866 | -2.4038 | -2.4976 | -2.5913 | -2.65 | -2.6501 | -2.6504 | -2.6704 | -2.6905 | -2.7079 | -2.7446 | -2.9334 | -3.1036 | -3.3075 | -2.3836 | -2.506 | -2.6041 | -2.702 | -2.7633 | -2.7636 | -2.7639 | -2.7891 | -2.8142 | -2.836 | -2.8784 | -3.0965 | -3.3093 | -3.5642 | -3.0786 | -3.1971 | -3.292 | -3.3869 | -3.4462 | -3.4464 | -3.4466 | -3.4716 | -3.4966 | -3.5182 | -3.5599 | -3.7747 | -3.9875 | -4.2423
|  | NIGG | LW |  |  |  | -2.4035 | -2.4505 | -2.5325 | -2.7549 | -2.7551 | -2.7554 | -2.7558 | -2.782 | -2.8092 | -2.8317 | -2.8569 | -2.9879 | -3.3493 | -3.8631 | -2.5057 | -2.5548 | -2.6405 | -2.8728 | -2.8731 | -2.8735 | -2.8741 | -2.9069 | -2.941 | -2.9692 | -3.0008 | -3.1649 | -3.6166 | -4.2588 | -3.1969 | -3.2444 | -3.3274 | -3.5524 | -3.5526 | -3.5529 | -3.5533 | -3.5859 | -3.6197 | -3.6477 | -3.679 | -3.8426 | -4.2943 | -4.9365
|  | NIGG | ST |  |  |  | -2.2865 | -2.4035 | -2.4972 | -2.5908 | -2.6494 | -2.6496 | -2.6498 | -2.6935 | -2.7092 | -2.7226 | -2.7614 | -2.949 | -3.2125 | -3.5073 | -2.3835 | -2.5057 | -2.6035 | -2.7013 | -2.7626 | -2.7628 | -2.7631 | -2.8178 | -2.8375 | -2.8543 | -2.8993 | -3.1161 | -3.4457 | -3.8141 | -3.0785 | -3.1969 | -3.2916 | -3.3864 | -3.4457 | -3.4459 | -3.446 | -3.5006 | -3.5202 | -3.5368 | -3.581 | -3.7939 | -4.1232 | -4.4916
|  | NIGG | FS |  |  |  | -1.8187 | -1.9357 | -2.0235 | -2.082 | -2.1406 | -2.1992 | -2.2577 | -2.3321 | -2.4014 | -2.4708 | -2.5693 | -2.8176 | -2.8333 | -2.867 | -1.895 | -2.0172 | -2.1089 | -2.17 | -2.2312 | -2.2924 | -2.3536 | -2.4346 | -2.5092 | -2.5839 | -2.6891 | -2.9516 | -2.9714 | -3.0137 | -2.605 | -2.7234 | -2.8123 | -2.8715 | -2.9308 | -2.99 | -3.0493 | -3.1283 | -3.201 | -3.2737 | -3.376 | -3.6302 | -3.6494 | -3.6912
| CHARLESTON | NINEWELLS | MINIMUM HEADROOM | NO 35148 30641 | NO | YES | 8.4389 | 8.017 | 7.4391 | 6.5093 | 5.8076 | 5.327 | 4.8766 | 4.5618 | 4.0836 | 3.7442 | 3.4244 | 2.5886 | 2.0181 | 1.3671 | 9.2075 | 8.8096 | 8.2691 | 7.1671 | 6.4117 | 6.1401 | 5.9297 | 5.7463 | 5.4145 | 5.245 | 5.0258 | 4.2857 | 3.6285 | 3.1342 | 9.14 | 8.6683 | 8.0371 | 6.9527 | 6.1346 | 5.6904 | 5.2921 | 5.0301 | 4.6094 | 4.3314 | 4.0507 | 3.238 | 2.604 | 1.8332
|  | NINEWELLS | CT |  |  |  | 8.5842 | 8.2508 | 7.6966 | 6.7433 | 6.0795 | 5.6551 | 5.283 | 4.9606 | 4.4866 | 4.1643 | 3.8316 | 2.7692 | 2.156 | 1.7103 | 9.2193 | 8.8533 | 8.3333 | 7.2396 | 6.5057 | 6.2192 | 5.9862 | 5.7463 | 5.4145 | 5.245 | 5.0258 | 4.3008 | 3.9594 | 3.6531 | 9.2761 | 8.8965 | 8.3036 | 7.2043 | 6.4314 | 6.0178 | 5.6613 | 5.3649 | 4.9403 | 4.6694 | 4.3809 | 3.3933 | 2.7593 | 2.2792
|  | NINEWELLS | LW |  |  |  | 8.4389 | 8.017 | 7.4391 | 6.5093 | 5.8076 | 5.327 | 4.8766 | 4.5618 | 4.0836 | 3.7442 | 3.4244 | 2.5886 | 2.0181 | 1.3671 | 9.2075 | 8.8096 | 8.2691 | 7.1671 | 6.4117 | 6.1401 | 5.9297 | 5.8219 | 5.4876 | 5.2969 | 5.1196 | 4.6464 | 4.1516 | 3.4885 | 9.14 | 8.6683 | 8.0371 | 6.9527 | 6.1346 | 5.6904 | 5.2921 | 5.0301 | 4.6094 | 4.3314 | 4.0507 | 3.238 | 2.604 | 1.8332
|  | NINEWELLS | ST |  |  |  | 8.6496 | 8.3711 | 8.0091 | 7.2523 | 6.7422 | 6.4641 | 6.2342 | 6.0549 | 5.7524 | 5.589 | 5.3973 | 4.219 | 3.4098 | 2.777 | 9.2579 | 8.9334 | 8.4513 | 7.351 | 6.6327 | 6.3589 | 6.1424 | 5.9857 | 5.7237 | 5.5949 | 5.411 | 4.2857 | 3.6285 | 3.1342 | 9.3365 | 9.0097 | 8.5886 | 7.6603 | 7.0334 | 6.7609 | 6.5439 | 6.3721 | 6.0941 | 5.9605 | 5.7991 | 4.7636 | 4.0117 | 3.2476
|  | NINEWELLS | FS |  |  |  | 8.743 | 8.5327 | 8.238 | 7.644 | 7.222 | 6.9536 | 6.7198 | 6.5304 | 6.2035 | 5.9958 | 5.8244 | 4.7929 | 3.8125 | 3.1588 | 9.3638 | 9.1197 | 8.7514 | 7.9245 | 7.348 | 7.0531 | 6.8113 | 6.6373 | 6.2971 | 6.1128 | 5.9962 | 5.1422 | 4.3203 | 3.8204 | 9.4376 | 9.1932 | 8.8609 | 8.1489 | 7.6346 | 7.3486 | 7.1111 | 6.9173 | 6.5762 | 6.3694 | 6.215 | 5.3017 | 4.3834 | 3.8408
| THURSO | NORTH HOY | MINIMUM HEADROOM | HY 25681 02549 | YES | YES | 0.1789 | 0.17333 | 0.16956 | 0.16411 | 0.15626 | 0.14982 | 0.14532 | 0.14176 | 0.1365 | 0.12722 | 0.11797 | 0.098583 | 0.094778 | 0.093552 | 0.18038 | 0.17753 | 0.17315 | 0.16902 | 0.1654 | 0.16153 | 0.15761 | 0.15389 | 0.15036 | 0.14335 | 0.13672 | 0.12055 | 0.11755 | 0.11543 | 0.16981 | 0.16539 | 0.15877 | 0.15329 | 0.14667 | 0.14032 | 0.1349 | 0.13075 | 0.12577 | 0.11681 | 0.108 | 0.089247 | 0.085625 | 0.084532
|  | NORTH HOY | CT |  |  |  | 0.1794 | 0.17691 | 0.16956 | 0.16411 | 0.15626 | 0.14982 | 0.14532 | 0.14176 | 0.1365 | 0.13297 | 0.12807 | 0.11433 | 0.11026 | 0.10819 | 0.18061 | 0.17769 | 0.17315 | 0.16902 | 0.1654 | 0.16153 | 0.15761 | 0.15389 | 0.15036 | 0.14714 | 0.14294 | 0.13192 | 0.13018 | 0.12895 | 0.16989 | 0.16539 | 0.15877 | 0.15329 | 0.14667 | 0.14032 | 0.1349 | 0.13075 | 0.12577 | 0.12231 | 0.11754 | 0.10426 | 0.10059 | 0.098687
|  | NORTH HOY | LW |  |  |  | 0.1789 | 0.17333 | 0.17137 | 0.1657 | 0.16204 | 0.1548 | 0.14766 | 0.14406 | 0.13735 | 0.12722 | 0.11797 | 0.098583 | 0.094778 | 0.093552 | 0.18038 | 0.17753 | 0.17612 | 0.1732 | 0.1711 | 0.16687 | 0.16172 | 0.15631 | 0.1504 | 0.14335 | 0.13672 | 0.12055 | 0.11755 | 0.11723 | 0.16981 | 0.16564 | 0.16284 | 0.15807 | 0.15409 | 0.14673 | 0.13922 | 0.133 | 0.12643 | 0.11681 | 0.108 | 0.089247 | 0.085625 | 0.084554
|  | NORTH HOY | ST |  |  |  | 0.18178 | 0.1823 | 0.17822 | 0.17868 | 0.1756 | 0.17561 | 0.17283 | 0.16722 | 0.16238 | 0.15616 | 0.1496 | 0.11427 | 0.10297 | 0.10117 | 0.18171 | 0.18169 | 0.17979 | 0.17944 | 0.17778 | 0.1758 | 0.17335 | 0.16989 | 0.16611 | 0.1615 | 0.15635 | 0.12872 | 0.1202 | 0.11942 | 0.17099 | 0.17034 | 0.16884 | 0.16747 | 0.16493 | 0.16266 | 0.15962 | 0.15455 | 0.14989 | 0.14402 | 0.13768 | 0.10338 | 0.092563 | 0.090976
|  | NORTH HOY | FS |  |  |  | 0.18195 | 0.18119 | 0.17875 | 0.17952 | 0.17684 | 0.17553 | 0.17251 | 0.17075 | 0.1706 | 0.16685 | 0.16195 | 0.13658 | 0.1112 | 0.093876 | 0.18184 | 0.18135 | 0.1802 | 0.18015 | 0.17879 | 0.17787 | 0.17624 | 0.17473 | 0.17281 | 0.17028 | 0.16721 | 0.14825 | 0.12829 | 0.11543 | 0.17119 | 0.17081 | 0.16978 | 0.16893 | 0.16712 | 0.16524 | 0.16288 | 0.1603 | 0.15812 | 0.15452 | 0.14978 | 0.12549 | 0.10106 | 0.084532
| BEAULY | NORTH KESSOCK | MINIMUM HEADROOM | NH 65004 48461 | YES | YES | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36
|  | NORTH KESSOCK | CT |  |  |  | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36
|  | NORTH KESSOCK | LW |  |  |  | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36
|  | NORTH KESSOCK | ST |  |  |  | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36
|  | NORTH KESSOCK | FS |  |  |  | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36
| BROADFORD | NOSTIE BRIDGE | MINIMUM HEADROOM | NG 85209 27252 | YES | YES | -1.3025 | -1.4628 | -1.66 | -1.7537 | -1.8569 | -1.9742 | -2.0799 | -2.1579 | -2.2197 | -2.2889 | -2.3489 | -2.4947 | -2.5871 | -2.6371 | -0.69862 | -0.85109 | -1.0598 | -1.1068 | -1.1701 | -1.2332 | -1.2838 | -1.3373 | -1.3747 | -1.4155 | -1.4517 | -1.5337 | -1.6004 | -1.644 | -1.137 | -1.3014 | -1.49 | -1.5381 | -1.6024 | -1.6705 | -1.7308 | -1.7969 | -1.859 | -1.9439 | -2.018 | -2.1617 | -2.236 | -2.2777
|  | NOSTIE BRIDGE | CT |  |  |  | -1.2677 | -1.3971 | -1.5912 | -1.714 | -1.8344 | -1.9469 | -2.0652 | -2.135 | -2.1915 | -2.2564 | -2.3091 | -2.4554 | -2.5871 | -2.6371 | -0.69685 | -0.80768 | -1.0067 | -1.0754 | -1.1394 | -1.1984 | -1.2602 | -1.3141 | -1.3491 | -1.3874 | -1.4217 | -1.5225 | -1.6004 | -1.644 | -1.1353 | -1.28 | -1.4492 | -1.5129 | -1.5776 | -1.6391 | -1.7054 | -1.7688 | -1.8151 | -1.8979 | -1.9663 | -2.1245 | -2.236 | -2.2777
|  | NOSTIE BRIDGE | LW |  |  |  | -1.3025 | -1.4628 | -1.66 | -1.7537 | -1.8569 | -1.9742 | -2.0799 | -2.1579 | -2.2197 | -2.2889 | -2.3489 | -2.4947 | -2.5693 | -2.5916 | -0.69862 | -0.85109 | -1.0598 | -1.1068 | -1.1701 | -1.2332 | -1.2838 | -1.3373 | -1.3747 | -1.4155 | -1.4517 | -1.5337 | -1.5687 | -1.578 | -1.137 | -1.3014 | -1.49 | -1.5381 | -1.6024 | -1.6705 | -1.7308 | -1.7969 | -1.859 | -1.9439 | -2.018 | -2.1617 | -2.2228 | -2.2401
|  | NOSTIE BRIDGE | ST |  |  |  | -1.2161 | -1.3235 | -1.4455 | -1.4872 | -1.5308 | -1.5781 | -1.6317 | -1.6995 | -1.7591 | -1.8295 | -1.906 | -2.2925 | -2.4067 | -2.4602 | -0.69316 | -0.76936 | -0.92749 | -0.9567 | -0.99268 | -1.0284 | -1.0675 | -1.12 | -1.1526 | -1.1904 | -1.2302 | -1.44 | -1.5205 | -1.5703 | -1.0607 | -1.1894 | -1.3297 | -1.3618 | -1.3987 | -1.4387 | -1.4833 | -1.5414 | -1.5849 | -1.6355 | -1.6906 | -1.994 | -2.105 | -2.134
|  | NOSTIE BRIDGE | FS |  |  |  | -1.2063 | -1.2893 | -1.3816 | -1.424 | -1.4591 | -1.5061 | -1.5426 | -1.5949 | -1.6578 | -1.72 | -1.7731 | -2.1573 | -2.4358 | -2.5173 | -0.69263 | -0.74041 | -0.84166 | -0.88134 | -0.90973 | -0.95068 | -0.97337 | -1.0148 | -1.0673 | -1.1134 | -1.1451 | -1.3629 | -1.5271 | -1.6139 | -1.057 | -1.1547 | -1.2589 | -1.2949 | -1.3198 | -1.3597 | -1.3854 | -1.4283 | -1.4819 | -1.5305 | -1.5684 | -1.829 | -2.1061 | -2.179
| TAYNUILT | OBAN | MINIMUM HEADROOM | NM 85643 29338 | NO | YES | 8.2205 | 7.5779 | 6.6966 | 5.7354 | 4.6554 | 3.3128 | 1.9481 | 0.90745 | -0.25253 | -1.5154 | -2.9426 | -9.5885 | -12.8474 | -14.2056 | 12.175 | 11.729 | 11.1858 | 10.5759 | 9.8751 | 8.9444 | 7.99 | 7.1468 | 6.1535 | 5.0702 | 3.967 | -1.7716 | -4.3483 | -5.3338 | 9.6802 | 9.6444 | 9.0566 | 8.171 | 7.1203 | 5.8145 | 4.3968 | 3.0899 | 1.5351 | -0.27941 | -2.3087 | -9.5521 | -12.6559 | -13.9037
|  | OBAN | CT |  |  |  | 8.312 | 7.8254 | 6.9789 | 5.9382 | 4.8046 | 3.6042 | 2.3765 | 1.417 | 0.36458 | -0.6754 | -1.8797 | -9.3272 | -12.358 | -12.5067 | 12.2831 | 11.8686 | 11.2647 | 10.6123 | 9.9052 | 9.1501 | 8.3732 | 7.6137 | 6.7709 | 5.9119 | 4.679 | -1.4377 | -3.732 | -3.8407 | 9.6802 | 9.6444 | 9.1108 | 8.2116 | 7.1203 | 5.9363 | 4.6106 | 3.3086 | 1.896 | 0.43096 | -1.5008 | -9.2052 | -12.1246 | -12.2594
|  | OBAN | LW |  |  |  | 8.2205 | 7.5779 | 6.6966 | 5.7354 | 4.6554 | 3.3128 | 1.9481 | 0.90745 | -0.25253 | -1.5154 | -2.9426 | -9.5885 | -12.6952 | -12.7923 | 12.175 | 11.729 | 11.1858 | 10.5759 | 9.8751 | 8.9444 | 7.99 | 7.1468 | 6.1535 | 5.0702 | 3.967 | -1.7716 | -4.1218 | -4.1894 | 9.7127 | 9.6882 | 9.0566 | 8.171 | 7.1504 | 5.8145 | 4.3968 | 3.0899 | 1.5351 | -0.27941 | -2.3087 | -9.5521 | -12.5502 | -12.644
|  | OBAN | ST |  |  |  | 8.6591 | 8.5211 | 8.2898 | 8.0143 | 7.6808 | 7.213 | 6.7161 | 6.0974 | 5.3168 | 3.6901 | 1.7671 | -9.1789 | -12.8474 | -13.0092 | 12.577 | 12.4321 | 12.1789 | 11.8955 | 11.5756 | 11.121 | 10.6756 | 10.1498 | 9.5001 | 8.3467 | 6.8685 | -1.5372 | -4.3483 | -4.4578 | 9.7691 | 9.781 | 9.7268 | 9.6891 | 9.1748 | 8.3518 | 7.4324 | 6.3297 | 4.9591 | 3.3217 | 1.463 | -9.1158 | -12.6559 | -12.8007
|  | OBAN | FS |  |  |  | 8.725 | 8.6369 | 8.5079 | 8.3555 | 8.1681 | 7.953 | 7.6756 | 7.3296 | 6.9295 | 6.4731 | 5.958 | 0.3141 | -8.0922 | -14.2056 | 12.6196 | 12.5069 | 12.3257 | 12.1197 | 11.8839 | 11.6208 | 11.335 | 11.0289 | 10.6723 | 10.2626 | 9.7984 | 5.8891 | -0.5881 | -5.3338 | 9.7586 | 9.7673 | 9.7679 | 9.7668 | 9.7603 | 9.6832 | 9.2189 | 8.708 | 8.0906 | 7.3612 | 6.528 | 0.12335 | -8.0003 | -13.9037
| MILTON OF CRAIGIE | OLD CRAIGIE ROAD | MINIMUM HEADROOM | NO 42156 32130 | NO | YES | 7.2239 | 6.991 | 6.4367 | 5.8935 | 5.2352 | 4.4605 | 3.7571 | 3.2487 | 2.7079 | 2.1666 | 1.6468 | 0.26326 | -0.5223 | -1.3323 | 7.8651 | 7.7239 | 7.3788 | 7.0236 | 6.5242 | 5.9277 | 5.4307 | 5.0611 | 4.664 | 4.2691 | 3.8912 | 2.9277 | 2.1806 | 1.203 | 7.4817 | 7.2647 | 6.7677 | 6.2638 | 5.6197 | 4.8434 | 4.1592 | 3.6523 | 3.1106 | 2.5692 | 2.0512 | 0.72763 | -0.12332 | -1.1304
|  | OLD CRAIGIE ROAD | CT |  |  |  | 7.4376 | 7.2962 | 6.8589 | 6.3985 | 5.8619 | 5.3028 | 4.8673 | 4.4053 | 3.8747 | 3.3486 | 2.8296 | 1.1346 | 0.23532 | -0.37195 | 7.9496 | 7.8527 | 7.5898 | 7.3116 | 6.9197 | 6.5051 | 6.2412 | 5.932 | 5.5649 | 5.1987 | 4.8376 | 3.6158 | 2.7299 | 1.6775 | 7.6554 | 7.5228 | 7.1156 | 6.6945 | 6.1804 | 5.6413 | 5.2558 | 4.8265 | 4.3221 | 3.8214 | 3.3313 | 1.7919 | 0.95423 | 0.32978
|  | OLD CRAIGIE ROAD | LW |  |  |  | 7.2239 | 6.991 | 6.4367 | 5.8935 | 5.2352 | 4.4605 | 3.7571 | 3.2487 | 2.7079 | 2.1666 | 1.6468 | 0.26326 | -0.5223 | -1.3323 | 7.8651 | 7.7239 | 7.3788 | 7.0236 | 6.5242 | 5.9277 | 5.4307 | 5.0611 | 4.664 | 4.2691 | 3.8912 | 2.9277 | 2.1806 | 1.203 | 7.4817 | 7.2647 | 6.7677 | 6.2638 | 5.6197 | 4.8434 | 4.1592 | 3.6523 | 3.1106 | 2.5692 | 2.0512 | 0.72763 | -0.12332 | -1.1304
|  | OLD CRAIGIE ROAD | ST |  |  |  | 7.5135 | 7.448 | 7.2303 | 7.0671 | 6.9202 | 6.6012 | 6.4151 | 6.1875 | 5.9617 | 5.7176 | 5.4333 | 3.6702 | 2.5358 | 1.5209 | 7.9939 | 7.9477 | 7.716 | 7.5419 | 7.3965 | 7.0457 | 6.8686 | 6.6416 | 6.4398 | 6.2215 | 5.9638 | 4.4803 | 3.3068 | 1.9828 | 7.726 | 7.6672 | 7.4213 | 7.2353 | 7.0751 | 6.7051 | 6.5065 | 6.2635 | 6.0368 | 5.7926 | 5.5053 | 3.769 | 2.6168 | 1.5793
|  | OLD CRAIGIE ROAD | FS |  |  |  | 7.5407 | 7.4823 | 7.3752 | 7.276 | 7.1659 | 7.0477 | 6.9166 | 6.743 | 6.5573 | 6.3562 | 6.1415 | 4.7706 | 3.3533 | 2.4511 | 8.0075 | 7.9651 | 7.8715 | 7.7794 | 7.6756 | 7.5631 | 7.4434 | 7.2921 | 7.1292 | 6.9469 | 6.7485 | 5.509 | 3.9484 | 2.1756 | 7.7496 | 7.698 | 7.5922 | 7.4892 | 7.3744 | 7.251 | 7.1163 | 6.9441 | 6.763 | 6.5667 | 6.3565 | 5.0461 | 3.7067 | 2.9116
| KINTORE | OLDMELDRUM | MINIMUM HEADROOM | NJ 81659 27360 | NO | YES | 1.8461 | 1.6011 | 1.2187 | 0.73693 | 0.27271 | -0.39141 | -1.0641 | -1.7516 | -2.1471 | -2.5599 | -2.966 | -4.0912 | -4.6893 | -5.0844 | 3.9343 | 3.7995 | 3.5776 | 3.2652 | 2.9545 | 2.4633 | 1.9837 | 1.4494 | 1.176 | 0.88948 | 0.60686 | -0.12607 | -0.71819 | -1.0894 | 2.7924 | 2.5663 | 2.2081 | 1.7535 | 1.3006 | 0.64942 | 0.0024761 | -0.65398 | -1.0465 | -1.4547 | -1.8544 | -2.9175 | -3.4885 | -3.9136
|  | OLDMELDRUM | CT |  |  |  | 2.0563 | 1.8637 | 1.4668 | 0.96278 | 0.50657 | -0.083538 | -0.63038 | -1.294 | -1.7188 | -2.1458 | -2.5661 | -3.7919 | -4.6161 | -5.0609 | 4.002 | 3.8759 | 3.6472 | 3.3221 | 3.0156 | 2.589 | 2.229 | 1.7294 | 1.4356 | 1.141 | 0.8555 | 0.015753 | -0.54278 | -1.0894 | 2.9705 | 2.7892 | 2.421 | 1.9483 | 1.5065 | 0.93946 | 0.43672 | -0.18455 | -0.59915 | -1.0154 | -1.4199 | -2.5722 | -3.305 | -3.7194
|  | OLDMELDRUM | LW |  |  |  | 1.8461 | 1.6011 | 1.2187 | 0.73693 | 0.27271 | -0.39141 | -1.0641 | -1.7516 | -2.1471 | -2.5599 | -2.966 | -4.0912 | -4.6893 | -5.0844 | 3.9343 | 3.7995 | 3.5776 | 3.2652 | 2.9545 | 2.4633 | 1.9837 | 1.4494 | 1.176 | 0.88948 | 0.60686 | -0.12607 | -0.51839 | -0.8777 | 2.7924 | 2.5663 | 2.2081 | 1.7535 | 1.3006 | 0.64942 | 0.0024761 | -0.65398 | -1.0465 | -1.4547 | -1.8544 | -2.9175 | -3.4885 | -3.9136
|  | OLDMELDRUM | ST |  |  |  | 2.1681 | 2.0822 | 1.8776 | 1.609 | 1.4273 | 1.0186 | 0.66805 | 0.14677 | -0.11267 | -0.39143 | -0.69539 | -2.5292 | -3.506 | -4.0663 | 4.0601 | 4.0096 | 3.8353 | 3.6137 | 3.4773 | 3.1058 | 2.8186 | 2.3765 | 2.1761 | 1.9315 | 1.6126 | -0.013316 | -0.71819 | -1.0868 | 3.0701 | 2.9927 | 2.7788 | 2.5129 | 2.3333 | 1.9128 | 1.5744 | 1.0759 | 0.82107 | 0.52046 | 0.13354 | -1.9099 | -2.8568 | -3.401
|  | OLDMELDRUM | FS |  |  |  | 2.2274 | 2.1647 | 2.0531 | 1.8688 | 1.7294 | 1.5154 | 1.2546 | 0.84345 | 0.62119 | 0.38297 | 0.13572 | -1.3807 | -2.7307 | -3.7424 | 4.0845 | 4.0447 | 3.9687 | 3.8313 | 3.7325 | 3.5652 | 3.3561 | 3.0276 | 2.8691 | 2.6955 | 2.5132 | 1.4303 | 0.24518 | -0.6849 | 3.1213 | 3.0645 | 2.9582 | 2.7842 | 2.6506 | 2.4473 | 2.2003 | 1.8174 | 1.607 | 1.3807 | 1.1443 | -0.29327 | -1.8661 | -2.9165
| THURSO | ORMLIE | MINIMUM HEADROOM | ND 10757 67408 | YES | YES | 3.5557 | 3.28 | 2.761 | 2.2866 | 1.8266 | 1.2362 | 0.50694 | -0.10291 | -0.74044 | -1.3968 | -2.0338 | -3.8128 | -4.9616 | -5.7811 | 4.8877 | 4.7111 | 4.4422 | 4.1732 | 3.9008 | 3.6077 | 3.246 | 2.8549 | 2.4394 | 2.0144 | 1.6038 | 0.4994 | -0.45634 | -1.3725 | 3.3914 | 3.13 | 2.7456 | 2.3494 | 1.9425 | 1.4951 | 0.97375 | 0.4237 | -0.19885 | -0.83766 | -1.4553 | -3.1385 | -4.2852 | -5.2248
|  | ORMLIE | CT |  |  |  | 3.8202 | 3.6075 | 3.0412 | 2.5216 | 2.0405 | 1.5061 | 0.89742 | 0.30603 | -0.31818 | -0.95471 | -1.5677 | -3.5341 | -4.9295 | -5.6857 | 4.9825 | 4.8244 | 4.4892 | 4.1732 | 3.9008 | 3.6077 | 3.2885 | 2.9313 | 2.5416 | 2.1477 | 1.7674 | 0.4994 | -0.45634 | -1.3725 | 3.527 | 3.2639 | 2.7908 | 2.3494 | 1.9425 | 1.4951 | 1.0201 | 0.53467 | 0.06908 | -0.43421 | -1.0165 | -2.859 | -4.1245 | -4.8648
|  | ORMLIE | LW |  |  |  | 3.5557 | 3.28 | 2.761 | 2.2866 | 1.8266 | 1.2362 | 0.50694 | -0.10291 | -0.74044 | -1.3968 | -2.0338 | -3.8128 | -4.9616 | -5.7811 | 4.8877 | 4.7111 | 4.4422 | 4.1887 | 3.9559 | 3.6394 | 3.246 | 2.8549 | 2.4394 | 2.0144 | 1.6038 | 0.50647 | -0.33364 | -1.1877 | 3.3914 | 3.13 | 2.7456 | 2.3531 | 1.9686 | 1.5241 | 0.97375 | 0.4237 | -0.19885 | -0.83766 | -1.4553 | -3.1385 | -4.2852 | -5.2248
|  | ORMLIE | ST |  |  |  | 4.0404 | 3.9822 | 3.8378 | 3.7338 | 3.6156 | 3.4664 | 3.2681 | 2.9634 | 2.6152 | 2.2311 | 1.7454 | -1.1266 | -2.404 | -3.2941 | 5.0871 | 5.0352 | 4.9206 | 4.8268 | 4.7247 | 4.5884 | 4.4194 | 4.1492 | 3.8882 | 3.5985 | 3.2635 | 1.0068 | -0.10423 | -0.95321 | 3.6944 | 3.6152 | 3.4684 | 3.3301 | 3.1703 | 2.9639 | 2.7129 | 2.3483 | 1.9699 | 1.5432 | 1.049 | -1.6097 | -3.0831 | -4.1075
|  | ORMLIE | FS |  |  |  | 4.0747 | 4.0311 | 3.8876 | 3.7762 | 3.6627 | 3.5312 | 3.3569 | 3.1264 | 2.8614 | 2.5644 | 2.2409 | 0.25996 | -1.5701 | -2.8636 | 5.1148 | 5.0722 | 4.9727 | 4.8906 | 4.8032 | 4.7005 | 4.5644 | 4.3768 | 4.1794 | 3.9636 | 3.7246 | 2.2856 | 0.67775 | -0.93421 | 3.737 | 3.677 | 3.5519 | 3.4358 | 3.3088 | 3.1615 | 2.9803 | 2.747 | 2.4977 | 2.2256 | 1.9233 | 0.021419 | -1.8584 | -3.2369
| DUNOON | OTTER FERRY | MINIMUM HEADROOM | NR 93352 84713 | YES | YES | -0.18785 | -0.20426 | -0.2233 | -0.24266 | -0.26145 | -0.28428 | -0.31299 | -0.33758 | -0.36525 | -0.39074 | -0.41668 | -0.45452 | -0.47086 | -0.48 | -0.025786 | -0.036081 | -0.046465 | -0.06201 | -0.072795 | -0.084948 | -0.10223 | -0.12124 | -0.14221 | -0.16268 | -0.18221 | -0.20938 | -0.21839 | -0.22783 | -0.28728 | -0.29223 | -0.29902 | -0.30534 | -0.31004 | -0.31531 | -0.323 | -0.33713 | -0.35494 | -0.37343 | -0.39094 | -0.42668 | -0.43207 | -0.43883
|  | OTTER FERRY | CT |  |  |  | -0.17857 | -0.19272 | -0.21799 | -0.24266 | -0.26145 | -0.28366 | -0.30456 | -0.32194 | -0.34871 | -0.37633 | -0.39702 | -0.44439 | -0.46946 | -0.48 | -0.022239 | -0.031175 | -0.046347 | -0.06201 | -0.072795 | -0.084948 | -0.096756 | -0.11054 | -0.13106 | -0.15211 | -0.16904 | -0.20505 | -0.21839 | -0.22783 | -0.28728 | -0.29223 | -0.29902 | -0.30534 | -0.31004 | -0.31531 | -0.323 | -0.33351 | -0.34468 | -0.35614 | -0.36954 | -0.40349 | -0.40881 | -0.41184
|  | OTTER FERRY | LW |  |  |  | -0.18785 | -0.20426 | -0.2233 | -0.24129 | -0.26003 | -0.28428 | -0.31299 | -0.33758 | -0.36525 | -0.39074 | -0.41668 | -0.45452 | -0.47086 | -0.47419 | -0.025786 | -0.036081 | -0.046465 | -0.057323 | -0.067429 | -0.083355 | -0.10223 | -0.12124 | -0.14221 | -0.16268 | -0.18221 | -0.20938 | -0.21619 | -0.21726 | -0.28713 | -0.29154 | -0.29521 | -0.2995 | -0.30355 | -0.31086 | -0.32156 | -0.33713 | -0.35494 | -0.37343 | -0.39094 | -0.42668 | -0.43207 | -0.43266
|  | OTTER FERRY | ST |  |  |  | -0.17229 | -0.17531 | -0.18091 | -0.1908 | -0.20001 | -0.2107 | -0.22444 | -0.23746 | -0.25248 | -0.27466 | -0.29267 | -0.40139 | -0.42635 | -0.43915 | -0.01893 | -0.021383 | -0.025225 | -0.031153 | -0.03712 | -0.044262 | -0.053217 | -0.062992 | -0.074745 | -0.089814 | -0.10443 | -0.18539 | -0.20276 | -0.21088 | -0.28537 | -0.28665 | -0.28842 | -0.29079 | -0.29357 | -0.29707 | -0.30133 | -0.30664 | -0.31319 | -0.32358 | -0.33571 | -0.40991 | -0.43191 | -0.43475
|  | OTTER FERRY | FS |  |  |  | -0.16899 | -0.17148 | -0.17883 | -0.18636 | -0.19396 | -0.20396 | -0.21099 | -0.22305 | -0.23661 | -0.24864 | -0.26456 | -0.36447 | -0.44117 | -0.45677 | -0.017499 | -0.019551 | -0.023674 | -0.02819 | -0.032846 | -0.038751 | -0.044073 | -0.051813 | -0.060643 | -0.069493 | -0.080303 | -0.14918 | -0.20737 | -0.22035 | -0.28498 | -0.28599 | -0.28732 | -0.28904 | -0.29094 | -0.29324 | -0.29595 | -0.29924 | -0.30304 | -0.30737 | -0.31226 | -0.362 | -0.41288 | -0.43883
| DUDHOPE | OVERGATE | MINIMUM HEADROOM | NO 40033 30155 | NO | NO | 21.1316 | 20.8993 | 20.428 | 20.2048 | 19.9689 | 19.7004 | 19.4706 | 19.1921 | 18.9173 | 18.5848 | 18.2672 | 17.1976 | 16.4095 | 16.0286 | 23.1118 | 22.9717 | 22.565 | 22.4092 | 22.1952 | 21.9514 | 21.7478 | 21.565 | 21.3666 | 21.1693 | 20.9786 | 20.3961 | 19.5143 | 18.3281 | 23.421 | 23.2641 | 22.7722 | 22.5889 | 22.3328 | 22.0491 | 21.8011 | 21.5788 | 21.3377 | 21.0964 | 20.862 | 20.1803 | 19.6361 | 18.9643
|  | OVERGATE | CT |  |  |  | 21.1316 | 20.8993 | 20.428 | 20.2048 | 19.9689 | 19.7004 | 19.4706 | 19.1921 | 18.9725 | 18.7554 | 18.4902 | 17.6428 | 17.3923 | 17.1576 | 23.1155 | 22.9717 | 22.565 | 22.4092 | 22.2241 | 22.0171 | 21.8605 | 21.6706 | 21.5049 | 21.3392 | 21.1627 | 20.464 | 19.87 | 19.0262 | 23.4434 | 23.2658 | 22.7896 | 22.6081 | 22.3952 | 22.1585 | 21.9652 | 21.7419 | 21.5649 | 21.3893 | 21.197 | 20.5289 | 20.1917 | 19.8815
|  | OVERGATE | LW |  |  |  | 21.1524 | 20.975 | 20.4516 | 20.2732 | 20.0362 | 19.768 | 19.5237 | 19.2404 | 18.9173 | 18.5848 | 18.2672 | 17.4003 | 16.9187 | 16.3796 | 23.1118 | 22.9897 | 22.5722 | 22.4187 | 22.1952 | 21.9514 | 21.7478 | 21.565 | 21.3666 | 21.1693 | 20.9786 | 20.4233 | 19.9016 | 19.2407 | 23.421 | 23.2641 | 22.7722 | 22.5889 | 22.3328 | 22.0491 | 21.8011 | 21.5788 | 21.3377 | 21.0964 | 20.862 | 20.1803 | 19.6361 | 18.9643
|  | OVERGATE | ST |  |  |  | 21.2188 | 21.1273 | 20.74 | 20.6274 | 20.4907 | 20.273 | 20.0835 | 19.8278 | 19.5755 | 19.2877 | 18.9557 | 17.1976 | 16.4095 | 16.0286 | 23.1587 | 23.0829 | 22.7174 | 22.6095 | 22.5084 | 22.3245 | 22.1988 | 22.0163 | 21.866 | 21.6976 | 21.5019 | 20.3961 | 19.5143 | 18.5434 | 23.5103 | 23.4275 | 23.0331 | 22.9285 | 22.83 | 22.6442 | 22.514 | 22.3196 | 22.156 | 21.9689 | 21.7531 | 20.5743 | 19.8913 | 19.3976
|  | OVERGATE | FS |  |  |  | 21.2752 | 21.2069 | 20.9346 | 20.8358 | 20.7448 | 20.6221 | 20.5082 | 20.3694 | 20.1952 | 20.0141 | 19.8293 | 18.6547 | 17.5123 | 16.7632 | 23.2043 | 23.1452 | 22.8854 | 22.7947 | 22.7167 | 22.6108 | 22.5202 | 22.4064 | 22.2628 | 22.1181 | 21.976 | 21.068 | 19.9028 | 18.3281 | 23.5618 | 23.5072 | 23.2405 | 23.1578 | 23.0867 | 22.9893 | 22.9073 | 22.8048 | 22.6737 | 22.543 | 22.4165 | 21.6299 | 20.8586 | 20.328
| CASSLEY | OVERSCAIG | MINIMUM HEADROOM | NC 39711 25382 | YES | YES | 0.15549 | 0.15491 | 0.15369 | 0.15269 | 0.15023 | 0.1488 | 0.14614 | 0.14343 | 0.1401 | 0.13722 | 0.13285 | 0.12572 | 0.1257 | 0.12471 | 0.14608 | 0.1456 | 0.14416 | 0.1432 | 0.14195 | 0.14088 | 0.13912 | 0.13683 | 0.1343 | 0.13177 | 0.12883 | 0.1237 | 0.1227 | 0.12218 | 0.14382 | 0.14271 | 0.14041 | 0.1392 | 0.13694 | 0.13557 | 0.1331 | 0.13039 | 0.12719 | 0.12436 | 0.12026 | 0.1135 | 0.11348 | 0.11238
|  | OVERSCAIG | CT |  |  |  | 0.15549 | 0.15491 | 0.15369 | 0.15269 | 0.15023 | 0.1488 | 0.14614 | 0.144 | 0.14229 | 0.14119 | 0.13857 | 0.13063 | 0.13157 | 0.1304 | 0.14608 | 0.1456 | 0.14416 | 0.1432 | 0.14195 | 0.14088 | 0.13948 | 0.13785 | 0.13651 | 0.13531 | 0.13332 | 0.12757 | 0.12783 | 0.12738 | 0.14382 | 0.14271 | 0.14041 | 0.1392 | 0.13694 | 0.13557 | 0.1331 | 0.13104 | 0.1294 | 0.12828 | 0.12576 | 0.11822 | 0.11902 | 0.11799
|  | OVERSCAIG | LW |  |  |  | 0.15711 | 0.15642 | 0.15403 | 0.15338 | 0.15097 | 0.14914 | 0.14644 | 0.14343 | 0.1401 | 0.13722 | 0.13285 | 0.12572 | 0.1257 | 0.12745 | 0.14666 | 0.14598 | 0.14499 | 0.14409 | 0.14287 | 0.14116 | 0.13912 | 0.13683 | 0.1343 | 0.13177 | 0.12883 | 0.1237 | 0.12368 | 0.12433 | 0.1445 | 0.1433 | 0.14151 | 0.1403 | 0.13806 | 0.13589 | 0.1333 | 0.13039 | 0.12719 | 0.12436 | 0.12026 | 0.1135 | 0.11348 | 0.11501
|  | OVERSCAIG | ST |  |  |  | 0.15737 | 0.15718 | 0.15691 | 0.15656 | 0.15616 | 0.15552 | 0.15418 | 0.15248 | 0.15038 | 0.14842 | 0.14579 | 0.13103 | 0.12599 | 0.12651 | 0.14686 | 0.14671 | 0.1465 | 0.1462 | 0.14555 | 0.14473 | 0.14372 | 0.14246 | 0.14088 | 0.13913 | 0.13706 | 0.12615 | 0.1227 | 0.12286 | 0.14494 | 0.14463 | 0.14421 | 0.14358 | 0.14277 | 0.14173 | 0.14044 | 0.13887 | 0.13689 | 0.13487 | 0.13234 | 0.11827 | 0.11351 | 0.11396
|  | OVERSCAIG | FS |  |  |  | 0.15741 | 0.15725 | 0.15705 | 0.15678 | 0.15649 | 0.15614 | 0.15572 | 0.15485 | 0.15369 | 0.15121 | 0.1497 | 0.13804 | 0.1298 | 0.12471 | 0.1469 | 0.14677 | 0.14661 | 0.1464 | 0.14613 | 0.1456 | 0.14496 | 0.14421 | 0.14335 | 0.14211 | 0.14096 | 0.13291 | 0.12618 | 0.12218 | 0.14498 | 0.14476 | 0.14445 | 0.14404 | 0.14349 | 0.14283 | 0.14203 | 0.14108 | 0.13998 | 0.13778 | 0.13633 | 0.12526 | 0.11728 | 0.11238
| KINTORE | PARK | MINIMUM HEADROOM | NO 79107 99434 | YES | YES | -1.7434 | -1.8338 | -2.4291 | -3.0912 | -4.3103 | -5.6287 | -6.4618 | -6.7523 | -7.0524 | -7.3305 | -7.6214 | -8.7561 | -9.3419 | -9.8294 | -0.69569 | -0.74743 | -1.4162 | -2.1628 | -3.604 | -5.1489 | -6.0802 | -6.3728 | -6.6779 | -6.9493 | -7.2377 | -8.4639 | -9.0888 | -9.6513 | -1.1635 | -1.2101 | -1.8992 | -2.6809 | -4.1572 | -5.7379 | -6.707 | -7.0205 | -7.3454 | -7.6489 | -7.9766 | -9.2984 | -9.9759 | -10.5609
|  | PARK | CT |  |  |  | -1.6726 | -1.7371 | -1.9419 | -2.1981 | -2.8847 | -3.612 | -3.8933 | -4.0974 | -4.318 | -4.5303 | -4.7412 | -5.5281 | -5.9769 | -6.2627 | -0.6683 | -0.71147 | -0.87539 | -1.1058 | -1.8828 | -2.7094 | -2.9698 | -3.1562 | -3.3591 | -3.5492 | -3.7418 | -4.5413 | -4.96 | -5.3269 | -1.1635 | -1.2101 | -1.3514 | -1.5742 | -2.384 | -3.2435 | -3.5426 | -3.7465 | -3.9683 | -4.185 | -4.4132 | -5.2926 | -5.7555 | -6.0656
|  | PARK | LW |  |  |  | -1.7434 | -1.8338 | -2.4291 | -3.0912 | -4.3103 | -5.6287 | -6.4618 | -6.7523 | -7.0524 | -7.3305 | -7.6214 | -8.7561 | -9.3419 | -9.8294 | -0.69569 | -0.74743 | -1.4162 | -2.1628 | -3.604 | -5.1489 | -6.0802 | -6.3728 | -6.6779 | -6.9493 | -7.2377 | -8.4639 | -9.0888 | -9.6513 | -1.1611 | -1.197 | -1.8992 | -2.6809 | -4.1572 | -5.7379 | -6.707 | -7.0205 | -7.3454 | -7.6489 | -7.9766 | -9.2984 | -9.9759 | -10.5609
|  | PARK | ST |  |  |  | -1.6416 | -1.674 | -2.2262 | -2.6232 | -2.9069 | -3.7507 | -4.0303 | -4.3037 | -4.4519 | -4.6029 | -4.798 | -5.7673 | -6.3158 | -6.7476 | -0.65155 | -0.67124 | -1.3352 | -1.7986 | -2.1183 | -3.138 | -3.4525 | -3.7539 | -3.8983 | -4.0381 | -4.23 | -5.1773 | -5.7509 | -6.2334 | -1.1467 | -1.1577 | -1.8122 | -2.2639 | -2.5729 | -3.5839 | -3.8953 | -4.2072 | -4.3603 | -4.5112 | -4.7135 | -5.7808 | -6.3906 | -6.8111
|  | PARK | FS |  |  |  | -1.6183 | -1.6419 | -1.7797 | -1.9254 | -2.0885 | -2.2537 | -2.4074 | -2.5426 | -2.6564 | -2.7763 | -2.9009 | -3.4616 | -3.8948 | -4.1462 | -0.64162 | -0.6573 | -0.8081 | -0.96381 | -1.142 | -1.3227 | -1.4859 | -1.6173 | -1.7224 | -1.8323 | -1.9467 | -2.3734 | -2.7588 | -3.0743 | -1.1429 | -1.1512 | -1.2928 | -1.437 | -1.605 | -1.776 | -1.9284 | -2.05 | -2.1664 | -2.2877 | -2.4132 | -2.9104 | -3.3216 | -3.5561
| ALNESS | PEDDIESTON | MINIMUM HEADROOM | NH 74198 63656 | NO | YES | 1.727 | 1.6746 | 1.6171 | 1.5532 | 1.4625 | 1.3666 | 1.2874 | 1.2123 | 1.1221 | 1.0379 | 0.95766 | 0.69858 | 0.21111 | -0.4851 | 2.1015 | 2.0745 | 2.047 | 2.0033 | 1.9393 | 1.8729 | 1.8299 | 1.7611 | 1.6768 | 1.5973 | 1.5193 | 1.2206 | 0.71503 | -0.12927 | 1.4771 | 1.4323 | 1.3833 | 1.3277 | 1.2366 | 1.1442 | 1.0737 | 0.99666 | 0.90552 | 0.82147 | 0.7402 | 0.45422 | -0.11444 | -0.97295
|  | PEDDIESTON | CT |  |  |  | 1.754 | 1.722 | 1.6434 | 1.5571 | 1.4625 | 1.3666 | 1.2874 | 1.2123 | 1.1221 | 1.0379 | 0.95766 | 0.69858 | 0.38075 | 0.079239 | 2.1111 | 2.0929 | 2.051 | 2.0033 | 1.9393 | 1.8729 | 1.8299 | 1.7611 | 1.6768 | 1.5973 | 1.5193 | 1.228 | 0.88111 | 0.48549 | 1.4998 | 1.4726 | 1.404 | 1.3277 | 1.2366 | 1.1442 | 1.0737 | 0.99666 | 0.90552 | 0.82147 | 0.7402 | 0.45422 | 0.093282 | -0.26821
|  | PEDDIESTON | LW |  |  |  | 1.727 | 1.6746 | 1.6171 | 1.5532 | 1.5002 | 1.4192 | 1.3372 | 1.2507 | 1.1581 | 1.0664 | 0.98075 | 0.72509 | 0.21111 | -0.4851 | 2.1015 | 2.0745 | 2.047 | 2.016 | 1.9905 | 1.9482 | 1.9032 | 1.8263 | 1.7401 | 1.6589 | 1.5793 | 1.3197 | 0.71889 | -0.12927 | 1.4771 | 1.4323 | 1.3833 | 1.3288 | 1.2835 | 1.2137 | 1.1433 | 1.0563 | 0.96349 | 0.87377 | 0.78794 | 0.50784 | -0.11444 | -0.97295
|  | PEDDIESTON | ST |  |  |  | 1.778 | 1.7587 | 1.7102 | 1.6676 | 1.6307 | 1.5668 | 1.5186 | 1.4078 | 1.3356 | 1.2651 | 1.177 | 0.76749 | 0.33405 | -0.095526 | 2.1217 | 2.1118 | 2.0708 | 2.0373 | 2.01 | 1.95 | 1.9164 | 1.8055 | 1.7464 | 1.6858 | 1.6058 | 1.2206 | 0.71503 | 0.17262 | 1.5207 | 1.5046 | 1.4549 | 1.413 | 1.3778 | 1.3102 | 1.2655 | 1.144 | 1.073 | 1.0049 | 0.91648 | 0.50262 | -0.0034509 | -0.52004
|  | PEDDIESTON | FS |  |  |  | 1.7886 | 1.7732 | 1.747 | 1.7197 | 1.6878 | 1.6571 | 1.6209 | 1.5615 | 1.5074 | 1.4512 | 1.3942 | 1.1078 | 0.90573 | 0.81114 | 2.1256 | 2.1173 | 2.1007 | 2.0829 | 2.0626 | 2.0418 | 2.0188 | 1.968 | 1.9252 | 1.8806 | 1.8333 | 1.6258 | 1.4341 | 1.2691 | 1.5293 | 1.5164 | 1.4927 | 1.4682 | 1.4391 | 1.4112 | 1.3788 | 1.3185 | 1.2657 | 1.2111 | 1.1557 | 0.90109 | 0.71911 | 0.62435
| PETERHEAD GRANGE | PETERHEAD GRANGE | MINIMUM HEADROOM | NK 11738 46516 | NO | YES | 9.655 | 9.1648 | 8.1714 | 7.1161 | 5.9844 | 4.1664 | 2.5931 | 1.3875 | 0.20256 | -1.0239 | -2.2032 | -5.6551 | -7.5641 | -9.1848 | 12.4771 | 12.1879 | 11.6711 | 11.1034 | 10.4468 | 9.1804 | 8.1547 | 7.3866 | 6.6528 | 5.8922 | 5.167 | 3.2119 | 1.9273 | 0.095715 | 12.2838 | 11.8376 | 10.9279 | 9.9583 | 8.894 | 7.1766 | 5.7043 | 4.5955 | 3.5305 | 2.4313 | 1.3701 | -1.794 | -3.6614 | -5.048
|  | PETERHEAD GRANGE | CT |  |  |  | 10.2355 | 9.9452 | 9.0375 | 8.0698 | 7.1346 | 5.6976 | 4.5683 | 3.3517 | 2.1115 | 0.86731 | -0.33386 | -4.5799 | -7.4444 | -9.1848 | 12.685 | 12.4735 | 11.9728 | 11.423 | 10.8621 | 9.8508 | 9.1469 | 8.4287 | 7.6875 | 6.9468 | 6.2318 | 3.7813 | 1.9273 | 0.095715 | 12.7934 | 12.5263 | 11.7091 | 10.8387 | 9.9626 | 8.6037 | 7.5629 | 6.4591 | 5.3434 | 4.2283 | 3.1459 | -0.72285 | -3.3858 | -4.9956
|  | PETERHEAD GRANGE | LW |  |  |  | 9.655 | 9.1648 | 8.1714 | 7.1161 | 5.9844 | 4.1664 | 2.5931 | 1.3875 | 0.20256 | -1.0239 | -2.2032 | -5.6551 | -7.5641 | -8.8895 | 12.4771 | 12.1879 | 11.6711 | 11.1034 | 10.4468 | 9.1804 | 8.1547 | 7.3866 | 6.6528 | 5.8922 | 5.167 | 3.2119 | 2.0131 | 0.83881 | 12.2838 | 11.8376 | 10.9279 | 9.9583 | 8.894 | 7.1766 | 5.7043 | 4.5955 | 3.5305 | 2.4313 | 1.3701 | -1.794 | -3.6614 | -5.048
|  | PETERHEAD GRANGE | ST |  |  |  | 10.4035 | 10.2839 | 10.0126 | 9.7329 | 9.4462 | 8.5579 | 7.9796 | 7.4646 | 7.0132 | 6.5189 | 5.9808 | 2.4401 | -0.13514 | -2.9965 | 12.773 | 12.6889 | 12.4462 | 12.2155 | 11.9927 | 11.1845 | 10.6939 | 10.2518 | 9.8787 | 9.4748 | 9.0243 | 6.3728 | 4.3993 | 2.0698 | 12.9468 | 12.8406 | 12.5655 | 12.3023 | 12.0417 | 11.1741 | 10.636 | 10.1584 | 9.7557 | 9.3187 | 8.8382 | 5.491 | 3.1555 | 0.50348
|  | PETERHEAD GRANGE | FS |  |  |  | 10.455 | 10.3659 | 10.1827 | 9.9738 | 9.7405 | 9.2202 | 8.767 | 8.292 | 7.8472 | 7.3795 | 6.8997 | 3.6477 | 0.2977 | -2.1748 | 12.7978 | 12.7305 | 12.5952 | 12.4398 | 12.2666 | 11.8299 | 11.4505 | 11.0894 | 10.7511 | 10.3904 | 10.0102 | 7.5313 | 4.4861 | 1.2198 | 12.9927 | 12.9139 | 12.7447 | 12.5589 | 12.3515 | 11.8705 | 11.4538 | 11.0235 | 10.624 | 10.2064 | 9.7784 | 6.8846 | 3.8782 | 1.6062
| PETERHEAD GRANGE | PETERHEAD NORTH STREET | MINIMUM HEADROOM | NK 13470 46450 | NO | YES | 9.5199 | 9.4357 | 9.2602 | 9.0634 | 8.9036 | 8.73 | 8.5522 | 8.3762 | 8.2065 | 7.9716 | 7.7257 | 6.6566 | 6.0014 | 5.3185 | 14.1641 | 14.0295 | 13.8806 | 13.7208 | 13.6009 | 13.4695 | 13.3293 | 13.1786 | 13.0377 | 12.9004 | 12.7385 | 11.9536 | 11.3123 | 10.5961 | 12.8727 | 12.8437 | 12.7622 | 12.4997 | 12.2811 | 12.0436 | 11.7955 | 11.5436 | 11.317 | 11.0002 | 10.6429 | 9.4699 | 8.6663 | 7.8993
|  | PETERHEAD NORTH STREET | CT |  |  |  | 9.5681 | 9.4459 | 9.2602 | 9.0634 | 8.9036 | 8.73 | 8.5522 | 8.3762 | 8.2065 | 8.0395 | 7.86 | 7.1072 | 6.2996 | 5.6922 | 14.1641 | 14.0295 | 13.8806 | 13.7208 | 13.6009 | 13.4695 | 13.3293 | 13.1786 | 13.0377 | 12.9004 | 12.7472 | 12.2408 | 11.9316 | 11.5115 | 12.8743 | 12.8437 | 12.7622 | 12.4997 | 12.2811 | 12.0436 | 11.7955 | 11.5436 | 11.317 | 11.0935 | 10.834 | 9.8899 | 9.2978 | 8.7904
|  | PETERHEAD NORTH STREET | LW |  |  |  | 9.5199 | 9.4357 | 9.3175 | 9.1905 | 9.0553 | 8.8778 | 8.6782 | 8.4575 | 8.2218 | 7.9716 | 7.7257 | 6.6566 | 6.0014 | 5.3185 | 14.1702 | 14.105 | 14.0466 | 13.9764 | 13.8994 | 13.7784 | 13.6327 | 13.4318 | 13.2083 | 12.9733 | 12.7385 | 11.9536 | 11.3123 | 10.5961 | 12.8727 | 12.8466 | 12.8234 | 12.7278 | 12.5501 | 12.3051 | 12.0253 | 11.7089 | 11.3646 | 11.0002 | 10.6429 | 9.4699 | 8.6663 | 7.8993
|  | PETERHEAD NORTH STREET | ST |  |  |  | 9.6169 | 9.593 | 9.5572 | 9.5128 | 9.4589 | 9.3879 | 9.3102 | 9.171 | 9.0476 | 8.8984 | 8.6941 | 7.0703 | 6.2746 | 5.8694 | 14.1958 | 14.1715 | 14.1318 | 14.0848 | 14.0288 | 13.9515 | 13.8664 | 13.7033 | 13.5575 | 13.3923 | 13.1912 | 12.1212 | 11.4416 | 10.9853 | 12.8818 | 12.8729 | 12.8543 | 12.8342 | 12.813 | 12.7801 | 12.7504 | 12.5803 | 12.3789 | 12.1438 | 11.8647 | 10.3223 | 9.4161 | 8.7364
|  | PETERHEAD NORTH STREET | FS |  |  |  | 9.6262 | 9.6118 | 9.5834 | 9.5521 | 9.5141 | 9.471 | 9.4211 | 9.3441 | 9.2635 | 9.1737 | 9.076 | 8.3585 | 7.1596 | 6.3174 | 14.2065 | 14.1899 | 14.1664 | 14.1378 | 14.1038 | 14.0628 | 14.015 | 13.9379 | 13.8587 | 13.7692 | 13.6677 | 13.0261 | 12.2567 | 11.6678 | 12.8843 | 12.8773 | 12.867 | 12.8541 | 12.8397 | 12.8227 | 12.8037 | 12.7607 | 12.7224 | 12.6069 | 12.4549 | 11.4261 | 10.2744 | 9.3919
| FORT WILLIAM | PINEGROVE | MINIMUM HEADROOM | NN 10496 73556 | NO | YES | 5.4641 | 5.2921 | 5.1164 | 4.7106 | 4.1795 | 3.5526 | 2.9752 | 2.5541 | 2.2062 | 1.9379 | 1.7457 | 1.366 | 1.0335 | 0.81614 | 6.7771 | 6.5983 | 6.4365 | 6.1878 | 5.8969 | 5.5892 | 5.3191 | 5.0936 | 4.8638 | 4.6517 | 4.4782 | 4.011 | 3.6694 | 3.2667 | 5.9444 | 5.6847 | 5.4063 | 4.9991 | 4.5716 | 4.0633 | 3.5839 | 3.2151 | 2.8957 | 2.6182 | 2.4024 | 1.9993 | 1.7217 | 1.4388
|  | PINEGROVE | CT |  |  |  | 5.4736 | 5.3415 | 5.153 | 4.7988 | 4.2177 | 3.6121 | 3.0538 | 2.6877 | 2.3148 | 2.0171 | 1.8054 | 1.389 | 1.0335 | 0.83499 | 6.8205 | 6.6775 | 6.4725 | 6.1922 | 5.8969 | 5.5892 | 5.3191 | 5.1038 | 4.8783 | 4.6724 | 4.497 | 4.011 | 3.6694 | 3.2667 | 6.0609 | 5.8577 | 5.5148 | 5.0564 | 4.5716 | 4.0633 | 3.5954 | 3.301 | 2.9701 | 2.6991 | 2.4973 | 2.0262 | 1.7217 | 1.5363
|  | PINEGROVE | LW |  |  |  | 5.4641 | 5.2921 | 5.1164 | 4.7106 | 4.1795 | 3.5526 | 2.9752 | 2.5541 | 2.2062 | 1.9379 | 1.7457 | 1.366 | 1.0931 | 0.81614 | 6.7771 | 6.5983 | 6.4365 | 6.1878 | 5.9341 | 5.6239 | 5.3336 | 5.0936 | 4.8638 | 4.6517 | 4.4782 | 4.1648 | 3.9764 | 3.7146 | 5.9444 | 5.6847 | 5.4063 | 4.9991 | 4.5722 | 4.0689 | 3.5839 | 3.2151 | 2.8957 | 2.6182 | 2.4024 | 1.9993 | 1.7428 | 1.4388
|  | PINEGROVE | ST |  |  |  | 5.5513 | 5.4595 | 5.3917 | 5.2631 | 5.1333 | 4.9779 | 4.8623 | 4.6335 | 4.3694 | 4.1341 | 3.9341 | 3.0789 | 2.8501 | 2.6207 | 6.8857 | 6.7897 | 6.6942 | 6.549 | 6.4019 | 6.2184 | 6.0687 | 5.8805 | 5.7016 | 5.5301 | 5.364 | 4.5576 | 4.1862 | 3.7646 | 6.2044 | 6.0666 | 5.9432 | 5.7428 | 5.5388 | 5.2975 | 5.097 | 4.8499 | 4.6117 | 4.3893 | 4.1851 | 3.2673 | 3.0104 | 2.7987
|  | PINEGROVE | FS |  |  |  | 5.5517 | 5.4699 | 5.4155 | 5.3013 | 5.18 | 5.0496 | 4.9451 | 4.7816 | 4.5801 | 4.4069 | 4.2533 | 3.364 | 2.7988 | 2.5876 | 6.8913 | 6.8077 | 6.729 | 6.6023 | 6.4676 | 6.3214 | 6.189 | 6.0399 | 5.9009 | 5.7702 | 5.6428 | 4.8875 | 4.139 | 3.4226 | 6.213 | 6.0989 | 5.9859 | 5.8058 | 5.6167 | 5.4123 | 5.2319 | 5.0385 | 4.8619 | 4.7024 | 4.5537 | 3.6897 | 3.0953 | 2.9119
| TUMMEL BRIDGE | PITLOCHRY | MINIMUM HEADROOM | NN 95756 58991 | NO | YES | 2.7235 | 2.5789 | 2.3027 | 4.766 | 4.3893 | 3.9801 | 3.621 | 3.4294 | 3.229 | 3.0456 | 2.8644 | 2.3162 | 1.9978 | 1.8157 | 3.4993 | 3.4441 | 3.3172 | 5.609 | 5.3289 | 4.9622 | 4.6611 | 4.4751 | 4.2762 | 4.084 | 3.9001 | 3.4594 | 3.2529 | 3.0759 | 2.202 | 2.0482 | 1.7583 | 3.8837 | 3.4741 | 3.0049 | 2.5951 | 2.3483 | 2.0873 | 1.8396 | 1.6009 | 0.99068 | 0.68181 | 0.46779
|  | PITLOCHRY | CT |  |  |  | 2.8585 | 2.7578 | 2.5154 | 5.0126 | 4.6856 | 4.342 | 4.0764 | 3.8897 | 3.6962 | 3.5216 | 3.3391 | 2.7931 | 2.3502 | 2.1356 | 3.5013 | 3.4441 | 3.3588 | 5.7059 | 5.5241 | 5.2823 | 5.1146 | 4.9619 | 4.7801 | 4.6054 | 4.436 | 3.962 | 3.6826 | 3.4567 | 2.3262 | 2.2155 | 1.9606 | 4.1207 | 3.7734 | 3.4081 | 3.1385 | 2.9197 | 2.6721 | 2.4395 | 2.2101 | 1.5786 | 1.163 | 0.9496
|  | PITLOCHRY | LW |  |  |  | 2.7235 | 2.5789 | 2.3027 | 4.766 | 4.3893 | 3.9801 | 3.621 | 3.4294 | 3.229 | 3.0456 | 2.8644 | 2.3162 | 1.9978 | 1.8157 | 3.4993 | 3.449 | 3.3172 | 5.609 | 5.3289 | 4.9622 | 4.6611 | 4.4751 | 4.2762 | 4.084 | 3.9001 | 3.4594 | 3.2529 | 3.0759 | 2.202 | 2.0482 | 1.7583 | 3.8837 | 3.4741 | 3.0049 | 2.5951 | 2.3483 | 2.0873 | 1.8396 | 1.6009 | 0.99068 | 0.68181 | 0.46779
|  | PITLOCHRY | ST |  |  |  | 2.9552 | 2.9312 | 2.7921 | 5.4296 | 5.3251 | 5.1209 | 5.0032 | 4.8912 | 4.7804 | 4.6648 | 4.5422 | 3.8606 | 3.4176 | 3.0189 | 3.538 | 3.5181 | 3.385 | 5.7214 | 5.6367 | 5.4275 | 5.3289 | 5.2465 | 5.1636 | 5.0733 | 4.9686 | 4.2942 | 3.9613 | 3.6803 | 2.4312 | 2.3828 | 2.2157 | 4.5117 | 4.3868 | 4.1344 | 3.9887 | 3.8516 | 3.7108 | 3.5605 | 3.3971 | 2.5174 | 2.0819 | 1.7311
|  | PITLOCHRY | FS |  |  |  | 2.9619 | 2.9467 | 2.8878 | 5.5665 | 5.4839 | 5.3984 | 5.3084 | 5.2148 | 5.1187 | 5.0252 | 4.9268 | 4.2499 | 3.6674 | 3.2393 | 3.5445 | 3.5295 | 3.488 | 5.8833 | 5.8318 | 5.777 | 5.7214 | 5.6757 | 5.6271 | 5.5765 | 5.5202 | 4.9257 | 4.3325 | 3.9252 | 2.4478 | 2.4139 | 2.3296 | 4.6803 | 4.5856 | 4.4855 | 4.3795 | 4.2716 | 4.1585 | 4.0438 | 3.9214 | 3.11 | 2.4152 | 2.0341
| ARDMORE | POLLACHAR | MINIMUM HEADROOM | NF 75073 14513 | NO | YES | 2.4085 | 2.315 | 2.2101 | 2.0792 | 1.9603 | 1.8375 | 1.6957 | 1.5644 | 1.2831 | 0.99765 | 0.86559 | 0.67721 | 0.60611 | 0.56122 | 2.9304 | 2.9005 | 2.8734 | 2.8376 | 2.7714 | 2.6957 | 2.6002 | 2.496 | 2.2478 | 1.9968 | 1.8923 | 1.7342 | 1.6559 | 1.5727 | 1.941 | 1.9067 | 1.834 | 1.7158 | 1.6058 | 1.493 | 1.3625 | 1.2435 | 0.97688 | 0.70669 | 0.587 | 0.41878 | 0.35076 | 0.30938
|  | POLLACHAR | CT |  |  |  | 2.4576 | 2.3843 | 2.2335 | 2.0792 | 1.9603 | 1.8375 | 1.7174 | 1.6215 | 1.3429 | 1.0655 | 0.94206 | 0.70511 | 0.60611 | 0.56122 | 2.9437 | 2.9126 | 2.8734 | 2.8376 | 2.7714 | 2.6957 | 2.6228 | 2.5443 | 2.2979 | 2.0508 | 1.9503 | 1.7342 | 1.6559 | 1.5851 | 1.9483 | 1.9125 | 1.8582 | 1.7158 | 1.6058 | 1.493 | 1.3833 | 1.2967 | 1.0318 | 0.76779 | 0.65547 | 0.44237 | 0.35076 | 0.30938
|  | POLLACHAR | LW |  |  |  | 2.4085 | 2.315 | 2.2101 | 2.0917 | 1.9961 | 1.8559 | 1.6957 | 1.5644 | 1.2831 | 0.99765 | 0.86559 | 0.67721 | 0.61707 | 0.60036 | 2.9304 | 2.9005 | 2.8766 | 2.8464 | 2.8037 | 2.7093 | 2.6002 | 2.496 | 2.2478 | 1.9968 | 1.8923 | 1.7449 | 1.706 | 1.6965 | 1.941 | 1.9067 | 1.834 | 1.7247 | 1.6367 | 1.5086 | 1.3625 | 1.2435 | 0.97688 | 0.70669 | 0.587 | 0.41878 | 0.36268 | 0.34784
|  | POLLACHAR | ST |  |  |  | 2.5007 | 2.466 | 2.4235 | 2.3732 | 2.3212 | 2.2656 | 2.1983 | 2.1153 | 1.8787 | 1.629 | 1.5049 | 0.89013 | 0.75648 | 0.71135 | 2.9585 | 2.9418 | 2.9226 | 2.9019 | 2.8798 | 2.8562 | 2.8317 | 2.8015 | 2.588 | 2.3691 | 2.3082 | 1.8196 | 1.6992 | 1.6335 | 1.9699 | 1.9533 | 1.9349 | 1.9133 | 1.8905 | 1.8652 | 1.8277 | 1.7537 | 1.5291 | 1.2929 | 1.1816 | 0.62824 | 0.51122 | 0.47102
|  | POLLACHAR | FS |  |  |  | 2.529 | 2.5041 | 2.4623 | 2.4184 | 2.3756 | 2.3277 | 2.275 | 2.2117 | 2.0612 | 1.9013 | 1.7971 | 1.1901 | 0.73913 | 0.65503 | 2.9893 | 2.9761 | 2.9593 | 2.9425 | 2.9274 | 2.9101 | 2.8903 | 2.8678 | 2.74 | 2.6047 | 2.5454 | 2.0835 | 1.7024 | 1.5727 | 1.9965 | 1.9839 | 1.9681 | 1.9515 | 1.9372 | 1.9197 | 1.8993 | 1.8424 | 1.699 | 1.5468 | 1.4502 | 0.89242 | 0.48442 | 0.41436
| FORT WILLIAM | POOR HOUSE | MINIMUM HEADROOM | NM 71766 70148 | YES | YES | 0.1024 | 0.10238 | 0.10237 | 0.10236 | 0.10233 | 0.1023 | 0.10226 | 0.10221 | 0.10217 | 0.10212 | 0.10208 | 0.10197 | 0.10186 | 0.10177 | 0.097792 | 0.097729 | 0.097684 | 0.097623 | 0.097561 | 0.097491 | 0.097414 | 0.09734 | 0.097251 | 0.097154 | 0.097057 | 0.096389 | 0.094974 | 0.092313 | 0.096015 | 0.095988 | 0.095967 | 0.095939 | 0.095918 | 0.09589 | 0.09585 | 0.095805 | 0.09576 | 0.095713 | 0.095674 | 0.09558 | 0.095484 | 0.095411
|  | POOR HOUSE | CT |  |  |  | 0.1024 | 0.10239 | 0.10238 | 0.10236 | 0.10233 | 0.10231 | 0.10229 | 0.10225 | 0.1022 | 0.10215 | 0.10211 | 0.10202 | 0.10192 | 0.10183 | 0.097803 | 0.097745 | 0.097687 | 0.097623 | 0.097561 | 0.097491 | 0.097414 | 0.09734 | 0.097251 | 0.097154 | 0.097057 | 0.096419 | 0.095316 | 0.093407 | 0.09602 | 0.095999 | 0.09597 | 0.095939 | 0.095918 | 0.095896 | 0.095872 | 0.095838 | 0.095791 | 0.095743 | 0.095706 | 0.095616 | 0.095536 | 0.095464
|  | POOR HOUSE | LW |  |  |  | 0.1024 | 0.10238 | 0.10237 | 0.10236 | 0.10234 | 0.1023 | 0.10226 | 0.10221 | 0.10217 | 0.10212 | 0.10208 | 0.10197 | 0.10186 | 0.10177 | 0.097871 | 0.097853 | 0.097838 | 0.097821 | 0.097808 | 0.097784 | 0.097757 | 0.097728 | 0.097697 | 0.097666 | 0.09764 | 0.097573 | 0.097502 | 0.097447 | 0.096015 | 0.095988 | 0.095967 | 0.095943 | 0.095924 | 0.09589 | 0.09585 | 0.095805 | 0.09576 | 0.095713 | 0.095674 | 0.09558 | 0.095484 | 0.095411
|  | POOR HOUSE | ST |  |  |  | 0.1024 | 0.10239 | 0.10238 | 0.10238 | 0.10237 | 0.10236 | 0.10234 | 0.10231 | 0.10228 | 0.10225 | 0.10222 | 0.10204 | 0.10193 | 0.10185 | 0.097805 | 0.097752 | 0.097705 | 0.097652 | 0.097593 | 0.097525 | 0.09745 | 0.097381 | 0.097305 | 0.097219 | 0.097125 | 0.096433 | 0.095322 | 0.093418 | 0.096023 | 0.09601 | 0.095998 | 0.095983 | 0.095967 | 0.095948 | 0.095926 | 0.095901 | 0.095873 | 0.095841 | 0.09581 | 0.095637 | 0.095545 | 0.095481
|  | POOR HOUSE | FS |  |  |  | 0.1024 | 0.10239 | 0.10239 | 0.10238 | 0.10237 | 0.10236 | 0.10235 | 0.10233 | 0.10231 | 0.10229 | 0.10227 | 0.10213 | 0.10198 | 0.10191 | 0.097792 | 0.097729 | 0.097684 | 0.097632 | 0.097575 | 0.097509 | 0.097433 | 0.097365 | 0.097289 | 0.097202 | 0.097106 | 0.096389 | 0.094974 | 0.092313 | 0.096026 | 0.096013 | 0.096002 | 0.095988 | 0.095975 | 0.09596 | 0.095942 | 0.095923 | 0.095903 | 0.095881 | 0.095859 | 0.095728 | 0.095585 | 0.095529
| PORT ANN | PORT ASKAIG | MINIMUM HEADROOM | NR 42082 68818 | YES | YES | 1.6818 | 1.6407 | 1.5868 | 1.5374 | 1.4904 | 1.4373 | 1.385 | 1.3079 | 1.24 | 1.1466 | 1.0529 | 0.72453 | 0.32985 | -0.14212 | 1.7363 | 1.7132 | 1.6868 | 1.6502 | 1.6228 | 1.5931 | 1.5623 | 1.4877 | 1.4076 | 1.3317 | 1.2559 | 1.019 | 0.5526 | -0.093351 | 1.7674 | 1.7363 | 1.6992 | 1.6534 | 1.6076 | 1.5576 | 1.5125 | 1.4413 | 1.3499 | 1.2612 | 1.1726 | 0.85129 | 0.3969 | -0.24219
|  | PORT ASKAIG | CT |  |  |  | 1.6818 | 1.6407 | 1.5868 | 1.5374 | 1.4904 | 1.4373 | 1.385 | 1.3079 | 1.24 | 1.1741 | 1.0961 | 0.8201 | 0.61869 | 0.40322 | 1.7434 | 1.7222 | 1.6868 | 1.6502 | 1.6228 | 1.5931 | 1.5649 | 1.5053 | 1.4368 | 1.3705 | 1.3076 | 1.0932 | 0.85291 | 0.57923 | 1.7886 | 1.7591 | 1.7052 | 1.6534 | 1.6076 | 1.5576 | 1.5125 | 1.4488 | 1.3806 | 1.3046 | 1.2317 | 0.94959 | 0.70825 | 0.44283
|  | PORT ASKAIG | LW |  |  |  | 1.6818 | 1.6465 | 1.6147 | 1.5801 | 1.5459 | 1.4905 | 1.4256 | 1.3377 | 1.2415 | 1.1466 | 1.0529 | 0.76774 | 0.38065 | -0.14212 | 1.7363 | 1.7132 | 1.6907 | 1.6657 | 1.6443 | 1.6064 | 1.5623 | 1.4877 | 1.4076 | 1.3317 | 1.2559 | 1.019 | 0.5526 | -0.093351 | 1.7674 | 1.7363 | 1.6992 | 1.6611 | 1.6266 | 1.5746 | 1.5155 | 1.4413 | 1.3499 | 1.2612 | 1.1726 | 0.88409 | 0.40846 | -0.24219
|  | PORT ASKAIG | ST |  |  |  | 1.7099 | 1.6962 | 1.6776 | 1.6556 | 1.6298 | 1.598 | 1.5585 | 1.4673 | 1.3945 | 1.3151 | 1.2195 | 0.72453 | 0.32985 | 0.0049913 | 1.7543 | 1.7467 | 1.736 | 1.7229 | 1.7091 | 1.6923 | 1.671 | 1.5899 | 1.5394 | 1.4868 | 1.4207 | 1.0757 | 0.65067 | 0.26312 | 1.8099 | 1.7986 | 1.7818 | 1.764 | 1.7474 | 1.7276 | 1.701 | 1.6076 | 1.5333 | 1.4532 | 1.3553 | 0.85129 | 0.3969 | 0.00042374
|  | PORT ASKAIG | FS |  |  |  | 1.7156 | 1.7061 | 1.6916 | 1.6756 | 1.6561 | 1.634 | 1.6081 | 1.5623 | 1.5188 | 1.4697 | 1.4158 | 1.1165 | 0.84024 | 0.64847 | 1.7569 | 1.7514 | 1.7426 | 1.7328 | 1.7214 | 1.7089 | 1.694 | 1.656 | 1.6236 | 1.587 | 1.5481 | 1.3654 | 1.2003 | 1.0679 | 1.8152 | 1.8085 | 1.7938 | 1.7804 | 1.763 | 1.7468 | 1.727 | 1.6822 | 1.6474 | 1.604 | 1.5578 | 1.2676 | 0.9979 | 0.80443
| PORT ANN | PORT ELLEN | MINIMUM HEADROOM | NR 36459 45513 | YES | YES | 1.2551 | 1.2158 | 1.157 | 1.0902 | 1.0236 | 0.94965 | 0.86418 | 0.77118 | 0.67363 | 0.57799 | 0.48672 | 0.21979 | -0.17798 | -0.73703 | 1.5545 | 1.5152 | 1.4759 | 1.428 | 1.3857 | 1.3404 | 1.2857 | 1.2002 | 1.1096 | 1.0226 | 0.93727 | 0.66661 | 0.19302 | -0.48244 | 1.2097 | 1.1676 | 1.1179 | 1.0557 | 0.9991 | 0.93831 | 0.86629 | 0.77585 | 0.68118 | 0.58995 | 0.50165 | 0.21927 | -0.26831 | -0.95073
|  | PORT ELLEN | CT |  |  |  | 1.264 | 1.2234 | 1.1672 | 1.093 | 1.0236 | 0.94965 | 0.87465 | 0.80645 | 0.7297 | 0.65815 | 0.58474 | 0.36272 | 0.12278 | -0.10384 | 1.5682 | 1.5372 | 1.4838 | 1.428 | 1.3857 | 1.3404 | 1.294 | 1.2303 | 1.1596 | 1.0932 | 1.024 | 0.7888 | 0.52306 | 0.2283 | 1.2189 | 1.1811 | 1.1179 | 1.0557 | 0.9991 | 0.93831 | 0.87531 | 0.80827 | 0.73618 | 0.66718 | 0.59554 | 0.36458 | 0.084691 | -0.1948
|  | PORT ELLEN | LW |  |  |  | 1.2551 | 1.2158 | 1.157 | 1.0902 | 1.0316 | 0.95335 | 0.86418 | 0.77118 | 0.67363 | 0.57799 | 0.48672 | 0.21979 | -0.17798 | -0.73703 | 1.5545 | 1.5152 | 1.4759 | 1.4349 | 1.399 | 1.3465 | 1.2857 | 1.2002 | 1.1096 | 1.0226 | 0.93727 | 0.66661 | 0.19302 | -0.48244 | 1.2097 | 1.1676 | 1.122 | 1.0697 | 1.016 | 0.9458 | 0.86629 | 0.77585 | 0.68118 | 0.58995 | 0.50165 | 0.21927 | -0.26831 | -0.95073
|  | PORT ELLEN | ST |  |  |  | 1.2889 | 1.2686 | 1.2489 | 1.2278 | 1.2051 | 1.1778 | 1.1474 | 1.0675 | 1.011 | 0.94733 | 0.86813 | 0.49191 | 0.14902 | -0.17402 | 1.5854 | 1.567 | 1.5494 | 1.5308 | 1.5114 | 1.4879 | 1.4621 | 1.3755 | 1.321 | 1.2648 | 1.1941 | 0.84865 | 0.44929 | 0.040571 | 1.2422 | 1.224 | 1.206 | 1.1866 | 1.1633 | 1.1343 | 1.1029 | 1.0097 | 0.94824 | 0.88408 | 0.80378 | 0.40567 | -0.024692 | -0.42777
|  | PORT ELLEN | FS |  |  |  | 1.2966 | 1.2815 | 1.2643 | 1.2453 | 1.2255 | 1.2056 | 1.1821 | 1.1412 | 1.1028 | 1.0547 | 1.001 | 0.71354 | 0.49835 | 0.39916 | 1.5912 | 1.5766 | 1.5613 | 1.5437 | 1.5264 | 1.5086 | 1.4873 | 1.4445 | 1.4049 | 1.363 | 1.3178 | 1.0953 | 0.89731 | 0.75124 | 1.2492 | 1.2358 | 1.2202 | 1.2029 | 1.1847 | 1.164 | 1.1382 | 1.0913 | 1.048 | 1.0017 | 0.95201 | 0.69809 | 0.49087 | 0.33656
| DUNVEGAN | PORTREE | MINIMUM HEADROOM | NG 48102 44602 | NO | YES | 2.3599 | 1.8204 | 1.5274 | 1.225 | 0.90351 | 0.59704 | 0.035579 | -0.10204 | -0.26778 | -0.42713 | -0.56822 | -0.87481 | -1.2799 | -1.4841 | 3.9897 | 3.5785 | 3.4195 | 3.2562 | 3.0659 | 2.8641 | 2.5931 | 2.4868 | 2.3468 | 2.2091 | 2.0845 | 1.7442 | 1.4529 | 1.1828 | 3.6085 | 3.1278 | 2.8988 | 2.6633 | 2.3796 | 2.0615 | 1.5828 | 1.4505 | 1.2906 | 1.1365 | 0.99293 | 0.64829 | 0.27076 | 0.060532
|  | PORTREE | CT |  |  |  | 2.5284 | 2.0772 | 1.7175 | 1.3421 | 0.94855 | 0.59704 | 0.035579 | -0.10204 | -0.26778 | -0.42713 | -0.56822 | -0.87481 | -1.2799 | -1.4841 | 4.0707 | 3.7196 | 3.5134 | 3.295 | 3.0659 | 2.8641 | 2.5931 | 2.4868 | 2.3468 | 2.2091 | 2.0845 | 1.7442 | 1.4529 | 1.1828 | 3.6542 | 3.3138 | 3.0263 | 2.7223 | 2.3881 | 2.0615 | 1.5828 | 1.4505 | 1.2906 | 1.1365 | 0.99293 | 0.64829 | 0.27076 | 0.060532
|  | PORTREE | LW |  |  |  | 2.3599 | 1.8204 | 1.5274 | 1.225 | 0.90351 | 0.62051 | 0.082492 | -0.053457 | -0.19738 | -0.34025 | -0.46825 | -0.77084 | -1.0856 | -1.3502 | 3.9897 | 3.5785 | 3.4195 | 3.2562 | 3.083 | 2.9337 | 2.6693 | 2.5553 | 2.4318 | 2.3088 | 2.1966 | 1.9699 | 1.7242 | 1.4459 | 3.6085 | 3.1278 | 2.8988 | 2.6633 | 2.3796 | 2.1202 | 1.6632 | 1.5309 | 1.3905 | 1.2426 | 1.1021 | 0.79372 | 0.47027 | 0.16588
|  | PORTREE | ST |  |  |  | 2.6567 | 2.2683 | 2.098 | 1.9322 | 1.7768 | 1.6202 | 1.3898 | 1.2285 | 1.0673 | 0.9012 | 0.72316 | -0.090904 | -0.47409 | -0.76831 | 4.1284 | 3.8164 | 3.6862 | 3.5617 | 3.4479 | 3.3116 | 3.1479 | 3.0234 | 2.9113 | 2.7934 | 2.6613 | 2.0053 | 1.6563 | 1.3318 | 3.6844 | 3.3724 | 3.2637 | 3.1621 | 3.0502 | 2.8812 | 2.6886 | 2.5336 | 2.3901 | 2.2401 | 2.0719 | 1.2413 | 0.80048 | 0.50007
|  | PORTREE | FS |  |  |  | 2.7503 | 2.4565 | 2.3207 | 2.1738 | 2.0272 | 1.919 | 1.7197 | 1.5948 | 1.4487 | 1.2971 | 1.1425 | 0.20143 | -0.34305 | -0.56019 | 4.1942 | 3.9538 | 3.8623 | 3.7593 | 3.6574 | 3.5816 | 3.4437 | 3.3489 | 3.25 | 3.1448 | 3.0347 | 2.393 | 1.9026 | 1.5546 | 3.7455 | 3.5024 | 3.4331 | 3.3529 | 3.2743 | 3.2012 | 3.044 | 2.9208 | 2.7943 | 2.6635 | 2.5283 | 1.6901 | 1.1268 | 0.89277
| MACDUFF | PORTSOY | MINIMUM HEADROOM | NJ 58491 65037 | YES | YES | -0.44901 | -0.52526 | -0.65921 | -0.79971 | -0.93844 | -1.0989 | -1.2677 | -1.4001 | -1.5376 | -1.6783 | -1.8119 | -2.2888 | -2.6568 | -2.8712 | 0.14646 | 0.10456 | 0.043562 | -0.022196 | -0.10143 | -0.20492 | -0.27942 | -0.3701 | -0.47274 | -0.57519 | -0.67493 | -1.0013 | -1.247 | -1.471 | 0.35753 | 0.30347 | 0.22366 | 0.13534 | 0.010631 | -0.13822 | -0.29605 | -0.43198 | -0.57776 | -0.72606 | -0.8721 | -1.3625 | -1.6897 | -1.8987
|  | PORTSOY | CT |  |  |  | -0.35729 | -0.40339 | -0.5436 | -0.68564 | -0.84551 | -1.0094 | -1.1513 | -1.2987 | -1.4574 | -1.6176 | -1.7764 | -2.2888 | -2.6568 | -2.8712 | 0.18058 | 0.15107 | 0.076618 | -0.0020483 | -0.10143 | -0.20492 | -0.27942 | -0.3701 | -0.47274 | -0.57519 | -0.67493 | -1.0013 | -1.247 | -1.471 | 0.37551 | 0.34717 | 0.26413 | 0.17425 | 0.054992 | -0.099454 | -0.22772 | -0.37437 | -0.54213 | -0.7109 | -0.8721 | -1.3625 | -1.6897 | -1.8987
|  | PORTSOY | LW |  |  |  | -0.44901 | -0.52526 | -0.65921 | -0.79971 | -0.93844 | -1.0989 | -1.2677 | -1.4001 | -1.5376 | -1.6783 | -1.8119 | -2.1711 | -2.4765 | -2.7162 | 0.14646 | 0.10456 | 0.043562 | -0.022196 | -0.084988 | -0.16638 | -0.2544 | -0.3378 | -0.42522 | -0.51379 | -0.59729 | -0.79887 | -1.0294 | -1.2829 | 0.35753 | 0.30347 | 0.22366 | 0.13534 | 0.010631 | -0.13822 | -0.29605 | -0.43198 | -0.57776 | -0.72606 | -0.86558 | -1.1976 | -1.4962 | -1.7678
|  | PORTSOY | ST |  |  |  | -0.31259 | -0.33403 | -0.38749 | -0.43444 | -0.48276 | -0.55863 | -0.6121 | -0.68929 | -0.75155 | -0.81991 | -0.89593 | -1.3671 | -1.7583 | -2.1698 | 0.20082 | 0.18798 | 0.13789 | 0.095778 | 0.057639 | -0.018628 | -0.062311 | -0.13526 | -0.18814 | -0.24483 | -0.31184 | -0.68417 | -0.98013 | -1.298 | 0.39063 | 0.38208 | 0.33691 | 0.29948 | 0.26688 | 0.19282 | 0.14109 | 0.06062 | -0.0014145 | -0.069079 | -0.14825 | -0.6452 | -1.0134 | -1.3786
|  | PORTSOY | FS |  |  |  | -0.30309 | -0.31915 | -0.35089 | -0.3874 | -0.42232 | -0.46158 | -0.5016 | -0.56546 | -0.62785 | -0.6899 | -0.75451 | -1.1725 | -1.5591 | -1.8503 | 0.20501 | 0.19477 | 0.17253 | 0.14697 | 0.12059 | 0.091175 | 0.061031 | 0.013813 | -0.031441 | -0.078772 | -0.12909 | -0.42202 | -0.73701 | -1.0386 | 0.39299 | 0.38613 | 0.37034 | 0.35244 | 0.33187 | 0.309 | 0.27586 | 0.22434 | 0.1741 | 0.12238 | 0.067544 | -0.34602 | -0.74056 | -0.9723
| WOODHILL | QUEENS LANE NORTH | MINIMUM HEADROOM | NJ 92224 05823 | NO | NO | 1.4621 | 0.76404 | -0.2438 | -1.3613 | -2.6236 | -4.395 | -6.2766 | -7.9825 | -9.8522 | -11.7965 | -13.6611 | -18.2225 | -19.2795 | -21.724 | 4.9461 | 4.4338 | 3.7407 | 2.9537 | 1.9862 | 0.60805 | -0.80485 | -2.1057 | -3.5382 | -5.0262 | -6.4471 | -9.8682 | -10.7438 | -17.004 | 3.2646 | 2.5867 | 1.602 | 0.50459 | -0.77293 | -2.5583 | -4.4215 | -6.1013 | -7.944 | -9.8586 | -11.6912 | -16.1692 | -17.2694 | -19.8225
|  | QUEENS LANE NORTH | CT |  |  |  | 1.7013 | 1.2517 | 0.19797 | -0.95929 | -2.051 | -3.241 | -4.3161 | -5.5357 | -6.7693 | -7.9963 | -9.4452 | -14.5213 | -16.1429 | -16.9854 | 4.9487 | 4.5522 | 3.8023 | 2.9559 | 2.0987 | 1.1518 | 0.34728 | -0.59887 | -1.5667 | -2.5376 | -3.6995 | -8.1014 | -10.5048 | -13.6245 | 3.4717 | 3.0304 | 2.0219 | 0.90598 | -0.1767 | -1.3588 | -2.3945 | -3.5776 | -4.7753 | -5.9658 | -7.3773 | -12.2746 | -13.8017 | -14.6254
|  | QUEENS LANE NORTH | LW |  |  |  | 1.4621 | 0.76404 | -0.2438 | -1.3613 | -2.6236 | -4.395 | -6.2766 | -7.9825 | -9.8522 | -11.7965 | -13.6611 | -18.2225 | -19.2795 | -21.724 | 4.9461 | 4.4338 | 3.7407 | 2.9537 | 1.9862 | 0.60805 | -0.80485 | -2.1057 | -3.5382 | -5.0262 | -6.4471 | -9.8682 | -10.7438 | -12.9101 | 3.2646 | 2.5867 | 1.602 | 0.50459 | -0.77293 | -2.5583 | -4.4215 | -6.1013 | -7.944 | -9.8586 | -11.6912 | -16.1692 | -17.2694 | -19.8225
|  | QUEENS LANE NORTH | ST |  |  |  | 2.0226 | 1.8483 | 1.4886 | 1.1108 | 0.68502 | 0.0087878 | -0.62413 | -1.358 | -2.2044 | -3.1756 | -4.279 | -10.5142 | -13.094 | -14.727 | 5.164 | 4.9743 | 4.5702 | 4.164 | 3.7304 | 3.0179 | 2.4064 | 1.7164 | 0.94417 | 0.064867 | -0.93649 | -6.5719 | -9.8812 | -13.4322 | 3.7784 | 3.6056 | 3.2117 | 2.8112 | 2.3728 | 1.6456 | 1.0033 | 0.26276 | -0.57923 | -1.5434 | -2.6404 | -8.7538 | -11.2747 | -12.8405
|  | QUEENS LANE NORTH | FS |  |  |  | 2.042 | 1.9005 | 1.6782 | 1.4077 | 1.0895 | 0.71775 | 0.27713 | -0.22883 | -0.80049 | -1.4415 | -2.1501 | -6.9345 | -11.5954 | -14.6658 | 5.1742 | 5.0015 | 4.7598 | 4.4719 | 4.1353 | 3.7412 | 3.2868 | 2.7837 | 2.2158 | 1.5755 | 0.85839 | -4.0044 | -9.9116 | -17.004 | 3.7999 | 3.6599 | 3.4353 | 3.163 | 2.8422 | 2.4679 | 2.0277 | 1.5284 | 0.966 | 0.33558 | -0.36224 | -5.0267 | -9.5185 | -12.4146
| QUOICH | QUOICH | MINIMUM HEADROOM | NH 11700 01900 | YES | YES | 0.88314 | 0.87739 | 0.87485 | 0.8686 | 0.85963 | 0.85454 | 0.84615 | 0.84341 | 0.83699 | 0.83541 | 0.83304 | 0.82661 | 0.82206 | 0.81787 | 0.92358 | 0.92046 | 0.91908 | 0.91603 | 0.91138 | 0.90891 | 0.90517 | 0.90316 | 0.89905 | 0.89652 | 0.8938 | 0.88944 | 0.88742 | 0.8857 | 0.90261 | 0.89628 | 0.89384 | 0.88758 | 0.87936 | 0.87475 | 0.8672 | 0.86457 | 0.8586 | 0.85685 | 0.85425 | 0.84816 | 0.84409 | 0.84035
|  | QUOICH | CT |  |  |  | 0.88518 | 0.88104 | 0.87604 | 0.87104 | 0.85963 | 0.85454 | 0.84762 | 0.84341 | 0.83699 | 0.83541 | 0.83428 | 0.82833 | 0.82206 | 0.81787 | 0.92431 | 0.92199 | 0.9192 | 0.91632 | 0.91138 | 0.90891 | 0.90577 | 0.9032 | 0.8994 | 0.89709 | 0.89512 | 0.88996 | 0.88742 | 0.8857 | 0.90453 | 0.90049 | 0.89522 | 0.89004 | 0.87936 | 0.87475 | 0.86852 | 0.86457 | 0.8586 | 0.85685 | 0.85553 | 0.84967 | 0.84409 | 0.84035
|  | QUOICH | LW |  |  |  | 0.88314 | 0.87739 | 0.87485 | 0.8686 | 0.8619 | 0.85587 | 0.84615 | 0.84485 | 0.83808 | 0.83615 | 0.83304 | 0.82661 | 0.82267 | 0.8242 | 0.92358 | 0.92046 | 0.91908 | 0.91603 | 0.91312 | 0.90993 | 0.90517 | 0.90316 | 0.89905 | 0.89652 | 0.8938 | 0.88944 | 0.88796 | 0.88846 | 0.90261 | 0.89628 | 0.89384 | 0.88758 | 0.88158 | 0.87603 | 0.8672 | 0.86571 | 0.8594 | 0.85732 | 0.85425 | 0.84816 | 0.84468 | 0.84602
|  | QUOICH | ST |  |  |  | 0.89127 | 0.88807 | 0.88352 | 0.88267 | 0.88036 | 0.87919 | 0.87777 | 0.86909 | 0.86528 | 0.86311 | 0.86053 | 0.83557 | 0.82582 | 0.82171 | 0.929 | 0.9273 | 0.9249 | 0.92441 | 0.92313 | 0.92243 | 0.92152 | 0.91701 | 0.91476 | 0.91281 | 0.91062 | 0.89531 | 0.89081 | 0.88934 | 0.91071 | 0.9076 | 0.90302 | 0.90227 | 0.8998 | 0.89875 | 0.89748 | 0.88815 | 0.88459 | 0.88244 | 0.87996 | 0.85659 | 0.8478 | 0.84419
|  | QUOICH | FS |  |  |  | 0.89335 | 0.89024 | 0.88838 | 0.88637 | 0.88567 | 0.88484 | 0.88128 | 0.87872 | 0.87322 | 0.87028 | 0.8671 | 0.84271 | 0.82912 | 0.82272 | 0.93031 | 0.92866 | 0.92765 | 0.92656 | 0.92615 | 0.92566 | 0.92376 | 0.92233 | 0.9193 | 0.91748 | 0.91548 | 0.90181 | 0.89266 | 0.89 | 0.91268 | 0.90975 | 0.90794 | 0.90597 | 0.90529 | 0.90447 | 0.90106 | 0.89848 | 0.89238 | 0.88937 | 0.8862 | 0.86371 | 0.85085 | 0.84513
| THURSO | RACKWICK | MINIMUM HEADROOM | ND 20206 99857 | YES | YES | 0.087038 | 0.087038 | 0.087038 | 0.087038 | 0.087038 | 0.087038 | 0.087038 | 0.04355 | 0.02813 | 0.012541 | -0.012222 | -0.14241 | -0.50381 | -1.0176 | 0.088614 | 0.088614 | 0.088614 | 0.088614 | 0.088614 | 0.088614 | 0.088614 | 0.034255 | 0.01498 | -0.0045061 | -0.03546 | -0.1982 | -0.64995 | -1.2921 | 0.082899 | 0.082899 | 0.082899 | 0.082899 | 0.082899 | 0.082899 | 0.082899 | 0.02854 | 0.0092643 | -0.010221 | -0.041176 | -0.20392 | -0.65567 | -1.2978
|  | RACKWICK | CT |  |  |  | 0.087038 | 0.087038 | 0.087038 | 0.087038 | 0.087038 | 0.087038 | 0.087038 | 0.067269 | 0.04743 | 0.03027 | 0.011414 | -0.088711 | -0.25889 | -0.4628 | 0.088614 | 0.088614 | 0.088614 | 0.088614 | 0.088614 | 0.088614 | 0.088614 | 0.063903 | 0.039104 | 0.017655 | -0.0059153 | -0.13107 | -0.3438 | -0.59868 | 0.082899 | 0.082899 | 0.082899 | 0.082899 | 0.082899 | 0.082899 | 0.082899 | 0.058188 | 0.033389 | 0.01194 | -0.011631 | -0.13679 | -0.34951 | -0.6044
|  | RACKWICK | LW |  |  |  | 0.087038 | 0.087038 | 0.087038 | 0.087038 | 0.087038 | 0.087038 | 0.087038 | 0.061261 | 0.034533 | 0.012541 | -0.012222 | -0.14241 | -0.50381 | -1.0176 | 0.088614 | 0.088614 | 0.088614 | 0.088614 | 0.088614 | 0.088614 | 0.088614 | 0.056393 | 0.022984 | -0.0045061 | -0.03546 | -0.1982 | -0.64995 | -1.2921 | 0.082899 | 0.082899 | 0.082899 | 0.082899 | 0.082899 | 0.082899 | 0.082899 | 0.050678 | 0.017268 | -0.010221 | -0.041176 | -0.20392 | -0.65567 | -1.2978
|  | RACKWICK | ST |  |  |  | 0.087038 | 0.087038 | 0.087038 | 0.087038 | 0.087038 | 0.087038 | 0.087038 | 0.04355 | 0.02813 | 0.015072 | -0.0057933 | -0.10362 | -0.3666 | -0.66132 | 0.088614 | 0.088614 | 0.088614 | 0.088614 | 0.088614 | 0.088614 | 0.088614 | 0.034255 | 0.01498 | -0.0013429 | -0.027424 | -0.14971 | -0.47843 | -0.84684 | 0.082899 | 0.082899 | 0.082899 | 0.082899 | 0.082899 | 0.082899 | 0.082899 | 0.02854 | 0.0092643 | -0.0070582 | -0.03314 | -0.15542 | -0.48415 | -0.85255
|  | RACKWICK | FS |  |  |  | 0.087038 | 0.087038 | 0.087038 | 0.087038 | 0.087038 | 0.087038 | 0.087038 | 0.071297 | 0.060622 | 0.049947 | 0.039272 | 0.026333 | 0.011915 | -0.021015 | 0.088614 | 0.088614 | 0.088614 | 0.088614 | 0.088614 | 0.088614 | 0.088614 | 0.068938 | 0.055595 | 0.042251 | 0.028907 | 0.012734 | -0.0052887 | -0.046452 | 0.082899 | 0.082899 | 0.082899 | 0.082899 | 0.082899 | 0.082899 | 0.082899 | 0.063222 | 0.04988 | 0.036536 | 0.023192 | 0.0070185 | -0.011004 | -0.052167
| FORT WILLIAM | RAHOY | MINIMUM HEADROOM | NM 69621 49222 | YES | YES | 0.97495 | 0.97398 | 0.96975 | 0.96721 | 0.9663 | 0.96315 | 0.95737 | 0.9548 | 0.9509 | 0.94679 | 0.94358 | 0.9358 | 0.9341 | 0.9342 | 0.98208 | 0.98144 | 0.97966 | 0.97828 | 0.9777 | 0.97585 | 0.97295 | 0.96998 | 0.96691 | 0.96367 | 0.96089 | 0.955 | 0.95339 | 0.95306 | 0.97851 | 0.97663 | 0.97363 | 0.97069 | 0.96876 | 0.96578 | 0.96114 | 0.95789 | 0.95413 | 0.95019 | 0.94704 | 0.93961 | 0.93812 | 0.93794
|  | RAHOY | CT |  |  |  | 0.97579 | 0.97442 | 0.97171 | 0.96721 | 0.9663 | 0.96363 | 0.95737 | 0.95655 | 0.95341 | 0.95209 | 0.94798 | 0.94295 | 0.94105 | 0.94047 | 0.98274 | 0.98166 | 0.98029 | 0.97828 | 0.9777 | 0.97599 | 0.97332 | 0.97161 | 0.96965 | 0.96832 | 0.96557 | 0.9604 | 0.95961 | 0.95938 | 0.9786 | 0.97684 | 0.97406 | 0.97069 | 0.96876 | 0.96619 | 0.96114 | 0.95963 | 0.95674 | 0.95537 | 0.95152 | 0.94643 | 0.94475 | 0.94424
|  | RAHOY | LW |  |  |  | 0.97495 | 0.97398 | 0.96975 | 0.96913 | 0.96641 | 0.96315 | 0.95887 | 0.9548 | 0.9509 | 0.94679 | 0.94358 | 0.9358 | 0.9341 | 0.93524 | 0.98208 | 0.98144 | 0.97966 | 0.97916 | 0.97793 | 0.97585 | 0.97295 | 0.96998 | 0.96691 | 0.96367 | 0.96089 | 0.955 | 0.95437 | 0.95479 | 0.97851 | 0.97663 | 0.97363 | 0.97224 | 0.9693 | 0.96578 | 0.96176 | 0.95789 | 0.95413 | 0.95019 | 0.94704 | 0.93961 | 0.93812 | 0.93912
|  | RAHOY | ST |  |  |  | 0.97614 | 0.97595 | 0.97657 | 0.976 | 0.97486 | 0.97368 | 0.97089 | 0.96939 | 0.96634 | 0.9635 | 0.96088 | 0.94068 | 0.93494 | 0.93607 | 0.9829 | 0.98275 | 0.983 | 0.98272 | 0.98229 | 0.98144 | 0.97974 | 0.97833 | 0.97638 | 0.97425 | 0.97193 | 0.95745 | 0.95339 | 0.95378 | 0.97941 | 0.97899 | 0.97846 | 0.97774 | 0.97666 | 0.97553 | 0.97283 | 0.97124 | 0.96846 | 0.96574 | 0.96316 | 0.94402 | 0.9386 | 0.93958
|  | RAHOY | FS |  |  |  | 0.97618 | 0.97603 | 0.9761 | 0.9743 | 0.97541 | 0.97461 | 0.9729 | 0.97117 | 0.96979 | 0.96881 | 0.96708 | 0.95133 | 0.94032 | 0.9342 | 0.98293 | 0.98281 | 0.98254 | 0.9817 | 0.98199 | 0.98172 | 0.98077 | 0.98019 | 0.97916 | 0.97807 | 0.97676 | 0.96631 | 0.95788 | 0.95306 | 0.97951 | 0.97918 | 0.97858 | 0.97747 | 0.977 | 0.97622 | 0.97471 | 0.97315 | 0.97182 | 0.97073 | 0.96912 | 0.95436 | 0.94382 | 0.93794
| INVERNESS | RAIGMORE | MINIMUM HEADROOM | NH 68427 44693 | NO | YES | -4.7303 | -15.2338 | -16.1692 | -17.1738 | -18.382 | -19.8707 | -21.4278 | -22.934 | -24.5455 | -26.2141 | -27.814 | -32.215 | -33.4723 | -34.5816 | -4.3734 | -17.2554 | -18.2405 | -19.3096 | -20.6771 | -22.2292 | -23.7263 | -24.9583 | -26.2918 | -27.6601 | -28.9828 | -32.7208 | -33.925 | -35.1501 | -7.0866 | -20.0502 | -21.0779 | -22.2007 | -23.6278 | -25.3765 | -27.1645 | -28.6685 | -30.2954 | -31.9736 | -33.5901 | -38.082 | -39.4098 | -40.7053
|  | RAIGMORE | CT |  |  |  | 4.04 | 2.1734 | 1.3497 | 0.47013 | -0.45039 | -1.5127 | -2.5321 | -3.7028 | -4.7619 | -5.7792 | -6.909 | -11.1268 | -12.0009 | -12.5437 | 6.6538 | 4.6114 | 3.8949 | 3.0908 | 2.0548 | 0.7407 | -0.11939 | -1.0378 | -1.8855 | -2.6952 | -3.5879 | -6.988 | -7.6386 | -8.1364 | 3.8732 | 1.7024 | 0.84534 | -0.089727 | -1.1432 | -2.621 | -3.6605 | -4.7939 | -5.8408 | -6.8428 | -7.9429 | -12.0938 | -12.8393 | -13.357
|  | RAIGMORE | LW |  |  |  | -4.7303 | -15.2338 | -16.1692 | -17.1738 | -18.382 | -19.8707 | -21.4278 | -22.934 | -24.5455 | -26.2141 | -27.814 | -32.215 | -33.4723 | -34.5816 | -4.3734 | -17.2554 | -18.2405 | -19.3096 | -20.6771 | -22.2292 | -23.7263 | -24.9583 | -26.2918 | -27.6601 | -28.9828 | -32.7208 | -33.925 | -35.1501 | -7.0866 | -20.0502 | -21.0779 | -22.2007 | -23.6278 | -25.3765 | -27.1645 | -28.6685 | -30.2954 | -31.9736 | -33.5901 | -38.082 | -39.4098 | -40.7053
|  | RAIGMORE | ST |  |  |  | -0.26501 | -6.6084 | -7.4176 | -8.1834 | -8.6955 | -9.6715 | -10.3053 | -11.0513 | -11.9731 | -13.3111 | -14.9344 | -23.6663 | -26.9734 | -28.0054 | 1.1786 | -6.6272 | -7.4696 | -8.2395 | -8.7096 | -9.7256 | -10.3261 | -11.1807 | -12.1441 | -13.2471 | -14.5403 | -21.482 | -24.2499 | -25.2508 | -1.5493 | -9.372 | -10.279 | -11.1275 | -11.7011 | -12.8465 | -13.5521 | -14.3677 | -15.543 | -16.9052 | -18.4955 | -27.0336 | -30.3507 | -31.4653
|  | RAIGMORE | FS |  |  |  | 5.5451 | 4.9577 | 4.5494 | 4.083 | 3.7537 | 3.3919 | 3.0233 | 2.6058 | 2.1545 | 1.6777 | 1.1632 | -4.3171 | -9.8525 | -13.4328 | 8.4086 | 7.7705 | 7.3852 | 6.932 | 6.626 | 6.2961 | 5.9755 | 5.6223 | 5.2431 | 4.7165 | 4.0343 | -0.34826 | -4.6447 | -7.4522 | 5.6852 | 5.0362 | 4.6106 | 4.114 | 3.7512 | 3.3507 | 2.9446 | 2.4981 | 2.0123 | 1.4976 | 0.73743 | -4.6688 | -10.0185 | -13.4809
| ARBROATH | REDFORD | MINIMUM HEADROOM | NO 55879 44046 | YES | YES | -2.0064 | -2.134 | -2.2631 | -2.3937 | -2.5756 | -2.8383 | -3.0109 | -3.1699 | -3.344 | -3.5134 | -3.6768 | -4.2257 | -4.7079 | -5.1852 | -1.0293 | -1.0924 | -1.1515 | -1.2606 | -1.4358 | -1.6513 | -1.7563 | -1.8846 | -2.0269 | -2.1621 | -2.2958 | -2.8331 | -3.455 | -4.068 | -1.745 | -1.856 | -1.968 | -2.083 | -2.3086 | -2.5812 | -2.7425 | -2.909 | -3.0948 | -3.2743 | -3.4471 | -4.043 | -4.5852 | -5.2264
|  | REDFORD | CT |  |  |  | -1.9039 | -1.987 | -2.1495 | -2.3268 | -2.5756 | -2.8383 | -3.0109 | -3.1699 | -3.344 | -3.5134 | -3.6768 | -4.2257 | -4.7079 | -5.0728 | -0.99164 | -1.0365 | -1.1273 | -1.233 | -1.4358 | -1.6513 | -1.7563 | -1.8846 | -2.0269 | -2.1621 | -2.2958 | -2.8027 | -3.2383 | -3.6713 | -1.6607 | -1.7338 | -1.8833 | -2.0505 | -2.3086 | -2.5812 | -2.7425 | -2.909 | -3.0948 | -3.2743 | -3.4471 | -4.043 | -4.5488 | -4.9669
|  | REDFORD | LW |  |  |  | -2.0064 | -2.134 | -2.2631 | -2.3937 | -2.5216 | -2.6719 | -2.8329 | -2.9663 | -3.1006 | -3.2384 | -3.3762 | -3.7161 | -4.2797 | -4.9854 | -1.0293 | -1.0924 | -1.1515 | -1.2133 | -1.2715 | -1.3491 | -1.4347 | -1.5323 | -1.6333 | -1.733 | -1.8315 | -2.089 | -2.7065 | -3.5634 | -1.745 | -1.856 | -1.968 | -2.083 | -2.1938 | -2.3301 | -2.4778 | -2.6149 | -2.7546 | -2.8958 | -3.0359 | -3.3811 | -4.043 | -4.9122
|  | REDFORD | ST |  |  |  | -1.86 | -1.9115 | -2.062 | -2.1874 | -2.2905 | -2.5123 | -2.6217 | -2.8157 | -2.9362 | -3.0602 | -3.2085 | -3.9672 | -4.6053 | -5.1852 | -0.97163 | -0.99764 | -1.1469 | -1.2606 | -1.3473 | -1.5754 | -1.6673 | -1.8566 | -1.9573 | -2.0567 | -2.1859 | -2.8331 | -3.455 | -4.068 | -1.6234 | -1.6665 | -1.8357 | -1.9715 | -2.0798 | -2.3326 | -2.4477 | -2.6649 | -2.7924 | -2.9219 | -3.0816 | -3.889 | -4.5852 | -5.2264
|  | REDFORD | FS |  |  |  | -1.8214 | -1.8604 | -1.9303 | -1.9983 | -2.0727 | -2.1474 | -2.2233 | -2.337 | -2.4413 | -2.5475 | -2.66 | -3.2484 | -3.6657 | -3.9013 | -0.95673 | -0.97768 | -1.0267 | -1.0766 | -1.1324 | -1.1896 | -1.2458 | -1.3364 | -1.4137 | -1.4936 | -1.5776 | -1.9414 | -2.2447 | -2.4727 | -1.5918 | -1.6244 | -1.6927 | -1.7603 | -1.8347 | -1.9102 | -1.9862 | -2.1033 | -2.208 | -2.3153 | -2.4287 | -2.9838 | -3.3857 | -3.5969
| BURGHMUIR | REDGORTON | MINIMUM HEADROOM | NO 07650 28860 | NO | YES | 8.5262 | 7.4067 | 6.3014 | 5.0196 | 3.6814 | 2.7301 | 1.6095 | 0.52867 | -0.54413 | -1.7682 | -2.7754 | -5.771 | -6.6308 | -7.1328 | 9.6843 | 8.737 | 7.9517 | 7.0103 | 6.0394 | 5.6449 | 5.2194 | 4.5646 | 3.9467 | 3.1792 | 2.5538 | 0.77348 | 0.20057 | -0.26051 | 8.8761 | 7.8079 | 6.742 | 5.4975 | 4.2029 | 3.3273 | 2.3694 | 1.4047 | 0.44471 | -0.65823 | -1.5638 | -4.1704 | -4.9678 | -5.5128
|  | REDGORTON | CT |  |  |  | 8.8935 | 7.9347 | 6.8322 | 5.4867 | 4.1295 | 3.1808 | 2.1913 | 1.1629 | 0.06633 | -1.1744 | -2.1905 | -4.7 | -5.4789 | -5.9045 | 9.8615 | 8.9891 | 8.2085 | 7.2124 | 6.206 | 5.757 | 5.3526 | 4.8212 | 4.1744 | 3.3975 | 2.7768 | 0.99454 | 0.36491 | -0.24763 | 9.1915 | 8.3053 | 7.2363 | 5.917 | 4.5892 | 3.706 | 2.817 | 1.9193 | 0.93916 | -0.17476 | -1.086 | -3.3795 | -4.0996 | -4.5128
|  | REDGORTON | LW |  |  |  | 8.5262 | 7.4067 | 6.3014 | 5.0196 | 3.6814 | 2.7301 | 1.6095 | 0.52867 | -0.54413 | -1.7682 | -2.7754 | -5.771 | -6.6308 | -7.1328 | 9.6843 | 8.737 | 7.9517 | 7.0103 | 6.0394 | 5.6449 | 5.2194 | 4.5646 | 3.9467 | 3.1792 | 2.5538 | 0.77348 | 0.20057 | -0.26051 | 8.8761 | 7.8079 | 6.742 | 5.4975 | 4.2029 | 3.3273 | 2.3694 | 1.4047 | 0.44471 | -0.65823 | -1.5638 | -4.1704 | -4.9678 | -5.5128
|  | REDGORTON | ST |  |  |  | 9.0941 | 8.2514 | 7.4569 | 6.4737 | 5.4966 | 4.9284 | 4.3773 | 3.7623 | 3.0483 | 2.1722 | 1.429 | -1.4172 | -2.22 | -2.8315 | 9.8885 | 9.067 | 8.3134 | 7.3547 | 6.4088 | 5.9681 | 5.5784 | 5.1342 | 4.7699 | 4.2625 | 3.8764 | 2.2742 | 1.5416 | 0.82854 | 9.3653 | 8.5996 | 7.8048 | 6.816 | 5.8359 | 5.2847 | 4.7649 | 4.1738 | 3.6159 | 2.8351 | 2.1678 | -0.59851 | -1.3873 | -1.9509
|  | REDGORTON | FS |  |  |  | 9.4103 | 8.7632 | 8.1365 | 7.3263 | 6.5356 | 6.01 | 5.4872 | 4.9083 | 4.2578 | 3.5032 | 2.8706 | -0.38725 | -2.3952 | -3.0723 | 10.2177 | 9.5865 | 9.0199 | 8.2523 | 7.5161 | 7.1154 | 6.7265 | 6.291 | 5.833 | 5.3391 | 4.9768 | 3.1486 | 1.4889 | 0.4088 | 9.6368 | 9.0581 | 8.4956 | 7.6992 | 6.9168 | 6.4194 | 5.9275 | 5.3757 | 4.7957 | 4.1296 | 3.5711 | 0.63312 | -1.2804 | -1.8721
| REDMOSS | REDMOSS | MINIMUM HEADROOM | NJ 94562 01919 | NO | YES | 18.2828 | 17.4481 | 16.2778 | 14.7946 | 13.127 | 11.2672 | 9.671 | 8.3719 | 7.2744 | 6.2516 | 5.4393 | 2.9662 | 1.6995 | 0.22515 | 20.8241 | 20.0821 | 19.1291 | 17.9344 | 16.596 | 15.0365 | 13.7838 | 12.7468 | 11.945 | 11.1463 | 10.4322 | 8.1969 | 6.9604 | 5.4196 | 15.4933 | 14.6868 | 13.6386 | 12.3545 | 10.9145 | 9.2513 | 7.8728 | 6.7199 | 5.7562 | 4.7952 | 3.9379 | 1.3899 | 0.095616 | -1.4709
|  | REDMOSS | CT |  |  |  | 18.5122 | 17.7276 | 16.7389 | 15.5784 | 14.2101 | 12.6932 | 11.4687 | 10.2217 | 9.1651 | 8.1951 | 7.397 | 4.5581 | 3.2219 | 2.2796 | 20.9363 | 20.1877 | 19.3087 | 18.3022 | 17.1374 | 15.9412 | 15.0734 | 14.1541 | 13.5563 | 13.0034 | 12.4041 | 10.1824 | 9.3897 | 8.6618 | 15.6399 | 14.8329 | 13.836 | 12.7282 | 11.4616 | 10.1359 | 9.1538 | 8.1411 | 7.4252 | 6.7586 | 6.0434 | 3.511 | 2.6363 | 1.8725
|  | REDMOSS | LW |  |  |  | 18.2828 | 17.4481 | 16.2778 | 14.7946 | 13.127 | 11.2672 | 9.671 | 8.3719 | 7.2744 | 6.2516 | 5.4393 | 2.9662 | 1.6995 | 0.22515 | 20.8241 | 20.0821 | 19.1291 | 17.9344 | 16.596 | 15.0365 | 13.7838 | 12.7468 | 11.945 | 11.1463 | 10.4322 | 8.1969 | 6.9604 | 5.4196 | 15.4933 | 14.6868 | 13.6386 | 12.3545 | 10.9145 | 9.2513 | 7.8728 | 6.7199 | 5.7562 | 4.7952 | 3.9379 | 1.3899 | 0.095616 | -1.4709
|  | REDMOSS | ST |  |  |  | 18.642 | 18.071 | 17.274 | 16.3568 | 15.5025 | 14.3512 | 13.5037 | 12.5995 | 11.923 | 11.2123 | 10.4717 | 6.3736 | 4.5677 | 3.435 | 21.0677 | 20.5093 | 19.6766 | 18.7502 | 17.8855 | 16.7295 | 15.9595 | 15.1253 | 14.5774 | 14.0063 | 13.397 | 10.0105 | 8.3676 | 7.279 | 15.8114 | 15.2434 | 14.3956 | 13.4578 | 12.5736 | 11.372 | 10.5469 | 9.6599 | 9.013 | 8.3317 | 7.6072 | 3.611 | 1.7208 | 0.57295
|  | REDMOSS | FS |  |  |  | 20.1856 | 19.7211 | 18.0527 | 17.399 | 16.7359 | 16.0487 | 15.3997 | 14.7373 | 14.1277 | 13.5472 | 13.0228 | 9.8591 | 7.1095 | 5.1912 | 22.9127 | 22.4679 | 20.5221 | 19.8744 | 19.2196 | 18.5527 | 17.9264 | 17.2788 | 16.7563 | 16.263 | 15.8221 | 13.2429 | 11.0832 | 9.7242 | 17.6513 | 17.2054 | 15.2491 | 14.5958 | 13.9301 | 13.2353 | 12.579 | 11.9004 | 11.3221 | 10.7683 | 10.2614 | 7.2328 | 4.5989 | 2.9468
| CASSLEY | RHICONICH | MINIMUM HEADROOM | NC 25554 52924 | YES | YES | -0.73318 | -0.77887 | -0.83719 | -0.89436 | -0.96143 | -1.0288 | -1.1073 | -1.1415 | -1.1764 | -1.218 | -1.2593 | -1.3524 | -1.5075 | -1.5783 | -0.45043 | -0.48376 | -0.51701 | -0.56817 | -0.60693 | -0.64629 | -0.69499 | -0.75052 | -0.8102 | -0.87014 | -0.92516 | -1.0143 | -1.0747 | -1.109 | -0.77285 | -0.8248 | -0.88408 | -0.95213 | -1.0209 | -1.0889 | -1.1718 | -1.2422 | -1.3175 | -1.3921 | -1.4617 | -1.5757 | -1.639 | -1.6955
|  | RHICONICH | CT |  |  |  | -0.70129 | -0.74077 | -0.81511 | -0.8922 | -0.96143 | -1.0288 | -1.1073 | -1.1415 | -1.1758 | -1.2147 | -1.2536 | -1.3415 | -1.4262 | -1.4584 | -0.4398 | -0.46757 | -0.51624 | -0.56817 | -0.60693 | -0.64629 | -0.68866 | -0.73195 | -0.78925 | -0.84905 | -0.90144 | -1.0143 | -1.0643 | -1.1057 | -0.74635 | -0.78726 | -0.86589 | -0.95213 | -1.0209 | -1.0889 | -1.1648 | -1.2192 | -1.289 | -1.3636 | -1.4286 | -1.5605 | -1.639 | -1.6747
|  | RHICONICH | LW |  |  |  | -0.73318 | -0.77887 | -0.83719 | -0.89436 | -0.94934 | -1.0176 | -1.091 | -1.1323 | -1.1764 | -1.218 | -1.2593 | -1.3455 | -1.3922 | -1.4105 | -0.45043 | -0.48376 | -0.51701 | -0.55335 | -0.58476 | -0.63627 | -0.69499 | -0.75052 | -0.8102 | -0.87014 | -0.92516 | -1.0069 | -1.0261 | -1.0326 | -0.77285 | -0.8248 | -0.88408 | -0.94606 | -1.0019 | -1.0824 | -1.1718 | -1.2422 | -1.3175 | -1.3921 | -1.4617 | -1.5757 | -1.6182 | -1.6332
|  | RHICONICH | ST |  |  |  | -0.66705 | -0.68322 | -0.70148 | -0.72597 | -0.75045 | -0.77804 | -0.8112 | -0.84821 | -0.89409 | -0.94062 | -0.99103 | -1.3524 | -1.5075 | -1.557 | -0.42427 | -0.43527 | -0.44888 | -0.46715 | -0.48665 | -0.50996 | -0.53813 | -0.57155 | -0.61259 | -0.65795 | -0.7081 | -0.97004 | -1.0747 | -1.1016 | -0.72006 | -0.73663 | -0.75663 | -0.7835 | -0.81115 | -0.84344 | -0.88242 | -0.92841 | -0.98529 | -1.0459 | -1.1122 | -1.4863 | -1.6321 | -1.6771
|  | RHICONICH | FS |  |  |  | -0.65699 | -0.67177 | -0.69204 | -0.71027 | -0.73126 | -0.75421 | -0.77923 | -0.81181 | -0.84494 | -0.88208 | -0.91611 | -1.1707 | -1.4095 | -1.5783 | -0.4202 | -0.42995 | -0.44252 | -0.45664 | -0.47202 | -0.48989 | -0.51045 | -0.53559 | -0.56347 | -0.59485 | -0.62789 | -0.85014 | -1.0399 | -1.109 | -0.71209 | -0.72705 | -0.74706 | -0.76774 | -0.79043 | -0.8162 | -0.84531 | -0.88285 | -0.92335 | -0.96859 | -1.0137 | -1.3266 | -1.5639 | -1.6955
| DUDHOPE | ROSEBANK STREET | MINIMUM HEADROOM | NO 39943 31150 | NO | NO | 9.2648 | 8.7786 | 7.7985 | 6.7919 | 5.7764 | 4.5944 | 3.3343 | 2.4792 | 1.5643 | 0.62747 | -0.27234 | -2.7639 | -4.973 | -6.0878 | 12.8021 | 12.5303 | 12.0964 | 11.5667 | 10.9879 | 10.3805 | 9.8055 | 9.2235 | 8.5483 | 7.8587 | 7.1112 | 3.8472 | 0.81739 | -7.9201 | 10.9874 | 10.546 | 9.6697 | 8.7656 | 7.856 | 6.7839 | 5.6346 | 4.8229 | 3.9541 | 3.0338 | 2.0958 | -0.40416 | -2.1878 | -3.2862
|  | ROSEBANK STREET | CT |  |  |  | 9.8706 | 9.6037 | 8.6014 | 7.5652 | 6.5644 | 5.5452 | 4.5532 | 3.7265 | 2.857 | 1.9821 | 1.0619 | -2.6468 | -4.973 | -6.0878 | 12.9343 | 12.6973 | 12.1496 | 11.5667 | 10.9879 | 10.3805 | 9.8055 | 9.2235 | 8.5483 | 7.8587 | 7.1112 | 3.8472 | 0.86671 | -3.228 | 11.5153 | 11.2677 | 10.3586 | 9.4155 | 8.4991 | 7.5616 | 6.6614 | 5.886 | 5.0725 | 4.2566 | 3.3953 | -0.064925 | -2.1878 | -3.2862
|  | ROSEBANK STREET | LW |  |  |  | 9.2648 | 8.7786 | 7.7985 | 6.7919 | 5.7764 | 4.5944 | 3.3343 | 2.4792 | 1.5643 | 0.62747 | -0.27234 | -2.7639 | -3.9101 | -5.1393 | 12.8021 | 12.5303 | 12.0964 | 11.6404 | 11.1814 | 10.5914 | 9.9417 | 9.331 | 8.6377 | 7.9267 | 7.2486 | 5.5264 | 4.5544 | 3.1313 | 10.9874 | 10.546 | 9.6697 | 8.7656 | 7.856 | 6.7839 | 5.6346 | 4.8229 | 3.9541 | 3.0338 | 2.0958 | -0.40416 | -1.6058 | -3.1437
|  | ROSEBANK STREET | ST |  |  |  | 10.223 | 10.1684 | 10.0868 | 9.9929 | 9.8811 | 9.6936 | 9.5241 | 9.2165 | 8.9013 | 8.5419 | 8.1244 | 4.9164 | 2.6192 | -0.0023907 | 13.0974 | 12.9907 | 12.829 | 12.6563 | 12.4664 | 12.1845 | 11.9046 | 11.4642 | 11.0283 | 10.5408 | 9.9752 | 6.3566 | 3.032 | -1.5577 | 11.8324 | 11.7836 | 11.6879 | 11.5843 | 11.4669 | 11.2609 | 11.0357 | 10.6505 | 10.2666 | 9.8333 | 9.33 | 5.927 | 3.7441 | 1.4677
|  | ROSEBANK STREET | FS |  |  |  | 10.2032 | 10.1514 | 10.026 | 9.8943 | 9.7442 | 9.5766 | 9.3887 | 9.0895 | 8.7771 | 8.432 | 8.0656 | 5.301 | 2.136 | -0.6583 | 13.0819 | 12.9679 | 12.8054 | 12.6236 | 12.4166 | 12.1775 | 11.9078 | 11.5405 | 11.1254 | 10.6474 | 10.1155 | 6.3749 | 0.81739 | -7.9201 | 11.814 | 11.7696 | 11.6524 | 11.526 | 11.3817 | 11.2197 | 11.0382 | 10.7491 | 10.4389 | 10.0722 | 9.6784 | 6.8918 | 3.8795 | 1.4962
| KEITH | ROTHES | MINIMUM HEADROOM | NJ 27901 49693 | NO | YES | 1.7805 | 1.6435 | 0.33969 | -1.1264 | -3.8116 | -6.6758 | -8.4208 | -8.9248 | -9.4573 | -9.9264 | -10.425 | -12.5943 | -13.223 | -13.4555 | 2.9383 | 2.8361 | 1.3701 | -0.30455 | -3.5373 | -6.9946 | -9.0494 | -9.6316 | -10.2447 | -10.7836 | -11.361 | -13.9499 | -14.6179 | -14.8463 | 1.5038 | 1.3756 | -0.17299 | -1.9147 | -5.2112 | -8.7289 | -10.8448 | -11.4458 | -12.0796 | -12.6371 | -13.2335 | -15.9124 | -16.6239 | -16.8635
|  | ROTHES | CT |  |  |  | 1.8788 | 1.7706 | 1.397 | 0.91553 | -0.43826 | -1.867 | -2.3792 | -2.6627 | -2.9602 | -3.2355 | -3.5273 | -4.6829 | -5.1238 | -5.3187 | 2.9383 | 2.8361 | 2.5277 | 2.0964 | 0.53554 | -1.1272 | -1.641 | -1.9478 | -2.2319 | -2.4913 | -2.8034 | -4.1039 | -4.4283 | -4.5531 | 1.5605 | 1.4366 | 1.0548 | 0.55268 | -1.0792 | -2.8097 | -3.394 | -3.7268 | -4.0373 | -4.322 | -4.6595 | -6.0465 | -6.4909 | -6.67
|  | ROTHES | LW |  |  |  | 1.7805 | 1.6435 | 0.33969 | -1.1264 | -3.8116 | -6.6758 | -8.4208 | -8.9248 | -9.4573 | -9.9264 | -10.425 | -12.5943 | -13.223 | -13.4555 | 2.9384 | 2.8532 | 1.3701 | -0.30455 | -3.5373 | -6.9946 | -9.0494 | -9.6316 | -10.2447 | -10.7836 | -11.361 | -13.9499 | -14.6179 | -14.8463 | 1.5038 | 1.3756 | -0.17299 | -1.9147 | -5.2112 | -8.7289 | -10.8448 | -11.4458 | -12.0796 | -12.6371 | -13.2335 | -15.9124 | -16.6239 | -16.8635
|  | ROTHES | ST |  |  |  | 1.9538 | 1.9008 | 0.77298 | -0.023441 | -0.55511 | -2.2397 | -2.7691 | -3.1891 | -3.4127 | -3.6537 | -4.0103 | -5.7917 | -6.4619 | -6.7265 | 2.9937 | 2.9569 | 1.5987 | 0.65358 | 0.016374 | -2.0584 | -2.6949 | -3.1937 | -3.45 | -3.7008 | -4.0439 | -5.7282 | -6.3181 | -6.5155 | 1.6439 | 1.5917 | 0.21322 | -0.75117 | -1.4054 | -3.4996 | -4.1533 | -4.6684 | -4.9409 | -5.2158 | -5.6018 | -7.5155 | -8.2234 | -8.4942
|  | ROTHES | FS |  |  |  | 2.0135 | 1.976 | 1.6952 | 1.4077 | 1.098 | 0.78363 | 0.50291 | 0.29628 | 0.12519 | -0.053389 | -0.24373 | -1.1154 | -1.9009 | -2.4192 | 3.041 | 3.013 | 2.7069 | 2.3954 | 2.0408 | 1.6799 | 1.3573 | 1.1449 | 0.97228 | 0.79141 | 0.59691 | -0.11864 | -0.69411 | -1.0582 | 1.7017 | 1.6644 | 1.3413 | 1.0116 | 0.63946 | 0.26133 | -0.076744 | -0.3133 | -0.50822 | -0.71211 | -0.92983 | -1.8274 | -2.5812 | -3.0728
| DUNOON | ROTHESAY | MINIMUM HEADROOM | NS 08636 64647 | NO | YES | 8.943 | 8.7509 | 8.3546 | 7.9399 | 7.534 | 7.0563 | 6.5436 | 6.1457 | 5.7271 | 5.2996 | 4.8866 | 3.401 | 2.2543 | 1.4045 | 10.4381 | 10.3367 | 10.1604 | 9.9693 | 9.7837 | 9.5335 | 9.2527 | 8.9979 | 8.7236 | 8.4404 | 8.1714 | 7.4132 | 6.787 | 6.114 | 9.4444 | 9.2617 | 8.9174 | 8.5533 | 8.1979 | 7.7621 | 7.2875 | 6.899 | 6.4869 | 6.0643 | 5.6588 | 4.3167 | 3.4875 | 2.8181
|  | ROTHESAY | CT |  |  |  | 9.1756 | 9.0788 | 8.7192 | 8.3237 | 7.9642 | 7.6054 | 7.2358 | 6.8739 | 6.4903 | 6.1115 | 5.7112 | 3.8208 | 2.2543 | 1.4045 | 10.5286 | 10.4566 | 10.258 | 10.0462 | 9.8696 | 9.6889 | 9.5006 | 9.2903 | 9.0588 | 8.8262 | 8.5764 | 7.5658 | 6.787 | 6.114 | 9.6527 | 9.5558 | 9.2107 | 8.8507 | 8.5332 | 8.2143 | 7.8851 | 7.5491 | 7.1878 | 6.8295 | 6.4499 | 4.7764 | 3.4875 | 2.8181
|  | ROTHESAY | LW |  |  |  | 8.943 | 8.7509 | 8.3546 | 7.9399 | 7.534 | 7.0563 | 6.5436 | 6.1457 | 5.7271 | 5.2996 | 4.8866 | 3.401 | 2.5514 | 2.1905 | 10.4381 | 10.3367 | 10.1604 | 9.9693 | 9.7837 | 9.5335 | 9.2527 | 8.9979 | 8.7236 | 8.4404 | 8.1714 | 7.4132 | 7.1049 | 6.8822 | 9.4444 | 9.2617 | 8.9174 | 8.5533 | 8.1979 | 7.7621 | 7.2875 | 6.899 | 6.4869 | 6.0643 | 5.6588 | 4.3167 | 3.6176 | 3.2674
|  | ROTHESAY | ST |  |  |  | 9.2584 | 9.2258 | 9.1829 | 9.1258 | 9.0633 | 8.9835 | 8.8883 | 8.7722 | 8.6307 | 8.4737 | 8.2958 | 6.9994 | 6.1271 | 4.7818 | 10.5779 | 10.5532 | 10.5161 | 10.468 | 10.4136 | 10.3458 | 10.2649 | 10.1674 | 10.0495 | 9.9169 | 9.7672 | 8.8054 | 8.1607 | 7.3138 | 9.7374 | 9.7048 | 9.6617 | 9.6049 | 9.5435 | 9.4649 | 9.3721 | 9.2592 | 9.1221 | 8.9704 | 8.7985 | 7.5408 | 6.6726 | 5.5693
|  | ROTHESAY | FS |  |  |  | 9.2659 | 9.2413 | 9.1906 | 9.1331 | 9.0717 | 8.9998 | 8.9174 | 8.7877 | 8.6466 | 8.497 | 8.33 | 7.0297 | 5.6997 | 4.5495 | 10.5815 | 10.5611 | 10.5223 | 10.4755 | 10.4243 | 10.3639 | 10.2942 | 10.1942 | 10.0829 | 9.9612 | 9.8261 | 8.8526 | 7.679 | 6.325 | 9.7451 | 9.7205 | 9.6679 | 9.6087 | 9.546 | 9.4733 | 9.3904 | 9.2572 | 9.1133 | 8.9613 | 8.7955 | 7.5601 | 6.327 | 5.3475
| THURSO | ROUSAY | MINIMUM HEADROOM | HY 43876 30573 | YES | YES | 0.54647 | 0.53329 | 0.51556 | 0.49339 | 0.4721 | 0.45048 | 0.43018 | 0.39652 | 0.3526 | 0.31154 | 0.26898 | 0.092845 | -0.28116 | -0.79861 | 0.65517 | 0.64642 | 0.63448 | 0.62035 | 0.60898 | 0.59731 | 0.58584 | 0.54384 | 0.49513 | 0.45143 | 0.40543 | 0.21679 | -0.24147 | -0.88586 | 0.72341 | 0.71205 | 0.69698 | 0.68122 | 0.66373 | 0.64585 | 0.62886 | 0.59417 | 0.54539 | 0.50163 | 0.45568 | 0.27011 | -0.1896 | -0.83606
|  | ROUSAY | CT |  |  |  | 0.54647 | 0.53896 | 0.51569 | 0.49339 | 0.4721 | 0.45048 | 0.43018 | 0.39763 | 0.36482 | 0.33136 | 0.29745 | 0.17433 | -0.012865 | -0.22362 | 0.65624 | 0.64939 | 0.63448 | 0.62035 | 0.60898 | 0.59731 | 0.58584 | 0.55029 | 0.51233 | 0.47642 | 0.43988 | 0.29018 | 0.065797 | -0.19908 | 0.7245 | 0.71788 | 0.69698 | 0.68122 | 0.66373 | 0.64585 | 0.62886 | 0.59545 | 0.56542 | 0.52874 | 0.49157 | 0.34577 | 0.11961 | -0.14136
|  | ROUSAY | LW |  |  |  | 0.54676 | 0.53329 | 0.51556 | 0.50031 | 0.48423 | 0.46298 | 0.43736 | 0.39652 | 0.3526 | 0.31154 | 0.26898 | 0.092845 | -0.28116 | -0.79861 | 0.65517 | 0.64642 | 0.63718 | 0.62812 | 0.61937 | 0.60592 | 0.58981 | 0.54384 | 0.49513 | 0.45143 | 0.40543 | 0.21679 | -0.24147 | -0.88586 | 0.72341 | 0.71205 | 0.69787 | 0.68621 | 0.67283 | 0.65647 | 0.63655 | 0.59417 | 0.54539 | 0.50163 | 0.45568 | 0.27011 | -0.1896 | -0.83606
|  | ROUSAY | ST |  |  |  | 0.54875 | 0.54722 | 0.54506 | 0.54233 | 0.53898 | 0.5348 | 0.52974 | 0.4798 | 0.45654 | 0.42711 | 0.38738 | 0.18596 | -0.11051 | -0.41229 | 0.66185 | 0.66028 | 0.65757 | 0.65421 | 0.65001 | 0.64442 | 0.63941 | 0.57695 | 0.54781 | 0.52089 | 0.48294 | 0.29736 | -0.047585 | -0.4257 | 0.73325 | 0.73207 | 0.73045 | 0.72824 | 0.72578 | 0.72056 | 0.7164 | 0.6533 | 0.6234 | 0.59641 | 0.55881 | 0.37409 | 0.031499 | -0.34549
|  | ROUSAY | FS |  |  |  | 0.5493 | 0.54816 | 0.54665 | 0.54479 | 0.54263 | 0.54004 | 0.53324 | 0.51121 | 0.49188 | 0.474 | 0.45594 | 0.37359 | 0.28803 | 0.20925 | 0.66226 | 0.66054 | 0.65752 | 0.65466 | 0.65133 | 0.64712 | 0.64101 | 0.61615 | 0.59637 | 0.5766 | 0.55621 | 0.48727 | 0.4211 | 0.35895 | 0.73351 | 0.73255 | 0.73129 | 0.72961 | 0.72577 | 0.72045 | 0.71203 | 0.68651 | 0.66573 | 0.64588 | 0.62538 | 0.55267 | 0.49128 | 0.43818
| CRAIGIEBUCKLER | RUTHRIESTON | MINIMUM HEADROOM | NJ 92574 04060 | NO | YES | 14.0829 | 13.6519 | 12.7464 | 11.7799 | 10.6308 | 9.234 | 7.8463 | 6.7578 | 5.5942 | 4.3525 | 3.1085 | -0.048369 | -1.0025 | -2.4862 | 17.5427 | 17.2364 | 16.6383 | 15.9769 | 15.0844 | 13.9594 | 12.9521 | 12.1495 | 11.239 | 10.3057 | 9.4059 | 7.1826 | 6.3902 | 3.4031 | 15.8517 | 15.4133 | 14.5214 | 13.5569 | 12.3633 | 10.8881 | 9.4856 | 8.3534 | 7.1353 | 5.8851 | 4.6742 | 1.6079 | 0.61576 | -0.97369
|  | RUTHRIESTON | CT |  |  |  | 14.4241 | 14.1685 | 13.3776 | 12.5322 | 11.6174 | 10.6313 | 9.8074 | 8.9181 | 7.9836 | 7.05 | 6.0528 | 2.4436 | 0.98639 | 0.18048 | 17.6211 | 17.3893 | 16.8746 | 16.2979 | 15.6024 | 14.8496 | 14.299 | 13.6879 | 13.0293 | 12.3288 | 11.5614 | 8.7213 | 6.9971 | 4.8586 | 16.1381 | 15.868 | 15.1018 | 14.2685 | 13.3416 | 12.3518 | 11.5568 | 10.6794 | 9.747 | 8.8157 | 7.8124 | 4.3631 | 3.0055 | 2.2402
|  | RUTHRIESTON | LW |  |  |  | 14.0829 | 13.6519 | 12.7464 | 11.7799 | 10.6308 | 9.234 | 7.8463 | 6.7578 | 5.5942 | 4.3525 | 3.1085 | -0.048369 | -1.0025 | -2.4862 | 17.5427 | 17.2364 | 16.6383 | 15.9769 | 15.0844 | 13.9594 | 12.9521 | 12.1495 | 11.239 | 10.3057 | 9.4059 | 7.1826 | 6.3902 | 4.9941 | 15.8517 | 15.4133 | 14.5214 | 13.5569 | 12.3633 | 10.8881 | 9.4856 | 8.3534 | 7.1353 | 5.8851 | 4.6742 | 1.6079 | 0.61576 | -0.97369
|  | RUTHRIESTON | ST |  |  |  | 14.5954 | 14.5021 | 14.1897 | 13.9042 | 13.6338 | 13.1115 | 12.7181 | 12.2866 | 11.7998 | 11.2526 | 10.5843 | 6.422 | 4.3231 | 2.7821 | 17.7354 | 17.6299 | 17.2647 | 16.9407 | 16.639 | 16.0371 | 15.6401 | 15.2286 | 14.7854 | 14.2868 | 13.6751 | 10.0862 | 7.7772 | 5.2568 | 16.3067 | 16.2051 | 15.8369 | 15.5064 | 15.1978 | 14.5824 | 14.1307 | 13.6547 | 13.1256 | 12.5301 | 11.8479 | 7.8024 | 5.7801 | 4.3113
|  | RUTHRIESTON | FS |  |  |  | 14.6215 | 14.544 | 14.3856 | 14.2025 | 13.9989 | 13.766 | 13.5073 | 13.1877 | 12.8128 | 12.4024 | 11.9544 | 8.7832 | 5.4543 | 3.2081 | 17.7476 | 17.6513 | 17.4794 | 17.2812 | 17.0553 | 16.7967 | 16.5115 | 16.194 | 15.8424 | 15.4499 | 15.0129 | 11.9553 | 8.0556 | 3.4031 | 16.3336 | 16.25 | 16.0788 | 15.8804 | 15.6574 | 15.4024 | 15.12 | 14.7785 | 14.3908 | 13.9641 | 13.4961 | 10.35 | 7.1881 | 5.1154
| FORT WILLIAM | SALEN | MINIMUM HEADROOM | NM 69002 65519 | NO | YES | 6.4942 | 6.419 | 6.3642 | 6.2944 | 6.2218 | 6.1401 | 6.0636 | 5.9881 | 5.9014 | 5.8136 | 5.7329 | 5.5818 | 5.5419 | 5.5181 | 6.6428 | 6.5976 | 6.565 | 6.509 | 6.4664 | 6.4191 | 6.3735 | 6.313 | 6.2448 | 6.175 | 6.111 | 5.9985 | 5.9709 | 5.9266 | 2.3508 | 2.2805 | 2.2268 | 2.1557 | 2.0848 | 2.0051 | 1.9301 | 1.8568 | 1.7712 | 1.6843 | 1.6044 | 1.4526 | 1.4115 | 1.388
|  | SALEN | CT |  |  |  | 6.5279 | 6.4643 | 6.3832 | 6.2944 | 6.2218 | 6.1401 | 6.0636 | 6.003 | 5.9222 | 5.8454 | 5.7721 | 5.6295 | 5.561 | 5.5262 | 6.6569 | 6.6169 | 6.5656 | 6.509 | 6.4664 | 6.4191 | 6.3735 | 6.3259 | 6.2627 | 6.2003 | 6.1429 | 6.019 | 5.9709 | 5.9276 | 2.3824 | 2.323 | 2.2429 | 2.1557 | 2.0848 | 2.0051 | 1.9301 | 1.8701 | 1.7908 | 1.7149 | 1.6425 | 1.4999 | 1.4319 | 1.3959
|  | SALEN | LW |  |  |  | 6.4942 | 6.419 | 6.3642 | 6.3019 | 6.2465 | 6.1624 | 6.0675 | 5.9881 | 5.9014 | 5.8136 | 5.7329 | 5.5818 | 5.5419 | 5.5181 | 6.6428 | 6.5976 | 6.565 | 6.5273 | 6.4945 | 6.4393 | 6.3756 | 6.313 | 6.2448 | 6.175 | 6.111 | 5.9985 | 5.9766 | 5.9626 | 2.3508 | 2.2805 | 2.2268 | 2.1656 | 2.1109 | 2.0284 | 1.9351 | 1.8568 | 1.7712 | 1.6843 | 1.6044 | 1.4526 | 1.4115 | 1.388
|  | SALEN | ST |  |  |  | 6.5581 | 6.5255 | 6.5074 | 6.4814 | 6.4498 | 6.4129 | 6.3723 | 6.3255 | 6.2681 | 6.2032 | 6.1352 | 5.7873 | 5.704 | 5.6735 | 6.672 | 6.6526 | 6.6397 | 6.6215 | 6.5996 | 6.5734 | 6.5435 | 6.5084 | 6.4655 | 6.4166 | 6.3635 | 6.087 | 6.0142 | 5.9766 | 2.4113 | 2.3821 | 2.3638 | 2.3381 | 2.3071 | 2.2712 | 2.2312 | 2.185 | 2.1283 | 2.0639 | 1.9965 | 1.6486 | 1.5613 | 1.5287
|  | SALEN | FS |  |  |  | 6.5743 | 6.5442 | 6.5222 | 6.4967 | 6.4725 | 6.4433 | 6.411 | 6.3785 | 6.3357 | 6.2928 | 6.2466 | 5.9366 | 5.6809 | 5.6045 | 6.6799 | 6.6621 | 6.6484 | 6.6321 | 6.6157 | 6.5961 | 6.5739 | 6.5498 | 6.5201 | 6.4885 | 6.4537 | 6.2234 | 6.0131 | 5.9266 | 2.426 | 2.3996 | 2.3784 | 2.3535 | 2.3297 | 2.3009 | 2.269 | 2.2369 | 2.1948 | 2.1523 | 2.1063 | 1.7993 | 1.5455 | 1.4675
| TAYNUILT | SALEN 2 | MINIMUM HEADROOM | NM 57252 42849 | YES | YES | 0.090202 | 0.04035 | -0.022078 | -0.095054 | -0.17339 | -0.25081 | -0.32755 | -0.38759 | -0.45713 | -0.52612 | -0.58967 | -0.69823 | -0.76262 | -0.7971 | 0.51805 | 0.48711 | 0.45384 | 0.40368 | 0.3627 | 0.32115 | 0.27672 | 0.22637 | 0.17134 | 0.11597 | 0.065473 | -0.014006 | -0.060093 | -0.09224 | 0.46967 | 0.42267 | 0.36524 | 0.29562 | 0.22391 | 0.15278 | 0.082277 | 0.020313 | -0.048441 | -0.11685 | -0.17973 | -0.28442 | -0.34246 | -0.37392
|  | SALEN 2 | CT |  |  |  | 0.12407 | 0.082844 | -0.0058307 | -0.095054 | -0.17339 | -0.25081 | -0.32755 | -0.3762 | -0.44053 | -0.50746 | -0.56314 | -0.67973 | -0.76262 | -0.7971 | 0.5306 | 0.50457 | 0.45484 | 0.40368 | 0.3627 | 0.32115 | 0.27993 | 0.24059 | 0.18789 | 0.13356 | 0.08707 | -0.014006 | -0.060093 | -0.09224 | 0.4996 | 0.46075 | 0.37861 | 0.29562 | 0.22391 | 0.15278 | 0.082277 | 0.034122 | -0.029901 | -0.096377 | -0.15189 | -0.26796 | -0.34246 | -0.37392
|  | SALEN 2 | LW |  |  |  | 0.090202 | 0.04035 | -0.022078 | -0.087561 | -0.14859 | -0.23347 | -0.3249 | -0.38759 | -0.45713 | -0.52612 | -0.58967 | -0.69823 | -0.73711 | -0.75399 | 0.51805 | 0.48711 | 0.45384 | 0.41746 | 0.3852 | 0.33396 | 0.27672 | 0.22637 | 0.17134 | 0.11597 | 0.065473 | -0.011452 | -0.028749 | -0.03577 | 0.46967 | 0.42267 | 0.36524 | 0.3046 | 0.24853 | 0.16885 | 0.08248 | 0.020313 | -0.048441 | -0.11685 | -0.17973 | -0.28442 | -0.31914 | -0.334
|  | SALEN 2 | ST |  |  |  | 0.14555 | 0.12989 | 0.10545 | 0.077951 | 0.048686 | 0.014775 | -0.025289 | -0.071528 | -0.1255 | -0.18691 | -0.25008 | -0.57689 | -0.6696 | -0.71367 | 0.5422 | 0.53239 | 0.51809 | 0.50079 | 0.48192 | 0.4594 | 0.43247 | 0.40046 | 0.36223 | 0.31852 | 0.27164 | 0.027849 | -0.037267 | -0.070488 | 0.51933 | 0.50465 | 0.48193 | 0.45604 | 0.42839 | 0.39618 | 0.35803 | 0.31371 | 0.26174 | 0.20255 | 0.14119 | -0.17619 | -0.26306 | -0.30213
|  | SALEN 2 | FS |  |  |  | 0.15661 | 0.14429 | 0.11936 | 0.098495 | 0.072475 | 0.046801 | 0.016645 | -0.017655 | -0.059635 | -0.09955 | -0.14854 | -0.45752 | -0.68771 | -0.74833 | 0.54696 | 0.53905 | 0.52566 | 0.51246 | 0.49694 | 0.48033 | 0.46073 | 0.43801 | 0.41081 | 0.3828 | 0.34984 | 0.13935 | -0.035123 | -0.08977 | 0.52922 | 0.51766 | 0.49479 | 0.47515 | 0.4509 | 0.42665 | 0.39813 | 0.36555 | 0.32581 | 0.28749 | 0.24081 | -0.054015 | -0.27644 | -0.33203
| THURSO | SANDAY | MINIMUM HEADROOM | HY 61184 35797 | YES | YES | 0.32363 | 0.28407 | 0.24042 | 0.18871 | 0.12997 | 0.070982 | 0.0081529 | -0.038932 | -0.091548 | -0.14739 | -0.20085 | -0.34924 | -0.48978 | -0.52226 | 0.56948 | 0.54574 | 0.52126 | 0.48519 | 0.45378 | 0.42066 | 0.38675 | 0.35179 | 0.3078 | 0.26199 | 0.21532 | 0.0074553 | -0.098286 | -0.1215 | 0.43949 | 0.40257 | 0.36253 | 0.31303 | 0.25927 | 0.20488 | 0.14727 | 0.099479 | 0.044115 | -0.014107 | -0.06805 | -0.27558 | -0.41072 | -0.44156
|  | SANDAY | CT |  |  |  | 0.34641 | 0.31594 | 0.25129 | 0.18871 | 0.12997 | 0.070982 | 0.0081529 | -0.030264 | -0.077557 | -0.12627 | -0.16894 | -0.29167 | -0.35319 | -0.37907 | 0.57744 | 0.55749 | 0.52126 | 0.48519 | 0.45378 | 0.42066 | 0.38675 | 0.35734 | 0.31979 | 0.27969 | 0.24437 | 0.12394 | 0.11101 | 0.092748 | 0.45947 | 0.43072 | 0.37105 | 0.31303 | 0.25927 | 0.20488 | 0.14727 | 0.10993 | 0.060695 | 0.0093159 | -0.035482 | -0.15554 | -0.21063 | -0.23388
|  | SANDAY | LW |  |  |  | 0.32363 | 0.28407 | 0.24042 | 0.19183 | 0.14428 | 0.084983 | 0.012633 | -0.038932 | -0.091548 | -0.14739 | -0.20085 | -0.32073 | -0.36074 | -0.38 | 0.56948 | 0.54574 | 0.52232 | 0.49581 | 0.47078 | 0.4344 | 0.39054 | 0.35179 | 0.3078 | 0.26199 | 0.21532 | 0.087723 | 0.071445 | 0.058556 | 0.43949 | 0.40257 | 0.36253 | 0.31785 | 0.27439 | 0.21881 | 0.15112 | 0.099479 | 0.044115 | -0.014107 | -0.06805 | -0.19763 | -0.23001 | -0.2492
|  | SANDAY | ST |  |  |  | 0.36998 | 0.35677 | 0.33576 | 0.31494 | 0.29129 | 0.26083 | 0.22748 | 0.18593 | 0.13926 | 0.087245 | 0.031059 | -0.34924 | -0.48978 | -0.52226 | 0.58937 | 0.58136 | 0.56945 | 0.55625 | 0.54096 | 0.52155 | 0.4992 | 0.47003 | 0.42665 | 0.37615 | 0.31836 | 0.0074553 | -0.098286 | -0.1215 | 0.4809 | 0.46864 | 0.44931 | 0.4298 | 0.40758 | 0.37886 | 0.34619 | 0.30176 | 0.24807 | 0.18644 | 0.11652 | -0.27558 | -0.41072 | -0.44156
|  | SANDAY | FS |  |  |  | 0.37742 | 0.36948 | 0.34893 | 0.33337 | 0.31333 | 0.28933 | 0.26306 | 0.23573 | 0.20372 | 0.16898 | 0.13298 | -0.12173 | -0.32634 | -0.46879 | 0.59284 | 0.5874 | 0.57675 | 0.56706 | 0.55521 | 0.541 | 0.52493 | 0.50733 | 0.48676 | 0.46398 | 0.43941 | 0.2445 | 0.04548 | -0.075867 | 0.48691 | 0.48013 | 0.46145 | 0.44693 | 0.42837 | 0.40611 | 0.38161 | 0.35543 | 0.32454 | 0.29078 | 0.25531 | 0.004119 | -0.23428 | -0.3837
| DUNOON | SANDBANK | MINIMUM HEADROOM | NS 15274 81386 | NO | YES | 4.3287 | 4.2331 | 4.1121 | 3.9859 | 3.86 | 3.698 | 3.5136 | 3.351 | 3.1806 | 3.0033 | 2.8401 | 2.5132 | 2.2611 | 2.1264 | 5.1159 | 5.0579 | 4.9892 | 4.9079 | 4.8086 | 4.7049 | 4.6209 | 4.528 | 4.4098 | 4.2901 | 4.1811 | 3.8789 | 3.6739 | 3.4997 | 4.2266 | 4.1907 | 4.1085 | 4.0285 | 3.9334 | 3.8114 | 3.6388 | 3.4931 | 3.3422 | 3.174 | 3.0135 | 2.6682 | 2.3822 | 2.2266
|  | SANDBANK | CT |  |  |  | 4.3913 | 4.3228 | 4.1708 | 4.0064 | 3.86 | 3.7082 | 3.5724 | 3.4381 | 3.2631 | 3.0851 | 2.9267 | 2.5184 | 2.2611 | 2.1264 | 5.1459 | 5.102 | 5.0093 | 4.9079 | 4.8086 | 4.7049 | 4.6209 | 4.5283 | 4.4098 | 4.2901 | 4.1811 | 3.8789 | 3.6739 | 3.4997 | 4.2369 | 4.2134 | 4.1557 | 4.0558 | 3.9458 | 3.8183 | 3.6821 | 3.5552 | 3.3948 | 3.2322 | 3.0773 | 2.6682 | 2.3822 | 2.2266
|  | SANDBANK | LW |  |  |  | 4.3287 | 4.2331 | 4.1121 | 3.9859 | 3.8651 | 3.698 | 3.5136 | 3.351 | 3.1806 | 3.0033 | 2.8401 | 2.5132 | 2.3146 | 2.1344 | 5.1159 | 5.0579 | 4.9892 | 4.9161 | 4.8473 | 4.7471 | 4.6351 | 4.528 | 4.4148 | 4.298 | 4.19 | 3.9753 | 3.8093 | 3.6217 | 4.2266 | 4.1907 | 4.1085 | 4.0285 | 3.9334 | 3.8114 | 3.6388 | 3.4931 | 3.3422 | 3.174 | 3.0135 | 2.6935 | 2.4637 | 2.2523
|  | SANDBANK | ST |  |  |  | 4.4513 | 4.4254 | 4.3755 | 4.3167 | 4.2648 | 4.1824 | 4.1069 | 4.0105 | 3.9091 | 3.7985 | 3.6725 | 3.0249 | 2.7701 | 2.5607 | 5.1816 | 5.1644 | 5.1206 | 5.0754 | 5.0357 | 4.9644 | 4.91 | 4.8334 | 4.7619 | 4.6843 | 4.5941 | 4.1266 | 3.8947 | 3.6718 | 4.2735 | 4.268 | 4.2388 | 4.2119 | 4.1914 | 4.142 | 4.113 | 4.0643 | 3.9987 | 3.8888 | 3.7626 | 3.1164 | 2.857 | 2.6465
|  | SANDBANK | FS |  |  |  | 4.4629 | 4.4427 | 4.4063 | 4.3626 | 4.3168 | 4.267 | 4.2107 | 4.1368 | 4.0621 | 3.9794 | 3.8924 | 3.3115 | 2.845 | 2.6884 | 5.1881 | 5.1739 | 5.1485 | 5.1184 | 5.0862 | 5.051 | 5.0118 | 4.9594 | 4.9068 | 4.8488 | 4.7869 | 4.3958 | 4.0401 | 3.8293 | 4.2775 | 4.2737 | 4.2627 | 4.2498 | 4.2351 | 4.2193 | 4.2017 | 4.1747 | 4.1391 | 4.0901 | 4.0044 | 3.4444 | 2.9924 | 2.8481
| SHETLAND | SANDWICK | MINIMUM HEADROOM | HU4308625957 | YES | YES | 2.8 | 2.8 | 2.7874 | 2.7789 | 2.7733 | 2.754 | 2.7486 | 2.6906 | 2.6701 | 2.6526 | 2.6248 | 2.4943 | 2.1276 | 1.5281 | 1.6488 | 1.6336 | 1.6162 | 1.5898 | 1.5587 | 1.5258 | 1.5067 | 1.4474 | 1.3797 | 1.3141 | 1.2519 | 0.99841 | 0.51659 | -0.2328 | 1.6733 | 1.6544 | 1.6342 | 1.6026 | 1.5686 | 1.5325 | 1.5104 | 1.447 | 1.3696 | 1.2956 | 1.2265 | 0.96578 | 0.45464 | -0.30414
|  | SANDWICK | CT |  |  |  | 2.8 | 2.8 | 2.7984 | 2.7955 | 2.7815 | 2.7666 | 2.7628 | 2.7364 | 2.71 | 2.6871 | 2.6619 | 2.5284 | 2.3266 | 2.0887 | 1.6508 | 1.6389 | 1.6162 | 1.5898 | 1.5587 | 1.5258 | 1.5067 | 1.4489 | 1.3797 | 1.3141 | 1.2519 | 1.0241 | 0.75815 | 0.4453 | 1.6761 | 1.6616 | 1.6342 | 1.6026 | 1.5686 | 1.5325 | 1.5104 | 1.447 | 1.3696 | 1.2956 | 1.2265 | 0.98739 | 0.70566 | 0.35109
|  | SANDWICK | LW |  |  |  | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.7716 | 2.7422 | 2.718 | 2.6908 | 2.5476 | 2.1276 | 1.5281 | 1.6488 | 1.6336 | 1.6206 | 1.6049 | 1.593 | 1.5686 | 1.5398 | 1.471 | 1.3985 | 1.3318 | 1.2648 | 1.0447 | 0.51659 | -0.2328 | 1.6733 | 1.6544 | 1.6383 | 1.619 | 1.6043 | 1.5741 | 1.5385 | 1.4618 | 1.3808 | 1.3055 | 1.2308 | 1.0009 | 0.45464 | -0.30414
|  | SANDWICK | ST |  |  |  | 2.8 | 2.8 | 2.7874 | 2.7789 | 2.7733 | 2.754 | 2.7486 | 2.6906 | 2.6701 | 2.6526 | 2.6248 | 2.4943 | 2.1834 | 1.8395 | 1.6539 | 1.6492 | 1.6272 | 1.608 | 1.5921 | 1.5568 | 1.5366 | 1.4474 | 1.4014 | 1.3564 | 1.2956 | 0.99841 | 0.58434 | 0.14507 | 1.6798 | 1.6744 | 1.6511 | 1.6301 | 1.6123 | 1.5746 | 1.5515 | 1.4587 | 1.4082 | 1.358 | 1.2916 | 0.96578 | 0.55175 | 0.12115
|  | SANDWICK | FS |  |  |  | 2.8 | 2.8 | 2.7974 | 2.7949 | 2.7919 | 2.7889 | 2.7863 | 2.7653 | 2.7511 | 2.7368 | 2.7226 | 2.7053 | 2.6879 | 2.6495 | 1.6546 | 1.6507 | 1.6424 | 1.6325 | 1.6221 | 1.6102 | 1.5974 | 1.5596 | 1.5285 | 1.4957 | 1.461 | 1.3316 | 1.2138 | 1.1488 | 1.6808 | 1.6763 | 1.667 | 1.6557 | 1.644 | 1.6305 | 1.6157 | 1.5756 | 1.5418 | 1.5058 | 1.4677 | 1.3168 | 1.1852 | 1.1339
| SHETLAND | SCALLOWAY | MINIMUM HEADROOM | HU4139939639 | YES | YES | -3.4354 | -3.5419 | -3.6819 | -3.8276 | -3.9749 | -4.1428 | -4.3278 | -4.477 | -4.6264 | -4.7826 | -4.9249 | -5.2482 | -5.6941 | -6.2491 | -1.6744 | -1.7086 | -1.7436 | -1.7882 | -1.8273 | -1.8692 | -1.9299 | -2.0188 | -2.1123 | -2.203 | -2.2919 | -2.5747 | -3.0632 | -3.7294 | -4.2531 | -4.3644 | -4.4968 | -4.6414 | -4.7904 | -4.9471 | -5.1493 | -5.3407 | -5.5378 | -5.739 | -5.9246 | -6.3246 | -6.8514 | -7.5353
|  | SCALLOWAY | CT |  |  |  | -3.3621 | -3.4384 | -3.6239 | -3.8155 | -3.9749 | -4.1428 | -4.3075 | -4.4193 | -4.5517 | -4.6912 | -4.8183 | -5.0922 | -5.4233 | -5.6992 | -1.6648 | -1.6933 | -1.7436 | -1.7882 | -1.8273 | -1.869 | -1.9115 | -1.9782 | -2.0436 | -2.1067 | -2.1801 | -2.4963 | -2.8458 | -3.2513 | -4.19 | -4.2702 | -4.4512 | -4.6414 | -4.7904 | -4.9471 | -5.1014 | -5.244 | -5.4226 | -5.6069 | -5.7724 | -6.1479 | -6.5052 | -6.8316
|  | SCALLOWAY | LW |  |  |  | -3.4354 | -3.5419 | -3.6819 | -3.8276 | -3.9601 | -4.1365 | -4.3278 | -4.477 | -4.6264 | -4.7826 | -4.9249 | -5.2482 | -5.6941 | -6.2491 | -1.6744 | -1.7086 | -1.7431 | -1.7809 | -1.8158 | -1.8692 | -1.9299 | -2.0188 | -2.1123 | -2.203 | -2.2919 | -2.5747 | -3.0632 | -3.7294 | -4.2531 | -4.3644 | -4.4968 | -4.6383 | -4.764 | -4.9467 | -5.1493 | -5.3407 | -5.5378 | -5.739 | -5.9246 | -6.3246 | -6.8514 | -7.5353
|  | SCALLOWAY | ST |  |  |  | -3.271 | -3.2968 | -3.3309 | -3.3733 | -3.4157 | -3.4661 | -3.5245 | -3.6417 | -3.7428 | -3.8477 | -3.9752 | -4.5963 | -4.979 | -5.3281 | -1.6451 | -1.6561 | -1.6708 | -1.6889 | -1.7081 | -1.7314 | -1.759 | -1.846 | -1.904 | -1.9639 | -2.0393 | -2.4182 | -2.8244 | -3.2757 | -4.1158 | -4.1445 | -4.1827 | -4.2311 | -4.2812 | -4.3412 | -4.4117 | -4.554 | -4.6773 | -4.8079 | -4.9643 | -5.7178 | -6.1793 | -6.6158
|  | SCALLOWAY | FS |  |  |  | -3.2716 | -3.2906 | -3.335 | -3.3816 | -3.4264 | -3.4791 | -3.5364 | -3.6126 | -3.6906 | -3.7689 | -3.8536 | -4.3907 | -4.7797 | -4.9048 | -1.6432 | -1.6521 | -1.6666 | -1.6828 | -1.699 | -1.7182 | -1.7397 | -1.7826 | -1.8218 | -1.8631 | -1.9075 | -2.1262 | -2.4276 | -2.728 | -4.1143 | -4.1363 | -4.1804 | -4.2291 | -4.277 | -4.3335 | -4.3963 | -4.4846 | -4.5753 | -4.6694 | -4.7716 | -5.3905 | -5.8642 | -5.9857
| TAYNUILT | SCAMMADALE | MINIMUM HEADROOM | NM 84207 19638 | YES | YES | 0.045586 | 0.042977 | 0.043546 | 0.040539 | 0.037962 | 0.036838 | 0.030815 | 0.029414 | 0.028905 | 0.02639 | 0.024121 | 0.020507 | 0.019534 | 0.01784 | 0.054671 | 0.0533 | 0.053287 | 0.051496 | 0.050214 | 0.049364 | 0.046886 | 0.044914 | 0.043426 | 0.041455 | 0.039676 | 0.037365 | 0.036598 | 0.035863 | 0.046757 | 0.044282 | 0.044781 | 0.041863 | 0.039551 | 0.038462 | 0.0331 | 0.031487 | 0.030342 | 0.027918 | 0.025717 | 0.022219 | 0.021106 | 0.019419
|  | SCAMMADALE | CT |  |  |  | 0.047112 | 0.047541 | 0.044797 | 0.040539 | 0.037962 | 0.037167 | 0.030815 | 0.029414 | 0.030432 | 0.027991 | 0.025895 | 0.020507 | 0.019741 | 0.01784 | 0.055451 | 0.055439 | 0.053802 | 0.051496 | 0.050214 | 0.049478 | 0.046886 | 0.045732 | 0.044699 | 0.04272 | 0.041078 | 0.037365 | 0.036778 | 0.035863 | 0.048224 | 0.048507 | 0.045938 | 0.041863 | 0.039551 | 0.038728 | 0.0331 | 0.031707 | 0.03188 | 0.029481 | 0.02745 | 0.022219 | 0.021344 | 0.019419
|  | SCAMMADALE | LW |  |  |  | 0.045586 | 0.042977 | 0.043546 | 0.042355 | 0.040075 | 0.036838 | 0.035186 | 0.029592 | 0.028905 | 0.02639 | 0.024121 | 0.021279 | 0.019534 | 0.019534 | 0.054671 | 0.0533 | 0.053287 | 0.052417 | 0.051226 | 0.049364 | 0.047825 | 0.044914 | 0.043426 | 0.041455 | 0.039676 | 0.03744 | 0.036598 | 0.036598 | 0.046757 | 0.044282 | 0.044781 | 0.043515 | 0.041403 | 0.038462 | 0.036559 | 0.031487 | 0.030342 | 0.027918 | 0.025717 | 0.022954 | 0.021106 | 0.021106
|  | SCAMMADALE | ST |  |  |  | 0.047316 | 0.04703 | 0.047854 | 0.047315 | 0.047937 | 0.045832 | 0.043568 | 0.042445 | 0.038495 | 0.038126 | 0.036359 | 0.024387 | 0.024028 | 0.025206 | 0.055595 | 0.055403 | 0.055687 | 0.055264 | 0.055248 | 0.054112 | 0.052852 | 0.05197 | 0.049862 | 0.049069 | 0.047683 | 0.039331 | 0.038552 | 0.038972 | 0.048426 | 0.048141 | 0.048818 | 0.048281 | 0.048755 | 0.046823 | 0.044692 | 0.043603 | 0.039824 | 0.039357 | 0.037643 | 0.025912 | 0.025337 | 0.02637
|  | SCAMMADALE | FS |  |  |  | 0.047343 | 0.047132 | 0.048035 | 0.04625 | 0.045659 | 0.045132 | 0.044504 | 0.043738 | 0.042846 | 0.040467 | 0.037967 | 0.027876 | 0.021587 | 0.022767 | 0.05563 | 0.055472 | 0.055825 | 0.054865 | 0.054452 | 0.054078 | 0.053587 | 0.052986 | 0.052287 | 0.050936 | 0.049491 | 0.042592 | 0.037671 | 0.038065 | 0.048478 | 0.048243 | 0.048998 | 0.047384 | 0.046721 | 0.046209 | 0.045601 | 0.044859 | 0.043994 | 0.041684 | 0.039258 | 0.029304 | 0.023093 | 0.024222
| ABERNETHY | SCONE | MINIMUM HEADROOM | NO 14401 25495 | NO | YES | 9.5503 | 9.2789 | 8.7055 | 8.072 | 7.3735 | 6.5828 | 5.8258 | 5.2382 | 4.603 | 3.9549 | 3.3231 | 1.392 | 0.68414 | 0.39692 | 10.6371 | 10.4661 | 10.1305 | 9.7439 | 9.2813 | 8.7235 | 8.2269 | 7.8504 | 7.4515 | 7.0445 | 6.6541 | 5.6188 | 5.274 | 5.0626 | 9.9641 | 9.7051 | 9.1839 | 8.6012 | 7.938 | 7.1571 | 6.4235 | 5.8508 | 5.2492 | 4.6362 | 4.0432 | 2.3527 | 1.7489 | 1.4646
|  | SCONE | CT |  |  |  | 9.8266 | 9.6494 | 9.1576 | 8.631 | 8.0599 | 7.482 | 6.9666 | 6.3723 | 5.7132 | 5.0336 | 4.3709 | 2.4262 | 1.4387 | 0.92668 | 10.7383 | 10.6029 | 10.3168 | 9.9984 | 9.6287 | 9.2513 | 8.9656 | 8.6313 | 8.2398 | 7.8374 | 7.45 | 6.3334 | 5.7106 | 5.1097 | 10.1869 | 10.0113 | 9.56 | 9.0685 | 8.5329 | 7.9867 | 7.5264 | 6.9847 | 6.375 | 5.7496 | 5.1453 | 3.4157 | 2.5833 | 2.1444
|  | SCONE | LW |  |  |  | 9.5503 | 9.2789 | 8.7055 | 8.072 | 7.3735 | 6.5828 | 5.8258 | 5.2382 | 4.603 | 3.9549 | 3.3231 | 1.392 | 0.68414 | 0.39692 | 10.6371 | 10.4661 | 10.1305 | 9.7439 | 9.2813 | 8.7235 | 8.2269 | 7.8504 | 7.4515 | 7.0445 | 6.6541 | 5.6188 | 5.274 | 5.0626 | 9.9641 | 9.7051 | 9.1839 | 8.6012 | 7.938 | 7.1571 | 6.4235 | 5.8508 | 5.2492 | 4.6362 | 4.0432 | 2.3527 | 1.7489 | 1.4646
|  | SCONE | ST |  |  |  | 9.9474 | 9.8487 | 9.6359 | 9.4361 | 9.2486 | 8.9462 | 8.7142 | 8.4766 | 8.211 | 7.9133 | 7.5895 | 5.8581 | 4.9758 | 4.0706 | 10.7957 | 10.7211 | 10.5161 | 10.3325 | 10.1683 | 9.8725 | 9.6863 | 9.5092 | 9.3134 | 9.0931 | 8.8484 | 7.5626 | 6.8987 | 6.1526 | 10.2837 | 10.1929 | 9.9653 | 9.755 | 9.5613 | 9.2334 | 9.0112 | 8.7917 | 8.5464 | 8.271 | 7.9685 | 6.335 | 5.5604 | 4.7577
|  | SCONE | FS |  |  |  | 10.0301 | 9.9469 | 9.8043 | 9.6537 | 9.4937 | 9.3266 | 9.1419 | 8.918 | 8.6795 | 8.4259 | 8.1492 | 6.443 | 4.8908 | 3.9472 | 10.8627 | 10.7962 | 10.6878 | 10.5711 | 10.4443 | 10.3082 | 10.1636 | 10.0082 | 9.8399 | 9.6567 | 9.4532 | 8.1965 | 6.8641 | 5.6448 | 10.3548 | 10.2781 | 10.1454 | 10.0018 | 9.8478 | 9.6835 | 9.5085 | 9.313 | 9.1033 | 8.8786 | 8.6304 | 7.0838 | 5.6578 | 4.8212
| THURSO | SHAPINSAY | MINIMUM HEADROOM | HY 48313 17148 | YES | YES | 0.68683 | 0.67466 | 0.66198 | 0.64375 | 0.6168 | 0.59366 | 0.57314 | 0.53986 | 0.49806 | 0.4636 | 0.42502 | 0.2603 | -0.15301 | -0.72756 | 0.74753 | 0.7406 | 0.73385 | 0.72007 | 0.6996 | 0.67994 | 0.66766 | 0.61721 | 0.58669 | 0.55061 | 0.51113 | 0.32041 | -0.17688 | -0.89163 | 0.58543 | 0.57756 | 0.56831 | 0.55264 | 0.5243 | 0.49901 | 0.47821 | 0.44039 | 0.39971 | 0.36731 | 0.32633 | 0.1204 | -0.39186 | -1.1086
|  | SHAPINSAY | CT |  |  |  | 0.69651 | 0.6854 | 0.66696 | 0.64375 | 0.6168 | 0.59366 | 0.57314 | 0.53986 | 0.49806 | 0.4636 | 0.42502 | 0.27483 | 0.063279 | -0.17273 | 0.7514 | 0.74524 | 0.73408 | 0.72007 | 0.6996 | 0.67994 | 0.66766 | 0.63008 | 0.5876 | 0.55061 | 0.51113 | 0.33844 | 0.089442 | -0.20053 | 0.59464 | 0.58681 | 0.5724 | 0.55264 | 0.5243 | 0.49901 | 0.47821 | 0.44039 | 0.39971 | 0.36731 | 0.32633 | 0.14804 | -0.10786 | -0.39866
|  | SHAPINSAY | LW |  |  |  | 0.68683 | 0.67466 | 0.66198 | 0.64699 | 0.63187 | 0.61587 | 0.59402 | 0.5537 | 0.50864 | 0.46963 | 0.42938 | 0.2603 | -0.15301 | -0.72756 | 0.74753 | 0.7406 | 0.73385 | 0.72585 | 0.71828 | 0.70846 | 0.69579 | 0.65131 | 0.60379 | 0.56282 | 0.51972 | 0.32869 | -0.17688 | -0.89163 | 0.58543 | 0.57756 | 0.56831 | 0.5561 | 0.54158 | 0.52758 | 0.50825 | 0.46305 | 0.41365 | 0.3708 | 0.32642 | 0.1204 | -0.39186 | -1.1086
|  | SHAPINSAY | ST |  |  |  | 0.70232 | 0.69892 | 0.68507 | 0.67325 | 0.66554 | 0.6437 | 0.63475 | 0.5705 | 0.54182 | 0.51481 | 0.47425 | 0.28396 | -0.031194 | -0.36839 | 0.75408 | 0.75206 | 0.73858 | 0.7279 | 0.72026 | 0.69908 | 0.69045 | 0.61721 | 0.58669 | 0.55885 | 0.51714 | 0.32041 | -0.059744 | -0.47499 | 0.60057 | 0.5984 | 0.58407 | 0.5736 | 0.56602 | 0.54138 | 0.53154 | 0.45489 | 0.42204 | 0.39162 | 0.34576 | 0.1273 | -0.26786 | -0.68489
|  | SHAPINSAY | FS |  |  |  | 0.70246 | 0.70232 | 0.69548 | 0.68802 | 0.67901 | 0.67223 | 0.66355 | 0.63533 | 0.61531 | 0.593 | 0.57159 | 0.48981 | 0.41863 | 0.36842 | 0.75423 | 0.75354 | 0.74868 | 0.74333 | 0.73713 | 0.73155 | 0.72525 | 0.696 | 0.67494 | 0.65273 | 0.63056 | 0.56855 | 0.513 | 0.45819 | 0.60003 | 0.60116 | 0.59508 | 0.58891 | 0.58151 | 0.57561 | 0.56665 | 0.53429 | 0.51197 | 0.48719 | 0.46312 | 0.38461 | 0.31812 | 0.24633
| BROADFORD | SHIELDAIG | MINIMUM HEADROOM | NG 81637 52250 | YES | YES | 0.27747 | 0.25162 | 0.22717 | 0.19967 | 0.17149 | 0.13503 | 0.10343 | 0.079022 | 0.056764 | 0.034269 | 0.0114 | -0.035344 | -0.059776 | -0.076768 | 0.56433 | 0.54768 | 0.53306 | 0.51068 | 0.49314 | 0.47453 | 0.44848 | 0.42026 | 0.39089 | 0.36108 | 0.33409 | 0.29773 | 0.27742 | 0.25855 | 0.25361 | 0.24798 | 0.23052 | 0.20631 | 0.18087 | 0.14742 | 0.11794 | 0.087125 | 0.05096 | 0.014502 | -0.018872 | -0.068352 | -0.092593 | -0.11048
|  | SHIELDAIG | CT |  |  |  | 0.29044 | 0.28042 | 0.24197 | 0.20712 | 0.17448 | 0.13932 | 0.10601 | 0.08838 | 0.069972 | 0.047713 | 0.032335 | -0.022873 | -0.059776 | -0.076768 | 0.56999 | 0.55815 | 0.5346 | 0.51068 | 0.49314 | 0.47453 | 0.45637 | 0.43534 | 0.40661 | 0.37626 | 0.3517 | 0.29989 | 0.27742 | 0.25855 | 0.25361 | 0.24798 | 0.23902 | 0.21219 | 0.18274 | 0.15105 | 0.12097 | 0.10401 | 0.072025 | 0.034831 | 0.0066231 | -0.054496 | -0.092593 | -0.11048
|  | SHIELDAIG | LW |  |  |  | 0.27747 | 0.25162 | 0.22717 | 0.19967 | 0.17149 | 0.13503 | 0.10343 | 0.079022 | 0.056764 | 0.034269 | 0.0114 | -0.035344 | -0.05513 | -0.060113 | 0.56433 | 0.54768 | 0.53306 | 0.51596 | 0.50091 | 0.4755 | 0.44848 | 0.42026 | 0.39089 | 0.36108 | 0.33409 | 0.29773 | 0.28929 | 0.28747 | 0.25453 | 0.24805 | 0.23052 | 0.20631 | 0.18087 | 0.14742 | 0.11794 | 0.087125 | 0.05096 | 0.014502 | -0.018872 | -0.068352 | -0.088969 | -0.094341
|  | SHIELDAIG | ST |  |  |  | 0.29226 | 0.28995 | 0.28682 | 0.27419 | 0.26131 | 0.24915 | 0.23353 | 0.21471 | 0.1955 | 0.17307 | 0.14695 | 0.025253 | -0.014711 | -0.030996 | 0.57435 | 0.57068 | 0.56332 | 0.55426 | 0.54496 | 0.53445 | 0.52148 | 0.50557 | 0.48709 | 0.46581 | 0.44178 | 0.32351 | 0.29368 | 0.27779 | 0.2571 | 0.25562 | 0.25358 | 0.25039 | 0.24702 | 0.24276 | 0.23581 | 0.21828 | 0.20018 | 0.17906 | 0.14652 | -0.0078296 | -0.051012 | -0.068715
|  | SHIELDAIG | FS |  |  |  | 0.29269 | 0.29078 | 0.28828 | 0.28494 | 0.27455 | 0.26787 | 0.25094 | 0.23681 | 0.21993 | 0.20192 | 0.18467 | 0.058415 | -0.030195 | -0.047974 | 0.57735 | 0.57322 | 0.56774 | 0.56063 | 0.55266 | 0.54556 | 0.53478 | 0.52346 | 0.51019 | 0.49543 | 0.47968 | 0.37459 | 0.28854 | 0.26594 | 0.25775 | 0.25653 | 0.25519 | 0.25285 | 0.25027 | 0.24791 | 0.24413 | 0.23882 | 0.2233 | 0.2066 | 0.19047 | 0.043456 | -0.063972 | -0.084088
| SHIN | SHIN | MINIMUM HEADROOM | NH 57246 97463 | YES | YES | 2.4954 | 2.4608 | 2.4243 | 2.3861 | 2.3518 | 2.3062 | 2.2581 | 2.2323 | 2.199 | 2.1692 | 2.1431 | 2.0808 | 2.039 | 2.016 | 2.4233 | 2.4117 | 2.4004 | 2.3814 | 2.3624 | 2.3396 | 2.3114 | 2.2891 | 2.2635 | 2.2387 | 2.2167 | 2.1786 | 2.156 | 2.138 | 2.2317 | 2.2109 | 2.1846 | 2.1566 | 2.1304 | 2.098 | 2.0645 | 2.0523 | 2.0349 | 2.0205 | 1.9947 | 1.9352 | 1.9007 | 1.8805
|  | SHIN | CT |  |  |  | 2.5202 | 2.4992 | 2.4497 | 2.4018 | 2.3601 | 2.3167 | 2.2712 | 2.2494 | 2.2224 | 2.1889 | 2.1613 | 2.1062 | 2.039 | 2.016 | 2.428 | 2.4193 | 2.4034 | 2.382 | 2.3624 | 2.342 | 2.3208 | 2.3028 | 2.2792 | 2.253 | 2.2312 | 2.1868 | 2.156 | 2.138 | 2.2437 | 2.2295 | 2.2005 | 2.1714 | 2.1395 | 2.1064 | 2.0714 | 2.0589 | 2.0504 | 2.0365 | 2.0149 | 1.9573 | 1.9007 | 1.8805
|  | SHIN | LW |  |  |  | 2.4954 | 2.4608 | 2.4243 | 2.3861 | 2.3518 | 2.3062 | 2.2581 | 2.2323 | 2.199 | 2.1692 | 2.1431 | 2.0808 | 2.0468 | 2.0364 | 2.4233 | 2.4117 | 2.4004 | 2.3814 | 2.3651 | 2.3396 | 2.3114 | 2.2891 | 2.2635 | 2.2387 | 2.2167 | 2.1786 | 2.1654 | 2.1617 | 2.2317 | 2.2109 | 2.1846 | 2.1566 | 2.1304 | 2.098 | 2.0645 | 2.0523 | 2.0349 | 2.0205 | 1.9947 | 1.9352 | 1.9068 | 1.8984
|  | SHIN | ST |  |  |  | 2.5338 | 2.521 | 2.5022 | 2.4856 | 2.4684 | 2.4498 | 2.4229 | 2.4005 | 2.3724 | 2.3421 | 2.3101 | 2.1595 | 2.0953 | 2.0623 | 2.4334 | 2.4291 | 2.4233 | 2.4175 | 2.411 | 2.4036 | 2.3908 | 2.3763 | 2.3585 | 2.3387 | 2.3173 | 2.2109 | 2.1761 | 2.1569 | 2.253 | 2.2449 | 2.2338 | 2.2235 | 2.2124 | 2.2001 | 2.1833 | 2.1684 | 2.1504 | 2.1308 | 2.1095 | 2.003 | 1.9473 | 1.9202
|  | SHIN | FS |  |  |  | 2.5452 | 2.535 | 2.522 | 2.5063 | 2.4886 | 2.4717 | 2.4523 | 2.4319 | 2.4077 | 2.3856 | 2.3575 | 2.1826 | 2.0742 | 2.0408 | 2.436 | 2.4327 | 2.4284 | 2.4234 | 2.4176 | 2.4116 | 2.4047 | 2.3944 | 2.3807 | 2.367 | 2.3505 | 2.2464 | 2.1678 | 2.1426 | 2.2588 | 2.2525 | 2.2443 | 2.2351 | 2.2244 | 2.2135 | 2.2014 | 2.189 | 2.1743 | 2.1603 | 2.1433 | 2.025 | 1.9308 | 1.9033
| FORT WILLIAM | SHONA BEG | MINIMUM HEADROOM | NM 67173 74363 | YES | YES | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513
|  | SHONA BEG | CT |  |  |  | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513
|  | SHONA BEG | LW |  |  |  | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513
|  | SHONA BEG | ST |  |  |  | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513
|  | SHONA BEG | FS |  |  |  | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.095757 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.093184 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513 | 0.090513
| KINTORE | SKENE | MINIMUM HEADROOM | NJ 82203 06495 | NO | YES | 15.3093 | 14.8262 | 14.0935 | 13.2809 | 12.5129 | 11.5574 | 10.5157 | 9.5433 | 8.5369 | 7.5011 | 6.5257 | 4.0501 | 2.5434 | 1.5102 | 18.4165 | 18.217 | 17.9535 | 17.531 | 17.1524 | 16.6187 | 16.0253 | 15.4211 | 14.769 | 14.0729 | 13.4228 | 11.733 | 10.4482 | 9.0854 | 16.1812 | 15.8196 | 15.4507 | 15.0126 | 14.5828 | 13.9626 | 13.0786 | 12.2109 | 11.3107 | 10.3861 | 9.5139 | 7.2857 | 5.7597 | 4.794
|  | SKENE | CT |  |  |  | 15.7078 | 15.3961 | 14.662 | 13.8908 | 13.161 | 12.3996 | 11.6799 | 10.7476 | 9.7464 | 8.7377 | 7.7287 | 4.3787 | 2.5434 | 1.5102 | 18.4165 | 18.217 | 17.9877 | 17.6343 | 17.1988 | 16.7366 | 16.3267 | 15.7731 | 15.1577 | 14.5221 | 13.8697 | 11.733 | 10.4482 | 9.0854 | 16.2576 | 15.9465 | 15.4718 | 15.0457 | 14.5828 | 14.0787 | 13.6252 | 12.9967 | 12.3292 | 11.4241 | 10.5122 | 7.4524 | 5.7597 | 4.794
|  | SKENE | LW |  |  |  | 15.3093 | 14.8262 | 14.0935 | 13.2809 | 12.5129 | 11.5574 | 10.5157 | 9.5433 | 8.5369 | 7.5011 | 6.5257 | 4.0501 | 2.8124 | 1.8525 | 18.4432 | 18.237 | 17.9535 | 17.531 | 17.1524 | 16.6187 | 16.0253 | 15.4211 | 14.769 | 14.0729 | 13.4228 | 11.977 | 11.2837 | 10.483 | 16.1812 | 15.8196 | 15.4507 | 15.0126 | 14.6077 | 13.9626 | 13.0786 | 12.2109 | 11.3107 | 10.3861 | 9.5139 | 7.2857 | 6.1075 | 5.157
|  | SKENE | ST |  |  |  | 15.8679 | 15.6998 | 15.4594 | 15.1976 | 14.9341 | 14.5805 | 14.2454 | 13.8346 | 13.4014 | 12.9218 | 12.3831 | 9.1295 | 7.1592 | 5.2428 | 18.4955 | 18.3935 | 18.2441 | 18.0875 | 17.9406 | 17.698 | 17.496 | 17.2066 | 16.8598 | 16.4571 | 15.984 | 13.3662 | 11.8051 | 10.126 | 16.4177 | 16.2756 | 16.067 | 15.8411 | 15.6093 | 15.2662 | 14.9454 | 14.5265 | 14.083 | 13.5808 | 13.0007 | 9.8796 | 8.4947 | 7.3886
|  | SKENE | FS |  |  |  | 15.9833 | 15.8516 | 15.6765 | 15.4778 | 15.2678 | 15.0274 | 14.7743 | 14.415 | 14.0416 | 13.642 | 13.2051 | 10.4065 | 7.7094 | 5.8184 | 18.5776 | 18.4945 | 18.4157 | 18.3227 | 18.2163 | 18.0952 | 17.9615 | 17.7334 | 17.4515 | 17.1425 | 16.798 | 14.5846 | 12.0737 | 9.5955 | 16.514 | 16.402 | 16.2739 | 16.1264 | 15.9588 | 15.7661 | 15.5532 | 15.2794 | 14.9863 | 14.6644 | 14.3021 | 12.0435 | 9.8773 | 8.1232
| BROADFORD | SKULAMUS | MINIMUM HEADROOM | NG 65881 22438 | YES | YES | -1.8093 | -1.9564 | -2.059 | -2.1675 | -2.2738 | -2.4211 | -2.5751 | -2.6911 | -2.8108 | -2.9303 | -3.0227 | -3.1628 | -3.2463 | -3.2934 | -0.84056 | -0.92017 | -0.97312 | -1.0367 | -1.0995 | -1.1732 | -1.2584 | -1.3408 | -1.4275 | -1.5143 | -1.5859 | -1.6942 | -1.7699 | -1.8393 | -1.5076 | -1.6329 | -1.7252 | -1.8231 | -1.9215 | -2.0546 | -2.1899 | -2.2881 | -2.3913 | -2.4949 | -2.5747 | -2.7009 | -2.792 | -2.8424
|  | SKULAMUS | CT |  |  |  | -1.7534 | -1.8701 | -2.0082 | -2.1497 | -2.2738 | -2.4211 | -2.5704 | -2.6618 | -2.7815 | -2.8942 | -2.9805 | -3.1364 | -3.2463 | -3.2934 | -0.81831 | -0.88278 | -0.95806 | -1.0367 | -1.0995 | -1.1732 | -1.2475 | -1.3123 | -1.4001 | -1.4859 | -1.5547 | -1.6942 | -1.7699 | -1.8393 | -1.4563 | -1.5545 | -1.6797 | -1.8084 | -1.9215 | -2.0546 | -2.1899 | -2.2686 | -2.3725 | -2.4702 | -2.5446 | -2.6766 | -2.792 | -2.8424
|  | SKULAMUS | LW |  |  |  | -1.8093 | -1.9564 | -2.059 | -2.1675 | -2.2673 | -2.4155 | -2.5751 | -2.6911 | -2.8108 | -2.9303 | -3.0227 | -3.1628 | -3.2145 | -3.2306 | -0.84056 | -0.92017 | -0.97312 | -1.031 | -1.0818 | -1.1655 | -1.2584 | -1.3408 | -1.4275 | -1.5143 | -1.5859 | -1.6846 | -1.7071 | -1.7133 | -1.5076 | -1.6329 | -1.7252 | -1.8231 | -1.9136 | -2.0458 | -2.188 | -2.2881 | -2.3913 | -2.4949 | -2.5747 | -2.7009 | -2.7572 | -2.7745
|  | SKULAMUS | ST |  |  |  | -1.7179 | -1.8024 | -1.84 | -1.8855 | -1.9347 | -2.0031 | -2.0775 | -2.1582 | -2.2461 | -2.3372 | -2.4314 | -2.882 | -2.9936 | -3.0481 | -0.80106 | -0.84486 | -0.86647 | -0.8936 | -0.92361 | -0.96461 | -1.0105 | -1.0618 | -1.12 | -1.1824 | -1.2484 | -1.579 | -1.6682 | -1.7333 | -1.4238 | -1.4937 | -1.5266 | -1.5667 | -1.6095 | -1.668 | -1.732 | -1.801 | -1.876 | -1.9542 | -2.0356 | -2.4295 | -2.5297 | -2.5854
|  | SKULAMUS | FS |  |  |  | -1.6962 | -1.7676 | -1.8064 | -1.8481 | -1.8937 | -1.9499 | -2.0078 | -2.0702 | -2.1395 | -2.2106 | -2.2802 | -2.7162 | -3.0299 | -3.0883 | -0.79198 | -0.83012 | -0.85134 | -0.8757 | -0.90225 | -0.93489 | -0.96979 | -1.0087 | -1.0525 | -1.0986 | -1.1456 | -1.4429 | -1.6955 | -1.7921 | -1.4049 | -1.4631 | -1.4973 | -1.5335 | -1.5731 | -1.6219 | -1.6719 | -1.7258 | -1.7857 | -1.8473 | -1.9085 | -2.2941 | -2.5682 | -2.6209
| WOODHILL | SPRINGHILL | MINIMUM HEADROOM | NJ 89850 06421 | NO | NO | 1.3198 | 3.3475 | 2.2976 | 1.0602 | -0.36187 | -2.0024 | -3.4342 | -4.422 | -5.469 | -6.5234 | -7.5918 | -10.7451 | -12.0258 | -13.26 | 6.6692 | 9.9302 | 9.1926 | 8.2818 | 7.086 | 5.6845 | 4.576 | 3.8538 | 3.0779 | 2.3007 | 1.5238 | -0.71308 | -1.795 | -3.3085 | 5.9961 | 9.1163 | 8.0735 | 6.8423 | 5.3365 | 3.6051 | 2.1568 | 1.2009 | 0.18526 | -0.86583 | -1.9316 | -5.0064 | -6.3194 | -7.7377
|  | SPRINGHILL | CT |  |  |  | 1.6767 | 3.8664 | 3.0469 | 2.1436 | 1.0811 | -0.023346 | -0.87346 | -1.7588 | -2.6981 | -3.6333 | -4.6351 | -8.0514 | -9.7318 | -10.631 | 6.7449 | 10.061 | 9.5523 | 8.9559 | 8.1195 | 7.2344 | 6.6736 | 6.0687 | 5.4057 | 4.7412 | 4.0135 | 1.327 | -0.56796 | -2.833 | 6.3043 | 9.5701 | 8.81 | 7.9608 | 6.8811 | 5.7532 | 4.9501 | 4.1187 | 3.2332 | 2.3537 | 1.4085 | -1.8184 | -3.3811 | -4.264
|  | SPRINGHILL | LW |  |  |  | 1.3198 | 3.3475 | 2.2976 | 1.0602 | -0.36187 | -2.0024 | -3.4342 | -4.422 | -5.469 | -6.5234 | -7.5918 | -10.7451 | -12.0258 | -13.26 | 6.6692 | 9.9302 | 9.1926 | 8.2818 | 7.086 | 5.6845 | 4.576 | 3.8538 | 3.0779 | 2.3007 | 1.5238 | -0.71308 | -1.795 | -3.0899 | 5.9961 | 9.1163 | 8.0735 | 6.8423 | 5.3365 | 3.6051 | 2.1568 | 1.2009 | 0.18526 | -0.86583 | -1.9316 | -5.0064 | -6.3194 | -7.7377
|  | SPRINGHILL | ST |  |  |  | 1.8718 | 4.1973 | 3.6743 | 3.1948 | 2.8152 | 2.0606 | 1.6188 | 1.151 | 0.69865 | 0.20037 | -0.3809 | -3.8565 | -5.9072 | -7.5177 | 6.8727 | 10.2923 | 9.7354 | 9.2568 | 8.8864 | 8.0549 | 7.6213 | 7.1637 | 6.7436 | 6.2811 | 5.7322 | 2.6082 | 0.33715 | -2.2646 | 6.4882 | 9.8851 | 9.3033 | 8.794 | 8.3999 | 7.5447 | 7.0897 | 6.6038 | 6.1376 | 5.6244 | 5.0218 | 1.5429 | -0.3991 | -1.8768
|  | SPRINGHILL | FS |  |  |  | 2.1651 | 4.5255 | 4.2651 | 3.9947 | 3.6953 | 3.3799 | 3.0454 | 2.6546 | 2.2534 | 1.8269 | 1.3511 | -1.5211 | -4.3925 | -6.4634 | 7.0779 | 10.5117 | 10.277 | 10.0253 | 9.7429 | 9.4368 | 9.1152 | 8.7646 | 8.3983 | 7.9974 | 7.5396 | 4.7758 | 1.2202 | -3.3085 | 6.7563 | 10.186 | 9.9323 | 9.6664 | 9.3701 | 9.0575 | 8.7297 | 8.3583 | 7.9793 | 7.5658 | 7.1007 | 4.3333 | 1.6172 | -0.20164
| BRIDGE OF DUN | ST CYRUS | MINIMUM HEADROOM | NO 74889 65577 | NO | YES | 6.132 | 6.0063 | 5.8719 | 5.731 | 5.5364 | 5.2728 | 5.0704 | 4.928 | 4.7645 | 4.6006 | 4.4392 | 3.947 | 3.3085 | 2.5007 | 6.4358 | 6.369 | 6.3021 | 6.1864 | 6.0569 | 5.8754 | 5.7579 | 5.6337 | 5.4845 | 5.3395 | 5.198 | 4.7452 | 4.1414 | 3.1847 | 5.6124 | 5.4963 | 5.3747 | 5.2365 | 5.0413 | 4.7894 | 4.6035 | 4.4507 | 4.2796 | 4.1134 | 3.9402 | 3.4505 | 2.7013 | 1.7201
|  | ST CYRUS | CT |  |  |  | 6.2262 | 6.1311 | 5.94 | 5.7392 | 5.5364 | 5.2728 | 5.0704 | 4.928 | 4.7645 | 4.6006 | 4.4392 | 3.9921 | 3.5251 | 3.1312 | 6.4685 | 6.4104 | 6.3035 | 6.1864 | 6.0569 | 5.8754 | 5.7579 | 5.6337 | 5.4845 | 5.3395 | 5.198 | 4.7452 | 4.285 | 3.7813 | 5.6927 | 5.6032 | 5.4255 | 5.2365 | 5.0413 | 4.7894 | 4.6035 | 4.4507 | 4.2796 | 4.1134 | 3.9402 | 3.4505 | 2.947 | 2.4934
|  | ST CYRUS | LW |  |  |  | 6.132 | 6.0063 | 5.8719 | 5.731 | 5.5902 | 5.3613 | 5.1544 | 4.9898 | 4.8091 | 4.6278 | 4.4514 | 3.947 | 3.3085 | 2.5007 | 6.4358 | 6.369 | 6.3021 | 6.2288 | 6.1584 | 6.0109 | 5.8831 | 5.7383 | 5.5817 | 5.4273 | 5.2775 | 4.8452 | 4.1414 | 3.1847 | 5.6124 | 5.4963 | 5.3747 | 5.2458 | 5.119 | 4.9046 | 4.7085 | 4.5362 | 4.3531 | 4.1613 | 3.975 | 3.4514 | 2.7013 | 1.7201
|  | ST CYRUS | ST |  |  |  | 6.3209 | 6.2781 | 6.1921 | 6.1053 | 6.0241 | 5.8487 | 5.7422 | 5.5692 | 5.4334 | 5.2948 | 5.1304 | 4.313 | 3.693 | 3.1534 | 6.5117 | 6.4882 | 6.4184 | 6.3541 | 6.2965 | 6.1439 | 6.0622 | 5.8992 | 5.7911 | 5.6776 | 5.537 | 4.8398 | 4.1775 | 3.5153 | 5.7754 | 5.7365 | 5.6473 | 5.56 | 5.4799 | 5.3006 | 5.1951 | 5.005 | 4.8688 | 4.731 | 4.5574 | 3.7168 | 3.0223 | 2.3949
|  | ST CYRUS | FS |  |  |  | 6.3462 | 6.3154 | 6.2586 | 6.1959 | 6.1322 | 6.026 | 5.9471 | 5.8375 | 5.7333 | 5.6277 | 5.5103 | 4.8516 | 4.3412 | 4.1083 | 6.5225 | 6.5044 | 6.4697 | 6.4305 | 6.3889 | 6.3144 | 6.2567 | 6.1694 | 6.0892 | 6.0068 | 5.9156 | 5.4417 | 4.9898 | 4.6454 | 5.7976 | 5.7694 | 5.7159 | 5.6565 | 5.5955 | 5.4955 | 5.4193 | 5.3073 | 5.2021 | 5.0967 | 4.9813 | 4.347 | 3.8535 | 3.6259
| ST FERGUS GAS | ST FERGUS GAS TERM | MINIMUM HEADROOM | NK 0916 5377 | NO | YES | 32.1746 | 32.1152 | 29.9903 | 27.6238 | 22.9597 | 17.9995 | 15.0984 | 14.3164 | 13.5134 | 12.8279 | 12.0778 | 8.434 | 7.1758 | 6.4705 | 32.0294 | 32.0175 | 29.476 | 26.6382 | 20.9221 | 14.8609 | 11.3675 | 10.4661 | 9.533 | 8.7496 | 7.8823 | 3.5379 | 2.077 | 1.2273 | 32.0275 | 32.0131 | 29.4695 | 26.6061 | 20.8127 | 14.6555 | 11.0706 | 10.1284 | 9.1571 | 8.3342 | 7.4292 | 2.9754 | 1.4574 | 0.59266
|  | ST FERGUS GAS TERM | CT |  |  |  | 32.2371 | 32.2039 | 31.8585 | 31.3244 | 29.147 | 26.8325 | 26.1703 | 25.7808 | 25.3858 | 25.0179 | 24.6375 | 22.8708 | 22.1897 | 21.826 | 32.0306 | 32.0209 | 31.7001 | 31.1413 | 28.5259 | 25.7371 | 25.0206 | 24.6587 | 24.2477 | 23.8749 | 23.4786 | 21.5427 | 20.8625 | 20.4501 | 32.0291 | 32.0175 | 31.6933 | 31.1309 | 28.5012 | 25.6412 | 24.8487 | 24.4 | 23.942 | 23.5217 | 23.0832 | 21.0074 | 20.2475 | 19.8334
|  | ST FERGUS GAS TERM | LW |  |  |  | 32.1746 | 32.1152 | 29.9903 | 27.6238 | 22.9597 | 17.9995 | 15.0984 | 14.3164 | 13.5134 | 12.8279 | 12.0778 | 8.434 | 7.1758 | 6.4705 | 32.0294 | 32.0175 | 29.476 | 26.6382 | 20.9221 | 14.8609 | 11.3675 | 10.4661 | 9.533 | 8.7496 | 7.8823 | 3.5379 | 2.077 | 1.2273 | 32.0275 | 32.0131 | 29.4695 | 26.6061 | 20.8127 | 14.6555 | 11.0706 | 10.1284 | 9.1571 | 8.3342 | 7.4292 | 2.9754 | 1.4574 | 0.59266
|  | ST FERGUS GAS TERM | ST |  |  |  | 32.265 | 32.2446 | 30.3508 | 29.0565 | 28.1921 | 25.2807 | 24.4473 | 23.8029 | 23.5421 | 23.307 | 22.9647 | 21.2521 | 20.3833 | 19.7821 | 32.0333 | 32.0293 | 29.6819 | 28.0912 | 27.0372 | 23.4321 | 22.4208 | 21.6534 | 21.3701 | 21.1254 | 20.7434 | 18.9027 | 17.9724 | 17.3757 | 32.0325 | 32.0278 | 29.6796 | 28.0876 | 27.0323 | 23.4255 | 22.4121 | 21.642 | 21.3555 | 21.107 | 20.7208 | 18.7031 | 17.7025 | 17.0436
|  | ST FERGUS GAS TERM | FS |  |  |  | 32.2705 | 32.259 | 31.8562 | 31.4492 | 30.9791 | 30.5015 | 30.0921 | 29.8341 | 29.6417 | 29.4467 | 29.2472 | 28.7289 | 28.3427 | 28.0764 | 32.034 | 32.0306 | 31.5474 | 31.0629 | 30.4987 | 29.9334 | 29.4464 | 29.164 | 28.9683 | 28.7712 | 28.5728 | 28.2458 | 27.9267 | 27.6859 | 32.0333 | 32.0295 | 31.5456 | 31.0603 | 30.4951 | 29.9286 | 29.4402 | 29.1562 | 28.9587 | 28.7594 | 28.5587 | 28.0522 | 27.6673 | 27.4247
| ST FILLANS | ST FILLANS | MINIMUM HEADROOM | NN 6942 2464 | YES | NO | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175
|  | ST FILLANS | CT |  |  |  | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175
|  | ST FILLANS | LW |  |  |  | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175
|  | ST FILLANS | ST |  |  |  | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175
|  | ST FILLANS | FS |  |  |  | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.85 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175 | 8.175
| PERSLEY | ST MACHAR | MINIMUM HEADROOM | NJ 93584 08102 | NO | YES | 14.3456 | 13.9047 | 12.8958 | 11.8227 | 10.4693 | 8.9252 | 7.5564 | 6.752 | 5.8946 | 5.0229 | 4.1692 | 1.7631 | 0.8916 | -0.22641 | 15.4419 | 15.1571 | 14.4987 | 13.7686 | 12.6873 | 11.3933 | 10.3301 | 9.6346 | 8.8796 | 8.1156 | 7.3736 | 5.3846 | 4.4799 | -2.2213 | 14.0581 | 13.6425 | 12.7346 | 11.7467 | 10.4087 | 8.8296 | 7.4667 | 6.5976 | 5.66 | 4.7065 | 3.78 | 1.2854 | 0.42806 | -0.96296
|  | ST MACHAR | CT |  |  |  | 14.843 | 14.6205 | 13.803 | 12.9282 | 11.9103 | 10.855 | 10.0045 | 9.3391 | 8.651 | 7.9704 | 7.2142 | 4.2567 | 2.4626 | 1.6996 | 15.5028 | 15.2767 | 14.7772 | 14.2051 | 13.441 | 12.6264 | 12.0605 | 11.5145 | 10.9345 | 10.3484 | 9.6718 | 6.8246 | 4.4799 | 1.3438 | 14.3902 | 14.159 | 13.4666 | 12.7002 | 11.7642 | 10.7838 | 10.0571 | 9.4224 | 8.7561 | 8.0955 | 7.3439 | 4.6265 | 3.2517 | 2.6107
|  | ST MACHAR | LW |  |  |  | 14.3456 | 13.9047 | 12.8958 | 11.8227 | 10.4693 | 8.9252 | 7.5564 | 6.752 | 5.8946 | 5.0229 | 4.1692 | 1.7631 | 0.8916 | -0.22641 | 15.4419 | 15.1571 | 14.4987 | 13.7686 | 12.6873 | 11.3933 | 10.3301 | 9.6346 | 8.8796 | 8.1156 | 7.3736 | 5.3846 | 4.6654 | 3.4095 | 14.0581 | 13.6425 | 12.7346 | 11.7467 | 10.4087 | 8.8296 | 7.4667 | 6.5976 | 5.66 | 4.7065 | 3.78 | 1.2854 | 0.42806 | -0.96296
|  | ST MACHAR | ST |  |  |  | 15.0428 | 14.9343 | 14.5564 | 14.2324 | 13.9365 | 13.345 | 12.9867 | 12.6295 | 12.2753 | 11.891 | 11.4516 | 8.5411 | 6.6336 | 4.8295 | 15.6128 | 15.4816 | 15.0294 | 14.6435 | 14.2978 | 13.5834 | 13.1599 | 12.7324 | 12.3118 | 11.847 | 11.3114 | 8.0641 | 5.3856 | 1.8561 | 14.5625 | 14.4525 | 14.0149 | 13.6459 | 13.3233 | 12.6341 | 12.2381 | 11.8393 | 11.4485 | 11.0208 | 10.5291 | 7.614 | 6.0176 | 4.6604
|  | ST MACHAR | FS |  |  |  | 15.1141 | 15.0339 | 14.8405 | 14.6371 | 14.4041 | 14.1509 | 13.8839 | 13.5579 | 13.2236 | 12.8612 | 12.4826 | 9.8203 | 7.2856 | 5.2762 | 15.6273 | 15.4998 | 15.2796 | 15.0342 | 14.7551 | 14.4416 | 14.1029 | 13.741 | 13.3498 | 12.9127 | 12.4286 | 9.1107 | 4.5622 | -2.2213 | 14.6162 | 14.5311 | 14.3375 | 14.127 | 13.8902 | 13.6316 | 13.3569 | 13.0469 | 12.7248 | 12.3725 | 11.9975 | 9.4968 | 7.2039 | 5.6283
| THURSO | ST MARYS | MINIMUM HEADROOM | HY 46965 01396 | YES | YES | -1.6638 | -1.763 | -1.8949 | -2.0735 | -2.2449 | -2.4173 | -2.5936 | -2.6697 | -2.7771 | -2.8955 | -3.0159 | -3.2234 | -3.318 | -3.3814 | -0.88495 | -0.92591 | -0.97689 | -1.0236 | -1.063 | -1.1062 | -1.1518 | -1.2083 | -1.2711 | -1.3547 | -1.4334 | -1.6194 | -1.7329 | -1.7594 | -1.2065 | -1.2664 | -1.3605 | -1.4777 | -1.6082 | -1.7395 | -1.8753 | -1.9004 | -1.9461 | -2.0114 | -2.1087 | -2.2941 | -2.3717 | -2.4427
|  | ST MARYS | CT |  |  |  | -1.6031 | -1.679 | -1.8716 | -2.0735 | -2.2449 | -2.4173 | -2.5936 | -2.6697 | -2.7771 | -2.8898 | -2.9834 | -3.1526 | -3.3085 | -3.3814 | -0.88495 | -0.92591 | -0.97689 | -1.0236 | -1.063 | -1.1062 | -1.1518 | -1.2083 | -1.2612 | -1.3143 | -1.3775 | -1.5487 | -1.5681 | -1.5817 | -1.1605 | -1.2072 | -1.3427 | -1.4777 | -1.6082 | -1.7395 | -1.8753 | -1.9004 | -1.9461 | -1.9968 | -2.0758 | -2.2137 | -2.3352 | -2.3951
|  | ST MARYS | LW |  |  |  | -1.6638 | -1.763 | -1.8949 | -2.0372 | -2.172 | -2.3448 | -2.5365 | -2.6458 | -2.7739 | -2.8955 | -3.0159 | -3.2234 | -3.318 | -3.3551 | -0.87831 | -0.9114 | -0.9384 | -0.96978 | -1.001 | -1.0548 | -1.1189 | -1.1914 | -1.2711 | -1.3547 | -1.4334 | -1.6041 | -1.6269 | -1.6332 | -1.2065 | -1.2664 | -1.3605 | -1.4584 | -1.5581 | -1.6669 | -1.7845 | -1.8325 | -1.9205 | -2.0114 | -2.1087 | -2.2941 | -2.3717 | -2.4007
|  | ST MARYS | ST |  |  |  | -1.5432 | -1.5755 | -1.6174 | -1.6679 | -1.7243 | -1.7835 | -1.8536 | -1.942 | -2.0402 | -2.1499 | -2.2726 | -2.8736 | -3.0536 | -3.1388 | -0.86126 | -0.87248 | -0.88759 | -0.90707 | -0.93103 | -0.96059 | -0.99694 | -1.0421 | -1.0972 | -1.1611 | -1.2343 | -1.6194 | -1.7329 | -1.7499 | -1.1055 | -1.1253 | -1.1495 | -1.1774 | -1.2095 | -1.2408 | -1.2779 | -1.323 | -1.3991 | -1.4885 | -1.5893 | -2.0972 | -2.2954 | -2.3756
|  | ST MARYS | FS |  |  |  | -1.5259 | -1.5547 | -1.5938 | -1.6385 | -1.6894 | -1.7382 | -1.7965 | -1.8645 | -1.9369 | -2.0165 | -2.1031 | -2.6751 | -3.1091 | -3.2331 | -0.85698 | -0.86533 | -0.87641 | -0.89008 | -0.90615 | -0.92507 | -0.94753 | -0.97433 | -1.0053 | -1.0403 | -1.0803 | -1.3497 | -1.6116 | -1.7594 | -1.0929 | -1.1116 | -1.136 | -1.1627 | -1.1946 | -1.2225 | -1.2563 | -1.2935 | -1.332 | -1.3734 | -1.434 | -1.8826 | -2.2338 | -2.4427
| WILLOWDALE | ST NICHOLAS | MINIMUM HEADROOM | NJ 93737 06782 | NO | NO | 27.1959 | 27.0263 | 26.9108 | 26.7152 | 26.5216 | 26.255 | 25.9459 | 25.6574 | 25.344 | 25.0221 | 24.7063 | 23.8882 | 23.4031 | 22.6256 | 27.0955 | 26.9554 | 26.8275 | 26.6877 | 26.563 | 26.4236 | 26.273 | 26.0893 | 25.853 | 25.6151 | 25.3389 | 23.9986 | 21.4567 | 16.7569 | 26.4032 | 26.2767 | 26.1682 | 26.0053 | 25.833 | 25.5977 | 25.3255 | 25.0647 | 24.7819 | 24.493 | 24.2089 | 23.4118 | 22.8472 | 21.9161
|  | ST NICHOLAS | CT |  |  |  | 27.2333 | 27.0716 | 26.9539 | 26.7737 | 26.5747 | 26.3535 | 26.1177 | 25.9035 | 25.681 | 25.4702 | 25.2223 | 24.3711 | 23.8997 | 23.5635 | 27.0955 | 26.9554 | 26.8275 | 26.6877 | 26.563 | 26.4236 | 26.273 | 26.0893 | 25.853 | 25.6151 | 25.3389 | 23.9986 | 22.4737 | 20.1155 | 26.4032 | 26.2767 | 26.2032 | 26.0486 | 25.8711 | 25.6755 | 25.4677 | 25.2732 | 25.0716 | 24.881 | 24.6574 | 23.8757 | 23.3957 | 23.0256
|  | ST NICHOLAS | LW |  |  |  | 27.1959 | 27.0263 | 26.9108 | 26.7152 | 26.5216 | 26.255 | 25.9459 | 25.6574 | 25.344 | 25.0221 | 24.7063 | 23.8882 | 23.4031 | 22.6256 | 27.1111 | 26.9871 | 26.9106 | 26.8284 | 26.7459 | 26.6306 | 26.4964 | 26.3455 | 26.1107 | 25.857 | 25.6084 | 24.9394 | 24.4129 | 23.5697 | 26.4045 | 26.2878 | 26.1682 | 26.0053 | 25.833 | 25.5977 | 25.3255 | 25.0647 | 24.7819 | 24.493 | 24.2089 | 23.4118 | 22.8472 | 21.9161
|  | ST NICHOLAS | ST |  |  |  | 27.2901 | 27.1865 | 27.1774 | 27.1624 | 27.1346 | 27.0864 | 27.026 | 26.9192 | 26.8276 | 26.6817 | 26.5036 | 25.4852 | 24.8971 | 24.3445 | 27.1354 | 27.0373 | 26.9951 | 26.9438 | 26.8821 | 26.8061 | 26.7152 | 26.5665 | 26.4372 | 26.2422 | 25.998 | 24.4633 | 22.7524 | 20.2386 | 26.4278 | 26.3497 | 26.3347 | 26.3137 | 26.2851 | 26.2442 | 26.1911 | 26.0799 | 25.9908 | 25.8948 | 25.7757 | 24.8807 | 24.2671 | 23.6682
|  | ST NICHOLAS | FS |  |  |  | 27.2948 | 27.2115 | 27.1963 | 27.1751 | 27.1516 | 27.124 | 27.0952 | 27.0439 | 26.9769 | 26.8695 | 26.7509 | 25.9872 | 25.2037 | 24.6396 | 27.1311 | 27.0418 | 26.9864 | 26.9205 | 26.8473 | 26.7614 | 26.6664 | 26.5402 | 26.4065 | 26.1919 | 25.9458 | 24.2265 | 21.4567 | 16.7569 | 26.4343 | 26.3632 | 26.35 | 26.3337 | 26.3122 | 26.2874 | 26.2594 | 26.2076 | 26.1569 | 26.1006 | 26.0383 | 25.3649 | 24.6647 | 24.1443
| ARDMORE | STOCKINISH | MINIMUM HEADROOM | NG 13447 94222 | YES | YES | -0.049063 | -0.090899 | -0.1231 | -0.15983 | -0.19877 | -0.24004 | -0.27968 | -0.30404 | -0.33241 | -0.36166 | -0.38951 | -0.43516 | -0.46225 | -0.48202 | 0.45967 | 0.43252 | 0.41731 | 0.39749 | 0.377 | 0.3556 | 0.33167 | 0.3067 | 0.28057 | 0.25382 | 0.22921 | 0.19399 | 0.17117 | 0.15174 | 0.44135 | 0.41668 | 0.40192 | 0.38929 | 0.37715 | 0.33986 | 0.3032 | 0.27188 | 0.23999 | 0.2072 | 0.17648 | 0.12916 | 0.10629 | 0.088301
|  | STOCKINISH | CT |  |  |  | -0.034124 | -0.064805 | -0.10945 | -0.15983 | -0.19877 | -0.24004 | -0.27968 | -0.30126 | -0.32878 | -0.357 | -0.38154 | -0.42377 | -0.46225 | -0.48202 | 0.45967 | 0.43252 | 0.41731 | 0.39749 | 0.377 | 0.3556 | 0.33447 | 0.31533 | 0.28947 | 0.26293 | 0.23994 | 0.19399 | 0.17117 | 0.15174 | 0.44135 | 0.41668 | 0.40192 | 0.38929 | 0.37715 | 0.33986 | 0.30382 | 0.28019 | 0.24886 | 0.21673 | 0.1892 | 0.14003 | 0.10629 | 0.088301
|  | STOCKINISH | LW |  |  |  | -0.049063 | -0.090899 | -0.1231 | -0.15635 | -0.1895 | -0.23285 | -0.27558 | -0.30404 | -0.33241 | -0.36166 | -0.38951 | -0.43516 | -0.45251 | -0.45871 | 0.46209 | 0.43344 | 0.42165 | 0.40338 | 0.38597 | 0.3594 | 0.33167 | 0.3067 | 0.28057 | 0.25382 | 0.22921 | 0.19421 | 0.1868 | 0.18464 | 0.44446 | 0.41879 | 0.40944 | 0.40035 | 0.38653 | 0.34498 | 0.3032 | 0.27188 | 0.23999 | 0.2072 | 0.17648 | 0.12916 | 0.11403 | 0.10891
|  | STOCKINISH | ST |  |  |  | -0.016914 | -0.033696 | -0.048963 | -0.064178 | -0.077238 | -0.092889 | -0.11123 | -0.12743 | -0.15393 | -0.17819 | -0.20407 | -0.34485 | -0.38194 | -0.40086 | 0.46662 | 0.44702 | 0.44113 | 0.43408 | 0.42578 | 0.41631 | 0.40439 | 0.3915 | 0.37546 | 0.35713 | 0.33664 | 0.22692 | 0.19791 | 0.18107 | 0.44834 | 0.43139 | 0.42586 | 0.41903 | 0.41096 | 0.40149 | 0.38964 | 0.37634 | 0.35992 | 0.34108 | 0.31986 | 0.18544 | 0.13412 | 0.11729
|  | STOCKINISH | FS |  |  |  | -0.014088 | -0.027142 | -0.03984 | -0.051641 | -0.062672 | -0.077368 | -0.092198 | -0.10643 | -0.12785 | -0.14695 | -0.16755 | -0.30677 | -0.40869 | -0.43272 | 0.46769 | 0.4529 | 0.44852 | 0.44304 | 0.43678 | 0.43011 | 0.42231 | 0.41353 | 0.40319 | 0.3913 | 0.37576 | 0.27366 | 0.18971 | 0.16447 | 0.44931 | 0.43655 | 0.43257 | 0.42731 | 0.42137 | 0.41484 | 0.40722 | 0.39842 | 0.38818 | 0.37676 | 0.36398 | 0.25628 | 0.15131 | 0.1036
| PORT ANN | STONEFIELD | MINIMUM HEADROOM | NR 86244 73400 | YES | YES | 0.3326 | 0.33204 | 0.25333 | 0.19559 | 0.15842 | 0.024336 | -0.01292 | -0.10861 | -0.1432 | -0.17123 | -0.21984 | -0.44287 | -0.76198 | -1.0862 | 0.31914 | 0.31863 | 0.21725 | 0.14667 | 0.10037 | -0.060691 | -0.10564 | -0.22512 | -0.26798 | -0.30392 | -0.36255 | -0.63616 | -1.031 | -1.4346 | 0.30301 | 0.30238 | 0.20269 | 0.13121 | 0.084848 | -0.079897 | -0.12569 | -0.2453 | -0.28832 | -0.32368 | -0.38346 | -0.65961 | -1.0566 | -1.4612
|  | STONEFIELD | CT |  |  |  | 0.33618 | 0.33546 | 0.32034 | 0.2967 | 0.20117 | 0.10104 | 0.073784 | 0.029562 | -0.013744 | -0.054597 | -0.097127 | -0.32394 | -0.5312 | -0.75631 | 0.32056 | 0.32003 | 0.30458 | 0.27869 | 0.1625 | 0.039263 | 0.007136 | -0.047748 | -0.10258 | -0.15143 | -0.20414 | -0.48194 | -0.74063 | -1.0203 | 0.30617 | 0.30542 | 0.28804 | 0.2601 | 0.1421 | 0.017804 | -0.015377 | -0.070457 | -0.12479 | -0.17479 | -0.22762 | -0.50851 | -0.76738 | -1.048
|  | STONEFIELD | LW |  |  |  | 0.3326 | 0.33204 | 0.33304 | 0.32501 | 0.32113 | 0.31663 | 0.31554 | 0.29726 | 0.27971 | 0.26371 | 0.24419 | 0.15348 | -0.23042 | -0.79231 | 0.31914 | 0.31863 | 0.31876 | 0.31553 | 0.31391 | 0.31184 | 0.31086 | 0.28858 | 0.26599 | 0.24656 | 0.22435 | 0.11477 | -0.3648 | -1.0672 | 0.30301 | 0.30238 | 0.30319 | 0.29608 | 0.29269 | 0.28871 | 0.2875 | 0.26495 | 0.24285 | 0.22326 | 0.19992 | 0.088287 | -0.39144 | -1.0938
|  | STONEFIELD | ST |  |  |  | 0.33635 | 0.33458 | 0.25333 | 0.19559 | 0.15842 | 0.024336 | -0.01292 | -0.10861 | -0.1432 | -0.17123 | -0.21984 | -0.44287 | -0.76198 | -1.0862 | 0.32068 | 0.31986 | 0.21725 | 0.14667 | 0.10037 | -0.060691 | -0.10564 | -0.22512 | -0.26798 | -0.30392 | -0.36255 | -0.63616 | -1.031 | -1.4346 | 0.30633 | 0.30468 | 0.20269 | 0.13121 | 0.084848 | -0.079897 | -0.12569 | -0.2453 | -0.28832 | -0.32368 | -0.38346 | -0.65961 | -1.0566 | -1.4612
|  | STONEFIELD | FS |  |  |  | 0.33638 | 0.33464 | 0.31899 | 0.30185 | 0.28028 | 0.25694 | 0.23785 | 0.20295 | 0.17905 | 0.15507 | 0.12773 | 0.090917 | 0.061987 | 0.023714 | 0.32071 | 0.31991 | 0.29926 | 0.278 | 0.25256 | 0.22651 | 0.20445 | 0.16103 | 0.1314 | 0.10171 | 0.070754 | 0.030239 | 0.00041184 | -0.045522 | 0.30636 | 0.30474 | 0.28474 | 0.26339 | 0.23709 | 0.20926 | 0.1862 | 0.14269 | 0.11295 | 0.083144 | 0.050382 | 0.007028 | -0.026098 | -0.073132
| FIDDES | STONEHAVEN | MINIMUM HEADROOM | NO 85903 85641 | NO | YES | 10.2859 | 9.8295 | 8.9467 | 7.9978 | 6.9217 | 5.4918 | 4.0213 | 2.7626 | 1.5448 | 0.27736 | -0.79149 | -3.7033 | -5.1701 | -6.3161 | 12.7457 | 12.4568 | 11.941 | 11.3665 | 10.6404 | 9.5862 | 8.5371 | 7.6063 | 6.7589 | 5.8832 | 5.1759 | 3.3754 | 2.2046 | 0.57144 | 12.4729 | 12.0375 | 11.2065 | 10.3054 | 9.2494 | 7.8332 | 6.4011 | 5.1819 | 4.0523 | 2.8873 | 1.9098 | -0.8076 | -2.2762 | -3.4688
|  | STONEHAVEN | CT |  |  |  | 10.7498 | 10.4776 | 9.6755 | 8.811 | 7.8739 | 6.7378 | 5.688 | 4.4521 | 3.2317 | 1.9936 | 0.91651 | -2.6603 | -4.8109 | -6.0462 | 12.8869 | 12.675 | 12.1991 | 11.6648 | 10.9954 | 10.1487 | 9.4525 | 8.6001 | 7.7563 | 6.9089 | 6.1965 | 3.8026 | 2.2046 | 0.57144 | 12.8651 | 12.599 | 11.8566 | 11.0543 | 10.1208 | 8.9909 | 8.0051 | 6.8439 | 5.6997 | 4.5523 | 3.5573 | 0.20483 | -1.8001 | -2.9275
|  | STONEHAVEN | LW |  |  |  | 10.2859 | 9.8295 | 8.9467 | 7.9978 | 6.9217 | 5.4918 | 4.0213 | 2.7626 | 1.5448 | 0.27736 | -0.79149 | -3.7033 | -5.1701 | -6.3161 | 12.7457 | 12.4568 | 11.941 | 11.3665 | 10.6404 | 9.5862 | 8.5371 | 7.6063 | 6.7589 | 5.8832 | 5.1759 | 3.3754 | 2.4219 | 1.3986 | 12.4729 | 12.0375 | 11.2065 | 10.3054 | 9.2494 | 7.8332 | 6.4011 | 5.1819 | 4.0523 | 2.8873 | 1.9098 | -0.8076 | -2.2762 | -3.4688
|  | STONEHAVEN | ST |  |  |  | 10.9561 | 10.8393 | 10.4705 | 10.121 | 9.7947 | 9.0568 | 8.425 | 7.6898 | 7.0356 | 6.3309 | 5.7247 | 2.2316 | 0.16172 | -1.8343 | 12.9996 | 12.9061 | 12.5319 | 12.2077 | 11.9207 | 11.1902 | 10.6403 | 9.9862 | 9.4325 | 8.8395 | 8.3271 | 5.5252 | 3.7254 | 1.7254 | 13.0538 | 12.9415 | 12.5374 | 12.1806 | 11.8613 | 11.0839 | 10.4738 | 9.765 | 9.1548 | 8.5018 | 7.944 | 4.6282 | 2.669 | 0.75774
|  | STONEHAVEN | FS |  |  |  | 11.0081 | 10.9178 | 10.7275 | 10.4986 | 10.2546 | 9.8929 | 9.4349 | 8.8439 | 8.3339 | 7.7844 | 7.2807 | 4.1557 | 1.148 | -0.79405 | 13.0229 | 12.9441 | 12.7832 | 12.5978 | 12.3934 | 12.0851 | 11.6908 | 11.2054 | 10.7927 | 10.3407 | 9.9261 | 7.4179 | 4.5054 | 1.5251 | 13.1008 | 13.0136 | 12.8246 | 12.6083 | 12.3767 | 12.0328 | 11.5981 | 11.0398 | 10.5646 | 10.0542 | 9.5906 | 6.7429 | 3.9742 | 2.159
| STRICHEN | STONEYHILL | MINIMUM HEADROOM | NK 6773 4109 | YES | YES | -2.8668 | -2.8682 | -2.8731 | -2.878 | -2.8818 | -2.8924 | -2.8965 | -2.9489 | -2.9691 | -2.9868 | -3.014 | -3.1431 | -3.5283 | -4.0842 | -3.0287 | -3.0288 | -3.0364 | -3.0417 | -3.0452 | -3.0571 | -3.0605 | -3.1239 | -3.1465 | -3.1661 | -3.1996 | -3.3585 | -3.8406 | -4.5354 | -3.448 | -3.4487 | -3.4558 | -3.4614 | -3.4654 | -3.4778 | -3.4819 | -3.5461 | -3.5696 | -3.5899 | -3.6218 | -3.7719 | -4.2524 | -4.9472
|  | STONEYHILL | CT |  |  |  | -2.8668 | -2.8682 | -2.8709 | -2.8736 | -2.8818 | -2.8906 | -2.8941 | -2.9193 | -2.9441 | -2.9659 | -2.9905 | -3.1142 | -3.3001 | -3.5207 | -3.0287 | -3.0288 | -3.0299 | -3.0318 | -3.0405 | -3.0498 | -3.0522 | -3.0816 | -3.1124 | -3.1392 | -3.1695 | -3.323 | -3.5561 | -3.8319 | -3.448 | -3.4487 | -3.4507 | -3.4532 | -3.4625 | -3.4724 | -3.4755 | -3.5054 | -3.5352 | -3.5611 | -3.5899 | -3.7393 | -3.9715 | -4.2473
|  | STONEYHILL | LW |  |  |  | -2.8665 | -2.868 | -2.8691 | -2.8704 | -2.8718 | -2.8741 | -2.877 | -2.9072 | -2.9388 | -2.9655 | -2.995 | -3.1381 | -3.5283 | -4.0842 | -3.0287 | -3.0288 | -3.0289 | -3.029 | -3.0291 | -3.0293 | -3.0295 | -3.0662 | -3.105 | -3.1379 | -3.1741 | -3.3525 | -3.8406 | -4.5354 | -3.4479 | -3.4486 | -3.4492 | -3.4499 | -3.4506 | -3.4518 | -3.4533 | -3.4887 | -3.5256 | -3.5563 | -3.5906 | -3.7647 | -4.2524 | -4.9472
|  | STONEYHILL | ST |  |  |  | -2.8659 | -2.8664 | -2.8731 | -2.878 | -2.8817 | -2.8924 | -2.8965 | -2.9489 | -2.9691 | -2.9868 | -3.014 | -3.1431 | -3.4339 | -3.7528 | -3.0286 | -3.0287 | -3.0364 | -3.0417 | -3.0452 | -3.0571 | -3.0605 | -3.1239 | -3.1465 | -3.1661 | -3.1996 | -3.3585 | -3.7217 | -4.1204 | -3.4476 | -3.4478 | -3.4558 | -3.4614 | -3.4654 | -3.4778 | -3.4819 | -3.5461 | -3.5696 | -3.5899 | -3.6218 | -3.7719 | -4.1322 | -4.5308
|  | STONEYHILL | FS |  |  |  | -2.8658 | -2.8662 | -2.8679 | -2.8697 | -2.8718 | -2.874 | -2.8762 | -2.8956 | -2.9092 | -2.9231 | -2.9371 | -2.9627 | -2.9881 | -3.0293 | -3.0286 | -3.0286 | -3.0303 | -3.0319 | -3.0338 | -3.0357 | -3.0373 | -3.0603 | -3.0759 | -3.0916 | -3.1072 | -3.1351 | -3.1657 | -3.2164 | -3.4475 | -3.4477 | -3.4495 | -3.4514 | -3.4535 | -3.4558 | -3.4578 | -3.4813 | -3.4974 | -3.5137 | -3.53 | -3.5543 | -3.5791 | -3.6264
| PERSLEY | STONEYWOOD T1&T2 | MINIMUM HEADROOM | NJ 89285 11082 | NO | YES | 9.7811 | 8.2347 | 6.4857 | 4.569 | 1.6555 | -1.2483 | -3.1029 | -3.9018 | -4.5778 | -5.2004 | -5.9158 | -8.2247 | -8.9178 | -9.4433 | 13.3523 | 11.9031 | 10.2145 | 8.2748 | 5.0761 | 1.9448 | 0.086978 | -0.70988 | -1.522 | -2.2813 | -3.1395 | -5.9808 | -6.7988 | -7.3205 | 12.5594 | 11.1896 | 9.321 | 7.2524 | 3.9066 | 0.5207 | -1.5963 | -2.4299 | -3.1814 | -3.9581 | -4.9228 | -8.0082 | -8.8513 | -9.3822
|  | STONEYWOOD T1&T2 | CT |  |  |  | 10.1515 | 8.7523 | 7.8201 | 6.8404 | 5.0706 | 3.4095 | 2.5887 | 1.9709 | 1.4801 | 1.0247 | 0.47868 | -1.3076 | -1.8661 | -2.1722 | 13.6227 | 12.2605 | 11.5492 | 10.7839 | 9.0111 | 7.3869 | 6.7464 | 6.2155 | 5.7751 | 5.3619 | 4.7554 | 2.6972 | 2.2452 | 2.0068 | 12.8783 | 11.6065 | 10.7839 | 9.8454 | 7.9308 | 6.0993 | 5.2912 | 4.7021 | 4.203 | 3.739 | 3.0524 | 0.70196 | 0.16892 | -0.10408
|  | STONEYWOOD T1&T2 | LW |  |  |  | 9.7811 | 8.2347 | 6.4857 | 4.569 | 1.6555 | -1.2483 | -3.1029 | -3.9018 | -4.5778 | -5.2004 | -5.9158 | -8.2247 | -8.9178 | -9.4433 | 13.3523 | 11.9031 | 10.2145 | 8.2748 | 5.0761 | 1.9448 | 0.086978 | -0.70988 | -1.522 | -2.2813 | -3.1395 | -5.9808 | -6.7988 | -7.3205 | 12.5594 | 11.1896 | 9.321 | 7.2524 | 3.9066 | 0.5207 | -1.5963 | -2.4299 | -3.1814 | -3.9581 | -4.9228 | -8.0082 | -8.8513 | -9.3822
|  | STONEYWOOD T1&T2 | ST |  |  |  | 10.2427 | 8.9295 | 7.4385 | 6.2821 | 5.2913 | 3.5447 | 2.8235 | 2.247 | 1.9093 | 1.5681 | 1.0807 | -1.9472 | -3.106 | -3.4821 | 13.6764 | 12.3797 | 10.7887 | 9.5885 | 8.5983 | 6.655 | 5.9646 | 5.4425 | 5.0746 | 4.6782 | 4.0727 | 1.1102 | 0.04457 | -0.34698 | 12.9593 | 11.7541 | 10.1686 | 8.9573 | 7.9438 | 5.9202 | 5.1532 | 4.5459 | 4.095 | 3.5639 | 2.8297 | -0.62332 | -1.8416 | -2.3093
|  | STONEYWOOD T1&T2 | FS |  |  |  | 11.0284 | 10.0188 | 9.3293 | 8.6709 | 7.9442 | 7.3378 | 6.7896 | 6.3252 | 5.946 | 5.5641 | 5.1192 | 3.3366 | 1.6317 | 0.47229 | 14.4953 | 13.4793 | 12.8442 | 12.2318 | 11.5465 | 11.0019 | 10.5154 | 10.1204 | 9.7652 | 9.4099 | 8.9379 | 6.9118 | 5.5069 | 4.5974 | 13.6264 | 12.7353 | 12.0948 | 11.4767 | 10.7832 | 10.1965 | 9.6566 | 9.2152 | 8.8461 | 8.4725 | 8.0013 | 5.5646 | 3.8094 | 2.6411
| PERSLEY | STONEYWOOD T3 | MINIMUM HEADROOM | NJ 89285 11082 | YES | YES | 6.699 | 6.003 | 5.2059 | 4.2648 | 2.8246 | 1.3921 | 0.47446 | 0.084594 | -0.24622 | -0.55018 | -0.9004 | -2.0441 | -2.3889 | -2.6371 | 8.0391 | 7.3367 | 6.4939 | 5.5425 | 3.9586 | 2.3876 | 1.4428 | 1.1064 | 0.76682 | 0.45577 | 0.091426 | -1.2438 | -1.6571 | -1.9195 | 6.4142 | 5.7132 | 4.8404 | 3.8577 | 2.2325 | 0.57837 | -0.46308 | -0.9006 | -1.3424 | -1.7606 | -2.2259 | -3.747 | -4.1783 | -4.4474
|  | STONEYWOOD T3 | CT |  |  |  | 6.8234 | 6.1681 | 5.8081 | 5.3907 | 4.5213 | 3.7065 | 3.3093 | 3.0081 | 2.7709 | 2.5512 | 2.285 | 1.4052 | 1.1287 | 0.97712 | 8.1624 | 7.4977 | 7.1352 | 6.7478 | 5.8638 | 5.0527 | 4.7479 | 4.5416 | 4.3656 | 4.2024 | 3.9605 | 3.0971 | 2.8768 | 2.7172 | 6.5206 | 5.8507 | 5.4382 | 5.0089 | 4.0783 | 3.2018 | 2.8267 | 2.5338 | 2.2911 | 2.062 | 1.734 | 0.62408 | 0.39261 | 0.27798
|  | STONEYWOOD T3 | LW |  |  |  | 6.699 | 6.003 | 5.2059 | 4.2648 | 2.8246 | 1.3921 | 0.47446 | 0.084594 | -0.24622 | -0.55018 | -0.9004 | -2.0441 | -2.3889 | -2.6371 | 8.0391 | 7.3367 | 6.4939 | 5.5425 | 3.9586 | 2.3876 | 1.4428 | 1.1064 | 0.76682 | 0.45577 | 0.091426 | -1.2438 | -1.6571 | -1.9195 | 6.4142 | 5.7132 | 4.8404 | 3.8577 | 2.2325 | 0.57837 | -0.46308 | -0.9006 | -1.3424 | -1.7606 | -2.2259 | -3.747 | -4.1783 | -4.4474
|  | STONEYWOOD T3 | ST |  |  |  | 6.8604 | 6.25 | 5.5596 | 5.0265 | 4.5683 | 3.7334 | 3.4011 | 3.1337 | 2.971 | 2.8013 | 2.5489 | 1.1561 | 0.59748 | 0.43495 | 8.2007 | 7.5819 | 6.791 | 6.1938 | 5.701 | 4.719 | 4.3586 | 4.0767 | 3.9067 | 3.7315 | 3.4628 | 2.2517 | 1.7272 | 1.5401 | 6.5899 | 5.9998 | 5.2037 | 4.5925 | 4.0735 | 3.0484 | 2.6352 | 2.288 | 2.0427 | 1.7811 | 1.4168 | -0.2825 | -0.86785 | -1.0552
|  | STONEYWOOD T3 | FS |  |  |  | 7.2262 | 6.7417 | 6.4365 | 6.1429 | 5.814 | 5.5454 | 5.3034 | 5.099 | 4.9232 | 4.7448 | 4.5323 | 3.6954 | 2.9489 | 2.4047 | 8.5888 | 8.1043 | 7.7931 | 7.4914 | 7.1513 | 6.8762 | 6.6277 | 6.4236 | 6.2385 | 6.0509 | 5.8276 | 4.9557 | 4.4324 | 4.0079 | 6.9497 | 6.4888 | 6.1725 | 5.8619 | 5.5072 | 5.2075 | 4.9294 | 4.6923 | 4.474 | 4.2472 | 3.9793 | 2.7879 | 1.9368 | 1.4108
| CLACHAN | STRACHUR | MINIMUM HEADROOM | NN 08672 01180 | YES | YES | 0.13531 | 0.12692 | 0.087472 | 0.046393 | 0.0017387 | -0.045959 | -0.095471 | -0.12257 | -0.16674 | -0.22555 | -0.28093 | -0.37772 | -0.44563 | -0.4831 | 0.52093 | 0.49141 | 0.46027 | 0.42055 | 0.37815 | 0.3381 | 0.30278 | 0.26101 | 0.21316 | 0.16405 | 0.12367 | 0.029438 | -0.020617 | -0.065111 | 0.28069 | 0.27601 | 0.27048 | 0.23411 | 0.18289 | 0.1238 | 0.063486 | 0.0039216 | -0.059211 | -0.11798 | -0.17294 | -0.27515 | -0.33694 | -0.37388
|  | STRACHUR | CT |  |  |  | 0.13692 | 0.13254 | 0.1084 | 0.060319 | 0.004199 | -0.045959 | -0.095471 | -0.12257 | -0.15154 | -0.2179 | -0.26803 | -0.37772 | -0.44563 | -0.4831 | 0.53119 | 0.50677 | 0.46563 | 0.42055 | 0.37815 | 0.3381 | 0.30278 | 0.2638 | 0.21387 | 0.16405 | 0.12367 | 0.029438 | -0.020617 | -0.065111 | 0.28214 | 0.27809 | 0.27159 | 0.24474 | 0.18289 | 0.1238 | 0.068383 | 0.016775 | -0.048183 | -0.11338 | -0.16377 | -0.27515 | -0.33694 | -0.37388
|  | STRACHUR | LW |  |  |  | 0.13531 | 0.12692 | 0.087472 | 0.046393 | 0.0017387 | -0.042029 | -0.082969 | -0.10784 | -0.16674 | -0.22555 | -0.28093 | -0.37175 | -0.42334 | -0.46807 | 0.52093 | 0.49141 | 0.46027 | 0.42624 | 0.39444 | 0.35178 | 0.30629 | 0.26101 | 0.21316 | 0.16749 | 0.12514 | 0.057886 | 0.015166 | -0.03346 | 0.28069 | 0.27601 | 0.27048 | 0.23411 | 0.19393 | 0.12997 | 0.063486 | 0.0039216 | -0.059211 | -0.11798 | -0.17294 | -0.26062 | -0.31261 | -0.36461
|  | STRACHUR | ST |  |  |  | 0.13859 | 0.13557 | 0.12742 | 0.12047 | 0.11451 | 0.099957 | 0.081352 | 0.057572 | 0.0361 | 0.014005 | -0.0062597 | -0.22447 | -0.29672 | -0.34405 | 0.54152 | 0.52818 | 0.50689 | 0.48455 | 0.46224 | 0.43405 | 0.4102 | 0.37754 | 0.34596 | 0.31209 | 0.27584 | 0.091435 | 0.026152 | -0.023563 | 0.28366 | 0.2809 | 0.27172 | 0.26419 | 0.25793 | 0.24546 | 0.23999 | 0.21362 | 0.17199 | 0.12713 | 0.081233 | -0.14936 | -0.21956 | -0.26492
|  | STRACHUR | FS |  |  |  | 0.13922 | 0.13644 | 0.13234 | 0.12804 | 0.12336 | 0.11955 | 0.10517 | 0.085761 | 0.06812 | 0.054311 | 0.035195 | -0.11588 | -0.27235 | -0.3093 | 0.54464 | 0.5328 | 0.51784 | 0.50028 | 0.48187 | 0.46515 | 0.44605 | 0.42355 | 0.40118 | 0.37925 | 0.35349 | 0.2039 | 0.077838 | 0.036211 | 0.28424 | 0.28169 | 0.27759 | 0.27329 | 0.26859 | 0.26465 | 0.26085 | 0.25537 | 0.23576 | 0.20795 | 0.17346 | -0.025974 | -0.17885 | -0.21026
| TARLAND | STRATHDON | MINIMUM HEADROOM | NJ 37343 11904 | YES | YES | 0.015268 | -0.034729 | -0.085948 | -0.13635 | -0.26059 | -0.40554 | -0.48785 | -0.55451 | -0.62606 | -0.70303 | -0.77955 | -1.1196 | -1.5021 | -1.8443 | 0.27182 | 0.24931 | 0.18697 | 0.11454 | 0.056518 | -0.086982 | -0.14096 | -0.2609 | -0.31857 | -0.37302 | -0.44791 | -0.80766 | -1.1894 | -1.5614 | 0.22038 | 0.1722 | 0.12386 | 0.058701 | -0.080944 | -0.24137 | -0.32368 | -0.40585 | -0.49894 | -0.58276 | -0.66694 | -1.0757 | -1.5136 | -1.9147
|  | STRATHDON | CT |  |  |  | 0.060299 | 0.026296 | -0.044406 | -0.12462 | -0.26059 | -0.40554 | -0.48785 | -0.55451 | -0.62606 | -0.70303 | -0.77955 | -1.068 | -1.3489 | -1.5811 | 0.28563 | 0.26936 | 0.2284 | 0.17693 | 0.056518 | -0.071755 | -0.12296 | -0.1913 | -0.26779 | -0.33737 | -0.40769 | -0.69931 | -0.95861 | -1.2212 | 0.26151 | 0.22889 | 0.15542 | 0.06982 | -0.080944 | -0.24137 | -0.32368 | -0.40585 | -0.49894 | -0.58276 | -0.66694 | -0.99458 | -1.3064 | -1.5804
|  | STRATHDON | LW |  |  |  | 0.015268 | -0.034729 | -0.085948 | -0.13635 | -0.18494 | -0.24763 | -0.30503 | -0.35735 | -0.41179 | -0.47209 | -0.53339 | -0.70614 | -1.0763 | -1.5721 | 0.27182 | 0.24931 | 0.22782 | 0.20501 | 0.18493 | 0.15345 | 0.12122 | 0.073723 | 0.025599 | -0.020633 | -0.066674 | -0.205 | -0.62324 | -1.2206 | 0.22038 | 0.1722 | 0.12386 | 0.074783 | 0.029874 | -0.033148 | -0.093594 | -0.15829 | -0.22095 | -0.2833 | -0.3458 | -0.52824 | -0.97317 | -1.5839
|  | STRATHDON | ST |  |  |  | 0.079237 | 0.058825 | -0.034173 | -0.1131 | -0.17483 | -0.31612 | -0.37932 | -0.49592 | -0.56131 | -0.62426 | -0.70896 | -1.1196 | -1.5021 | -1.8443 | 0.29381 | 0.28444 | 0.18697 | 0.11454 | 0.062157 | -0.086982 | -0.14096 | -0.2609 | -0.31857 | -0.37302 | -0.44791 | -0.80766 | -1.1894 | -1.5614 | 0.27741 | 0.25898 | 0.14757 | 0.058701 | -0.0091483 | -0.17554 | -0.24577 | -0.38333 | -0.45828 | -0.53054 | -0.62472 | -1.0757 | -1.5136 | -1.9147
|  | STRATHDON | FS |  |  |  | 0.094728 | 0.080199 | 0.045288 | 0.010152 | -0.027719 | -0.068613 | -0.11134 | -0.17313 | -0.22671 | -0.28444 | -0.34031 | -0.62841 | -0.82289 | -0.91926 | 0.29959 | 0.29261 | 0.26532 | 0.23744 | 0.20625 | 0.17401 | 0.14265 | 0.090569 | 0.048724 | 0.0045828 | -0.039918 | -0.20492 | -0.32719 | -0.40462 | 0.2785 | 0.27547 | 0.24193 | 0.20211 | 0.15896 | 0.11425 | 0.068808 | 0.00016253 | -0.058484 | -0.12139 | -0.18349 | -0.47278 | -0.6586 | -0.75499
| STRICHEN | STRICHEN | MINIMUM HEADROOM | NJ 95900 55137 | NO | YES | 9.9423 | 9.7762 | 9.5942 | 9.2104 | 8.9037 | 8.6036 | 8.3568 | 8.2042 | 8.0329 | 7.8619 | 7.6967 | 7.2334 | 6.752 | 6.427 | 10.9365 | 10.8534 | 10.7686 | 10.4802 | 10.218 | 10.0163 | 9.8848 | 9.7588 | 9.6129 | 9.4699 | 9.3311 | 8.892 | 8.3982 | 7.9467 | 9.7308 | 9.5804 | 9.4189 | 9.0692 | 8.7495 | 8.4556 | 8.23 | 8.0694 | 7.8847 | 7.7016 | 7.5262 | 7.0205 | 6.5441 | 6.093
|  | STRICHEN | CT |  |  |  | 10.0849 | 9.9647 | 9.7162 | 9.2702 | 8.9037 | 8.6036 | 8.3568 | 8.2042 | 8.0329 | 7.8619 | 7.6967 | 7.2334 | 6.752 | 6.4413 | 10.9871 | 10.9225 | 10.7924 | 10.4802 | 10.218 | 10.0163 | 9.8848 | 9.7588 | 9.6129 | 9.4699 | 9.3311 | 8.892 | 8.5275 | 8.1907 | 9.8518 | 9.7422 | 9.5152 | 9.1011 | 8.7495 | 8.4556 | 8.23 | 8.0694 | 7.8847 | 7.7016 | 7.5262 | 7.0205 | 6.5441 | 6.2066
|  | STRICHEN | LW |  |  |  | 9.9423 | 9.7762 | 9.5942 | 9.2104 | 8.95 | 8.7296 | 8.4938 | 8.3322 | 8.162 | 7.9921 | 7.8324 | 7.4399 | 6.9875 | 6.4604 | 10.9365 | 10.8534 | 10.7686 | 10.5041 | 10.3481 | 10.2298 | 10.0988 | 9.9744 | 9.842 | 9.7101 | 9.5859 | 9.2974 | 8.8526 | 8.2566 | 9.7308 | 9.5804 | 9.4189 | 9.0692 | 8.8377 | 8.6348 | 8.4154 | 8.2486 | 8.0722 | 7.8963 | 7.7311 | 7.3386 | 6.8319 | 6.2044
|  | STRICHEN | ST |  |  |  | 10.1719 | 10.11 | 9.9567 | 9.6225 | 9.423 | 9.2175 | 9.0792 | 8.8838 | 8.7301 | 8.5632 | 8.3812 | 7.4819 | 6.8858 | 6.427 | 11.0242 | 10.9939 | 10.8702 | 10.5937 | 10.4378 | 10.2549 | 10.1571 | 9.9911 | 9.8776 | 9.7579 | 9.6159 | 8.9077 | 8.3982 | 7.9467 | 9.9267 | 9.8719 | 9.7123 | 9.3912 | 9.2012 | 8.9797 | 8.8426 | 8.6354 | 8.4802 | 8.3136 | 8.1264 | 7.2011 | 6.5825 | 6.093
|  | STRICHEN | FS |  |  |  | 10.2194 | 10.1765 | 10.0923 | 9.8595 | 9.701 | 9.5884 | 9.4741 | 9.333 | 9.188 | 9.05 | 8.9084 | 8.0633 | 7.4983 | 7.2331 | 11.0421 | 11.0196 | 10.9692 | 10.788 | 10.6695 | 10.5937 | 10.517 | 10.4169 | 10.3192 | 10.225 | 10.1286 | 9.6144 | 9.1939 | 8.945 | 9.9672 | 9.9287 | 9.8494 | 9.6321 | 9.4841 | 9.3767 | 9.2677 | 9.1292 | 8.9893 | 8.8548 | 8.7161 | 7.919 | 7.3694 | 7.1311
| THURSO | STROMNESS | MINIMUM HEADROOM | HY 25978 10409 | NO | YES | -2.5168 | -12.7207 | -13.3535 | -14.1053 | -14.7419 | -15.1267 | -15.5746 | -15.9032 | -16.083 | -16.3352 | -16.5661 | -17.0457 | -17.6459 | -18.2904 | -3.7615 | -16.3056 | -16.742 | -17.2998 | -17.7435 | -17.9743 | -18.2627 | -18.5797 | -18.7688 | -19.0184 | -19.2508 | -19.7316 | -20.2738 | -20.9725 | -3.6857 | -16.3188 | -16.8998 | -17.6062 | -18.1977 | -18.5308 | -18.9236 | -19.2391 | -19.4063 | -19.6463 | -19.8707 | -20.4172 | -21.0625 | -21.7863
|  | STROMNESS | CT |  |  |  | 6.477 | 4.9638 | 4.2168 | 3.4129 | 2.6554 | 2.1818 | 1.6588 | 1.4313 | 1.2923 | 1.0822 | 0.88935 | 0.59856 | 0.031541 | -0.37833 | 7.2611 | 5.5103 | 5.0902 | 4.5377 | 4.0339 | 3.792 | 3.5079 | 3.2381 | 3.0654 | 2.8325 | 2.615 | 2.1333 | 1.6445 | 1.1165 | 7.464 | 5.668 | 4.9864 | 4.2564 | 3.563 | 3.1624 | 2.7126 | 2.4406 | 2.3398 | 2.1723 | 1.9771 | 1.5731 | 1.0595 | 0.64228
|  | STROMNESS | LW |  |  |  | -2.5168 | -12.7207 | -13.3535 | -14.1053 | -14.7419 | -15.1267 | -15.5746 | -15.9032 | -16.083 | -16.3352 | -16.5661 | -17.0457 | -17.6459 | -18.2904 | -3.7615 | -16.3056 | -16.742 | -17.2998 | -17.7435 | -17.9743 | -18.2627 | -18.5797 | -18.7688 | -19.0184 | -19.2508 | -19.7316 | -20.2738 | -20.9725 | -3.6857 | -16.3188 | -16.8998 | -17.6062 | -18.1977 | -18.5308 | -18.9236 | -19.2391 | -19.4063 | -19.6463 | -19.8707 | -20.4172 | -21.0625 | -21.7863
|  | STROMNESS | ST |  |  |  | 2.1032 | -4.0766 | -4.4117 | -4.8121 | -5.186 | -5.2769 | -5.4405 | -5.7533 | -5.9069 | -6.1332 | -6.4101 | -7.5027 | -8.1443 | -8.6425 | 1.6864 | -5.9762 | -6.3318 | -6.7532 | -7.148 | -7.2364 | -7.3872 | -7.6849 | -7.8085 | -8.0359 | -8.2884 | -9.3017 | -9.9188 | -10.3818 | 2.0095 | -5.6554 | -6.0254 | -6.4665 | -6.8828 | -7.013 | -7.1994 | -7.5414 | -7.7199 | -7.9858 | -8.2947 | -9.5799 | -10.3241 | -10.8728
|  | STROMNESS | FS |  |  |  | 8.1172 | 7.6424 | 7.3785 | 7.0413 | 6.6993 | 6.505 | 6.2959 | 6.0004 | 5.7738 | 5.5253 | 5.2798 | 3.9828 | 3.1868 | 2.8616 | 9.1333 | 8.59 | 8.3105 | 7.9829 | 7.669 | 7.5218 | 7.352 | 7.0869 | 6.8841 | 6.6483 | 6.4216 | 5.4711 | 4.7507 | 4.2249 | 9.4426 | 8.8967 | 8.5762 | 8.2058 | 7.8494 | 7.6449 | 7.4234 | 7.1107 | 6.867 | 6.5982 | 6.3352 | 5.1507 | 4.3563 | 3.8689
| THURSO | STRONSAY | MINIMUM HEADROOM | HY 64548 27016 | YES | YES | 0.66159 | 0.64874 | 0.63133 | 0.60376 | 0.56177 | 0.51397 | 0.48729 | 0.46229 | 0.43518 | 0.40922 | 0.38491 | 0.30111 | 0.22247 | 0.13478 | 0.78239 | 0.7748 | 0.75991 | 0.73924 | 0.70335 | 0.66043 | 0.64172 | 0.61778 | 0.5905 | 0.56396 | 0.53874 | 0.42931 | 0.31203 | 0.19535 | 0.72061 | 0.70863 | 0.6927 | 0.66433 | 0.61804 | 0.56601 | 0.53949 | 0.51137 | 0.47973 | 0.4496 | 0.42215 | 0.32446 | 0.22246 | 0.10509
|  | STRONSAY | CT |  |  |  | 0.67245 | 0.66062 | 0.63274 | 0.60376 | 0.56177 | 0.51397 | 0.48729 | 0.46229 | 0.43518 | 0.40922 | 0.38491 | 0.30111 | 0.22247 | 0.15662 | 0.78643 | 0.77925 | 0.76225 | 0.74262 | 0.70335 | 0.66043 | 0.64172 | 0.61778 | 0.5905 | 0.56396 | 0.53874 | 0.44322 | 0.36144 | 0.27808 | 0.73022 | 0.7192 | 0.6927 | 0.66433 | 0.61804 | 0.56601 | 0.53949 | 0.51137 | 0.47973 | 0.4496 | 0.42215 | 0.32446 | 0.23528 | 0.15586
|  | STRONSAY | LW |  |  |  | 0.66159 | 0.64874 | 0.63133 | 0.61472 | 0.59392 | 0.57545 | 0.55058 | 0.53235 | 0.50874 | 0.48688 | 0.46156 | 0.40844 | 0.29683 | 0.1473 | 0.78239 | 0.7748 | 0.76599 | 0.75698 | 0.74693 | 0.73547 | 0.7208 | 0.70338 | 0.6823 | 0.66263 | 0.64232 | 0.59228 | 0.4625 | 0.27956 | 0.72061 | 0.70863 | 0.6928 | 0.67754 | 0.65874 | 0.64133 | 0.61734 | 0.59628 | 0.57037 | 0.54682 | 0.5212 | 0.46384 | 0.32893 | 0.14396
|  | STRONSAY | ST |  |  |  | 0.68422 | 0.67863 | 0.65555 | 0.63841 | 0.62089 | 0.58267 | 0.56814 | 0.53048 | 0.51041 | 0.49118 | 0.4658 | 0.3329 | 0.23342 | 0.13478 | 0.79147 | 0.78842 | 0.75991 | 0.73924 | 0.72252 | 0.67737 | 0.66122 | 0.62228 | 0.60303 | 0.5841 | 0.55842 | 0.42931 | 0.31203 | 0.19535 | 0.73478 | 0.73353 | 0.70536 | 0.68473 | 0.66582 | 0.61905 | 0.60141 | 0.55798 | 0.53521 | 0.5138 | 0.48571 | 0.34109 | 0.22246 | 0.10509
|  | STRONSAY | FS |  |  |  | 0.68314 | 0.68121 | 0.67192 | 0.65862 | 0.64971 | 0.63837 | 0.6256 | 0.60882 | 0.59458 | 0.57951 | 0.5651 | 0.48567 | 0.42439 | 0.39549 | 0.7912 | 0.78961 | 0.78134 | 0.77129 | 0.76213 | 0.7518 | 0.74129 | 0.72493 | 0.71166 | 0.69772 | 0.68362 | 0.62266 | 0.57041 | 0.53897 | 0.73511 | 0.7342 | 0.72749 | 0.71427 | 0.70384 | 0.6913 | 0.67779 | 0.65873 | 0.64275 | 0.62592 | 0.60934 | 0.5304 | 0.4696 | 0.44031
| FORT WILLIAM | STRONTIAN | MINIMUM HEADROOM | NM 81521 61955 | YES | YES | 0.064849 | 0.055543 | 0.046706 | 0.036048 | 0.0062988 | -0.024918 | -0.066553 | -0.084997 | -0.10718 | -0.12968 | -0.14945 | -0.18298 | -0.20062 | -0.21564 | 0.46372 | 0.45139 | 0.43783 | 0.42094 | 0.40451 | 0.38873 | 0.36825 | 0.34626 | 0.3245 | 0.30241 | 0.28263 | 0.25554 | 0.2404 | 0.22503 | 0.12896 | 0.11798 | 0.1065 | 0.092206 | 0.078068 | 0.063837 | 0.045806 | 0.029074 | 0.014447 | -0.00066383 | -0.01409 | -0.041149 | -0.045832 | -0.049045
|  | STRONTIAN | CT |  |  |  | 0.067189 | 0.05878 | 0.04762 | 0.036048 | 0.0062988 | -0.024918 | -0.066553 | -0.084725 | -0.10546 | -0.12572 | -0.14437 | -0.16951 | -0.20062 | -0.21564 | 0.46903 | 0.45837 | 0.44025 | 0.42094 | 0.40451 | 0.38873 | 0.36825 | 0.35343 | 0.33346 | 0.31156 | 0.29266 | 0.25751 | 0.2404 | 0.22503 | 0.13285 | 0.12273 | 0.10662 | 0.092206 | 0.078068 | 0.063837 | 0.045806 | 0.032811 | 0.023344 | 0.014369 | 0.0027317 | -0.022913 | -0.033654 | -0.039209
|  | STRONTIAN | LW |  |  |  | 0.064849 | 0.055543 | 0.046706 | 0.039235 | 0.019834 | -0.014982 | -0.053998 | -0.084997 | -0.10718 | -0.12968 | -0.14945 | -0.18298 | -0.19431 | -0.2041 | 0.46372 | 0.45139 | 0.43783 | 0.42509 | 0.41321 | 0.39386 | 0.37063 | 0.34626 | 0.3245 | 0.30241 | 0.28263 | 0.25554 | 0.251 | 0.24819 | 0.12896 | 0.11798 | 0.1065 | 0.095358 | 0.084203 | 0.0677 | 0.047144 | 0.029074 | 0.014447 | -0.00066383 | -0.01409 | -0.041149 | -0.045832 | -0.049045
|  | STRONTIAN | ST |  |  |  | 0.07126 | 0.068408 | 0.065592 | 0.062445 | 0.060303 | 0.055721 | 0.046792 | 0.037602 | 0.029577 | 0.022509 | 0.0064033 | -0.098488 | -0.12445 | -0.14023 | 0.4729 | 0.46907 | 0.46404 | 0.45802 | 0.45343 | 0.44567 | 0.43429 | 0.42017 | 0.40537 | 0.39018 | 0.37326 | 0.28446 | 0.2639 | 0.25101 | 0.13753 | 0.13369 | 0.12912 | 0.12365 | 0.11889 | 0.11154 | 0.10149 | 0.090174 | 0.078778 | 0.067403 | 0.054682 | -0.01378 | -0.035841 | -0.042978
|  | STRONTIAN | FS |  |  |  | 0.073174 | 0.068757 | 0.066849 | 0.064162 | 0.061659 | 0.058854 | 0.05233 | 0.044902 | 0.040173 | 0.03561 | 0.029318 | -0.068518 | -0.13811 | -0.1584 | 0.47567 | 0.47014 | 0.46599 | 0.46145 | 0.45639 | 0.45076 | 0.44195 | 0.43178 | 0.42313 | 0.41234 | 0.39998 | 0.32268 | 0.2581 | 0.23781 | 0.14014 | 0.13533 | 0.13128 | 0.1275 | 0.12262 | 0.11726 | 0.10958 | 0.10065 | 0.093695 | 0.085518 | 0.076544 | 0.020406 | -0.021992 | -0.043828
| SHETLAND | SUMBURGH | MINIMUM HEADROOM | HU3900512755 | YES | YES | -0.95087 | -0.99001 | -1.0396 | -1.1109 | -1.1806 | -1.2553 | -1.3315 | -1.3992 | -1.4468 | -1.4979 | -1.5646 | -1.7303 | -1.798 | -1.9175 | -0.23338 | -0.25772 | -0.2915 | -0.32651 | -0.36947 | -0.41648 | -0.46552 | -0.52551 | -0.5688 | -0.61433 | -0.67541 | -0.88262 | -0.99034 | -1.0574 | -0.06141 | -0.10262 | -0.1603 | -0.22551 | -0.28954 | -0.35818 | -0.4284 | -0.49265 | -0.53811 | -0.5923 | -0.66976 | -0.87481 | -1.0184 | -1.1274
|  | SUMBURGH | CT |  |  |  | -0.9352 | -0.97211 | -1.0396 | -1.1109 | -1.1806 | -1.2553 | -1.3315 | -1.3992 | -1.4468 | -1.4979 | -1.5646 | -1.7303 | -1.798 | -1.8234 | -0.23315 | -0.25772 | -0.2915 | -0.32651 | -0.36947 | -0.41648 | -0.46552 | -0.52551 | -0.5688 | -0.61433 | -0.67541 | -0.84198 | -0.87261 | -0.88178 | -0.053569 | -0.096543 | -0.1603 | -0.22551 | -0.28954 | -0.35818 | -0.4284 | -0.49265 | -0.53811 | -0.5923 | -0.66976 | -0.8738 | -0.92741 | -0.94661
|  | SUMBURGH | LW |  |  |  | -0.95087 | -0.99001 | -1.0346 | -1.0817 | -1.1296 | -1.1894 | -1.2613 | -1.309 | -1.3603 | -1.4115 | -1.4597 | -1.5515 | -1.584 | -1.59 | -0.23338 | -0.25527 | -0.27716 | -0.30057 | -0.32369 | -0.35571 | -0.39278 | -0.43689 | -0.48419 | -0.53185 | -0.57525 | -0.65232 | -0.66194 | -0.6636 | -0.06141 | -0.10262 | -0.145 | -0.19002 | -0.23484 | -0.29409 | -0.36058 | -0.40616 | -0.45968 | -0.51546 | -0.56846 | -0.64922 | -0.67696 | -0.68147
|  | SUMBURGH | ST |  |  |  | -0.88614 | -0.89347 | -0.90658 | -0.93135 | -0.95684 | -0.98952 | -1.0312 | -1.0811 | -1.1387 | -1.2041 | -1.2765 | -1.6478 | -1.7774 | -1.839 | -0.20785 | -0.21401 | -0.22326 | -0.23636 | -0.2499 | -0.27563 | -0.31183 | -0.3553 | -0.4077 | -0.46766 | -0.53504 | -0.88262 | -0.99034 | -1.0256 | -0.0085213 | -0.019895 | -0.037036 | -0.061355 | -0.085618 | -0.11665 | -0.15613 | -0.21101 | -0.27751 | -0.35311 | -0.43774 | -0.87481 | -1.0184 | -1.0738
|  | SUMBURGH | FS |  |  |  | -0.88666 | -0.89037 | -0.91096 | -0.9299 | -0.95451 | -0.98783 | -1.0178 | -1.0544 | -1.0942 | -1.1374 | -1.1855 | -1.5018 | -1.7578 | -1.9175 | -0.20678 | -0.21025 | -0.22121 | -0.23235 | -0.245 | -0.26128 | -0.2766 | -0.30534 | -0.33818 | -0.37469 | -0.41569 | -0.68441 | -0.91569 | -1.0574 | -0.0068304 | -0.013518 | -0.035514 | -0.057072 | -0.081595 | -0.11242 | -0.14059 | -0.17494 | -0.21247 | -0.25325 | -0.30502 | -0.65418 | -0.94729 | -1.1274
| ALNESS | TAIN | MINIMUM HEADROOM | NH 77578 81489 | NO | YES | 7.6394 | 7.3334 | 6.9323 | 6.4784 | 5.8969 | 5.2837 | 4.7736 | 4.5436 | 4.2944 | 4.0497 | 3.8119 | 3.1249 | 2.7207 | 2.342 | 9.6837 | 9.4426 | 9.137 | 8.7822 | 8.2816 | 7.7389 | 7.331 | 7.13 | 6.9129 | 6.6997 | 6.4932 | 5.7253 | 5.0077 | 4.7003 | 7.7493 | 7.4577 | 7.0751 | 6.6409 | 6.0501 | 5.4018 | 4.8811 | 4.6162 | 4.3218 | 3.9742 | 3.6405 | 2.7119 | 2.1052 | 1.703
|  | TAIN | CT |  |  |  | 7.8056 | 7.5462 | 7.1593 | 6.7541 | 6.2106 | 5.6788 | 5.2967 | 5.0905 | 4.8782 | 4.668 | 4.4661 | 3.8144 | 3.3791 | 3.1619 | 9.7777 | 9.5587 | 9.3155 | 9.0514 | 8.6347 | 8.2161 | 7.9781 | 7.8089 | 7.627 | 7.4487 | 7.2731 | 6.5159 | 6.2861 | 5.9474 | 7.8761 | 7.6133 | 7.2653 | 6.9034 | 6.3693 | 5.8252 | 5.4623 | 5.2198 | 4.9813 | 4.7218 | 4.4408 | 3.4428 | 3.0932 | 2.8864
|  | TAIN | LW |  |  |  | 7.6394 | 7.3334 | 6.9323 | 6.4784 | 5.8969 | 5.2837 | 4.7736 | 4.5436 | 4.2944 | 4.0497 | 3.8119 | 3.1249 | 2.7207 | 2.342 | 9.6837 | 9.4426 | 9.137 | 8.7822 | 8.2816 | 7.7389 | 7.331 | 7.13 | 6.9129 | 6.6997 | 6.4932 | 5.7946 | 5.4826 | 5.1191 | 7.7493 | 7.4577 | 7.0751 | 6.6409 | 6.0501 | 5.4018 | 4.8811 | 4.6162 | 4.3218 | 3.9742 | 3.6405 | 2.7119 | 2.3063 | 1.9115
|  | TAIN | ST |  |  |  | 7.9663 | 7.8064 | 7.5141 | 7.2632 | 7.0213 | 6.6406 | 6.4175 | 6.1886 | 5.9609 | 5.7156 | 5.4392 | 3.6463 | 2.7864 | 2.3963 | 9.8535 | 9.6951 | 9.4071 | 9.1723 | 8.9678 | 8.5739 | 8.3816 | 8.1906 | 8.0183 | 7.8265 | 7.4951 | 5.7253 | 5.0077 | 4.7003 | 8.0139 | 7.8527 | 7.5345 | 7.2659 | 7.018 | 6.5683 | 6.2866 | 5.992 | 5.6936 | 5.3609 | 4.9773 | 2.962 | 2.1052 | 1.703
|  | TAIN | FS |  |  |  | 8.1096 | 7.9806 | 7.8148 | 7.6442 | 7.4581 | 7.2835 | 7.1089 | 6.9452 | 6.7749 | 6.5961 | 6.4036 | 5.2104 | 4.1796 | 3.3849 | 9.9928 | 9.8678 | 9.7372 | 9.603 | 9.4583 | 9.3191 | 9.1797 | 9.0488 | 8.9151 | 8.7722 | 8.6157 | 7.6611 | 6.6256 | 5.9655 | 8.1458 | 8.0183 | 7.8584 | 7.6929 | 7.5128 | 7.333 | 7.1512 | 6.9772 | 6.7887 | 6.5723 | 6.3344 | 4.8767 | 3.6707 | 2.9075
| ARDMORE | TARBERT | MINIMUM HEADROOM | NB 15289 00157 | NO | YES | -0.1063 | -0.2016 | -0.27183 | -0.3445 | -0.42229 | -0.50703 | -0.59685 | -0.66139 | -0.72801 | -0.7973 | -0.85828 | -0.95592 | -0.99082 | -1.0244 | 0.026191 | -0.049458 | -0.085319 | -0.12904 | -0.17014 | -0.21495 | -0.27264 | -0.32561 | -0.3819 | -0.43975 | -0.49154 | -0.56444 | -0.59083 | -0.62321 | -0.082038 | -0.16141 | -0.20921 | -0.25995 | -0.3114 | -0.38893 | -0.46201 | -0.52007 | -0.58786 | -0.65812 | -0.72034 | -0.81537 | -0.84303 | -0.86934
|  | TARBERT | CT |  |  |  | -0.068914 | -0.14202 | -0.24116 | -0.34238 | -0.42229 | -0.50703 | -0.5887 | -0.63205 | -0.69434 | -0.75885 | -0.81513 | -0.91595 | -0.99082 | -1.0244 | 0.044434 | -0.016799 | -0.071695 | -0.12904 | -0.17014 | -0.21412 | -0.25461 | -0.29247 | -0.34652 | -0.40204 | -0.45026 | -0.55046 | -0.59083 | -0.62321 | -0.064952 | -0.12662 | -0.18408 | -0.25529 | -0.3114 | -0.38893 | -0.46201 | -0.48926 | -0.54713 | -0.6132 | -0.67047 | -0.77842 | -0.84068 | -0.86934
|  | TARBERT | LW |  |  |  | -0.1063 | -0.2016 | -0.27183 | -0.3445 | -0.41243 | -0.50087 | -0.59685 | -0.66139 | -0.72801 | -0.7973 | -0.85828 | -0.95592 | -0.9899 | -1.0078 | 0.026191 | -0.049458 | -0.085319 | -0.12535 | -0.16244 | -0.21495 | -0.27264 | -0.32561 | -0.3819 | -0.43975 | -0.49154 | -0.56444 | -0.57711 | -0.5852 | -0.082038 | -0.16141 | -0.20921 | -0.25995 | -0.31053 | -0.38398 | -0.46163 | -0.52007 | -0.58786 | -0.65812 | -0.72034 | -0.81537 | -0.84303 | -0.85817
|  | TARBERT | ST |  |  |  | -0.036316 | -0.088772 | -0.11482 | -0.14755 | -0.18013 | -0.21663 | -0.25489 | -0.29324 | -0.34468 | -0.39764 | -0.45625 | -0.75423 | -0.8321 | -0.86794 | 0.059088 | 0.011698 | -0.0068818 | -0.029747 | -0.052161 | -0.078495 | -0.10519 | -0.13354 | -0.1697 | -0.2092 | -0.25332 | -0.48292 | -0.53585 | -0.563 | -0.042095 | -0.089311 | -0.10819 | -0.13031 | -0.15555 | -0.18457 | -0.21378 | -0.24336 | -0.28167 | -0.32257 | -0.36722 | -0.6451 | -0.71459 | -0.74237
|  | TARBERT | FS |  |  |  | -0.013251 | -0.051268 | -0.079135 | -0.1092 | -0.13776 | -0.16597 | -0.20169 | -0.23453 | -0.27553 | -0.31975 | -0.36588 | -0.67116 | -0.88253 | -0.92814 | 0.078402 | 0.043459 | 0.026368 | 0.0062069 | -0.012235 | -0.031175 | -0.053929 | -0.077721 | -0.1059 | -0.13684 | -0.17017 | -0.3868 | -0.55259 | -0.59732 | -0.02119 | -0.05601 | -0.073731 | -0.095918 | -0.11795 | -0.14003 | -0.16679 | -0.19293 | -0.22443 | -0.25833 | -0.29426 | -0.5482 | -0.75292 | -0.7908
| PORT ANN | TARBERT JURA | MINIMUM HEADROOM | NR 60552 82166 | YES | YES | 0.15396 | 0.14905 | 0.14594 | 0.1395 | 0.13861 | 0.13483 | 0.1271 | 0.12423 | 0.12388 | 0.11937 | 0.11623 | 0.10617 | 0.10134 | 0.10067 | 0.15004 | 0.14774 | 0.14613 | 0.14327 | 0.14203 | 0.13972 | 0.13596 | 0.13372 | 0.132 | 0.12882 | 0.12631 | 0.12011 | 0.11599 | 0.11292 | 0.14038 | 0.13597 | 0.13307 | 0.12737 | 0.12638 | 0.12282 | 0.11583 | 0.11295 | 0.11229 | 0.10759 | 0.10448 | 0.095123 | 0.090948 | 0.090283
|  | TARBERT JURA | CT |  |  |  | 0.1579 | 0.15273 | 0.1491 | 0.14342 | 0.14037 | 0.13583 | 0.1271 | 0.12513 | 0.12388 | 0.12258 | 0.11645 | 0.10769 | 0.10134 | 0.10067 | 0.15144 | 0.14899 | 0.14683 | 0.14379 | 0.14203 | 0.13972 | 0.13596 | 0.13411 | 0.132 | 0.12995 | 0.12642 | 0.12011 | 0.11599 | 0.11294 | 0.14379 | 0.13913 | 0.13575 | 0.13055 | 0.12774 | 0.12362 | 0.11583 | 0.11387 | 0.11229 | 0.11059 | 0.1049 | 0.09661 | 0.090948 | 0.090283
|  | TARBERT JURA | LW |  |  |  | 0.15396 | 0.14905 | 0.14594 | 0.1395 | 0.13861 | 0.13483 | 0.1288 | 0.12423 | 0.1245 | 0.11937 | 0.11623 | 0.10617 | 0.10202 | 0.10202 | 0.15004 | 0.14774 | 0.14613 | 0.14327 | 0.14247 | 0.14015 | 0.1368 | 0.13372 | 0.13219 | 0.12882 | 0.12631 | 0.1205 | 0.11867 | 0.11867 | 0.14038 | 0.13597 | 0.13307 | 0.12737 | 0.12638 | 0.12282 | 0.11727 | 0.11295 | 0.11249 | 0.10759 | 0.10448 | 0.095123 | 0.091409 | 0.091409
|  | TARBERT JURA | ST |  |  |  | 0.15815 | 0.15596 | 0.15333 | 0.14934 | 0.1487 | 0.14596 | 0.14303 | 0.14168 | 0.13857 | 0.13816 | 0.13574 | 0.11154 | 0.1068 | 0.10504 | 0.15164 | 0.15063 | 0.14941 | 0.14763 | 0.14699 | 0.14553 | 0.1439 | 0.14268 | 0.14062 | 0.1393 | 0.13726 | 0.12211 | 0.11797 | 0.11478 | 0.14404 | 0.14208 | 0.13972 | 0.13621 | 0.13551 | 0.13301 | 0.13032 | 0.12897 | 0.12606 | 0.12522 | 0.12281 | 0.10015 | 0.09574 | 0.094195
|  | TARBERT JURA | FS |  |  |  | 0.15823 | 0.15796 | 0.15728 | 0.15311 | 0.15261 | 0.15015 | 0.14942 | 0.14525 | 0.14237 | 0.14119 | 0.13616 | 0.11831 | 0.10917 | 0.10481 | 0.15169 | 0.15139 | 0.15094 | 0.14914 | 0.14867 | 0.14742 | 0.14675 | 0.14475 | 0.14314 | 0.14198 | 0.13941 | 0.12762 | 0.11861 | 0.11292 | 0.14412 | 0.14385 | 0.14321 | 0.1395 | 0.139 | 0.13678 | 0.13606 | 0.1323 | 0.12965 | 0.12848 | 0.12393 | 0.10699 | 0.097876 | 0.093935
| PORT ANN | TARBERT LOCH FYNE | MINIMUM HEADROOM | NR 86003 68479 | NO | YES | 1.6349 | 1.5673 | 1.4864 | 1.4107 | 1.2861 | 1.1584 | 1.0569 | 0.98298 | 0.90507 | 0.83085 | 0.75443 | 0.53259 | 0.36088 | 0.11527 | 2.2006 | 2.1662 | 2.1293 | 2.0848 | 1.9968 | 1.9044 | 1.8512 | 1.7942 | 1.734 | 1.6774 | 1.6174 | 1.4036 | 1.2072 | 0.99482 | 0.88309 | 0.8768 | 0.83527 | 0.80199 | 0.77888 | 0.66698 | 0.58525 | 0.51631 | 0.44387 | 0.37566 | 0.30504 | 0.07853 | -0.10282 | -0.37655
|  | TARBERT LOCH FYNE | CT |  |  |  | 1.6679 | 1.6157 | 1.5122 | 1.4107 | 1.2861 | 1.1584 | 1.0569 | 0.98298 | 0.90507 | 0.83085 | 0.75443 | 0.53259 | 0.36088 | 0.23217 | 2.215 | 2.1886 | 2.1376 | 2.0848 | 1.9968 | 1.9044 | 1.8512 | 1.7942 | 1.734 | 1.6774 | 1.6174 | 1.4036 | 1.2202 | 1.0352 | 0.88488 | 0.87948 | 0.86529 | 0.84798 | 0.78578 | 0.66698 | 0.58525 | 0.51631 | 0.44387 | 0.37566 | 0.30504 | 0.07853 | -0.10282 | -0.25999
|  | TARBERT LOCH FYNE | LW |  |  |  | 1.6349 | 1.5673 | 1.4864 | 1.4179 | 1.3471 | 1.259 | 1.1585 | 1.0824 | 1.0004 | 0.91817 | 0.83887 | 0.64557 | 0.4271 | 0.11527 | 2.2006 | 2.1662 | 2.1293 | 2.0981 | 2.0671 | 2.0242 | 1.9748 | 1.9236 | 1.8688 | 1.8145 | 1.7621 | 1.6249 | 1.387 | 1.0349 | 0.88309 | 0.8768 | 0.86973 | 0.86491 | 0.84756 | 0.78012 | 0.70374 | 0.63981 | 0.5713 | 0.50346 | 0.43794 | 0.25611 | -0.0022288 | -0.37655
|  | TARBERT LOCH FYNE | ST |  |  |  | 1.7197 | 1.693 | 1.6257 | 1.5807 | 1.5377 | 1.449 | 1.3989 | 1.3135 | 1.2529 | 1.191 | 1.1166 | 0.766 | 0.56727 | 0.39016 | 2.2311 | 2.2153 | 2.151 | 2.1065 | 2.0697 | 1.9789 | 1.9378 | 1.8598 | 1.8147 | 1.77 | 1.7128 | 1.4331 | 1.2072 | 0.99482 | 0.88891 | 0.88563 | 0.83527 | 0.80199 | 0.77888 | 0.70398 | 0.68102 | 0.6233 | 0.60058 | 0.5805 | 0.53273 | 0.20229 | -0.038781 | -0.25859
|  | TARBERT LOCH FYNE | FS |  |  |  | 1.7274 | 1.701 | 1.6628 | 1.6304 | 1.5936 | 1.5561 | 1.5159 | 1.4683 | 1.4264 | 1.3791 | 1.3304 | 1.0634 | 0.85628 | 0.75331 | 2.2356 | 2.2205 | 2.1932 | 2.1695 | 2.1429 | 2.1154 | 2.0876 | 2.0495 | 2.0173 | 1.9827 | 1.9468 | 1.7877 | 1.6435 | 1.477 | 0.88987 | 0.88652 | 0.8735 | 0.86205 | 0.84872 | 0.83527 | 0.82316 | 0.80126 | 0.78582 | 0.76996 | 0.75408 | 0.54789 | 0.38657 | 0.30522
| TAYNUILT | TAYNUILT | MINIMUM HEADROOM | NN 01856 31079 | NO | YES | 1.3993 | 1.3437 | 1.2668 | 1.1906 | 1.1121 | 1.0169 | 0.92264 | 0.89128 | 0.84049 | 0.7873 | 0.73538 | 0.636 | 0.58475 | 0.54517 | 1.7967 | 1.7682 | 1.7335 | 1.6924 | 1.6503 | 1.6074 | 1.5615 | 1.5227 | 1.48 | 1.4375 | 1.3974 | 1.3298 | 1.2849 | 1.2355 | 1.2914 | 1.2691 | 1.223 | 1.1634 | 1.097 | 1.0266 | 0.95087 | 0.90024 | 0.84423 | 0.78908 | 0.73648 | 0.64472 | 0.60645 | 0.57932
|  | TAYNUILT | CT |  |  |  | 1.4475 | 1.4099 | 1.3083 | 1.2069 | 1.1121 | 1.0169 | 0.92264 | 0.89512 | 0.85576 | 0.81125 | 0.76966 | 0.69267 | 0.58668 | 0.54517 | 1.8135 | 1.7923 | 1.7433 | 1.6924 | 1.6503 | 1.6074 | 1.5644 | 1.5359 | 1.4978 | 1.458 | 1.4231 | 1.3467 | 1.2849 | 1.2355 | 1.3083 | 1.2918 | 1.2471 | 1.1664 | 1.097 | 1.0266 | 0.95659 | 0.92063 | 0.87288 | 0.82203 | 0.77892 | 0.69578 | 0.61466 | 0.58068
|  | TAYNUILT | LW |  |  |  | 1.3993 | 1.3437 | 1.2668 | 1.1906 | 1.1153 | 1.0275 | 0.9346 | 0.89128 | 0.84049 | 0.7873 | 0.73538 | 0.636 | 0.58475 | 0.5538 | 1.7967 | 1.7682 | 1.7335 | 1.6968 | 1.6625 | 1.6145 | 1.5615 | 1.5227 | 1.48 | 1.4375 | 1.3974 | 1.3298 | 1.3085 | 1.2917 | 1.2914 | 1.2691 | 1.223 | 1.1634 | 1.1066 | 1.0318 | 0.95087 | 0.90024 | 0.84423 | 0.78908 | 0.73648 | 0.64472 | 0.60645 | 0.57932
|  | TAYNUILT | ST |  |  |  | 1.4884 | 1.4713 | 1.4468 | 1.416 | 1.3881 | 1.3569 | 1.3207 | 1.2783 | 1.2353 | 1.1838 | 1.1317 | 0.87617 | 0.78726 | 0.73249 | 1.8338 | 1.8244 | 1.8114 | 1.7949 | 1.7786 | 1.7596 | 1.7375 | 1.7113 | 1.6826 | 1.6488 | 1.6131 | 1.4311 | 1.3679 | 1.3168 | 1.336 | 1.3303 | 1.3217 | 1.3104 | 1.3001 | 1.2795 | 1.2481 | 1.2104 | 1.1707 | 1.1234 | 1.0745 | 0.83652 | 0.76843 | 0.73132
|  | TAYNUILT | FS |  |  |  | 1.5053 | 1.4906 | 1.4671 | 1.4417 | 1.4126 | 1.3851 | 1.354 | 1.3205 | 1.2824 | 1.2405 | 1.1979 | 0.90992 | 0.72078 | 0.65986 | 1.8405 | 1.8324 | 1.8205 | 1.807 | 1.7917 | 1.776 | 1.7579 | 1.7378 | 1.7149 | 1.6893 | 1.6623 | 1.4816 | 1.3324 | 1.2518 | 1.3444 | 1.3396 | 1.3316 | 1.3229 | 1.3122 | 1.3027 | 1.2792 | 1.2507 | 1.2183 | 1.1823 | 1.1451 | 0.89436 | 0.71961 | 0.67199
| BURGHMUIR | THIMBLEROW | MINIMUM HEADROOM | NO 11356 23764 | NO | YES | 11.2658 | 10.8613 | 10.0879 | 9.2694 | 8.3178 | 7.1058 | 5.906 | 5.0218 | 4.0877 | 3.1187 | 2.1869 | -0.37716 | -1.4421 | -2.4379 | 15.5887 | 15.3155 | 14.8331 | 14.3037 | 13.6389 | 12.805 | 12.0249 | 11.4341 | 10.7994 | 10.1428 | 9.5157 | 7.677 | 5.6197 | 0.46675 | 17.1711 | 16.756 | 15.9869 | 15.1628 | 14.1856 | 12.9945 | 11.841 | 10.9997 | 10.1073 | 9.1832 | 8.2663 | 5.6895 | 4.7421 | 3.666
|  | THIMBLEROW | CT |  |  |  | 11.6278 | 11.335 | 10.5832 | 9.7998 | 8.9272 | 7.9841 | 7.1199 | 6.356 | 5.5879 | 4.8155 | 3.9676 | 0.7925 | -1.2011 | -2.4379 | 15.6121 | 15.401 | 14.9182 | 14.3745 | 13.7343 | 13.054 | 12.5077 | 11.9704 | 11.4221 | 10.8643 | 10.237 | 7.677 | 5.6197 | 2.9949 | 17.2755 | 17.0289 | 16.4683 | 15.6808 | 14.7946 | 13.8597 | 13.0577 | 12.341 | 11.6186 | 10.8933 | 10.0947 | 7.1448 | 5.3628 | 4.2499
|  | THIMBLEROW | LW |  |  |  | 11.2658 | 10.8613 | 10.0879 | 9.2694 | 8.3178 | 7.1058 | 5.906 | 5.0218 | 4.0877 | 3.1187 | 2.1869 | -0.37716 | -1.4421 | -2.3956 | 15.5887 | 15.3155 | 14.8331 | 14.3037 | 13.6389 | 12.805 | 12.0249 | 11.4341 | 10.7994 | 10.1428 | 9.5157 | 7.9071 | 7.314 | 6.5799 | 17.1711 | 16.756 | 15.9869 | 15.1628 | 14.1856 | 12.9945 | 11.841 | 10.9997 | 10.1073 | 9.1832 | 8.2663 | 5.6895 | 4.7421 | 3.666
|  | THIMBLEROW | ST |  |  |  | 11.9236 | 11.8786 | 11.6384 | 11.4101 | 11.1771 | 10.7601 | 10.4452 | 10.0985 | 9.708 | 9.2582 | 8.5139 | 3.6411 | 1.9807 | 1.3854 | 15.7168 | 15.6406 | 15.377 | 15.1424 | 14.9172 | 14.4673 | 14.1272 | 13.767 | 13.3762 | 12.8396 | 12.1064 | 8.2559 | 6.8713 | 4.3118 | 17.4064 | 17.3276 | 17.0576 | 16.8121 | 16.5712 | 16.1101 | 15.79 | 15.445 | 14.7728 | 13.9886 | 13.0901 | 8.3736 | 6.7462 | 5.8297
|  | THIMBLEROW | FS |  |  |  | 11.9262 | 11.8911 | 11.7862 | 11.6646 | 11.4704 | 11.2602 | 11.0343 | 10.7814 | 10.5118 | 10.1883 | 9.7999 | 7.0416 | 4.0714 | 1.7484 | 15.7338 | 15.672 | 15.5583 | 15.3977 | 15.1689 | 14.9127 | 14.6315 | 14.3267 | 13.9901 | 13.6129 | 13.1878 | 10.2054 | 6.1985 | 0.46675 | 17.4336 | 17.3767 | 17.2662 | 17.1391 | 16.9867 | 16.815 | 16.6246 | 16.4287 | 16.2106 | 15.8946 | 15.4093 | 12.0566 | 8.7363 | 6.3017
| TAYNUILT | TIRORAN BRIDGE | MINIMUM HEADROOM | NM 48666 28729 | YES | YES | 0.18489 | 0.17566 | 0.1727 | 0.16992 | 0.16701 | 0.16082 | 0.15642 | 0.15497 | 0.14991 | 0.14468 | 0.14135 | 0.13468 | 0.12921 | 0.12649 | 0.18052 | 0.17647 | 0.1749 | 0.17329 | 0.17176 | 0.16854 | 0.16579 | 0.16359 | 0.16004 | 0.15644 | 0.15376 | 0.14947 | 0.14747 | 0.14619 | 0.17391 | 0.16565 | 0.16292 | 0.16033 | 0.15766 | 0.15198 | 0.14782 | 0.14595 | 0.14084 | 0.13567 | 0.13236 | 0.12602 | 0.12122 | 0.11876
|  | TIRORAN BRIDGE | CT |  |  |  | 0.18489 | 0.18198 | 0.17463 | 0.17269 | 0.17085 | 0.1659 | 0.16136 | 0.15547 | 0.1505 | 0.15012 | 0.14533 | 0.13728 | 0.12921 | 0.12649 | 0.18052 | 0.179 | 0.1755 | 0.17395 | 0.17275 | 0.17038 | 0.16816 | 0.16494 | 0.16145 | 0.15949 | 0.15638 | 0.15082 | 0.14747 | 0.14619 | 0.17391 | 0.17124 | 0.16459 | 0.16266 | 0.16091 | 0.15642 | 0.1523 | 0.14688 | 0.142 | 0.14072 | 0.13615 | 0.1284 | 0.12122 | 0.11876
|  | TIRORAN BRIDGE | LW |  |  |  | 0.18625 | 0.17566 | 0.1727 | 0.16992 | 0.16701 | 0.16082 | 0.15642 | 0.15497 | 0.14991 | 0.14468 | 0.14135 | 0.13468 | 0.13059 | 0.12887 | 0.18096 | 0.17647 | 0.1749 | 0.17329 | 0.17176 | 0.16854 | 0.16579 | 0.16359 | 0.16004 | 0.15644 | 0.15376 | 0.14947 | 0.14782 | 0.14719 | 0.17509 | 0.16565 | 0.16292 | 0.16033 | 0.15766 | 0.15198 | 0.14782 | 0.14595 | 0.14084 | 0.13567 | 0.13236 | 0.12602 | 0.12239 | 0.1209
|  | TIRORAN BRIDGE | ST |  |  |  | 0.18706 | 0.18636 | 0.18585 | 0.18145 | 0.17891 | 0.17794 | 0.17644 | 0.17312 | 0.17131 | 0.1678 | 0.16536 | 0.14575 | 0.14251 | 0.13696 | 0.18146 | 0.18104 | 0.18063 | 0.1787 | 0.17743 | 0.17665 | 0.17557 | 0.17364 | 0.17197 | 0.16958 | 0.16743 | 0.1544 | 0.15231 | 0.15043 | 0.17585 | 0.17519 | 0.17469 | 0.17075 | 0.16843 | 0.16747 | 0.16602 | 0.16288 | 0.16085 | 0.15737 | 0.15478 | 0.13602 | 0.13293 | 0.12806
|  | TIRORAN BRIDGE | FS |  |  |  | 0.18713 | 0.18807 | 0.18424 | 0.18185 | 0.18128 | 0.17874 | 0.17727 | 0.17627 | 0.17368 | 0.17051 | 0.17057 | 0.14822 | 0.13713 | 0.13499 | 0.18152 | 0.18183 | 0.18014 | 0.17903 | 0.17857 | 0.17733 | 0.17644 | 0.17564 | 0.17414 | 0.17236 | 0.17144 | 0.15869 | 0.15068 | 0.14969 | 0.17592 | 0.1768 | 0.1733 | 0.17115 | 0.17058 | 0.16827 | 0.16689 | 0.1659 | 0.16349 | 0.16051 | 0.16004 | 0.13903 | 0.12825 | 0.12633
| BOAT OF GARTEN | TOMATIN | MINIMUM HEADROOM | NH 79106 29734 | YES | YES | 0.080461 | 0.049196 | 0.016291 | -0.020144 | -0.18 | -0.25036 | -0.40919 | -0.53207 | -0.6765 | -0.74785 | -0.81478 | -1.0163 | -1.1533 | -1.2521 | 0.37998 | 0.36915 | 0.34202 | 0.31151 | 0.22529 | 0.16633 | 0.093425 | 0.022342 | -0.060999 | -0.11406 | -0.16351 | -0.33037 | -0.47827 | -0.63525 | 0.15162 | 0.12185 | 0.091535 | 0.051131 | -0.091243 | -0.16651 | -0.29643 | -0.40588 | -0.53438 | -0.60628 | -0.67389 | -0.88262 | -1.0265 | -1.1416
|  | TOMATIN | CT |  |  |  | 0.10246 | 0.082364 | 0.029805 | -0.019109 | -0.18 | -0.25036 | -0.40919 | -0.53207 | -0.6765 | -0.74785 | -0.81478 | -1.0163 | -1.1533 | -1.2521 | 0.38216 | 0.36915 | 0.3493 | 0.3211 | 0.22529 | 0.16633 | 0.093425 | 0.022342 | -0.060999 | -0.11406 | -0.16351 | -0.33037 | -0.44831 | -0.56275 | 0.17023 | 0.1499 | 0.09986 | 0.051131 | -0.091243 | -0.16651 | -0.29643 | -0.40588 | -0.53438 | -0.60628 | -0.67389 | -0.88262 | -1.0265 | -1.1416
|  | TOMATIN | LW |  |  |  | 0.080461 | 0.049196 | 0.016291 | -0.020144 | -0.15173 | -0.19588 | -0.37377 | -0.51436 | -0.66042 | -0.71044 | -0.75416 | -0.85885 | -1.015 | -1.2151 | 0.37998 | 0.36922 | 0.35315 | 0.3348 | 0.27767 | 0.25304 | 0.17295 | 0.099747 | 0.023262 | -0.013547 | -0.047221 | -0.12603 | -0.29774 | -0.53869 | 0.15162 | 0.12185 | 0.091535 | 0.057607 | -0.045846 | -0.088753 | -0.23385 | -0.35404 | -0.4793 | -0.53113 | -0.57736 | -0.68485 | -0.86946 | -1.1152
|  | TOMATIN | ST |  |  |  | 0.11417 | 0.097765 | 0.05357 | 0.015578 | -0.075314 | -0.14094 | -0.23821 | -0.34544 | -0.44241 | -0.49858 | -0.55832 | -0.84079 | -1.0118 | -1.1549 | 0.38902 | 0.38347 | 0.34202 | 0.31151 | 0.25908 | 0.19363 | 0.13576 | 0.056685 | -0.0022205 | -0.041616 | -0.088046 | -0.31032 | -0.47827 | -0.63525 | 0.18039 | 0.16562 | 0.11591 | 0.074465 | -0.0027248 | -0.077551 | -0.15986 | -0.26116 | -0.34552 | -0.40012 | -0.4612 | -0.75405 | -0.94467 | -1.1089
|  | TOMATIN | FS |  |  |  | 0.13154 | 0.11722 | 0.098333 | 0.078668 | 0.0063214 | -0.01935 | -0.10071 | -0.17671 | -0.25653 | -0.30007 | -0.34782 | -0.56942 | -0.6985 | -0.75025 | 0.39901 | 0.39433 | 0.38165 | 0.3693 | 0.3293 | 0.31089 | 0.26467 | 0.21562 | 0.16786 | 0.13835 | 0.10642 | -0.027561 | -0.12035 | -0.16293 | 0.19426 | 0.18179 | 0.16257 | 0.14224 | 0.083449 | 0.05776 | -0.0076979 | -0.07293 | -0.1399 | -0.18185 | -0.22749 | -0.43611 | -0.56672 | -0.61459
| LAIRG | TORBOLL | MINIMUM HEADROOM | NC 75779 00296 | YES | YES | 0.11122 | 0.11109 | 0.11095 | 0.11079 | 0.11067 | 0.10867 | 0.10844 | 0.10811 | 0.10744 | 0.10733 | 0.10667 | 0.10543 | 0.10542 | 0.10542 | 0.1051 | 0.10498 | 0.10472 | 0.10454 | 0.10435 | 0.10385 | 0.10343 | 0.10295 | 0.10242 | 0.10208 | 0.10156 | 0.10059 | 0.10035 | 0.10034 | 0.10337 | 0.10317 | 0.10285 | 0.10262 | 0.10238 | 0.10114 | 0.10062 | 0.10004 | 0.09939 | 0.099233 | 0.0986 | 0.097405 | 0.097381 | 0.09737
|  | TORBOLL | CT |  |  |  | 0.11122 | 0.11112 | 0.11095 | 0.11079 | 0.11067 | 0.11039 | 0.10855 | 0.10836 | 0.10812 | 0.10783 | 0.10732 | 0.10656 | 0.10652 | 0.10651 | 0.10511 | 0.10498 | 0.10472 | 0.10454 | 0.10435 | 0.10414 | 0.1036 | 0.10327 | 0.103 | 0.10273 | 0.10233 | 0.10148 | 0.10145 | 0.10144 | 0.10337 | 0.10317 | 0.10285 | 0.10262 | 0.10238 | 0.10212 | 0.10084 | 0.10043 | 0.1001 | 0.09977 | 0.099278 | 0.098491 | 0.098454 | 0.098448
|  | TORBOLL | LW |  |  |  | 0.11122 | 0.11109 | 0.11099 | 0.11086 | 0.11076 | 0.10867 | 0.10844 | 0.10811 | 0.10744 | 0.10733 | 0.10667 | 0.10543 | 0.10542 | 0.10542 | 0.1051 | 0.105 | 0.10485 | 0.10467 | 0.10449 | 0.10385 | 0.10343 | 0.10295 | 0.10242 | 0.10208 | 0.10156 | 0.10059 | 0.10058 | 0.10058 | 0.10341 | 0.1032 | 0.10301 | 0.10278 | 0.10255 | 0.10114 | 0.10062 | 0.10004 | 0.09939 | 0.099233 | 0.0986 | 0.097405 | 0.097402 | 0.097402
|  | TORBOLL | ST |  |  |  | 0.11126 | 0.11123 | 0.11118 | 0.11111 | 0.11104 | 0.11094 | 0.11082 | 0.11061 | 0.11018 | 0.10969 | 0.10937 | 0.10667 | 0.10545 | 0.10544 | 0.10514 | 0.10511 | 0.10507 | 0.10502 | 0.10491 | 0.10475 | 0.10456 | 0.1043 | 0.10398 | 0.10362 | 0.10328 | 0.10111 | 0.10035 | 0.10034 | 0.10347 | 0.10343 | 0.10335 | 0.10324 | 0.10309 | 0.10289 | 0.10263 | 0.10232 | 0.10193 | 0.10146 | 0.10111 | 0.098513 | 0.097381 | 0.09737
|  | TORBOLL | FS |  |  |  | 0.11127 | 0.11124 | 0.1112 | 0.11115 | 0.1111 | 0.11103 | 0.11095 | 0.11086 | 0.11075 | 0.11067 | 0.11039 | 0.10857 | 0.10688 | 0.10589 | 0.10515 | 0.10512 | 0.10509 | 0.10505 | 0.10501 | 0.10492 | 0.1048 | 0.10465 | 0.10448 | 0.10431 | 0.10409 | 0.10262 | 0.10127 | 0.1005 | 0.10348 | 0.10345 | 0.10339 | 0.10332 | 0.10323 | 0.10311 | 0.10295 | 0.10276 | 0.10254 | 0.10236 | 0.1021 | 0.10035 | 0.09871 | 0.097767
| KINTORE | TORRYBURN | MINIMUM HEADROOM | NJ 79129 15653 | NO | YES | 13.2714 | 12.9548 | 12.2982 | 11.4722 | 10.3299 | 9.0002 | 7.8106 | 6.33 | 5.0275 | 4.1666 | 3.4638 | 1.4874 | 0.25714 | -0.64127 | 14.4165 | 14.286 | 13.9709 | 13.4807 | 12.6379 | 11.6504 | 10.8061 | 9.5285 | 8.4543 | 7.9294 | 7.5484 | 6.3675 | 5.2406 | 4.1054 | 12.6984 | 12.5128 | 12.1084 | 11.5481 | 10.549 | 9.2403 | 8.0779 | 6.6443 | 5.4018 | 4.5877 | 3.9239 | 2.0771 | 0.8512 | -0.15606
|  | TORRYBURN | CT |  |  |  | 13.367 | 13.161 | 12.7257 | 11.9972 | 10.8755 | 9.669 | 8.7152 | 7.2482 | 5.8283 | 4.8684 | 4.0916 | 1.7407 | 0.25714 | -0.59977 | 14.4427 | 14.2909 | 13.9709 | 13.5022 | 12.6379 | 11.675 | 10.993 | 9.7884 | 8.6785 | 8.1716 | 7.784 | 6.3675 | 5.2406 | 4.1054 | 12.7805 | 12.5849 | 12.1653 | 11.623 | 10.6857 | 9.6569 | 8.9049 | 7.5078 | 6.1372 | 5.2309 | 4.4987 | 2.2894 | 0.9072 | 0.069848
|  | TORRYBURN | LW |  |  |  | 13.2714 | 12.9548 | 12.2982 | 11.4722 | 10.3299 | 9.0002 | 7.8106 | 6.33 | 5.0275 | 4.1666 | 3.4638 | 1.4874 | 0.26152 | -0.64127 | 14.4165 | 14.286 | 13.9718 | 13.4807 | 12.6521 | 11.6504 | 10.8061 | 9.5285 | 8.4543 | 7.9294 | 7.5484 | 6.3778 | 5.5795 | 4.7287 | 12.6984 | 12.5128 | 12.1084 | 11.5481 | 10.549 | 9.2403 | 8.0779 | 6.6443 | 5.4018 | 4.5877 | 3.9239 | 2.0771 | 0.8512 | -0.15606
|  | TORRYBURN | ST |  |  |  | 13.4492 | 13.3758 | 13.0436 | 12.6176 | 11.9462 | 11.0129 | 10.3617 | 9.1644 | 8.0935 | 7.5485 | 7.116 | 4.7404 | 3.1137 | 1.6043 | 14.4987 | 14.4474 | 14.1054 | 13.6723 | 13.0239 | 12.0672 | 11.432 | 10.229 | 9.1612 | 8.6722 | 8.2952 | 6.6875 | 5.7785 | 4.5493 | 12.8581 | 12.79 | 12.4227 | 11.9847 | 11.3224 | 10.3579 | 9.715 | 8.5371 | 7.4985 | 6.9683 | 6.5403 | 4.5963 | 3.2887 | 1.8465
|  | TORRYBURN | FS |  |  |  | 13.5179 | 13.4618 | 13.2944 | 13.0241 | 12.5384 | 12.039 | 11.5294 | 10.6191 | 9.8974 | 9.3941 | 8.9599 | 6.543 | 4.216 | 2.894 | 14.5538 | 14.5128 | 14.3627 | 14.1004 | 13.635 | 13.1542 | 12.6582 | 11.7633 | 11.0594 | 10.6518 | 10.3339 | 8.932 | 7.1154 | 5.3651 | 12.9224 | 12.8702 | 12.6992 | 12.4319 | 11.9572 | 11.4688 | 10.9724 | 10.091 | 9.3928 | 8.9547 | 8.601 | 6.8408 | 4.6706 | 3.4801
| LAIRG | TRESSADY | MINIMUM HEADROOM | NC 70537 03678 | YES | YES | 0.1875 | 0.15737 | 0.53801 | 0.49956 | 0.46796 | 0.42484 | 0.37936 | 0.35011 | 0.31545 | 0.28173 | 0.25424 | 0.19202 | 0.16114 | 0.13853 | 0.32491 | 0.30877 | 0.74888 | 0.72989 | 0.71144 | 0.69045 | 0.66438 | 0.6417 | 0.61511 | 0.58854 | 0.56556 | 0.52676 | 0.50877 | 0.49155 | 0.21823 | 0.19024 | 0.61833 | 0.5834 | 0.55479 | 0.51452 | 0.47223 | 0.44376 | 0.40871 | 0.3734 | 0.34398 | 0.28508 | 0.25889 | 0.23896
|  | TRESSADY | CT |  |  |  | 0.21162 | 0.19305 | 0.55805 | 0.51101 | 0.47293 | 0.42913 | 0.39401 | 0.36921 | 0.33646 | 0.30618 | 0.2772 | 0.21846 | 0.16114 | 0.13853 | 0.33357 | 0.3226 | 0.75432 | 0.73002 | 0.71144 | 0.69052 | 0.67272 | 0.65547 | 0.63035 | 0.6052 | 0.58253 | 0.53649 | 0.50877 | 0.49155 | 0.23887 | 0.22148 | 0.63533 | 0.59228 | 0.55777 | 0.51819 | 0.48621 | 0.4624 | 0.4307 | 0.398 | 0.36784 | 0.30922 | 0.25889 | 0.23896
|  | TRESSADY | LW |  |  |  | 0.1875 | 0.15737 | 0.53801 | 0.49956 | 0.46796 | 0.42484 | 0.37936 | 0.35011 | 0.31545 | 0.28173 | 0.25424 | 0.19202 | 0.16475 | 0.15658 | 0.32491 | 0.30877 | 0.74888 | 0.72989 | 0.71438 | 0.69045 | 0.66438 | 0.6417 | 0.61511 | 0.58854 | 0.56556 | 0.52676 | 0.51579 | 0.51288 | 0.21823 | 0.19024 | 0.61833 | 0.5834 | 0.55479 | 0.51452 | 0.47223 | 0.44376 | 0.40871 | 0.3734 | 0.34398 | 0.28508 | 0.26155 | 0.25493
|  | TRESSADY | ST |  |  |  | 0.2308 | 0.21473 | 0.61058 | 0.59366 | 0.5757 | 0.55797 | 0.53694 | 0.51206 | 0.48467 | 0.45805 | 0.42632 | 0.27246 | 0.21351 | 0.18347 | 0.34264 | 0.33518 | 0.78295 | 0.774 | 0.76434 | 0.75405 | 0.74174 | 0.72697 | 0.71001 | 0.69154 | 0.66976 | 0.56129 | 0.52746 | 0.50928 | 0.25606 | 0.24163 | 0.68375 | 0.66825 | 0.65177 | 0.63532 | 0.61577 | 0.59255 | 0.56668 | 0.54002 | 0.50874 | 0.358 | 0.30431 | 0.27801
|  | TRESSADY | FS |  |  |  | 0.23675 | 0.22823 | 0.62194 | 0.60903 | 0.59503 | 0.57754 | 0.56071 | 0.54131 | 0.51838 | 0.49602 | 0.46897 | 0.30335 | 0.19526 | 0.16655 | 0.34512 | 0.34064 | 0.78802 | 0.78115 | 0.77372 | 0.76455 | 0.75512 | 0.74414 | 0.73124 | 0.71795 | 0.70233 | 0.60049 | 0.52207 | 0.49959 | 0.26136 | 0.25361 | 0.69395 | 0.68213 | 0.66933 | 0.65334 | 0.63782 | 0.61987 | 0.59867 | 0.57782 | 0.55258 | 0.39535 | 0.28881 | 0.26468
| SHETLAND | TUMBLIN | MINIMUM HEADROOM | HU3334053363 | YES | YES | 4.6711 | 4.6163 | 4.5484 | 4.4769 | 4.3638 | 4.2482 | 4.1539 | 4.0778 | 4.0052 | 3.9388 | 3.8571 | 3.5884 | 3.0673 | 2.3644 | 5.2509 | 5.207 | 5.1605 | 5.0831 | 4.9924 | 4.8985 | 4.8327 | 4.7379 | 4.6226 | 4.5123 | 4.4065 | 4.064 | 3.5429 | 2.6704 | 3.8081 | 3.7692 | 3.7141 | 3.6553 | 3.5489 | 3.441 | 3.3609 | 3.2896 | 3.2102 | 3.1298 | 3.0314 | 2.6892 | 2.0786 | 1.2077
|  | TUMBLIN | CT |  |  |  | 4.7057 | 4.6665 | 4.5705 | 4.4778 | 4.3638 | 4.2482 | 4.1539 | 4.0778 | 4.0052 | 3.9388 | 3.8571 | 3.5884 | 3.2722 | 2.9642 | 5.267 | 5.2349 | 5.1626 | 5.0831 | 4.9924 | 4.8985 | 4.8327 | 4.7379 | 4.6226 | 4.5123 | 4.4065 | 4.064 | 3.7022 | 3.3 | 3.8381 | 3.8127 | 3.735 | 3.6553 | 3.5489 | 3.441 | 3.3609 | 3.2896 | 3.2102 | 3.1298 | 3.0314 | 2.6892 | 2.3397 | 1.9723
|  | TUMBLIN | LW |  |  |  | 4.6711 | 4.6163 | 4.5484 | 4.4769 | 4.4081 | 4.3215 | 4.2276 | 4.141 | 4.0474 | 3.9597 | 3.8705 | 3.5924 | 3.0673 | 2.3644 | 5.2509 | 5.207 | 5.1605 | 5.1082 | 5.0635 | 4.9922 | 4.9115 | 4.8016 | 4.6841 | 4.5734 | 4.4646 | 4.1664 | 3.5429 | 2.6704 | 3.8081 | 3.7692 | 3.7141 | 3.6569 | 3.6024 | 3.5386 | 3.4639 | 3.3677 | 3.2554 | 3.1487 | 3.0419 | 2.7105 | 2.0786 | 1.2077
|  | TUMBLIN | ST |  |  |  | 4.7567 | 4.7438 | 4.6954 | 4.6567 | 4.6183 | 4.5505 | 4.5066 | 4.3936 | 4.3189 | 4.247 | 4.1514 | 3.6973 | 3.2265 | 2.7739 | 5.2926 | 5.2812 | 5.2315 | 5.1896 | 5.152 | 5.076 | 5.0302 | 4.899 | 4.8179 | 4.7373 | 4.6319 | 4.1221 | 3.5897 | 3.0372 | 3.8876 | 3.8816 | 3.836 | 3.8025 | 3.7614 | 3.682 | 3.6331 | 3.4992 | 3.4151 | 3.332 | 3.2229 | 2.69 | 2.1274 | 1.5929
|  | TUMBLIN | FS |  |  |  | 4.7587 | 4.7483 | 4.7184 | 4.6855 | 4.6517 | 4.6184 | 4.5787 | 4.5203 | 4.4682 | 4.4141 | 4.3544 | 4.0578 | 3.843 | 3.6876 | 5.2937 | 5.2842 | 5.261 | 5.2344 | 5.2063 | 5.1764 | 5.1424 | 5.0797 | 5.0241 | 4.965 | 4.9007 | 4.5999 | 4.3421 | 4.1969 | 3.8862 | 3.8818 | 3.8588 | 3.8345 | 3.8089 | 3.7805 | 3.7424 | 3.6782 | 3.6214 | 3.5619 | 3.4973 | 3.1953 | 2.9584 | 2.7889
| TUMMEL BRIDGE | TUMMEL BRIDGE | MINIMUM HEADROOM | NN 75906 59080 | YES | YES | 0.26626 | 0.25827 | 0.17577 | 0.11289 | 0.070246 | -0.068582 | -0.11126 | -0.21905 | -0.26301 | -0.30281 | -0.36515 | -0.70357 | -1.0769 | -1.4271 | 0.40035 | 0.39084 | 0.28788 | 0.20951 | 0.15644 | -0.016948 | -0.070126 | -0.20454 | -0.25913 | -0.30847 | -0.38256 | -0.7372 | -1.1752 | -1.6048 | 0.15957 | 0.14629 | 0.047085 | -0.032991 | -0.088364 | -0.26409 | -0.32071 | -0.45863 | -0.51791 | -0.57224 | -0.65217 | -1.0385 | -1.4871 | -1.9182
|  | TUMMEL BRIDGE | CT |  |  |  | 0.26626 | 0.25827 | 0.2373 | 0.20745 | 0.096754 | -0.024986 | -0.069674 | -0.12596 | -0.19012 | -0.25143 | -0.31419 | -0.58192 | -0.82021 | -1.0697 | 0.40035 | 0.39084 | 0.36542 | 0.32942 | 0.20004 | 0.062064 | 0.020057 | -0.04742 | -0.11434 | -0.17353 | -0.24013 | -0.56079 | -0.83866 | -1.1379 | 0.15962 | 0.14629 | 0.11557 | 0.074386 | -0.05937 | -0.20195 | -0.24898 | -0.32115 | -0.39199 | -0.45531 | -0.527 | -0.86072 | -1.1412 | -1.442
|  | TUMMEL BRIDGE | LW |  |  |  | 0.26676 | 0.26113 | 0.25659 | 0.24525 | 0.23277 | 0.21287 | 0.1935 | 0.15872 | 0.11736 | 0.079902 | 0.0408 | -0.11118 | -0.52948 | -1.1299 | 0.40139 | 0.39465 | 0.3893 | 0.38071 | 0.37453 | 0.36417 | 0.35173 | 0.31503 | 0.27584 | 0.23969 | 0.20191 | 0.049832 | -0.46654 | -1.2142 | 0.15957 | 0.14971 | 0.14144 | 0.12965 | 0.11991 | 0.10387 | 0.085229 | 0.042003 | -0.0042385 | -0.047881 | -0.092816 | -0.26243 | -0.78186 | -1.53
|  | TUMMEL BRIDGE | ST |  |  |  | 0.26851 | 0.26606 | 0.17577 | 0.11289 | 0.070246 | -0.068582 | -0.11126 | -0.21905 | -0.26301 | -0.30281 | -0.36515 | -0.70357 | -1.0769 | -1.4271 | 0.40343 | 0.4006 | 0.28788 | 0.20951 | 0.15644 | -0.016948 | -0.070126 | -0.20454 | -0.25913 | -0.30847 | -0.38256 | -0.7372 | -1.1752 | -1.6048 | 0.16488 | 0.16092 | 0.047085 | -0.032991 | -0.088364 | -0.26409 | -0.32071 | -0.45863 | -0.51791 | -0.57224 | -0.65217 | -1.0385 | -1.4871 | -1.9182
|  | TUMMEL BRIDGE | FS |  |  |  | 0.27224 | 0.27028 | 0.25041 | 0.23017 | 0.20658 | 0.18262 | 0.16115 | 0.12032 | 0.090587 | 0.060316 | 0.028869 | -0.074577 | -0.17329 | -0.25882 | 0.40782 | 0.40548 | 0.38077 | 0.35564 | 0.32639 | 0.29659 | 0.26993 | 0.21914 | 0.18232 | 0.14478 | 0.10585 | 0.019019 | -0.056498 | -0.1333 | 0.16867 | 0.16578 | 0.13968 | 0.11335 | 0.082534 | 0.050947 | 0.022612 | -0.030887 | -0.070383 | -0.11068 | -0.15285 | -0.26247 | -0.35953 | -0.44905
| MACDUFF | TURRIFF | MINIMUM HEADROOM | NJ 72407 50271 | NO | YES | 3.7574 | 3.601 | 3.4136 | 3.1713 | 2.8925 | 2.2182 | 1.2556 | 0.50556 | 0.055842 | -0.4426 | -0.92164 | -2.4693 | -3.7272 | -4.4519 | 7.5417 | 7.3288 | 7.0768 | 6.8002 | 6.4763 | 5.7994 | 4.9586 | 4.3002 | 3.9094 | 3.4781 | 3.0539 | 1.7874 | 0.88359 | 0.10415 | 3.8509 | 3.4792 | 2.9969 | 2.4802 | 1.973 | 1.0312 | -0.15775 | -1.007 | -1.5825 | -2.2058 | -2.7961 | -4.4274 | -5.6501 | -6.3475
|  | TURRIFF | CT |  |  |  | 3.8433 | 3.692 | 3.435 | 3.1713 | 2.8925 | 2.2182 | 1.433 | 0.8286 | 0.35912 | -0.13476 | -0.65327 | -2.3467 | -3.7272 | -4.4519 | 7.6825 | 7.5149 | 7.1854 | 6.8313 | 6.4763 | 5.7994 | 5.0243 | 4.3784 | 3.9262 | 3.4781 | 3.0539 | 1.7874 | 0.88359 | 0.10415 | 4.1882 | 3.9276 | 3.3583 | 2.7585 | 2.1701 | 1.2541 | 0.22166 | -0.61715 | -1.2645 | -1.91 | -2.5242 | -4.3507 | -5.6501 | -6.3475
|  | TURRIFF | LW |  |  |  | 3.7574 | 3.601 | 3.4136 | 3.208 | 2.9995 | 2.3281 | 1.2556 | 0.50556 | 0.055842 | -0.4426 | -0.92164 | -2.4693 | -3.4442 | -4.0843 | 7.5417 | 7.3288 | 7.0768 | 6.8002 | 6.5335 | 5.8547 | 4.9586 | 4.3002 | 3.9094 | 3.4795 | 3.072 | 2.0004 | 1.3775 | 0.76987 | 3.8509 | 3.4792 | 2.9969 | 2.4802 | 1.973 | 1.0312 | -0.15775 | -1.007 | -1.5825 | -2.2058 | -2.7961 | -4.4274 | -5.3548 | -6.0756
|  | TURRIFF | ST |  |  |  | 3.927 | 3.8743 | 3.7486 | 3.6263 | 3.5057 | 2.9302 | 2.2515 | 1.6909 | 1.4272 | 1.1526 | 0.86092 | -0.5469 | -1.4271 | -2.623 | 7.7648 | 7.6911 | 7.5262 | 7.364 | 7.2078 | 6.6537 | 6.0055 | 5.4391 | 5.1345 | 4.815 | 4.4711 | 2.7375 | 1.6769 | 0.67361 | 4.3426 | 4.219 | 3.9864 | 3.7513 | 3.5224 | 2.8891 | 2.1412 | 1.4841 | 1.0871 | 0.67047 | 0.22751 | -2.078 | -3.4682 | -4.6334
|  | TURRIFF | FS |  |  |  | 3.9601 | 3.9213 | 3.8523 | 3.7763 | 3.6931 | 3.3784 | 2.8689 | 2.4659 | 2.2637 | 2.0488 | 1.8392 | 0.62532 | -0.93054 | -2.1913 | 7.804 | 7.7466 | 7.6482 | 7.5378 | 7.4208 | 7.1126 | 6.6191 | 6.1973 | 5.9442 | 5.6735 | 5.4011 | 3.7742 | 2.0909 | 0.7505 | 4.4278 | 4.3359 | 4.1785 | 4.0078 | 3.8319 | 3.46 | 2.8877 | 2.3713 | 2.0281 | 1.6663 | 1.3012 | -0.95836 | -2.899 | -3.9674
| RANNOCH | TYNDRUM | MINIMUM HEADROOM | NN 32894 30860 | YES | YES | 2.3807 | 2.3593 | 2.3382 | 2.3048 | 2.278 | 2.2483 | 2.2032 | 2.146 | 2.1068 | 2.0658 | 2.006 | 1.7998 | 1.6894 | 1.6274 | 1.8797 | 1.869 | 1.8576 | 1.8398 | 1.8277 | 1.8145 | 1.8013 | 1.7857 | 1.7672 | 1.7491 | 1.7062 | 1.535 | 1.455 | 1.4142 | 0.98122 | 0.95098 | 0.91528 | 0.87491 | 0.83921 | 0.79939 | 0.7587 | 0.71364 | 0.68291 | 0.65087 | 0.60298 | 0.45597 | 0.3655 | 0.30742
|  | TYNDRUM | CT |  |  |  | 2.3927 | 2.3746 | 2.3436 | 2.3048 | 2.278 | 2.2483 | 2.2032 | 2.146 | 2.1068 | 2.0658 | 2.006 | 1.8363 | 1.7967 | 1.7824 | 1.8823 | 1.8728 | 1.8576 | 1.8398 | 1.8277 | 1.8145 | 1.8013 | 1.7859 | 1.768 | 1.7497 | 1.7062 | 1.5776 | 1.5554 | 1.5485 | 0.98157 | 0.95098 | 0.91528 | 0.87491 | 0.83921 | 0.79939 | 0.7587 | 0.71364 | 0.68291 | 0.65087 | 0.60298 | 0.46824 | 0.42816 | 0.41259
|  | TYNDRUM | LW |  |  |  | 2.3807 | 2.3593 | 2.3382 | 2.3117 | 2.2883 | 2.2548 | 2.2258 | 2.2026 | 2.178 | 2.1529 | 2.1128 | 2.0349 | 2.017 | 2.0063 | 1.8797 | 1.869 | 1.8592 | 1.8472 | 1.8371 | 1.8201 | 1.8029 | 1.7857 | 1.7672 | 1.7491 | 1.7316 | 1.7036 | 1.6939 | 1.6881 | 0.98122 | 0.95911 | 0.93753 | 0.91151 | 0.88786 | 0.85127 | 0.81524 | 0.78321 | 0.74922 | 0.71593 | 0.68357 | 0.6181 | 0.59781 | 0.58584
|  | TYNDRUM | ST |  |  |  | 2.4084 | 2.4003 | 2.3914 | 2.3791 | 2.3656 | 2.3465 | 2.328 | 2.3054 | 2.2566 | 2.197 | 2.1331 | 1.7998 | 1.6894 | 1.6472 | 1.8894 | 1.8857 | 1.8811 | 1.8749 | 1.8679 | 1.8587 | 1.8487 | 1.8375 | 1.825 | 1.8089 | 1.7854 | 1.535 | 1.455 | 1.4283 | 1.0046 | 0.99488 | 0.98323 | 0.96573 | 0.945 | 0.91759 | 0.8876 | 0.85399 | 0.81611 | 0.76813 | 0.71815 | 0.45597 | 0.3655 | 0.3264
|  | TYNDRUM | FS |  |  |  | 2.4154 | 2.407 | 2.3969 | 2.3864 | 2.3726 | 2.3671 | 2.3517 | 2.3367 | 2.3204 | 2.2977 | 2.2557 | 1.9914 | 1.772 | 1.6274 | 1.8918 | 1.8882 | 1.8838 | 1.8786 | 1.8725 | 1.8681 | 1.8605 | 1.8522 | 1.843 | 1.8322 | 1.8199 | 1.6904 | 1.5226 | 1.4142 | 1.0116 | 1.0034 | 0.99224 | 0.98033 | 0.96244 | 0.94882 | 0.92666 | 0.90348 | 0.87722 | 0.84689 | 0.81205 | 0.59676 | 0.42386 | 0.30742
| DUNVEGAN | UIG | MINIMUM HEADROOM | NG 39131 64412 | YES | YES | 1.4671 | 1.4044 | 1.3356 | 1.2574 | 1.144 | 1.0189 | 0.92578 | 0.85495 | 0.76344 | 0.67474 | 0.59471 | 0.38636 | 0.20392 | 0.082101 | 1.6357 | 1.601 | 1.5668 | 1.506 | 1.4253 | 1.3386 | 1.2859 | 1.2245 | 1.1468 | 1.071 | 1.0016 | 0.79935 | 0.59957 | 0.41976 | 1.4084 | 1.3529 | 1.2937 | 1.218 | 1.1075 | 0.98762 | 0.90477 | 0.83147 | 0.73719 | 0.64555 | 0.56286 | 0.33813 | 0.15816 | -0.014372
|  | UIG | CT |  |  |  | 1.5072 | 1.4629 | 1.3682 | 1.2588 | 1.144 | 1.0189 | 0.92578 | 0.85495 | 0.76344 | 0.67474 | 0.59471 | 0.38636 | 0.20392 | 0.082101 | 1.6507 | 1.6236 | 1.5691 | 1.506 | 1.4253 | 1.3386 | 1.2859 | 1.2245 | 1.1468 | 1.071 | 1.0016 | 0.79935 | 0.65404 | 0.51798 | 1.4439 | 1.4024 | 1.3163 | 1.218 | 1.1075 | 0.98762 | 0.90477 | 0.83147 | 0.73719 | 0.64555 | 0.56286 | 0.33813 | 0.15816 | 0.023644
|  | UIG | LW |  |  |  | 1.4671 | 1.4044 | 1.3356 | 1.2574 | 1.193 | 1.0973 | 0.9951 | 0.91964 | 0.84083 | 0.7599 | 0.68417 | 0.53527 | 0.34483 | 0.13106 | 1.6357 | 1.601 | 1.5668 | 1.5272 | 1.4952 | 1.4413 | 1.3813 | 1.3203 | 1.2556 | 1.1907 | 1.1302 | 1.0153 | 0.82523 | 0.57233 | 1.4084 | 1.3529 | 1.2937 | 1.226 | 1.1707 | 1.0853 | 0.99302 | 0.91682 | 0.83675 | 0.75537 | 0.67923 | 0.53156 | 0.31847 | 0.058787
|  | UIG | ST |  |  |  | 1.5364 | 1.515 | 1.4583 | 1.4094 | 1.3612 | 1.2776 | 1.2208 | 1.1363 | 1.0672 | 0.99109 | 0.90531 | 0.48861 | 0.27168 | 0.10086 | 1.6649 | 1.6529 | 1.6011 | 1.5585 | 1.5212 | 1.4415 | 1.3982 | 1.3231 | 1.2694 | 1.2121 | 1.1434 | 0.80404 | 0.59957 | 0.41976 | 1.4704 | 1.4507 | 1.3888 | 1.3368 | 1.2877 | 1.1962 | 1.1402 | 1.0508 | 0.98216 | 0.90744 | 0.82111 | 0.40197 | 0.17217 | -0.014372
|  | UIG | FS |  |  |  | 1.5489 | 1.5335 | 1.5032 | 1.4684 | 1.4324 | 1.3962 | 1.3537 | 1.2961 | 1.2423 | 1.1865 | 1.1207 | 0.76206 | 0.51074 | 0.43575 | 1.6701 | 1.661 | 1.6402 | 1.6165 | 1.5911 | 1.5644 | 1.5355 | 1.4941 | 1.4558 | 1.415 | 1.3693 | 1.1353 | 0.94757 | 0.87905 | 1.4815 | 1.4673 | 1.4375 | 1.4033 | 1.3677 | 1.3316 | 1.2915 | 1.2359 | 1.1842 | 1.1302 | 1.0676 | 0.73603 | 0.49644 | 0.42989
| GRUDIE BRIDGE | ULLAPOOL | MINIMUM HEADROOM | NH 13018 94588 | NO | YES | -1.4012 | 3.1467 | 3.0697 | 2.9838 | 2.8828 | 2.7804 | 2.6755 | 2.6591 | 2.6432 | 2.6248 | 2.5998 | 2.497 | 2.4411 | 2.3954 | -0.64607 | 3.519 | 3.4809 | 3.4221 | 3.3764 | 3.3292 | 3.276 | 3.2243 | 3.1663 | 3.1068 | 3.0527 | 2.9665 | 2.9115 | 2.8032 | -0.90326 | 3.2722 | 3.2063 | 3.1212 | 3.0398 | 2.9565 | 2.8715 | 2.8127 | 2.7421 | 2.6697 | 2.604 | 2.495 | 2.4512 | 2.4104
|  | ULLAPOOL | CT |  |  |  | -1.3669 | 3.1969 | 3.089 | 2.9838 | 2.8828 | 2.7804 | 2.6755 | 2.6591 | 2.6432 | 2.6248 | 2.5998 | 2.5499 | 2.456 | 2.4084 | -0.63665 | 3.5369 | 3.4809 | 3.4221 | 3.3764 | 3.3292 | 3.276 | 3.2386 | 3.1904 | 3.1395 | 3.0894 | 2.9802 | 2.9115 | 2.8368 | -0.90326 | 3.2795 | 3.2183 | 3.1212 | 3.0398 | 2.9565 | 2.8715 | 2.828 | 2.7703 | 2.71 | 2.6518 | 2.5464 | 2.4697 | 2.4319
|  | ULLAPOOL | LW |  |  |  | -1.4012 | 3.1467 | 3.0697 | 2.9868 | 2.9104 | 2.8253 | 2.7299 | 2.7059 | 2.6776 | 2.6485 | 2.61 | 2.497 | 2.4411 | 2.3954 | -0.64607 | 3.519 | 3.4813 | 3.4364 | 3.3992 | 3.3429 | 3.2773 | 3.2243 | 3.1663 | 3.1068 | 3.0527 | 2.9665 | 2.944 | 2.9174 | -0.89687 | 3.2722 | 3.2063 | 3.1321 | 3.0668 | 2.9783 | 2.8766 | 2.8127 | 2.7421 | 2.6697 | 2.604 | 2.495 | 2.4512 | 2.4104
|  | ULLAPOOL | ST |  |  |  | -1.3418 | 3.2507 | 3.2428 | 3.2321 | 3.2093 | 3.1877 | 3.1594 | 3.1268 | 3.092 | 3.0502 | 3.0087 | 2.7797 | 2.6927 | 2.6376 | -0.61493 | 3.5733 | 3.5596 | 3.5419 | 3.5228 | 3.5016 | 3.4753 | 3.4437 | 3.4066 | 3.3635 | 3.3166 | 3.0786 | 3.0032 | 2.9391 | -0.88774 | 3.3052 | 3.2975 | 3.2872 | 3.277 | 3.2645 | 3.2402 | 3.1984 | 3.1502 | 3.0938 | 3.0343 | 2.7417 | 2.6687 | 2.6315
|  | ULLAPOOL | FS |  |  |  | -1.3316 | 3.2624 | 3.2561 | 3.247 | 3.2218 | 3.195 | 3.1723 | 3.1407 | 3.109 | 3.0794 | 3.0453 | 2.8131 | 2.6242 | 2.5555 | -0.60703 | 3.5835 | 3.5701 | 3.5553 | 3.5386 | 3.5195 | 3.4993 | 3.4736 | 3.4453 | 3.4149 | 3.3803 | 3.1568 | 2.9482 | 2.8032 | -0.87785 | 3.3165 | 3.3104 | 3.303 | 3.2948 | 3.2851 | 3.2667 | 3.2318 | 3.1944 | 3.1559 | 3.1124 | 2.8276 | 2.6115 | 2.5534
| SHETLAND | UNST | MINIMUM HEADROOM | HP6398113411 | YES | YES | -0.72005 | -0.73447 | -0.75971 | -0.78544 | -0.81477 | -0.84543 | -0.87736 | -0.90184 | -0.9311 | -0.95945 | -1.005 | -1.1885 | -1.5685 | -2.0872 | 0.025689 | 0.010619 | -0.0088542 | -0.02959 | -0.049256 | -0.069466 | -0.093866 | -0.15271 | -0.21561 | -0.2733 | -0.33249 | -0.54547 | -1.0033 | -1.6469 | -0.91674 | -0.92427 | -0.93984 | -0.95954 | -0.97911 | -0.99845 | -1.0183 | -1.0439 | -1.0817 | -1.1393 | -1.2047 | -1.432 | -1.8975 | -2.5431
|  | UNST | CT |  |  |  | -0.70992 | -0.71847 | -0.74859 | -0.78329 | -0.81477 | -0.84543 | -0.87736 | -0.90184 | -0.92754 | -0.95047 | -0.97447 | -1.102 | -1.3 | -1.5222 | 0.027005 | 0.014545 | -0.0088542 | -0.02959 | -0.049256 | -0.069466 | -0.09094 | -0.13668 | -0.18073 | -0.22146 | -0.26991 | -0.45257 | -0.6759 | -0.93755 | -0.91337 | -0.91839 | -0.93716 | -0.95954 | -0.97911 | -0.99845 | -1.0183 | -1.0439 | -1.0704 | -1.0942 | -1.1433 | -1.3295 | -1.5634 | -1.8327
|  | UNST | LW |  |  |  | -0.72005 | -0.73447 | -0.75971 | -0.78544 | -0.80795 | -0.83435 | -0.86529 | -0.89647 | -0.9311 | -0.95945 | -1.005 | -1.1885 | -1.5685 | -2.0872 | 0.025689 | 0.010619 | -0.0052176 | -0.022573 | -0.038685 | -0.064126 | -0.093866 | -0.15271 | -0.21561 | -0.2733 | -0.33249 | -0.54547 | -1.0033 | -1.6469 | -0.91674 | -0.92427 | -0.93984 | -0.95578 | -0.96973 | -0.98587 | -1.0055 | -1.0394 | -1.0817 | -1.1393 | -1.2047 | -1.432 | -1.8975 | -2.5431
|  | UNST | ST |  |  |  | -0.6721 | -0.66901 | -0.66575 | -0.66185 | -0.65939 | -0.65475 | -0.65516 | -0.7015 | -0.71706 | -0.73748 | -0.7619 | -0.97514 | -1.2817 | -1.5975 | 0.039586 | 0.038732 | 0.033194 | 0.026595 | 0.018121 | 0.0082871 | -0.0047606 | -0.075206 | -0.11315 | -0.15257 | -0.20346 | -0.45538 | -0.8207 | -1.1981 | -0.88455 | -0.88041 | -0.87553 | -0.87058 | -0.86625 | -0.86048 | -0.85844 | -0.91276 | -0.93011 | -0.94947 | -0.995 | -1.2796 | -1.6571 | -2.0442
|  | UNST | FS |  |  |  | -0.67955 | -0.6797 | -0.68088 | -0.68858 | -0.69205 | -0.69567 | -0.70239 | -0.71884 | -0.73156 | -0.74542 | -0.75715 | -0.82872 | -0.93127 | -1.018 | 0.037095 | 0.037512 | 0.033165 | 0.025382 | 0.01776 | 0.0091913 | -0.0013115 | -0.031318 | -0.056754 | -0.083545 | -0.11152 | -0.22595 | -0.3271 | -0.41281 | -0.89065 | -0.88905 | -0.88703 | -0.88979 | -0.88937 | -0.88934 | -0.89141 | -0.90906 | -0.92124 | -0.93458 | -0.94609 | -1.0553 | -1.1783 | -1.278
| SHETLAND | VOE | MINIMUM HEADROOM | HU4117663079 | YES | YES | 5.6572 | 5.6227 | 5.5578 | 5.4798 | 5.3591 | 5.2223 | 5.082 | 5.0014 | 4.8752 | 4.734 | 4.6078 | 4.3209 | 3.8892 | 3.3566 | 6.378 | 6.3283 | 6.2687 | 6.1857 | 6.1136 | 6.0348 | 5.9552 | 5.8471 | 5.7242 | 5.6021 | 5.4889 | 5.2125 | 4.7304 | 4.0805 | 4.88 | 4.8276 | 4.744 | 4.6554 | 4.5521 | 4.4359 | 4.3172 | 4.2749 | 4.1783 | 4.0709 | 3.9697 | 3.6637 | 3.1567 | 2.4978
|  | VOE | CT |  |  |  | 5.6902 | 5.6674 | 5.5779 | 5.486 | 5.3591 | 5.2223 | 5.082 | 5.0137 | 4.9202 | 4.7904 | 4.6825 | 4.4403 | 4.1306 | 3.8589 | 6.4003 | 6.3631 | 6.2757 | 6.1857 | 6.1136 | 6.0348 | 5.9552 | 5.8778 | 5.7752 | 5.6623 | 5.5629 | 5.293 | 4.9934 | 4.6657 | 4.9207 | 4.8885 | 4.7731 | 4.6605 | 4.5521 | 4.4359 | 4.3172 | 4.2749 | 4.225 | 4.1619 | 4.0817 | 3.8446 | 3.5325 | 3.2318
|  | VOE | LW |  |  |  | 5.6572 | 5.6227 | 5.5578 | 5.4798 | 5.3782 | 5.2462 | 5.1035 | 5.0014 | 4.8752 | 4.734 | 4.6078 | 4.3209 | 3.8892 | 3.3566 | 6.378 | 6.3283 | 6.2687 | 6.2024 | 6.1448 | 6.0549 | 5.9552 | 5.8471 | 5.7242 | 5.6021 | 5.4889 | 5.2125 | 4.7304 | 4.0805 | 4.88 | 4.8276 | 4.744 | 4.6554 | 4.5727 | 4.4706 | 4.3624 | 4.2908 | 4.1783 | 4.0709 | 3.9697 | 3.6637 | 3.1567 | 2.4978
|  | VOE | ST |  |  |  | 5.7462 | 5.744 | 5.7375 | 5.7338 | 5.7245 | 5.6874 | 5.6358 | 5.5294 | 5.4381 | 5.3433 | 5.2333 | 4.6786 | 4.2541 | 3.8956 | 6.4323 | 6.4197 | 6.4009 | 6.3792 | 6.3531 | 6.3204 | 6.2836 | 6.183 | 6.1071 | 6.0293 | 5.9372 | 5.4505 | 5.0222 | 4.5828 | 4.97 | 4.9679 | 4.9601 | 4.9457 | 4.9242 | 4.9 | 4.8757 | 4.7895 | 4.7118 | 4.6275 | 4.5275 | 4.0356 | 3.5673 | 3.1286
|  | VOE | FS |  |  |  | 5.7447 | 5.7418 | 5.7288 | 5.716 | 5.7023 | 5.6877 | 5.6516 | 5.5887 | 5.5244 | 5.4576 | 5.3882 | 4.9827 | 4.6722 | 4.4772 | 6.4346 | 6.4235 | 6.4041 | 6.3814 | 6.358 | 6.3292 | 6.2974 | 6.2429 | 6.1892 | 6.1328 | 6.0748 | 5.7382 | 5.4405 | 5.2981 | 4.9688 | 4.9661 | 4.9545 | 4.9312 | 4.9059 | 4.8789 | 4.8501 | 4.8024 | 4.7567 | 4.7118 | 4.6536 | 4.2891 | 4.0236 | 3.8416
| DUDHOPE | WALTON | MINIMUM HEADROOM | NO 38995 30333 | NO | NO | 17.92 | 17.7752 | 16.8192 | 15.7358 | 14.051 | 12.2284 | 10.9989 | 10.4972 | 9.966 | 9.4581 | 8.9455 | 7.065 | 6.3155 | 5.6692 | 18.8463 | 18.7416 | 17.9052 | 16.8844 | 15.0581 | 13.0066 | 11.6943 | 11.1419 | 10.5489 | 9.9868 | 9.4134 | 7.2986 | 6.4839 | 5.8132 | 18.3987 | 18.296 | 17.2723 | 16.1118 | 14.1755 | 12.0065 | 10.5772 | 10.0033 | 9.3871 | 8.7945 | 8.194 | 6.0032 | 5.1274 | 4.3016
|  | WALTON | CT |  |  |  | 18.069 | 17.9544 | 17.4947 | 16.9311 | 16.0054 | 15.0291 | 14.5422 | 14.1916 | 13.8454 | 13.5019 | 13.127 | 11.6712 | 10.9022 | 10.4534 | 18.8463 | 18.7416 | 18.4595 | 18.0744 | 17.1302 | 16.1024 | 15.6768 | 15.3217 | 15.0135 | 14.7176 | 14.3444 | 12.9182 | 11.6435 | 9.9453 | 18.4812 | 18.369 | 17.9812 | 17.4778 | 16.4821 | 15.4267 | 14.9367 | 14.5626 | 14.1824 | 13.807 | 13.3943 | 11.7751 | 11.0969 | 10.6227
|  | WALTON | LW |  |  |  | 17.92 | 17.7752 | 16.8192 | 15.7358 | 14.051 | 12.2284 | 10.9989 | 10.4972 | 9.966 | 9.4581 | 8.9455 | 7.065 | 6.3155 | 5.6692 | 18.8657 | 18.802 | 17.9052 | 16.8844 | 15.0581 | 13.0066 | 11.6943 | 11.1419 | 10.5489 | 9.9868 | 9.4134 | 7.2986 | 6.4839 | 5.8132 | 18.3987 | 18.296 | 17.2723 | 16.1118 | 14.1755 | 12.0065 | 10.5772 | 10.0033 | 9.3871 | 8.7945 | 8.194 | 6.0032 | 5.1274 | 4.3016
|  | WALTON | ST |  |  |  | 18.231 | 18.2318 | 17.614 | 17.1178 | 16.8376 | 15.9378 | 15.6449 | 15.3569 | 15.1784 | 14.9385 | 14.4855 | 12.0839 | 11.0845 | 10.5622 | 18.8815 | 18.8471 | 18.0368 | 17.4094 | 17.0328 | 15.8856 | 15.5007 | 15.14 | 14.9264 | 14.6124 | 14.2096 | 12.126 | 11.1905 | 9.5314 | 18.5283 | 18.4996 | 17.7083 | 17.0893 | 16.7169 | 15.5727 | 15.1886 | 14.8257 | 14.6054 | 14.2989 | 13.8346 | 11.3967 | 10.3418 | 9.7706
|  | WALTON | FS |  |  |  | 18.2149 | 18.2124 | 18.0283 | 17.7965 | 17.6154 | 17.4193 | 17.2382 | 17.0874 | 16.9338 | 16.7824 | 16.6209 | 15.5207 | 14.041 | 12.9956 | 18.9006 | 18.8707 | 18.6368 | 18.3687 | 18.1471 | 17.9091 | 17.6952 | 17.5205 | 17.351 | 17.1789 | 16.9678 | 15.5212 | 13.4191 | 9.8972 | 18.5493 | 18.5288 | 18.3157 | 18.0628 | 17.853 | 17.6299 | 17.4299 | 17.2702 | 17.1193 | 16.9671 | 16.8091 | 15.3757 | 13.9567 | 12.9517
| INVERNESS | WATERLOO PLACE | MINIMUM HEADROOM | NH 66301 45800 | NO | YES | 8.0975 | 7.6217 | 7.1246 | 6.6058 | 5.8307 | 4.7346 | 3.7229 | 2.5799 | 1.6034 | 0.62962 | -0.71164 | -7.3409 | -10.4417 | -11.3785 | 10.6015 | 10.2077 | 9.7823 | 9.3358 | 8.6726 | 7.8548 | 7.1559 | 6.374 | 5.6899 | 4.6901 | 3.6361 | -1.3997 | -3.929 | -4.7959 | 10.8796 | 10.4276 | 9.9485 | 9.4461 | 8.8701 | 8.1966 | 7.6347 | 6.7404 | 5.7935 | 4.693 | 3.388 | -2.9166 | -5.982 | -6.9663
|  | WATERLOO PLACE | CT |  |  |  | 8.0975 | 7.6217 | 7.1246 | 6.6058 | 5.8307 | 4.7346 | 3.7229 | 2.5799 | 1.6034 | 0.64198 | -0.47406 | -4.4012 | -4.9631 | -5.2838 | 10.6015 | 10.2077 | 9.7823 | 9.3358 | 8.6726 | 7.8548 | 7.1559 | 6.374 | 5.6983 | 4.951 | 4.0776 | 0.9944 | 0.48958 | 0.14135 | 10.8796 | 10.4276 | 9.9485 | 9.4461 | 8.8701 | 8.1966 | 7.6347 | 6.7404 | 5.7935 | 4.8621 | 3.7817 | -0.029649 | -0.61527 | -0.97981
|  | WATERLOO PLACE | LW |  |  |  | 8.1585 | 7.8057 | 7.4556 | 7.0572 | 6.5489 | 5.8143 | 4.6274 | 3.3958 | 2.0413 | 0.62962 | -0.71164 | -4.2051 | -5.0762 | -5.8492 | 10.6492 | 10.362 | 10.028 | 9.6463 | 9.1282 | 8.4182 | 7.5052 | 6.6405 | 5.6899 | 4.6901 | 3.6361 | 0.85536 | 0.015671 | -0.82338 | 10.9388 | 10.6048 | 10.2415 | 9.8282 | 9.2771 | 8.5062 | 7.7376 | 7.0502 | 6.0646 | 4.693 | 3.388 | -0.039616 | -0.98533 | -1.8774
|  | WATERLOO PLACE | ST |  |  |  | 8.2972 | 8.1382 | 7.8567 | 7.5618 | 7.2287 | 6.7075 | 6.1973 | 5.3886 | 4.1937 | 2.8026 | 1.2017 | -7.3409 | -10.4417 | -11.3785 | 10.7688 | 10.6396 | 10.356 | 10.0764 | 9.776 | 9.2739 | 8.8404 | 8.1717 | 7.3458 | 6.3866 | 5.2728 | -1.3997 | -3.929 | -4.7959 | 11.0713 | 10.9218 | 10.6213 | 10.3185 | 9.9866 | 9.4422 | 8.9462 | 8.3894 | 7.7513 | 6.901 | 5.351 | -2.9166 | -5.982 | -6.9663
|  | WATERLOO PLACE | FS |  |  |  | 8.3945 | 8.2789 | 8.1293 | 7.9553 | 7.7494 | 7.5086 | 7.2001 | 6.8872 | 6.5294 | 5.9511 | 5.1154 | -0.54923 | -6.2034 | -9.9471 | 10.8627 | 10.7709 | 10.6332 | 10.4763 | 10.2923 | 10.0782 | 9.8194 | 9.5484 | 9.2413 | 8.764 | 8.186 | 4.0751 | -0.31966 | -3.2562 | 11.1658 | 11.0579 | 10.9086 | 10.7363 | 10.5325 | 10.2952 | 9.9979 | 9.6945 | 9.3494 | 8.9576 | 8.514 | 3.7665 | -1.69 | -5.3077
| LYNDHURST | WEST KIRKTON | MINIMUM HEADROOM | NO 39194 33796 | NO | YES | 14.0514 | 13.6434 | 12.9748 | 12.345 | 11.7061 | 10.9918 | 10.2709 | 9.6399 | 8.9705 | 8.2957 | 7.6549 | 5.9682 | 5.1168 | 4.3395 | 15.5767 | 15.3399 | 15.0338 | 14.7358 | 14.4462 | 14.072 | 13.6769 | 13.2624 | 12.8178 | 12.3714 | 11.9507 | 10.7729 | 9.7322 | 8.489 | 14.1087 | 13.7589 | 13.1762 | 12.6178 | 12.0572 | 11.4112 | 10.7525 | 10.1578 | 9.5271 | 8.8928 | 8.2898 | 6.7211 | 5.8097 | 4.8787
|  | WEST KIRKTON | CT |  |  |  | 14.3692 | 14.0992 | 13.4659 | 12.8516 | 12.2696 | 11.7046 | 11.1708 | 10.5412 | 9.812 | 9.0891 | 8.4036 | 6.2474 | 5.1282 | 4.3977 | 15.6864 | 15.5115 | 15.1747 | 14.8365 | 14.5317 | 14.2292 | 13.9526 | 13.5694 | 13.1038 | 12.6382 | 12.1977 | 10.7729 | 9.7322 | 8.489 | 14.3862 | 14.1583 | 13.5958 | 13.0412 | 12.5176 | 12.0048 | 11.5238 | 10.9402 | 10.2626 | 9.5908 | 8.953 | 6.9577 | 5.8926 | 5.1536
|  | WEST KIRKTON | LW |  |  |  | 14.0514 | 13.6434 | 12.9748 | 12.345 | 11.7061 | 10.9918 | 10.2709 | 9.6399 | 8.9705 | 8.2957 | 7.6549 | 5.9682 | 5.1168 | 4.3395 | 15.5767 | 15.3399 | 15.0338 | 14.7358 | 14.4462 | 14.072 | 13.6769 | 13.2624 | 12.8178 | 12.3714 | 11.9507 | 10.9588 | 10.2273 | 9.3153 | 14.1087 | 13.7589 | 13.1762 | 12.6178 | 12.0572 | 11.4112 | 10.7525 | 10.1578 | 9.5271 | 8.8928 | 8.2898 | 6.7211 | 5.8097 | 4.8787
|  | WEST KIRKTON | ST |  |  |  | 14.4467 | 14.2632 | 14.0994 | 13.9597 | 13.8152 | 13.6469 | 13.4936 | 13.2554 | 13.0218 | 12.7655 | 12.4835 | 10.5657 | 9.1527 | 7.8103 | 15.7298 | 15.6192 | 15.4952 | 15.3804 | 15.2609 | 15.1049 | 14.9634 | 14.7195 | 14.4938 | 14.2474 | 13.9663 | 12.3098 | 10.9977 | 9.4671 | 14.4577 | 14.3128 | 14.1694 | 14.0418 | 13.9115 | 13.7475 | 13.6007 | 13.3545 | 13.1269 | 12.8776 | 12.5972 | 10.7471 | 9.367 | 8.0539
|  | WEST KIRKTON | FS |  |  |  | 14.4787 | 14.3292 | 14.1832 | 14.0562 | 13.9177 | 13.79 | 13.6668 | 13.4537 | 13.2258 | 12.9893 | 12.7361 | 11.1091 | 9.2963 | 7.9946 | 15.7441 | 15.6489 | 15.5473 | 15.4489 | 15.3412 | 15.2311 | 15.117 | 14.9314 | 14.7332 | 14.5184 | 14.2837 | 12.8044 | 10.8945 | 8.6824 | 14.4852 | 14.3697 | 14.249 | 14.1383 | 14.0176 | 13.9021 | 13.7862 | 13.5831 | 13.3693 | 13.1459 | 12.9056 | 11.3845 | 9.7065 | 8.5417
| KILLIN | WESTER DRUMMOND | MINIMUM HEADROOM | NN 72155 44784 | YES | YES | 0.062171 | 0.046483 | 0.029658 | 0.0083334 | -0.037942 | -0.092323 | -0.11941 | -0.14763 | -0.17727 | -0.20256 | -0.22918 | -0.33006 | -0.43182 | -0.5544 | 0.080479 | 0.072819 | 0.051154 | 0.026575 | 0.00012004 | -0.049147 | -0.068035 | -0.11095 | -0.13235 | -0.15136 | -0.17965 | -0.30975 | -0.45093 | -0.59416 | 0.060103 | 0.045929 | 0.030831 | 0.0097525 | -0.04414 | -0.10369 | -0.13078 | -0.16186 | -0.19448 | -0.22255 | -0.25275 | -0.36966 | -0.5114 | -0.65727
|  | WESTER DRUMMOND | CT |  |  |  | 0.075366 | 0.066265 | 0.041406 | 0.010753 | -0.037942 | -0.092323 | -0.11941 | -0.14763 | -0.17727 | -0.20256 | -0.22918 | -0.33006 | -0.4268 | -0.51491 | 0.085147 | 0.080092 | 0.065218 | 0.045639 | 0.00012004 | -0.049147 | -0.068035 | -0.09462 | -0.12344 | -0.14916 | -0.17548 | -0.28488 | -0.38388 | -0.48708 | 0.071716 | 0.063407 | 0.039617 | 0.0097525 | -0.04414 | -0.10369 | -0.13078 | -0.16186 | -0.19448 | -0.22255 | -0.25275 | -0.36966 | -0.47914 | -0.58276
|  | WESTER DRUMMOND | LW |  |  |  | 0.062171 | 0.046483 | 0.029658 | 0.0083334 | -0.0083474 | -0.035545 | -0.052913 | -0.073384 | -0.091677 | -0.10764 | -0.12998 | -0.18531 | -0.3259 | -0.51308 | 0.080479 | 0.072819 | 0.065108 | 0.055461 | 0.0479 | 0.034907 | 0.024363 | 0.0068685 | -0.010291 | -0.025877 | -0.043375 | -0.093677 | -0.25395 | -0.48109 | 0.060103 | 0.045929 | 0.030831 | 0.011716 | -0.0032377 | -0.027764 | -0.044034 | -0.065599 | -0.084912 | -0.10289 | -0.12586 | -0.18608 | -0.35512 | -0.58595
|  | WESTER DRUMMOND | ST |  |  |  | 0.087386 | 0.081843 | 0.049627 | 0.028934 | 0.0089068 | -0.042304 | -0.059406 | -0.098835 | -0.12288 | -0.1432 | -0.17456 | -0.30782 | -0.43182 | -0.5544 | 0.089828 | 0.087083 | 0.051154 | 0.026575 | 0.0074345 | -0.048719 | -0.06714 | -0.11095 | -0.13235 | -0.15136 | -0.17965 | -0.30975 | -0.45093 | -0.59416 | 0.08215 | 0.077139 | 0.038887 | 0.013727 | -0.0085338 | -0.068798 | -0.088824 | -0.13535 | -0.1612 | -0.18328 | -0.21719 | -0.36449 | -0.5114 | -0.65727
|  | WESTER DRUMMOND | FS |  |  |  | 0.09277 | 0.085891 | 0.074854 | 0.061624 | 0.048847 | 0.036015 | 0.020374 | -9.3172e-06 | -0.016954 | -0.032949 | -0.052824 | -0.13356 | -0.19009 | -0.22096 | 0.091841 | 0.08866 | 0.079139 | 0.068601 | 0.057343 | 0.045763 | 0.033777 | 0.014773 | -0.00016274 | -0.01509 | -0.031622 | -0.086424 | -0.13035 | -0.16263 | 0.086837 | 0.080736 | 0.068906 | 0.055103 | 0.041353 | 0.027513 | 0.011496 | -0.010859 | -0.029125 | -0.046778 | -0.067642 | -0.14573 | -0.20095 | -0.2324
| THURSO | WESTRAY | MINIMUM HEADROOM | HY 50213 39413 | YES | YES | 0.28727 | 0.26756 | 0.23273 | 0.19276 | 0.14308 | 0.096612 | 0.050127 | 0.046422 | 0.043228 | 0.036313 | 0.031164 | -0.032441 | -0.049951 | -0.053446 | 0.54206 | 0.53206 | 0.51713 | 0.49609 | 0.47536 | 0.45561 | 0.43564 | 0.42918 | 0.42164 | 0.39736 | 0.37154 | 0.31448 | 0.30591 | 0.29625 | 0.41267 | 0.39478 | 0.36434 | 0.32867 | 0.28592 | 0.24578 | 0.20557 | 0.20041 | 0.18423 | 0.15092 | 0.12008 | 0.048359 | 0.032631 | 0.029591
|  | WESTRAY | CT |  |  |  | 0.3024 | 0.29093 | 0.23919 | 0.19276 | 0.14308 | 0.096612 | 0.050127 | 0.046422 | 0.043228 | 0.036313 | 0.031164 | 0.029866 | -0.003835 | -0.020799 | 0.54744 | 0.54022 | 0.51713 | 0.49609 | 0.47536 | 0.45561 | 0.43564 | 0.42918 | 0.42164 | 0.41267 | 0.40463 | 0.36142 | 0.35168 | 0.34601 | 0.42596 | 0.41528 | 0.36951 | 0.32867 | 0.28592 | 0.24578 | 0.20557 | 0.20041 | 0.19473 | 0.18329 | 0.16154 | 0.10893 | 0.088283 | 0.077086
|  | WESTRAY | LW |  |  |  | 0.28727 | 0.26756 | 0.23273 | 0.19726 | 0.16393 | 0.12621 | 0.08109 | 0.070036 | 0.05974 | 0.04844 | 0.038105 | -0.032441 | -0.049951 | -0.053446 | 0.54206 | 0.53206 | 0.51717 | 0.50169 | 0.48731 | 0.46914 | 0.44748 | 0.43678 | 0.42505 | 0.39736 | 0.37154 | 0.31448 | 0.30591 | 0.30425 | 0.41267 | 0.39478 | 0.36434 | 0.33344 | 0.30454 | 0.27096 | 0.23087 | 0.21528 | 0.18423 | 0.15092 | 0.12008 | 0.048359 | 0.032631 | 0.029591
|  | WESTRAY | ST |  |  |  | 0.31991 | 0.31691 | 0.30986 | 0.29825 | 0.29128 | 0.28155 | 0.26931 | 0.25575 | 0.24061 | 0.22072 | 0.20453 | 0.046669 | -0.013871 | -0.029638 | 0.5548 | 0.5527 | 0.54882 | 0.54288 | 0.53838 | 0.53246 | 0.52513 | 0.51666 | 0.50455 | 0.48454 | 0.46239 | 0.34497 | 0.30777 | 0.30285 | 0.43555 | 0.43349 | 0.43063 | 0.42082 | 0.41044 | 0.39752 | 0.38103 | 0.36071 | 0.33665 | 0.30779 | 0.27806 | 0.11941 | 0.062804 | 0.048953
|  | WESTRAY | FS |  |  |  | 0.32402 | 0.32174 | 0.31308 | 0.30208 | 0.29256 | 0.28118 | 0.27215 | 0.261 | 0.24548 | 0.23594 | 0.22253 | 0.12605 | 0.019286 | -0.048074 | 0.55646 | 0.55475 | 0.55054 | 0.54522 | 0.5403 | 0.53446 | 0.52919 | 0.52278 | 0.51442 | 0.50792 | 0.49959 | 0.42061 | 0.34312 | 0.29625 | 0.43623 | 0.43464 | 0.43246 | 0.42546 | 0.41689 | 0.40659 | 0.39584 | 0.38206 | 0.3647 | 0.34902 | 0.33041 | 0.20285 | 0.09616 | 0.032253
| TARLAND | WHITEHOUSE | MINIMUM HEADROOM | NJ 61658 15058 | NO | YES | 2.6985 | 2.4045 | 2.0804 | 1.7476 | 1.4159 | 0.90259 | 0.50535 | 0.29862 | 0.075929 | -0.15852 | -0.374 | -0.9113 | -1.4014 | -1.7229 | 4.527 | 4.3645 | 4.2028 | 4.0082 | 3.7802 | 3.4323 | 3.2158 | 3.0284 | 2.7951 | 2.5501 | 2.3243 | 1.8421 | 1.46 | 1.1302 | 3.4154 | 3.1597 | 2.8949 | 2.6133 | 2.3445 | 1.8909 | 1.4848 | 1.1997 | 0.89996 | 0.58815 | 0.30159 | -0.31571 | -0.7663 | -1.0844
|  | WHITEHOUSE | CT |  |  |  | 2.9693 | 2.7603 | 2.3407 | 1.9116 | 1.4885 | 0.92357 | 0.50535 | 0.3142 | 0.10509 | -0.10585 | -0.31542 | -0.76348 | -1.4014 | -1.7229 | 4.6217 | 4.4939 | 4.2596 | 4.0082 | 3.7802 | 3.4323 | 3.2158 | 3.0284 | 2.8 | 2.5703 | 2.3566 | 1.8421 | 1.46 | 1.1302 | 3.6089 | 3.4308 | 3.0741 | 2.6982 | 2.3503 | 1.8909 | 1.4986 | 1.253 | 0.96792 | 0.68009 | 0.40872 | -0.17687 | -0.7663 | -1.0844
|  | WHITEHOUSE | LW |  |  |  | 2.6985 | 2.4045 | 2.0804 | 1.7476 | 1.4159 | 0.90259 | 0.51427 | 0.29862 | 0.075929 | -0.15852 | -0.374 | -0.9113 | -1.265 | -1.561 | 4.527 | 4.3645 | 4.2028 | 4.0263 | 3.8609 | 3.5108 | 3.2541 | 3.032 | 2.7951 | 2.5501 | 2.3243 | 1.8764 | 1.6301 | 1.3585 | 3.4154 | 3.1597 | 2.8949 | 2.6133 | 2.3445 | 1.8913 | 1.4848 | 1.1997 | 0.89996 | 0.58815 | 0.30159 | -0.31571 | -0.67321 | -1.0085
|  | WHITEHOUSE | ST |  |  |  | 3.1673 | 3.0657 | 2.8928 | 2.7268 | 2.5604 | 2.2205 | 2.0393 | 1.813 | 1.5957 | 1.3687 | 1.1253 | -0.040329 | -0.67916 | -1.1539 | 4.7 | 4.6443 | 4.5395 | 4.4336 | 4.3274 | 4.0647 | 3.9338 | 3.7602 | 3.5881 | 3.4021 | 3.1938 | 2.1466 | 1.6721 | 1.2924 | 3.7522 | 3.6679 | 3.5194 | 3.371 | 3.2226 | 2.923 | 2.7489 | 2.5292 | 2.3119 | 2.079 | 1.8235 | 0.5258 | -0.11246 | -0.55145
|  | WHITEHOUSE | FS |  |  |  | 3.2587 | 3.1845 | 3.0507 | 2.9096 | 2.7653 | 2.5393 | 2.3827 | 2.1919 | 1.9982 | 1.8035 | 1.5968 | 0.21748 | -0.68306 | -1.1797 | 4.7324 | 4.6885 | 4.617 | 4.5361 | 4.4512 | 4.2935 | 4.1906 | 4.0615 | 3.926 | 3.7834 | 3.6284 | 2.6519 | 1.8151 | 1.3177 | 3.8127 | 3.748 | 3.6382 | 3.5174 | 3.393 | 3.2007 | 3.0578 | 2.883 | 2.7016 | 2.5134 | 2.3112 | 0.98085 | -0.023755 | -0.45003
| PERSLEY | WHITESTRIPES | MINIMUM HEADROOM | NJ 92850 11054 | NO | YES | 6.4977 | 5.8367 | 4.8942 | 3.8936 | 2.914 | 1.6999 | 0.38124 | -0.90023 | -2.2317 | -3.5828 | -4.8976 | -8.799 | -10.297 | -11.6902 | 8.151 | 7.7702 | 7.2967 | 6.7868 | 6.296 | 5.6467 | 4.9293 | 4.1698 | 3.3724 | 2.5462 | 1.7174 | -0.53198 | -1.7629 | -3.2742 | 7.1844 | 6.6201 | 5.8022 | 4.9328 | 4.0807 | 3.0241 | 1.8758 | 0.753 | -0.46549 | -1.6988 | -2.8927 | -6.2783 | -7.7916 | -9.3964
|  | WHITESTRIPES | CT |  |  |  | 6.8623 | 6.379 | 5.428 | 4.4051 | 3.4206 | 2.4028 | 1.4001 | 0.20279 | -1.1378 | -2.5022 | -3.806 | -7.2068 | -8.5498 | -9.5494 | 8.2897 | 8.0027 | 7.4777 | 6.9042 | 6.3328 | 5.7378 | 5.1942 | 4.4884 | 3.6807 | 2.8609 | 2.0686 | -0.27273 | -1.6403 | -3.2742 | 7.4976 | 7.1043 | 6.2754 | 5.3817 | 4.4978 | 3.5824 | 2.703 | 1.644 | 0.44658 | -0.78814 | -1.969 | -5.1015 | -6.4045 | -7.4234
|  | WHITESTRIPES | LW |  |  |  | 6.4977 | 5.8367 | 4.8942 | 3.8936 | 2.914 | 1.6999 | 0.38124 | -0.90023 | -2.2317 | -3.5828 | -4.8976 | -8.799 | -10.297 | -11.6902 | 8.151 | 7.7702 | 7.2967 | 6.7868 | 6.296 | 5.6467 | 4.9293 | 4.1698 | 3.3724 | 2.5462 | 1.7174 | -0.53198 | -1.7629 | -3.2705 | 7.1844 | 6.6201 | 5.8022 | 4.9328 | 4.0807 | 3.0241 | 1.8758 | 0.753 | -0.46549 | -1.6988 | -2.8927 | -6.2783 | -7.7916 | -9.3964
|  | WHITESTRIPES | ST |  |  |  | 7.0109 | 6.6745 | 6.2565 | 5.8324 | 5.3998 | 4.8641 | 4.3622 | 3.7091 | 3.0581 | 2.3484 | 1.5811 | -1.8996 | -3.603 | -5.0887 | 8.3687 | 8.1757 | 7.8837 | 7.5955 | 7.3082 | 6.904 | 6.5617 | 6.0571 | 5.5972 | 5.099 | 4.5432 | 1.7652 | 0.0087812 | -1.9155 | 7.6351 | 7.3728 | 7.0128 | 6.6579 | 6.3039 | 5.8331 | 5.409 | 4.7995 | 4.2158 | 3.5801 | 2.8786 | -0.44191 | -2.1545 | -3.6544
|  | WHITESTRIPES | FS |  |  |  | 7.1129 | 6.8444 | 6.5177 | 6.1607 | 5.7856 | 5.378 | 4.9454 | 4.4071 | 3.8531 | 3.2667 | 2.6508 | -0.83959 | -3.8224 | -5.3241 | 8.4155 | 8.2519 | 8.0431 | 7.8125 | 7.5662 | 7.2958 | 7.0061 | 6.6265 | 6.2377 | 5.8203 | 5.3752 | 2.8187 | 0.040819 | -2.535 | 7.7212 | 7.5205 | 7.2634 | 6.9799 | 6.6822 | 6.3569 | 6.0121 | 5.5509 | 5.0693 | 4.5567 | 4.0146 | 0.92494 | -1.785 | -3.1278
| CARRADALE | WHITING BAY | MINIMUM HEADROOM | NS 04169 26277 | YES | YES | 7.0596 | 6.9849 | 6.8947 | 6.8002 | 6.706 | 6.5984 | 6.4681 | 6.3751 | 6.2777 | 6.1745 | 6.0836 | 5.9457 | 5.8748 | 5.8289 | 7.3035 | 7.2573 | 7.2077 | 7.1469 | 7.0907 | 7.0343 | 6.9524 | 6.8807 | 6.8045 | 6.7254 | 6.6548 | 6.5552 | 6.5022 | 6.4558 | 6.4913 | 6.4156 | 6.3202 | 6.2221 | 6.1319 | 6.0156 | 5.8876 | 5.8077 | 5.7248 | 5.6357 | 5.5576 | 5.4272 | 5.345 | 5.2938
|  | WHITING BAY | CT |  |  |  | 7.1075 | 7.0554 | 6.9346 | 6.8086 | 6.706 | 6.6045 | 6.5003 | 6.4275 | 6.3272 | 6.2246 | 6.1382 | 5.9895 | 5.8748 | 5.8289 | 7.3252 | 7.2916 | 7.2212 | 7.1469 | 7.0907 | 7.0343 | 6.9767 | 6.9213 | 6.8436 | 6.7639 | 6.6967 | 6.5699 | 6.5022 | 6.4558 | 6.5471 | 6.4956 | 6.3705 | 6.2418 | 6.1319 | 6.0236 | 5.9123 | 5.8477 | 5.7622 | 5.6748 | 5.5999 | 5.4745 | 5.345 | 5.2938
|  | WHITING BAY | LW |  |  |  | 7.0596 | 6.9849 | 6.8947 | 6.8002 | 6.7172 | 6.5984 | 6.4681 | 6.3751 | 6.2777 | 6.1745 | 6.0836 | 5.9457 | 5.8883 | 5.8737 | 7.3035 | 7.2573 | 7.2077 | 7.1537 | 7.1077 | 7.0345 | 6.9524 | 6.8807 | 6.8045 | 6.7254 | 6.6548 | 6.5552 | 6.5275 | 6.5212 | 6.4913 | 6.4156 | 6.3202 | 6.2221 | 6.1341 | 6.0156 | 5.8876 | 5.8077 | 5.7248 | 5.6357 | 5.5576 | 5.4272 | 5.36 | 5.3421
|  | WHITING BAY | ST |  |  |  | 7.1619 | 7.1439 | 7.1149 | 7.084 | 7.0488 | 7.009 | 6.9645 | 6.908 | 6.8363 | 6.7635 | 6.6795 | 6.2853 | 6.1987 | 6.1483 | 7.35 | 7.3375 | 7.3191 | 7.2976 | 7.2736 | 7.2455 | 7.2131 | 7.1728 | 7.1226 | 7.0688 | 7.0076 | 6.705 | 6.634 | 6.5913 | 6.6078 | 6.5894 | 6.5596 | 6.5293 | 6.4948 | 6.4568 | 6.4153 | 6.3636 | 6.2975 | 6.2327 | 6.1571 | 5.8056 | 5.7129 | 5.6494
|  | WHITING BAY | FS |  |  |  | 7.167 | 7.1536 | 7.1246 | 7.0928 | 7.059 | 7.0229 | 6.9817 | 6.9366 | 6.8855 | 6.831 | 6.7706 | 6.3683 | 6.0753 | 6.0235 | 7.3529 | 7.343 | 7.3256 | 7.3055 | 7.2843 | 7.2607 | 7.2335 | 7.2027 | 7.1677 | 7.1295 | 7.0869 | 6.8091 | 6.5845 | 6.5303 | 6.613 | 6.5994 | 6.5683 | 6.5351 | 6.4999 | 6.4631 | 6.4218 | 6.3777 | 6.3286 | 6.277 | 6.22 | 5.8391 | 5.5744 | 5.5131
| MYBSTER | WICK | MINIMUM HEADROOM | ND 35583 50947 | NO | YES | 5.5586 | 5.1306 | 4.3574 | 3.5809 | 2.8524 | 2.4138 | 1.9626 | 1.7324 | 1.4978 | 1.2643 | 1.0298 | -0.028234 | -1.3917 | -2.1338 | 8.2176 | 7.9658 | 7.467 | 6.9664 | 6.5055 | 6.3259 | 6.1322 | 5.9506 | 5.7932 | 5.6381 | 5.4725 | 4.696 | 3.7275 | 2.7632 | 6.332 | 5.9497 | 5.2368 | 4.5214 | 3.8494 | 3.4631 | 3.0653 | 2.8482 | 2.6261 | 2.4067 | 2.1849 | 1.1467 | -0.148 | -1.0726
|  | WICK | CT |  |  |  | 5.9687 | 5.6297 | 4.8384 | 4.0576 | 3.2797 | 2.7607 | 2.2709 | 1.9637 | 1.6905 | 1.4162 | 1.1361 | -0.016026 | -1.3917 | -2.1338 | 8.4033 | 8.1716 | 7.6562 | 7.1481 | 6.6322 | 6.3621 | 6.1322 | 5.9506 | 5.7932 | 5.6381 | 5.4725 | 4.696 | 3.7275 | 2.7632 | 6.695 | 6.3883 | 5.6575 | 4.9346 | 4.2065 | 3.733 | 3.296 | 3.0086 | 2.753 | 2.4983 | 2.2362 | 1.1467 | -0.148 | -0.9018
|  | WICK | LW |  |  |  | 5.5586 | 5.1306 | 4.3574 | 3.5809 | 2.8524 | 2.4138 | 1.9626 | 1.7324 | 1.4978 | 1.2643 | 1.0298 | -0.028234 | -1.1861 | -2.0904 | 8.2176 | 7.9658 | 7.467 | 6.9664 | 6.5055 | 6.3259 | 6.1379 | 6.0085 | 5.8742 | 5.7434 | 5.61 | 5.0155 | 4.1192 | 3.1331 | 6.332 | 5.9497 | 5.2368 | 4.5214 | 3.8494 | 3.4631 | 3.0653 | 2.8482 | 2.6261 | 2.4067 | 2.1849 | 1.1868 | -0.013509 | -1.0726
|  | WICK | ST |  |  |  | 6.1096 | 5.8499 | 5.3398 | 4.8625 | 4.4111 | 4.1826 | 3.9943 | 3.7653 | 3.5997 | 3.4328 | 3.2399 | 2.1007 | 0.89041 | -0.37418 | 8.4564 | 8.2668 | 7.8388 | 7.4392 | 7.0648 | 6.8933 | 6.773 | 6.5829 | 6.4702 | 6.3569 | 6.2142 | 5.3757 | 4.3151 | 3.0531 | 6.8195 | 6.5854 | 6.0936 | 5.6346 | 5.2023 | 4.9807 | 4.8081 | 4.5735 | 4.4152 | 4.2568 | 4.0687 | 2.9771 | 1.7709 | 0.51122
|  | WICK | FS |  |  |  | 6.4242 | 6.2234 | 5.818 | 5.4131 | 5.0398 | 4.802 | 4.6035 | 4.3477 | 4.0568 | 3.7955 | 3.5638 | 2.172 | 1.2044 | 0.34747 | 8.6982 | 8.5493 | 8.2254 | 7.9007 | 7.6017 | 7.4347 | 7.2966 | 7.1166 | 6.9046 | 6.7153 | 6.553 | 5.6572 | 4.7211 | 3.3747 | 7.1083 | 6.9281 | 6.5459 | 6.1627 | 5.8092 | 5.5906 | 5.4098 | 5.1691 | 4.8966 | 4.6527 | 4.4379 | 3.1841 | 2.3107 | 1.5357
| WOODHILL | WOODHILL | MINIMUM HEADROOM | NJ 91259 07053 | NO | NO | 4.6089 | 4.205 | 2.4647 | 0.57832 | -2.5482 | -5.968 | -8.3296 | -9.3561 | -10.4296 | -11.4559 | -12.5149 | -16.1424 | -17.2602 | -18.0758 | 6.7364 | 6.4363 | 4.8943 | 3.0824 | -0.31267 | -4.0527 | -6.5218 | -7.5829 | -8.7191 | -9.8062 | -10.9016 | -14.6072 | -15.6338 | -16.425 | 4.5933 | 4.2213 | 2.2735 | 0.14728 | -3.5293 | -7.532 | -10.1988 | -11.2697 | -12.3912 | -13.4497 | -14.5442 | -18.4517 | -19.6806 | -20.5924
|  | WOODHILL | CT |  |  |  | 4.9825 | 4.7186 | 3.9023 | 2.9794 | 1.194 | -0.69812 | -1.6796 | -2.4562 | -3.2545 | -4.0276 | -4.8351 | -8.07 | -9.5634 | -10.2132 | 6.7364 | 6.4363 | 5.8728 | 5.2272 | 3.459 | 1.5317 | 0.74453 | 0.048847 | -0.58422 | -1.1871 | -1.906 | -4.6707 | -6.2139 | -8.4901 | 4.9181 | 4.6706 | 3.8816 | 2.9602 | 0.95201 | -1.1818 | -2.1792 | -2.941 | -3.7249 | -4.4797 | -5.2705 | -8.4511 | -9.8566 | -10.4915
|  | WOODHILL | LW |  |  |  | 4.6089 | 4.205 | 2.4647 | 0.57832 | -2.5482 | -5.968 | -8.3296 | -9.3561 | -10.4296 | -11.4559 | -12.5149 | -16.1424 | -17.2602 | -18.0758 | 6.7797 | 6.5049 | 4.8943 | 3.0824 | -0.31267 | -4.0527 | -6.5218 | -7.5829 | -8.7191 | -9.8062 | -10.9016 | -14.6072 | -15.6338 | -16.425 | 4.5933 | 4.2213 | 2.2735 | 0.14728 | -3.5293 | -7.532 | -10.1988 | -11.2697 | -12.3912 | -13.4497 | -14.5442 | -18.4517 | -19.6806 | -20.5924
|  | WOODHILL | ST |  |  |  | 5.1636 | 5.051 | 3.8838 | 3.0186 | 2.3622 | 0.56387 | -0.14635 | -0.7556 | -1.2344 | -1.7474 | -2.3645 | -7.1592 | -9.1963 | -9.9686 | 6.8307 | 6.7639 | 5.4011 | 4.359 | 3.5581 | 1.3099 | 0.40739 | -0.39382 | -1.0574 | -1.7882 | -2.672 | -7.2968 | -9.095 | -10.0888 | 5.0853 | 4.9816 | 3.5698 | 2.5436 | 1.7854 | -0.39259 | -1.1984 | -1.8672 | -2.4331 | -3.3118 | -4.3641 | -9.8887 | -12.0885 | -13.0336
|  | WOODHILL | FS |  |  |  | 5.2339 | 5.1495 | 4.8008 | 4.4363 | 4.0294 | 3.6027 | 3.1834 | 2.7971 | 2.4206 | 2.0194 | 1.5923 | -1.0491 | -3.6509 | -5.6401 | 6.8498 | 6.797 | 6.4686 | 6.1264 | 5.6766 | 5.189 | 4.7099 | 4.3224 | 3.9364 | 3.5111 | 3.0415 | 0.35488 | -3.2564 | -8.3556 | 5.1474 | 5.0703 | 4.6823 | 4.2779 | 3.8222 | 3.3472 | 2.8894 | 2.4965 | 2.122 | 1.7236 | 1.2994 | -1.8061 | -5.0946 | -7.4761

## Primary Headroom Gen
#VALUE! | Grid Supply Point | Primary Substation | Scenario | Grid Reference | Single Transformer Site (YES/NO) | Upstream Constraint (YES / NO) | Generation Headroom Winter (MVA) | [13 empty] | Generation Headroom Summer (MVA) | [13 empty] | Generation Headroom Spring/Autumn (MVA)
[7 empty] | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050
| FORT AUGUSTUS | ABERCHALDER | MINIMUM HEADROOM | NH 33843 03575 | YES | YES | -0.062964 | -0.19707 | -0.32518 | -0.4487 | -0.56765 | -0.68202 | -0.79181 | -0.84311 | -0.86875 | -0.89412 | -0.91912 | -1.0417 | -1.1522 | -1.2649 | -0.015759 | -0.12299 | -0.22546 | -0.32426 | -0.41941 | -0.5109 | -0.59874 | -0.6399 | -0.66058 | -0.68105 | -0.70122 | -0.80008 | -0.88942 | -0.98039 | -0.072904 | -0.2077 | -0.33648 | -0.46065 | -0.58023 | -0.6952 | -0.80558 | -0.85719 | -0.88303 | -0.9086 | -0.9338 | -1.0573 | -1.1688 | -1.2823
|  | ABERCHALDER | CT |  |  |  | -0.062964 | -0.19707 | -0.32518 | -0.4487 | -0.56765 | -0.68202 | -0.79181 | -0.84311 | -0.86875 | -0.89412 | -0.91912 | -1.0417 | -1.1522 | -1.2649 | -0.015759 | -0.12299 | -0.22546 | -0.32426 | -0.41941 | -0.5109 | -0.59874 | -0.6399 | -0.66058 | -0.68105 | -0.70122 | -0.80008 | -0.88942 | -0.98039 | -0.072904 | -0.2077 | -0.33648 | -0.46065 | -0.58023 | -0.6952 | -0.80558 | -0.85719 | -0.88303 | -0.9086 | -0.9338 | -1.0573 | -1.1688 | -1.2823
|  | ABERCHALDER | LW |  |  |  | 0.17388 | 0.15348 | 0.13048 | 0.10518 | 0.077818 | 0.048621 | 0.017822 | -0.010719 | -0.040101 | -0.070093 | -0.10046 | -0.26115 | -0.41899 | -0.58552 | 0.17326 | 0.15672 | 0.13804 | 0.11754 | 0.095393 | 0.071792 | 0.046918 | 0.023824 | 6.0336e-05 | -0.024188 | -0.048735 | -0.17849 | -0.30601 | -0.44044 | 0.16448 | 0.14391 | 0.12069 | 0.09518 | 0.067608 | 0.038204 | 0.0071996 | -0.021558 | -0.051156 | -0.081363 | -0.11195 | -0.27371 | -0.43285 | -0.60071
|  | ABERCHALDER | ST |  |  |  | 0.21446 | 0.19803 | 0.1913 | 0.18454 | 0.17515 | 0.16602 | 0.15715 | 0.14858 | 0.13617 | 0.12409 | 0.11236 | 0.058043 | 0.0095813 | -0.035837 | 0.20606 | 0.19431 | 0.18785 | 0.1815 | 0.17386 | 0.16644 | 0.15922 | 0.15224 | 0.14219 | 0.13241 | 0.1229 | 0.078884 | 0.039577 | 0.0027055 | 0.19877 | 0.19088 | 0.18286 | 0.175 | 0.16551 | 0.15629 | 0.14733 | 0.13867 | 0.12616 | 0.11399 | 0.10216 | 0.04739 | -0.0014664 | -0.047268
|  | ABERCHALDER | FS |  |  |  | 0.19803 | 0.19112 | 0.18053 | 0.1688 | 0.15723 | 0.1458 | 0.13452 | 0.1234 | 0.11243 | 0.10162 | 0.090971 | 0.027199 | -0.029257 | -0.081619 | 0.19456 | 0.18817 | 0.17865 | 0.16925 | 0.15996 | 0.1508 | 0.14174 | 0.1328 | 0.12399 | 0.1153 | 0.10675 | 0.055582 | 0.010272 | -0.031754 | 0.19111 | 0.18309 | 0.17119 | 0.15942 | 0.1478 | 0.13634 | 0.12501 | 0.11384 | 0.10282 | 0.091968 | 0.081273 | 0.017271 | -0.039398 | -0.092059
| TUMMEL BRIDGE | ABERFELDY | MINIMUM HEADROOM | NN 84889 48876 | NO | YES | 6.7961 | 6.7913 | 6.7851 | 6.7792 | 6.7732 | 6.7664 | 6.7599 | 6.7528 | 6.7456 | 6.7314 | 6.6712 | 6.3066 | 5.7199 | 5.3709 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.2464 | 7.1647 | 7.0762 | 6.9863 | 6.8897 | 6.8221 | 6.4128 | 5.8275 | 5.4357 | 6.5521 | 6.5521 | 6.5521 | 6.5521 | 6.5005 | 6.4071 | 6.3158 | 6.2171 | 6.1167 | 6.0124 | 5.9417 | 5.5138 | 4.8655 | 4.4558
|  | ABERFELDY | CT |  |  |  | 6.7965 | 6.7927 | 6.7883 | 6.784 | 6.7795 | 6.7744 | 6.7693 | 6.7636 | 6.7578 | 6.7517 | 6.7476 | 6.5481 | 6.0454 | 5.782 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.2817 | 7.2115 | 7.1388 | 7.0618 | 7.0115 | 6.684 | 6.1929 | 5.8972 | 6.5521 | 6.5521 | 6.5521 | 6.5521 | 6.5521 | 6.518 | 6.4465 | 6.3681 | 6.287 | 6.201 | 6.1448 | 5.7973 | 5.2476 | 4.9384
|  | ABERFELDY | LW |  |  |  | 6.7961 | 6.7913 | 6.7851 | 6.7792 | 6.7732 | 6.7664 | 6.7599 | 6.7528 | 6.7456 | 6.7314 | 6.6712 | 6.3066 | 5.7199 | 5.3709 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.2464 | 7.1647 | 7.0762 | 6.9863 | 6.8897 | 6.8221 | 6.4128 | 5.8275 | 5.4357 | 6.5521 | 6.5521 | 6.5521 | 6.5521 | 6.5005 | 6.4071 | 6.3158 | 6.2171 | 6.1167 | 6.0124 | 5.9417 | 5.5138 | 4.8655 | 4.4558
|  | ABERFELDY | ST |  |  |  | 6.7977 | 6.7959 | 6.7933 | 6.7904 | 6.7868 | 6.7829 | 6.7789 | 6.7745 | 6.77 | 6.7652 | 6.762 | 6.747 | 6.5657 | 6.4142 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.2907 | 7.2308 | 7.1904 | 7.0037 | 6.7403 | 6.5703 | 6.5521 | 6.5521 | 6.5521 | 6.5521 | 6.5521 | 6.5521 | 6.5521 | 6.5198 | 6.4566 | 6.3897 | 6.3445 | 6.1362 | 5.8381 | 5.6603
|  | ABERFELDY | FS |  |  |  | 6.7985 | 6.7981 | 6.7971 | 6.7962 | 6.7949 | 6.7934 | 6.7918 | 6.7901 | 6.7883 | 6.7865 | 6.7852 | 6.7792 | 6.7743 | 6.7699 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.3111 | 7.2893 | 6.5521 | 6.5521 | 6.5521 | 6.5521 | 6.5521 | 6.5521 | 6.5521 | 6.5521 | 6.5521 | 6.5521 | 6.5521 | 6.5521 | 6.5165 | 6.455
| STRATHLEVEN | ABERFOYLE | MINIMUM HEADROOM | NS 53215 99705 | YES | YES | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.4707 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.1885 | 4.1828 | 4.1752 | 4.1669 | 4.1579 | 4.1457 | 4.1313 | 4.1157 | 4.0986 | 4.0814 | 4.0635 | 3.8824 | 3.6979 | 3.5141
|  | ABERFOYLE | CT |  |  |  | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.189 | 4.1847 | 4.1793 | 4.1733 | 4.1666 | 4.1593 | 4.1517 | 4.14 | 4.127 | 4.1139 | 4.1001 | 3.9643 | 3.8258 | 3.6874
|  | ABERFOYLE | LW |  |  |  | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.4707 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.1885 | 4.1828 | 4.1752 | 4.1669 | 4.1579 | 4.1457 | 4.1313 | 4.1157 | 4.0986 | 4.0814 | 4.0635 | 3.8824 | 3.6979 | 3.5141
|  | ABERFOYLE | ST |  |  |  | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.1903 | 4.1883 | 4.1851 | 4.1809 | 4.1708 | 4.1604 | 4.1487 | 4.132 | 4.1143 | 4.0967 | 4.0787 | 3.9855 | 3.8942 | 3.8046
|  | ABERFOYLE | FS |  |  |  | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.5364 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.4225 | 4.1913 | 4.1909 | 4.1898 | 4.1885 | 4.1852 | 4.1818 | 4.1777 | 4.1736 | 4.1693 | 4.1651 | 4.1607 | 4.13 | 4.0948 | 4.0592
| KEITH | ABERLOUR | MINIMUM HEADROOM | NJ 24809 40878 | NO | YES | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 6.525 | 6.5194 | 6.5177 | 6.5165 | 6.5154 | 6.5143 | 6.5132 | 6.512 | 6.5108 | 6.5096 | 6.5085 | 6.4887 | 6.4684 | 6.4485 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582
|  | ABERLOUR | CT |  |  |  | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 6.5269 | 6.5199 | 6.5187 | 6.5179 | 6.517 | 6.516 | 6.5149 | 6.5139 | 6.513 | 6.5122 | 6.5114 | 6.4952 | 6.4787 | 6.4624 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582
|  | ABERLOUR | LW |  |  |  | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 6.525 | 6.5194 | 6.5177 | 6.5165 | 6.5154 | 6.5143 | 6.5132 | 6.512 | 6.5108 | 6.5096 | 6.5085 | 6.4887 | 6.4684 | 6.4485 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582
|  | ABERLOUR | ST |  |  |  | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 6.5331 | 6.5253 | 6.5206 | 6.52 | 6.5185 | 6.5169 | 6.5153 | 6.5136 | 6.512 | 6.5105 | 6.5091 | 6.5019 | 6.4948 | 6.4877 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582
|  | ABERLOUR | FS |  |  |  | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 7.0368 | 6.5383 | 6.5351 | 6.5323 | 6.5305 | 6.5251 | 6.5207 | 6.52 | 6.5193 | 6.5186 | 6.5179 | 6.5173 | 6.5143 | 6.5116 | 6.5089 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582 | 7.1582
| ABERNETHY | ABERNETHY | MINIMUM HEADROOM | NO 20094 17132 | YES | YES | 1.5137 | 1.4382 | 1.3707 | 1.3056 | 1.2429 | 1.1827 | 1.1248 | 1.0941 | 1.0788 | 1.0636 | 1.0487 | 0.9795 | 0.51319 | 0.44029 | 1.5617 | 1.5281 | 1.4979 | 1.4688 | 1.4407 | 1.3888 | 1.329 | 1.2925 | 1.27 | 1.2472 | 1.2243 | 1.1132 | 0.65177 | 0.54341 | 1.2283 | 1.1407 | 1.0607 | 0.98291 | 0.90731 | 0.83492 | 0.76511 | 0.72363 | 0.69893 | 0.67406 | 0.64908 | 0.52884 | -0.014404 | -0.13302
|  | ABERNETHY | CT |  |  |  | 1.5137 | 1.4382 | 1.3707 | 1.3056 | 1.2429 | 1.1827 | 1.1248 | 1.0941 | 1.0788 | 1.0636 | 1.0487 | 0.9795 | 0.51319 | 0.44029 | 1.5617 | 1.5281 | 1.4979 | 1.4688 | 1.4407 | 1.3888 | 1.329 | 1.2925 | 1.27 | 1.2472 | 1.2243 | 1.1132 | 0.65177 | 0.54341 | 1.2283 | 1.1407 | 1.0607 | 0.98291 | 0.90731 | 0.83492 | 0.76511 | 0.72363 | 0.69893 | 0.67406 | 0.64908 | 0.52884 | -0.014404 | -0.13302
|  | ABERNETHY | LW |  |  |  | 1.6474 | 1.6361 | 1.6233 | 1.6093 | 1.594 | 1.5778 | 1.5606 | 1.5425 | 1.5239 | 1.5049 | 1.4856 | 1.3835 | 0.8739 | 0.76327 | 1.6206 | 1.6153 | 1.6092 | 1.6025 | 1.5953 | 1.5876 | 1.5796 | 1.5711 | 1.5623 | 1.5534 | 1.5444 | 1.4363 | 0.91659 | 0.75549 | 1.3714 | 1.3517 | 1.3289 | 1.3046 | 1.2785 | 1.2517 | 1.224 | 1.1945 | 1.1646 | 1.1339 | 1.1025 | 0.92825 | 0.32019 | 0.1433
|  | ABERNETHY | ST |  |  |  | 1.6668 | 1.6622 | 1.6579 | 1.6536 | 1.6484 | 1.6433 | 1.6384 | 1.634 | 1.6275 | 1.6213 | 1.6152 | 1.5821 | 1.3545 | 1.3242 | 1.6294 | 1.6273 | 1.6252 | 1.6232 | 1.6205 | 1.618 | 1.6155 | 1.6132 | 1.61 | 1.6069 | 1.6038 | 1.5874 | 1.4571 | 1.3983 | 1.3967 | 1.3898 | 1.3821 | 1.3736 | 1.3614 | 1.3497 | 1.3383 | 1.3268 | 1.3132 | 1.2997 | 1.2861 | 1.2161 | 0.9405 | 0.87844
|  | ABERNETHY | FS |  |  |  | 1.6622 | 1.6577 | 1.6511 | 1.6445 | 1.638 | 1.6316 | 1.6252 | 1.619 | 1.6129 | 1.6068 | 1.6008 | 1.5651 | 1.5283 | 1.4928 | 1.6276 | 1.6256 | 1.6226 | 1.6196 | 1.6166 | 1.6137 | 1.6108 | 1.6079 | 1.605 | 1.6022 | 1.5994 | 1.583 | 1.5661 | 1.5499 | 1.3945 | 1.3892 | 1.381 | 1.3727 | 1.3635 | 1.3545 | 1.345 | 1.3357 | 1.3265 | 1.3174 | 1.3083 | 1.2565 | 1.2048 | 1.1559
| TARLAND | ABOYNE | MINIMUM HEADROOM | NO 52048 98716 | NO | YES | 18.7177 | 18.7123 | 18.7055 | 18.6988 | 18.6919 | 18.6851 | 18.6783 | 18.671 | 18.664 | 18.6567 | 18.6496 | 18.5813 | 18.5126 | 18.4454 | 15.9972 | 15.9835 | 15.9783 | 15.975 | 15.9716 | 15.9682 | 15.9649 | 15.9613 | 15.9578 | 15.9543 | 15.9507 | 13.6119 | 12.9514 | 12.3049 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 13.5088 | 12.8547
|  | ABOYNE | CT |  |  |  | 18.7179 | 18.7137 | 18.7087 | 18.7037 | 18.6987 | 18.6935 | 18.6885 | 18.683 | 18.6778 | 18.6724 | 18.6671 | 18.6223 | 18.5773 | 18.5334 | 15.9978 | 15.987 | 15.9799 | 15.9774 | 15.9749 | 15.9724 | 15.9699 | 15.9672 | 15.9647 | 15.962 | 15.9594 | 15.9373 | 13.5741 | 13.1514 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 13.7112
|  | ABOYNE | LW |  |  |  | 18.7177 | 18.7123 | 18.7055 | 18.6988 | 18.6919 | 18.6851 | 18.6783 | 18.671 | 18.664 | 18.6567 | 18.6496 | 18.5813 | 18.5126 | 18.4454 | 15.9972 | 15.9835 | 15.9783 | 15.975 | 15.9716 | 15.9682 | 15.9649 | 15.9613 | 15.9578 | 15.9543 | 15.9507 | 13.6119 | 12.9514 | 12.3049 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 13.5088 | 12.8547
|  | ABOYNE | ST |  |  |  | 18.7197 | 18.7183 | 18.7162 | 18.7136 | 18.7072 | 18.7009 | 18.6948 | 18.6881 | 18.6816 | 18.6751 | 18.6687 | 18.6375 | 18.607 | 18.577 | 16.0021 | 15.9987 | 15.9933 | 15.9868 | 15.9792 | 15.9761 | 15.973 | 15.9697 | 15.9665 | 15.9633 | 15.9602 | 15.9448 | 15.9297 | 13.5714 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968
|  | ABOYNE | FS |  |  |  | 18.7204 | 18.7202 | 18.7196 | 18.7188 | 18.7167 | 18.7146 | 18.712 | 18.7094 | 18.7069 | 18.7043 | 18.7019 | 18.6899 | 18.6787 | 18.6681 | 16.004 | 16.0036 | 16.002 | 16 | 15.9947 | 15.9894 | 15.9828 | 15.9802 | 15.979 | 15.9777 | 15.9765 | 15.9706 | 15.9651 | 15.9599 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968 | 16.7968
| GRUDIE BRIDGE | ACHILTIBUIE | MINIMUM HEADROOM | NC 01618 09557 | YES | YES | 2.0605 | 2.0603 | 2.06 | 2.0597 | 2.0594 | 2.0591 | 2.0586 | 2.058 | 2.0575 | 2.0569 | 2.0564 | 2.0514 | 0.95512 | 0.93439 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 0.66597 | 0.58341 | 1.4043 | 1.404 | 1.4037 | 1.4034 | 1.4031 | 1.4028 | 1.4023 | 1.4016 | 1.401 | 1.4004 | 1.3998 | 1.3946 | 0.4772 | 0.39696
|  | ACHILTIBUIE | CT |  |  |  | 2.0606 | 2.0604 | 2.0602 | 2.0599 | 2.0597 | 2.0595 | 2.0593 | 2.0591 | 2.0589 | 2.0587 | 2.0585 | 2.054 | 0.96957 | 0.95455 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 0.72349 | 0.66371 | 1.4043 | 1.4041 | 1.4039 | 1.4037 | 1.4034 | 1.4032 | 1.403 | 1.4028 | 1.4026 | 1.4024 | 1.4021 | 1.3974 | 0.5331 | 0.475
|  | ACHILTIBUIE | LW |  |  |  | 2.0605 | 2.0603 | 2.06 | 2.0597 | 2.0594 | 2.0591 | 2.0588 | 2.0585 | 2.0582 | 2.0579 | 2.0576 | 2.0514 | 0.95512 | 0.93439 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 0.66597 | 0.58341 | 1.4043 | 1.404 | 1.4037 | 1.4034 | 1.4031 | 1.4028 | 1.4025 | 1.4022 | 1.4018 | 1.4015 | 1.4012 | 1.3946 | 0.4772 | 0.39696
|  | ACHILTIBUIE | ST |  |  |  | 2.0606 | 2.0605 | 2.0604 | 2.0603 | 2.0597 | 2.0592 | 2.0586 | 2.058 | 2.0575 | 2.0569 | 2.0564 | 2.0536 | 1.8534 | 1.8507 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 0.9106 | 0.87479 | 1.4044 | 1.4043 | 1.4042 | 1.404 | 1.4034 | 1.4028 | 1.4023 | 1.4016 | 1.401 | 1.4004 | 1.3998 | 1.397 | 0.7812 | 0.7464
|  | ACHILTIBUIE | FS |  |  |  | 2.0607 | 2.0607 | 2.0606 | 2.0606 | 2.0604 | 2.0602 | 2.06 | 2.0597 | 2.0595 | 2.0593 | 2.0591 | 2.058 | 2.057 | 2.0561 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 1.8805 | 1.4044 | 1.4044 | 1.4044 | 1.4043 | 1.4041 | 1.404 | 1.4037 | 1.4035 | 1.4032 | 1.403 | 1.4027 | 1.4016 | 1.4006 | 1.3996
| BEAULY | AIGAS | MINIMUM HEADROOM | NH 45362 40529 | YES | YES | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.48505 | 0.54648 | 0.54598 | 0.54536 | 0.54476 | 0.54417 | 0.54333 | 0.54232 | 0.54192 | 0.54166 | 0.54161 | 0.54161 | 0.49532 | 0.46403 | 0.43332 | 0.55253 | 0.55229 | 0.55199 | 0.55174 | 0.55174 | 0.55174 | 0.55174 | 0.55174 | 0.55174 | 0.55174 | 0.55174 | 0.55174 | 0.4732 | 0.44248
|  | AIGAS | CT |  |  |  | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.54651 | 0.54613 | 0.5457 | 0.54528 | 0.54486 | 0.54446 | 0.54406 | 0.54365 | 0.54333 | 0.54301 | 0.54269 | 0.54161 | 0.4852 | 0.46313 | 0.55255 | 0.55236 | 0.55215 | 0.55195 | 0.55175 | 0.55174 | 0.55174 | 0.55174 | 0.55174 | 0.55174 | 0.55174 | 0.55174 | 0.49408 | 0.4723
|  | AIGAS | LW |  |  |  | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.48505 | 0.54648 | 0.54598 | 0.54536 | 0.54476 | 0.54417 | 0.54362 | 0.5432 | 0.54273 | 0.54228 | 0.54206 | 0.54195 | 0.49532 | 0.46403 | 0.43332 | 0.55253 | 0.55229 | 0.55199 | 0.55174 | 0.55174 | 0.55174 | 0.55174 | 0.55174 | 0.55174 | 0.55174 | 0.55174 | 0.55174 | 0.4732 | 0.44248
|  | AIGAS | ST |  |  |  | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.54664 | 0.54649 | 0.54625 | 0.54597 | 0.54457 | 0.54333 | 0.54232 | 0.54192 | 0.54166 | 0.54161 | 0.54161 | 0.54161 | 0.49014 | 0.47668 | 0.55261 | 0.55254 | 0.55242 | 0.55229 | 0.55174 | 0.55174 | 0.55174 | 0.55174 | 0.55174 | 0.55174 | 0.55174 | 0.55174 | 0.4989 | 0.48578
|  | AIGAS | FS |  |  |  | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.5852 | 0.54673 | 0.54672 | 0.54665 | 0.54657 | 0.54611 | 0.54566 | 0.54509 | 0.54452 | 0.54396 | 0.54349 | 0.54308 | 0.5419 | 0.54161 | 0.54161 | 0.55266 | 0.55265 | 0.55262 | 0.55258 | 0.55236 | 0.55214 | 0.55186 | 0.55174 | 0.55174 | 0.55174 | 0.55174 | 0.55174 | 0.55174 | 0.55174
| ARDMORE | AIRD | MINIMUM HEADROOM | NF 79163 53853 | NO | YES | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 7.4504 | 7.4327 | 7.2853 | 8.7311 | 8.7222 | 8.7114 | 8.7007 | 8.6902 | 8.6799 | 8.6698 | 8.6589 | 8.648 | 8.6372 | 8.6265 | 7.1045 | 6.9504 | 6.7986 | 8.8446 | 8.8365 | 8.8265 | 8.8167 | 8.8071 | 8.7977 | 8.7884 | 8.7788 | 8.7762 | 8.7736 | 8.771 | 6.8444 | 6.6807 | 6.5195
|  | AIRD | CT |  |  |  | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 7.4504 | 7.4504 | 7.4504 | 8.7318 | 8.7254 | 8.7181 | 8.711 | 8.7039 | 8.697 | 8.6902 | 8.6829 | 8.6756 | 8.6684 | 8.6612 | 7.2259 | 7.1125 | 7.0008 | 8.8452 | 8.8394 | 8.8327 | 8.8261 | 8.8197 | 8.8134 | 8.8072 | 8.8005 | 8.7938 | 8.7871 | 8.7806 | 6.9734 | 6.8529 | 6.7343
|  | AIRD | LW |  |  |  | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 7.4504 | 7.4327 | 7.2853 | 8.7311 | 8.7222 | 8.7114 | 8.7007 | 8.6902 | 8.6799 | 8.6698 | 8.6589 | 8.648 | 8.6372 | 8.6265 | 7.1045 | 6.9504 | 6.7986 | 8.8446 | 8.8365 | 8.8265 | 8.8167 | 8.8071 | 8.7977 | 8.7884 | 8.7788 | 8.7762 | 8.7736 | 8.771 | 6.8444 | 6.6807 | 6.5195
|  | AIRD | ST |  |  |  | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.2658 | 9.2658 | 9.2658 | 8.7339 | 8.7313 | 8.7272 | 8.7222 | 8.7161 | 8.7101 | 8.7042 | 8.6979 | 8.6916 | 8.6855 | 8.6795 | 8.3844 | 7.5711 | 7.5031 | 8.8472 | 8.8448 | 8.841 | 8.8365 | 8.8309 | 8.8254 | 8.82 | 8.8141 | 8.8084 | 8.8028 | 8.7973 | 7.4786 | 7.4062 | 7.3339
|  | AIRD | FS |  |  |  | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 9.6363 | 8.7355 | 8.7353 | 8.7341 | 8.7327 | 8.7308 | 8.7288 | 8.7263 | 8.7239 | 8.7215 | 8.7191 | 8.7168 | 8.7057 | 8.6954 | 8.6857 | 8.8486 | 8.8484 | 8.8474 | 8.8461 | 8.8443 | 8.8425 | 8.8402 | 8.838 | 8.8358 | 8.8336 | 8.8315 | 8.8214 | 8.8119 | 8.803
| PORT ANN | AIRIGH-NA-BRODAIG | MINIMUM HEADROOM | NR 85849 74792 | YES | YES | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315
|  | AIRIGH-NA-BRODAIG | CT |  |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315
|  | AIRIGH-NA-BRODAIG | LW |  |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315
|  | AIRIGH-NA-BRODAIG | ST |  |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315
|  | AIRIGH-NA-BRODAIG | FS |  |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315
| COUPAR ANGUS | ALYTH | MINIMUM HEADROOM | NO 23579 48311 | NO | YES | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.2685 | 7.2685 | 4.8166 | 6.6028 | 6.5966 | 6.5887 | 6.5796 | 6.569 | 6.565 | 6.565 | 6.565 | 6.565 | 6.565 | 6.565 | 4.4061 | 3.9432 | 3.4949 | 6.9521 | 6.9459 | 6.9379 | 6.9287 | 6.918 | 6.9062 | 4.9314 | 4.8366 | 4.7559 | 4.6733 | 4.6105 | 3.9175 | 3.4681 | 3.033
|  | ALYTH | CT |  |  |  | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.2685 | 7.2685 | 7.2685 | 6.6034 | 6.5986 | 6.5927 | 6.5856 | 6.5772 | 6.568 | 6.565 | 6.565 | 6.565 | 6.565 | 6.565 | 4.6783 | 4.3463 | 4.0284 | 6.9527 | 6.9478 | 6.9419 | 6.9348 | 6.9263 | 6.917 | 6.9076 | 4.9893 | 4.9125 | 4.8314 | 4.7752 | 4.1818 | 3.8595 | 3.5509
|  | ALYTH | LW |  |  |  | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.2685 | 7.2685 | 4.8166 | 6.6028 | 6.5966 | 6.5887 | 6.5796 | 6.569 | 6.565 | 6.565 | 6.565 | 6.565 | 6.565 | 6.565 | 4.4061 | 3.9432 | 3.4949 | 6.9521 | 6.9459 | 6.9379 | 6.9287 | 6.918 | 6.9062 | 4.9314 | 4.8366 | 4.7559 | 4.6733 | 4.6105 | 3.9175 | 3.4681 | 3.033
|  | ALYTH | ST |  |  |  | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.3747 | 7.3747 | 7.3747 | 6.6051 | 6.6026 | 6.5991 | 6.5945 | 6.5874 | 6.5799 | 6.5723 | 6.5657 | 6.565 | 6.565 | 6.565 | 6.5041 | 4.8793 | 4.6838 | 6.9545 | 6.952 | 6.9484 | 6.9437 | 6.9366 | 6.929 | 6.9213 | 6.9147 | 6.9084 | 6.9018 | 4.955 | 4.6069 | 4.4093 | 4.2194
|  | ALYTH | FS |  |  |  | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 7.4808 | 6.623 | 6.6056 | 6.6041 | 6.6023 | 6.5996 | 6.5966 | 6.5934 | 6.5909 | 6.5885 | 6.5861 | 6.5841 | 6.5754 | 6.5687 | 6.565 | 6.9607 | 6.9549 | 6.9535 | 6.9516 | 6.9489 | 6.9459 | 6.9427 | 6.9401 | 6.9377 | 6.9353 | 6.9333 | 6.9245 | 6.9177 | 6.9115
| FORT WILLIAM | ANNAT | MINIMUM HEADROOM | NN 08452 76751 | YES | YES | 9.2711 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 8.698 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 7.2967 | 7.0649 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 7.4012 | 7.1692 | 6.942
|  | ANNAT | CT |  |  |  | 9.2711 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 8.698 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 7.3696 | 7.1706 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 7.439 | 7.2406 | 7.0456
|  | ANNAT | LW |  |  |  | 9.2771 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 8.7009 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 7.2967 | 7.0649 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 7.4012 | 7.1692 | 6.942
|  | ANNAT | ST |  |  |  | 9.2933 | 9.279 | 9.2567 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 8.7086 | 8.7018 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796
|  | ANNAT | FS |  |  |  | 9.3015 | 9.3003 | 9.2939 | 9.2863 | 9.2814 | 9.2766 | 9.2704 | 9.2643 | 9.2583 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 9.2526 | 8.7125 | 8.712 | 8.7089 | 8.7052 | 8.7029 | 8.7006 | 8.6976 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6965 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796 | 8.6796
| KILLIN | ARDCHYLE | MINIMUM HEADROOM | NN 52734 29223 | YES | YES | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
|  | ARDCHYLE | CT |  |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
|  | ARDCHYLE | LW |  |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
|  | ARDCHYLE | ST |  |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
|  | ARDCHYLE | FS |  |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
| NAIRN | ARDERSIER | MINIMUM HEADROOM | NH 80475 55905 | NO | YES | 6.4454 | 6.4429 | 6.4398 | 6.4366 | 6.4331 | 6.4293 | 6.4252 | 6.4208 | 6.4163 | 6.416 | 6.416 | 6.416 | 6.416 | 6.416 | 5.9289 | 5.91 | 5.8874 | 5.8696 | 5.8696 | 5.8696 | 5.8696 | 5.8696 | 5.8696 | 5.8696 | 5.8696 | 4.687 | 4.533 | 4.3839 | 5.9546 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 4.8169 | 4.6725 | 4.5326
|  | ARDERSIER | CT |  |  |  | 6.4461 | 6.4446 | 6.4429 | 6.441 | 6.4387 | 6.4362 | 6.4333 | 6.43 | 6.4265 | 6.4225 | 6.4186 | 6.416 | 6.416 | 6.416 | 5.934 | 5.923 | 5.9106 | 5.8959 | 5.8787 | 5.8696 | 5.8696 | 5.8696 | 5.8696 | 5.8696 | 5.8696 | 4.9832 | 4.8661 | 4.7565 | 5.9565 | 5.9524 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 4.9848 | 4.882
|  | ARDERSIER | LW |  |  |  | 6.4454 | 6.4429 | 6.4398 | 6.4366 | 6.4331 | 6.4293 | 6.4252 | 6.4208 | 6.4163 | 6.416 | 6.416 | 6.416 | 6.416 | 6.416 | 5.9289 | 5.91 | 5.8874 | 5.8696 | 5.8696 | 5.8696 | 5.8696 | 5.8696 | 5.8696 | 5.8696 | 5.8696 | 4.687 | 4.533 | 4.3839 | 5.9546 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 4.8169 | 4.6725 | 4.5326
|  | ARDERSIER | ST |  |  |  | 6.4466 | 6.4451 | 6.4432 | 6.4408 | 6.4384 | 6.4359 | 6.4332 | 6.4301 | 6.4268 | 6.4231 | 6.4194 | 6.416 | 6.416 | 6.416 | 5.9381 | 5.927 | 5.9123 | 5.8944 | 5.8767 | 5.8696 | 5.8696 | 5.8696 | 5.8696 | 5.8696 | 5.8696 | 5.8696 | 4.9904 | 4.9262 | 5.958 | 5.9539 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518 | 5.9518
|  | ARDERSIER | FS |  |  |  | 6.4552 | 6.4547 | 6.4541 | 6.4533 | 6.4524 | 6.4514 | 6.4503 | 6.4491 | 6.4478 | 6.4464 | 6.445 | 6.4383 | 6.435 | 6.433 | 6.0024 | 5.9987 | 5.9937 | 5.9883 | 5.9813 | 5.9739 | 5.9654 | 5.9563 | 5.9467 | 5.9365 | 5.9258 | 5.8758 | 5.8696 | 5.8696 | 5.9819 | 5.9805 | 5.9786 | 5.9766 | 5.974 | 5.9713 | 5.9681 | 5.9647 | 5.9612 | 5.9574 | 5.9534 | 5.9518 | 5.9518 | 5.9518
| FORT AUGUSTUS | ARDOCHY | MINIMUM HEADROOM | NH 47714 12561 | YES | YES | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
|  | ARDOCHY | CT |  |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
|  | ARDOCHY | LW |  |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
|  | ARDOCHY | ST |  |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
|  | ARDOCHY | FS |  |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
| FORT WILLIAM | ARISAIG | MINIMUM HEADROOM | NM 66564 86619 | YES | YES | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9292 | 2.9269 | 2.924 | 2.9212 | 2.9184 | 2.9157 | 2.913 | 2.9101 | 2.9065 | 2.9024 | 2.8984 | 2.8787 | 2.8637 | 2.8607 | 2.9242 | 2.9234 | 2.9224 | 2.9215 | 2.9206 | 2.9196 | 2.9187 | 2.918 | 2.918 | 2.918 | 2.918 | 2.918 | 2.918 | 2.918
|  | ARISAIG | CT |  |  |  | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9294 | 2.9276 | 2.9256 | 2.9236 | 2.9217 | 2.9198 | 2.9179 | 2.9158 | 2.9138 | 2.9118 | 2.9098 | 2.8857 | 2.8724 | 2.8633 | 2.9242 | 2.9236 | 2.923 | 2.9223 | 2.9217 | 2.921 | 2.9204 | 2.9197 | 2.919 | 2.9183 | 2.918 | 2.918 | 2.918 | 2.918
|  | ARISAIG | LW |  |  |  | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9292 | 2.9269 | 2.924 | 2.9212 | 2.9184 | 2.9157 | 2.913 | 2.9101 | 2.9072 | 2.9043 | 2.9015 | 2.8787 | 2.8637 | 2.8607 | 2.9242 | 2.9234 | 2.9224 | 2.9215 | 2.9206 | 2.9196 | 2.9187 | 2.918 | 2.918 | 2.918 | 2.918 | 2.918 | 2.918 | 2.918
|  | ARISAIG | ST |  |  |  | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.93 | 2.9293 | 2.9282 | 2.9269 | 2.9228 | 2.9188 | 2.9149 | 2.9107 | 2.9065 | 2.9024 | 2.8984 | 2.8874 | 2.8803 | 2.8731 | 2.9244 | 2.9242 | 2.9238 | 2.9234 | 2.922 | 2.9207 | 2.9194 | 2.918 | 2.918 | 2.918 | 2.918 | 2.918 | 2.918 | 2.918
|  | ARISAIG | FS |  |  |  | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9937 | 2.9304 | 2.9303 | 2.93 | 2.9297 | 2.9283 | 2.9269 | 2.9252 | 2.9235 | 2.9218 | 2.9201 | 2.9185 | 2.9108 | 2.9034 | 2.8964 | 2.9246 | 2.9246 | 2.9245 | 2.9243 | 2.9239 | 2.9234 | 2.9228 | 2.9223 | 2.9217 | 2.9211 | 2.9206 | 2.918 | 2.918 | 2.918
| STORNOWAY | ARNISH | MINIMUM HEADROOM | NB 42300 30440 | YES | YES | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 12 | 11.9999 | 11.9998 | 11.9998 | 11.9997 | 11.9996 | 11.9996 | 11.9995 | 11.9994 | 11.9994 | 11.9993 | 11.999 | 11.9987 | 11.9983 | 12 | 11.9999 | 11.9998 | 11.9998 | 11.9997 | 11.9996 | 11.9996 | 11.9995 | 11.9995 | 11.9994 | 11.9993 | 11.999 | 11.9987 | 11.9983
|  | ARNISH | CT |  |  |  | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 12 | 11.9999 | 11.9999 | 11.9998 | 11.9998 | 11.9997 | 11.9997 | 11.9997 | 11.9996 | 11.9996 | 11.9995 | 11.9993 | 11.9991 | 11.9988 | 12 | 11.9999 | 11.9999 | 11.9998 | 11.9998 | 11.9997 | 11.9997 | 11.9997 | 11.9996 | 11.9996 | 11.9995 | 11.9993 | 11.9991 | 11.9988
|  | ARNISH | LW |  |  |  | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 12 | 11.9999 | 11.9998 | 11.9998 | 11.9997 | 11.9996 | 11.9996 | 11.9995 | 11.9994 | 11.9994 | 11.9993 | 11.999 | 11.9987 | 11.9983 | 12 | 11.9999 | 11.9998 | 11.9998 | 11.9997 | 11.9996 | 11.9996 | 11.9995 | 11.9995 | 11.9994 | 11.9993 | 11.999 | 11.9987 | 11.9983
|  | ARNISH | ST |  |  |  | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 12 | 12 | 11.9999 | 11.9999 | 11.9999 | 11.9999 | 11.9998 | 11.9998 | 11.9998 | 11.9997 | 11.9997 | 11.9996 | 11.9994 | 11.9993 | 12 | 12 | 11.9999 | 11.9999 | 11.9999 | 11.9999 | 11.9998 | 11.9998 | 11.9998 | 11.9997 | 11.9997 | 11.9996 | 11.9994 | 11.9993
|  | ARNISH | FS |  |  |  | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 17.6744 | 12 | 12 | 12 | 12 | 12 | 12 | 11.9999 | 11.9999 | 11.9999 | 11.9999 | 11.9999 | 11.9998 | 11.9998 | 11.9997 | 12 | 12 | 12 | 12 | 12 | 12 | 11.9999 | 11.9999 | 11.9999 | 11.9999 | 11.9999 | 11.9998 | 11.9998 | 11.9997
| ELGIN | ASHGROVE | MINIMUM HEADROOM | NJ 22458 62130 | YES | YES | 27.5923 | 27.5147 | 27.4438 | 27.3754 | 27.3096 | 27.2463 | 27.1855 | 27.1522 | 27.1356 | 27.1192 | 27.103 | 27.0264 | 22.7252 | 22.0693 | 24.0205 | 23.8749 | 23.8011 | 23.7592 | 23.7211 | 23.6845 | 23.6493 | 23.63 | 21.9058 | 21.5434 | 21.1698 | 19.544 | 18.8095 | 18.0938 | 24.2105 | 24.1102 | 24.0214 | 23.9514 | 23.8858 | 23.8228 | 23.7623 | 23.729 | 23.7125 | 21.747 | 21.3681 | 19.7145 | 18.9491 | 18.2015
|  | ASHGROVE | CT |  |  |  | 27.5923 | 27.5147 | 27.4438 | 27.3754 | 27.3096 | 27.2463 | 27.1855 | 27.1522 | 27.1356 | 27.1192 | 27.103 | 27.0264 | 26.9473 | 23.0985 | 24.0205 | 23.8749 | 23.8011 | 23.7592 | 23.7211 | 23.6845 | 23.6493 | 23.63 | 22.0157 | 21.7322 | 21.4316 | 20.5505 | 19.9844 | 19.4503 | 24.2105 | 24.1102 | 24.0214 | 23.9514 | 23.8858 | 23.8228 | 23.7623 | 23.729 | 23.7125 | 21.8194 | 21.5146 | 20.6139 | 20.0278 | 19.4724
|  | ASHGROVE | LW |  |  |  | 27.7297 | 27.718 | 27.7049 | 27.6905 | 27.6748 | 27.6581 | 27.6405 | 27.6213 | 27.6016 | 27.5815 | 27.561 | 27.4529 | 22.7252 | 22.0693 | 24.1177 | 23.9955 | 23.9522 | 23.9415 | 23.9325 | 23.9228 | 23.9126 | 23.9015 | 21.9058 | 21.5434 | 21.1698 | 19.544 | 18.8095 | 18.0938 | 24.347 | 24.3063 | 24.2894 | 24.2745 | 24.2585 | 24.2413 | 24.2232 | 24.2036 | 24.1833 | 21.747 | 21.3681 | 19.7145 | 18.9491 | 18.2015
|  | ASHGROVE | ST |  |  |  | 27.7496 | 27.7449 | 27.7404 | 27.736 | 27.7307 | 27.7255 | 27.7205 | 27.7158 | 27.709 | 27.7024 | 27.696 | 27.661 | 27.6297 | 27.596 | 24.1791 | 24.1337 | 24.0861 | 24.0358 | 23.9913 | 23.9717 | 23.9609 | 23.9562 | 23.9522 | 23.9484 | 23.9447 | 22.0688 | 21.753 | 21.457 | 24.3788 | 24.3635 | 24.3476 | 24.3312 | 24.3158 | 24.3105 | 24.3053 | 24.3005 | 24.2936 | 24.2868 | 24.2802 | 24.2443 | 21.9687 | 21.6642
|  | ASHGROVE | FS |  |  |  | 27.7449 | 27.7403 | 27.7334 | 27.7267 | 27.72 | 27.7134 | 27.7069 | 27.7005 | 27.6942 | 27.688 | 27.6818 | 27.6451 | 27.607 | 27.5702 | 24.1983 | 24.1806 | 24.158 | 24.1349 | 24.1119 | 24.0889 | 24.0629 | 24.0206 | 23.9757 | 23.9524 | 23.9419 | 23.9152 | 23.8932 | 23.8719 | 24.38 | 24.3717 | 24.3603 | 24.3489 | 24.3376 | 24.3264 | 24.3145 | 24.2985 | 24.2819 | 24.272 | 24.2657 | 24.2279 | 24.1888 | 24.151
| MILTON OF CRAIGIE | ASHLUDIE | MINIMUM HEADROOM | NO 49222 33584 | NO | YES | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 8.9249 | 7.7076 | 6.5091 | 15.8582 | 15.746 | 15.6249 | 15.5825 | 15.5597 | 15.5373 | 15.5153 | 15.4914 | 15.4676 | 15.4439 | 9.8149 | 8.3371 | 6.8651 | 5.4159 | 16.0725 | 15.9795 | 15.8679 | 15.7584 | 15.6769 | 15.6082 | 15.5406 | 15.489 | 15.489 | 15.489 | 15.489 | 8.8817 | 7.4527 | 6.0458
|  | ASHLUDIE | CT |  |  |  | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 9.2886 | 15.8802 | 15.8002 | 15.7315 | 15.6639 | 15.6002 | 15.5873 | 15.5747 | 15.5611 | 15.5476 | 15.5341 | 15.5206 | 15.4693 | 9.7731 | 8.7769 | 16.0866 | 16.0295 | 15.9662 | 15.9038 | 15.842 | 15.781 | 15.7229 | 15.6812 | 15.6396 | 15.5982 | 15.5571 | 15.489 | 15.489 | 9.3087
|  | ASHLUDIE | LW |  |  |  | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 8.9249 | 7.7076 | 6.5091 | 15.8582 | 15.746 | 15.6249 | 15.5825 | 15.5597 | 15.5373 | 15.5153 | 15.4914 | 15.4676 | 15.4439 | 9.8149 | 8.3371 | 6.8651 | 5.4159 | 16.0725 | 15.9795 | 15.8679 | 15.7584 | 15.6769 | 15.6082 | 15.5406 | 15.489 | 15.489 | 15.489 | 15.489 | 8.8817 | 7.4527 | 6.0458
|  | ASHLUDIE | ST |  |  |  | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 15.9093 | 15.8636 | 15.8031 | 15.7462 | 15.711 | 15.6763 | 15.6427 | 15.6065 | 15.5951 | 15.5882 | 15.5814 | 15.5478 | 15.515 | 15.4824 | 16.1053 | 16.076 | 16.0322 | 15.9797 | 15.9472 | 15.9153 | 15.8842 | 15.8509 | 15.8178 | 15.7853 | 15.7533 | 15.6403 | 15.5399 | 15.489
|  | ASHLUDIE | FS |  |  |  | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 16.297 | 15.9388 | 15.9344 | 15.9151 | 15.8925 | 15.8759 | 15.8597 | 15.8389 | 15.8191 | 15.805 | 15.7911 | 15.7776 | 15.7124 | 15.6519 | 15.5998 | 16.1243 | 16.1214 | 16.109 | 16.0945 | 16.0839 | 16.0734 | 16.0601 | 16.0469 | 16.0339 | 16.0212 | 16.0087 | 15.9486 | 15.8927 | 15.8399
| GRUDIE BRIDGE | AULTBEA | MINIMUM HEADROOM | NG 87458 88885 | YES | YES | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0224 | 2.0161 | 2.0085 | 2.0011 | 1.9938 | 1.9867 | 1.9727 | 1.9645 | 1.9627 | 1.9609 | 1.9592 | 1.9422 | 1.9205 | 0.89409 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 0.94761
|  | AULTBEA | CT |  |  |  | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0227 | 2.018 | 2.0127 | 2.0075 | 2.0024 | 1.9974 | 1.9925 | 1.9872 | 1.9819 | 1.9767 | 1.9715 | 1.9493 | 1.9322 | 1.9154 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743
|  | AULTBEA | LW |  |  |  | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0224 | 2.0161 | 2.0085 | 2.0011 | 1.9938 | 1.9867 | 1.9797 | 1.9722 | 1.9653 | 1.9644 | 1.9636 | 1.9422 | 1.9205 | 0.89409 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 0.94761
|  | AULTBEA | ST |  |  |  | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0244 | 2.0225 | 2.0195 | 2.0161 | 2.0013 | 1.9869 | 1.9727 | 1.9645 | 1.9627 | 1.9609 | 1.9592 | 1.9507 | 1.9422 | 1.9338 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743
|  | AULTBEA | FS |  |  |  | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0633 | 2.0255 | 2.0253 | 2.0245 | 2.0235 | 2.0182 | 2.013 | 2.0062 | 1.9996 | 1.9932 | 1.9868 | 1.9806 | 1.9637 | 1.9603 | 1.9572 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743 | 2.0743
| BOAT OF GARTEN | AVIEMORE | MINIMUM HEADROOM | NH 89856 11394 | NO | YES | 20.9624 | 20.9479 | 20.9334 | 20.9182 | 20.9024 | 20.8752 | 20.8571 | 20.8377 | 20.8199 | 20.8013 | 20.7911 | 20.742 | 20.6919 | 20.643 | 19.7932 | 19.784 | 19.7747 | 19.7651 | 19.755 | 19.7376 | 19.7261 | 19.7137 | 19.7024 | 19.6905 | 19.684 | 19.6527 | 19.6207 | 19.5896 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394
|  | AVIEMORE | CT |  |  |  | 20.9639 | 20.9522 | 20.9415 | 20.9298 | 20.917 | 20.8944 | 20.8787 | 20.8619 | 20.8454 | 20.828 | 20.8185 | 20.7769 | 20.7405 | 20.7054 | 19.7942 | 19.7868 | 19.7799 | 19.7725 | 19.7643 | 19.7499 | 19.7399 | 19.7292 | 19.7187 | 19.7075 | 19.7015 | 19.675 | 19.6518 | 19.6294 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394
|  | AVIEMORE | LW |  |  |  | 20.9624 | 20.9479 | 20.9334 | 20.9182 | 20.9024 | 20.8752 | 20.8571 | 20.8377 | 20.8199 | 20.8013 | 20.7911 | 20.742 | 20.6919 | 20.643 | 19.7932 | 19.784 | 19.7747 | 19.7651 | 19.755 | 19.7376 | 19.7261 | 19.7137 | 19.7024 | 19.6905 | 19.684 | 19.6527 | 19.6207 | 19.5896 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394
|  | AVIEMORE | ST |  |  |  | 20.9691 | 20.9627 | 20.9563 | 20.9486 | 20.94 | 20.9249 | 20.9144 | 20.903 | 20.8916 | 20.8794 | 20.873 | 20.8455 | 20.8228 | 20.8009 | 19.7975 | 19.7935 | 19.7894 | 19.7844 | 19.7789 | 19.7693 | 19.7626 | 19.7554 | 19.7481 | 19.7403 | 19.7363 | 19.7187 | 19.7042 | 19.6903 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394
|  | AVIEMORE | FS |  |  |  | 20.9733 | 20.9707 | 20.968 | 20.965 | 20.9615 | 20.9555 | 20.9512 | 20.9466 | 20.9422 | 20.9375 | 20.9348 | 20.9233 | 20.9147 | 20.9066 | 19.8002 | 19.7985 | 19.7968 | 19.7949 | 19.7927 | 19.7888 | 19.7861 | 19.7832 | 19.7803 | 19.7774 | 19.7756 | 19.7683 | 19.7628 | 19.7577 | 19.7433 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394 | 19.7394
| ALNESS | BALALDIE | MINIMUM HEADROOM | NH 87017 79720 | YES | YES | 3.3933 | 3.3933 | 3.3933 | 3.3933 | 3.3933 | 3.3933 | 3.3933 | 3.3933 | 3.3933 | 3.3933 | 3.3933 | 3.3076 | 3.3076 | 0.83187 | 2.2929 | 2.258 | 2.218 | 2.1783 | 2.1396 | 2.1095 | 2.1095 | 2.1095 | 2.1095 | 0.96946 | 0.89141 | 0.59739 | 0.36313 | 0.13276 | 2.6063 | 2.5848 | 2.5774 | 2.5717 | 2.5717 | 2.5717 | 2.5717 | 2.5717 | 2.5717 | 2.5717 | 2.5717 | 2.4847 | 0.77868 | 0.55665
|  | BALALDIE | CT |  |  |  | 3.3933 | 3.3933 | 3.3933 | 3.3933 | 3.3933 | 3.3933 | 3.3933 | 3.3933 | 3.3933 | 3.3933 | 3.3933 | 3.3076 | 3.3076 | 0.83187 | 2.2929 | 2.258 | 2.218 | 2.1783 | 2.1396 | 2.1095 | 2.1095 | 2.1095 | 2.1095 | 0.96946 | 0.89141 | 0.59739 | 0.36313 | 0.13276 | 2.6063 | 2.5848 | 2.5774 | 2.5717 | 2.5717 | 2.5717 | 2.5717 | 2.5717 | 2.5717 | 2.5717 | 2.5717 | 2.4847 | 0.77868 | 0.55665
|  | BALALDIE | LW |  |  |  | 3.3933 | 3.3933 | 3.3933 | 3.3933 | 3.3933 | 3.3933 | 3.3933 | 3.3933 | 3.3933 | 3.3933 | 3.3933 | 3.3076 | 3.3076 | 0.91499 | 2.3013 | 2.2765 | 2.2462 | 2.2161 | 2.1868 | 2.1592 | 2.1321 | 2.1095 | 2.1095 | 2.1095 | 2.1095 | 0.77508 | 0.49968 | 0.23033 | 2.6121 | 2.5949 | 2.5826 | 2.5771 | 2.5717 | 2.5717 | 2.5717 | 2.5717 | 2.5717 | 2.5717 | 2.5717 | 2.4847 | 0.91027 | 0.65069
|  | BALALDIE | ST |  |  |  | 3.3933 | 3.3933 | 3.3933 | 3.3933 | 3.3933 | 3.3933 | 3.3933 | 3.3933 | 3.3933 | 3.3933 | 3.3933 | 3.3505 | 3.3505 | 3.3505 | 2.3109 | 2.3054 | 2.2972 | 2.2874 | 2.2751 | 2.2636 | 2.2522 | 2.2398 | 2.2277 | 2.2159 | 2.2045 | 2.1145 | 2.0851 | 2.0851 | 2.6187 | 2.6149 | 2.6092 | 2.6024 | 2.5939 | 2.5859 | 2.5837 | 2.5814 | 2.5792 | 2.577 | 2.575 | 2.5282 | 2.5282 | 2.5282
|  | BALALDIE | FS |  |  |  | 3.3933 | 3.3933 | 3.3933 | 3.3933 | 3.3933 | 3.3933 | 3.3933 | 3.3933 | 3.3933 | 3.3933 | 3.3933 | 3.3933 | 3.3933 | 3.3933 | 2.3138 | 2.3128 | 2.3094 | 2.3054 | 2.3012 | 2.2973 | 2.2923 | 2.2875 | 2.2827 | 2.278 | 2.2735 | 2.252 | 2.2312 | 2.211 | 2.6207 | 2.62 | 2.6177 | 2.6149 | 2.612 | 2.6093 | 2.6059 | 2.6025 | 2.5992 | 2.5959 | 2.5928 | 2.5837 | 2.5799 | 2.5761
| ABERNETHY | BALBEGGIE | MINIMUM HEADROOM | NO 17499 29606 | YES | YES | 10.9655 | 10.8804 | 10.7927 | 10.708 | 10.6266 | 10.5482 | 10.473 | 10.4252 | 10.4014 | 10.3779 | 10.3547 | 10.2351 | 9.6726 | 9.524 | 9.9784 | 9.9242 | 9.8663 | 9.8065 | 9.7486 | 9.6888 | 9.6351 | 9.5943 | 9.5754 | 9.5619 | 9.5486 | 9.4799 | 6.8987 | 6.4187 | 9.5599 | 9.4784 | 9.3934 | 9.3098 | 9.2293 | 9.1501 | 9.0756 | 9.0254 | 8.9964 | 7.4987 | 7.4363 | 7.0537 | 6.216 | 5.8242
|  | BALBEGGIE | CT |  |  |  | 10.9655 | 10.8804 | 10.7927 | 10.708 | 10.6266 | 10.5482 | 10.473 | 10.4252 | 10.4014 | 10.3779 | 10.3547 | 10.2351 | 9.6726 | 9.524 | 9.9784 | 9.9242 | 9.8663 | 9.8065 | 9.7486 | 9.6888 | 9.6351 | 9.5943 | 9.5754 | 9.5619 | 9.5486 | 9.4799 | 6.8987 | 6.5484 | 9.5599 | 9.4784 | 9.3934 | 9.3098 | 9.2293 | 9.1501 | 9.0756 | 9.0254 | 8.9964 | 7.4987 | 7.4363 | 7.0537 | 6.216 | 5.8325
|  | BALBEGGIE | LW |  |  |  | 11.1161 | 11.1034 | 11.089 | 11.0732 | 11.056 | 11.0377 | 11.0184 | 10.9937 | 10.9683 | 10.9423 | 10.916 | 10.7767 | 10.1774 | 9.9621 | 10.0524 | 10.0303 | 10.0033 | 9.9717 | 9.951 | 9.9405 | 9.9294 | 9.9152 | 9.9006 | 9.8857 | 9.8706 | 9.7907 | 6.9394 | 6.4187 | 9.6951 | 9.6771 | 9.6559 | 9.6318 | 9.6067 | 9.5787 | 9.5525 | 9.5213 | 9.4895 | 9.4568 | 9.4266 | 7.3821 | 6.3921 | 5.8242
|  | BALBEGGIE | ST |  |  |  | 11.138 | 11.1329 | 11.1279 | 11.1231 | 11.1173 | 11.1116 | 11.1061 | 11.1003 | 11.0919 | 11.0837 | 11.0758 | 11.031 | 10.7746 | 10.7214 | 10.0687 | 10.06 | 10.0485 | 10.0335 | 10.0149 | 9.9942 | 9.9797 | 9.9764 | 9.9716 | 9.9669 | 9.9623 | 9.9367 | 9.7895 | 9.759 | 9.717 | 9.7099 | 9.7017 | 9.6921 | 9.6803 | 9.6678 | 9.6566 | 9.6448 | 9.6302 | 9.6156 | 9.6033 | 9.5397 | 9.2878 | 7.4388
|  | BALBEGGIE | FS |  |  |  | 11.1329 | 11.1278 | 11.1203 | 11.1129 | 11.1055 | 11.0983 | 11.0912 | 11.0842 | 11.0773 | 11.0704 | 11.0637 | 11.0234 | 10.9797 | 10.9371 | 10.0694 | 10.0652 | 10.0581 | 10.0498 | 10.0403 | 10.0298 | 10.0199 | 10.0101 | 10.0002 | 9.9903 | 9.982 | 9.9394 | 9.9072 | 9.8828 | 9.7138 | 9.7085 | 9.7004 | 9.6918 | 9.6827 | 9.6734 | 9.6643 | 9.6554 | 9.6465 | 9.6376 | 9.6295 | 9.5838 | 9.5368 | 9.4914
| MILTON OF CRAIGIE | BALDOVIE | MINIMUM HEADROOM | NO 45279 32147 | NO | YES | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 22.3684 | 26.5049 | 26.4151 | 26.307 | 26.205 | 26.1038 | 26.0031 | 25.9042 | 25.8765 | 25.8765 | 21.8601 | 21.5386 | 20.5632 | 19.6213 | 18.7146 | 28.2039 | 28.1665 | 28.1216 | 28.0792 | 28.0371 | 27.9952 | 27.9541 | 27.9091 | 21.9065 | 21.6081 | 21.3124 | 20.4154 | 19.5491 | 18.7152
|  | BALDOVIE | CT |  |  |  | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 26.5093 | 26.4388 | 26.3598 | 26.2855 | 26.2116 | 26.1388 | 26.067 | 25.9891 | 25.9093 | 25.8765 | 25.8765 | 21.6466 | 20.9506 | 20.283 | 28.2057 | 28.1764 | 28.1436 | 28.1126 | 28.0819 | 28.0516 | 28.0218 | 27.9894 | 27.9562 | 27.923 | 22.0797 | 21.4118 | 20.7716 | 20.1577
|  | BALDOVIE | LW |  |  |  | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 22.3684 | 26.5049 | 26.4151 | 26.307 | 26.205 | 26.1038 | 26.0031 | 25.9042 | 25.8765 | 25.8765 | 21.8601 | 21.5386 | 20.5632 | 19.6213 | 18.7146 | 28.2039 | 28.1665 | 28.1216 | 28.0792 | 28.0371 | 27.9952 | 27.9541 | 27.9091 | 21.9065 | 21.6081 | 21.3124 | 20.4154 | 19.5491 | 18.7152
|  | BALDOVIE | ST |  |  |  | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 26.5369 | 26.5101 | 26.4709 | 26.4266 | 26.3985 | 26.3708 | 26.3434 | 26.3139 | 26.283 | 26.2521 | 26.2217 | 26.0734 | 25.9359 | 25.8765 | 28.2172 | 28.2061 | 28.1897 | 28.1713 | 28.1596 | 28.1481 | 28.1367 | 28.1244 | 28.1116 | 28.0988 | 28.0861 | 28.0244 | 27.9673 | 27.9121
|  | BALDOVIE | FS |  |  |  | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 29.3736 | 26.5527 | 26.5491 | 26.5369 | 26.524 | 26.5147 | 26.5056 | 26.4939 | 26.4821 | 26.4701 | 26.4582 | 26.4465 | 26.3898 | 26.3394 | 26.2935 | 28.2238 | 28.2223 | 28.2172 | 28.2118 | 28.208 | 28.2042 | 28.1993 | 28.1944 | 28.1894 | 28.1845 | 28.1796 | 28.156 | 28.1351 | 28.116
| TARLAND | BALLATER | MINIMUM HEADROOM | NO 37542 97131 | NO | YES | 10.9414 | 10.938 | 10.9342 | 10.9303 | 10.9265 | 10.9227 | 10.9189 | 10.9149 | 10.9109 | 10.9069 | 10.903 | 10.8783 | 10.8474 | 10.8165 | 14.286 | 14.2603 | 14.2305 | 14.2027 | 14.1758 | 14.154 | 14.1401 | 14.1251 | 14.1104 | 14.0956 | 14.0808 | 13.9891 | 13.8742 | 11.6978 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 11.7481 | 11.3086
|  | BALLATER | CT |  |  |  | 10.9414 | 10.938 | 10.9342 | 10.9303 | 10.9265 | 10.9227 | 10.9189 | 10.9149 | 10.9109 | 10.9069 | 10.903 | 10.8783 | 10.8535 | 10.8291 | 14.286 | 14.2603 | 14.2305 | 14.2027 | 14.1758 | 14.154 | 14.1401 | 14.1251 | 14.1104 | 14.0956 | 14.0808 | 13.9891 | 13.8969 | 11.8731 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 11.8332 | 11.4895
|  | BALLATER | LW |  |  |  | 10.9421 | 10.9395 | 10.9363 | 10.9331 | 10.9299 | 10.9266 | 10.9235 | 10.9201 | 10.9168 | 10.9134 | 10.9101 | 10.8788 | 10.8474 | 10.8165 | 14.2913 | 14.2714 | 14.2467 | 14.222 | 14.1994 | 14.1768 | 14.157 | 14.1444 | 14.1321 | 14.1197 | 14.1073 | 13.991 | 13.8742 | 11.6978 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 11.7481 | 11.3086
|  | BALLATER | ST |  |  |  | 10.9429 | 10.9421 | 10.9408 | 10.9393 | 10.9365 | 10.9337 | 10.9309 | 10.9279 | 10.925 | 10.9221 | 10.9193 | 10.9054 | 10.8918 | 10.8785 | 14.2977 | 14.2915 | 14.2818 | 14.2702 | 14.2483 | 14.2266 | 14.2068 | 14.1858 | 14.1653 | 14.1519 | 14.1413 | 14.0898 | 14.0395 | 13.9898 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073
|  | BALLATER | FS |  |  |  | 10.9433 | 10.9433 | 10.9429 | 10.9425 | 10.9415 | 10.9406 | 10.9394 | 10.9382 | 10.937 | 10.9359 | 10.9347 | 10.9293 | 10.9242 | 10.9195 | 14.3011 | 14.3005 | 14.2977 | 14.2943 | 14.287 | 14.2797 | 14.2704 | 14.2613 | 14.2524 | 14.2436 | 14.2349 | 14.1957 | 14.1598 | 14.1421 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073 | 14.2073
| CARRADALE | BALLIEKINE | MINIMUM HEADROOM | NR 87179 38819 | YES | YES | 1.1704 | 1.1704 | 1.1704 | 1.1704 | 1.1704 | 1.1704 | 1.1704 | 1.1704 | 1.1704 | 1.1704 | 1.1704 | 0.9913 | 0.95241 | 0.91416 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 0.99338 | 0.94825 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 0.96477
|  | BALLIEKINE | CT |  |  |  | 1.1704 | 1.1704 | 1.1704 | 1.1704 | 1.1704 | 1.1704 | 1.1704 | 1.1704 | 1.1704 | 1.1704 | 1.1704 | 1.1704 | 0.97066 | 0.94053 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 0.97936 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 0.9912
|  | BALLIEKINE | LW |  |  |  | 1.1704 | 1.1704 | 1.1704 | 1.1704 | 1.1704 | 1.1704 | 1.1704 | 1.1704 | 1.1704 | 1.1704 | 1.1704 | 0.9913 | 0.95241 | 0.91416 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 0.99338 | 0.94825 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 0.96477
|  | BALLIEKINE | ST |  |  |  | 1.1704 | 1.1704 | 1.1704 | 1.1704 | 1.1704 | 1.1704 | 1.1704 | 1.1704 | 1.1704 | 1.1704 | 1.1704 | 1.1704 | 0.99001 | 0.97454 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379
|  | BALLIEKINE | FS |  |  |  | 1.1704 | 1.1704 | 1.1704 | 1.1704 | 1.1704 | 1.1704 | 1.1704 | 1.1704 | 1.1704 | 1.1704 | 1.1704 | 1.1704 | 1.1704 | 1.1704 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3115 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379 | 1.3379
| BOAT OF GARTEN | BALLINDALLOCH | MINIMUM HEADROOM | NJ 19279 34652 | NO | YES | 15.5342 | 15.459 | 15.3906 | 15.3247 | 15.2612 | 15.2002 | 15.1416 | 15.1096 | 15.0937 | 15.078 | 15.0625 | 14.9894 | 14.9144 | 14.8352 | 12.8199 | 12.7568 | 12.6984 | 12.6419 | 12.5875 | 12.5351 | 12.4847 | 12.4547 | 12.4435 | 12.4325 | 12.4216 | 12.3623 | 11.472 | 11.2572 | 14.3022 | 14.2339 | 14.1715 | 14.1114 | 14.0534 | 13.9977 | 13.9442 | 13.9145 | 13.8991 | 13.884 | 13.869 | 13.7915 | 13.7121 | 13.6291
|  | BALLINDALLOCH | CT |  |  |  | 15.5342 | 15.459 | 15.3906 | 15.3247 | 15.2612 | 15.2002 | 15.1416 | 15.1096 | 15.0937 | 15.078 | 15.0625 | 14.9894 | 14.9144 | 14.8352 | 12.8199 | 12.7568 | 12.6984 | 12.6419 | 12.5875 | 12.5351 | 12.4847 | 12.4547 | 12.4435 | 12.4325 | 12.4216 | 12.3623 | 11.472 | 11.2572 | 14.3022 | 14.2339 | 14.1715 | 14.1114 | 14.0534 | 13.9977 | 13.9442 | 13.9145 | 13.8991 | 13.884 | 13.869 | 13.7915 | 13.7121 | 13.6291
|  | BALLINDALLOCH | LW |  |  |  | 15.6673 | 15.656 | 15.6433 | 15.6293 | 15.6142 | 15.598 | 15.5809 | 15.5624 | 15.5434 | 15.524 | 15.5044 | 15.4003 | 15.2834 | 15.1642 | 12.9233 | 12.9086 | 12.8915 | 12.8734 | 12.8546 | 12.8351 | 12.8151 | 12.7934 | 12.7714 | 12.7491 | 12.7266 | 12.6096 | 12.5175 | 11.3218 | 14.4214 | 14.41 | 14.3971 | 14.383 | 14.368 | 14.352 | 14.3352 | 14.3172 | 14.2986 | 14.2797 | 14.2605 | 14.1507 | 14.0292 | 13.9058
|  | BALLINDALLOCH | ST |  |  |  | 15.6865 | 15.6821 | 15.6777 | 15.6734 | 15.6683 | 15.6632 | 15.6583 | 15.6539 | 15.6473 | 15.641 | 15.6348 | 15.6011 | 15.571 | 15.5389 | 12.9403 | 12.935 | 12.9288 | 12.9222 | 12.9117 | 12.9014 | 12.8913 | 12.8811 | 12.8694 | 12.8579 | 12.8467 | 12.7892 | 12.7348 | 12.697 | 14.4391 | 14.4347 | 14.4302 | 14.4256 | 14.4196 | 14.4137 | 14.408 | 14.4026 | 14.3953 | 14.3882 | 14.3813 | 14.3444 | 14.3109 | 14.2755
|  | BALLINDALLOCH | FS |  |  |  | 15.6821 | 15.6776 | 15.6709 | 15.6644 | 15.6579 | 15.6515 | 15.6452 | 15.639 | 15.6329 | 15.6269 | 15.6209 | 15.5853 | 15.5485 | 15.5129 | 12.9378 | 12.9341 | 12.9282 | 12.9221 | 12.9149 | 12.9077 | 12.9 | 12.8924 | 12.8849 | 12.8776 | 12.8703 | 12.8301 | 12.7897 | 12.751 | 14.4353 | 14.4312 | 14.4251 | 14.419 | 14.4128 | 14.4066 | 14.4003 | 14.3942 | 14.3881 | 14.3821 | 14.3763 | 14.3417 | 14.3062 | 14.2719
| CARRADALE | BALLURE | MINIMUM HEADROOM | NR 71425 49944 | YES | YES | 2.1259 | 2.0617 | 2.0011 | 1.9427 | 1.8865 | 1.217 | 1.1445 | 1.0895 | 1.052 | 1.0147 | 0.97779 | 0.6446 | 0.41536 | 0.27741 | 2.0763 | 1.9966 | 1.9174 | 1.8405 | 1.7662 | 1.197 | 1.1274 | 1.0767 | 1.04 | 1.0035 | 0.96745 | 0.68531 | 0.48648 | 0.36117 | 1.9763 | 1.8833 | 1.7914 | 1.7023 | 1.616 | 0.93498 | 0.8544 | 0.79672 | 0.75587 | 0.71534 | 0.67519 | 0.3434 | 0.11181 | -0.031512
|  | BALLURE | CT |  |  |  | 2.1259 | 2.0617 | 2.0011 | 1.9427 | 1.8865 | 1.217 | 1.1445 | 1.0895 | 1.052 | 1.0147 | 0.97779 | 0.6446 | 0.41536 | 0.27741 | 2.0763 | 1.9966 | 1.9174 | 1.8405 | 1.7662 | 1.197 | 1.1274 | 1.0767 | 1.04 | 1.0035 | 0.96745 | 0.68531 | 0.48648 | 0.36117 | 1.9763 | 1.8833 | 1.7914 | 1.7023 | 1.616 | 0.93498 | 0.8544 | 0.79672 | 0.75587 | 0.71534 | 0.67519 | 0.3434 | 0.11181 | -0.031512
|  | BALLURE | LW |  |  |  | 2.2396 | 2.23 | 2.2192 | 2.2072 | 2.1943 | 1.644 | 1.629 | 1.6111 | 1.5878 | 1.5641 | 1.5401 | 1.2022 | 0.93055 | 0.74344 | 2.1909 | 2.1755 | 2.1575 | 2.1387 | 2.1191 | 1.6016 | 1.5808 | 1.5575 | 1.5339 | 1.5099 | 1.4859 | 1.1769 | 0.94161 | 0.77536 | 2.1127 | 2.0951 | 2.0746 | 2.0531 | 2.0306 | 1.4097 | 1.3857 | 1.3589 | 1.3315 | 1.3039 | 1.276 | 0.91272 | 0.63807 | 0.44627
|  | BALLURE | ST |  |  |  | 2.2561 | 2.2523 | 2.2485 | 2.2449 | 2.2405 | 1.9684 | 1.9643 | 1.9603 | 1.9545 | 1.9489 | 1.9434 | 1.824 | 1.7527 | 1.7056 | 2.2083 | 2.2028 | 2.1963 | 2.1894 | 2.1802 | 1.9226 | 1.9139 | 1.9049 | 1.8944 | 1.8841 | 1.874 | 1.7388 | 1.6504 | 1.5978 | 2.1333 | 2.127 | 2.1196 | 2.1118 | 2.1014 | 1.7926 | 1.7828 | 1.7728 | 1.7608 | 1.7492 | 1.7378 | 1.5787 | 1.4759 | 1.4161
|  | BALLURE | FS |  |  |  | 2.2523 | 2.2484 | 2.2428 | 2.2372 | 2.2316 | 2.2262 | 2.2208 | 2.2155 | 2.2103 | 2.2051 | 2.2 | 2.1696 | 2.1377 | 2.1068 | 2.2058 | 2.2021 | 2.196 | 2.1898 | 2.1829 | 2.1762 | 2.1691 | 2.162 | 2.1551 | 2.1483 | 2.1415 | 2.1037 | 2.0652 | 2.0283 | 2.1302 | 2.1257 | 2.1185 | 2.1112 | 2.1032 | 2.0954 | 2.0871 | 2.0789 | 2.0709 | 2.063 | 2.0552 | 2.0111 | 1.9661 | 1.9229
| DYCE | BALMEDIE | MINIMUM HEADROOM | NJ 95546 18627 | YES | YES | 10.4442 | 10.4323 | 10.4178 | 10.4033 | 10.389 | 10.3749 | 10.361 | 10.3603 | 10.3603 | 10.3603 | 10.3603 | 10.3603 | 10.3603 | 6.9923 | 9.6191 | 9.5475 | 9.4593 | 9.3719 | 9.3283 | 9.3004 | 9.273 | 9.2433 | 7.2931 | 7.1104 | 6.9291 | 6.3138 | 5.6947 | 5.0888 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 7.0345 | 6.4606 | 5.8988
|  | BALMEDIE | CT |  |  |  | 10.446 | 10.4389 | 10.4307 | 10.4226 | 10.4146 | 10.4065 | 10.3986 | 10.3901 | 10.3817 | 10.3733 | 10.3649 | 10.3603 | 10.3603 | 10.3603 | 9.6301 | 9.5873 | 9.5379 | 9.4887 | 9.4399 | 9.3912 | 9.3472 | 9.3303 | 9.3138 | 9.2972 | 9.2807 | 7.2966 | 6.883 | 6.4787 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 7.1874
|  | BALMEDIE | LW |  |  |  | 10.4442 | 10.4323 | 10.4178 | 10.4033 | 10.389 | 10.3749 | 10.361 | 10.3603 | 10.3603 | 10.3603 | 10.3603 | 10.3603 | 10.3603 | 6.9923 | 9.6191 | 9.5475 | 9.4593 | 9.3719 | 9.3283 | 9.3004 | 9.273 | 9.2433 | 7.2931 | 7.1104 | 6.9291 | 6.3138 | 5.6947 | 5.0888 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 7.0345 | 6.4606 | 5.8988
|  | BALMEDIE | ST |  |  |  | 10.4479 | 10.4443 | 10.4386 | 10.4317 | 10.427 | 10.4223 | 10.4177 | 10.4127 | 10.4079 | 10.4031 | 10.3983 | 10.375 | 10.3603 | 10.3603 | 9.6419 | 9.6197 | 9.5852 | 9.5437 | 9.5151 | 9.4867 | 9.4588 | 9.4287 | 9.3995 | 9.3702 | 9.3465 | 9.3007 | 9.2557 | 7.2769 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 10.0523
|  | BALMEDIE | FS |  |  |  | 10.45 | 10.4497 | 10.448 | 10.446 | 10.4445 | 10.4429 | 10.441 | 10.4391 | 10.4372 | 10.4354 | 10.4335 | 10.4247 | 10.4164 | 10.4086 | 9.6543 | 9.6524 | 9.6424 | 9.6305 | 9.6211 | 9.6118 | 9.6 | 9.5883 | 9.5771 | 9.5658 | 9.5547 | 9.5015 | 9.4512 | 9.4038 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 10.0523 | 10.0523
| CLAYHILLS | BALNAGASK | MINIMUM HEADROOM | NJ 96055 05234 | YES | NO | 14.1111 | 14.008 | 13.9102 | 13.8152 | 13.7236 | 13.636 | 13.5519 | 13.5015 | 13.4742 | 13.4471 | 13.4204 | 11.4978 | 11.394 | 11.2833 | 14.1928 | 14.1206 | 14.0519 | 13.9848 | 13.9198 | 13.8581 | 13.7987 | 13.7618 | 13.7404 | 13.7192 | 13.6982 | 13.5611 | 13.4172 | 13.2711 | 13.3763 | 13.2773 | 13.1834 | 13.092 | 13.0038 | 12.9196 | 12.8387 | 12.7897 | 12.7626 | 12.7359 | 12.7093 | 11.4533 | 11.3583 | 11.2571
|  | BALNAGASK | CT |  |  |  | 14.1111 | 14.008 | 13.9102 | 13.8152 | 13.7236 | 13.636 | 13.5519 | 13.5015 | 13.4742 | 13.4471 | 13.4204 | 11.4978 | 11.394 | 11.2833 | 14.1928 | 14.1206 | 14.0519 | 13.9848 | 13.9198 | 13.8581 | 13.7987 | 13.7618 | 13.7404 | 13.7192 | 13.6982 | 13.5611 | 13.4172 | 13.2711 | 13.3763 | 13.2773 | 13.1834 | 13.092 | 13.0038 | 12.9196 | 12.8387 | 12.7897 | 12.7626 | 12.7359 | 12.7093 | 11.4533 | 11.3583 | 11.2571
|  | BALNAGASK | LW |  |  |  | 14.2849 | 14.2645 | 14.2414 | 14.2168 | 14.1908 | 14.1636 | 14.1353 | 14.1034 | 14.0709 | 14.0379 | 14.003 | 13.7939 | 13.5584 | 13.3084 | 14.309 | 14.2914 | 14.2716 | 14.2509 | 14.2293 | 14.2069 | 14.184 | 14.1583 | 14.1323 | 14.1059 | 14.0772 | 13.8926 | 13.6886 | 13.4756 | 13.541 | 13.5201 | 13.4966 | 13.4717 | 13.4455 | 13.4181 | 13.3897 | 13.3579 | 13.3255 | 13.2926 | 13.2575 | 13.0425 | 12.8145 | 12.5908
|  | BALNAGASK | ST |  |  |  | 14.3153 | 14.3075 | 14.2993 | 14.2903 | 14.2759 | 14.2623 | 14.249 | 14.2355 | 14.2193 | 14.2034 | 14.1879 | 14.1007 | 14.0175 | 13.9311 | 14.3328 | 14.3262 | 14.319 | 14.3108 | 14.2959 | 14.282 | 14.2685 | 14.2544 | 14.2386 | 14.2231 | 14.2078 | 14.1217 | 14.0386 | 13.9544 | 13.5711 | 13.5632 | 13.5547 | 13.5454 | 13.5298 | 13.5151 | 13.5007 | 13.486 | 13.4688 | 13.4519 | 13.4354 | 13.3422 | 13.2533 | 13.1832
|  | BALNAGASK | FS |  |  |  | 14.313 | 14.3066 | 14.2968 | 14.2872 | 14.2766 | 14.2661 | 14.2552 | 14.2444 | 14.2339 | 14.2235 | 14.2134 | 14.155 | 14.0938 | 14.0339 | 14.3337 | 14.329 | 14.3216 | 14.3146 | 14.306 | 14.2976 | 14.2884 | 14.2794 | 14.2707 | 14.2621 | 14.2537 | 14.2067 | 14.1574 | 14.1087 | 13.5699 | 13.5636 | 13.554 | 13.5447 | 13.5341 | 13.5236 | 13.5125 | 13.5016 | 13.491 | 13.4806 | 13.4704 | 13.412 | 13.3509 | 13.2908
| KINTORE | BANCHORY | MINIMUM HEADROOM | NO 69262 96297 | NO | YES | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 19.2555 | 19.0924 | 18.8907 | 18.7047 | 18.5667 | 18.4291 | 18.3848 | 18.3813 | 18.3813 | 18.3813 | 18.3813 | 18.3813 | 12.8442 | 11.6536 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 12.0258 | 10.7876 | 9.5762
|  | BANCHORY | CT |  |  |  | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 19.2797 | 19.1806 | 19.0654 | 18.9499 | 18.8343 | 18.7245 | 18.6457 | 18.5606 | 18.4777 | 18.3951 | 18.3865 | 18.3813 | 18.3813 | 18.3813 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 12.7913 | 11.9734
|  | BANCHORY | LW |  |  |  | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 19.2555 | 19.0924 | 18.8907 | 18.7047 | 18.5667 | 18.4291 | 18.3848 | 18.3813 | 18.3813 | 18.3813 | 18.3813 | 18.3813 | 12.8442 | 11.6536 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 12.0258 | 10.7876 | 9.5762
|  | BANCHORY | ST |  |  |  | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 19.3085 | 19.26 | 19.1841 | 19.0924 | 19.0087 | 18.925 | 18.8429 | 18.7543 | 18.6901 | 18.6304 | 18.5717 | 18.3839 | 18.3813 | 18.3813 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603
|  | BANCHORY | FS |  |  |  | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 23.7317 | 19.3355 | 19.3309 | 19.3082 | 19.2811 | 19.2535 | 19.2259 | 19.1912 | 19.1569 | 19.1237 | 19.0903 | 19.0575 | 18.8994 | 18.7498 | 18.6488 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603 | 17.6603
| TAYNUILT | BARCALDINE | MINIMUM HEADROOM | NM 96356 42181 | YES | YES | 0.61425 | 0.61425 | 0.61425 | 0.61425 | 0.61425 | 0.61425 | 0.61425 | 0.61425 | 0.61425 | 0.61425 | 0.61226 | 0.59936 | 0.51147 | 0.33085 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315
|  | BARCALDINE | CT |  |  |  | 0.61425 | 0.61425 | 0.61425 | 0.61425 | 0.61425 | 0.61425 | 0.61425 | 0.61425 | 0.61425 | 0.61425 | 0.61226 | 0.60021 | 0.55672 | 0.41066 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315
|  | BARCALDINE | LW |  |  |  | 0.61425 | 0.61425 | 0.61425 | 0.61425 | 0.61425 | 0.61425 | 0.61425 | 0.61425 | 0.61425 | 0.61425 | 0.61425 | 0.59936 | 0.51147 | 0.33085 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315
|  | BARCALDINE | ST |  |  |  | 0.61425 | 0.61425 | 0.61425 | 0.61425 | 0.61425 | 0.61425 | 0.61425 | 0.61425 | 0.61425 | 0.61425 | 0.61425 | 0.61425 | 0.61425 | 0.60989 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315
|  | BARCALDINE | FS |  |  |  | 0.61425 | 0.61425 | 0.61425 | 0.61425 | 0.61425 | 0.61425 | 0.61425 | 0.61425 | 0.61425 | 0.61425 | 0.61425 | 0.61425 | 0.61425 | 0.61425 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 3.4437 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315 | 0.36315
| STORNOWAY | BARVAS | MINIMUM HEADROOM | NB 35613 48891 | NO | YES | 4.4185 | 4.4133 | 4.4073 | 4.4014 | 4.3956 | 4.3899 | 4.3843 | 4.3783 | 4.3723 | 4.3663 | 4.3604 | 4.3541 | 4.3541 | 4.3541 | 4.0364 | 3.9905 | 3.9379 | 3.893 | 3.8628 | 3.8331 | 3.8238 | 3.8238 | 3.8238 | 3.8238 | 3.8238 | 3.8238 | 2.3054 | 1.9953 | 4.0498 | 4.0184 | 3.9824 | 3.9471 | 3.9354 | 3.9354 | 3.9354 | 3.9354 | 3.9354 | 3.9354 | 3.9354 | 3.9354 | 2.3008 | 1.9937
|  | BARVAS | CT |  |  |  | 4.4185 | 4.4133 | 4.4073 | 4.4014 | 4.3956 | 4.3899 | 4.3843 | 4.3783 | 4.3723 | 4.3663 | 4.3604 | 4.3541 | 4.3541 | 4.3541 | 4.0364 | 3.9905 | 3.9379 | 3.893 | 3.8628 | 3.8331 | 3.8238 | 3.8238 | 3.8238 | 3.8238 | 3.8238 | 3.8238 | 2.3054 | 1.9953 | 4.0498 | 4.0184 | 3.9824 | 3.9471 | 3.9354 | 3.9354 | 3.9354 | 3.9354 | 3.9354 | 3.9354 | 3.9354 | 3.9354 | 2.3008 | 1.9937
|  | BARVAS | LW |  |  |  | 4.4205 | 4.4183 | 4.4155 | 4.4128 | 4.4101 | 4.4075 | 4.405 | 4.4022 | 4.3994 | 4.3967 | 4.394 | 4.3644 | 4.3541 | 4.3541 | 4.0544 | 4.0345 | 4.0102 | 3.9864 | 3.963 | 3.9401 | 3.9176 | 3.8971 | 3.8827 | 3.8684 | 3.8542 | 3.8238 | 3.8238 | 2.2581 | 4.062 | 4.0485 | 4.0319 | 4.0155 | 3.9996 | 3.9839 | 3.9685 | 3.9518 | 3.9354 | 3.9354 | 3.9354 | 3.9354 | 3.9354 | 2.254
|  | BARVAS | ST |  |  |  | 4.4216 | 4.4214 | 4.4212 | 4.4208 | 4.4185 | 4.4162 | 4.4139 | 4.4115 | 4.4091 | 4.4068 | 4.4045 | 4.3932 | 4.382 | 4.3709 | 4.0636 | 4.0621 | 4.0597 | 4.0569 | 4.0363 | 4.0161 | 3.9964 | 3.9751 | 3.9542 | 3.9337 | 3.9135 | 3.8503 | 3.8238 | 3.8238 | 4.0684 | 4.0673 | 4.0657 | 4.0638 | 4.0497 | 4.0359 | 4.0224 | 4.0078 | 3.9935 | 3.9795 | 3.9657 | 3.9354 | 3.9354 | 3.9354
|  | BARVAS | FS |  |  |  | 4.4217 | 4.4217 | 4.4216 | 4.4215 | 4.4206 | 4.4198 | 4.4187 | 4.4176 | 4.4165 | 4.4155 | 4.4145 | 4.4096 | 4.4051 | 4.4008 | 4.0645 | 4.0644 | 4.0636 | 4.0627 | 4.0551 | 4.0476 | 4.038 | 4.0285 | 4.0192 | 4.0101 | 4.0011 | 3.9584 | 3.9185 | 3.8899 | 4.069 | 4.0689 | 4.0684 | 4.0678 | 4.0626 | 4.0574 | 4.0508 | 4.0443 | 4.038 | 4.0317 | 4.0256 | 3.9964 | 3.9691 | 3.9435
| STORNOWAY | BATTERY POINT | MINIMUM HEADROOM | NB 43147 32182 | NO | YES | 21.3682 | 21.3682 | 21.3682 | 34.9482 | 34.9482 | 34.9482 | 34.9482 | 34.9482 | 34.9482 | 34.9482 | 34.9482 | 34.6913 | 34.6913 | 28.7927 | 17.8587 | 17.749 | 17.6406 | 30.4746 | 30.4558 | 30.4558 | 30.4558 | 30.4558 | 30.4558 | 30.4558 | 30.4558 | 26.265 | 25.1128 | 23.979 | 18.3008 | 18.2713 | 18.2713 | 31.1513 | 31.1513 | 31.1513 | 31.1513 | 31.1513 | 31.1513 | 31.1513 | 31.1513 | 26.81 | 25.6774 | 24.5432
|  | BATTERY POINT | CT |  |  |  | 21.3682 | 21.3682 | 21.3682 | 34.9482 | 34.9482 | 34.9482 | 34.9482 | 34.9482 | 34.9482 | 34.9482 | 34.9482 | 34.6913 | 34.6913 | 34.6913 | 17.8592 | 17.7633 | 17.6699 | 30.486 | 30.4676 | 30.4558 | 30.4558 | 30.4558 | 30.4558 | 30.4558 | 30.4558 | 26.997 | 26.1748 | 25.3658 | 18.301 | 18.2713 | 18.2713 | 31.1513 | 31.1513 | 31.1513 | 31.1513 | 31.1513 | 31.1513 | 31.1513 | 31.1513 | 27.5229 | 26.7221 | 25.9306
|  | BATTERY POINT | LW |  |  |  | 21.3682 | 21.3682 | 21.3682 | 34.9482 | 34.9482 | 34.9482 | 34.9482 | 34.9482 | 34.9482 | 34.9482 | 34.9482 | 34.6913 | 34.6913 | 28.7927 | 17.8587 | 17.749 | 17.6406 | 30.4746 | 30.4558 | 30.4558 | 30.4558 | 30.4558 | 30.4558 | 30.4558 | 30.4558 | 26.265 | 25.1128 | 23.979 | 18.3008 | 18.2713 | 18.2713 | 31.1513 | 31.1513 | 31.1513 | 31.1513 | 31.1513 | 31.1513 | 31.1513 | 31.1513 | 26.81 | 25.6774 | 24.5432
|  | BATTERY POINT | ST |  |  |  | 21.3682 | 21.3682 | 21.3682 | 34.9482 | 34.9482 | 34.9482 | 34.9482 | 34.9482 | 34.9482 | 34.9482 | 34.9482 | 34.8197 | 34.8197 | 34.8197 | 17.9015 | 17.8717 | 17.8275 | 30.655 | 30.6006 | 30.5589 | 30.5196 | 30.4883 | 30.4783 | 30.4687 | 30.4594 | 30.3815 | 30.3815 | 27.5724 | 18.3215 | 18.3071 | 18.2856 | 31.1513 | 31.1513 | 31.1513 | 31.1513 | 31.1513 | 31.1513 | 31.1513 | 31.1513 | 31.0234 | 31.0234 | 31.0234
|  | BATTERY POINT | FS |  |  |  | 21.3682 | 21.3682 | 21.3682 | 34.9482 | 34.9482 | 34.9482 | 34.9482 | 34.9482 | 34.9482 | 34.9482 | 34.9482 | 34.9482 | 34.9482 | 34.9482 | 17.919 | 17.9135 | 17.8968 | 30.7574 | 30.7387 | 30.7202 | 30.6977 | 30.6757 | 30.6541 | 30.6329 | 30.6124 | 30.537 | 30.4866 | 30.4715 | 18.33 | 18.3274 | 18.3193 | 31.1898 | 31.1808 | 31.1718 | 31.1609 | 31.1513 | 31.1513 | 31.1513 | 31.1513 | 31.1513 | 31.1513 | 31.1513
| MYBSTER | BETTYHILL | MINIMUM HEADROOM | NC 70763 61645 | YES | YES | 0.97814 | 0.87447 | 0.77609 | 0.68008 | 0.58764 | 0.49875 | 0.41343 | 0.37558 | 0.35676 | 0.33657 | 0.31333 | 0.15178 | 0.004463 | -0.14207 | 1.2978 | 0.97907 | 0.89009 | 0.80063 | 0.71323 | 0.62915 | 0.54837 | 0.51067 | 0.49037 | 0.47026 | 0.45045 | 0.28953 | 0.13953 | -0.00931 | 0.97059 | 0.87129 | 0.77572 | 0.66298 | 0.55437 | 0.44989 | 0.34954 | 0.30331 | 0.27889 | 0.25471 | 0.23088 | 0.054153 | -0.11261 | -0.27827
|  | BETTYHILL | CT |  |  |  | 0.97814 | 0.87447 | 0.77609 | 0.68008 | 0.58764 | 0.49875 | 0.41343 | 0.37558 | 0.35676 | 0.33657 | 0.31333 | 0.15178 | 0.004463 | -0.14207 | 1.2978 | 0.97907 | 0.89009 | 0.80063 | 0.71323 | 0.62915 | 0.54837 | 0.51067 | 0.49037 | 0.47026 | 0.45045 | 0.28953 | 0.13953 | -0.00931 | 0.97059 | 0.87129 | 0.77572 | 0.66298 | 0.55437 | 0.44989 | 0.34954 | 0.30331 | 0.27889 | 0.25471 | 0.23088 | 0.054153 | -0.11261 | -0.27827
|  | BETTYHILL | LW |  |  |  | 1.4305 | 1.4135 | 1.3944 | 1.3734 | 1.3506 | 1.3264 | 1.3008 | 1.2782 | 1.2548 | 0.97834 | 0.95617 | 0.81424 | 0.59945 | 0.37449 | 1.4496 | 1.4352 | 1.4189 | 1.4012 | 1.3821 | 1.3619 | 1.3407 | 1.3217 | 1.3022 | 1.2823 | 1.2621 | 0.78756 | 0.57374 | 0.36073 | 1.3775 | 1.361 | 1.3425 | 1.3221 | 1.3 | 1.2764 | 1.2514 | 1.2294 | 0.99176 | 0.97079 | 0.94942 | 0.7056 | 0.46917 | 0.23301
|  | BETTYHILL | ST |  |  |  | 1.459 | 1.4523 | 1.4457 | 1.4393 | 1.4308 | 1.4225 | 1.4145 | 1.4067 | 1.3958 | 1.3852 | 1.3749 | 1.3284 | 1.2929 | 0.96264 | 1.4721 | 1.4665 | 1.4608 | 1.4551 | 1.4453 | 1.4357 | 1.4263 | 1.4169 | 1.4051 | 1.3937 | 1.3825 | 1.3305 | 0.94814 | 0.87096 | 1.406 | 1.3992 | 1.3927 | 1.3865 | 1.3789 | 1.3716 | 1.3645 | 1.3577 | 1.3478 | 1.3381 | 1.3287 | 1.2866 | 0.92479 | 0.84252
|  | BETTYHILL | FS |  |  |  | 1.4525 | 1.4458 | 1.436 | 1.4263 | 1.4164 | 1.4068 | 1.3971 | 1.3876 | 1.3782 | 1.369 | 1.3599 | 1.3058 | 1.2589 | 0.96721 | 1.4672 | 1.4621 | 1.4543 | 1.4466 | 1.4379 | 1.4293 | 1.4205 | 1.4118 | 1.4032 | 1.3948 | 1.3865 | 1.3385 | 1.2966 | 0.98033 | 1.3994 | 1.3927 | 1.3828 | 1.3733 | 1.3638 | 1.3545 | 1.3453 | 1.3363 | 1.3273 | 1.3185 | 1.3099 | 1.2579 | 0.99015 | 0.92901
| GRUDIE BRIDGE | BIDEN CLAN RAONAILD | MINIMUM HEADROOM | NH 06927 58342 | YES | YES | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.099866 | 0.099592 | 0.10068 | 0.10065 | 0.10062 | 0.10062 | 0.10061 | 0.10061 | 0.10061 | 0.10061 | 0.10061 | 0.099954 | 0.099888 | 0.099565 | 0.099239 | 0.098918 | 0.10077 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.0997 | 0.099375 | 0.099053
|  | BIDEN CLAN RAONAILD | CT |  |  |  | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10068 | 0.10066 | 0.10064 | 0.10062 | 0.10062 | 0.10061 | 0.10061 | 0.10061 | 0.10061 | 0.10061 | 0.10061 | 0.099858 | 0.09963 | 0.099405 | 0.10077 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.099987 | 0.099765 | 0.099541
|  | BIDEN CLAN RAONAILD | LW |  |  |  | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.099866 | 0.099592 | 0.10068 | 0.10065 | 0.10062 | 0.10062 | 0.10061 | 0.10061 | 0.10061 | 0.10061 | 0.10061 | 0.099954 | 0.099888 | 0.099565 | 0.099239 | 0.098918 | 0.10077 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.0997 | 0.099375 | 0.099053
|  | BIDEN CLAN RAONAILD | ST |  |  |  | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10069 | 0.10068 | 0.10066 | 0.10065 | 0.10064 | 0.10063 | 0.10062 | 0.10062 | 0.10062 | 0.10061 | 0.10061 | 0.10061 | 0.099988 | 0.099847 | 0.10078 | 0.10077 | 0.10077 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.099977
|  | BIDEN CLAN RAONAILD | FS |  |  |  | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10115 | 0.10069 | 0.10069 | 0.10069 | 0.10068 | 0.10068 | 0.10067 | 0.10067 | 0.10066 | 0.10065 | 0.10065 | 0.10064 | 0.10062 | 0.10062 | 0.10061 | 0.10078 | 0.10078 | 0.10078 | 0.10077 | 0.10077 | 0.10077 | 0.10077 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076 | 0.10076
| ELGIN | BILBOHALL | MINIMUM HEADROOM | NJ 20782 61556 | YES | YES | 26.1131 | 26.0962 | 26.077 | 26.0518 | 26.026 | 26.0003 | 25.9739 | 25.9443 | 25.9123 | 25.877 | 25.854 | 25.7542 | 25.7125 | 25.6851 | 23.4407 | 23.4275 | 23.4125 | 23.3928 | 23.3727 | 23.3526 | 23.332 | 23.3089 | 23.2839 | 23.2563 | 23.2383 | 23.1238 | 23.0135 | 22.0148 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 22.0716 | 21.9346
|  | BILBOHALL | CT |  |  |  | 26.1131 | 26.0962 | 26.077 | 26.0518 | 26.026 | 26.0003 | 25.9739 | 25.9443 | 25.9123 | 25.877 | 25.854 | 25.7542 | 25.7125 | 25.6851 | 23.4407 | 23.4275 | 23.4125 | 23.3928 | 23.3727 | 23.3526 | 23.332 | 23.3089 | 23.2839 | 23.2563 | 23.2383 | 23.1238 | 23.0135 | 22.0148 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 22.0716 | 21.9346
|  | BILBOHALL | LW |  |  |  | 26.1209 | 26.1162 | 26.1105 | 26.0978 | 26.084 | 26.069 | 26.053 | 26.0356 | 26.0172 | 25.9957 | 25.9884 | 25.8172 | 25.7334 | 25.6937 | 23.4468 | 23.4431 | 23.4386 | 23.4287 | 23.418 | 23.4063 | 23.3938 | 23.3801 | 23.3658 | 23.349 | 23.3433 | 23.2096 | 23.0733 | 22.0684 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 21.9865
|  | BILBOHALL | ST |  |  |  | 26.1225 | 26.121 | 26.1187 | 26.1119 | 26.0919 | 26.0722 | 26.052 | 26.0294 | 26.0051 | 25.9783 | 25.9605 | 25.8791 | 25.8037 | 25.7616 | 23.448 | 23.4468 | 23.4451 | 23.4397 | 23.4242 | 23.4087 | 23.393 | 23.3754 | 23.3563 | 23.3354 | 23.3215 | 23.258 | 23.1991 | 23.1417 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637
|  | BILBOHALL | FS |  |  |  | 26.1233 | 26.1231 | 26.1224 | 26.1198 | 26.1127 | 26.1055 | 26.0967 | 26.0875 | 26.0781 | 26.068 | 26.061 | 26.0285 | 26.0016 | 25.9762 | 23.4487 | 23.4485 | 23.448 | 23.4459 | 23.4404 | 23.4348 | 23.4279 | 23.4207 | 23.4133 | 23.4054 | 23.4 | 23.3746 | 23.3536 | 23.3338 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637 | 23.637
| RANNOCH | BLACKMOUNT | MINIMUM HEADROOM | NN 30077 41404 | YES | YES | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.049599 | 0.075531 | 0.074601 | 0.074377 | 0.07419 | 0.074008 | 0.07391 | 0.07391 | 0.07391 | 0.07391 | 0.07391 | 0.07391 | 0.040556 | 0.030478 | 0.020501 | 0.079161 | 0.079161 | 0.079161 | 0.079161 | 0.079161 | 0.079161 | 0.079161 | 0.079161 | 0.079161 | 0.079161 | 0.079161 | 0.043958 | 0.033877 | 0.023897
|  | BLACKMOUNT | CT |  |  |  | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.075593 | 0.074807 | 0.074482 | 0.074351 | 0.074224 | 0.074099 | 0.073977 | 0.07391 | 0.07391 | 0.07391 | 0.07391 | 0.04965 | 0.042595 | 0.035612 | 0.079161 | 0.079161 | 0.079161 | 0.079161 | 0.079161 | 0.079161 | 0.079161 | 0.079161 | 0.079161 | 0.079161 | 0.079161 | 0.079161 | 0.045998 | 0.039012
|  | BLACKMOUNT | LW |  |  |  | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.049599 | 0.075531 | 0.074601 | 0.074377 | 0.07419 | 0.074008 | 0.07391 | 0.07391 | 0.07391 | 0.07391 | 0.07391 | 0.07391 | 0.040556 | 0.030478 | 0.020501 | 0.079161 | 0.079161 | 0.079161 | 0.079161 | 0.079161 | 0.079161 | 0.079161 | 0.079161 | 0.079161 | 0.079161 | 0.079161 | 0.043958 | 0.033877 | 0.023897
|  | BLACKMOUNT | ST |  |  |  | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.07587 | 0.075551 | 0.075055 | 0.074598 | 0.074481 | 0.074398 | 0.074317 | 0.07423 | 0.074145 | 0.074061 | 0.073978 | 0.07391 | 0.07391 | 0.049325 | 0.079161 | 0.079161 | 0.079161 | 0.079161 | 0.079161 | 0.079161 | 0.079161 | 0.079161 | 0.079161 | 0.079161 | 0.079161 | 0.079161 | 0.079161 | 0.079161
|  | BLACKMOUNT | FS |  |  |  | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.1008 | 0.076051 | 0.076029 | 0.07589 | 0.075725 | 0.075533 | 0.075343 | 0.075098 | 0.074858 | 0.074664 | 0.074579 | 0.074522 | 0.074362 | 0.074215 | 0.07408 | 0.079161 | 0.079161 | 0.079161 | 0.079161 | 0.079161 | 0.079161 | 0.079161 | 0.079161 | 0.079161 | 0.079161 | 0.079161 | 0.079161 | 0.079161 | 0.079161
| BEAULY | BLACKSTAND | MINIMUM HEADROOM | NH 71036 59151 | YES | YES | 7.4269 | 7.3087 | 7.1959 | 5.9691 | 5.7845 | 5.605 | 5.4247 | 5.303 | 5.2069 | 5.1113 | 5.0168 | 4.6717 | 4.3315 | 3.9933 | 7.1383 | 7.015 | 6.8934 | 5.8507 | 5.6994 | 5.5517 | 5.4013 | 5.29 | 5.1959 | 5.1023 | 5.0098 | 4.6746 | 4.3141 | 3.815 | 7.2434 | 7.1251 | 7.0123 | 6.9035 | 5.969 | 5.7781 | 5.5854 | 5.4514 | 5.3429 | 5.2351 | 5.1284 | 4.7441 | 4.3635 | 3.9856
|  | BLACKSTAND | CT |  |  |  | 7.4269 | 7.3087 | 7.1959 | 5.9691 | 5.7845 | 5.605 | 5.4247 | 5.303 | 5.2069 | 5.1113 | 5.0168 | 4.6717 | 4.3315 | 3.9933 | 7.1383 | 7.015 | 6.8934 | 5.8507 | 5.6994 | 5.5517 | 5.4013 | 5.29 | 5.1959 | 5.1023 | 5.0098 | 4.6746 | 4.3141 | 3.9568 | 7.2434 | 7.1251 | 7.0123 | 6.9035 | 5.969 | 5.7781 | 5.5854 | 5.4514 | 5.3429 | 5.2351 | 5.1284 | 4.7441 | 4.3635 | 3.9856
|  | BLACKSTAND | LW |  |  |  | 7.636 | 7.6183 | 7.5983 | 7.5763 | 7.5525 | 7.5271 | 7.5002 | 5.9362 | 5.8087 | 5.6815 | 5.5548 | 5.086 | 4.6117 | 4.1364 | 7.3035 | 7.2518 | 7.1917 | 7.1307 | 7.0865 | 5.8854 | 5.7576 | 5.6307 | 5.5041 | 5.3779 | 5.2525 | 4.8084 | 4.3143 | 3.815 | 7.4531 | 7.435 | 7.415 | 7.393 | 7.3692 | 7.3437 | 7.3168 | 7.2921 | 5.9056 | 5.7613 | 5.6178 | 5.0949 | 4.5629 | 4.0248
|  | BLACKSTAND | ST |  |  |  | 7.6663 | 7.6593 | 7.6524 | 7.6457 | 7.6376 | 7.6297 | 7.622 | 7.6146 | 7.6038 | 7.5933 | 7.5831 | 7.5361 | 7.4943 | 5.9 | 7.3403 | 7.3245 | 7.3047 | 7.2821 | 7.2631 | 7.2444 | 7.2241 | 7.205 | 7.1834 | 7.1622 | 7.1416 | 5.9613 | 5.7794 | 5.6009 | 7.4841 | 7.4769 | 7.4699 | 7.463 | 7.4547 | 7.4467 | 7.4388 | 7.4313 | 7.4205 | 7.41 | 7.3998 | 7.3527 | 7.3109 | 7.272
|  | BLACKSTAND | FS |  |  |  | 7.6593 | 7.6522 | 7.6418 | 7.6315 | 7.6213 | 7.6112 | 7.6014 | 7.5916 | 7.582 | 7.5725 | 7.5632 | 7.5072 | 7.4577 | 7.4119 | 7.3399 | 7.333 | 7.3206 | 7.3075 | 7.2952 | 7.2831 | 7.2692 | 7.2562 | 7.2434 | 7.2308 | 7.2184 | 7.1503 | 7.0885 | 7.0303 | 7.4769 | 7.4697 | 7.459 | 7.4485 | 7.4381 | 7.4279 | 7.418 | 7.4083 | 7.3987 | 7.3892 | 7.3798 | 7.3238 | 7.2743 | 7.2284
| COUPAR ANGUS | BLAIRGOWRIE | MINIMUM HEADROOM | NO 18741 44551 | NO | YES | 28.1421 | 28.1421 | 28.1421 | 28.1421 | 28.1421 | 28.1421 | 28.1421 | 28.1421 | 28.1421 | 28.1421 | 28.1421 | 27.8236 | 27.8236 | 22.0399 | 25.0101 | 24.8883 | 24.8735 | 24.8585 | 24.8417 | 24.8235 | 24.8045 | 24.784 | 24.7631 | 24.7425 | 24.7258 | 21.0939 | 20.1798 | 19.3438 | 25.2461 | 25.2392 | 25.2392 | 25.2392 | 25.2392 | 25.2392 | 25.2392 | 25.2392 | 25.2392 | 25.2392 | 25.2392 | 21.0122 | 20.1183 | 19.3007
|  | BLAIRGOWRIE | CT |  |  |  | 28.1421 | 28.1421 | 28.1421 | 28.1421 | 28.1421 | 28.1421 | 28.1421 | 28.1421 | 28.1421 | 28.1421 | 28.1421 | 27.8236 | 27.8236 | 27.8236 | 25.014 | 24.892 | 24.8783 | 24.8661 | 24.852 | 24.8368 | 24.8206 | 24.8029 | 24.7845 | 24.7658 | 24.7506 | 24.4794 | 20.9689 | 20.3199 | 25.2468 | 25.2392 | 25.2392 | 25.2392 | 25.2392 | 25.2392 | 25.2392 | 25.2392 | 25.2392 | 25.2392 | 25.2392 | 24.9241 | 20.8899 | 20.2553
|  | BLAIRGOWRIE | LW |  |  |  | 28.1421 | 28.1421 | 28.1421 | 28.1421 | 28.1421 | 28.1421 | 28.1421 | 28.1421 | 28.1421 | 28.1421 | 28.1421 | 27.8236 | 27.8236 | 22.0399 | 25.0101 | 24.8883 | 24.8735 | 24.8585 | 24.8417 | 24.8235 | 24.8045 | 24.784 | 24.7631 | 24.7425 | 24.7258 | 21.0939 | 20.1798 | 19.3438 | 25.2461 | 25.2392 | 25.2392 | 25.2392 | 25.2392 | 25.2392 | 25.2392 | 25.2392 | 25.2392 | 25.2392 | 25.2392 | 21.0122 | 20.1183 | 19.3007
|  | BLAIRGOWRIE | ST |  |  |  | 28.1421 | 28.1421 | 28.1421 | 28.1421 | 28.1421 | 28.1421 | 28.1421 | 28.1421 | 28.1421 | 28.1421 | 28.1421 | 27.9829 | 27.9829 | 27.9829 | 25.0641 | 25.0172 | 24.9568 | 24.89 | 24.8799 | 24.8691 | 24.8577 | 24.845 | 24.8318 | 24.8182 | 24.8072 | 24.6636 | 24.6283 | 24.5952 | 25.2545 | 25.2472 | 25.2392 | 25.2392 | 25.2392 | 25.2392 | 25.2392 | 25.2392 | 25.2392 | 25.2392 | 25.2392 | 25.0817 | 25.0817 | 25.0817
|  | BLAIRGOWRIE | FS |  |  |  | 28.1421 | 28.1421 | 28.1421 | 28.1421 | 28.1421 | 28.1421 | 28.1421 | 28.1421 | 28.1421 | 28.1421 | 28.1421 | 28.1421 | 28.1421 | 28.1421 | 25.1798 | 25.1645 | 25.1398 | 25.1127 | 25.0712 | 25.0265 | 24.9736 | 24.9181 | 24.8876 | 24.8825 | 24.8783 | 24.8575 | 24.8416 | 24.8294 | 25.2724 | 25.2701 | 25.2662 | 25.262 | 25.2556 | 25.2487 | 25.2405 | 25.2392 | 25.2392 | 25.2392 | 25.2392 | 25.2392 | 25.2392 | 25.2392
| STRATHLEVEN | BLAIRLINNANS | MINIMUM HEADROOM | NS 40709 85121 | YES | YES | 0.44711 | 0.44614 | 0.44494 | 0.44377 | 0.44263 | 0.44151 | 0.44041 | 0.43923 | 0.43806 | 0.43689 | 0.43573 | 0.42573 | 0.32942 | 0.31948 | 0.24272 | 0.24153 | 0.24009 | 0.23868 | 0.23729 | 0.23594 | 0.23462 | 0.23319 | 0.23177 | 0.23037 | 0.22897 | 0.21689 | 0.14183 | 0.12984 | 0.26831 | 0.26714 | 0.26569 | 0.26428 | 0.2629 | 0.26155 | 0.26024 | 0.25881 | 0.25739 | 0.25599 | 0.25459 | 0.24254 | 0.14521 | 0.13324
|  | BLAIRLINNANS | CT |  |  |  | 0.44717 | 0.44644 | 0.4456 | 0.44478 | 0.44398 | 0.4432 | 0.44243 | 0.4416 | 0.44078 | 0.43997 | 0.43915 | 0.43204 | 0.33864 | 0.33156 | 0.24279 | 0.2419 | 0.24089 | 0.2399 | 0.23893 | 0.23798 | 0.23706 | 0.23606 | 0.23507 | 0.23408 | 0.2331 | 0.22451 | 0.15297 | 0.14443 | 0.26838 | 0.2675 | 0.26649 | 0.2655 | 0.26454 | 0.26359 | 0.26267 | 0.26167 | 0.26068 | 0.2597 | 0.25872 | 0.25014 | 0.15633 | 0.1478
|  | BLAIRLINNANS | LW |  |  |  | 0.44711 | 0.44614 | 0.44494 | 0.44377 | 0.44263 | 0.44151 | 0.44041 | 0.43923 | 0.43806 | 0.43689 | 0.43573 | 0.42573 | 0.32942 | 0.31948 | 0.24272 | 0.24153 | 0.24009 | 0.23868 | 0.23729 | 0.23594 | 0.23462 | 0.23319 | 0.23177 | 0.23037 | 0.22897 | 0.21689 | 0.14183 | 0.12984 | 0.26831 | 0.26714 | 0.26569 | 0.26428 | 0.2629 | 0.26155 | 0.26024 | 0.25881 | 0.25739 | 0.25599 | 0.25459 | 0.24254 | 0.14521 | 0.13324
|  | BLAIRLINNANS | ST |  |  |  | 0.44743 | 0.44713 | 0.44668 | 0.44613 | 0.4452 | 0.44429 | 0.4434 | 0.44244 | 0.4415 | 0.44058 | 0.43967 | 0.43525 | 0.38778 | 0.38344 | 0.2431 | 0.24274 | 0.24219 | 0.24152 | 0.2404 | 0.2393 | 0.23823 | 0.23707 | 0.23594 | 0.23482 | 0.23372 | 0.22838 | 0.19169 | 0.18645 | 0.26869 | 0.26834 | 0.26779 | 0.26713 | 0.266 | 0.26491 | 0.26384 | 0.26268 | 0.26155 | 0.26043 | 0.25934 | 0.25401 | 0.20618 | 0.20095
|  | BLAIRLINNANS | FS |  |  |  | 1.3221 | 0.44758 | 0.44745 | 0.4473 | 0.44699 | 0.44669 | 0.4463 | 0.44591 | 0.44554 | 0.44517 | 0.44481 | 0.44308 | 0.44148 | 0.43999 | 1.29 | 0.24328 | 0.24312 | 0.24294 | 0.24257 | 0.2422 | 0.24173 | 0.24126 | 0.24081 | 0.24036 | 0.23993 | 0.23784 | 0.2359 | 0.23411 | 1.297 | 0.26887 | 0.26872 | 0.26853 | 0.26816 | 0.2678 | 0.26733 | 0.26686 | 0.26641 | 0.26597 | 0.26553 | 0.26345 | 0.26152 | 0.25972
| BOAT OF GARTEN | BOAT OF GARTEN | MINIMUM HEADROOM | NH 95609 19427 | NO | YES | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 7.7729 | 9.5624 | 9.5261 | 9.4815 | 9.4378 | 9.3947 | 9.3524 | 9.3108 | 9.2658 | 9.2211 | 9.1886 | 9.172 | 9.1204 | 7.86 | 7.5361 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 7.809 | 7.5093
|  | BOAT OF GARTEN | CT |  |  |  | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.5694 | 9.5495 | 9.5267 | 9.5041 | 9.4816 | 9.4593 | 9.4378 | 9.4145 | 9.3914 | 9.3685 | 9.3459 | 9.1847 | 9.1317 | 9.1144 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696
|  | BOAT OF GARTEN | LW |  |  |  | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 7.7729 | 9.5624 | 9.5261 | 9.4815 | 9.4378 | 9.3947 | 9.3524 | 9.3108 | 9.2658 | 9.2211 | 9.1886 | 9.172 | 9.1204 | 7.86 | 7.5361 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 7.809 | 7.5093
|  | BOAT OF GARTEN | ST |  |  |  | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.5761 | 9.5653 | 9.5485 | 9.5284 | 9.5033 | 9.4786 | 9.4546 | 9.4288 | 9.4034 | 9.3785 | 9.354 | 9.2339 | 9.1648 | 9.1328 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696
|  | BOAT OF GARTEN | FS |  |  |  | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.8219 | 9.5835 | 9.5827 | 9.5778 | 9.5721 | 9.564 | 9.5559 | 9.5457 | 9.5355 | 9.5256 | 9.5159 | 9.5064 | 9.4609 | 9.4179 | 9.377 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696 | 9.696
| PETERHEAD SHELL | BODDAM | MINIMUM HEADROOM | NK 12219 42512 | YES | NO | 10.5654 | 10.557 | 10.5466 | 10.543 | 10.5397 | 10.5365 | 10.5333 | 10.5299 | 10.5265 | 10.5231 | 10.5197 | 10.5049 | 10.49 | 10.4755 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607
|  | BODDAM | CT |  |  |  | 10.566 | 10.5598 | 10.5527 | 10.546 | 10.5437 | 10.5415 | 10.5393 | 10.5369 | 10.5346 | 10.5322 | 10.5299 | 10.5192 | 10.5085 | 10.498 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607
|  | BODDAM | LW |  |  |  | 10.5654 | 10.557 | 10.5466 | 10.543 | 10.5397 | 10.5365 | 10.5333 | 10.5299 | 10.5265 | 10.5231 | 10.5197 | 10.5049 | 10.49 | 10.4755 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607
|  | BODDAM | ST |  |  |  | 10.5682 | 10.5658 | 10.562 | 10.5575 | 10.5531 | 10.5487 | 10.5456 | 10.5441 | 10.5427 | 10.5413 | 10.5399 | 10.533 | 10.5263 | 10.5197 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607
|  | BODDAM | FS |  |  |  | 10.5696 | 10.5694 | 10.5683 | 10.567 | 10.5655 | 10.5641 | 10.5622 | 10.5604 | 10.5587 | 10.5569 | 10.5552 | 10.547 | 10.5439 | 10.5416 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.2952 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607 | 10.8607
| TUMMEL BRIDGE | BONSKEID | MINIMUM HEADROOM | NN 90919 60658 | YES | YES | 2.7767 | 2.6383 | 2.5014 | 2.3675 | 2.2364 | 2.1219 | 2.0265 | 1.9637 | 1.9223 | 1.8802 | 1.8436 | 1.7065 | 0.83093 | 0.59469 | 2.9321 | 2.8548 | 2.7776 | 2.702 | 2.6278 | 2.556 | 2.4851 | 2.4318 | 2.3905 | 2.3624 | 2.3472 | 2.2771 | 2.209 | 0.82294 | 2.9052 | 2.7977 | 2.6945 | 2.5942 | 2.4967 | 2.4027 | 2.3111 | 2.251 | 2.2114 | 2.1712 | 2.1399 | 2.0263 | 0.83547 | 0.5802
|  | BONSKEID | CT |  |  |  | 2.7767 | 2.6383 | 2.5014 | 2.3675 | 2.2364 | 2.1219 | 2.0265 | 1.9637 | 1.9223 | 1.8802 | 1.8436 | 1.7065 | 0.83093 | 0.59469 | 2.9321 | 2.8548 | 2.7776 | 2.702 | 2.6278 | 2.556 | 2.4851 | 2.4318 | 2.3905 | 2.3624 | 2.3472 | 2.2771 | 2.209 | 0.82294 | 2.9052 | 2.7977 | 2.6945 | 2.5942 | 2.4967 | 2.4027 | 2.3111 | 2.251 | 2.2114 | 2.1712 | 2.1399 | 2.0263 | 0.83547 | 0.5802
|  | BONSKEID | LW |  |  |  | 2.9656 | 2.9104 | 2.842 | 2.771 | 2.6976 | 2.6229 | 2.5767 | 2.5274 | 2.4771 | 2.4365 | 2.4096 | 2.2673 | 2.1047 | 0.78784 | 3.0337 | 3.0003 | 2.9588 | 2.9159 | 2.8715 | 2.8266 | 2.7806 | 2.7608 | 2.7417 | 2.7222 | 2.7032 | 2.606 | 2.502 | 0.82537 | 3.0723 | 3.0419 | 3.005 | 2.9662 | 2.9256 | 2.8838 | 2.8406 | 2.7935 | 2.753 | 2.7256 | 2.6978 | 2.5508 | 2.3828 | 0.72054
|  | BONSKEID | ST |  |  |  | 3.0046 | 2.9854 | 2.9588 | 2.9284 | 2.8988 | 2.8699 | 2.8401 | 2.8081 | 2.772 | 2.7347 | 2.706 | 2.5984 | 2.5221 | 2.4527 | 3.0558 | 3.0443 | 3.028 | 3.0094 | 2.9914 | 2.9738 | 2.9556 | 2.936 | 2.9141 | 2.8914 | 2.8742 | 2.7944 | 2.7643 | 2.7322 | 3.1014 | 3.0904 | 3.0764 | 3.061 | 3.0452 | 3.0299 | 3.0142 | 2.9979 | 2.9785 | 2.9586 | 2.9426 | 2.8615 | 2.7892 | 2.7423
|  | BONSKEID | FS |  |  |  | 3.0042 | 2.9957 | 2.9795 | 2.9623 | 2.9451 | 2.9279 | 2.9091 | 2.8902 | 2.8711 | 2.8519 | 2.8356 | 2.7482 | 2.6647 | 2.5861 | 3.0561 | 3.0513 | 3.042 | 3.032 | 3.022 | 3.012 | 3.001 | 2.9898 | 2.9786 | 2.9673 | 2.9578 | 2.9074 | 2.8596 | 2.8147 | 3.0982 | 3.0917 | 3.0806 | 3.0691 | 3.0576 | 3.0462 | 3.0342 | 3.0222 | 3.0102 | 2.9982 | 2.9874 | 2.9274 | 2.8681 | 2.8115
| PORT ANN | BOWMORE | MINIMUM HEADROOM | NR 32021 60211 | YES | YES | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821
|  | BOWMORE | CT |  |  |  | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821
|  | BOWMORE | LW |  |  |  | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821
|  | BOWMORE | ST |  |  |  | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821
|  | BOWMORE | FS |  |  |  | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.8189 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.3305 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821 | 5.4821
| SHETLAND | BRAE | MINIMUM HEADROOM | HU3604068816 | YES | YES | 2.9918 | 2.9024 | 2.8188 | 2.7382 | 2.6606 | 2.586 | 2.5143 | 2.4738 | 2.4537 | 2.4337 | 2.4141 | 0.84134 | 0.73985 | 0.54347 | 2.026 | 1.9412 | 1.8611 | 1.7837 | 1.7096 | 1.6676 | 1.6326 | 1.6126 | 1.6026 | 1.5926 | 1.5829 | 0.64981 | 0.43645 | 0.21911 | 1.9875 | 1.8857 | 1.7902 | 1.698 | 0.97183 | 0.89938 | 0.82982 | 0.79046 | 0.77089 | 0.75152 | 0.73244 | 0.48817 | 0.31659 | 0.075936
|  | BRAE | CT |  |  |  | 2.9918 | 2.9024 | 2.8188 | 2.7382 | 2.6606 | 2.586 | 2.5143 | 2.4738 | 2.4537 | 2.4337 | 2.4141 | 0.84134 | 0.73985 | 0.54347 | 2.026 | 1.9412 | 1.8611 | 1.7837 | 1.7096 | 1.6676 | 1.6326 | 1.6126 | 1.6026 | 1.5926 | 1.5829 | 0.64981 | 0.43645 | 0.21911 | 1.9875 | 1.8857 | 1.7902 | 1.698 | 0.97183 | 0.89938 | 0.82982 | 0.79046 | 0.77089 | 0.75152 | 0.73244 | 0.48817 | 0.31659 | 0.075936
|  | BRAE | LW |  |  |  | 3.1501 | 3.1367 | 3.1216 | 3.1049 | 3.0869 | 3.0676 | 3.0473 | 3.0245 | 3.0011 | 2.9772 | 2.9529 | 2.6678 | 2.5196 | 0.92192 | 2.1716 | 2.1561 | 2.138 | 2.1183 | 2.0981 | 2.0765 | 2.0539 | 2.0291 | 2.004 | 1.9785 | 1.9527 | 1.6932 | 0.79752 | 0.50562 | 2.1658 | 2.1493 | 2.1305 | 2.1099 | 2.088 | 2.0647 | 2.0402 | 2.0129 | 1.985 | 1.9565 | 1.9277 | 0.97887 | 0.76743 | 0.44141
|  | BRAE | ST |  |  |  | 3.173 | 3.1677 | 3.1625 | 3.1574 | 3.1512 | 3.1453 | 3.1395 | 3.134 | 3.126 | 3.1182 | 3.1106 | 2.9908 | 2.9529 | 2.9111 | 2.1938 | 2.1879 | 2.1813 | 2.1745 | 2.1576 | 2.1409 | 2.1245 | 2.1078 | 2.0891 | 2.0709 | 2.053 | 1.9025 | 1.8711 | 1.837 | 2.1921 | 2.1856 | 2.179 | 2.1724 | 2.1607 | 2.1492 | 2.138 | 2.1268 | 2.113 | 2.0995 | 2.0863 | 1.9387 | 1.8913 | 1.8396
|  | BRAE | FS |  |  |  | 3.1677 | 3.1623 | 3.1544 | 3.1466 | 3.1389 | 3.1313 | 3.1239 | 3.1165 | 3.1092 | 3.102 | 3.0949 | 3.0526 | 3.0083 | 2.9655 | 2.1895 | 2.1844 | 2.1766 | 2.1687 | 2.158 | 2.1473 | 2.1357 | 2.1243 | 2.1132 | 2.1023 | 2.0915 | 2.0322 | 1.9725 | 1.9153 | 2.1863 | 2.1802 | 2.1711 | 2.162 | 2.1518 | 2.1417 | 2.1312 | 2.121 | 2.1109 | 2.101 | 2.0912 | 2.0348 | 1.9769 | 1.921
| BRIDGE OF DUN | BRECHIN | MINIMUM HEADROOM | NO 60998 59682 | NO | YES | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.2588 | 11.154 | 10.6255 | 14.429 | 14.3609 | 14.2815 | 14.196 | 14.1546 | 14.1233 | 14.092 | 14.0582 | 14.0241 | 13.9895 | 13.9576 | 10.7651 | 9.5167 | 8.8963 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 10.9667 | 9.5608 | 8.9725
|  | BRECHIN | CT |  |  |  | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.2588 | 11.3929 | 10.9858 | 14.429 | 14.3609 | 14.2823 | 14.2023 | 14.159 | 14.1283 | 14.0967 | 14.0622 | 14.0272 | 13.9923 | 13.9606 | 10.9047 | 9.7972 | 9.3193 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 11.0962 | 9.8208 | 9.3777
|  | BRECHIN | LW |  |  |  | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.2588 | 11.154 | 10.6255 | 14.4333 | 14.365 | 14.2815 | 14.196 | 14.1546 | 14.1233 | 14.092 | 14.0582 | 14.0241 | 13.9895 | 13.9576 | 10.7651 | 9.5167 | 8.8963 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 10.9667 | 9.5608 | 8.9725
|  | BRECHIN | ST |  |  |  | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.5536 | 16.1745 | 16.1745 | 14.4554 | 14.4312 | 14.3972 | 14.3571 | 14.3147 | 14.2737 | 14.2314 | 14.1875 | 14.1628 | 14.1426 | 14.1247 | 13.8416 | 11.4279 | 11.1676 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.5477 | 14.1695 | 11.3123
|  | BRECHIN | FS |  |  |  | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 16.8484 | 14.4942 | 14.4877 | 14.4753 | 14.4611 | 14.4456 | 14.4311 | 14.4134 | 14.3954 | 14.3773 | 14.359 | 14.3423 | 14.2752 | 14.2171 | 14.174 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418 | 14.8418
| PERSLEY | BRIDGE OF DON | MINIMUM HEADROOM | NJ 94130 10184 | NO | YES | 36.6207 | 36.3729 | 36.074 | 35.8273 | 35.8273 | 35.8273 | 35.8273 | 35.8273 | 35.8273 | 35.8273 | 35.8273 | 35.5493 | 35.5493 | 35.5493 | 33.4413 | 33.2249 | 32.9638 | 32.7406 | 32.5299 | 32.3233 | 32.1202 | 31.9004 | 31.6823 | 31.4663 | 31.2453 | 30.4332 | 29.8818 | 29.4026 | 33.0762 | 32.7063 | 32.3493 | 32.2024 | 32.0638 | 31.9361 | 31.8508 | 31.7585 | 31.6669 | 31.5762 | 31.4834 | 30.951 | 30.6708 | 30.4385
|  | BRIDGE OF DON | CT |  |  |  | 36.6513 | 36.4789 | 36.2841 | 36.1258 | 35.9748 | 35.8273 | 35.8273 | 35.8273 | 35.8273 | 35.8273 | 35.8273 | 35.5493 | 35.5493 | 35.5493 | 33.4684 | 33.3175 | 33.1473 | 33.009 | 32.8771 | 32.7406 | 32.6024 | 32.455 | 32.3162 | 32.1816 | 32.0496 | 31.4389 | 30.981 | 30.5369 | 33.1219 | 32.8646 | 32.5737 | 32.379 | 32.2923 | 32.2024 | 32.1114 | 32.0144 | 31.9331 | 31.8766 | 31.8212 | 31.3733 | 31.181 | 30.9945
|  | BRIDGE OF DON | LW |  |  |  | 36.6207 | 36.3729 | 36.074 | 35.8273 | 35.8273 | 35.8273 | 35.8273 | 35.8273 | 35.8273 | 35.8273 | 35.8273 | 35.5493 | 35.5493 | 35.5493 | 33.4413 | 33.2249 | 32.9638 | 32.7406 | 32.5299 | 32.3233 | 32.1202 | 31.9004 | 31.6823 | 31.4663 | 31.2453 | 30.4332 | 29.8818 | 29.4026 | 33.0762 | 32.7063 | 32.3493 | 32.2024 | 32.0638 | 31.9361 | 31.8508 | 31.7585 | 31.6669 | 31.5762 | 31.4834 | 30.951 | 30.6708 | 30.4385
|  | BRIDGE OF DON | ST |  |  |  | 36.712 | 36.6311 | 36.5183 | 36.412 | 36.3416 | 36.2674 | 36.1917 | 36.1111 | 36.0376 | 35.9679 | 35.9008 | 35.6883 | 35.6883 | 35.6883 | 33.5322 | 33.4504 | 33.3519 | 33.259 | 33.1976 | 33.1327 | 33.0665 | 32.9962 | 32.932 | 32.8711 | 32.8124 | 32.4206 | 32.1118 | 31.8114 | 33.2126 | 33.0918 | 32.9234 | 32.7646 | 32.6596 | 32.5488 | 32.4357 | 32.3706 | 32.3284 | 32.2883 | 32.2497 | 31.9135 | 31.7516 | 31.6254
|  | BRIDGE OF DON | FS |  |  |  | 36.8185 | 36.7367 | 36.6966 | 36.6635 | 36.6387 | 36.6138 | 36.5833 | 36.5536 | 36.5247 | 36.4961 | 36.4688 | 36.344 | 36.221 | 36.1002 | 33.6739 | 33.5581 | 33.516 | 33.4813 | 33.457 | 33.4353 | 33.4087 | 33.3827 | 33.3575 | 33.3325 | 33.3086 | 33.1996 | 33.0922 | 32.9866 | 33.3716 | 33.2494 | 33.1896 | 33.1401 | 33.103 | 33.0659 | 33.0204 | 32.9761 | 32.9329 | 32.8902 | 32.8494 | 32.6631 | 32.4796 | 32.3643
| BRIDGE OF DUN | BRIDGE OF DUN | MINIMUM HEADROOM | NO 66018 58883 | YES | YES | 1.6287 | 1.6287 | 1.6287 | 1.6287 | 1.6287 | 1.6287 | 1.6287 | 1.6287 | 1.6287 | 1.6287 | 1.6287 | 0.6641 | 0.62973 | 0.59571 | 1.4054 | 1.4054 | 1.4054 | 1.4054 | 1.4054 | 1.4054 | 1.4054 | 1.4054 | 1.4054 | 0.99598 | 0.98222 | 0.54084 | 0.49976 | 0.4591 | 1.5903 | 1.5884 | 1.5863 | 1.5841 | 1.5821 | 1.58 | 1.578 | 1.5759 | 1.5758 | 1.5758 | 1.5758 | 0.52657 | 0.48305 | 0.43999
|  | BRIDGE OF DUN | CT |  |  |  | 1.6287 | 1.6287 | 1.6287 | 1.6287 | 1.6287 | 1.6287 | 1.6287 | 1.6287 | 1.6287 | 1.6287 | 1.6287 | 0.67319 | 0.64787 | 0.62283 | 1.4054 | 1.4054 | 1.4054 | 1.4054 | 1.4054 | 1.4054 | 1.4054 | 1.4054 | 1.4054 | 0.99598 | 0.98228 | 0.55171 | 0.52145 | 0.49151 | 1.5903 | 1.5884 | 1.5863 | 1.5841 | 1.5821 | 1.58 | 1.578 | 1.5759 | 1.5758 | 1.5758 | 1.5758 | 0.53807 | 0.50602 | 0.47432
|  | BRIDGE OF DUN | LW |  |  |  | 1.6287 | 1.6287 | 1.6287 | 1.6287 | 1.6287 | 1.6287 | 1.6287 | 1.6287 | 1.6287 | 1.6287 | 1.6287 | 0.6641 | 0.62973 | 0.59571 | 1.4054 | 1.4054 | 1.4054 | 1.4054 | 1.4054 | 1.4054 | 1.4054 | 1.4054 | 1.4054 | 0.99615 | 0.98222 | 0.54084 | 0.49976 | 0.4591 | 1.5905 | 1.5887 | 1.5865 | 1.5844 | 1.5823 | 1.5802 | 1.5782 | 1.576 | 1.5758 | 1.5758 | 1.5758 | 0.52657 | 0.48305 | 0.43999
|  | BRIDGE OF DUN | ST |  |  |  | 1.6287 | 1.6287 | 1.6287 | 1.6287 | 1.6287 | 1.6287 | 1.6287 | 1.6287 | 1.6287 | 1.6287 | 1.6287 | 1.3824 | 1.3824 | 0.99331 | 1.4054 | 1.4054 | 1.4054 | 1.4054 | 1.4054 | 1.4054 | 1.4054 | 1.4054 | 1.4054 | 1.4054 | 1.4054 | 0.86594 | 0.84704 | 0.82811 | 1.5911 | 1.5906 | 1.5898 | 1.5888 | 1.5882 | 1.5876 | 1.587 | 1.5863 | 1.5857 | 1.5851 | 1.5845 | 0.89481 | 0.87664 | 0.85843
|  | BRIDGE OF DUN | FS |  |  |  | 1.6287 | 1.6287 | 1.6287 | 1.6287 | 1.6287 | 1.6287 | 1.6287 | 1.6287 | 1.6287 | 1.6287 | 1.6287 | 1.6287 | 1.6287 | 1.6287 | 1.4054 | 1.4054 | 1.4054 | 1.4054 | 1.4054 | 1.4054 | 1.4054 | 1.4054 | 1.4054 | 1.4054 | 1.4054 | 1.4054 | 1.4054 | 1.4054 | 1.5914 | 1.5914 | 1.5912 | 1.5909 | 1.5907 | 1.5905 | 1.5902 | 1.5899 | 1.5897 | 1.5894 | 1.5892 | 1.588 | 1.5869 | 1.5859
| ABERNETHY | BRIDGE OF EARN | MINIMUM HEADROOM | NO 13343 17764 | NO | YES | 17.3877 | 17.3877 | 17.3877 | 17.3877 | 17.3877 | 17.3877 | 17.3877 | 17.3877 | 17.3877 | 17.3877 | 17.3877 | 14.3727 | 13.9752 | 13.6306 | 15.2873 | 15.2404 | 15.1833 | 15.1537 | 15.1537 | 15.1537 | 15.1537 | 13.6889 | 13.495 | 13.2931 | 13.1274 | 12.427 | 11.9254 | 11.4906 | 15.5197 | 15.5197 | 15.5197 | 15.5197 | 15.5197 | 15.5197 | 15.5197 | 13.7053 | 13.5165 | 13.3198 | 13.1584 | 12.4762 | 11.9876 | 11.5641
|  | BRIDGE OF EARN | CT |  |  |  | 17.3877 | 17.3877 | 17.3877 | 17.3877 | 17.3877 | 17.3877 | 17.3877 | 17.3877 | 17.3877 | 17.3877 | 17.3877 | 17.3877 | 14.5393 | 14.3018 | 15.2893 | 15.2498 | 15.2043 | 15.1585 | 15.1537 | 15.1537 | 15.1537 | 15.1537 | 13.7196 | 13.5395 | 13.3928 | 12.9584 | 12.6373 | 12.3375 | 15.5197 | 15.5197 | 15.5197 | 15.5197 | 15.5197 | 15.5197 | 15.5197 | 15.5197 | 13.7353 | 13.5598 | 13.4169 | 12.9938 | 12.681 | 12.389
|  | BRIDGE OF EARN | LW |  |  |  | 17.3877 | 17.3877 | 17.3877 | 17.3877 | 17.3877 | 17.3877 | 17.3877 | 17.3877 | 17.3877 | 17.3877 | 17.3877 | 14.3727 | 13.9752 | 13.6306 | 15.2873 | 15.2404 | 15.1833 | 15.1537 | 15.1537 | 15.1537 | 15.1537 | 13.6889 | 13.495 | 13.2931 | 13.1274 | 12.427 | 11.9254 | 11.4906 | 15.5197 | 15.5197 | 15.5197 | 15.5197 | 15.5197 | 15.5197 | 15.5197 | 13.7053 | 13.5165 | 13.3198 | 13.1584 | 12.4762 | 11.9876 | 11.5641
|  | BRIDGE OF EARN | ST |  |  |  | 17.3896 | 17.3877 | 17.3877 | 17.3877 | 17.3877 | 17.3877 | 17.3877 | 17.3877 | 17.3877 | 17.3877 | 17.3877 | 17.3877 | 17.3877 | 17.3877 | 15.3048 | 15.2893 | 15.2682 | 15.244 | 15.2177 | 15.189 | 15.1579 | 15.1537 | 15.1537 | 15.1537 | 15.1537 | 13.7921 | 13.5843 | 13.3896 | 15.5197 | 15.5197 | 15.5197 | 15.5197 | 15.5197 | 15.5197 | 15.5197 | 15.5197 | 15.5197 | 15.5197 | 15.5197 | 15.5197 | 13.6035 | 13.4138
|  | BRIDGE OF EARN | FS |  |  |  | 17.3913 | 17.3903 | 17.3885 | 17.3877 | 17.3877 | 17.3877 | 17.3877 | 17.3877 | 17.3877 | 17.3877 | 17.3877 | 17.3877 | 17.3877 | 17.3877 | 15.3126 | 15.3077 | 15.2996 | 15.2909 | 15.2808 | 15.2699 | 15.2572 | 15.2438 | 15.2297 | 15.2148 | 15.2028 | 15.1537 | 15.1537 | 15.1537 | 15.5197 | 15.5197 | 15.5197 | 15.5197 | 15.5197 | 15.5197 | 15.5197 | 15.5197 | 15.5197 | 15.5197 | 15.5197 | 15.5197 | 15.5197 | 15.5197
| RANNOCH | BRIDGE OF GAUR | MINIMUM HEADROOM | NN 50676 57767 | YES | YES | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.2189 | 1.2171 | 1.2148 | 1.2126 | 1.2104 | 1.2085 | 1.2073 | 1.2068 | 1.2064 | 1.2061 | 1.2058 | 1.2041 | 1.2024 | 1.2015 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458
|  | BRIDGE OF GAUR | CT |  |  |  | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.219 | 1.2176 | 1.2161 | 1.2145 | 1.213 | 1.2115 | 1.2101 | 1.2087 | 1.2075 | 1.2071 | 1.2067 | 1.2056 | 1.2045 | 1.2034 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458
|  | BRIDGE OF GAUR | LW |  |  |  | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.2189 | 1.2171 | 1.2148 | 1.2126 | 1.2104 | 1.2085 | 1.2073 | 1.2068 | 1.2064 | 1.2061 | 1.2058 | 1.2041 | 1.2024 | 1.2015 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458
|  | BRIDGE OF GAUR | ST |  |  |  | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.2195 | 1.2189 | 1.2181 | 1.217 | 1.216 | 1.215 | 1.2139 | 1.2129 | 1.2118 | 1.2107 | 1.2097 | 1.2069 | 1.2061 | 1.2054 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458
|  | BRIDGE OF GAUR | FS |  |  |  | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.4282 | 1.2198 | 1.2197 | 1.2195 | 1.2192 | 1.2189 | 1.2185 | 1.2181 | 1.2176 | 1.2172 | 1.2168 | 1.2164 | 1.2144 | 1.2125 | 1.2108 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458 | 1.2458
| BROADFORD | BROADFORD | MINIMUM HEADROOM | NG 62656 24360 | YES | YES | 6.0989 | 6.0978 | 6.0965 | 6.0952 | 6.0913 | 6.09 | 6.0887 | 6.0873 | 6.0859 | 6.0846 | 6.0832 | 6.0817 | 6.0817 | 6.0817 | 5.852 | 5.8452 | 5.8371 | 5.8291 | 5.8056 | 5.7974 | 5.7944 | 5.7944 | 5.7944 | 5.7944 | 5.7944 | 5.7944 | 5.7944 | 4.9446 | 5.9487 | 5.9438 | 5.938 | 5.9322 | 5.9154 | 5.9095 | 5.9036 | 5.8976 | 5.8916 | 5.8856 | 5.8797 | 5.8373 | 5.8211 | 5.8211
|  | BROADFORD | CT |  |  |  | 6.099 | 6.0982 | 6.0973 | 6.0964 | 6.0932 | 6.0924 | 6.0915 | 6.0906 | 6.0895 | 6.0882 | 6.0872 | 6.0817 | 6.0817 | 6.0817 | 5.8526 | 5.8476 | 5.8421 | 5.8365 | 5.8171 | 5.8118 | 5.8066 | 5.8011 | 5.7944 | 5.7944 | 5.7944 | 5.7944 | 5.7944 | 5.7944 | 5.9491 | 5.9456 | 5.9416 | 5.9376 | 5.9236 | 5.9199 | 5.9161 | 5.9121 | 5.9072 | 5.9014 | 5.897 | 5.8666 | 5.8358 | 5.8211
|  | BROADFORD | LW |  |  |  | 6.0989 | 6.0978 | 6.0965 | 6.0952 | 6.0913 | 6.09 | 6.0887 | 6.0873 | 6.0859 | 6.0846 | 6.0832 | 6.0817 | 6.0817 | 6.0817 | 5.852 | 5.8452 | 5.8371 | 5.8291 | 5.8056 | 5.7974 | 5.7944 | 5.7944 | 5.7944 | 5.7944 | 5.7944 | 5.7944 | 5.7944 | 4.9446 | 5.9487 | 5.9438 | 5.938 | 5.9322 | 5.9154 | 5.9095 | 5.9036 | 5.8976 | 5.8916 | 5.8856 | 5.8797 | 5.8373 | 5.8211 | 5.8211
|  | BROADFORD | ST |  |  |  | 6.0994 | 6.0992 | 6.0987 | 6.0982 | 6.0958 | 6.0949 | 6.094 | 6.0931 | 6.0921 | 6.0909 | 6.0899 | 6.0855 | 6.0817 | 6.0817 | 5.8553 | 5.8536 | 5.851 | 5.8478 | 5.8329 | 5.8275 | 5.8222 | 5.8165 | 5.81 | 5.8026 | 5.7967 | 5.7944 | 5.7944 | 5.7944 | 5.9511 | 5.9498 | 5.948 | 5.9457 | 5.935 | 5.9311 | 5.9273 | 5.9232 | 5.9186 | 5.9133 | 5.909 | 5.8896 | 5.8704 | 5.8513
|  | BROADFORD | FS |  |  |  | 6.0997 | 6.0997 | 6.0995 | 6.0994 | 6.0984 | 6.0981 | 6.0977 | 6.0973 | 6.0969 | 6.0965 | 6.0961 | 6.0944 | 6.0928 | 6.0913 | 5.8571 | 5.8569 | 5.8559 | 5.8549 | 5.8492 | 5.8473 | 5.8448 | 5.8422 | 5.8397 | 5.8373 | 5.835 | 5.8242 | 5.8145 | 5.8053 | 5.9524 | 5.9522 | 5.9515 | 5.9508 | 5.9467 | 5.9453 | 5.9435 | 5.9417 | 5.9398 | 5.9382 | 5.9365 | 5.9287 | 5.9218 | 5.9152
| CARRADALE | BRODICK | MINIMUM HEADROOM | NS 01976 35459 | NO | YES | 10.9316 | 10.9203 | 10.9061 | 10.8923 | 10.8791 | 10.8791 | 10.8791 | 10.8791 | 10.8791 | 10.8791 | 10.8791 | 10.8791 | 10.8791 | 10.8791 | 10.8611 | 10.8514 | 10.8394 | 10.8276 | 10.8161 | 10.8047 | 10.7935 | 10.7814 | 10.7667 | 10.7495 | 10.7326 | 10.5542 | 10.5026 | 10.4518 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869
|  | BRODICK | CT |  |  |  | 10.9331 | 10.9248 | 10.9152 | 10.9056 | 10.8956 | 10.885 | 10.8791 | 10.8791 | 10.8791 | 10.8791 | 10.8791 | 10.8791 | 10.8791 | 10.8791 | 10.8624 | 10.8553 | 10.8471 | 10.8389 | 10.8304 | 10.8214 | 10.8134 | 10.8046 | 10.7963 | 10.7879 | 10.7796 | 10.6097 | 10.5242 | 10.4797 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869
|  | BRODICK | LW |  |  |  | 10.9316 | 10.9203 | 10.9061 | 10.8923 | 10.8791 | 10.8791 | 10.8791 | 10.8791 | 10.8791 | 10.8791 | 10.8791 | 10.8791 | 10.8791 | 10.8791 | 10.8611 | 10.8514 | 10.8394 | 10.8276 | 10.8161 | 10.8047 | 10.7935 | 10.7814 | 10.7694 | 10.7574 | 10.7455 | 10.5542 | 10.5026 | 10.4518 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869
|  | BRODICK | ST |  |  |  | 10.9374 | 10.9342 | 10.929 | 10.9227 | 10.9023 | 10.8817 | 10.8791 | 10.8791 | 10.8791 | 10.8791 | 10.8791 | 10.8791 | 10.8791 | 10.8791 | 10.866 | 10.8632 | 10.8588 | 10.8535 | 10.8361 | 10.8187 | 10.8021 | 10.7841 | 10.7667 | 10.7495 | 10.7326 | 10.6501 | 10.5683 | 10.5371 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869
|  | BRODICK | FS |  |  |  | 10.9405 | 10.9403 | 10.9388 | 10.937 | 10.9302 | 10.9236 | 10.915 | 10.9066 | 10.8983 | 10.8902 | 10.8823 | 10.8791 | 10.8791 | 10.8791 | 10.8687 | 10.8685 | 10.8672 | 10.8657 | 10.8599 | 10.8542 | 10.847 | 10.8398 | 10.8328 | 10.8258 | 10.8191 | 10.787 | 10.7569 | 10.7287 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869 | 10.1869
| BRORA | BRORA | MINIMUM HEADROOM | NC 90482 04236 | NO | YES | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 4.8645 | 5.9989 | 5.9891 | 5.977 | 5.9651 | 5.9535 | 5.9419 | 5.9306 | 5.9183 | 5.9062 | 5.8999 | 5.897 | 5.8926 | 4.9868 | 4.7675 | 6.014 | 5.9879 | 5.956 | 5.9245 | 5.8936 | 5.8632 | 5.8562 | 5.8511 | 5.8461 | 5.841 | 5.8361 | 5.8145 | 5.8145 | 4.9582
|  | BRORA | CT |  |  |  | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 5.9997 | 5.9927 | 5.9846 | 5.9767 | 5.9689 | 5.9612 | 5.9535 | 5.9453 | 5.9371 | 5.929 | 5.921 | 5.8926 | 5.8926 | 5.8926 | 6.0161 | 5.9974 | 5.9761 | 5.9551 | 5.9345 | 5.914 | 5.8939 | 5.8721 | 5.859 | 5.8556 | 5.8523 | 5.825 | 5.8145 | 5.8145
|  | BRORA | LW |  |  |  | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 4.8645 | 5.9989 | 5.9891 | 5.977 | 5.9651 | 5.9535 | 5.9419 | 5.9306 | 5.9183 | 5.9062 | 5.8999 | 5.897 | 5.8926 | 4.9868 | 4.7675 | 6.014 | 5.9879 | 5.956 | 5.9245 | 5.8936 | 5.8632 | 5.8562 | 5.8511 | 5.8461 | 5.841 | 5.8361 | 5.8145 | 5.8145 | 4.9582
|  | BRORA | ST |  |  |  | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.0047 | 6.0029 | 6.0018 | 6.0004 | 5.9932 | 5.9862 | 5.9792 | 5.9717 | 5.9644 | 5.9571 | 5.95 | 5.9152 | 5.8963 | 5.8926 | 6.0263 | 6.0244 | 6.0214 | 6.0179 | 5.9989 | 5.9802 | 5.9618 | 5.942 | 5.9225 | 5.9033 | 5.8846 | 5.8498 | 5.8349 | 5.8202
|  | BRORA | FS |  |  |  | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.4674 | 6.0059 | 6.0056 | 6.0048 | 6.0038 | 6.0009 | 5.9985 | 5.9955 | 5.9925 | 5.9896 | 5.9867 | 5.9839 | 5.9704 | 5.9575 | 5.9449 | 6.0274 | 6.0272 | 6.0264 | 6.0254 | 6.0191 | 6.0128 | 6.0048 | 5.9969 | 5.9891 | 5.9815 | 5.9741 | 5.9386 | 5.9042 | 5.8711
| MILTON OF CRAIGIE | BROUGHTY FERRY | MINIMUM HEADROOM | NO 46658 30758 | NO | YES | 15.0935 | 15.0281 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 14.2746 | 14.2405 | 14.1986 | 14.1576 | 14.1162 | 14.0744 | 14.0334 | 13.9878 | 13.9409 | 13.8937 | 13.847 | 13.6872 | 13.6284 | 13.6284 | 14.4915 | 14.4467 | 14.3914 | 14.3376 | 14.2831 | 14.2742 | 14.2742 | 14.2742 | 14.2742 | 14.2742 | 14.2742 | 14.2742 | 14.2742 | 14.2742
|  | BROUGHTY FERRY | CT |  |  |  | 15.0989 | 15.0525 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 14.2774 | 14.2532 | 14.2254 | 14.198 | 14.1708 | 14.1445 | 14.1187 | 14.0902 | 14.0588 | 14.0267 | 13.9948 | 13.8811 | 13.7783 | 13.6822 | 14.4953 | 14.4634 | 14.4268 | 14.3907 | 14.3549 | 14.3203 | 14.2864 | 14.2742 | 14.2742 | 14.2742 | 14.2742 | 14.2742 | 14.2742 | 14.2742
|  | BROUGHTY FERRY | LW |  |  |  | 15.0935 | 15.0281 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 14.2746 | 14.2405 | 14.1986 | 14.1576 | 14.1162 | 14.0744 | 14.0334 | 13.9878 | 13.9409 | 13.8937 | 13.847 | 13.6872 | 13.6284 | 13.6284 | 14.4915 | 14.4467 | 14.3914 | 14.3376 | 14.2831 | 14.2742 | 14.2742 | 14.2742 | 14.2742 | 14.2742 | 14.2742 | 14.2742 | 14.2742 | 14.2742
|  | BROUGHTY FERRY | ST |  |  |  | 15.1146 | 15.0952 | 15.0651 | 15.029 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 14.2856 | 14.2755 | 14.2598 | 14.241 | 14.2279 | 14.2154 | 14.2032 | 14.1896 | 14.174 | 14.158 | 14.1421 | 14.0645 | 13.9966 | 13.9328 | 14.506 | 14.4927 | 14.472 | 14.4472 | 14.4301 | 14.4136 | 14.3975 | 14.3796 | 14.3591 | 14.3381 | 14.3171 | 14.2742 | 14.2742 | 14.2742
|  | BROUGHTY FERRY | FS |  |  |  | 15.1256 | 15.1241 | 15.1156 | 15.1059 | 15.0982 | 15.0905 | 15.0805 | 15.0701 | 15.059 | 15.0479 | 15.037 | 15.0068 | 15.0068 | 15.0068 | 14.2913 | 14.2905 | 14.2862 | 14.2811 | 14.277 | 14.273 | 14.2679 | 14.2624 | 14.2566 | 14.2509 | 14.2451 | 14.2161 | 14.1912 | 14.1693 | 14.5136 | 14.5125 | 14.5067 | 14.5001 | 14.4947 | 14.4895 | 14.4826 | 14.4755 | 14.4679 | 14.4603 | 14.4527 | 14.4145 | 14.3818 | 14.3529
| DUNOON | BRUCHAG | MINIMUM HEADROOM | NS 11372 57191 | NO | YES | 16.1094 | 16.0353 | 15.9646 | 15.8965 | 15.8309 | 15.7679 | 15.7074 | 15.6722 | 15.6548 | 15.6375 | 15.6205 | 14.4637 | 14.1744 | 13.8821 | 14.8461 | 14.781 | 14.7182 | 14.6575 | 14.599 | 14.5427 | 14.4885 | 14.4633 | 14.4531 | 14.443 | 14.4331 | 13.6093 | 13.2995 | 12.9881 | 14.6558 | 14.5835 | 14.5147 | 14.4483 | 14.3843 | 13.7778 | 13.7038 | 13.6573 | 13.6305 | 13.604 | 13.5778 | 13.2981 | 13.0091 | 12.6771
|  | BRUCHAG | CT |  |  |  | 16.1094 | 16.0353 | 15.9646 | 15.8965 | 15.8309 | 15.7679 | 15.7074 | 15.6722 | 15.6548 | 15.6375 | 15.6205 | 14.4637 | 14.1744 | 13.8821 | 14.8461 | 14.781 | 14.7182 | 14.6575 | 14.599 | 14.5427 | 14.4885 | 14.4633 | 14.4531 | 14.443 | 14.4331 | 13.6093 | 13.2995 | 12.9881 | 14.6558 | 14.5835 | 14.5147 | 14.4483 | 14.3843 | 13.7778 | 13.7038 | 13.6573 | 13.6305 | 13.604 | 13.5778 | 13.2981 | 13.0091 | 12.6771
|  | BRUCHAG | LW |  |  |  | 16.2406 | 16.2294 | 16.2169 | 16.2031 | 16.1882 | 16.1723 | 16.1554 | 16.136 | 16.1161 | 16.0957 | 16.0751 | 15.9658 | 14.4544 | 14.0669 | 14.9535 | 14.9389 | 14.9219 | 14.9041 | 14.8854 | 14.866 | 14.846 | 14.8235 | 14.8005 | 14.7772 | 14.7538 | 14.6344 | 13.4978 | 13.0845 | 14.7837 | 14.7728 | 14.7606 | 14.7472 | 14.7326 | 14.7171 | 14.7006 | 14.6818 | 14.6623 | 14.6425 | 14.6224 | 13.7004 | 13.2915 | 12.834
|  | BRUCHAG | ST |  |  |  | 16.2596 | 16.2552 | 16.2508 | 16.2466 | 16.2415 | 16.2366 | 16.2318 | 16.2271 | 16.2204 | 16.2138 | 16.2074 | 16.1722 | 16.1394 | 16.1025 | 14.9709 | 14.9656 | 14.9595 | 14.953 | 14.9379 | 14.9231 | 14.9087 | 14.8937 | 14.877 | 14.8607 | 14.8448 | 14.7635 | 14.7356 | 14.7141 | 14.8022 | 14.7979 | 14.7937 | 14.7896 | 14.7846 | 14.7798 | 14.7751 | 14.7706 | 14.764 | 14.7576 | 14.7514 | 14.717 | 14.6851 | 14.6491
|  | BRUCHAG | FS |  |  |  | 16.2552 | 16.2507 | 16.2442 | 16.2377 | 16.2313 | 16.225 | 16.2188 | 16.2127 | 16.2067 | 16.2007 | 16.1949 | 16.1598 | 16.1228 | 16.087 | 14.9682 | 14.9645 | 14.9584 | 14.9522 | 14.943 | 14.9339 | 14.9237 | 14.9137 | 14.9039 | 14.8942 | 14.8847 | 14.8334 | 14.7821 | 14.733 | 14.7979 | 14.7936 | 14.7872 | 14.7809 | 14.7747 | 14.7685 | 14.7625 | 14.7565 | 14.7506 | 14.7449 | 14.7391 | 14.7049 | 14.6689 | 14.634
| KEITH | BUCKIE | MINIMUM HEADROOM | NJ 43291 64802 | NO | YES | 34.4841 | 34.475 | 34.4644 | 34.4529 | 34.4411 | 34.429 | 34.4173 | 34.4043 | 34.3917 | 34.3808 | 34.3708 | 33.5408 | 33.4758 | 33.4123 | 32.0284 | 31.9599 | 31.8808 | 31.7953 | 31.7066 | 31.6163 | 31.5289 | 31.432 | 31.3473 | 31.3153 | 31.3153 | 30.8766 | 30.8766 | 30.8766 | 32.5926 | 32.5657 | 32.5345 | 32.5009 | 32.466 | 32.4305 | 32.3961 | 32.3579 | 32.3207 | 32.2886 | 32.2593 | 31.4665 | 31.4665 | 31.4665
|  | BUCKIE | CT |  |  |  | 34.4841 | 34.475 | 34.4644 | 34.4529 | 34.4411 | 34.429 | 34.4173 | 34.4043 | 34.3917 | 34.3808 | 34.3708 | 33.5408 | 33.4758 | 33.4123 | 32.0284 | 31.9599 | 31.8808 | 31.7953 | 31.7066 | 31.6163 | 31.5289 | 31.432 | 31.3473 | 31.3153 | 31.3153 | 30.8766 | 30.8766 | 30.8766 | 32.5926 | 32.5657 | 32.5345 | 32.5009 | 32.466 | 32.4305 | 32.3961 | 32.3579 | 32.3207 | 32.2886 | 32.2593 | 31.4665 | 31.4665 | 31.4665
|  | BUCKIE | LW |  |  |  | 34.4861 | 34.4797 | 34.4718 | 34.4629 | 34.4536 | 34.4438 | 34.4348 | 34.4249 | 34.4158 | 34.409 | 34.4027 | 33.5697 | 33.4989 | 33.4298 | 32.0442 | 31.9952 | 31.9362 | 31.8697 | 31.8 | 31.7272 | 31.6594 | 31.5854 | 31.5179 | 31.4668 | 31.4198 | 30.8766 | 30.8766 | 30.8766 | 32.5984 | 32.5795 | 32.5563 | 32.5302 | 32.5027 | 32.4741 | 32.4474 | 32.4183 | 32.3917 | 32.3716 | 32.3531 | 31.4665 | 31.4665 | 31.4665
|  | BUCKIE | ST |  |  |  | 34.4888 | 34.4865 | 34.4834 | 34.4792 | 34.4715 | 34.4636 | 34.456 | 34.4475 | 34.4392 | 34.4321 | 34.4258 | 34.0143 | 33.9863 | 33.9589 | 32.0763 | 32.0492 | 32.0229 | 31.9918 | 31.9339 | 31.8751 | 31.8182 | 31.7546 | 31.6924 | 31.6397 | 31.5922 | 31.096 | 31.096 | 31.096 | 32.6062 | 32.5996 | 32.5904 | 32.5782 | 32.5554 | 32.5323 | 32.5099 | 32.4849 | 32.4604 | 32.4396 | 32.421 | 31.9426 | 31.8603 | 31.8556
|  | BUCKIE | FS |  |  |  | 34.4901 | 34.4894 | 34.4881 | 34.4865 | 34.4835 | 34.4805 | 34.4771 | 34.4736 | 34.4702 | 34.4673 | 34.4646 | 34.4523 | 34.4421 | 34.432 | 32.0929 | 32.0842 | 32.0687 | 32.0489 | 32.024 | 32.0014 | 31.9758 | 31.9494 | 31.9242 | 31.9028 | 31.8826 | 31.7908 | 31.7139 | 31.6384 | 32.6103 | 32.6081 | 32.6044 | 32.5995 | 32.5909 | 32.582 | 32.5719 | 32.5615 | 32.5516 | 32.5432 | 32.5352 | 32.4991 | 32.4688 | 32.4391
| FORT AUGUSTUS | BUNOICH | MINIMUM HEADROOM | NH 37662 09672 | YES | YES | 2.1501 | 2.148 | 2.1455 | 2.143 | 2.1424 | 2.1424 | 1.9914 | 1.9844 | 1.9772 | 1.9718 | 1.9663 | 1.9227 | 1.8823 | 1.8426 | 2.1189 | 2.1151 | 2.1106 | 2.1062 | 2.1025 | 2.0989 | 1.9562 | 1.9479 | 1.9395 | 1.9331 | 1.9266 | 1.8753 | 1.8276 | 1.7808 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 1.9498 | 1.9415 | 1.9331 | 1.9267 | 1.9203 | 1.8691 | 1.8216 | 1.7749
|  | BUNOICH | CT |  |  |  | 2.1502 | 2.1487 | 2.1469 | 2.1452 | 2.1435 | 2.1424 | 2.1424 | 2.1424 | 2.1424 | 1.9953 | 1.9859 | 1.9421 | 1.9142 | 1.8867 | 2.1191 | 2.1163 | 2.1131 | 2.1099 | 2.1068 | 2.1043 | 1.9852 | 1.9784 | 1.9715 | 1.9608 | 1.9497 | 1.8981 | 1.8652 | 1.8328 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 1.9787 | 1.9719 | 1.965 | 1.9543 | 1.9433 | 1.8918 | 1.8591 | 1.8268
|  | BUNOICH | LW |  |  |  | 2.1501 | 2.148 | 2.1455 | 2.143 | 2.1424 | 2.1424 | 1.9914 | 1.9844 | 1.9772 | 1.9718 | 1.9663 | 1.9227 | 1.8823 | 1.8426 | 2.1189 | 2.1151 | 2.1106 | 2.1062 | 2.1025 | 2.0989 | 1.9562 | 1.9479 | 1.9395 | 1.9331 | 1.9266 | 1.8753 | 1.8276 | 1.7808 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 1.9498 | 1.9415 | 1.9331 | 1.9267 | 1.9203 | 1.8691 | 1.8216 | 1.7749
|  | BUNOICH | ST |  |  |  | 2.1508 | 2.1501 | 2.1492 | 2.148 | 2.1459 | 2.1438 | 2.1424 | 2.1424 | 2.1424 | 2.1424 | 2.1424 | 1.9859 | 1.9682 | 1.9505 | 2.1201 | 2.1189 | 2.1172 | 2.1151 | 2.1112 | 2.1074 | 2.0954 | 2.0954 | 2.0954 | 1.9947 | 1.9848 | 1.9497 | 1.9288 | 1.908 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 1.9976 | 1.9881 | 1.9783 | 1.9433 | 1.9225 | 1.9017
|  | BUNOICH | FS |  |  |  | 2.1511 | 2.1511 | 2.1508 | 2.1505 | 2.1498 | 2.1491 | 2.1424 | 2.1424 | 2.1424 | 2.1424 | 2.1424 | 2.1424 | 2.1424 | 2.1424 | 2.1207 | 2.1206 | 2.1201 | 2.1196 | 2.1183 | 2.117 | 2.0964 | 2.0954 | 2.0954 | 2.0954 | 2.0954 | 2.0954 | 2.0954 | 2.0954 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101
| THURSO | BURGARHILL | MINIMUM HEADROOM | HY 34441 26078 | YES | YES | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 3.9981 | 3.9841 | 3.9705 | 3.9569 | 3.5692 | 2.9551 | 2.8021 | 4.0362 | 4.0339 | 4.0336 | 4.0336 | 4.0336 | 3.9902 | 3.9749 | 3.9581 | 3.9418 | 3.9257 | 3.9098 | 3.5629 | 3.0165 | 2.8377 | 4.0417 | 4.0417 | 4.0417 | 4.0417 | 4.0417 | 3.9973 | 3.9823 | 3.9655 | 3.9491 | 3.9331 | 3.9172 | 3.5081 | 2.8678 | 2.6833
|  | BURGARHILL | CT |  |  |  | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 3.6207 | 3.0417 | 2.923 | 4.0364 | 4.0345 | 4.0336 | 4.0336 | 4.0336 | 4.0336 | 3.9996 | 3.9942 | 3.989 | 3.984 | 3.9787 | 3.6232 | 3.1176 | 2.9789 | 4.0418 | 4.0417 | 4.0417 | 4.0417 | 4.0417 | 4.0417 | 4.0417 | 4.0417 | 3.9961 | 3.9912 | 3.9861 | 3.5702 | 2.9721 | 2.829
|  | BURGARHILL | LW |  |  |  | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 3.9982 | 3.5692 | 2.9551 | 2.8021 | 4.0362 | 4.0339 | 4.0336 | 4.0336 | 4.0336 | 3.9942 | 3.9877 | 3.9801 | 3.9727 | 3.9656 | 3.9582 | 3.5629 | 3.0165 | 2.8377 | 4.0417 | 4.0417 | 4.0417 | 4.0417 | 4.0417 | 4.0417 | 3.9948 | 3.9874 | 3.9801 | 3.973 | 3.9656 | 3.5081 | 2.8678 | 2.6833
|  | BURGARHILL | ST |  |  |  | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 3.9981 | 3.9841 | 3.9705 | 3.9569 | 3.7552 | 3.4628 | 3.3991 | 4.0371 | 4.0362 | 4.0349 | 4.0339 | 4.0336 | 3.9902 | 3.9749 | 3.9581 | 3.9418 | 3.9257 | 3.9098 | 3.7277 | 3.4729 | 3.3986 | 4.0422 | 4.0417 | 4.0417 | 4.0417 | 4.0417 | 3.9973 | 3.9823 | 3.9655 | 3.9491 | 3.9331 | 3.9172 | 3.7032 | 3.3998 | 3.3232
|  | BURGARHILL | FS |  |  |  | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 4.0687 | 3.9957 | 3.9715 | 3.9486 | 4.0376 | 4.0375 | 4.0371 | 4.0366 | 4.0343 | 4.0336 | 4.0336 | 4.0336 | 3.9983 | 3.9919 | 3.9856 | 3.9553 | 3.927 | 3.9001 | 4.0424 | 4.0424 | 4.0422 | 4.0419 | 4.0417 | 4.0417 | 4.0417 | 4.0417 | 4.0417 | 3.999 | 3.9928 | 3.9627 | 3.9343 | 3.9074
| ELGIN | BURGHEAD | MINIMUM HEADROOM | NJ 12666 68781 | NO | YES | 19.0786 | 19.003 | 18.9338 | 18.867 | 18.8028 | 18.741 | 18.6817 | 18.649 | 18.6328 | 18.6167 | 18.6009 | 18.5258 | 18.448 | 14.3863 | 16.7653 | 16.6452 | 16.5292 | 16.4204 | 16.3816 | 16.3444 | 16.3086 | 16.2889 | 16.2791 | 16.2694 | 16.2599 | 13.0216 | 12.1206 | 11.2305 | 18.2297 | 18.1147 | 18.0017 | 17.8915 | 17.784 | 17.6825 | 17.5844 | 17.5121 | 17.4624 | 17.4452 | 17.4283 | 17.3479 | 13.668 | 12.7381
|  | BURGHEAD | CT |  |  |  | 19.0786 | 19.003 | 18.9338 | 18.867 | 18.8028 | 18.741 | 18.6817 | 18.649 | 18.6328 | 18.6167 | 18.6009 | 18.5258 | 18.448 | 18.3657 | 16.7653 | 16.6452 | 16.5292 | 16.4204 | 16.3816 | 16.3444 | 16.3086 | 16.2889 | 16.2791 | 16.2694 | 16.2599 | 13.3664 | 12.7306 | 12.1006 | 18.2297 | 18.1147 | 18.0017 | 17.8915 | 17.784 | 17.6825 | 17.5844 | 17.5121 | 17.4624 | 17.4452 | 17.4283 | 17.3479 | 17.2647 | 13.5394
|  | BURGHEAD | LW |  |  |  | 19.2167 | 19.2048 | 19.1914 | 19.1766 | 19.1606 | 19.1435 | 19.1255 | 19.1068 | 19.0875 | 19.0678 | 19.0479 | 18.9423 | 18.8229 | 14.3863 | 16.8749 | 16.7906 | 16.7003 | 16.6094 | 16.5964 | 16.5866 | 16.5763 | 16.565 | 16.5533 | 16.5415 | 16.5294 | 13.0216 | 12.1206 | 11.2305 | 18.3725 | 18.3184 | 18.2533 | 18.1871 | 18.1198 | 18.0555 | 17.9919 | 17.9694 | 17.9488 | 17.9277 | 17.9064 | 17.7935 | 13.668 | 12.7381
|  | BURGHEAD | ST |  |  |  | 19.2371 | 19.2324 | 19.2277 | 19.2232 | 19.2178 | 19.2125 | 19.2073 | 19.2025 | 19.1956 | 19.1888 | 19.1822 | 19.1463 | 19.1146 | 19.0816 | 16.9256 | 16.8881 | 16.8429 | 16.8024 | 16.7669 | 16.7348 | 16.7037 | 16.6704 | 16.6357 | 16.6126 | 16.6088 | 16.5882 | 16.5697 | 16.5498 | 18.4069 | 18.3888 | 18.3641 | 18.3357 | 18.31 | 18.2866 | 18.2639 | 18.24 | 18.214 | 18.1886 | 18.1642 | 18.0426 | 17.9779 | 17.9425
|  | BURGHEAD | FS |  |  |  | 19.2324 | 19.2276 | 19.2206 | 19.2137 | 19.2068 | 19.2001 | 19.1934 | 19.1869 | 19.1804 | 19.1741 | 19.1678 | 19.1301 | 19.0928 | 19.0569 | 16.9398 | 16.9314 | 16.9102 | 16.8864 | 16.8633 | 16.8423 | 16.8237 | 16.807 | 16.7906 | 16.7745 | 16.7588 | 16.6787 | 16.602 | 16.5349 | 18.4091 | 18.4025 | 18.3892 | 18.3749 | 18.361 | 18.3479 | 18.3336 | 18.3194 | 18.3054 | 18.2918 | 18.2783 | 18.2069 | 18.137 | 18.0697
| BURGHMUIR | BURGHMUIR | MINIMUM HEADROOM | NO 08256 23702 | NO | YES | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 11.9485 | 11.028 | 17.0988 | 16.9576 | 16.7745 | 16.5745 | 16.4966 | 16.4783 | 16.4595 | 16.44 | 16.4207 | 16.4009 | 16.3806 | 10.2399 | 8.9714 | 7.8582 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 11.2329 | 10.8695 | 10.4986 | 8.9062 | 7.727 | 6.6985
|  | BURGHMUIR | CT |  |  |  | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 17.1157 | 17.0208 | 16.9031 | 16.7691 | 16.63 | 16.5059 | 16.4931 | 16.4795 | 16.4656 | 16.4508 | 16.4359 | 16.3833 | 11.1813 | 10.4046 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 10.5494 | 9.7823 | 9.0595
|  | BURGHMUIR | LW |  |  |  | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 11.9485 | 11.028 | 17.0988 | 16.9576 | 16.7745 | 16.5745 | 16.4966 | 16.4783 | 16.4595 | 16.44 | 16.4207 | 16.4009 | 16.3806 | 10.2399 | 8.9714 | 7.8582 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 11.2329 | 10.8695 | 10.4986 | 8.9062 | 7.727 | 6.6985
|  | BURGHMUIR | ST |  |  |  | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 17.1512 | 17.1077 | 17.0347 | 16.937 | 16.8528 | 16.7622 | 16.6686 | 16.5679 | 16.5045 | 16.4953 | 16.4858 | 16.4507 | 16.4241 | 16.399 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 11.295 | 10.8362
|  | BURGHMUIR | FS |  |  |  | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 19.2947 | 17.1806 | 17.1763 | 17.1537 | 17.1229 | 17.0932 | 17.0601 | 17.0202 | 16.9803 | 16.9406 | 16.8992 | 16.8561 | 16.636 | 16.5051 | 16.4955 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365 | 16.4365
| CLACHAN | BUTTERBRIDGE | MINIMUM HEADROOM | NN 19306 09936 | YES | YES | 0.10428 | 0.10428 | 0.098655 | 0.096497 | 0.094386 | 0.092321 | 0.0903 | 0.088105 | 0.085926 | 0.083761 | 0.081611 | 0.071157 | 0.060636 | 0.050221 | 0.10287 | 0.099524 | 0.096925 | 0.09438 | 0.091889 | 0.089453 | 0.087071 | 0.084495 | 0.081936 | 0.079394 | 0.07687 | 0.064557 | 0.052163 | 0.039893 | 0.10349 | 0.099747 | 0.097147 | 0.094601 | 0.09211 | 0.089673 | 0.08729 | 0.084713 | 0.082153 | 0.079611 | 0.077086 | 0.064808 | 0.052452 | 0.04022
|  | BUTTERBRIDGE | CT |  |  |  | 0.10428 | 0.10428 | 0.099871 | 0.098362 | 0.096885 | 0.095441 | 0.094029 | 0.092501 | 0.090983 | 0.08947 | 0.087965 | 0.080649 | 0.073286 | 0.065996 | 0.10287 | 0.10287 | 0.09836 | 0.09658 | 0.094838 | 0.093134 | 0.091468 | 0.089665 | 0.087875 | 0.086096 | 0.08433 | 0.075739 | 0.067064 | 0.058477 | 0.10349 | 0.10349 | 0.098583 | 0.096802 | 0.09506 | 0.093355 | 0.091688 | 0.089885 | 0.088094 | 0.086315 | 0.084549 | 0.075956 | 0.067308 | 0.058747
|  | BUTTERBRIDGE | LW |  |  |  | 0.10428 | 0.10428 | 0.098655 | 0.096497 | 0.094386 | 0.092321 | 0.0903 | 0.088105 | 0.085926 | 0.083761 | 0.081611 | 0.071157 | 0.060636 | 0.050221 | 0.10287 | 0.099524 | 0.096925 | 0.09438 | 0.091889 | 0.089453 | 0.087071 | 0.084495 | 0.081936 | 0.079394 | 0.07687 | 0.064557 | 0.052163 | 0.039893 | 0.10349 | 0.099747 | 0.097147 | 0.094601 | 0.09211 | 0.089673 | 0.08729 | 0.084713 | 0.082153 | 0.079611 | 0.077086 | 0.064808 | 0.052452 | 0.04022
|  | BUTTERBRIDGE | ST |  |  |  | 0.10428 | 0.10428 | 0.10428 | 0.10428 | 0.099859 | 0.098902 | 0.097969 | 0.096962 | 0.095972 | 0.094998 | 0.094041 | 0.089405 | 0.084861 | 0.08031 | 0.10295 | 0.10287 | 0.10287 | 0.099504 | 0.098346 | 0.097217 | 0.096116 | 0.094928 | 0.09376 | 0.092611 | 0.091482 | 0.086021 | 0.080686 | 0.075339 | 0.10354 | 0.10349 | 0.10349 | 0.099727 | 0.098569 | 0.09744 | 0.096339 | 0.09515 | 0.093982 | 0.092832 | 0.091703 | 0.08624 | 0.080903 | 0.075558
|  | BUTTERBRIDGE | FS |  |  |  | 0.10428 | 0.10428 | 0.10428 | 0.10428 | 0.10428 | 0.10428 | 0.10428 | 0.10428 | 0.10428 | 0.10428 | 0.10428 | 0.098489 | 0.096785 | 0.095223 | 0.10307 | 0.10304 | 0.10296 | 0.10287 | 0.10287 | 0.10287 | 0.10287 | 0.10287 | 0.099823 | 0.09936 | 0.098904 | 0.096729 | 0.094719 | 0.092877 | 0.10357 | 0.10357 | 0.10354 | 0.10351 | 0.10349 | 0.10349 | 0.10349 | 0.10349 | 0.10349 | 0.099583 | 0.099128 | 0.096951 | 0.094941 | 0.093098
| BRACO | CALLANDER | MINIMUM HEADROOM | NN 62995 07081 | NO | YES | 9.4376 | 7.7514 | 7.737 | 7.7221 | 7.7065 | 7.6905 | 7.6747 | 7.6576 | 7.6361 | 7.5289 | 7.4193 | 6.8177 | 6.204 | 5.5911 | 9.3038 | 9.253 | 9.1878 | 9.1204 | 9.0498 | 8.9882 | 8.9882 | 7.3196 | 7.1934 | 7.067 | 6.9377 | 6.228 | 5.5039 | 4.7809 | 9.2299 | 9.2121 | 9.1894 | 9.1658 | 9.1411 | 7.3454 | 7.2362 | 7.118 | 6.9935 | 6.8687 | 6.7411 | 6.0409 | 5.3265 | 4.6131
|  | CALLANDER | CT |  |  |  | 9.4376 | 7.7542 | 7.7434 | 7.7322 | 7.7204 | 7.7082 | 7.6961 | 7.6831 | 7.6693 | 7.6554 | 7.6412 | 7.1943 | 6.733 | 6.2712 | 9.3059 | 9.2657 | 9.2171 | 9.1663 | 9.1128 | 9.0574 | 9.0029 | 8.9882 | 8.9882 | 7.3044 | 7.2046 | 6.6723 | 6.128 | 5.5832 | 9.2307 | 9.2166 | 9.1996 | 9.1819 | 9.1631 | 9.1438 | 9.1247 | 7.2944 | 7.1988 | 7.1029 | 7.0045 | 6.4792 | 5.9422 | 5.4048
|  | CALLANDER | LW |  |  |  | 9.4376 | 7.7514 | 7.737 | 7.7221 | 7.7065 | 7.6905 | 7.6747 | 7.6576 | 7.6361 | 7.5289 | 7.4193 | 6.8177 | 6.204 | 5.5911 | 9.3038 | 9.253 | 9.1878 | 9.1204 | 9.0498 | 8.9882 | 8.9882 | 7.3196 | 7.1934 | 7.067 | 6.9377 | 6.228 | 5.5039 | 4.7809 | 9.2299 | 9.2121 | 9.1894 | 9.1658 | 9.1411 | 7.3454 | 7.2362 | 7.118 | 6.9935 | 6.8687 | 6.7411 | 6.0409 | 5.3265 | 4.6131
|  | CALLANDER | ST |  |  |  | 9.4376 | 9.4376 | 7.7562 | 7.7487 | 7.7409 | 7.7329 | 7.725 | 7.7164 | 7.7072 | 7.698 | 7.6885 | 7.6321 | 7.3432 | 7.0605 | 9.3193 | 9.3022 | 9.2747 | 9.2407 | 9.2055 | 9.1692 | 9.1334 | 9.0944 | 9.0529 | 9.0113 | 8.9882 | 7.1887 | 6.8479 | 6.5144 | 9.2353 | 9.2293 | 9.2197 | 9.2079 | 9.1956 | 9.1828 | 9.1703 | 9.1567 | 9.1422 | 9.1276 | 7.3318 | 6.9888 | 6.6525 | 6.3235
|  | CALLANDER | FS |  |  |  | 9.4376 | 9.4376 | 9.4376 | 9.4376 | 9.4376 | 7.7589 | 7.7557 | 7.7524 | 7.749 | 7.7455 | 7.742 | 7.7232 | 7.7037 | 7.6838 | 9.3287 | 9.3267 | 9.3197 | 9.311 | 9.2992 | 9.2869 | 9.2725 | 9.2578 | 9.2422 | 9.2266 | 9.2106 | 9.1253 | 9.0373 | 8.9882 | 9.2386 | 9.2379 | 9.2355 | 9.2324 | 9.2283 | 9.224 | 9.219 | 9.2138 | 9.2084 | 9.2029 | 9.1973 | 9.1675 | 9.1367 | 7.2994
| STORNOWAY | CALLANISH | MINIMUM HEADROOM | NB 22040 33554 | YES | YES | 5.7305 | 5.7288 | 5.7266 | 5.7245 | 5.7224 | 5.7203 | 5.7183 | 5.7161 | 5.7139 | 5.7118 | 5.7096 | 5.6948 | 3.6615 | 3.5089 | 5.1294 | 5.1201 | 5.1087 | 5.0976 | 5.0866 | 5.0759 | 5.0653 | 5.0539 | 5.0425 | 5.0313 | 5.0255 | 5.0255 | 3.5982 | 3.4198 | 5.1141 | 5.0923 | 5.0655 | 5.0393 | 5.0182 | 5.0182 | 5.0182 | 5.0182 | 5.0182 | 5.0182 | 5.0182 | 5.0182 | 3.2876 | 3.1099
|  | CALLANISH | CT |  |  |  | 5.7306 | 5.7291 | 5.7275 | 5.7259 | 5.7243 | 5.7227 | 5.7212 | 5.7195 | 5.7179 | 5.7162 | 5.7146 | 5.7009 | 3.7367 | 3.5955 | 5.1296 | 5.122 | 5.1134 | 5.1049 | 5.0966 | 5.0885 | 5.0805 | 5.0718 | 5.0632 | 5.0546 | 5.0461 | 5.0255 | 3.6859 | 3.5212 | 5.1145 | 5.0968 | 5.0765 | 5.0566 | 5.0371 | 5.0182 | 5.0182 | 5.0182 | 5.0182 | 5.0182 | 5.0182 | 5.0182 | 3.3751 | 3.2107
|  | CALLANISH | LW |  |  |  | 5.7305 | 5.7288 | 5.7266 | 5.7245 | 5.7224 | 5.7203 | 5.7183 | 5.7161 | 5.7139 | 5.7118 | 5.7096 | 5.6948 | 3.6615 | 3.5089 | 5.1294 | 5.1201 | 5.1087 | 5.0976 | 5.0866 | 5.0759 | 5.0653 | 5.0539 | 5.0425 | 5.0313 | 5.0255 | 5.0255 | 3.5982 | 3.4198 | 5.1141 | 5.0923 | 5.0655 | 5.0393 | 5.0182 | 5.0182 | 5.0182 | 5.0182 | 5.0182 | 5.0182 | 5.0182 | 5.0182 | 3.2876 | 3.1099
|  | CALLANISH | ST |  |  |  | 5.7314 | 5.7313 | 5.7311 | 5.7309 | 5.7296 | 5.7284 | 5.7272 | 5.7259 | 5.7247 | 5.7234 | 5.7222 | 5.7162 | 5.328 | 5.3222 | 5.1338 | 5.1332 | 5.1323 | 5.1312 | 5.1247 | 5.1183 | 5.1121 | 5.1054 | 5.0987 | 5.0922 | 5.0859 | 5.0546 | 4.8197 | 4.8137 | 5.1245 | 5.1231 | 5.1209 | 5.1183 | 5.103 | 5.088 | 5.0734 | 5.0576 | 5.042 | 5.0268 | 5.0182 | 5.0182 | 4.6406 | 3.983
|  | CALLANISH | FS |  |  |  | 5.7314 | 5.7314 | 5.7311 | 5.7309 | 5.7304 | 5.73 | 5.7294 | 5.7289 | 5.7284 | 5.7278 | 5.7273 | 5.7249 | 5.7226 | 5.7204 | 5.134 | 5.1338 | 5.1326 | 5.1311 | 5.1288 | 5.1266 | 5.1237 | 5.1209 | 5.1181 | 5.1153 | 5.1126 | 5.0998 | 5.0878 | 5.0766 | 5.1248 | 5.1243 | 5.1215 | 5.1181 | 5.1128 | 5.1075 | 5.1007 | 5.094 | 5.0874 | 5.0809 | 5.0746 | 5.0445 | 5.0182 | 5.0182
| TUMMEL BRIDGE | CALVINE | MINIMUM HEADROOM | NN 80186 65270 | YES | YES | 1.8473 | 1.8465 | 1.8455 | 1.8445 | 1.8436 | 1.8427 | 1.8417 | 1.8408 | 1.8398 | 1.8388 | 1.8378 | 1.8309 | 1.824 | 1.8172 | 1.7251 | 1.7211 | 1.7161 | 1.7113 | 1.7065 | 1.7018 | 1.6972 | 1.6923 | 1.6874 | 1.6825 | 1.6776 | 1.6506 | 1.6245 | 1.5988 | 1.6616 | 1.6568 | 1.6509 | 1.6451 | 1.6394 | 1.6338 | 1.6284 | 1.624 | 1.6203 | 1.6165 | 1.6128 | 1.5875 | 1.5765 | 1.5657
|  | CALVINE | CT |  |  |  | 1.8474 | 1.8468 | 1.8461 | 1.8454 | 1.8447 | 1.844 | 1.8434 | 1.8427 | 1.842 | 1.8413 | 1.8406 | 1.8358 | 1.831 | 1.8263 | 1.7254 | 1.7223 | 1.7189 | 1.7154 | 1.7121 | 1.7088 | 1.7056 | 1.7021 | 1.6986 | 1.6952 | 1.6918 | 1.6691 | 1.6509 | 1.633 | 1.6618 | 1.6582 | 1.6541 | 1.65 | 1.646 | 1.6421 | 1.6383 | 1.6342 | 1.63 | 1.6263 | 1.6236 | 1.6051 | 1.5876 | 1.5801
|  | CALVINE | LW |  |  |  | 1.8473 | 1.8465 | 1.8455 | 1.8445 | 1.8436 | 1.8427 | 1.8417 | 1.8408 | 1.8398 | 1.8388 | 1.8378 | 1.8309 | 1.824 | 1.8172 | 1.7251 | 1.7211 | 1.7161 | 1.7113 | 1.7065 | 1.7018 | 1.6972 | 1.6923 | 1.6874 | 1.6825 | 1.6776 | 1.6506 | 1.6245 | 1.5988 | 1.6616 | 1.6568 | 1.6509 | 1.6451 | 1.6394 | 1.6338 | 1.6284 | 1.624 | 1.6203 | 1.6165 | 1.6128 | 1.5875 | 1.5765 | 1.5657
|  | CALVINE | ST |  |  |  | 1.8476 | 1.8473 | 1.8469 | 1.8465 | 1.8458 | 1.8452 | 1.8446 | 1.8439 | 1.8433 | 1.8426 | 1.842 | 1.8388 | 1.8358 | 1.8328 | 1.7264 | 1.7252 | 1.7233 | 1.721 | 1.7177 | 1.7146 | 1.7115 | 1.7081 | 1.7048 | 1.7015 | 1.6983 | 1.6827 | 1.669 | 1.6576 | 1.6631 | 1.6616 | 1.6594 | 1.6567 | 1.6528 | 1.649 | 1.6453 | 1.6413 | 1.6374 | 1.6335 | 1.6297 | 1.6166 | 1.6049 | 1.5933
|  | CALVINE | FS |  |  |  | 1.8477 | 1.8477 | 1.8476 | 1.8475 | 1.8472 | 1.847 | 1.8468 | 1.8465 | 1.8462 | 1.846 | 1.8457 | 1.8445 | 1.8434 | 1.8423 | 1.7271 | 1.727 | 1.7265 | 1.7259 | 1.7248 | 1.7237 | 1.7224 | 1.721 | 1.7197 | 1.7184 | 1.7171 | 1.711 | 1.7054 | 1.7002 | 1.6639 | 1.6638 | 1.6632 | 1.6624 | 1.6611 | 1.6599 | 1.6582 | 1.6567 | 1.6551 | 1.6536 | 1.652 | 1.6448 | 1.638 | 1.6319
| CARRADALE | CAMPBELTOWN | MINIMUM HEADROOM | NR 71509 20746 | NO | YES | 19.1156 | 18.9405 | 18.7644 | 18.5946 | 14.5392 | 14.3927 | 14.252 | 14.165 | 14.1217 | 14.0789 | 14.0368 | 13.7425 | 13.267 | 12.6181 | 16.7422 | 16.601 | 16.4566 | 16.3185 | 16.1861 | 16.058 | 15.948 | 15.9061 | 15.8853 | 15.8647 | 15.8444 | 13.3063 | 12.6438 | 12.0053 | 16.178 | 15.9825 | 15.7837 | 15.593 | 13.6902 | 13.5562 | 13.4274 | 13.3459 | 13.3035 | 13.203 | 13.086 | 12.3339 | 11.5915 | 10.8794
|  | CAMPBELTOWN | CT |  |  |  | 19.1156 | 18.9405 | 18.7644 | 18.5946 | 14.5392 | 14.3927 | 14.252 | 14.165 | 14.1217 | 14.0789 | 14.0368 | 13.7425 | 13.267 | 12.6181 | 16.7422 | 16.601 | 16.4566 | 16.3185 | 16.1861 | 16.058 | 15.948 | 15.9061 | 15.8853 | 15.8647 | 15.8444 | 13.3063 | 12.6438 | 12.0053 | 16.178 | 15.9825 | 15.7837 | 15.593 | 13.6902 | 13.5562 | 13.4274 | 13.3459 | 13.3035 | 13.203 | 13.086 | 12.3339 | 11.5915 | 10.8794
|  | CAMPBELTOWN | LW |  |  |  | 19.4256 | 19.3993 | 19.3698 | 19.3372 | 19.3019 | 19.2642 | 19.2244 | 19.1752 | 19.1247 | 19.073 | 19.0207 | 18.6578 | 14.0908 | 13.1996 | 16.9596 | 16.9224 | 16.8787 | 16.8354 | 16.7922 | 16.7477 | 16.7021 | 16.6486 | 16.5941 | 16.5391 | 16.4839 | 16.188 | 13.1641 | 12.2976 | 16.4941 | 16.45 | 16.3987 | 16.3466 | 16.3014 | 16.2631 | 16.2227 | 16.1728 | 16.1214 | 16.069 | 16.0159 | 13.337 | 12.3807 | 11.4067
|  | CAMPBELTOWN | ST |  |  |  | 19.4706 | 19.4601 | 19.4499 | 19.44 | 19.4279 | 19.4162 | 19.4048 | 19.3933 | 19.3765 | 19.3601 | 19.3441 | 19.2121 | 19.1044 | 19.0024 | 16.9994 | 16.9856 | 16.969 | 16.9523 | 16.9306 | 16.9092 | 16.8882 | 16.8661 | 16.8409 | 16.8165 | 16.7928 | 16.6395 | 16.5042 | 16.3729 | 16.5476 | 16.5309 | 16.5118 | 16.4927 | 16.4682 | 16.4441 | 16.4205 | 16.3958 | 16.377 | 16.3604 | 16.3442 | 16.2102 | 16.1009 | 15.9973
|  | CAMPBELTOWN | FS |  |  |  | 19.4601 | 19.4496 | 19.4342 | 19.4189 | 19.4038 | 19.3889 | 19.3743 | 19.3598 | 19.3456 | 19.3315 | 19.3177 | 19.2347 | 19.1457 | 19.059 | 16.9972 | 16.9884 | 16.9743 | 16.9606 | 16.9455 | 16.9307 | 16.9148 | 16.8992 | 16.8838 | 16.8687 | 16.8539 | 16.7719 | 16.6875 | 16.6063 | 16.5416 | 16.5296 | 16.5108 | 16.4925 | 16.473 | 16.4537 | 16.4336 | 16.4138 | 16.3943 | 16.3752 | 16.3563 | 16.2498 | 16.1428 | 16.0548
| COUPAR ANGUS | CAPUTH | MINIMUM HEADROOM | NO 09277 40265 | NO | YES | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.1495 | 15.1495 | 11.9225 | 14.3484 | 14.2895 | 14.217 | 14.1453 | 14.074 | 14.0044 | 13.9358 | 13.8616 | 13.7948 | 13.7588 | 13.7226 | 13.4216 | 11.6174 | 11.0314 | 14.523 | 14.5077 | 14.4926 | 14.4926 | 14.4926 | 14.4926 | 14.4926 | 14.4926 | 14.4926 | 14.4926 | 14.4926 | 14.4062 | 11.6567 | 11.0718
|  | CAPUTH | CT |  |  |  | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.1495 | 15.1495 | 15.1495 | 14.3574 | 14.3219 | 14.281 | 14.2405 | 14.1998 | 14.1602 | 14.1212 | 14.0789 | 14.0371 | 13.9949 | 13.9523 | 13.6485 | 13.4684 | 11.9152 | 14.5253 | 14.5161 | 14.5055 | 14.495 | 14.4926 | 14.4926 | 14.4926 | 14.4926 | 14.4926 | 14.4926 | 14.4926 | 14.4062 | 14.4062 | 11.954
|  | CAPUTH | LW |  |  |  | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.1495 | 15.1495 | 11.9225 | 14.3484 | 14.2895 | 14.217 | 14.1453 | 14.074 | 14.0044 | 13.9358 | 13.8616 | 13.7948 | 13.7588 | 13.7226 | 13.4216 | 11.6174 | 11.0314 | 14.523 | 14.5077 | 14.4926 | 14.4926 | 14.4926 | 14.4926 | 14.4926 | 14.4926 | 14.4926 | 14.4926 | 14.4926 | 14.4062 | 11.6567 | 11.0718
|  | CAPUTH | ST |  |  |  | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.1916 | 15.1916 | 15.1916 | 14.3673 | 14.3493 | 14.3213 | 14.2876 | 14.2397 | 14.1931 | 14.1474 | 14.0979 | 14.0494 | 14.0011 | 13.953 | 13.7379 | 13.6268 | 13.5179 | 14.5279 | 14.5232 | 14.5159 | 14.5072 | 14.4948 | 14.4926 | 14.4926 | 14.4926 | 14.4926 | 14.4926 | 14.4926 | 14.4494 | 14.4494 | 14.4494
|  | CAPUTH | FS |  |  |  | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 15.2337 | 14.4569 | 14.3759 | 14.3679 | 14.3583 | 14.3424 | 14.3269 | 14.307 | 14.2874 | 14.2682 | 14.2492 | 14.2303 | 14.1393 | 14.0552 | 13.9774 | 14.5511 | 14.5301 | 14.528 | 14.5255 | 14.5214 | 14.5174 | 14.5122 | 14.5072 | 14.5022 | 14.4973 | 14.4926 | 14.4926 | 14.4926 | 14.4926
| ARBROATH | CARNOUSTIE | MINIMUM HEADROOM | NO 55631 35403 | NO | YES | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 13.8338 | 12.9303 | 18.5904 | 18.441 | 18.284 | 18.2305 | 18.218 | 18.2058 | 18.1939 | 18.181 | 18.1681 | 18.1554 | 18.1428 | 13.266 | 12.1654 | 11.0729 | 17.7612 | 17.6742 | 17.595 | 17.5318 | 17.4874 | 17.4874 | 17.4874 | 17.4874 | 17.4874 | 13.7567 | 13.5258 | 12.5073 | 11.4904 | 10.481
|  | CARNOUSTIE | CT |  |  |  | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 14.1757 | 18.5971 | 18.4761 | 18.3382 | 18.2628 | 18.2311 | 18.2217 | 18.2122 | 18.2019 | 18.1919 | 18.1823 | 18.1728 | 18.1326 | 13.3715 | 12.5789 | 17.7651 | 17.6947 | 17.6241 | 17.5764 | 17.5349 | 17.4928 | 17.4874 | 17.4874 | 17.4874 | 17.4874 | 17.4874 | 13.341 | 12.6048 | 11.8725
|  | CARNOUSTIE | LW |  |  |  | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 13.8338 | 12.9303 | 18.5904 | 18.441 | 18.284 | 18.2305 | 18.218 | 18.2058 | 18.1939 | 18.181 | 18.1681 | 18.1554 | 18.1428 | 13.266 | 12.1654 | 11.0729 | 17.7612 | 17.6742 | 17.595 | 17.5318 | 17.4874 | 17.4874 | 17.4874 | 17.4874 | 17.4874 | 13.7567 | 13.5258 | 12.5073 | 11.4904 | 10.481
|  | CARNOUSTIE | ST |  |  |  | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 18.639 | 18.5848 | 18.5069 | 18.4219 | 18.3603 | 18.3003 | 18.2733 | 18.2441 | 18.2314 | 18.2262 | 18.2213 | 18.1966 | 18.1724 | 18.148 | 17.7894 | 17.7579 | 17.7126 | 17.6632 | 17.6324 | 17.6091 | 17.5856 | 17.5602 | 17.5359 | 17.513 | 17.4909 | 17.4874 | 17.4874 | 13.6226
|  | CARNOUSTIE | FS |  |  |  | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 19.7374 | 18.6685 | 18.6574 | 18.6326 | 18.6078 | 18.5865 | 18.5653 | 18.5387 | 18.5128 | 18.4875 | 18.4626 | 18.4384 | 18.3257 | 18.2676 | 18.233 | 17.8066 | 17.8001 | 17.7857 | 17.7713 | 17.7589 | 17.7466 | 17.7311 | 17.716 | 17.7013 | 17.6868 | 17.6728 | 17.6195 | 17.5806 | 17.5432
| KILLIN | CASHLIE | MINIMUM HEADROOM | NN 50711 42144 | YES | YES | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.0537 | 1.0518 | 1.0513 | 1.0509 | 1.0506 | 1.0503 | 1.0503 | 1.0503 | 1.0503 | 1.0503 | 1.0503 | 0.98403 | 0.96411 | 0.94441 | 1.0613 | 1.0613 | 1.0613 | 1.0613 | 1.0613 | 1.0613 | 1.0613 | 1.0613 | 1.0613 | 1.0613 | 1.0613 | 0.99118 | 0.97125 | 0.95155
|  | CASHLIE | CT |  |  |  | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.0539 | 1.0523 | 1.0515 | 1.0512 | 1.051 | 1.0507 | 1.0505 | 1.0503 | 1.0503 | 1.0503 | 1.0503 | 1.0503 | 0.988 | 0.9742 | 1.0613 | 1.0613 | 1.0613 | 1.0613 | 1.0613 | 1.0613 | 1.0613 | 1.0613 | 1.0613 | 1.0613 | 1.0613 | 1.0613 | 0.99515 | 0.98135
|  | CASHLIE | LW |  |  |  | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.0537 | 1.0518 | 1.0513 | 1.0509 | 1.0506 | 1.0503 | 1.0503 | 1.0503 | 1.0503 | 1.0503 | 1.0503 | 0.98403 | 0.96411 | 0.94441 | 1.0613 | 1.0613 | 1.0613 | 1.0613 | 1.0613 | 1.0613 | 1.0613 | 1.0613 | 1.0613 | 1.0613 | 1.0613 | 0.99118 | 0.97125 | 0.95155
|  | CASHLIE | ST |  |  |  | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.0544 | 1.0538 | 1.0528 | 1.0518 | 1.0515 | 1.0513 | 1.0512 | 1.051 | 1.0508 | 1.0507 | 1.0505 | 1.0503 | 1.0503 | 1.0503 | 1.0613 | 1.0613 | 1.0613 | 1.0613 | 1.0613 | 1.0613 | 1.0613 | 1.0613 | 1.0613 | 1.0613 | 1.0613 | 1.0613 | 1.0613 | 1.0613
|  | CASHLIE | FS |  |  |  | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.1068 | 1.0548 | 1.0547 | 1.0544 | 1.0541 | 1.0537 | 1.0534 | 1.0529 | 1.0524 | 1.052 | 1.0517 | 1.0516 | 1.0513 | 1.051 | 1.0507 | 1.0613 | 1.0613 | 1.0613 | 1.0613 | 1.0613 | 1.0613 | 1.0613 | 1.0613 | 1.0613 | 1.0613 | 1.0613 | 1.0613 | 1.0613 | 1.0613
| KILLIN | CHAORACH | MINIMUM HEADROOM | NN 45400 27553 | YES | YES | -2.0501 | -2.0502 | -2.0502 | -2.0503 | -2.0503 | -2.0504 | -2.0504 | -2.0504 | -2.0505 | -2.0505 | -2.0506 | -2.0508 | -2.051 | -2.0512 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.9572 | -1.9577 | -1.9583 | -1.9588 | -1.9594 | -1.9599 | -1.9604 | -1.961 | -1.9616 | -1.9621 | -1.9627 | -1.9654 | -1.9681 | -1.9708
|  | CHAORACH | CT |  |  |  | -2.0501 | -2.0502 | -2.0502 | -2.0502 | -2.0503 | -2.0503 | -2.0503 | -2.0504 | -2.0504 | -2.0504 | -2.0504 | -2.0506 | -2.0507 | -2.0509 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.9572 | -1.9575 | -1.9579 | -1.9583 | -1.9587 | -1.9591 | -1.9595 | -1.9599 | -1.9603 | -1.9606 | -1.961 | -1.9629 | -1.9648 | -1.9667
|  | CHAORACH | LW |  |  |  | -2.0501 | -2.0502 | -2.0502 | -2.0503 | -2.0503 | -2.0504 | -2.0504 | -2.0504 | -2.0505 | -2.0505 | -2.0506 | -2.0508 | -2.051 | -2.0512 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.9572 | -1.9577 | -1.9583 | -1.9588 | -1.9594 | -1.9599 | -1.9604 | -1.961 | -1.9616 | -1.9621 | -1.9627 | -1.9654 | -1.9681 | -1.9708
|  | CHAORACH | ST |  |  |  | -2.0501 | -2.0501 | -2.0502 | -2.0502 | -2.0502 | -2.0502 | -2.0502 | -2.0503 | -2.0503 | -2.0503 | -2.0503 | -2.0504 | -2.0505 | -2.0506 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.9571 | -1.9572 | -1.9574 | -1.9577 | -1.9579 | -1.9582 | -1.9584 | -1.9587 | -1.959 | -1.9592 | -1.9595 | -1.9607 | -1.9618 | -1.963
|  | CHAORACH | FS |  |  |  | -2.0501 | -2.0501 | -2.0501 | -2.0501 | -2.0501 | -2.0502 | -2.0502 | -2.0502 | -2.0502 | -2.0502 | -2.0502 | -2.0502 | -2.0503 | -2.0503 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.6519 | -1.957 | -1.957 | -1.9571 | -1.9571 | -1.9572 | -1.9573 | -1.9574 | -1.9575 | -1.9576 | -1.9577 | -1.9578 | -1.9583 | -1.9587 | -1.9592
| ARBROATH | CHARLES AVENUE | MINIMUM HEADROOM | NO 62954 41097 | NO | YES | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 15.4539 | 15.4448 | 15.4336 | 15.4227 | 15.4119 | 15.4014 | 15.3911 | 15.38 | 15.3689 | 15.3579 | 15.347 | 15.2751 | 15.2035 | 15.1827 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937
|  | CHARLES AVENUE | CT |  |  |  | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 15.4539 | 15.4461 | 15.4371 | 15.4284 | 15.4198 | 15.4114 | 15.4031 | 15.3941 | 15.3852 | 15.3764 | 15.3677 | 15.3139 | 15.2601 | 15.2064 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937
|  | CHARLES AVENUE | LW |  |  |  | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 15.454 | 15.4448 | 15.4336 | 15.4227 | 15.4119 | 15.4014 | 15.3911 | 15.38 | 15.3689 | 15.3579 | 15.347 | 15.2751 | 15.2035 | 15.1827 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937
|  | CHARLES AVENUE | ST |  |  |  | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 15.4571 | 15.4544 | 15.4504 | 15.4456 | 15.4394 | 15.4333 | 15.4274 | 15.421 | 15.4147 | 15.4085 | 15.4025 | 15.3719 | 15.3421 | 15.312 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937
|  | CHARLES AVENUE | FS |  |  |  | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 16.0581 | 15.4585 | 15.4583 | 15.4571 | 15.4558 | 15.4538 | 15.4518 | 15.4492 | 15.4467 | 15.4443 | 15.4418 | 15.4395 | 15.428 | 15.4172 | 15.4068 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937 | 15.7937
| CHARLESTON | CHARLESTON | MINIMUM HEADROOM | NO 35734 31818 | NO | YES | 17.5045 | 17.4973 | 17.4885 | 17.48 | 17.4712 | 17.4619 | 17.4528 | 17.4425 | 17.4313 | 17.4199 | 17.4121 | 17.3512 | 17.3512 | 17.3512 | 16.8066 | 16.7954 | 16.7818 | 16.7688 | 16.755 | 16.7407 | 16.7267 | 16.7107 | 16.6934 | 16.6757 | 16.6584 | 16.5112 | 16.505 | 16.505 | 16.7795 | 16.7695 | 16.7573 | 16.7457 | 16.7334 | 16.7206 | 16.7081 | 16.6938 | 16.6784 | 16.6626 | 16.6471 | 16.6264 | 16.6104 | 16.5951
|  | CHARLESTON | CT |  |  |  | 17.505 | 17.4995 | 17.4933 | 17.4872 | 17.4811 | 17.4754 | 17.4699 | 17.4635 | 17.4556 | 17.4473 | 17.4389 | 17.3761 | 17.3512 | 17.3512 | 16.8073 | 16.7989 | 16.7893 | 16.7799 | 16.7704 | 16.7616 | 16.753 | 16.7432 | 16.7309 | 16.7181 | 16.7052 | 16.5664 | 16.5071 | 16.505 | 16.7801 | 16.7725 | 16.764 | 16.7556 | 16.7472 | 16.7393 | 16.7316 | 16.7229 | 16.7119 | 16.7004 | 16.689 | 16.6347 | 16.6223 | 16.6106
|  | CHARLESTON | LW |  |  |  | 17.5045 | 17.4973 | 17.4885 | 17.48 | 17.4712 | 17.4619 | 17.4528 | 17.4425 | 17.4313 | 17.4199 | 17.4121 | 17.3512 | 17.3512 | 17.3512 | 16.8066 | 16.7954 | 16.7818 | 16.7688 | 16.755 | 16.7407 | 16.7267 | 16.7107 | 16.6934 | 16.6757 | 16.6584 | 16.5112 | 16.505 | 16.505 | 16.7795 | 16.7695 | 16.7573 | 16.7457 | 16.7334 | 16.7206 | 16.7081 | 16.6938 | 16.6784 | 16.6626 | 16.6471 | 16.6264 | 16.6104 | 16.5951
|  | CHARLESTON | ST |  |  |  | 17.5079 | 17.5057 | 17.5023 | 17.4982 | 17.4883 | 17.4787 | 17.4694 | 17.4591 | 17.4479 | 17.4364 | 17.4251 | 17.3887 | 17.3587 | 17.3512 | 16.8119 | 16.8084 | 16.8031 | 16.7969 | 16.7815 | 16.7667 | 16.7523 | 16.7364 | 16.719 | 16.7013 | 16.6838 | 16.5986 | 16.522 | 16.5083 | 16.7842 | 16.7811 | 16.7763 | 16.7707 | 16.757 | 16.7439 | 16.731 | 16.7168 | 16.7013 | 16.6855 | 16.6698 | 16.6377 | 16.6305 | 16.6235
|  | CHARLESTON | FS |  |  |  | 17.51 | 17.5098 | 17.5088 | 17.5077 | 17.5046 | 17.5015 | 17.4975 | 17.4934 | 17.4892 | 17.4849 | 17.4808 | 17.46 | 17.4419 | 17.4258 | 16.8152 | 16.8148 | 16.8133 | 16.8116 | 16.8067 | 16.8019 | 16.7958 | 16.7894 | 16.7828 | 16.7763 | 16.7699 | 16.7377 | 16.7098 | 16.6848 | 16.7871 | 16.7868 | 16.7854 | 16.7839 | 16.7796 | 16.7753 | 16.7698 | 16.7641 | 16.7582 | 16.7524 | 16.7467 | 16.718 | 16.693 | 16.6707
| ARDMORE | CLACHAN | MINIMUM HEADROOM | NF 81863 64360 | YES | YES | 3.1644 | 3.1644 | 3.1644 | 3.1644 | 3.1644 | 3.1644 | 3.1644 | 3.1357 | 3.1061 | 3.0766 | 3.0473 | 2.9065 | 2.7641 | 2.6246 | 4.1933 | 4.1698 | 3.2793 | 3.2455 | 3.2124 | 3.1798 | 3.1478 | 3.1132 | 3.0788 | 3.0446 | 3.0106 | 2.8472 | 2.6819 | 2.5199 | 3.2335 | 3.2128 | 3.1785 | 3.1448 | 3.1117 | 3.0792 | 3.0473 | 3.0128 | 2.9784 | 2.9443 | 2.9104 | 2.7473 | 2.5823 | 2.4207
|  | CLACHAN | CT |  |  |  | 3.1644 | 3.1644 | 3.1644 | 3.1644 | 3.1644 | 3.1644 | 3.1644 | 3.1644 | 3.1644 | 3.1589 | 3.139 | 3.0177 | 2.8951 | 2.7745 | 4.1949 | 4.1778 | 3.2998 | 3.2768 | 3.2543 | 3.2321 | 3.2104 | 3.1868 | 3.1634 | 3.1401 | 3.117 | 2.9761 | 2.8339 | 2.6939 | 3.2336 | 3.2223 | 3.199 | 3.1761 | 3.1536 | 3.1314 | 3.1097 | 3.0862 | 3.0629 | 3.0396 | 3.0166 | 2.876 | 2.734 | 2.5943
|  | CLACHAN | LW |  |  |  | 3.1644 | 3.1644 | 3.1644 | 3.1644 | 3.1644 | 3.1644 | 3.1644 | 3.1357 | 3.1061 | 3.0766 | 3.0473 | 2.9065 | 2.7641 | 2.6246 | 4.1933 | 4.1698 | 3.2793 | 3.2455 | 3.2124 | 3.1798 | 3.1478 | 3.1132 | 3.0788 | 3.0446 | 3.0106 | 2.8472 | 2.6819 | 2.5199 | 3.2335 | 3.2128 | 3.1785 | 3.1448 | 3.1117 | 3.0792 | 3.0473 | 3.0128 | 2.9784 | 2.9443 | 2.9104 | 2.7473 | 2.5823 | 2.4207
|  | CLACHAN | ST |  |  |  | 4.6625 | 4.6625 | 4.6625 | 4.6625 | 4.6625 | 4.6625 | 4.6625 | 4.6625 | 4.6625 | 4.6625 | 4.6625 | 4.6625 | 4.6625 | 4.6625 | 4.535 | 4.5339 | 4.5323 | 4.5304 | 4.5213 | 4.5125 | 4.5038 | 4.4945 | 4.4852 | 4.4762 | 4.4673 | 4.4238 | 4.4007 | 4.3894 | 4.8273 | 4.8273 | 4.8273 | 4.8273 | 4.8273 | 4.8273 | 4.8273 | 4.8273 | 4.8273 | 4.8273 | 4.8273 | 4.8273 | 4.8273 | 4.8273
|  | CLACHAN | FS |  |  |  | 4.6625 | 4.6625 | 4.6625 | 4.6625 | 4.6625 | 4.6625 | 4.6625 | 4.6625 | 4.6625 | 4.6625 | 4.6625 | 4.6625 | 4.6625 | 4.6625 | 4.5355 | 4.5355 | 4.535 | 4.5345 | 4.5315 | 4.5286 | 4.5248 | 4.5211 | 4.5174 | 4.5138 | 4.5103 | 4.4935 | 4.4778 | 4.463 | 4.8273 | 4.8273 | 4.8273 | 4.8273 | 4.8273 | 4.8273 | 4.8273 | 4.8273 | 4.8273 | 4.8273 | 4.8273 | 4.8273 | 4.8273 | 4.8273
| CARRADALE | CLAONAIG | MINIMUM HEADROOM | NR 86915 56467 | YES | YES | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.36959 | 0.3687 | 0.36797 | 0.36741 | 0.36687 | 0.36633 | 0.36581 | 0.36525 | 0.365 | 0.365 | 0.365 | 0.365 | 0.365 | 0.365 | 0.38084 | 0.38068 | 0.38048 | 0.38029 | 0.3801 | 0.37991 | 0.37973 | 0.37953 | 0.37934 | 0.37914 | 0.37905 | 0.37905 | 0.37905 | 0.37905
|  | CLAONAIG | CT |  |  |  | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.36964 | 0.36897 | 0.36829 | 0.3679 | 0.36751 | 0.36714 | 0.36678 | 0.36638 | 0.36599 | 0.3656 | 0.36521 | 0.365 | 0.365 | 0.365 | 0.38086 | 0.38073 | 0.38059 | 0.38045 | 0.38032 | 0.38019 | 0.38006 | 0.37993 | 0.37979 | 0.37965 | 0.37952 | 0.37905 | 0.37905 | 0.37905
|  | CLAONAIG | LW |  |  |  | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.36959 | 0.3687 | 0.36797 | 0.36741 | 0.36687 | 0.36633 | 0.36581 | 0.36525 | 0.365 | 0.365 | 0.365 | 0.365 | 0.365 | 0.365 | 0.38084 | 0.38068 | 0.38048 | 0.38029 | 0.3801 | 0.37991 | 0.37973 | 0.37953 | 0.37934 | 0.37914 | 0.37905 | 0.37905 | 0.37905 | 0.37905
|  | CLAONAIG | ST |  |  |  | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.36987 | 0.3696 | 0.36919 | 0.36869 | 0.36824 | 0.36794 | 0.36765 | 0.36734 | 0.36704 | 0.36673 | 0.36644 | 0.36501 | 0.365 | 0.365 | 0.38097 | 0.38084 | 0.38077 | 0.38068 | 0.38057 | 0.38047 | 0.38037 | 0.38026 | 0.38015 | 0.38005 | 0.37995 | 0.37945 | 0.37905 | 0.37905
|  | CLAONAIG | FS |  |  |  | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.42483 | 0.37002 | 0.37 | 0.36989 | 0.36975 | 0.36956 | 0.36937 | 0.36913 | 0.36889 | 0.36866 | 0.36843 | 0.36828 | 0.36772 | 0.3672 | 0.36672 | 0.38105 | 0.38104 | 0.38098 | 0.38091 | 0.38084 | 0.3808 | 0.38076 | 0.38071 | 0.38067 | 0.38063 | 0.38059 | 0.38039 | 0.38021 | 0.38004
| CLAYHILLS | CLAYHILLS | MINIMUM HEADROOM | NJ 94047 05518 | NO | NO | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 29.5384 | 29.3688 | 29.1966 | 29.0277 | 28.8619 | 28.6989 | 28.5388 | 28.4559 | 28.4246 | 28.3936 | 28.3619 | 28.2962 | 21.7799 | 19.9673 | 29.7522 | 29.4901 | 29.2657 | 29.2657 | 29.2657 | 29.2657 | 29.2657 | 29.2657 | 29.2657 | 29.2657 | 29.2657 | 29.2657 | 29.2657 | 20.5049
|  | CLAYHILLS | CT |  |  |  | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 29.5974 | 29.5205 | 29.4365 | 29.377 | 29.3184 | 29.2608 | 29.2044 | 29.1434 | 29.0829 | 29.0229 | 28.963 | 28.5881 | 28.4272 | 28.3599 | 29.8281 | 29.7291 | 29.6162 | 29.5053 | 29.3962 | 29.2939 | 29.2657 | 29.2657 | 29.2657 | 29.2657 | 29.2657 | 29.2657 | 29.2657 | 29.2657
|  | CLAYHILLS | LW |  |  |  | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 29.5384 | 29.3688 | 29.1966 | 29.0277 | 28.8619 | 28.6989 | 28.5388 | 28.4559 | 28.4246 | 28.3936 | 28.3619 | 28.2962 | 21.7799 | 19.9673 | 29.7522 | 29.4901 | 29.2657 | 29.2657 | 29.2657 | 29.2657 | 29.2657 | 29.2657 | 29.2657 | 29.2657 | 29.2657 | 29.2657 | 29.2657 | 20.5049
|  | CLAYHILLS | ST |  |  |  | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 29.5866 | 29.4959 | 29.3827 | 29.2662 | 29.1672 | 29.0703 | 28.9755 | 28.8732 | 28.7727 | 28.6739 | 28.5765 | 28.4044 | 28.3154 | 28.2962 | 29.8143 | 29.6975 | 29.516 | 29.3031 | 29.2657 | 29.2657 | 29.2657 | 29.2657 | 29.2657 | 29.2657 | 29.2657 | 29.2657 | 29.2657 | 29.2657
|  | CLAYHILLS | FS |  |  |  | 33.0248 | 33.0182 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 32.9921 | 29.6415 | 29.6359 | 29.6042 | 29.5667 | 29.524 | 29.4817 | 29.4328 | 29.396 | 29.3599 | 29.3245 | 29.2899 | 29.1237 | 28.9644 | 28.8118 | 29.8848 | 29.8777 | 29.8369 | 29.7886 | 29.7336 | 29.6792 | 29.6094 | 29.5408 | 29.4736 | 29.4076 | 29.344 | 29.2657 | 29.2657 | 29.2657
| MYBSTER | COLDBACKIE | MINIMUM HEADROOM | NC 62182 59590 | YES | YES | 1.4597 | 1.4594 | 1.4591 | 1.4587 | 1.4584 | 1.4581 | 1.4578 | 1.4573 | 1.4568 | 1.4562 | 1.4557 | 1.4555 | 1.4555 | 1.4555 | 1.4344 | 1.4321 | 1.4295 | 1.4278 | 1.4262 | 1.4246 | 1.423 | 1.4207 | 1.418 | 1.4154 | 1.4128 | 1.3793 | 1.371 | 0.94526 | 1.564 | 1.5624 | 1.5603 | 1.5583 | 1.5564 | 1.5545 | 1.5526 | 1.5499 | 1.5467 | 1.5436 | 1.5405 | 1.5118 | 1.4972 | 1.4944
|  | COLDBACKIE | CT |  |  |  | 1.4597 | 1.4595 | 1.4593 | 1.459 | 1.4588 | 1.4586 | 1.4584 | 1.4581 | 1.4579 | 1.4576 | 1.4574 | 1.4555 | 1.4555 | 1.4555 | 1.4345 | 1.4328 | 1.4308 | 1.4293 | 1.4281 | 1.427 | 1.4259 | 1.4247 | 1.4235 | 1.4223 | 1.4212 | 1.394 | 1.371 | 1.371 | 1.5641 | 1.5629 | 1.5614 | 1.56 | 1.5587 | 1.5573 | 1.556 | 1.5546 | 1.5532 | 1.5518 | 1.5504 | 1.5212 | 1.5036 | 1.4966
|  | COLDBACKIE | LW |  |  |  | 1.4597 | 1.4594 | 1.4591 | 1.4587 | 1.4584 | 1.4581 | 1.4578 | 1.4574 | 1.4571 | 1.4567 | 1.4564 | 1.4555 | 1.4555 | 1.4555 | 1.4344 | 1.4321 | 1.4295 | 1.4278 | 1.4262 | 1.4246 | 1.423 | 1.4213 | 1.4196 | 1.4179 | 1.4162 | 1.3793 | 1.371 | 0.94526 | 1.564 | 1.5624 | 1.5603 | 1.5583 | 1.5564 | 1.5545 | 1.5526 | 1.5506 | 1.5486 | 1.5466 | 1.5446 | 1.5118 | 1.4972 | 1.4944
|  | COLDBACKIE | ST |  |  |  | 1.4598 | 1.4597 | 1.4596 | 1.4594 | 1.4589 | 1.4584 | 1.4579 | 1.4573 | 1.4568 | 1.4562 | 1.4557 | 1.4555 | 1.4555 | 1.4555 | 1.4351 | 1.4344 | 1.4334 | 1.4321 | 1.4286 | 1.426 | 1.4235 | 1.4207 | 1.418 | 1.4154 | 1.4128 | 1.4001 | 1.3875 | 1.3749 | 1.5646 | 1.5641 | 1.5633 | 1.5623 | 1.5592 | 1.5561 | 1.5531 | 1.5499 | 1.5467 | 1.5436 | 1.5405 | 1.5255 | 1.517 | 1.509
|  | COLDBACKIE | FS |  |  |  | 1.4599 | 1.4598 | 1.4598 | 1.4598 | 1.4595 | 1.4593 | 1.4591 | 1.4588 | 1.4585 | 1.4582 | 1.458 | 1.4568 | 1.4556 | 1.4555 | 1.4355 | 1.4355 | 1.4352 | 1.4348 | 1.433 | 1.4313 | 1.4294 | 1.428 | 1.4267 | 1.4254 | 1.4241 | 1.418 | 1.4123 | 1.4069 | 1.5649 | 1.5648 | 1.5646 | 1.5643 | 1.563 | 1.5618 | 1.5601 | 1.5585 | 1.557 | 1.5554 | 1.5539 | 1.5467 | 1.5399 | 1.5335
| DUNOON | COLINTRAIVE | MINIMUM HEADROOM | NS 03209 74814 | YES | YES | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.55315 | 0.55257 | 0.55201 | 0.55164 | 0.55128 | 0.55093 | 0.55059 | 0.55022 | 0.54985 | 0.5496 | 0.5496 | 0.5496 | 0.5496 | 0.5496 | 0.56171 | 0.5616 | 0.56147 | 0.56134 | 0.56121 | 0.56109 | 0.56097 | 0.56084 | 0.56072 | 0.56059 | 0.56046 | 0.56033 | 0.56033 | 0.56033
|  | COLINTRAIVE | CT |  |  |  | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.55319 | 0.55275 | 0.55225 | 0.55196 | 0.55171 | 0.55146 | 0.55122 | 0.55096 | 0.55071 | 0.55045 | 0.5502 | 0.5496 | 0.5496 | 0.5496 | 0.56173 | 0.56163 | 0.56154 | 0.56145 | 0.56136 | 0.56128 | 0.56119 | 0.5611 | 0.56101 | 0.56092 | 0.56084 | 0.56041 | 0.56033 | 0.56033
|  | COLINTRAIVE | LW |  |  |  | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.55315 | 0.55257 | 0.55201 | 0.55164 | 0.55128 | 0.55093 | 0.55059 | 0.55022 | 0.54985 | 0.5496 | 0.5496 | 0.5496 | 0.5496 | 0.5496 | 0.56171 | 0.5616 | 0.56147 | 0.56134 | 0.56121 | 0.56109 | 0.56097 | 0.56084 | 0.56072 | 0.56059 | 0.56046 | 0.56033 | 0.56033 | 0.56033
|  | COLINTRAIVE | ST |  |  |  | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.55334 | 0.55316 | 0.55289 | 0.55257 | 0.55225 | 0.55205 | 0.55189 | 0.55172 | 0.55155 | 0.55139 | 0.55123 | 0.55044 | 0.54967 | 0.5496 | 0.5618 | 0.56172 | 0.56165 | 0.56159 | 0.56154 | 0.56148 | 0.56143 | 0.56137 | 0.56131 | 0.56125 | 0.56119 | 0.56092 | 0.56065 | 0.56039
|  | COLINTRAIVE | FS |  |  |  | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.59526 | 0.55344 | 0.55343 | 0.55335 | 0.55326 | 0.55315 | 0.55305 | 0.55292 | 0.55278 | 0.55265 | 0.55253 | 0.5524 | 0.55198 | 0.55169 | 0.55143 | 0.56185 | 0.56184 | 0.56181 | 0.56176 | 0.56171 | 0.56168 | 0.56166 | 0.56163 | 0.56161 | 0.56159 | 0.56156 | 0.56146 | 0.56136 | 0.56126
| STORNOWAY | COLL | MINIMUM HEADROOM | NB 47510 40182 | YES | YES | 3.884 | 3.8725 | 3.8582 | 3.8443 | 3.8306 | 3.8225 | 2.4003 | 2.2511 | 2.1027 | 1.9553 | 1.8087 | 0.66585 | 0.31576 | -0.028395 | 3.9119 | 3.875 | 2.4733 | 2.3024 | 2.1347 | 1.9698 | 1.8077 | 1.6324 | 1.458 | 1.2847 | 1.1125 | 0.11859 | -0.2928 | -0.69721 | 3.5369 | 3.5048 | 3.4653 | 2.4818 | 2.3256 | 2.1721 | 2.0214 | 1.8581 | 1.6958 | 1.5277 | 1.3593 | 0.13787 | -0.26443 | -0.65991
|  | COLL | CT |  |  |  | 3.885 | 3.8767 | 3.8672 | 3.8579 | 3.8487 | 3.8397 | 3.8309 | 3.8225 | 2.4834 | 2.3851 | 2.2873 | 1.24 | 0.98648 | 0.73734 | 3.9149 | 3.8885 | 3.8582 | 2.4688 | 2.3569 | 2.2468 | 2.1387 | 2.0217 | 1.9054 | 1.7898 | 1.6749 | 0.79325 | 0.49536 | 0.20259 | 3.5395 | 3.5165 | 3.4902 | 3.4643 | 3.44 | 2.43 | 2.3294 | 2.2205 | 2.1122 | 2.0047 | 1.8977 | 0.79603 | 0.50632 | 0.22002
|  | COLL | LW |  |  |  | 3.884 | 3.8725 | 3.8582 | 3.8443 | 3.8306 | 3.8225 | 2.4003 | 2.2511 | 2.1027 | 1.9553 | 1.8087 | 0.66585 | 0.31576 | -0.028395 | 3.9119 | 3.875 | 2.4733 | 2.3024 | 2.1347 | 1.9698 | 1.8077 | 1.6324 | 1.458 | 1.2847 | 1.1125 | 0.11859 | -0.2928 | -0.69721 | 3.5369 | 3.5048 | 3.4653 | 2.4818 | 2.3256 | 2.1721 | 2.0214 | 1.8581 | 1.6958 | 1.5277 | 1.3593 | 0.13787 | -0.26443 | -0.65991
|  | COLL | ST |  |  |  | 3.8878 | 3.8845 | 3.8792 | 3.873 | 3.8702 | 3.8675 | 3.8649 | 3.862 | 3.8592 | 3.8565 | 3.8538 | 2.3836 | 2.2465 | 2.1101 | 3.9241 | 3.9134 | 3.8966 | 3.8766 | 3.8679 | 3.8593 | 3.8508 | 3.8418 | 2.4853 | 2.4516 | 2.4185 | 1.9626 | 1.8015 | 1.6412 | 3.5474 | 3.5381 | 3.5236 | 3.5062 | 3.4985 | 3.4911 | 3.4837 | 3.4758 | 3.4681 | 3.4604 | 3.4529 | 2.0249 | 1.875 | 1.7258
|  | COLL | FS |  |  |  | 3.8897 | 3.8895 | 3.888 | 3.8862 | 3.8852 | 3.8843 | 3.883 | 3.8818 | 3.8806 | 3.8794 | 3.8783 | 3.8728 | 3.8677 | 3.8629 | 3.9301 | 3.9293 | 3.9245 | 3.9188 | 3.9157 | 3.9126 | 3.9087 | 3.9048 | 3.901 | 3.8973 | 3.8936 | 3.8761 | 3.8598 | 3.8444 | 3.5527 | 3.552 | 3.5478 | 3.5428 | 3.5401 | 3.5375 | 3.534 | 3.5307 | 3.5274 | 3.5241 | 3.5209 | 3.5058 | 3.4915 | 3.4782
| CLAYHILLS | COMMERCE STREET | MINIMUM HEADROOM | NJ 94816 06282 | NO | NO | 32.3008 | 32.262 | 32.2145 | 32.168 | 32.1276 | 32.1152 | 32.1031 | 32.09 | 32.077 | 32.0641 | 32.0508 | 31.9775 | 31.9033 | 31.8299 | 30.0796 | 30.0334 | 29.9768 | 29.9214 | 29.8672 | 29.8141 | 29.7622 | 29.7061 | 29.6504 | 29.5951 | 29.5385 | 29.2245 | 28.9109 | 28.6025 | 27.3095 | 27.2889 | 27.2637 | 27.2389 | 27.2147 | 27.1911 | 27.1679 | 27.1429 | 27.118 | 27.0934 | 27.0681 | 26.928 | 26.786 | 26.6816
|  | COMMERCE STREET | CT |  |  |  | 32.3032 | 32.2742 | 32.2411 | 32.2087 | 32.1769 | 32.1458 | 32.1256 | 32.1164 | 32.1073 | 32.0983 | 32.0893 | 32.04 | 31.9902 | 31.9413 | 30.0824 | 30.0479 | 30.0084 | 29.9698 | 29.932 | 29.895 | 29.8587 | 29.8195 | 29.7806 | 29.742 | 29.7035 | 29.4922 | 29.2787 | 29.0706 | 27.3108 | 27.2954 | 27.2778 | 27.2606 | 27.2437 | 27.2271 | 27.211 | 27.1935 | 27.1761 | 27.1589 | 27.1417 | 27.0474 | 26.9522 | 26.8586
|  | COMMERCE STREET | LW |  |  |  | 32.3008 | 32.262 | 32.2145 | 32.168 | 32.1276 | 32.1152 | 32.1031 | 32.09 | 32.077 | 32.0641 | 32.0508 | 31.9775 | 31.9033 | 31.8299 | 30.0796 | 30.0334 | 29.9768 | 29.9214 | 29.8672 | 29.8141 | 29.7622 | 29.7061 | 29.6504 | 29.5951 | 29.5385 | 29.2245 | 28.9109 | 28.6025 | 27.3095 | 27.2889 | 27.2637 | 27.2389 | 27.2147 | 27.1911 | 27.1679 | 27.1429 | 27.118 | 27.0934 | 27.0681 | 26.928 | 26.786 | 26.6816
|  | COMMERCE STREET | ST |  |  |  | 32.3133 | 32.3016 | 32.2833 | 32.2616 | 32.235 | 32.2091 | 32.1837 | 32.1563 | 32.1295 | 32.1221 | 32.1149 | 32.0782 | 32.0422 | 32.0066 | 30.0944 | 30.0805 | 30.0588 | 30.0329 | 30.0012 | 29.9703 | 29.94 | 29.9074 | 29.8753 | 29.8438 | 29.8127 | 29.6556 | 29.5014 | 29.3489 | 27.3162 | 27.3099 | 27.3002 | 27.2887 | 27.2746 | 27.2607 | 27.2473 | 27.2327 | 27.2184 | 27.2043 | 27.1905 | 27.1203 | 27.0515 | 26.9835
|  | COMMERCE STREET | FS |  |  |  | 32.4522 | 32.3191 | 32.314 | 32.3079 | 32.2998 | 32.2918 | 32.2815 | 32.2714 | 32.2614 | 32.2517 | 32.2421 | 32.1962 | 32.1525 | 32.1244 | 30.26 | 30.1014 | 30.0953 | 30.088 | 30.0784 | 30.0688 | 30.0566 | 30.0445 | 30.0326 | 30.021 | 30.0097 | 29.955 | 29.9029 | 29.8537 | 27.39 | 27.3193 | 27.3165 | 27.3133 | 27.309 | 27.3047 | 27.2993 | 27.2939 | 27.2886 | 27.2834 | 27.2783 | 27.2539 | 27.2307 | 27.2088
| ST FILLANS | COMRIE | MINIMUM HEADROOM | NN 76887 22417 | YES | NO | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.04905 | 0.045173 | 0.041335 | 0.056709 | 0.056355 | 0.056172 | 0.05615 | 0.05615 | 0.05615 | 0.049909 | 0.048959 | 0.048016 | 0.047079 | 0.046148 | 0.041625 | 0.037073 | 0.032567 | 0.057686 | 0.057647 | 0.057647 | 0.057647 | 0.057647 | 0.057647 | 0.057647 | 0.057647 | 0.049323 | 0.04841 | 0.047504 | 0.042979 | 0.038426 | 0.033918
|  | COMRIE | CT |  |  |  | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.049835 | 0.047148 | 0.056731 | 0.056446 | 0.05622 | 0.056161 | 0.05615 | 0.05615 | 0.05615 | 0.05615 | 0.05615 | 0.04955 | 0.048898 | 0.045732 | 0.042546 | 0.039392 | 0.057697 | 0.057647 | 0.057647 | 0.057647 | 0.057647 | 0.057647 | 0.057647 | 0.057647 | 0.057647 | 0.057647 | 0.057647 | 0.047087 | 0.0439 | 0.040745
|  | COMRIE | LW |  |  |  | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.04905 | 0.045173 | 0.041335 | 0.056709 | 0.056355 | 0.056172 | 0.05615 | 0.05615 | 0.05615 | 0.049909 | 0.048959 | 0.048016 | 0.047079 | 0.046148 | 0.041625 | 0.037073 | 0.032567 | 0.057686 | 0.057647 | 0.057647 | 0.057647 | 0.057647 | 0.057647 | 0.057647 | 0.057647 | 0.049323 | 0.04841 | 0.047504 | 0.042979 | 0.038426 | 0.033918
|  | COMRIE | ST |  |  |  | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.056833 | 0.056716 | 0.056534 | 0.056352 | 0.056219 | 0.056182 | 0.05615 | 0.05615 | 0.05615 | 0.05615 | 0.05615 | 0.049522 | 0.047555 | 0.045585 | 0.057747 | 0.05769 | 0.057647 | 0.057647 | 0.057647 | 0.057647 | 0.057647 | 0.057647 | 0.057647 | 0.057647 | 0.057647 | 0.057647 | 0.048874 | 0.04694
|  | COMRIE | FS |  |  |  | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.062593 | 0.056899 | 0.056891 | 0.05684 | 0.056779 | 0.056709 | 0.056639 | 0.05655 | 0.056462 | 0.056397 | 0.056332 | 0.05627 | 0.056166 | 0.05615 | 0.05615 | 0.057779 | 0.057775 | 0.05775 | 0.057721 | 0.057687 | 0.057653 | 0.057647 | 0.057647 | 0.057647 | 0.057647 | 0.057647 | 0.057647 | 0.057647 | 0.057647
| TAYNUILT | CONNEL | MINIMUM HEADROOM | NM 91213 33970 | YES | YES | 2.2145 | 2.2145 | 2.2145 | 2.2145 | 2.2145 | 2.2145 | 2.2145 | 2.2145 | 2.2145 | 2.2145 | 2.2145 | 0.81054 | 0.63732 | 0.46689 | 1.8444 | 1.8372 | 1.8282 | 1.819 | 1.8096 | 1.7999 | 1.7912 | 1.7834 | 1.7757 | 1.7643 | 1.7531 | 0.6404 | 0.45002 | 0.26048 | 1.7475 | 1.7464 | 1.7451 | 1.7437 | 1.7423 | 1.7409 | 1.7405 | 1.7405 | 1.7405 | 1.7405 | 1.7405 | 0.65516 | 0.45821 | 0.26443
|  | CONNEL | CT |  |  |  | 2.2145 | 2.2145 | 2.2145 | 2.2145 | 2.2145 | 2.2145 | 2.2145 | 2.2145 | 2.2145 | 2.2145 | 2.2145 | 0.86223 | 0.72828 | 0.59653 | 1.8444 | 1.8379 | 1.8303 | 1.8224 | 1.8143 | 1.8061 | 1.7984 | 1.7913 | 1.7841 | 1.777 | 1.7703 | 0.6972 | 0.54999 | 0.40519 | 1.7475 | 1.7465 | 1.7454 | 1.7442 | 1.743 | 1.7418 | 1.7406 | 1.7405 | 1.7405 | 1.7405 | 1.7405 | 0.71393 | 0.56163 | 0.41182
|  | CONNEL | LW |  |  |  | 2.2145 | 2.2145 | 2.2145 | 2.2145 | 2.2145 | 2.2145 | 2.2145 | 2.2145 | 2.2145 | 2.2145 | 2.2145 | 0.81054 | 0.63732 | 0.46689 | 1.8445 | 1.8372 | 1.8282 | 1.819 | 1.8096 | 1.7999 | 1.7912 | 1.7834 | 1.7757 | 1.7681 | 1.7606 | 0.6404 | 0.45002 | 0.26048 | 1.7475 | 1.7464 | 1.7451 | 1.7437 | 1.7423 | 1.7409 | 1.7405 | 1.7405 | 1.7405 | 1.7405 | 1.7405 | 0.65516 | 0.45821 | 0.26443
|  | CONNEL | ST |  |  |  | 2.2145 | 2.2145 | 2.2145 | 2.2145 | 2.2145 | 2.2145 | 2.2145 | 2.2145 | 2.2145 | 2.2145 | 2.2145 | 2.0234 | 2.0234 | 0.94828 | 1.8472 | 1.8447 | 1.841 | 1.8366 | 1.8241 | 1.8118 | 1.7999 | 1.7879 | 1.776 | 1.7643 | 1.7531 | 0.90067 | 0.81943 | 0.73862 | 1.7479 | 1.7475 | 1.747 | 1.7463 | 1.7445 | 1.7426 | 1.7409 | 1.7405 | 1.7405 | 1.7405 | 1.7405 | 0.94683 | 0.86278 | 0.77918
|  | CONNEL | FS |  |  |  | 2.2145 | 2.2145 | 2.2145 | 2.2145 | 2.2145 | 2.2145 | 2.2145 | 2.2145 | 2.2145 | 2.2145 | 2.2145 | 2.2145 | 2.2145 | 2.2145 | 1.8487 | 1.8481 | 1.8469 | 1.8454 | 1.8412 | 1.837 | 1.8319 | 1.8272 | 1.8225 | 1.8179 | 1.8135 | 1.7926 | 1.7733 | 1.7552 | 1.7481 | 1.748 | 1.7478 | 1.7476 | 1.747 | 1.7464 | 1.7456 | 1.7449 | 1.7442 | 1.7435 | 1.7429 | 1.7405 | 1.7405 | 1.7405
| BEAULY | CONON BRIDGE | MINIMUM HEADROOM | NH 54996 55499 | NO | YES | 8.6629 | 8.6629 | 8.6629 | 8.6629 | 8.6629 | 8.6629 | 8.6629 | 8.6629 | 8.6629 | 6.2902 | 6.1955 | 5.4717 | 4.9814 | 4.5016 | 7.6561 | 7.6117 | 7.6007 | 7.5934 | 5.9604 | 5.8346 | 5.6712 | 5.5403 | 5.4095 | 5.2867 | 5.1651 | 4.4459 | 3.855 | 3.2767 | 7.8379 | 7.8242 | 7.8242 | 7.8242 | 7.8242 | 7.8242 | 5.8565 | 5.729 | 5.6016 | 5.4819 | 5.3635 | 4.5672 | 3.9916 | 3.4284
|  | CONON BRIDGE | CT |  |  |  | 8.6629 | 8.6629 | 8.6629 | 8.6629 | 8.6629 | 8.6629 | 8.6629 | 8.6629 | 8.6629 | 6.2902 | 6.1955 | 5.485 | 5.125 | 4.7709 | 7.6561 | 7.6117 | 7.6007 | 7.5934 | 5.9604 | 5.8346 | 5.6712 | 5.5403 | 5.4095 | 5.2867 | 5.1651 | 4.4619 | 4.028 | 3.6013 | 7.8379 | 7.8242 | 7.8242 | 7.8242 | 7.8242 | 7.8242 | 5.8565 | 5.729 | 5.6016 | 5.4819 | 5.3635 | 4.5828 | 4.1602 | 3.7446
|  | CONON BRIDGE | LW |  |  |  | 8.6629 | 8.6629 | 8.6629 | 8.6629 | 8.6629 | 8.6629 | 8.6629 | 8.6629 | 8.6629 | 8.6629 | 6.3001 | 5.4717 | 4.9814 | 4.5016 | 7.6593 | 7.6162 | 7.6018 | 7.5947 | 7.5893 | 5.8913 | 5.7455 | 5.6316 | 5.5183 | 5.4081 | 5.2993 | 4.4459 | 3.855 | 3.2767 | 7.8398 | 7.8242 | 7.8242 | 7.8242 | 7.8242 | 7.8242 | 5.9289 | 5.8179 | 5.7075 | 5.6002 | 5.4942 | 4.5672 | 3.9916 | 3.4284
|  | CONON BRIDGE | ST |  |  |  | 8.6629 | 8.6629 | 8.6629 | 8.6629 | 8.6629 | 8.6629 | 8.6629 | 8.6629 | 8.6629 | 8.6629 | 8.6629 | 8.4982 | 6.2462 | 6.0501 | 7.6722 | 7.6538 | 7.6425 | 7.6253 | 7.6114 | 7.6039 | 7.5996 | 7.5965 | 7.5934 | 7.5907 | 5.9717 | 5.579 | 5.3251 | 5.0735 | 7.8476 | 7.8365 | 7.8298 | 7.8242 | 7.8242 | 7.8242 | 7.8242 | 7.8242 | 7.8242 | 7.8242 | 7.8242 | 5.7188 | 5.4715 | 5.2264
|  | CONON BRIDGE | FS |  |  |  | 8.6629 | 8.6629 | 8.6629 | 8.6629 | 8.6629 | 8.6629 | 8.6629 | 8.6629 | 8.6629 | 8.6629 | 8.6629 | 8.6629 | 8.6629 | 8.6629 | 7.6796 | 7.6724 | 7.6684 | 7.6623 | 7.6571 | 7.6519 | 7.6434 | 7.6371 | 7.631 | 7.6249 | 7.6191 | 7.6034 | 7.5988 | 7.5943 | 7.852 | 7.8477 | 7.8453 | 7.8416 | 7.8385 | 7.8354 | 7.8303 | 7.8266 | 7.8242 | 7.8242 | 7.8242 | 7.8242 | 7.8242 | 7.8242
| GRUDIE BRIDGE | CONON FALLS | MINIMUM HEADROOM | NH 38745 57593 | YES | YES | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.73504 | 0.73425 | 0.73328 | 0.73234 | 0.73142 | 0.73051 | 0.72963 | 0.72868 | 0.72773 | 0.72679 | 0.72586 | 0.71752 | 0.71234 | 0.71129 | 0.71007 | 0.70976 | 0.70938 | 0.70901 | 0.70865 | 0.70829 | 0.70795 | 0.70757 | 0.7072 | 0.70683 | 0.70646 | 0.70317 | 0.70064 | 0.70038
|  | CONON FALLS | CT |  |  |  | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.73508 | 0.73449 | 0.73381 | 0.73315 | 0.73251 | 0.73187 | 0.73125 | 0.73058 | 0.72992 | 0.72926 | 0.72861 | 0.72201 | 0.71624 | 0.7129 | 0.71009 | 0.70986 | 0.70959 | 0.70933 | 0.70908 | 0.70883 | 0.70858 | 0.70832 | 0.70806 | 0.7078 | 0.70754 | 0.70478 | 0.70277 | 0.70097
|  | CONON FALLS | LW |  |  |  | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.73504 | 0.73425 | 0.73328 | 0.73234 | 0.73142 | 0.73051 | 0.72963 | 0.72868 | 0.72773 | 0.72679 | 0.72586 | 0.71752 | 0.71234 | 0.71129 | 0.71007 | 0.70976 | 0.70938 | 0.70901 | 0.70865 | 0.70829 | 0.70795 | 0.70757 | 0.7072 | 0.70683 | 0.70646 | 0.70317 | 0.70064 | 0.70038
|  | CONON FALLS | ST |  |  |  | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.73529 | 0.73505 | 0.73468 | 0.73424 | 0.73333 | 0.73245 | 0.73158 | 0.73065 | 0.72973 | 0.72883 | 0.72795 | 0.72366 | 0.72019 | 0.71674 | 0.71017 | 0.71008 | 0.70993 | 0.70976 | 0.7094 | 0.70905 | 0.70871 | 0.70835 | 0.70799 | 0.70763 | 0.70728 | 0.70558 | 0.70401 | 0.70293
|  | CONON FALLS | FS |  |  |  | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.80698 | 0.73543 | 0.73541 | 0.7353 | 0.73518 | 0.73488 | 0.73459 | 0.7342 | 0.73383 | 0.73347 | 0.73311 | 0.73276 | 0.73108 | 0.72951 | 0.72803 | 0.71023 | 0.71022 | 0.71018 | 0.71013 | 0.71001 | 0.7099 | 0.70975 | 0.7096 | 0.70946 | 0.70931 | 0.70918 | 0.70852 | 0.7079 | 0.70732
| DUDHOPE | CONSTABLE STREET | MINIMUM HEADROOM | NO 40903 30821 | NO | NO | 36.8551 | 36.7816 | 36.7195 | 36.7025 | 36.7025 | 36.7025 | 36.7025 | 36.7025 | 36.7025 | 36.7025 | 36.7025 | 36.7025 | 36.7025 | 36.7025 | 34.5084 | 34.3887 | 34.2877 | 34.2159 | 34.1437 | 34.0702 | 33.9982 | 33.9174 | 33.8327 | 33.7482 | 33.6656 | 33.5313 | 33.5313 | 33.5313 | 36.1376 | 36.0968 | 36.0623 | 36.0379 | 36.0132 | 36.0023 | 36.0023 | 36.0023 | 36.0023 | 36.0023 | 36.0023 | 36.0023 | 36.0023 | 36.0023
|  | CONSTABLE STREET | CT |  |  |  | 36.8609 | 36.7976 | 36.7484 | 36.7133 | 36.7025 | 36.7025 | 36.7025 | 36.7025 | 36.7025 | 36.7025 | 36.7025 | 36.7025 | 36.7025 | 36.7025 | 34.5178 | 34.4147 | 34.3347 | 34.2776 | 34.2153 | 34.1448 | 34.0745 | 34.005 | 33.9346 | 33.866 | 33.799 | 33.6056 | 33.5525 | 33.5313 | 36.1408 | 36.1057 | 36.0784 | 36.0589 | 36.0377 | 36.0136 | 36.0023 | 36.0023 | 36.0023 | 36.0023 | 36.0023 | 36.0023 | 36.0023 | 36.0023
|  | CONSTABLE STREET | LW |  |  |  | 36.8551 | 36.7816 | 36.7195 | 36.7025 | 36.7025 | 36.7025 | 36.7025 | 36.7025 | 36.7025 | 36.7025 | 36.7025 | 36.7025 | 36.7025 | 36.7025 | 34.5084 | 34.3887 | 34.2877 | 34.2159 | 34.1437 | 34.0702 | 33.9982 | 33.9174 | 33.8327 | 33.7482 | 33.6656 | 33.5313 | 33.5313 | 33.5313 | 36.1376 | 36.0968 | 36.0623 | 36.0379 | 36.0132 | 36.0023 | 36.0023 | 36.0023 | 36.0023 | 36.0023 | 36.0023 | 36.0023 | 36.0023 | 36.0023
|  | CONSTABLE STREET | ST |  |  |  | 36.8797 | 36.8376 | 36.7968 | 36.7588 | 36.7025 | 36.7025 | 36.7025 | 36.7025 | 36.7025 | 36.7025 | 36.7025 | 36.7025 | 36.7025 | 36.7025 | 34.5484 | 34.4799 | 34.4135 | 34.3517 | 34.2586 | 34.1612 | 34.0651 | 33.9655 | 33.8662 | 33.7693 | 33.6745 | 33.5696 | 33.5313 | 33.5313 | 36.1513 | 36.1279 | 36.1053 | 36.0842 | 36.0524 | 36.0192 | 36.0023 | 36.0023 | 36.0023 | 36.0023 | 36.0023 | 36.0023 | 36.0023 | 36.0023
|  | CONSTABLE STREET | FS |  |  |  | 36.9043 | 36.8905 | 36.8788 | 36.8707 | 36.8529 | 36.8355 | 36.8141 | 36.7925 | 36.7707 | 36.749 | 36.7283 | 36.7025 | 36.7025 | 36.7025 | 34.5885 | 34.5661 | 34.547 | 34.5337 | 34.5048 | 34.4765 | 34.4416 | 34.4064 | 34.3709 | 34.3357 | 34.302 | 34.1432 | 34.0021 | 33.874 | 36.165 | 36.1573 | 36.1508 | 36.1463 | 36.1364 | 36.1267 | 36.1149 | 36.1029 | 36.0907 | 36.0787 | 36.0672 | 36.0131 | 36.0023 | 36.0023
| ALNESS | CONTULLICH | MINIMUM HEADROOM | NN 59226 32752 | YES | YES | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.11279 | 0.11268 | 0.11255 | 0.11241 | 0.11228 | 0.11216 | 0.11203 | 0.11193 | 0.11183 | 0.11173 | 0.11163 | 0.11148 | 0.11144 | 0.11144 | 0.11445 | 0.11439 | 0.11433 | 0.11426 | 0.11422 | 0.11422 | 0.11422 | 0.11422 | 0.11422 | 0.11422 | 0.11422 | 0.11422 | 0.11422 | 0.11422
|  | CONTULLICH | CT |  |  |  | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.1128 | 0.11272 | 0.11262 | 0.11253 | 0.11244 | 0.11235 | 0.11226 | 0.11217 | 0.11208 | 0.11199 | 0.11192 | 0.11159 | 0.1115 | 0.11144 | 0.11445 | 0.11441 | 0.11436 | 0.11432 | 0.11428 | 0.11423 | 0.11422 | 0.11422 | 0.11422 | 0.11422 | 0.11422 | 0.11422 | 0.11422 | 0.11422
|  | CONTULLICH | LW |  |  |  | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.11279 | 0.11268 | 0.11255 | 0.11241 | 0.11228 | 0.11216 | 0.11203 | 0.11193 | 0.11183 | 0.11173 | 0.11163 | 0.11148 | 0.11144 | 0.11144 | 0.11445 | 0.11439 | 0.11433 | 0.11426 | 0.11422 | 0.11422 | 0.11422 | 0.11422 | 0.11422 | 0.11422 | 0.11422 | 0.11422 | 0.11422 | 0.11422
|  | CONTULLICH | ST |  |  |  | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.11283 | 0.1128 | 0.11274 | 0.11268 | 0.11262 | 0.11256 | 0.1125 | 0.11244 | 0.11238 | 0.11232 | 0.11226 | 0.11199 | 0.11178 | 0.11158 | 0.11447 | 0.11445 | 0.11442 | 0.11439 | 0.11436 | 0.11434 | 0.11431 | 0.11428 | 0.11425 | 0.11422 | 0.11422 | 0.11422 | 0.11422 | 0.11422
|  | CONTULLICH | FS |  |  |  | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.12342 | 0.11285 | 0.11285 | 0.11283 | 0.11281 | 0.11279 | 0.11277 | 0.11275 | 0.11272 | 0.1127 | 0.11267 | 0.11265 | 0.11254 | 0.11243 | 0.11234 | 0.11447 | 0.11447 | 0.11447 | 0.11446 | 0.11445 | 0.11444 | 0.11443 | 0.11441 | 0.1144 | 0.11439 | 0.11438 | 0.11432 | 0.11427 | 0.11423
| FORT WILLIAM | CORRAN | MINIMUM HEADROOM | NN 02545 63126 | YES | YES | 1.4996 | 0.91388 | 0.79637 | 0.68307 | 0.57397 | 0.43257 | 0.28998 | 0.20363 | 0.14445 | 0.085738 | 0.027643 | -0.18157 | -0.38247 | -0.58516 | 1.5258 | 1.4352 | 0.86246 | 0.72174 | 0.58555 | 0.45384 | 0.32662 | 0.24496 | 0.18578 | 0.12705 | 0.068894 | -0.12951 | -0.32147 | -0.51449 | 1.5519 | 0.92051 | 0.74797 | 0.58091 | 0.41934 | 0.26321 | 0.11251 | 0.018985 | -0.046684 | -0.11184 | -0.17633 | -0.40319 | -0.62174 | -0.84191
|  | CORRAN | CT |  |  |  | 1.4996 | 0.91388 | 0.79637 | 0.68307 | 0.57397 | 0.43257 | 0.28998 | 0.20363 | 0.14445 | 0.085738 | 0.027643 | -0.18157 | -0.38247 | -0.58516 | 1.5258 | 1.4352 | 0.86246 | 0.72174 | 0.58555 | 0.45384 | 0.32662 | 0.24496 | 0.18578 | 0.12705 | 0.068894 | -0.12951 | -0.32147 | -0.51449 | 1.5519 | 0.92051 | 0.74797 | 0.58091 | 0.41934 | 0.26321 | 0.11251 | 0.018985 | -0.046684 | -0.11184 | -0.17633 | -0.40319 | -0.62174 | -0.84191
|  | CORRAN | LW |  |  |  | 1.7278 | 1.7085 | 1.6867 | 1.6627 | 1.6367 | 1.6089 | 1.5796 | 0.93331 | 0.85211 | 0.77058 | 0.68897 | 0.42363 | 0.15595 | -0.12279 | 1.676 | 1.6553 | 1.6313 | 1.606 | 1.5795 | 0.96944 | 0.88968 | 0.80682 | 0.7236 | 0.6402 | 0.55685 | 0.30628 | 0.053322 | -0.20825 | 1.749 | 1.7323 | 1.7135 | 1.6928 | 1.6703 | 0.92471 | 0.83706 | 0.74649 | 0.6554 | 0.56402 | 0.4726 | 0.18541 | -0.10441 | -0.4053
|  | CORRAN | ST |  |  |  | 1.7609 | 1.7532 | 1.7457 | 1.7384 | 1.7295 | 1.7209 | 1.7125 | 1.7044 | 1.6925 | 1.681 | 1.6698 | 1.6173 | 1.5701 | 1.5248 | 1.7004 | 1.6929 | 1.6843 | 1.6751 | 1.6674 | 1.66 | 1.6528 | 1.6456 | 1.6359 | 1.6265 | 1.6174 | 1.5741 | 0.98436 | 0.89376 | 1.7776 | 1.771 | 1.7645 | 1.7582 | 1.7505 | 1.7431 | 1.7358 | 1.7288 | 1.7186 | 1.7086 | 1.6989 | 1.6535 | 0.93299 | 0.83122
|  | CORRAN | FS |  |  |  | 1.7532 | 1.7455 | 1.7341 | 1.7228 | 1.7117 | 1.7008 | 1.69 | 1.6794 | 1.6689 | 1.6585 | 1.6483 | 1.5872 | 1.5324 | 1.4813 | 1.6966 | 1.6914 | 1.6828 | 1.6741 | 1.6662 | 1.6584 | 1.6505 | 1.6428 | 1.6352 | 1.6276 | 1.6202 | 1.5766 | 1.5374 | 1.5008 | 1.771 | 1.7643 | 1.7545 | 1.7448 | 1.7352 | 1.7257 | 1.7164 | 1.7072 | 1.6981 | 1.6892 | 1.6804 | 1.6276 | 1.5802 | 0.99311
| KILLIN | COSHIEVILLE | MINIMUM HEADROOM | NN 77193 48683 | YES | YES | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 2.4386 | 1.786 | 1.5873 | 3.3001 | 3.2977 | 3.2947 | 3.2914 | 3.2882 | 3.285 | 3.2819 | 3.2784 | 3.275 | 3.2717 | 2.4912 | 2.2536 | 1.6714 | 1.4407 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 2.3348 | 1.6525 | 1.4191
|  | COSHIEVILLE | CT |  |  |  | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 1.983 | 1.8418 | 3.3003 | 3.2984 | 3.2963 | 3.294 | 3.2917 | 3.2894 | 3.2872 | 3.2847 | 3.2821 | 3.2797 | 3.2775 | 2.4174 | 1.9 | 1.7361 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 2.473 | 1.8698 | 1.7162
|  | COSHIEVILLE | LW |  |  |  | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 2.4386 | 1.786 | 1.5873 | 3.3001 | 3.2977 | 3.2947 | 3.2914 | 3.2882 | 3.285 | 3.2819 | 3.2784 | 3.275 | 3.2717 | 2.4912 | 2.2536 | 1.6714 | 1.4407 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 2.3348 | 1.6525 | 1.4191
|  | COSHIEVILLE | ST |  |  |  | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 2.3841 | 2.3029 | 3.3009 | 3.3002 | 3.299 | 3.2975 | 3.2954 | 3.2935 | 3.2915 | 3.2893 | 3.2871 | 3.285 | 3.2831 | 3.2741 | 2.2805 | 2.1862 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 2.2699 | 2.1971
|  | COSHIEVILLE | FS |  |  |  | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3971 | 3.3013 | 3.3013 | 3.301 | 3.3005 | 3.2998 | 3.299 | 3.2981 | 3.2972 | 3.2963 | 3.2954 | 3.2946 | 3.2908 | 3.2873 | 3.2842 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266 | 3.4266
| COUPAR ANGUS | COUPAR ANGUS | MINIMUM HEADROOM | NO 21784 39212 | NO | YES | 8.3906 | 8.3333 | 8.2746 | 8.2179 | 8.1634 | 8.1109 | 8.0606 | 8.0288 | 8.013 | 7.9973 | 7.9819 | 7.5027 | 7.413 | 4.6996 | 8.8712 | 8.8323 | 8.7922 | 8.7534 | 8.7159 | 8.6793 | 8.644 | 8.6204 | 8.6068 | 8.5931 | 8.5805 | 8.2601 | 4.9544 | 4.5445 | 7.7684 | 7.7141 | 7.6584 | 7.6047 | 7.5529 | 7.5032 | 7.4554 | 7.4253 | 7.4103 | 7.3954 | 7.3808 | 6.9264 | 4.9936 | 4.6036
|  | COUPAR ANGUS | CT |  |  |  | 8.3906 | 8.3333 | 8.2746 | 8.2179 | 8.1634 | 8.1109 | 8.0606 | 8.0288 | 8.013 | 7.9973 | 7.9819 | 7.5027 | 7.413 | 4.6996 | 8.8712 | 8.8323 | 8.7922 | 8.7534 | 8.7159 | 8.6793 | 8.644 | 8.6204 | 8.6068 | 8.5931 | 8.5805 | 8.2601 | 4.9907 | 4.6644 | 7.7684 | 7.7141 | 7.6584 | 7.6047 | 7.5529 | 7.5032 | 7.4554 | 7.4253 | 7.4103 | 7.3954 | 7.3808 | 6.9264 | 4.9936 | 4.6263
|  | COUPAR ANGUS | LW |  |  |  | 8.492 | 8.4834 | 8.4737 | 8.4631 | 8.4515 | 8.4392 | 8.4262 | 8.4097 | 8.3927 | 8.3753 | 8.3578 | 7.8649 | 7.7487 | 4.7466 | 8.9356 | 8.9269 | 8.9169 | 8.9062 | 8.8949 | 8.8826 | 8.8701 | 8.8549 | 8.8394 | 8.8236 | 8.8087 | 8.4776 | 4.9544 | 4.5445 | 7.8646 | 7.8564 | 7.8473 | 7.8372 | 7.8262 | 7.8145 | 7.8022 | 7.7865 | 7.7704 | 7.754 | 7.7373 | 7.2698 | 7.1597 | 4.6036
|  | COUPAR ANGUS | ST |  |  |  | 8.5067 | 8.5033 | 8.4999 | 8.4967 | 8.4927 | 8.4889 | 8.4852 | 8.4813 | 8.4757 | 8.4702 | 8.4649 | 8.2351 | 8.2058 | 8.1705 | 8.9461 | 8.9432 | 8.94 | 8.9367 | 8.9325 | 8.9281 | 8.9237 | 8.9191 | 8.9133 | 8.9074 | 8.9024 | 8.748 | 8.7224 | 8.6933 | 7.8785 | 7.8753 | 7.8721 | 7.869 | 7.8653 | 7.8617 | 7.8581 | 7.8545 | 7.8492 | 7.844 | 7.8389 | 7.621 | 7.5932 | 7.5597
|  | COUPAR ANGUS | FS |  |  |  | 8.5033 | 8.4998 | 8.4948 | 8.4898 | 8.4848 | 8.48 | 8.4752 | 8.4705 | 8.4658 | 8.4612 | 8.4567 | 8.4295 | 8.4002 | 8.3716 | 8.9442 | 8.9419 | 8.9383 | 8.9347 | 8.9309 | 8.9271 | 8.9232 | 8.9193 | 8.9155 | 8.9116 | 8.9081 | 8.8876 | 8.8663 | 8.8457 | 7.8753 | 7.872 | 7.8672 | 7.8625 | 7.8578 | 7.8532 | 7.8487 | 7.8442 | 7.8398 | 7.8354 | 7.8311 | 7.8054 | 7.7776 | 7.7504
| CRAIGIEBUCKLER | CRAIGIEBUCKLER | MINIMUM HEADROOM | NJ 90775 04519 | NO | YES | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 22.8815 | 22.0049 | 21.1062 | 20.2237 | 23.9152 | 23.9152 | 23.9152 | 21.7773 | 21.4363 | 21.1009 | 20.772 | 20.4161 | 20.0628 | 19.7118 | 19.351 | 18.3219 | 17.2667 | 16.2307 | 24.2662 | 24.2662 | 24.2662 | 22.0169 | 21.6758 | 21.3404 | 21.0114 | 20.6553 | 20.3019 | 19.9508 | 19.5898 | 18.5604 | 17.5049 | 16.4685
|  | CRAIGIEBUCKLER | CT |  |  |  | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 22.7324 | 22.1337 | 23.9152 | 23.9152 | 23.9152 | 23.9152 | 21.9529 | 21.7383 | 21.5259 | 21.2935 | 21.062 | 20.838 | 20.6152 | 19.9021 | 19.1759 | 18.473 | 24.2662 | 24.2662 | 24.2662 | 24.2662 | 24.2662 | 21.9779 | 21.7655 | 21.5331 | 21.3015 | 21.0774 | 20.8545 | 20.1412 | 19.4147 | 18.7116
|  | CRAIGIEBUCKLER | LW |  |  |  | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 22.8815 | 22.0049 | 21.1062 | 20.2237 | 23.9152 | 23.9152 | 23.9152 | 21.7773 | 21.4363 | 21.1009 | 20.772 | 20.4161 | 20.0628 | 19.7118 | 19.351 | 18.3219 | 17.2667 | 16.2307 | 24.2662 | 24.2662 | 24.2662 | 22.0169 | 21.6758 | 21.3404 | 21.0114 | 20.6553 | 20.3019 | 19.9508 | 19.5898 | 18.5604 | 17.5049 | 16.4685
|  | CRAIGIEBUCKLER | ST |  |  |  | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 23.9152 | 23.9152 | 23.9152 | 23.9152 | 23.9152 | 23.9152 | 23.9152 | 22.0774 | 21.9796 | 21.8875 | 21.7968 | 21.3144 | 20.835 | 20.3698 | 24.2662 | 24.2662 | 24.2662 | 24.2662 | 24.2662 | 24.2662 | 24.2662 | 24.2662 | 24.2662 | 24.2662 | 22.0364 | 21.554 | 21.0744 | 20.609
|  | CRAIGIEBUCKLER | FS |  |  |  | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 27.2236 | 24.1479 | 23.9152 | 23.9152 | 23.9152 | 23.9152 | 23.9152 | 23.9152 | 23.9152 | 23.9152 | 23.9152 | 23.9152 | 23.9152 | 23.9152 | 23.9152 | 24.317 | 24.2662 | 24.2662 | 24.2662 | 24.2662 | 24.2662 | 24.2662 | 24.2662 | 24.2662 | 24.2662 | 24.2662 | 24.2662 | 24.2662 | 24.2662
| CLAYHILLS | CRAIGINCHES | MINIMUM HEADROOM | NJ 94694 04089 | NO | NO | 28.8087 | 28.8063 | 28.8033 | 28.8003 | 28.7974 | 28.7946 | 28.7918 | 28.7888 | 28.7858 | 28.7828 | 28.7794 | 28.7524 | 28.7245 | 28.6971 | 27.0554 | 27.0285 | 26.9954 | 26.9627 | 26.9306 | 26.899 | 26.868 | 26.8345 | 26.8014 | 26.7685 | 26.7305 | 26.6767 | 26.6219 | 26.5863 | 27.3107 | 27.3005 | 27.288 | 27.2756 | 27.2635 | 27.2515 | 27.2398 | 27.2271 | 27.2145 | 27.2021 | 27.1877 | 27.1168 | 27.1168 | 27.1168
|  | CRAIGINCHES | CT |  |  |  | 28.8088 | 28.807 | 28.8049 | 28.8029 | 28.8008 | 28.7988 | 28.7968 | 28.7947 | 28.7926 | 28.7905 | 28.7883 | 28.7679 | 28.7471 | 28.7271 | 27.057 | 27.0369 | 27.0137 | 26.9908 | 26.9682 | 26.9458 | 26.9238 | 26.9 | 26.8765 | 26.8532 | 26.8296 | 26.7073 | 26.6664 | 26.6268 | 27.3113 | 27.3037 | 27.2949 | 27.2862 | 27.2777 | 27.2692 | 27.2609 | 27.2519 | 27.243 | 27.2341 | 27.2252 | 27.1396 | 27.1168 | 27.1168
|  | CRAIGINCHES | LW |  |  |  | 28.8087 | 28.8063 | 28.8033 | 28.8003 | 28.7974 | 28.7946 | 28.7918 | 28.7888 | 28.7858 | 28.7828 | 28.7794 | 28.7524 | 28.7245 | 28.6971 | 27.0554 | 27.0285 | 26.9954 | 26.9627 | 26.9306 | 26.899 | 26.868 | 26.8345 | 26.8014 | 26.7685 | 26.7305 | 26.6767 | 26.6219 | 26.5863 | 27.3107 | 27.3005 | 27.288 | 27.2756 | 27.2635 | 27.2515 | 27.2398 | 27.2271 | 27.2145 | 27.2021 | 27.1877 | 27.1168 | 27.1168 | 27.1168
|  | CRAIGINCHES | ST |  |  |  | 28.8095 | 28.8087 | 28.8076 | 28.8062 | 28.8038 | 28.8015 | 28.7991 | 28.7966 | 28.7941 | 28.7917 | 28.7893 | 28.7757 | 28.7623 | 28.7494 | 27.0642 | 27.056 | 27.0434 | 27.0283 | 27.0015 | 26.9752 | 26.9494 | 26.9214 | 26.8941 | 26.8671 | 26.8403 | 26.7227 | 26.6963 | 26.6708 | 27.314 | 27.3109 | 27.3061 | 27.3004 | 27.2903 | 27.2803 | 27.2706 | 27.26 | 27.2496 | 27.2394 | 27.2293 | 27.1723 | 27.1168 | 27.1168
|  | CRAIGINCHES | FS |  |  |  | 28.8173 | 28.8098 | 28.8095 | 28.8091 | 28.8084 | 28.8076 | 28.8066 | 28.8056 | 28.8047 | 28.8037 | 28.8028 | 28.7983 | 28.7937 | 28.7891 | 27.1511 | 27.0681 | 27.0645 | 27.0603 | 27.0517 | 27.0431 | 27.0321 | 27.0213 | 27.0107 | 27.0003 | 26.9901 | 26.9403 | 26.8894 | 26.8383 | 27.3469 | 27.3155 | 27.3141 | 27.3125 | 27.3093 | 27.306 | 27.3019 | 27.2978 | 27.2938 | 27.2898 | 27.286 | 27.2671 | 27.2479 | 27.2285
| CRAIGIEBUCKLER | CRAIGTON | MINIMUM HEADROOM | NJ 89195 03438 | YES | YES | 16.9225 | 16.8125 | 16.7056 | 16.6024 | 16.5031 | 16.4076 | 16.316 | 14.3104 | 14.029 | 13.7279 | 13.5832 | 12.1258 | 11.318 | 10.4898 | 13.7884 | 13.7019 | 13.4422 | 13.1678 | 12.8736 | 12.5656 | 12.2368 | 11.8702 | 11.4732 | 11.0579 | 10.8473 | 9.4288 | 8.5668 | 7.6934 | 14.4712 | 13.7754 | 13.4996 | 13.2107 | 12.8958 | 12.5664 | 12.2145 | 11.8742 | 11.5415 | 11.1822 | 10.9636 | 9.333 | 8.4205 | 7.4894
|  | CRAIGTON | CT |  |  |  | 16.9225 | 16.8125 | 16.7056 | 16.6024 | 16.5031 | 16.4076 | 16.316 | 14.3104 | 14.029 | 13.7279 | 13.5832 | 12.1646 | 11.5811 | 11.0185 | 13.7884 | 13.7019 | 13.4422 | 13.1678 | 12.8736 | 12.5656 | 12.2368 | 11.9104 | 11.5846 | 11.2349 | 11.0736 | 9.7576 | 9.1348 | 8.5417 | 14.4712 | 13.7754 | 13.4996 | 13.2107 | 12.8958 | 12.5664 | 12.2145 | 11.8742 | 11.5415 | 11.1848 | 11.0168 | 9.4977 | 8.8381 | 8.2056
|  | CRAIGTON | LW |  |  |  | 17.1171 | 17.1006 | 17.0821 | 17.0616 | 17.0394 | 17.0158 | 16.9908 | 14.5496 | 14.2003 | 13.8351 | 13.6441 | 12.1258 | 11.318 | 10.4898 | 14.4162 | 14.3873 | 13.5504 | 13.2541 | 12.9394 | 12.6057 | 12.253 | 11.8702 | 11.4732 | 11.0579 | 10.8473 | 9.4288 | 8.5668 | 7.6934 | 14.6637 | 14.6464 | 13.7196 | 13.4199 | 13.0994 | 12.7597 | 12.4005 | 12.0102 | 11.6055 | 11.1822 | 10.9636 | 9.333 | 8.4205 | 7.4894
|  | CRAIGTON | ST |  |  |  | 17.1453 | 17.1388 | 17.1324 | 17.1262 | 17.1186 | 17.1112 | 17.1041 | 17.0971 | 17.0868 | 17.0769 | 17.0672 | 14.279 | 13.9291 | 13.5924 | 14.4976 | 14.4344 | 14.4084 | 13.7839 | 13.6243 | 13.454 | 13.2683 | 13.0591 | 12.8286 | 12.5779 | 12.4633 | 11.6758 | 11.2869 | 10.9169 | 14.7083 | 14.6863 | 14.6789 | 14.6726 | 14.6648 | 13.6323 | 13.4448 | 13.2337 | 13.0005 | 12.7472 | 12.6301 | 11.7441 | 11.3423 | 10.9575
|  | CRAIGTON | FS |  |  |  | 17.1388 | 17.1322 | 17.1225 | 17.1129 | 17.1034 | 17.0941 | 17.0849 | 17.0758 | 17.0669 | 17.058 | 17.0494 | 16.9972 | 16.9421 | 16.8884 | 14.5349 | 14.5084 | 14.4686 | 14.4254 | 14.3986 | 14.3869 | 14.3782 | 13.774 | 13.6816 | 13.5847 | 13.5348 | 13.3092 | 13.1382 | 12.9828 | 14.7125 | 14.7004 | 14.6823 | 14.6635 | 14.6492 | 14.6397 | 14.6302 | 14.6209 | 14.6117 | 13.7462 | 13.6951 | 13.4587 | 13.2738 | 13.1048
| BRACO | CRIEFF | MINIMUM HEADROOM | NN 85626 22119 | NO | YES | 21.6078 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 17.5411 | 25.7307 | 25.6247 | 25.5161 | 25.4097 | 25.3107 | 25.2844 | 25.2667 | 25.2508 | 25.2345 | 25.218 | 21.7735 | 20.8409 | 19.9758 | 17.5867 | 25.775 | 25.6676 | 25.6128 | 25.5905 | 25.5905 | 25.5905 | 25.5905 | 25.5905 | 25.5905 | 25.5905 | 21.9302 | 20.9865 | 20.1112
|  | CRIEFF | CT |  |  |  | 21.6078 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 17.5483 | 25.7577 | 25.6803 | 25.5999 | 25.5199 | 25.4438 | 25.3655 | 25.3028 | 25.2803 | 25.2674 | 25.2546 | 25.1878 | 21.8484 | 21.2082 | 17.594 | 25.8024 | 25.724 | 25.6425 | 25.6138 | 25.5943 | 25.5905 | 25.5905 | 25.5905 | 25.5905 | 25.5905 | 25.5905 | 22.0059 | 21.3581
|  | CRIEFF | LW |  |  |  | 21.6078 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 17.5411 | 25.7307 | 25.6247 | 25.5161 | 25.4097 | 25.3107 | 25.2844 | 25.2667 | 25.2508 | 25.2345 | 25.218 | 21.7735 | 20.8409 | 19.9758 | 17.5867 | 25.775 | 25.6676 | 25.6128 | 25.5905 | 25.5905 | 25.5905 | 25.5905 | 25.5905 | 25.5905 | 25.5905 | 21.9302 | 20.9865 | 20.1112
|  | CRIEFF | ST |  |  |  | 21.6078 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 17.5743 | 25.8216 | 25.7783 | 25.7261 | 25.6629 | 25.6026 | 25.5412 | 25.474 | 25.4067 | 25.3383 | 25.3 | 25.2487 | 25.2117 | 25.1762 | 17.6204 | 25.8672 | 25.8233 | 25.7704 | 25.7064 | 25.6452 | 25.6192 | 25.602 | 25.5905 | 25.5905 | 25.5905 | 25.5905 | 25.5905 | 25.5905
|  | CRIEFF | FS |  |  |  | 21.6078 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 30.3378 | 17.5928 | 25.864 | 25.8484 | 25.8304 | 25.8079 | 25.7871 | 25.7617 | 25.7359 | 25.7102 | 25.684 | 25.6575 | 25.5285 | 25.4217 | 25.335 | 17.639 | 25.9101 | 25.8943 | 25.8761 | 25.8533 | 25.8323 | 25.8065 | 25.7803 | 25.7543 | 25.7277 | 25.7009 | 25.6159 | 25.5905 | 25.5905
| PORT ANN | CRINAN | MINIMUM HEADROOM | NR 79620 92347 | YES | YES | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 0.88958 | 0.77031 | 1.4711 | 1.4653 | 1.4582 | 1.4513 | 1.4446 | 1.4402 | 1.4393 | 1.4385 | 1.4378 | 1.4378 | 1.4378 | 0.86187 | 0.70839 | 0.55712 | 1.4555 | 1.4555 | 1.4555 | 1.4555 | 1.4555 | 1.4555 | 1.4555 | 1.4555 | 1.4555 | 1.4555 | 1.4555 | 0.91661 | 0.76699 | 0.61911
|  | CRINAN | CT |  |  |  | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 0.98131 | 0.89662 | 1.4714 | 1.4671 | 1.4621 | 1.4573 | 1.4526 | 1.4479 | 1.4434 | 1.4402 | 1.4396 | 1.439 | 1.4384 | 0.93385 | 0.82472 | 0.71732 | 1.4555 | 1.4555 | 1.4555 | 1.4555 | 1.4555 | 1.4555 | 1.4555 | 1.4555 | 1.4555 | 1.4555 | 1.4555 | 0.98679 | 0.8804 | 0.77569
|  | CRINAN | LW |  |  |  | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 0.88958 | 0.77031 | 1.4711 | 1.4653 | 1.4582 | 1.4513 | 1.4446 | 1.4402 | 1.4393 | 1.4385 | 1.4378 | 1.4378 | 1.4378 | 0.86187 | 0.70839 | 0.55712 | 1.4555 | 1.4555 | 1.4555 | 1.4555 | 1.4555 | 1.4555 | 1.4555 | 1.4555 | 1.4555 | 1.4555 | 1.4555 | 0.91661 | 0.76699 | 0.61911
|  | CRINAN | ST |  |  |  | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 0.96229 | 1.4729 | 1.4711 | 1.4683 | 1.465 | 1.4548 | 1.4449 | 1.4398 | 1.4385 | 1.4378 | 1.4378 | 1.4378 | 0.93337 | 0.86687 | 0.8006 | 1.4555 | 1.4555 | 1.4555 | 1.4555 | 1.4555 | 1.4555 | 1.4555 | 1.4555 | 1.4555 | 1.4555 | 1.4555 | 0.98632 | 0.92149 | 0.85689
|  | CRINAN | FS |  |  |  | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 1.4055 | 1.4739 | 1.4738 | 1.473 | 1.4721 | 1.4687 | 1.4655 | 1.4612 | 1.4571 | 1.453 | 1.449 | 1.4451 | 1.4387 | 1.4378 | 0.99851 | 1.4555 | 1.4555 | 1.4555 | 1.4555 | 1.4555 | 1.4555 | 1.4555 | 1.4555 | 1.4555 | 1.4555 | 1.4555 | 1.4555 | 1.4555 | 1.4555
| PORT ANN | CROMALT | MINIMUM HEADROOM | NN 08395 07755 | YES | YES | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.47517 | 0.46223 | 0.4562 | 0.45051 | 0.44608 | 0.44436 | 0.44267 | 0.44083 | 0.43901 | 0.43726 | 0.43552 | 0.42636 | 0.41714 | 0.41211 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947
|  | CROMALT | CT |  |  |  | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.47695 | 0.46626 | 0.46245 | 0.45836 | 0.45352 | 0.44737 | 0.44495 | 0.44339 | 0.442 | 0.44078 | 0.43956 | 0.43365 | 0.42769 | 0.42179 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947
|  | CROMALT | LW |  |  |  | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.47517 | 0.46223 | 0.4562 | 0.45051 | 0.44608 | 0.44436 | 0.44267 | 0.44083 | 0.43901 | 0.43726 | 0.43552 | 0.42636 | 0.41714 | 0.41211 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947
|  | CROMALT | ST |  |  |  | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.48237 | 0.47613 | 0.47405 | 0.47134 | 0.46791 | 0.46363 | 0.45959 | 0.45617 | 0.45312 | 0.45046 | 0.44785 | 0.44288 | 0.43887 | 0.43485 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947
|  | CROMALT | FS |  |  |  | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.65632 | 0.48705 | 0.48406 | 0.48308 | 0.48203 | 0.48067 | 0.47941 | 0.478 | 0.47658 | 0.47521 | 0.47386 | 0.47269 | 0.46772 | 0.46311 | 0.45886 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947 | 0.47947
| ALNESS | CROSSHILLS | MINIMUM HEADROOM | NH 65470 70156 | NO | YES | 19.5688 | 19.5494 | 19.5231 | 19.4964 | 19.4777 | 19.4596 | 19.4436 | 19.4275 | 19.4134 | 19.3984 | 19.3874 | 19.3427 | 19.2929 | 19.2374 | 17.3607 | 17.2987 | 17.2148 | 17.1293 | 17.0449 | 16.9578 | 16.8811 | 16.8325 | 16.8036 | 16.7731 | 16.7507 | 16.7112 | 16.7112 | 16.7112 | 17.4342 | 17.4078 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839
|  | CROSSHILLS | CT |  |  |  | 19.5688 | 19.5494 | 19.5231 | 19.4964 | 19.4777 | 19.4596 | 19.4436 | 19.4275 | 19.4134 | 19.3984 | 19.3874 | 19.3427 | 19.301 | 19.2605 | 17.3607 | 17.2987 | 17.2148 | 17.1293 | 17.0449 | 16.9578 | 16.8811 | 16.8325 | 16.8036 | 16.7731 | 16.7507 | 16.7112 | 16.7112 | 16.7112 | 17.4342 | 17.4078 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839
|  | CROSSHILLS | LW |  |  |  | 19.5727 | 19.5582 | 19.5359 | 19.513 | 19.4894 | 19.4676 | 19.4519 | 19.4369 | 19.4253 | 19.4132 | 19.4055 | 19.3499 | 19.2929 | 19.2374 | 17.3731 | 17.3267 | 17.2555 | 17.1824 | 17.1071 | 16.9963 | 16.9208 | 16.8517 | 16.8279 | 16.8033 | 16.7875 | 16.7112 | 16.7112 | 16.7112 | 17.4394 | 17.4197 | 17.3894 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839
|  | CROSSHILLS | ST |  |  |  | 19.5799 | 19.5761 | 19.5676 | 19.5573 | 19.5417 | 19.5146 | 19.491 | 19.477 | 19.4685 | 19.4595 | 19.4533 | 19.4252 | 19.4 | 19.3756 | 17.3963 | 17.384 | 17.3568 | 17.3241 | 17.274 | 17.1875 | 17.1122 | 17.0414 | 17.0009 | 16.9573 | 16.9275 | 16.8277 | 16.7763 | 16.7264 | 17.4493 | 17.4441 | 17.4325 | 17.4186 | 17.3973 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839
|  | CROSSHILLS | FS |  |  |  | 19.5837 | 19.5833 | 19.5805 | 19.5775 | 19.5719 | 19.5613 | 19.5512 | 19.5418 | 19.5337 | 19.5252 | 19.5192 | 19.4918 | 19.4779 | 19.469 | 17.4083 | 17.4069 | 17.3982 | 17.3884 | 17.3705 | 17.3367 | 17.3046 | 17.2744 | 17.2486 | 17.2215 | 17.2023 | 17.1149 | 17.0455 | 17.0031 | 17.4544 | 17.4538 | 17.4501 | 17.4459 | 17.4383 | 17.424 | 17.4103 | 17.3975 | 17.3865 | 17.3839 | 17.3839 | 17.3839 | 17.3839 | 17.3839
| KEITH | CULLEN | MINIMUM HEADROOM | NJ 51590 65032 | YES | YES | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 7.444 | 7.1307 | 8.5473 | 8.54 | 8.5292 | 8.5187 | 8.5092 | 8.4995 | 8.4923 | 8.4851 | 8.4743 | 8.4621 | 8.4506 | 7.2219 | 6.4238 | 5.988 | 8.9727 | 8.9674 | 8.9596 | 8.9521 | 8.9453 | 8.9383 | 8.9331 | 8.9278 | 8.92 | 8.9113 | 8.903 | 8.8135 | 6.7104 | 6.3017
|  | CULLEN | CT |  |  |  | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 7.444 | 7.3748 | 8.5479 | 8.5422 | 8.5339 | 8.5259 | 8.5187 | 8.5112 | 8.5054 | 8.499 | 8.4926 | 8.4866 | 8.4812 | 7.3572 | 6.6449 | 6.2926 | 8.9731 | 8.969 | 8.9631 | 8.9573 | 8.9521 | 8.9467 | 8.9425 | 8.9379 | 8.9333 | 8.9289 | 8.925 | 8.8444 | 6.9178 | 6.5873
|  | CULLEN | LW |  |  |  | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 7.444 | 7.1307 | 8.5473 | 8.54 | 8.5292 | 8.5187 | 8.5092 | 8.4995 | 8.4923 | 8.4851 | 8.4779 | 8.4707 | 8.4637 | 7.2219 | 6.4238 | 5.988 | 8.9727 | 8.9674 | 8.9596 | 8.9521 | 8.9453 | 8.9383 | 8.9331 | 8.9278 | 8.9226 | 8.9175 | 8.9124 | 8.8135 | 6.7104 | 6.3017
|  | CULLEN | ST |  |  |  | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.2543 | 9.2543 | 8.55 | 8.5473 | 8.5423 | 8.537 | 8.524 | 8.5111 | 8.4994 | 8.4868 | 8.4743 | 8.4621 | 8.4506 | 7.4396 | 7.0896 | 6.9181 | 8.9747 | 8.9727 | 8.9691 | 8.9652 | 8.9559 | 8.9466 | 8.9382 | 8.9291 | 8.92 | 8.9113 | 8.903 | 8.8633 | 7.3878 | 7.2383
|  | CULLEN | FS |  |  |  | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 9.4648 | 8.5517 | 8.5509 | 8.5489 | 8.5469 | 8.5422 | 8.5375 | 8.5322 | 8.5271 | 8.5221 | 8.5172 | 8.5124 | 8.4901 | 8.47 | 8.4506 | 8.9758 | 8.9753 | 8.9738 | 8.9724 | 8.969 | 8.9656 | 8.9618 | 8.9582 | 8.9545 | 8.951 | 8.9475 | 8.9315 | 8.917 | 8.9029
| INVERNESS | CULLODEN | MINIMUM HEADROOM | NH 71240 45502 | NO | YES | 23.5162 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 23.1272 | 22.0118 | 21.3155 | 28.2272 | 28.0094 | 27.7852 | 27.5625 | 27.4066 | 27.3658 | 27.3218 | 27.277 | 27.2332 | 27.2021 | 20.8558 | 19.4932 | 18.1643 | 21.2669 | 28.2938 | 28.2252 | 28.1545 | 28.0843 | 28.0727 | 28.0727 | 28.0727 | 28.0727 | 28.0727 | 28.0727 | 21.0637 | 19.7212 | 18.4118
|  | CULLODEN | CT |  |  |  | 23.5162 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 21.3308 | 28.282 | 28.123 | 27.9569 | 27.7893 | 27.6235 | 27.4488 | 27.3906 | 27.354 | 27.3178 | 27.2932 | 27.2029 | 21.2625 | 20.3569 | 21.2717 | 28.3111 | 28.261 | 28.2086 | 28.1558 | 28.1035 | 28.0727 | 28.0727 | 28.0727 | 28.0727 | 28.0727 | 28.0727 | 21.4644 | 20.5721
|  | CULLODEN | LW |  |  |  | 23.5162 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 23.1272 | 22.0118 | 21.3155 | 28.2272 | 28.0094 | 27.7852 | 27.5625 | 27.4066 | 27.3658 | 27.3218 | 27.277 | 27.2332 | 27.2021 | 20.8558 | 19.4932 | 18.1643 | 21.2669 | 28.2938 | 28.2252 | 28.1545 | 28.0843 | 28.0727 | 28.0727 | 28.0727 | 28.0727 | 28.0727 | 28.0727 | 21.0637 | 19.7212 | 18.4118
|  | CULLODEN | ST |  |  |  | 23.5162 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 21.385 | 28.4084 | 28.3211 | 28.2168 | 28.1174 | 28.0193 | 27.9152 | 27.7979 | 27.6742 | 27.5513 | 27.475 | 27.368 | 27.3108 | 27.2552 | 21.2888 | 28.351 | 28.3234 | 28.2905 | 28.2592 | 28.2283 | 28.1955 | 28.1585 | 28.1195 | 28.0808 | 28.0727 | 28.0727 | 28.0727 | 28.0727
|  | CULLODEN | FS |  |  |  | 23.5162 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 31.7962 | 21.4215 | 28.4867 | 28.4535 | 28.4158 | 28.3784 | 28.3416 | 28.2978 | 28.2523 | 28.2051 | 28.1592 | 28.1285 | 27.9925 | 27.8794 | 27.7727 | 21.3003 | 28.3756 | 28.3652 | 28.3533 | 28.3415 | 28.3299 | 28.3161 | 28.3017 | 28.2869 | 28.2724 | 28.2627 | 28.2199 | 28.1842 | 28.1506
| CRAIGIEBUCKLER | CULTER | MINIMUM HEADROOM | NJ 84009 00884 | NO | YES | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 22.2283 | 21.4977 | 25.4303 | 25.3126 | 25.1776 | 25.0584 | 25.034 | 25.0096 | 24.9852 | 24.9588 | 24.9345 | 21.9763 | 21.7244 | 20.8874 | 19.6731 | 18.8387 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 21.8277 | 21.5603 | 21.3096 | 21.0533 | 20.2016 | 18.8947 | 18.0458
|  | CULTER | CT |  |  |  | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 27.8172 | 23.1527 | 25.4481 | 25.3734 | 25.2957 | 25.2172 | 25.137 | 25.0605 | 25.0452 | 25.0288 | 25.014 | 25.0003 | 24.987 | 24.9335 | 21.2793 | 20.7305 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 21.5489 | 20.529 | 19.9706
|  | CULTER | LW |  |  |  | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 22.2283 | 21.4977 | 25.4303 | 25.3126 | 25.1776 | 25.0584 | 25.034 | 25.0096 | 24.9852 | 24.9588 | 24.9345 | 21.9763 | 21.7244 | 20.8874 | 19.6731 | 18.8387 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 21.8277 | 21.5603 | 21.3096 | 21.0533 | 20.2016 | 18.8947 | 18.0458
|  | CULTER | ST |  |  |  | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.0277 | 28.0277 | 25.4682 | 25.425 | 25.367 | 25.2975 | 25.2499 | 25.2009 | 25.1508 | 25.0966 | 25.0593 | 25.0515 | 25.0439 | 25.0057 | 24.8372 | 22.0295 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 21.7195 | 21.3281
|  | CULTER | FS |  |  |  | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 28.2383 | 25.4922 | 25.4841 | 25.4668 | 25.4467 | 25.4299 | 25.4129 | 25.3922 | 25.3711 | 25.3526 | 25.3358 | 25.3195 | 25.2447 | 25.1752 | 25.1075 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887 | 24.0887
| ELGIN | CUMMING STREET | MINIMUM HEADROOM | NJ 21542 63007 | NO | YES | 29.7348 | 29.7082 | 29.6725 | 29.6333 | 29.5932 | 29.5523 | 29.5173 | 29.4837 | 29.4503 | 29.4171 | 29.3842 | 29.1362 | 28.879 | 28.6267 | 26.6514 | 26.6133 | 26.5621 | 26.5058 | 26.4483 | 26.3897 | 26.3395 | 26.2913 | 26.2434 | 26.1959 | 26.1486 | 25.8371 | 25.7704 | 25.7704 | 26.9049 | 26.8596 | 26.7986 | 26.7318 | 26.6633 | 26.5936 | 26.5592 | 26.543 | 26.527 | 26.511 | 26.4952 | 26.3759 | 26.2522 | 26.156
|  | CUMMING STREET | CT |  |  |  | 29.7363 | 29.7163 | 29.6907 | 29.6621 | 29.6328 | 29.6034 | 29.578 | 29.553 | 29.5268 | 29.5008 | 29.4764 | 29.2943 | 29.1084 | 28.9256 | 26.6536 | 26.6249 | 26.5882 | 26.5472 | 26.5051 | 26.463 | 26.4266 | 26.3908 | 26.3532 | 26.3158 | 26.2809 | 26.0197 | 25.8226 | 25.7704 | 26.9075 | 26.8734 | 26.8298 | 26.781 | 26.7309 | 26.6808 | 26.6375 | 26.5949 | 26.5638 | 26.5513 | 26.5395 | 26.452 | 26.3626 | 26.2747
|  | CUMMING STREET | LW |  |  |  | 29.7348 | 29.7082 | 29.6725 | 29.6333 | 29.5932 | 29.5523 | 29.5173 | 29.4837 | 29.4503 | 29.4171 | 29.3842 | 29.1362 | 28.879 | 28.6267 | 26.6514 | 26.6133 | 26.5621 | 26.5058 | 26.4483 | 26.3897 | 26.3395 | 26.2913 | 26.2434 | 26.1959 | 26.1486 | 25.8371 | 25.7704 | 25.7704 | 26.9049 | 26.8596 | 26.7986 | 26.7318 | 26.6633 | 26.5936 | 26.5592 | 26.543 | 26.527 | 26.511 | 26.4952 | 26.3759 | 26.2522 | 26.156
|  | CUMMING STREET | ST |  |  |  | 29.7422 | 29.7331 | 29.7175 | 29.6971 | 29.6692 | 29.6414 | 29.6165 | 29.5912 | 29.5653 | 29.5396 | 29.5154 | 29.4011 | 29.2872 | 29.1743 | 26.6621 | 26.649 | 26.6267 | 26.5974 | 26.5573 | 26.5176 | 26.4819 | 26.4456 | 26.4083 | 26.3716 | 26.3368 | 26.1728 | 26.0095 | 25.857 | 26.9176 | 26.9021 | 26.8755 | 26.8406 | 26.793 | 26.7457 | 26.7032 | 26.66 | 26.6157 | 26.572 | 26.5583 | 26.5033 | 26.4486 | 26.3943
|  | CUMMING STREET | FS |  |  |  | 29.747 | 29.746 | 29.7413 | 29.7351 | 29.7255 | 29.7158 | 29.705 | 29.6952 | 29.6854 | 29.6757 | 29.6663 | 29.6221 | 29.5829 | 29.5445 | 26.6689 | 26.6675 | 26.6608 | 26.6519 | 26.6381 | 26.6242 | 26.6088 | 26.5947 | 26.5806 | 26.5668 | 26.5532 | 26.4898 | 26.4335 | 26.3786 | 26.9257 | 26.9241 | 26.9161 | 26.9054 | 26.8891 | 26.8725 | 26.8542 | 26.8374 | 26.8207 | 26.8042 | 26.7881 | 26.7126 | 26.6457 | 26.5803
| ST FILLANS | DALCHONZIE | MINIMUM HEADROOM | NN 74079 21921 | YES | NO | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 5.7498 | 5.4764 | 6.7411 | 6.7411 | 6.7411 | 6.7411 | 6.7411 | 6.7411 | 6.7411 | 6.7411 | 6.7411 | 6.7411 | 5.9228 | 5.5878 | 5.2559 | 4.9338 | 7.0442 | 7.0442 | 7.0442 | 7.0442 | 7.0442 | 7.0442 | 7.0442 | 7.0442 | 7.0442 | 7.0442 | 7.0442 | 5.8945 | 5.5636 | 5.2425
|  | DALCHONZIE | CT |  |  |  | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 5.9806 | 5.7755 | 6.7411 | 6.7411 | 6.7411 | 6.7411 | 6.7411 | 6.7411 | 6.7411 | 6.7411 | 6.7411 | 6.7411 | 6.7411 | 5.7773 | 5.5278 | 5.2862 | 7.0442 | 7.0442 | 7.0442 | 7.0442 | 7.0442 | 7.0442 | 7.0442 | 7.0442 | 7.0442 | 7.0442 | 7.0442 | 7.0442 | 5.8346 | 5.5938
|  | DALCHONZIE | LW |  |  |  | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 5.7498 | 5.4764 | 6.7411 | 6.7411 | 6.7411 | 6.7411 | 6.7411 | 6.7411 | 6.7411 | 6.7411 | 6.7411 | 6.7411 | 5.9228 | 5.5878 | 5.2559 | 4.9338 | 7.0442 | 7.0442 | 7.0442 | 7.0442 | 7.0442 | 7.0442 | 7.0442 | 7.0442 | 7.0442 | 7.0442 | 7.0442 | 5.8945 | 5.5636 | 5.2425
|  | DALCHONZIE | ST |  |  |  | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 6.7411 | 6.7411 | 6.7411 | 6.7411 | 6.7411 | 6.7411 | 6.7411 | 6.7411 | 6.7411 | 6.7411 | 6.7411 | 6.7411 | 6.7411 | 5.9921 | 7.0442 | 7.0442 | 7.0442 | 7.0442 | 7.0442 | 7.0442 | 7.0442 | 7.0442 | 7.0442 | 7.0442 | 7.0442 | 7.0442 | 7.0442 | 7.0442
|  | DALCHONZIE | FS |  |  |  | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 7.3137 | 6.7411 | 6.7411 | 6.7411 | 6.7411 | 6.7411 | 6.7411 | 6.7411 | 6.7411 | 6.7411 | 6.7411 | 6.7411 | 6.7411 | 6.7411 | 6.7411 | 7.0442 | 7.0442 | 7.0442 | 7.0442 | 7.0442 | 7.0442 | 7.0442 | 7.0442 | 7.0442 | 7.0442 | 7.0442 | 7.0442 | 7.0442 | 7.0442
| NAIRN | DALCROSS | MINIMUM HEADROOM | NH 76333 51847 | NO | YES | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 14.4466 | 14.2754 | 14.2204 | 14.052 | 13.905 | 13.7604 | 15.143 | 15.1312 | 15.1171 | 15.1017 | 15.0852 | 15.0655 | 13.7123 | 13.5344 | 13.3476 | 13.1456 | 13.0807 | 12.8821 | 12.7087 | 12.5381 | 15.213 | 15.1988 | 15.1817 | 15.1727 | 15.1727 | 15.1727 | 15.1727 | 13.7402 | 13.5582 | 13.3615 | 13.2983 | 13.1048 | 12.9359 | 12.7697
|  | DALCROSS | CT |  |  |  | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 14.5006 | 14.3264 | 14.2536 | 14.0578 | 13.9438 | 13.8439 | 15.1435 | 15.1323 | 15.1195 | 15.1055 | 15.0899 | 15.0718 | 13.7704 | 13.5979 | 13.4113 | 13.2058 | 13.1199 | 12.8889 | 12.7544 | 12.6366 | 15.2135 | 15.2001 | 15.1847 | 15.1727 | 15.1727 | 15.1727 | 15.1727 | 15.1727 | 13.6203 | 13.4201 | 13.3365 | 13.1115 | 12.9805 | 12.8657
|  | DALCROSS | LW |  |  |  | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 14.4466 | 14.2754 | 14.2204 | 14.052 | 13.905 | 13.7604 | 15.143 | 15.1312 | 15.1171 | 15.1017 | 15.0852 | 15.0655 | 13.7123 | 13.5344 | 13.3476 | 13.1456 | 13.0807 | 12.8821 | 12.7087 | 12.5381 | 15.213 | 15.1988 | 15.1817 | 15.1727 | 15.1727 | 15.1727 | 15.1727 | 13.7402 | 13.5582 | 13.3615 | 13.2983 | 13.1048 | 12.9359 | 12.7697
|  | DALCROSS | ST |  |  |  | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 14.5205 | 15.1491 | 15.1437 | 15.1369 | 15.1287 | 15.1204 | 15.1104 | 15.099 | 15.0861 | 15.0715 | 13.7952 | 13.7526 | 13.5945 | 13.5094 | 13.4348 | 15.2203 | 15.2139 | 15.2056 | 15.1958 | 15.1858 | 15.1737 | 15.1727 | 15.1727 | 15.1727 | 15.1727 | 15.1727 | 13.7987 | 13.7158 | 13.6432
|  | DALCROSS | FS |  |  |  | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 16.4176 | 15.153 | 15.1507 | 15.1476 | 15.1442 | 15.1406 | 15.1364 | 15.1318 | 15.1266 | 15.121 | 15.1149 | 15.1126 | 15.1034 | 15.0989 | 15.0956 | 15.225 | 15.2222 | 15.2185 | 15.2144 | 15.2101 | 15.2051 | 15.1995 | 15.1933 | 15.1865 | 15.1791 | 15.1764 | 15.1727 | 15.1727 | 15.1727
| TAYNUILT | DALMALLY | MINIMUM HEADROOM | NN 15538 26930 | YES | YES | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.0956 | 1.0938 | 1.092 | 1.092 | 1.092 | 1.092 | 1.092 | 1.092 | 1.092 | 1.092 | 1.092 | 0.99995 | 0.96288 | 0.92633 | 1.1138 | 1.1131 | 1.1123 | 1.112 | 1.1119 | 1.1119 | 1.1119 | 1.1119 | 1.1119 | 1.1119 | 1.1119 | 1.1119 | 0.97004 | 0.93347
|  | DALMALLY | CT |  |  |  | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.0959 | 1.0944 | 1.0926 | 1.092 | 1.092 | 1.092 | 1.092 | 1.092 | 1.092 | 1.092 | 1.092 | 1.092 | 0.99192 | 0.96651 | 1.1138 | 1.1133 | 1.1127 | 1.1124 | 1.1122 | 1.1119 | 1.1119 | 1.1119 | 1.1119 | 1.1119 | 1.1119 | 1.1119 | 0.99909 | 0.97367
|  | DALMALLY | LW |  |  |  | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.0956 | 1.0938 | 1.092 | 1.092 | 1.092 | 1.092 | 1.092 | 1.092 | 1.092 | 1.092 | 1.092 | 0.99995 | 0.96288 | 0.92633 | 1.1138 | 1.1131 | 1.1123 | 1.112 | 1.1119 | 1.1119 | 1.1119 | 1.1119 | 1.1119 | 1.1119 | 1.1119 | 1.1119 | 0.97004 | 0.93347
|  | DALMALLY | ST |  |  |  | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.0965 | 1.0956 | 1.0945 | 1.0941 | 1.0931 | 1.092 | 1.092 | 1.092 | 1.092 | 1.092 | 1.092 | 1.092 | 1.092 | 0.99616 | 1.1141 | 1.1138 | 1.1134 | 1.1132 | 1.1129 | 1.1125 | 1.1121 | 1.1119 | 1.1119 | 1.1119 | 1.1119 | 1.1119 | 1.1119 | 1.1119
|  | DALMALLY | FS |  |  |  | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.1768 | 1.0973 | 1.0967 | 1.0962 | 1.096 | 1.0956 | 1.0952 | 1.0948 | 1.0944 | 1.0939 | 1.0935 | 1.0932 | 1.092 | 1.092 | 1.092 | 1.1143 | 1.1141 | 1.1139 | 1.1139 | 1.1137 | 1.1136 | 1.1135 | 1.1133 | 1.1132 | 1.113 | 1.1129 | 1.1123 | 1.1119 | 1.1119
| TAYNUILT | DALMALLY SCHOOL | MINIMUM HEADROOM | NN 17249 27128 | YES | YES | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315
|  | DALMALLY SCHOOL | CT |  |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315
|  | DALMALLY SCHOOL | LW |  |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315
|  | DALMALLY SCHOOL | ST |  |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315
|  | DALMALLY SCHOOL | FS |  |  |  | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315
| INVERNESS | DALNEIGH | MINIMUM HEADROOM | NH 65564 44955 | YES | YES | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 17.1175 | 16.9711 | 16.7931 | 16.6355 | 16.6052 | 16.5812 | 16.5575 | 16.532 | 16.5066 | 16.4814 | 16.4566 | 16.3657 | 11.046 | 10.0182 | 17.4086 | 17.351 | 17.2886 | 17.2455 | 17.2032 | 17.1656 | 17.1656 | 17.1656 | 17.1656 | 17.1656 | 17.1656 | 17.1656 | 11.167 | 10.1271
|  | DALNEIGH | CT |  |  |  | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 17.1282 | 17.0197 | 16.8964 | 16.7805 | 16.6693 | 16.6189 | 16.6023 | 16.5844 | 16.5668 | 16.5494 | 16.5323 | 16.4676 | 16.3985 | 11.7118 | 17.4129 | 17.3702 | 17.3216 | 17.2853 | 17.2561 | 17.227 | 17.198 | 17.167 | 17.1656 | 17.1656 | 17.1656 | 17.1656 | 17.1656 | 11.8408
|  | DALNEIGH | LW |  |  |  | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 17.1175 | 16.9711 | 16.7931 | 16.6355 | 16.6052 | 16.5812 | 16.5575 | 16.532 | 16.5066 | 16.4814 | 16.4566 | 16.3657 | 11.046 | 10.0182 | 17.4086 | 17.351 | 17.2886 | 17.2455 | 17.2032 | 17.1656 | 17.1656 | 17.1656 | 17.1656 | 17.1656 | 17.1656 | 17.1656 | 11.167 | 10.1271
|  | DALNEIGH | ST |  |  |  | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 17.1699 | 17.1272 | 17.0633 | 16.9912 | 16.936 | 16.8809 | 16.8262 | 16.7677 | 16.7111 | 16.6608 | 16.6263 | 16.5871 | 16.5457 | 16.5049 | 17.4293 | 17.4125 | 17.3873 | 17.3589 | 17.3372 | 17.3155 | 17.297 | 17.2821 | 17.2676 | 17.2534 | 17.2398 | 17.1717 | 17.1656 | 17.1656
|  | DALNEIGH | FS |  |  |  | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 19.3618 | 17.1953 | 17.1897 | 17.1696 | 17.148 | 17.1294 | 17.1108 | 17.0872 | 17.0641 | 17.0414 | 17.0192 | 16.9977 | 16.8959 | 16.7945 | 16.6944 | 17.4392 | 17.437 | 17.4291 | 17.4206 | 17.4133 | 17.406 | 17.3967 | 17.3876 | 17.3787 | 17.3699 | 17.3615 | 17.3214 | 17.2889 | 17.2634
| COUPAR ANGUS | DALRULZION | MINIMUM HEADROOM | NO 13498 58153 | YES | YES | 3.5123 | 3.5106 | 3.5085 | 3.5064 | 3.5044 | 3.5024 | 3.5004 | 3.4983 | 3.4963 | 3.4942 | 3.4921 | 3.403 | 3.3928 | 2.4424 | 3.3611 | 3.3551 | 3.3478 | 3.3406 | 3.3336 | 3.3267 | 3.32 | 3.3127 | 3.3074 | 3.306 | 3.3046 | 2.492 | 2.3582 | 2.2261 | 3.3297 | 3.3277 | 3.3251 | 3.3226 | 3.3202 | 3.3178 | 3.3155 | 3.3129 | 3.3104 | 3.3079 | 3.3054 | 3.2075 | 2.4148 | 2.291
|  | DALRULZION | CT |  |  |  | 3.5124 | 3.5111 | 3.5096 | 3.5082 | 3.5068 | 3.5054 | 3.504 | 3.5025 | 3.5011 | 3.4996 | 3.4982 | 3.412 | 3.4049 | 3.3979 | 3.3614 | 3.3569 | 3.3518 | 3.3468 | 3.3418 | 3.337 | 3.3323 | 3.3272 | 3.3221 | 3.3171 | 3.3121 | 3.253 | 3.2482 | 2.4258 | 3.3299 | 3.3283 | 3.3265 | 3.3248 | 3.3231 | 3.3214 | 3.3197 | 3.318 | 3.3162 | 3.3145 | 3.3127 | 3.2184 | 3.2099 | 2.4783
|  | DALRULZION | LW |  |  |  | 3.5123 | 3.5106 | 3.5085 | 3.5064 | 3.5044 | 3.5024 | 3.5004 | 3.4983 | 3.4963 | 3.4942 | 3.4921 | 3.403 | 3.3928 | 2.4424 | 3.3611 | 3.3551 | 3.3478 | 3.3406 | 3.3336 | 3.3267 | 3.32 | 3.3127 | 3.3074 | 3.306 | 3.3046 | 2.492 | 2.3582 | 2.2261 | 3.3297 | 3.3277 | 3.3251 | 3.3226 | 3.3202 | 3.3178 | 3.3155 | 3.3129 | 3.3104 | 3.3079 | 3.3054 | 3.2075 | 2.4148 | 2.291
|  | DALRULZION | ST |  |  |  | 3.5129 | 3.5123 | 3.5115 | 3.5106 | 3.5094 | 3.5083 | 3.5072 | 3.5061 | 3.5049 | 3.5038 | 3.5027 | 3.4577 | 3.4525 | 3.4472 | 3.363 | 3.3612 | 3.3584 | 3.355 | 3.3511 | 3.3472 | 3.3435 | 3.3394 | 3.3355 | 3.3315 | 3.3277 | 3.2826 | 3.279 | 3.2755 | 3.3304 | 3.3298 | 3.3288 | 3.3276 | 3.3263 | 3.3249 | 3.3236 | 3.3222 | 3.3208 | 3.3195 | 3.3181 | 3.2687 | 3.2624 | 3.2561
|  | DALRULZION | FS |  |  |  | 3.5132 | 3.5131 | 3.5129 | 3.5126 | 3.5123 | 3.512 | 3.5116 | 3.5112 | 3.5108 | 3.5104 | 3.51 | 3.5082 | 3.5065 | 3.505 | 3.364 | 3.3639 | 3.3631 | 3.3621 | 3.361 | 3.3599 | 3.3585 | 3.3571 | 3.3558 | 3.3545 | 3.3531 | 3.3469 | 3.3411 | 3.3358 | 3.3308 | 3.3307 | 3.3304 | 3.3301 | 3.3297 | 3.3294 | 3.3289 | 3.3284 | 3.3279 | 3.3274 | 3.327 | 3.3248 | 3.3228 | 3.3209
| BOAT OF GARTEN | DALWHINNIE | MINIMUM HEADROOM | NN 63711 84671 | YES | YES | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.3996 | 1.3957 | 1.3908 | 1.3859 | 1.3811 | 1.3764 | 1.3718 | 1.3681 | 1.3667 | 1.3652 | 1.3638 | 1.3571 | 1.3546 | 1.3522 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231
|  | DALWHINNIE | CT |  |  |  | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.3999 | 1.3969 | 1.3935 | 1.3901 | 1.3868 | 1.3835 | 1.3803 | 1.3768 | 1.3734 | 1.3699 | 1.368 | 1.3632 | 1.3582 | 1.3558 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231
|  | DALWHINNIE | LW |  |  |  | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.3996 | 1.3957 | 1.3908 | 1.3859 | 1.3811 | 1.3764 | 1.3718 | 1.3681 | 1.3667 | 1.3652 | 1.3638 | 1.3571 | 1.3546 | 1.3522 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231
|  | DALWHINNIE | ST |  |  |  | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4009 | 1.3997 | 1.3979 | 1.3957 | 1.3935 | 1.3914 | 1.3893 | 1.387 | 1.3847 | 1.3825 | 1.3803 | 1.3697 | 1.3659 | 1.3628 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231
|  | DALWHINNIE | FS |  |  |  | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4574 | 1.4015 | 1.4014 | 1.401 | 1.4004 | 1.3997 | 1.399 | 1.3981 | 1.3972 | 1.3963 | 1.3954 | 1.3946 | 1.3904 | 1.3865 | 1.3829 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231 | 1.4231
| WILLOWDALE | DENBURN | MINIMUM HEADROOM | NJ 93484 06342 | NO | NO | 30.1068 | 29.9678 | 29.8279 | 29.6922 | 29.5606 | 29.433 | 29.3096 | 29.2145 | 29.1578 | 29.1319 | 29.1062 | 28.9728 | 28.8325 | 28.6862 | 27.317 | 27.1822 | 27.0443 | 26.9219 | 26.8109 | 26.7032 | 26.599 | 26.5173 | 26.4533 | 26.3899 | 26.3267 | 25.6242 | 25.1964 | 25.0014 | 26.1707 | 26.0258 | 25.8789 | 25.7363 | 25.5979 | 25.4637 | 25.3337 | 25.2309 | 25.1498 | 25.0694 | 24.9893 | 24.7551 | 24.6514 | 24.5409
|  | DENBURN | CT |  |  |  | 30.1068 | 29.9678 | 29.8279 | 29.6922 | 29.5606 | 29.433 | 29.3096 | 29.2145 | 29.1578 | 29.1319 | 29.1062 | 28.9728 | 28.8325 | 28.6862 | 27.317 | 27.1822 | 27.0443 | 26.9219 | 26.8109 | 26.7032 | 26.599 | 26.5173 | 26.4533 | 26.3899 | 26.3267 | 25.9403 | 25.5445 | 25.1504 | 26.1707 | 26.0258 | 25.8789 | 25.7363 | 25.5979 | 25.4637 | 25.3337 | 25.2309 | 25.1498 | 25.0694 | 24.9893 | 24.7551 | 24.6514 | 24.5409
|  | DENBURN | LW |  |  |  | 30.2595 | 30.1679 | 30.057 | 29.9464 | 29.8363 | 29.7831 | 29.7533 | 29.7201 | 29.6862 | 29.6519 | 29.617 | 29.4084 | 29.1775 | 28.9352 | 27.4412 | 27.3344 | 27.2134 | 27.1154 | 27.0178 | 26.9208 | 26.8245 | 26.7196 | 26.6148 | 26.5102 | 26.402 | 25.6242 | 25.1964 | 25.0014 | 26.3188 | 26.215 | 26.0892 | 25.9639 | 25.8395 | 25.7157 | 25.593 | 25.4726 | 25.4488 | 25.4244 | 25.3997 | 25.269 | 25.1176 | 24.9536
|  | DENBURN | ST |  |  |  | 30.2991 | 30.2557 | 30.1914 | 30.1159 | 30.03 | 29.9459 | 29.8637 | 29.849 | 29.8325 | 29.8163 | 29.8005 | 29.7169 | 29.6373 | 29.554 | 27.4806 | 27.4296 | 27.353 | 27.263 | 27.1862 | 27.111 | 27.0375 | 26.9588 | 26.8793 | 26.8011 | 26.7242 | 26.3307 | 25.9443 | 25.5593 | 26.3605 | 26.3111 | 26.2376 | 26.1509 | 26.0524 | 25.956 | 25.8617 | 25.7608 | 25.6589 | 25.5674 | 25.5597 | 25.5175 | 25.4787 | 25.4358
|  | DENBURN | FS |  |  |  | 30.3162 | 30.3085 | 30.2886 | 30.2666 | 30.2346 | 30.2029 | 30.1646 | 30.1269 | 30.0899 | 30.0536 | 30.018 | 29.8381 | 29.722 | 29.6653 | 27.5036 | 27.4964 | 27.4751 | 27.4513 | 27.4152 | 27.3794 | 27.3355 | 27.2923 | 27.2499 | 27.2123 | 27.1808 | 27.0228 | 26.8682 | 26.7201 | 26.3813 | 26.3734 | 26.3518 | 26.3277 | 26.292 | 26.2566 | 26.2135 | 26.1712 | 26.1296 | 26.0888 | 26.0488 | 25.8479 | 25.6515 | 25.4634
| TAYNUILT | DERVAIG | MINIMUM HEADROOM | NM 42441 51227 | YES | YES | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 3.7474 | 3.0209 | 3.0209 | 5.5406 | 5.5284 | 5.5136 | 5.5002 | 5.4875 | 5.475 | 5.4629 | 5.4497 | 5.4366 | 5.4274 | 5.4201 | 3.7031 | 2.8797 | 2.7079 | 3.6902 | 3.6813 | 3.6704 | 3.6605 | 3.6508 | 3.6398 | 3.6291 | 3.6175 | 3.6059 | 3.5945 | 3.5831 | 2.5424 | 1.5472 | 1.37
|  | DERVAIG | CT |  |  |  | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 3.7474 | 3.0209 | 3.0209 | 5.542 | 5.5328 | 5.5223 | 5.5127 | 5.5033 | 5.4936 | 5.4845 | 5.4747 | 5.4653 | 5.4562 | 5.4472 | 3.7782 | 2.9995 | 2.8637 | 3.6912 | 3.6844 | 3.6767 | 3.6697 | 3.6628 | 3.6557 | 3.6482 | 3.6395 | 3.6313 | 3.6232 | 3.6153 | 2.6284 | 1.6708 | 1.5307
|  | DERVAIG | LW |  |  |  | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 3.7474 | 3.0209 | 3.0209 | 5.5406 | 5.5284 | 5.5136 | 5.5002 | 5.4875 | 5.475 | 5.4629 | 5.4497 | 5.4366 | 5.4274 | 5.4201 | 3.7031 | 2.8797 | 2.7079 | 3.6902 | 3.6813 | 3.6704 | 3.6605 | 3.6508 | 3.6398 | 3.6291 | 3.6175 | 3.6059 | 3.5945 | 3.5831 | 2.5424 | 1.5472 | 1.37
|  | DERVAIG | ST |  |  |  | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.5802 | 3.7736 | 3.7736 | 5.547 | 5.543 | 5.5371 | 5.5307 | 5.5174 | 5.5041 | 5.4913 | 5.4775 | 5.4642 | 5.4512 | 5.4385 | 5.2017 | 3.771 | 3.7 | 3.6949 | 3.6919 | 3.6876 | 3.6829 | 3.6732 | 3.6634 | 3.654 | 3.642 | 3.6303 | 3.6188 | 3.6076 | 3.112 | 2.6226 | 2.5412
|  | DERVAIG | FS |  |  |  | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.9866 | 5.5508 | 5.5501 | 5.5481 | 5.5461 | 5.5417 | 5.5373 | 5.5318 | 5.5264 | 5.5211 | 5.5158 | 5.5108 | 5.4868 | 5.4645 | 5.4437 | 3.6977 | 3.6971 | 3.6956 | 3.6942 | 3.691 | 3.6878 | 3.6837 | 3.6797 | 3.6758 | 3.672 | 3.6683 | 3.6503 | 3.6305 | 3.6122
| BEAULY | DINGWALL | MINIMUM HEADROOM | NH 53956 59680 | NO | YES | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 13.4188 | 12.6225 | 11.8438 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 12.8298 | 11.8864 | 10.9639 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7139 | 12.2267 | 11.337 | 10.4383
|  | DINGWALL | CT |  |  |  | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 13.4941 | 12.9186 | 12.353 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 12.919 | 12.2372 | 11.5671 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7139 | 12.3108 | 11.6678 | 11.0359
|  | DINGWALL | LW |  |  |  | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 13.4188 | 12.6225 | 11.8438 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 12.8298 | 11.8864 | 10.9639 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 12.2267 | 11.337 | 10.4383
|  | DINGWALL | ST |  |  |  | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.1797 | 14.1797 | 14.1797 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.5124 | 13.5124 | 13.5124 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.4088 | 13.4088 | 13.0919
|  | DINGWALL | FS |  |  |  | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 14.5132 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.6688 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262 | 13.7262
| CARRADALE | DIPPEN | MINIMUM HEADROOM | NR 80026 37592 | YES | YES | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.3222 | 1.3195 | 1.3173 | 1.3163 | 1.3153 | 1.3144 | 1.3135 | 1.3125 | 1.3115 | 1.3106 | 1.3096 | 1.3018 | 1.3018 | 1.3018 | 1.3752 | 1.3748 | 1.3743 | 1.374 | 1.3736 | 1.3733 | 1.373 | 1.3726 | 1.3723 | 1.372 | 1.3716 | 1.3675 | 1.3671 | 1.3671
|  | DIPPEN | CT |  |  |  | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.3225 | 1.3203 | 1.3186 | 1.3174 | 1.3166 | 1.3158 | 1.315 | 1.3142 | 1.3135 | 1.3128 | 1.3122 | 1.3018 | 1.3018 | 1.3018 | 1.3753 | 1.3749 | 1.3746 | 1.3743 | 1.3741 | 1.3738 | 1.3735 | 1.3732 | 1.373 | 1.3728 | 1.3725 | 1.3675 | 1.3671 | 1.3671
|  | DIPPEN | LW |  |  |  | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.3222 | 1.3195 | 1.3173 | 1.3163 | 1.3153 | 1.3144 | 1.3135 | 1.3125 | 1.3115 | 1.3106 | 1.3096 | 1.3018 | 1.3018 | 1.3018 | 1.3752 | 1.3748 | 1.3743 | 1.374 | 1.3736 | 1.3733 | 1.373 | 1.3726 | 1.3723 | 1.372 | 1.3716 | 1.3684 | 1.3671 | 1.3671
|  | DIPPEN | ST |  |  |  | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.3234 | 1.3223 | 1.3212 | 1.3204 | 1.3187 | 1.3172 | 1.3163 | 1.3153 | 1.3145 | 1.3136 | 1.3128 | 1.3088 | 1.3049 | 1.3018 | 1.3755 | 1.3753 | 1.3751 | 1.3749 | 1.3746 | 1.3743 | 1.374 | 1.3736 | 1.3733 | 1.373 | 1.3727 | 1.3714 | 1.37 | 1.3686
|  | DIPPEN | FS |  |  |  | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.5797 | 1.3241 | 1.3237 | 1.3233 | 1.323 | 1.3224 | 1.3218 | 1.3211 | 1.3204 | 1.3197 | 1.319 | 1.3184 | 1.3164 | 1.3149 | 1.3135 | 1.3759 | 1.3757 | 1.3755 | 1.3754 | 1.3753 | 1.3752 | 1.375 | 1.3749 | 1.3748 | 1.3747 | 1.3745 | 1.374 | 1.3735 | 1.373
| BRORA | DORNOCH | MINIMUM HEADROOM | NH 79721 89953 | YES | YES | 6.5177 | 6.515 | 6.5117 | 6.5086 | 6.5054 | 6.5001 | 6.497 | 6.4936 | 6.4903 | 6.487 | 6.4838 | 6.4609 | 6.4375 | 6.4171 | 5.7286 | 5.715 | 5.6983 | 5.6819 | 5.6659 | 5.6384 | 5.6225 | 5.6117 | 5.6077 | 5.6039 | 5.6039 | 5.6039 | 5.6039 | 3.8841 | 6.2066 | 6.2037 | 6.2001 | 6.1966 | 6.1932 | 6.1873 | 6.1839 | 6.1802 | 6.1766 | 6.173 | 6.1695 | 6.1444 | 6.1187 | 6.0936
|  | DORNOCH | CT |  |  |  | 6.5179 | 6.516 | 6.5138 | 6.5116 | 6.5094 | 6.5053 | 6.5031 | 6.5007 | 6.4983 | 6.4959 | 6.4936 | 6.4761 | 6.4585 | 6.4411 | 5.7301 | 5.7202 | 5.7088 | 5.6975 | 5.6862 | 5.6651 | 5.6538 | 5.6415 | 5.6292 | 5.6169 | 5.6117 | 5.6039 | 5.6039 | 5.6039 | 6.2069 | 6.2048 | 6.2024 | 6.2 | 6.1975 | 6.193 | 6.1906 | 6.188 | 6.1853 | 6.1827 | 6.1802 | 6.1611 | 6.1417 | 6.1227
|  | DORNOCH | LW |  |  |  | 6.5177 | 6.515 | 6.5117 | 6.5086 | 6.5054 | 6.5001 | 6.497 | 6.4936 | 6.4903 | 6.487 | 6.4838 | 6.4609 | 6.4375 | 6.4171 | 5.7286 | 5.715 | 5.6983 | 5.6819 | 5.6659 | 5.6384 | 5.6225 | 5.6117 | 5.6077 | 5.6039 | 5.6039 | 5.6039 | 5.6039 | 3.8841 | 6.2066 | 6.2037 | 6.2001 | 6.1966 | 6.1932 | 6.1873 | 6.1839 | 6.1802 | 6.1766 | 6.173 | 6.1695 | 6.1444 | 6.1187 | 6.0936
|  | DORNOCH | ST |  |  |  | 6.5188 | 6.5181 | 6.5169 | 6.5156 | 6.5137 | 6.5105 | 6.5087 | 6.5067 | 6.5047 | 6.5027 | 6.5008 | 6.4916 | 6.4825 | 6.4734 | 5.7346 | 5.7308 | 5.7249 | 5.7179 | 5.7082 | 5.6921 | 5.6826 | 5.6723 | 5.6621 | 5.6519 | 5.6423 | 5.6093 | 5.6039 | 5.6039 | 6.2079 | 6.2071 | 6.2058 | 6.2043 | 6.2022 | 6.1988 | 6.1968 | 6.1946 | 6.1924 | 6.1902 | 6.1881 | 6.178 | 6.168 | 6.1581
|  | DORNOCH | FS |  |  |  | 6.5194 | 6.5193 | 6.519 | 6.5185 | 6.5179 | 6.5168 | 6.516 | 6.5152 | 6.5144 | 6.5136 | 6.5128 | 6.5092 | 6.5059 | 6.5027 | 5.7375 | 5.7371 | 5.7353 | 5.7331 | 5.7299 | 5.7241 | 5.7199 | 5.7158 | 5.7117 | 5.7076 | 5.7038 | 5.6855 | 5.6684 | 5.6521 | 6.2085 | 6.2084 | 6.208 | 6.2076 | 6.2069 | 6.2056 | 6.2048 | 6.2039 | 6.203 | 6.2021 | 6.2013 | 6.1974 | 6.1937 | 6.1902
| CLACHAN | DOUGLAS PIER | MINIMUM HEADROOM | NS 19396 99616 | YES | YES | 2.9787 | 2.9761 | 2.9729 | 2.9697 | 2.9666 | 2.9636 | 2.9624 | 2.9624 | 2.9624 | 2.9624 | 2.9624 | 2.4373 | 2.3602 | 2.2841 | 2.9696 | 2.9566 | 2.9536 | 2.9536 | 2.9536 | 2.9536 | 2.9536 | 2.9536 | 2.9536 | 2.9536 | 2.9536 | 2.4206 | 2.3296 | 2.2399 | 2.9975 | 2.9943 | 2.9905 | 2.9867 | 2.983 | 2.9793 | 2.9757 | 2.9719 | 2.968 | 2.9642 | 2.9604 | 2.4256 | 2.3346 | 2.2448
|  | DOUGLAS PIER | CT |  |  |  | 2.9788 | 2.9769 | 2.9746 | 2.9724 | 2.9702 | 2.968 | 2.9659 | 2.9637 | 2.9624 | 2.9624 | 2.9624 | 2.9624 | 2.4641 | 2.3888 | 2.9703 | 2.9605 | 2.9536 | 2.9536 | 2.9536 | 2.9536 | 2.9536 | 2.9536 | 2.9536 | 2.9536 | 2.9536 | 2.9536 | 2.4522 | 2.3634 | 2.9977 | 2.9953 | 2.9926 | 2.9899 | 2.9873 | 2.9847 | 2.9822 | 2.9794 | 2.9767 | 2.974 | 2.9713 | 2.9632 | 2.4572 | 2.3683
|  | DOUGLAS PIER | LW |  |  |  | 2.9787 | 2.9761 | 2.9729 | 2.9697 | 2.9666 | 2.9636 | 2.9624 | 2.9624 | 2.9624 | 2.9624 | 2.9624 | 2.4373 | 2.3602 | 2.2841 | 2.9696 | 2.9566 | 2.9536 | 2.9536 | 2.9536 | 2.9536 | 2.9536 | 2.9536 | 2.9536 | 2.9536 | 2.9536 | 2.4206 | 2.3296 | 2.2399 | 2.9975 | 2.9943 | 2.9905 | 2.9867 | 2.983 | 2.9793 | 2.9757 | 2.9719 | 2.968 | 2.9642 | 2.9604 | 2.4256 | 2.3346 | 2.2448
|  | DOUGLAS PIER | ST |  |  |  | 2.9799 | 2.9798 | 2.9796 | 2.9793 | 2.9787 | 2.9781 | 2.9775 | 2.9768 | 2.9762 | 2.9756 | 2.975 | 2.972 | 2.9691 | 2.9662 | 2.9759 | 2.9751 | 2.974 | 2.9726 | 2.9696 | 2.9666 | 2.9636 | 2.9605 | 2.9573 | 2.9543 | 2.9536 | 2.9536 | 2.9536 | 2.9536 | 2.999 | 2.9988 | 2.9985 | 2.9982 | 2.9975 | 2.9967 | 2.996 | 2.9953 | 2.9945 | 2.9938 | 2.993 | 2.9895 | 2.986 | 2.9825
|  | DOUGLAS PIER | FS |  |  |  | 2.98 | 2.98 | 2.98 | 2.9799 | 2.9797 | 2.9795 | 2.9792 | 2.979 | 2.9787 | 2.9785 | 2.9782 | 2.9771 | 2.976 | 2.975 | 2.9763 | 2.9763 | 2.9759 | 2.9756 | 2.9745 | 2.9735 | 2.9722 | 2.971 | 2.9697 | 2.9685 | 2.9673 | 2.9616 | 2.9563 | 2.9536 | 2.9991 | 2.9991 | 2.999 | 2.9989 | 2.9987 | 2.9984 | 2.9981 | 2.9978 | 2.9975 | 2.9972 | 2.9969 | 2.9955 | 2.9943 | 2.9931
| DOUNREAY | DOUNREAY | MINIMUM HEADROOM | NC 9815 6665 | NO | YES | 19.7483 | 19.6286 | 19.5143 | 19.4088 | 19.3072 | 19.2095 | 19.1156 | 19.0711 | 19.0478 | 19.0248 | 19.0021 | 18.899 | 18.8067 | 18.7131 | 18.452 | 18.3792 | 18.3091 | 18.2413 | 18.176 | 18.1131 | 18.0527 | 18.0221 | 18.0045 | 17.9872 | 17.97 | 17.9026 | 17.8417 | 17.7878 | 18.6095 | 18.5028 | 18.4011 | 18.3031 | 18.2087 | 18.1179 | 18.0308 | 17.9906 | 17.9707 | 17.9509 | 17.9315 | 17.8365 | 17.7552 | 17.6726
|  | DOUNREAY | CT |  |  |  | 19.7483 | 19.6286 | 19.5143 | 19.4088 | 19.3072 | 19.2095 | 19.1156 | 19.0711 | 19.0478 | 19.0248 | 19.0021 | 18.899 | 18.8067 | 18.7131 | 18.452 | 18.3792 | 18.3091 | 18.2413 | 18.176 | 18.1131 | 18.0527 | 18.0221 | 18.0045 | 17.9872 | 17.97 | 17.9026 | 17.8417 | 17.7878 | 18.6095 | 18.5028 | 18.4011 | 18.3031 | 18.2087 | 18.1179 | 18.0308 | 17.9906 | 17.9707 | 17.9509 | 17.9315 | 17.8365 | 17.7552 | 17.6726
|  | DOUNREAY | LW |  |  |  | 19.9547 | 19.933 | 19.9082 | 19.8814 | 19.8529 | 19.8229 | 19.7916 | 19.7621 | 19.7336 | 19.7056 | 19.6772 | 19.5412 | 19.4088 | 19.2704 | 18.573 | 18.5567 | 18.5377 | 18.5177 | 18.4967 | 18.4749 | 18.4524 | 18.4307 | 18.4086 | 18.3862 | 18.3636 | 18.2744 | 18.1873 | 18.0967 | 18.7984 | 18.7824 | 18.7643 | 18.7445 | 18.723 | 18.7 | 18.6757 | 18.6535 | 18.6307 | 18.6073 | 18.5836 | 18.4583 | 18.3365 | 18.209
|  | DOUNREAY | ST |  |  |  | 19.9861 | 19.9778 | 19.9691 | 19.9602 | 19.9516 | 19.9432 | 19.9351 | 19.9273 | 19.9161 | 19.9052 | 19.8946 | 19.8457 | 19.802 | 19.7615 | 18.5926 | 18.5867 | 18.5799 | 18.5726 | 18.5671 | 18.5618 | 18.5566 | 18.5515 | 18.5444 | 18.5376 | 18.5309 | 18.4999 | 18.472 | 18.446 | 18.8257 | 18.8194 | 18.8132 | 18.8071 | 18.7998 | 18.7926 | 18.7857 | 18.779 | 18.7693 | 18.7598 | 18.7507 | 18.7084 | 18.6709 | 18.6363
|  | DOUNREAY | FS |  |  |  | 19.9798 | 19.9727 | 19.9618 | 19.951 | 19.9407 | 19.9307 | 19.9206 | 19.9108 | 19.9011 | 19.8915 | 19.882 | 19.8256 | 19.776 | 19.7299 | 18.5895 | 18.5852 | 18.5784 | 18.5714 | 18.5653 | 18.5592 | 18.5531 | 18.5471 | 18.5412 | 18.5354 | 18.5297 | 18.4957 | 18.4657 | 18.4379 | 18.8194 | 18.813 | 18.8036 | 18.7943 | 18.7851 | 18.776 | 18.7671 | 18.7583 | 18.7496 | 18.741 | 18.7326 | 18.682 | 18.6375 | 18.5963
| ARDMORE | DRIMORE | MINIMUM HEADROOM | NF 77377 40049 | YES | YES | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 2.3248 | 2.274 | 3.052 | 3.052 | 3.052 | 3.052 | 3.052 | 3.052 | 3.052 | 3.052 | 3.052 | 3.052 | 3.052 | 3.052 | 2.2901 | 2.2304 | 3.1312 | 3.1305 | 3.1297 | 3.129 | 3.1282 | 3.1275 | 3.1267 | 3.1254 | 3.1241 | 3.1228 | 3.1215 | 3.1148 | 2.8265 | 2.4846
|  | DRIMORE | CT |  |  |  | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 2.3609 | 2.324 | 3.052 | 3.052 | 3.052 | 3.052 | 3.052 | 3.052 | 3.052 | 3.052 | 3.052 | 3.052 | 3.052 | 3.052 | 2.3325 | 2.2892 | 3.1312 | 3.1307 | 3.1302 | 3.1296 | 3.1291 | 3.1286 | 3.1281 | 3.1275 | 3.127 | 3.1264 | 3.1259 | 3.1171 | 2.8303 | 2.8264
|  | DRIMORE | LW |  |  |  | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 2.3248 | 2.274 | 3.052 | 3.052 | 3.052 | 3.052 | 3.052 | 3.052 | 3.052 | 3.052 | 3.052 | 3.052 | 3.052 | 3.052 | 2.2901 | 2.2304 | 3.1312 | 3.1305 | 3.1297 | 3.129 | 3.1282 | 3.1275 | 3.1267 | 3.126 | 3.1252 | 3.1244 | 3.1237 | 3.1148 | 2.8265 | 2.4846
|  | DRIMORE | ST |  |  |  | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 3.1765 | 3.1765 | 3.052 | 3.052 | 3.052 | 3.052 | 3.052 | 3.052 | 3.052 | 3.052 | 3.052 | 3.052 | 3.052 | 3.052 | 2.4648 | 2.4393 | 3.1314 | 3.1312 | 3.1309 | 3.1305 | 3.1292 | 3.128 | 3.1267 | 3.1254 | 3.1241 | 3.1228 | 3.1215 | 3.1171 | 2.9733 | 2.971
|  | DRIMORE | FS |  |  |  | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 3.3124 | 3.052 | 3.052 | 3.052 | 3.052 | 3.052 | 3.052 | 3.052 | 3.052 | 3.052 | 3.052 | 3.052 | 3.052 | 3.052 | 3.052 | 3.1315 | 3.1315 | 3.1314 | 3.1313 | 3.1309 | 3.1304 | 3.1299 | 3.1293 | 3.1288 | 3.1283 | 3.1278 | 3.1254 | 3.1231 | 3.121
| CEANNACROC | DRUMNADROCHIT | MINIMUM HEADROOM | NH 50306 29824 | YES | YES | 7.3836 | 7.3805 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 6.6968 | 6.6947 | 6.6922 | 6.6896 | 6.6872 | 6.6847 | 6.6823 | 6.6797 | 6.6772 | 6.6746 | 6.6721 | 5.663 | 5.4282 | 5.1821 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 5.658 | 5.4141
|  | DRUMNADROCHIT | CT |  |  |  | 7.384 | 7.3819 | 7.3795 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 6.6971 | 6.6957 | 6.694 | 6.6924 | 6.6908 | 6.6892 | 6.6877 | 6.686 | 6.6844 | 6.6827 | 6.6811 | 6.6719 | 6.6625 | 5.5448 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552
|  | DRUMNADROCHIT | LW |  |  |  | 7.3836 | 7.3805 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 6.6968 | 6.6947 | 6.6922 | 6.6896 | 6.6872 | 6.6847 | 6.6823 | 6.6797 | 6.6772 | 6.6746 | 6.6721 | 5.663 | 5.4282 | 5.1821 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 5.658 | 5.4141
|  | DRUMNADROCHIT | ST |  |  |  | 7.385 | 7.3841 | 7.3827 | 7.381 | 7.3793 | 7.3777 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 7.3775 | 6.6978 | 6.6972 | 6.6962 | 6.6951 | 6.694 | 6.6928 | 6.6918 | 6.6906 | 6.6895 | 6.6883 | 6.6873 | 6.6819 | 6.6764 | 6.671 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552
|  | DRUMNADROCHIT | FS |  |  |  | 7.3858 | 7.3857 | 7.3853 | 7.3848 | 7.3842 | 7.3837 | 7.383 | 7.3823 | 7.3817 | 7.381 | 7.3804 | 7.3775 | 7.3775 | 7.3775 | 6.6983 | 6.6983 | 6.698 | 6.6976 | 6.6973 | 6.6969 | 6.6964 | 6.696 | 6.6955 | 6.6951 | 6.6947 | 6.6926 | 6.6907 | 6.6888 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552 | 6.9552
| GRUDIE BRIDGE | DRUMRUNIE | MINIMUM HEADROOM | NC 16664 05298 | YES | YES | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.0805 | 1.0799 | 1.0791 | 1.0783 | 1.0776 | 1.0768 | 1.0761 | 1.0754 | 1.0748 | 1.0743 | 1.0737 | 1.0719 | 0.9971 | 0.97049 | 1.0909 | 1.0906 | 1.0902 | 1.0898 | 1.0895 | 1.0895 | 1.0895 | 1.0895 | 1.0895 | 1.0895 | 1.0895 | 1.0895 | 1.0895 | 0.98595
|  | DRUMRUNIE | CT |  |  |  | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.0805 | 1.0801 | 1.0795 | 1.079 | 1.0785 | 1.0779 | 1.0774 | 1.0769 | 1.0764 | 1.0758 | 1.0754 | 1.0719 | 1.0719 | 0.99221 | 1.0909 | 1.0907 | 1.0904 | 1.0902 | 1.0899 | 1.0897 | 1.0895 | 1.0895 | 1.0895 | 1.0895 | 1.0895 | 1.0895 | 1.0895 | 1.0895
|  | DRUMRUNIE | LW |  |  |  | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.0805 | 1.0799 | 1.0791 | 1.0783 | 1.0776 | 1.0768 | 1.0761 | 1.0754 | 1.0748 | 1.0743 | 1.0737 | 1.0719 | 0.9971 | 0.97049 | 1.0909 | 1.0906 | 1.0902 | 1.0898 | 1.0895 | 1.0895 | 1.0895 | 1.0895 | 1.0895 | 1.0895 | 1.0895 | 1.0895 | 1.0895 | 0.98595
|  | DRUMRUNIE | ST |  |  |  | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.0807 | 1.0805 | 1.0802 | 1.0799 | 1.0794 | 1.079 | 1.0786 | 1.0782 | 1.0778 | 1.0774 | 1.077 | 1.0751 | 1.0736 | 1.0727 | 1.091 | 1.0909 | 1.0908 | 1.0906 | 1.0904 | 1.0902 | 1.09 | 1.0898 | 1.0896 | 1.0895 | 1.0895 | 1.0895 | 1.0895 | 1.0895
|  | DRUMRUNIE | FS |  |  |  | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.0808 | 1.0808 | 1.0807 | 1.0806 | 1.0802 | 1.0798 | 1.0794 | 1.0789 | 1.0784 | 1.0779 | 1.0775 | 1.0753 | 1.0738 | 1.0727 | 1.0911 | 1.091 | 1.091 | 1.091 | 1.0908 | 1.0906 | 1.0903 | 1.0901 | 1.0899 | 1.0896 | 1.0895 | 1.0895 | 1.0895 | 1.0895
| STRATHLEVEN | DRYMEN | MINIMUM HEADROOM | NS 48494 88026 | YES | YES | 0.79085 | 0.74456 | 0.69614 | 0.64945 | 0.60449 | 0.56127 | 0.51977 | 0.493 | 0.47969 | 0.46651 | 0.45354 | 0.38605 | 0.28019 | -0.096913 | 2.5511 | 2.5212 | 2.489 | 2.4571 | 2.4255 | 2.3943 | 2.3642 | 2.3423 | 2.3276 | 2.3128 | 2.2978 | 2.1724 | 0.75114 | 0.36775 | 0.82933 | 0.76835 | 0.70227 | 0.63672 | 0.57149 | 0.5071 | 0.44484 | 0.39901 | 0.36739 | 0.33573 | 0.30336 | 0.027199 | -0.35203 | -0.76476
|  | DRYMEN | CT |  |  |  | 0.79085 | 0.74456 | 0.69614 | 0.64945 | 0.60449 | 0.56127 | 0.51977 | 0.493 | 0.47969 | 0.46651 | 0.45354 | 0.38605 | 0.30769 | 0.044016 | 2.5511 | 2.5212 | 2.489 | 2.4571 | 2.4255 | 2.3943 | 2.3642 | 2.3423 | 2.3276 | 2.3128 | 2.2978 | 2.1724 | 0.91968 | 0.63905 | 0.82933 | 0.76835 | 0.70227 | 0.63672 | 0.57149 | 0.5071 | 0.44484 | 0.39901 | 0.36739 | 0.33573 | 0.30336 | 0.027199 | -0.26613 | -0.56686
|  | DRYMEN | LW |  |  |  | 0.87277 | 0.86583 | 0.85801 | 0.8494 | 0.84007 | 0.83011 | 0.81958 | 0.80591 | 0.79182 | 0.77744 | 0.76287 | 0.62913 | 0.28019 | -0.096913 | 2.5948 | 2.5786 | 2.5582 | 2.5368 | 2.5142 | 2.4908 | 2.4673 | 2.4405 | 2.4125 | 2.3844 | 2.3557 | 2.1954 | 0.75114 | 0.36775 | 0.91616 | 0.88022 | 0.8349 | 0.78721 | 0.73701 | 0.68506 | 0.63297 | 0.57376 | 0.51207 | 0.44994 | 0.38672 | 0.032218 | -0.35203 | -0.76476
|  | DRYMEN | ST |  |  |  | 0.88465 | 0.88188 | 0.87919 | 0.87657 | 0.87339 | 0.87029 | 0.86728 | 0.86411 | 0.85947 | 0.85497 | 0.85059 | 0.82581 | 0.8012 | 0.77114 | 2.6051 | 2.5991 | 2.5904 | 2.58 | 2.5689 | 2.5576 | 2.5465 | 2.5345 | 2.521 | 2.5076 | 2.494 | 2.4224 | 2.3519 | 2.279 | 0.93788 | 0.92462 | 0.90516 | 0.88183 | 0.85695 | 0.8316 | 0.80665 | 0.77956 | 0.74952 | 0.71958 | 0.68918 | 0.52932 | 0.37175 | 0.20975
|  | DRYMEN | FS |  |  |  | 0.88188 | 0.87912 | 0.87503 | 0.87099 | 0.86701 | 0.86308 | 0.8592 | 0.85538 | 0.85162 | 0.8479 | 0.84424 | 0.82231 | 0.79844 | 0.77511 | 2.6058 | 2.6038 | 2.5996 | 2.5949 | 2.5896 | 2.5841 | 2.5781 | 2.5721 | 2.5659 | 2.5597 | 2.5535 | 2.5191 | 2.4831 | 2.4472 | 0.94003 | 0.9358 | 0.92677 | 0.91682 | 0.90518 | 0.89341 | 0.88022 | 0.86698 | 0.85341 | 0.83989 | 0.82622 | 0.75109 | 0.67257 | 0.59408
| DUNVEGAN | DRYNOCH | MINIMUM HEADROOM | NG 41080 31292 | YES | YES | 2.9477 | 2.9477 | 2.9477 | 2.9477 | 2.9477 | 2.4985 | 2.4345 | 2.3639 | 2.2932 | 2.223 | 2.1532 | 1.3784 | 1.1962 | 1.017 | 3.3075 | 3.3041 | 3.2999 | 3.2958 | 3.2917 | 2.4333 | 2.3599 | 2.2803 | 2.2013 | 2.1228 | 2.0448 | 1.4198 | 1.2051 | 0.994 | 3.2218 | 3.2218 | 3.2218 | 3.2218 | 2.4451 | 2.3686 | 2.2934 | 2.2121 | 2.1312 | 2.0509 | 1.9711 | 1.1617 | 0.95328 | 0.74832
|  | DRYNOCH | CT |  |  |  | 2.9477 | 2.9477 | 2.9477 | 2.9477 | 2.9477 | 2.9477 | 2.9477 | 2.9477 | 2.4698 | 2.4237 | 2.3771 | 1.629 | 1.4833 | 1.338 | 3.3078 | 3.3053 | 3.3025 | 3.2997 | 3.297 | 3.2943 | 3.2916 | 2.4536 | 2.4004 | 2.3475 | 2.295 | 1.7161 | 1.5455 | 1.3722 | 3.2218 | 3.2218 | 3.2218 | 3.2218 | 3.2218 | 2.4947 | 2.4441 | 2.3893 | 2.3349 | 2.2808 | 2.2271 | 1.4547 | 1.2837 | 1.1154
|  | DRYNOCH | LW |  |  |  | 2.9477 | 2.9477 | 2.9477 | 2.9477 | 2.9477 | 2.4985 | 2.4345 | 2.3639 | 2.2932 | 2.223 | 2.1532 | 1.3784 | 1.1962 | 1.017 | 3.3075 | 3.3041 | 3.2999 | 3.2958 | 3.2917 | 2.4333 | 2.3599 | 2.2803 | 2.2013 | 2.1228 | 2.0448 | 1.4198 | 1.2051 | 0.994 | 3.2218 | 3.2218 | 3.2218 | 3.2218 | 2.4451 | 2.3686 | 2.2934 | 2.2121 | 2.1312 | 2.0509 | 1.9711 | 1.1617 | 0.95328 | 0.74832
|  | DRYNOCH | ST |  |  |  | 2.9477 | 2.9477 | 2.9477 | 2.9477 | 2.9477 | 2.9477 | 2.9477 | 2.9477 | 2.9477 | 2.9477 | 2.9477 | 2.3173 | 2.242 | 2.1672 | 3.3089 | 3.3084 | 3.3075 | 3.3065 | 3.3055 | 3.3046 | 3.3036 | 3.3027 | 3.3017 | 3.3007 | 3.2998 | 2.3657 | 2.2793 | 2.1935 | 3.2218 | 3.2218 | 3.2218 | 3.2218 | 3.2218 | 3.2218 | 3.2218 | 3.2218 | 3.2218 | 3.2218 | 3.2218 | 2.2093 | 2.1209 | 2.0331
|  | DRYNOCH | FS |  |  |  | 2.9477 | 2.9477 | 2.9477 | 2.9477 | 2.9477 | 2.9477 | 2.9477 | 2.9477 | 2.9477 | 2.9477 | 2.9477 | 2.9477 | 2.9477 | 2.9477 | 3.3092 | 3.3092 | 3.3089 | 3.3086 | 3.3082 | 3.3079 | 3.3075 | 3.3071 | 3.3067 | 3.3064 | 3.306 | 3.3042 | 3.3025 | 3.3009 | 3.2218 | 3.2218 | 3.2218 | 3.2218 | 3.2218 | 3.2218 | 3.2218 | 3.2218 | 3.2218 | 3.2218 | 3.2218 | 3.2218 | 3.2218 | 3.2218
| KEITH | DUFFTOWN | MINIMUM HEADROOM | NJ 32060 39722 | NO | YES | 7.8307 | 7.7096 | 7.5916 | 7.4769 | 7.3663 | 7.2598 | 7.1572 | 7.0957 | 7.0641 | 7.0329 | 7.0022 | 6.8392 | 6.6606 | 6.4708 | 8.8601 | 8.736 | 8.6193 | 8.4964 | 8.3758 | 8.258 | 8.1413 | 8.0709 | 8.0238 | 7.9774 | 7.9333 | 7.7275 | 7.6042 | 7.4763 | 8.1046 | 7.9545 | 7.8144 | 7.7011 | 7.6026 | 7.5077 | 7.4164 | 7.3616 | 7.3333 | 7.3054 | 7.278 | 7.1315 | 6.9712 | 6.8009
|  | DUFFTOWN | CT |  |  |  | 7.8307 | 7.7096 | 7.5916 | 7.4769 | 7.3663 | 7.2598 | 7.1572 | 7.0957 | 7.0641 | 7.0329 | 7.0022 | 6.8392 | 6.6606 | 6.4708 | 8.8601 | 8.736 | 8.6193 | 8.4964 | 8.3758 | 8.258 | 8.1413 | 8.0709 | 8.0238 | 7.9774 | 7.9333 | 7.7275 | 7.6042 | 7.4763 | 8.1046 | 7.9545 | 7.8144 | 7.7011 | 7.6026 | 7.5077 | 7.4164 | 7.3616 | 7.3333 | 7.3054 | 7.278 | 7.1315 | 6.9712 | 6.8009
|  | DUFFTOWN | LW |  |  |  | 8.0419 | 8.0221 | 8.0006 | 7.976 | 7.9494 | 7.9211 | 7.8911 | 7.8573 | 7.8225 | 7.7871 | 7.7512 | 7.5493 | 7.3101 | 7.0378 | 9.0446 | 9.0082 | 8.9745 | 8.9278 | 8.878 | 8.8249 | 8.7691 | 8.7231 | 8.6765 | 8.6297 | 8.5827 | 8.1967 | 7.9055 | 7.7332 | 8.3336 | 8.2924 | 8.2537 | 8.2012 | 8.145 | 8.0953 | 8.0684 | 8.0382 | 8.0072 | 7.9755 | 7.9435 | 7.7623 | 7.5479 | 7.3041
|  | DUFFTOWN | ST |  |  |  | 8.0728 | 8.0649 | 8.0575 | 8.0495 | 8.0389 | 8.0285 | 8.0181 | 8.0085 | 7.9952 | 7.9823 | 7.9698 | 7.9022 | 7.838 | 7.7653 | 9.0753 | 9.0604 | 9.0484 | 9.0286 | 8.9938 | 8.9589 | 8.9227 | 8.8935 | 8.8596 | 8.8263 | 8.7949 | 8.6419 | 8.4947 | 8.3411 | 8.3708 | 8.3541 | 8.3403 | 8.3185 | 8.2807 | 8.2428 | 8.2037 | 8.1729 | 8.1609 | 8.1492 | 8.138 | 8.0771 | 8.0192 | 7.9538
|  | DUFFTOWN | FS |  |  |  | 8.0659 | 8.0585 | 8.0478 | 8.037 | 8.0258 | 8.0148 | 8.0037 | 7.993 | 7.9825 | 7.9721 | 7.9619 | 7.9017 | 7.8387 | 7.7773 | 9.0713 | 9.0621 | 9.0512 | 9.0371 | 9.018 | 8.9987 | 8.9774 | 8.9594 | 8.9416 | 8.924 | 8.9067 | 8.8163 | 8.7287 | 8.6435 | 8.3655 | 8.3547 | 8.3414 | 8.3249 | 8.3032 | 8.2813 | 8.2573 | 8.2368 | 8.2166 | 8.1965 | 8.1768 | 8.0782 | 8.0218 | 7.9671
| BRACO | DUNBLANE | MINIMUM HEADROOM | NN 77907 01544 | NO | YES | 19.6535 | 19.5615 | 19.4775 | 19.3965 | 19.3185 | 19.2435 | 19.1715 | 19.132 | 19.1123 | 19.0929 | 19.0737 | 11.5859 | 9.6145 | 7.6397 | 16.8521 | 16.6504 | 16.4347 | 16.2534 | 16.0695 | 15.9192 | 15.8587 | 15.8165 | 11.0529 | 10.4418 | 9.8225 | 7.6605 | 5.4411 | 3.1871 | 16.946 | 16.8121 | 16.6785 | 16.5466 | 16.4156 | 16.2865 | 16.1612 | 11.3212 | 10.7361 | 10.1236 | 9.486 | 7.2466 | 4.9439 | 2.6379
|  | DUNBLANE | CT |  |  |  | 19.6535 | 19.5615 | 19.4775 | 19.3965 | 19.3185 | 19.2435 | 19.1715 | 19.132 | 19.1123 | 19.0929 | 19.0737 | 18.9831 | 11.8759 | 10.4042 | 16.8521 | 16.6504 | 16.4347 | 16.2534 | 16.0695 | 15.9192 | 15.8587 | 15.8165 | 15.7855 | 15.7545 | 15.7365 | 9.9285 | 8.2748 | 6.6138 | 16.946 | 16.8121 | 16.6785 | 16.5466 | 16.4156 | 16.2865 | 16.1612 | 16.0649 | 16.0378 | 11.3532 | 10.974 | 9.3989 | 7.6874 | 5.9668
|  | DUNBLANE | LW |  |  |  | 19.8162 | 19.8025 | 19.7869 | 19.7698 | 19.7513 | 19.7315 | 19.7106 | 19.6879 | 19.6645 | 19.6406 | 19.6164 | 11.5859 | 9.6145 | 7.6397 | 16.9558 | 16.7408 | 16.5166 | 16.3061 | 16.2005 | 16.1607 | 16.1207 | 16.0919 | 11.0529 | 10.4418 | 9.8225 | 7.6605 | 5.4411 | 3.1871 | 17.1031 | 17.0248 | 16.928 | 16.8284 | 16.7253 | 16.6555 | 16.6346 | 11.3212 | 10.7361 | 10.1236 | 9.486 | 7.2466 | 4.9439 | 2.6379
|  | DUNBLANE | ST |  |  |  | 19.8398 | 19.8344 | 19.829 | 19.8238 | 19.8175 | 19.8113 | 19.8053 | 19.7998 | 19.7918 | 19.784 | 19.7764 | 19.7349 | 19.6978 | 19.658 | 17.0357 | 16.9612 | 16.8458 | 16.7059 | 16.6329 | 16.5636 | 16.4956 | 16.4222 | 16.342 | 16.2616 | 16.2251 | 16.1453 | 11.3951 | 10.3476 | 17.1463 | 17.1186 | 17.0781 | 17.0301 | 16.9977 | 16.9646 | 16.9321 | 16.8976 | 16.8586 | 16.8197 | 16.7799 | 16.6589 | 11.0714 | 10.033
|  | DUNBLANE | FS |  |  |  | 19.8344 | 19.8289 | 19.8207 | 19.8127 | 19.8048 | 19.797 | 19.7893 | 19.7817 | 19.7742 | 19.7668 | 19.7596 | 19.716 | 19.6709 | 19.6272 | 17.0698 | 17.058 | 17.0194 | 16.9742 | 16.9397 | 16.9045 | 16.8643 | 16.8236 | 16.7808 | 16.738 | 16.6942 | 16.4934 | 16.2993 | 16.1402 | 17.1528 | 17.145 | 17.1266 | 17.1062 | 17.0893 | 17.0722 | 17.0536 | 17.035 | 17.0158 | 16.9967 | 16.9773 | 16.8689 | 16.7567 | 16.644
| DUNOON | DUNOON | MINIMUM HEADROOM | NS 17135 77531 | NO | YES | 28.1196 | 28.0043 | 27.8949 | 27.7893 | 27.6877 | 27.59 | 27.4961 | 27.4536 | 27.4324 | 27.4114 | 27.3908 | 27.2902 | 27.2022 | 27.1132 | 26.4027 | 26.2533 | 26.1008 | 25.9521 | 25.8076 | 25.668 | 25.5326 | 25.4341 | 25.3534 | 25.2733 | 25.1937 | 25.0743 | 22.5671 | 21.6915 | 26.4839 | 26.3426 | 26.2044 | 26.0703 | 25.947 | 25.846 | 25.7491 | 25.7051 | 25.6832 | 25.6615 | 25.6402 | 25.5363 | 25.4453 | 22.0987
|  | DUNOON | CT |  |  |  | 28.1196 | 28.0043 | 27.8949 | 27.7893 | 27.6877 | 27.59 | 27.4961 | 27.4536 | 27.4324 | 27.4114 | 27.3908 | 27.2902 | 27.2022 | 27.1132 | 26.4027 | 26.2533 | 26.1008 | 25.9521 | 25.8076 | 25.668 | 25.5326 | 25.4341 | 25.3534 | 25.2733 | 25.1937 | 25.0743 | 22.6155 | 21.9567 | 26.4839 | 26.3426 | 26.2044 | 26.0703 | 25.947 | 25.846 | 25.7491 | 25.7051 | 25.6832 | 25.6615 | 25.6402 | 25.5363 | 25.4453 | 22.269
|  | DUNOON | LW |  |  |  | 28.3237 | 28.3064 | 28.2869 | 28.2655 | 28.2422 | 28.2174 | 28.1912 | 28.1675 | 28.1432 | 28.1183 | 28.0931 | 27.9597 | 27.8319 | 27.6999 | 26.5689 | 26.4902 | 26.3954 | 26.3004 | 26.2053 | 26.1102 | 26.0154 | 25.9166 | 25.8177 | 25.7189 | 25.6203 | 25.4483 | 22.5671 | 21.6915 | 26.6951 | 26.6518 | 26.6006 | 26.5479 | 26.52 | 26.4943 | 26.4672 | 26.4428 | 26.4176 | 26.3919 | 26.3659 | 26.228 | 26.096 | 22.0987
|  | DUNOON | ST |  |  |  | 28.3532 | 28.3464 | 28.3397 | 28.3331 | 28.3252 | 28.3175 | 28.31 | 28.3028 | 28.2923 | 28.2822 | 28.2723 | 28.2271 | 28.1874 | 28.1512 | 26.6197 | 26.5977 | 26.567 | 26.5311 | 26.4824 | 26.4351 | 26.3889 | 26.3398 | 26.2887 | 26.2386 | 26.1894 | 25.9513 | 25.7198 | 25.575 | 26.7363 | 26.7227 | 26.7059 | 26.6871 | 26.6622 | 26.6381 | 26.6146 | 26.5901 | 26.5717 | 26.5612 | 26.551 | 26.5044 | 26.4633 | 26.4259
|  | DUNOON | FS |  |  |  | 28.3464 | 28.3395 | 28.3293 | 28.3192 | 28.3093 | 28.2995 | 28.2899 | 28.2804 | 28.271 | 28.2617 | 28.2526 | 28.198 | 28.1503 | 28.1062 | 26.6266 | 26.6196 | 26.6039 | 26.5871 | 26.565 | 26.5432 | 26.5175 | 26.4922 | 26.4674 | 26.4431 | 26.4191 | 26.2958 | 26.1832 | 26.0784 | 26.7341 | 26.7264 | 26.7129 | 26.6992 | 26.6834 | 26.6678 | 26.6508 | 26.634 | 26.6175 | 26.6014 | 26.5854 | 26.4978 | 26.425 | 26.3794
| DUNVEGAN | DUNVEGAN | MINIMUM HEADROOM | NG 27646 47150 | YES | YES | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.2169 | 3.2169 | 3.2169 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.2337 | 3.2337 | 3.2337 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.2166 | 3.2166 | 3.2166
|  | DUNVEGAN | CT |  |  |  | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.2169 | 3.2169 | 3.2169 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.2337 | 3.2337 | 3.2337 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.2166 | 3.2166 | 3.2166
|  | DUNVEGAN | LW |  |  |  | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.2169 | 3.2169 | 3.2169 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.2337 | 3.2337 | 3.2337 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.2166 | 3.2166 | 3.2166
|  | DUNVEGAN | ST |  |  |  | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.2585 | 3.2585 | 3.2585 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.2669 | 3.2669 | 3.2669 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.2583 | 3.2583 | 3.2583
|  | DUNVEGAN | FS |  |  |  | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3
| DYCE | DYCE NORTH | MINIMUM HEADROOM | NJ 89092 12705 | NO | YES | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.4654 | 30.4654 | 26.9332 | 26.8736 | 26.8736 | 26.8736 | 26.8736 | 26.8736 | 26.8736 | 26.8736 | 26.8736 | 26.8736 | 26.8736 | 26.8736 | 21.9818 | 21.1515 | 27.278 | 27.278 | 27.278 | 27.278 | 27.278 | 27.278 | 27.278 | 27.278 | 27.278 | 27.278 | 27.278 | 27.278 | 27.1669 | 21.6225
|  | DYCE NORTH | CT |  |  |  | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.4654 | 30.4654 | 26.9362 | 26.8736 | 26.8736 | 26.8736 | 26.8736 | 26.8736 | 26.8736 | 26.8736 | 26.8736 | 26.8736 | 26.8736 | 26.8736 | 26.8106 | 26.8106 | 27.278 | 27.278 | 27.278 | 27.278 | 27.278 | 27.278 | 27.278 | 27.278 | 27.278 | 27.278 | 27.278 | 27.278 | 27.1669 | 27.1669
|  | DYCE NORTH | LW |  |  |  | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.4654 | 30.4654 | 26.9332 | 26.8736 | 26.8736 | 26.8736 | 26.8736 | 26.8736 | 26.8736 | 26.8736 | 26.8736 | 26.8736 | 26.8736 | 26.8736 | 21.9818 | 21.1515 | 27.278 | 27.278 | 27.278 | 27.278 | 27.278 | 27.278 | 27.278 | 27.278 | 27.278 | 27.278 | 27.278 | 27.278 | 27.1669 | 21.6225
|  | DYCE NORTH | ST |  |  |  | 30.5897 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5273 | 30.5273 | 26.9659 | 26.9371 | 26.8924 | 26.8736 | 26.8736 | 26.8736 | 26.8736 | 26.8736 | 26.8736 | 26.8736 | 26.8736 | 26.8736 | 26.8421 | 26.8421 | 27.278 | 27.278 | 27.278 | 27.278 | 27.278 | 27.278 | 27.278 | 27.278 | 27.278 | 27.278 | 27.278 | 27.278 | 27.2224 | 27.2224
|  | DYCE NORTH | FS |  |  |  | 30.643 | 30.5937 | 30.5905 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 30.5892 | 27.1737 | 26.9813 | 26.969 | 26.9543 | 26.9398 | 26.9254 | 26.907 | 26.8889 | 26.8736 | 26.8736 | 26.8736 | 26.8736 | 26.8736 | 26.8736 | 27.278 | 27.278 | 27.278 | 27.278 | 27.278 | 27.278 | 27.278 | 27.278 | 27.278 | 27.278 | 27.278 | 27.278 | 27.278 | 27.278
| THURSO | EDAY | MINIMUM HEADROOM | HY 56341 33422 | YES | YES | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.1859 | 1.1859 | 1.1857 | 1.1855 | 1.1852 | 1.1849 | 1.1846 | 1.1843 | 1.1839 | 1.1835 | 1.1832 | 1.1813 | 1.1794 | 0.99391 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 0.99638
|  | EDAY | CT |  |  |  | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.1859 | 1.1859 | 1.1858 | 1.1857 | 1.1855 | 1.1854 | 1.1852 | 1.1849 | 1.1847 | 1.1845 | 1.1842 | 1.1829 | 1.1816 | 1.1802 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381
|  | EDAY | LW |  |  |  | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.1859 | 1.1859 | 1.1857 | 1.1855 | 1.1852 | 1.1849 | 1.1846 | 1.1843 | 1.1839 | 1.1835 | 1.1832 | 1.1813 | 1.1794 | 0.99391 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 0.99638
|  | EDAY | ST |  |  |  | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.1859 | 1.1859 | 1.1859 | 1.1859 | 1.1858 | 1.1858 | 1.1857 | 1.1856 | 1.1854 | 1.1853 | 1.1852 | 1.1844 | 1.1836 | 1.1828 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381
|  | EDAY | FS |  |  |  | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.152 | 1.1859 | 1.1859 | 1.1859 | 1.1859 | 1.1859 | 1.186 | 1.186 | 1.1859 | 1.1859 | 1.1859 | 1.1859 | 1.1857 | 1.1855 | 1.1853 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381 | 1.1381
| THURSO | EDAY TIDAL | MINIMUM HEADROOM | HY 54226 31320 | YES | YES | 1.7158 | 1.7158 | 1.7158 | 1.7158 | 1.7158 | 1.7158 | 1.7158 | 1.7158 | 1.7158 | 1.7158 | 1.7158 | 0.70054 | 0.70054 | 0.70054 | 1.7641 | 1.764 | 1.7639 | 1.7638 | 1.7637 | 1.7637 | 1.7636 | 1.7635 | 1.7634 | 1.7633 | 1.7633 | 1.2665 | 1.2663 | 1.2661 | 1.6463 | 1.6462 | 1.6462 | 1.6462 | 1.6462 | 1.6461 | 1.6461 | 1.6461 | 1.646 | 1.646 | 1.646 | 0.72737 | 0.72681 | 0.72626
|  | EDAY TIDAL | CT |  |  |  | 1.7158 | 1.7158 | 1.7158 | 1.7158 | 1.7158 | 1.7158 | 1.7158 | 1.7158 | 1.7158 | 1.7158 | 1.7158 | 0.70054 | 0.70054 | 0.70054 | 1.7641 | 1.764 | 1.764 | 1.7639 | 1.7638 | 1.7638 | 1.7637 | 1.7637 | 1.7636 | 1.7636 | 1.7635 | 1.2667 | 1.2666 | 1.2664 | 1.6463 | 1.6463 | 1.6462 | 1.6462 | 1.6462 | 1.6462 | 1.6461 | 1.6461 | 1.6461 | 1.6461 | 1.6461 | 0.72787 | 0.72748 | 0.7271
|  | EDAY TIDAL | LW |  |  |  | 1.7158 | 1.7158 | 1.7158 | 1.7158 | 1.7158 | 1.7158 | 1.7158 | 1.7158 | 1.7158 | 1.7158 | 1.7158 | 0.70054 | 0.70054 | 0.70054 | 1.7641 | 1.764 | 1.7639 | 1.7638 | 1.7637 | 1.7637 | 1.7636 | 1.7635 | 1.7634 | 1.7633 | 1.7633 | 1.2665 | 1.2663 | 1.2661 | 1.6463 | 1.6462 | 1.6462 | 1.6462 | 1.6462 | 1.6461 | 1.6461 | 1.6461 | 1.646 | 1.646 | 1.646 | 0.72737 | 0.72681 | 0.72626
|  | EDAY TIDAL | ST |  |  |  | 1.7158 | 1.7158 | 1.7158 | 1.7158 | 1.7158 | 1.7158 | 1.7158 | 1.7158 | 1.7158 | 1.7158 | 1.7158 | 1.3368 | 1.3368 | 1.3368 | 1.7641 | 1.7641 | 1.764 | 1.764 | 1.764 | 1.7639 | 1.7639 | 1.7638 | 1.7638 | 1.7638 | 1.7637 | 1.4673 | 1.4672 | 1.4671 | 1.6463 | 1.6463 | 1.6463 | 1.6462 | 1.6462 | 1.6462 | 1.6462 | 1.6462 | 1.6462 | 1.6462 | 1.6461 | 1.2537 | 1.2536 | 1.2535
|  | EDAY TIDAL | FS |  |  |  | 1.7158 | 1.7158 | 1.7158 | 1.7158 | 1.7158 | 1.7158 | 1.7158 | 1.7158 | 1.7158 | 1.7158 | 1.7158 | 1.7158 | 1.7158 | 1.7158 | 1.7641 | 1.7641 | 1.7641 | 1.7641 | 1.7641 | 1.764 | 1.764 | 1.764 | 1.764 | 1.764 | 1.764 | 1.7639 | 1.7638 | 1.7638 | 1.6463 | 1.6463 | 1.6463 | 1.6463 | 1.6463 | 1.6463 | 1.6463 | 1.6463 | 1.6463 | 1.6462 | 1.6462 | 1.6462 | 1.6462 | 1.6462
| FIDDES | EDZELL | MINIMUM HEADROOM | NO 63500 70513 | YES | YES | 3.6731 | 3.6731 | 3.6731 | 3.6731 | 3.6731 | 3.6731 | 3.6731 | 3.6731 | 3.6731 | 3.6731 | 3.6731 | 3.2814 | 3.0953 | 2.8614 | 3.9957 | 3.9946 | 3.9933 | 3.9925 | 3.9918 | 3.991 | 3.9903 | 3.9892 | 3.9879 | 3.9866 | 3.9853 | 3.4435 | 3.1654 | 2.8917 | 3.919 | 3.9036 | 3.8838 | 3.8727 | 3.8617 | 3.8509 | 3.8398 | 3.8244 | 3.8051 | 3.7862 | 3.768 | 3.1386 | 2.8819 | 2.6294
|  | EDZELL | CT |  |  |  | 3.6731 | 3.6731 | 3.6731 | 3.6731 | 3.6731 | 3.6731 | 3.6731 | 3.6731 | 3.6731 | 3.6731 | 3.6731 | 3.2814 | 3.2525 | 3.0972 | 3.9957 | 3.9946 | 3.9934 | 3.9927 | 3.9919 | 3.9911 | 3.9903 | 3.9894 | 3.9886 | 3.9878 | 3.9871 | 3.5335 | 3.3491 | 3.1675 | 3.919 | 3.9036 | 3.8854 | 3.875 | 3.8643 | 3.8525 | 3.8398 | 3.8265 | 3.815 | 3.8037 | 3.7931 | 3.2216 | 3.0515 | 2.8839
|  | EDZELL | LW |  |  |  | 3.6731 | 3.6731 | 3.6731 | 3.6731 | 3.6731 | 3.6731 | 3.6731 | 3.6731 | 3.6731 | 3.6731 | 3.6731 | 3.2814 | 3.0953 | 2.8614 | 3.9957 | 3.9946 | 3.9933 | 3.9925 | 3.9918 | 3.991 | 3.9903 | 3.9895 | 3.9887 | 3.988 | 3.9872 | 3.4435 | 3.1654 | 2.8917 | 3.9195 | 3.9037 | 3.8838 | 3.8727 | 3.8617 | 3.8509 | 3.8403 | 3.8289 | 3.8177 | 3.8065 | 3.7957 | 3.1386 | 2.8819 | 2.6294
|  | EDZELL | ST |  |  |  | 3.6731 | 3.6731 | 3.6731 | 3.6731 | 3.6731 | 3.6731 | 3.6731 | 3.6731 | 3.6731 | 3.6731 | 3.6731 | 3.4792 | 3.4792 | 3.4599 | 3.996 | 3.9955 | 3.9949 | 3.9945 | 3.9933 | 3.992 | 3.9906 | 3.9892 | 3.9879 | 3.9866 | 3.9853 | 3.7262 | 3.6082 | 3.4911 | 3.9236 | 3.9167 | 3.9073 | 3.9022 | 3.8837 | 3.8646 | 3.8451 | 3.8244 | 3.8051 | 3.7862 | 3.768 | 3.4618 | 3.3529 | 3.2448
|  | EDZELL | FS |  |  |  | 3.6731 | 3.6731 | 3.6731 | 3.6731 | 3.6731 | 3.6731 | 3.6731 | 3.6731 | 3.6731 | 3.6731 | 3.6731 | 3.6731 | 3.6731 | 3.6731 | 3.9962 | 3.996 | 3.9957 | 3.9956 | 3.9951 | 3.9947 | 3.9941 | 3.9936 | 3.993 | 3.9925 | 3.992 | 3.9896 | 3.9873 | 3.9852 | 3.9259 | 3.9233 | 3.9194 | 3.9176 | 3.911 | 3.9044 | 3.8962 | 3.8883 | 3.8804 | 3.8726 | 3.8651 | 3.8299 | 3.797 | 3.766
| MILTON OF CRAIGIE | EDZELL STREET | MINIMUM HEADROOM | NO 47103 32070 | YES | YES | 11.4711 | 11.452 | 11.452 | 11.452 | 11.452 | 11.452 | 11.452 | 11.452 | 11.452 | 11.452 | 11.452 | 9.7335 | 9.3307 | 8.9431 | 11.5049 | 11.4625 | 11.4139 | 11.3662 | 11.3547 | 11.3463 | 11.3381 | 11.3292 | 11.3198 | 11.3104 | 11.301 | 9.5505 | 9.0807 | 8.6287 | 11.8799 | 11.8666 | 11.8513 | 11.8362 | 11.8214 | 11.8069 | 11.7927 | 11.7772 | 11.7609 | 11.7446 | 11.7283 | 9.7239 | 9.2834 | 8.8594
|  | EDZELL STREET | CT |  |  |  | 11.4711 | 11.452 | 11.452 | 11.452 | 11.452 | 11.452 | 11.452 | 11.452 | 11.452 | 11.452 | 11.452 | 9.8332 | 9.5328 | 9.2447 | 11.5049 | 11.4625 | 11.4139 | 11.3662 | 11.3547 | 11.3463 | 11.3381 | 11.3292 | 11.3198 | 11.3104 | 11.301 | 9.6668 | 9.3164 | 8.9804 | 11.8799 | 11.8666 | 11.8513 | 11.8362 | 11.8214 | 11.8069 | 11.7927 | 11.7772 | 11.7609 | 11.7446 | 11.7283 | 9.8329 | 9.5044 | 9.1893
|  | EDZELL STREET | LW |  |  |  | 11.4807 | 11.452 | 11.452 | 11.452 | 11.452 | 11.452 | 11.452 | 11.452 | 11.452 | 11.452 | 11.452 | 9.7335 | 9.3307 | 8.9431 | 11.5105 | 11.4711 | 11.4227 | 11.3756 | 11.3564 | 11.3477 | 11.3393 | 11.33 | 11.3205 | 11.311 | 11.3015 | 9.5505 | 9.0807 | 8.6287 | 11.8817 | 11.8693 | 11.854 | 11.8392 | 11.8243 | 11.8093 | 11.7947 | 11.7785 | 11.7621 | 11.7456 | 11.7292 | 9.7239 | 9.2834 | 8.8594
|  | EDZELL STREET | ST |  |  |  | 11.5031 | 11.4832 | 11.4524 | 11.452 | 11.452 | 11.452 | 11.452 | 11.452 | 11.452 | 11.452 | 11.452 | 11.452 | 11.452 | 11.452 | 11.5235 | 11.512 | 11.4941 | 11.4728 | 11.4523 | 11.4325 | 11.4131 | 11.3919 | 11.3692 | 11.3596 | 11.3555 | 11.3354 | 11.3168 | 11.2989 | 11.8858 | 11.8822 | 11.8765 | 11.8698 | 11.8634 | 11.8571 | 11.851 | 11.8443 | 11.8372 | 11.83 | 11.8228 | 11.7879 | 11.7557 | 11.7246
|  | EDZELL STREET | FS |  |  |  | 11.5143 | 11.5126 | 11.5033 | 11.4925 | 11.4812 | 11.4699 | 11.4554 | 11.452 | 11.452 | 11.452 | 11.452 | 11.452 | 11.452 | 11.452 | 11.5299 | 11.529 | 11.5236 | 11.5174 | 11.5108 | 11.5043 | 11.4959 | 11.4874 | 11.4787 | 11.4701 | 11.4616 | 11.4196 | 11.3823 | 11.36 | 11.8878 | 11.8875 | 11.8858 | 11.8839 | 11.8818 | 11.8797 | 11.8771 | 11.8744 | 11.8717 | 11.869 | 11.8663 | 11.8531 | 11.8413 | 11.8306
| ELGIN | ELGIN | MINIMUM HEADROOM | NJ 21256 64664 | NO | YES | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 12.487 | 12.4417 | 12.3986 | 12.3763 | 12.3534 | 12.3444 | 12.3361 | 12.3272 | 12.3179 | 12.3079 | 9.8033 | 9.1017 | 8.6098 | 8.1224 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 9.8204 | 9.1292 | 8.6446 | 8.1714
|  | ELGIN | CT |  |  |  | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 12.4929 | 12.4574 | 12.4204 | 12.3943 | 12.3762 | 12.356 | 12.3458 | 12.3379 | 12.3295 | 12.3204 | 12.3112 | 9.4662 | 9.0952 | 8.749 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 9.4883 | 9.1227 | 8.7816
|  | ELGIN | LW |  |  |  | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 12.487 | 12.4417 | 12.3986 | 12.3763 | 12.3534 | 12.3444 | 12.3361 | 12.3272 | 12.3179 | 12.3079 | 9.8033 | 9.1017 | 8.6098 | 8.1224 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 9.8204 | 9.1292 | 8.6446 | 8.1714
|  | ELGIN | ST |  |  |  | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 12.5055 | 12.4848 | 12.4614 | 12.4349 | 12.4017 | 12.3849 | 12.3664 | 12.3498 | 12.3428 | 12.3352 | 12.3276 | 9.9668 | 9.723 | 9.4945 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 9.9815 | 9.7413 | 9.5162
|  | ELGIN | FS |  |  |  | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 14.1986 | 12.5164 | 12.5071 | 12.4963 | 12.4849 | 12.4706 | 12.4557 | 12.4386 | 12.4203 | 12.4026 | 12.3938 | 12.3845 | 12.355 | 12.3477 | 12.3438 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263 | 12.7263
| ARBROATH | ELLIOT DEPOT | MINIMUM HEADROOM | NO 62251 40381 | YES | YES | 5.1951 | 5.0405 | 4.8746 | 4.7122 | 4.5567 | 4.4125 | 4.2717 | 4.1614 | 4.0819 | 4.0041 | 3.9286 | 3.6805 | 3.472 | 0.80919 | 3.7089 | 3.5827 | 3.4439 | 3.3066 | 3.2343 | 3.1674 | 3.1027 | 3.0576 | 3.0303 | 3.0035 | 2.9774 | 0.80224 | 0.46113 | 0.029261 | 4.9738 | 4.8761 | 4.7752 | 4.6779 | 4.5841 | 4.494 | 4.4075 | 4.3524 | 4.325 | 4.2978 | 4.2711 | 4.133 | 0.79935 | 0.41167
|  | ELLIOT DEPOT | CT |  |  |  | 5.1951 | 5.0405 | 4.8746 | 4.7122 | 4.5567 | 4.4125 | 4.2717 | 4.1614 | 4.0819 | 4.0041 | 3.9286 | 3.6805 | 3.472 | 0.80919 | 3.7089 | 3.5827 | 3.4439 | 3.3066 | 3.2343 | 3.1674 | 3.1027 | 3.0576 | 3.0303 | 3.0035 | 2.9774 | 0.80224 | 0.46113 | 0.10972 | 4.9738 | 4.8761 | 4.7752 | 4.6779 | 4.5841 | 4.494 | 4.4075 | 4.3524 | 4.325 | 4.2978 | 4.2711 | 4.133 | 0.79935 | 0.41167
|  | ELLIOT DEPOT | LW |  |  |  | 5.3849 | 5.3117 | 5.2228 | 5.1317 | 5.0423 | 4.9604 | 4.8784 | 4.7849 | 4.6909 | 4.5967 | 4.5025 | 4.2726 | 4.0395 | 0.90937 | 3.8152 | 3.7265 | 3.6177 | 3.5676 | 3.5418 | 3.5169 | 3.4914 | 3.461 | 3.4302 | 3.399 | 3.3677 | 0.98443 | 0.52705 | 0.029261 | 5.1466 | 5.132 | 5.1155 | 5.0973 | 5.0776 | 5.0566 | 5.0344 | 5.006 | 4.9767 | 4.9468 | 4.9166 | 4.7563 | 0.96826 | 0.41818
|  | ELLIOT DEPOT | ST |  |  |  | 5.4324 | 5.4084 | 5.3761 | 5.339 | 5.3139 | 5.2936 | 5.2728 | 5.2502 | 5.2242 | 5.1995 | 5.1764 | 5.0571 | 4.9401 | 4.811 | 3.8584 | 3.8304 | 3.7905 | 3.7438 | 3.715 | 3.6927 | 3.6695 | 3.644 | 3.6166 | 3.5908 | 3.5775 | 3.5322 | 3.4876 | 3.436 | 5.1717 | 5.1658 | 5.1601 | 5.1546 | 5.1479 | 5.1414 | 5.135 | 5.1284 | 5.1187 | 5.1093 | 5.1002 | 5.0487 | 4.9979 | 4.9365
|  | ELLIOT DEPOT | FS |  |  |  | 5.5194 | 5.5094 | 5.4903 | 5.47 | 5.4544 | 5.4407 | 5.426 | 5.4115 | 5.3973 | 5.3833 | 5.3697 | 5.2954 | 5.2191 | 5.1449 | 3.9851 | 3.9765 | 3.9578 | 3.9373 | 3.9232 | 3.9117 | 3.8987 | 3.8858 | 3.8733 | 3.8611 | 3.8491 | 3.7879 | 3.7274 | 3.6688 | 5.1658 | 5.16 | 5.1514 | 5.1428 | 5.1344 | 5.1261 | 5.118 | 5.1099 | 5.102 | 5.0941 | 5.0864 | 5.0401 | 4.99 | 4.9411
| DYCE | ELLON | MINIMUM HEADROOM | NJ 95510 30054 | NO | YES | 22.1258 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 32.6069 | 22.923 | 21.521 | 17.5552 | 27.9368 | 27.8275 | 27.8023 | 27.7774 | 27.7525 | 27.728 | 27.7015 | 21.9981 | 21.4974 | 21.0009 | 18.7808 | 17.1122 | 15.477 | 19.3494 | 29.8669 | 29.7896 | 29.7126 | 29.636 | 29.5597 | 29.4846 | 29.4427 | 29.4427 | 29.4427 | 29.4427 | 20.2596 | 18.5886 | 16.9566
|  | ELLON | CT |  |  |  | 22.1258 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 32.6069 | 32.6069 | 32.6069 | 17.5651 | 27.9927 | 27.8403 | 27.8222 | 27.8041 | 27.7861 | 27.7683 | 27.7492 | 27.7304 | 27.7114 | 27.6926 | 20.6022 | 19.4605 | 18.3447 | 19.3525 | 29.8845 | 29.8289 | 29.7734 | 29.718 | 29.6627 | 29.6083 | 29.5496 | 29.492 | 29.4427 | 29.4427 | 28.7464 | 20.9511 | 19.8185
|  | ELLON | LW |  |  |  | 22.1258 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 32.6069 | 22.923 | 21.521 | 17.5552 | 27.9368 | 27.8275 | 27.8023 | 27.7774 | 27.7525 | 27.728 | 27.7015 | 21.9981 | 21.4974 | 21.0009 | 18.7808 | 17.1122 | 15.477 | 19.3494 | 29.8669 | 29.7896 | 29.7126 | 29.636 | 29.5597 | 29.4846 | 29.4427 | 29.4427 | 29.4427 | 29.4427 | 20.2596 | 18.5886 | 16.9566
|  | ELLON | ST |  |  |  | 22.1258 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 32.9438 | 32.9438 | 32.9438 | 17.6175 | 28.135 | 28.0373 | 27.9193 | 27.843 | 27.835 | 27.8272 | 27.8187 | 27.8106 | 27.8023 | 27.7942 | 27.5506 | 27.5118 | 21.7499 | 19.3691 | 29.9293 | 29.8985 | 29.8613 | 29.8371 | 29.8127 | 29.7887 | 29.7628 | 29.7379 | 29.7126 | 29.6877 | 29.2218 | 29.103 | 29.0945
|  | ELLON | FS |  |  |  | 22.1258 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 33.2808 | 17.6528 | 28.2274 | 28.2006 | 28.1685 | 28.1432 | 28.1176 | 28.0858 | 28.0543 | 28.0238 | 27.993 | 27.9628 | 27.8403 | 27.826 | 27.8125 | 19.3802 | 29.9585 | 29.95 | 29.9399 | 29.9319 | 29.9239 | 29.9138 | 29.9039 | 29.8943 | 29.8846 | 29.8751 | 29.829 | 29.7853 | 29.7438
| TAYNUILT | EREDINE | MINIMUM HEADROOM | NM 97142 09376 | YES | YES | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.24833 | 0.24811 | 0.24784 | 0.24757 | 0.24731 | 0.24717 | 0.24704 | 0.24689 | 0.24675 | 0.24662 | 0.24648 | 0.24495 | 0.24495 | 0.24495 | 0.256 | 0.25591 | 0.25586 | 0.25581 | 0.25576 | 0.25572 | 0.25567 | 0.25562 | 0.25557 | 0.25552 | 0.25548 | 0.25491 | 0.25467 | 0.25467
|  | EREDINE | CT |  |  |  | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.24834 | 0.24818 | 0.24799 | 0.2478 | 0.24762 | 0.24744 | 0.24728 | 0.24718 | 0.24708 | 0.24698 | 0.24689 | 0.24642 | 0.24594 | 0.24547 | 0.25601 | 0.25593 | 0.25588 | 0.25585 | 0.25582 | 0.25579 | 0.25575 | 0.25572 | 0.25569 | 0.25565 | 0.25562 | 0.25545 | 0.25529 | 0.25513
|  | EREDINE | LW |  |  |  | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.24833 | 0.24811 | 0.24784 | 0.24757 | 0.24731 | 0.24717 | 0.24704 | 0.24689 | 0.24675 | 0.24662 | 0.24648 | 0.24495 | 0.24495 | 0.24495 | 0.256 | 0.25591 | 0.25586 | 0.25581 | 0.25576 | 0.25572 | 0.25567 | 0.25562 | 0.25557 | 0.25552 | 0.25548 | 0.25491 | 0.25467 | 0.25467
|  | EREDINE | ST |  |  |  | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.2484 | 0.24833 | 0.24823 | 0.24811 | 0.24781 | 0.24753 | 0.24726 | 0.2471 | 0.24695 | 0.24679 | 0.24664 | 0.24591 | 0.24518 | 0.24495 | 0.25604 | 0.25601 | 0.25596 | 0.25591 | 0.25585 | 0.2558 | 0.25575 | 0.25569 | 0.25564 | 0.25559 | 0.25553 | 0.25528 | 0.25502 | 0.25477
|  | EREDINE | FS |  |  |  | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.28633 | 0.24844 | 0.24843 | 0.24841 | 0.24837 | 0.24828 | 0.24818 | 0.24806 | 0.24794 | 0.24783 | 0.24771 | 0.2476 | 0.24717 | 0.24691 | 0.24666 | 0.25606 | 0.25606 | 0.25604 | 0.25602 | 0.25598 | 0.25593 | 0.2559 | 0.25588 | 0.25586 | 0.25583 | 0.25581 | 0.25572 | 0.25563 | 0.25554
| INVERNESS | ERROGIE | MINIMUM HEADROOM | NH 56674 22810 | YES | YES | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.60512 | 0.59256 | 0.58008 | 1.0538 | 1.0532 | 1.0526 | 1.0519 | 1.0512 | 1.0506 | 1.0501 | 1.0496 | 1.0491 | 1.0487 | 1.0486 | 0.65499 | 0.64089 | 0.62688 | 1.0608 | 1.0605 | 1.0602 | 1.0599 | 1.0599 | 1.0599 | 1.0599 | 1.0599 | 1.0599 | 1.0599 | 1.0599 | 0.56798 | 0.55501 | 0.54127
|  | ERROGIE | CT |  |  |  | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.60524 | 0.59256 | 0.58008 | 1.0538 | 1.0534 | 1.0529 | 1.0525 | 1.052 | 1.0516 | 1.0511 | 1.0506 | 1.0503 | 1.0499 | 1.0496 | 0.65513 | 0.64089 | 0.62688 | 1.0608 | 1.0606 | 1.0604 | 1.0602 | 1.0599 | 1.0599 | 1.0599 | 1.0599 | 1.0599 | 1.0599 | 1.0599 | 0.5681 | 0.55501 | 0.54127
|  | ERROGIE | LW |  |  |  | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.60512 | 0.59565 | 0.58638 | 1.0538 | 1.0532 | 1.0526 | 1.0519 | 1.0512 | 1.0506 | 1.0501 | 1.0496 | 1.0491 | 1.0487 | 1.0486 | 0.65499 | 0.64436 | 0.63395 | 1.0608 | 1.0605 | 1.0602 | 1.0599 | 1.0599 | 1.0599 | 1.0599 | 1.0599 | 1.0599 | 1.0599 | 1.0599 | 0.56798 | 0.5582 | 0.54831
|  | ERROGIE | ST |  |  |  | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.84335 | 0.83966 | 0.83561 | 1.054 | 1.0538 | 1.0536 | 1.0532 | 1.0527 | 1.0522 | 1.0518 | 1.0512 | 1.0507 | 1.0503 | 1.0499 | 0.84956 | 0.84496 | 0.84041 | 1.0609 | 1.0608 | 1.0607 | 1.0605 | 1.0603 | 1.06 | 1.0599 | 1.0599 | 1.0599 | 1.0599 | 1.0599 | 0.80856 | 0.80432 | 0.80014
|  | ERROGIE | FS |  |  |  | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 1.0541 | 1.0541 | 1.054 | 1.0539 | 1.0537 | 1.0536 | 1.0534 | 1.0532 | 1.0529 | 1.0527 | 1.0525 | 1.0516 | 1.0507 | 1.05 | 1.0609 | 1.0609 | 1.0609 | 1.0609 | 1.0608 | 1.0607 | 1.0606 | 1.0605 | 1.0604 | 1.0603 | 1.0602 | 1.0599 | 1.0599 | 1.0599
| ABERNETHY | ERROL | MINIMUM HEADROOM | NO 23206 23038 | NO | YES | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 4.9852 | 4.824 | 4.6626 | 3.7706 | 3.2952 | 2.834 | 6.3766 | 6.3363 | 6.2867 | 6.2361 | 6.1944 | 4.8171 | 4.6362 | 4.4405 | 4.2463 | 4.052 | 3.8575 | 2.9679 | 2.395 | 1.8392 | 6.4056 | 6.361 | 6.3362 | 6.3108 | 6.2855 | 6.2615 | 4.8515 | 4.6609 | 4.4691 | 4.2747 | 4.0802 | 3.0948 | 2.5217 | 1.9658
|  | ERROL | CT |  |  |  | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 4.6211 | 4.3053 | 4.0003 | 6.3829 | 6.3588 | 6.3311 | 6.3023 | 6.2733 | 6.2466 | 6.2202 | 6.1964 | 4.9125 | 4.8016 | 4.6911 | 3.9929 | 3.6123 | 3.2448 | 6.414 | 6.3812 | 6.3584 | 6.344 | 6.3294 | 6.316 | 6.3028 | 6.2884 | 6.274 | 6.2604 | 4.905 | 4.1172 | 3.7394 | 3.3718
|  | ERROL | LW |  |  |  | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 4.9852 | 4.824 | 4.6626 | 3.7706 | 3.2952 | 2.834 | 6.3766 | 6.3363 | 6.2867 | 6.2361 | 6.1944 | 4.8171 | 4.6362 | 4.4405 | 4.2463 | 4.052 | 3.8575 | 2.9679 | 2.395 | 1.8392 | 6.4056 | 6.361 | 6.3362 | 6.3108 | 6.2855 | 6.2615 | 4.8515 | 4.6609 | 4.4691 | 4.2747 | 4.0802 | 3.0948 | 2.5217 | 1.9658
|  | ERROL | ST |  |  |  | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.723 | 6.723 | 4.9278 | 6.3893 | 6.3767 | 6.357 | 6.3324 | 6.3177 | 6.3044 | 6.2913 | 6.2771 | 6.2629 | 6.2487 | 6.2347 | 4.7696 | 4.5162 | 4.2699 | 6.4228 | 6.4056 | 6.3787 | 6.3591 | 6.3517 | 6.345 | 6.3385 | 6.3313 | 6.3242 | 6.3171 | 6.31 | 4.9277 | 4.6808 | 4.4408
|  | ERROL | FS |  |  |  | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.3965 | 6.3955 | 6.39 | 6.383 | 6.378 | 6.3736 | 6.3679 | 6.3622 | 6.3567 | 6.3512 | 6.3457 | 6.3193 | 6.295 | 6.2725 | 6.4326 | 6.4312 | 6.4237 | 6.4143 | 6.4075 | 6.4014 | 6.3936 | 6.3859 | 6.3784 | 6.3709 | 6.3658 | 6.3525 | 6.3403 | 6.329
| FASNAKYLE | FASNAKYLE | MINIMUM HEADROOM | NH 31948 29998 | YES | NO | 1.2878 | 1.2876 | 1.2874 | 1.2872 | 1.287 | 1.2866 | 1.2861 | 1.2855 | 1.285 | 1.2845 | 1.284 | 0.44894 | 0.29889 | 0.24163 | 1.2453 | 1.2453 | 1.2453 | 1.2453 | 1.2453 | 1.2453 | 1.2453 | 1.2453 | 1.2453 | 1.2453 | 1.2453 | 0.57565 | 0.43557 | 0.36734 | 1.2849 | 1.2849 | 1.2849 | 1.2849 | 1.2849 | 1.2849 | 1.2849 | 1.2849 | 1.2849 | 1.2849 | 1.2849 | 0.44397 | 0.29138 | 0.22662
|  | FASNAKYLE | CT |  |  |  | 1.2878 | 1.2877 | 1.2875 | 1.2874 | 1.2872 | 1.2871 | 1.287 | 1.2868 | 1.2867 | 1.2865 | 1.2864 | 0.47433 | 0.34292 | 0.30388 | 1.2453 | 1.2453 | 1.2453 | 1.2453 | 1.2453 | 1.2453 | 1.2453 | 1.2453 | 1.2453 | 1.2453 | 1.2453 | 0.6059 | 0.48803 | 0.44151 | 1.2849 | 1.2849 | 1.2849 | 1.2849 | 1.2849 | 1.2849 | 1.2849 | 1.2849 | 1.2849 | 1.2849 | 1.2849 | 0.47018 | 0.33683 | 0.29652
|  | FASNAKYLE | LW |  |  |  | 1.2878 | 1.2876 | 1.2874 | 1.2872 | 1.287 | 1.2868 | 1.2866 | 1.2863 | 1.2861 | 1.2859 | 1.2857 | 0.44894 | 0.29889 | 0.24163 | 1.2453 | 1.2453 | 1.2453 | 1.2453 | 1.2453 | 1.2453 | 1.2453 | 1.2453 | 1.2453 | 1.2453 | 1.2453 | 0.57565 | 0.43557 | 0.36734 | 1.2849 | 1.2849 | 1.2849 | 1.2849 | 1.2849 | 1.2849 | 1.2849 | 1.2849 | 1.2849 | 1.2849 | 1.2849 | 0.44397 | 0.29138 | 0.22662
|  | FASNAKYLE | ST |  |  |  | 1.2878 | 1.2878 | 1.2877 | 1.2876 | 1.2871 | 1.2866 | 1.2861 | 1.2855 | 1.285 | 1.2845 | 1.284 | 0.78354 | 0.7118 | 0.68604 | 1.2453 | 1.2453 | 1.2453 | 1.2453 | 1.2453 | 1.2453 | 1.2453 | 1.2453 | 1.2453 | 1.2453 | 1.2453 | 0.83888 | 0.77275 | 0.74207 | 1.2849 | 1.2849 | 1.2849 | 1.2849 | 1.2849 | 1.2849 | 1.2849 | 1.2849 | 1.2849 | 1.2849 | 1.2849 | 0.77851 | 0.70348 | 0.67285
|  | FASNAKYLE | FS |  |  |  | 1.2879 | 1.2879 | 1.2879 | 1.2878 | 1.2877 | 1.2875 | 1.2873 | 1.2871 | 1.2869 | 1.2867 | 1.2865 | 1.2855 | 1.2846 | 1.2838 | 1.2453 | 1.2453 | 1.2453 | 1.2453 | 1.2453 | 1.2453 | 1.2453 | 1.2453 | 1.2453 | 1.2453 | 1.2453 | 1.2453 | 1.2453 | 1.2453 | 1.2849 | 1.2849 | 1.2849 | 1.2849 | 1.2849 | 1.2849 | 1.2849 | 1.2849 | 1.2849 | 1.2849 | 1.2849 | 1.2849 | 1.2849 | 1.2849
| TUMMEL BRIDGE | FINCASTLE | MINIMUM HEADROOM | NN 87976 61147 | YES | YES | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.099991 | 0.12494 | 0.12403 | 0.12381 | 0.12363 | 0.12346 | 0.12335 | 0.12335 | 0.12335 | 0.12335 | 0.12335 | 0.12335 | 0.091044 | 0.081291 | 0.071636 | 0.12848 | 0.12848 | 0.12848 | 0.12848 | 0.12848 | 0.12848 | 0.12848 | 0.12848 | 0.12848 | 0.12848 | 0.12848 | 0.094367 | 0.084611 | 0.074952
|  | FINCASTLE | CT |  |  |  | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.125 | 0.12424 | 0.12392 | 0.12379 | 0.12367 | 0.12354 | 0.12343 | 0.12335 | 0.12335 | 0.12335 | 0.12335 | 0.099845 | 0.093018 | 0.086259 | 0.12848 | 0.12848 | 0.12848 | 0.12848 | 0.12848 | 0.12848 | 0.12848 | 0.12848 | 0.12848 | 0.12848 | 0.12848 | 0.12848 | 0.096341 | 0.089581
|  | FINCASTLE | LW |  |  |  | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.099991 | 0.12494 | 0.12403 | 0.12381 | 0.12363 | 0.12346 | 0.12335 | 0.12335 | 0.12335 | 0.12335 | 0.12335 | 0.12335 | 0.091044 | 0.081291 | 0.071636 | 0.12848 | 0.12848 | 0.12848 | 0.12848 | 0.12848 | 0.12848 | 0.12848 | 0.12848 | 0.12848 | 0.12848 | 0.12848 | 0.094367 | 0.084611 | 0.074952
|  | FINCASTLE | ST |  |  |  | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.12527 | 0.12496 | 0.12448 | 0.12403 | 0.12391 | 0.12383 | 0.12376 | 0.12367 | 0.12359 | 0.12351 | 0.12343 | 0.12335 | 0.12335 | 0.099531 | 0.12848 | 0.12848 | 0.12848 | 0.12848 | 0.12848 | 0.12848 | 0.12848 | 0.12848 | 0.12848 | 0.12848 | 0.12848 | 0.12848 | 0.12848 | 0.12848
|  | FINCASTLE | FS |  |  |  | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.14962 | 0.12545 | 0.12542 | 0.12529 | 0.12513 | 0.12494 | 0.12476 | 0.12452 | 0.12429 | 0.1241 | 0.12401 | 0.12395 | 0.1238 | 0.12366 | 0.12353 | 0.12848 | 0.12848 | 0.12848 | 0.12848 | 0.12848 | 0.12848 | 0.12848 | 0.12848 | 0.12848 | 0.12848 | 0.12848 | 0.12848 | 0.12848 | 0.12848
| SHETLAND | FIRTH | MINIMUM HEADROOM | HU4396874166 | YES | YES | 2.1312 | 2.131 | 2.1307 | 2.1305 | 2.1303 | 2.1295 | 2.1287 | 2.1279 | 2.127 | 2.1261 | 2.1258 | 2.1222 | 2.1187 | 2.1152 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.6933 | 1.6931 | 1.6928 | 1.6925 | 1.6922 | 1.6913 | 1.6903 | 1.6892 | 1.6882 | 1.687 | 1.6867 | 1.6822 | 1.6778 | 1.6734
|  | FIRTH | CT |  |  |  | 2.1312 | 2.1311 | 2.1309 | 2.1307 | 2.1305 | 2.13 | 2.1293 | 2.1286 | 2.128 | 2.1272 | 2.1269 | 2.1238 | 2.1213 | 2.1188 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.6934 | 1.6932 | 1.693 | 1.6927 | 1.6925 | 1.6918 | 1.691 | 1.6902 | 1.6893 | 1.6883 | 1.688 | 1.6842 | 1.681 | 1.678
|  | FIRTH | LW |  |  |  | 2.1312 | 2.131 | 2.1307 | 2.1305 | 2.1303 | 2.1295 | 2.1287 | 2.1279 | 2.127 | 2.1261 | 2.1258 | 2.1222 | 2.1187 | 2.1152 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.6933 | 1.6931 | 1.6928 | 1.6925 | 1.6922 | 1.6913 | 1.6903 | 1.6892 | 1.6882 | 1.687 | 1.6867 | 1.6822 | 1.6778 | 1.6734
|  | FIRTH | ST |  |  |  | 2.1312 | 2.1312 | 2.1311 | 2.131 | 2.1306 | 2.13 | 2.1294 | 2.1287 | 2.128 | 2.1272 | 2.1267 | 2.1248 | 2.1232 | 2.1217 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.6934 | 1.6933 | 1.6932 | 1.6931 | 1.6926 | 1.6919 | 1.6911 | 1.6902 | 1.6893 | 1.6884 | 1.6878 | 1.6854 | 1.6834 | 1.6815
|  | FIRTH | FS |  |  |  | 2.1313 | 2.1313 | 2.1312 | 2.1312 | 2.1311 | 2.1309 | 2.1306 | 2.1303 | 2.13 | 2.1297 | 2.1296 | 2.1288 | 2.1282 | 2.1277 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.8786 | 1.6935 | 1.6934 | 1.6934 | 1.6934 | 1.6932 | 1.6929 | 1.6926 | 1.6923 | 1.6919 | 1.6915 | 1.6913 | 1.6904 | 1.6896 | 1.689
| FORT WILLIAM | FISHNISH | MINIMUM HEADROOM | NM 66623 42191 | YES | YES | 0.20229 | 0.20229 | 0.20229 | 0.20229 | 0.19948 | 0.19894 | 0.19841 | 0.19783 | 0.19726 | 0.19669 | 0.19613 | 0.19338 | 0.19061 | 0.18787 | 0.20228 | 0.20221 | 0.20221 | 0.1999 | 0.19924 | 0.1986 | 0.19797 | 0.1973 | 0.19662 | 0.19595 | 0.19529 | 0.19206 | 0.18881 | 0.18559 | 0.20273 | 0.20269 | 0.20269 | 0.20269 | 0.19942 | 0.19877 | 0.19815 | 0.19747 | 0.19679 | 0.19612 | 0.19546 | 0.19223 | 0.18897 | 0.18576
|  | FISHNISH | CT |  |  |  | 0.20229 | 0.20229 | 0.20229 | 0.20229 | 0.20229 | 0.19976 | 0.19939 | 0.19899 | 0.19859 | 0.19819 | 0.19779 | 0.19588 | 0.19394 | 0.19202 | 0.20229 | 0.20221 | 0.20221 | 0.20221 | 0.20221 | 0.19957 | 0.19913 | 0.19866 | 0.19819 | 0.19772 | 0.19725 | 0.19499 | 0.19271 | 0.19046 | 0.20273 | 0.20269 | 0.20269 | 0.20269 | 0.20269 | 0.19974 | 0.19931 | 0.19883 | 0.19836 | 0.19789 | 0.19742 | 0.19516 | 0.19288 | 0.19063
|  | FISHNISH | LW |  |  |  | 0.20229 | 0.20229 | 0.20229 | 0.20229 | 0.19948 | 0.19894 | 0.19841 | 0.19783 | 0.19726 | 0.19669 | 0.19613 | 0.19338 | 0.19061 | 0.18787 | 0.20228 | 0.20221 | 0.20221 | 0.1999 | 0.19924 | 0.1986 | 0.19797 | 0.1973 | 0.19662 | 0.19595 | 0.19529 | 0.19206 | 0.18881 | 0.18559 | 0.20273 | 0.20269 | 0.20269 | 0.20269 | 0.19942 | 0.19877 | 0.19815 | 0.19747 | 0.19679 | 0.19612 | 0.19546 | 0.19223 | 0.18897 | 0.18576
|  | FISHNISH | ST |  |  |  | 0.20229 | 0.20229 | 0.20229 | 0.20229 | 0.20229 | 0.20229 | 0.20229 | 0.20229 | 0.1999 | 0.19964 | 0.19939 | 0.19817 | 0.19698 | 0.19579 | 0.20233 | 0.20229 | 0.20222 | 0.20221 | 0.20221 | 0.20221 | 0.20221 | 0.20221 | 0.19974 | 0.19943 | 0.19914 | 0.1977 | 0.19629 | 0.19489 | 0.20275 | 0.20273 | 0.20271 | 0.20269 | 0.20269 | 0.20269 | 0.20269 | 0.20269 | 0.19991 | 0.19961 | 0.19931 | 0.19787 | 0.19646 | 0.19506
|  | FISHNISH | FS |  |  |  | 0.20229 | 0.20229 | 0.20229 | 0.20229 | 0.20229 | 0.20229 | 0.20229 | 0.20229 | 0.20229 | 0.20229 | 0.20229 | 0.20229 | 0.20229 | 0.1997 | 0.20238 | 0.20237 | 0.20234 | 0.20231 | 0.20228 | 0.20226 | 0.20222 | 0.20221 | 0.20221 | 0.20221 | 0.20221 | 0.20221 | 0.19999 | 0.1995 | 0.20276 | 0.20275 | 0.20275 | 0.20274 | 0.20273 | 0.20272 | 0.20271 | 0.2027 | 0.20269 | 0.20269 | 0.20269 | 0.20269 | 0.20269 | 0.19968
| THURSO | FLOTTA | MINIMUM HEADROOM | NC 94318 95432 | YES | YES | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -1.576 | -1.5761 | -1.5763 | -1.5765 | -1.5767 | -1.5769 | -1.577 | -1.5772 | -1.5774 | -1.5776 | -1.5778 | -1.5787 | -1.58 | -1.5813 | -0.41386 | -0.41574 | -0.41804 | -0.42029 | -0.4225 | -0.42465 | -0.42675 | -0.42907 | -0.43134 | -0.43359 | -0.43585 | -0.44681 | -0.46292 | -0.47958
|  | FLOTTA | CT |  |  |  | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -1.576 | -1.5761 | -1.5762 | -1.5763 | -1.5765 | -1.5766 | -1.5767 | -1.5768 | -1.577 | -1.5771 | -1.5772 | -1.5786 | -1.58 | -1.5813 | -0.41375 | -0.41516 | -0.41677 | -0.41836 | -0.41991 | -0.42142 | -0.42289 | -0.42452 | -0.42612 | -0.4277 | -0.42929 | -0.44605 | -0.46292 | -0.47958
|  | FLOTTA | LW |  |  |  | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -1.576 | -1.5761 | -1.5763 | -1.5765 | -1.5767 | -1.5769 | -1.577 | -1.5772 | -1.5774 | -1.5776 | -1.5778 | -1.5787 | -1.5796 | -1.5805 | -0.41386 | -0.41574 | -0.41804 | -0.42029 | -0.4225 | -0.42465 | -0.42675 | -0.42907 | -0.43134 | -0.43359 | -0.43585 | -0.44681 | -0.45782 | -0.46875
|  | FLOTTA | ST |  |  |  | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -1.5759 | -1.576 | -1.576 | -1.5761 | -1.5762 | -1.5763 | -1.5764 | -1.5765 | -1.5766 | -1.5766 | -1.5767 | -1.5771 | -1.5775 | -1.5779 | -0.41326 | -0.41383 | -0.41472 | -0.41578 | -0.41681 | -0.41781 | -0.41879 | -0.41986 | -0.42091 | -0.42193 | -0.42296 | -0.42789 | -0.43268 | -0.43749
|  | FLOTTA | FS |  |  |  | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -2.3426 | -1.5759 | -1.5759 | -1.5759 | -1.576 | -1.576 | -1.576 | -1.576 | -1.5761 | -1.5761 | -1.5761 | -1.5762 | -1.5763 | -1.5765 | -1.5766 | -0.41294 | -0.41298 | -0.41323 | -0.41353 | -0.41388 | -0.41422 | -0.41465 | -0.41509 | -0.41551 | -0.41593 | -0.41634 | -0.4183 | -0.42012 | -0.42181
| ELGIN | FOCHABERS | MINIMUM HEADROOM | NC 94318 95432 | NO | YES | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 16.514 | 16.5103 | 16.505 | 16.5001 | 16.4951 | 16.4901 | 16.4853 | 16.4805 | 16.476 | 16.4715 | 16.4671 | 16.4655 | 13.2918 | 12.7833 | 16.9653 | 16.9478 | 16.9228 | 16.8995 | 16.8759 | 16.8523 | 16.8296 | 16.8071 | 16.7902 | 16.7765 | 16.7671 | 16.7671 | 16.7671 | 13.308
|  | FOCHABERS | CT |  |  |  | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 16.514 | 16.5103 | 16.5057 | 16.5014 | 16.497 | 16.4926 | 16.4883 | 16.4838 | 16.4796 | 16.4754 | 16.4714 | 16.4655 | 13.6387 | 13.2634 | 16.9653 | 16.948 | 16.9261 | 16.9056 | 16.8849 | 16.8642 | 16.8437 | 16.8229 | 16.8029 | 16.7884 | 16.7761 | 16.7671 | 16.7671 | 13.7938
|  | FOCHABERS | LW |  |  |  | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 16.5142 | 16.5103 | 16.505 | 16.5001 | 16.4951 | 16.4901 | 16.4853 | 16.4805 | 16.476 | 16.4715 | 16.4671 | 16.4655 | 13.2918 | 12.7833 | 16.9661 | 16.9478 | 16.9228 | 16.8995 | 16.8759 | 16.8523 | 16.8296 | 16.8071 | 16.7902 | 16.7765 | 16.7671 | 16.7671 | 16.7671 | 13.308
|  | FOCHABERS | ST |  |  |  | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 16.5177 | 16.5139 | 16.5114 | 16.5088 | 16.5061 | 16.5033 | 16.5007 | 16.4979 | 16.4953 | 16.4928 | 16.4904 | 16.479 | 16.4677 | 16.4655 | 16.9716 | 16.9648 | 16.9533 | 16.9407 | 16.9278 | 16.9149 | 16.9023 | 16.8894 | 16.8772 | 16.8652 | 16.8538 | 16.7999 | 16.7671 | 16.7671
|  | FOCHABERS | FS |  |  |  | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 18.4219 | 16.5226 | 16.5214 | 16.5168 | 16.5144 | 16.5135 | 16.5125 | 16.5114 | 16.5103 | 16.5093 | 16.5083 | 16.5073 | 16.5029 | 16.4989 | 16.4951 | 16.9754 | 16.9744 | 16.9709 | 16.9674 | 16.9629 | 16.9583 | 16.9528 | 16.9478 | 16.9431 | 16.9384 | 16.9338 | 16.9128 | 16.8941 | 16.8759
| NAIRN | FORRES | MINIMUM HEADROOM | NJ 03362 59425 | NO | YES | 20.9325 | 20.6665 | 20.4099 | 20.1625 | 19.9243 | 19.6952 | 19.4754 | 19.3575 | 19.2989 | 19.2409 | 19.1837 | 13.7842 | 12.9593 | 12.047 | 18.0998 | 17.8099 | 17.5071 | 17.2889 | 17.0899 | 16.8997 | 16.7186 | 13.7951 | 13.4681 | 13.1593 | 12.8397 | 11.3142 | 10.0873 | 8.7408 | 17.8982 | 17.5938 | 17.2906 | 17.0006 | 16.7336 | 16.5113 | 13.7112 | 13.3829 | 13.1038 | 12.7875 | 12.4512 | 10.7097 | 9.6725 | 8.31
|  | FORRES | CT |  |  |  | 20.9325 | 20.6665 | 20.4099 | 20.1625 | 19.9243 | 19.6952 | 19.4754 | 19.3575 | 19.2989 | 19.2409 | 19.1837 | 13.7842 | 12.9593 | 12.0649 | 18.0998 | 17.8099 | 17.5071 | 17.2889 | 17.0899 | 16.8997 | 16.7186 | 13.7951 | 13.4681 | 13.1593 | 12.8397 | 11.3142 | 10.3537 | 9.3977 | 17.8982 | 17.5938 | 17.2906 | 17.0006 | 16.7336 | 16.5113 | 13.7112 | 13.3829 | 13.1038 | 12.7875 | 12.4512 | 10.7097 | 9.6725 | 8.6399
|  | FORRES | LW |  |  |  | 21.4031 | 21.3632 | 21.3183 | 21.2688 | 21.2152 | 21.158 | 21.0975 | 21.0333 | 20.9671 | 20.8995 | 20.831 | 19.8738 | 13.3446 | 12.047 | 18.4582 | 18.3231 | 18.1523 | 17.9894 | 17.8799 | 17.7899 | 17.7035 | 17.6107 | 17.5218 | 17.4844 | 13.4972 | 11.4644 | 10.0873 | 8.7408 | 18.3723 | 18.2885 | 18.1864 | 18.0843 | 17.986 | 17.9305 | 17.8718 | 17.8095 | 17.7453 | 17.6797 | 13.5195 | 11.247 | 9.7689 | 8.31
|  | FORRES | ST |  |  |  | 21.4713 | 21.4554 | 21.44 | 21.4249 | 21.4066 | 21.3888 | 21.3715 | 21.3547 | 21.3302 | 21.3063 | 21.2831 | 20.8668 | 20.7571 | 20.6403 | 18.5492 | 18.5011 | 18.433 | 18.3635 | 18.2977 | 18.2363 | 18.1801 | 18.1191 | 18.0466 | 17.9792 | 17.9411 | 17.5875 | 17.4445 | 17.3408 | 18.4573 | 18.4263 | 18.3873 | 18.3479 | 18.3079 | 18.27 | 18.2347 | 18.1976 | 18.1505 | 18.1059 | 18.0606 | 17.6479 | 17.5416 | 17.4283
|  | FORRES | FS |  |  |  | 21.4554 | 21.4395 | 21.416 | 21.3928 | 21.37 | 21.3474 | 21.3251 | 21.3032 | 21.2815 | 21.2602 | 21.2392 | 21.1132 | 20.9899 | 20.8723 | 18.5932 | 18.5367 | 18.498 | 18.4609 | 18.4238 | 18.3887 | 18.3536 | 18.3183 | 18.2811 | 18.2461 | 18.2091 | 18.0188 | 17.8526 | 17.7222 | 18.4647 | 18.4302 | 18.3979 | 18.3664 | 18.3351 | 18.305 | 18.2749 | 18.2451 | 18.2146 | 18.1853 | 18.1554 | 17.9892 | 17.8348 | 17.6916
| THURSO | FORSS | MINIMUM HEADROOM | ND 02614 69148 | YES | YES | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 0.95176 | 1.2389 | 1.2288 | 1.2199 | 1.2177 | 1.2173 | 1.2173 | 1.2173 | 1.2173 | 1.2173 | 0.97584 | 0.9513 | 0.86346 | 0.77456 | 0.68688 | 1.2725 | 1.2702 | 1.2702 | 1.2702 | 1.2702 | 1.2702 | 1.2702 | 1.2702 | 1.2702 | 1.2702 | 0.99693 | 0.91135 | 0.82242 | 0.73471
|  | FORSS | CT |  |  |  | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.2393 | 1.2314 | 1.2238 | 1.2193 | 1.2177 | 1.2173 | 1.2173 | 1.2173 | 1.2173 | 1.2173 | 1.2173 | 0.9454 | 0.87472 | 0.80509 | 1.2726 | 1.2702 | 1.2702 | 1.2702 | 1.2702 | 1.2702 | 1.2702 | 1.2702 | 1.2702 | 1.2702 | 1.2702 | 0.99119 | 0.92235 | 0.85296
|  | FORSS | LW |  |  |  | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 0.95176 | 1.2389 | 1.2288 | 1.2199 | 1.2177 | 1.2173 | 1.2173 | 1.2173 | 1.2173 | 1.2173 | 0.97584 | 0.9513 | 0.86346 | 0.77456 | 0.68688 | 1.2725 | 1.2702 | 1.2702 | 1.2702 | 1.2702 | 1.2702 | 1.2702 | 1.2702 | 1.2702 | 1.2702 | 0.99693 | 0.91135 | 0.82242 | 0.73471
|  | FORSS | ST |  |  |  | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.2422 | 1.2393 | 1.2348 | 1.2294 | 1.2261 | 1.2231 | 1.2202 | 1.2193 | 1.2186 | 1.2178 | 1.2173 | 1.2173 | 1.2173 | 0.99837 | 1.2741 | 1.2727 | 1.2705 | 1.2702 | 1.2702 | 1.2702 | 1.2702 | 1.2702 | 1.2702 | 1.2702 | 1.2702 | 1.2702 | 1.2702 | 1.2702
|  | FORSS | FS |  |  |  | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.4449 | 1.2438 | 1.2436 | 1.2423 | 1.2407 | 1.2394 | 1.2381 | 1.2364 | 1.2348 | 1.2331 | 1.2316 | 1.23 | 1.224 | 1.2197 | 1.2185 | 1.2749 | 1.2747 | 1.2741 | 1.2734 | 1.2727 | 1.2721 | 1.2713 | 1.2705 | 1.2702 | 1.2702 | 1.2702 | 1.2702 | 1.2702 | 1.2702
| BRACO | FORTEVIOT | MINIMUM HEADROOM | NO 04539 18092 | YES | YES | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 6.2251 | 6.0103 | 5.802 | 7.2722 | 7.2606 | 7.2479 | 7.2375 | 7.23 | 7.23 | 7.23 | 6.2909 | 6.224 | 6.1574 | 6.0909 | 5.8293 | 5.5698 | 5.3182 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 6.2389 | 5.9777 | 5.7188 | 5.4676
|  | FORTEVIOT | CT |  |  |  | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 6.2079 | 7.2733 | 7.2646 | 7.2558 | 7.2488 | 7.2416 | 7.234 | 7.23 | 7.23 | 7.23 | 7.23 | 6.2929 | 6.1278 | 5.9653 | 5.8085 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 6.2757 | 6.1135 | 5.957
|  | FORTEVIOT | LW |  |  |  | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 6.2251 | 6.0103 | 5.802 | 7.2722 | 7.2606 | 7.2479 | 7.2375 | 7.23 | 7.23 | 7.23 | 6.2909 | 6.224 | 6.1574 | 6.0909 | 5.8293 | 5.5698 | 5.3182 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 6.2389 | 5.9777 | 5.7188 | 5.4676
|  | FORTEVIOT | ST |  |  |  | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.2762 | 7.2718 | 7.2665 | 7.2616 | 7.2574 | 7.253 | 7.2485 | 7.2438 | 7.2396 | 7.2355 | 7.2314 | 7.23 | 6.2675 | 6.1517 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 6.2986
|  | FORTEVIOT | FS |  |  |  | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.4813 | 7.2786 | 7.2773 | 7.2754 | 7.2739 | 7.2725 | 7.271 | 7.2693 | 7.2676 | 7.2659 | 7.2643 | 7.2627 | 7.2552 | 7.2484 | 7.2421 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719 | 7.2719
| INVERNESS | FOYERS | MINIMUM HEADROOM | NH 49740 21044 | YES | YES | 0.86059 | 0.7485 | 0.63897 | 0.52117 | 0.40772 | 0.29862 | 0.19387 | 0.14547 | 0.12084 | 0.096453 | 0.072428 | -0.057675 | -0.1762 | -0.29558 | 0.89884 | 0.80711 | 0.71713 | 0.62222 | 0.5308 | 0.44286 | 0.35841 | 0.31887 | 0.29831 | 0.27794 | 0.25788 | 0.14564 | 0.043778 | -0.058673 | 0.86268 | 0.73421 | 0.61184 | 0.49381 | 0.38013 | 0.2708 | 0.16581 | 0.11692 | 0.091706 | 0.066746 | 0.042154 | -0.092113 | -0.21331 | -0.33533
|  | FOYERS | CT |  |  |  | 0.86059 | 0.7485 | 0.63897 | 0.52117 | 0.40772 | 0.29862 | 0.19387 | 0.14547 | 0.12084 | 0.096453 | 0.072428 | -0.057675 | -0.1762 | -0.29558 | 0.89884 | 0.80711 | 0.71713 | 0.62222 | 0.5308 | 0.44286 | 0.35841 | 0.31887 | 0.29831 | 0.27794 | 0.25788 | 0.14564 | 0.043778 | -0.058673 | 0.86268 | 0.73421 | 0.61184 | 0.49381 | 0.38013 | 0.2708 | 0.16581 | 0.11692 | 0.091706 | 0.066746 | 0.042154 | -0.092113 | -0.21331 | -0.33533
|  | FOYERS | LW |  |  |  | 1.1703 | 1.1532 | 1.134 | 1.1128 | 0.97978 | 0.95565 | 0.93017 | 0.9071 | 0.88174 | 0.84997 | 0.81787 | 0.64236 | 0.47212 | 0.29716 | 1.1829 | 1.1716 | 1.1588 | 0.99662 | 0.97337 | 0.94898 | 0.9236 | 0.89976 | 0.87539 | 0.85066 | 0.82572 | 0.68697 | 0.55001 | 0.40019 | 1.1914 | 1.1735 | 1.1534 | 1.1312 | 0.97747 | 0.94538 | 0.91187 | 0.88068 | 0.84874 | 0.81628 | 0.7835 | 0.6034 | 0.42847 | 0.24892
|  | FOYERS | ST |  |  |  | 1.1996 | 1.1928 | 1.1862 | 1.1797 | 1.1719 | 1.1642 | 1.1568 | 1.1497 | 1.1393 | 1.1293 | 1.1195 | 0.96496 | 0.92511 | 0.87482 | 1.1995 | 1.1953 | 1.1909 | 1.1864 | 1.181 | 1.1757 | 1.1706 | 1.1656 | 1.1587 | 1.1521 | 0.99498 | 0.94731 | 0.90379 | 0.86302 | 1.222 | 1.2149 | 1.2079 | 1.2012 | 1.193 | 1.185 | 1.1772 | 1.1698 | 1.159 | 1.1484 | 1.1382 | 0.94692 | 0.89112 | 0.83916
|  | FOYERS | FS |  |  |  | 1.1928 | 1.186 | 1.1759 | 1.166 | 1.1561 | 1.1465 | 1.1369 | 1.1275 | 1.1182 | 0.99874 | 0.98988 | 0.93676 | 0.89031 | 0.84737 | 1.1961 | 1.1923 | 1.1866 | 1.1809 | 1.1751 | 1.1694 | 1.1637 | 1.1581 | 1.1525 | 1.1471 | 0.99527 | 0.9477 | 0.90578 | 0.86694 | 1.2149 | 1.2078 | 1.1972 | 1.1868 | 1.1765 | 1.1664 | 1.1564 | 1.1466 | 1.1369 | 0.99916 | 0.99086 | 0.93744 | 0.88056 | 0.8279
| FRASERBURGH | FRASERBURGH | MINIMUM HEADROOM | NH 51502 69028 | NO | YES | 45.3555 | 45.2765 | 45.2021 | 45.1303 | 45.0611 | 44.9946 | 44.9308 | 44.8943 | 44.8761 | 44.8581 | 44.8404 | 38.0549 | 35.8192 | 34.6174 | 47.4904 | 47.2996 | 47.0919 | 46.8852 | 46.68 | 46.4754 | 46.2755 | 46.0862 | 45.9164 | 45.7436 | 45.5727 | 45.0197 | 44.2841 | 35.536 | 44.3604 | 44.2846 | 44.2132 | 44.1443 | 44.0779 | 44.0141 | 43.9529 | 43.9178 | 43.9004 | 43.8831 | 43.8661 | 35.5441 | 33.0164 | 31.4205
|  | FRASERBURGH | CT |  |  |  | 45.3555 | 45.2765 | 45.2021 | 45.1303 | 45.0611 | 44.9946 | 44.9308 | 44.8943 | 44.8761 | 44.8581 | 44.8404 | 38.0549 | 35.8192 | 34.785 | 47.4904 | 47.2996 | 47.0919 | 46.8852 | 46.68 | 46.4754 | 46.2755 | 46.0862 | 45.9164 | 45.7436 | 45.5727 | 45.0197 | 44.2841 | 35.9533 | 44.3604 | 44.2846 | 44.2132 | 44.1443 | 44.0779 | 44.0141 | 43.9529 | 43.9178 | 43.9004 | 43.8831 | 43.8661 | 35.5441 | 33.0442 | 31.7474
|  | FRASERBURGH | LW |  |  |  | 45.4952 | 45.4834 | 45.4701 | 45.4554 | 45.4395 | 45.4225 | 45.4045 | 45.3842 | 45.3632 | 45.3418 | 45.3201 | 44.6872 | 35.896 | 34.6174 | 47.6192 | 47.4918 | 47.3348 | 47.1749 | 47.0129 | 46.8479 | 46.6846 | 46.508 | 46.3364 | 46.1605 | 45.9862 | 45.2798 | 44.5112 | 35.536 | 44.4945 | 44.4831 | 44.4703 | 44.4562 | 44.441 | 44.4247 | 44.4074 | 44.3879 | 44.3678 | 44.3473 | 44.3265 | 35.8146 | 33.0164 | 31.4205
|  | FRASERBURGH | ST |  |  |  | 45.5155 | 45.5108 | 45.5062 | 45.5017 | 45.4963 | 45.491 | 45.4859 | 45.481 | 45.4739 | 45.4669 | 45.4602 | 45.164 | 44.5778 | 44.5397 | 47.68 | 47.6489 | 47.6027 | 47.5471 | 47.4624 | 47.3767 | 47.2927 | 47.2026 | 47.1143 | 47.0241 | 46.9357 | 46.2915 | 45.4262 | 45.2536 | 44.5139 | 44.5094 | 44.505 | 44.5007 | 44.4955 | 44.4904 | 44.4855 | 44.4808 | 44.474 | 44.4673 | 44.4609 | 44.1767 | 43.6141 | 36.5728
|  | FRASERBURGH | FS |  |  |  | 45.5108 | 45.5061 | 45.4991 | 45.4922 | 45.4854 | 45.4787 | 45.4721 | 45.4656 | 45.4591 | 45.4528 | 45.4466 | 45.4092 | 45.37 | 45.332 | 47.9291 | 47.683 | 47.6629 | 47.6399 | 47.6068 | 47.5732 | 47.5334 | 47.4939 | 47.4558 | 47.4172 | 47.3793 | 47.1898 | 47.0066 | 46.8326 | 44.5094 | 44.5049 | 44.4982 | 44.4916 | 44.4851 | 44.4786 | 44.4723 | 44.466 | 44.4599 | 44.4538 | 44.4478 | 44.4119 | 44.3743 | 44.3378
| LUNANHEAD | FRIOCKHEIM | MINIMUM HEADROOM | NO 58834 49317 | YES | YES | 3.7473 | 3.6506 | 3.5505 | 3.454 | 3.3611 | 3.2717 | 3.186 | 3.1313 | 3.1041 | 3.0771 | 2.9938 | 1.975 | 1.1029 | 0.6694 | 4.5129 | 4.3648 | 4.2047 | 4.0492 | 3.8919 | 3.7388 | 3.5962 | 3.4754 | 3.3784 | 3.2815 | 3.1865 | 2.3213 | 1.5662 | 1.0613 | 4.2643 | 4.1099 | 3.9457 | 3.7865 | 3.6284 | 3.475 | 3.3307 | 3.219 | 3.1238 | 3.024 | 2.9261 | 1.8711 | 0.96562 | 0.50752
|  | FRIOCKHEIM | CT |  |  |  | 3.7473 | 3.6506 | 3.5505 | 3.454 | 3.3611 | 3.2717 | 3.186 | 3.1313 | 3.1041 | 3.0771 | 2.9938 | 1.975 | 1.1029 | 0.6694 | 4.5129 | 4.3648 | 4.2047 | 4.0492 | 3.8919 | 3.7388 | 3.5962 | 3.4754 | 3.3784 | 3.2815 | 3.1865 | 2.3213 | 1.5662 | 1.1411 | 4.2643 | 4.1099 | 3.9457 | 3.7865 | 3.6284 | 3.475 | 3.3307 | 3.219 | 3.1238 | 3.024 | 2.9261 | 1.8711 | 0.96562 | 0.50752
|  | FRIOCKHEIM | LW |  |  |  | 3.9186 | 3.9041 | 3.8877 | 3.8697 | 3.8502 | 3.8294 | 3.8074 | 3.7792 | 3.7502 | 3.654 | 3.5368 | 2.4146 | 1.415 | 0.81459 | 4.6608 | 4.5683 | 4.4564 | 4.3448 | 4.2267 | 4.1081 | 3.9977 | 3.8745 | 3.7514 | 3.6282 | 3.5052 | 2.5292 | 1.6447 | 1.0613 | 4.4624 | 4.393 | 4.3097 | 4.2257 | 4.1365 | 4.0461 | 3.9605 | 3.8406 | 3.7157 | 3.5906 | 3.4655 | 2.2997 | 1.2588 | 0.62524
|  | FRIOCKHEIM | ST |  |  |  | 3.9434 | 3.9376 | 3.932 | 3.9265 | 3.9199 | 3.9134 | 3.9071 | 3.9005 | 3.891 | 3.8817 | 3.8726 | 3.5561 | 3.3134 | 3.1889 | 4.7137 | 4.6931 | 4.664 | 4.6303 | 4.5871 | 4.5447 | 4.5072 | 4.467 | 4.4241 | 4.3816 | 4.3407 | 3.8999 | 3.5278 | 3.3151 | 4.5119 | 4.4949 | 4.4724 | 4.447 | 4.4147 | 4.3829 | 4.3546 | 4.3242 | 4.2904 | 4.2569 | 4.2246 | 3.7484 | 3.3419 | 3.1222
|  | FRIOCKHEIM | FS |  |  |  | 3.9376 | 3.9319 | 3.9233 | 3.9149 | 3.9065 | 3.8983 | 3.8902 | 3.8822 | 3.8744 | 3.8666 | 3.859 | 3.8131 | 3.7634 | 3.7149 | 4.7168 | 4.7101 | 4.6927 | 4.6736 | 4.6537 | 4.6338 | 4.6128 | 4.592 | 4.5714 | 4.5513 | 4.5316 | 4.429 | 4.3277 | 4.2304 | 4.5105 | 4.5027 | 4.4862 | 4.4687 | 4.4506 | 4.4328 | 4.4141 | 4.3957 | 4.3776 | 4.3598 | 4.3423 | 4.2478 | 4.1519 | 4.0593
| KINTORE | FYVIE | MINIMUM HEADROOM | NJ 76759 37635 | NO | YES | 11.4686 | 11.4638 | 11.458 | 11.4523 | 11.4466 | 11.4409 | 10.9612 | 10.9552 | 10.9493 | 10.9434 | 10.2658 | 7.2809 | 5.7156 | 5.4259 | 10.8068 | 10.773 | 10.7314 | 10.7149 | 7.3498 | 7.3038 | 6.8475 | 6.7987 | 6.7507 | 6.7025 | 6.0721 | 5.226 | 3.9671 | 3.6386 | 9.8657 | 9.8507 | 9.8321 | 9.8137 | 9.7956 | 9.7775 | 9.2472 | 9.2347 | 9.2225 | 9.2102 | 8.4669 | 6.2086 | 4.478 | 4.118
|  | FYVIE | CT |  |  |  | 11.469 | 11.4658 | 11.4621 | 11.4583 | 11.4546 | 11.451 | 10.9732 | 10.9693 | 10.9655 | 10.9616 | 10.2862 | 7.449 | 5.9604 | 5.8305 | 10.8102 | 10.7869 | 10.7601 | 10.7335 | 10.7215 | 10.7112 | 6.9447 | 6.913 | 6.882 | 6.8506 | 6.237 | 5.4469 | 4.2446 | 4.074 | 9.8672 | 9.8569 | 9.8449 | 9.8331 | 9.8213 | 9.8095 | 9.2748 | 9.2639 | 9.256 | 9.248 | 8.509 | 6.545 | 4.9007 | 4.6409
|  | FYVIE | LW |  |  |  | 11.4686 | 11.4638 | 11.458 | 11.4523 | 11.4466 | 11.4409 | 10.9612 | 10.9552 | 10.9493 | 10.9434 | 10.2658 | 7.2809 | 5.7156 | 5.4259 | 10.8068 | 10.773 | 10.7314 | 10.7149 | 7.3498 | 7.3038 | 6.8475 | 6.7987 | 6.7507 | 6.7025 | 6.0721 | 5.226 | 3.9671 | 3.6386 | 9.8657 | 9.8507 | 9.8321 | 9.8137 | 9.7956 | 9.7775 | 9.2472 | 9.2347 | 9.2225 | 9.2102 | 8.4669 | 6.2086 | 4.478 | 4.118
|  | FYVIE | ST |  |  |  | 11.47 | 11.4685 | 11.4661 | 11.4633 | 11.4607 | 11.4582 | 11.2186 | 11.2159 | 11.2133 | 11.2107 | 10.8723 | 10.5041 | 9.8991 | 9.8869 | 10.8173 | 10.8064 | 10.7894 | 10.7689 | 10.7505 | 10.7322 | 7.2177 | 7.1959 | 7.1746 | 7.1533 | 6.8411 | 6.4305 | 5.8161 | 5.7172 | 9.8704 | 9.8655 | 9.8579 | 9.8488 | 9.8406 | 9.8325 | 9.5629 | 9.5543 | 9.5459 | 9.5376 | 9.1599 | 8.7468 | 7.0494 | 6.9038
|  | FYVIE | FS |  |  |  | 11.4709 | 11.4707 | 11.47 | 11.4692 | 11.4684 | 11.4675 | 11.4664 | 11.4654 | 11.4643 | 11.4633 | 11.4623 | 11.4575 | 11.4529 | 11.4486 | 10.8234 | 10.8224 | 10.8174 | 10.8115 | 10.8054 | 10.7992 | 10.7915 | 10.7839 | 10.7766 | 10.7692 | 10.762 | 10.7294 | 10.7166 | 10.7046 | 9.8731 | 9.8727 | 9.8704 | 9.8678 | 9.8651 | 9.8623 | 9.8589 | 9.8555 | 9.8522 | 9.849 | 9.8457 | 9.8303 | 9.8157 | 9.802
| GRUDIE BRIDGE | GARBAT FOREST | MINIMUM HEADROOM | NH 41255 67993 | YES | YES | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10137 | 0.10134 | 0.10131 | 0.10128 | 0.10125 | 0.10124 | 0.10124 | 0.10123 | 0.10123 | 0.10123 | 0.10123 | 0.10123 | 0.09981 | 0.099488 | 0.10155 | 0.10154 | 0.10153 | 0.10153 | 0.10153 | 0.10153 | 0.10153 | 0.10153 | 0.10153 | 0.10153 | 0.10153 | 0.10153 | 0.10153 | 0.099752
|  | GARBAT FOREST | CT |  |  |  | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10137 | 0.10135 | 0.10132 | 0.1013 | 0.10128 | 0.10127 | 0.10125 | 0.10124 | 0.10124 | 0.10123 | 0.10123 | 0.10123 | 0.10123 | 0.099975 | 0.10155 | 0.10154 | 0.10153 | 0.10153 | 0.10153 | 0.10153 | 0.10153 | 0.10153 | 0.10153 | 0.10153 | 0.10153 | 0.10153 | 0.10153 | 0.10153
|  | GARBAT FOREST | LW |  |  |  | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10137 | 0.10134 | 0.10131 | 0.10128 | 0.10125 | 0.10124 | 0.10124 | 0.10123 | 0.10123 | 0.10123 | 0.10123 | 0.10123 | 0.09981 | 0.099488 | 0.10155 | 0.10154 | 0.10153 | 0.10153 | 0.10153 | 0.10153 | 0.10153 | 0.10153 | 0.10153 | 0.10153 | 0.10153 | 0.10153 | 0.10153 | 0.099752
|  | GARBAT FOREST | ST |  |  |  | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10138 | 0.10137 | 0.10135 | 0.10134 | 0.10132 | 0.10131 | 0.1013 | 0.10128 | 0.10127 | 0.10126 | 0.10125 | 0.10123 | 0.10123 | 0.10123 | 0.10155 | 0.10155 | 0.10154 | 0.10154 | 0.10153 | 0.10153 | 0.10153 | 0.10153 | 0.10153 | 0.10153 | 0.10153 | 0.10153 | 0.10153 | 0.10153
|  | GARBAT FOREST | FS |  |  |  | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10229 | 0.10138 | 0.10138 | 0.10138 | 0.10137 | 0.10137 | 0.10136 | 0.10136 | 0.10135 | 0.10134 | 0.10134 | 0.10133 | 0.1013 | 0.10128 | 0.10126 | 0.10156 | 0.10156 | 0.10155 | 0.10155 | 0.10155 | 0.10155 | 0.10154 | 0.10154 | 0.10154 | 0.10153 | 0.10153 | 0.10153 | 0.10153 | 0.10153
| STORNOWAY | GISLA | MINIMUM HEADROOM | NB 12846 25823 | YES | YES | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.0933 | 2.0915 | 2.0893 | 2.0871 | 2.085 | 2.0813 | 2.0764 | 2.0711 | 2.0659 | 2.0608 | 2.0558 | 2.0205 | 1.9873 | 1.982 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166
|  | GISLA | CT |  |  |  | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.0934 | 2.092 | 2.0905 | 2.089 | 2.0875 | 2.086 | 2.0846 | 2.0831 | 2.0815 | 2.08 | 2.0785 | 2.0382 | 2.0049 | 1.9861 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166
|  | GISLA | LW |  |  |  | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.0933 | 2.0915 | 2.0893 | 2.0871 | 2.085 | 2.0829 | 2.0809 | 2.0787 | 2.0765 | 2.0743 | 2.0722 | 2.0205 | 1.9873 | 1.982 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166
|  | GISLA | ST |  |  |  | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.0939 | 2.0933 | 2.0925 | 2.0915 | 2.0863 | 2.0813 | 2.0764 | 2.0711 | 2.0659 | 2.0608 | 2.0558 | 2.0329 | 2.0133 | 1.9974 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166
|  | GISLA | FS |  |  |  | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.3308 | 2.0942 | 2.0941 | 2.0939 | 2.0936 | 2.0919 | 2.0903 | 2.0881 | 2.0861 | 2.084 | 2.082 | 2.08 | 2.0706 | 2.0617 | 2.0535 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166 | 1.9166
| ALNESS | GLASTULLICH | MINIMUM HEADROOM | NH 78509 76508 | YES | YES | 4.9091 | 4.9081 | 4.9069 | 4.9058 | 4.9047 | 4.9036 | 4.9025 | 4.9013 | 4.9002 | 4.899 | 4.8979 | 4.895 | 3.4159 | 3.3555 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 3.5079 | 3.4349 | 4.9787 | 4.9779 | 4.977 | 4.9761 | 4.9752 | 4.9743 | 4.9735 | 4.9725 | 4.9716 | 4.9707 | 4.9698 | 4.9653 | 3.4229 | 3.3554
|  | GLASTULLICH | CT |  |  |  | 4.9091 | 4.9081 | 4.9069 | 4.9058 | 4.9047 | 4.9036 | 4.9025 | 4.9013 | 4.9002 | 4.899 | 4.8979 | 4.895 | 3.4159 | 3.3555 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 3.5079 | 3.4349 | 4.9787 | 4.9779 | 4.977 | 4.9761 | 4.9752 | 4.9743 | 4.9735 | 4.9725 | 4.9716 | 4.9707 | 4.9698 | 4.9653 | 3.4229 | 3.3554
|  | GLASTULLICH | LW |  |  |  | 4.9096 | 4.9093 | 4.909 | 4.9087 | 4.9084 | 4.9081 | 4.9078 | 4.9075 | 4.9072 | 4.9069 | 4.9066 | 4.8984 | 3.4538 | 3.3682 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 3.5537 | 3.4503 | 4.9791 | 4.9789 | 4.9786 | 4.9784 | 4.9782 | 4.9779 | 4.9777 | 4.9775 | 4.9772 | 4.977 | 4.9767 | 4.9702 | 3.4653 | 3.3696
|  | GLASTULLICH | ST |  |  |  | 4.9096 | 4.9096 | 4.9094 | 4.9093 | 4.9086 | 4.9079 | 4.9072 | 4.9064 | 4.9057 | 4.905 | 4.9043 | 4.9008 | 3.9342 | 3.8999 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 3.9455 | 3.9014 | 4.9792 | 4.9791 | 4.979 | 4.9789 | 4.9783 | 4.9777 | 4.9772 | 4.9766 | 4.976 | 4.9754 | 4.9749 | 4.9721 | 3.963 | 3.9222
|  | GLASTULLICH | FS |  |  |  | 4.9097 | 4.9097 | 4.9096 | 4.9096 | 4.9094 | 4.9091 | 4.9088 | 4.9085 | 4.9082 | 4.908 | 4.9077 | 4.9064 | 4.9051 | 4.9038 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.6768 | 4.9792 | 4.9792 | 4.9792 | 4.9791 | 4.9789 | 4.9787 | 4.9785 | 4.9783 | 4.978 | 4.9778 | 4.9776 | 4.9765 | 4.9755 | 4.9745
| SHIN | GLEDFIELD | MINIMUM HEADROOM | NH 58876 90837 | YES | YES | 3.4501 | 3.4497 | 3.4492 | 3.4488 | 3.4483 | 3.4477 | 3.446 | 3.4449 | 3.4439 | 3.4428 | 3.4418 | 3.433 | 3.4218 | 3.4108 | 3.0793 | 3.0746 | 3.0689 | 3.0633 | 3.0578 | 3.0508 | 3.0342 | 3.0294 | 3.0246 | 3.0197 | 3.015 | 3.014 | 3.014 | 2.3999 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 2.4296
|  | GLEDFIELD | CT |  |  |  | 3.4501 | 3.4498 | 3.4495 | 3.4491 | 3.4488 | 3.4485 | 3.4471 | 3.4467 | 3.4463 | 3.4459 | 3.4455 | 3.4371 | 3.4288 | 3.4206 | 3.0796 | 3.076 | 3.072 | 3.0681 | 3.0642 | 3.0604 | 3.0429 | 3.0384 | 3.0357 | 3.0337 | 3.0318 | 3.014 | 3.014 | 3.014 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572
|  | GLEDFIELD | LW |  |  |  | 3.4501 | 3.4497 | 3.4492 | 3.4488 | 3.4483 | 3.4479 | 3.446 | 3.4455 | 3.445 | 3.4445 | 3.444 | 3.433 | 3.4218 | 3.4108 | 3.0793 | 3.0746 | 3.0689 | 3.0633 | 3.0578 | 3.0525 | 3.0343 | 3.0319 | 3.0296 | 3.0274 | 3.0252 | 3.014 | 3.014 | 2.3999 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 2.4296
|  | GLEDFIELD | ST |  |  |  | 3.4502 | 3.4501 | 3.4499 | 3.4497 | 3.4487 | 3.4477 | 3.446 | 3.4449 | 3.4439 | 3.4428 | 3.4418 | 3.4368 | 3.432 | 3.4273 | 3.0808 | 3.0794 | 3.0772 | 3.0745 | 3.0625 | 3.0508 | 3.0342 | 3.0294 | 3.0246 | 3.0197 | 3.015 | 3.014 | 3.014 | 3.014 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572
|  | GLEDFIELD | FS |  |  |  | 3.4503 | 3.4503 | 3.4502 | 3.4501 | 3.4498 | 3.4495 | 3.4488 | 3.4484 | 3.4479 | 3.4475 | 3.4471 | 3.4452 | 3.4435 | 3.4418 | 3.0816 | 3.0815 | 3.0809 | 3.0801 | 3.0762 | 3.0723 | 3.0636 | 3.0585 | 3.0535 | 3.0484 | 3.0434 | 3.0305 | 3.0226 | 3.015 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572 | 3.1572
| FORT AUGUSTUS | GLEN LAOGH | MINIMUM HEADROOM | NH 27430 00910 | YES | YES | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.09915 | 0.10234 | 0.10226 | 0.10217 | 0.10214 | 0.10213 | 0.10213 | 0.10213 | 0.10213 | 0.10213 | 0.10213 | 0.099858 | 0.098816 | 0.097699 | 0.096609 | 0.10267 | 0.10265 | 0.10265 | 0.10265 | 0.10265 | 0.10265 | 0.10265 | 0.10265 | 0.10265 | 0.10265 | 0.10265 | 0.099282 | 0.098167 | 0.097078
|  | GLEN LAOGH | CT |  |  |  | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10235 | 0.10228 | 0.10222 | 0.10216 | 0.10214 | 0.10213 | 0.10213 | 0.10213 | 0.10213 | 0.10213 | 0.10213 | 0.099734 | 0.098943 | 0.09816 | 0.10267 | 0.10265 | 0.10265 | 0.10265 | 0.10265 | 0.10265 | 0.10265 | 0.10265 | 0.10265 | 0.10265 | 0.10265 | 0.10265 | 0.099405 | 0.098629
|  | GLEN LAOGH | LW |  |  |  | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.09915 | 0.10234 | 0.10226 | 0.10217 | 0.10214 | 0.10213 | 0.10213 | 0.10213 | 0.10213 | 0.10213 | 0.10213 | 0.099858 | 0.098816 | 0.097699 | 0.096609 | 0.10267 | 0.10265 | 0.10265 | 0.10265 | 0.10265 | 0.10265 | 0.10265 | 0.10265 | 0.10265 | 0.10265 | 0.10265 | 0.099282 | 0.098167 | 0.097078
|  | GLEN LAOGH | ST |  |  |  | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10237 | 0.10234 | 0.1023 | 0.10226 | 0.10222 | 0.10218 | 0.10215 | 0.10214 | 0.10213 | 0.10213 | 0.10213 | 0.10213 | 0.10213 | 0.099593 | 0.10268 | 0.10267 | 0.10265 | 0.10265 | 0.10265 | 0.10265 | 0.10265 | 0.10265 | 0.10265 | 0.10265 | 0.10265 | 0.10265 | 0.10265 | 0.10265
|  | GLEN LAOGH | FS |  |  |  | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10426 | 0.10239 | 0.10238 | 0.10237 | 0.10236 | 0.10234 | 0.10233 | 0.10231 | 0.10229 | 0.10227 | 0.10225 | 0.10223 | 0.10216 | 0.10214 | 0.10213 | 0.10269 | 0.10269 | 0.10268 | 0.10268 | 0.10267 | 0.10266 | 0.10265 | 0.10265 | 0.10265 | 0.10265 | 0.10265 | 0.10265 | 0.10265 | 0.10265
| KINLOCHLEVEN | GLENCOE | MINIMUM HEADROOM | NN 10658 58797 | YES | YES | 4.5534 | 4.5427 | 4.5323 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.33 | 4.319 | 4.3095 | 4.3058 | 4.3022 | 4.2987 | 4.2953 | 4.2915 | 4.2878 | 4.2841 | 4.2805 | 4.2672 | 4.2535 | 3.1548 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824
|  | GLENCOE | CT |  |  |  | 4.5543 | 4.5467 | 4.5403 | 4.5339 | 4.5277 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.3309 | 4.3231 | 4.3164 | 4.3101 | 4.3078 | 4.3056 | 4.3033 | 4.3009 | 4.2985 | 4.2962 | 4.294 | 4.2839 | 4.2736 | 4.2634 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824
|  | GLENCOE | LW |  |  |  | 4.5534 | 4.5427 | 4.5323 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.33 | 4.319 | 4.3095 | 4.3058 | 4.3022 | 4.2987 | 4.2953 | 4.2915 | 4.2878 | 4.2841 | 4.2805 | 4.2672 | 4.2535 | 3.1548 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824
|  | GLENCOE | ST |  |  |  | 4.5561 | 4.5522 | 4.5483 | 4.5435 | 4.54 | 4.5365 | 4.5329 | 4.5292 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.5259 | 4.3327 | 4.3288 | 4.3247 | 4.3197 | 4.3162 | 4.3125 | 4.3097 | 4.3084 | 4.3071 | 4.3059 | 4.3047 | 4.2987 | 4.2927 | 4.2868 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824
|  | GLENCOE | FS |  |  |  | 4.5575 | 4.5566 | 4.5555 | 4.5541 | 4.553 | 4.5518 | 4.5503 | 4.5489 | 4.5475 | 4.5461 | 4.5447 | 4.5384 | 4.5324 | 4.5266 | 4.3343 | 4.3333 | 4.3321 | 4.3307 | 4.3295 | 4.3283 | 4.3268 | 4.3253 | 4.3238 | 4.3224 | 4.321 | 4.3145 | 4.3095 | 4.3075 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824 | 4.3824
| DUNOON | GLENDARUEL | MINIMUM HEADROOM | NN 03067 59147 | YES | YES | 0.44235 | 0.44235 | 0.44235 | 0.31252 | 0.27939 | 0.24685 | 0.21486 | 0.18024 | 0.14584 | 0.11163 | 0.077641 | 0.025779 | -0.026687 | -0.078392 | 0.38131 | 0.38131 | 0.28793 | 0.24817 | 0.20909 | 0.1707 | 0.13296 | 0.092115 | 0.051538 | 0.011177 | -0.028922 | -0.090105 | -0.152 | -0.213 | 0.39603 | 0.39565 | 0.29308 | 0.25331 | 0.21422 | 0.17581 | 0.13807 | 0.097206 | 0.056615 | 0.016241 | -0.02387 | -0.085074 | -0.14699 | -0.20801
|  | GLENDARUEL | CT |  |  |  | 0.44235 | 0.44235 | 0.44235 | 0.44235 | 0.44235 | 0.44235 | 0.44235 | 0.44235 | 0.44235 | 0.44235 | 0.44235 | 0.44235 | 0.44235 | 0.29253 | 0.38579 | 0.38469 | 0.384 | 0.38331 | 0.38263 | 0.38196 | 0.38131 | 0.38131 | 0.38131 | 0.38131 | 0.38131 | 0.30874 | 0.26634 | 0.22459 | 0.39744 | 0.39723 | 0.39699 | 0.39675 | 0.39651 | 0.39628 | 0.39605 | 0.39581 | 0.39565 | 0.39565 | 0.39565 | 0.3139 | 0.27148 | 0.22972
|  | GLENDARUEL | LW |  |  |  | 0.44235 | 0.44235 | 0.44235 | 0.31252 | 0.27939 | 0.24685 | 0.21486 | 0.18024 | 0.14584 | 0.11163 | 0.077641 | 0.025779 | -0.026687 | -0.078392 | 0.38131 | 0.38131 | 0.28793 | 0.24817 | 0.20909 | 0.1707 | 0.13296 | 0.092115 | 0.051538 | 0.011177 | -0.028922 | -0.090105 | -0.152 | -0.213 | 0.39603 | 0.39565 | 0.29308 | 0.25331 | 0.21422 | 0.17581 | 0.13807 | 0.097206 | 0.056615 | 0.016241 | -0.02387 | -0.085074 | -0.14699 | -0.20801
|  | GLENDARUEL | ST |  |  |  | 0.44235 | 0.44235 | 0.44235 | 0.44235 | 0.44235 | 0.44235 | 0.44235 | 0.44235 | 0.44235 | 0.44235 | 0.44235 | 0.44235 | 0.29942 | 0.27639 | 0.38394 | 0.38134 | 0.38131 | 0.38131 | 0.38131 | 0.38131 | 0.3105 | 0.30459 | 0.29879 | 0.29307 | 0.28744 | 0.25994 | 0.23272 | 0.20555 | 0.39697 | 0.39606 | 0.39565 | 0.39565 | 0.39565 | 0.39565 | 0.39565 | 0.30975 | 0.30395 | 0.29823 | 0.2926 | 0.26509 | 0.23786 | 0.21068
|  | GLENDARUEL | FS |  |  |  | 0.44235 | 0.44235 | 0.44235 | 0.44235 | 0.44235 | 0.44235 | 0.44235 | 0.44235 | 0.44235 | 0.44235 | 0.44235 | 0.44235 | 0.44235 | 0.44235 | 0.38602 | 0.38568 | 0.3841 | 0.38275 | 0.38227 | 0.3818 | 0.38131 | 0.38131 | 0.38131 | 0.38131 | 0.38131 | 0.38131 | 0.38131 | 0.38131 | 0.39748 | 0.39742 | 0.39702 | 0.39655 | 0.39638 | 0.39622 | 0.39601 | 0.3958 | 0.39565 | 0.39565 | 0.39565 | 0.39565 | 0.39565 | 0.39565
| ABERNETHY | GLENDEVON | MINIMUM HEADROOM | NO 00101 02760 | YES | YES | 3.046 | 3.0002 | 2.9441 | 2.8861 | 2.8255 | 2.7664 | 2.7073 | 2.6433 | 2.5797 | 2.5154 | 2.4607 | 2.2852 | 2.1105 | 1.9386 | 3.1976 | 3.1404 | 3.0704 | 2.9981 | 2.9225 | 2.8488 | 2.7749 | 2.6951 | 2.6159 | 2.5356 | 2.4674 | 2.2484 | 2.0304 | 1.8161 | 2.9254 | 2.9254 | 2.9254 | 2.9254 | 2.9126 | 2.84 | 2.7672 | 2.6886 | 2.6105 | 2.5314 | 2.4642 | 2.2485 | 2.0337 | 1.8225
|  | GLENDEVON | CT |  |  |  | 3.0533 | 3.0258 | 2.9943 | 2.9608 | 2.9246 | 2.8899 | 2.8547 | 2.8162 | 2.7768 | 2.7359 | 2.7036 | 2.5737 | 2.4503 | 2.3302 | 3.2066 | 3.1723 | 3.133 | 3.0913 | 3.0461 | 3.0028 | 2.9589 | 2.9108 | 2.8617 | 2.8106 | 2.7703 | 2.6083 | 2.4544 | 2.3046 | 2.9254 | 2.9254 | 2.9254 | 2.9254 | 2.9254 | 2.9254 | 2.9254 | 2.9011 | 2.8527 | 2.8024 | 2.7627 | 2.6031 | 2.4514 | 2.3038
|  | GLENDEVON | LW |  |  |  | 3.046 | 3.0002 | 2.9441 | 2.8861 | 2.8255 | 2.7664 | 2.7073 | 2.6433 | 2.5797 | 2.5154 | 2.4607 | 2.2852 | 2.1105 | 1.9386 | 3.1976 | 3.1404 | 3.0704 | 2.9981 | 2.9225 | 2.8488 | 2.7749 | 2.6951 | 2.6159 | 2.5356 | 2.4674 | 2.2484 | 2.0304 | 1.8161 | 2.9254 | 2.9254 | 2.9254 | 2.9254 | 2.9126 | 2.84 | 2.7672 | 2.6886 | 2.6105 | 2.5314 | 2.4642 | 2.2485 | 2.0337 | 1.8225
|  | GLENDEVON | ST |  |  |  | 3.0611 | 3.0466 | 3.0244 | 2.9964 | 2.9753 | 2.9552 | 2.9348 | 2.9123 | 2.8891 | 2.8648 | 2.8469 | 2.7632 | 2.6859 | 2.61 | 3.2164 | 3.1983 | 3.1706 | 3.1356 | 3.1093 | 3.0843 | 3.0588 | 3.0307 | 3.0018 | 2.9715 | 2.9491 | 2.8447 | 2.7483 | 2.6536 | 2.9254 | 2.9254 | 2.9254 | 2.9254 | 2.9254 | 2.9254 | 2.9254 | 2.9254 | 2.9254 | 2.9254 | 2.9254 | 2.8359 | 2.741 | 2.6477
|  | GLENDEVON | FS |  |  |  | 3.2139 | 3.2123 | 3.2058 | 3.1975 | 3.1901 | 3.1829 | 3.1742 | 3.1652 | 3.1562 | 3.1471 | 3.14 | 3.1072 | 3.0791 | 3.0533 | 3.407 | 3.405 | 3.3969 | 3.3865 | 3.3772 | 3.3684 | 3.3574 | 3.3462 | 3.335 | 3.3236 | 3.3148 | 3.2739 | 3.2388 | 3.2066 | 2.9254 | 2.9254 | 2.9254 | 2.9254 | 2.9254 | 2.9254 | 2.9254 | 2.9254 | 2.9254 | 2.9254 | 2.9254 | 2.9254 | 2.9254 | 2.9254
| FORT AUGUSTUS | GLENDOE | MINIMUM HEADROOM | NH 40060 08894 | YES | YES | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.519 | 2.517 | 2.5146 | 2.5122 | 2.5099 | 2.5076 | 2.5048 | 2.5005 | 2.4963 | 2.4922 | 2.4881 | 2.4694 | 2.4694 | 1.9441 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 1.9314
|  | GLENDOE | CT |  |  |  | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5191 | 2.5176 | 2.5159 | 2.5143 | 2.5126 | 2.5111 | 2.5095 | 2.5078 | 2.5062 | 2.5045 | 2.5029 | 2.4707 | 2.4694 | 2.4694 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592
|  | GLENDOE | LW |  |  |  | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.519 | 2.517 | 2.5146 | 2.5122 | 2.5099 | 2.5076 | 2.5054 | 2.503 | 2.5007 | 2.4983 | 2.496 | 2.4694 | 2.4694 | 1.9441 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 1.9314
|  | GLENDOE | ST |  |  |  | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5196 | 2.519 | 2.5181 | 2.517 | 2.5128 | 2.5088 | 2.5048 | 2.5005 | 2.4963 | 2.4922 | 2.4881 | 2.4694 | 2.4694 | 2.4694 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592
|  | GLENDOE | FS |  |  |  | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5858 | 2.5199 | 2.5199 | 2.5196 | 2.5193 | 2.518 | 2.5166 | 2.5149 | 2.5132 | 2.5116 | 2.5099 | 2.5083 | 2.5007 | 2.4936 | 2.4869 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592 | 2.4592
| BRACO | GLENEAGLES | MINIMUM HEADROOM | NN 91540 11582 | NO | YES | 31.2866 | 31.1755 | 31.0717 | 30.9716 | 30.8753 | 30.7826 | 30.6937 | 30.6435 | 30.6185 | 30.5938 | 30.5694 | 30.2834 | 30.159 | 30.0266 | 28.6896 | 28.6148 | 28.5547 | 28.4968 | 28.4411 | 28.3874 | 28.336 | 28.3069 | 28.2924 | 28.2781 | 28.264 | 28.0985 | 28.0265 | 27.9499 | 30.4743 | 30.3395 | 30.2087 | 30.0831 | 29.9573 | 29.8315 | 29.7102 | 29.6261 | 29.5671 | 29.5055 | 29.4557 | 29.0035 | 28.8251 | 28.6931
|  | GLENEAGLES | CT |  |  |  | 31.2866 | 31.1755 | 31.0717 | 30.9716 | 30.8753 | 30.7826 | 30.6937 | 30.6435 | 30.6185 | 30.5938 | 30.5694 | 30.2834 | 30.159 | 30.0266 | 28.6896 | 28.6148 | 28.5547 | 28.4968 | 28.4411 | 28.3874 | 28.336 | 28.3069 | 28.2924 | 28.2781 | 28.264 | 28.0985 | 28.0265 | 27.9499 | 30.4743 | 30.3395 | 30.2087 | 30.0831 | 29.9573 | 29.8315 | 29.7102 | 29.6261 | 29.5671 | 29.5055 | 29.4557 | 29.0035 | 28.8251 | 28.6931
|  | GLENEAGLES | LW |  |  |  | 31.4834 | 31.4667 | 31.4479 | 31.4272 | 31.4048 | 31.3809 | 31.3556 | 31.3274 | 31.2983 | 31.2686 | 31.2385 | 30.9106 | 30.7269 | 30.53 | 28.8177 | 28.7901 | 28.7724 | 28.7605 | 28.7475 | 28.7337 | 28.719 | 28.7027 | 28.6859 | 28.6687 | 28.6512 | 28.4615 | 28.3552 | 28.2412 | 30.6765 | 30.6344 | 30.5839 | 30.533 | 30.476 | 30.4125 | 30.3496 | 30.2804 | 30.2101 | 30.1371 | 30.0765 | 29.575 | 29.3917 | 29.1952
|  | GLENEAGLES | ST |  |  |  | 31.5119 | 31.5052 | 31.4988 | 31.4925 | 31.4848 | 31.4774 | 31.4702 | 31.4634 | 31.4534 | 31.4438 | 31.4344 | 31.2987 | 31.2516 | 31.1998 | 28.8473 | 28.8312 | 28.8177 | 28.8035 | 28.7938 | 28.7895 | 28.7853 | 28.7814 | 28.7756 | 28.7701 | 28.7646 | 28.6861 | 28.6589 | 28.6289 | 30.7141 | 30.6978 | 30.6773 | 30.6558 | 30.6253 | 30.5926 | 30.5606 | 30.5266 | 30.4885 | 30.4486 | 30.4172 | 30.1787 | 30.0452 | 29.9105
|  | GLENEAGLES | FS |  |  |  | 31.5052 | 31.4986 | 31.4888 | 31.4791 | 31.4695 | 31.4601 | 31.4508 | 31.4416 | 31.4326 | 31.4236 | 31.4149 | 31.3622 | 31.3072 | 31.254 | 28.852 | 28.8421 | 28.8254 | 28.8158 | 28.8041 | 28.7917 | 28.7788 | 28.7688 | 28.7636 | 28.7584 | 28.7533 | 28.7228 | 28.691 | 28.6602 | 30.7121 | 30.7031 | 30.6882 | 30.6735 | 30.6555 | 30.6365 | 30.6166 | 30.5964 | 30.5762 | 30.5556 | 30.538 | 30.4435 | 30.3542 | 30.2705
| RANNOCH | GLENETIVE | MINIMUM HEADROOM | NN 25850 54886 | YES | YES | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.2912 | 0.28038 | 0.34996 | 0.34866 | 0.3479 | 0.34782 | 0.34782 | 0.29955 | 0.29159 | 0.28298 | 0.27442 | 0.26592 | 0.25746 | 0.2446 | 0.23161 | 0.21891 | 0.35832 | 0.35832 | 0.35832 | 0.35832 | 0.35832 | 0.35832 | 0.29839 | 0.28979 | 0.28123 | 0.27272 | 0.26426 | 0.25139 | 0.2384 | 0.2257
|  | GLENETIVE | CT |  |  |  | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.35045 | 0.34895 | 0.34848 | 0.34801 | 0.34782 | 0.34782 | 0.34782 | 0.34782 | 0.34782 | 0.29499 | 0.2898 | 0.28083 | 0.27177 | 0.26283 | 0.35832 | 0.35832 | 0.35832 | 0.35832 | 0.35832 | 0.35832 | 0.35832 | 0.35832 | 0.35832 | 0.35832 | 0.29661 | 0.28763 | 0.27857 | 0.26962
|  | GLENETIVE | LW |  |  |  | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.2912 | 0.28038 | 0.34996 | 0.34866 | 0.3479 | 0.34782 | 0.34782 | 0.29955 | 0.29159 | 0.28298 | 0.27442 | 0.26592 | 0.25746 | 0.2446 | 0.23161 | 0.21891 | 0.35832 | 0.35832 | 0.35832 | 0.35832 | 0.35832 | 0.35832 | 0.29839 | 0.28979 | 0.28123 | 0.27272 | 0.26426 | 0.25139 | 0.2384 | 0.2257
|  | GLENETIVE | ST |  |  |  | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.35132 | 0.35004 | 0.349 | 0.34865 | 0.34854 | 0.34844 | 0.34834 | 0.34823 | 0.34812 | 0.34801 | 0.3479 | 0.34782 | 0.34782 | 0.34782 | 0.35832 | 0.35832 | 0.35832 | 0.35832 | 0.35832 | 0.35832 | 0.35832 | 0.35832 | 0.35832 | 0.35832 | 0.35832 | 0.35832 | 0.35832 | 0.35832
|  | GLENETIVE | FS |  |  |  | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.40161 | 0.35204 | 0.35195 | 0.35139 | 0.35073 | 0.35049 | 0.35026 | 0.34995 | 0.34966 | 0.34943 | 0.34924 | 0.34916 | 0.34892 | 0.34873 | 0.34856 | 0.35832 | 0.35832 | 0.35832 | 0.35832 | 0.35832 | 0.35832 | 0.35832 | 0.35832 | 0.35832 | 0.35832 | 0.35832 | 0.35832 | 0.35832 | 0.35832
| FORT WILLIAM | GLENUIG | MINIMUM HEADROOM | NM 67224 77119 | YES | YES | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.092177 | 0.13324 | 0.13293 | 0.13257 | 0.13238 | 0.13219 | 0.1318 | 0.13133 | 0.13099 | 0.13099 | 0.13099 | 0.13099 | 0.13099 | 0.081073 | 0.060905 | 0.13857 | 0.1385 | 0.13843 | 0.13836 | 0.1383 | 0.13816 | 0.138 | 0.13782 | 0.13769 | 0.13769 | 0.13769 | 0.13769 | 0.083481 | 0.063306
|  | GLENUIG | CT |  |  |  | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.13325 | 0.13302 | 0.13276 | 0.13255 | 0.13242 | 0.13228 | 0.13216 | 0.13202 | 0.13188 | 0.13175 | 0.13161 | 0.13099 | 0.094517 | 0.079844 | 0.13858 | 0.13852 | 0.13847 | 0.13842 | 0.13838 | 0.13833 | 0.13829 | 0.13824 | 0.13819 | 0.13814 | 0.1381 | 0.13769 | 0.096929 | 0.082251
|  | GLENUIG | LW |  |  |  | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.092177 | 0.13324 | 0.13293 | 0.13257 | 0.13238 | 0.13219 | 0.13201 | 0.13182 | 0.13163 | 0.13143 | 0.13124 | 0.13105 | 0.13099 | 0.081073 | 0.060905 | 0.13857 | 0.1385 | 0.13843 | 0.13836 | 0.1383 | 0.13823 | 0.13817 | 0.1381 | 0.13804 | 0.13797 | 0.1379 | 0.13769 | 0.083481 | 0.063306
|  | GLENUIG | ST |  |  |  | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.13333 | 0.13324 | 0.1331 | 0.13292 | 0.13228 | 0.1318 | 0.13133 | 0.13099 | 0.13099 | 0.13099 | 0.13099 | 0.13099 | 0.097312 | 0.088364 | 0.13862 | 0.13857 | 0.13853 | 0.1385 | 0.13833 | 0.13816 | 0.138 | 0.13782 | 0.13769 | 0.13769 | 0.13769 | 0.13769 | 0.099725 | 0.090774
|  | GLENUIG | FS |  |  |  | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.13339 | 0.13338 | 0.13334 | 0.13329 | 0.13298 | 0.13268 | 0.13244 | 0.13224 | 0.13204 | 0.13185 | 0.13166 | 0.13099 | 0.13099 | 0.13099 | 0.13864 | 0.13864 | 0.13862 | 0.1386 | 0.13851 | 0.13846 | 0.13839 | 0.13832 | 0.13825 | 0.13818 | 0.13811 | 0.1378 | 0.13769 | 0.13769
| BRORA | GOLSPIE | MINIMUM HEADROOM | NC 82996 00240 | YES | YES | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 4.9394 | 4.9258 | 4.9101 | 4.8947 | 4.8808 | 4.8668 | 4.8528 | 4.8377 | 4.8229 | 4.8084 | 4.7959 | 4.7673 | 4.7673 | 3.9964 | 5.0566 | 5.0516 | 5.0458 | 5.0401 | 5.0349 | 5.0297 | 5.0245 | 5.0189 | 5.0134 | 5.008 | 5.0027 | 4.9697 | 4.9353 | 4.9039
|  | GOLSPIE | CT |  |  |  | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 4.9394 | 4.9258 | 4.9101 | 4.8947 | 4.8808 | 4.8668 | 4.8528 | 4.8377 | 4.8229 | 4.8084 | 4.7959 | 4.7673 | 4.7673 | 3.9964 | 5.0566 | 5.0516 | 5.0458 | 5.0401 | 5.0349 | 5.0297 | 5.0245 | 5.0189 | 5.0134 | 5.008 | 5.0027 | 4.9697 | 4.9353 | 4.9039
|  | GOLSPIE | LW |  |  |  | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 4.9452 | 4.9406 | 4.935 | 4.9296 | 4.9256 | 4.9217 | 4.9179 | 4.9137 | 4.9097 | 4.9056 | 4.9018 | 4.7936 | 4.7673 | 4.7673 | 5.0588 | 5.0571 | 5.055 | 5.053 | 5.0515 | 5.0501 | 5.0486 | 5.0471 | 5.0456 | 5.0441 | 5.0427 | 5.0017 | 4.9593 | 4.9179
|  | GOLSPIE | ST |  |  |  | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 4.947 | 4.9452 | 4.9427 | 4.94 | 4.931 | 4.9219 | 4.9128 | 4.9031 | 4.8936 | 4.8845 | 4.8756 | 4.8321 | 4.7902 | 4.7673 | 5.0594 | 5.0588 | 5.0579 | 5.0569 | 5.0535 | 5.0501 | 5.0468 | 5.0432 | 5.0396 | 5.0362 | 5.033 | 5.0168 | 5.0001 | 4.9836
|  | GOLSPIE | FS |  |  |  | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 5.749 | 4.948 | 4.9474 | 4.9465 | 4.9455 | 4.9422 | 4.9389 | 4.9346 | 4.9305 | 4.9264 | 4.9224 | 4.9186 | 4.9003 | 4.8827 | 4.8656 | 5.0598 | 5.0596 | 5.0593 | 5.0589 | 5.0577 | 5.0564 | 5.0549 | 5.0533 | 5.0518 | 5.0503 | 5.0489 | 5.0421 | 5.0356 | 5.0293
| BURGHMUIR | GOODLYBURN | MINIMUM HEADROOM | NO 10084 24586 | NO | YES | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.0208 | 16.9612 | 16.8866 | 16.8114 | 16.7515 | 16.7196 | 16.688 | 16.6536 | 16.6197 | 16.5851 | 16.5498 | 16.3749 | 16.2158 | 16.2158 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495
|  | GOODLYBURN | CT |  |  |  | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.0338 | 17.0042 | 16.9689 | 16.9327 | 16.8946 | 16.858 | 16.8212 | 16.7811 | 16.7546 | 16.7372 | 16.719 | 16.5862 | 16.4579 | 16.3361 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495
|  | GOODLYBURN | LW |  |  |  | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.0208 | 16.9612 | 16.8866 | 16.8114 | 16.7515 | 16.7196 | 16.688 | 16.6536 | 16.6197 | 16.5851 | 16.5498 | 16.3749 | 16.2158 | 16.2158 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495
|  | GOODLYBURN | ST |  |  |  | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.0397 | 17.0196 | 16.9882 | 16.95 | 16.9126 | 16.8764 | 16.8405 | 16.8014 | 16.7637 | 16.7469 | 16.7298 | 16.6454 | 16.5664 | 16.4917 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495
|  | GOODLYBURN | FS |  |  |  | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.4471 | 17.0515 | 17.0494 | 17.0404 | 17.0295 | 17.0174 | 17.0057 | 16.991 | 16.9763 | 16.9619 | 16.9472 | 16.9323 | 16.8584 | 16.7906 | 16.7491 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495 | 16.2495
| CHARLESTON | GOURDIE | MINIMUM HEADROOM | NO 34573 32203 | YES | YES | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 6.1927 | 5.8495 | 5.5069 | 5.1718 | 7.7242 | 7.7242 | 7.7242 | 7.7242 | 6.2408 | 6.1102 | 5.9818 | 5.8426 | 5.7041 | 5.5662 | 5.4295 | 5.0246 | 4.6205 | 4.2251 | 7.9573 | 7.9573 | 7.9573 | 7.9573 | 7.9573 | 7.9573 | 6.212 | 6.0764 | 5.9415 | 5.8072 | 5.674 | 5.2796 | 4.886 | 4.5009
|  | GOURDIE | CT |  |  |  | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 6.1962 | 7.7242 | 7.7242 | 7.7242 | 7.7242 | 7.7242 | 7.7242 | 7.7242 | 7.7242 | 7.7242 | 6.2883 | 6.232 | 5.9628 | 5.695 | 5.4336 | 7.9573 | 7.9573 | 7.9573 | 7.9573 | 7.9573 | 7.9573 | 7.9573 | 7.9573 | 7.9573 | 7.9573 | 7.9573 | 6.1935 | 5.9326 | 5.678
|  | GOURDIE | LW |  |  |  | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 6.1927 | 5.8495 | 5.5069 | 5.1718 | 7.7242 | 7.7242 | 7.7242 | 7.7242 | 6.2408 | 6.1102 | 5.9818 | 5.8426 | 5.7041 | 5.5662 | 5.4295 | 5.0246 | 4.6205 | 4.2251 | 7.9573 | 7.9573 | 7.9573 | 7.9573 | 7.9573 | 7.9573 | 6.212 | 6.0764 | 5.9415 | 5.8072 | 5.674 | 5.2796 | 4.886 | 4.5009
|  | GOURDIE | ST |  |  |  | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 7.7242 | 7.7242 | 7.7242 | 7.7242 | 7.7242 | 7.7242 | 7.7242 | 7.7242 | 7.7242 | 7.7242 | 7.7242 | 6.1739 | 5.9932 | 5.8152 | 7.9573 | 7.9573 | 7.9573 | 7.9573 | 7.9573 | 7.9573 | 7.9573 | 7.9573 | 7.9573 | 7.9573 | 7.9573 | 7.9573 | 6.2231 | 6.0497
|  | GOURDIE | FS |  |  |  | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 8.1256 | 7.7242 | 7.7242 | 7.7242 | 7.7242 | 7.7242 | 7.7242 | 7.7242 | 7.7242 | 7.7242 | 7.7242 | 7.7242 | 7.7242 | 7.7242 | 7.7242 | 7.9573 | 7.9573 | 7.9573 | 7.9573 | 7.9573 | 7.9573 | 7.9573 | 7.9573 | 7.9573 | 7.9573 | 7.9573 | 7.9573 | 7.9573 | 7.9573
| BOAT OF GARTEN | GRANTOWN | MINIMUM HEADROOM | NJ 03670 26311 | NO | YES | 18.0544 | 17.9424 | 17.8359 | 17.7332 | 17.6343 | 17.5392 | 17.448 | 17.4061 | 17.3853 | 17.3647 | 17.3444 | 17.2453 | 14.4557 | 14.074 | 16.3025 | 16.187 | 16.0739 | 15.9658 | 15.8752 | 15.8192 | 15.7655 | 15.7408 | 15.7286 | 15.7165 | 15.7045 | 15.6462 | 13.6918 | 13.1169 | 16.535 | 16.4132 | 16.2972 | 16.1854 | 16.0778 | 15.9743 | 15.8749 | 15.8294 | 15.8067 | 15.7843 | 15.7622 | 15.6543 | 13.5185 | 12.9623
|  | GRANTOWN | CT |  |  |  | 18.0544 | 17.9424 | 17.8359 | 17.7332 | 17.6343 | 17.5392 | 17.448 | 17.4061 | 17.3853 | 17.3647 | 17.3444 | 17.2453 | 14.4557 | 14.074 | 16.3025 | 16.187 | 16.0739 | 15.9658 | 15.8752 | 15.8192 | 15.7655 | 15.7408 | 15.7286 | 15.7165 | 15.7045 | 15.6462 | 13.7804 | 13.3462 | 16.535 | 16.4132 | 16.2972 | 16.1854 | 16.0778 | 15.9743 | 15.8749 | 15.8294 | 15.8067 | 15.7843 | 15.7622 | 15.6543 | 13.5185 | 13.0579
|  | GRANTOWN | LW |  |  |  | 18.2525 | 18.2357 | 18.2168 | 18.196 | 18.1734 | 18.1493 | 18.1239 | 18.1007 | 18.0768 | 18.0524 | 18.0277 | 17.8969 | 17.7704 | 14.1068 | 16.4602 | 16.4105 | 16.3526 | 16.2958 | 16.2383 | 16.1802 | 16.1633 | 16.1496 | 16.1356 | 16.1212 | 16.1067 | 16.0297 | 13.6918 | 13.1169 | 16.7506 | 16.7323 | 16.7118 | 16.6891 | 16.6646 | 16.6383 | 16.6106 | 16.5854 | 16.5594 | 16.5329 | 16.506 | 16.3636 | 13.5757 | 12.9623
|  | GRANTOWN | ST |  |  |  | 18.2812 | 18.2745 | 18.268 | 18.2617 | 18.2539 | 18.2465 | 18.2392 | 18.2322 | 18.222 | 18.2121 | 18.2025 | 18.1583 | 18.1193 | 18.0833 | 16.4977 | 16.4808 | 16.4593 | 16.436 | 16.4138 | 16.3916 | 16.3699 | 16.3475 | 16.3232 | 16.2994 | 16.2763 | 16.1835 | 16.1606 | 16.1394 | 16.7819 | 16.7746 | 16.7675 | 16.7606 | 16.7522 | 16.7441 | 16.7362 | 16.7286 | 16.7175 | 16.7067 | 16.6962 | 16.6481 | 16.6056 | 16.5665
|  | GRANTOWN | FS |  |  |  | 18.2745 | 18.2678 | 18.2579 | 18.2482 | 18.2385 | 18.229 | 18.2197 | 18.2104 | 18.2013 | 18.1923 | 18.1835 | 18.1304 | 18.0839 | 18.0408 | 16.4999 | 16.4925 | 16.4794 | 16.466 | 16.4528 | 16.4397 | 16.4253 | 16.4112 | 16.3973 | 16.3836 | 16.3703 | 16.2981 | 16.2322 | 16.1701 | 16.7746 | 16.7673 | 16.7566 | 16.7459 | 16.7354 | 16.7251 | 16.7149 | 16.7048 | 16.6949 | 16.6852 | 16.6755 | 16.6178 | 16.5671 | 16.5202
| SHETLAND | GREMISTA | MINIMUM HEADROOM | HU4646842756 | NO | YES | 35.1212 | 35.1212 | 35.1212 | 35.1212 | 35.1212 | 35.1212 | 35.1212 | 35.1212 | 35.1212 | 35.1212 | 35.1212 | 34.0593 | 33.3603 | 32.6722 | 33.3145 | 33.173 | 32.9971 | 32.8206 | 32.6532 | 32.4517 | 32.2485 | 32.0315 | 31.8161 | 31.5954 | 31.3764 | 30.1686 | 29.3872 | 28.618 | 42.1961 | 42.1961 | 35.9051 | 35.7476 | 35.5982 | 35.4183 | 35.237 | 35.0434 | 34.8511 | 34.6541 | 34.4586 | 33.2425 | 32.5408 | 31.7982
|  | GREMISTA | CT |  |  |  | 35.1212 | 35.1212 | 35.1212 | 35.1212 | 35.1212 | 35.1212 | 35.1212 | 35.1212 | 35.1212 | 35.1212 | 35.1212 | 34.7245 | 34.3215 | 33.8363 | 33.3319 | 33.2389 | 33.13 | 33.0197 | 32.9163 | 32.7843 | 32.6499 | 32.5064 | 32.3617 | 32.2088 | 32.0551 | 31.0632 | 30.4829 | 29.9193 | 42.1961 | 42.1961 | 42.1961 | 35.9253 | 35.8329 | 35.7152 | 35.5952 | 35.4671 | 35.338 | 35.2015 | 35.0644 | 34.0409 | 33.523 | 33.02
|  | GREMISTA | LW |  |  |  | 35.1212 | 35.1212 | 35.1212 | 35.1212 | 35.1212 | 35.1212 | 35.1212 | 35.1212 | 35.1212 | 35.1212 | 35.1212 | 34.0593 | 33.3603 | 32.6722 | 33.3145 | 33.173 | 32.9971 | 32.8206 | 32.6532 | 32.4517 | 32.2485 | 32.0315 | 31.8161 | 31.5954 | 31.3764 | 30.1686 | 29.3872 | 28.618 | 42.1961 | 42.1961 | 35.9051 | 35.7476 | 35.5982 | 35.4183 | 35.237 | 35.0434 | 34.8511 | 34.6541 | 34.4586 | 33.2425 | 32.5408 | 31.7982
|  | GREMISTA | ST |  |  |  | 35.1212 | 35.1212 | 35.1212 | 35.1212 | 35.1212 | 35.1212 | 35.1212 | 35.1212 | 35.1212 | 35.1212 | 35.1212 | 34.9229 | 34.9229 | 34.9229 | 33.3629 | 33.3212 | 33.2562 | 33.1777 | 33.0988 | 33.0014 | 32.9027 | 32.7965 | 32.6896 | 32.5768 | 32.4634 | 31.8717 | 31.5173 | 31.1695 | 42.1961 | 42.1961 | 42.1961 | 42.1961 | 35.9959 | 35.9089 | 35.8208 | 35.7261 | 35.6307 | 35.5299 | 35.4288 | 34.8316 | 34.5152 | 34.2049
|  | GREMISTA | FS |  |  |  | 35.1212 | 35.1212 | 35.1212 | 35.1212 | 35.1212 | 35.1212 | 35.1212 | 35.1212 | 35.1212 | 35.1212 | 35.1212 | 35.1212 | 35.1212 | 35.1212 | 33.3863 | 33.3811 | 33.3602 | 33.3352 | 33.309 | 33.2746 | 33.2329 | 33.1911 | 33.1489 | 33.1055 | 33.0621 | 32.8807 | 32.7439 | 32.6256 | 42.1961 | 42.1961 | 42.1961 | 42.1961 | 42.1961 | 42.1961 | 42.1961 | 42.1961 | 42.1961 | 42.1961 | 35.9631 | 35.8012 | 35.6791 | 35.5735
| WILLOWDALE | GREYFRIARS | MINIMUM HEADROOM | NJ 94327 07070 | NO | NO | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 25.4021 | 25.3623 | 25.3222 | 25.2957 | 25.2689 | 25.2242 | 25.1787 | 25.13 | 25.0833 | 25.038 | 24.9937 | 24.9028 | 24.8149 | 21.4391 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 21.6205
|  | GREYFRIARS | CT |  |  |  | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 25.4216 | 25.3858 | 25.3665 | 25.3595 | 25.3525 | 25.3445 | 25.334 | 25.3234 | 25.3148 | 25.3069 | 25.2997 | 25.2295 | 25.1578 | 25.0891 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934
|  | GREYFRIARS | LW |  |  |  | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 25.4021 | 25.3623 | 25.3222 | 25.2957 | 25.2699 | 25.2448 | 25.22 | 25.1933 | 25.1667 | 25.1407 | 25.1128 | 24.9028 | 24.8149 | 21.4391 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 21.6205
|  | GREYFRIARS | ST |  |  |  | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 25.4052 | 25.3741 | 25.3422 | 25.3138 | 25.2689 | 25.2242 | 25.1787 | 25.13 | 25.0833 | 25.038 | 24.9937 | 24.9066 | 24.8531 | 24.8003 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934
|  | GREYFRIARS | FS |  |  |  | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 27.921 | 25.4293 | 25.4165 | 25.3903 | 25.3829 | 25.37 | 25.3571 | 25.3408 | 25.325 | 25.3094 | 25.294 | 25.279 | 25.2087 | 25.1413 | 25.0765 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934 | 25.5934
| GRUDIE BRIDGE | GRUDIE BRIDGE | MINIMUM HEADROOM | NH 309 623 | NO | YES | 22.8431 | 22.6395 | 22.4388 | 22.2452 | 22.0587 | 21.8795 | 21.7075 | 21.6161 | 21.5707 | 21.5258 | 21.4815 | 21.2586 | 21.0313 | 20.7924 | 21.7313 | 21.5688 | 21.4086 | 21.2541 | 21.1053 | 20.9622 | 20.8249 | 20.752 | 20.7158 | 20.6799 | 20.6445 | 20.4667 | 20.2853 | 20.0946 | 21.6411 | 21.4366 | 21.2349 | 21.0404 | 20.8531 | 20.6731 | 20.5002 | 20.4085 | 20.3628 | 20.3177 | 20.2732 | 20.0493 | 19.821 | 19.581
|  | GRUDIE BRIDGE | CT |  |  |  | 22.8431 | 22.6395 | 22.4388 | 22.2452 | 22.0587 | 21.8795 | 21.7075 | 21.6161 | 21.5707 | 21.5258 | 21.4815 | 21.2586 | 21.0313 | 20.7924 | 21.7313 | 21.5688 | 21.4086 | 21.2541 | 21.1053 | 20.9622 | 20.8249 | 20.752 | 20.7158 | 20.6799 | 20.6445 | 20.4667 | 20.2853 | 20.0946 | 21.6411 | 21.4366 | 21.2349 | 21.0404 | 20.8531 | 20.6731 | 20.5002 | 20.4085 | 20.3628 | 20.3177 | 20.2732 | 20.0493 | 19.821 | 19.581
|  | GRUDIE BRIDGE | LW |  |  |  | 23.2034 | 23.1729 | 23.1385 | 23.1007 | 23.0596 | 23.0158 | 22.9695 | 22.9208 | 22.8706 | 22.8193 | 22.7674 | 22.4924 | 22.1892 | 21.8403 | 22.0189 | 21.9945 | 21.9671 | 21.9369 | 21.9041 | 21.8691 | 21.8322 | 21.7933 | 21.7532 | 21.7123 | 21.6709 | 21.4514 | 21.2094 | 20.9309 | 22.0031 | 21.9724 | 21.9379 | 21.8998 | 21.8586 | 21.8146 | 21.7681 | 21.7191 | 21.6687 | 21.6172 | 21.565 | 21.2887 | 20.9842 | 20.6337
|  | GRUDIE BRIDGE | ST |  |  |  | 23.2557 | 23.2435 | 23.2317 | 23.2202 | 23.2062 | 23.1925 | 23.1793 | 23.1661 | 23.1469 | 23.1282 | 23.1101 | 23.0193 | 22.9347 | 22.8449 | 22.0606 | 22.0509 | 22.0414 | 22.0322 | 22.0211 | 22.0102 | 21.9996 | 21.9891 | 21.9738 | 21.9589 | 21.9444 | 21.8719 | 21.8044 | 21.7327 | 22.0556 | 22.0434 | 22.0315 | 22.0199 | 22.0058 | 21.9921 | 21.9788 | 21.9656 | 21.9463 | 21.9275 | 21.9093 | 21.8181 | 21.7331 | 21.6429
|  | GRUDIE BRIDGE | FS |  |  |  | 23.2435 | 23.2314 | 23.2134 | 23.1956 | 23.1781 | 23.1608 | 23.1438 | 23.127 | 23.1104 | 23.0941 | 23.078 | 22.9815 | 22.8894 | 22.8022 | 22.0509 | 22.0412 | 22.0268 | 22.0127 | 21.9987 | 21.9849 | 21.9713 | 21.9579 | 21.9446 | 21.9316 | 21.9188 | 21.8418 | 21.7683 | 21.6986 | 22.0434 | 22.0312 | 22.0131 | 21.9952 | 21.9776 | 21.9603 | 21.9431 | 21.9263 | 21.9096 | 21.8932 | 21.877 | 21.7801 | 21.6876 | 21.6
| SHETLAND | GUTCHER | MINIMUM HEADROOM | HU5453899599 | YES | YES | 1.5831 | 1.5799 | 1.576 | 1.573 | 1.573 | 1.573 | 1.573 | 1.573 | 1.573 | 0.97313 | 0.93259 | 0.87758 | 0.82185 | 0.76711 | 1.474 | 1.4525 | 1.4525 | 1.4525 | 1.4525 | 1.4525 | 0.97001 | 0.92385 | 0.87798 | 0.8324 | 0.78708 | 0.72559 | 0.66329 | 0.6021 | 1 | 1 | 0.99894 | 0.95236 | 0.90661 | 0.86165 | 0.81744 | 0.7696 | 0.72208 | 0.67484 | 0.62789 | 0.56417 | 0.4996 | 0.4362
|  | GUTCHER | CT |  |  |  | 1.5834 | 1.5811 | 1.5785 | 1.576 | 1.5735 | 1.573 | 1.573 | 1.573 | 1.573 | 1.573 | 1.573 | 1.573 | 0.9832 | 0.94146 | 1.4773 | 1.4525 | 1.4525 | 1.4525 | 1.4525 | 1.4525 | 1.4525 | 1.4525 | 0.99804 | 0.96792 | 0.93797 | 0.89108 | 0.84365 | 0.79699 | 1 | 1 | 1 | 0.99869 | 0.96846 | 0.93872 | 0.90949 | 0.87788 | 0.84648 | 0.81527 | 0.78424 | 0.73565 | 0.6865 | 0.63815
|  | GUTCHER | LW |  |  |  | 1.5831 | 1.5799 | 1.576 | 1.573 | 1.573 | 1.573 | 1.573 | 1.573 | 1.573 | 0.97313 | 0.93259 | 0.87758 | 0.82185 | 0.76711 | 1.474 | 1.4525 | 1.4525 | 1.4525 | 1.4525 | 1.4525 | 0.97001 | 0.92385 | 0.87798 | 0.8324 | 0.78708 | 0.72559 | 0.66329 | 0.6021 | 1 | 1 | 0.99894 | 0.95236 | 0.90661 | 0.86165 | 0.81744 | 0.7696 | 0.72208 | 0.67484 | 0.62789 | 0.56417 | 0.4996 | 0.4362
|  | GUTCHER | ST |  |  |  | 1.5841 | 1.5832 | 1.5818 | 1.58 | 1.5796 | 1.5792 | 1.5787 | 1.5783 | 1.5779 | 1.5774 | 1.577 | 1.5749 | 1.573 | 1.573 | 1.4868 | 1.4754 | 1.4575 | 1.4525 | 1.4525 | 1.4525 | 1.4525 | 1.4525 | 1.4525 | 1.4525 | 1.4525 | 1.4525 | 1.4525 | 1.4525 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.98617 | 0.9612 | 0.93634
|  | GUTCHER | FS |  |  |  | 1.5847 | 1.5846 | 1.5842 | 1.5837 | 1.5835 | 1.5834 | 1.5832 | 1.583 | 1.5828 | 1.5826 | 1.5824 | 1.5815 | 1.5807 | 1.58 | 1.4933 | 1.4925 | 1.4873 | 1.4812 | 1.4793 | 1.4774 | 1.475 | 1.4726 | 1.4703 | 1.468 | 1.4657 | 1.455 | 1.4525 | 1.4525 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| THURSO | HALKIRK | MINIMUM HEADROOM | ND 13246 58223 | YES | YES | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 2.4064 | 2.1671 | 1.9328 | 3.6861 | 3.6801 | 3.6726 | 3.6653 | 3.6581 | 3.651 | 3.644 | 3.6365 | 3.629 | 3.6215 | 3.6141 | 3.6134 | 2.2764 | 2.042
|  | HALKIRK | CT |  |  |  | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 2.4823 | 2.3002 | 3.6868 | 3.6827 | 3.678 | 3.6734 | 3.6689 | 3.6644 | 3.66 | 3.6552 | 3.6505 | 3.6458 | 3.6412 | 3.6177 | 3.6134 | 2.4096
|  | HALKIRK | LW |  |  |  | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 2.4064 | 2.1671 | 1.9328 | 3.6861 | 3.6801 | 3.6726 | 3.6653 | 3.6581 | 3.651 | 3.644 | 3.6365 | 3.629 | 3.6215 | 3.6141 | 3.6134 | 2.2764 | 2.042
|  | HALKIRK | ST |  |  |  | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 3.6881 | 3.6864 | 3.6836 | 3.6803 | 3.6776 | 3.6749 | 3.6723 | 3.6695 | 3.6667 | 3.6639 | 3.6612 | 3.648 | 3.6346 | 3.6213
|  | HALKIRK | FS |  |  |  | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 4.2713 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 3.6302 | 3.6891 | 3.689 | 3.6882 | 3.6873 | 3.6864 | 3.6855 | 3.6844 | 3.6832 | 3.6821 | 3.6811 | 3.68 | 3.675 | 3.6702 | 3.6656
| ABERNETHY | HARBOUR | MINIMUM HEADROOM | NO 11948 22049 | NO | YES | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 24.5962 | 24.5394 | 24.4661 | 24.3797 | 24.2933 | 24.2117 | 24.1324 | 24.0511 | 23.9695 | 23.8848 | 23.8395 | 23.8395 | 23.8395 | 19.4934 | 25.5521 | 25.481 | 25.3893 | 25.2811 | 25.173 | 25.127 | 25.0906 | 25.0534 | 25.016 | 24.9772 | 24.94 | 24.715 | 24.5651 | 24.5651
|  | HARBOUR | CT |  |  |  | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 24.6012 | 24.5595 | 24.5081 | 24.4451 | 24.382 | 24.3238 | 24.2651 | 24.2027 | 24.1368 | 24.0683 | 24.0054 | 23.8395 | 23.8395 | 23.8395 | 25.5584 | 25.5061 | 25.4418 | 25.363 | 25.2841 | 25.2113 | 25.1514 | 25.1228 | 25.0926 | 25.0613 | 25.0325 | 24.8826 | 24.747 | 24.618
|  | HARBOUR | LW |  |  |  | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 24.5962 | 24.5394 | 24.4661 | 24.3797 | 24.2933 | 24.2117 | 24.1324 | 24.0511 | 23.9695 | 23.8848 | 23.8395 | 23.8395 | 23.8395 | 19.4934 | 25.5521 | 25.481 | 25.3893 | 25.2811 | 25.173 | 25.127 | 25.0906 | 25.0534 | 25.016 | 24.9772 | 24.94 | 24.715 | 24.5651 | 24.5651
|  | HARBOUR | ST |  |  |  | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 24.6135 | 24.5933 | 24.5622 | 24.5189 | 24.4617 | 24.4082 | 24.3546 | 24.2971 | 24.237 | 24.1751 | 24.1173 | 23.883 | 23.8395 | 23.8395 | 25.5737 | 25.5484 | 25.5096 | 25.4553 | 25.3838 | 25.3168 | 25.2498 | 25.1778 | 25.1385 | 25.1102 | 25.0837 | 24.9764 | 24.882 | 24.7916
|  | HARBOUR | FS |  |  |  | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 25.1496 | 24.6228 | 24.6182 | 24.6074 | 24.5921 | 24.5715 | 24.5522 | 24.5295 | 24.5072 | 24.4848 | 24.4617 | 24.4394 | 24.3422 | 24.2612 | 24.1914 | 25.5854 | 25.5796 | 25.566 | 25.5469 | 25.5212 | 25.497 | 25.4686 | 25.4407 | 25.4126 | 25.3838 | 25.3559 | 25.2343 | 25.1496 | 25.1177
| STORNOWAY | HARRIS GRID | MINIMUM HEADROOM | NG 13495 94249 | YES | YES | 29.8157 | 29.6223 | 29.4353 | 29.2551 | 29.0815 | 28.9146 | 28.7544 | 28.6724 | 28.6314 | 28.5908 | 28.5508 | 28.3465 | 28.0068 | 27.7973 | 29.7984 | 29.6437 | 29.4942 | 29.35 | 29.2112 | 29.0777 | 28.9495 | 28.8837 | 28.8506 | 28.8179 | 28.7857 | 28.6162 | 28.3385 | 28.1648 | 29.7277 | 29.5339 | 29.3465 | 29.1659 | 28.9919 | 28.8247 | 28.6641 | 28.5818 | 28.5405 | 28.4997 | 28.4595 | 28.2512 | 27.9073 | 27.6938
|  | HARRIS GRID | CT |  |  |  | 29.8157 | 29.6223 | 29.4353 | 29.2551 | 29.0815 | 28.9146 | 28.7544 | 28.6724 | 28.6314 | 28.5908 | 28.5508 | 28.3465 | 28.0068 | 27.7973 | 29.7984 | 29.6437 | 29.4942 | 29.35 | 29.2112 | 29.0777 | 28.9495 | 28.8837 | 28.8506 | 28.8179 | 28.7857 | 28.6162 | 28.3385 | 28.1648 | 29.7277 | 29.5339 | 29.3465 | 29.1659 | 28.9919 | 28.8247 | 28.6641 | 28.5818 | 28.5405 | 28.4997 | 28.4595 | 28.2512 | 27.9073 | 27.6938
|  | HARRIS GRID | LW |  |  |  | 30.2078 | 30.1814 | 30.1516 | 30.1188 | 29.9962 | 29.9606 | 29.9225 | 29.8836 | 29.8406 | 29.7933 | 29.7454 | 29.4833 | 29.065 | 28.7567 | 30.097 | 30.0813 | 30.0648 | 29.9905 | 29.9585 | 29.9245 | 29.8886 | 29.8522 | 29.8147 | 29.7764 | 29.7377 | 29.5204 | 29.1788 | 28.9254 | 30.1007 | 30.0741 | 30.0445 | 29.9696 | 29.9298 | 29.8874 | 29.8426 | 29.7973 | 29.7506 | 29.7029 | 29.6547 | 29.3878 | 28.9651 | 28.6529
|  | HARRIS GRID | ST |  |  |  | 30.253 | 30.2425 | 30.2322 | 30.2222 | 30.2101 | 30.1983 | 30.1869 | 30.1757 | 30.1594 | 30.1436 | 30.1282 | 29.9672 | 29.8239 | 29.7409 | 30.1331 | 30.1244 | 30.1159 | 30.1075 | 30.0982 | 30.0907 | 30.0834 | 30.0769 | 30.0675 | 30.0583 | 29.9891 | 29.916 | 29.7929 | 29.7235 | 30.1476 | 30.1366 | 30.1259 | 30.1155 | 30.1027 | 30.091 | 30.0796 | 30.0685 | 30.0523 | 29.99 | 29.9717 | 29.8817 | 29.7296 | 29.6451
|  | HARRIS GRID | FS |  |  |  | 30.2425 | 30.2319 | 30.2164 | 30.201 | 30.1858 | 30.1709 | 30.1561 | 30.1416 | 30.1273 | 30.1131 | 30.0992 | 29.9324 | 29.8547 | 29.7719 | 30.1246 | 30.1161 | 30.1033 | 30.0927 | 30.0839 | 30.0756 | 30.0673 | 30.0592 | 29.9976 | 29.9848 | 29.972 | 29.8961 | 29.8247 | 29.7574 | 30.1367 | 30.1258 | 30.1097 | 30.0937 | 30.0786 | 30.0637 | 30.049 | 29.993 | 29.9787 | 29.9627 | 29.9468 | 29.8526 | 29.764 | 29.6804
| DYCE | HARVEST AVENUE | MINIMUM HEADROOM | NJ 86978 11769 | NO | YES | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08
|  | HARVEST AVENUE | CT |  |  |  | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08
|  | HARVEST AVENUE | LW |  |  |  | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08
|  | HARVEST AVENUE | ST |  |  |  | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08
|  | HARVEST AVENUE | FS |  |  |  | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 23.28 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08 | 22.08
| THURSO | HASTIGROW | MINIMUM HEADROOM | ND 26576 60773 | YES | YES | 6.517 | 4.9966 | 4.8379 | 4.6849 | 4.5375 | 4.3959 | 4.2408 | 4.0978 | 3.9961 | 3.8952 | 3.7953 | 2.9085 | 2.4721 | 2.0303 | 6.0669 | 5.9355 | 4.8686 | 4.6531 | 4.4442 | 4.2418 | 4.0458 | 3.904 | 3.7953 | 3.6874 | 3.5805 | 2.7661 | 2.3108 | 1.853 | 6.0574 | 5.8999 | 4.8872 | 4.643 | 4.4067 | 4.178 | 3.9571 | 3.8068 | 3.6984 | 3.5853 | 3.47 | 2.5214 | 2.0245 | 1.5231
|  | HASTIGROW | CT |  |  |  | 6.517 | 4.9966 | 4.8379 | 4.6849 | 4.5375 | 4.3959 | 4.2408 | 4.0978 | 3.9961 | 3.8952 | 3.7953 | 2.9085 | 2.4721 | 2.0303 | 6.0669 | 5.9355 | 4.8686 | 4.6531 | 4.4442 | 4.2418 | 4.0458 | 3.904 | 3.7953 | 3.6874 | 3.5805 | 2.7661 | 2.3108 | 1.853 | 6.0574 | 5.8999 | 4.8872 | 4.643 | 4.4067 | 4.178 | 3.9571 | 3.8068 | 3.6984 | 3.5853 | 3.47 | 2.5214 | 2.0245 | 1.5231
|  | HASTIGROW | LW |  |  |  | 6.8206 | 6.7949 | 6.7659 | 6.734 | 6.6994 | 6.6625 | 6.6235 | 6.5832 | 6.5417 | 6.4993 | 6.4564 | 4.012 | 3.4419 | 2.8403 | 6.3001 | 6.2518 | 6.2121 | 6.1707 | 6.1396 | 6.1102 | 6.0797 | 4.8991 | 4.7917 | 4.684 | 4.5763 | 3.6445 | 3.0532 | 2.4391 | 6.3674 | 6.3358 | 6.2997 | 6.2607 | 6.2191 | 6.1771 | 6.143 | 6.1078 | 4.9397 | 4.8226 | 4.7053 | 3.6272 | 2.98 | 2.3024
|  | HASTIGROW | ST |  |  |  | 6.8647 | 6.8544 | 6.8444 | 6.8347 | 6.8229 | 6.8114 | 6.8003 | 6.7892 | 6.7731 | 6.7575 | 6.7422 | 6.4564 | 6.3867 | 4.8133 | 6.3514 | 6.3376 | 6.321 | 6.3029 | 6.2744 | 6.2573 | 6.2407 | 6.2234 | 6.2027 | 6.1824 | 6.168 | 4.849 | 4.6251 | 4.3994 | 6.4145 | 6.4033 | 6.3919 | 6.3805 | 6.3653 | 6.3505 | 6.3361 | 6.3216 | 6.302 | 6.2829 | 6.2643 | 4.9625 | 4.7373 | 4.4949
|  | HASTIGROW | FS |  |  |  | 6.8544 | 6.8442 | 6.829 | 6.814 | 6.7993 | 6.7847 | 6.7703 | 6.7562 | 6.7422 | 6.7285 | 6.7149 | 6.6336 | 6.5569 | 6.4844 | 6.3461 | 6.3374 | 6.3226 | 6.3076 | 6.2885 | 6.2697 | 6.249 | 6.2317 | 6.2181 | 6.2047 | 6.1915 | 6.1168 | 6.0572 | 6.0066 | 6.4046 | 6.3941 | 6.3783 | 6.3626 | 6.3465 | 6.3307 | 6.3147 | 6.299 | 6.2835 | 6.2683 | 6.2532 | 6.1646 | 6.0848 | 6.0215
| STRICHEN | HATTON | MINIMUM HEADROOM | NK 06441 37348 | NO | YES | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 5.9304 | 4.4688 | 4.153 | 7.9934 | 7.9868 | 7.98 | 7.98 | 7.98 | 7.98 | 7.98 | 7.98 | 7.98 | 7.98 | 6.2452 | 5.721 | 4.4386 | 4.0334 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 5.8064 | 4.2722 | 3.8965
|  | HATTON | CT |  |  |  | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 6.0905 | 4.7285 | 4.5099 | 7.9934 | 7.987 | 7.98 | 7.98 | 7.98 | 7.98 | 7.98 | 7.98 | 7.98 | 7.98 | 7.98 | 5.9264 | 4.7718 | 4.4913 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 5.9968 | 4.5811 | 4.321
|  | HATTON | LW |  |  |  | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 5.9304 | 4.4688 | 4.153 | 7.9938 | 7.9868 | 7.98 | 7.98 | 7.98 | 7.98 | 7.98 | 7.98 | 7.98 | 7.98 | 6.2452 | 5.721 | 4.4386 | 4.0334 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 5.8064 | 4.2722 | 3.8965
|  | HATTON | ST |  |  |  | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6205 | 5.6991 | 5.5592 | 7.9964 | 7.995 | 7.9927 | 7.9897 | 7.9839 | 7.98 | 7.98 | 7.98 | 7.98 | 7.98 | 7.98 | 6.2999 | 5.6827 | 5.5032 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.128 | 5.6203 | 5.4539
|  | HATTON | FS |  |  |  | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.6891 | 8.0263 | 8.0262 | 8.0256 | 8.0248 | 8.0229 | 8.0211 | 8.0187 | 8.0164 | 8.0141 | 8.0118 | 8.0095 | 7.9983 | 7.9876 | 7.98 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953 | 8.1953
| PERSLEY | HAUDAGAIN | MINIMUM HEADROOM | NJ 91425 09066 | NO | YES | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 22.8127 | 22.7739 | 22.7424 | 22.7191 | 22.6964 | 22.6741 | 22.6521 | 22.6284 | 22.605 | 22.5821 | 22.5537 | 22.2654 | 22.1477 | 22.1176 | 21.9859 | 21.98 | 21.9742 | 21.97 | 21.9658 | 21.9617 | 21.9577 | 21.9534 | 21.9491 | 21.9449 | 21.9397 | 21.8868 | 21.8322 | 21.8135
|  | HAUDAGAIN | CT |  |  |  | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 22.8281 | 22.7973 | 22.7772 | 22.7637 | 22.7465 | 22.7256 | 22.7087 | 22.6919 | 22.6786 | 22.666 | 22.6535 | 22.4524 | 22.2469 | 22.1562 | 21.9878 | 21.9839 | 21.9806 | 21.9781 | 21.975 | 21.9712 | 21.9681 | 21.965 | 21.9625 | 21.9602 | 21.958 | 21.9211 | 21.8834 | 21.8473
|  | HAUDAGAIN | LW |  |  |  | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 22.8127 | 22.7739 | 22.7424 | 22.7191 | 22.6964 | 22.6741 | 22.6521 | 22.6284 | 22.605 | 22.5821 | 22.5537 | 22.2654 | 22.1477 | 22.1176 | 21.9859 | 21.98 | 21.9742 | 21.97 | 21.9658 | 21.9617 | 21.9577 | 21.9534 | 21.9491 | 21.9449 | 21.9397 | 21.8868 | 21.8322 | 21.8135
|  | HAUDAGAIN | ST |  |  |  | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 22.8586 | 22.8393 | 22.82 | 22.8024 | 22.7694 | 22.738 | 22.7096 | 22.6799 | 22.6529 | 22.6268 | 22.6011 | 22.4543 | 22.3085 | 22.1688 | 21.9917 | 21.9892 | 21.9868 | 21.9846 | 21.9792 | 21.9734 | 21.9682 | 21.9628 | 21.9578 | 21.9531 | 21.9484 | 21.9214 | 21.8947 | 21.8691
|  | HAUDAGAIN | FS |  |  |  | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 25.6755 | 22.8885 | 22.8804 | 22.8714 | 22.8647 | 22.8503 | 22.8365 | 22.8196 | 22.8029 | 22.7879 | 22.7771 | 22.7671 | 22.7199 | 22.6709 | 22.6211 | 21.9993 | 21.9944 | 21.9933 | 21.9924 | 21.9906 | 21.9889 | 21.9867 | 21.9846 | 21.9826 | 21.9806 | 21.9788 | 21.9701 | 21.9611 | 21.952
| WILLOWDALE | HAYTON | MINIMUM HEADROOM | NJ 92753 08909 | NO | NO | 25.5717 | 25.4826 | 25.3992 | 25.3188 | 25.2413 | 25.1668 | 25.0953 | 25.0548 | 25.0346 | 25.0146 | 24.9949 | 22.0986 | 21.4291 | 20.693 | 23.7591 | 23.6793 | 23.6025 | 23.5282 | 23.4675 | 23.4209 | 23.3761 | 23.3499 | 23.3361 | 23.3224 | 23.3088 | 20.5448 | 19.8386 | 19.1329 | 24.0118 | 23.9166 | 23.8265 | 23.7396 | 23.6557 | 23.575 | 23.4973 | 23.4509 | 23.4253 | 23.4001 | 23.375 | 20.7381 | 19.9084 | 19.078
|  | HAYTON | CT |  |  |  | 25.5717 | 25.4826 | 25.3992 | 25.3188 | 25.2413 | 25.1668 | 25.0953 | 25.0548 | 25.0346 | 25.0146 | 24.9949 | 24.8997 | 22.0621 | 21.6409 | 23.7591 | 23.6793 | 23.6025 | 23.5282 | 23.4675 | 23.4209 | 23.3761 | 23.3499 | 23.3361 | 23.3224 | 23.3088 | 21.1387 | 20.6906 | 20.2508 | 24.0118 | 23.9166 | 23.8265 | 23.7396 | 23.6557 | 23.575 | 23.4973 | 23.4509 | 23.4253 | 23.4001 | 23.375 | 23.2093 | 20.8435 | 20.3252
|  | HAYTON | LW |  |  |  | 25.7293 | 25.7159 | 25.7009 | 25.6843 | 25.6664 | 25.6472 | 25.627 | 25.6042 | 25.5808 | 25.5569 | 25.5327 | 22.0986 | 21.4291 | 20.693 | 23.8673 | 23.8165 | 23.7555 | 23.7209 | 23.7036 | 23.6856 | 23.6671 | 23.6466 | 23.6257 | 23.6046 | 23.5882 | 20.5448 | 19.8386 | 19.1329 | 24.1666 | 24.1361 | 24.1002 | 24.0631 | 24.025 | 23.9859 | 23.946 | 23.902 | 23.8585 | 23.8223 | 23.7848 | 20.7381 | 19.9084 | 19.078
|  | HAYTON | ST |  |  |  | 25.7521 | 25.7468 | 25.7417 | 25.7366 | 25.7305 | 25.7245 | 25.7187 | 25.7133 | 25.7053 | 25.6975 | 25.69 | 25.6485 | 25.6106 | 25.5686 | 23.8956 | 23.8751 | 23.8458 | 23.8117 | 23.7824 | 23.7537 | 23.7424 | 23.7356 | 23.7274 | 23.7193 | 23.7115 | 23.6681 | 23.6317 | 20.9238 | 24.1943 | 24.1821 | 24.1662 | 24.1485 | 24.132 | 24.1159 | 24.1002 | 24.084 | 24.0654 | 24.0472 | 24.0294 | 23.931 | 23.8589 | 23.7849
|  | HAYTON | FS |  |  |  | 25.7468 | 25.7415 | 25.7336 | 25.7259 | 25.7182 | 25.7107 | 25.7032 | 25.6958 | 25.6886 | 25.6815 | 25.6744 | 25.6322 | 25.5881 | 25.5454 | 23.9351 | 23.9299 | 23.9179 | 23.905 | 23.8913 | 23.8778 | 23.8622 | 23.8468 | 23.8317 | 23.8169 | 23.8024 | 23.7257 | 23.6665 | 23.6346 | 24.2071 | 24.2012 | 24.1907 | 24.1799 | 24.1689 | 24.158 | 24.1463 | 24.1348 | 24.1234 | 24.1123 | 24.1013 | 24.04 | 23.9765 | 23.9143
| BRORA | HELMSDALE | MINIMUM HEADROOM | ND 02372 15376 | YES | YES | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.6151 | 4.6139 | 4.6125 | 4.611 | 4.6097 | 4.6083 | 4.607 | 4.6049 | 4.6028 | 4.602 | 4.6012 | 4.5923 | 4.5821 | 4.5736 | 4.5479 | 4.5471 | 4.5463 | 4.5454 | 4.5446 | 4.5438 | 4.543 | 4.5418 | 4.5404 | 4.5398 | 4.5398 | 4.5398 | 4.5398 | 4.5398
|  | HELMSDALE | CT |  |  |  | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.6151 | 4.6142 | 4.6132 | 4.6123 | 4.6113 | 4.6103 | 4.6094 | 4.6083 | 4.6073 | 4.6063 | 4.6053 | 4.5961 | 4.5882 | 4.5805 | 4.5479 | 4.5474 | 4.5468 | 4.5462 | 4.5456 | 4.545 | 4.5444 | 4.5438 | 4.5432 | 4.5426 | 4.542 | 4.5398 | 4.5398 | 4.5398
|  | HELMSDALE | LW |  |  |  | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.6151 | 4.6139 | 4.6125 | 4.611 | 4.6097 | 4.6083 | 4.607 | 4.6055 | 4.6041 | 4.6028 | 4.6023 | 4.5923 | 4.5821 | 4.5736 | 4.5479 | 4.5471 | 4.5463 | 4.5454 | 4.5446 | 4.5438 | 4.543 | 4.5421 | 4.5413 | 4.5404 | 4.5398 | 4.5398 | 4.5398 | 4.5398
|  | HELMSDALE | ST |  |  |  | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.6155 | 4.6151 | 4.6145 | 4.6139 | 4.6116 | 4.6094 | 4.6072 | 4.6049 | 4.6028 | 4.602 | 4.6012 | 4.5975 | 4.5937 | 4.5899 | 4.5481 | 4.5479 | 4.5475 | 4.5471 | 4.5458 | 4.5445 | 4.5432 | 4.5418 | 4.5404 | 4.5398 | 4.5398 | 4.5398 | 4.5398 | 4.5398
|  | HELMSDALE | FS |  |  |  | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.7338 | 4.6157 | 4.6156 | 4.6155 | 4.6153 | 4.6144 | 4.6136 | 4.6125 | 4.6114 | 4.6104 | 4.6094 | 4.6084 | 4.6036 | 4.6015 | 4.6 | 4.5482 | 4.5482 | 4.5481 | 4.548 | 4.5475 | 4.547 | 4.5463 | 4.5457 | 4.5451 | 4.5445 | 4.5439 | 4.541 | 4.5398 | 4.5398
| INVERNESS | HILTON | MINIMUM HEADROOM | NH 67326 43262 | NO | YES | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 22.3492 | 20.9192 | 28.2202 | 28.062 | 27.8691 | 27.6805 | 27.5205 | 27.4843 | 27.4481 | 27.4265 | 27.4265 | 27.4265 | 27.4265 | 21.1999 | 19.4905 | 17.8035 | 28.9352 | 28.8583 | 28.7646 | 28.673 | 28.6515 | 28.6515 | 28.6515 | 28.6515 | 28.6515 | 28.6515 | 28.6515 | 21.7109 | 19.9815 | 18.2939
|  | HILTON | CT |  |  |  | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 28.2313 | 28.1139 | 27.9805 | 27.8496 | 27.7208 | 27.5802 | 27.5103 | 27.4826 | 27.455 | 27.427 | 27.4265 | 27.4265 | 21.7259 | 20.6261 | 28.9406 | 28.8835 | 28.8187 | 28.7552 | 28.6926 | 28.6515 | 28.6515 | 28.6515 | 28.6515 | 28.6515 | 28.6515 | 28.6515 | 28.6515 | 21.1174
|  | HILTON | LW |  |  |  | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 22.3492 | 20.9192 | 28.2202 | 28.062 | 27.8691 | 27.6805 | 27.5205 | 27.4843 | 27.4481 | 27.4265 | 27.4265 | 27.4265 | 27.4265 | 21.1999 | 19.4905 | 17.8035 | 28.9352 | 28.8583 | 28.7646 | 28.673 | 28.6515 | 28.6515 | 28.6515 | 28.6515 | 28.6515 | 28.6515 | 28.6515 | 21.7109 | 19.9815 | 18.2939
|  | HILTON | ST |  |  |  | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 28.2727 | 28.2206 | 28.1407 | 28.0457 | 27.9703 | 27.8871 | 27.8036 | 27.7132 | 27.6238 | 27.5326 | 27.5108 | 27.4381 | 27.4265 | 27.4265 | 28.9607 | 28.9354 | 28.8966 | 28.8504 | 28.8138 | 28.7734 | 28.7328 | 28.6889 | 28.6515 | 28.6515 | 28.6515 | 28.6515 | 28.6515 | 28.6515
|  | HILTON | FS |  |  |  | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 31.3486 | 28.3054 | 28.3007 | 28.2791 | 28.2541 | 28.2299 | 28.2018 | 28.1667 | 28.1316 | 28.097 | 28.0622 | 28.0276 | 27.8721 | 27.7344 | 27.6041 | 28.9765 | 28.9743 | 28.9638 | 28.9516 | 28.9399 | 28.9263 | 28.9092 | 28.8921 | 28.8753 | 28.8584 | 28.8416 | 28.7661 | 28.6992 | 28.6515
| ARBROATH | HUME STREET | MINIMUM HEADROOM | NO 64067 41180 | NO | YES | 30.2244 | 30.0607 | 29.8992 | 29.744 | 29.5942 | 29.4489 | 29.3082 | 29.2165 | 29.1678 | 29.1203 | 29.0734 | 28.7341 | 28.4466 | 28.1393 | 26.7305 | 26.4636 | 26.2689 | 26.0859 | 25.9819 | 25.8945 | 25.8099 | 25.7547 | 25.7254 | 25.6967 | 25.6684 | 25.4639 | 25.2904 | 21.772 | 28.1139 | 27.899 | 27.7111 | 27.5318 | 27.3581 | 27.1856 | 27.0149 | 26.8988 | 26.828 | 26.7606 | 26.6941 | 26.2127 | 25.8336 | 25.5703
|  | HUME STREET | CT |  |  |  | 30.2244 | 30.0607 | 29.8992 | 29.744 | 29.5942 | 29.4489 | 29.3082 | 29.2165 | 29.1678 | 29.1203 | 29.0734 | 28.7341 | 28.4466 | 28.1393 | 26.7305 | 26.4636 | 26.2689 | 26.0859 | 25.9819 | 25.8945 | 25.8099 | 25.7547 | 25.7254 | 25.6967 | 25.6684 | 25.4639 | 25.2904 | 21.772 | 28.1139 | 27.899 | 27.7111 | 27.5318 | 27.3581 | 27.1856 | 27.0149 | 26.8988 | 26.828 | 26.7606 | 26.6941 | 26.2127 | 25.8336 | 25.5703
|  | HUME STREET | LW |  |  |  | 30.4891 | 30.4511 | 30.4184 | 30.3839 | 30.3474 | 30.309 | 30.2689 | 30.2185 | 30.1669 | 30.1146 | 30.0618 | 29.6778 | 29.315 | 28.8797 | 26.956 | 26.7834 | 26.6878 | 26.5983 | 26.51 | 26.4211 | 26.3864 | 26.356 | 26.3249 | 26.2934 | 26.2615 | 26.0299 | 25.811 | 21.9613 | 28.3891 | 28.3005 | 28.2428 | 28.1858 | 28.1279 | 28.0682 | 28.0073 | 27.934 | 27.8595 | 27.7852 | 27.7105 | 27.146 | 26.7172 | 26.3365
|  | HUME STREET | ST |  |  |  | 30.5303 | 30.5139 | 30.5026 | 30.4916 | 30.4766 | 30.4613 | 30.4456 | 30.4302 | 30.4103 | 30.3913 | 30.3728 | 30.2288 | 30.1287 | 30.0116 | 27.0165 | 26.9348 | 26.9021 | 26.8696 | 26.8149 | 26.7537 | 26.6867 | 26.6262 | 26.5636 | 26.5065 | 26.4509 | 26.3619 | 26.3013 | 26.2306 | 28.4408 | 28.4 | 28.3803 | 28.3607 | 28.3304 | 28.2976 | 28.2626 | 28.23 | 28.1933 | 28.1592 | 28.126 | 27.9057 | 27.7329 | 27.5416
|  | HUME STREET | FS |  |  |  | 30.5228 | 30.5104 | 30.4962 | 30.4822 | 30.4676 | 30.4531 | 30.4385 | 30.4241 | 30.4099 | 30.3959 | 30.3821 | 30.3028 | 30.2179 | 30.1352 | 27.0234 | 26.9811 | 26.9601 | 26.9402 | 26.9114 | 26.8829 | 26.8518 | 26.821 | 26.7906 | 26.7605 | 26.7315 | 26.5871 | 26.4431 | 26.3064 | 28.4377 | 28.4137 | 28.3958 | 28.3785 | 28.3575 | 28.3368 | 28.3151 | 28.2936 | 28.2725 | 28.2515 | 28.2312 | 28.1218 | 28.0084 | 27.8982
| KEITH | HUNTLY | MINIMUM HEADROOM | NJ 52762 39217 | NO | YES | 18.2442 | 18.1722 | 18.1049 | 18.04 | 17.9776 | 17.9175 | 17.8598 | 17.8272 | 17.811 | 17.795 | 17.7792 | 14.4958 | 13.1991 | 13.1161 | 16.8309 | 16.7374 | 16.6587 | 16.5863 | 16.5146 | 16.4435 | 16.3744 | 16.318 | 16.2732 | 16.2272 | 16.1817 | 15.9519 | 12.4493 | 11.9275 | 15.715 | 15.6323 | 15.5513 | 15.4721 | 15.4002 | 15.3462 | 15.2942 | 15.2649 | 15.2503 | 13.7536 | 13.6888 | 13.2063 | 11.3324 | 10.8484
|  | HUNTLY | CT |  |  |  | 18.2442 | 18.1722 | 18.1049 | 18.04 | 17.9776 | 17.9175 | 17.8598 | 17.8272 | 17.811 | 17.795 | 17.7792 | 14.4958 | 13.1991 | 13.1161 | 16.8309 | 16.7374 | 16.6587 | 16.5863 | 16.5146 | 16.4435 | 16.3744 | 16.318 | 16.2732 | 16.2272 | 16.1817 | 15.9519 | 12.4493 | 11.9275 | 15.715 | 15.6323 | 15.5513 | 15.4721 | 15.4002 | 15.3462 | 15.2942 | 15.2649 | 15.2503 | 13.7536 | 13.6888 | 13.2063 | 11.3324 | 10.8484
|  | HUNTLY | LW |  |  |  | 18.3717 | 18.3609 | 18.3487 | 18.3353 | 18.3208 | 18.3053 | 18.2889 | 18.2706 | 18.2517 | 18.2325 | 18.2129 | 18.1096 | 13.5544 | 13.431 | 16.9357 | 16.9001 | 16.8558 | 16.8085 | 16.762 | 16.725 | 16.6879 | 16.6477 | 16.6088 | 16.5682 | 16.5279 | 16.1521 | 12.6675 | 12.0053 | 15.8389 | 15.8184 | 15.7938 | 15.7674 | 15.7393 | 15.7096 | 15.6806 | 15.6641 | 15.6471 | 15.6297 | 15.6122 | 13.6675 | 11.658 | 11.0227
|  | HUNTLY | ST |  |  |  | 18.3901 | 18.3858 | 18.3817 | 18.3776 | 18.3726 | 18.3678 | 18.3631 | 18.3587 | 18.3523 | 18.346 | 18.3399 | 18.3065 | 14.4392 | 14.4068 | 16.9582 | 16.9459 | 16.9285 | 16.9076 | 16.8563 | 16.8045 | 16.7628 | 16.7255 | 16.6883 | 16.6505 | 16.6134 | 16.4298 | 15.9461 | 15.8797 | 15.8595 | 15.8521 | 15.8428 | 15.8323 | 15.81 | 15.7875 | 15.7655 | 15.7434 | 15.7376 | 15.732 | 15.7265 | 15.6964 | 13.2335 | 12.992
|  | HUNTLY | FS |  |  |  | 18.3858 | 18.3815 | 18.3752 | 18.3689 | 18.3627 | 18.3566 | 18.3506 | 18.3446 | 18.3387 | 18.333 | 18.3273 | 18.2931 | 18.2575 | 18.223 | 16.9597 | 16.955 | 16.9458 | 16.9356 | 16.9147 | 16.8937 | 16.8689 | 16.8442 | 16.8203 | 16.7962 | 16.7726 | 16.687 | 16.6043 | 16.5257 | 15.8572 | 15.8526 | 15.8449 | 15.837 | 15.8251 | 15.8132 | 15.8 | 15.7868 | 15.774 | 15.7612 | 15.7486 | 15.6844 | 15.6523 | 15.6212
| BRIDGE OF DUN | INCHBARE | MINIMUM HEADROOM | NO 60684 65379 | YES | YES | 3.0792 | 2.9822 | 2.4668 | 2.3832 | 2.3028 | 2.2072 | 2.1123 | 2.0521 | 2.0171 | 1.9825 | 1.9483 | 1.797 | 1.6347 | 1.4635 | 3.0521 | 3.0005 | 2.9503 | 2.9018 | 2.855 | 2.4547 | 2.3758 | 2.3241 | 2.2926 | 2.2613 | 2.2305 | 2.0985 | 1.9576 | 1.8099 | 2.8857 | 2.7946 | 2.4875 | 2.387 | 2.2833 | 2.1833 | 2.0872 | 2.0255 | 1.9889 | 1.9526 | 1.9168 | 1.7604 | 1.5929 | 1.4167
|  | INCHBARE | CT |  |  |  | 3.0792 | 2.9822 | 2.4668 | 2.3832 | 2.3028 | 2.2072 | 2.1123 | 2.0521 | 2.0171 | 1.9825 | 1.9483 | 1.797 | 1.6347 | 1.4635 | 3.0521 | 3.0005 | 2.9503 | 2.9018 | 2.855 | 2.4547 | 2.3758 | 2.3241 | 2.2926 | 2.2613 | 2.2305 | 2.0985 | 1.9576 | 1.8099 | 2.8857 | 2.7946 | 2.4875 | 2.387 | 2.2833 | 2.1833 | 2.0872 | 2.0255 | 1.9889 | 1.9526 | 1.9168 | 1.7604 | 1.5929 | 1.4167
|  | INCHBARE | LW |  |  |  | 3.2497 | 3.2347 | 3.2178 | 3.1992 | 3.1792 | 3.1578 | 3.1353 | 3.1092 | 3.0823 | 3.0549 | 3.0272 | 2.423 | 2.1939 | 1.9424 | 3.1634 | 3.1515 | 3.1378 | 3.1231 | 3.1073 | 3.0906 | 3.0732 | 3.0531 | 3.037 | 3.021 | 3.0048 | 2.9157 | 2.4041 | 2.1872 | 3.0434 | 3.0285 | 3.0116 | 2.9933 | 2.9735 | 2.9526 | 2.9307 | 2.9054 | 2.8793 | 2.8528 | 2.826 | 2.388 | 2.1515 | 1.8927
|  | INCHBARE | ST |  |  |  | 3.2745 | 3.2686 | 3.2628 | 3.257 | 3.25 | 3.2431 | 3.2365 | 3.23 | 3.2208 | 3.2117 | 3.203 | 3.1547 | 3.1095 | 3.0584 | 3.1814 | 3.1768 | 3.172 | 3.1672 | 3.1612 | 3.1554 | 3.1497 | 3.1441 | 3.1366 | 3.1292 | 3.122 | 3.0831 | 3.0465 | 3.0117 | 3.0667 | 3.0609 | 3.055 | 3.0491 | 3.0419 | 3.0352 | 3.0288 | 3.0226 | 3.0136 | 3.0047 | 2.9962 | 2.9487 | 2.9044 | 2.8554
|  | INCHBARE | FS |  |  |  | 3.2689 | 3.2631 | 3.2546 | 3.2461 | 3.2377 | 3.2294 | 3.2212 | 3.213 | 3.205 | 3.1972 | 3.1894 | 3.1431 | 3.0943 | 3.047 | 3.1777 | 3.1736 | 3.1674 | 3.1612 | 3.1549 | 3.1487 | 3.1425 | 3.1363 | 3.1303 | 3.1243 | 3.1185 | 3.0839 | 3.0521 | 3.0262 | 3.0616 | 3.0563 | 3.0483 | 3.0403 | 3.0323 | 3.0243 | 3.0164 | 3.0086 | 3.001 | 2.9934 | 2.9859 | 2.9417 | 2.8954 | 2.8505
| DUNOON | INNELLAN | MINIMUM HEADROOM | NS 15129 70875 | YES | YES | 3.0994 | 2.3827 | 2.225 | 2.0729 | 1.9265 | 1.7702 | 1.5951 | 1.4777 | 1.4085 | 1.34 | 1.2723 | 0.9105 | 0.51689 | 0.10512 | 2.9022 | 2.8034 | 2.344 | 2.1803 | 2.0221 | 1.8698 | 1.723 | 1.6215 | 1.5584 | 1.4959 | 1.434 | 1.0992 | 0.73851 | 0.36418 | 2.4146 | 2.2134 | 2.0089 | 1.8112 | 1.6203 | 1.4365 | 1.2597 | 1.1408 | 1.0706 | 1.0011 | 0.93235 | 0.56481 | 0.16515 | -0.25862
|  | INNELLAN | CT |  |  |  | 3.0994 | 2.3827 | 2.225 | 2.0729 | 1.9265 | 1.7702 | 1.5951 | 1.4777 | 1.4085 | 1.34 | 1.2723 | 0.9105 | 0.51689 | 0.10512 | 2.9022 | 2.8034 | 2.344 | 2.1803 | 2.0221 | 1.8698 | 1.723 | 1.6215 | 1.5584 | 1.4959 | 1.434 | 1.0992 | 0.73851 | 0.36418 | 2.4146 | 2.2134 | 2.0089 | 1.8112 | 1.6203 | 1.4365 | 1.2597 | 1.1408 | 1.0706 | 1.0011 | 0.93235 | 0.56481 | 0.16515 | -0.25862
|  | INNELLAN | LW |  |  |  | 3.3924 | 3.3675 | 3.3396 | 3.3088 | 3.2754 | 3.2398 | 3.2022 | 3.1558 | 3.1081 | 2.4403 | 2.3576 | 1.9154 | 1.4068 | 0.83293 | 3.1347 | 3.0969 | 3.0526 | 3.0063 | 2.9751 | 2.9563 | 2.9365 | 2.4983 | 2.4226 | 2.3463 | 2.2696 | 1.8591 | 1.3952 | 0.88019 | 3.0364 | 3.0086 | 2.9769 | 2.9424 | 2.4925 | 2.4247 | 2.3552 | 2.2738 | 2.1912 | 2.1076 | 2.0235 | 1.573 | 1.0377 | 0.4376
|  | INNELLAN | ST |  |  |  | 3.4348 | 3.425 | 3.4153 | 3.406 | 3.3946 | 3.3835 | 3.3727 | 3.3618 | 3.3459 | 3.3305 | 3.3155 | 3.2313 | 3.1501 | 2.3813 | 3.1758 | 3.1625 | 3.1465 | 3.129 | 3.1099 | 3.0913 | 3.0732 | 3.0543 | 3.0314 | 3.0091 | 2.9962 | 2.9519 | 2.4377 | 2.2808 | 3.0806 | 3.0698 | 3.0588 | 3.0478 | 3.0347 | 3.022 | 3.0097 | 2.9971 | 2.9795 | 2.9623 | 2.9456 | 2.3728 | 2.2184 | 2.0479
|  | INNELLAN | FS |  |  |  | 3.425 | 3.4151 | 3.4004 | 3.386 | 3.3718 | 3.3577 | 3.3438 | 3.3302 | 3.3167 | 3.3034 | 3.2903 | 3.2119 | 3.1279 | 2.4892 | 3.1713 | 3.1629 | 3.1486 | 3.1341 | 3.1192 | 3.1046 | 3.0892 | 3.0741 | 3.0592 | 3.0445 | 3.03 | 2.948 | 2.8974 | 2.8542 | 3.0711 | 3.061 | 3.0457 | 3.0306 | 3.0157 | 3.0009 | 2.9862 | 2.9717 | 2.9574 | 2.9433 | 2.9294 | 2.4809 | 2.3649 | 2.2529
| KEITH | INSCH | MINIMUM HEADROOM | NJ 63100 28651 | NO | YES | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.1615 | 13.9905 | 13.8192 | 13.6079 | 12.0765 | 11.0994 | 10.3938 | 15.045 | 14.9453 | 14.858 | 14.846 | 14.846 | 13.7423 | 13.5491 | 13.3404 | 13.1344 | 12.9279 | 12.6918 | 11.2127 | 10.1506 | 9.3001 | 13.0924 | 12.9521 | 12.779 | 12.6075 | 12.4378 | 12.2695 | 12.104 | 11.9252 | 11.7487 | 11.5718 | 11.3531 | 9.6994 | 8.5978 | 7.7695
|  | INSCH | CT |  |  |  | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.1623 | 13.991 | 12.6825 | 11.9305 | 11.4457 | 15.0469 | 14.9656 | 14.8774 | 14.8516 | 14.846 | 14.846 | 14.846 | 13.6566 | 13.4993 | 13.3414 | 13.1535 | 11.9431 | 11.1521 | 10.5679 | 13.0951 | 12.9806 | 12.8486 | 12.7178 | 12.5881 | 12.4594 | 12.3329 | 12.1961 | 12.0614 | 11.9261 | 11.7502 | 10.4109 | 9.5734 | 9.0043
|  | INSCH | LW |  |  |  | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.1615 | 13.9905 | 13.8192 | 13.6079 | 12.0765 | 11.0994 | 10.3938 | 15.045 | 14.9453 | 14.858 | 14.846 | 14.846 | 13.7423 | 13.5491 | 13.3404 | 13.1344 | 12.9279 | 12.6918 | 11.2127 | 10.1506 | 9.3001 | 13.0924 | 12.9521 | 12.779 | 12.6075 | 12.4378 | 12.2695 | 12.104 | 11.9252 | 11.7487 | 11.5718 | 11.3531 | 9.6994 | 8.5978 | 7.7695
|  | INSCH | ST |  |  |  | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2156 | 13.8625 | 13.4719 | 13.1556 | 15.0762 | 15.0448 | 14.9958 | 14.9369 | 14.8882 | 14.8606 | 14.8536 | 14.8461 | 14.846 | 14.846 | 14.8351 | 13.2432 | 12.7595 | 12.3784 | 13.1362 | 13.0921 | 13.0232 | 12.9402 | 12.8717 | 12.8037 | 12.7371 | 12.6652 | 12.5951 | 12.5252 | 12.4356 | 11.6879 | 11.2273 | 10.9008
|  | INSCH | FS |  |  |  | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 14.2334 | 15.0938 | 15.0912 | 15.0772 | 15.0604 | 15.0445 | 15.0287 | 15.0086 | 14.9888 | 14.9695 | 14.9503 | 14.9314 | 14.8607 | 14.8481 | 14.846 | 13.161 | 13.1574 | 13.1376 | 13.1141 | 13.0917 | 13.0694 | 13.0411 | 13.0133 | 12.9861 | 12.959 | 12.9325 | 12.805 | 12.6848 | 12.5715
| BURGHMUIR | INVERALMOND | MINIMUM HEADROOM | NO 08721 25807 | NO | YES | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  | INVERALMOND | CT |  |  |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  | INVERALMOND | LW |  |  |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  | INVERALMOND | ST |  |  |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  | INVERALMOND | FS |  |  |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
| CLACHAN | INVERARAY | MINIMUM HEADROOM | NN 09172 09746 | YES | YES | 2.6853 | 2.6176 | 2.459 | 2.3842 | 2.3122 | 2.2429 | 2.1764 | 2.1373 | 2.1172 | 2.0973 | 2.0777 | 1.9817 | 1.8786 | 1.7691 | 2.7779 | 2.7321 | 2.485 | 2.4246 | 2.3663 | 2.3103 | 2.2565 | 2.2247 | 2.2081 | 2.1917 | 2.1755 | 2.0964 | 2.0116 | 1.9217 | 2.7416 | 2.466 | 2.4049 | 2.3459 | 2.2892 | 2.2346 | 2.1822 | 2.1517 | 2.1361 | 2.1207 | 2.1055 | 2.0312 | 1.9365 | 1.826
|  | INVERARAY | CT |  |  |  | 2.6853 | 2.6176 | 2.459 | 2.3842 | 2.3122 | 2.2429 | 2.1764 | 2.1373 | 2.1172 | 2.0973 | 2.0777 | 1.9817 | 1.8786 | 1.7691 | 2.7779 | 2.7321 | 2.485 | 2.4246 | 2.3663 | 2.3103 | 2.2565 | 2.2247 | 2.2081 | 2.1917 | 2.1755 | 2.0964 | 2.0116 | 1.9217 | 2.7416 | 2.466 | 2.4049 | 2.3459 | 2.2892 | 2.2346 | 2.1822 | 2.1517 | 2.1361 | 2.1207 | 2.1055 | 2.0312 | 1.9365 | 1.826
|  | INVERARAY | LW |  |  |  | 2.8103 | 2.7997 | 2.7878 | 2.7746 | 2.7604 | 2.7452 | 2.7292 | 2.7108 | 2.6919 | 2.6725 | 2.6539 | 2.4357 | 2.2886 | 2.127 | 2.8817 | 2.8712 | 2.8592 | 2.8462 | 2.8323 | 2.8176 | 2.8022 | 2.7847 | 2.7706 | 2.7568 | 2.7429 | 2.4583 | 2.3372 | 2.2046 | 2.8709 | 2.8583 | 2.844 | 2.8284 | 2.8118 | 2.7942 | 2.7758 | 2.7563 | 2.7384 | 2.7202 | 2.7017 | 2.4063 | 2.2956 | 2.1732
|  | INVERARAY | ST |  |  |  | 2.8284 | 2.8242 | 2.8201 | 2.8161 | 2.8112 | 2.8065 | 2.8019 | 2.7975 | 2.7911 | 2.7849 | 2.7788 | 2.7453 | 2.7143 | 2.6794 | 2.8978 | 2.8938 | 2.8896 | 2.8853 | 2.8804 | 2.8756 | 2.8709 | 2.8664 | 2.8601 | 2.8539 | 2.8479 | 2.8155 | 2.7853 | 2.7589 | 2.8902 | 2.8853 | 2.8803 | 2.8752 | 2.8693 | 2.8636 | 2.858 | 2.8525 | 2.845 | 2.8376 | 2.8305 | 2.7917 | 2.7593 | 2.7263
|  | INVERARAY | FS |  |  |  | 2.8242 | 2.82 | 2.8137 | 2.8076 | 2.8015 | 2.7955 | 2.7896 | 2.7838 | 2.778 | 2.7724 | 2.7668 | 2.7333 | 2.6982 | 2.6645 | 2.8944 | 2.8907 | 2.8851 | 2.8796 | 2.8741 | 2.8687 | 2.8633 | 2.8579 | 2.8526 | 2.8474 | 2.8423 | 2.812 | 2.782 | 2.7593 | 2.8861 | 2.8817 | 2.875 | 2.8684 | 2.8618 | 2.8553 | 2.8488 | 2.8424 | 2.8361 | 2.8299 | 2.8237 | 2.7874 | 2.7495 | 2.7133
| LUNANHEAD | INVERARITY | MINIMUM HEADROOM | NO 44549 44200 | YES | YES | 0.98051 | 0.90511 | 0.82743 | 0.75251 | 0.68034 | 0.61094 | 0.54429 | 0.50146 | 0.47948 | 0.45773 | 0.43628 | -0.29231 | -0.41962 | -0.55627 | 1.2234 | 0.94153 | 0.87439 | 0.80959 | 0.74714 | 0.68703 | 0.62927 | 0.59102 | 0.57006 | 0.54931 | 0.52883 | -0.09122 | -0.21333 | -0.34304 | 0.89275 | 0.81223 | 0.72902 | 0.64873 | 0.57137 | 0.49693 | 0.4254 | 0.37842 | 0.35311 | 0.32805 | 0.30334 | -0.46832 | -0.61555 | -0.77237
|  | INVERARITY | CT |  |  |  | 0.98051 | 0.90511 | 0.82743 | 0.75251 | 0.68034 | 0.61094 | 0.54429 | 0.50146 | 0.47948 | 0.45773 | 0.43628 | -0.29231 | -0.41962 | -0.55627 | 1.2234 | 0.94153 | 0.87439 | 0.80959 | 0.74714 | 0.68703 | 0.62927 | 0.59102 | 0.57006 | 0.54931 | 0.52883 | -0.09122 | -0.21333 | -0.34304 | 0.89275 | 0.81223 | 0.72902 | 0.64873 | 0.57137 | 0.49693 | 0.4254 | 0.37842 | 0.35311 | 0.32805 | 0.30334 | -0.46832 | -0.61555 | -0.77237
|  | INVERARITY | LW |  |  |  | 1.4318 | 1.4174 | 1.4008 | 1.383 | 1.3642 | 1.3444 | 1.3239 | 0.99178 | 0.96774 | 0.94324 | 0.91847 | 0.16349 | -0.0052352 | -0.20836 | 1.2873 | 1.2819 | 1.2758 | 1.2691 | 1.2618 | 1.254 | 1.2458 | 0.98919 | 0.96534 | 0.94115 | 0.91676 | 0.25696 | 0.08248 | -0.12002 | 1.3745 | 1.3639 | 0.99386 | 0.97396 | 0.95299 | 0.93109 | 0.90838 | 0.8805 | 0.85199 | 0.82303 | 0.7938 | -0.021364 | -0.2279 | -0.46973
|  | INVERARITY | ST |  |  |  | 1.4518 | 1.4464 | 1.4405 | 1.4344 | 1.4259 | 1.4177 | 1.4097 | 1.4012 | 1.3905 | 1.3801 | 1.3699 | 0.70853 | 0.66271 | 0.60903 | 1.2965 | 1.2944 | 1.2923 | 1.2902 | 1.2877 | 1.2853 | 1.283 | 1.2806 | 1.277 | 1.2736 | 1.2702 | 0.73952 | 0.68631 | 0.62662 | 1.3926 | 1.3884 | 1.3843 | 1.3803 | 1.3754 | 1.3707 | 1.3661 | 0.9914 | 0.97913 | 0.96716 | 0.95548 | 0.57274 | 0.5114 | 0.44194
|  | INVERARITY | FS |  |  |  | 1.448 | 1.4435 | 1.4366 | 1.4296 | 1.4222 | 1.4148 | 1.4073 | 1.3998 | 1.3925 | 1.3852 | 1.3781 | 1.337 | 0.98298 | 0.94329 | 1.2944 | 1.2922 | 1.289 | 1.2859 | 1.2828 | 1.2797 | 1.2767 | 1.2737 | 1.2708 | 1.2679 | 1.265 | 1.2479 | 0.98868 | 0.95059 | 1.3884 | 1.3842 | 1.378 | 1.3718 | 1.3657 | 1.3597 | 1.3538 | 0.99386 | 0.98574 | 0.97774 | 0.96987 | 0.92486 | 0.87747 | 0.83154
| INVERNESS | INVERARNIE | MINIMUM HEADROOM | NH 68830 34971 | YES | YES | 2.395 | 2.2882 | 2.1868 | 2.0891 | 1.9931 | 1.8958 | 1.8024 | 1.7601 | 1.739 | 1.7182 | 1.6977 | 1.5978 | 1.5105 | 1.3948 | 2.3947 | 2.2933 | 2.1966 | 2.1034 | 2.0136 | 1.9272 | 1.8442 | 1.8053 | 1.7849 | 1.7647 | 1.7447 | 1.5934 | 1.4519 | 1.3108 | 2.4322 | 2.3092 | 2.1875 | 2.0701 | 1.957 | 1.8483 | 1.7439 | 1.6955 | 1.6707 | 1.646 | 1.6218 | 1.4607 | 1.3006 | 1.139
|  | INVERARNIE | CT |  |  |  | 2.395 | 2.2882 | 2.1868 | 2.0891 | 1.9931 | 1.8958 | 1.8024 | 1.7601 | 1.739 | 1.7182 | 1.6977 | 1.5978 | 1.5105 | 1.3948 | 2.3947 | 2.2933 | 2.1966 | 2.1034 | 2.0136 | 1.9272 | 1.8442 | 1.8053 | 1.7849 | 1.7647 | 1.7447 | 1.5934 | 1.4519 | 1.3108 | 2.4322 | 2.3092 | 2.1875 | 2.0701 | 1.957 | 1.8483 | 1.7439 | 1.6955 | 1.6707 | 1.646 | 1.6218 | 1.4607 | 1.3006 | 1.139
|  | INVERARNIE | LW |  |  |  | 3.1073 | 3.0877 | 3.0654 | 3.0413 | 3.0155 | 2.4842 | 2.4584 | 2.4349 | 2.4108 | 2.3862 | 2.3613 | 2.1599 | 1.928 | 1.6935 | 2.8329 | 2.8148 | 2.4812 | 2.4368 | 2.3913 | 2.3449 | 2.2977 | 2.2507 | 2.2033 | 2.1557 | 2.1079 | 1.885 | 1.6658 | 1.4448 | 2.9367 | 2.9181 | 2.8969 | 2.8747 | 2.458 | 2.4056 | 2.3522 | 2.2995 | 2.2462 | 2.1925 | 2.1386 | 1.8846 | 1.6354 | 1.3836
|  | INVERARNIE | ST |  |  |  | 3.1359 | 3.1284 | 3.1205 | 3.1124 | 3.1034 | 3.0946 | 3.0861 | 3.0777 | 3.0664 | 3.0553 | 3.0445 | 2.4919 | 2.4521 | 2.4157 | 2.8556 | 2.849 | 2.8414 | 2.8334 | 2.8251 | 2.817 | 2.4965 | 2.4799 | 2.4605 | 2.4416 | 2.4232 | 2.3357 | 2.253 | 2.1736 | 2.9644 | 2.9573 | 2.9498 | 2.9422 | 2.9337 | 2.9253 | 2.9172 | 2.9093 | 2.8988 | 2.8888 | 2.4964 | 2.3979 | 2.3054 | 2.217
|  | INVERARNIE | FS |  |  |  | 3.1301 | 3.1236 | 3.1137 | 3.1037 | 3.094 | 3.0844 | 3.0747 | 3.0652 | 3.0558 | 3.0466 | 3.0375 | 2.4676 | 2.4234 | 2.3827 | 2.8518 | 2.8468 | 2.8388 | 2.8307 | 2.8228 | 2.815 | 2.8071 | 2.7992 | 2.7915 | 2.4885 | 2.4768 | 2.4113 | 2.3529 | 2.2987 | 2.9587 | 2.9524 | 2.9428 | 2.9332 | 2.9237 | 2.9144 | 2.9051 | 2.896 | 2.8869 | 2.878 | 2.8692 | 2.4706 | 2.4017 | 2.3379
| FIDDES | INVERBERVIE | MINIMUM HEADROOM | NO 82850 72935 | NO | YES | 6.7293 | 6.7087 | 6.683 | 6.6566 | 6.6298 | 6.6021 | 6.575 | 6.5458 | 6.518 | 6.489 | 6.4605 | 4.6661 | 2.4909 | 2.3308 | 5.5631 | 5.537 | 5.5044 | 5.471 | 5.4369 | 5.4018 | 5.3674 | 5.3304 | 5.2951 | 5.2584 | 5.2222 | 3.7538 | 2.0039 | 1.8131 | 5.7276 | 5.7275 | 5.7057 | 5.6833 | 5.6606 | 5.6371 | 5.6141 | 5.5894 | 5.5658 | 5.5413 | 5.5171 | 3.7693 | 1.663 | 1.5355
|  | INVERBERVIE | CT |  |  |  | 6.7307 | 6.7153 | 6.6971 | 6.6783 | 6.6589 | 6.6388 | 6.6191 | 6.5979 | 6.5778 | 6.5568 | 6.5361 | 4.7874 | 2.6688 | 2.5563 | 5.5649 | 5.5454 | 5.5223 | 5.4984 | 5.4739 | 5.4484 | 5.4233 | 5.3964 | 5.371 | 5.3443 | 5.3181 | 3.9076 | 2.2158 | 2.0818 | 5.7276 | 5.7276 | 5.7176 | 5.7017 | 5.6853 | 5.6682 | 5.6515 | 5.6335 | 5.6165 | 5.5987 | 5.5812 | 3.872 | 1.8045 | 1.715
|  | INVERBERVIE | LW |  |  |  | 6.7293 | 6.7087 | 6.683 | 6.6566 | 6.6298 | 6.6021 | 6.575 | 6.5458 | 6.518 | 6.489 | 6.4605 | 4.6661 | 2.4909 | 2.3308 | 5.5631 | 5.537 | 5.5044 | 5.471 | 5.4369 | 5.4018 | 5.3674 | 5.3304 | 5.2951 | 5.2584 | 5.2222 | 3.7538 | 2.0039 | 1.8131 | 5.7276 | 5.7275 | 5.7057 | 5.6833 | 5.6606 | 5.6371 | 5.6141 | 5.5894 | 5.5658 | 5.5413 | 5.5171 | 3.7693 | 1.663 | 1.5355
|  | INVERBERVIE | ST |  |  |  | 6.736 | 6.7295 | 6.7193 | 6.7068 | 6.6927 | 6.6782 | 6.6639 | 6.6486 | 6.634 | 6.6188 | 6.6039 | 5.712 | 4.6411 | 4.5744 | 5.5716 | 5.5633 | 5.5504 | 5.5346 | 5.5167 | 5.4983 | 5.4802 | 5.4607 | 5.4423 | 5.423 | 5.4041 | 4.6765 | 3.8118 | 3.7272 | 5.7276 | 5.7276 | 5.7276 | 5.7258 | 5.7139 | 5.7016 | 5.6895 | 5.6765 | 5.6642 | 5.6513 | 5.6387 | 4.7692 | 3.7228 | 3.6663
|  | INVERBERVIE | FS |  |  |  | 6.7396 | 6.7386 | 6.7354 | 6.7316 | 6.7266 | 6.7216 | 6.7155 | 6.7094 | 6.7036 | 6.6976 | 6.6917 | 6.663 | 6.6355 | 6.6095 | 5.5761 | 5.5749 | 5.5709 | 5.566 | 5.5597 | 5.5533 | 5.5456 | 5.5379 | 5.5305 | 5.5229 | 5.5155 | 5.4791 | 5.4442 | 5.4112 | 5.7276 | 5.7276 | 5.7276 | 5.7276 | 5.7276 | 5.7276 | 5.7276 | 5.7276 | 5.7231 | 5.7181 | 5.7131 | 5.6887 | 5.6654 | 5.6434
| GRUDIE BRIDGE | INVERBROOM | MINIMUM HEADROOM | NH 17885 84667 | YES | YES | 0.30703 | 0.30703 | 0.42203 | 0.42203 | 0.42203 | 0.42203 | 0.42203 | 0.42203 | 0.42203 | 0.42203 | 0.42203 | 0.42203 | 0.42203 | 0.42203 | 0.25864 | 0.25847 | 0.37326 | 0.37306 | 0.37254 | 0.37164 | 0.37076 | 0.36983 | 0.36913 | 0.36843 | 0.36788 | 0.36727 | 0.36727 | 0.29862 | 0.26611 | 0.26603 | 0.38093 | 0.38083 | 0.38058 | 0.38014 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.30972
|  | INVERBROOM | CT |  |  |  | 0.30703 | 0.30703 | 0.42203 | 0.42203 | 0.42203 | 0.42203 | 0.42203 | 0.42203 | 0.42203 | 0.42203 | 0.42203 | 0.42203 | 0.42203 | 0.42203 | 0.25865 | 0.25852 | 0.37337 | 0.37323 | 0.37309 | 0.37296 | 0.37282 | 0.37267 | 0.37253 | 0.37239 | 0.37225 | 0.36757 | 0.36727 | 0.36727 | 0.26612 | 0.26606 | 0.38099 | 0.38092 | 0.38085 | 0.38078 | 0.38072 | 0.38065 | 0.38058 | 0.38051 | 0.38044 | 0.38 | 0.38 | 0.38
|  | INVERBROOM | LW |  |  |  | 0.30703 | 0.30703 | 0.42203 | 0.42203 | 0.42203 | 0.42203 | 0.42203 | 0.42203 | 0.42203 | 0.42203 | 0.42203 | 0.42203 | 0.42203 | 0.42203 | 0.25864 | 0.25847 | 0.37326 | 0.37306 | 0.37286 | 0.37267 | 0.37248 | 0.37227 | 0.37207 | 0.37186 | 0.37167 | 0.36727 | 0.36727 | 0.29862 | 0.26611 | 0.26603 | 0.38093 | 0.38083 | 0.38074 | 0.38064 | 0.38055 | 0.38045 | 0.38035 | 0.38025 | 0.38016 | 0.38 | 0.38 | 0.30972
|  | INVERBROOM | ST |  |  |  | 0.30703 | 0.30703 | 0.42203 | 0.42203 | 0.42203 | 0.42203 | 0.42203 | 0.42203 | 0.42203 | 0.42203 | 0.42203 | 0.42203 | 0.42203 | 0.42203 | 0.25869 | 0.25864 | 0.37356 | 0.37347 | 0.37254 | 0.37164 | 0.37076 | 0.36983 | 0.36913 | 0.36843 | 0.36788 | 0.36727 | 0.36727 | 0.36727 | 0.26614 | 0.26612 | 0.38108 | 0.38103 | 0.38058 | 0.38014 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38
|  | INVERBROOM | FS |  |  |  | 0.30703 | 0.30703 | 0.42203 | 0.42203 | 0.42203 | 0.42203 | 0.42203 | 0.42203 | 0.42203 | 0.42203 | 0.42203 | 0.42203 | 0.42203 | 0.42203 | 0.25872 | 0.25872 | 0.37369 | 0.37367 | 0.37337 | 0.37308 | 0.3727 | 0.37233 | 0.37196 | 0.3716 | 0.37125 | 0.36967 | 0.36848 | 0.36779 | 0.26616 | 0.26615 | 0.38114 | 0.38113 | 0.38098 | 0.38084 | 0.38066 | 0.38048 | 0.3803 | 0.38013 | 0.38 | 0.38 | 0.38 | 0.38
| FORT AUGUSTUS | INVERGARRY | MINIMUM HEADROOM | NH 29862 01000 | YES | YES | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.1366 | 1.1356 | 1.1343 | 1.1331 | 1.1319 | 1.1307 | 1.1296 | 1.1283 | 1.1274 | 1.1264 | 1.1252 | 1.122 | 1.122 | 0.97824 | 1.1542 | 1.1537 | 1.1531 | 1.1525 | 1.1519 | 1.1517 | 1.1517 | 1.1517 | 1.1517 | 1.1517 | 1.1517 | 1.1517 | 1.1517 | 1.1517
|  | INVERGARRY | CT |  |  |  | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.1366 | 1.1359 | 1.135 | 1.1341 | 1.1333 | 1.1325 | 1.1317 | 1.1308 | 1.1299 | 1.1291 | 1.1282 | 1.1223 | 1.122 | 1.122 | 1.1542 | 1.1538 | 1.1534 | 1.153 | 1.1526 | 1.1522 | 1.1518 | 1.1517 | 1.1517 | 1.1517 | 1.1517 | 1.1517 | 1.1517 | 1.1517
|  | INVERGARRY | LW |  |  |  | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.1366 | 1.1356 | 1.1343 | 1.1331 | 1.1319 | 1.1307 | 1.1296 | 1.1283 | 1.1274 | 1.1264 | 1.1255 | 1.122 | 1.122 | 0.97824 | 1.1542 | 1.1537 | 1.1531 | 1.1525 | 1.1519 | 1.1517 | 1.1517 | 1.1517 | 1.1517 | 1.1517 | 1.1517 | 1.1517 | 1.1517 | 1.1517
|  | INVERGARRY | ST |  |  |  | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.1369 | 1.1366 | 1.1361 | 1.1355 | 1.1339 | 1.1323 | 1.1308 | 1.1291 | 1.1276 | 1.1264 | 1.1252 | 1.1225 | 1.122 | 1.122 | 1.1543 | 1.1542 | 1.154 | 1.1537 | 1.1529 | 1.1521 | 1.1517 | 1.1517 | 1.1517 | 1.1517 | 1.1517 | 1.1517 | 1.1517 | 1.1517
|  | INVERGARRY | FS |  |  |  | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.2499 | 1.1371 | 1.137 | 1.1369 | 1.1368 | 1.1362 | 1.1357 | 1.135 | 1.1343 | 1.1337 | 1.133 | 1.1324 | 1.1294 | 1.1269 | 1.1249 | 1.1544 | 1.1544 | 1.1543 | 1.1543 | 1.154 | 1.1538 | 1.1534 | 1.1531 | 1.1528 | 1.1525 | 1.1522 | 1.1517 | 1.1517 | 1.1517
| ALNESS | INVERGORDON | MINIMUM HEADROOM | NH 70756 69177 | NO | YES | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 14.484 | 14.3407 | 14.191 | 14.0762 | 13.9606 | 13.8458 | 13.761 | 13.3856 | 13.0052 | 12.6333 | 16.6895 | 16.6328 | 16.548 | 16.4781 | 16.4458 | 16.4307 | 16.4194 | 16.4194 | 16.4194 | 16.4194 | 16.4194 | 16.4194 | 13.7625 | 13.3259 | 16.2265 | 16.2265 | 16.2265 | 16.2265 | 13.7333 | 13.565 | 13.3891 | 13.2544 | 13.1186 | 12.9838 | 12.8842 | 12.4433 | 11.9965 | 11.5598
|  | INVERGORDON | CT |  |  |  | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 14.4468 | 14.3125 | 14.1971 | 14.079 | 13.9651 | 13.8835 | 13.5422 | 13.2233 | 12.9127 | 16.6927 | 16.6432 | 16.571 | 16.5076 | 16.4622 | 16.4419 | 16.4278 | 16.4194 | 16.4194 | 16.4194 | 16.4194 | 16.4194 | 16.4194 | 13.6539 | 16.2265 | 16.2265 | 16.2265 | 16.2265 | 16.2265 | 13.6895 | 13.5319 | 13.3963 | 13.2577 | 13.1239 | 13.028 | 12.6272 | 12.2527 | 11.8879
|  | INVERGORDON | LW |  |  |  | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 14.484 | 14.3407 | 14.191 | 14.0762 | 13.9606 | 13.8458 | 13.761 | 13.3856 | 13.0052 | 12.6333 | 16.6895 | 16.6328 | 16.548 | 16.4781 | 16.4458 | 16.4307 | 16.4194 | 16.4194 | 16.4194 | 16.4194 | 16.4194 | 16.4194 | 13.7625 | 13.3259 | 16.2265 | 16.2265 | 16.2265 | 16.2265 | 13.7333 | 13.565 | 13.3891 | 13.2544 | 13.1186 | 12.9838 | 12.8842 | 12.4433 | 11.9965 | 11.5598
|  | INVERGORDON | ST |  |  |  | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 14.5079 | 14.4643 | 14.2804 | 14.1176 | 13.9587 | 16.7182 | 16.7024 | 16.6721 | 16.6361 | 16.6021 | 16.5604 | 16.5238 | 16.4945 | 16.4642 | 16.4483 | 16.4437 | 16.4244 | 16.4194 | 16.4194 | 16.2265 | 16.2265 | 16.2265 | 16.2265 | 16.2265 | 16.2265 | 16.2265 | 16.2265 | 16.2265 | 13.7613 | 13.7101 | 13.4941 | 13.3029 | 13.1163
|  | INVERGORDON | FS |  |  |  | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 17.0555 | 16.7287 | 16.7218 | 16.7076 | 16.6919 | 16.6781 | 16.6614 | 16.6419 | 16.6274 | 16.6127 | 16.5978 | 16.5869 | 16.5451 | 16.5189 | 16.4941 | 16.2265 | 16.2265 | 16.2265 | 16.2265 | 16.2265 | 16.2265 | 16.2265 | 16.2265 | 16.2265 | 16.2265 | 16.2265 | 16.2265 | 16.2265 | 16.2265
| FORT WILLIAM | INVERLOCHY | MINIMUM HEADROOM | NN 11653 74987 | NO | YES | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 17.8552 | 17.8013 | 17.7517 | 17.7101 | 17.6717 | 17.6337 | 17.5961 | 17.5557 | 17.5158 | 17.4764 | 17.4379 | 17.0308 | 16.6076 | 16.4507 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.833 | 12.3182
|  | INVERLOCHY | CT |  |  |  | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 17.8618 | 17.8201 | 17.7866 | 17.7525 | 17.7211 | 17.6904 | 17.661 | 17.6314 | 17.6029 | 17.5753 | 17.5484 | 17.2224 | 16.8805 | 16.5639 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.754
|  | INVERLOCHY | LW |  |  |  | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 17.8552 | 17.8013 | 17.7517 | 17.7101 | 17.6717 | 17.6337 | 17.5961 | 17.5557 | 17.5158 | 17.4764 | 17.4379 | 17.0308 | 16.6076 | 16.4507 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.833 | 12.3182
|  | INVERLOCHY | ST |  |  |  | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 17.8842 | 17.8639 | 17.8455 | 17.8227 | 17.7775 | 17.7329 | 17.6966 | 17.6587 | 17.6221 | 17.5865 | 17.552 | 17.381 | 17.2036 | 17.0279 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506
|  | INVERLOCHY | FS |  |  |  | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 13.8623 | 17.9022 | 17.896 | 17.8896 | 17.8824 | 17.8668 | 17.8515 | 17.8323 | 17.8134 | 17.7949 | 17.7768 | 17.7595 | 17.6892 | 17.6238 | 17.5603 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506 | 12.9506
| PORT ANN | INVERNEIL | MINIMUM HEADROOM | NR 84790 80580 | YES | YES | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.2805 | 6.2587 | 6.2372 | 6.214 | 6.1909 | 6.168 | 6.1452 | 6.0728 | 5.9998 | 5.9278 | 6.5959 | 6.2808 | 6.2515 | 6.2228 | 6.1946 | 6.167 | 6.1398 | 6.1104 | 6.0812 | 6.0521 | 6.0232 | 5.9316 | 5.8391 | 5.748 | 6.6503 | 6.6503 | 6.6503 | 6.2995 | 6.2714 | 6.2438 | 6.2167 | 6.1874 | 6.1582 | 6.1293 | 6.1005 | 6.0092 | 5.917 | 5.8261
|  | INVERNEIL | CT |  |  |  | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.29 | 6.2747 | 6.2582 | 6.2418 | 6.2255 | 6.2092 | 6.1622 | 6.1147 | 6.0679 | 6.5964 | 6.2876 | 6.2668 | 6.2464 | 6.2263 | 6.2066 | 6.1873 | 6.1663 | 6.1455 | 6.1249 | 6.1043 | 6.0448 | 5.9846 | 5.9254 | 6.6503 | 6.6503 | 6.6503 | 6.6503 | 6.6503 | 6.2833 | 6.264 | 6.2432 | 6.2224 | 6.2018 | 6.1814 | 6.122 | 6.062 | 6.0029
|  | INVERNEIL | LW |  |  |  | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.2805 | 6.2587 | 6.2372 | 6.214 | 6.1909 | 6.168 | 6.1452 | 6.0728 | 5.9998 | 5.9278 | 6.5959 | 6.2808 | 6.2515 | 6.2228 | 6.1946 | 6.167 | 6.1398 | 6.1104 | 6.0812 | 6.0521 | 6.0232 | 5.9316 | 5.8391 | 5.748 | 6.6503 | 6.6503 | 6.6503 | 6.2995 | 6.2714 | 6.2438 | 6.2167 | 6.1874 | 6.1582 | 6.1293 | 6.1005 | 6.0092 | 5.917 | 5.8261
|  | INVERNEIL | ST |  |  |  | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.2688 | 6.2367 | 6.2048 | 6.5991 | 6.5961 | 6.294 | 6.2807 | 6.2721 | 6.2637 | 6.2555 | 6.2466 | 6.2379 | 6.2293 | 6.2209 | 6.1798 | 6.1391 | 6.0987 | 6.6503 | 6.6503 | 6.6503 | 6.6503 | 6.6503 | 6.6503 | 6.6503 | 6.6503 | 6.6503 | 6.6503 | 6.2976 | 6.2565 | 6.2161 | 6.1757
|  | INVERNEIL | FS |  |  |  | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.7458 | 6.6008 | 6.6006 | 6.5993 | 6.5977 | 6.5965 | 6.5954 | 6.2998 | 6.2964 | 6.2929 | 6.2896 | 6.2863 | 6.2706 | 6.256 | 6.2424 | 6.6503 | 6.6503 | 6.6503 | 6.6503 | 6.6503 | 6.6503 | 6.6503 | 6.6503 | 6.6503 | 6.6503 | 6.6503 | 6.6503 | 6.6503 | 6.6503
| INVERNESS | INVERNESS | MINIMUM HEADROOM | NH 65302 42625 | NO | YES | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 17.9083 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 13.3534 | 12.612 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 13.5117 | 12.7779
|  | INVERNESS | CT |  |  |  | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 17.9215 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 13.5603 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 13.728
|  | INVERNESS | LW |  |  |  | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 17.9083 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 13.3534 | 12.612 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 13.5117 | 12.7779
|  | INVERNESS | ST |  |  |  | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 17.9517 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993
|  | INVERNESS | FS |  |  |  | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 21.4886 | 17.9825 | 17.9616 | 17.9376 | 17.9109 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 17.9056 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993 | 18.1993
| KINTORE | INVERURIE | MINIMUM HEADROOM | NJ 75665 21688 | NO | YES | 39.1713 | 39.1713 | 39.1713 | 39.1713 | 39.1713 | 39.1713 | 39.1713 | 39.1713 | 39.1713 | 39.1713 | 39.1713 | 38.0004 | 28.3677 | 27.0846 | 35.6791 | 35.4455 | 35.1571 | 34.8696 | 34.6714 | 34.4741 | 34.2801 | 34.0707 | 33.9241 | 33.9028 | 33.8817 | 33.1947 | 26.0356 | 24.5351 | 36.4229 | 36.3445 | 36.2478 | 36.1514 | 36.0555 | 35.9596 | 35.8906 | 35.8522 | 35.852 | 35.852 | 35.852 | 27.5166 | 25.7954 | 24.3092
|  | INVERURIE | CT |  |  |  | 39.1713 | 39.1713 | 39.1713 | 39.1713 | 39.1713 | 39.1713 | 39.1713 | 39.1713 | 39.1713 | 39.1713 | 39.1713 | 38.0004 | 37.8109 | 29.0857 | 35.6907 | 35.5108 | 35.3026 | 35.0945 | 34.8869 | 34.7372 | 34.596 | 34.4437 | 34.2948 | 34.1441 | 33.9948 | 33.1947 | 33.0851 | 26.8614 | 36.4267 | 36.3664 | 36.2966 | 36.2268 | 36.1572 | 36.0875 | 36.0189 | 35.9449 | 35.8933 | 35.8657 | 35.852 | 34.6422 | 34.4464 | 26.6271
|  | INVERURIE | LW |  |  |  | 39.1713 | 39.1713 | 39.1713 | 39.1713 | 39.1713 | 39.1713 | 39.1713 | 39.1713 | 39.1713 | 39.1713 | 39.1713 | 38.0004 | 28.3677 | 27.0846 | 35.6791 | 35.4455 | 35.1571 | 34.8696 | 34.6714 | 34.4741 | 34.2801 | 34.0707 | 33.9241 | 33.9028 | 33.8817 | 33.1947 | 26.0356 | 24.5351 | 36.4229 | 36.3445 | 36.2478 | 36.1514 | 36.0555 | 35.9596 | 35.8906 | 35.8522 | 35.852 | 35.852 | 35.852 | 27.5166 | 25.7954 | 24.3092
|  | INVERURIE | ST |  |  |  | 39.1713 | 39.1713 | 39.1713 | 39.1713 | 39.1713 | 39.1713 | 39.1713 | 39.1713 | 39.1713 | 39.1713 | 39.1713 | 38.5859 | 38.4911 | 38.4911 | 35.758 | 35.6918 | 35.5887 | 35.4641 | 35.3633 | 35.2618 | 35.1624 | 35.0551 | 34.9518 | 34.8532 | 34.782 | 33.9572 | 33.5413 | 33.5021 | 36.4493 | 36.4271 | 36.3925 | 36.3508 | 36.317 | 36.2829 | 36.2496 | 36.2136 | 36.179 | 36.1438 | 36.1092 | 35.3342 | 35.1646 | 35.1492
|  | INVERURIE | FS |  |  |  | 39.1713 | 39.1713 | 39.1713 | 39.1713 | 39.1713 | 39.1713 | 39.1713 | 39.1713 | 39.1713 | 39.1713 | 39.1713 | 39.1713 | 39.1713 | 39.1713 | 35.7945 | 35.7878 | 35.7558 | 35.7176 | 35.6838 | 35.6497 | 35.6075 | 35.5657 | 35.5253 | 35.4845 | 35.4445 | 35.2511 | 35.0676 | 34.8942 | 36.4616 | 36.4593 | 36.4486 | 36.4358 | 36.4244 | 36.413 | 36.3989 | 36.3848 | 36.3713 | 36.3576 | 36.3442 | 36.2793 | 36.2178 | 36.1597
| BROADFORD | KALNAKIL | MINIMUM HEADROOM | NG 69146 53941 | YES | YES | [14 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: Generation Headroom Winter (MVA) 2025 to Generation Headroom Winter (MVA) 2050
|  | KALNAKIL | CT | [17 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: Generation Headroom Winter (MVA) 2025 to Generation Headroom Winter (MVA) 2050
|  | KALNAKIL | LW | [17 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: Generation Headroom Winter (MVA) 2025 to Generation Headroom Winter (MVA) 2050
|  | KALNAKIL | ST | [17 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: Generation Headroom Winter (MVA) 2025 to Generation Headroom Winter (MVA) 2050
|  | KALNAKIL | FS | [17 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: Generation Headroom Winter (MVA) 2025 to Generation Headroom Winter (MVA) 2050
| DUNOON | KAMES | MINIMUM HEADROOM | NR 96305 71237 | YES | YES | 2.8497 | 2.8497 | 2.8497 | 2.8497 | 2.8497 | 2.8497 | 2.8497 | 2.8497 | 2.8497 | 2.8497 | 2.8497 | 2.4334 | 2.3353 | 2.2387 | 2.7229 | 2.7206 | 2.7184 | 2.7176 | 2.7168 | 2.7161 | 2.716 | 2.716 | 2.716 | 2.716 | 2.716 | 2.3902 | 2.2677 | 2.1455 | 2.8041 | 2.8041 | 2.8041 | 2.8041 | 2.8041 | 2.8041 | 2.8041 | 2.8041 | 2.8041 | 2.8041 | 2.8041 | 2.4437 | 2.3216 | 2.2014
|  | KAMES | CT |  |  |  | 2.8497 | 2.8497 | 2.8497 | 2.8497 | 2.8497 | 2.8497 | 2.8497 | 2.8497 | 2.8497 | 2.8497 | 2.8497 | 2.4537 | 2.3585 | 2.2648 | 2.7232 | 2.7213 | 2.7193 | 2.7183 | 2.7177 | 2.7172 | 2.7167 | 2.7161 | 2.716 | 2.716 | 2.716 | 2.4154 | 2.297 | 2.1785 | 2.8041 | 2.8041 | 2.8041 | 2.8041 | 2.8041 | 2.8041 | 2.8041 | 2.8041 | 2.8041 | 2.8041 | 2.8041 | 2.469 | 2.3505 | 2.2338
|  | KAMES | LW |  |  |  | 2.8497 | 2.8497 | 2.8497 | 2.8497 | 2.8497 | 2.8497 | 2.8497 | 2.8497 | 2.8497 | 2.8497 | 2.8497 | 2.4334 | 2.3353 | 2.2387 | 2.7229 | 2.7206 | 2.7184 | 2.7176 | 2.7168 | 2.7161 | 2.716 | 2.716 | 2.716 | 2.716 | 2.716 | 2.3902 | 2.2677 | 2.1455 | 2.8041 | 2.8041 | 2.8041 | 2.8041 | 2.8041 | 2.8041 | 2.8041 | 2.8041 | 2.8041 | 2.8041 | 2.8041 | 2.4437 | 2.3216 | 2.2014
|  | KAMES | ST |  |  |  | 2.8497 | 2.8497 | 2.8497 | 2.8497 | 2.8497 | 2.8497 | 2.8497 | 2.8497 | 2.8497 | 2.8497 | 2.8497 | 2.4882 | 2.4467 | 2.4053 | 2.7245 | 2.7236 | 2.7224 | 2.7212 | 2.7186 | 2.7176 | 2.7166 | 2.716 | 2.716 | 2.716 | 2.716 | 2.4581 | 2.4066 | 2.3553 | 2.8041 | 2.8041 | 2.8041 | 2.8041 | 2.8041 | 2.8041 | 2.8041 | 2.8041 | 2.8041 | 2.8041 | 2.8041 | 2.8041 | 2.4602 | 2.4087
|  | KAMES | FS |  |  |  | 2.8497 | 2.8497 | 2.8497 | 2.8497 | 2.8497 | 2.8497 | 2.8497 | 2.8497 | 2.8497 | 2.8497 | 2.8497 | 2.8497 | 2.8497 | 2.8497 | 2.7256 | 2.7253 | 2.7248 | 2.7244 | 2.7234 | 2.7224 | 2.7211 | 2.7199 | 2.7187 | 2.7183 | 2.7179 | 2.7161 | 2.716 | 2.716 | 2.8041 | 2.8041 | 2.8041 | 2.8041 | 2.8041 | 2.8041 | 2.8041 | 2.8041 | 2.8041 | 2.8041 | 2.8041 | 2.8041 | 2.8041 | 2.8041
| KEITH | KEITH | MINIMUM HEADROOM | NJ 43925 50405 | NO | YES | 19.7953 | 19.6877 | 19.5824 | 19.4823 | 19.3855 | 19.2921 | 19.202 | 19.1446 | 19.1116 | 19.079 | 19.0468 | 18.7149 | 17.2839 | 17.0862 | 18.1068 | 18.0403 | 17.9753 | 17.9134 | 17.8537 | 17.7959 | 17.7403 | 17.7048 | 17.6843 | 17.6641 | 17.6442 | 17.4387 | 12.9804 | 12.4244 | 17.6817 | 17.5577 | 17.4323 | 17.3161 | 17.2032 | 17.0931 | 16.9862 | 16.9209 | 16.8869 | 16.8533 | 16.8203 | 16.4812 | 13.1201 | 12.5587
|  | KEITH | CT |  |  |  | 19.7953 | 19.6877 | 19.5824 | 19.4823 | 19.3855 | 19.2921 | 19.202 | 19.1446 | 19.1116 | 19.079 | 19.0468 | 18.7149 | 17.2839 | 17.0862 | 18.1068 | 18.0403 | 17.9753 | 17.9134 | 17.8537 | 17.7959 | 17.7403 | 17.7048 | 17.6843 | 17.6641 | 17.6442 | 17.4387 | 12.9804 | 12.4244 | 17.6817 | 17.5577 | 17.4323 | 17.3161 | 17.2032 | 17.0931 | 16.9862 | 16.9209 | 16.8869 | 16.8533 | 16.8203 | 16.4812 | 13.1201 | 12.5587
|  | KEITH | LW |  |  |  | 19.9721 | 19.9523 | 19.9295 | 19.907 | 19.883 | 19.8578 | 19.8315 | 19.8011 | 19.7699 | 19.7382 | 19.7063 | 19.3339 | 17.845 | 17.5762 | 18.2158 | 18.2036 | 18.1895 | 18.1755 | 18.1607 | 18.1451 | 18.1288 | 18.11 | 18.0908 | 18.0712 | 18.0514 | 17.8209 | 13.6501 | 12.9853 | 17.8547 | 17.8237 | 17.7869 | 17.7552 | 17.7223 | 17.6886 | 17.654 | 17.6146 | 17.5745 | 17.534 | 17.4934 | 17.1071 | 15.6041 | 13.229
|  | KEITH | ST |  |  |  | 19.9994 | 19.9915 | 19.983 | 19.9755 | 19.9624 | 19.9495 | 19.9367 | 19.9237 | 19.9081 | 19.8929 | 19.8782 | 19.7237 | 19.0284 | 18.9478 | 18.2327 | 18.2278 | 18.2225 | 18.2179 | 18.2097 | 18.2017 | 18.1938 | 18.1856 | 18.176 | 18.1665 | 18.1574 | 18.0617 | 17.6327 | 17.5826 | 17.8854 | 17.8731 | 17.8583 | 17.8463 | 17.8183 | 17.7903 | 17.7627 | 17.7334 | 17.7026 | 17.6752 | 17.6599 | 17.502 | 16.8005 | 16.7169
|  | KEITH | FS |  |  |  | 19.9947 | 19.9882 | 19.9784 | 19.9692 | 19.9585 | 19.948 | 19.937 | 19.9262 | 19.9156 | 19.9051 | 19.8947 | 19.8362 | 19.7761 | 19.7178 | 18.2298 | 18.2258 | 18.2198 | 18.2141 | 18.2075 | 18.2009 | 18.1941 | 18.1874 | 18.1808 | 18.1743 | 18.1679 | 18.1317 | 18.0945 | 18.0584 | 17.8842 | 17.8764 | 17.8645 | 17.8543 | 17.8388 | 17.8234 | 17.8063 | 17.7894 | 17.7728 | 17.7564 | 17.7403 | 17.6557 | 17.5722 | 17.4986
| KINTORE | KEMNAY | MINIMUM HEADROOM | NJ 73180 16804 | NO | YES | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 14.4122 | 14.0803 | 15.8935 | 15.8532 | 15.8184 | 15.7926 | 15.7666 | 15.7403 | 15.7145 | 15.6867 | 15.6597 | 15.6322 | 15.6049 | 13.4092 | 13.0117 | 12.6246 | 15.8626 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 13.683 | 13.282 | 12.8903
|  | KEMNAY | CT |  |  |  | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 15.8988 | 15.873 | 15.8429 | 15.823 | 15.807 | 15.7907 | 15.7746 | 15.7573 | 15.7407 | 15.7236 | 15.7067 | 15.6206 | 13.5848 | 13.3215 | 15.864 | 15.8574 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 13.5954
|  | KEMNAY | LW |  |  |  | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 14.4122 | 14.0803 | 15.8935 | 15.8532 | 15.8184 | 15.7926 | 15.7666 | 15.7403 | 15.7145 | 15.6867 | 15.6597 | 15.6322 | 15.6049 | 13.4092 | 13.0117 | 12.6246 | 15.8626 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 13.683 | 13.282 | 12.8903
|  | KEMNAY | ST |  |  |  | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 15.905 | 15.8901 | 15.8671 | 15.8391 | 15.8249 | 15.8128 | 15.8009 | 15.7881 | 15.7758 | 15.7633 | 15.7509 | 15.6906 | 15.6321 | 13.713 | 15.8656 | 15.8618 | 15.8559 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525
|  | KEMNAY | FS |  |  |  | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 17.0725 | 15.9132 | 15.9116 | 15.9048 | 15.8966 | 15.889 | 15.8812 | 15.8717 | 15.8622 | 15.8531 | 15.8439 | 15.8348 | 15.8119 | 15.7903 | 15.7698 | 15.8677 | 15.8673 | 15.8655 | 15.8634 | 15.8615 | 15.8595 | 15.8571 | 15.8546 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525 | 15.8525
| TAYNUILT | KENMORE | MINIMUM HEADROOM | NN 00325 34042 | YES | YES | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.61038 | 0.60972 | 0.60891 | 0.60811 | 0.60768 | 0.60728 | 0.60689 | 0.60647 | 0.60605 | 0.60563 | 0.60522 | 0.60275 | 0.60275 | 0.60275 | 0.62797 | 0.62774 | 0.62759 | 0.62745 | 0.6273 | 0.62717 | 0.62703 | 0.62688 | 0.62674 | 0.62659 | 0.62645 | 0.62522 | 0.62496 | 0.62496
|  | KENMORE | CT |  |  |  | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.61042 | 0.60992 | 0.60936 | 0.6088 | 0.60826 | 0.60789 | 0.60762 | 0.60732 | 0.60703 | 0.60673 | 0.60644 | 0.60389 | 0.60275 | 0.60275 | 0.62799 | 0.62778 | 0.62767 | 0.62757 | 0.62747 | 0.62738 | 0.62728 | 0.62718 | 0.62708 | 0.62697 | 0.62687 | 0.62598 | 0.62509 | 0.62496
|  | KENMORE | LW |  |  |  | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.61038 | 0.60972 | 0.60891 | 0.60811 | 0.60768 | 0.60728 | 0.60689 | 0.60647 | 0.60605 | 0.60563 | 0.60522 | 0.60275 | 0.60275 | 0.60275 | 0.62797 | 0.62774 | 0.62759 | 0.62745 | 0.6273 | 0.62717 | 0.62703 | 0.62688 | 0.62674 | 0.62659 | 0.62645 | 0.62522 | 0.62496 | 0.62496
|  | KENMORE | ST |  |  |  | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.6106 | 0.6104 | 0.61009 | 0.60971 | 0.60909 | 0.60849 | 0.60798 | 0.60764 | 0.60731 | 0.60699 | 0.60667 | 0.60511 | 0.60359 | 0.60275 | 0.62807 | 0.62797 | 0.62782 | 0.62774 | 0.62763 | 0.62752 | 0.62741 | 0.62729 | 0.62717 | 0.62706 | 0.62695 | 0.62641 | 0.62588 | 0.62535
|  | KENMORE | FS |  |  |  | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.69732 | 0.61071 | 0.6107 | 0.61061 | 0.61051 | 0.6103 | 0.6101 | 0.60984 | 0.60958 | 0.60933 | 0.60908 | 0.60884 | 0.60787 | 0.6073 | 0.60678 | 0.62813 | 0.62812 | 0.62808 | 0.62803 | 0.62793 | 0.62783 | 0.62776 | 0.62772 | 0.62767 | 0.62762 | 0.62758 | 0.62737 | 0.62717 | 0.62699
| STRATHLEVEN | KEPCULLOCH | MINIMUM HEADROOM | NS 53864 91598 | NO | YES | 5.6312 | 5.6135 | 5.5893 | 5.5623 | 5.5315 | 5.4982 | 5.4653 | 5.4297 | 5.3899 | 5.3497 | 5.3075 | 4.8423 | 4.4518 | 4.0609 | 7.5289 | 7.5164 | 7.4994 | 7.4804 | 7.4619 | 7.4595 | 7.4571 | 7.4545 | 7.4516 | 5.9644 | 5.9083 | 5.3347 | 4.8164 | 4.2977 | 8.1474 | 8.1474 | 8.1474 | 8.1474 | 8.1474 | 8.1474 | 8.1474 | 8.1474 | 8.1474 | 8.1474 | 8.1474 | 5.8571 | 5.3476 | 4.811
|  | KEPCULLOCH | CT |  |  |  | 5.6318 | 5.617 | 5.5976 | 5.5758 | 5.5508 | 5.5236 | 5.4967 | 5.4676 | 5.4349 | 5.4018 | 5.367 | 5.0114 | 4.7319 | 4.4512 | 7.5293 | 7.5189 | 7.5052 | 7.4899 | 7.4724 | 7.4613 | 7.4593 | 7.4572 | 7.4549 | 7.4525 | 7.45 | 5.5591 | 5.1882 | 4.8156 | 8.1474 | 8.1474 | 8.1474 | 8.1474 | 8.1474 | 8.1474 | 8.1474 | 8.1474 | 8.1474 | 8.1474 | 8.1474 | 8.0717 | 5.7234 | 5.3468
|  | KEPCULLOCH | LW |  |  |  | 5.6312 | 5.6135 | 5.5893 | 5.5623 | 5.5315 | 5.4982 | 5.4653 | 5.4297 | 5.3899 | 5.3497 | 5.3075 | 4.8423 | 4.4518 | 4.0609 | 7.5289 | 7.5164 | 7.4994 | 7.4804 | 7.4619 | 7.4595 | 7.4571 | 7.4545 | 7.4516 | 5.9644 | 5.9083 | 5.3347 | 4.8164 | 4.2977 | 8.1474 | 8.1474 | 8.1474 | 8.1474 | 8.1474 | 8.1474 | 8.1474 | 8.1474 | 8.1474 | 8.1474 | 8.1474 | 5.8571 | 5.3476 | 4.811
|  | KEPCULLOCH | ST |  |  |  | 5.9564 | 5.95 | 5.9394 | 5.9257 | 5.8958 | 5.8647 | 5.8341 | 5.8008 | 5.7649 | 5.7287 | 5.6913 | 5.4526 | 5.2596 | 5.0712 | 7.7573 | 7.7528 | 7.7454 | 7.7358 | 7.7148 | 7.6929 | 7.6714 | 7.648 | 7.6228 | 7.5974 | 7.5711 | 7.4362 | 5.8667 | 5.6166 | 8.3102 | 8.3024 | 8.2895 | 8.2728 | 8.2363 | 8.1983 | 8.1826 | 8.1752 | 8.1673 | 8.1593 | 8.151 | 8.1096 | 8.1096 | 8.1096
|  | KEPCULLOCH | FS |  |  |  | 5.9595 | 5.958 | 5.9542 | 5.9495 | 5.9393 | 5.9288 | 5.9166 | 5.9041 | 5.8907 | 5.8773 | 5.8634 | 5.7887 | 5.7109 | 5.6303 | 7.7595 | 7.7584 | 7.7558 | 7.7525 | 7.7453 | 7.7379 | 7.7293 | 7.7206 | 7.7112 | 7.7017 | 7.692 | 7.6395 | 7.5848 | 7.5282 | 8.314 | 8.3122 | 8.3076 | 8.3018 | 8.2894 | 8.2765 | 8.2616 | 8.2464 | 8.2301 | 8.2137 | 8.1968 | 8.1726 | 8.1553 | 8.1474
| TAYNUILT | KERRERA | MINIMUM HEADROOM | NM 82340 27997 | YES | YES | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805
|  | KERRERA | CT |  |  |  | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805
|  | KERRERA | LW |  |  |  | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805
|  | KERRERA | ST |  |  |  | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805
|  | KERRERA | FS |  |  |  | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.374 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34152 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805 | 0.34805
| GRUDIE BRIDGE | KERRY FALLS | MINIMUM HEADROOM | NG 82909 71978 | YES | YES | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1011 | 3.9633 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.0085 | 3.8643 | 3.7226 | 4.1788 | 4.1782 | 4.1753 | 4.1718 | 4.1684 | 4.1651 | 4.1619 | 4.1583 | 4.1536 | 4.1486 | 4.1436 | 4.032 | 3.8728 | 3.7162
|  | KERRY FALLS | CT |  |  |  | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1031 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.0731 | 3.9689 | 3.8664 | 4.1789 | 4.1784 | 4.1772 | 4.1748 | 4.1724 | 4.1701 | 4.1678 | 4.1653 | 4.1629 | 4.1604 | 4.158 | 4.1034 | 3.9883 | 3.8751
|  | KERRY FALLS | LW |  |  |  | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1011 | 3.9633 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.0085 | 3.8643 | 3.7226 | 4.1788 | 4.1782 | 4.1753 | 4.1718 | 4.1684 | 4.1651 | 4.1619 | 4.1583 | 4.1548 | 4.1513 | 4.1479 | 4.032 | 3.8728 | 3.7162
|  | KERRY FALLS | ST |  |  |  | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1505 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.0801 | 4.0203 | 3.9608 | 4.179 | 4.1788 | 4.1785 | 4.1782 | 4.1737 | 4.1688 | 4.164 | 4.1588 | 4.1536 | 4.1486 | 4.1436 | 4.1111 | 4.045 | 3.9794
|  | KERRY FALLS | FS |  |  |  | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1526 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1109 | 4.1791 | 4.1791 | 4.179 | 4.1789 | 4.1786 | 4.1782 | 4.1767 | 4.1747 | 4.1726 | 4.1706 | 4.1687 | 4.1594 | 4.1505 | 4.1422
| TAYNUILT | KILCHRENAN | MINIMUM HEADROOM | NN 03495 23835 | YES | YES | 1.1632 | 1.1632 | 1.1632 | 0.99441 | 0.9798 | 0.96547 | 0.95143 | 0.93623 | 0.92113 | 0.90613 | 0.89122 | 0.82139 | 0.7495 | 0.65031 | 1.5046 | 1.4968 | 1.488 | 1.4793 | 1.4708 | 1.4625 | 1.4543 | 1.4455 | 1.4367 | 1.428 | 1.4193 | 1.3787 | 0.99962 | 0.88821 | 1.2293 | 1.2227 | 1.2164 | 0.9995 | 0.98352 | 0.96785 | 0.95249 | 0.93586 | 0.91935 | 0.90294 | 0.88588 | 0.80348 | 0.71863 | 0.60158
|  | KILCHRENAN | CT |  |  |  | 1.1632 | 1.1632 | 1.1632 | 0.99441 | 0.9798 | 0.96547 | 0.95143 | 0.93623 | 0.92113 | 0.90613 | 0.89122 | 0.82139 | 0.75098 | 0.68159 | 1.5046 | 1.4968 | 1.488 | 1.4793 | 1.4708 | 1.4625 | 1.4543 | 1.4455 | 1.4367 | 1.428 | 1.4193 | 1.3787 | 1.3513 | 0.92334 | 1.2293 | 1.2227 | 1.2164 | 0.9995 | 0.98352 | 0.96785 | 0.95249 | 0.93586 | 0.91935 | 0.90294 | 0.88588 | 0.80348 | 0.72038 | 0.63849
|  | KILCHRENAN | LW |  |  |  | 1.1632 | 1.1632 | 1.1632 | 1.1632 | 1.1632 | 0.99658 | 0.98775 | 0.9782 | 0.96871 | 0.9593 | 0.94994 | 0.85018 | 0.7495 | 0.65031 | 1.5069 | 1.5023 | 1.4967 | 1.4912 | 1.4858 | 1.4806 | 1.4755 | 1.4699 | 1.4644 | 1.4589 | 1.4535 | 1.3954 | 0.99962 | 0.88821 | 1.2323 | 1.2267 | 1.2226 | 1.2187 | 1.2148 | 1.211 | 0.99221 | 0.98176 | 0.97139 | 0.96109 | 0.95086 | 0.83746 | 0.71863 | 0.60158
|  | KILCHRENAN | ST |  |  |  | 1.1632 | 1.1632 | 1.1632 | 1.1632 | 1.1632 | 1.1632 | 1.1632 | 0.9955 | 0.98569 | 0.97606 | 0.96658 | 0.92043 | 0.87496 | 0.8296 | 1.5084 | 1.507 | 1.5049 | 1.5023 | 1.4967 | 1.4911 | 1.4858 | 1.48 | 1.4743 | 1.4686 | 1.4631 | 1.4363 | 1.4098 | 1.3834 | 1.2341 | 1.2324 | 1.2297 | 1.2266 | 1.2226 | 1.2186 | 1.2148 | 1.2106 | 0.98995 | 0.97942 | 0.96906 | 0.91859 | 0.86669 | 0.81316
|  | KILCHRENAN | FS |  |  |  | 1.1632 | 1.1632 | 1.1632 | 1.1632 | 1.1632 | 1.1632 | 1.1632 | 1.1632 | 1.1632 | 1.1632 | 1.1632 | 1.1632 | 0.98537 | 0.97057 | 1.5092 | 1.5091 | 1.5085 | 1.5078 | 1.506 | 1.5042 | 1.502 | 1.4998 | 1.4976 | 1.4955 | 1.4934 | 1.4834 | 1.4741 | 1.4655 | 1.2351 | 1.235 | 1.2342 | 1.2333 | 1.2311 | 1.2289 | 1.2264 | 1.2248 | 1.2233 | 1.2217 | 1.2202 | 1.2131 | 0.98961 | 0.97342
| STRATHLEVEN | KILLEARN | MINIMUM HEADROOM | NS 51313 86758 | YES | YES | 2.439 | 2.439 | 2.439 | 2.439 | 2.439 | 2.439 | 2.439 | 2.439 | 2.439 | 0.89731 | 0.76777 | 0.32331 | -0.13102 | -0.58709 | 1.9111 | 1.8849 | 1.8517 | 1.8391 | 0.94162 | 0.80184 | 0.66338 | 0.51358 | 0.36391 | 0.21431 | 0.062221 | -0.45959 | -0.99299 | -1.5284 | 2.0387 | 2.0387 | 2.0387 | 2.0387 | 0.9849 | 0.84507 | 0.70657 | 0.55671 | 0.407 | 0.25735 | 0.10521 | -0.41677 | -0.95035 | -1.486
|  | KILLEARN | CT |  |  |  | 2.439 | 2.439 | 2.439 | 2.439 | 2.439 | 2.439 | 2.439 | 2.439 | 2.439 | 2.439 | 2.439 | 0.8736 | 0.53405 | 0.19236 | 1.9149 | 1.8984 | 1.8784 | 1.8575 | 1.8452 | 1.8372 | 0.9679 | 0.87154 | 0.77446 | 0.67719 | 0.57805 | 0.18647 | -0.21217 | -0.61333 | 2.0387 | 2.0387 | 2.0387 | 2.0387 | 2.0387 | 2.0387 | 2.0387 | 0.9148 | 0.81768 | 0.72038 | 0.62121 | 0.2295 | -0.16928 | -0.57057
|  | KILLEARN | LW |  |  |  | 2.439 | 2.439 | 2.439 | 2.439 | 2.439 | 2.439 | 2.439 | 2.439 | 2.439 | 0.89731 | 0.76777 | 0.32331 | -0.13102 | -0.58709 | 1.9111 | 1.8849 | 1.8517 | 1.8391 | 0.94162 | 0.80184 | 0.66338 | 0.51358 | 0.36391 | 0.21431 | 0.062221 | -0.45959 | -0.99299 | -1.5284 | 2.0387 | 2.0387 | 2.0387 | 2.0387 | 0.9849 | 0.84507 | 0.70657 | 0.55671 | 0.407 | 0.25735 | 0.10521 | -0.41677 | -0.95035 | -1.486
|  | KILLEARN | ST |  |  |  | 2.439 | 2.439 | 2.439 | 2.439 | 2.439 | 2.439 | 2.439 | 2.439 | 2.439 | 2.439 | 2.439 | 2.439 | 2.439 | 0.83127 | 1.919 | 1.9094 | 1.8943 | 1.8757 | 1.8644 | 1.8524 | 1.847 | 1.8425 | 1.8378 | 1.8332 | 0.95816 | 0.67615 | 0.40287 | 0.13677 | 2.0387 | 2.0387 | 2.0387 | 2.0387 | 2.0387 | 2.0387 | 2.0387 | 2.0387 | 2.0387 | 2.0387 | 2.0387 | 0.71934 | 0.44597 | 0.17978
|  | KILLEARN | FS |  |  |  | 2.439 | 2.439 | 2.439 | 2.439 | 2.439 | 2.439 | 2.439 | 2.439 | 2.439 | 2.439 | 2.439 | 2.439 | 2.439 | 2.439 | 1.9245 | 1.9232 | 1.9189 | 1.9138 | 1.9098 | 1.9056 | 1.9008 | 1.8959 | 1.8909 | 1.8859 | 1.8807 | 1.8528 | 1.8412 | 0.98472 | 2.0387 | 2.0387 | 2.0387 | 2.0387 | 2.0387 | 2.0387 | 2.0387 | 2.0387 | 2.0387 | 2.0387 | 2.0387 | 2.0387 | 2.0387 | 2.0387
| KILLIN | KILLIN TOWN | MINIMUM HEADROOM | NN 56931 32662 | YES | YES | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 2.3559 | 3.0363 | 3.0266 | 3.0205 | 3.0153 | 3.0096 | 3.0036 | 2.9977 | 2.9913 | 2.9843 | 2.9773 | 2.9746 | 2.4813 | 2.2987 | 2.1167 | 3.1928 | 3.1832 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 2.4926 | 2.3159
|  | KILLIN TOWN | CT |  |  |  | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0369 | 3.0295 | 3.023 | 3.0191 | 3.0148 | 3.0103 | 3.0058 | 3.0009 | 2.9956 | 2.9903 | 2.9847 | 2.9672 | 2.4354 | 2.3019 | 3.1934 | 3.1861 | 3.1768 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 2.4957
|  | KILLIN TOWN | LW |  |  |  | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 2.3559 | 3.0363 | 3.0266 | 3.0205 | 3.0153 | 3.0096 | 3.0036 | 2.9977 | 2.9913 | 2.9843 | 2.9773 | 2.9746 | 2.4813 | 2.2987 | 2.1167 | 3.1928 | 3.1832 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 2.4926 | 2.3159
|  | KILLIN TOWN | ST |  |  |  | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0392 | 3.036 | 3.0307 | 3.0244 | 3.0196 | 3.0146 | 3.0098 | 3.0044 | 2.9988 | 2.9931 | 2.9873 | 2.9715 | 2.9672 | 2.4682 | 3.1957 | 3.1925 | 3.1873 | 3.1806 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736
|  | KILLIN TOWN | FS |  |  |  | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0671 | 3.0409 | 3.0403 | 3.0386 | 3.0365 | 3.0318 | 3.027 | 3.0233 | 3.0211 | 3.0187 | 3.0164 | 3.014 | 3.0014 | 2.9886 | 2.9759 | 3.1974 | 3.1968 | 3.1951 | 3.193 | 3.1883 | 3.1835 | 3.1778 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736 | 3.1736
| TAYNUILT | KILMELFORD | MINIMUM HEADROOM | NM 84056 14437 | YES | YES | 2.4837 | 2.4317 | 2.3984 | 2.3984 | 2.3984 | 2.3984 | 2.3984 | 2.3984 | 2.3984 | 2.3984 | 0.89519 | 0.027589 | -0.11734 | -0.26014 | 2.5519 | 2.5196 | 2.4969 | 2.493 | 2.4891 | 2.4855 | 0.98209 | 0.90581 | 0.82995 | 0.75463 | 0.10683 | -0.64339 | -0.8061 | -0.96849 | 2.0126 | 2.0126 | 2.0126 | 2.0126 | 2.0126 | 2.0126 | 2.0126 | 2.0126 | 0.95062 | 0.87543 | 0.030603 | -0.86714 | -1.0419 | -1.214
|  | KILMELFORD | CT |  |  |  | 2.4886 | 2.4517 | 2.4105 | 2.3984 | 2.3984 | 2.3984 | 2.3984 | 2.3984 | 2.3984 | 2.3984 | 1.7445 | 0.28897 | 0.2131 | 0.13827 | 2.555 | 2.532 | 2.5064 | 2.4969 | 2.4944 | 2.492 | 2.4896 | 2.487 | 2.4845 | 0.98249 | 0.3427 | -0.33647 | -0.42715 | -0.51658 | 2.0126 | 2.0126 | 2.0126 | 2.0126 | 2.0126 | 2.0126 | 2.0126 | 2.0126 | 2.0126 | 2.0126 | 0.28388 | -0.53757 | -0.63494 | -0.73097
|  | KILMELFORD | LW |  |  |  | 2.4837 | 2.4317 | 2.3984 | 2.3984 | 2.3984 | 2.3984 | 2.3984 | 2.3984 | 2.3984 | 2.3984 | 0.89519 | 0.027589 | -0.11734 | -0.26014 | 2.5519 | 2.5196 | 2.4969 | 2.493 | 2.4891 | 2.4855 | 0.98209 | 0.90581 | 0.82995 | 0.75463 | 0.10683 | -0.64339 | -0.8061 | -0.96849 | 2.0126 | 2.0126 | 2.0126 | 2.0126 | 2.0126 | 2.0126 | 2.0126 | 2.0126 | 0.95062 | 0.87543 | 0.030603 | -0.86714 | -1.0419 | -1.214
|  | KILMELFORD | ST |  |  |  | 2.5014 | 2.4854 | 2.462 | 2.4346 | 2.4203 | 2.4071 | 2.3984 | 2.3984 | 2.3984 | 2.3984 | 2.0714 | 1.7637 | 1.7637 | 1.7637 | 2.5629 | 2.553 | 2.5384 | 2.5214 | 2.5125 | 2.5043 | 2.4985 | 2.4976 | 2.4967 | 2.4959 | 0.94171 | 0.57497 | 0.50388 | 0.43298 | 2.0126 | 2.0126 | 2.0126 | 2.0126 | 2.0126 | 2.0126 | 2.0126 | 2.0126 | 2.0126 | 2.0126 | 0.97606 | 0.53617 | 0.45984 | 0.3837
|  | KILMELFORD | FS |  |  |  | 2.5104 | 2.5082 | 2.501 | 2.4928 | 2.4878 | 2.4834 | 2.4779 | 2.4725 | 2.4671 | 2.4619 | 2.4568 | 2.4331 | 2.4111 | 2.3984 | 2.5685 | 2.5672 | 2.5627 | 2.5576 | 2.5545 | 2.5518 | 2.5483 | 2.5449 | 2.5416 | 2.5384 | 2.5352 | 2.5204 | 2.5068 | 2.4982 | 2.0126 | 2.0126 | 2.0126 | 2.0126 | 2.0126 | 2.0126 | 2.0126 | 2.0126 | 2.0126 | 2.0126 | 2.0126 | 2.0126 | 2.0126 | 2.0126
| TAYNUILT | KILNINVER | MINIMUM HEADROOM | NM 83049 22251 | YES | YES | 2.0143 | 2.0143 | 2.0143 | 2.0143 | 2.0143 | 2.0143 | 2.0143 | 2.0143 | 2.0143 | 2.0143 | 0.59209 | 0.50635 | 0.50635 | 0.50635 | 1.7256 | 1.7225 | 1.7191 | 1.7191 | 1.7191 | 1.7191 | 1.7191 | 1.7191 | 1.7191 | 1.7191 | 0.74109 | 0.54973 | 0.43093 | 0.31385 | 1.7533 | 1.7527 | 1.7518 | 1.751 | 1.7503 | 1.7495 | 0.99169 | 0.98201 | 0.9724 | 0.96285 | 0.43646 | 0.22842 | 0.11418 | 0.0015882
|  | KILNINVER | CT |  |  |  | 2.0143 | 2.0143 | 2.0143 | 2.0143 | 2.0143 | 2.0143 | 2.0143 | 2.0143 | 2.0143 | 2.0143 | 0.59209 | 0.50635 | 0.50635 | 0.50635 | 1.7258 | 1.7234 | 1.7208 | 1.7191 | 1.7191 | 1.7191 | 1.7191 | 1.7191 | 1.7191 | 1.7191 | 0.77023 | 0.61021 | 0.52301 | 0.43714 | 1.7534 | 1.7529 | 1.7523 | 1.7517 | 1.7512 | 1.7507 | 1.7501 | 1.7496 | 0.99471 | 0.98803 | 0.46447 | 0.28658 | 0.20273 | 0.12016
|  | KILNINVER | LW |  |  |  | 2.0143 | 2.0143 | 2.0143 | 2.0143 | 2.0143 | 2.0143 | 2.0143 | 2.0143 | 2.0143 | 2.0143 | 0.59209 | 0.50635 | 0.50635 | 0.50635 | 1.7256 | 1.7225 | 1.7191 | 1.7191 | 1.7191 | 1.7191 | 1.7191 | 1.7191 | 1.7191 | 1.7191 | 0.74109 | 0.54973 | 0.43093 | 0.31385 | 1.7533 | 1.7527 | 1.7518 | 1.751 | 1.7503 | 1.7495 | 0.99169 | 0.98201 | 0.9724 | 0.96285 | 0.43646 | 0.22842 | 0.11418 | 0.0015882
|  | KILNINVER | ST |  |  |  | 2.0143 | 2.0143 | 2.0143 | 2.0143 | 2.0143 | 2.0143 | 2.0143 | 2.0143 | 2.0143 | 2.0143 | 0.82595 | 0.78308 | 0.78308 | 0.78308 | 1.7266 | 1.7256 | 1.7242 | 1.7224 | 1.7191 | 1.7191 | 1.7191 | 1.7191 | 1.7191 | 1.7191 | 0.95504 | 0.86664 | 0.81574 | 0.76503 | 1.7535 | 1.7533 | 1.753 | 1.7526 | 1.7518 | 1.7509 | 1.7501 | 0.99722 | 0.98668 | 0.97632 | 0.70767 | 0.61066 | 0.56172 | 0.51295
|  | KILNINVER | FS |  |  |  | 2.0143 | 2.0143 | 2.0143 | 2.0143 | 2.0143 | 2.0143 | 2.0143 | 2.0143 | 2.0143 | 2.0143 | 2.0143 | 2.0143 | 2.0143 | 2.0143 | 1.7271 | 1.727 | 1.7266 | 1.7261 | 1.7248 | 1.7235 | 1.7218 | 1.7202 | 1.7191 | 1.7191 | 1.7191 | 1.7191 | 1.7191 | 1.7191 | 1.7536 | 1.7536 | 1.7535 | 1.7534 | 1.7532 | 1.7529 | 1.7525 | 1.7522 | 1.7518 | 1.7515 | 1.7511 | 1.7495 | 0.98301 | 0.96631
| BEAULY | KILTARLITY | MINIMUM HEADROOM | NH 50271 41265 | YES | YES | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 5.9714 | 5.8462 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 5.9994 | 5.9764 | 5.8252 | 5.671 | 5.5197 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 5.9394 | 5.7876 | 5.6387
|  | KILTARLITY | CT |  |  |  | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 5.9932 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 5.9347 | 5.815 | 5.6973 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 5.9293 | 5.8134
|  | KILTARLITY | LW |  |  |  | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 5.9714 | 5.8462 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 5.9994 | 5.9764 | 5.8252 | 5.671 | 5.5197 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 5.9394 | 5.7876 | 5.6387
|  | KILTARLITY | ST |  |  |  | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 5.9583 | 5.8933 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233
|  | KILTARLITY | FS |  |  |  | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.9455 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.5761 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233 | 6.6233
| REDMOSS | KINCORTH | MINIMUM HEADROOM | NJ 94445 03252 | NO | YES | 16.1748 | 16.0952 | 16.0198 | 15.9469 | 15.8759 | 15.8069 | 15.7415 | 15.7019 | 15.6802 | 15.6587 | 15.6375 | 15.5187 | 15.414 | 15.3234 | 14.6136 | 14.5475 | 14.4832 | 14.4206 | 14.3577 | 14.2976 | 14.2661 | 14.2482 | 14.2393 | 14.2305 | 14.2219 | 14.1799 | 14.1351 | 11.4029 | 15.0577 | 14.9735 | 14.8932 | 14.8153 | 14.7388 | 14.6637 | 14.5934 | 14.5489 | 14.5229 | 14.4971 | 14.4715 | 14.3642 | 14.2756 | 14.1813
|  | KINCORTH | CT |  |  |  | 16.1748 | 16.0952 | 16.0198 | 15.9469 | 15.8759 | 15.8069 | 15.7415 | 15.7019 | 15.6802 | 15.6587 | 15.6375 | 15.5187 | 15.414 | 15.3234 | 14.6136 | 14.5475 | 14.4832 | 14.4206 | 14.3577 | 14.2976 | 14.2661 | 14.2482 | 14.2393 | 14.2305 | 14.2219 | 14.1799 | 14.1351 | 11.4029 | 15.0577 | 14.9735 | 14.8932 | 14.8153 | 14.7388 | 14.6637 | 14.5934 | 14.5489 | 14.5229 | 14.4971 | 14.4715 | 14.3642 | 14.2756 | 14.1813
|  | KINCORTH | LW |  |  |  | 16.3082 | 16.2938 | 16.2774 | 16.26 | 16.2416 | 16.2221 | 16.2017 | 16.179 | 16.1557 | 16.132 | 16.1074 | 15.9552 | 15.797 | 15.6624 | 14.7071 | 14.6893 | 14.6687 | 14.6482 | 14.6271 | 14.6053 | 14.5831 | 14.5586 | 14.5338 | 14.5088 | 14.4814 | 14.4018 | 14.3365 | 14.2657 | 15.1926 | 15.1753 | 15.1554 | 15.1349 | 15.1132 | 15.0906 | 15.0672 | 15.0411 | 15.0145 | 14.9875 | 14.9589 | 14.8037 | 14.6742 | 14.5342
|  | KINCORTH | ST |  |  |  | 16.332 | 16.3264 | 16.3206 | 16.3146 | 16.3052 | 16.2957 | 16.287 | 16.2784 | 16.2679 | 16.2577 | 16.2477 | 16.1924 | 16.1401 | 16.0851 | 14.7346 | 14.7283 | 14.7206 | 14.7119 | 14.6951 | 14.6771 | 14.6618 | 14.6456 | 14.6292 | 14.6131 | 14.5972 | 14.5092 | 14.4924 | 14.4739 | 15.2206 | 15.2141 | 15.2069 | 15.1992 | 15.1861 | 15.1723 | 15.1602 | 15.1478 | 15.134 | 15.1204 | 15.1071 | 15.033 | 14.9831 | 14.9464
|  | KINCORTH | FS |  |  |  | 16.3302 | 16.3254 | 16.3182 | 16.3109 | 16.303 | 16.2953 | 16.2873 | 16.2795 | 16.2718 | 16.2642 | 16.2568 | 16.2143 | 16.17 | 16.1268 | 14.7401 | 14.7361 | 14.7296 | 14.7229 | 14.7138 | 14.7051 | 14.6955 | 14.6859 | 14.6765 | 14.6674 | 14.6588 | 14.6121 | 14.5637 | 14.516 | 15.2212 | 15.2161 | 15.2083 | 15.2003 | 15.1911 | 15.1821 | 15.1726 | 15.1632 | 15.154 | 15.1449 | 15.1362 | 15.0871 | 15.0361 | 14.9861
| FORT WILLIAM | KINGAIRLOCH | MINIMUM HEADROOM | NM 76917 56652 | YES | YES | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.13446 | 0.13421 | 0.1339 | 0.13368 | 0.13353 | 0.13337 | 0.13323 | 0.13307 | 0.13291 | 0.13275 | 0.1326 | 0.1321 | 0.1321 | 0.1321 | 0.13997 | 0.1399 | 0.13984 | 0.13978 | 0.13973 | 0.13968 | 0.13963 | 0.13957 | 0.13952 | 0.13946 | 0.13941 | 0.13914 | 0.13904 | 0.13904
|  | KINGAIRLOCH | CT |  |  |  | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.13448 | 0.13429 | 0.13407 | 0.13386 | 0.13371 | 0.1336 | 0.1335 | 0.13339 | 0.13328 | 0.13316 | 0.13306 | 0.13252 | 0.1321 | 0.1321 | 0.13997 | 0.13991 | 0.13987 | 0.13983 | 0.13979 | 0.13976 | 0.13972 | 0.13968 | 0.13964 | 0.13961 | 0.13957 | 0.13938 | 0.13919 | 0.13904
|  | KINGAIRLOCH | LW |  |  |  | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.13446 | 0.13421 | 0.1339 | 0.13368 | 0.13353 | 0.13337 | 0.13323 | 0.13307 | 0.13291 | 0.13275 | 0.1326 | 0.1321 | 0.1321 | 0.1321 | 0.13997 | 0.1399 | 0.13984 | 0.13978 | 0.13973 | 0.13968 | 0.13963 | 0.13957 | 0.13952 | 0.13946 | 0.13941 | 0.13914 | 0.13904 | 0.13904
|  | KINGAIRLOCH | ST |  |  |  | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.13454 | 0.13447 | 0.13435 | 0.13421 | 0.13407 | 0.13394 | 0.13381 | 0.13371 | 0.13364 | 0.13357 | 0.1335 | 0.13316 | 0.13282 | 0.13248 | 0.14001 | 0.13997 | 0.13992 | 0.13989 | 0.13987 | 0.13985 | 0.13982 | 0.1398 | 0.13977 | 0.13975 | 0.13972 | 0.1396 | 0.13949 | 0.13937
|  | KINGAIRLOCH | FS |  |  |  | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.16165 | 0.13458 | 0.13458 | 0.13455 | 0.13451 | 0.13446 | 0.13442 | 0.13436 | 0.1343 | 0.13424 | 0.13419 | 0.13414 | 0.13388 | 0.1337 | 0.13358 | 0.14003 | 0.14002 | 0.14001 | 0.13999 | 0.13997 | 0.13994 | 0.13992 | 0.13991 | 0.1399 | 0.13989 | 0.13988 | 0.13983 | 0.13979 | 0.13975
| DYCE | KINGSEAT | MINIMUM HEADROOM | NJ 89545 19709 | NO | YES | 7.7557 | 7.7557 | 7.7557 | 17.3057 | 17.3057 | 17.3057 | 17.3057 | 17.3057 | 14.4857 | 14.3077 | 14.1311 | 12.8063 | 12.2898 | 11.7847 | 6.4635 | 6.3634 | 6.3109 | 15.0785 | 13.6718 | 13.4728 | 13.277 | 13.0654 | 12.8566 | 12.6472 | 12.4394 | 11.2334 | 10.6257 | 10.0314 | 6.8455 | 6.8324 | 6.8162 | 15.6001 | 15.5841 | 13.7807 | 13.6011 | 13.407 | 13.2156 | 13.0235 | 12.8252 | 11.4339 | 10.8357 | 10.2506
|  | KINGSEAT | CT |  |  |  | 7.7557 | 7.7557 | 7.7557 | 17.3057 | 17.3057 | 17.3057 | 17.3057 | 17.3057 | 17.3057 | 17.3057 | 17.3057 | 14.1753 | 13.8436 | 13.495 | 6.4968 | 6.4663 | 6.4305 | 15.1942 | 15.1578 | 15.1323 | 15.1227 | 15.1124 | 15.1024 | 15.0921 | 15.082 | 12.874 | 12.454 | 12.0438 | 6.8499 | 6.8459 | 6.8412 | 15.6364 | 15.6317 | 15.6268 | 15.6221 | 15.6169 | 15.6119 | 15.6068 | 15.6018 | 13.0177 | 12.6325 | 12.2317
|  | KINGSEAT | LW |  |  |  | 7.7557 | 7.7557 | 7.7557 | 17.3057 | 17.3057 | 17.3057 | 17.3057 | 17.3057 | 14.4857 | 14.3077 | 14.1311 | 12.8063 | 12.2898 | 11.7847 | 6.4635 | 6.3634 | 6.3109 | 15.0785 | 13.6718 | 13.4728 | 13.277 | 13.0654 | 12.8566 | 12.6472 | 12.4394 | 11.2334 | 10.6257 | 10.0314 | 6.8455 | 6.8324 | 6.8162 | 15.6001 | 15.5841 | 13.7807 | 13.6011 | 13.407 | 13.2156 | 13.0235 | 12.8252 | 11.4339 | 10.8357 | 10.2506
|  | KINGSEAT | ST |  |  |  | 7.7557 | 7.7557 | 7.7557 | 17.3057 | 17.3057 | 17.3057 | 17.3057 | 17.3057 | 17.3057 | 17.3057 | 17.3057 | 14.5389 | 14.3997 | 14.1654 | 6.4903 | 6.4521 | 6.3923 | 15.1321 | 15.123 | 15.1138 | 15.1048 | 15.0951 | 15.0857 | 15.0762 | 13.7996 | 13.2126 | 12.9319 | 12.6562 | 6.849 | 6.844 | 6.8362 | 15.6267 | 15.6222 | 15.6176 | 15.6132 | 15.6083 | 15.6036 | 15.5989 | 15.5943 | 13.4351 | 13.1777 | 12.9248
|  | KINGSEAT | FS |  |  |  | 7.7557 | 7.7557 | 7.7557 | 17.3057 | 17.3057 | 17.3057 | 17.3057 | 17.3057 | 17.3057 | 17.3057 | 17.3057 | 17.3057 | 17.3057 | 17.3057 | 6.6203 | 6.6176 | 6.6028 | 15.3852 | 15.3741 | 15.3629 | 15.3489 | 15.3351 | 15.3216 | 15.3081 | 15.2948 | 15.2307 | 15.1699 | 15.1301 | 6.8661 | 6.8657 | 6.8638 | 15.6615 | 15.66 | 15.6585 | 15.6567 | 15.6549 | 15.6531 | 15.6514 | 15.6496 | 15.6412 | 15.6332 | 15.6257
| BOAT OF GARTEN | KINGUSSIE | MINIMUM HEADROOM | NH 75429 00426 | NO | YES | 9.5657 | 9.5212 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 8.9452 | 8.9452 | 8.6037 | 8.5827 | 8.5571 | 8.532 | 8.5064 | 8.4793 | 8.4515 | 8.4215 | 8.3947 | 8.3674 | 8.3462 | 8.1889 | 5.6822 | 5.2662 | 8.6358 | 8.6231 | 8.6076 | 8.5924 | 8.5769 | 8.5605 | 8.5436 | 8.5255 | 8.5092 | 8.4927 | 8.4823 | 8.4486 | 5.881 | 5.4712
|  | KINGUSSIE | CT |  |  |  | 9.5706 | 9.5383 | 9.5013 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 8.9452 | 8.9452 | 8.606 | 8.5908 | 8.5734 | 8.5561 | 8.5381 | 8.5186 | 8.498 | 8.4755 | 8.4552 | 8.4343 | 8.4188 | 8.31 | 6.1444 | 5.8669 | 8.6372 | 8.628 | 8.6174 | 8.607 | 8.5961 | 8.5843 | 8.5718 | 8.5582 | 8.5459 | 8.5332 | 8.5239 | 8.4745 | 6.3359 | 6.063
|  | KINGUSSIE | LW |  |  |  | 9.5657 | 9.5212 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 8.9452 | 8.9452 | 8.6037 | 8.5827 | 8.5571 | 8.532 | 8.5064 | 8.4793 | 8.4515 | 8.4215 | 8.3947 | 8.3674 | 8.3462 | 8.1889 | 5.6822 | 5.2662 | 8.6358 | 8.6231 | 8.6076 | 8.5924 | 8.5769 | 8.5605 | 8.5436 | 8.5255 | 8.5092 | 8.4927 | 8.4823 | 8.4486 | 5.881 | 5.4712
|  | KINGUSSIE | ST |  |  |  | 9.5827 | 9.5668 | 9.5441 | 9.518 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 9.2213 | 9.2213 | 8.6117 | 8.6042 | 8.5935 | 8.5812 | 8.5637 | 8.5453 | 8.5264 | 8.5056 | 8.4864 | 8.4667 | 8.4512 | 8.378 | 8.0942 | 8.0251 | 8.6406 | 8.6361 | 8.6296 | 8.6222 | 8.6116 | 8.6005 | 8.589 | 8.5764 | 8.5648 | 8.5528 | 8.5434 | 8.4991 | 8.2287 | 8.214
|  | KINGUSSIE | FS |  |  |  | 9.5926 | 9.5887 | 9.5807 | 9.5721 | 9.559 | 9.545 | 9.528 | 9.5107 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 9.4974 | 8.6163 | 8.6145 | 8.6107 | 8.6067 | 8.6005 | 8.5939 | 8.5859 | 8.5778 | 8.5703 | 8.5627 | 8.5565 | 8.5281 | 8.5026 | 8.4786 | 8.6435 | 8.6424 | 8.6401 | 8.6376 | 8.6339 | 8.6299 | 8.625 | 8.6201 | 8.6156 | 8.611 | 8.6072 | 8.59 | 8.5746 | 8.5601
| TAYNUILT | KINLOCH | MINIMUM HEADROOM | NM 52465 27215 | YES | YES | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 0.99146 | 1.7342 | 1.7341 | 1.7341 | 1.7341 | 1.7341 | 1.7341 | 1.7341 | 1.7341 | 1.7341 | 1.7341 | 1.7341 | 1.7341 | 1.7341 | 0.8814
|  | KINLOCH | CT |  |  |  | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.7343 | 1.7341 | 1.7341 | 1.7341 | 1.7341 | 1.7341 | 1.7341 | 1.7341 | 1.7341 | 1.7341 | 1.7341 | 1.7341 | 1.7341 | 1.7341
|  | KINLOCH | LW |  |  |  | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 0.99146 | 1.7342 | 1.7341 | 1.7341 | 1.7341 | 1.7341 | 1.7341 | 1.7341 | 1.7341 | 1.7341 | 1.7341 | 1.7341 | 1.7341 | 1.7341 | 0.8814
|  | KINLOCH | ST |  |  |  | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.7351 | 1.7342 | 1.7341 | 1.7341 | 1.7341 | 1.7341 | 1.7341 | 1.7341 | 1.7341 | 1.7341 | 1.7341 | 1.7341 | 1.7341 | 1.7341
|  | KINLOCH | FS |  |  |  | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.9693 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.7356 | 1.7356 | 1.7352 | 1.7347 | 1.7341 | 1.7341 | 1.7341 | 1.7341 | 1.7341 | 1.7341 | 1.7341 | 1.7341 | 1.7341 | 1.7341
| TUMMEL BRIDGE | KINLOCH RANNOCH | MINIMUM HEADROOM | NN 65927 58500 | YES | YES | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.293 | 1.2873 | 1.2807 | 1.2781 | 1.2772 | 1.2762 | 1.2753 | 1.2743 | 1.2733 | 1.2723 | 1.2713 | 1.2713 | 0.9806 | 0.90533 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 0.94393
|  | KINLOCH RANNOCH | CT |  |  |  | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.2933 | 1.2891 | 1.2842 | 1.2799 | 1.2784 | 1.2776 | 1.277 | 1.2763 | 1.2756 | 1.2749 | 1.2742 | 1.2713 | 1.2713 | 1.2713 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309
|  | KINLOCH RANNOCH | LW |  |  |  | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.293 | 1.2873 | 1.2807 | 1.2781 | 1.2772 | 1.2762 | 1.2753 | 1.2743 | 1.2733 | 1.2723 | 1.2713 | 1.2713 | 0.9806 | 0.90533 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 0.94393
|  | KINLOCH RANNOCH | ST |  |  |  | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.2948 | 1.2931 | 1.2904 | 1.2872 | 1.2829 | 1.2794 | 1.2783 | 1.2776 | 1.277 | 1.2764 | 1.2758 | 1.2727 | 1.2713 | 1.2713 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309
|  | KINLOCH RANNOCH | FS |  |  |  | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.5764 | 1.2957 | 1.2956 | 1.2949 | 1.294 | 1.2925 | 1.2911 | 1.2893 | 1.2875 | 1.2858 | 1.2841 | 1.2824 | 1.2782 | 1.2771 | 1.2761 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309 | 1.3309
| GRUDIE BRIDGE | KINLOCHEWE | MINIMUM HEADROOM | NH 03723 62321 | YES | YES | 0.47609 | 0.47609 | 0.47609 | 0.47609 | 0.47609 | 0.47609 | 0.47609 | 0.47609 | 0.47609 | 0.47609 | 0.47609 | 0.4575 | 0.40604 | 0.35527 | 0.47726 | 0.47726 | 0.47726 | 0.4727 | 0.46785 | 0.46308 | 0.4584 | 0.45333 | 0.44828 | 0.44327 | 0.4383 | 0.37904 | 0.31902 | 0.2598 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526
|  | KINLOCHEWE | CT |  |  |  | 0.47609 | 0.47609 | 0.47609 | 0.47609 | 0.47609 | 0.47609 | 0.47609 | 0.47609 | 0.47609 | 0.47609 | 0.47609 | 0.47609 | 0.44717 | 0.41057 | 0.47726 | 0.47726 | 0.47726 | 0.47696 | 0.47359 | 0.47027 | 0.46701 | 0.46347 | 0.45995 | 0.45645 | 0.45297 | 0.41031 | 0.36698 | 0.3243 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526
|  | KINLOCHEWE | LW |  |  |  | 0.47609 | 0.47609 | 0.47609 | 0.47609 | 0.47609 | 0.47609 | 0.47609 | 0.47609 | 0.47609 | 0.47609 | 0.47609 | 0.4575 | 0.40604 | 0.35527 | 0.47726 | 0.47726 | 0.47726 | 0.4727 | 0.46785 | 0.46308 | 0.4584 | 0.45333 | 0.44828 | 0.44327 | 0.4383 | 0.37904 | 0.31902 | 0.2598 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526
|  | KINLOCHEWE | ST |  |  |  | 0.47609 | 0.47609 | 0.47609 | 0.47609 | 0.47609 | 0.47609 | 0.47609 | 0.47609 | 0.47609 | 0.47609 | 0.47609 | 0.47609 | 0.46912 | 0.44761 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.4772 | 0.47195 | 0.4668 | 0.46123 | 0.45575 | 0.45036 | 0.44505 | 0.41907 | 0.39325 | 0.3675 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526
|  | KINLOCHEWE | FS |  |  |  | 0.47609 | 0.47609 | 0.47609 | 0.47609 | 0.47609 | 0.47609 | 0.47609 | 0.47609 | 0.47609 | 0.47609 | 0.47609 | 0.47609 | 0.47609 | 0.47609 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47726 | 0.47517 | 0.4731 | 0.46314 | 0.45376 | 0.44495 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526
| KINLOCHLEVEN | KINLOCHLEVEN | MINIMUM HEADROOM | NN 19285 62002 | NO | YES | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.0451 | 3.0421 | 3.0384 | 3.0347 | 3.0311 | 3.0275 | 3.0239 | 3.0201 | 3.0163 | 3.0126 | 3.009 | 2.9647 | 2.9529 | 2.9529 | 3.0481 | 3.0471 | 3.0458 | 3.0446 | 3.0434 | 3.0422 | 3.041 | 3.0397 | 3.0384 | 3.0372 | 3.036 | 3.0212 | 3.0054 | 3.0046
|  | KINLOCHLEVEN | CT |  |  |  | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.0451 | 3.0423 | 3.0391 | 3.036 | 3.0329 | 3.0298 | 3.0268 | 3.0235 | 3.0202 | 3.017 | 3.0139 | 2.9824 | 2.9529 | 2.9529 | 3.0481 | 3.0472 | 3.0461 | 3.0451 | 3.044 | 3.043 | 3.042 | 3.0408 | 3.0398 | 3.0387 | 3.0376 | 3.0271 | 3.0156 | 3.0046
|  | KINLOCHLEVEN | LW |  |  |  | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.0452 | 3.0421 | 3.0384 | 3.0347 | 3.0311 | 3.0275 | 3.0239 | 3.0201 | 3.0163 | 3.0126 | 3.009 | 2.9647 | 2.9529 | 2.9529 | 3.0481 | 3.0471 | 3.0458 | 3.0446 | 3.0434 | 3.0422 | 3.041 | 3.0397 | 3.0384 | 3.0372 | 3.036 | 3.0212 | 3.0054 | 3.0046
|  | KINLOCHLEVEN | ST |  |  |  | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.0463 | 3.0453 | 3.0438 | 3.0421 | 3.0379 | 3.0337 | 3.0296 | 3.0252 | 3.0209 | 3.0167 | 3.0126 | 2.9921 | 2.9703 | 2.9529 | 3.0485 | 3.0482 | 3.0477 | 3.0471 | 3.0457 | 3.0443 | 3.0429 | 3.0414 | 3.04 | 3.0386 | 3.0372 | 3.0303 | 3.023 | 3.0158
|  | KINLOCHLEVEN | FS |  |  |  | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.2755 | 3.0469 | 3.0467 | 3.0463 | 3.0458 | 3.0444 | 3.043 | 3.0412 | 3.0395 | 3.0378 | 3.0361 | 3.0344 | 3.0266 | 3.0188 | 3.011 | 3.0487 | 3.0486 | 3.0485 | 3.0483 | 3.0479 | 3.0474 | 3.0468 | 3.0462 | 3.0456 | 3.0451 | 3.0445 | 3.0419 | 3.0393 | 3.0367
| FORT WILLIAM | KINLOCHMOIDART | MINIMUM HEADROOM | NM 71407 72091 | YES | YES | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0297 | 1.0296 | 1.0294 | 1.0292 | 1.029 | 1.0289 | 1.0288 | 1.0286 | 1.0284 | 1.0283 | 1.0281 | 1.0277 | 1.0277 | 0.99967 | 1.0345 | 1.0344 | 1.0344 | 1.0343 | 1.0343 | 1.0343 | 1.0342 | 1.0342 | 1.0341 | 1.034 | 1.034 | 1.0337 | 1.0337 | 1.0337
|  | KINLOCHMOIDART | CT |  |  |  | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0297 | 1.0296 | 1.0295 | 1.0293 | 1.0292 | 1.0291 | 1.029 | 1.0289 | 1.0289 | 1.0288 | 1.0287 | 1.0277 | 1.0277 | 1.0277 | 1.0345 | 1.0344 | 1.0344 | 1.0344 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0342 | 1.0342 | 1.0342 | 1.0337 | 1.0337 | 1.0337
|  | KINLOCHMOIDART | LW |  |  |  | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0297 | 1.0296 | 1.0294 | 1.0292 | 1.029 | 1.0289 | 1.0288 | 1.0287 | 1.0286 | 1.0285 | 1.0284 | 1.0277 | 1.0277 | 0.99967 | 1.0345 | 1.0344 | 1.0344 | 1.0343 | 1.0343 | 1.0343 | 1.0342 | 1.0342 | 1.0342 | 1.0341 | 1.0341 | 1.0337 | 1.0337 | 1.0337
|  | KINLOCHMOIDART | ST |  |  |  | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0298 | 1.0297 | 1.0297 | 1.0296 | 1.0292 | 1.029 | 1.0288 | 1.0286 | 1.0284 | 1.0283 | 1.0281 | 1.0277 | 1.0277 | 1.0277 | 1.0345 | 1.0345 | 1.0344 | 1.0344 | 1.0343 | 1.0343 | 1.0342 | 1.0342 | 1.0341 | 1.034 | 1.034 | 1.0337 | 1.0337 | 1.0337
|  | KINLOCHMOIDART | FS |  |  |  | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0531 | 1.0298 | 1.0298 | 1.0298 | 1.0298 | 1.0296 | 1.0295 | 1.0294 | 1.0292 | 1.0291 | 1.029 | 1.029 | 1.0286 | 1.0283 | 1.028 | 1.0345 | 1.0345 | 1.0345 | 1.0345 | 1.0344 | 1.0344 | 1.0344 | 1.0343 | 1.0343 | 1.0343 | 1.0343 | 1.0342 | 1.034 | 1.0339
| ELGIN | KINLOSS | MINIMUM HEADROOM | NJ 06695 61740 | NO | YES | 16.3428 | 16.341 | 16.3388 | 16.3365 | 16.3343 | 16.3321 | 16.33 | 16.3279 | 16.3258 | 16.3237 | 16.3216 | 16.3047 | 13.7739 | 13.7739 | 15.082 | 15.0709 | 15.0573 | 15.0439 | 13.78 | 13.7531 | 13.7273 | 13.701 | 13.6749 | 13.6489 | 13.6231 | 13.4163 | 12.5241 | 12.3172 | 14.794 | 14.786 | 14.7763 | 13.7966 | 13.7734 | 13.7504 | 13.7282 | 13.7057 | 13.6833 | 13.6611 | 13.639 | 13.4618 | 12.3781 | 12.1989
|  | KINLOSS | CT |  |  |  | 16.3433 | 16.3425 | 16.3416 | 16.3406 | 16.3397 | 16.3387 | 16.3378 | 16.3369 | 16.336 | 16.3351 | 16.3342 | 16.3253 | 13.7739 | 13.7739 | 15.0849 | 15.0799 | 15.0743 | 15.0686 | 15.0628 | 15.057 | 15.0514 | 15.046 | 15.0405 | 13.7893 | 13.7787 | 13.6692 | 12.8669 | 12.7595 | 14.7961 | 14.7925 | 14.7885 | 14.7844 | 14.7803 | 14.7761 | 14.7721 | 14.7682 | 13.7908 | 13.7813 | 13.7723 | 13.6784 | 12.6809 | 12.586
|  | KINLOSS | LW |  |  |  | 16.3428 | 16.341 | 16.3388 | 16.3365 | 16.3343 | 16.3321 | 16.33 | 16.3279 | 16.3258 | 16.3237 | 16.3216 | 16.3047 | 13.7739 | 13.7739 | 15.082 | 15.0709 | 15.0573 | 15.0439 | 13.78 | 13.7531 | 13.7273 | 13.701 | 13.6749 | 13.6489 | 13.6231 | 13.4163 | 12.5241 | 12.3172 | 14.794 | 14.786 | 14.7763 | 13.7966 | 13.7734 | 13.7504 | 13.7282 | 13.7057 | 13.6833 | 13.6611 | 13.639 | 13.4618 | 12.3781 | 12.1989
|  | KINLOSS | ST |  |  |  | 16.3434 | 16.3426 | 16.3415 | 16.3401 | 16.3383 | 16.3365 | 16.3347 | 16.3328 | 16.331 | 16.3292 | 16.3274 | 16.3189 | 14.1678 | 14.1678 | 15.0851 | 15.0806 | 15.0738 | 15.0657 | 15.0545 | 15.0434 | 13.7843 | 13.7615 | 13.739 | 13.7168 | 13.6952 | 13.5911 | 13.1487 | 13.0454 | 14.7963 | 14.793 | 14.7881 | 14.7823 | 14.7743 | 13.7958 | 13.7771 | 13.7576 | 13.7382 | 13.7192 | 13.7008 | 13.6116 | 13.0718 | 12.9834
|  | KINLOSS | FS |  |  |  | 16.3438 | 16.3437 | 16.3434 | 16.343 | 16.3424 | 16.3418 | 16.3411 | 16.3404 | 16.3397 | 16.339 | 16.3383 | 16.3352 | 16.3324 | 16.3297 | 15.0877 | 15.0872 | 15.0851 | 15.0828 | 15.0792 | 15.0756 | 15.0712 | 15.067 | 15.0629 | 15.0588 | 15.0548 | 13.7913 | 13.7567 | 13.7232 | 14.7981 | 14.7977 | 14.7963 | 14.7946 | 14.792 | 14.7894 | 14.7863 | 14.7833 | 14.7803 | 14.7774 | 14.7745 | 13.783 | 13.7534 | 13.7247
| BRACO | KIPPEN | MINIMUM HEADROOM | NS 66376 95628 | NO | YES | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.6285 | 10.6285 | 7.6258 | 9.3653 | 9.3145 | 9.2504 | 9.1996 | 9.1933 | 9.187 | 7.3245 | 7.192 | 7.0554 | 6.9189 | 6.7807 | 6.1282 | 5.528 | 4.9301 | 9.8295 | 9.8209 | 9.8111 | 9.8111 | 9.8111 | 9.8111 | 9.8111 | 9.8111 | 9.8111 | 9.8111 | 9.8111 | 6.7925 | 6.1851 | 5.5802
|  | KIPPEN | CT |  |  |  | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.6285 | 10.6285 | 10.6285 | 9.3682 | 9.3294 | 9.2832 | 9.2359 | 9.1998 | 9.1951 | 9.1905 | 9.1855 | 7.3175 | 7.2168 | 7.1144 | 6.6232 | 6.1863 | 5.75 | 9.83 | 9.8234 | 9.8157 | 9.8111 | 9.8111 | 9.8111 | 9.8111 | 9.8111 | 9.8111 | 9.8111 | 9.8111 | 7.2933 | 6.8512 | 6.4097
|  | KIPPEN | LW |  |  |  | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.6285 | 10.6285 | 7.6258 | 9.3653 | 9.3145 | 9.2504 | 9.1996 | 9.1933 | 9.187 | 7.3245 | 7.192 | 7.0554 | 6.9189 | 6.7807 | 6.1282 | 5.528 | 4.9301 | 9.8295 | 9.8209 | 9.8111 | 9.8111 | 9.8111 | 9.8111 | 9.8111 | 9.8111 | 9.8111 | 9.8111 | 9.8111 | 6.7925 | 6.1851 | 5.5802
|  | KIPPEN | ST |  |  |  | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.6664 | 10.6664 | 10.6664 | 9.3814 | 9.364 | 9.3363 | 9.3024 | 9.2762 | 9.2493 | 9.2231 | 9.2005 | 9.1977 | 9.1949 | 9.192 | 7.2203 | 6.9332 | 6.6514 | 9.8322 | 9.8293 | 9.8246 | 9.8189 | 9.8145 | 9.8111 | 9.8111 | 9.8111 | 9.8111 | 9.8111 | 9.8111 | 9.7733 | 9.7733 | 7.3305
|  | KIPPEN | FS |  |  |  | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 10.7043 | 9.3918 | 9.39 | 9.382 | 9.3723 | 9.3636 | 9.3547 | 9.3441 | 9.3333 | 9.322 | 9.3107 | 9.2993 | 9.2394 | 9.199 | 9.1932 | 9.8339 | 9.8336 | 9.8323 | 9.8306 | 9.8292 | 9.8277 | 9.8259 | 9.8241 | 9.8222 | 9.8203 | 9.8184 | 9.8111 | 9.8111 | 9.8111
| THURSO | KIRKWALL | MINIMUM HEADROOM | HY 44669 10987 | NO | YES | 33.4632 | 33.4538 | 33.4421 | 33.4304 | 33.4186 | 33.4075 | 33.3967 | 33.3836 | 33.3713 | 33.3594 | 33.3468 | 23.5768 | 22.5773 | 21.5796 | 30.4129 | 30.3638 | 30.3024 | 30.2413 | 30.1797 | 30.1219 | 30.0653 | 29.9971 | 29.9327 | 29.8705 | 29.8046 | 21.4371 | 20.2636 | 19.0922 | 29.126 | 29.0999 | 29.0674 | 29.035 | 29.0023 | 28.9716 | 28.9416 | 28.9054 | 28.8712 | 28.8382 | 28.8032 | 23.0681 | 21.9251 | 20.7841
|  | KIRKWALL | CT |  |  |  | 33.4634 | 33.4556 | 33.4464 | 33.4372 | 33.4279 | 33.4193 | 33.4108 | 33.4005 | 33.3908 | 33.3815 | 33.3716 | 31.4531 | 23.3556 | 22.6161 | 30.414 | 30.3731 | 30.3252 | 30.2771 | 30.2284 | 30.1833 | 30.1391 | 30.0853 | 30.0347 | 29.986 | 29.9341 | 22.0454 | 21.1774 | 20.3091 | 29.1266 | 29.1049 | 29.0795 | 29.0539 | 29.0281 | 29.0041 | 28.9807 | 28.9522 | 28.9253 | 28.8995 | 28.8719 | 23.2659 | 22.8151 | 21.9694
|  | KIRKWALL | LW |  |  |  | 33.4632 | 33.4538 | 33.4421 | 33.4304 | 33.4186 | 33.4075 | 33.3967 | 33.3836 | 33.3713 | 33.3594 | 33.3468 | 23.5768 | 22.5773 | 21.5796 | 30.4129 | 30.3638 | 30.3024 | 30.2413 | 30.1797 | 30.1219 | 30.0653 | 29.9971 | 29.9327 | 29.8705 | 29.8046 | 21.4371 | 20.2636 | 19.0922 | 29.126 | 29.0999 | 29.0674 | 29.035 | 29.0023 | 28.9716 | 28.9416 | 28.9054 | 28.8712 | 28.8382 | 28.8032 | 23.0681 | 21.9251 | 20.7841
|  | KIRKWALL | ST |  |  |  | 34.2313 | 33.4639 | 33.4593 | 33.4538 | 33.4449 | 33.4365 | 33.4283 | 33.4186 | 33.4095 | 33.4006 | 33.3915 | 32.423 | 32.3797 | 32.3363 | 30.8396 | 30.4164 | 30.3926 | 30.364 | 30.3173 | 30.2733 | 30.2304 | 30.1799 | 30.1321 | 30.086 | 30.038 | 23.3657 | 22.8347 | 22.3018 | 29.8413 | 29.1279 | 29.1153 | 29.1001 | 29.0753 | 29.052 | 29.0292 | 29.0024 | 28.977 | 28.9525 | 28.9271 | 27.9509 | 27.8309 | 27.7106
|  | KIRKWALL | FS |  |  |  | 34.2333 | 34.233 | 34.2315 | 34.2299 | 34.227 | 34.2242 | 34.2207 | 34.217 | 34.2135 | 34.2101 | 34.2066 | 34.1897 | 34.1738 | 34.1582 | 30.8501 | 30.8481 | 30.8406 | 30.8321 | 30.8168 | 30.8024 | 30.7841 | 30.7647 | 30.7463 | 30.7285 | 30.7101 | 30.622 | 30.5388 | 30.4574 | 29.8469 | 29.8458 | 29.8419 | 29.8373 | 29.8292 | 29.8216 | 29.8119 | 29.8016 | 29.7918 | 29.7824 | 29.7726 | 29.7258 | 29.6817 | 29.6385
| BROADFORD | KISHORNHILL | MINIMUM HEADROOM | NG 88304 40591 | YES | YES | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 0.94682 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 0.96367 | 0.80502 | 1.7947 | 1.7935 | 1.7919 | 1.7904 | 1.7889 | 1.7873 | 1.7843 | 1.7811 | 1.7779 | 1.7748 | 1.7718 | 1.744 | 0.97906 | 0.82667
|  | KISHORNHILL | CT |  |  |  | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 0.90074 | 1.7948 | 1.7938 | 1.7928 | 1.7917 | 1.7907 | 1.7897 | 1.7887 | 1.7876 | 1.7865 | 1.7854 | 1.7843 | 1.7542 | 1.7235 | 0.91861
|  | KISHORNHILL | LW |  |  |  | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 0.94682 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 0.96367 | 0.80502 | 1.7947 | 1.7935 | 1.7919 | 1.7904 | 1.7889 | 1.7875 | 1.786 | 1.7845 | 1.7829 | 1.7814 | 1.7799 | 1.744 | 0.97906 | 0.82667
|  | KISHORNHILL | ST |  |  |  | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.7951 | 1.7947 | 1.7941 | 1.7935 | 1.7903 | 1.7873 | 1.7843 | 1.7811 | 1.7779 | 1.7748 | 1.7718 | 1.7568 | 1.7418 | 1.7269
|  | KISHORNHILL | FS |  |  |  | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.3535 | 1.7953 | 1.7953 | 1.7951 | 1.7949 | 1.7939 | 1.7929 | 1.7916 | 1.7903 | 1.789 | 1.7878 | 1.7866 | 1.7807 | 1.7753 | 1.7701
| BROADFORD | KYLE | MINIMUM HEADROOM | NG 76499 27247 | NO | YES | 7.7091 | 7.5766 | 7.4486 | 7.3252 | 7.2062 | 7.092 | 6.9823 | 6.2978 | 6.2716 | 6.2456 | 6.2201 | 6.0935 | 5.8821 | 5.6556 | 7.342 | 7.2414 | 7.1441 | 7.0557 | 6.9727 | 6.8929 | 6.8164 | 6.2513 | 6.2204 | 6.1897 | 6.1596 | 5.9456 | 5.7345 | 5.5214 | 7.3532 | 7.2341 | 7.1191 | 7.0082 | 6.2411 | 6.1051 | 5.9744 | 5.9063 | 5.8686 | 5.8313 | 5.7946 | 5.5474 | 5.3047 | 5.0591
|  | KYLE | CT |  |  |  | 7.7091 | 7.5766 | 7.4486 | 7.3252 | 7.2062 | 7.092 | 6.9823 | 6.2978 | 6.2716 | 6.2456 | 6.2201 | 6.0935 | 5.8821 | 5.6556 | 7.342 | 7.2414 | 7.1441 | 7.0557 | 6.9727 | 6.8929 | 6.8164 | 6.2513 | 6.2204 | 6.1897 | 6.1596 | 5.9456 | 5.7345 | 5.5214 | 7.3532 | 7.2341 | 7.1191 | 7.0082 | 6.2411 | 6.1051 | 5.9744 | 5.9063 | 5.8686 | 5.8313 | 5.7946 | 5.5474 | 5.3047 | 5.0591
|  | KYLE | LW |  |  |  | 7.9423 | 7.9218 | 7.8987 | 7.8733 | 7.8459 | 7.8167 | 7.7859 | 7.7559 | 7.7251 | 7.6937 | 7.6619 | 7.4865 | 7.3062 | 6.2754 | 7.5164 | 7.4991 | 7.4797 | 7.4586 | 7.436 | 7.4121 | 7.387 | 7.3624 | 7.3372 | 7.3115 | 7.2856 | 7.1436 | 6.2732 | 5.9694 | 7.5639 | 7.5461 | 7.526 | 7.5038 | 7.4798 | 7.4542 | 7.4271 | 7.4009 | 7.3738 | 7.3462 | 7.3182 | 7.1701 | 6.0255 | 5.6739
|  | KYLE | ST |  |  |  | 7.9767 | 7.9686 | 7.9606 | 7.9527 | 7.9426 | 7.9328 | 7.9232 | 7.9138 | 7.9006 | 7.8877 | 7.8752 | 7.8154 | 7.7608 | 7.7069 | 7.5436 | 7.5369 | 7.5301 | 7.5231 | 7.5129 | 7.503 | 7.4934 | 7.4837 | 7.4712 | 7.459 | 7.4472 | 7.3902 | 7.3368 | 7.2924 | 7.5945 | 7.5874 | 7.5805 | 7.5737 | 7.5655 | 7.5575 | 7.5498 | 7.5423 | 7.5313 | 7.5206 | 7.5102 | 7.4607 | 7.4158 | 7.3717
|  | KYLE | FS |  |  |  | 7.9693 | 7.9614 | 7.9496 | 7.9379 | 7.9263 | 7.9147 | 7.9032 | 7.8919 | 7.8808 | 7.8698 | 7.859 | 7.7946 | 7.7359 | 7.6811 | 7.539 | 7.533 | 7.5238 | 7.5148 | 7.5052 | 7.4957 | 7.486 | 7.4765 | 7.4671 | 7.4579 | 7.4488 | 7.3959 | 7.3475 | 7.3021 | 7.5874 | 7.5803 | 7.5697 | 7.5594 | 7.5491 | 7.539 | 7.529 | 7.5192 | 7.5095 | 7.5 | 7.4905 | 7.4341 | 7.3828 | 7.3348
| LAIRG | LAIRG | MINIMUM HEADROOM | NC 58798 07111 | YES | YES | 1.5347 | 0.99209 | 0.83621 | 0.68559 | 0.54025 | 0.40018 | 0.26539 | 0.19219 | 0.1486 | 0.10539 | 0.062732 | -0.14594 | -0.34748 | -0.55211 | 0.97196 | 0.83796 | 0.70579 | 0.57792 | 0.45439 | 0.33518 | 0.2203 | 0.15411 | 0.11167 | 0.069555 | 0.027945 | -0.17483 | -0.37277 | -0.57246 | 0.99157 | 0.82842 | 0.66819 | 0.51326 | 0.36367 | 0.21942 | 0.080495 | 0.0027306 | -0.045425 | -0.093187 | -0.14036 | -0.37066 | -0.59436 | -0.8206
|  | LAIRG | CT |  |  |  | 1.5347 | 0.99209 | 0.83621 | 0.68559 | 0.54025 | 0.40018 | 0.26539 | 0.19219 | 0.1486 | 0.10539 | 0.062732 | -0.14594 | -0.34748 | -0.55211 | 0.97196 | 0.83796 | 0.70579 | 0.57792 | 0.45439 | 0.33518 | 0.2203 | 0.15411 | 0.11167 | 0.069555 | 0.027945 | -0.17483 | -0.37277 | -0.57246 | 0.99157 | 0.82842 | 0.66819 | 0.51326 | 0.36367 | 0.21942 | 0.080495 | 0.0027306 | -0.045425 | -0.093187 | -0.14036 | -0.37066 | -0.59436 | -0.8206
|  | LAIRG | LW |  |  |  | 1.7632 | 1.7438 | 1.722 | 1.698 | 1.672 | 1.6442 | 1.6148 | 1.5866 | 1.5576 | 1.528 | 1.498 | 0.79623 | 0.52748 | 0.24442 | 1.5076 | 1.4916 | 1.4734 | 1.4535 | 1.4322 | 1.4095 | 1.3858 | 0.97562 | 0.94213 | 0.90752 | 0.87263 | 0.61789 | 0.35806 | 0.087734 | 1.5413 | 1.5234 | 1.5031 | 1.4809 | 1.4568 | 1.4311 | 1.404 | 1.378 | 0.96721 | 0.92591 | 0.88427 | 0.5941 | 0.29846 | -0.010957
|  | LAIRG | ST |  |  |  | 1.7963 | 1.7886 | 1.7811 | 1.7738 | 1.7649 | 1.7563 | 1.7479 | 1.7397 | 1.7278 | 1.7162 | 1.705 | 1.6518 | 1.6038 | 1.5571 | 1.5326 | 1.5265 | 1.5202 | 1.514 | 1.5047 | 1.4956 | 1.4868 | 1.478 | 1.4664 | 1.4551 | 1.4441 | 0.95842 | 0.86628 | 0.77547 | 1.5714 | 1.5644 | 1.5574 | 1.5506 | 1.5418 | 1.5334 | 1.5251 | 1.5171 | 1.5056 | 1.4944 | 1.4836 | 1.4322 | 0.91078 | 0.81074
|  | LAIRG | FS |  |  |  | 1.7886 | 1.7809 | 1.7695 | 1.7582 | 1.7471 | 1.7361 | 1.7253 | 1.7147 | 1.7042 | 1.6938 | 1.6836 | 1.6224 | 1.5671 | 1.5155 | 1.5272 | 1.5214 | 1.5128 | 1.5042 | 1.4951 | 1.4861 | 1.4769 | 1.4679 | 1.4591 | 1.4503 | 1.4417 | 1.3913 | 0.94818 | 0.88535 | 1.5645 | 1.5575 | 1.5472 | 1.5369 | 1.5266 | 1.5165 | 1.5064 | 1.4965 | 1.4867 | 1.4771 | 1.4676 | 1.4109 | 0.9759 | 0.90096
| MYBSTER | LATHERON | MINIMUM HEADROOM | ND 19924 33627 | YES | YES | 4.1495 | 2.9158 | 2.7429 | 2.5762 | 2.4157 | 2.2613 | 2.1132 | 2.0348 | 1.9958 | 1.9573 | 1.9193 | 1.5403 | 0.93596 | 0.5743 | 3.7329 | 2.8329 | 2.6408 | 2.4547 | 2.2747 | 2.1008 | 1.9328 | 1.8228 | 1.7475 | 1.6727 | 1.5989 | 1.1949 | 0.66199 | 0.32089 | 3.9384 | 2.9536 | 2.7184 | 2.4907 | 2.2708 | 2.0585 | 1.8538 | 1.7256 | 1.6425 | 1.5601 | 1.4788 | 1.0115 | 0.37776 | -0.0071831
|  | LATHERON | CT |  |  |  | 4.1495 | 2.9158 | 2.7429 | 2.5762 | 2.4157 | 2.2613 | 2.1132 | 2.0348 | 1.9958 | 1.9573 | 1.9193 | 1.5403 | 0.93596 | 0.5743 | 3.7329 | 2.8329 | 2.6408 | 2.4547 | 2.2747 | 2.1008 | 1.9328 | 1.8228 | 1.7475 | 1.6727 | 1.5989 | 1.1949 | 0.66199 | 0.32089 | 3.9384 | 2.9536 | 2.7184 | 2.4907 | 2.2708 | 2.0585 | 1.8538 | 1.7256 | 1.6425 | 1.5601 | 1.4788 | 1.0115 | 0.37776 | -0.0071831
|  | LATHERON | LW |  |  |  | 4.4797 | 4.4478 | 4.4115 | 4.372 | 4.3297 | 4.285 | 4.238 | 4.1886 | 4.1379 | 4.0863 | 4.0341 | 2.704 | 2.0555 | 1.5499 | 3.9111 | 3.8931 | 3.8726 | 3.8503 | 3.8262 | 2.9977 | 2.9306 | 2.8592 | 2.7868 | 2.7139 | 2.6408 | 2.1587 | 1.5297 | 1.0686 | 4.2415 | 4.2147 | 4.1844 | 4.1511 | 4.115 | 4.0764 | 4.0357 | 3.9929 | 2.974 | 2.8915 | 2.8088 | 2.2539 | 1.5092 | 0.98174
|  | LATHERON | ST |  |  |  | 4.5288 | 4.5166 | 4.5041 | 4.4915 | 4.4763 | 4.4614 | 4.447 | 4.4324 | 4.4124 | 4.3929 | 4.3739 | 4.2335 | 4.0247 | 2.9377 | 3.9401 | 3.9331 | 3.926 | 3.919 | 3.9105 | 3.9022 | 3.8942 | 3.8861 | 3.8748 | 3.8637 | 3.853 | 2.8993 | 2.6537 | 2.5038 | 4.2875 | 4.2768 | 4.2664 | 4.2562 | 4.2439 | 4.2319 | 4.2203 | 4.2087 | 4.1918 | 4.1754 | 4.1594 | 4.0357 | 2.817 | 2.652
|  | LATHERON | FS |  |  |  | 4.5183 | 4.5072 | 4.4902 | 4.4734 | 4.4565 | 4.4398 | 4.4231 | 4.4067 | 4.3905 | 4.3745 | 4.3588 | 4.2657 | 4.1771 | 4.0931 | 3.9337 | 3.927 | 3.917 | 3.9071 | 3.8973 | 3.8876 | 3.8779 | 3.8684 | 3.859 | 3.8497 | 3.8406 | 3.7863 | 2.9538 | 2.8572 | 4.2768 | 4.2661 | 4.2503 | 4.2346 | 4.2192 | 4.204 | 4.189 | 4.1742 | 4.1596 | 4.1453 | 4.1311 | 4.0462 | 3.9654 | 3.8888
| FIDDES | LAURENCEKIRK | MINIMUM HEADROOM | NO 70915 71028 | NO | YES | 18.375 | 18.375 | 18.375 | 18.375 | 18.375 | 18.375 | 18.375 | 18.375 | 18.375 | 18.375 | 18.375 | 14.4321 | 13.503 | 13.0427 | 17.0908 | 17.0427 | 16.983 | 16.9234 | 16.8641 | 16.8049 | 16.7467 | 16.6839 | 16.6256 | 16.5928 | 13.6977 | 12.296 | 11.3934 | 10.8374 | 15.2839 | 15.2839 | 15.2839 | 15.2839 | 15.2839 | 15.2839 | 13.7341 | 13.6249 | 13.5134 | 13.3905 | 13.2686 | 11.5752 | 10.5654 | 10.0251
|  | LAURENCEKIRK | CT |  |  |  | 18.375 | 18.375 | 18.375 | 18.375 | 18.375 | 18.375 | 18.375 | 18.375 | 18.375 | 18.375 | 18.375 | 17.3299 | 14.0214 | 13.6842 | 17.093 | 17.0556 | 17.0122 | 16.9689 | 16.9256 | 16.8823 | 16.8396 | 16.7936 | 16.7486 | 16.703 | 16.6579 | 12.7708 | 12.0196 | 11.6122 | 15.2839 | 15.2839 | 15.2839 | 15.2839 | 15.2839 | 15.2839 | 15.2839 | 15.2839 | 13.7373 | 13.6582 | 13.5797 | 12.0366 | 11.174 | 10.7781
|  | LAURENCEKIRK | LW |  |  |  | 18.375 | 18.375 | 18.375 | 18.375 | 18.375 | 18.375 | 18.375 | 18.375 | 18.375 | 18.375 | 18.375 | 14.4321 | 13.503 | 13.0427 | 17.0908 | 17.0427 | 16.983 | 16.9234 | 16.8641 | 16.8049 | 16.7467 | 16.6839 | 16.6256 | 16.5928 | 13.6977 | 12.296 | 11.3934 | 10.8374 | 15.2839 | 15.2839 | 15.2839 | 15.2839 | 15.2839 | 15.2839 | 13.7341 | 13.6249 | 13.5134 | 13.3905 | 13.2686 | 11.5752 | 10.5654 | 10.0251
|  | LAURENCEKIRK | ST |  |  |  | 18.375 | 18.375 | 18.375 | 18.375 | 18.375 | 18.375 | 18.375 | 18.375 | 18.375 | 18.375 | 18.375 | 17.8525 | 17.6434 | 17.6434 | 17.1047 | 17.0876 | 17.0609 | 17.0286 | 17.003 | 16.9774 | 16.9523 | 16.9251 | 16.8988 | 16.8723 | 16.8463 | 13.7277 | 13.3069 | 13.0582 | 15.2839 | 15.2839 | 15.2839 | 15.2839 | 15.2839 | 15.2839 | 15.2839 | 15.2839 | 15.2839 | 15.2839 | 15.2839 | 13.108 | 12.657 | 12.4153
|  | LAURENCEKIRK | FS |  |  |  | 18.375 | 18.375 | 18.375 | 18.375 | 18.375 | 18.375 | 18.375 | 18.375 | 18.375 | 18.375 | 18.375 | 18.375 | 18.375 | 18.375 | 17.1635 | 17.162 | 17.1541 | 17.1446 | 17.1363 | 17.1279 | 17.1173 | 17.1069 | 17.0968 | 17.0867 | 17.0767 | 17.0286 | 16.983 | 16.94 | 15.284 | 15.2839 | 15.2839 | 15.2839 | 15.2839 | 15.2839 | 15.2839 | 15.2839 | 15.2839 | 15.2839 | 15.2839 | 15.2839 | 15.2839 | 15.2839
| STORNOWAY | LAXAY | MINIMUM HEADROOM | NB 33424 21925 | YES | YES | 1.7947 | 1.6704 | 0.96397 | 0.85137 | 0.71128 | 0.56913 | 0.43216 | 0.35524 | 0.30473 | 0.25464 | 0.20508 | -0.06769 | -0.37345 | -0.63238 | 1.7443 | 1.6691 | 0.95118 | 0.81606 | 0.68534 | 0.55897 | 0.43695 | 0.36143 | 0.30693 | 0.25285 | 0.19929 | -0.087485 | -0.40091 | -0.67563 | 1.5044 | 1.3855 | 0.85935 | 0.69925 | 0.54448 | 0.39502 | 0.25088 | 0.1661 | 0.10774 | 0.04986 | -0.0074451 | -0.31097 | -0.64748 | -0.93622
|  | LAXAY | CT |  |  |  | 1.7947 | 1.6704 | 0.96397 | 0.85137 | 0.71128 | 0.56913 | 0.43216 | 0.35524 | 0.30473 | 0.25464 | 0.20508 | -0.06769 | -0.37345 | -0.63238 | 1.7443 | 1.6691 | 0.95118 | 0.81606 | 0.68534 | 0.55897 | 0.43695 | 0.36143 | 0.30693 | 0.25285 | 0.19929 | -0.087485 | -0.40091 | -0.67563 | 1.5044 | 1.3855 | 0.85935 | 0.69925 | 0.54448 | 0.39502 | 0.25088 | 0.1661 | 0.10774 | 0.04986 | -0.0074451 | -0.31097 | -0.64748 | -0.93622
|  | LAXAY | LW |  |  |  | 2.0147 | 1.996 | 1.9751 | 1.9519 | 1.9269 | 1.9001 | 1.8719 | 1.8461 | 1.8196 | 1.7925 | 1.7651 | 0.75255 | 0.36261 | 0.019998 | 1.9033 | 1.8832 | 1.86 | 1.8394 | 1.8243 | 1.8081 | 1.791 | 1.7754 | 1.7594 | 0.98514 | 0.93255 | 0.5715 | 0.17754 | -0.17865 | 1.719 | 1.6954 | 1.6696 | 1.6456 | 1.6199 | 1.5926 | 1.564 | 1.5375 | 1.5103 | 0.96324 | 0.90508 | 0.52058 | 0.093417 | -0.28536
|  | LAXAY | ST |  |  |  | 2.0466 | 2.0392 | 2.0319 | 2.0249 | 2.0163 | 2.008 | 1.9999 | 1.9923 | 1.9811 | 1.9703 | 1.9598 | 1.9109 | 1.848 | 1.8089 | 1.93 | 1.9241 | 1.9182 | 1.9123 | 1.9007 | 1.8894 | 1.8784 | 1.8673 | 1.8571 | 1.8505 | 1.8441 | 1.8146 | 0.95976 | 0.83097 | 1.7548 | 1.7467 | 1.7386 | 1.7307 | 1.7185 | 1.7065 | 1.6949 | 1.6841 | 1.672 | 1.6602 | 1.6488 | 1.5953 | 0.95871 | 0.8259
|  | LAXAY | FS |  |  |  | 2.0392 | 2.0317 | 2.0208 | 2.0099 | 1.9992 | 1.9887 | 1.9783 | 1.968 | 1.9579 | 1.9479 | 1.9381 | 1.8792 | 1.8268 | 1.7783 | 1.9246 | 1.9189 | 1.9099 | 1.9009 | 1.8912 | 1.8817 | 1.8718 | 1.862 | 1.8524 | 1.8429 | 1.8335 | 1.7954 | 1.7638 | 1.7344 | 1.7469 | 1.7389 | 1.7267 | 1.7146 | 1.7021 | 1.6898 | 1.6774 | 1.6652 | 1.6551 | 1.6451 | 1.6353 | 1.5771 | 1.5253 | 1.4772
| COUPAR ANGUS | LEOCH | MINIMUM HEADROOM | NO 35945 36287 | YES | YES | 0.31214 | -0.0052747 | -0.31075 | -0.6053 | -0.88892 | -1.1616 | -1.4234 | -1.5264 | -1.6171 | -1.7348 | -1.8514 | -3.6484 | -4.8254 | -5.262 | 0.57576 | 0.39965 | 0.089539 | -0.25536 | -0.5888 | -0.91082 | -1.2214 | -1.3895 | -1.5088 | -1.6272 | -1.7444 | -3.2902 | -4.3351 | -4.78 | -0.047712 | -0.45281 | -0.85734 | -1.2706 | -1.67 | -2.0556 | -2.4273 | -2.6227 | -2.7583 | -2.8928 | -3.0259 | -4.8831 | -6.1237 | -6.6265
|  | LEOCH | CT |  |  |  | 0.31214 | -0.0052747 | -0.31075 | -0.6053 | -0.88892 | -1.1616 | -1.4234 | -1.5264 | -1.6171 | -1.7348 | -1.8514 | -3.6484 | -4.8254 | -5.262 | 0.57576 | 0.39965 | 0.089539 | -0.25536 | -0.5888 | -0.91082 | -1.2214 | -1.3895 | -1.5088 | -1.6272 | -1.7444 | -3.2902 | -4.3351 | -4.78 | -0.047712 | -0.45281 | -0.85734 | -1.2706 | -1.67 | -2.0556 | -2.4273 | -2.6227 | -2.7583 | -2.8928 | -3.0259 | -4.8831 | -6.1237 | -6.6265
|  | LEOCH | LW |  |  |  | 0.8738 | 0.82622 | 0.77264 | 0.71359 | 0.64963 | 0.5813 | 0.50915 | 0.4528 | 0.29242 | 0.11857 | -0.055616 | -2.0331 | -3.3923 | -4.02 | 0.88036 | 0.85455 | 0.82549 | 0.79347 | 0.62614 | 0.44225 | 0.257 | 0.076764 | -0.10428 | -0.28569 | -0.46717 | -2.197 | -3.4272 | -4.064 | 0.57957 | 0.45202 | 0.26522 | 0.063652 | -0.14112 | -0.34854 | -0.55798 | -0.75973 | -0.9626 | -1.166 | -1.3697 | -3.4348 | -4.8849 | -5.6059
|  | LEOCH | ST |  |  |  | 0.95525 | 0.9363 | 0.91785 | 0.89988 | 0.87803 | 0.8568 | 0.83618 | 0.81616 | 0.78693 | 0.7585 | 0.73087 | 0.066357 | -0.35259 | -0.58394 | 0.92453 | 0.91425 | 0.90424 | 0.8945 | 0.88265 | 0.87113 | 0.85995 | 0.84909 | 0.83324 | 0.81782 | 0.80284 | 0.01425 | -0.54582 | -0.78991 | 0.69505 | 0.65045 | 0.59359 | 0.53028 | 0.47477 | 0.41181 | 0.35041 | 0.28672 | 0.21315 | 0.14117 | 0.070812 | -0.8832 | -1.5447 | -1.8174
|  | LEOCH | FS |  |  |  | 0.9363 | 0.91735 | 0.8893 | 0.86162 | 0.8343 | 0.80736 | 0.78079 | 0.75459 | 0.72877 | 0.70331 | 0.67822 | 0.52781 | 0.41146 | 0.30805 | 0.91425 | 0.90398 | 0.88876 | 0.87375 | 0.85894 | 0.84433 | 0.82992 | 0.81571 | 0.8017 | 0.7879 | 0.77429 | 0.69272 | 0.62962 | 0.51419 | 0.68655 | 0.66328 | 0.62106 | 0.57735 | 0.53785 | 0.49886 | 0.45795 | 0.41764 | 0.37795 | 0.33887 | 0.30042 | 0.073361 | -0.12802 | -0.31113
| NAIRN | LETHEN | MINIMUM HEADROOM | NH 92307 50795 | YES | YES | 2.9145 | 2.8093 | 2.7097 | 1.8881 | 0.95517 | 0.84584 | 0.74072 | 0.68902 | 0.65928 | 0.62982 | 0.60077 | 0.38444 | 0.21486 | 0.04399 | 2.5241 | 2.455 | 2.3887 | 1.9671 | 1.2158 | 1.1244 | 1.0365 | 0.9915 | 0.96433 | 0.9374 | 0.91083 | 0.7049 | 0.53619 | 0.36863 | 2.72 | 2.6143 | 2.5139 | 1.9088 | 0.96139 | 0.84979 | 0.74248 | 0.68932 | 0.65846 | 0.62789 | 0.59773 | 0.37144 | 0.19246 | 0.014404
|  | LETHEN | CT |  |  |  | 2.9145 | 2.8093 | 2.7097 | 1.8881 | 0.95517 | 0.84584 | 0.74072 | 0.68902 | 0.65928 | 0.62982 | 0.60077 | 0.38444 | 0.21486 | 0.04399 | 2.5241 | 2.455 | 2.3887 | 1.9671 | 1.2158 | 1.1244 | 1.0365 | 0.9915 | 0.96433 | 0.9374 | 0.91083 | 0.7049 | 0.53619 | 0.36863 | 2.72 | 2.6143 | 2.5139 | 1.9088 | 0.96139 | 0.84979 | 0.74248 | 0.68932 | 0.65846 | 0.62789 | 0.59773 | 0.37144 | 0.19246 | 0.014404
|  | LETHEN | LW |  |  |  | 3.0993 | 3.0827 | 3.0639 | 3.0433 | 1.5182 | 1.4809 | 1.4425 | 1.4062 | 1.3692 | 1.3318 | 1.2942 | 1.0038 | 0.75333 | 0.49527 | 2.6372 | 2.6208 | 2.6017 | 2.5817 | 1.6656 | 1.6311 | 1.5957 | 1.5617 | 1.5272 | 1.4924 | 1.4574 | 1.1764 | 0.92273 | 0.66964 | 2.9032 | 2.8848 | 2.8638 | 2.8411 | 1.5315 | 1.4928 | 1.4528 | 1.415 | 1.3765 | 1.3375 | 1.2983 | 0.99358 | 0.72724 | 0.44618
|  | LETHEN | ST |  |  |  | 3.1264 | 3.1199 | 3.1134 | 3.107 | 3.0987 | 3.0906 | 3.0828 | 3.0751 | 3.0646 | 3.0543 | 3.0442 | 2.9861 | 2.95 | 2.9178 | 2.6559 | 2.65 | 2.6432 | 2.6359 | 2.6235 | 2.6115 | 2.5998 | 2.5876 | 2.5738 | 2.5602 | 2.547 | 2.4879 | 2.4681 | 1.9556 | 2.9307 | 2.9236 | 2.9163 | 2.9089 | 2.8984 | 2.8883 | 2.8783 | 2.8685 | 2.8557 | 2.8433 | 2.8312 | 2.7607 | 2.7098 | 2.6627
|  | LETHEN | FS |  |  |  | 3.1231 | 3.1168 | 3.1075 | 3.0982 | 3.0889 | 3.0797 | 3.0705 | 3.0614 | 3.0525 | 3.0437 | 3.035 | 2.9835 | 2.9388 | 2.8976 | 2.6755 | 2.6701 | 2.6622 | 2.6556 | 2.6476 | 2.6397 | 2.6311 | 2.6227 | 2.6144 | 2.6063 | 2.5983 | 2.5538 | 2.5143 | 2.4776 | 2.9332 | 2.9269 | 2.9174 | 2.9079 | 2.898 | 2.8881 | 2.8781 | 2.8683 | 2.8586 | 2.849 | 2.8395 | 2.7846 | 2.7365 | 2.6921
| GRUDIE BRIDGE | LETTEREWE | MINIMUM HEADROOM | NG 93546 70082 | YES | YES | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10275 | 0.10272 | 0.10269 | 0.10265 | 0.10262 | 0.10259 | 0.10257 | 0.10254 | 0.10251 | 0.10249 | 0.10248 | 0.10246 | 0.10246 | 0.10246 | 0.10311 | 0.10309 | 0.10308 | 0.10306 | 0.10306 | 0.10306 | 0.10306 | 0.10306 | 0.10306 | 0.10306 | 0.10306 | 0.10306 | 0.10306 | 0.10306
|  | LETTEREWE | CT |  |  |  | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10275 | 0.10273 | 0.10271 | 0.10268 | 0.10266 | 0.10264 | 0.10262 | 0.10259 | 0.10257 | 0.10256 | 0.10254 | 0.10248 | 0.10246 | 0.10246 | 0.10311 | 0.1031 | 0.10309 | 0.10307 | 0.10306 | 0.10306 | 0.10306 | 0.10306 | 0.10306 | 0.10306 | 0.10306 | 0.10306 | 0.10306 | 0.10306
|  | LETTEREWE | LW |  |  |  | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10275 | 0.10272 | 0.10269 | 0.10265 | 0.10262 | 0.10259 | 0.10257 | 0.10254 | 0.10251 | 0.10249 | 0.10248 | 0.10246 | 0.10246 | 0.10246 | 0.10311 | 0.10309 | 0.10308 | 0.10306 | 0.10306 | 0.10306 | 0.10306 | 0.10306 | 0.10306 | 0.10306 | 0.10306 | 0.10306 | 0.10306 | 0.10306
|  | LETTEREWE | ST |  |  |  | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10276 | 0.10275 | 0.10274 | 0.10272 | 0.10271 | 0.10269 | 0.10268 | 0.10266 | 0.10265 | 0.10263 | 0.10262 | 0.10256 | 0.1025 | 0.10248 | 0.10311 | 0.10311 | 0.1031 | 0.10309 | 0.10309 | 0.10308 | 0.10307 | 0.10306 | 0.10306 | 0.10306 | 0.10306 | 0.10306 | 0.10306 | 0.10306
|  | LETTEREWE | FS |  |  |  | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10458 | 0.10276 | 0.10276 | 0.10276 | 0.10275 | 0.10275 | 0.10274 | 0.10274 | 0.10273 | 0.10273 | 0.10272 | 0.10271 | 0.10268 | 0.10266 | 0.10263 | 0.10311 | 0.10311 | 0.10311 | 0.10311 | 0.10311 | 0.1031 | 0.1031 | 0.1031 | 0.10309 | 0.10309 | 0.10309 | 0.10307 | 0.10306 | 0.10306
| ELGIN | LHANBRYDE | MINIMUM HEADROOM | NJ 27940 61640 | NO | YES | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 4.985 | 4.9534 | 4.7799 | 4.6006 | 4.425 | 5.7385 | 5.7099 | 5.6846 | 5.6601 | 4.9612 | 4.9224 | 4.8843 | 4.8428 | 4.8014 | 4.7607 | 4.7201 | 4.4975 | 4.2674 | 4.0422 | 5.6502 | 5.6502 | 5.6502 | 4.982 | 4.9454 | 4.9094 | 4.8741 | 4.8356 | 4.7973 | 4.7595 | 4.7219 | 4.5155 | 4.3022 | 4.0934
|  | LHANBRYDE | CT |  |  |  | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 4.9217 | 4.7965 | 4.6738 | 5.7413 | 5.719 | 5.7019 | 5.6848 | 5.6671 | 4.9814 | 4.9515 | 4.9212 | 4.8918 | 4.8634 | 4.8351 | 4.6794 | 4.5188 | 4.3614 | 5.6502 | 5.6502 | 5.6502 | 5.6502 | 4.9927 | 4.9641 | 4.9364 | 4.9083 | 4.8811 | 4.8547 | 4.8285 | 4.6842 | 4.5353 | 4.3893
|  | LHANBRYDE | LW |  |  |  | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 4.985 | 4.9534 | 4.7799 | 4.6006 | 4.425 | 5.7385 | 5.7099 | 5.6846 | 5.6601 | 4.9612 | 4.9224 | 4.8843 | 4.8428 | 4.8014 | 4.7607 | 4.7201 | 4.4975 | 4.2674 | 4.0422 | 5.6502 | 5.6502 | 5.6502 | 4.982 | 4.9454 | 4.9094 | 4.8741 | 4.8356 | 4.7973 | 4.7595 | 4.7219 | 4.5155 | 4.3022 | 4.0934
|  | LHANBRYDE | ST |  |  |  | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 4.9656 | 4.8855 | 5.7505 | 5.7398 | 5.7307 | 5.7197 | 5.7061 | 5.6918 | 5.678 | 5.6639 | 4.9847 | 4.9633 | 4.9423 | 4.8396 | 4.7357 | 4.633 | 5.6502 | 5.6502 | 5.6502 | 5.6502 | 5.6502 | 5.6502 | 5.6502 | 4.9879 | 4.9672 | 4.9474 | 4.9279 | 4.8327 | 4.7363 | 4.6411
|  | LHANBRYDE | FS |  |  |  | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7853 | 5.7574 | 5.754 | 5.751 | 5.7475 | 5.7431 | 5.7388 | 5.7335 | 5.7283 | 5.7231 | 5.7181 | 5.7132 | 5.691 | 5.6705 | 4.9849 | 5.6502 | 5.6502 | 5.6502 | 5.6502 | 5.6502 | 5.6502 | 5.6502 | 5.6502 | 5.6502 | 5.6502 | 5.6502 | 5.6502 | 4.9979 | 4.9674
| FORT WILLIAM | LIDDESDALE | MINIMUM HEADROOM | NM 78116 59480 | YES | YES | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.53573 | 0.53253 | 0.52886 | 0.52525 | 0.52171 | 0.51822 | 0.5148 | 0.5111 | 0.50742 | 0.50376 | 0.50012 | 0.49595 | 0.49552 | 0.49508 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652
|  | LIDDESDALE | CT |  |  |  | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.53573 | 0.53253 | 0.52886 | 0.52525 | 0.52171 | 0.51822 | 0.5148 | 0.5111 | 0.50742 | 0.50376 | 0.50012 | 0.49595 | 0.49552 | 0.49508 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652
|  | LIDDESDALE | LW |  |  |  | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.53763 | 0.5375 | 0.53733 | 0.53717 | 0.53701 | 0.53685 | 0.5367 | 0.53653 | 0.53637 | 0.53621 | 0.53604 | 0.5292 | 0.52228 | 0.51549 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652
|  | LIDDESDALE | ST |  |  |  | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.53768 | 0.53764 | 0.53757 | 0.5375 | 0.53688 | 0.53629 | 0.5357 | 0.53507 | 0.53445 | 0.53383 | 0.53323 | 0.5303 | 0.52739 | 0.52449 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652
|  | LIDDESDALE | FS |  |  |  | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.69487 | 0.5377 | 0.5377 | 0.53768 | 0.53766 | 0.53746 | 0.53726 | 0.537 | 0.53675 | 0.53651 | 0.53626 | 0.53602 | 0.53489 | 0.53384 | 0.53283 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652 | 0.54652
| KEITH | LIMEHILLOCKS | MINIMUM HEADROOM | NJ 52093 50703 | YES | YES | 2.0278 | 1.9282 | 1.8306 | 1.7361 | 1.6448 | 1.5565 | 1.4713 | 1.4131 | 1.3743 | 1.3357 | 1.2976 | 0.86018 | -0.021668 | -0.20946 | 2.046 | 1.9564 | 1.8675 | 1.7814 | 1.6979 | 1.6172 | 1.5392 | 1.483 | 1.443 | 1.4033 | 1.364 | 0.96699 | 0.19964 | 0.01065 | 2.1207 | 2.0208 | 1.9175 | 1.8173 | 1.7204 | 1.6266 | 1.536 | 1.4713 | 1.4259 | 1.3808 | 1.3361 | 0.87422 | -0.054751 | -0.27996
|  | LIMEHILLOCKS | CT |  |  |  | 2.0278 | 1.9282 | 1.8306 | 1.7361 | 1.6448 | 1.5565 | 1.4713 | 1.4131 | 1.3743 | 1.3357 | 1.2976 | 0.86018 | -0.021668 | -0.20946 | 2.046 | 1.9564 | 1.8675 | 1.7814 | 1.6979 | 1.6172 | 1.5392 | 1.483 | 1.443 | 1.4033 | 1.364 | 0.96699 | 0.19964 | 0.01065 | 2.1207 | 2.0208 | 1.9175 | 1.8173 | 1.7204 | 1.6266 | 1.536 | 1.4713 | 1.4259 | 1.3808 | 1.3361 | 0.87422 | -0.054751 | -0.27996
|  | LIMEHILLOCKS | LW |  |  |  | 2.1781 | 2.1538 | 2.1253 | 2.0956 | 2.0648 | 2.0331 | 2.0007 | 1.9647 | 1.9281 | 1.8911 | 1.8539 | 1.366 | 0.41997 | 0.16153 | 2.1727 | 2.1479 | 2.1185 | 2.0882 | 2.0571 | 2.0254 | 1.9931 | 1.9574 | 1.9213 | 1.8848 | 1.8482 | 1.4012 | 0.57225 | 0.31637 | 2.2682 | 2.2468 | 2.2133 | 2.1789 | 2.1434 | 2.1072 | 2.0703 | 2.0294 | 1.9881 | 1.9463 | 1.9044 | 1.3852 | 0.40786 | 0.10186
|  | LIMEHILLOCKS | ST |  |  |  | 2.2033 | 2.1952 | 2.1854 | 2.1748 | 2.1596 | 2.1447 | 2.1302 | 2.1152 | 2.0981 | 2.0813 | 2.0648 | 1.849 | 1.4183 | 1.3332 | 2.1953 | 2.1873 | 2.1773 | 2.1661 | 2.1497 | 2.1337 | 2.1181 | 2.1019 | 2.0838 | 2.0661 | 2.0488 | 1.8513 | 1.4752 | 1.3869 | 2.2918 | 2.2849 | 2.2771 | 2.2681 | 2.2497 | 2.2316 | 2.214 | 2.1957 | 2.1753 | 2.1553 | 2.1356 | 1.9063 | 1.4652 | 1.365
|  | LIMEHILLOCKS | FS |  |  |  | 2.2002 | 2.195 | 2.1863 | 2.1774 | 2.167 | 2.1568 | 2.1458 | 2.135 | 2.1243 | 2.1138 | 2.1035 | 2.046 | 1.988 | 1.9321 | 2.1934 | 2.189 | 2.1812 | 2.1731 | 2.1632 | 2.1535 | 2.1427 | 2.1321 | 2.1217 | 2.1115 | 2.1014 | 2.0465 | 1.9915 | 1.9388 | 2.288 | 2.283 | 2.2748 | 2.2666 | 2.2576 | 2.2486 | 2.2393 | 2.2281 | 2.2162 | 2.2044 | 2.1928 | 2.1296 | 2.0661 | 2.0052
| ARDMORE | LOCH CARNAN | MINIMUM HEADROOM | NF 83230 42735 | NO | YES | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 9.7485 | 9.748 | 9.7473 | 9.7466 | 9.746 | 9.7453 | 9.7447 | 9.7441 | 9.7431 | 9.7422 | 9.7412 | 9.7328 | 9.7294 | 9.7289 | 9.7715 | 9.7713 | 9.7709 | 9.7706 | 9.7703 | 9.77 | 9.7697 | 9.7694 | 9.7689 | 9.7685 | 9.7681 | 9.7681 | 9.7681 | 9.7681
|  | LOCH CARNAN | CT |  |  |  | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 9.7486 | 9.7481 | 9.7477 | 9.7472 | 9.7467 | 9.7463 | 9.7459 | 9.7454 | 9.7449 | 9.7445 | 9.744 | 9.736 | 9.7306 | 9.7291 | 9.7716 | 9.7714 | 9.7711 | 9.7709 | 9.7707 | 9.7705 | 9.7703 | 9.77 | 9.7698 | 9.7696 | 9.7694 | 9.7681 | 9.7681 | 9.7681
|  | LOCH CARNAN | LW |  |  |  | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 9.7485 | 9.748 | 9.7473 | 9.7466 | 9.746 | 9.7453 | 9.7447 | 9.7441 | 9.7434 | 9.7427 | 9.7421 | 9.7328 | 9.7294 | 9.7289 | 9.7715 | 9.7713 | 9.7709 | 9.7706 | 9.7703 | 9.77 | 9.7697 | 9.7694 | 9.7691 | 9.7687 | 9.7684 | 9.7681 | 9.7681 | 9.7681
|  | LOCH CARNAN | ST |  |  |  | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 9.7487 | 9.7485 | 9.7483 | 9.748 | 9.747 | 9.746 | 9.7451 | 9.7441 | 9.7431 | 9.7422 | 9.7412 | 9.7368 | 9.7333 | 9.7307 | 9.7716 | 9.7716 | 9.7714 | 9.7713 | 9.7708 | 9.7703 | 9.7699 | 9.7694 | 9.7689 | 9.7685 | 9.7681 | 9.7681 | 9.7681 | 9.7681
|  | LOCH CARNAN | FS |  |  |  | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 10.4175 | 9.7488 | 9.7488 | 9.7487 | 9.7486 | 9.7483 | 9.748 | 9.7476 | 9.7472 | 9.7468 | 9.7464 | 9.746 | 9.7442 | 9.7426 | 9.741 | 9.7717 | 9.7717 | 9.7716 | 9.7716 | 9.7714 | 9.7713 | 9.7711 | 9.7709 | 9.7707 | 9.7705 | 9.7703 | 9.7695 | 9.7687 | 9.7681
| GRUDIE BRIDGE | LOCH GLASCARNOCH | MINIMUM HEADROOM | NH 31620 71996 | YES | YES | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.49987 | 0.49959 | 0.50068 | 0.50065 | 0.50062 | 0.50062 | 0.50061 | 0.50061 | 0.50061 | 0.50061 | 0.50061 | 0.49995 | 0.49989 | 0.49956 | 0.49924 | 0.49892 | 0.50077 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.4997 | 0.49937 | 0.49905
|  | LOCH GLASCARNOCH | CT |  |  |  | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50068 | 0.50066 | 0.50064 | 0.50062 | 0.50062 | 0.50061 | 0.50061 | 0.50061 | 0.50061 | 0.50061 | 0.50061 | 0.49986 | 0.49963 | 0.49941 | 0.50077 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.49999 | 0.49977 | 0.49954
|  | LOCH GLASCARNOCH | LW |  |  |  | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.49987 | 0.49959 | 0.50068 | 0.50065 | 0.50062 | 0.50062 | 0.50061 | 0.50061 | 0.50061 | 0.50061 | 0.50061 | 0.49995 | 0.49989 | 0.49956 | 0.49924 | 0.49892 | 0.50077 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.4997 | 0.49937 | 0.49905
|  | LOCH GLASCARNOCH | ST |  |  |  | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50069 | 0.50068 | 0.50066 | 0.50065 | 0.50064 | 0.50063 | 0.50062 | 0.50062 | 0.50062 | 0.50061 | 0.50061 | 0.50061 | 0.49999 | 0.49985 | 0.50078 | 0.50077 | 0.50077 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.49998
|  | LOCH GLASCARNOCH | FS |  |  |  | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50115 | 0.50069 | 0.50069 | 0.50069 | 0.50068 | 0.50068 | 0.50067 | 0.50067 | 0.50066 | 0.50065 | 0.50065 | 0.50064 | 0.50062 | 0.50062 | 0.50061 | 0.50078 | 0.50078 | 0.50078 | 0.50077 | 0.50077 | 0.50077 | 0.50077 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076 | 0.50076
| FORT WILLIAM | LOCHALINE | MINIMUM HEADROOM | NM 67939 45444 | YES | YES | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.6314 | 1.6309 | 1.6304 | 1.6299 | 1.6295 | 1.629 | 1.6285 | 1.628 | 1.6275 | 1.627 | 1.6265 | 1.6241 | 1.6215 | 1.619 | 1.5394 | 1.5392 | 1.539 | 1.5389 | 1.5387 | 1.5385 | 1.5383 | 1.5381 | 1.5379 | 1.5377 | 1.5376 | 1.5366 | 1.5356 | 1.5347
|  | LOCHALINE | CT |  |  |  | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.6314 | 1.6311 | 1.6307 | 1.6304 | 1.63 | 1.6297 | 1.6294 | 1.629 | 1.6287 | 1.6283 | 1.628 | 1.6263 | 1.6245 | 1.6227 | 1.5394 | 1.5393 | 1.5391 | 1.539 | 1.5389 | 1.5388 | 1.5386 | 1.5385 | 1.5384 | 1.5382 | 1.5381 | 1.5375 | 1.5368 | 1.5361
|  | LOCHALINE | LW |  |  |  | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.6314 | 1.6309 | 1.6304 | 1.6299 | 1.6295 | 1.629 | 1.6285 | 1.628 | 1.6275 | 1.627 | 1.6265 | 1.6241 | 1.6215 | 1.619 | 1.5394 | 1.5392 | 1.539 | 1.5389 | 1.5387 | 1.5385 | 1.5383 | 1.5381 | 1.5379 | 1.5377 | 1.5376 | 1.5366 | 1.5356 | 1.5347
|  | LOCHALINE | ST |  |  |  | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.6315 | 1.6314 | 1.6312 | 1.6309 | 1.6307 | 1.6305 | 1.6303 | 1.63 | 1.6298 | 1.6296 | 1.6294 | 1.6283 | 1.6272 | 1.6261 | 1.5394 | 1.5394 | 1.5393 | 1.5392 | 1.5391 | 1.5391 | 1.539 | 1.5389 | 1.5388 | 1.5387 | 1.5386 | 1.5382 | 1.5378 | 1.5374
|  | LOCHALINE | FS |  |  |  | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.5395 | 1.6316 | 1.6316 | 1.6315 | 1.6314 | 1.6314 | 1.6313 | 1.6312 | 1.6311 | 1.631 | 1.6309 | 1.6308 | 1.6304 | 1.63 | 1.6296 | 1.5395 | 1.5395 | 1.5394 | 1.5394 | 1.5394 | 1.5394 | 1.5393 | 1.5393 | 1.5393 | 1.5392 | 1.5392 | 1.539 | 1.5389 | 1.5387
| GRUDIE BRIDGE | LOCHCARRON | MINIMUM HEADROOM | NG 91944 41839 | YES | YES | [14 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: Generation Headroom Winter (MVA) 2025 to Generation Headroom Winter (MVA) 2050
|  | LOCHCARRON | CT | [17 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: Generation Headroom Winter (MVA) 2025 to Generation Headroom Winter (MVA) 2050
|  | LOCHCARRON | LW | [17 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: Generation Headroom Winter (MVA) 2025 to Generation Headroom Winter (MVA) 2050
|  | LOCHCARRON | ST | [17 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: Generation Headroom Winter (MVA) 2025 to Generation Headroom Winter (MVA) 2050
|  | LOCHCARRON | FS | [17 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: Generation Headroom Winter (MVA) 2025 to Generation Headroom Winter (MVA) 2050
| TAYNUILT | LOCHDONHEAD | MINIMUM HEADROOM | NM 72902 34134 | YES | YES | 1.6735 | 1.6724 | 1.6712 | 1.6699 | 1.6687 | 1.6676 | 1.6664 | 1.6652 | 1.6639 | 1.6627 | 1.6615 | 1.6542 | 1.6469 | 1.6396 | 1.4947 | 1.49 | 1.4842 | 1.4786 | 1.473 | 1.4676 | 1.4624 | 1.4566 | 1.451 | 1.4453 | 1.4397 | 1.423 | 1.4108 | 1.4025 | 1.5253 | 1.523 | 1.5203 | 1.5176 | 1.5149 | 1.5123 | 1.5098 | 1.5071 | 1.5043 | 1.5016 | 1.499 | 1.483 | 1.4694 | 1.4694
|  | LOCHDONHEAD | CT |  |  |  | 1.6735 | 1.6727 | 1.6719 | 1.671 | 1.6702 | 1.6693 | 1.6685 | 1.6677 | 1.6668 | 1.6659 | 1.6651 | 1.658 | 1.6508 | 1.6437 | 1.495 | 1.4914 | 1.4874 | 1.4835 | 1.4796 | 1.4758 | 1.4721 | 1.4681 | 1.4641 | 1.4602 | 1.4563 | 1.4293 | 1.4174 | 1.4056 | 1.5254 | 1.5237 | 1.5218 | 1.5199 | 1.518 | 1.5162 | 1.5145 | 1.5126 | 1.5107 | 1.5088 | 1.5069 | 1.4913 | 1.4756 | 1.4694
|  | LOCHDONHEAD | LW |  |  |  | 1.6735 | 1.6724 | 1.6712 | 1.6699 | 1.6687 | 1.6676 | 1.6664 | 1.6652 | 1.6639 | 1.6627 | 1.6615 | 1.6542 | 1.6469 | 1.6396 | 1.4947 | 1.49 | 1.4842 | 1.4786 | 1.473 | 1.4676 | 1.4624 | 1.4566 | 1.451 | 1.4453 | 1.4397 | 1.423 | 1.4108 | 1.4025 | 1.5253 | 1.523 | 1.5203 | 1.5176 | 1.5149 | 1.5123 | 1.5098 | 1.5071 | 1.5043 | 1.5016 | 1.499 | 1.483 | 1.4694 | 1.4694
|  | LOCHDONHEAD | ST |  |  |  | 1.6738 | 1.6735 | 1.673 | 1.6724 | 1.6717 | 1.6711 | 1.6704 | 1.6697 | 1.669 | 1.6684 | 1.6677 | 1.6645 | 1.6613 | 1.6582 | 1.4962 | 1.4948 | 1.4926 | 1.4899 | 1.4868 | 1.4838 | 1.4808 | 1.4776 | 1.4745 | 1.4714 | 1.4683 | 1.4536 | 1.4391 | 1.4297 | 1.526 | 1.5253 | 1.5243 | 1.523 | 1.5215 | 1.5201 | 1.5186 | 1.5171 | 1.5156 | 1.5141 | 1.5126 | 1.5056 | 1.4987 | 1.4918
|  | LOCHDONHEAD | FS |  |  |  | 1.674 | 1.6739 | 1.6738 | 1.6736 | 1.6734 | 1.6732 | 1.6729 | 1.6726 | 1.6724 | 1.6721 | 1.6718 | 1.6705 | 1.6694 | 1.6683 | 1.497 | 1.4969 | 1.4963 | 1.4956 | 1.4945 | 1.4935 | 1.4922 | 1.4909 | 1.4896 | 1.4884 | 1.4872 | 1.4813 | 1.4759 | 1.4709 | 1.5264 | 1.5263 | 1.526 | 1.5257 | 1.5252 | 1.5247 | 1.5241 | 1.5235 | 1.5228 | 1.5222 | 1.5217 | 1.5189 | 1.5163 | 1.5139
| KILLIN | LOCHEARNHEAD | MINIMUM HEADROOM | NN 58766 24177 | YES | YES | 0.12883 | 0.12883 | 0.12883 | 0.12883 | 0.12883 | 0.12883 | 0.12883 | 0.12883 | 0.12883 | 0.12883 | 0.12883 | 0.10431 | -0.001028 | -0.12595 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.36558 | -0.57431 | -0.34971 | -0.38266 | -0.42431 | -0.46553 | -0.50642 | -0.54688 | -0.58661 | -0.62963 | -0.67278 | -0.71575 | -0.7587 | -0.96241 | -1.1684 | -1.3717
|  | LOCHEARNHEAD | CT |  |  |  | 0.12883 | 0.12883 | 0.12883 | 0.12883 | 0.12883 | 0.12883 | 0.12883 | 0.12883 | 0.12883 | 0.12883 | 0.12883 | 0.12883 | 0.113 | 0.033522 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.29622 | -0.34845 | -0.37157 | -0.4003 | -0.42879 | -0.45712 | -0.48519 | -0.51276 | -0.54261 | -0.57263 | -0.60253 | -0.63245 | -0.78804 | -0.94542 | -1.1009
|  | LOCHEARNHEAD | LW |  |  |  | 0.12883 | 0.12883 | 0.12883 | 0.12883 | 0.12883 | 0.12883 | 0.12883 | 0.12883 | 0.12883 | 0.12883 | 0.12883 | 0.10431 | -0.001028 | -0.12595 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.36558 | -0.57431 | -0.34971 | -0.38266 | -0.42431 | -0.46553 | -0.50642 | -0.54688 | -0.58661 | -0.62963 | -0.67278 | -0.71575 | -0.7587 | -0.96241 | -1.1684 | -1.3717
|  | LOCHEARNHEAD | ST |  |  |  | 0.12883 | 0.12883 | 0.12883 | 0.12883 | 0.12883 | 0.12883 | 0.12883 | 0.12883 | 0.12883 | 0.12883 | 0.12883 | 0.12883 | 0.12883 | 0.12883 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.34371 | -0.34952 | -0.36483 | -0.38433 | -0.40299 | -0.42141 | -0.43946 | -0.45897 | -0.47846 | -0.4977 | -0.51682 | -0.6116 | -0.70505 | -0.79765
|  | LOCHEARNHEAD | FS |  |  |  | 0.12883 | 0.12883 | 0.12883 | 0.12883 | 0.12883 | 0.12883 | 0.12883 | 0.12883 | 0.12883 | 0.12883 | 0.12883 | 0.12883 | 0.12883 | 0.12883 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.27154 | -0.34043 | -0.34089 | -0.34348 | -0.34658 | -0.34997 | -0.35543 | -0.36304 | -0.37056 | -0.37803 | -0.38539 | -0.39271 | -0.42839 | -0.46249 | -0.49508
| LYNDHURST | LOCHEE | MINIMUM HEADROOM | NO 38065 31416 | NO | YES | 25.8604 | 25.8392 | 25.8392 | 25.8392 | 25.8392 | 25.8392 | 25.8392 | 25.8392 | 25.8392 | 25.8392 | 25.8392 | 25.8392 | 25.8392 | 25.8392 | 24.013 | 23.9821 | 23.9613 | 23.9414 | 23.9206 | 23.8985 | 23.877 | 23.8521 | 23.8251 | 23.7977 | 23.7709 | 23.7168 | 23.696 | 23.6767 | 24.0462 | 24.0416 | 24.0385 | 24.0356 | 24.0325 | 24.0292 | 24.026 | 24.0223 | 24.0183 | 24.0142 | 24.0138 | 24.0138 | 24.0138 | 24.0138
|  | LOCHEE | CT |  |  |  | 25.8621 | 25.8392 | 25.8392 | 25.8392 | 25.8392 | 25.8392 | 25.8392 | 25.8392 | 25.8392 | 25.8392 | 25.8392 | 25.8392 | 25.8392 | 25.8392 | 24.0142 | 23.9893 | 23.9753 | 23.9617 | 23.9479 | 23.9337 | 23.9181 | 23.9029 | 23.8834 | 23.8638 | 23.8441 | 23.7336 | 23.7185 | 23.7046 | 24.0464 | 24.0427 | 24.0406 | 24.0386 | 24.0365 | 24.0344 | 24.0321 | 24.0298 | 24.027 | 24.024 | 24.0211 | 24.0138 | 24.0138 | 24.0138
|  | LOCHEE | LW |  |  |  | 25.8604 | 25.8392 | 25.8392 | 25.8392 | 25.8392 | 25.8392 | 25.8392 | 25.8392 | 25.8392 | 25.8392 | 25.8392 | 25.8392 | 25.8392 | 25.8392 | 24.013 | 23.9821 | 23.9613 | 23.9414 | 23.9206 | 23.8985 | 23.877 | 23.8521 | 23.8251 | 23.7977 | 23.7709 | 23.7168 | 23.696 | 23.6767 | 24.0462 | 24.0416 | 24.0385 | 24.0356 | 24.0325 | 24.0292 | 24.026 | 24.0223 | 24.0183 | 24.0142 | 24.0138 | 24.0138 | 24.0138 | 24.0138
|  | LOCHEE | ST |  |  |  | 25.8678 | 25.8492 | 25.8392 | 25.8392 | 25.8392 | 25.8392 | 25.8392 | 25.8392 | 25.8392 | 25.8392 | 25.8392 | 25.8392 | 25.8392 | 25.8392 | 24.0184 | 24.0048 | 23.9968 | 23.9874 | 23.975 | 23.9623 | 23.9488 | 23.9353 | 23.9189 | 23.9024 | 23.886 | 23.8065 | 23.741 | 23.7272 | 24.0507 | 24.045 | 24.0438 | 24.0424 | 24.0405 | 24.0387 | 24.0367 | 24.0347 | 24.0322 | 24.0298 | 24.0273 | 24.0155 | 24.0138 | 24.0138
|  | LOCHEE | FS |  |  |  | 25.8718 | 25.8648 | 25.8614 | 25.8577 | 25.8518 | 25.846 | 25.8392 | 25.8392 | 25.8392 | 25.8392 | 25.8392 | 25.8392 | 25.8392 | 25.8392 | 24.0214 | 24.0162 | 24.0137 | 24.011 | 24.0067 | 24.0024 | 23.9972 | 23.9915 | 23.9854 | 23.9792 | 23.9731 | 23.9426 | 23.9178 | 23.8966 | 24.0548 | 24.0476 | 24.0463 | 24.0459 | 24.0453 | 24.0446 | 24.0438 | 24.043 | 24.0421 | 24.0412 | 24.0403 | 24.0357 | 24.0321 | 24.0289
| PORT ANN | LOCHGILPHEAD | MINIMUM HEADROOM | NR 86092 88371 | NO | YES | 13.4022 | 13.4022 | 13.4022 | 13.4022 | 13.4022 | 13.4022 | 13.4022 | 13.4022 | 13.4022 | 13.4022 | 13.4022 | 12.9829 | 12.4447 | 11.9151 | 11.9736 | 11.9736 | 11.9736 | 11.9736 | 11.9736 | 11.9736 | 11.9121 | 11.8094 | 11.7074 | 11.6062 | 11.5059 | 10.5742 | 9.9156 | 9.2675 | 11.9182 | 11.9182 | 11.9182 | 11.9182 | 11.915 | 11.8303 | 11.7473 | 11.6573 | 11.5593 | 11.4564 | 11.3543 | 10.3517 | 9.6815 | 9.0222
|  | LOCHGILPHEAD | CT |  |  |  | 13.4022 | 13.4022 | 13.4022 | 13.4022 | 13.4022 | 13.4022 | 13.4022 | 13.4022 | 13.4022 | 13.4022 | 13.4022 | 13.1075 | 12.8465 | 12.4737 | 11.9736 | 11.9736 | 11.9736 | 11.9736 | 11.9736 | 11.9736 | 11.9703 | 11.8773 | 11.7864 | 11.6972 | 11.6091 | 10.8707 | 10.4072 | 9.9511 | 11.9182 | 11.9182 | 11.9182 | 11.9182 | 11.9182 | 11.8746 | 11.7983 | 11.7168 | 11.6371 | 11.549 | 11.4593 | 10.6533 | 10.1818 | 9.7177
|  | LOCHGILPHEAD | LW |  |  |  | 13.4022 | 13.4022 | 13.4022 | 13.4022 | 13.4022 | 13.4022 | 13.4022 | 13.4022 | 13.4022 | 13.4022 | 13.4022 | 12.9829 | 12.4447 | 11.9151 | 11.9736 | 11.9736 | 11.9736 | 11.9736 | 11.9736 | 11.9736 | 11.9121 | 11.8094 | 11.7074 | 11.6062 | 11.5059 | 10.5742 | 9.9156 | 9.2675 | 11.9182 | 11.9182 | 11.9182 | 11.9182 | 11.915 | 11.8303 | 11.7473 | 11.6573 | 11.5593 | 11.4564 | 11.3543 | 10.3517 | 9.6815 | 9.0222
|  | LOCHGILPHEAD | ST |  |  |  | 13.4022 | 13.4022 | 13.4022 | 13.4022 | 13.4022 | 13.4022 | 13.4022 | 13.4022 | 13.4022 | 13.4022 | 13.4022 | 13.2548 | 13.2548 | 13.2548 | 11.9736 | 11.9736 | 11.9736 | 11.9736 | 11.9736 | 11.9736 | 11.9736 | 11.9736 | 11.9736 | 11.9736 | 11.9736 | 11.5969 | 11.3085 | 11.0214 | 11.9182 | 11.9182 | 11.9182 | 11.9182 | 11.9182 | 11.9182 | 11.9182 | 11.9182 | 11.9182 | 11.9012 | 11.8489 | 11.4196 | 11.1261 | 10.834
|  | LOCHGILPHEAD | FS |  |  |  | 13.4022 | 13.4022 | 13.4022 | 13.4022 | 13.4022 | 13.4022 | 13.4022 | 13.4022 | 13.4022 | 13.4022 | 13.4022 | 13.4022 | 13.4022 | 13.4022 | 11.9736 | 11.9736 | 11.9736 | 11.9736 | 11.9736 | 11.9736 | 11.9736 | 11.9736 | 11.9736 | 11.9736 | 11.9736 | 11.9736 | 11.9736 | 11.9736 | 11.9182 | 11.9182 | 11.9182 | 11.9182 | 11.9182 | 11.9182 | 11.9182 | 11.9182 | 11.9182 | 11.9182 | 11.9182 | 11.9182 | 11.9182 | 11.8845
| CLACHAN | LOCHGOILHEAD | MINIMUM HEADROOM | NN 20159 01862 | YES | YES | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 2.1036 | 2.1025 | 2.1012 | 2.0999 | 2.0987 | 2.0975 | 2.0963 | 2.095 | 2.0937 | 2.0925 | 2.0912 | 2.0767 | 2.0621 | 2.0485 | 2.4558 | 2.4556 | 2.4553 | 2.455 | 2.4548 | 2.4545 | 2.4543 | 2.454 | 2.4537 | 2.4534 | 2.4532 | 2.4501 | 2.4471 | 2.4471
|  | LOCHGOILHEAD | CT |  |  |  | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 2.1036 | 2.1028 | 2.1019 | 2.101 | 2.1002 | 2.0993 | 2.0985 | 2.0976 | 2.0967 | 2.0958 | 2.0949 | 2.0805 | 2.0659 | 2.0516 | 2.4558 | 2.4557 | 2.4555 | 2.4553 | 2.4551 | 2.4549 | 2.4547 | 2.4545 | 2.4543 | 2.4542 | 2.454 | 2.4509 | 2.4477 | 2.4471
|  | LOCHGOILHEAD | LW |  |  |  | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 2.1036 | 2.1025 | 2.1012 | 2.0999 | 2.0987 | 2.0975 | 2.0963 | 2.095 | 2.0937 | 2.0925 | 2.0912 | 2.0767 | 2.0621 | 2.0485 | 2.4558 | 2.4556 | 2.4553 | 2.455 | 2.4548 | 2.4545 | 2.4543 | 2.454 | 2.4537 | 2.4534 | 2.4532 | 2.4501 | 2.4471 | 2.4471
|  | LOCHGOILHEAD | ST |  |  |  | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 2.1039 | 2.1036 | 2.1031 | 2.1025 | 2.1011 | 2.0998 | 2.0985 | 2.0971 | 2.0958 | 2.0944 | 2.0931 | 2.0867 | 2.0803 | 2.074 | 2.4559 | 2.4558 | 2.4557 | 2.4556 | 2.4553 | 2.455 | 2.4547 | 2.4544 | 2.4541 | 2.4539 | 2.4536 | 2.4522 | 2.4508 | 2.4495
|  | LOCHGOILHEAD | FS |  |  |  | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 1.5964 | 2.1041 | 2.1041 | 2.1039 | 2.1037 | 2.1033 | 2.1029 | 2.1023 | 2.1018 | 2.1012 | 2.1007 | 2.1002 | 2.0977 | 2.0953 | 2.0932 | 2.4559 | 2.4559 | 2.4559 | 2.4558 | 2.4558 | 2.4557 | 2.4555 | 2.4554 | 2.4553 | 2.4552 | 2.4551 | 2.4545 | 2.4541 | 2.4536
| GRUDIE BRIDGE | LOCHINVER | MINIMUM HEADROOM | NC 09516 22243 | YES | YES | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.8485 | 1.8427 | 1.8361 | 1.8295 | 1.8231 | 1.8168 | 1.8106 | 1.804 | 1.7973 | 1.7907 | 1.7842 | 1.7738 | 1.7738 | 1.7738 | 1.9159 | 1.9083 | 1.8995 | 1.8913 | 1.8913 | 1.8913 | 1.8913 | 1.8913 | 1.8913 | 1.8913 | 1.8913 | 1.8913 | 1.8913 | 1.8913
|  | LOCHINVER | CT |  |  |  | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.8485 | 1.8427 | 1.8361 | 1.8295 | 1.8231 | 1.8168 | 1.8106 | 1.804 | 1.7973 | 1.7907 | 1.7842 | 1.7738 | 1.7738 | 1.7738 | 1.9159 | 1.9083 | 1.8995 | 1.8913 | 1.8913 | 1.8913 | 1.8913 | 1.8913 | 1.8913 | 1.8913 | 1.8913 | 1.8913 | 1.8913 | 1.8913
|  | LOCHINVER | LW |  |  |  | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.8509 | 1.8487 | 1.846 | 1.8433 | 1.8407 | 1.8382 | 1.8356 | 1.8329 | 1.8303 | 1.8276 | 1.825 | 1.7879 | 1.7738 | 1.7738 | 1.9191 | 1.9162 | 1.9126 | 1.9091 | 1.9057 | 1.9023 | 1.899 | 1.8954 | 1.8919 | 1.8913 | 1.8913 | 1.8913 | 1.8913 | 1.8913
|  | LOCHINVER | ST |  |  |  | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.8517 | 1.851 | 1.8499 | 1.8487 | 1.8457 | 1.8428 | 1.8399 | 1.8368 | 1.8338 | 1.8308 | 1.8279 | 1.8136 | 1.7993 | 1.785 | 1.9201 | 1.9192 | 1.9178 | 1.9161 | 1.9122 | 1.9084 | 1.9046 | 1.9006 | 1.8966 | 1.8926 | 1.8913 | 1.8913 | 1.8913 | 1.8913
|  | LOCHINVER | FS |  |  |  | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.7836 | 1.852 | 1.852 | 1.8517 | 1.8513 | 1.8502 | 1.8491 | 1.8477 | 1.8463 | 1.845 | 1.8436 | 1.8423 | 1.8361 | 1.8302 | 1.8246 | 1.9206 | 1.9205 | 1.9201 | 1.9196 | 1.9182 | 1.9167 | 1.9149 | 1.9131 | 1.9113 | 1.9095 | 1.9078 | 1.8996 | 1.8918 | 1.8913
| LUNANHEAD | LOCHSIDE | MINIMUM HEADROOM | NO 45151 50548 | NO | YES | 35.5706 | 35.5601 | 35.5469 | 35.5334 | 35.5195 | 35.5051 | 35.4943 | 35.4824 | 35.4702 | 35.4583 | 35.4473 | 35.3348 | 35.3207 | 35.3207 | 28.6483 | 28.5442 | 28.4425 | 28.4425 | 28.4425 | 28.4425 | 28.4425 | 28.4425 | 28.4425 | 28.4425 | 28.4425 | 28.4035 | 28.4035 | 28.4035 | 30.8469 | 30.8159 | 30.7773 | 30.7376 | 30.6965 | 30.6543 | 30.6226 | 30.5874 | 30.5517 | 30.5168 | 30.4843 | 30.3299 | 30.3299 | 30.3299
|  | LOCHSIDE | CT |  |  |  | 35.5706 | 35.5601 | 35.5469 | 35.5334 | 35.5195 | 35.5051 | 35.4943 | 35.4824 | 35.4702 | 35.4583 | 35.4473 | 35.3348 | 35.3207 | 35.3207 | 28.6483 | 28.5442 | 28.4425 | 28.4425 | 28.4425 | 28.4425 | 28.4425 | 28.4425 | 28.4425 | 28.4425 | 28.4425 | 28.4035 | 28.4035 | 28.4035 | 30.8469 | 30.8159 | 30.7773 | 30.7376 | 30.6965 | 30.6543 | 30.6226 | 30.5874 | 30.5517 | 30.5168 | 30.4843 | 30.3299 | 30.3299 | 30.3299
|  | LOCHSIDE | LW |  |  |  | 35.5721 | 35.5636 | 35.5519 | 35.5399 | 35.5275 | 35.5145 | 35.506 | 35.4969 | 35.4878 | 35.4789 | 35.47 | 35.3452 | 35.3207 | 35.3207 | 28.6635 | 28.5789 | 28.4638 | 28.4425 | 28.4425 | 28.4425 | 28.4425 | 28.4425 | 28.4425 | 28.4425 | 28.4425 | 28.4035 | 28.4035 | 28.4035 | 30.8514 | 30.8262 | 30.792 | 30.7567 | 30.7202 | 30.682 | 30.657 | 30.6301 | 30.6035 | 30.5772 | 30.5511 | 30.3299 | 30.3299 | 30.3299
|  | LOCHSIDE | ST |  |  |  | 35.5766 | 35.5741 | 35.57 | 35.565 | 35.5577 | 35.5501 | 35.5449 | 35.5391 | 35.5331 | 35.5273 | 35.5222 | 35.4635 | 35.44 | 35.4162 | 28.7073 | 28.6832 | 28.6425 | 28.5933 | 28.5212 | 28.4464 | 28.4425 | 28.4425 | 28.4425 | 28.4425 | 28.4425 | 28.423 | 28.423 | 28.423 | 30.8645 | 30.8573 | 30.8452 | 30.8305 | 30.809 | 30.7867 | 30.7714 | 30.7542 | 30.7367 | 30.7197 | 30.7045 | 30.597 | 30.5278 | 30.458
|  | LOCHSIDE | FS |  |  |  | 35.5935 | 35.578 | 35.5763 | 35.5744 | 35.5717 | 35.5689 | 35.5665 | 35.5642 | 35.5618 | 35.5596 | 35.5574 | 35.5474 | 35.5386 | 35.5301 | 28.8747 | 28.7217 | 28.705 | 28.6861 | 28.6592 | 28.6312 | 28.6079 | 28.5847 | 28.5616 | 28.5392 | 28.5179 | 28.4425 | 28.4425 | 28.4425 | 31.0228 | 30.8688 | 30.8638 | 30.8582 | 30.8502 | 30.8418 | 30.8349 | 30.8279 | 30.8211 | 30.8144 | 30.8081 | 30.7788 | 30.7527 | 30.7278
| BRIDGE OF DUN | LOGIE PERT | MINIMUM HEADROOM | NO 67764 64427 | YES | YES | 5.653 | 5.653 | 5.653 | 5.653 | 5.653 | 5.653 | 5.653 | 5.653 | 5.653 | 5.653 | 5.653 | 5.653 | 4.9674 | 4.9071 | 4.8793 | 4.8736 | 4.8667 | 4.8599 | 4.8533 | 4.8468 | 4.8405 | 4.8337 | 4.8269 | 4.8202 | 4.8135 | 4.7426 | 4.6711 | 4.6007 | 4.6765 | 4.6712 | 4.6649 | 4.6586 | 4.6525 | 4.6465 | 4.6407 | 4.6344 | 4.6281 | 4.6219 | 4.6157 | 4.5503 | 4.4844 | 4.4194
|  | LOGIE PERT | CT |  |  |  | 5.653 | 5.653 | 5.653 | 5.653 | 5.653 | 5.653 | 5.653 | 5.653 | 5.653 | 5.653 | 5.653 | 5.653 | 5.653 | 4.9769 | 4.8796 | 4.8753 | 4.8705 | 4.8658 | 4.8611 | 4.8566 | 4.8522 | 4.8474 | 4.8426 | 4.8379 | 4.8332 | 4.7829 | 4.7322 | 4.6822 | 4.6768 | 4.6728 | 4.6684 | 4.664 | 4.6597 | 4.6555 | 4.6515 | 4.647 | 4.6427 | 4.6383 | 4.634 | 4.5875 | 4.5408 | 4.4946
|  | LOGIE PERT | LW |  |  |  | 5.653 | 5.653 | 5.653 | 5.653 | 5.653 | 5.653 | 5.653 | 5.653 | 5.653 | 5.653 | 5.653 | 5.653 | 4.9674 | 4.9071 | 4.8793 | 4.8736 | 4.8667 | 4.8599 | 4.8533 | 4.8468 | 4.8405 | 4.8337 | 4.8269 | 4.8202 | 4.8135 | 4.7426 | 4.6711 | 4.6007 | 4.6765 | 4.6712 | 4.6649 | 4.6586 | 4.6525 | 4.6465 | 4.6407 | 4.6344 | 4.6281 | 4.6219 | 4.6157 | 4.5503 | 4.4844 | 4.4194
|  | LOGIE PERT | ST |  |  |  | 5.653 | 5.653 | 5.653 | 5.653 | 5.653 | 5.653 | 5.653 | 5.653 | 5.653 | 5.653 | 5.653 | 5.653 | 5.653 | 5.653 | 4.8811 | 4.8794 | 4.8767 | 4.8735 | 4.867 | 4.8606 | 4.8543 | 4.8475 | 4.8409 | 4.8344 | 4.8279 | 4.7966 | 4.7657 | 4.7349 | 4.6781 | 4.6766 | 4.6741 | 4.6712 | 4.6651 | 4.6592 | 4.6534 | 4.6472 | 4.641 | 4.635 | 4.6291 | 4.6002 | 4.5717 | 4.5433
|  | LOGIE PERT | FS |  |  |  | 5.653 | 5.653 | 5.653 | 5.653 | 5.653 | 5.653 | 5.653 | 5.653 | 5.653 | 5.653 | 5.653 | 5.653 | 5.653 | 5.653 | 4.8821 | 4.8819 | 4.8812 | 4.8803 | 4.8781 | 4.876 | 4.8733 | 4.8706 | 4.8679 | 4.8653 | 4.8628 | 4.8506 | 4.8393 | 4.8288 | 4.679 | 4.6789 | 4.6782 | 4.6774 | 4.6754 | 4.6735 | 4.6709 | 4.6684 | 4.666 | 4.6636 | 4.6613 | 4.65 | 4.6396 | 4.6299
| MILTON OF CRAIGIE | LONGHAUGH | MINIMUM HEADROOM | NO 42768 33789 | NO | YES | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.1513 | 28.1513 | 28.1513 | 27.6533 | 27.6027 | 27.5366 | 27.481 | 27.4241 | 27.3661 | 27.3209 | 27.3143 | 27.3074 | 27.3005 | 27.2937 | 27.0006 | 26.965 | 26.9311 | 27.3645 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 26.9245 | 22.7507 | 22.1008
|  | LONGHAUGH | CT |  |  |  | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.1513 | 28.1513 | 28.1513 | 27.6589 | 27.6241 | 27.5804 | 27.5454 | 27.5099 | 27.475 | 27.4401 | 27.4011 | 27.3577 | 27.3213 | 27.3167 | 27.0317 | 27.0037 | 26.9773 | 27.3673 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 26.9245 | 26.9245 | 26.9245
|  | LONGHAUGH | LW |  |  |  | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.1513 | 28.1513 | 28.1513 | 27.6533 | 27.6027 | 27.5366 | 27.481 | 27.4241 | 27.3661 | 27.3209 | 27.3143 | 27.3074 | 27.3005 | 27.2937 | 27.0006 | 26.965 | 26.9311 | 27.3645 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 26.9245 | 22.7507 | 22.1008
|  | LONGHAUGH | ST |  |  |  | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.3637 | 28.3637 | 28.3637 | 27.6695 | 27.6504 | 27.6194 | 27.5887 | 27.5596 | 27.531 | 27.5026 | 27.471 | 27.4366 | 27.4015 | 27.367 | 27.1821 | 27.1668 | 27.1524 | 27.3724 | 27.3631 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.1406 | 27.1406 | 27.1406
|  | LONGHAUGH | FS |  |  |  | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 28.576 | 27.681 | 27.6783 | 27.6691 | 27.6615 | 27.6519 | 27.6423 | 27.6301 | 27.6174 | 27.6042 | 27.5909 | 27.5779 | 27.5132 | 27.4577 | 27.4081 | 27.378 | 27.3767 | 27.3722 | 27.3685 | 27.3638 | 27.3592 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568 | 27.3568
| ELGIN | LOSSIEMOUTH | MINIMUM HEADROOM | NJ 23203 69923 | NO | YES | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 17.8091 | 17.7891 | 17.7648 | 17.7404 | 17.7161 | 17.6917 | 17.6674 | 17.6407 | 17.6138 | 17.5866 | 17.5592 | 17.4819 | 17.4819 | 13.6983 | 18.0011 | 17.9928 | 17.9826 | 17.9725 | 17.9623 | 17.9522 | 17.942 | 17.9309 | 17.9197 | 17.9084 | 17.897 | 17.8031 | 17.8031 | 17.8031
|  | LOSSIEMOUTH | CT |  |  |  | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 17.8134 | 17.8028 | 17.7908 | 17.7785 | 17.7659 | 17.7531 | 17.74 | 17.7254 | 17.7103 | 17.6946 | 17.679 | 17.535 | 17.4819 | 17.4819 | 18.0029 | 17.9985 | 17.9935 | 17.9884 | 17.9831 | 17.9778 | 17.9723 | 17.9662 | 17.9599 | 17.9534 | 17.9469 | 17.8869 | 17.8279 | 17.8031
|  | LOSSIEMOUTH | LW |  |  |  | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 17.8091 | 17.7891 | 17.7648 | 17.7404 | 17.7161 | 17.6917 | 17.6674 | 17.6407 | 17.6138 | 17.5866 | 17.5592 | 17.4819 | 17.4819 | 13.6983 | 18.0011 | 17.9928 | 17.9826 | 17.9725 | 17.9623 | 17.9522 | 17.942 | 17.9309 | 17.9197 | 17.9084 | 17.897 | 17.8031 | 17.8031 | 17.8031
|  | LOSSIEMOUTH | ST |  |  |  | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 17.8162 | 17.8097 | 17.8002 | 17.7888 | 17.7677 | 17.7467 | 17.7257 | 17.7027 | 17.6796 | 17.6563 | 17.6332 | 17.5311 | 17.4819 | 17.4819 | 18.0041 | 18.0014 | 17.9974 | 17.9926 | 17.9838 | 17.9751 | 17.9663 | 17.9568 | 17.9471 | 17.9374 | 17.9278 | 17.8853 | 17.8444 | 17.8044
|  | LOSSIEMOUTH | FS |  |  |  | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 19.595 | 17.82 | 17.8189 | 17.8157 | 17.812 | 17.8049 | 17.7978 | 17.7888 | 17.7798 | 17.7708 | 17.7618 | 17.7528 | 17.7094 | 17.6726 | 17.6391 | 18.0057 | 18.0052 | 18.0038 | 18.0023 | 17.9993 | 17.9964 | 17.9926 | 17.9889 | 17.9851 | 17.9814 | 17.9777 | 17.9596 | 17.9442 | 17.9302
| BROADFORD | LOWER OLLACH | MINIMUM HEADROOM | NG 51241 37001 | YES | YES | 0.88867 | 0.66358 | 0.41175 | 0.16268 | -0.077183 | -0.30784 | -0.52929 | -0.65335 | -0.71598 | -0.77797 | -0.83904 | -1.1881 | -1.5603 | -1.9529 | 0.95427 | 0.75838 | 0.56076 | 0.36851 | 0.18132 | -0.0041789 | -0.18229 | -0.28256 | -0.33367 | -0.38427 | -0.43412 | -0.73904 | -1.0585 | -1.3921 | 0.7889 | 0.52919 | 0.26956 | 0.019185 | -0.22194 | -0.45382 | -0.67645 | -0.80137 | -0.86464 | -0.92727 | -0.98896 | -1.3499 | -1.7287 | -2.1256
|  | LOWER OLLACH | CT |  |  |  | 0.88867 | 0.66358 | 0.41175 | 0.16268 | -0.077183 | -0.30784 | -0.52929 | -0.65335 | -0.71598 | -0.77797 | -0.83904 | -1.1881 | -1.5603 | -1.9529 | 0.95427 | 0.75838 | 0.56076 | 0.36851 | 0.18132 | -0.0041789 | -0.18229 | -0.28256 | -0.33367 | -0.38427 | -0.43412 | -0.73904 | -1.0585 | -1.3921 | 0.7889 | 0.52919 | 0.26956 | 0.019185 | -0.22194 | -0.45382 | -0.67645 | -0.80137 | -0.86464 | -0.92727 | -0.98896 | -1.3499 | -1.7287 | -2.1256
|  | LOWER OLLACH | LW |  |  |  | 1.5545 | 1.5199 | 1.481 | 1.4381 | 1.3917 | 1.342 | 1.2896 | 0.97186 | 0.91365 | 0.8542 | 0.7887 | 0.35629 | -0.13539 | -0.7005 | 1.5746 | 1.5523 | 1.5271 | 1.4994 | 1.4694 | 1.4374 | 1.4036 | 0.99956 | 0.94565 | 0.89071 | 0.83516 | 0.46771 | 0.055712 | -0.41178 | 1.4472 | 1.417 | 1.383 | 1.3455 | 1.3049 | 0.99136 | 0.92969 | 0.86166 | 0.79171 | 0.72037 | 0.6482 | 0.20322 | -0.29494 | -0.86602
|  | LOWER OLLACH | ST |  |  |  | 1.6136 | 1.5998 | 1.5864 | 1.5734 | 1.5575 | 1.5421 | 1.5271 | 1.512 | 1.49 | 1.4686 | 1.4478 | 1.3407 | 0.91742 | 0.76371 | 1.6125 | 1.6036 | 1.5949 | 1.5864 | 1.5756 | 1.565 | 1.5547 | 1.5443 | 1.5295 | 1.5151 | 1.5011 | 1.4295 | 0.89149 | 0.75835 | 1.4988 | 1.4868 | 1.4751 | 1.4637 | 1.4498 | 1.4364 | 1.4233 | 1.4101 | 1.3908 | 1.3721 | 1.3539 | 0.91935 | 0.77207 | 0.61349
|  | LOWER OLLACH | FS |  |  |  | 1.5998 | 1.5861 | 1.5657 | 1.5456 | 1.5258 | 1.5062 | 1.4869 | 1.4679 | 1.4491 | 1.4306 | 1.4124 | 1.3032 | 0.93684 | 0.81583 | 1.6038 | 1.595 | 1.5819 | 1.569 | 1.5561 | 1.5434 | 1.5308 | 1.5183 | 1.5061 | 1.494 | 1.4821 | 1.411 | 0.94426 | 0.84477 | 1.4868 | 1.4748 | 1.457 | 1.4394 | 1.4221 | 1.405 | 1.3881 | 1.3715 | 1.3551 | 1.339 | 1.323 | 0.93225 | 0.79998 | 0.67393
| KILLIN | LUBNAIG | MINIMUM HEADROOM | NN 57455 13800 | YES | YES | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.064387 | 0.062517 | 0.20588 | 0.20567 | 0.20562 | 0.20558 | 0.20553 | 0.20551 | 0.20551 | 0.20551 | 0.20551 | 0.20551 | 0.20551 | 0.19796 | 0.086034 | 0.083935 | 0.20672 | 0.20672 | 0.20672 | 0.20672 | 0.20672 | 0.20672 | 0.20672 | 0.20672 | 0.20672 | 0.20672 | 0.20672 | 0.19875 | 0.058983 | 0.056921
|  | LUBNAIG | CT |  |  |  | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.066657 | 0.065349 | 0.2059 | 0.20572 | 0.20564 | 0.20561 | 0.20558 | 0.20555 | 0.20553 | 0.20551 | 0.20551 | 0.20551 | 0.20551 | 0.20551 | 0.088583 | 0.087114 | 0.20672 | 0.20672 | 0.20672 | 0.20672 | 0.20672 | 0.20672 | 0.20672 | 0.20672 | 0.20672 | 0.20672 | 0.20672 | 0.20672 | 0.061327 | 0.059976
|  | LUBNAIG | LW |  |  |  | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.064387 | 0.062517 | 0.20588 | 0.20567 | 0.20562 | 0.20558 | 0.20553 | 0.20551 | 0.20551 | 0.20551 | 0.20551 | 0.20551 | 0.20551 | 0.19796 | 0.086034 | 0.083935 | 0.20672 | 0.20672 | 0.20672 | 0.20672 | 0.20672 | 0.20672 | 0.20672 | 0.20672 | 0.20672 | 0.20672 | 0.20672 | 0.19875 | 0.058983 | 0.056921
|  | LUBNAIG | ST |  |  |  | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.13754 | 0.13672 | 0.20596 | 0.20589 | 0.20578 | 0.20567 | 0.20564 | 0.20562 | 0.2056 | 0.20558 | 0.20556 | 0.20555 | 0.20553 | 0.20551 | 0.14616 | 0.14524 | 0.20672 | 0.20672 | 0.20672 | 0.20672 | 0.20672 | 0.20672 | 0.20672 | 0.20672 | 0.20672 | 0.20672 | 0.20672 | 0.20672 | 0.13277 | 0.13191
|  | LUBNAIG | FS |  |  |  | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.206 | 0.206 | 0.20596 | 0.20593 | 0.20588 | 0.20584 | 0.20579 | 0.20573 | 0.20569 | 0.20566 | 0.20565 | 0.20561 | 0.20558 | 0.20555 | 0.20672 | 0.20672 | 0.20672 | 0.20672 | 0.20672 | 0.20672 | 0.20672 | 0.20672 | 0.20672 | 0.20672 | 0.20672 | 0.20672 | 0.20672 | 0.20672
| LUNANHEAD | LUNANHEAD | MINIMUM HEADROOM | NO 47042 51733 | NO | YES | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 12.8754 | 11.3973 | 10.9153 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 11.8297 | 10.4735 | 9.9247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.7879 | 12.6941 | 11.217 | 9.6493 | 9.0832
|  | LUNANHEAD | CT |  |  |  | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.212 | 11.8504 | 11.4834 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.2129 | 10.9893 | 10.5716 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 11.6123 | 10.1815 | 9.7505
|  | LUNANHEAD | LW |  |  |  | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 12.8754 | 11.3973 | 10.9153 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 11.8297 | 10.4735 | 9.9247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.7879 | 12.6941 | 11.217 | 9.6493 | 9.0832
|  | LUNANHEAD | ST |  |  |  | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.6099 | 13.1881 | 13.0983 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.6158 | 12.3355 | 12.0984 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.4384 | 11.7311 | 11.4865
|  | LUNANHEAD | FS |  |  |  | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 13.9934 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8048 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247 | 12.8247
| PORT ANN | LUSSAGIVEN | MINIMUM HEADROOM | NR 63461 86798 | YES | YES | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.095523 | 0.089721 | 0.11034 | 0.1101 | 0.10983 | 0.10979 | 0.10979 | 0.10979 | 0.10979 | 0.10979 | 0.10979 | 0.10979 | 0.099109 | 0.092213 | 0.085283 | 0.078437 | 0.11215 | 0.11208 | 0.11198 | 0.11191 | 0.11191 | 0.11191 | 0.11191 | 0.11191 | 0.11191 | 0.11191 | 0.099871 | 0.092973 | 0.08604 | 0.079193
|  | LUSSAGIVEN | CT |  |  |  | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.099276 | 0.094089 | 0.11036 | 0.11017 | 0.10998 | 0.1098 | 0.10979 | 0.10979 | 0.10979 | 0.10979 | 0.10979 | 0.10979 | 0.10979 | 0.095904 | 0.08971 | 0.083591 | 0.11216 | 0.1121 | 0.11203 | 0.11197 | 0.11191 | 0.11191 | 0.11191 | 0.11191 | 0.11191 | 0.11191 | 0.11191 | 0.096665 | 0.090469 | 0.084348
|  | LUSSAGIVEN | LW |  |  |  | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.095523 | 0.089721 | 0.11034 | 0.1101 | 0.10983 | 0.10979 | 0.10979 | 0.10979 | 0.10979 | 0.10979 | 0.10979 | 0.10979 | 0.099109 | 0.092213 | 0.085283 | 0.078437 | 0.11215 | 0.11208 | 0.11198 | 0.11191 | 0.11191 | 0.11191 | 0.11191 | 0.11191 | 0.11191 | 0.11191 | 0.099871 | 0.092973 | 0.08604 | 0.079193
|  | LUSSAGIVEN | ST |  |  |  | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.11047 | 0.11034 | 0.11022 | 0.1101 | 0.10993 | 0.10979 | 0.10979 | 0.10979 | 0.10979 | 0.10979 | 0.10979 | 0.10979 | 0.097438 | 0.094419 | 0.11218 | 0.11215 | 0.11212 | 0.11207 | 0.11202 | 0.11196 | 0.11191 | 0.11191 | 0.11191 | 0.11191 | 0.11191 | 0.11191 | 0.0982 | 0.095179
|  | LUSSAGIVEN | FS |  |  |  | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.1188 | 0.11054 | 0.11053 | 0.11048 | 0.11041 | 0.11031 | 0.11025 | 0.11018 | 0.11011 | 0.11004 | 0.10997 | 0.10991 | 0.10979 | 0.10979 | 0.10979 | 0.11221 | 0.1122 | 0.11218 | 0.11217 | 0.11215 | 0.11213 | 0.1121 | 0.11208 | 0.11205 | 0.11203 | 0.11201 | 0.11191 | 0.11191 | 0.11191
| LYNDHURST | LYNDHURST | MINIMUM HEADROOM | NO 37434 32575 | NO | YES | 18.2689 | 18.2481 | 18.2226 | 18.1981 | 18.1727 | 18.1466 | 18.121 | 18.0921 | 18.0615 | 18.0304 | 17.9998 | 17.8152 | 17.7871 | 17.7688 | 16.3036 | 16.2789 | 16.2523 | 16.229 | 16.205 | 16.1802 | 16.1575 | 16.1367 | 16.1147 | 16.0924 | 16.0704 | 15.9185 | 15.8992 | 15.8878 | 16.3999 | 16.3773 | 16.3497 | 16.3231 | 16.2956 | 16.2673 | 16.2395 | 16.2082 | 16.1849 | 16.1761 | 16.1675 | 16.1068 | 16.05 | 16.011
|  | LYNDHURST | CT |  |  |  | 18.2692 | 18.2519 | 18.2321 | 18.2128 | 18.1935 | 18.1751 | 18.157 | 18.1369 | 18.1134 | 18.0891 | 18.0649 | 17.8968 | 17.8022 | 17.788 | 16.3038 | 16.2834 | 16.2613 | 16.2429 | 16.2246 | 16.2071 | 16.1901 | 16.171 | 16.152 | 16.1346 | 16.1171 | 15.9964 | 15.9086 | 15.8998 | 16.4002 | 16.3814 | 16.36 | 16.339 | 16.3181 | 16.2981 | 16.2786 | 16.2568 | 16.2313 | 16.205 | 16.1858 | 16.1383 | 16.0942 | 16.0526
|  | LYNDHURST | LW |  |  |  | 18.2689 | 18.2481 | 18.2226 | 18.1981 | 18.1727 | 18.1466 | 18.121 | 18.0921 | 18.0615 | 18.0304 | 17.9998 | 17.8152 | 17.7871 | 17.7688 | 16.3036 | 16.2789 | 16.2523 | 16.229 | 16.205 | 16.1802 | 16.1575 | 16.1367 | 16.1147 | 16.0924 | 16.0704 | 15.9185 | 15.8992 | 15.8878 | 16.3999 | 16.3773 | 16.3497 | 16.3231 | 16.2956 | 16.2673 | 16.2395 | 16.2082 | 16.1849 | 16.1761 | 16.1675 | 16.1068 | 16.05 | 16.011
|  | LYNDHURST | ST |  |  |  | 18.2757 | 18.2693 | 18.2594 | 18.2477 | 18.2312 | 18.2155 | 18.2001 | 18.1831 | 18.1638 | 18.1441 | 18.1246 | 18.0296 | 17.946 | 17.8749 | 16.3115 | 16.304 | 16.2923 | 16.2785 | 16.2604 | 16.2455 | 16.2309 | 16.2147 | 16.1965 | 16.1778 | 16.16 | 16.0918 | 16.0318 | 15.9752 | 16.4072 | 16.4003 | 16.3896 | 16.3769 | 16.3591 | 16.342 | 16.3253 | 16.3068 | 16.286 | 16.2646 | 16.2434 | 16.1759 | 16.1522 | 16.13
|  | LYNDHURST | FS |  |  |  | 18.2793 | 18.2787 | 18.2758 | 18.2726 | 18.2671 | 18.2616 | 18.2546 | 18.2472 | 18.2396 | 18.2319 | 18.2244 | 18.1865 | 18.1539 | 18.125 | 16.3158 | 16.3151 | 16.3117 | 16.3079 | 16.3014 | 16.2949 | 16.2866 | 16.2779 | 16.2689 | 16.2611 | 16.2539 | 16.218 | 16.1871 | 16.1603 | 16.4112 | 16.4105 | 16.4074 | 16.4039 | 16.3979 | 16.392 | 16.3843 | 16.3764 | 16.3681 | 16.3598 | 16.3516 | 16.3105 | 16.2752 | 16.2438
| THURSO | LYNESS | MINIMUM HEADROOM | ND 30350 94625 | YES | YES | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 0.23616 | 0.19934 | 0.16285 | 1.3246 | 1.3246 | 1.3246 | 1.3246 | 1.3246 | 1.3246 | 1.3246 | 1.3246 | 1.3246 | 1.3246 | 1.3246 | 0.36827 | 0.32157 | 0.27528 | 1.4252 | 1.4252 | 1.4252 | 1.4252 | 1.4252 | 1.4252 | 1.4252 | 1.4252 | 1.4252 | 1.4252 | 1.4252 | 0.19016 | 0.14636 | 0.10295
|  | LYNESS | CT |  |  |  | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 0.25311 | 0.22562 | 0.19842 | 1.3246 | 1.3246 | 1.3246 | 1.3246 | 1.3246 | 1.3246 | 1.3246 | 1.3246 | 1.3246 | 1.3246 | 1.3246 | 0.38976 | 0.35491 | 0.3204 | 1.4252 | 1.4252 | 1.4252 | 1.4252 | 1.4252 | 1.4252 | 1.4252 | 1.4252 | 1.4252 | 1.4252 | 1.4252 | 0.21031 | 0.17762 | 0.14527
|  | LYNESS | LW |  |  |  | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 0.23616 | 0.19934 | 0.16285 | 1.3246 | 1.3246 | 1.3246 | 1.3246 | 1.3246 | 1.3246 | 1.3246 | 1.3246 | 1.3246 | 1.3246 | 1.3246 | 0.36827 | 0.32157 | 0.27528 | 1.4252 | 1.4252 | 1.4252 | 1.4252 | 1.4252 | 1.4252 | 1.4252 | 1.4252 | 1.4252 | 1.4252 | 1.4252 | 0.19016 | 0.14636 | 0.10295
|  | LYNESS | ST |  |  |  | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 0.66749 | 0.65178 | 0.6361 | 1.3246 | 1.3246 | 1.3246 | 1.3246 | 1.3246 | 1.3246 | 1.3246 | 1.3246 | 1.3246 | 1.3246 | 1.3246 | 0.71348 | 0.69356 | 0.67367 | 1.4252 | 1.4252 | 1.4252 | 1.4252 | 1.4252 | 1.4252 | 1.4252 | 1.4252 | 1.4252 | 1.4252 | 1.4252 | 0.62965 | 0.61097 | 0.59232
|  | LYNESS | FS |  |  |  | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3481 | 1.3246 | 1.3246 | 1.3246 | 1.3246 | 1.3246 | 1.3246 | 1.3246 | 1.3246 | 1.3246 | 1.3246 | 1.3246 | 1.3246 | 1.3246 | 1.3246 | 1.4252 | 1.4252 | 1.4252 | 1.4252 | 1.4252 | 1.4252 | 1.4252 | 1.4252 | 1.4252 | 1.4252 | 1.4252 | 1.4252 | 1.4252 | 1.4252
| STORNOWAY | MAARUIG | MINIMUM HEADROOM | NB 19162 06332 | YES | YES | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.21962 | 0.21942 | 0.21919 | 0.21895 | 0.21873 | 0.21851 | 0.21833 | 0.21815 | 0.21797 | 0.2178 | 0.21774 | 0.21755 | 0.19828 | 0.19175 | 0.22216 | 0.22207 | 0.22195 | 0.22184 | 0.22182 | 0.22182 | 0.22182 | 0.22182 | 0.22182 | 0.22182 | 0.22182 | 0.22182 | 0.22182 | 0.19555
|  | MAARUIG | CT |  |  |  | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.21963 | 0.21948 | 0.21932 | 0.21915 | 0.219 | 0.21884 | 0.21869 | 0.21853 | 0.21838 | 0.21826 | 0.21814 | 0.21755 | 0.21755 | 0.19778 | 0.22217 | 0.2221 | 0.22202 | 0.22194 | 0.22186 | 0.22182 | 0.22182 | 0.22182 | 0.22182 | 0.22182 | 0.22182 | 0.22182 | 0.22182 | 0.22182
|  | MAARUIG | LW |  |  |  | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.21962 | 0.21942 | 0.21919 | 0.21895 | 0.21873 | 0.21851 | 0.21833 | 0.21815 | 0.21797 | 0.2178 | 0.21774 | 0.21755 | 0.19828 | 0.19175 | 0.22216 | 0.22207 | 0.22195 | 0.22184 | 0.22182 | 0.22182 | 0.22182 | 0.22182 | 0.22182 | 0.22182 | 0.22182 | 0.22182 | 0.22182 | 0.19555
|  | MAARUIG | ST |  |  |  | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.21968 | 0.21962 | 0.21953 | 0.21942 | 0.21913 | 0.21885 | 0.21857 | 0.21831 | 0.21809 | 0.21787 | 0.21774 | 0.21755 | 0.21755 | 0.21755 | 0.22219 | 0.22217 | 0.22212 | 0.22207 | 0.22193 | 0.22182 | 0.22182 | 0.22182 | 0.22182 | 0.22182 | 0.22182 | 0.22182 | 0.22182 | 0.22182
|  | MAARUIG | FS |  |  |  | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.23594 | 0.21971 | 0.21971 | 0.21968 | 0.21965 | 0.21956 | 0.21946 | 0.21934 | 0.21922 | 0.2191 | 0.21898 | 0.21887 | 0.21835 | 0.21797 | 0.21773 | 0.22221 | 0.22221 | 0.2222 | 0.22218 | 0.22213 | 0.22209 | 0.22203 | 0.22197 | 0.22191 | 0.22185 | 0.22182 | 0.22182 | 0.22182 | 0.22182
| LYNDHURST | MACALPINE ROAD | MINIMUM HEADROOM | NO 38034 33691 | NO | YES | 19.464 | 19.3327 | 19.2084 | 19.0934 | 18.9822 | 18.8745 | 18.7695 | 18.7013 | 18.6551 | 18.609 | 18.5637 | 18.3657 | 18.172 | 14.2622 | 17.8388 | 17.7777 | 17.7226 | 17.6695 | 17.6184 | 17.5692 | 17.522 | 17.4965 | 17.4839 | 17.4714 | 14.9894 | 14.0933 | 13.2237 | 12.3824 | 17.9068 | 17.7749 | 17.6707 | 17.5701 | 17.4733 | 17.3802 | 17.2909 | 17.2427 | 17.2188 | 17.1951 | 17.1717 | 14.2111 | 13.3083 | 12.4385
|  | MACALPINE ROAD | CT |  |  |  | 19.464 | 19.3327 | 19.2084 | 19.0934 | 18.9822 | 18.8745 | 18.7695 | 18.7013 | 18.6551 | 18.609 | 18.5637 | 18.3657 | 18.172 | 14.7088 | 17.8388 | 17.7777 | 17.7226 | 17.6695 | 17.6184 | 17.5692 | 17.522 | 17.4965 | 17.4839 | 17.4714 | 17.459 | 14.4536 | 13.7903 | 13.1503 | 17.9068 | 17.7749 | 17.6707 | 17.5701 | 17.4733 | 17.3802 | 17.2909 | 17.2427 | 17.2188 | 17.1951 | 17.1717 | 14.4028 | 13.7203 | 13.0592
|  | MACALPINE ROAD | LW |  |  |  | 19.653 | 19.6051 | 19.5479 | 19.4955 | 19.4415 | 19.386 | 19.3298 | 19.2687 | 19.2061 | 19.1429 | 19.0798 | 18.8978 | 18.7197 | 14.2622 | 17.9468 | 17.9377 | 17.9273 | 17.916 | 17.9037 | 17.8905 | 17.8767 | 17.8618 | 17.8466 | 17.831 | 14.9894 | 14.0933 | 13.2237 | 12.3824 | 18.1138 | 18.0777 | 18.0582 | 18.0367 | 18.0134 | 17.9885 | 17.9623 | 17.9342 | 17.9053 | 17.8758 | 17.846 | 14.2111 | 13.3083 | 12.4385
|  | MACALPINE ROAD | ST |  |  |  | 19.6895 | 19.6722 | 19.6502 | 19.6296 | 19.6127 | 19.596 | 19.579 | 19.5618 | 19.5412 | 19.5208 | 19.501 | 19.3996 | 19.3093 | 19.219 | 17.9625 | 17.9588 | 17.9553 | 17.9518 | 17.9476 | 17.9435 | 17.9396 | 17.936 | 17.9307 | 17.9256 | 17.9206 | 17.8935 | 17.8695 | 17.8442 | 18.1528 | 18.135 | 18.1124 | 18.1045 | 18.0966 | 18.0888 | 18.0813 | 18.0745 | 18.0645 | 18.0548 | 18.0454 | 17.9942 | 17.9488 | 17.9008
|  | MACALPINE ROAD | FS |  |  |  | 19.6875 | 19.6787 | 19.6638 | 19.6501 | 19.6375 | 19.6249 | 19.6117 | 19.5985 | 19.5852 | 19.5721 | 19.5592 | 19.487 | 19.416 | 19.3487 | 17.9588 | 17.9552 | 17.9498 | 17.9445 | 17.9392 | 17.934 | 17.9289 | 17.9239 | 17.9189 | 17.914 | 17.9092 | 17.8802 | 17.8504 | 17.8216 | 18.1646 | 18.1469 | 18.125 | 18.1104 | 18.0969 | 18.0835 | 18.0695 | 18.0554 | 18.0422 | 18.033 | 18.0238 | 17.969 | 17.9126 | 17.858
| MACDUFF | MACDUFF | MINIMUM HEADROOM | NJ 70363 63908 | NO | YES | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468
|  | MACDUFF | CT |  |  |  | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468
|  | MACDUFF | LW |  |  |  | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468
|  | MACDUFF | ST |  |  |  | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468
|  | MACDUFF | FS |  |  |  | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 23.8941 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.5527 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468 | 22.6468
| CARRADALE | MACHRIE | MINIMUM HEADROOM | NR 90092 33864 | YES | YES | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.3855 | 3.3706 | 3.3535 | 3.3366 | 3.3201 | 3.3039 | 3.2879 | 3.2726 | 3.2713 | 3.2699 | 3.2686 | 2.4799 | 2.3676 | 2.2572 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683
|  | MACHRIE | CT |  |  |  | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.3855 | 3.3706 | 3.3535 | 3.3366 | 3.3201 | 3.3039 | 3.2879 | 3.2726 | 3.2713 | 3.2699 | 3.2686 | 2.4799 | 2.3676 | 2.2572 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683
|  | MACHRIE | LW |  |  |  | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.3938 | 3.392 | 3.3898 | 3.3876 | 3.3855 | 3.3834 | 3.3814 | 3.3792 | 3.377 | 3.3748 | 3.3727 | 3.2802 | 3.266 | 2.398 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683
|  | MACHRIE | ST |  |  |  | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.3944 | 3.3938 | 3.393 | 3.392 | 3.3837 | 3.3756 | 3.3676 | 3.3591 | 3.3507 | 3.3424 | 3.3343 | 3.2945 | 3.2714 | 3.2683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683
|  | MACHRIE | FS |  |  |  | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.7951 | 3.3947 | 3.3947 | 3.3944 | 3.3941 | 3.3914 | 3.3887 | 3.3852 | 3.3818 | 3.3785 | 3.3752 | 3.372 | 3.3566 | 3.3423 | 3.3288 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683
| FORT WILLIAM | MALLAIG | MINIMUM HEADROOM | NM 67637 94811 | YES | YES | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 7.4771
|  | MALLAIG | CT |  |  |  | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317
|  | MALLAIG | LW |  |  |  | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 7.4771
|  | MALLAIG | ST |  |  |  | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317
|  | MALLAIG | FS |  |  |  | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.3022 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317 | 8.1317
| KEITH | MARNOCH | MINIMUM HEADROOM | NJ 61955 53001 | NO | YES | 2.6423 | 2.6423 | 2.6423 | 2.6423 | 2.6423 | 2.6423 | 2.6423 | 2.6423 | 2.6423 | 2.6423 | 2.6211 | 1.9045 | -0.28183 | -0.40864 | 4.6875 | 4.6391 | 4.5767 | 4.5146 | 4.4528 | 4.3912 | 4.3308 | 4.2656 | 4.2015 | 4.137 | 4.073 | 3.3539 | 1.5344 | 1.2598 | 2.8672 | 2.8672 | 2.8672 | 2.8672 | 2.8672 | 2.8672 | 2.8672 | 2.8672 | 2.8672 | 2.8672 | 2.8672 | 2.3886 | 0.42805 | 0.16425
|  | MARNOCH | CT |  |  |  | 2.6423 | 2.6423 | 2.6423 | 2.6423 | 2.6423 | 2.6423 | 2.6423 | 2.6423 | 2.6423 | 2.6423 | 2.6423 | 1.9484 | -0.22993 | -0.349 | 4.6875 | 4.6407 | 4.5867 | 4.5329 | 4.4795 | 4.4263 | 4.374 | 4.3176 | 4.2622 | 4.2064 | 4.151 | 3.4491 | 1.6468 | 1.389 | 2.8672 | 2.8672 | 2.8672 | 2.8672 | 2.8672 | 2.8672 | 2.8672 | 2.8672 | 2.8672 | 2.8672 | 2.8672 | 2.3886 | 0.53385 | 0.28832
|  | MARNOCH | LW |  |  |  | 2.6423 | 2.6423 | 2.6423 | 2.6423 | 2.6423 | 2.6423 | 2.6423 | 2.6423 | 2.6423 | 2.6423 | 2.6211 | 1.9045 | -0.28183 | -0.40864 | 4.6898 | 4.6391 | 4.5767 | 4.5146 | 4.4528 | 4.3912 | 4.3308 | 4.2656 | 4.2015 | 4.137 | 4.073 | 3.3539 | 1.5344 | 1.2598 | 2.8672 | 2.8672 | 2.8672 | 2.8672 | 2.8672 | 2.8672 | 2.8672 | 2.8672 | 2.8672 | 2.8672 | 2.8672 | 2.3886 | 0.42805 | 0.16425
|  | MARNOCH | ST |  |  |  | 2.6423 | 2.6423 | 2.6423 | 2.6423 | 2.6423 | 2.6423 | 2.6423 | 2.6423 | 2.6423 | 2.6423 | 2.6423 | 2.3855 | 1.3787 | 1.3241 | 4.7099 | 4.7002 | 4.6851 | 4.6668 | 4.6418 | 4.6169 | 4.5924 | 4.566 | 4.5405 | 4.5148 | 4.4895 | 4.1463 | 3.2564 | 3.1382 | 2.8672 | 2.8672 | 2.8672 | 2.8672 | 2.8672 | 2.8672 | 2.8672 | 2.8672 | 2.8672 | 2.8672 | 2.8672 | 2.6279 | 1.7903 | 1.7903
|  | MARNOCH | FS |  |  |  | 2.6423 | 2.6423 | 2.6423 | 2.6423 | 2.6423 | 2.6423 | 2.6423 | 2.6423 | 2.6423 | 2.6423 | 2.6423 | 2.6423 | 2.6423 | 2.6423 | 4.7149 | 4.7136 | 4.7073 | 4.6998 | 4.6913 | 4.6828 | 4.6721 | 4.6616 | 4.6515 | 4.6413 | 4.6312 | 4.5828 | 4.5371 | 4.4941 | 2.8672 | 2.8672 | 2.8672 | 2.8672 | 2.8672 | 2.8672 | 2.8672 | 2.8672 | 2.8672 | 2.8672 | 2.8672 | 2.8672 | 2.8672 | 2.8672
| BEAULY | MARYBANK | MINIMUM HEADROOM | NH 46749 53948 | YES | YES | 3.8754 | 3.5861 | 3.291 | 3.0056 | 2.7296 | 2.4632 | 2.1754 | 2.0062 | 1.8945 | 1.7823 | 1.6712 | 1.2675 | 0.8549 | 0.42714 | 3.8096 | 3.5672 | 3.3173 | 3.0753 | 2.8411 | 2.6145 | 2.3589 | 2.2052 | 2.096 | 1.986 | 1.877 | 1.5139 | 1.1459 | 0.76184 | 3.7293 | 3.4368 | 3.1383 | 2.8484 | 2.564 | 2.2892 | 1.9879 | 1.8093 | 1.6882 | 1.5664 | 1.4457 | 1.0212 | 0.58855 | 0.14103
|  | MARYBANK | CT |  |  |  | 3.8754 | 3.5861 | 3.291 | 3.0056 | 2.7296 | 2.4632 | 2.1754 | 2.0062 | 1.8945 | 1.7823 | 1.6712 | 1.2675 | 0.8549 | 0.42714 | 3.8096 | 3.5672 | 3.3173 | 3.0753 | 2.8411 | 2.6145 | 2.3589 | 2.2052 | 2.096 | 1.986 | 1.877 | 1.5139 | 1.1459 | 0.76184 | 3.7293 | 3.4368 | 3.1383 | 2.8484 | 2.564 | 2.2892 | 1.9879 | 1.8093 | 1.6882 | 1.5664 | 1.4457 | 1.0212 | 0.58855 | 0.14103
|  | MARYBANK | LW |  |  |  | 4.7923 | 4.7597 | 4.723 | 3.9385 | 3.8082 | 3.6758 | 3.504 | 3.3574 | 3.2095 | 3.0614 | 2.913 | 2.4109 | 1.8622 | 1.2495 | 4.8107 | 4.7574 | 3.8892 | 3.7556 | 3.6209 | 3.4852 | 3.3038 | 3.1545 | 3.0044 | 2.8547 | 2.705 | 2.2501 | 1.7589 | 1.2197 | 4.6671 | 4.6306 | 3.9012 | 3.7566 | 3.6101 | 3.462 | 3.2669 | 3.1032 | 2.9384 | 2.7737 | 2.6088 | 2.0776 | 1.5 | 0.85998
|  | MARYBANK | ST |  |  |  | 4.8481 | 4.8351 | 4.8225 | 4.8102 | 4.7952 | 4.7807 | 4.7665 | 4.7523 | 4.7316 | 4.7115 | 3.9891 | 3.8021 | 3.6265 | 3.4415 | 4.8528 | 4.8351 | 4.8118 | 4.7854 | 4.7696 | 4.7543 | 3.9521 | 3.921 | 3.8845 | 3.8477 | 3.8115 | 3.6358 | 3.471 | 3.2991 | 4.7204 | 4.7066 | 4.6919 | 4.6769 | 4.6618 | 4.6471 | 3.975 | 3.9402 | 3.8985 | 3.8565 | 3.8154 | 3.6143 | 3.4255 | 3.2276
|  | MARYBANK | FS |  |  |  | 4.8351 | 4.8222 | 4.8029 | 4.784 | 4.7653 | 4.7468 | 4.7286 | 4.7106 | 4.6929 | 4.6755 | 4.6583 | 3.9674 | 3.8299 | 3.6992 | 4.8516 | 4.8437 | 4.8285 | 4.8125 | 4.7997 | 4.7872 | 4.7698 | 4.7567 | 4.7438 | 3.9951 | 3.9728 | 3.8498 | 3.7333 | 3.6226 | 4.7097 | 4.6976 | 4.6791 | 4.6607 | 4.6431 | 4.6257 | 4.6076 | 4.5906 | 4.5738 | 3.9917 | 3.9658 | 3.8201 | 3.6805 | 3.5459
| LUNANHEAD | MARYTON | MINIMUM HEADROOM | NO 39206 53075 | NO | YES | 17.9012 | 17.557 | 14.3862 | 14.0939 | 13.8123 | 13.5417 | 13.2819 | 13.1807 | 13.1304 | 13.0709 | 12.9357 | 11.6244 | 10.9764 | 10.3425 | 13.5167 | 13.1411 | 12.758 | 12.3887 | 12.0378 | 11.6967 | 11.3641 | 11.1626 | 11.0067 | 10.8522 | 10.7084 | 9.4683 | 8.7449 | 8.0343 | 13.129 | 12.68 | 12.2293 | 11.7948 | 11.3805 | 10.979 | 10.589 | 10.3722 | 10.2047 | 10.0388 | 9.8836 | 8.4549 | 7.694 | 6.9482
|  | MARYTON | CT |  |  |  | 17.9012 | 17.557 | 14.3862 | 14.0939 | 13.8123 | 13.5417 | 13.2819 | 13.1807 | 13.1304 | 13.0709 | 12.9357 | 11.6244 | 10.9764 | 10.3425 | 13.5167 | 13.1411 | 12.758 | 12.3887 | 12.0378 | 11.6967 | 11.3641 | 11.1626 | 11.0067 | 10.8522 | 10.7084 | 9.4683 | 8.7449 | 8.0343 | 13.129 | 12.68 | 12.2293 | 11.7948 | 11.3805 | 10.979 | 10.589 | 10.3722 | 10.2047 | 10.0388 | 9.8836 | 8.4549 | 7.694 | 6.9482
|  | MARYTON | LW |  |  |  | 18.496 | 18.436 | 18.3671 | 18.2928 | 18.2141 | 18.131 | 18.044 | 17.9734 | 17.9095 | 17.8479 | 17.7854 | 13.3555 | 12.4456 | 11.5433 | 15.6012 | 15.5723 | 13.6559 | 13.4613 | 13.2728 | 13.0823 | 12.8902 | 12.702 | 12.5125 | 12.3217 | 12.1408 | 10.6126 | 9.5973 | 8.5906 | 13.774 | 13.6182 | 13.4288 | 13.2372 | 13.0458 | 12.8393 | 12.6304 | 12.4297 | 12.2272 | 12.0232 | 11.8287 | 10.0965 | 9.0283 | 7.969
|  | MARYTON | ST |  |  |  | 18.5854 | 18.5623 | 18.538 | 18.5136 | 18.4841 | 18.4553 | 18.4271 | 18.399 | 18.3613 | 18.3245 | 18.2892 | 17.8759 | 17.7763 | 14.526 | 15.6507 | 15.6392 | 15.628 | 15.6171 | 15.6038 | 13.7182 | 13.6233 | 13.5219 | 13.4133 | 13.3066 | 13.2087 | 12.5236 | 12.0909 | 11.6785 | 15.7365 | 15.716 | 13.7754 | 13.6982 | 13.6063 | 13.5156 | 13.4253 | 13.3296 | 13.2217 | 13.1089 | 13.0048 | 12.2294 | 11.7771 | 11.3515
|  | MARYTON | FS |  |  |  | 18.5705 | 18.55 | 18.5187 | 18.4877 | 18.4566 | 18.4259 | 18.3949 | 18.3645 | 18.3344 | 18.3047 | 18.2757 | 18.1047 | 17.9715 | 17.8528 | 15.6392 | 15.6277 | 15.6106 | 15.5938 | 15.5772 | 15.5608 | 15.5447 | 15.5288 | 13.7845 | 13.7296 | 13.6776 | 13.4038 | 13.1725 | 12.9595 | 15.716 | 15.6956 | 15.6654 | 15.6355 | 13.7541 | 13.7 | 13.6403 | 13.5814 | 13.5232 | 13.4657 | 13.4109 | 13.1151 | 12.8697 | 12.644
| STRICHEN | MAUD | MINIMUM HEADROOM | NJ 92528 47491 | NO | YES | 6.3467 | 6.2443 | 6.1448 | 6.0488 | 5.9564 | 5.8676 | 5.7824 | 5.7317 | 5.7065 | 5.6816 | 5.657 | 4.505 | 3.0228 | 2.6496 | 5.9188 | 5.7917 | 5.6612 | 5.5339 | 5.4098 | 5.2887 | 5.1715 | 5.0811 | 5.0139 | 4.9464 | 4.8797 | 3.8421 | 2.6016 | 2.2087 | 6.4533 | 6.3572 | 6.2634 | 6.1729 | 6.0856 | 5.9881 | 5.8482 | 5.7442 | 5.6703 | 5.5961 | 5.5228 | 4.2509 | 2.7143 | 2.2829
|  | MAUD | CT |  |  |  | 6.3467 | 6.2443 | 6.1448 | 6.0488 | 5.9564 | 5.8676 | 5.7824 | 5.7317 | 5.7065 | 5.6816 | 5.657 | 4.505 | 3.0228 | 2.6496 | 5.9188 | 5.7917 | 5.6612 | 5.5339 | 5.4098 | 5.2887 | 5.1715 | 5.0811 | 5.0139 | 4.9464 | 4.8797 | 3.8421 | 2.6016 | 2.2087 | 6.4533 | 6.3572 | 6.2634 | 6.1729 | 6.0856 | 5.9881 | 5.8482 | 5.7442 | 5.6703 | 5.5961 | 5.5228 | 4.2509 | 2.7143 | 2.2829
|  | MAUD | LW |  |  |  | 6.5279 | 6.5125 | 6.4952 | 6.4762 | 6.4555 | 6.4335 | 6.4102 | 6.3828 | 6.3545 | 6.3256 | 6.2964 | 5.0872 | 3.4853 | 2.9743 | 6.0785 | 6.0241 | 5.9584 | 5.8912 | 5.8227 | 5.753 | 5.6831 | 5.6057 | 5.5287 | 5.4504 | 5.3724 | 4.2276 | 2.8637 | 2.3343 | 6.6194 | 6.6029 | 6.584 | 6.5635 | 6.5415 | 6.5183 | 6.494 | 6.4424 | 6.3579 | 6.2719 | 6.1861 | 4.7981 | 3.1246 | 2.5387
|  | MAUD | ST |  |  |  | 6.5542 | 6.548 | 6.5421 | 6.5363 | 6.5292 | 6.5224 | 6.5157 | 6.5092 | 6.4997 | 6.4904 | 6.4814 | 6.0534 | 5.4659 | 5.2892 | 6.1147 | 6.097 | 6.0724 | 6.0439 | 6.0067 | 5.9698 | 5.9337 | 5.8953 | 5.8552 | 5.8153 | 5.7761 | 5.2499 | 4.6339 | 4.4395 | 6.6443 | 6.6379 | 6.6313 | 6.6246 | 6.6163 | 6.6081 | 6.6002 | 6.5922 | 6.5816 | 6.5712 | 6.5611 | 5.9988 | 5.2401 | 5.0313
|  | MAUD | FS |  |  |  | 6.548 | 6.5419 | 6.5329 | 6.5239 | 6.5151 | 6.5064 | 6.4979 | 6.4894 | 6.4811 | 6.4729 | 6.4648 | 6.4162 | 6.3649 | 6.315 | 6.171 | 6.1097 | 6.0961 | 6.0814 | 6.0633 | 6.0452 | 6.0246 | 6.0042 | 5.9844 | 5.9646 | 5.9452 | 5.8436 | 5.7427 | 5.6462 | 6.6424 | 6.6334 | 6.6248 | 6.6162 | 6.6075 | 6.5989 | 6.5902 | 6.5817 | 6.5733 | 6.565 | 6.5569 | 6.5088 | 6.4584 | 6.4095
| MYBSTER | MELVICH | MINIMUM HEADROOM | NC 88547 64274 | YES | YES | 1.4589 | 1.368 | 1.368 | 1.368 | 1.368 | 1.368 | 1.368 | 1.368 | 1.368 | 1.368 | 1.368 | 1.368 | 0.93365 | 0.85984 | 2.444 | 2.3856 | 2.3851 | 2.3847 | 2.3842 | 2.3838 | 2.3834 | 2.3829 | 2.3825 | 2.382 | 2.3816 | 2.373 | 2.3644 | 2.3559 | 3.004 | 2.9093 | 2.9089 | 2.9084 | 2.908 | 2.9075 | 2.9071 | 2.9066 | 2.9062 | 2.9057 | 2.9053 | 2.8967 | 2.888 | 2.8794
|  | MELVICH | CT |  |  |  | 1.4589 | 1.4589 | 1.4589 | 1.4589 | 1.4589 | 1.4589 | 1.4589 | 1.4589 | 1.4589 | 1.4589 | 1.4589 | 1.4589 | 1.4589 | 1.4589 | 2.444 | 2.4437 | 2.4434 | 2.4431 | 2.4428 | 2.4425 | 2.4422 | 2.4419 | 2.4415 | 2.4412 | 2.4409 | 2.4346 | 2.4282 | 2.4219 | 3.004 | 3.0037 | 3.0034 | 3.0031 | 3.0028 | 3.0025 | 3.0022 | 3.0018 | 3.0015 | 3.0012 | 3.0009 | 2.9945 | 2.988 | 2.9817
|  | MELVICH | LW |  |  |  | 1.4589 | 1.368 | 1.368 | 1.368 | 1.368 | 1.368 | 1.368 | 1.368 | 1.368 | 1.368 | 1.368 | 1.368 | 0.93365 | 0.85984 | 2.444 | 2.3856 | 2.3851 | 2.3847 | 2.3842 | 2.3838 | 2.3834 | 2.3829 | 2.3825 | 2.382 | 2.3816 | 2.373 | 2.3644 | 2.3559 | 3.004 | 2.9093 | 2.9089 | 2.9084 | 2.908 | 2.9075 | 2.9071 | 2.9066 | 2.9062 | 2.9057 | 2.9053 | 2.8967 | 2.888 | 2.8794
|  | MELVICH | ST |  |  |  | 1.4589 | 1.4589 | 1.4589 | 1.4589 | 1.4589 | 1.4589 | 1.4589 | 1.4589 | 1.4589 | 1.4589 | 1.4589 | 1.4589 | 1.4589 | 1.4589 | 2.4441 | 2.444 | 2.4438 | 2.4436 | 2.443 | 2.4423 | 2.4416 | 2.4409 | 2.4403 | 2.4396 | 2.4389 | 2.4357 | 2.4324 | 2.4292 | 3.0041 | 3.004 | 3.0038 | 3.0036 | 3.0029 | 3.0023 | 3.0016 | 3.0009 | 3.0002 | 2.9995 | 2.9989 | 2.9956 | 2.9923 | 2.9891
|  | MELVICH | FS |  |  |  | 1.4589 | 1.4589 | 1.4589 | 1.4589 | 1.4589 | 1.4589 | 1.4589 | 1.4589 | 1.4589 | 1.4589 | 1.4589 | 1.4589 | 1.4589 | 1.4589 | 2.4442 | 2.4442 | 2.4441 | 2.4441 | 2.4439 | 2.4436 | 2.4434 | 2.4431 | 2.4428 | 2.4425 | 2.4423 | 2.441 | 2.4398 | 2.4387 | 3.0042 | 3.0042 | 3.0041 | 3.0041 | 3.0039 | 3.0036 | 3.0033 | 3.0031 | 3.0028 | 3.0025 | 3.0023 | 3.001 | 2.9998 | 2.9987
| CHARLESTON | MENZIESHILL | MINIMUM HEADROOM | NO 35918 31022 | NO | YES | 29.1955 | 29.0382 | 28.884 | 28.7468 | 28.6127 | 28.4821 | 28.3601 | 28.2852 | 28.2319 | 28.1784 | 28.059 | 27.7961 | 27.5438 | 27.2882 | 25.3599 | 25.3065 | 25.2583 | 25.2117 | 25.167 | 25.1239 | 25.0826 | 25.0602 | 25.0491 | 25.0381 | 24.995 | 24.9443 | 18.2818 | 17.112 | 23.6652 | 23.5539 | 23.4533 | 23.3564 | 23.263 | 23.1732 | 23.0871 | 23.0405 | 23.0174 | 22.9945 | 22.9045 | 22.7988 | 18.4633 | 17.248
|  | MENZIESHILL | CT |  |  |  | 29.1955 | 29.0382 | 28.884 | 28.7468 | 28.6127 | 28.4821 | 28.3601 | 28.2852 | 28.2319 | 28.1784 | 28.059 | 27.7961 | 27.5438 | 27.2941 | 25.3599 | 25.3065 | 25.2583 | 25.2117 | 25.167 | 25.1239 | 25.0826 | 25.0602 | 25.0491 | 25.0381 | 24.995 | 24.9443 | 24.8927 | 18.9373 | 23.6652 | 23.5539 | 23.4533 | 23.3564 | 23.263 | 23.1732 | 23.0871 | 23.0405 | 23.0174 | 22.9945 | 22.9045 | 22.7988 | 22.6913 | 18.9463
|  | MENZIESHILL | LW |  |  |  | 29.3889 | 29.3065 | 29.2056 | 29.1187 | 29.0293 | 28.9528 | 28.8835 | 28.8075 | 28.7292 | 28.6501 | 28.5046 | 28.0716 | 27.6343 | 27.2882 | 25.4544 | 25.4464 | 25.4374 | 25.4275 | 25.4167 | 25.4052 | 25.3931 | 25.3801 | 25.3667 | 25.3531 | 25.3069 | 25.2337 | 18.2818 | 17.112 | 23.8622 | 23.8455 | 23.8267 | 23.806 | 23.7836 | 23.7596 | 23.7343 | 23.7072 | 23.6794 | 23.6509 | 23.5547 | 23.402 | 18.4633 | 17.248
|  | MENZIESHILL | ST |  |  |  | 29.4376 | 29.4038 | 29.3566 | 29.3117 | 29.2641 | 29.2168 | 29.1697 | 29.1197 | 29.0653 | 29.021 | 28.9492 | 28.7568 | 28.5816 | 28.4092 | 25.4681 | 25.4649 | 25.4618 | 25.4588 | 25.4551 | 25.4516 | 25.4481 | 25.4449 | 25.4403 | 25.4358 | 25.4153 | 25.3916 | 25.3705 | 25.3483 | 23.8907 | 23.8841 | 23.8776 | 23.8713 | 23.8637 | 23.8562 | 23.849 | 23.8424 | 23.8328 | 23.8234 | 23.7806 | 23.7312 | 23.6873 | 23.641
|  | MENZIESHILL | FS |  |  |  | 29.4457 | 29.4338 | 29.4114 | 29.3919 | 29.3694 | 29.347 | 29.3215 | 29.2959 | 29.27 | 29.2444 | 29.2192 | 29.0871 | 28.9627 | 28.854 | 25.4649 | 25.4617 | 25.457 | 25.4524 | 25.4478 | 25.4432 | 25.4388 | 25.4344 | 25.43 | 25.4257 | 25.4215 | 25.3962 | 25.3701 | 25.3449 | 23.8841 | 23.8775 | 23.8676 | 23.8579 | 23.8483 | 23.8389 | 23.8296 | 23.8204 | 23.8113 | 23.8024 | 23.7936 | 23.7408 | 23.6864 | 23.6339
| KINTORE | METHLICK | MINIMUM HEADROOM | NJ 85339 36835 | NO | YES | 3.1358 | 3.0321 | 2.9312 | 2.8334 | 2.738 | 2.6462 | 2.5581 | 2.5057 | 1.6509 | 1.5948 | 1.5393 | 0.74926 | 0.013396 | -0.27283 | 2.9583 | 2.8398 | 2.7196 | 2.6019 | 2.4854 | 2.3727 | 2.2638 | 2.1847 | 1.473 | 1.4183 | 1.3642 | 0.69173 | 0.062034 | -0.26954 | 2.9504 | 2.8058 | 2.6609 | 2.5205 | 2.3847 | 2.2533 | 2.1267 | 2.0387 | 1.1496 | 1.0924 | 1.0358 | 0.23718 | -0.50694 | -0.79816
|  | METHLICK | CT |  |  |  | 3.1358 | 3.0321 | 2.9312 | 2.8334 | 2.738 | 2.6462 | 2.5581 | 2.5057 | 1.6509 | 1.5948 | 1.5393 | 0.74926 | 0.013396 | -0.27283 | 2.9583 | 2.8398 | 2.7196 | 2.6019 | 2.4854 | 2.3727 | 2.2638 | 2.1847 | 1.473 | 1.4183 | 1.3642 | 0.69173 | 0.062034 | -0.20916 | 2.9504 | 2.8058 | 2.6609 | 2.5205 | 2.3847 | 2.2533 | 2.1267 | 2.0387 | 1.1496 | 1.0924 | 1.0358 | 0.23718 | -0.50694 | -0.79816
|  | METHLICK | LW |  |  |  | 3.3194 | 3.3039 | 3.2863 | 3.267 | 3.2461 | 3.2238 | 3.2002 | 3.1164 | 2.2046 | 2.1178 | 2.0309 | 1.1417 | 0.28497 | -0.1415 | 3.1091 | 3.044 | 2.9653 | 2.886 | 2.8062 | 2.726 | 2.6457 | 2.5569 | 1.8364 | 1.7477 | 1.659 | 0.88477 | 0.13591 | -0.26954 | 3.1558 | 3.0936 | 3.0189 | 2.943 | 2.8659 | 2.7879 | 2.7093 | 2.6216 | 1.702 | 1.6132 | 1.5244 | 0.6243 | -0.2431 | -0.67711
|  | METHLICK | ST |  |  |  | 3.346 | 3.3398 | 3.3338 | 3.3279 | 3.3208 | 3.3139 | 3.3071 | 3.3005 | 2.9339 | 2.9245 | 2.9153 | 2.6054 | 2.2398 | 2.0961 | 3.1492 | 3.1285 | 3.0995 | 3.0659 | 3.0393 | 3.0132 | 2.9876 | 2.9606 | 2.6193 | 2.5905 | 2.5623 | 2.2157 | 1.8947 | 1.7504 | 3.2012 | 3.181 | 3.1536 | 3.1224 | 3.0966 | 3.0713 | 3.0466 | 3.0208 | 2.576 | 2.5474 | 2.5195 | 2.1097 | 1.7395 | 1.5927
|  | METHLICK | FS |  |  |  | 3.3398 | 3.3336 | 3.3245 | 3.3154 | 3.3065 | 3.2977 | 3.289 | 3.2805 | 3.272 | 3.2637 | 3.2555 | 3.2063 | 3.1543 | 3.1037 | 3.1524 | 3.1458 | 3.1311 | 3.1152 | 3.1008 | 3.0866 | 3.0706 | 3.0549 | 3.0395 | 3.0243 | 3.0094 | 2.929 | 2.8485 | 2.7715 | 3.2014 | 3.1932 | 3.1768 | 3.1594 | 3.1434 | 3.1275 | 3.1103 | 3.0932 | 3.0765 | 3.0601 | 3.0438 | 2.9546 | 2.864 | 2.777
| SHETLAND | MID YELL | MINIMUM HEADROOM | HU4817291442 | YES | YES | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.6001 | 1.5987 | 1.5968 | 1.595 | 1.5924 | 1.5864 | 1.5805 | 1.5742 | 1.568 | 1.562 | 1.556 | 1.4916 | 1.4373 | 1.4291 | 1.4841 | 1.484 | 1.4839 | 1.4837 | 1.4836 | 1.4832 | 1.4829 | 1.4825 | 1.4821 | 1.4817 | 1.4814 | 1.4775 | 1.4731 | 1.4731
|  | MID YELL | CT |  |  |  | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.6002 | 1.5991 | 1.5978 | 1.5965 | 1.5953 | 1.5941 | 1.5929 | 1.5917 | 1.5905 | 1.5894 | 1.5882 | 1.5183 | 1.4477 | 1.4354 | 1.4842 | 1.484 | 1.4839 | 1.4838 | 1.4838 | 1.4837 | 1.4836 | 1.4835 | 1.4835 | 1.4834 | 1.4833 | 1.4791 | 1.4748 | 1.4731
|  | MID YELL | LW |  |  |  | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.6001 | 1.5987 | 1.5968 | 1.595 | 1.5933 | 1.5916 | 1.59 | 1.5882 | 1.5865 | 1.5849 | 1.5832 | 1.4916 | 1.4373 | 1.4291 | 1.4841 | 1.484 | 1.4839 | 1.4837 | 1.4836 | 1.4835 | 1.4834 | 1.4833 | 1.4832 | 1.4831 | 1.483 | 1.4775 | 1.4731 | 1.4731
|  | MID YELL | ST |  |  |  | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.6006 | 1.6001 | 1.5994 | 1.5985 | 1.5924 | 1.5864 | 1.5805 | 1.5742 | 1.568 | 1.562 | 1.556 | 1.5268 | 1.4979 | 1.4691 | 1.4845 | 1.4841 | 1.484 | 1.484 | 1.4836 | 1.4832 | 1.4829 | 1.4825 | 1.4821 | 1.4817 | 1.4814 | 1.4796 | 1.4779 | 1.4761
|  | MID YELL | FS |  |  |  | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.5297 | 1.6008 | 1.6008 | 1.6006 | 1.6003 | 1.598 | 1.5958 | 1.5928 | 1.59 | 1.5872 | 1.5845 | 1.5818 | 1.569 | 1.5571 | 1.5458 | 1.4848 | 1.4847 | 1.4845 | 1.4843 | 1.4839 | 1.4838 | 1.4836 | 1.4834 | 1.4833 | 1.4831 | 1.4829 | 1.4822 | 1.4815 | 1.4808
| KINTORE | MIDMAR | MINIMUM HEADROOM | NJ 68253 06875 | YES | YES | 4.4565 | 4.4565 | 4.4565 | 4.413 | 4.3657 | 4.3187 | 4.2724 | 4.2225 | 4.1731 | 4.1236 | 4.0745 | 3.4536 | 2.2165 | 2.0079 | 4.5745 | 4.5311 | 4.4773 | 4.4238 | 4.3708 | 4.3182 | 4.2665 | 4.2105 | 4.1553 | 4.0999 | 4.0449 | 3.4811 | 2.4245 | 2.1742 | 4.5083 | 4.4874 | 4.4536 | 4.42 | 4.3867 | 4.3537 | 4.3212 | 4.2703 | 4.216 | 4.1616 | 4.1077 | 3.4597 | 2.1863 | 1.9569
|  | MIDMAR | CT |  |  |  | 4.4565 | 4.4565 | 4.4565 | 4.4565 | 4.4527 | 4.4266 | 4.401 | 4.3733 | 4.346 | 4.3185 | 4.2912 | 3.7487 | 2.5906 | 2.4596 | 4.5815 | 4.5562 | 4.5268 | 4.4975 | 4.4682 | 4.4391 | 4.4104 | 4.3793 | 4.3488 | 4.318 | 4.2875 | 3.8114 | 2.8433 | 2.6966 | 4.5083 | 4.5032 | 4.4848 | 4.4663 | 4.448 | 4.4296 | 4.4116 | 4.3921 | 4.3729 | 4.3536 | 4.3344 | 3.784 | 2.5975 | 2.4534
|  | MIDMAR | LW |  |  |  | 4.4565 | 4.4565 | 4.4565 | 4.413 | 4.3657 | 4.3187 | 4.2724 | 4.2225 | 4.1731 | 4.1236 | 4.0745 | 3.4536 | 2.2165 | 2.0079 | 4.5745 | 4.5311 | 4.4773 | 4.4238 | 4.3708 | 4.3182 | 4.2665 | 4.2105 | 4.1553 | 4.0999 | 4.0449 | 3.4811 | 2.4245 | 2.1742 | 4.5083 | 4.4874 | 4.4536 | 4.42 | 4.3867 | 4.3537 | 4.3212 | 4.2703 | 4.216 | 4.1616 | 4.1077 | 3.4597 | 2.1863 | 1.9569
|  | MIDMAR | ST |  |  |  | 4.4565 | 4.4565 | 4.4565 | 4.4565 | 4.4565 | 4.4565 | 4.4467 | 4.4254 | 4.4046 | 4.3838 | 4.3633 | 4.0582 | 3.4474 | 3.3499 | 4.5882 | 4.5749 | 4.5541 | 4.5289 | 4.5062 | 4.4837 | 4.4616 | 4.4377 | 4.4144 | 4.3911 | 4.3682 | 4.0923 | 3.5726 | 3.4635 | 4.5083 | 4.5083 | 4.5019 | 4.486 | 4.4718 | 4.4576 | 4.4438 | 4.4288 | 4.4141 | 4.3995 | 4.3851 | 4.107 | 3.4788 | 3.3716
|  | MIDMAR | FS |  |  |  | 4.4565 | 4.4565 | 4.4565 | 4.4565 | 4.4565 | 4.4565 | 4.4565 | 4.4565 | 4.4565 | 4.4565 | 4.4565 | 4.4565 | 4.4324 | 4.4002 | 4.5956 | 4.5946 | 4.5887 | 4.5817 | 4.5747 | 4.5677 | 4.5587 | 4.5499 | 4.5413 | 4.5328 | 4.5243 | 4.4838 | 4.4455 | 4.4094 | 4.5083 | 4.5083 | 4.5083 | 4.5083 | 4.5083 | 4.5083 | 4.5048 | 4.4993 | 4.4939 | 4.4885 | 4.4832 | 4.4577 | 4.4337 | 4.411
| BRIDGE OF DUN | MILL RD | MINIMUM HEADROOM | NO 71317 57683 | NO | YES | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 15.1105 | 15.0726 | 15.0668 | 15.0612 | 15.0557 | 15.0503 | 15.045 | 15.0393 | 15.0337 | 15.0281 | 15.0225 | 14.9832 | 14.9448 | 14.9448 | 16.2327 | 16.2092 | 16.1807 | 16.1529 | 16.1257 | 16.1092 | 16.1001 | 16.0902 | 16.0804 | 16.0707 | 16.061 | 15.9928 | 15.9252 | 15.8736
|  | MILL RD | CT |  |  |  | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 15.1128 | 15.0844 | 15.0701 | 15.0661 | 15.0623 | 15.0585 | 15.0548 | 15.0508 | 15.0469 | 15.043 | 15.0391 | 15.0124 | 14.9857 | 14.9591 | 16.2341 | 16.2166 | 16.1967 | 16.1773 | 16.1583 | 16.1397 | 16.1216 | 16.1102 | 16.1034 | 16.0966 | 16.0898 | 16.0435 | 15.9973 | 15.951
|  | MILL RD | LW |  |  |  | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 15.1105 | 15.0726 | 15.0668 | 15.0612 | 15.0557 | 15.0503 | 15.045 | 15.0393 | 15.0337 | 15.0281 | 15.0225 | 14.9832 | 14.9448 | 14.9448 | 16.2327 | 16.2092 | 16.1807 | 16.1529 | 16.1257 | 16.1092 | 16.1001 | 16.0902 | 16.0804 | 16.0707 | 16.061 | 15.9928 | 15.9252 | 15.8736
|  | MILL RD | ST |  |  |  | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 15.1228 | 15.1113 | 15.0939 | 15.0731 | 15.0689 | 15.0652 | 15.0616 | 15.0577 | 15.0539 | 15.0502 | 15.0465 | 15.0281 | 15.0102 | 14.9921 | 16.2402 | 16.2332 | 16.2224 | 16.2096 | 16.191 | 16.1728 | 16.1551 | 16.1359 | 16.1171 | 16.109 | 16.1027 | 16.0707 | 16.0397 | 16.0083
|  | MILL RD | FS |  |  |  | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 16.4648 | 15.1292 | 15.1282 | 15.1232 | 15.1173 | 15.1075 | 15.0977 | 15.0853 | 15.073 | 15.0712 | 15.0697 | 15.0683 | 15.0612 | 15.0547 | 15.0485 | 16.2442 | 16.2436 | 16.2405 | 16.2369 | 16.2308 | 16.2248 | 16.2171 | 16.2095 | 16.2021 | 16.1949 | 16.1877 | 16.1531 | 16.1209 | 16.1061
| ABERNETHY | MILNATHORT | MINIMUM HEADROOM | NO 11900 05074 | NO | YES | 22.5375 | 22.1529 | 21.7752 | 21.4111 | 21.0604 | 20.7233 | 20.3997 | 20.2595 | 20.1898 | 20.1209 | 20.0529 | 14.4229 | 12.5399 | 11.1373 | 18.0564 | 17.818 | 17.6013 | 17.3992 | 17.212 | 13.4118 | 12.9498 | 12.6434 | 12.4003 | 12.161 | 11.9259 | 10.2805 | 7.9316 | 6.158 | 18.8898 | 18.5207 | 18.1583 | 17.8089 | 17.4724 | 13.7212 | 13.1828 | 12.8385 | 12.5725 | 12.3106 | 12.0531 | 10.3131 | 8.0348 | 6.1457
|  | MILNATHORT | CT |  |  |  | 22.5375 | 22.1529 | 21.7752 | 21.4111 | 21.0604 | 20.7233 | 20.3997 | 20.2595 | 20.1898 | 20.1209 | 20.0529 | 14.4229 | 12.5399 | 11.4147 | 18.0564 | 17.818 | 17.6013 | 17.3992 | 17.212 | 13.4118 | 12.9498 | 12.6434 | 12.4003 | 12.161 | 11.9259 | 10.3711 | 8.5553 | 7.3561 | 18.8898 | 18.5207 | 18.1583 | 17.8089 | 17.4724 | 13.7212 | 13.1828 | 12.8385 | 12.5725 | 12.3106 | 12.0531 | 10.3131 | 8.2652 | 6.9764
|  | MILNATHORT | LW |  |  |  | 23.2181 | 23.1604 | 23.0955 | 23.024 | 22.9464 | 22.8637 | 22.7762 | 22.7014 | 22.6244 | 22.5457 | 22.466 | 21.7211 | 12.7859 | 11.1373 | 18.4739 | 18.4108 | 18.3589 | 18.3178 | 18.2733 | 18.2258 | 18.1757 | 13.6264 | 13.2097 | 12.796 | 12.3787 | 10.2805 | 7.9316 | 6.158 | 19.5429 | 19.4875 | 19.4252 | 19.3566 | 19.2822 | 19.2028 | 19.1189 | 19.0471 | 18.9731 | 13.3842 | 12.9417 | 10.6507 | 8.0348 | 6.1457
|  | MILNATHORT | ST |  |  |  | 23.3168 | 23.2938 | 23.2715 | 23.2497 | 23.2232 | 23.1975 | 23.1725 | 23.1477 | 23.1116 | 23.0765 | 23.0423 | 22.7355 | 22.2658 | 22.153 | 18.5535 | 18.5191 | 18.4894 | 18.4574 | 18.4322 | 18.4174 | 18.4031 | 18.3888 | 18.3681 | 18.3479 | 18.3283 | 18.1523 | 12.9046 | 12.1694 | 19.6392 | 19.6165 | 19.5944 | 19.5732 | 19.5478 | 19.5231 | 19.4991 | 19.4754 | 19.4407 | 19.407 | 19.3742 | 19.0797 | 13.4458 | 12.6669
|  | MILNATHORT | FS |  |  |  | 23.2938 | 23.2709 | 23.2369 | 23.2033 | 23.1702 | 23.1376 | 23.1054 | 23.0736 | 23.0423 | 23.0115 | 22.9811 | 22.7988 | 22.6507 | 22.5168 | 18.5556 | 18.5353 | 18.4979 | 18.4685 | 18.4432 | 18.4182 | 18.3925 | 18.3675 | 18.3428 | 18.3185 | 18.2945 | 18.1886 | 18.1036 | 18.0268 | 19.6165 | 19.5938 | 19.5609 | 19.5287 | 19.4969 | 19.4656 | 19.4347 | 19.4043 | 19.3742 | 19.3446 | 19.3155 | 19.1406 | 18.9984 | 18.8699
| MILTON OF CRAIGIE | MILTON OF CRAIGIE | MINIMUM HEADROOM | NO 43137 31857 | NO | YES | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 24.0186 | 23.9838 | 23.9411 | 23.8999 | 23.8576 | 23.8275 | 23.8163 | 23.8037 | 23.7906 | 23.7891 | 23.7891 | 23.7891 | 23.7891 | 21.7949 | 24.03 | 24.0163 | 23.9995 | 23.9832 | 23.9666 | 23.9496 | 23.9342 | 23.9221 | 23.9093 | 23.8964 | 23.8871 | 23.8871 | 23.8871 | 21.8483
|  | MILTON OF CRAIGIE | CT |  |  |  | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 24.0237 | 24.0023 | 23.9779 | 23.9539 | 23.93 | 23.9072 | 23.8849 | 23.8599 | 23.8343 | 23.8235 | 23.8154 | 23.7891 | 23.7891 | 23.7891 | 24.032 | 24.0235 | 24.0139 | 24.0045 | 23.9951 | 23.9861 | 23.9774 | 23.9675 | 23.9558 | 23.9437 | 23.9334 | 23.8871 | 23.8871 | 23.8871
|  | MILTON OF CRAIGIE | LW |  |  |  | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 24.0186 | 23.9838 | 23.9411 | 23.8999 | 23.8576 | 23.8275 | 23.8163 | 23.8037 | 23.7906 | 23.7891 | 23.7891 | 23.7891 | 23.7891 | 21.7949 | 24.03 | 24.0163 | 23.9995 | 23.9832 | 23.9666 | 23.9496 | 23.9342 | 23.9221 | 23.9093 | 23.8964 | 23.8871 | 23.8871 | 23.8871 | 21.8483
|  | MILTON OF CRAIGIE | ST |  |  |  | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 24.0303 | 24.0202 | 24.0048 | 23.9863 | 23.9647 | 23.944 | 23.9238 | 23.9013 | 23.8759 | 23.8501 | 23.83 | 23.7967 | 23.7891 | 23.7891 | 24.0346 | 24.0306 | 24.0245 | 24.0173 | 24.0087 | 24.0006 | 23.9927 | 23.9838 | 23.9738 | 23.9635 | 23.9533 | 23.9153 | 23.8871 | 23.8871
|  | MILTON OF CRAIGIE | FS |  |  |  | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 33.7094 | 24.036 | 24.0351 | 24.0306 | 24.0256 | 24.0187 | 24.0119 | 24.0031 | 23.9939 | 23.9842 | 23.9746 | 23.9651 | 23.917 | 23.8759 | 23.8418 | 24.0368 | 24.0364 | 24.0347 | 24.0327 | 24.03 | 24.0273 | 24.0238 | 24.0202 | 24.0164 | 24.0126 | 24.0089 | 23.99 | 23.9738 | 23.9595
| STRICHEN | MINTLAW | MINIMUM HEADROOM | NK 00897 48662 | NO | YES | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 14.3554 | 13.0625 | 12.5524 | 17.9653 | 17.927 | 17.8781 | 17.8291 | 17.7802 | 17.7409 | 17.7351 | 17.7289 | 17.7228 | 17.7167 | 17.7106 | 13.3746 | 12.035 | 11.4389 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 11.9812 | 10.9795 | 10.3729
|  | MINTLAW | CT |  |  |  | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 14.3554 | 13.4361 | 13.0484 | 17.9653 | 17.9297 | 17.8884 | 17.847 | 17.8057 | 17.7641 | 17.7399 | 17.7347 | 17.7296 | 17.7244 | 17.7192 | 13.6723 | 12.4781 | 12.0185 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 11.9812 | 11.2269 | 10.9627
|  | MINTLAW | LW |  |  |  | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 14.3554 | 13.0625 | 12.5524 | 17.9665 | 17.927 | 17.8781 | 17.8291 | 17.7802 | 17.7409 | 17.7351 | 17.7289 | 17.7228 | 17.7167 | 17.7106 | 13.3746 | 12.035 | 11.4389 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 11.9812 | 10.9795 | 10.3729
|  | MINTLAW | ST |  |  |  | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.4425 | 14.4553 | 14.4553 | 17.9813 | 17.9721 | 17.9578 | 17.9405 | 17.9172 | 17.8937 | 17.8707 | 17.846 | 17.8221 | 17.7978 | 17.774 | 17.4135 | 17.1454 | 17.1322 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.4532 | 12.076 | 12.076
|  | MINTLAW | FS |  |  |  | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.969 | 18.0196 | 17.9852 | 17.9807 | 17.9753 | 17.9673 | 17.9592 | 17.9491 | 17.9392 | 17.9296 | 17.92 | 17.9105 | 17.8647 | 17.8212 | 17.7801 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251 | 12.9251
| BRIDGE OF DUN | MONTROSE NORTH | MINIMUM HEADROOM | NO 71226 59070 | NO | YES | 22.5551 | 22.4417 | 22.3243 | 22.2112 | 22.1022 | 21.9974 | 21.8968 | 21.8326 | 21.8007 | 21.7691 | 21.738 | 21.5771 | 21.298 | 21.0976 | 17.7818 | 17.6359 | 17.509 | 17.4278 | 17.3512 | 17.278 | 17.2077 | 17.1593 | 17.1311 | 17.1035 | 17.0764 | 16.9814 | 16.8212 | 13.5029 | 18.2872 | 18.1717 | 18.0523 | 17.9371 | 17.8262 | 17.7195 | 17.6171 | 17.5518 | 17.5193 | 17.4872 | 17.4555 | 17.2918 | 17.0127 | 13.6229
|  | MONTROSE NORTH | CT |  |  |  | 22.5551 | 22.4417 | 22.3243 | 22.2112 | 22.1022 | 21.9974 | 21.8968 | 21.8326 | 21.8007 | 21.7691 | 21.738 | 21.5771 | 21.298 | 21.0976 | 17.7818 | 17.6359 | 17.509 | 17.4278 | 17.3512 | 17.278 | 17.2077 | 17.1593 | 17.1311 | 17.1035 | 17.0764 | 16.9814 | 16.8212 | 13.5029 | 18.2872 | 18.1717 | 18.0523 | 17.9371 | 17.8262 | 17.7195 | 17.6171 | 17.5518 | 17.5193 | 17.4872 | 17.4555 | 17.2918 | 17.0127 | 13.6229
|  | MONTROSE NORTH | LW |  |  |  | 22.7558 | 22.7388 | 22.7197 | 22.6986 | 22.6757 | 22.6513 | 22.6255 | 22.5925 | 22.5584 | 22.5237 | 22.4885 | 22.302 | 21.9742 | 21.6841 | 17.9461 | 17.8794 | 17.7997 | 17.7359 | 17.7076 | 17.6849 | 17.6616 | 17.6332 | 17.6043 | 17.5749 | 17.5454 | 17.3974 | 17.2092 | 13.5521 | 18.4914 | 18.4741 | 18.4546 | 18.4332 | 18.4099 | 18.385 | 18.3588 | 18.3252 | 18.2905 | 18.2552 | 18.2193 | 18.0296 | 17.6959 | 17.4007
|  | MONTROSE NORTH | ST |  |  |  | 22.7849 | 22.7782 | 22.7716 | 22.7651 | 22.7573 | 22.7498 | 22.7424 | 22.7347 | 22.7235 | 22.7125 | 22.7019 | 22.642 | 22.5362 | 22.4646 | 17.995 | 17.972 | 17.9417 | 17.9067 | 17.861 | 17.8189 | 17.7803 | 17.7562 | 17.7393 | 17.727 | 17.7155 | 17.6545 | 17.5654 | 17.4975 | 18.521 | 18.5141 | 18.5074 | 18.5009 | 18.493 | 18.4852 | 18.4777 | 18.4699 | 18.4585 | 18.4474 | 18.4365 | 18.3756 | 18.2679 | 18.195
|  | MONTROSE NORTH | FS |  |  |  | 22.7782 | 22.7714 | 22.7614 | 22.7515 | 22.7417 | 22.7321 | 22.7226 | 22.7132 | 22.704 | 22.6949 | 22.6859 | 22.6322 | 22.574 | 22.5171 | 18.0034 | 17.9936 | 17.9767 | 17.9585 | 17.9367 | 17.9171 | 17.8946 | 17.8724 | 17.8506 | 17.8294 | 17.8088 | 17.7029 | 17.6503 | 17.6068 | 18.5141 | 18.5073 | 18.4971 | 18.487 | 18.4771 | 18.4673 | 18.4576 | 18.4481 | 18.4387 | 18.4294 | 18.4203 | 18.3656 | 18.3063 | 18.2484
| TARLAND | MOSSAT | MINIMUM HEADROOM | NJ 47470 19897 | NO | YES | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.67 | 2.4498 | 3.4567 | 3.4454 | 3.4315 | 3.4242 | 3.4231 | 3.422 | 3.4217 | 3.4217 | 3.4217 | 3.4217 | 3.4217 | 2.2833 | 1.9064 | 1.6556 | 3.447 | 3.4453 | 3.4433 | 3.4412 | 3.4392 | 3.4372 | 3.4352 | 3.433 | 3.4309 | 3.4288 | 3.4267 | 3.4117 | 2.1491 | 1.8955
|  | MOSSAT | CT |  |  |  | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.67 | 3.67 | 3.4573 | 3.4486 | 3.4386 | 3.4286 | 3.4243 | 3.4235 | 3.4227 | 3.4218 | 3.4217 | 3.4217 | 3.4217 | 2.4158 | 2.1156 | 1.9553 | 3.4471 | 3.4458 | 3.4443 | 3.4429 | 3.4414 | 3.4399 | 3.4385 | 3.4369 | 3.4354 | 3.4338 | 3.4323 | 3.4161 | 2.3563 | 2.2019
|  | MOSSAT | LW |  |  |  | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.67 | 2.4498 | 3.4567 | 3.4454 | 3.4315 | 3.4242 | 3.4231 | 3.422 | 3.4217 | 3.4217 | 3.4217 | 3.4217 | 3.4217 | 2.2833 | 1.9064 | 1.6556 | 3.447 | 3.4453 | 3.4433 | 3.4412 | 3.4392 | 3.4372 | 3.4352 | 3.433 | 3.4309 | 3.4288 | 3.4267 | 3.4117 | 2.1491 | 1.8955
|  | MOSSAT | ST |  |  |  | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.7647 | 3.7647 | 3.4603 | 3.4568 | 3.4513 | 3.4447 | 3.4298 | 3.424 | 3.4228 | 3.4217 | 3.4217 | 3.4217 | 3.4217 | 2.4435 | 2.269 | 2.164 | 3.4476 | 3.447 | 3.4462 | 3.4452 | 3.443 | 3.4408 | 3.4387 | 3.4364 | 3.4341 | 3.4319 | 3.4297 | 3.4189 | 3.3138 | 2.4315
|  | MOSSAT | FS |  |  |  | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.8595 | 3.4622 | 3.4619 | 3.4603 | 3.4584 | 3.4535 | 3.4487 | 3.4425 | 3.4364 | 3.4304 | 3.4248 | 3.4243 | 3.422 | 3.4217 | 3.4217 | 3.4478 | 3.4478 | 3.4476 | 3.4473 | 3.4466 | 3.4458 | 3.4449 | 3.444 | 3.4431 | 3.4422 | 3.4414 | 3.4373 | 3.4334 | 3.4298
| THURSO | MOUNT PLEASANT | MINIMUM HEADROOM | ND 12706 67832 | YES | YES | 9.8481 | 9.7184 | 9.5936 | 9.4733 | 9.3574 | 9.246 | 9.1391 | 9.0877 | 9.0621 | 9.0368 | 9.0118 | 8.8887 | 7.3368 | 7.0143 | 9.3362 | 9.2189 | 9.1042 | 8.9931 | 8.8859 | 8.7823 | 8.6824 | 8.6119 | 8.5615 | 8.5276 | 8.4975 | 8.4297 | 7.3004 | 6.9741 | 9.4605 | 9.3162 | 9.1764 | 9.0413 | 8.911 | 8.7855 | 8.6832 | 8.6294 | 8.5994 | 8.5731 | 8.547 | 7.2112 | 6.8664 | 6.5242
|  | MOUNT PLEASANT | CT |  |  |  | 9.8481 | 9.7184 | 9.5936 | 9.4733 | 9.3574 | 9.246 | 9.1391 | 9.0877 | 9.0621 | 9.0368 | 9.0118 | 8.8887 | 7.3368 | 7.0143 | 9.3362 | 9.2189 | 9.1042 | 8.9931 | 8.8859 | 8.7823 | 8.6824 | 8.6119 | 8.5615 | 8.5276 | 8.4975 | 8.4297 | 7.3004 | 6.9741 | 9.4605 | 9.3162 | 9.1764 | 9.0413 | 8.911 | 8.7855 | 8.6832 | 8.6294 | 8.5994 | 8.5731 | 8.547 | 7.2112 | 6.8664 | 6.5242
|  | MOUNT PLEASANT | LW |  |  |  | 10.0776 | 10.0582 | 10.0363 | 10.0121 | 9.986 | 9.9581 | 9.9286 | 9.9005 | 9.8715 | 9.8419 | 9.8119 | 9.6531 | 9.4924 | 7.4376 | 9.5263 | 9.4972 | 9.4629 | 9.4266 | 9.3889 | 9.3497 | 9.3093 | 9.2492 | 9.1867 | 9.144 | 9.1017 | 8.8507 | 8.7622 | 7.1774 | 9.706 | 9.6779 | 9.6454 | 9.6104 | 9.5734 | 9.5345 | 9.494 | 9.4433 | 9.3907 | 9.3488 | 9.3069 | 9.1316 | 7.4218 | 6.935
|  | MOUNT PLEASANT | ST |  |  |  | 10.1109 | 10.1031 | 10.0956 | 10.0883 | 10.0793 | 10.0707 | 10.0622 | 10.0541 | 10.0421 | 10.0305 | 10.0192 | 9.966 | 9.9181 | 9.8718 | 9.5597 | 9.5519 | 9.5436 | 9.5348 | 9.5106 | 9.4868 | 9.4634 | 9.4279 | 9.3882 | 9.3605 | 9.333 | 9.1991 | 9.0843 | 8.9809 | 9.7449 | 9.7358 | 9.7266 | 9.7172 | 9.6982 | 9.6796 | 9.6613 | 9.6365 | 9.607 | 9.5844 | 9.5621 | 9.4548 | 9.402 | 9.3546
|  | MOUNT PLEASANT | FS |  |  |  | 10.1031 | 10.0954 | 10.0839 | 10.0726 | 10.0615 | 10.0505 | 10.0396 | 10.0289 | 10.0183 | 10.0079 | 9.9977 | 9.9362 | 9.8808 | 9.8292 | 9.5541 | 9.5475 | 9.5374 | 9.5273 | 9.5126 | 9.498 | 9.4821 | 9.4619 | 9.4414 | 9.4258 | 9.4103 | 9.3252 | 9.2477 | 9.1746 | 9.737 | 9.7286 | 9.716 | 9.7035 | 9.6885 | 9.6737 | 9.6582 | 9.6404 | 9.6225 | 9.6074 | 9.5925 | 9.5076 | 9.4306 | 9.3583
| BEAULY | MUIR OF ORD | MINIMUM HEADROOM | NH 53420 48534 | NO | YES | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 30.6647 | 30.5928 | 30.539 | 30.5229 | 30.5089 | 30.495 | 30.4768 | 30.457 | 30.4373 | 30.4174 | 30.3974 | 30.3128 | 30.2477 | 30.1839 | 31.2453 | 31.2227 | 31.195 | 31.1671 | 31.1428 | 31.1187 | 31.0871 | 31.0812 | 31.0812 | 31.0812 | 31.0812 | 31.0812 | 31.0812 | 31.0812
|  | MUIR OF ORD | CT |  |  |  | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 30.6718 | 30.6179 | 30.5563 | 30.5368 | 30.5268 | 30.5167 | 30.503 | 30.4879 | 30.473 | 30.4578 | 30.4421 | 30.3816 | 30.3304 | 30.281 | 31.2476 | 31.2306 | 31.2112 | 31.1911 | 31.1739 | 31.1564 | 31.1325 | 31.1063 | 31.0812 | 31.0812 | 31.0812 | 31.0812 | 31.0812 | 31.0812
|  | MUIR OF ORD | LW |  |  |  | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 30.6647 | 30.5928 | 30.539 | 30.5229 | 30.5089 | 30.495 | 30.4768 | 30.457 | 30.4373 | 30.4174 | 30.3974 | 30.3128 | 30.2477 | 30.1839 | 31.2453 | 31.2227 | 31.195 | 31.1671 | 31.1428 | 31.1187 | 31.0871 | 31.0812 | 31.0812 | 31.0812 | 31.0812 | 31.0812 | 31.0812 | 31.0812
|  | MUIR OF ORD | ST |  |  |  | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 30.6969 | 30.6728 | 30.6381 | 30.5961 | 30.5618 | 30.543 | 30.5342 | 30.5245 | 30.5148 | 30.5049 | 30.4946 | 30.4582 | 30.4294 | 30.4015 | 31.2555 | 31.2479 | 31.2369 | 31.2237 | 31.2129 | 31.2019 | 31.1867 | 31.1698 | 31.1531 | 31.1359 | 31.1181 | 31.0812 | 31.0812 | 31.0812
|  | MUIR OF ORD | FS |  |  |  | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 34.9075 | 30.7157 | 30.7103 | 30.698 | 30.6842 | 30.6723 | 30.6604 | 30.6401 | 30.6193 | 30.5987 | 30.5776 | 30.5558 | 30.5309 | 30.5189 | 30.5091 | 31.2614 | 31.2597 | 31.2558 | 31.2515 | 31.2477 | 31.244 | 31.2376 | 31.231 | 31.2245 | 31.2179 | 31.211 | 31.1809 | 31.1601 | 31.1431
| BEAULY | MUIREND | MINIMUM HEADROOM | NH 64508 54337 | YES | YES | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.1346 | 7.1309 | 7.1264 | 7.1221 | 7.1179 | 7.1137 | 7.1087 | 7.1031 | 7.1016 | 7.1001 | 7.0987 | 7.0852 | 5.9765 | 5.7904 | 7.3616 | 7.3604 | 7.359 | 7.3577 | 7.3563 | 7.355 | 7.3534 | 7.3507 | 7.3481 | 7.3455 | 7.343 | 7.3195 | 7.2898 | 7.2805
|  | MUIREND | CT |  |  |  | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.1357 | 7.1329 | 7.1299 | 7.1268 | 7.1232 | 7.1192 | 7.116 | 7.1125 | 7.1094 | 7.1062 | 7.1037 | 7.093 | 7.0818 | 7.0707 | 7.3619 | 7.3611 | 7.3601 | 7.3591 | 7.358 | 7.3568 | 7.3557 | 7.3546 | 7.3537 | 7.3527 | 7.3517 | 7.3331 | 7.3136 | 7.2945
|  | MUIREND | LW |  |  |  | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.1346 | 7.1309 | 7.1264 | 7.1221 | 7.1179 | 7.1137 | 7.1096 | 7.1051 | 7.1033 | 7.1025 | 7.1017 | 7.0852 | 5.9765 | 5.7904 | 7.3616 | 7.3604 | 7.359 | 7.3577 | 7.3563 | 7.355 | 7.3537 | 7.3523 | 7.3509 | 7.3495 | 7.3482 | 7.3195 | 7.2898 | 7.2805
|  | MUIREND | ST |  |  |  | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.1389 | 7.1377 | 7.1361 | 7.134 | 7.1254 | 7.1168 | 7.1087 | 7.1031 | 7.1016 | 7.1001 | 7.0987 | 7.0915 | 7.084 | 7.0767 | 7.3629 | 7.3626 | 7.3621 | 7.3614 | 7.3587 | 7.356 | 7.3534 | 7.3507 | 7.3481 | 7.3455 | 7.343 | 7.3305 | 7.3176 | 7.3048
|  | MUIREND | FS |  |  |  | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.7941 | 7.1415 | 7.1413 | 7.1406 | 7.1399 | 7.1371 | 7.1344 | 7.1309 | 7.1274 | 7.1241 | 7.1208 | 7.1176 | 7.1036 | 7.101 | 7.0984 | 7.3638 | 7.3637 | 7.3635 | 7.3633 | 7.3624 | 7.3615 | 7.3604 | 7.3593 | 7.3583 | 7.3572 | 7.3563 | 7.3515 | 7.3469 | 7.3424
| NAIRN | NAIRN CENTRAL | MINIMUM HEADROOM | NH 88496 56295 | NO | YES | 23.6069 | 23.591 | 23.5787 | 23.5667 | 23.5549 | 23.5426 | 23.5293 | 23.5161 | 23.5029 | 23.4898 | 23.4779 | 23.437 | 23.437 | 23.437 | 19.6295 | 19.5122 | 19.4479 | 19.3848 | 19.3233 | 19.2592 | 19.1896 | 19.1204 | 19.0515 | 18.9833 | 18.9208 | 18.5168 | 18.1742 | 13.7154 | 20.048 | 20.0227 | 20.0031 | 19.9837 | 19.9649 | 19.9453 | 19.924 | 19.9028 | 19.8817 | 19.8608 | 19.8417 | 19.718 | 19.5885 | 19.4623
|  | NAIRN CENTRAL | CT |  |  |  | 23.6073 | 23.5935 | 23.5837 | 23.574 | 23.5642 | 23.5531 | 23.5409 | 23.5298 | 23.5187 | 23.5079 | 23.4979 | 23.4383 | 23.437 | 23.437 | 19.6331 | 19.5248 | 19.474 | 19.4232 | 19.3717 | 19.3141 | 19.2504 | 19.1919 | 19.1341 | 19.0775 | 19.0256 | 18.7139 | 18.3867 | 18.1742 | 20.0487 | 20.0266 | 20.011 | 19.9955 | 19.9797 | 19.9621 | 19.9426 | 19.9247 | 19.907 | 19.8897 | 19.8738 | 19.7783 | 19.6782 | 19.5798
|  | NAIRN CENTRAL | LW |  |  |  | 23.6069 | 23.591 | 23.5787 | 23.5667 | 23.5549 | 23.5426 | 23.5293 | 23.5161 | 23.5029 | 23.4898 | 23.4779 | 23.437 | 23.437 | 23.437 | 19.6295 | 19.5122 | 19.4479 | 19.3848 | 19.3233 | 19.2592 | 19.1896 | 19.1204 | 19.0515 | 18.9833 | 18.9208 | 18.5168 | 18.1742 | 13.7154 | 20.048 | 20.0227 | 20.0031 | 19.9837 | 19.9649 | 19.9453 | 19.924 | 19.9028 | 19.8817 | 19.8608 | 19.8417 | 19.718 | 19.5885 | 19.4623
|  | NAIRN CENTRAL | ST |  |  |  | 23.6121 | 23.6056 | 23.6011 | 23.5955 | 23.5885 | 23.5808 | 23.5723 | 23.5644 | 23.5566 | 23.5491 | 23.5422 | 23.5085 | 23.4737 | 23.4393 | 19.6774 | 19.618 | 19.5762 | 19.5356 | 19.499 | 19.4585 | 19.414 | 19.3728 | 19.3323 | 19.2929 | 19.2572 | 19.081 | 18.8987 | 18.719 | 20.0564 | 20.046 | 20.0388 | 20.0299 | 20.0187 | 20.0063 | 19.9927 | 19.98 | 19.9677 | 19.9556 | 19.9447 | 19.8907 | 19.8349 | 19.7799
|  | NAIRN CENTRAL | FS |  |  |  | 23.6152 | 23.6129 | 23.6114 | 23.6097 | 23.6072 | 23.6047 | 23.6013 | 23.5982 | 23.5951 | 23.592 | 23.5893 | 23.5766 | 23.5641 | 23.5519 | 19.7056 | 19.6848 | 19.6712 | 19.6555 | 19.633 | 19.6095 | 19.5787 | 19.5501 | 19.5336 | 19.5174 | 19.503 | 19.4366 | 19.3716 | 19.3077 | 20.0613 | 20.0577 | 20.0553 | 20.0526 | 20.0487 | 20.0446 | 20.0392 | 20.0342 | 20.0293 | 20.0243 | 20.0199 | 19.9996 | 19.9797 | 19.9601
| STRICHEN | NEW PITSLIGO | MINIMUM HEADROOM | NJ 88529 54853 | NO | YES | 5.0211 | 4.9535 | 4.8905 | 4.8297 | 4.7712 | 4.7149 | 4.6609 | 4.6303 | 4.6151 | 4.6001 | 4.5853 | 4.371 | 3.9365 | 3.8142 | 5.0946 | 5.0632 | 5.0336 | 5.005 | 4.9276 | 4.8477 | 4.7703 | 4.7123 | 4.6692 | 4.6256 | 4.5825 | 4.2309 | 3.6732 | 3.4065 | 4.8634 | 4.7628 | 4.6627 | 4.5645 | 4.4686 | 4.3748 | 4.284 | 4.2177 | 4.1699 | 4.1216 | 4.0739 | 3.6674 | 3.0079 | 2.7125
|  | NEW PITSLIGO | CT |  |  |  | 5.0211 | 4.9535 | 4.8905 | 4.8297 | 4.7712 | 4.7149 | 4.6609 | 4.6303 | 4.6151 | 4.6001 | 4.5853 | 4.371 | 3.9365 | 3.8142 | 5.0946 | 5.0632 | 5.0336 | 5.005 | 4.9276 | 4.8477 | 4.7703 | 4.7123 | 4.6692 | 4.6256 | 4.5825 | 4.2309 | 3.6732 | 3.4065 | 4.8634 | 4.7628 | 4.6627 | 4.5645 | 4.4686 | 4.3748 | 4.284 | 4.2177 | 4.1699 | 4.1216 | 4.0739 | 3.6674 | 3.0079 | 2.7125
|  | NEW PITSLIGO | LW |  |  |  | 5.1406 | 5.1305 | 5.1191 | 5.1065 | 5.0929 | 5.0784 | 5.063 | 5.0458 | 5.0282 | 5.0101 | 4.9918 | 4.7521 | 4.2831 | 4.1238 | 5.1485 | 5.1428 | 5.1363 | 5.1292 | 5.1216 | 5.1135 | 5.1051 | 5.066 | 5.0151 | 4.9632 | 4.9114 | 4.4917 | 3.8584 | 3.5093 | 5.0029 | 4.9674 | 4.923 | 4.8764 | 4.828 | 4.7781 | 4.7276 | 4.6723 | 4.6171 | 4.5609 | 4.5046 | 4.0216 | 3.273 | 2.8859
|  | NEW PITSLIGO | ST |  |  |  | 5.1579 | 5.1539 | 5.15 | 5.1461 | 5.1415 | 5.137 | 5.1326 | 5.1285 | 5.1224 | 5.1166 | 5.1109 | 5.0081 | 4.8009 | 4.7496 | 5.1568 | 5.1549 | 5.153 | 5.1512 | 5.1484 | 5.1456 | 5.1429 | 5.1402 | 5.1367 | 5.1333 | 5.1299 | 5.0573 | 4.7888 | 4.6607 | 5.0339 | 5.0283 | 5.0217 | 5.0141 | 4.9927 | 4.9712 | 4.9499 | 4.9275 | 4.9034 | 4.8792 | 4.8553 | 4.6515 | 4.3289 | 4.1874
|  | NEW PITSLIGO | FS |  |  |  | 5.1539 | 5.1499 | 5.1439 | 5.138 | 5.1322 | 5.1265 | 5.1208 | 5.1152 | 5.1097 | 5.1043 | 5.099 | 5.067 | 5.0336 | 5.0012 | 5.159 | 5.1531 | 5.1503 | 5.1476 | 5.1447 | 5.1419 | 5.139 | 5.1362 | 5.1334 | 5.1307 | 5.128 | 5.1121 | 5.0956 | 5.0797 | 5.1177 | 5.0242 | 5.0152 | 5.0057 | 4.9938 | 4.9818 | 4.9686 | 4.9553 | 4.9423 | 4.9294 | 4.9165 | 4.8466 | 4.7762 | 4.7083
| DUNOON | NEWTON | MINIMUM HEADROOM | NS 04939 98621 | YES | YES | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.35715 | 0.35668 | 0.3561 | 0.35577 | 0.35548 | 0.35519 | 0.35492 | 0.35462 | 0.35432 | 0.35402 | 0.35373 | 0.35326 | 0.35326 | 0.28763 | 0.3663 | 0.36618 | 0.36607 | 0.36597 | 0.36587 | 0.36577 | 0.36567 | 0.36557 | 0.36546 | 0.36536 | 0.36526 | 0.36477 | 0.36477 | 0.29178
|  | NEWTON | CT |  |  |  | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.35718 | 0.35682 | 0.35642 | 0.35603 | 0.35582 | 0.35562 | 0.35543 | 0.35522 | 0.35501 | 0.3548 | 0.3546 | 0.35326 | 0.35326 | 0.28763 | 0.36631 | 0.3662 | 0.36613 | 0.36606 | 0.36599 | 0.36592 | 0.36585 | 0.36578 | 0.36571 | 0.36563 | 0.36556 | 0.36477 | 0.36477 | 0.29178
|  | NEWTON | LW |  |  |  | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.35715 | 0.35668 | 0.3561 | 0.35577 | 0.35548 | 0.35519 | 0.35492 | 0.35462 | 0.35432 | 0.35402 | 0.35373 | 0.35326 | 0.35326 | 0.35326 | 0.3663 | 0.36618 | 0.36607 | 0.36597 | 0.36587 | 0.36577 | 0.36567 | 0.36557 | 0.36546 | 0.36536 | 0.36526 | 0.36477 | 0.36477 | 0.36477
|  | NEWTON | ST |  |  |  | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.3573 | 0.35716 | 0.35694 | 0.35667 | 0.35641 | 0.35615 | 0.35595 | 0.35581 | 0.35567 | 0.35553 | 0.35539 | 0.35473 | 0.35409 | 0.35344 | 0.36637 | 0.3663 | 0.36622 | 0.36618 | 0.36613 | 0.36608 | 0.36603 | 0.36598 | 0.36593 | 0.36589 | 0.36584 | 0.36561 | 0.36539 | 0.36516
|  | NEWTON | FS |  |  |  | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.40228 | 0.35738 | 0.35737 | 0.35731 | 0.35724 | 0.35715 | 0.35706 | 0.35695 | 0.35684 | 0.35673 | 0.35662 | 0.35652 | 0.35602 | 0.35577 | 0.35555 | 0.36641 | 0.36641 | 0.36638 | 0.36634 | 0.3663 | 0.36625 | 0.36623 | 0.36621 | 0.36619 | 0.36617 | 0.36615 | 0.36606 | 0.36597 | 0.36589
| REDMOSS | NEWTONHILL | MINIMUM HEADROOM | NO 90190 93653 | NO | YES | 23.284 | 23.2486 | 23.205 | 23.1617 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 13.4636 | 12.4206 | 19.5411 | 19.2852 | 19.1339 | 19.0587 | 19.0587 | 19.0587 | 19.0587 | 19.0587 | 13.3951 | 12.8468 | 12.3028 | 10.9398 | 8.946 | 7.608 | 20.0251 | 19.9575 | 19.8742 | 19.7932 | 19.7932 | 19.7932 | 19.7932 | 19.7932 | 19.7932 | 13.7463 | 13.2164 | 11.8887 | 9.7313 | 8.428
|  | NEWTONHILL | CT |  |  |  | 23.2859 | 23.2589 | 23.2278 | 23.197 | 23.1664 | 23.1359 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 22.3773 | 22.3773 | 19.5552 | 19.3536 | 19.179 | 19.1182 | 19.0587 | 19.0587 | 19.0587 | 19.0587 | 19.0587 | 19.0587 | 19.0587 | 12.8752 | 11.3207 | 10.4136 | 20.0287 | 19.9772 | 19.9179 | 19.859 | 19.8005 | 19.7932 | 19.7932 | 19.7932 | 19.7932 | 19.7932 | 19.7932 | 13.7739 | 12.0444 | 11.1608
|  | NEWTONHILL | LW |  |  |  | 23.284 | 23.2486 | 23.205 | 23.1617 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 13.4636 | 12.4206 | 19.5411 | 19.2852 | 19.1339 | 19.0587 | 19.0587 | 19.0587 | 19.0587 | 19.0587 | 13.3951 | 12.8468 | 12.3028 | 10.9398 | 8.946 | 7.608 | 20.0251 | 19.9575 | 19.8742 | 19.7932 | 19.7932 | 19.7932 | 19.7932 | 19.7932 | 19.7932 | 13.7463 | 13.2164 | 11.8887 | 9.7313 | 8.428
|  | NEWTONHILL | ST |  |  |  | 23.2954 | 23.2845 | 23.2676 | 23.2473 | 23.2368 | 23.2263 | 23.216 | 23.2049 | 23.1942 | 23.1833 | 23.1727 | 23.1354 | 22.7563 | 22.7563 | 19.6259 | 19.545 | 19.4187 | 19.2775 | 19.214 | 19.176 | 19.1557 | 19.1339 | 19.1127 | 19.0913 | 19.0703 | 19.0587 | 18.8394 | 18.8394 | 20.0467 | 20.0261 | 19.9938 | 19.955 | 19.935 | 19.915 | 19.8954 | 19.8741 | 19.8536 | 19.8329 | 19.8126 | 19.7932 | 19.4015 | 19.4015
|  | NEWTONHILL | FS |  |  |  | 23.3237 | 23.3005 | 23.2955 | 23.2896 | 23.2861 | 23.2827 | 23.2784 | 23.2741 | 23.27 | 23.2659 | 23.2618 | 23.2422 | 23.2236 | 23.206 | 19.8375 | 19.6642 | 19.627 | 19.5826 | 19.557 | 19.5311 | 19.499 | 19.4672 | 19.4364 | 19.4054 | 19.3751 | 19.2464 | 19.1706 | 19.1359 | 20.1008 | 20.0565 | 20.047 | 20.0357 | 20.0291 | 20.0225 | 20.0143 | 20.0062 | 19.9983 | 19.9904 | 19.9827 | 19.9452 | 19.9097 | 19.8762
| ALNESS | NIGG | MINIMUM HEADROOM | NH 79490 69773 | YES | YES | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.4671 | 1.467 | 1.467 | 1.467 | 1.4669 | 1.4669 | 1.4669 | 1.4668 | 1.4668 | 1.4667 | 1.4667 | 1.4665 | 1.4664 | 1.4662
|  | NIGG | CT |  |  |  | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.4671 | 1.467 | 1.467 | 1.467 | 1.467 | 1.4669 | 1.4669 | 1.4669 | 1.4669 | 1.4668 | 1.4668 | 1.4667 | 1.4666 | 1.4664
|  | NIGG | LW |  |  |  | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.4671 | 1.467 | 1.467 | 1.467 | 1.4669 | 1.4669 | 1.4669 | 1.4668 | 1.4668 | 1.4667 | 1.4667 | 1.4665 | 1.4664 | 1.4662
|  | NIGG | ST |  |  |  | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.4671 | 1.4671 | 1.4671 | 1.467 | 1.467 | 1.467 | 1.467 | 1.467 | 1.467 | 1.4669 | 1.4669 | 1.4668 | 1.4668 | 1.4667
|  | NIGG | FS |  |  |  | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.5523 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.6433 | 1.4671 | 1.4671 | 1.4671 | 1.4671 | 1.4671 | 1.4671 | 1.4671 | 1.467 | 1.467 | 1.467 | 1.467 | 1.467 | 1.467 | 1.4669
| CHARLESTON | NINEWELLS | MINIMUM HEADROOM | NO 35148 30641 | NO | YES | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 17.0262 | 16.9951 | 16.9639 | 16.9333 | 16.9027 | 16.8726 | 16.8492 | 16.8321 | 16.8149 | 16.7976 | 16.7803 | 16.6752 | 16.5724 | 16.5067 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257
|  | NINEWELLS | CT |  |  |  | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 17.0318 | 17.0118 | 16.9948 | 16.9774 | 16.9591 | 16.9401 | 16.922 | 16.9033 | 16.8845 | 16.8657 | 16.8513 | 16.7758 | 16.7023 | 16.6316 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257
|  | NINEWELLS | LW |  |  |  | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 17.0262 | 16.9951 | 16.9639 | 16.9333 | 16.9027 | 16.8726 | 16.8492 | 16.8321 | 16.8149 | 16.7976 | 16.7803 | 16.6752 | 16.5724 | 16.5067 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257
|  | NINEWELLS | ST |  |  |  | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 17.0392 | 17.0271 | 17.0139 | 16.9977 | 16.9785 | 16.9591 | 16.9405 | 16.921 | 16.9016 | 16.8823 | 16.8631 | 16.8104 | 16.7636 | 16.7182 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257
|  | NINEWELLS | FS |  |  |  | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 19.0271 | 17.0477 | 17.0449 | 17.041 | 17.0365 | 17.0302 | 17.0241 | 17.0165 | 17.0089 | 17.0013 | 16.9938 | 16.9865 | 16.9514 | 16.9194 | 16.8901 | 16.931 | 16.9284 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257 | 16.9257
| THURSO | NORTH HOY | MINIMUM HEADROOM | HY 25681 02549 | YES | YES | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.22349 | 0.22315 | 0.22273 | 0.22232 | 0.22197 | 0.22168 | 0.22139 | 0.22127 | 0.22119 | 0.22112 | 0.22106 | 0.22106 | 0.22106 | 0.19875 | 0.22658 | 0.22641 | 0.22621 | 0.22619 | 0.22619 | 0.22619 | 0.22619 | 0.22619 | 0.22619 | 0.22619 | 0.22619 | 0.22619 | 0.22619 | 0.22619
|  | NORTH HOY | CT |  |  |  | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.22351 | 0.22326 | 0.22296 | 0.22267 | 0.22239 | 0.22212 | 0.22192 | 0.22169 | 0.22146 | 0.22131 | 0.22126 | 0.22106 | 0.22106 | 0.22106 | 0.22658 | 0.22646 | 0.22632 | 0.22619 | 0.22619 | 0.22619 | 0.22619 | 0.22619 | 0.22619 | 0.22619 | 0.22619 | 0.22619 | 0.22619 | 0.22619
|  | NORTH HOY | LW |  |  |  | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.22349 | 0.22315 | 0.22273 | 0.22232 | 0.22197 | 0.22168 | 0.22139 | 0.22127 | 0.22119 | 0.22112 | 0.22106 | 0.22106 | 0.22106 | 0.19875 | 0.22658 | 0.22641 | 0.22621 | 0.22619 | 0.22619 | 0.22619 | 0.22619 | 0.22619 | 0.22619 | 0.22619 | 0.22619 | 0.22619 | 0.22619 | 0.22619
|  | NORTH HOY | ST |  |  |  | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.2236 | 0.22349 | 0.22333 | 0.22314 | 0.22295 | 0.22277 | 0.22259 | 0.22239 | 0.2222 | 0.22204 | 0.22189 | 0.2213 | 0.22114 | 0.22106 | 0.22663 | 0.22658 | 0.2265 | 0.22641 | 0.22631 | 0.22622 | 0.22619 | 0.22619 | 0.22619 | 0.22619 | 0.22619 | 0.22619 | 0.22619 | 0.22619
|  | NORTH HOY | FS |  |  |  | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.24313 | 0.22366 | 0.22365 | 0.2236 | 0.22355 | 0.22348 | 0.22342 | 0.22334 | 0.22326 | 0.22318 | 0.22311 | 0.22303 | 0.22267 | 0.22233 | 0.22204 | 0.22666 | 0.22665 | 0.22663 | 0.2266 | 0.22657 | 0.22654 | 0.2265 | 0.22646 | 0.22643 | 0.22639 | 0.22635 | 0.22619 | 0.22619 | 0.22619
| BEAULY | NORTH KESSOCK | MINIMUM HEADROOM | NH 65004 48461 | YES | YES | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  | NORTH KESSOCK | CT |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  | NORTH KESSOCK | LW |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  | NORTH KESSOCK | ST |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  | NORTH KESSOCK | FS |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
| BROADFORD | NOSTIE BRIDGE | MINIMUM HEADROOM | NG 85209 27252 | YES | YES | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.2371 | 2.2241 | 2.2202 | 2.2163 | 2.2126 | 2.2088 | 2.2052 | 2.2013 | 2.1973 | 2.1934 | 2.1896 | 2.174 | 0.94698 | 0.77318 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 0.86586 | 0.69259
|  | NOSTIE BRIDGE | CT |  |  |  | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.2371 | 2.2241 | 2.2202 | 2.2163 | 2.2126 | 2.2088 | 2.2052 | 2.2013 | 2.1973 | 2.1934 | 2.1896 | 2.174 | 0.94698 | 0.77318 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 0.86586 | 0.69259
|  | NOSTIE BRIDGE | LW |  |  |  | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.2444 | 2.2341 | 2.2249 | 2.2229 | 2.2208 | 2.2189 | 2.2169 | 2.2148 | 2.2127 | 2.2107 | 2.2086 | 2.1875 | 2.166 | 0.79732 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 0.95225 | 0.71666
|  | NOSTIE BRIDGE | ST |  |  |  | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.2477 | 2.2446 | 2.2398 | 2.234 | 2.2252 | 2.2234 | 2.2217 | 2.2198 | 2.2179 | 2.2161 | 2.2143 | 2.2056 | 2.1969 | 2.1882 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 2.1323
|  | NOSTIE BRIDGE | FS |  |  |  | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.4289 | 2.2495 | 2.2493 | 2.2479 | 2.2463 | 2.2427 | 2.2391 | 2.2345 | 2.23 | 2.2256 | 2.2249 | 2.2242 | 2.2208 | 2.2176 | 2.2146 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 2.1323 | 2.1323
| TAYNUILT | OBAN | MINIMUM HEADROOM | NM 85643 29338 | NO | YES | 32.4082 | 32.3818 | 32.3497 | 32.3178 | 32.286 | 32.2552 | 32.2272 | 32.1969 | 32.1669 | 32.1389 | 32.1389 | 32.1389 | 32.1389 | 32.1389 | 28.8605 | 28.6546 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 20.9516 | 29.2656 | 29.2042 | 29.1294 | 29.055 | 28.9808 | 28.909 | 28.8437 | 28.7732 | 28.7032 | 28.6484 | 28.6484 | 28.6484 | 21.9519 | 20.6967
|  | OBAN | CT |  |  |  | 32.41 | 32.3896 | 32.3665 | 32.3431 | 32.3196 | 32.2969 | 32.2763 | 32.2539 | 32.2316 | 32.2096 | 32.1882 | 32.1389 | 32.1389 | 32.1389 | 28.8746 | 28.7156 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 29.2697 | 29.2224 | 29.1684 | 29.1139 | 29.059 | 29.0061 | 28.9582 | 28.9061 | 28.854 | 28.8027 | 28.7529 | 28.6484 | 28.6484 | 28.6484
|  | OBAN | LW |  |  |  | 32.4082 | 32.3818 | 32.3497 | 32.3178 | 32.286 | 32.2552 | 32.2272 | 32.1969 | 32.1669 | 32.1389 | 32.1389 | 32.1389 | 32.1389 | 32.1389 | 28.8605 | 28.6546 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 20.9516 | 29.2656 | 29.2042 | 29.1294 | 29.055 | 28.9808 | 28.909 | 28.8437 | 28.7732 | 28.7032 | 28.6484 | 28.6484 | 28.6484 | 21.9519 | 20.6967
|  | OBAN | ST |  |  |  | 32.4187 | 32.4099 | 32.3968 | 32.381 | 32.3672 | 32.354 | 32.3423 | 32.3295 | 32.3168 | 32.3044 | 32.2927 | 32.2359 | 32.1802 | 32.1389 | 28.9427 | 28.8742 | 28.7718 | 28.6481 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 28.5811 | 29.29 | 29.2696 | 29.2391 | 29.2023 | 29.1701 | 29.1394 | 29.112 | 29.0822 | 29.0526 | 29.0238 | 28.9963 | 28.864 | 28.7342 | 28.6484
|  | OBAN | FS |  |  |  | 32.4695 | 32.4361 | 32.4321 | 32.4276 | 32.4228 | 32.4182 | 32.4131 | 32.408 | 32.403 | 32.3982 | 32.3934 | 32.3713 | 32.351 | 32.332 | 29.3404 | 29.0787 | 29.0476 | 29.0121 | 28.975 | 28.9393 | 28.899 | 28.8591 | 28.8202 | 28.7821 | 28.7452 | 28.5865 | 28.5811 | 28.5811 | 29.4085 | 29.3306 | 29.3213 | 29.3107 | 29.2997 | 29.289 | 29.277 | 29.2651 | 29.2535 | 29.2422 | 29.2312 | 29.1797 | 29.1323 | 29.0881
| MILTON OF CRAIGIE | OLD CRAIGIE ROAD | MINIMUM HEADROOM | NO 42156 32130 | NO | YES | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 14.0542 | 14.0173 | 13.9723 | 13.9354 | 13.897 | 13.8573 | 13.8493 | 13.8493 | 13.8493 | 13.8493 | 13.8493 | 13.8493 | 13.8493 | 13.8493 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018
|  | OLD CRAIGIE ROAD | CT |  |  |  | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 14.0643 | 14.0456 | 14.0242 | 14.0084 | 13.991 | 13.973 | 13.9562 | 13.9373 | 13.9146 | 13.8908 | 13.8672 | 13.8493 | 13.8493 | 13.8493 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018
|  | OLD CRAIGIE ROAD | LW |  |  |  | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 14.0542 | 14.0173 | 13.9723 | 13.9354 | 13.897 | 13.8573 | 13.8493 | 13.8493 | 13.8493 | 13.8493 | 13.8493 | 13.8493 | 13.8493 | 13.8493 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018
|  | OLD CRAIGIE ROAD | ST |  |  |  | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 14.0709 | 14.0573 | 14.0376 | 14.0185 | 13.987 | 13.9555 | 13.9254 | 13.8922 | 13.8567 | 13.8493 | 13.8493 | 13.8493 | 13.8493 | 13.8493 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018
|  | OLD CRAIGIE ROAD | FS |  |  |  | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 15.5066 | 14.0813 | 14.0784 | 14.0719 | 14.0666 | 14.0562 | 14.0461 | 14.0333 | 14.02 | 14.0063 | 13.9926 | 13.9793 | 13.9137 | 13.857 | 13.8493 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018 | 14.4018
| KINTORE | OLDMELDRUM | MINIMUM HEADROOM | NJ 81659 27360 | NO | YES | 10.5342 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 6.2755 | 5.0028 | 4.4639 | 7.1649 | 7.159 | 7.1517 | 7.1175 | 6.9633 | 6.8089 | 6.6569 | 6.4925 | 6.3313 | 6.1684 | 6.0069 | 4.2525 | 3.0501 | 2.4174 | 7.3306 | 7.3306 | 7.3306 | 7.2941 | 7.142 | 6.9897 | 6.8396 | 6.6775 | 6.5184 | 6.3577 | 6.1984 | 4.1198 | 2.7474 | 2.1145
|  | OLDMELDRUM | CT |  |  |  | 10.5355 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 6.9235 | 5.876 | 5.5072 | 7.1656 | 7.1619 | 7.1575 | 7.1531 | 7.1487 | 7.1151 | 7.0224 | 6.9222 | 6.8245 | 6.7251 | 6.6265 | 5.0742 | 4.0754 | 3.6424 | 7.3306 | 7.3306 | 7.3306 | 7.3306 | 7.3306 | 7.2917 | 7.2003 | 7.1015 | 7.0051 | 6.9069 | 6.8097 | 4.9417 | 3.7729 | 3.3398
|  | OLDMELDRUM | LW |  |  |  | 10.5342 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 6.2755 | 5.0028 | 4.4639 | 7.1649 | 7.159 | 7.1517 | 7.1175 | 6.9633 | 6.8089 | 6.6569 | 6.4925 | 6.3313 | 6.1684 | 6.0069 | 4.2525 | 3.0501 | 2.4174 | 7.3306 | 7.3306 | 7.3306 | 7.2941 | 7.142 | 6.9897 | 6.8396 | 6.6775 | 6.5184 | 6.3577 | 6.1984 | 4.1198 | 2.7474 | 2.1145
|  | OLDMELDRUM | ST |  |  |  | 10.5369 | 10.5332 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 7.5582 | 7.2409 | 7.2387 | 7.1665 | 7.1643 | 7.1609 | 7.1567 | 7.1539 | 7.1511 | 7.1483 | 7.1371 | 7.0757 | 7.0135 | 6.9523 | 6.0968 | 5.5253 | 5.2373 | 7.3306 | 7.3306 | 7.3306 | 7.3306 | 7.3306 | 7.3306 | 7.3306 | 7.3134 | 7.2529 | 7.1915 | 7.1311 | 6.1264 | 5.4778 | 5.1897
|  | OLDMELDRUM | FS |  |  |  | 10.5472 | 10.5388 | 10.5374 | 10.5357 | 10.5342 | 10.5326 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 10.5311 | 7.1725 | 7.1676 | 7.1667 | 7.1658 | 7.1649 | 7.1639 | 7.1628 | 7.1617 | 7.1606 | 7.1594 | 7.1583 | 7.153 | 7.1479 | 7.0917 | 7.3306 | 7.3306 | 7.3306 | 7.3306 | 7.3306 | 7.3306 | 7.3306 | 7.3306 | 7.3306 | 7.3306 | 7.3306 | 7.3306 | 7.3306 | 7.2686
| THURSO | ORMLIE | MINIMUM HEADROOM | ND 10757 67408 | YES | YES | 10.3717 | 10.3717 | 10.3717 | 10.3717 | 10.3717 | 10.3717 | 10.3717 | 10.3717 | 10.3717 | 10.3717 | 10.3717 | 10.1864 | 10.104 | 7.1128 | 9.8059 | 9.777 | 9.7262 | 9.6913 | 9.6569 | 9.6232 | 9.5718 | 9.5198 | 9.4738 | 9.4257 | 9.3775 | 9.2181 | 7.0938 | 6.503 | 9.818 | 9.8118 | 9.8009 | 9.7934 | 9.7861 | 9.7789 | 9.7679 | 9.756 | 9.7438 | 9.7311 | 9.7184 | 9.4641 | 7.0174 | 6.4696
|  | ORMLIE | CT |  |  |  | 10.3717 | 10.3717 | 10.3717 | 10.3717 | 10.3717 | 10.3717 | 10.3717 | 10.3717 | 10.3717 | 10.3717 | 10.3717 | 10.1864 | 10.104 | 10.104 | 9.8077 | 9.786 | 9.7473 | 9.723 | 9.6992 | 9.6754 | 9.6357 | 9.5912 | 9.5477 | 9.5069 | 9.4676 | 9.2181 | 9.171 | 7.174 | 9.8184 | 9.8137 | 9.8054 | 9.8002 | 9.7951 | 9.79 | 9.7816 | 9.772 | 9.7627 | 9.7526 | 9.7422 | 9.5074 | 7.484 | 7.0916
|  | ORMLIE | LW |  |  |  | 10.3717 | 10.3717 | 10.3717 | 10.3717 | 10.3717 | 10.3717 | 10.3717 | 10.3717 | 10.3717 | 10.3717 | 10.3717 | 10.1864 | 10.104 | 7.1128 | 9.8059 | 9.777 | 9.7262 | 9.6913 | 9.6569 | 9.6232 | 9.5718 | 9.5198 | 9.4738 | 9.4257 | 9.3775 | 9.2181 | 7.0938 | 6.503 | 9.818 | 9.8118 | 9.8009 | 9.7934 | 9.7861 | 9.7789 | 9.7679 | 9.756 | 9.7438 | 9.7311 | 9.7184 | 9.4641 | 7.0174 | 6.4696
|  | ORMLIE | ST |  |  |  | 10.3717 | 10.3717 | 10.3717 | 10.3717 | 10.3717 | 10.3717 | 10.3717 | 10.3717 | 10.3717 | 10.3717 | 10.3717 | 10.279 | 10.2379 | 10.2379 | 9.8155 | 9.8065 | 9.7836 | 9.7674 | 9.7353 | 9.7036 | 9.6617 | 9.615 | 9.5691 | 9.5232 | 9.4831 | 9.2773 | 9.2475 | 9.2475 | 9.82 | 9.8181 | 9.8132 | 9.8097 | 9.8029 | 9.7961 | 9.7871 | 9.7771 | 9.7673 | 9.7569 | 9.7463 | 9.6192 | 9.5451 | 9.5103
|  | ORMLIE | FS |  |  |  | 10.3717 | 10.3717 | 10.3717 | 10.3717 | 10.3717 | 10.3717 | 10.3717 | 10.3717 | 10.3717 | 10.3717 | 10.3717 | 10.3717 | 10.3717 | 10.3717 | 9.8208 | 9.8198 | 9.8112 | 9.8064 | 9.7958 | 9.785 | 9.7675 | 9.7498 | 9.7319 | 9.7134 | 9.6944 | 9.6221 | 9.5606 | 9.5093 | 9.8212 | 9.821 | 9.8191 | 9.8181 | 9.8158 | 9.8135 | 9.8098 | 9.806 | 9.8021 | 9.7982 | 9.7941 | 9.7786 | 9.7655 | 9.7532
| DUNOON | OTTER FERRY | MINIMUM HEADROOM | NR 93352 84713 | YES | YES | 1.9177 | 1.9168 | 1.9155 | 1.9144 | 1.9132 | 1.9121 | 1.911 | 1.9098 | 1.9086 | 1.9074 | 1.9062 | 1.8952 | 1.8842 | 1.8733 | 1.7321 | 1.7297 | 1.7293 | 1.7289 | 1.7287 | 1.7287 | 1.7287 | 1.7287 | 1.7287 | 1.7287 | 1.7287 | 1.7287 | 1.7287 | 1.7287 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008
|  | OTTER FERRY | CT |  |  |  | 1.9178 | 1.9171 | 1.9162 | 1.9154 | 1.9146 | 1.9138 | 1.913 | 1.9122 | 1.9113 | 1.9105 | 1.9097 | 1.9014 | 1.8929 | 1.8847 | 1.7324 | 1.7298 | 1.7295 | 1.7293 | 1.729 | 1.7287 | 1.7287 | 1.7287 | 1.7287 | 1.7287 | 1.7287 | 1.7287 | 1.7287 | 1.7287 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008
|  | OTTER FERRY | LW |  |  |  | 1.9177 | 1.9168 | 1.9155 | 1.9144 | 1.9132 | 1.9121 | 1.911 | 1.9098 | 1.9086 | 1.9074 | 1.9062 | 1.8952 | 1.8842 | 1.8733 | 1.7321 | 1.7297 | 1.7293 | 1.7289 | 1.7287 | 1.7287 | 1.7287 | 1.7287 | 1.7287 | 1.7287 | 1.7287 | 1.7287 | 1.7287 | 1.7287 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008
|  | OTTER FERRY | ST |  |  |  | 1.9181 | 1.9178 | 1.9173 | 1.9167 | 1.9157 | 1.9148 | 1.9138 | 1.9128 | 1.9118 | 1.9108 | 1.9098 | 1.9051 | 1.9005 | 1.8959 | 1.7337 | 1.7322 | 1.73 | 1.7297 | 1.7294 | 1.7291 | 1.7288 | 1.7287 | 1.7287 | 1.7287 | 1.7287 | 1.7287 | 1.7287 | 1.7287 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008
|  | OTTER FERRY | FS |  |  |  | 1.9182 | 1.9182 | 1.9181 | 1.9179 | 1.9176 | 1.9173 | 1.9168 | 1.9164 | 1.916 | 1.9156 | 1.9152 | 1.9134 | 1.9116 | 1.91 | 1.7345 | 1.7344 | 1.7337 | 1.733 | 1.7314 | 1.7299 | 1.7297 | 1.7296 | 1.7295 | 1.7293 | 1.7292 | 1.7287 | 1.7287 | 1.7287 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008 | 1.7008
| DUDHOPE | OVERGATE | MINIMUM HEADROOM | NO 40033 30155 | NO | NO | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 45.6217 | 45.6172 | 45.6093 | 45.6051 | 45.6009 | 45.5968 | 45.5928 | 45.5885 | 45.5841 | 45.5797 | 45.5755 | 45.5545 | 45.534 | 45.5139 | 44.2826 | 44.2613 | 44.2239 | 44.2039 | 44.1842 | 44.165 | 44.1462 | 44.1257 | 44.1049 | 44.0843 | 44.0643 | 43.9741 | 43.9375 | 43.9016
|  | OVERGATE | CT |  |  |  | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 45.622 | 45.6185 | 45.6123 | 45.6094 | 45.6065 | 45.6036 | 45.6003 | 45.5966 | 45.5933 | 45.5901 | 45.5871 | 45.5725 | 45.5583 | 45.5445 | 44.2839 | 44.2672 | 44.2379 | 44.2244 | 44.2109 | 44.197 | 44.1815 | 44.1639 | 44.1485 | 44.1333 | 44.1191 | 44.0502 | 43.9831 | 43.9561
|  | OVERGATE | LW |  |  |  | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 45.6217 | 45.6172 | 45.6093 | 45.6051 | 45.6009 | 45.5968 | 45.5928 | 45.5885 | 45.5841 | 45.5797 | 45.5755 | 45.5545 | 45.534 | 45.5139 | 44.2826 | 44.2613 | 44.2239 | 44.2039 | 44.1842 | 44.165 | 44.1462 | 44.1257 | 44.1049 | 44.0843 | 44.0643 | 43.9741 | 43.9375 | 43.9016
|  | OVERGATE | ST |  |  |  | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 45.623 | 45.6213 | 45.6175 | 45.6156 | 45.6135 | 45.6114 | 45.6091 | 45.6064 | 45.6041 | 45.6018 | 45.5997 | 45.5895 | 45.5799 | 45.5704 | 44.2887 | 44.2808 | 44.2628 | 44.2538 | 44.244 | 44.234 | 44.2229 | 44.2103 | 44.1993 | 44.1885 | 44.1785 | 44.1304 | 44.0849 | 44.0401
|  | OVERGATE | FS |  |  |  | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 44.7628 | 45.6283 | 45.6279 | 45.6263 | 45.6257 | 45.625 | 45.6242 | 45.6233 | 45.6223 | 45.6214 | 45.6205 | 45.6196 | 45.6156 | 45.612 | 45.6088 | 44.3138 | 44.3118 | 44.3045 | 44.3017 | 44.2981 | 44.2945 | 44.2899 | 44.2856 | 44.2812 | 44.2769 | 44.2726 | 44.2537 | 44.2368 | 44.2216
| CASSLEY | OVERSCAIG | MINIMUM HEADROOM | NC 39711 25382 | YES | YES | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.14805 | 0.15862 | 0.15848 | 0.15831 | 0.15814 | 0.15802 | 0.1579 | 0.15782 | 0.15779 | 0.15776 | 0.15773 | 0.15773 | 0.1487 | 0.1436 | 0.13859 | 0.15975 | 0.15968 | 0.15961 | 0.15961 | 0.15961 | 0.15961 | 0.15961 | 0.15961 | 0.15961 | 0.15961 | 0.15961 | 0.15961 | 0.14531 | 0.14029
|  | OVERSCAIG | CT |  |  |  | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.15862 | 0.15852 | 0.1584 | 0.15829 | 0.15817 | 0.15808 | 0.15799 | 0.15791 | 0.15783 | 0.15781 | 0.15779 | 0.15773 | 0.14713 | 0.14336 | 0.15976 | 0.15971 | 0.15965 | 0.15961 | 0.15961 | 0.15961 | 0.15961 | 0.15961 | 0.15961 | 0.15961 | 0.15961 | 0.15961 | 0.14878 | 0.14506
|  | OVERSCAIG | LW |  |  |  | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.14805 | 0.15862 | 0.15848 | 0.15831 | 0.15814 | 0.15802 | 0.1579 | 0.15782 | 0.15779 | 0.15776 | 0.15773 | 0.15773 | 0.1487 | 0.1436 | 0.13859 | 0.15975 | 0.15968 | 0.15961 | 0.15961 | 0.15961 | 0.15961 | 0.15961 | 0.15961 | 0.15961 | 0.15961 | 0.15961 | 0.15961 | 0.14531 | 0.14029
|  | OVERSCAIG | ST |  |  |  | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.15866 | 0.15862 | 0.15855 | 0.15848 | 0.15825 | 0.15805 | 0.15789 | 0.1578 | 0.15776 | 0.15773 | 0.15773 | 0.15773 | 0.14921 | 0.14707 | 0.15977 | 0.15975 | 0.15972 | 0.15968 | 0.15961 | 0.15961 | 0.15961 | 0.15961 | 0.15961 | 0.15961 | 0.15961 | 0.15961 | 0.15961 | 0.14873
|  | OVERSCAIG | FS |  |  |  | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.16583 | 0.15868 | 0.15868 | 0.15866 | 0.15864 | 0.15857 | 0.15849 | 0.1584 | 0.1583 | 0.15821 | 0.15812 | 0.15806 | 0.15781 | 0.15774 | 0.15773 | 0.15978 | 0.15978 | 0.15977 | 0.15976 | 0.15973 | 0.15969 | 0.15965 | 0.15961 | 0.15961 | 0.15961 | 0.15961 | 0.15961 | 0.15961 | 0.15961
| KINTORE | PARK | MINIMUM HEADROOM | NO 79107 99434 | YES | YES | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.0161 | 2.0034 | 1.9877 | 1.9722 | 1.9568 | 1.9415 | 1.9265 | 1.9145 | 0.98971 | 0.92987 | 0.87046 | 0.62049 | 0.36895 | 0.12231 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 0.80919 | 0.55651 | 0.30877
|  | PARK | CT |  |  |  | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.0205 | 2.0168 | 2.0126 | 2.0083 | 2.004 | 1.9996 | 1.9953 | 1.9907 | 1.9862 | 1.9816 | 1.9771 | 1.9362 | 0.99284 | 0.84299 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101
|  | PARK | LW |  |  |  | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.0161 | 2.0034 | 1.9877 | 1.9722 | 1.9568 | 1.9415 | 1.9265 | 1.9145 | 0.98971 | 0.92987 | 0.87046 | 0.62049 | 0.36895 | 0.12231 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 0.80919 | 0.55651 | 0.30877
|  | PARK | ST |  |  |  | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.0193 | 2.0141 | 2.006 | 1.9962 | 1.9899 | 1.9836 | 1.9774 | 1.9707 | 1.9642 | 1.9577 | 1.9513 | 1.92 | 0.97105 | 0.85809 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101
|  | PARK | FS |  |  |  | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.7748 | 2.0223 | 2.0219 | 2.0199 | 2.0175 | 2.0154 | 2.0133 | 2.0107 | 2.0082 | 2.0057 | 2.0032 | 2.0008 | 1.9891 | 1.978 | 1.9676 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101 | 2.101
| ALNESS | PEDDIESTON | MINIMUM HEADROOM | NH 74198 63656 | NO | YES | 3.7361 | 3.7344 | 3.7324 | 3.7304 | 3.7284 | 3.7265 | 3.7245 | 3.7224 | 3.7203 | 3.7181 | 3.717 | 3.717 | 3.717 | 3.717 | 3.3444 | 3.3367 | 3.3273 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 2.4514 | 2.2954 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 2.3734
|  | PEDDIESTON | CT |  |  |  | 3.7361 | 3.7347 | 3.7331 | 3.7315 | 3.73 | 3.7284 | 3.7269 | 3.7251 | 3.7234 | 3.7217 | 3.7201 | 3.717 | 3.717 | 3.717 | 3.3445 | 3.338 | 3.3306 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 2.4684 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191
|  | PEDDIESTON | LW |  |  |  | 3.7361 | 3.7344 | 3.7324 | 3.7304 | 3.7284 | 3.7265 | 3.7245 | 3.7224 | 3.7203 | 3.7181 | 3.717 | 3.717 | 3.717 | 3.717 | 3.3444 | 3.3367 | 3.3273 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 2.4514 | 2.2954 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 2.3734
|  | PEDDIESTON | ST |  |  |  | 3.7364 | 3.7354 | 3.734 | 3.7323 | 3.7311 | 3.7298 | 3.7286 | 3.7273 | 3.726 | 3.7247 | 3.7234 | 3.7177 | 3.717 | 3.717 | 3.3457 | 3.3413 | 3.3346 | 3.3267 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 3.3266 | 3.3205 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191
|  | PEDDIESTON | FS |  |  |  | 3.7369 | 3.7369 | 3.7366 | 3.7363 | 3.7359 | 3.7355 | 3.735 | 3.7345 | 3.734 | 3.7335 | 3.733 | 3.7308 | 3.7288 | 3.7268 | 3.3483 | 3.348 | 3.3469 | 3.3456 | 3.3438 | 3.3419 | 3.3395 | 3.3371 | 3.3347 | 3.3323 | 3.3301 | 3.3266 | 3.3266 | 3.3266 | 3.3239 | 3.3236 | 3.3221 | 3.3204 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191 | 3.3191
| PETERHEAD GRANGE | PETERHEAD GRANGE | MINIMUM HEADROOM | NK 11738 46516 | NO | YES | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 32.5576 | 32.5576 | 32.5576 | 30.1688 | 30.0025 | 29.7865 | 29.604 | 29.4744 | 29.3482 | 29.3482 | 29.3482 | 29.3482 | 29.3482 | 29.3482 | 28.9338 | 20.8185 | 19.5197 | 30.0754 | 30.045 | 30.0056 | 29.966 | 29.9264 | 29.8864 | 29.8471 | 29.8047 | 29.7634 | 29.7214 | 29.6799 | 28.9314 | 21.2429 | 19.9466
|  | PETERHEAD GRANGE | CT |  |  |  | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 32.5576 | 32.5576 | 32.5576 | 30.1688 | 30.0072 | 29.8196 | 29.6407 | 29.5282 | 29.4148 | 29.3482 | 29.3482 | 29.3482 | 29.3482 | 29.3482 | 28.9338 | 21.5819 | 20.4724 | 30.0754 | 30.0459 | 30.0117 | 29.9773 | 29.9428 | 29.9081 | 29.8739 | 29.8371 | 29.8013 | 29.7649 | 29.7288 | 28.9314 | 22.0049 | 20.8975
|  | PETERHEAD GRANGE | LW |  |  |  | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 32.5576 | 32.5576 | 32.5576 | 30.1767 | 30.0025 | 29.7865 | 29.604 | 29.4744 | 29.3482 | 29.3482 | 29.3482 | 29.3482 | 29.3482 | 29.3482 | 28.9338 | 20.8185 | 19.5197 | 30.0768 | 30.045 | 30.0056 | 29.966 | 29.9264 | 29.8864 | 29.8471 | 29.8047 | 29.7634 | 29.7214 | 29.6799 | 28.9314 | 21.2429 | 19.9466
|  | PETERHEAD GRANGE | ST |  |  |  | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 32.9156 | 32.9156 | 32.9156 | 30.2438 | 30.2061 | 30.1474 | 30.0759 | 29.992 | 29.9068 | 29.8231 | 29.7329 | 29.65 | 29.5971 | 29.5452 | 29.141 | 29.141 | 29.141 | 30.089 | 30.0821 | 30.0714 | 30.0584 | 30.0431 | 30.0275 | 30.0123 | 29.9958 | 29.9801 | 29.9639 | 29.948 | 29.5447 | 29.4695 | 29.3967
|  | PETERHEAD GRANGE | FS |  |  |  | 33.2852 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 33.2736 | 30.6867 | 30.2588 | 30.2385 | 30.214 | 30.1853 | 30.156 | 30.1202 | 30.0846 | 30.0505 | 30.0157 | 29.9816 | 29.8158 | 29.6575 | 29.567 | 30.1698 | 30.0918 | 30.0881 | 30.0836 | 30.0784 | 30.073 | 30.0665 | 30.06 | 30.0538 | 30.0474 | 30.0412 | 30.0109 | 29.9821 | 29.9547
| PETERHEAD GRANGE | PETERHEAD NORTH STREET | MINIMUM HEADROOM | NK 13470 46450 | NO | YES | 27.1505 | 27.148 | 27.1448 | 27.1416 | 27.1384 | 27.1352 | 27.132 | 27.1286 | 27.1253 | 27.1219 | 27.1185 | 27.1004 | 27.0823 | 27.0647 | 26.0708 | 26.0518 | 26.0281 | 26.0043 | 25.9803 | 25.956 | 25.9322 | 25.9066 | 25.882 | 25.8566 | 25.8316 | 25.6962 | 25.6501 | 25.6391 | 26.2641 | 26.2333 | 26.195 | 26.1563 | 26.1174 | 26.0781 | 26.0395 | 25.9981 | 25.9581 | 25.9303 | 25.9102 | 25.8015 | 25.6931 | 25.5871
|  | PETERHEAD NORTH STREET | CT |  |  |  | 27.1507 | 27.1488 | 27.1465 | 27.1442 | 27.1419 | 27.1395 | 27.1372 | 27.1348 | 27.1324 | 27.1299 | 27.1275 | 27.1141 | 27.1008 | 27.0878 | 26.072 | 26.0576 | 26.0408 | 26.0237 | 26.0064 | 25.9888 | 25.9715 | 25.953 | 25.9352 | 25.9168 | 25.8987 | 25.7986 | 25.6991 | 25.6535 | 26.2661 | 26.2427 | 26.2154 | 26.1877 | 26.1597 | 26.1312 | 26.1032 | 26.0731 | 26.0443 | 26.0145 | 25.9851 | 25.8837 | 25.8038 | 25.7258
|  | PETERHEAD NORTH STREET | LW |  |  |  | 27.1505 | 27.148 | 27.1448 | 27.1416 | 27.1384 | 27.1352 | 27.132 | 27.1286 | 27.1253 | 27.1219 | 27.1185 | 27.1004 | 27.0823 | 27.0647 | 26.0708 | 26.0518 | 26.0281 | 26.0043 | 25.9803 | 25.956 | 25.9322 | 25.9066 | 25.882 | 25.8566 | 25.8316 | 25.6962 | 25.6501 | 25.6391 | 26.2641 | 26.2333 | 26.195 | 26.1563 | 26.1174 | 26.0781 | 26.0395 | 25.9981 | 25.9581 | 25.9303 | 25.9102 | 25.8015 | 25.6931 | 25.5871
|  | PETERHEAD NORTH STREET | ST |  |  |  | 27.1513 | 27.1505 | 27.1493 | 27.1478 | 27.1461 | 27.1444 | 27.1427 | 27.1409 | 27.1392 | 27.1374 | 27.1357 | 27.1273 | 27.1192 | 27.1114 | 26.0769 | 26.0709 | 26.0615 | 26.0501 | 26.0375 | 26.0248 | 26.0123 | 25.9989 | 25.986 | 25.9728 | 25.9599 | 25.8971 | 25.837 | 25.7785 | 26.2741 | 26.2642 | 26.249 | 26.2305 | 26.2102 | 26.1895 | 26.1693 | 26.1475 | 26.1267 | 26.1053 | 26.0843 | 25.9826 | 25.9145 | 25.8676
|  | PETERHEAD NORTH STREET | FS |  |  |  | 27.1518 | 27.1517 | 27.1513 | 27.1509 | 27.1503 | 27.1497 | 27.149 | 27.1482 | 27.1476 | 27.1468 | 27.1462 | 27.1428 | 27.1396 | 27.1367 | 26.0803 | 26.0795 | 26.0767 | 26.0733 | 26.069 | 26.0646 | 26.0591 | 26.0538 | 26.0486 | 26.0433 | 26.0382 | 26.0131 | 25.9894 | 25.9673 | 26.2795 | 26.2783 | 26.2737 | 26.2682 | 26.2612 | 26.254 | 26.2452 | 26.2365 | 26.2281 | 26.2196 | 26.2112 | 26.1706 | 26.1322 | 26.0964
| FORT WILLIAM | PINEGROVE | MINIMUM HEADROOM | NN 10496 73556 | NO | YES | 15.4917 | 15.4812 | 15.4727 | 15.4563 | 15.4379 | 15.4174 | 15.4005 | 15.3824 | 15.3688 | 15.3601 | 15.355 | 15.3138 | 15.273 | 15.2514 | 14.0905 | 14.0573 | 14.0305 | 13.9785 | 13.9204 | 13.915 | 13.915 | 13.915 | 13.915 | 13.915 | 13.915 | 13.915 | 13.915 | 13.915 | 14.6846 | 14.6685 | 14.6554 | 14.6302 | 14.602 | 14.5704 | 14.5445 | 14.5167 | 14.4957 | 14.4824 | 14.4747 | 14.4555 | 14.4555 | 14.4555
|  | PINEGROVE | CT |  |  |  | 15.4924 | 15.4836 | 15.4771 | 15.4636 | 15.4482 | 15.4314 | 15.4165 | 15.4 | 15.3849 | 15.3736 | 15.3671 | 15.3327 | 15.3057 | 15.2802 | 14.0928 | 14.0649 | 14.0444 | 14.0015 | 13.9528 | 13.915 | 13.915 | 13.915 | 13.915 | 13.915 | 13.915 | 13.915 | 13.915 | 13.915 | 14.6857 | 14.6722 | 14.6622 | 14.6413 | 14.6177 | 14.5919 | 14.569 | 14.5438 | 14.5204 | 14.5031 | 14.4932 | 14.4555 | 14.4555 | 14.4555
|  | PINEGROVE | LW |  |  |  | 15.4917 | 15.4812 | 15.4727 | 15.4563 | 15.4379 | 15.4174 | 15.4005 | 15.3824 | 15.3688 | 15.3601 | 15.355 | 15.3138 | 15.273 | 15.2514 | 14.0905 | 14.0573 | 14.0305 | 13.9785 | 13.9204 | 13.915 | 13.915 | 13.915 | 13.915 | 13.915 | 13.915 | 13.915 | 13.915 | 13.915 | 14.6846 | 14.6685 | 14.6554 | 14.6302 | 14.602 | 14.5704 | 14.5445 | 14.5167 | 14.4957 | 14.4824 | 14.4747 | 14.4555 | 14.4555 | 14.4555
|  | PINEGROVE | ST |  |  |  | 15.4943 | 15.489 | 15.485 | 15.4759 | 15.4638 | 15.4508 | 15.4391 | 15.426 | 15.4135 | 15.4037 | 15.3974 | 15.3726 | 15.354 | 15.3361 | 14.0988 | 14.082 | 14.0692 | 14.0405 | 14.0023 | 13.9612 | 13.9242 | 13.915 | 13.915 | 13.915 | 13.915 | 13.915 | 13.915 | 13.915 | 14.6886 | 14.6804 | 14.6742 | 14.6603 | 14.6417 | 14.6218 | 14.6038 | 14.5836 | 14.5645 | 14.5494 | 14.5397 | 14.5017 | 14.473 | 14.4555
|  | PINEGROVE | FS |  |  |  | 15.4959 | 15.4933 | 15.4915 | 15.4875 | 15.4825 | 15.4771 | 15.4723 | 15.467 | 15.4625 | 15.4591 | 15.4564 | 15.446 | 15.4394 | 15.4332 | 14.1038 | 14.0957 | 14.0898 | 14.0772 | 14.0614 | 14.0444 | 14.0292 | 14.0124 | 13.9982 | 13.9872 | 13.9789 | 13.946 | 13.925 | 13.915 | 14.691 | 14.6871 | 14.6842 | 14.6781 | 14.6704 | 14.6622 | 14.6548 | 14.6467 | 14.6397 | 14.6344 | 14.6304 | 14.6144 | 14.6042 | 14.5947
| TUMMEL BRIDGE | PITLOCHRY | MINIMUM HEADROOM | NN 95756 58991 | NO | YES | 7.7274 | 7.7252 | 7.7225 | 7.9572 | 7.9542 | 7.9513 | 7.9482 | 7.945 | 7.9417 | 7.9391 | 7.9365 | 7.9281 | 7.9281 | 6.0201 | 7.3597 | 7.3481 | 7.3336 | 7.8686 | 7.853 | 7.8391 | 7.8312 | 7.8272 | 7.8272 | 7.8272 | 7.8272 | 7.8272 | 6.1829 | 5.8273 | 7.7946 | 7.7946 | 7.7946 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446
|  | PITLOCHRY | CT |  |  |  | 7.7275 | 7.7258 | 7.7239 | 7.9593 | 7.9571 | 7.9549 | 7.9526 | 7.95 | 7.9474 | 7.9453 | 7.9433 | 7.9281 | 7.9281 | 6.2901 | 7.3604 | 7.3514 | 7.3409 | 7.8799 | 7.8683 | 7.8566 | 7.8443 | 7.8359 | 7.829 | 7.8272 | 7.8272 | 7.8272 | 7.8272 | 6.1514 | 7.7961 | 7.7946 | 7.7946 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446
|  | PITLOCHRY | LW |  |  |  | 7.7274 | 7.7252 | 7.7225 | 7.9572 | 7.9542 | 7.9513 | 7.9482 | 7.945 | 7.9417 | 7.9391 | 7.9365 | 7.9281 | 7.9281 | 6.0201 | 7.3597 | 7.3481 | 7.3336 | 7.8686 | 7.853 | 7.8391 | 7.8312 | 7.8272 | 7.8272 | 7.8272 | 7.8272 | 7.8272 | 6.1829 | 5.8273 | 7.7946 | 7.7946 | 7.7946 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446
|  | PITLOCHRY | ST |  |  |  | 7.728 | 7.7273 | 7.7261 | 7.9623 | 7.9593 | 7.9563 | 7.9533 | 7.95 | 7.9466 | 7.9437 | 7.9409 | 7.9281 | 7.9281 | 7.9281 | 7.3631 | 7.359 | 7.353 | 7.8957 | 7.8798 | 7.8641 | 7.8481 | 7.8358 | 7.8272 | 7.8272 | 7.8272 | 7.8272 | 7.8272 | 7.8272 | 7.8019 | 7.7946 | 7.7946 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446
|  | PITLOCHRY | FS |  |  |  | 7.7284 | 7.7282 | 7.7278 | 7.9649 | 7.9638 | 7.9628 | 7.9615 | 7.9602 | 7.9589 | 7.9578 | 7.9567 | 7.9513 | 7.9466 | 7.9422 | 7.3649 | 7.364 | 7.3619 | 7.9096 | 7.9041 | 7.8986 | 7.8918 | 7.885 | 7.8781 | 7.8721 | 7.8661 | 7.8394 | 7.8272 | 7.8272 | 7.8059 | 7.8039 | 7.7995 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446 | 8.3446
| ARDMORE | POLLACHAR | MINIMUM HEADROOM | NF 75073 14513 | NO | YES | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 1.978 | 1.784 | 1.5816 | 3.583 | 3.5543 | 3.5212 | 3.4883 | 3.4578 | 3.4276 | 3.3978 | 3.3655 | 3.3335 | 3.302 | 3.2709 | 2.3488 | 2.0808 | 1.8012 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 1.5661 | 1.5231 | 1.4783
|  | POLLACHAR | CT |  |  |  | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 1.978 | 1.784 | 1.5932 | 3.583 | 3.5543 | 3.5212 | 3.4883 | 3.4578 | 3.4276 | 3.3978 | 3.3655 | 3.3335 | 3.302 | 3.2709 | 2.3488 | 2.0808 | 1.8172 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 1.5661 | 1.5231 | 1.4809
|  | POLLACHAR | LW |  |  |  | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.0766 | 1.827 | 1.5816 | 3.595 | 3.5844 | 3.5715 | 3.5583 | 3.5476 | 3.5372 | 3.527 | 3.5159 | 3.505 | 3.4941 | 3.4833 | 2.485 | 2.1402 | 1.8012 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 1.5879 | 1.5327 | 1.4783
|  | POLLACHAR | ST |  |  |  | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.5656 | 2.5237 | 2.442 | 3.5987 | 3.5951 | 3.5898 | 3.5834 | 3.5595 | 3.5358 | 3.5126 | 3.4874 | 3.4627 | 3.4388 | 3.4153 | 2.9723 | 2.8588 | 2.7458 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 1.9883 | 1.9823 | 1.9642
|  | POLLACHAR | FS |  |  |  | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 2.9243 | 3.6007 | 3.6 | 3.5982 | 3.5961 | 3.5874 | 3.5788 | 3.5677 | 3.5568 | 3.5461 | 3.5357 | 3.5254 | 3.4767 | 3.4312 | 3.3886 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664 | 2.3664
| FORT WILLIAM | POOR HOUSE | MINIMUM HEADROOM | NM 71766 70148 | YES | YES | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.10827 | 0.10814 | 0.10805 | 0.10796 | 0.10787 | 0.10779 | 0.10775 | 0.10775 | 0.10775 | 0.10775 | 0.10775 | 0.10775 | 0.10775 | 0.098718 | 0.10963 | 0.10961 | 0.10957 | 0.10954 | 0.10951 | 0.10948 | 0.10946 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.099321
|  | POOR HOUSE | CT |  |  |  | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.10828 | 0.10817 | 0.1081 | 0.10804 | 0.10798 | 0.10792 | 0.10786 | 0.10779 | 0.10775 | 0.10775 | 0.10775 | 0.10775 | 0.10775 | 0.10775 | 0.10963 | 0.10961 | 0.10959 | 0.10957 | 0.10955 | 0.10953 | 0.10951 | 0.10949 | 0.10946 | 0.10944 | 0.10942 | 0.10942 | 0.10942 | 0.10942
|  | POOR HOUSE | LW |  |  |  | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.10827 | 0.10814 | 0.10805 | 0.10796 | 0.10787 | 0.10779 | 0.10775 | 0.10775 | 0.10775 | 0.10775 | 0.10775 | 0.10775 | 0.10775 | 0.098718 | 0.10963 | 0.10961 | 0.10957 | 0.10954 | 0.10951 | 0.10948 | 0.10946 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.099321
|  | POOR HOUSE | ST |  |  |  | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.10832 | 0.10827 | 0.10821 | 0.10814 | 0.1081 | 0.10806 | 0.10802 | 0.10798 | 0.10794 | 0.1079 | 0.10786 | 0.10775 | 0.10775 | 0.10775 | 0.10965 | 0.10963 | 0.10962 | 0.10961 | 0.10959 | 0.10958 | 0.10956 | 0.10955 | 0.10954 | 0.10952 | 0.10951 | 0.10944 | 0.10942 | 0.10942
|  | POOR HOUSE | FS |  |  |  | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.11488 | 0.10834 | 0.10834 | 0.10832 | 0.1083 | 0.10827 | 0.10825 | 0.10821 | 0.10818 | 0.10815 | 0.10813 | 0.10812 | 0.10804 | 0.10797 | 0.10789 | 0.10966 | 0.10966 | 0.10965 | 0.10964 | 0.10963 | 0.10963 | 0.10962 | 0.10962 | 0.10961 | 0.1096 | 0.1096 | 0.10957 | 0.10955 | 0.10952
| PORT ANN | PORT ASKAIG | MINIMUM HEADROOM | NR 42082 68818 | YES | YES | 3.4048 | 3.3948 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3482 | 3.3482 | 3.0625 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0378 | 2.4055 | 3.2497 | 3.2466 | 3.2428 | 3.2392 | 3.2356 | 3.232 | 3.2286 | 3.2249 | 3.2219 | 3.2219 | 3.2219 | 3.2219 | 3.1811 | 2.4613
|  | PORT ASKAIG | CT |  |  |  | 3.4053 | 3.3978 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3482 | 3.3482 | 3.0626 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0378 | 3.0378 | 3.2498 | 3.2475 | 3.2449 | 3.2423 | 3.2398 | 3.2374 | 3.235 | 3.2323 | 3.2298 | 3.2272 | 3.2246 | 3.2219 | 3.1811 | 3.1811
|  | PORT ASKAIG | LW |  |  |  | 3.4048 | 3.3948 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3482 | 3.3482 | 3.0625 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0378 | 2.4055 | 3.2497 | 3.2466 | 3.2428 | 3.2392 | 3.2356 | 3.232 | 3.2286 | 3.2249 | 3.2219 | 3.2219 | 3.2219 | 3.2219 | 3.1811 | 2.4613
|  | PORT ASKAIG | ST |  |  |  | 3.4079 | 3.4049 | 3.4003 | 3.3947 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3693 | 3.3693 | 3.0635 | 3.0625 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.05 | 3.05 | 3.2506 | 3.2497 | 3.2483 | 3.2466 | 3.2436 | 3.2408 | 3.238 | 3.235 | 3.232 | 3.2291 | 3.2263 | 3.2219 | 3.2015 | 3.2015
|  | PORT ASKAIG | FS |  |  |  | 3.4097 | 3.4095 | 3.4081 | 3.4066 | 3.4035 | 3.4004 | 3.3964 | 3.3925 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.3903 | 3.0641 | 3.064 | 3.0636 | 3.0631 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.0622 | 3.2512 | 3.2511 | 3.2507 | 3.2502 | 3.2493 | 3.2483 | 3.2471 | 3.2459 | 3.2447 | 3.2436 | 3.2425 | 3.2371 | 3.2321 | 3.2274
| PORT ANN | PORT ELLEN | MINIMUM HEADROOM | NR 36459 45513 | YES | YES | 6.7993 | 6.7993 | 6.7993 | 6.7993 | 6.7993 | 6.7993 | 6.7993 | 6.7993 | 6.7993 | 6.7993 | 6.7993 | 6.5214 | 6.5214 | 6.5214 | 6.0328 | 6.0148 | 5.9956 | 5.9775 | 5.9621 | 5.947 | 5.9324 | 5.9276 | 5.9276 | 5.9276 | 5.9276 | 5.7723 | 5.7723 | 5.7723 | 5.908 | 5.908 | 5.908 | 5.908 | 5.908 | 5.908 | 5.908 | 5.908 | 5.908 | 5.908 | 5.908 | 5.6208 | 5.6208 | 5.6208
|  | PORT ELLEN | CT |  |  |  | 6.7993 | 6.7993 | 6.7993 | 6.7993 | 6.7993 | 6.7993 | 6.7993 | 6.7993 | 6.7993 | 6.7993 | 6.7993 | 6.5214 | 6.5214 | 6.5214 | 6.0346 | 6.0206 | 6.0069 | 5.9938 | 5.9824 | 5.9702 | 5.9584 | 5.9459 | 5.9341 | 5.9276 | 5.9276 | 5.7723 | 5.7723 | 5.7723 | 5.908 | 5.908 | 5.908 | 5.908 | 5.908 | 5.908 | 5.908 | 5.908 | 5.908 | 5.908 | 5.908 | 5.6208 | 5.6208 | 5.6208
|  | PORT ELLEN | LW |  |  |  | 6.7993 | 6.7993 | 6.7993 | 6.7993 | 6.7993 | 6.7993 | 6.7993 | 6.7993 | 6.7993 | 6.7993 | 6.7993 | 6.5214 | 6.5214 | 6.5214 | 6.0328 | 6.0148 | 5.9956 | 5.9775 | 5.9621 | 5.947 | 5.9324 | 5.9276 | 5.9276 | 5.9276 | 5.9276 | 5.7723 | 5.7723 | 5.7723 | 5.908 | 5.908 | 5.908 | 5.908 | 5.908 | 5.908 | 5.908 | 5.908 | 5.908 | 5.908 | 5.908 | 5.6208 | 5.6208 | 5.6208
|  | PORT ELLEN | ST |  |  |  | 6.7993 | 6.7993 | 6.7993 | 6.7993 | 6.7993 | 6.7993 | 6.7993 | 6.7993 | 6.7993 | 6.7993 | 6.7993 | 6.6604 | 6.6604 | 6.6604 | 6.0407 | 6.0339 | 6.026 | 6.0173 | 6.0021 | 5.9865 | 5.9714 | 5.9552 | 5.9397 | 5.9276 | 5.9276 | 5.85 | 5.85 | 5.85 | 5.908 | 5.908 | 5.908 | 5.908 | 5.908 | 5.908 | 5.908 | 5.908 | 5.908 | 5.908 | 5.908 | 5.7644 | 5.7644 | 5.7644
|  | PORT ELLEN | FS |  |  |  | 6.7993 | 6.7993 | 6.7993 | 6.7993 | 6.7993 | 6.7993 | 6.7993 | 6.7993 | 6.7993 | 6.7993 | 6.7993 | 6.7993 | 6.7993 | 6.7993 | 6.0453 | 6.0434 | 6.0405 | 6.0376 | 6.0324 | 6.0272 | 6.0207 | 6.0143 | 6.008 | 6.0019 | 5.9959 | 5.9683 | 5.9427 | 5.9276 | 5.908 | 5.908 | 5.908 | 5.908 | 5.908 | 5.908 | 5.908 | 5.908 | 5.908 | 5.908 | 5.908 | 5.908 | 5.908 | 5.908
| DUNVEGAN | PORTREE | MINIMUM HEADROOM | NG 48102 44602 | NO | YES | 10.1767 | 10.066 | 9.9608 | 9.8594 | 9.7617 | 9.6678 | 9.5777 | 9.5367 | 9.5163 | 9.4961 | 9.4762 | 9.3794 | 9.2944 | 9.2085 | 9.892 | 9.7364 | 9.6349 | 9.5594 | 9.5045 | 9.4516 | 9.4009 | 9.3778 | 9.3663 | 9.355 | 9.3438 | 9.2893 | 9.2415 | 9.1931 | 9.9652 | 9.8352 | 9.7134 | 9.5951 | 9.4804 | 9.373 | 9.2579 | 9.2056 | 9.1752 | 9.1451 | 9.1224 | 9.0215 | 8.9331 | 7.2552
|  | PORTREE | CT |  |  |  | 10.1767 | 10.066 | 9.9608 | 9.8594 | 9.7617 | 9.6678 | 9.5777 | 9.5367 | 9.5163 | 9.4961 | 9.4762 | 9.3794 | 9.2944 | 9.2085 | 9.892 | 9.7364 | 9.6349 | 9.5594 | 9.5045 | 9.4516 | 9.4009 | 9.3778 | 9.3663 | 9.355 | 9.3438 | 9.2893 | 9.2415 | 9.1931 | 9.9652 | 9.8352 | 9.7134 | 9.5951 | 9.4804 | 9.373 | 9.2579 | 9.2056 | 9.1752 | 9.1451 | 9.1224 | 9.0215 | 8.9331 | 7.2552
|  | PORTREE | LW |  |  |  | 10.3727 | 10.3561 | 10.3374 | 10.3168 | 10.2945 | 10.2706 | 10.2454 | 10.2227 | 10.1993 | 10.1753 | 10.1511 | 10.0227 | 9.8995 | 9.772 | 10.0702 | 9.9954 | 9.9344 | 9.8684 | 9.8043 | 9.7909 | 9.7767 | 9.7639 | 9.7507 | 9.7373 | 9.7236 | 9.6514 | 9.5821 | 9.5103 | 10.1815 | 10.1478 | 10.12 | 10.0896 | 10.0569 | 10.027 | 9.9823 | 9.953 | 9.923 | 9.8929 | 9.8626 | 9.6913 | 9.5631 | 9.4303
|  | PORTREE | ST |  |  |  | 10.4011 | 10.3945 | 10.388 | 10.3818 | 10.3741 | 10.3667 | 10.3595 | 10.3527 | 10.3426 | 10.3328 | 10.3233 | 10.2799 | 10.2416 | 10.2068 | 10.1069 | 10.0697 | 10.0435 | 10.0137 | 9.9654 | 9.9299 | 9.8507 | 9.8371 | 9.8314 | 9.8259 | 9.8206 | 9.7961 | 9.7746 | 9.755 | 10.2168 | 10.1984 | 10.1854 | 10.1744 | 10.1589 | 10.1459 | 10.1252 | 10.1118 | 10.0949 | 10.0784 | 10.0628 | 9.9924 | 9.9288 | 9.8829
|  | PORTREE | FS |  |  |  | 10.3945 | 10.3879 | 10.3781 | 10.3684 | 10.3589 | 10.3495 | 10.3402 | 10.3311 | 10.3221 | 10.3132 | 10.3044 | 10.252 | 10.2061 | 10.1637 | 10.1083 | 10.0876 | 10.0691 | 10.0495 | 10.0243 | 10.0053 | 9.9679 | 9.9463 | 9.9252 | 9.9038 | 9.8827 | 9.7815 | 9.7546 | 9.7308 | 10.212 | 10.1996 | 10.1855 | 10.171 | 10.1556 | 10.1436 | 10.1286 | 10.1165 | 10.1045 | 10.0926 | 10.081 | 10.0154 | 9.9582 | 9.9051
| MACDUFF | PORTSOY | MINIMUM HEADROOM | NJ 58491 65037 | YES | YES | 1.8535 | 1.8535 | 1.8535 | 1.8535 | 1.8535 | 1.8535 | 1.8535 | 1.8535 | 1.8535 | 1.8535 | 1.8535 | -0.13097 | -1.289 | -1.3231 | 2.312 | 2.3114 | 2.3106 | 2.3097 | 2.3089 | 2.308 | 2.3071 | 2.3062 | 2.3053 | 2.3044 | 2.3035 | 0.43473 | -0.80017 | -0.96092 | 3.6834 | 3.6819 | 3.6801 | 3.6782 | 3.6762 | 3.6741 | 3.6721 | 3.67 | 2.4337 | 2.4228 | 2.4121 | 0.059832 | -1.3614 | -1.4754
|  | PORTSOY | CT |  |  |  | 1.8535 | 1.8535 | 1.8535 | 1.8535 | 1.8535 | 1.8535 | 1.8535 | 1.8535 | 1.8535 | 1.8535 | 1.8535 | -0.13097 | -1.289 | -1.289 | 2.312 | 2.3115 | 2.311 | 2.3104 | 2.3097 | 2.3091 | 2.3084 | 2.3077 | 2.3071 | 2.3064 | 2.3057 | 0.48343 | -0.73974 | -0.88893 | 3.6835 | 3.6824 | 3.681 | 3.6796 | 3.6782 | 3.6766 | 3.6751 | 3.6735 | 3.672 | 3.6704 | 3.6688 | 0.094365 | -1.3185 | -1.4243
|  | PORTSOY | LW |  |  |  | 1.8535 | 1.8535 | 1.8535 | 1.8535 | 1.8535 | 1.8535 | 1.8535 | 1.8535 | 1.8535 | 1.8535 | 1.8535 | -0.13097 | -1.289 | -1.3231 | 2.312 | 2.3114 | 2.3106 | 2.3097 | 2.3089 | 2.308 | 2.3071 | 2.3062 | 2.3053 | 2.3044 | 2.3035 | 0.43473 | -0.80017 | -0.96092 | 3.6834 | 3.6819 | 3.6801 | 3.6782 | 3.6762 | 3.6741 | 3.6721 | 3.67 | 2.4337 | 2.4228 | 2.4121 | 0.059832 | -1.3614 | -1.4754
|  | PORTSOY | ST |  |  |  | 1.8535 | 1.8535 | 1.8535 | 1.8535 | 1.8535 | 1.8535 | 1.8535 | 1.8535 | 1.8535 | 1.8535 | 1.8535 | 0.86126 | 0.28226 | 0.28226 | 2.3122 | 2.312 | 2.3116 | 2.3112 | 2.3105 | 2.3097 | 2.309 | 2.3082 | 2.3074 | 2.3066 | 2.3059 | 1.4938 | 0.89864 | 0.84063 | 3.6839 | 3.6834 | 3.6826 | 3.6817 | 3.68 | 3.6782 | 3.6765 | 3.6746 | 3.6728 | 3.671 | 3.6692 | 1.2782 | 0.58347 | 0.54234
|  | PORTSOY | FS |  |  |  | 1.8535 | 1.8535 | 1.8535 | 1.8535 | 1.8535 | 1.8535 | 1.8535 | 1.8535 | 1.8535 | 1.8535 | 1.8535 | 1.8535 | 1.8535 | 1.8535 | 2.3123 | 2.3123 | 2.3122 | 2.312 | 2.3117 | 2.3114 | 2.3111 | 2.3107 | 2.3103 | 2.31 | 2.3096 | 2.3079 | 2.3063 | 2.3047 | 3.6841 | 3.684 | 3.6838 | 3.6835 | 3.6828 | 3.6821 | 3.6812 | 3.6804 | 3.6796 | 3.6787 | 3.6779 | 3.674 | 3.6702 | 2.4272
| WOODHILL | QUEENS LANE NORTH | MINIMUM HEADROOM | NJ 92224 05823 | NO | NO | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 16.755 | 16.6859 | 16.601 | 16.5177 | 16.4357 | 16.3551 | 16.2759 | 16.2069 | 16.2069 | 16.2069 | 16.2069 | 16.2069 | 10.9361 | 9.4537 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 10.7216 | 9.2329
|  | QUEENS LANE NORTH | CT |  |  |  | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 16.7657 | 16.7247 | 16.6777 | 16.6315 | 16.586 | 16.5411 | 16.497 | 16.4493 | 16.402 | 16.3549 | 16.3079 | 16.2069 | 16.2069 | 16.2069 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485
|  | QUEENS LANE NORTH | LW |  |  |  | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 16.755 | 16.6859 | 16.601 | 16.5177 | 16.4357 | 16.3551 | 16.2759 | 16.2069 | 16.2069 | 16.2069 | 16.2069 | 16.2069 | 10.9361 | 9.4537 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 10.7216 | 9.2329
|  | QUEENS LANE NORTH | ST |  |  |  | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 16.7677 | 16.7325 | 16.6776 | 16.6118 | 16.5546 | 16.4985 | 16.4436 | 16.3842 | 16.3259 | 16.2685 | 16.2119 | 16.2069 | 16.2069 | 16.2069 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485
|  | QUEENS LANE NORTH | FS |  |  |  | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 19.475 | 16.7886 | 16.7865 | 16.7746 | 16.7605 | 16.743 | 16.7257 | 16.7035 | 16.6817 | 16.6602 | 16.6392 | 16.6187 | 16.5196 | 16.4234 | 16.3303 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485 | 16.6485
| QUOICH | QUOICH | MINIMUM HEADROOM | NH 11700 01900 | YES | YES | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.9189 | -1.9191 | -1.9195 | -1.9198 | -1.9201 | -1.9205 | -1.9208 | -1.9211 | -1.9214 | -1.9218 | -1.9221 | -1.9241 | -1.9262 | -1.9282
|  | QUOICH | CT |  |  |  | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.9189 | -1.9191 | -1.9193 | -1.9195 | -1.9198 | -1.92 | -1.9202 | -1.9204 | -1.9207 | -1.9209 | -1.9211 | -1.9224 | -1.9236 | -1.9248
|  | QUOICH | LW |  |  |  | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.9189 | -1.9191 | -1.9195 | -1.9198 | -1.9201 | -1.9205 | -1.9208 | -1.9211 | -1.9214 | -1.9218 | -1.9221 | -1.9241 | -1.9262 | -1.9282
|  | QUOICH | ST |  |  |  | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.9188 | -1.9189 | -1.919 | -1.9191 | -1.9193 | -1.9195 | -1.9197 | -1.9199 | -1.9201 | -1.9203 | -1.9205 | -1.9214 | -1.9223 | -1.9232
|  | QUOICH | FS |  |  |  | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.9547 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.9187 | -1.9187 | -1.9188 | -1.9188 | -1.9189 | -1.9189 | -1.919 | -1.9191 | -1.9192 | -1.9193 | -1.9193 | -1.9197 | -1.92 | -1.9203
| THURSO | RACKWICK | MINIMUM HEADROOM | ND 20206 99857 | YES | YES | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.11328 | 0.11314 | 0.11297 | 0.11281 | 0.11264 | 0.11249 | 0.11237 | 0.11224 | 0.11212 | 0.11202 | 0.11199 | 0.11188 | 0.11188 | 0.11188 | 0.11501 | 0.11494 | 0.11486 | 0.11478 | 0.11478 | 0.11478 | 0.11478 | 0.11478 | 0.11478 | 0.11478 | 0.11478 | 0.11478 | 0.11478 | 0.11478
|  | RACKWICK | CT |  |  |  | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.11329 | 0.11318 | 0.11307 | 0.11295 | 0.11284 | 0.11273 | 0.11262 | 0.1125 | 0.11241 | 0.11232 | 0.11223 | 0.11198 | 0.11188 | 0.11188 | 0.11501 | 0.11496 | 0.1149 | 0.11485 | 0.11479 | 0.11478 | 0.11478 | 0.11478 | 0.11478 | 0.11478 | 0.11478 | 0.11478 | 0.11478 | 0.11478
|  | RACKWICK | LW |  |  |  | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.11328 | 0.11314 | 0.11297 | 0.11281 | 0.11264 | 0.11249 | 0.11237 | 0.11224 | 0.11212 | 0.11202 | 0.11199 | 0.11188 | 0.11188 | 0.11188 | 0.11501 | 0.11494 | 0.11486 | 0.11478 | 0.11478 | 0.11478 | 0.11478 | 0.11478 | 0.11478 | 0.11478 | 0.11478 | 0.11478 | 0.11478 | 0.11478
|  | RACKWICK | ST |  |  |  | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.11332 | 0.11328 | 0.11322 | 0.11314 | 0.11306 | 0.11299 | 0.11292 | 0.11284 | 0.11277 | 0.11269 | 0.11262 | 0.11232 | 0.11206 | 0.11197 | 0.11503 | 0.11501 | 0.11498 | 0.11494 | 0.1149 | 0.11487 | 0.11483 | 0.11479 | 0.11478 | 0.11478 | 0.11478 | 0.11478 | 0.11478 | 0.11478
|  | RACKWICK | FS |  |  |  | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.12433 | 0.11335 | 0.11334 | 0.11333 | 0.1133 | 0.11328 | 0.11325 | 0.11322 | 0.11319 | 0.11316 | 0.11313 | 0.1131 | 0.11296 | 0.11283 | 0.11271 | 0.11504 | 0.11504 | 0.11503 | 0.11502 | 0.11501 | 0.11499 | 0.11498 | 0.11496 | 0.11495 | 0.11493 | 0.11492 | 0.11485 | 0.11479 | 0.11478
| FORT WILLIAM | RAHOY | MINIMUM HEADROOM | NM 69621 49222 | YES | YES | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0131 | 1.0131 | 1.013 | 1.013 | 1.013 | 1.0129 | 1.0129 | 1.0129 | 1.0129 | 1.0128 | 1.0128 | 1.0127 | 1.0126 | 1.0125 | 1.0152 | 1.0152 | 1.0151 | 1.0151 | 1.0151 | 1.0151 | 1.0151 | 1.0151 | 1.0151 | 1.0151 | 1.0151 | 1.0151 | 1.015 | 1.015
|  | RAHOY | CT |  |  |  | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0131 | 1.0131 | 1.0131 | 1.013 | 1.013 | 1.013 | 1.013 | 1.013 | 1.0129 | 1.0129 | 1.0129 | 1.0128 | 1.0127 | 1.0127 | 1.0152 | 1.0152 | 1.0152 | 1.0151 | 1.0151 | 1.0151 | 1.0151 | 1.0151 | 1.0151 | 1.0151 | 1.0151 | 1.0151 | 1.0151 | 1.0151
|  | RAHOY | LW |  |  |  | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0131 | 1.0131 | 1.013 | 1.013 | 1.013 | 1.0129 | 1.0129 | 1.0129 | 1.0129 | 1.0128 | 1.0128 | 1.0127 | 1.0126 | 1.0125 | 1.0152 | 1.0152 | 1.0151 | 1.0151 | 1.0151 | 1.0151 | 1.0151 | 1.0151 | 1.0151 | 1.0151 | 1.0151 | 1.0151 | 1.015 | 1.015
|  | RAHOY | ST |  |  |  | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0131 | 1.0131 | 1.0131 | 1.0131 | 1.0131 | 1.013 | 1.013 | 1.013 | 1.013 | 1.013 | 1.013 | 1.0129 | 1.0128 | 1.0128 | 1.0152 | 1.0152 | 1.0152 | 1.0152 | 1.0152 | 1.0151 | 1.0151 | 1.0151 | 1.0151 | 1.0151 | 1.0151 | 1.0151 | 1.0151 | 1.0151
|  | RAHOY | FS |  |  |  | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0234 | 1.0131 | 1.0131 | 1.0131 | 1.0131 | 1.0131 | 1.0131 | 1.0131 | 1.0131 | 1.0131 | 1.0131 | 1.0131 | 1.013 | 1.013 | 1.013 | 1.0152 | 1.0152 | 1.0152 | 1.0152 | 1.0152 | 1.0152 | 1.0152 | 1.0152 | 1.0152 | 1.0152 | 1.0152 | 1.0151 | 1.0151 | 1.0151
| INVERNESS | RAIGMORE | MINIMUM HEADROOM | NH 68427 44693 | NO | YES | 31.3898 | 31.2604 | 31.1362 | 31.0164 | 30.9011 | 30.7902 | 30.6837 | 30.6329 | 30.6076 | 30.5825 | 30.5579 | 30.4369 | 30.326 | 30.2122 | 30.5107 | 30.3701 | 30.2173 | 30.0854 | 29.9556 | 29.8319 | 29.7116 | 29.6028 | 29.5346 | 29.4679 | 29.4043 | 28.9497 | 28.4847 | 28.3382 | 30.3239 | 30.1588 | 29.9875 | 29.8314 | 29.6795 | 29.5444 | 29.4171 | 29.3398 | 29.2968 | 29.2546 | 29.2136 | 28.9666 | 28.8276 | 28.7114
|  | RAIGMORE | CT |  |  |  | 31.3898 | 31.2604 | 31.1362 | 31.0164 | 30.9011 | 30.7902 | 30.6837 | 30.6329 | 30.6076 | 30.5825 | 30.5579 | 30.4369 | 30.326 | 30.2122 | 30.5107 | 30.3701 | 30.2173 | 30.0854 | 29.9556 | 29.8319 | 29.7116 | 29.6028 | 29.5346 | 29.4679 | 29.4043 | 28.9497 | 28.4847 | 28.3382 | 30.3239 | 30.1588 | 29.9875 | 29.8314 | 29.6795 | 29.5444 | 29.4171 | 29.3398 | 29.2968 | 29.2546 | 29.2136 | 28.9666 | 28.8276 | 28.7114
|  | RAIGMORE | LW |  |  |  | 31.6186 | 31.5992 | 31.5774 | 31.5534 | 31.5273 | 31.4994 | 31.4701 | 31.4422 | 31.4135 | 31.3842 | 31.3545 | 31.1972 | 31.039 | 30.8686 | 30.6706 | 30.5664 | 30.4503 | 30.3568 | 30.2645 | 30.1797 | 30.0949 | 29.9821 | 29.8928 | 29.8038 | 29.7169 | 29.0723 | 28.8226 | 28.7232 | 30.5559 | 30.4942 | 30.4132 | 30.3492 | 30.2978 | 30.2475 | 30.1958 | 30.1364 | 30.0838 | 30.0308 | 29.9782 | 29.7054 | 29.5464 | 29.3751
|  | RAIGMORE | ST |  |  |  | 31.6518 | 31.6441 | 31.6366 | 31.6293 | 31.6204 | 31.6117 | 31.6033 | 31.5952 | 31.5833 | 31.5717 | 31.5605 | 31.5077 | 31.4604 | 31.4148 | 30.7351 | 30.6922 | 30.6232 | 30.5611 | 30.4992 | 30.44 | 30.3818 | 30.3054 | 30.2434 | 30.1831 | 30.1257 | 29.8477 | 29.5669 | 29.2905 | 30.6087 | 30.5835 | 30.5463 | 30.5124 | 30.47 | 30.4295 | 30.3989 | 30.3676 | 30.3378 | 30.3088 | 30.2811 | 30.148 | 30.0185 | 29.9241
|  | RAIGMORE | FS |  |  |  | 31.6441 | 31.6364 | 31.6249 | 31.6137 | 31.6025 | 31.5916 | 31.5807 | 31.5701 | 31.5595 | 31.5492 | 31.5389 | 31.4777 | 31.4226 | 31.3714 | 30.7574 | 30.7433 | 30.7126 | 30.6872 | 30.6541 | 30.6236 | 30.5876 | 30.5454 | 30.5173 | 30.4898 | 30.4632 | 30.3319 | 30.2085 | 30.0898 | 30.6137 | 30.6018 | 30.5797 | 30.5601 | 30.5371 | 30.5154 | 30.4913 | 30.4644 | 30.441 | 30.418 | 30.3956 | 30.2781 | 30.1926 | 30.1119
| ARBROATH | REDFORD | MINIMUM HEADROOM | NO 55879 44046 | YES | YES | 2.718 | 2.6075 | 2.493 | 2.3827 | 0.96945 | 0.87445 | 0.77012 | 0.68154 | 0.6263 | 0.57178 | 0.5179 | -0.36039 | -1.1273 | -1.4654 | 0.54446 | 0.42681 | 0.30658 | 0.19019 | 0.076881 | -0.033995 | -0.14032 | -0.21901 | -0.27135 | -0.32298 | -0.37403 | -1.116 | -1.771 | -2.0892 | 0.50585 | 0.36083 | 0.21215 | 0.068375 | -0.071216 | -0.20722 | -0.33767 | -0.43097 | -0.48961 | -0.54748 | -0.60467 | -1.5244 | -2.3286 | -2.6871
|  | REDFORD | CT |  |  |  | 2.718 | 2.6075 | 2.493 | 2.3827 | 0.96945 | 0.87445 | 0.77012 | 0.68154 | 0.6263 | 0.57178 | 0.5179 | -0.36039 | -1.1273 | -1.4654 | 0.54446 | 0.42681 | 0.30658 | 0.19019 | 0.076881 | -0.033995 | -0.14032 | -0.21901 | -0.27135 | -0.32298 | -0.37403 | -1.116 | -1.771 | -2.0892 | 0.50585 | 0.36083 | 0.21215 | 0.068375 | -0.071216 | -0.20722 | -0.33767 | -0.43097 | -0.48961 | -0.54748 | -0.60467 | -1.5244 | -2.3286 | -2.6871
|  | REDFORD | LW |  |  |  | 2.9137 | 2.8971 | 2.8785 | 2.8579 | 2.8356 | 2.8118 | 2.7867 | 2.7545 | 2.7213 | 2.6874 | 2.6531 | 0.23073 | -0.6297 | -1.1019 | 0.70075 | 0.65043 | 0.59535 | 0.53973 | 0.48355 | 0.42685 | 0.36978 | 0.30393 | 0.23753 | 0.17091 | 0.10413 | -0.71008 | -1.4557 | -1.8962 | 0.71438 | 0.66234 | 0.6052 | 0.54695 | 0.48762 | 0.42731 | 0.36623 | 0.2947 | 0.22236 | 0.14958 | 0.076518 | -0.91836 | -1.822 | -2.3223
|  | REDFORD | ST |  |  |  | 2.9421 | 2.9355 | 2.929 | 2.9228 | 2.9152 | 2.9078 | 2.9006 | 2.8931 | 2.8821 | 2.8715 | 2.8611 | 2.5246 | 0.78737 | 0.63819 | 0.73651 | 0.71749 | 0.6951 | 0.6695 | 0.64383 | 0.61781 | 0.59288 | 0.56669 | 0.53833 | 0.51076 | 0.48378 | 0.11719 | -0.19351 | -0.34072 | 0.75676 | 0.73698 | 0.71413 | 0.68836 | 0.66208 | 0.63556 | 0.61011 | 0.58339 | 0.55354 | 0.52452 | 0.49614 | 0.046824 | -0.32901 | -0.48818
|  | REDFORD | FS |  |  |  | 2.9355 | 2.9289 | 2.9191 | 2.9094 | 2.8999 | 2.8905 | 2.8813 | 2.8722 | 2.8632 | 2.8543 | 2.8456 | 2.7932 | 2.7364 | 2.681 | 0.8759 | 0.86827 | 0.85588 | 0.84269 | 0.82843 | 0.81445 | 0.79889 | 0.78356 | 0.76846 | 0.75361 | 0.73917 | 0.66162 | 0.5828 | 0.50688 | 0.88384 | 0.87461 | 0.85995 | 0.84459 | 0.82827 | 0.81226 | 0.79482 | 0.77765 | 0.76072 | 0.74407 | 0.72784 | 0.6389 | 0.54737 | 0.45896
| BURGHMUIR | REDGORTON | MINIMUM HEADROOM | NO 07650 28860 | NO | YES | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 14.5079 | 14.2533 | 13.9903 | 13.7163 | 13.4563 | 12.2407 | 11.5069 | 10.9159 | 15.5312 | 15.4677 | 15.3869 | 15.3169 | 13.5556 | 13.2914 | 13.0129 | 12.7118 | 12.4009 | 12.0773 | 11.7714 | 10.341 | 9.4776 | 8.7822 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 13.5222 | 13.2217 | 12.9114 | 12.5884 | 12.2831 | 10.8555 | 9.9937 | 9.2995
|  | REDGORTON | CT |  |  |  | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 14.4207 | 14.1854 | 13.9682 | 13.2645 | 12.8166 | 12.4051 | 15.5384 | 15.4921 | 15.4356 | 15.3739 | 15.3169 | 13.6267 | 13.4106 | 13.1696 | 12.9097 | 12.6316 | 12.3748 | 11.5457 | 11.0187 | 10.5344 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 13.6787 | 13.4193 | 13.1417 | 12.8854 | 12.0578 | 11.5318 | 11.0485
|  | REDGORTON | LW |  |  |  | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 14.5079 | 14.2533 | 13.9903 | 13.7163 | 13.4563 | 12.2407 | 11.5069 | 10.9159 | 15.5312 | 15.4677 | 15.3869 | 15.3169 | 13.5556 | 13.2914 | 13.0129 | 12.7118 | 12.4009 | 12.0773 | 11.7714 | 10.341 | 9.4776 | 8.7822 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 13.5222 | 13.2217 | 12.9114 | 12.5884 | 12.2831 | 10.8555 | 9.9937 | 9.2995
|  | REDGORTON | ST |  |  |  | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 14.5118 | 14.0255 | 13.7352 | 13.4668 | 15.5526 | 15.5279 | 15.4926 | 15.4499 | 15.4012 | 15.3494 | 13.78 | 13.6054 | 13.4152 | 13.2095 | 13.0175 | 12.4425 | 12.0995 | 11.7837 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 13.7185 | 13.5268 | 12.9529 | 12.6106 | 12.2954
|  | REDGORTON | FS |  |  |  | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 16.7863 | 15.5641 | 15.5558 | 15.5414 | 15.525 | 15.5059 | 15.4855 | 15.4618 | 15.4365 | 15.4096 | 15.3814 | 15.3541 | 13.6035 | 13.3813 | 13.2544 | 15.5549 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 15.5543 | 13.7633
| REDMOSS | REDMOSS | MINIMUM HEADROOM | NJ 94562 01919 | NO | YES | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 43.428 | 43.232 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 35.7687 | 34.5977 | 33.4469 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 36.6348 | 35.4634 | 34.3122
|  | REDMOSS | CT |  |  |  | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 43.4549 | 43.3232 | 43.1789 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 36.0048 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362
|  | REDMOSS | LW |  |  |  | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 43.428 | 43.232 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 35.7687 | 34.5977 | 33.4469 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 36.6348 | 35.4634 | 34.3122
|  | REDMOSS | ST |  |  |  | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 43.5016 | 43.4329 | 43.3337 | 43.2151 | 43.1658 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 43.1537 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362
|  | REDMOSS | FS |  |  |  | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 48.9235 | 43.7685 | 43.5288 | 43.4944 | 43.455 | 43.4231 | 43.3901 | 43.3512 | 43.3103 | 43.2676 | 43.229 | 43.2025 | 43.1537 | 43.1537 | 43.1537 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362 | 44.6362
| CASSLEY | RHICONICH | MINIMUM HEADROOM | NC 25554 52924 | YES | YES | 2.0553 | 2.0478 | 2.0386 | 2.0296 | 2.0208 | 2.0122 | 2.0038 | 1.9947 | 1.9857 | 1.9767 | 1.9678 | 1.9403 | 1.9403 | 1.9403 | 2.0017 | 2.0012 | 2.0005 | 1.9999 | 1.9993 | 1.9987 | 1.9981 | 1.9974 | 1.9968 | 1.9961 | 1.9955 | 1.9883 | 1.9811 | 1.9739 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003
|  | RHICONICH | CT |  |  |  | 2.0558 | 2.0501 | 2.0437 | 2.0374 | 2.0312 | 2.0252 | 2.0192 | 2.0128 | 2.0065 | 2.0002 | 1.994 | 1.9403 | 1.9403 | 1.9403 | 2.0017 | 2.0013 | 2.0009 | 2.0004 | 2 | 1.9996 | 1.9992 | 1.9987 | 1.9983 | 1.9978 | 1.9974 | 1.9909 | 1.9843 | 1.9778 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003
|  | RHICONICH | LW |  |  |  | 2.0553 | 2.0478 | 2.0386 | 2.0296 | 2.0208 | 2.0122 | 2.0038 | 1.9947 | 1.9857 | 1.9767 | 1.9678 | 1.9403 | 1.9403 | 1.9403 | 2.0017 | 2.0012 | 2.0005 | 1.9999 | 1.9993 | 1.9987 | 1.9981 | 1.9974 | 1.9968 | 1.9961 | 1.9955 | 1.9883 | 1.9811 | 1.9739 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003
|  | RHICONICH | ST |  |  |  | 2.0577 | 2.0555 | 2.0519 | 2.0477 | 2.0385 | 2.0294 | 2.0206 | 2.011 | 2.0017 | 1.9924 | 1.9834 | 1.9403 | 1.9403 | 1.9403 | 2.0019 | 2.0017 | 2.0015 | 2.0012 | 2.0005 | 1.9999 | 1.9993 | 1.9986 | 1.9979 | 1.9973 | 1.9966 | 1.9935 | 1.9904 | 1.9873 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003
|  | RHICONICH | FS |  |  |  | 2.059 | 2.0589 | 2.0579 | 2.0567 | 2.0536 | 2.0506 | 2.0467 | 2.0428 | 2.039 | 2.0354 | 2.0317 | 2.0145 | 1.9982 | 1.9829 | 2.002 | 2.002 | 2.0019 | 2.0018 | 2.0016 | 2.0014 | 2.0011 | 2.0008 | 2.0006 | 2.0003 | 2 | 1.9988 | 1.9977 | 1.9966 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003 | 2.2003
| DUDHOPE | ROSEBANK STREET | MINIMUM HEADROOM | NO 39943 31150 | NO | NO | 30.1109 | 29.9882 | 29.8765 | 29.7688 | 29.6651 | 29.5654 | 29.4697 | 29.4174 | 29.3914 | 29.3657 | 29.3404 | 29.2208 | 29.0981 | 28.9683 | 27.0405 | 26.8837 | 26.7357 | 26.5907 | 26.4484 | 26.3123 | 26.1806 | 26.0801 | 25.9929 | 25.9061 | 25.8744 | 25.7143 | 25.6032 | 25.5281 | 27.6584 | 27.5035 | 27.3599 | 27.2204 | 27.0848 | 26.9547 | 26.8294 | 26.7473 | 26.7056 | 26.6792 | 26.6532 | 26.5305 | 26.4069 | 26.2774
|  | ROSEBANK STREET | CT |  |  |  | 30.1109 | 29.9882 | 29.8765 | 29.7688 | 29.6651 | 29.5654 | 29.4697 | 29.4174 | 29.3914 | 29.3657 | 29.3404 | 29.2208 | 29.0981 | 28.9683 | 27.0405 | 26.8837 | 26.7357 | 26.5907 | 26.4484 | 26.3123 | 26.1806 | 26.0801 | 25.9929 | 25.9061 | 25.8744 | 25.7143 | 25.6032 | 25.5281 | 27.6584 | 27.5035 | 27.3599 | 27.2204 | 27.0848 | 26.9547 | 26.8294 | 26.7473 | 26.7056 | 26.6792 | 26.6532 | 26.5305 | 26.4069 | 26.2774
|  | ROSEBANK STREET | LW |  |  |  | 30.3281 | 30.3097 | 30.2889 | 30.2661 | 30.2414 | 30.215 | 30.1871 | 30.1569 | 30.1259 | 30.0942 | 30.0621 | 29.8921 | 29.701 | 29.5058 | 27.2141 | 27.1261 | 27.0284 | 26.9319 | 26.8319 | 26.7287 | 26.6259 | 26.5115 | 26.3919 | 26.3309 | 26.2888 | 26.0627 | 25.9521 | 25.8391 | 27.8829 | 27.8288 | 27.7686 | 27.7075 | 27.6436 | 27.577 | 27.5222 | 27.4913 | 27.4594 | 27.4269 | 27.394 | 27.2195 | 27.0233 | 26.823
|  | ROSEBANK STREET | ST |  |  |  | 30.3596 | 30.3522 | 30.3451 | 30.3381 | 30.3297 | 30.3215 | 30.3135 | 30.3062 | 30.2955 | 30.2851 | 30.275 | 30.22 | 30.1708 | 30.1183 | 27.2686 | 27.2298 | 27.1801 | 27.1212 | 27.0432 | 26.9681 | 26.8948 | 26.8163 | 26.7298 | 26.6431 | 26.5574 | 26.3596 | 26.2498 | 26.1936 | 27.9295 | 27.9062 | 27.8777 | 27.845 | 27.8022 | 27.7609 | 27.7206 | 27.6783 | 27.6335 | 27.6229 | 27.6125 | 27.556 | 27.5056 | 27.4517
|  | ROSEBANK STREET | FS |  |  |  | 30.3522 | 30.3449 | 30.3341 | 30.3234 | 30.3128 | 30.3024 | 30.2921 | 30.282 | 30.272 | 30.2621 | 30.2524 | 30.1943 | 30.1341 | 30.076 | 27.2885 | 27.2774 | 27.2564 | 27.2345 | 27.2039 | 27.1738 | 27.1377 | 27.1011 | 27.0642 | 27.0276 | 26.9917 | 26.8056 | 26.6345 | 26.4769 | 27.9342 | 27.9242 | 27.9071 | 27.8896 | 27.8681 | 27.8469 | 27.8229 | 27.7988 | 27.7747 | 27.7507 | 27.7272 | 27.6003 | 27.4792 | 27.4083
| KEITH | ROTHES | MINIMUM HEADROOM | NJ 27901 49693 | NO | YES | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 6.3113 | 6.3029 | 6.2921 | 6.2814 | 6.2721 | 6.2655 | 6.2655 | 6.2655 | 6.2655 | 6.2655 | 6.2655 | 6.2655 | 4.9718 | 4.7484 | 7.761 | 7.7529 | 7.7425 | 7.7321 | 7.7231 | 7.7142 | 7.7054 | 7.6956 | 7.6896 | 7.6896 | 7.6896 | 7.6896 | 7.6896 | 7.6896
|  | ROTHES | CT |  |  |  | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 6.3113 | 6.3029 | 6.2921 | 6.2814 | 6.2721 | 6.2655 | 6.2655 | 6.2655 | 6.2655 | 6.2655 | 6.2655 | 6.2655 | 4.9718 | 4.7484 | 7.761 | 7.7529 | 7.7425 | 7.7321 | 7.7231 | 7.7142 | 7.7054 | 7.6956 | 7.6896 | 7.6896 | 7.6896 | 7.6896 | 7.6896 | 7.6896
|  | ROTHES | LW |  |  |  | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 6.3143 | 6.3103 | 6.3042 | 6.2978 | 6.2929 | 6.2882 | 6.2835 | 6.2784 | 6.2734 | 6.2683 | 6.2655 | 6.2655 | 6.2655 | 4.81 | 7.764 | 7.7601 | 7.7542 | 7.748 | 7.7433 | 7.7387 | 7.7342 | 7.7292 | 7.7243 | 7.7195 | 7.7146 | 7.6896 | 7.6896 | 7.6896
|  | ROTHES | ST |  |  |  | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 6.3158 | 6.3148 | 6.3125 | 6.3098 | 6.3057 | 6.3018 | 6.2978 | 6.2934 | 6.289 | 6.2848 | 6.2807 | 6.2655 | 6.2655 | 6.2655 | 7.7654 | 7.7644 | 7.7622 | 7.7596 | 7.7557 | 7.7519 | 7.748 | 7.7437 | 7.7395 | 7.7354 | 7.7314 | 7.7124 | 7.6932 | 7.6896
|  | ROTHES | FS |  |  |  | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 7.6838 | 6.3179 | 6.3175 | 6.3153 | 6.3143 | 6.3128 | 6.3114 | 6.3095 | 6.3076 | 6.3058 | 6.3041 | 6.3023 | 6.2941 | 6.2866 | 6.2793 | 7.7659 | 7.7658 | 7.7649 | 7.764 | 7.7625 | 7.7611 | 7.7593 | 7.7575 | 7.7558 | 7.7541 | 7.7524 | 7.7445 | 7.7372 | 7.7301
| DUNOON | ROTHESAY | MINIMUM HEADROOM | NS 08636 64647 | NO | YES | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 16.3862 | 16.3558 | 16.3301 | 16.3099 | 16.2901 | 16.2707 | 16.2516 | 16.231 | 16.2196 | 16.2196 | 16.2196 | 16.2196 | 16.2196 | 13.4937 | 16.8086 | 16.803 | 16.7959 | 16.7888 | 16.7819 | 16.7752 | 16.7686 | 16.7614 | 16.7543 | 16.7472 | 16.7428 | 16.7428 | 16.7428 | 13.682
|  | ROTHESAY | CT |  |  |  | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 16.3862 | 16.3564 | 16.3331 | 16.3155 | 16.2983 | 16.2814 | 16.2648 | 16.2469 | 16.2291 | 16.2196 | 16.2196 | 16.2196 | 16.2196 | 16.2196 | 16.8086 | 16.8031 | 16.7969 | 16.7908 | 16.7848 | 16.7789 | 16.7732 | 16.7669 | 16.7607 | 16.7546 | 16.7485 | 16.7428 | 16.7428 | 16.7428
|  | ROTHESAY | LW |  |  |  | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 16.3878 | 16.3558 | 16.3301 | 16.3099 | 16.2901 | 16.2707 | 16.2516 | 16.231 | 16.2196 | 16.2196 | 16.2196 | 16.2196 | 16.2196 | 13.4937 | 16.8089 | 16.803 | 16.7959 | 16.7888 | 16.7819 | 16.7752 | 16.7686 | 16.7614 | 16.7543 | 16.7472 | 16.7428 | 16.7428 | 16.7428 | 13.682
|  | ROTHESAY | ST |  |  |  | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 16.3988 | 16.3893 | 16.3745 | 16.3568 | 16.3374 | 16.3238 | 16.3106 | 16.2964 | 16.2824 | 16.2686 | 16.2551 | 16.2196 | 16.2196 | 16.2196 | 16.8132 | 16.8092 | 16.8064 | 16.8032 | 16.7984 | 16.7937 | 16.7891 | 16.7841 | 16.7793 | 16.7745 | 16.7698 | 16.7468 | 16.7428 | 16.7428
|  | ROTHESAY | FS |  |  |  | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 17.1036 | 16.4048 | 16.4041 | 16.3998 | 16.3949 | 16.3858 | 16.3769 | 16.3654 | 16.354 | 16.3439 | 16.3382 | 16.3326 | 16.3058 | 16.2807 | 16.2574 | 16.8161 | 16.8157 | 16.8137 | 16.8113 | 16.8085 | 16.8069 | 16.8048 | 16.8027 | 16.8007 | 16.7987 | 16.7967 | 16.7874 | 16.7787 | 16.7706
| THURSO | ROUSAY | MINIMUM HEADROOM | HY 43876 30573 | YES | YES | -0.39179 | -0.40576 | -0.4291 | -0.45927 | -0.48893 | -0.51808 | -0.54668 | -0.57776 | -0.6086 | -0.63923 | -0.66974 | -1.5507 | -1.6065 | -1.6616 | -0.36111 | -0.39091 | -0.4275 | -0.46345 | -0.49907 | -0.53419 | -0.56866 | -0.60611 | -0.64328 | -0.68019 | -0.71697 | -1.4156 | -1.482 | -1.5477 | -0.55547 | -0.58521 | -0.62173 | -0.6576 | -0.69287 | -0.72753 | -0.76153 | -0.79849 | -0.83515 | -0.87157 | -0.90786 | -1.7894 | -1.8549 | -1.9196
|  | ROUSAY | CT |  |  |  | -0.39075 | -0.40088 | -0.41324 | -0.43086 | -0.45095 | -0.47064 | -0.48999 | -0.51101 | -0.53187 | -0.55258 | -0.57321 | -1.4405 | -1.4825 | -1.524 | -0.3589 | -0.38051 | -0.40527 | -0.4296 | -0.45353 | -0.47703 | -0.50034 | -0.52567 | -0.55081 | -0.57577 | -0.60063 | -1.2843 | -1.3344 | -1.3837 | -0.55326 | -0.57483 | -0.59954 | -0.62382 | -0.6477 | -0.67112 | -0.69412 | -0.71912 | -0.74393 | -0.76855 | -0.79308 | -1.6601 | -1.7094 | -1.7581
|  | ROUSAY | LW |  |  |  | -0.39179 | -0.40576 | -0.4291 | -0.45927 | -0.48893 | -0.51808 | -0.54668 | -0.57776 | -0.6086 | -0.63923 | -0.66974 | -1.5507 | -1.6065 | -1.6616 | -0.36111 | -0.39091 | -0.4275 | -0.46345 | -0.49907 | -0.53419 | -0.56866 | -0.60611 | -0.64328 | -0.68019 | -0.71697 | -1.4156 | -1.482 | -1.5477 | -0.55547 | -0.58521 | -0.62173 | -0.6576 | -0.69287 | -0.72753 | -0.76153 | -0.79849 | -0.83515 | -0.87157 | -0.90786 | -1.7894 | -1.8549 | -1.9196
|  | ROUSAY | ST |  |  |  | -0.38721 | -0.39125 | -0.39757 | -0.40512 | -0.4079 | -0.41085 | -0.41423 | -0.41791 | -0.4221 | -0.42708 | -0.43201 | -0.86898 | -0.89281 | -0.91654 | -0.35134 | -0.35997 | -0.37344 | -0.38955 | -0.39549 | -0.40127 | -0.40694 | -0.41311 | -0.41916 | -0.42509 | -0.43097 | -0.77748 | -0.80588 | -0.83415 | -0.54571 | -0.55433 | -0.56777 | -0.58385 | -0.58977 | -0.59555 | -0.60121 | -0.60736 | -0.6134 | -0.61932 | -0.62519 | -1.062 | -1.09 | -1.1178
|  | ROUSAY | FS |  |  |  | -0.38492 | -0.38522 | -0.38704 | -0.38919 | -0.39012 | -0.39103 | -0.39219 | -0.39334 | -0.39447 | -0.39557 | -0.39667 | -0.40185 | -0.40674 | -0.41173 | -0.34645 | -0.34709 | -0.35097 | -0.35557 | -0.35756 | -0.35948 | -0.36196 | -0.36441 | -0.36682 | -0.36919 | -0.37152 | -0.38259 | -0.393 | -0.40274 | -0.54084 | -0.54148 | -0.54535 | -0.54994 | -0.55192 | -0.55384 | -0.55632 | -0.55876 | -0.56117 | -0.56353 | -0.56586 | -0.5769 | -0.5873 | -0.59701
| CRAIGIEBUCKLER | RUTHRIESTON | MINIMUM HEADROOM | NJ 92574 04060 | NO | YES | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 26.1988 | 26.0918 | 25.9608 | 25.8868 | 25.8698 | 25.8698 | 25.8698 | 25.8698 | 25.8698 | 25.8698 | 25.8698 | 22.562 | 21.4989 | 20.4552 | 26.4893 | 26.4619 | 26.4285 | 26.4187 | 26.4187 | 26.4187 | 26.4187 | 26.4187 | 26.4187 | 26.4187 | 26.4187 | 22.9368 | 21.8733 | 20.8294
|  | RUTHRIESTON | CT |  |  |  | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 26.2154 | 26.1516 | 26.0788 | 26.0072 | 25.9367 | 25.892 | 25.8819 | 25.871 | 25.8698 | 25.8698 | 25.8698 | 25.8698 | 25.8698 | 22.7167 | 26.4935 | 26.4772 | 26.4586 | 26.4403 | 26.4223 | 26.4187 | 26.4187 | 26.4187 | 26.4187 | 26.4187 | 26.4187 | 26.4187 | 26.4187 | 26.4187
|  | RUTHRIESTON | LW |  |  |  | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 26.1988 | 26.0918 | 25.9608 | 25.8868 | 25.8698 | 25.8698 | 25.8698 | 25.8698 | 25.8698 | 25.8698 | 25.8698 | 22.562 | 21.4989 | 20.4552 | 26.4893 | 26.4619 | 26.4285 | 26.4187 | 26.4187 | 26.4187 | 26.4187 | 26.4187 | 26.4187 | 26.4187 | 26.4187 | 22.9368 | 21.8733 | 20.8294
|  | RUTHRIESTON | ST |  |  |  | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 26.2294 | 26.1904 | 26.13 | 26.058 | 25.999 | 25.9411 | 25.902 | 25.8855 | 25.8766 | 25.8698 | 25.8698 | 25.8698 | 25.8698 | 25.8698 | 26.4971 | 26.4871 | 26.4717 | 26.4533 | 26.4383 | 26.4235 | 26.4187 | 26.4187 | 26.4187 | 26.4187 | 26.4187 | 26.4187 | 26.4187 | 26.4187
|  | RUTHRIESTON | FS |  |  |  | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 29.761 | 26.2521 | 26.2491 | 26.2336 | 26.2153 | 26.1969 | 26.1787 | 26.1555 | 26.1326 | 26.1102 | 26.0882 | 26.0667 | 25.9627 | 25.8907 | 25.8754 | 26.5029 | 26.5021 | 26.4982 | 26.4935 | 26.4888 | 26.4841 | 26.4782 | 26.4724 | 26.4666 | 26.461 | 26.4556 | 26.429 | 26.4187 | 26.4187
| FORT WILLIAM | SALEN | MINIMUM HEADROOM | NM 69002 65519 | NO | YES | 7.6187 | 7.6159 | 7.6132 | 7.6106 | 7.6081 | 7.6056 | 7.6032 | 7.6006 | 7.6004 | 7.6004 | 7.6004 | 7.6004 | 7.6004 | 6.2924 | 7.4864 | 7.4792 | 7.4725 | 7.4659 | 7.4596 | 7.4534 | 7.4473 | 7.4407 | 7.4342 | 7.4277 | 7.4213 | 7.3653 | 6.2555 | 6.0404 | 7.3631 | 7.3565 | 7.3502 | 7.3442 | 7.3384 | 7.3326 | 7.327 | 7.321 | 7.3149 | 7.309 | 7.3031 | 7.2515 | 6.2309 | 6.0164
|  | SALEN | CT |  |  |  | 7.6191 | 7.6169 | 7.6151 | 7.6132 | 7.6112 | 7.6092 | 7.6073 | 7.6054 | 7.6035 | 7.6017 | 7.6004 | 7.6004 | 7.6004 | 7.6004 | 7.4874 | 7.4819 | 7.4773 | 7.4725 | 7.4675 | 7.4623 | 7.4576 | 7.4527 | 7.448 | 7.4435 | 7.439 | 7.3967 | 7.3585 | 6.2674 | 7.364 | 7.3589 | 7.3547 | 7.3503 | 7.3457 | 7.3409 | 7.3365 | 7.332 | 7.3277 | 7.3236 | 7.3194 | 7.2804 | 7.2442 | 6.2427
|  | SALEN | LW |  |  |  | 7.6187 | 7.6159 | 7.6132 | 7.6106 | 7.6081 | 7.6056 | 7.6032 | 7.6006 | 7.6004 | 7.6004 | 7.6004 | 7.6004 | 7.6004 | 6.2924 | 7.4864 | 7.4792 | 7.4725 | 7.4659 | 7.4596 | 7.4534 | 7.4473 | 7.4407 | 7.4342 | 7.4277 | 7.4213 | 7.3653 | 6.2555 | 6.0404 | 7.3631 | 7.3565 | 7.3502 | 7.3442 | 7.3384 | 7.3326 | 7.327 | 7.321 | 7.3149 | 7.309 | 7.3031 | 7.2515 | 6.2309 | 6.0164
|  | SALEN | ST |  |  |  | 7.6206 | 7.6195 | 7.6185 | 7.6173 | 7.615 | 7.6127 | 7.6106 | 7.6083 | 7.6062 | 7.6041 | 7.602 | 7.6004 | 7.6004 | 7.6004 | 7.4911 | 7.4885 | 7.486 | 7.4828 | 7.4771 | 7.4714 | 7.4659 | 7.4602 | 7.4548 | 7.4495 | 7.4443 | 7.419 | 7.394 | 7.3691 | 7.3675 | 7.365 | 7.3627 | 7.3598 | 7.3546 | 7.3492 | 7.3442 | 7.339 | 7.3339 | 7.3291 | 7.3243 | 7.3009 | 7.2779 | 7.255
|  | SALEN | FS |  |  |  | 7.6218 | 7.6215 | 7.6211 | 7.6207 | 7.62 | 7.6192 | 7.6183 | 7.6174 | 7.6165 | 7.6157 | 7.6148 | 7.611 | 7.6073 | 7.604 | 7.4942 | 7.4934 | 7.4925 | 7.4915 | 7.4896 | 7.4878 | 7.4854 | 7.4831 | 7.4809 | 7.4787 | 7.4766 | 7.4668 | 7.4577 | 7.4492 | 7.3703 | 7.3695 | 7.3687 | 7.3678 | 7.366 | 7.3643 | 7.3622 | 7.3601 | 7.358 | 7.356 | 7.3541 | 7.345 | 7.3366 | 7.3288
| TAYNUILT | SALEN 2 | MINIMUM HEADROOM | NM 57252 42849 | YES | YES | 3.6798 | 3.6798 | 3.6798 | 3.6798 | 3.6798 | 3.6798 | 3.6798 | 3.6798 | 3.6798 | 3.6798 | 3.6798 | 3.3968 | 2.4573 | 2.3224 | 4.2293 | 4.2293 | 4.2293 | 4.2293 | 4.2293 | 4.2293 | 4.2293 | 4.2293 | 4.2293 | 4.2293 | 4.2293 | 4.0684 | 4.0684 | 4.0684 | 3.4884 | 3.4877 | 3.4868 | 3.4859 | 3.4851 | 3.4843 | 3.4834 | 3.4825 | 3.4812 | 3.4799 | 3.4786 | 2.4202 | 2.2546 | 2.0919
|  | SALEN 2 | CT |  |  |  | 3.6798 | 3.6798 | 3.6798 | 3.6798 | 3.6798 | 3.6798 | 3.6798 | 3.6798 | 3.6798 | 3.6798 | 3.6798 | 3.3968 | 3.3968 | 2.4327 | 4.2293 | 4.2293 | 4.2293 | 4.2293 | 4.2293 | 4.2293 | 4.2293 | 4.2293 | 4.2293 | 4.2293 | 4.2293 | 4.0684 | 4.0684 | 4.0684 | 3.4884 | 3.4879 | 3.4872 | 3.4866 | 3.486 | 3.4854 | 3.4848 | 3.4842 | 3.4836 | 3.483 | 3.4823 | 2.4822 | 2.3525 | 2.2249
|  | SALEN 2 | LW |  |  |  | 3.6798 | 3.6798 | 3.6798 | 3.6798 | 3.6798 | 3.6798 | 3.6798 | 3.6798 | 3.6798 | 3.6798 | 3.6798 | 3.3968 | 2.4573 | 2.3224 | 4.2293 | 4.2293 | 4.2293 | 4.2293 | 4.2293 | 4.2293 | 4.2293 | 4.2293 | 4.2293 | 4.2293 | 4.2293 | 4.0684 | 4.0684 | 4.0684 | 3.4884 | 3.4877 | 3.4868 | 3.4859 | 3.4851 | 3.4843 | 3.4834 | 3.4826 | 3.4817 | 3.4808 | 3.48 | 2.4202 | 2.2546 | 2.0919
|  | SALEN 2 | ST |  |  |  | 3.6798 | 3.6798 | 3.6798 | 3.6798 | 3.6798 | 3.6798 | 3.6798 | 3.6798 | 3.6798 | 3.6798 | 3.6798 | 3.5383 | 3.5383 | 3.5383 | 4.2293 | 4.2293 | 4.2293 | 4.2293 | 4.2293 | 4.2293 | 4.2293 | 4.2293 | 4.2293 | 4.2293 | 4.2293 | 4.1488 | 4.1488 | 4.1488 | 3.4886 | 3.4884 | 3.4881 | 3.4877 | 3.4864 | 3.4851 | 3.4839 | 3.4825 | 3.4812 | 3.4799 | 3.4786 | 3.331 | 3.3248 | 3.3187
|  | SALEN 2 | FS |  |  |  | 3.6798 | 3.6798 | 3.6798 | 3.6798 | 3.6798 | 3.6798 | 3.6798 | 3.6798 | 3.6798 | 3.6798 | 3.6798 | 3.6798 | 3.6798 | 3.6798 | 4.2293 | 4.2293 | 4.2293 | 4.2293 | 4.2293 | 4.2293 | 4.2293 | 4.2293 | 4.2293 | 4.2293 | 4.2293 | 4.2293 | 4.2293 | 4.2293 | 3.4888 | 3.4887 | 3.4886 | 3.4885 | 3.4881 | 3.4877 | 3.4871 | 3.4866 | 3.4861 | 3.4856 | 3.4851 | 3.4827 | 3.4804 | 3.4783
| THURSO | SANDAY | MINIMUM HEADROOM | HY 61184 35797 | YES | YES | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 0.98689 | 0.92191 | 0.85783 | 1.2475 | 1.2329 | 1.2301 | 1.2301 | 1.2301 | 0.99328 | 0.95467 | 0.91268 | 0.87103 | 0.8297 | 0.78851 | 0.71299 | 0.63669 | 0.56146 | 1.2861 | 1.2861 | 1.2861 | 1.2861 | 1.2861 | 1.2861 | 1.2861 | 0.96194 | 0.92137 | 0.88041 | 0.8392 | 0.76366 | 0.68734 | 0.61208
|  | SANDAY | CT |  |  |  | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 0.98689 | 0.92191 | 0.85783 | 1.2475 | 1.2329 | 1.2301 | 1.2301 | 1.2301 | 0.99328 | 0.95467 | 0.91268 | 0.87103 | 0.8297 | 0.78851 | 0.71299 | 0.63669 | 0.56146 | 1.2861 | 1.2861 | 1.2861 | 1.2861 | 1.2861 | 1.2861 | 1.2861 | 0.96194 | 0.92137 | 0.88041 | 0.8392 | 0.76366 | 0.68734 | 0.61208
|  | SANDAY | LW |  |  |  | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 0.99187 | 0.91838 | 1.2519 | 1.2397 | 1.2318 | 1.2301 | 1.2301 | 1.2301 | 1.2301 | 0.9878 | 0.95583 | 0.92411 | 0.89247 | 0.80611 | 0.71883 | 0.63255 | 1.288 | 1.2861 | 1.2861 | 1.2861 | 1.2861 | 1.2861 | 1.2861 | 1.2861 | 1.2861 | 0.97307 | 0.94225 | 0.85681 | 0.7695 | 0.68319
|  | SANDAY | ST |  |  |  | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 1.2581 | 1.2575 | 1.2565 | 1.2553 | 1.2515 | 1.2477 | 1.2441 | 1.2405 | 1.2376 | 1.2347 | 1.2327 | 1.2301 | 1.2301 | 1.2301 | 1.291 | 1.2907 | 1.2902 | 1.2897 | 1.2878 | 1.2861 | 1.2861 | 1.2861 | 1.2861 | 1.2861 | 1.2861 | 1.2861 | 1.2861 | 1.2861
|  | SANDAY | FS |  |  |  | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 1.4712 | 1.2585 | 1.2584 | 1.2581 | 1.2578 | 1.2565 | 1.2553 | 1.2537 | 1.2521 | 1.2505 | 1.249 | 1.2475 | 1.2407 | 1.2356 | 1.2325 | 1.2912 | 1.2912 | 1.291 | 1.2909 | 1.2903 | 1.2896 | 1.2889 | 1.2881 | 1.2874 | 1.2866 | 1.2861 | 1.2861 | 1.2861 | 1.2861
| DUNOON | SANDBANK | MINIMUM HEADROOM | NS 15274 81386 | NO | YES | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 7.7223 | 7.6657 | 7.3121 | 6.9551 | 6.6037 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 7.3419 | 7.2746 | 7.2078 | 7.1414 | 7.0754 | 6.6629 | 6.2466 | 5.8367 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.203 | 7.1387 | 6.7365 | 6.3306 | 5.9311
|  | SANDBANK | CT |  |  |  | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 7.6915 | 7.4132 | 7.1393 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 7.1055 | 6.7808 | 6.4614 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.168 | 6.8515 | 6.5401
|  | SANDBANK | LW |  |  |  | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 7.7223 | 7.6657 | 7.3121 | 6.9551 | 6.6037 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 7.3419 | 7.2746 | 7.2078 | 7.1414 | 7.0754 | 6.6629 | 6.2466 | 5.8367 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.203 | 7.1387 | 6.7365 | 6.3306 | 5.9311
|  | SANDBANK | ST |  |  |  | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 7.6541 | 7.5124 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 7.228 | 7.0619 | 6.8966 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.1255 | 6.9643
|  | SANDBANK | FS |  |  |  | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.8297 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 8.1598 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449 | 7.2449
| SHETLAND | SANDWICK | MINIMUM HEADROOM | HU4308625957 | YES | YES | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8
|  | SANDWICK | CT |  |  |  | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8
|  | SANDWICK | LW |  |  |  | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8
|  | SANDWICK | ST |  |  |  | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8
|  | SANDWICK | FS |  |  |  | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8
| SHETLAND | SCALLOWAY | MINIMUM HEADROOM | HU4139939639 | YES | YES | 4.1413 | 4.1303 | 4.1167 | 4.1033 | 4.0902 | 4.0773 | 4.0647 | 4.051 | 4.0376 | 4.0242 | 4.0108 | 3.9898 | 3.9898 | 3.9898 | 3.0535 | 2.9711 | 2.8696 | 2.7693 | 2.6939 | 2.6859 | 2.678 | 2.6695 | 2.6611 | 2.6528 | 2.6445 | 0.79449 | 0.44964 | 0.10707 | 3.0615 | 3.0309 | 2.9932 | 2.956 | 2.9199 | 2.8842 | 2.8561 | 2.8342 | 2.8336 | 2.8336 | 0.97337 | 0.65655 | 0.32079 | -0.0093733
|  | SCALLOWAY | CT |  |  |  | 4.1425 | 4.1352 | 4.1268 | 4.1184 | 4.1103 | 4.1023 | 4.0945 | 4.086 | 4.0777 | 4.0694 | 4.0611 | 4.0413 | 4.0213 | 4.0016 | 3.0627 | 3.008 | 2.9449 | 2.8825 | 2.8221 | 2.7623 | 2.7035 | 2.6913 | 2.6861 | 2.6809 | 2.6758 | 2.6634 | 2.651 | 2.6387 | 3.0649 | 3.0446 | 3.0212 | 2.998 | 2.9756 | 2.9534 | 2.9316 | 2.9081 | 2.885 | 2.8636 | 2.8504 | 2.8336 | 2.8336 | 0.86875
|  | SCALLOWAY | LW |  |  |  | 4.1413 | 4.1303 | 4.1167 | 4.1033 | 4.0902 | 4.0773 | 4.0647 | 4.051 | 4.0376 | 4.0242 | 4.0108 | 3.9898 | 3.9898 | 3.9898 | 3.0535 | 2.9711 | 2.8696 | 2.7693 | 2.6939 | 2.6859 | 2.678 | 2.6695 | 2.6611 | 2.6528 | 2.6445 | 0.79449 | 0.44964 | 0.10707 | 3.0615 | 3.0309 | 2.9932 | 2.956 | 2.9199 | 2.8842 | 2.8561 | 2.8342 | 2.8336 | 2.8336 | 0.97337 | 0.65655 | 0.32079 | -0.0093733
|  | SCALLOWAY | ST |  |  |  | 4.1448 | 4.1415 | 4.1363 | 4.13 | 4.1274 | 4.1248 | 4.1223 | 4.1195 | 4.1169 | 4.1143 | 4.1118 | 4.0993 | 4.087 | 4.0747 | 3.08 | 3.0552 | 3.0163 | 2.9695 | 2.95 | 2.9305 | 2.9114 | 2.891 | 2.8714 | 2.8521 | 2.8331 | 2.74 | 2.6919 | 2.6842 | 3.0713 | 3.0621 | 3.0477 | 3.0303 | 3.0231 | 3.0158 | 3.0087 | 3.0012 | 2.9939 | 2.9867 | 2.9797 | 2.9451 | 2.9109 | 2.8768
|  | SCALLOWAY | FS |  |  |  | 4.1467 | 4.1465 | 4.145 | 4.1432 | 4.1423 | 4.1415 | 4.1404 | 4.1393 | 4.1383 | 4.1373 | 4.1363 | 4.1316 | 4.1272 | 4.123 | 3.094 | 3.0921 | 3.081 | 3.0677 | 3.0613 | 3.0549 | 3.0468 | 3.0388 | 3.0311 | 3.0236 | 3.0162 | 2.981 | 2.948 | 2.917 | 3.0765 | 3.0758 | 3.0717 | 3.0668 | 3.0644 | 3.062 | 3.059 | 3.056 | 3.0532 | 3.0504 | 3.0477 | 3.0346 | 3.0223 | 3.0108
| TAYNUILT | SCAMMADALE | MINIMUM HEADROOM | NM 84207 19638 | YES | YES | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.13799 | 0.13785 | 0.13768 | 0.13752 | 0.13736 | 0.13714 | 0.13696 | 0.13676 | 0.13657 | 0.13638 | 0.1362 | 0.13532 | 0.13532 | 0.13532 | 0.14401 | 0.14394 | 0.1439 | 0.14387 | 0.14384 | 0.1438 | 0.14374 | 0.14367 | 0.14361 | 0.14354 | 0.14348 | 0.14296 | 0.14296 | 0.14296
|  | SCAMMADALE | CT |  |  |  | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.138 | 0.1379 | 0.13778 | 0.13766 | 0.13755 | 0.13744 | 0.13733 | 0.13721 | 0.13712 | 0.13706 | 0.137 | 0.13562 | 0.13532 | 0.13532 | 0.14402 | 0.14396 | 0.14392 | 0.1439 | 0.14388 | 0.14386 | 0.14384 | 0.14382 | 0.1438 | 0.14378 | 0.14375 | 0.14328 | 0.14296 | 0.14296
|  | SCAMMADALE | LW |  |  |  | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.13799 | 0.13785 | 0.13768 | 0.13752 | 0.13736 | 0.1372 | 0.13709 | 0.13701 | 0.13692 | 0.13683 | 0.13674 | 0.13532 | 0.13532 | 0.13532 | 0.14401 | 0.14394 | 0.1439 | 0.14387 | 0.14384 | 0.14382 | 0.14379 | 0.14376 | 0.14373 | 0.1437 | 0.14367 | 0.14296 | 0.14296 | 0.14296
|  | SCAMMADALE | ST |  |  |  | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.13804 | 0.13799 | 0.13793 | 0.13785 | 0.13749 | 0.13714 | 0.13696 | 0.13676 | 0.13657 | 0.13638 | 0.1362 | 0.13532 | 0.13532 | 0.13532 | 0.14403 | 0.14401 | 0.14398 | 0.14394 | 0.14387 | 0.1438 | 0.14374 | 0.14367 | 0.14361 | 0.14354 | 0.14348 | 0.14316 | 0.14296 | 0.14296
|  | SCAMMADALE | FS |  |  |  | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.16783 | 0.13806 | 0.13806 | 0.13804 | 0.13802 | 0.1379 | 0.13778 | 0.13764 | 0.13749 | 0.13735 | 0.13721 | 0.13711 | 0.13676 | 0.13644 | 0.13613 | 0.14404 | 0.14404 | 0.14403 | 0.14402 | 0.14397 | 0.14392 | 0.1439 | 0.14387 | 0.14384 | 0.14382 | 0.14379 | 0.14367 | 0.14356 | 0.14345
| ABERNETHY | SCONE | MINIMUM HEADROOM | NO 14401 25495 | NO | YES | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 13.6927 | 12.9949 | 12.3622 | 15.9994 | 15.8976 | 15.8323 | 15.7935 | 15.7888 | 15.7888 | 15.7888 | 13.5977 | 13.3325 | 13.0615 | 12.7867 | 11.7401 | 10.9024 | 10.143 | 16.0569 | 16.0297 | 16.0297 | 16.0297 | 16.0297 | 16.0297 | 13.7705 | 13.4925 | 13.2139 | 12.9291 | 12.6404 | 11.5652 | 10.724 | 9.9613
|  | SCONE | CT |  |  |  | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 14.23 | 13.7809 | 16.0119 | 15.9311 | 15.8749 | 15.8308 | 15.8001 | 15.7888 | 15.7888 | 15.7888 | 15.7888 | 13.7605 | 13.5635 | 12.9231 | 12.3799 | 11.8459 | 16.0601 | 16.0382 | 16.0297 | 16.0297 | 16.0297 | 16.0297 | 16.0297 | 16.0297 | 16.0297 | 13.6635 | 13.4565 | 12.7837 | 12.213 | 11.6715
|  | SCONE | LW |  |  |  | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 13.6927 | 12.9949 | 12.3622 | 15.9994 | 15.8976 | 15.8323 | 15.7935 | 15.7888 | 15.7888 | 15.7888 | 13.5977 | 13.3325 | 13.0615 | 12.7867 | 11.7401 | 10.9024 | 10.143 | 16.0569 | 16.0297 | 16.0297 | 16.0297 | 16.0297 | 16.0297 | 13.7705 | 13.4925 | 13.2139 | 12.9291 | 12.6404 | 11.5652 | 10.724 | 9.9613
|  | SCONE | ST |  |  |  | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 16.0424 | 16.0044 | 15.9469 | 15.8965 | 15.8731 | 15.8498 | 15.8259 | 15.8048 | 15.7954 | 15.7888 | 15.7888 | 15.7888 | 13.6455 | 13.3245 | 16.0679 | 16.0582 | 16.0432 | 16.0297 | 16.0297 | 16.0297 | 16.0297 | 16.0297 | 16.0297 | 16.0297 | 16.0297 | 16.0297 | 13.5427 | 13.2054
|  | SCONE | FS |  |  |  | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 18.0546 | 16.0643 | 16.0584 | 16.0386 | 16.0156 | 15.996 | 15.9765 | 15.9527 | 15.9329 | 15.9129 | 15.8978 | 15.8866 | 15.8301 | 15.8004 | 15.7891 | 16.0735 | 16.072 | 16.0669 | 16.0611 | 16.0561 | 16.0511 | 16.045 | 16.0388 | 16.0324 | 16.0297 | 16.0297 | 16.0297 | 16.0297 | 16.0297
| THURSO | SHAPINSAY | MINIMUM HEADROOM | HY 48313 17148 | YES | YES | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 0.1741 | 0.15349 | 1.1616 | 1.1616 | 1.1616 | 1.1616 | 1.1616 | 1.1616 | 1.1616 | 1.1616 | 1.1616 | 1.1616 | 1.1616 | 0.99548 | 0.29957 | 0.26697 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 0.20942 | 0.17943
|  | SHAPINSAY | CT |  |  |  | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 0.17574 | 0.15382 | 1.1616 | 1.1616 | 1.1616 | 1.1616 | 1.1616 | 1.1616 | 1.1616 | 1.1616 | 1.1616 | 1.1616 | 1.1616 | 1.1616 | 0.30217 | 0.26748 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 0.21181 | 0.1799
|  | SHAPINSAY | LW |  |  |  | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 0.1741 | 0.15349 | 1.1616 | 1.1616 | 1.1616 | 1.1616 | 1.1616 | 1.1616 | 1.1616 | 1.1616 | 1.1616 | 1.1616 | 1.1616 | 0.99548 | 0.29957 | 0.26697 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 0.20942 | 0.17943
|  | SHAPINSAY | ST |  |  |  | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 0.6134 | 0.60451 | 1.1616 | 1.1616 | 1.1616 | 1.1616 | 1.1616 | 1.1616 | 1.1616 | 1.1616 | 1.1616 | 1.1616 | 1.1616 | 1.1616 | 0.66902 | 0.65496 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 0.66014 | 0.64721
|  | SHAPINSAY | FS |  |  |  | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1895 | 1.1616 | 1.1616 | 1.1616 | 1.1616 | 1.1616 | 1.1616 | 1.1616 | 1.1616 | 1.1616 | 1.1616 | 1.1616 | 1.1616 | 1.1616 | 1.1616 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 1.2857 | 1.2857
| BROADFORD | SHIELDAIG | MINIMUM HEADROOM | NG 81637 52250 | YES | YES | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 0.97916 | 0.90188 | 1.2925 | 1.2913 | 1.2898 | 1.2887 | 1.2887 | 1.2887 | 1.2887 | 1.2887 | 1.2887 | 1.2887 | 1.2887 | 1.2887 | 0.95605 | 0.87111 | 1.3069 | 1.3066 | 1.3063 | 1.3059 | 1.3056 | 1.3052 | 1.3049 | 1.3044 | 1.3039 | 1.3033 | 1.3028 | 1.2976 | 0.92115 | 0.82995
|  | SHIELDAIG | CT |  |  |  | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 0.95195 | 1.2925 | 1.2916 | 1.2906 | 1.2896 | 1.2887 | 1.2887 | 1.2887 | 1.2887 | 1.2887 | 1.2887 | 1.2887 | 1.2887 | 0.99784 | 0.92614 | 1.3069 | 1.3067 | 1.3065 | 1.3062 | 1.306 | 1.3057 | 1.3055 | 1.3052 | 1.305 | 1.3047 | 1.3045 | 1.2996 | 0.96603 | 0.88904
|  | SHIELDAIG | LW |  |  |  | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 0.97916 | 0.90188 | 1.2925 | 1.2913 | 1.2898 | 1.2887 | 1.2887 | 1.2887 | 1.2887 | 1.2887 | 1.2887 | 1.2887 | 1.2887 | 1.2887 | 0.95605 | 0.87111 | 1.3069 | 1.3066 | 1.3063 | 1.3059 | 1.3056 | 1.3052 | 1.3049 | 1.3045 | 1.3042 | 1.3038 | 1.3035 | 1.2976 | 0.92115 | 0.82995
|  | SHIELDAIG | ST |  |  |  | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.2929 | 1.2925 | 1.2919 | 1.2913 | 1.289 | 1.2887 | 1.2887 | 1.2887 | 1.2887 | 1.2887 | 1.2887 | 1.2887 | 1.2887 | 1.2887 | 1.307 | 1.3069 | 1.3068 | 1.3066 | 1.3061 | 1.3055 | 1.305 | 1.3044 | 1.3039 | 1.3033 | 1.3028 | 1.3002 | 1.2976 | 0.97354
|  | SHIELDAIG | FS |  |  |  | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.3952 | 1.2931 | 1.293 | 1.2929 | 1.2927 | 1.292 | 1.2913 | 1.2904 | 1.2895 | 1.2887 | 1.2887 | 1.2887 | 1.2887 | 1.2887 | 1.2887 | 1.3071 | 1.307 | 1.307 | 1.307 | 1.3068 | 1.3066 | 1.3064 | 1.3062 | 1.3059 | 1.3057 | 1.3055 | 1.3045 | 1.3036 | 1.3027
| SHIN | SHIN | MINIMUM HEADROOM | NH 57246 97463 | YES | YES | 2.7721 | 2.772 | 2.7718 | 2.7716 | 2.7714 | 2.7708 | 2.7702 | 2.7696 | 2.769 | 2.7684 | 2.7678 | 2.7634 | 2.4644 | 2.3965 | 2.6818 | 2.6815 | 2.6811 | 2.6807 | 2.6803 | 2.6791 | 2.678 | 2.6767 | 2.6755 | 2.6743 | 2.6731 | 2.4535 | 2.3675 | 2.2833 | 2.6905 | 2.6905 | 2.6905 | 2.6905 | 2.6905 | 2.6905 | 2.6905 | 2.6905 | 2.6905 | 2.6905 | 2.6905 | 2.4642 | 2.3794 | 2.2963
|  | SHIN | CT |  |  |  | 2.7722 | 2.772 | 2.7719 | 2.7718 | 2.7716 | 2.7715 | 2.7714 | 2.7712 | 2.7711 | 2.7709 | 2.7708 | 2.7657 | 2.7605 | 2.4537 | 2.6819 | 2.6816 | 2.6814 | 2.6811 | 2.6808 | 2.6805 | 2.6803 | 2.68 | 2.6797 | 2.6794 | 2.6791 | 2.482 | 2.4174 | 2.3539 | 2.6905 | 2.6905 | 2.6905 | 2.6905 | 2.6905 | 2.6905 | 2.6905 | 2.6905 | 2.6905 | 2.6905 | 2.6905 | 2.4923 | 2.4286 | 2.366
|  | SHIN | LW |  |  |  | 2.7721 | 2.772 | 2.7718 | 2.7716 | 2.7714 | 2.7712 | 2.771 | 2.7708 | 2.7706 | 2.7704 | 2.7702 | 2.7634 | 2.4644 | 2.3965 | 2.6818 | 2.6815 | 2.6811 | 2.6807 | 2.6803 | 2.68 | 2.6796 | 2.6791 | 2.6787 | 2.6783 | 2.6779 | 2.4535 | 2.3675 | 2.2833 | 2.6905 | 2.6905 | 2.6905 | 2.6905 | 2.6905 | 2.6905 | 2.6905 | 2.6905 | 2.6905 | 2.6905 | 2.6905 | 2.4642 | 2.3794 | 2.2963
|  | SHIN | ST |  |  |  | 2.7722 | 2.7721 | 2.7721 | 2.772 | 2.7714 | 2.7708 | 2.7702 | 2.7696 | 2.769 | 2.7684 | 2.7678 | 2.7649 | 2.7619 | 2.4893 | 2.6819 | 2.6818 | 2.6817 | 2.6815 | 2.6803 | 2.6791 | 2.678 | 2.6767 | 2.6755 | 2.6743 | 2.6731 | 2.4716 | 2.4351 | 2.3989 | 2.6905 | 2.6905 | 2.6905 | 2.6905 | 2.6905 | 2.6905 | 2.6905 | 2.6905 | 2.6905 | 2.6905 | 2.6905 | 2.482 | 2.4461 | 2.4104
|  | SHIN | FS |  |  |  | 2.7722 | 2.7722 | 2.7722 | 2.7722 | 2.772 | 2.7718 | 2.7715 | 2.7713 | 2.771 | 2.7708 | 2.7706 | 2.7695 | 2.7684 | 2.7674 | 2.682 | 2.682 | 2.6819 | 2.6819 | 2.6815 | 2.6811 | 2.6806 | 2.6801 | 2.6796 | 2.6792 | 2.6787 | 2.6765 | 2.6744 | 2.6723 | 2.6905 | 2.6905 | 2.6905 | 2.6905 | 2.6905 | 2.6905 | 2.6905 | 2.6905 | 2.6905 | 2.6905 | 2.6905 | 2.6905 | 2.6905 | 2.6905
| FORT WILLIAM | SHONA BEG | MINIMUM HEADROOM | NM 67173 74363 | YES | YES | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138
|  | SHONA BEG | CT |  |  |  | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138
|  | SHONA BEG | LW |  |  |  | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138
|  | SHONA BEG | ST |  |  |  | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138
|  | SHONA BEG | FS |  |  |  | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.12126 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.11193 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138 | 0.1138
| KINTORE | SKENE | MINIMUM HEADROOM | NJ 82203 06495 | NO | YES | 38.4527 | 38.3665 | 38.2603 | 38.1551 | 38.051 | 37.9477 | 37.8461 | 37.7363 | 37.6281 | 37.5195 | 37.4368 | 37.0578 | 28.0269 | 26.6452 | 34.2276 | 33.955 | 33.6192 | 33.5167 | 33.4569 | 33.3975 | 33.3391 | 33.2976 | 27.1424 | 26.4672 | 25.7971 | 23.8591 | 22.1984 | 20.5684 | 33.6875 | 33.6376 | 33.576 | 33.5453 | 33.5453 | 33.5453 | 33.5453 | 33.5453 | 27.3847 | 26.6977 | 26.016 | 23.9702 | 22.3016 | 20.671
|  | SKENE | CT |  |  |  | 38.4666 | 38.4162 | 38.3581 | 38.3001 | 38.2426 | 38.1852 | 38.1287 | 38.0678 | 38.008 | 37.9477 | 37.8879 | 37.3619 | 37.1894 | 37.0578 | 34.2717 | 34.1123 | 33.9283 | 33.7452 | 33.567 | 33.534 | 33.5015 | 33.4665 | 33.4321 | 33.3975 | 33.3631 | 27.3598 | 26.2871 | 25.2409 | 33.6994 | 33.6664 | 33.6327 | 33.5991 | 33.5657 | 33.5453 | 33.5453 | 33.5453 | 33.5453 | 33.5453 | 33.5453 | 27.5408 | 26.4503 | 25.3857
|  | SKENE | LW |  |  |  | 38.4527 | 38.3665 | 38.2603 | 38.1551 | 38.051 | 37.9477 | 37.8461 | 37.7363 | 37.6281 | 37.5195 | 37.4368 | 37.0578 | 28.0269 | 26.6452 | 34.2276 | 33.955 | 33.6192 | 33.5167 | 33.4569 | 33.3975 | 33.3391 | 33.2976 | 27.1424 | 26.4672 | 25.7971 | 23.8591 | 22.1984 | 20.5684 | 33.6875 | 33.6376 | 33.576 | 33.5453 | 33.5453 | 33.5453 | 33.5453 | 33.5453 | 27.3847 | 26.6977 | 26.016 | 23.9702 | 22.3016 | 20.671
|  | SKENE | ST |  |  |  | 38.479 | 38.4508 | 38.4067 | 38.3538 | 38.3293 | 38.3047 | 38.2806 | 38.2546 | 38.2294 | 38.204 | 38.179 | 37.8798 | 37.7602 | 37.6431 | 34.3108 | 34.2215 | 34.0823 | 33.9147 | 33.8372 | 33.7595 | 33.6833 | 33.6011 | 33.5594 | 33.5448 | 33.5304 | 33.3415 | 33.2727 | 33.2101 | 33.7117 | 33.6864 | 33.6609 | 33.6302 | 33.616 | 33.6017 | 33.5878 | 33.5727 | 33.5581 | 33.5453 | 33.5453 | 33.3507 | 33.3507 | 33.3507
|  | SKENE | FS |  |  |  | 38.495 | 38.4928 | 38.4808 | 38.4666 | 38.4586 | 38.4506 | 38.4405 | 38.4306 | 38.421 | 38.4114 | 38.4019 | 38.3562 | 38.3128 | 38.2718 | 34.3614 | 34.3544 | 34.3166 | 34.2715 | 34.2462 | 34.2208 | 34.1892 | 34.1578 | 34.1274 | 34.0969 | 34.067 | 33.9223 | 33.7851 | 33.6554 | 33.7277 | 33.7254 | 33.7135 | 33.6993 | 33.6914 | 33.6863 | 33.6805 | 33.6747 | 33.6691 | 33.6636 | 33.6581 | 33.6316 | 33.6064 | 33.5827
| BROADFORD | SKULAMUS | MINIMUM HEADROOM | NG 65881 22438 | YES | YES | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.4325 | 2.4197 | 2.413 | 2.4065 | 2.4 | 2.392 | 2.3836 | 2.3746 | 2.3653 | 2.3557 | 2.3462 | 2.3025 | 2.2788 | 0.91785 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 0.84051
|  | SKULAMUS | CT |  |  |  | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.4336 | 2.4223 | 2.4171 | 2.4118 | 2.4057 | 2.3967 | 2.3875 | 2.3789 | 2.3703 | 2.3629 | 2.3577 | 2.3091 | 2.2911 | 2.2734 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296
|  | SKULAMUS | LW |  |  |  | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.4325 | 2.4197 | 2.413 | 2.4065 | 2.4 | 2.392 | 2.3836 | 2.3746 | 2.3653 | 2.3574 | 2.352 | 2.3025 | 2.2788 | 0.91785 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 0.84051
|  | SKULAMUS | ST |  |  |  | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.4371 | 2.4309 | 2.4283 | 2.4253 | 2.4151 | 2.4031 | 2.3911 | 2.3789 | 2.3668 | 2.3557 | 2.3462 | 2.3138 | 2.3034 | 2.2932 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296
|  | SKULAMUS | FS |  |  |  | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.7516 | 2.4398 | 2.4369 | 2.4358 | 2.4345 | 2.4308 | 2.4269 | 2.4221 | 2.4173 | 2.4125 | 2.4079 | 2.404 | 2.3865 | 2.3709 | 2.3563 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296 | 2.3296
| WOODHILL | SPRINGHILL | MINIMUM HEADROOM | NJ 89850 06421 | NO | NO | 30.7923 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 28.3196 | 31.7877 | 31.6521 | 31.5174 | 31.3887 | 31.2805 | 31.2134 | 31.1755 | 31.1376 | 31.0995 | 31.0582 | 30.9325 | 30.8521 | 30.7763 | 28.6868 | 32.2382 | 32.2036 | 32.1692 | 32.135 | 32.1009 | 32.0669 | 32.0302 | 31.9936 | 31.9567 | 31.9166 | 31.8536 | 31.8536 | 31.8536
|  | SPRINGHILL | CT |  |  |  | 30.7923 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 28.347 | 31.8726 | 31.8113 | 31.7485 | 31.6845 | 31.6211 | 31.5565 | 31.4861 | 31.4148 | 31.3548 | 31.295 | 31.1413 | 31.0358 | 30.953 | 28.6938 | 32.2599 | 32.2443 | 32.2282 | 32.2119 | 32.1957 | 32.1792 | 32.1612 | 32.143 | 32.1243 | 32.1055 | 31.9971 | 31.895 | 31.8536
|  | SPRINGHILL | LW |  |  |  | 30.7923 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 28.3196 | 31.7877 | 31.6521 | 31.5174 | 31.3887 | 31.2805 | 31.2134 | 31.1755 | 31.1376 | 31.0995 | 31.0582 | 30.9325 | 30.8521 | 30.7763 | 28.6868 | 32.2382 | 32.2036 | 32.1692 | 32.135 | 32.1009 | 32.0669 | 32.0302 | 31.9936 | 31.9567 | 31.9166 | 31.8536 | 31.8536 | 31.8536
|  | SPRINGHILL | ST |  |  |  | 30.7923 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 28.3708 | 31.9151 | 31.8623 | 31.7986 | 31.7507 | 31.7034 | 31.6555 | 31.6032 | 31.5503 | 31.4962 | 31.4418 | 31.2281 | 31.1641 | 31.1037 | 28.6999 | 32.2708 | 32.2573 | 32.241 | 32.2288 | 32.2167 | 32.2045 | 32.1911 | 32.1776 | 32.1638 | 32.1499 | 32.0812 | 32.0192 | 31.9607
|  | SPRINGHILL | FS |  |  |  | 30.7923 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 33.3223 | 28.4015 | 31.9756 | 31.9577 | 31.9377 | 31.9208 | 31.9038 | 31.8828 | 31.8616 | 31.8406 | 31.8194 | 31.7983 | 31.6924 | 31.5948 | 31.5062 | 28.7077 | 32.2862 | 32.2817 | 32.2765 | 32.2722 | 32.2679 | 32.2625 | 32.2571 | 32.2517 | 32.2463 | 32.2409 | 32.2139 | 32.189 | 32.1663
| BRIDGE OF DUN | ST CYRUS | MINIMUM HEADROOM | NO 74889 65577 | NO | YES | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 5.8143 | 2.0858 | 1.8406 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.7986 | 5.3124 | 2.5702 | 2.2667 | 5.536 | 5.4916 | 5.4361 | 5.3803 | 5.3244 | 5.2685 | 5.2134 | 5.1539 | 5.0956 | 5.0366 | 4.978 | 4.1994 | 0.38961 | 0.1034
|  | ST CYRUS | CT |  |  |  | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 5.9734 | 2.3113 | 2.1355 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.513 | 2.8546 | 2.6329 | 5.536 | 5.4982 | 5.454 | 5.4096 | 5.3651 | 5.3205 | 5.2766 | 5.2291 | 5.1826 | 5.1355 | 5.0888 | 4.3886 | 0.65783 | 0.44881
|  | ST CYRUS | LW |  |  |  | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 5.8143 | 2.0858 | 1.8406 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.7986 | 5.3124 | 2.5702 | 2.2667 | 5.5361 | 5.4916 | 5.4361 | 5.3803 | 5.3244 | 5.2685 | 5.2134 | 5.1539 | 5.0956 | 5.0366 | 4.978 | 4.1994 | 0.38961 | 0.1034
|  | ST CYRUS | ST |  |  |  | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.2567 | 4.6274 | 4.5211 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.7104 | 4.6598 | 4.5257 | 5.5523 | 5.5423 | 5.5263 | 5.5067 | 5.4806 | 5.4544 | 5.4287 | 5.4008 | 5.3738 | 5.3465 | 5.3196 | 4.9443 | 3.0569 | 2.9304
|  | ST CYRUS | FS |  |  |  | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 6.4634 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.8124 | 5.5578 | 5.5569 | 5.5523 | 5.5467 | 5.5382 | 5.5297 | 5.5189 | 5.5082 | 5.4978 | 5.4874 | 5.4771 | 5.4273 | 5.3798 | 5.335
| ST FERGUS GAS | ST FERGUS GAS TERM | MINIMUM HEADROOM | NK 0916 5377 | NO | YES | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 38.5609 | 38.1398 | 38.1398 | 38.1398 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29.4108 | 29.0425 | 29.0425 | 29.0425 | 34.9274 | 34.9203 | 34.9142 | 34.9121 | 34.9101 | 34.908 | 34.906 | 34.9038 | 34.9017 | 34.8995 | 34.3297 | 29.8891 | 29.8891 | 29.8891
|  | ST FERGUS GAS TERM | CT |  |  |  | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 38.5609 | 38.1398 | 38.1398 | 38.1398 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29.4108 | 29.0425 | 29.0425 | 29.0425 | 34.9274 | 34.9203 | 34.9142 | 34.9121 | 34.9101 | 34.908 | 34.906 | 34.9038 | 34.9017 | 34.8995 | 34.3297 | 29.8891 | 29.8891 | 29.8891
|  | ST FERGUS GAS TERM | LW |  |  |  | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 38.5609 | 38.1398 | 38.1398 | 38.1398 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29.4108 | 29.0425 | 29.0425 | 29.0425 | 34.9287 | 34.9227 | 34.9153 | 34.9132 | 34.9113 | 34.9095 | 34.9076 | 34.9057 | 34.9038 | 34.9018 | 34.3322 | 29.8891 | 29.8891 | 29.8891
|  | ST FERGUS GAS TERM | ST |  |  |  | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 38.8979 | 38.6873 | 38.6873 | 38.6873 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29.7054 | 29.5212 | 29.5212 | 29.5212 | 34.9309 | 34.9294 | 34.9271 | 34.9244 | 34.9209 | 34.9175 | 34.9147 | 34.9138 | 34.9129 | 34.912 | 34.6273 | 34.4455 | 34.4413 | 34.4372
|  | ST FERGUS GAS TERM | FS |  |  |  | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 39.2348 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 34.9316 | 34.9315 | 34.9307 | 34.9298 | 34.9286 | 34.9275 | 34.926 | 34.9245 | 34.9231 | 34.9217 | 34.9203 | 34.9146 | 34.913 | 34.9115
| ST FILLANS | ST FILLANS | MINIMUM HEADROOM | NN 6942 2464 | YES | NO | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
|  | ST FILLANS | CT |  |  |  | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
|  | ST FILLANS | LW |  |  |  | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
|  | ST FILLANS | ST |  |  |  | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
|  | ST FILLANS | FS |  |  |  | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
| PERSLEY | ST MACHAR | MINIMUM HEADROOM | NJ 93584 08102 | NO | YES | 28.2495 | 28.2459 | 28.2416 | 28.2374 | 28.2332 | 28.2276 | 28.2216 | 28.2173 | 28.2173 | 28.2173 | 28.2173 | 28.2173 | 28.2173 | 28.2173 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.8592 | 26.8553 | 26.8505 | 26.8458 | 26.8412 | 26.835 | 26.8283 | 26.8211 | 26.8141 | 26.8072 | 26.8003 | 26.7627 | 26.7627 | 26.7627
|  | ST MACHAR | CT |  |  |  | 28.2503 | 28.2484 | 28.2464 | 28.2443 | 28.2422 | 28.2402 | 28.2383 | 28.2362 | 28.2341 | 28.2321 | 28.23 | 28.2173 | 28.2173 | 28.2173 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.8601 | 26.8581 | 26.8558 | 26.8535 | 26.8512 | 26.849 | 26.8468 | 26.8445 | 26.8422 | 26.8399 | 26.8376 | 26.8159 | 26.7937 | 26.7725
|  | ST MACHAR | LW |  |  |  | 28.2495 | 28.2459 | 28.2416 | 28.2374 | 28.2332 | 28.2292 | 28.2252 | 28.2208 | 28.2173 | 28.2173 | 28.2173 | 28.2173 | 28.2173 | 28.2173 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.8592 | 26.8553 | 26.8505 | 26.8458 | 26.8412 | 26.8367 | 26.8323 | 26.8275 | 26.8227 | 26.818 | 26.8126 | 26.7627 | 26.7627 | 26.7627
|  | ST MACHAR | ST |  |  |  | 28.2502 | 28.2478 | 28.2443 | 28.24 | 28.2337 | 28.2276 | 28.2216 | 28.2173 | 28.2173 | 28.2173 | 28.2173 | 28.2173 | 28.2173 | 28.2173 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.86 | 26.8574 | 26.8535 | 26.8488 | 26.8418 | 26.835 | 26.8283 | 26.8211 | 26.8141 | 26.8072 | 26.8003 | 26.7642 | 26.7627 | 26.7627
|  | ST MACHAR | FS |  |  |  | 28.2518 | 28.2516 | 28.2509 | 28.25 | 28.2483 | 28.2466 | 28.2444 | 28.2423 | 28.2402 | 28.2381 | 28.2361 | 28.2264 | 28.2173 | 28.2173 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.7157 | 26.8618 | 26.8616 | 26.8608 | 26.8598 | 26.8579 | 26.856 | 26.8536 | 26.8512 | 26.8489 | 26.8466 | 26.8444 | 26.8337 | 26.823 | 26.8126
| THURSO | ST MARYS | MINIMUM HEADROOM | HY 46965 01396 | YES | YES | 3.2807 | 3.273 | 3.2631 | 3.2533 | 3.2437 | 3.2342 | 3.2249 | 3.2147 | 3.2047 | 3.1947 | 3.1848 | -1.0722 | -1.3848 | -1.6931 | 2.3484 | 0.92624 | 0.80375 | 0.68203 | 0.56216 | 0.44484 | 0.3296 | 0.20364 | 0.079007 | -0.044514 | -0.16805 | -2.1198 | -2.4965 | -2.8681 | 2.2015 | 2.2015 | 0.96317 | 0.88246 | 0.80297 | 0.72517 | 0.64875 | 0.56522 | 0.47421 | 0.35342 | 0.23262 | -2.3091 | -2.676 | -3.038
|  | ST MARYS | CT |  |  |  | 3.2807 | 3.273 | 3.2642 | 3.2555 | 3.2469 | 3.2385 | 3.2303 | 3.2213 | 3.2123 | 3.2035 | 3.1947 | -0.90955 | -1.1613 | -1.4096 | 2.3484 | 0.92624 | 0.81647 | 0.70853 | 0.60225 | 0.49823 | 0.39603 | 0.28435 | 0.17386 | 0.064355 | -0.045123 | -1.9238 | -2.2272 | -2.5265 | 2.2015 | 2.2015 | 0.97161 | 0.90003 | 0.82955 | 0.76057 | 0.6928 | 0.61874 | 0.54547 | 0.45989 | 0.35283 | -2.1182 | -2.4136 | -2.7052
|  | ST MARYS | LW |  |  |  | 3.2812 | 3.2731 | 3.2631 | 3.2533 | 3.2437 | 3.2342 | 3.2249 | 3.2147 | 3.2047 | 3.1947 | 3.1848 | -1.0722 | -1.3848 | -1.6931 | 2.3484 | 0.92757 | 0.80375 | 0.68203 | 0.56216 | 0.44484 | 0.3296 | 0.20364 | 0.079007 | -0.044514 | -0.16805 | -2.1198 | -2.4965 | -2.8681 | 2.2015 | 2.2015 | 0.96317 | 0.88246 | 0.80297 | 0.72517 | 0.64875 | 0.56522 | 0.47421 | 0.35342 | 0.23262 | -2.3091 | -2.676 | -3.038
|  | ST MARYS | ST |  |  |  | 3.2839 | 3.2815 | 3.2778 | 3.2734 | 3.2707 | 3.268 | 3.2655 | 3.2627 | 3.2599 | 3.2572 | 3.2545 | 0.2351 | 0.2351 | 0.2351 | 2.3484 | 2.3484 | 0.98575 | 0.93069 | 0.89723 | 0.86475 | 0.83298 | 0.79793 | 0.76381 | 0.7304 | 0.69706 | -0.24204 | -0.4025 | -0.56256 | 2.2015 | 2.2015 | 2.2015 | 2.2015 | 2.2015 | 2.2015 | 0.98256 | 0.95932 | 0.93669 | 0.91453 | 0.89243 | -0.2839 | -0.3903 | -0.49644
|  | ST MARYS | FS |  |  |  | 3.2852 | 3.285 | 3.284 | 3.2827 | 3.2818 | 3.2809 | 3.2798 | 3.2787 | 3.2776 | 3.2765 | 3.2755 | 3.2704 | 3.2657 | 3.2612 | 2.3484 | 2.3484 | 2.3484 | 2.3484 | 2.3484 | 2.3484 | 2.3484 | 0.99681 | 0.98331 | 0.97016 | 0.95705 | 0.89451 | 0.83576 | 0.78006 | 2.2015 | 2.2015 | 2.2015 | 2.2015 | 2.2015 | 2.2015 | 2.2015 | 2.2015 | 2.2015 | 2.2015 | 2.2015 | 2.2015 | 0.9844 | 0.94746
| WILLOWDALE | ST NICHOLAS | MINIMUM HEADROOM | NJ 93737 06782 | NO | NO | 28.249 | 28.1897 | 28.1583 | 28.1344 | 28.1313 | 28.1283 | 28.1254 | 28.1221 | 28.119 | 28.1159 | 28.1126 | 28.0904 | 28.0677 | 28.0454 | 27.0744 | 26.9987 | 26.9586 | 26.9195 | 26.882 | 26.8451 | 26.8089 | 26.7697 | 26.7309 | 26.6934 | 26.6529 | 26.467 | 26.2975 | 26.2611 | 27.3097 | 27.2595 | 27.2329 | 27.2069 | 27.1821 | 27.1576 | 27.1336 | 27.1076 | 27.0819 | 27.057 | 27.0302 | 26.8504 | 26.7842 | 26.7842
|  | ST NICHOLAS | CT |  |  |  | 28.2553 | 28.211 | 28.1955 | 28.1798 | 28.1635 | 28.1444 | 28.1337 | 28.1318 | 28.1299 | 28.1283 | 28.1267 | 28.1167 | 28.1064 | 28.0965 | 27.0825 | 27.0259 | 27.006 | 26.9861 | 26.9652 | 26.9393 | 26.9104 | 26.8872 | 26.8648 | 26.8453 | 26.8257 | 26.7026 | 26.5864 | 26.5125 | 27.3151 | 27.2775 | 27.2643 | 27.2511 | 27.2372 | 27.2201 | 27.2009 | 27.1855 | 27.1707 | 27.1577 | 27.1447 | 27.0631 | 26.98 | 26.8997
|  | ST NICHOLAS | LW |  |  |  | 28.249 | 28.1897 | 28.1583 | 28.1344 | 28.1313 | 28.1283 | 28.1254 | 28.1221 | 28.119 | 28.1159 | 28.1126 | 28.0904 | 28.0677 | 28.0454 | 27.0744 | 26.9987 | 26.9586 | 26.9195 | 26.882 | 26.8451 | 26.8089 | 26.7697 | 26.7309 | 26.6934 | 26.6529 | 26.467 | 26.2975 | 26.2611 | 27.3097 | 27.2595 | 27.2329 | 27.2069 | 27.1821 | 27.1576 | 27.1336 | 27.1076 | 27.0819 | 27.057 | 27.0302 | 26.8504 | 26.7842 | 26.7842
|  | ST NICHOLAS | ST |  |  |  | 28.264 | 28.2357 | 28.2238 | 28.2092 | 28.1853 | 28.1591 | 28.1357 | 28.1321 | 28.1296 | 28.1272 | 28.1248 | 28.1123 | 28.0999 | 28.0878 | 27.0936 | 27.0575 | 27.0422 | 27.0236 | 26.9931 | 26.9596 | 26.9246 | 26.8919 | 26.8602 | 26.831 | 26.802 | 26.649 | 26.5379 | 26.4477 | 27.3224 | 27.2985 | 27.2883 | 27.276 | 27.2558 | 27.2336 | 27.2103 | 27.1887 | 27.1677 | 27.1483 | 27.1291 | 27.0276 | 26.9273 | 26.8294
|  | ST NICHOLAS | FS |  |  |  | 28.2734 | 28.2613 | 28.2571 | 28.2524 | 28.2442 | 28.2361 | 28.2266 | 28.2171 | 28.2079 | 28.1987 | 28.19 | 28.1508 | 28.1328 | 28.1288 | 27.1056 | 27.0901 | 27.0848 | 27.0787 | 27.0683 | 27.058 | 27.0458 | 27.0337 | 27.0219 | 27.0102 | 26.9991 | 26.9489 | 26.8995 | 26.8513 | 27.3304 | 27.3201 | 27.3166 | 27.3126 | 27.3056 | 27.2988 | 27.2907 | 27.2827 | 27.2748 | 27.2671 | 27.2597 | 27.2265 | 27.1937 | 27.1617
| ARDMORE | STOCKINISH | MINIMUM HEADROOM | NG 13447 94222 | YES | YES | 1.4177 | 1.4152 | 1.4139 | 1.4139 | 1.4139 | 1.4139 | 1.4139 | 1.4139 | 1.4139 | 1.4139 | 1.4139 | 1.4139 | 1.4139 | 1.4139 | 1.3894 | 1.3868 | 1.3836 | 1.3805 | 1.3774 | 1.3744 | 1.3715 | 1.3684 | 1.3652 | 1.3621 | 1.359 | 1.3345 | 1.3162 | 1.3162 | 1.4163 | 1.416 | 1.4157 | 1.4154 | 1.4151 | 1.4148 | 1.4145 | 1.4142 | 1.4139 | 1.4136 | 1.4133 | 1.4109 | 1.4084 | 1.406
|  | STOCKINISH | CT |  |  |  | 1.4179 | 1.416 | 1.4139 | 1.4139 | 1.4139 | 1.4139 | 1.4139 | 1.4139 | 1.4139 | 1.4139 | 1.4139 | 1.4139 | 1.4139 | 1.4139 | 1.3895 | 1.3876 | 1.3854 | 1.3832 | 1.381 | 1.379 | 1.3769 | 1.3747 | 1.3725 | 1.3704 | 1.3682 | 1.3455 | 1.3226 | 1.3162 | 1.4163 | 1.4161 | 1.4159 | 1.4157 | 1.4155 | 1.4153 | 1.4151 | 1.4148 | 1.4146 | 1.4144 | 1.4142 | 1.4119 | 1.4097 | 1.4074
|  | STOCKINISH | LW |  |  |  | 1.4177 | 1.4152 | 1.4139 | 1.4139 | 1.4139 | 1.4139 | 1.4139 | 1.4139 | 1.4139 | 1.4139 | 1.4139 | 1.4139 | 1.4139 | 1.4139 | 1.3894 | 1.3868 | 1.3836 | 1.3805 | 1.3774 | 1.3744 | 1.3715 | 1.3684 | 1.3652 | 1.3621 | 1.359 | 1.3345 | 1.3162 | 1.3162 | 1.4163 | 1.416 | 1.4157 | 1.4154 | 1.4151 | 1.4148 | 1.4145 | 1.4142 | 1.4139 | 1.4136 | 1.4133 | 1.4109 | 1.4084 | 1.406
|  | STOCKINISH | ST |  |  |  | 1.4185 | 1.4178 | 1.4167 | 1.4154 | 1.4139 | 1.4139 | 1.4139 | 1.4139 | 1.4139 | 1.4139 | 1.4139 | 1.4139 | 1.4139 | 1.4139 | 1.3902 | 1.3895 | 1.3883 | 1.387 | 1.3847 | 1.3824 | 1.3802 | 1.3778 | 1.3755 | 1.3732 | 1.371 | 1.36 | 1.3492 | 1.3385 | 1.4164 | 1.4163 | 1.4162 | 1.4161 | 1.4158 | 1.4156 | 1.4154 | 1.4151 | 1.4149 | 1.4147 | 1.4145 | 1.4134 | 1.4123 | 1.4112
|  | STOCKINISH | FS |  |  |  | 1.4189 | 1.4189 | 1.4186 | 1.4182 | 1.4175 | 1.4168 | 1.4159 | 1.415 | 1.4141 | 1.4139 | 1.4139 | 1.4139 | 1.4139 | 1.4139 | 1.3907 | 1.3906 | 1.3903 | 1.3899 | 1.3891 | 1.3884 | 1.3874 | 1.3865 | 1.3856 | 1.3847 | 1.3838 | 1.3795 | 1.3756 | 1.3719 | 1.4164 | 1.4164 | 1.4164 | 1.4163 | 1.4163 | 1.4162 | 1.4161 | 1.416 | 1.4159 | 1.4158 | 1.4157 | 1.4153 | 1.4149 | 1.4146
| PORT ANN | STONEFIELD | MINIMUM HEADROOM | NR 86244 73400 | YES | YES | -0.024433 | -0.19464 | -0.365 | -0.52927 | -0.68746 | -0.83955 | -0.98556 | -1.0756 | -1.1205 | -1.165 | -1.2088 | -1.4309 | -1.6812 | -1.9502 | 0.036809 | -0.099333 | -0.23563 | -0.36707 | -0.49364 | -0.61534 | -0.73217 | -0.80433 | -0.84053 | -0.87636 | -0.91166 | -1.0905 | -1.2918 | -1.5081 | -0.03633 | -0.20743 | -0.3787 | -0.54385 | -0.70287 | -0.85578 | -1.0026 | -1.0931 | -1.1384 | -1.1832 | -1.2273 | -1.4511 | -1.7031 | -1.9739
|  | STONEFIELD | CT |  |  |  | -0.024433 | -0.19464 | -0.365 | -0.52927 | -0.68746 | -0.83955 | -0.98556 | -1.0756 | -1.1205 | -1.165 | -1.2088 | -1.4309 | -1.6812 | -1.9502 | 0.036809 | -0.099333 | -0.23563 | -0.36707 | -0.49364 | -0.61534 | -0.73217 | -0.80433 | -0.84053 | -0.87636 | -0.91166 | -1.0905 | -1.2918 | -1.5081 | -0.03633 | -0.20743 | -0.3787 | -0.54385 | -0.70287 | -0.85578 | -1.0026 | -1.0931 | -1.1384 | -1.1832 | -1.2273 | -1.4511 | -1.7031 | -1.9739
|  | STONEFIELD | LW |  |  |  | 0.27455 | 0.24854 | 0.21919 | 0.18694 | 0.1521 | 0.11495 | 0.075795 | 0.027886 | -0.021429 | -0.071764 | -0.12273 | -0.39565 | -0.72837 | -1.1225 | 0.27662 | 0.25552 | 0.23168 | 0.20552 | 0.17729 | 0.14721 | 0.11552 | 0.076789 | 0.036928 | -0.0037502 | -0.044934 | -0.26641 | -0.53592 | -0.85474 | 0.26555 | 0.23933 | 0.20974 | 0.17723 | 0.14209 | 0.10462 | 0.065123 | 0.016784 | -0.032976 | -0.083767 | -0.1352 | -0.41034 | -0.7459 | -1.1436
|  | STONEFIELD | ST |  |  |  | 0.32405 | 0.30636 | 0.29766 | 0.28771 | 0.2754 | 0.26342 | 0.25179 | 0.24 | 0.22314 | 0.20672 | 0.19076 | 0.10198 | 0.016351 | -0.084038 | 0.31166 | 0.30333 | 0.29508 | 0.28697 | 0.27686 | 0.26703 | 0.25748 | 0.24778 | 0.23402 | 0.22062 | 0.20758 | 0.13524 | 0.065455 | -0.016183 | 0.30954 | 0.29916 | 0.28893 | 0.27891 | 0.26653 | 0.25449 | 0.24279 | 0.23094 | 0.21396 | 0.19744 | 0.18137 | 0.091944 | 0.0057073 | -0.095455
|  | STONEFIELD | FS |  |  |  | 0.30636 | 0.29749 | 0.28303 | 0.2682 | 0.25344 | 0.23889 | 0.22446 | 0.21024 | 0.19622 | 0.1824 | 0.16879 | 0.087505 | 0.00071499 | -0.083744 | 0.3037 | 0.2956 | 0.28351 | 0.27157 | 0.25965 | 0.24789 | 0.23622 | 0.22471 | 0.21336 | 0.20218 | 0.19117 | 0.12549 | 0.055435 | -0.012723 | 0.29946 | 0.28926 | 0.2741 | 0.25912 | 0.24423 | 0.22954 | 0.21499 | 0.20064 | 0.18649 | 0.17256 | 0.15883 | 0.076798 | -0.010802 | -0.096055
| FIDDES | STONEHAVEN | MINIMUM HEADROOM | NO 85903 85641 | NO | YES | 30.4504 | 30.4218 | 30.3927 | 30.3927 | 30.3927 | 30.3927 | 30.3927 | 30.3927 | 30.3927 | 30.3927 | 30.3927 | 20.8858 | 17.3022 | 16.0861 | 28.1071 | 27.9578 | 27.7734 | 27.59 | 27.4078 | 27.2264 | 27.0479 | 22.0392 | 21.5942 | 21.1462 | 20.7019 | 18.0986 | 14.8299 | 13.3644 | 28.5477 | 28.5477 | 28.5477 | 28.5477 | 28.5477 | 28.5477 | 21.8137 | 21.3608 | 20.9157 | 20.4675 | 20.0231 | 17.0795 | 13.269 | 11.803
|  | STONEHAVEN | CT |  |  |  | 30.4546 | 30.4372 | 30.417 | 30.3968 | 30.3927 | 30.3927 | 30.3927 | 30.3927 | 30.3927 | 30.3927 | 30.3927 | 22.3315 | 19.6786 | 18.8807 | 28.1291 | 28.0381 | 27.9327 | 27.8272 | 27.7218 | 27.6162 | 27.5123 | 27.4002 | 27.2907 | 27.1797 | 27.0697 | 20.4491 | 17.6939 | 16.7322 | 28.5477 | 28.5477 | 28.5477 | 28.5477 | 28.5477 | 28.5477 | 28.5477 | 28.5477 | 28.5477 | 28.5477 | 21.8649 | 19.4309 | 16.1339 | 15.172
|  | STONEHAVEN | LW |  |  |  | 30.4504 | 30.4218 | 30.3927 | 30.3927 | 30.3927 | 30.3927 | 30.3927 | 30.3927 | 30.3927 | 30.3927 | 30.3927 | 20.8858 | 17.3022 | 16.0861 | 28.1071 | 27.9578 | 27.7734 | 27.59 | 27.4078 | 27.2264 | 27.0479 | 22.0392 | 21.5942 | 21.1462 | 20.7019 | 18.0986 | 14.8299 | 13.3644 | 28.5477 | 28.5477 | 28.5477 | 28.5477 | 28.5477 | 28.5477 | 21.8137 | 21.3608 | 20.9157 | 20.4675 | 20.0231 | 17.0795 | 13.269 | 11.803
|  | STONEHAVEN | ST |  |  |  | 30.4589 | 30.4493 | 30.4342 | 30.416 | 30.4045 | 30.3931 | 30.3927 | 30.3927 | 30.3927 | 30.3927 | 30.3927 | 22.9712 | 21.9517 | 21.9517 | 28.1517 | 28.1012 | 28.0224 | 27.9274 | 27.8676 | 27.8076 | 27.7487 | 27.6852 | 27.6238 | 27.5616 | 27.5006 | 26.8393 | 20.7285 | 20.0575 | 28.5477 | 28.5477 | 28.5477 | 28.5477 | 28.5477 | 28.5477 | 28.5477 | 28.5477 | 28.5477 | 28.5477 | 28.5477 | 21.4506 | 19.6096 | 18.9384
|  | STONEHAVEN | FS |  |  |  | 30.4644 | 30.4636 | 30.4596 | 30.4547 | 30.451 | 30.4472 | 30.4425 | 30.4378 | 30.4333 | 30.4287 | 30.4243 | 30.4027 | 30.3927 | 30.3927 | 28.1803 | 28.1762 | 28.1551 | 28.1298 | 28.1102 | 28.0904 | 28.0658 | 28.0414 | 28.0178 | 27.994 | 27.9707 | 27.858 | 27.7511 | 27.6501 | 28.5477 | 28.5477 | 28.5477 | 28.5477 | 28.5477 | 28.5477 | 28.5477 | 28.5477 | 28.5477 | 28.5477 | 28.5477 | 28.5477 | 28.5477 | 28.5477
| STRICHEN | STONEYHILL | MINIMUM HEADROOM | NK 6773 4109 | YES | YES | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.8105 | 4.8104 | 4.8103 | 4.8102 | 4.8101 | 4.81 | 4.8099 | 4.8098 | 4.8096 | 4.8095 | 4.8094 | 4.8089 | 4.8084 | 4.8079 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537
|  | STONEYHILL | CT |  |  |  | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.8105 | 4.8104 | 4.8103 | 4.8103 | 4.8102 | 4.8101 | 4.81 | 4.81 | 4.8099 | 4.8098 | 4.8097 | 4.8094 | 4.809 | 4.8087 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537
|  | STONEYHILL | LW |  |  |  | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.8105 | 4.8104 | 4.8103 | 4.8102 | 4.8101 | 4.81 | 4.8099 | 4.8098 | 4.8096 | 4.8095 | 4.8094 | 4.8089 | 4.8084 | 4.8079 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537
|  | STONEYHILL | ST |  |  |  | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.8105 | 4.8105 | 4.8104 | 4.8104 | 4.8103 | 4.8103 | 4.8102 | 4.8102 | 4.8101 | 4.8101 | 4.81 | 4.8098 | 4.8096 | 4.8094 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537
|  | STONEYHILL | FS |  |  |  | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.8105 | 4.8105 | 4.8105 | 4.8105 | 4.8105 | 4.8105 | 4.8104 | 4.8104 | 4.8104 | 4.8104 | 4.8104 | 4.8103 | 4.8102 | 4.8101 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537 | 4.9537
| PERSLEY | STONEYWOOD T1&T2 | MINIMUM HEADROOM | NJ 89285 11082 | NO | YES | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 25.4258 | 25.3931 | 25.3559 | 25.3189 | 25.2819 | 25.2418 | 25.2061 | 25.1723 | 25.1568 | 25.1421 | 25.1249 | 25.1161 | 25.1161 | 25.1161 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213
|  | STONEYWOOD T1&T2 | CT |  |  |  | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 25.4288 | 25.3991 | 25.3669 | 25.3341 | 25.2995 | 25.2608 | 25.2237 | 25.1866 | 25.1636 | 25.1421 | 25.1249 | 25.1161 | 25.1161 | 25.1161 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213
|  | STONEYWOOD T1&T2 | LW |  |  |  | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 25.4258 | 25.3931 | 25.3559 | 25.3189 | 25.2819 | 25.2418 | 25.2061 | 25.1723 | 25.1568 | 25.1422 | 25.1278 | 25.1161 | 25.1161 | 25.1161 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213
|  | STONEYWOOD T1&T2 | ST |  |  |  | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 25.4423 | 25.4265 | 25.4084 | 25.389 | 25.3635 | 25.3352 | 25.3082 | 25.2803 | 25.2622 | 25.245 | 25.231 | 25.1717 | 25.1221 | 25.1161 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213
|  | STONEYWOOD T1&T2 | FS |  |  |  | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 30.1393 | 25.4525 | 25.4445 | 25.4355 | 25.4267 | 25.416 | 25.4048 | 25.3938 | 25.3831 | 25.3765 | 25.3698 | 25.3635 | 25.3399 | 25.3224 | 25.3057 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213 | 25.4213
| PERSLEY | STONEYWOOD T3 | MINIMUM HEADROOM | NJ 89285 11082 | YES | YES | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 15.2643 | 15.2261 | 15.1825 | 15.1391 | 15.0958 | 15.0488 | 15.007 | 14.9673 | 14.9516 | 14.9376 | 14.9213 | 14.8253 | 14.8181 | 14.8181 | 16.0197 | 16.0046 | 15.9875 | 15.9704 | 15.9534 | 15.9349 | 15.9184 | 15.9028 | 15.8957 | 15.8889 | 15.881 | 15.8464 | 15.8135 | 15.7811
|  | STONEYWOOD T3 | CT |  |  |  | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 15.2679 | 15.2331 | 15.1953 | 15.1569 | 15.1164 | 15.071 | 15.0276 | 14.9841 | 14.958 | 14.9376 | 14.9213 | 14.8371 | 14.8181 | 14.8181 | 16.0211 | 16.0074 | 15.9925 | 15.9774 | 15.9615 | 15.9436 | 15.9266 | 15.9094 | 15.8988 | 15.8889 | 15.881 | 15.8524 | 15.8293 | 15.807
|  | STONEYWOOD T3 | LW |  |  |  | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 15.2643 | 15.2261 | 15.1825 | 15.1391 | 15.0958 | 15.0488 | 15.007 | 14.9673 | 14.9516 | 14.9377 | 14.924 | 14.8253 | 14.8181 | 14.8181 | 16.0197 | 16.0046 | 15.9875 | 15.9704 | 15.9534 | 15.9349 | 15.9184 | 15.9028 | 15.8957 | 15.889 | 15.8823 | 15.8464 | 15.8135 | 15.7811
|  | STONEYWOOD T3 | ST |  |  |  | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 15.2837 | 15.2652 | 15.244 | 15.2213 | 15.1913 | 15.1582 | 15.1265 | 15.0939 | 15.0727 | 15.0526 | 15.0361 | 14.9666 | 14.9187 | 14.8728 | 16.0273 | 16.02 | 16.0117 | 16.0028 | 15.991 | 15.9779 | 15.9655 | 15.9527 | 15.9443 | 15.9364 | 15.9299 | 15.9026 | 15.8797 | 15.8636
|  | STONEYWOOD T3 | FS |  |  |  | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 17.4198 | 15.2956 | 15.2863 | 15.2757 | 15.2654 | 15.2529 | 15.2398 | 15.2269 | 15.2144 | 15.2066 | 15.1987 | 15.1914 | 15.1637 | 15.1432 | 15.1237 | 16.032 | 16.0284 | 16.0242 | 16.0201 | 16.0152 | 16.01 | 16.005 | 16.0001 | 15.997 | 15.9939 | 15.991 | 15.9801 | 15.972 | 15.9644
| CLACHAN | STRACHUR | MINIMUM HEADROOM | NN 08672 01180 | YES | YES | 1.5264 | 1.5227 | 1.5181 | 1.5135 | 1.512 | 1.512 | 1.512 | 1.512 | 1.512 | 0.963 | 0.91965 | -0.0040946 | -0.1168 | -0.22771 | 1.3049 | 1.3049 | 0.96981 | 0.92062 | 0.87133 | 0.82052 | 0.77055 | 0.71656 | 0.66448 | 0.61469 | 0.56497 | -0.21918 | -0.3475 | -0.47376 | 1.3232 | 1.3232 | 1.3232 | 0.99118 | 0.93467 | 0.88113 | 0.82958 | 0.77389 | 0.72016 | 0.66879 | 0.61788 | -0.32936 | -0.46173 | -0.59198
|  | STRACHUR | CT |  |  |  | 1.5267 | 1.524 | 1.5209 | 1.5177 | 1.5145 | 1.512 | 1.512 | 1.512 | 1.512 | 1.512 | 1.512 | 0.1521 | 0.058307 | -0.033785 | 1.3049 | 1.3049 | 0.99982 | 0.96593 | 0.93152 | 0.89904 | 0.86746 | 0.82984 | 0.79271 | 0.75756 | 0.72371 | -0.041362 | -0.14814 | -0.25298 | 1.3232 | 1.3232 | 1.3232 | 1.3232 | 1.3232 | 0.96644 | 0.93023 | 0.89075 | 0.85245 | 0.81618 | 0.78126 | -0.14592 | -0.25607 | -0.36423
|  | STRACHUR | LW |  |  |  | 1.5264 | 1.5227 | 1.5181 | 1.5135 | 1.512 | 1.512 | 1.512 | 1.512 | 1.512 | 0.963 | 0.91965 | -0.0040946 | -0.1168 | -0.22771 | 1.3049 | 1.3049 | 0.96981 | 0.92062 | 0.87133 | 0.82052 | 0.77055 | 0.71656 | 0.66448 | 0.61469 | 0.56497 | -0.21918 | -0.3475 | -0.47376 | 1.3232 | 1.3232 | 1.3232 | 0.99118 | 0.93467 | 0.88113 | 0.82958 | 0.77389 | 0.72016 | 0.66879 | 0.61788 | -0.32936 | -0.46173 | -0.59198
|  | STRACHUR | ST |  |  |  | 1.5278 | 1.5266 | 1.5248 | 1.5227 | 1.5214 | 1.5202 | 1.519 | 1.5177 | 1.5165 | 1.5154 | 1.5143 | 0.78028 | 0.7398 | 0.69439 | 1.3049 | 1.3049 | 1.3049 | 1.3049 | 1.3049 | 0.99233 | 0.97976 | 0.96591 | 0.95276 | 0.94088 | 0.92986 | 0.55097 | 0.4969 | 0.44244 | 1.3232 | 1.3232 | 1.3232 | 1.3232 | 1.3232 | 1.3232 | 1.3232 | 1.3232 | 1.3232 | 1.3232 | 1.3232 | 0.5349 | 0.47832 | 0.42214
|  | STRACHUR | FS |  |  |  | 1.5311 | 1.5292 | 1.5277 | 1.527 | 1.5265 | 1.5261 | 1.5256 | 1.5251 | 1.5246 | 1.5242 | 1.5238 | 1.5219 | 1.5202 | 1.5186 | 1.3049 | 1.3049 | 1.3049 | 1.3049 | 1.3049 | 1.3049 | 1.3049 | 1.3049 | 1.3049 | 1.3049 | 1.3049 | 1.3049 | 0.99243 | 0.97573 | 1.3232 | 1.3232 | 1.3232 | 1.3232 | 1.3232 | 1.3232 | 1.3232 | 1.3232 | 1.3232 | 1.3232 | 1.3232 | 1.3232 | 1.3232 | 1.3232
| TARLAND | STRATHDON | MINIMUM HEADROOM | NJ 37343 11904 | YES | YES | 0.93622 | 0.79474 | 0.64786 | 0.50615 | 0.36962 | 0.23826 | 0.11211 | 0.034403 | -0.0058358 | -0.045705 | -0.085002 | -0.37138 | -0.60579 | -0.85442 | 0.99239 | 0.87161 | 0.75185 | 0.63625 | 0.52481 | 0.41753 | 0.31445 | 0.24984 | 0.21518 | 0.1808 | 0.1469 | -0.10019 | -0.30517 | -0.52125 | 0.93871 | 0.79803 | 0.65865 | 0.51597 | 0.37789 | 0.24501 | 0.11738 | 0.038354 | -0.0030232 | -0.044405 | -0.085217 | -0.38056 | -0.62299 | -0.87959
|  | STRATHDON | CT |  |  |  | 0.93622 | 0.79474 | 0.64786 | 0.50615 | 0.36962 | 0.23826 | 0.11211 | 0.034403 | -0.0058358 | -0.045705 | -0.085002 | -0.37138 | -0.60579 | -0.85442 | 0.99239 | 0.87161 | 0.75185 | 0.63625 | 0.52481 | 0.41753 | 0.31445 | 0.24984 | 0.21518 | 0.1808 | 0.1469 | -0.10019 | -0.30517 | -0.52125 | 0.93871 | 0.79803 | 0.65865 | 0.51597 | 0.37789 | 0.24501 | 0.11738 | 0.038354 | -0.0030232 | -0.044405 | -0.085217 | -0.38056 | -0.62299 | -0.87959
|  | STRATHDON | LW |  |  |  | 1.431 | 1.4112 | 1.3889 | 1.3643 | 1.3377 | 1.3093 | 0.99845 | 0.95277 | 0.90601 | 0.85839 | 0.8103 | 0.45978 | 0.135 | -0.23306 | 1.4691 | 1.456 | 1.4412 | 1.425 | 1.4075 | 1.3889 | 1.3693 | 0.9838 | 0.94375 | 0.90301 | 0.86189 | 0.5593 | 0.27763 | -0.039187 | 1.4952 | 1.4747 | 1.4517 | 1.4263 | 1.3988 | 1.3694 | 0.98013 | 0.93529 | 0.88943 | 0.84276 | 0.79565 | 0.44347 | 0.10708 | -0.27267
|  | STRATHDON | ST |  |  |  | 1.4649 | 1.457 | 1.4493 | 1.4419 | 1.4328 | 1.4239 | 1.4154 | 1.4068 | 1.3944 | 1.3823 | 1.3705 | 0.95727 | 0.86387 | 0.75956 | 1.4906 | 1.4855 | 1.4804 | 1.4753 | 1.469 | 1.4629 | 1.4569 | 1.4509 | 1.4425 | 1.4342 | 1.4262 | 0.98028 | 0.89679 | 0.80441 | 1.5303 | 1.5221 | 1.5142 | 1.5064 | 1.497 | 1.4879 | 1.479 | 1.4702 | 1.4573 | 1.4448 | 1.4326 | 0.93501 | 0.8412 | 0.73698
|  | STRATHDON | FS |  |  |  | 1.457 | 1.4491 | 1.4375 | 1.4259 | 1.4146 | 1.4034 | 1.3923 | 1.3814 | 1.3707 | 1.3601 | 1.3496 | 1.287 | 0.93923 | 0.8605 | 1.4857 | 1.4808 | 1.4733 | 1.466 | 1.4586 | 1.4513 | 1.4441 | 1.437 | 1.43 | 1.4231 | 1.4163 | 1.3757 | 0.97578 | 0.90902 | 1.5221 | 1.514 | 1.5019 | 1.49 | 1.4782 | 1.4666 | 1.4552 | 1.4439 | 1.4328 | 1.4219 | 1.4111 | 1.3463 | 0.92429 | 0.84751
| STRICHEN | STRICHEN | MINIMUM HEADROOM | NJ 95900 55137 | NO | YES | 6.7877 | 6.7839 | 6.7793 | 6.7746 | 6.7699 | 6.7652 | 6.7606 | 6.7556 | 6.1233 | 6.1184 | 5.486 | 4.1701 | 0.91508 | 0.57556 | 5.2122 | 5.1604 | 5.0969 | 5.0315 | 4.9666 | 4.902 | 4.8386 | 4.7701 | 4.1616 | 4.0938 | 3.4855 | 1.9689 | -0.73941 | -1.1413 | 4.9401 | 4.9118 | 4.8771 | 4.8414 | 4.784 | 4.722 | 4.661 | 4.5952 | 3.8413 | 3.7762 | 3.0225 | 1.2184 | -2.1027 | -2.4888
|  | STRICHEN | CT |  |  |  | 6.7877 | 6.7839 | 6.7796 | 6.7753 | 6.7711 | 6.7668 | 6.7626 | 6.7581 | 6.1262 | 6.1218 | 5.4899 | 4.1812 | 1.128 | 0.87122 | 5.2122 | 5.1604 | 5.1007 | 5.0414 | 4.9827 | 4.9242 | 4.8668 | 4.8047 | 4.2026 | 4.1412 | 3.5393 | 2.1215 | -0.48739 | -0.79133 | 4.9401 | 4.9118 | 4.8792 | 4.8469 | 4.7994 | 4.7433 | 4.6881 | 4.6285 | 3.8807 | 3.8218 | 3.0741 | 1.3649 | -1.8607 | -2.1526
|  | STRICHEN | LW |  |  |  | 6.788 | 6.7841 | 6.7793 | 6.7746 | 6.7699 | 6.7652 | 6.7606 | 6.7556 | 6.1233 | 6.1184 | 5.486 | 4.1701 | 0.91508 | 0.57556 | 5.2161 | 5.1627 | 5.0969 | 5.0315 | 4.9666 | 4.902 | 4.8386 | 4.7701 | 4.1616 | 4.0938 | 3.4855 | 1.9689 | -0.73941 | -1.1413 | 4.9423 | 4.9131 | 4.8771 | 4.8414 | 4.784 | 4.722 | 4.661 | 4.5952 | 3.8413 | 3.7762 | 3.0225 | 1.2184 | -2.1027 | -2.4888
|  | STRICHEN | ST |  |  |  | 6.7894 | 6.7885 | 6.787 | 6.7852 | 6.7826 | 6.78 | 6.7774 | 6.7746 | 6.4582 | 6.4555 | 6.1391 | 5.483 | 4.1377 | 4.1251 | 5.2356 | 5.2227 | 5.2026 | 5.1784 | 5.142 | 5.1058 | 5.0704 | 5.0322 | 4.7244 | 4.6873 | 4.3802 | 3.6469 | 2.3223 | 2.1494 | 4.9529 | 4.9459 | 4.9349 | 4.9217 | 4.9018 | 4.882 | 4.8627 | 4.8418 | 4.4666 | 4.431 | 4.0513 | 3.1732 | 1.5411 | 1.3751
|  | STRICHEN | FS |  |  |  | 6.7899 | 6.7898 | 6.7893 | 6.7887 | 6.7879 | 6.787 | 6.7859 | 6.7848 | 6.7837 | 6.7826 | 6.7816 | 6.7766 | 6.7718 | 6.7674 | 5.2426 | 5.2412 | 5.2346 | 5.2266 | 5.2144 | 5.2023 | 5.1869 | 5.1717 | 5.1569 | 5.1423 | 5.1279 | 5.0587 | 4.9935 | 4.9322 | 4.9568 | 4.956 | 4.9524 | 4.948 | 4.9414 | 4.9347 | 4.9263 | 4.918 | 4.91 | 4.9019 | 4.8941 | 4.8563 | 4.8098 | 4.7509
| THURSO | STROMNESS | MINIMUM HEADROOM | HY 25978 10409 | NO | YES | 10.2093 | 10.1504 | 10.0821 | 10.0147 | 9.9477 | 9.883 | 9.8196 | 9.7479 | 9.678 | 9.6094 | 9.5394 | 8.0893 | 7.7389 | 7.3909 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 12.9671 | 12.9671 | 12.9671 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.0837 | 11.0837 | 11.0837
|  | STROMNESS | CT |  |  |  | 10.2093 | 10.1504 | 10.0821 | 10.0147 | 9.9477 | 9.883 | 9.8196 | 9.7479 | 9.678 | 9.6094 | 9.5394 | 8.0893 | 7.7389 | 7.3909 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 12.9671 | 12.9671 | 12.9671 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.0837 | 11.0837 | 11.0837
|  | STROMNESS | LW |  |  |  | 10.2368 | 10.2206 | 10.1998 | 10.1789 | 10.1575 | 10.1379 | 10.1187 | 10.0944 | 10.072 | 10.0507 | 10.0273 | 8.4539 | 7.9795 | 7.5094 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 12.9671 | 12.9671 | 12.9671 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.0837 | 11.0837 | 11.0837
|  | STROMNESS | ST |  |  |  | 10.2421 | 10.2371 | 10.2291 | 10.2194 | 10.1785 | 10.1393 | 10.101 | 10.0574 | 10.0155 | 9.9748 | 9.9334 | 9.1809 | 8.9834 | 8.7859 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.2392 | 13.2392 | 13.2392 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.5387 | 11.5387 | 11.5387
|  | STROMNESS | FS |  |  |  | 10.2448 | 10.2442 | 10.2416 | 10.2386 | 10.225 | 10.2118 | 10.195 | 10.1777 | 10.161 | 10.1448 | 10.1285 | 10.05 | 9.9762 | 9.9051 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 13.5114 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937 | 11.9937
| THURSO | STRONSAY | MINIMUM HEADROOM | HY 64548 27016 | YES | YES | 1.2455 | 1.2455 | 1.2455 | 1.2455 | 1.2455 | 1.2455 | 1.2455 | 1.2455 | 1.2455 | 1.2455 | 1.2455 | 0.34591 | 0.32481 | 0.30348 | 1.1343 | 1.1335 | 1.1325 | 1.1315 | 1.1305 | 1.1296 | 1.1286 | 1.1276 | 1.1266 | 1.1257 | 1.1249 | 0.40968 | 0.38557 | 0.36163 | 1.1516 | 1.1512 | 1.1507 | 1.1502 | 1.1497 | 1.1493 | 1.1491 | 1.1491 | 1.1491 | 1.1491 | 1.1491 | 0.25648 | 0.23431 | 0.21139
|  | STRONSAY | CT |  |  |  | 1.2455 | 1.2455 | 1.2455 | 1.2455 | 1.2455 | 1.2455 | 1.2455 | 1.2455 | 1.2455 | 1.2455 | 1.2455 | 0.35076 | 0.33153 | 0.31122 | 1.1343 | 1.1337 | 1.133 | 1.1323 | 1.1316 | 1.1309 | 1.1303 | 1.1295 | 1.1288 | 1.1281 | 1.1273 | 0.41611 | 0.39312 | 0.37032 | 1.1516 | 1.1513 | 1.1509 | 1.1506 | 1.1503 | 1.1499 | 1.1496 | 1.1492 | 1.1491 | 1.1491 | 1.1491 | 0.2624 | 0.24125 | 0.22004
|  | STRONSAY | LW |  |  |  | 1.2455 | 1.2455 | 1.2455 | 1.2455 | 1.2455 | 1.2455 | 1.2455 | 1.2455 | 1.2455 | 1.2455 | 1.2455 | 0.34591 | 0.32481 | 0.30348 | 1.1343 | 1.1335 | 1.1325 | 1.1315 | 1.1305 | 1.1296 | 1.1286 | 1.1276 | 1.1266 | 1.1257 | 1.1249 | 0.40968 | 0.38557 | 0.36163 | 1.1516 | 1.1512 | 1.1507 | 1.1502 | 1.1497 | 1.1493 | 1.1491 | 1.1491 | 1.1491 | 1.1491 | 1.1491 | 0.25648 | 0.23431 | 0.21139
|  | STRONSAY | ST |  |  |  | 1.2455 | 1.2455 | 1.2455 | 1.2455 | 1.2455 | 1.2455 | 1.2455 | 1.2455 | 1.2455 | 1.2455 | 1.2455 | 0.77087 | 0.76216 | 0.75258 | 1.1346 | 1.1343 | 1.1339 | 1.1334 | 1.1322 | 1.1311 | 1.13 | 1.1287 | 1.1275 | 1.1263 | 1.1253 | 0.75529 | 0.74455 | 0.73379 | 1.1517 | 1.1516 | 1.1514 | 1.1511 | 1.1506 | 1.15 | 1.1495 | 1.1491 | 1.1491 | 1.1491 | 1.1491 | 0.68528 | 0.6754 | 0.66551
|  | STRONSAY | FS |  |  |  | 1.2455 | 1.2455 | 1.2455 | 1.2455 | 1.2455 | 1.2455 | 1.2455 | 1.2455 | 1.2455 | 1.2455 | 1.2455 | 1.2455 | 1.2455 | 1.2455 | 1.1347 | 1.1347 | 1.1345 | 1.1344 | 1.134 | 1.1336 | 1.1332 | 1.1327 | 1.1322 | 1.1317 | 1.1313 | 1.129 | 1.1269 | 1.1252 | 1.1518 | 1.1517 | 1.1517 | 1.1516 | 1.1514 | 1.1512 | 1.151 | 1.1508 | 1.1505 | 1.1503 | 1.1501 | 1.1491 | 1.1491 | 1.1491
| FORT WILLIAM | STRONTIAN | MINIMUM HEADROOM | NM 81521 61955 | YES | YES | 1.4189 | 1.4084 | 1.4084 | 1.4084 | 1.4084 | 1.4084 | 1.4084 | 1.4084 | 1.4084 | 1.4084 | 1.4084 | 0.98722 | 0.93628 | 0.88627 | 1.3439 | 1.3297 | 1.3147 | 1.2999 | 1.2924 | 1.2903 | 1.2881 | 1.2856 | 1.2835 | 1.2814 | 0.98546 | 0.93295 | 0.88077 | 0.82953 | 1.3853 | 1.3666 | 1.3467 | 1.327 | 1.3107 | 1.3107 | 1.3107 | 1.3107 | 1.3107 | 1.3107 | 1.3107 | 0.99152 | 0.9407 | 0.89081
|  | STRONTIAN | CT |  |  |  | 1.4189 | 1.4084 | 1.4084 | 1.4084 | 1.4084 | 1.4084 | 1.4084 | 1.4084 | 1.4084 | 1.4084 | 1.4084 | 0.98722 | 0.93628 | 0.88627 | 1.3439 | 1.3297 | 1.3147 | 1.2999 | 1.2924 | 1.2903 | 1.2881 | 1.2856 | 1.2835 | 1.2814 | 0.98546 | 0.93295 | 0.88077 | 0.82953 | 1.3853 | 1.3666 | 1.3467 | 1.327 | 1.3107 | 1.3107 | 1.3107 | 1.3107 | 1.3107 | 1.3107 | 1.3107 | 0.99152 | 0.9407 | 0.89081
|  | STRONTIAN | LW |  |  |  | 1.4274 | 1.424 | 1.4215 | 1.419 | 1.4166 | 1.4142 | 1.4092 | 1.4084 | 1.4084 | 1.4084 | 1.4084 | 1.4084 | 1.4084 | 1.4084 | 1.3509 | 1.3481 | 1.346 | 1.344 | 1.342 | 1.34 | 1.3358 | 1.3306 | 1.3284 | 1.3262 | 1.3241 | 1.2906 | 1.2833 | 0.95549 | 1.3947 | 1.391 | 1.3882 | 1.3855 | 1.3829 | 1.3802 | 1.3747 | 1.3678 | 1.3648 | 1.3619 | 1.3591 | 1.3107 | 1.3107 | 1.3107
|  | STRONTIAN | ST |  |  |  | 1.4288 | 1.4275 | 1.4266 | 1.4255 | 1.4198 | 1.4141 | 1.4084 | 1.4084 | 1.4084 | 1.4084 | 1.4084 | 1.4084 | 1.4084 | 1.4084 | 1.3521 | 1.351 | 1.3503 | 1.3493 | 1.3446 | 1.3399 | 1.334 | 1.3274 | 1.3225 | 1.3177 | 1.3129 | 1.293 | 1.2899 | 1.2868 | 1.3963 | 1.3948 | 1.3938 | 1.3926 | 1.3863 | 1.38 | 1.3723 | 1.3635 | 1.3571 | 1.3507 | 1.3443 | 1.3136 | 1.3107 | 1.3107
|  | STRONTIAN | FS |  |  |  | 1.4298 | 1.4292 | 1.429 | 1.4286 | 1.4267 | 1.4249 | 1.4219 | 1.4188 | 1.4165 | 1.4141 | 1.4118 | 1.4084 | 1.4084 | 1.4084 | 1.3529 | 1.3525 | 1.3522 | 1.3519 | 1.3504 | 1.3488 | 1.3464 | 1.3438 | 1.3419 | 1.3399 | 1.338 | 1.3292 | 1.3211 | 1.3134 | 1.3973 | 1.3967 | 1.3964 | 1.396 | 1.394 | 1.3919 | 1.3887 | 1.3853 | 1.3827 | 1.3801 | 1.3776 | 1.3659 | 1.3551 | 1.345
| SHETLAND | SUMBURGH | MINIMUM HEADROOM | HU3900512755 | YES | YES | 2.9257 | 2.9247 | 2.9247 | 2.9247 | 2.9247 | 2.9247 | 2.9247 | 2.9247 | 2.9247 | 2.9247 | 2.9247 | 2.9247 | 2.9247 | 2.9247 | 2.2306 | 2.2272 | 2.2241 | 2.221 | 2.218 | 2.215 | 2.2121 | 2.209 | 2.2059 | 2.2028 | 2.1997 | 2.1926 | 2.1882 | 2.1839 | 1.796 | 1.7883 | 1.7789 | 1.7696 | 1.7658 | 1.7628 | 1.7599 | 1.7568 | 1.7536 | 1.7505 | 1.7474 | 1.7403 | 1.7368 | 0.95304
|  | SUMBURGH | CT |  |  |  | 2.9258 | 2.9247 | 2.9247 | 2.9247 | 2.9247 | 2.9247 | 2.9247 | 2.9247 | 2.9247 | 2.9247 | 2.9247 | 2.9247 | 2.9247 | 2.9247 | 2.2311 | 2.2281 | 2.2259 | 2.2238 | 2.2218 | 2.2197 | 2.2177 | 2.2156 | 2.2134 | 2.2113 | 2.2092 | 2.2036 | 2.198 | 2.1925 | 1.7965 | 1.7909 | 1.7844 | 1.7781 | 1.7719 | 1.7675 | 1.7655 | 1.7634 | 1.7612 | 1.7591 | 1.757 | 1.7514 | 1.7458 | 1.7403
|  | SUMBURGH | LW |  |  |  | 2.9257 | 2.9247 | 2.9247 | 2.9247 | 2.9247 | 2.9247 | 2.9247 | 2.9247 | 2.9247 | 2.9247 | 2.9247 | 2.9247 | 2.9247 | 2.9247 | 2.2306 | 2.2272 | 2.2241 | 2.221 | 2.218 | 2.215 | 2.2121 | 2.209 | 2.2059 | 2.2028 | 2.1997 | 2.1926 | 2.1882 | 2.1839 | 1.796 | 1.7883 | 1.7789 | 1.7696 | 1.7658 | 1.7628 | 1.7599 | 1.7568 | 1.7536 | 1.7505 | 1.7474 | 1.7403 | 1.7368 | 0.95304
|  | SUMBURGH | ST |  |  |  | 2.9264 | 2.9258 | 2.9247 | 2.9247 | 2.9247 | 2.9247 | 2.9247 | 2.9247 | 2.9247 | 2.9247 | 2.9247 | 2.9247 | 2.9247 | 2.9247 | 2.2329 | 2.2309 | 2.2287 | 2.2274 | 2.2264 | 2.2255 | 2.2247 | 2.2237 | 2.2228 | 2.2219 | 2.221 | 2.2165 | 2.2122 | 2.2078 | 1.7985 | 1.7963 | 1.7929 | 1.7887 | 1.786 | 1.7832 | 1.7806 | 1.7777 | 1.7749 | 1.7721 | 1.7694 | 1.7643 | 1.76 | 1.7556
|  | SUMBURGH | FS |  |  |  | 2.9268 | 2.9268 | 2.9264 | 2.9261 | 2.9258 | 2.9255 | 2.9252 | 2.9248 | 2.9247 | 2.9247 | 2.9247 | 2.9247 | 2.9247 | 2.9247 | 2.2339 | 2.2338 | 2.2329 | 2.2319 | 2.2311 | 2.2303 | 2.2293 | 2.2289 | 2.2285 | 2.2282 | 2.2278 | 2.2261 | 2.2245 | 2.223 | 1.7998 | 1.7996 | 1.7986 | 1.7974 | 1.7965 | 1.7956 | 1.7944 | 1.7933 | 1.7922 | 1.7911 | 1.79 | 1.785 | 1.7802 | 1.7757
| ALNESS | TAIN | MINIMUM HEADROOM | NH 77578 81489 | NO | YES | 17.6344 | 17.5154 | 17.4001 | 17.2885 | 17.1803 | 17.0771 | 16.9779 | 16.9303 | 16.905 | 16.8799 | 16.8557 | 16.7285 | 16.6108 | 16.5047 | 16.1919 | 16.0742 | 15.9569 | 15.885 | 15.8123 | 15.7458 | 15.6816 | 15.6464 | 15.6229 | 15.5992 | 15.5776 | 15.4861 | 15.4048 | 13.6642 | 16.3658 | 16.2322 | 16.1071 | 16.0017 | 15.8994 | 15.8018 | 15.7081 | 15.663 | 15.639 | 15.6152 | 15.5921 | 15.4711 | 15.359 | 13.6458
|  | TAIN | CT |  |  |  | 17.6344 | 17.5154 | 17.4001 | 17.2885 | 17.1803 | 17.0771 | 16.9779 | 16.9303 | 16.905 | 16.8799 | 16.8557 | 16.7285 | 16.6108 | 16.5047 | 16.1919 | 16.0742 | 15.9569 | 15.885 | 15.8123 | 15.7458 | 15.6816 | 15.6464 | 15.6229 | 15.5992 | 15.5776 | 15.4861 | 15.4048 | 13.6642 | 16.3658 | 16.2322 | 16.1071 | 16.0017 | 15.8994 | 15.8018 | 15.7081 | 15.663 | 15.639 | 15.6152 | 15.5921 | 15.4711 | 15.359 | 13.6458
|  | TAIN | LW |  |  |  | 17.8411 | 17.8209 | 17.7966 | 17.77 | 17.7408 | 17.7112 | 17.6802 | 17.6521 | 17.6233 | 17.594 | 17.5645 | 17.3993 | 17.2558 | 17.1041 | 16.3529 | 16.3064 | 16.2344 | 16.1583 | 16.0969 | 16.066 | 16.0347 | 16.0082 | 15.9815 | 15.9546 | 15.9279 | 15.8008 | 15.7173 | 15.6288 | 16.5906 | 16.5635 | 16.5283 | 16.4902 | 16.4479 | 16.4071 | 16.3704 | 16.3437 | 16.3164 | 16.2886 | 16.2606 | 16.1034 | 15.9471 | 15.7839
|  | TAIN | ST |  |  |  | 17.8725 | 17.8648 | 17.8561 | 17.8472 | 17.8354 | 17.8245 | 17.814 | 17.8039 | 17.7905 | 17.7773 | 17.7647 | 17.7066 | 17.6534 | 17.6038 | 16.394 | 16.3795 | 16.3505 | 16.3171 | 16.265 | 16.222 | 16.1797 | 16.1407 | 16.1197 | 16.1033 | 16.0884 | 16.0193 | 15.9522 | 15.9201 | 16.6275 | 16.6177 | 16.6045 | 16.5905 | 16.5706 | 16.5531 | 16.5359 | 16.5199 | 16.4999 | 16.4803 | 16.462 | 16.3949 | 16.3441 | 16.2958
|  | TAIN | FS |  |  |  | 17.8663 | 17.8592 | 17.8481 | 17.8371 | 17.8256 | 17.8146 | 17.8035 | 17.7927 | 17.7821 | 17.7717 | 17.7615 | 17.7016 | 17.6482 | 17.5985 | 16.3977 | 16.3909 | 16.3736 | 16.3551 | 16.3301 | 16.3086 | 16.2845 | 16.2636 | 16.2431 | 16.2229 | 16.2034 | 16.1044 | 16.0524 | 16.0121 | 16.6221 | 16.6142 | 16.6007 | 16.5871 | 16.572 | 16.5578 | 16.5432 | 16.5294 | 16.5159 | 16.5026 | 16.4895 | 16.4157 | 16.3497 | 16.2936
| ARDMORE | TARBERT | MINIMUM HEADROOM | NB 15289 00157 | NO | YES | 1.7515 | 0.51807 | 0.51807 | 0.51807 | 0.51807 | 0.50685 | 0.47955 | 0.45 | 0.41862 | 0.38621 | 0.35135 | 0.21132 | 0.069866 | -0.06933 | 1.5343 | 0.60519 | 0.56618 | 0.52786 | 0.49027 | 0.45335 | 0.41713 | 0.3779 | 0.33892 | 0.30018 | 0.26169 | 0.10853 | -0.046174 | -0.19841 | 1.4999 | 0.39561 | 0.3636 | 0.32872 | 0.29414 | 0.26019 | 0.22687 | 0.19079 | 0.15494 | 0.11932 | 0.08392 | -0.072655 | -0.23442 | -0.3936
|  | TARBERT | CT |  |  |  | 1.7515 | 0.51807 | 0.51807 | 0.51807 | 0.51807 | 0.51807 | 0.51539 | 0.49242 | 0.4696 | 0.44693 | 0.4228 | 0.30936 | 0.19102 | 0.074651 | 1.5345 | 0.61077 | 0.58046 | 0.55072 | 0.52152 | 0.49285 | 0.46469 | 0.43421 | 0.40391 | 0.37382 | 0.34392 | 0.21577 | 0.086339 | -0.04094 | 1.4999 | 0.40019 | 0.37532 | 0.34974 | 0.32289 | 0.29651 | 0.27061 | 0.24258 | 0.21472 | 0.18705 | 0.15954 | 0.039469 | -0.09586 | -0.22894
|  | TARBERT | LW |  |  |  | 1.7515 | 0.51807 | 0.51807 | 0.51807 | 0.51807 | 0.50685 | 0.47955 | 0.45 | 0.41862 | 0.38621 | 0.35135 | 0.21132 | 0.069866 | -0.06933 | 1.5343 | 0.60519 | 0.56618 | 0.52786 | 0.49027 | 0.45335 | 0.41713 | 0.3779 | 0.33892 | 0.30018 | 0.26169 | 0.10853 | -0.046174 | -0.19841 | 1.4999 | 0.39561 | 0.3636 | 0.32872 | 0.29414 | 0.26019 | 0.22687 | 0.19079 | 0.15494 | 0.11932 | 0.08392 | -0.072655 | -0.23442 | -0.3936
|  | TARBERT | ST |  |  |  | 1.7515 | 1.7515 | 1.7515 | 1.7515 | 1.7515 | 1.7515 | 1.7515 | 1.7515 | 1.7515 | 1.7515 | 1.7515 | 1.7515 | 1.7515 | 1.7515 | 1.545 | 1.5439 | 1.5421 | 1.5399 | 1.5315 | 1.5232 | 1.5152 | 1.5065 | 1.4979 | 1.4936 | 1.4916 | 1.4816 | 1.4716 | 1.4645 | 1.5057 | 1.5051 | 1.5041 | 1.5029 | 1.4983 | 1.4942 | 1.4926 | 1.4909 | 1.4891 | 1.4885 | 1.4885 | 1.4885 | 1.4885 | 1.4885
|  | TARBERT | FS |  |  |  | 1.7515 | 1.7515 | 1.7515 | 1.7515 | 1.7515 | 1.7515 | 1.7515 | 1.7515 | 1.7515 | 1.7515 | 1.7515 | 1.7515 | 1.7515 | 1.7515 | 1.5457 | 1.5456 | 1.5451 | 1.5445 | 1.5414 | 1.5383 | 1.5343 | 1.5304 | 1.5266 | 1.5228 | 1.5191 | 1.5016 | 1.4925 | 1.4887 | 1.5061 | 1.506 | 1.5058 | 1.5054 | 1.5037 | 1.502 | 1.4998 | 1.4977 | 1.4956 | 1.4942 | 1.4934 | 1.4899 | 1.4885 | 1.4885
| PORT ANN | TARBERT JURA | MINIMUM HEADROOM | NR 60552 82166 | YES | YES | 0.16302 | 0.16302 | 0.16302 | 0.16302 | 0.16302 | 0.16302 | 0.16302 | 0.16302 | 0.16302 | 0.16302 | 0.16302 | 0.1411 | 0.12978 | 0.11865 | 0.15711 | 0.15689 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.14925 | 0.14823 | 0.14723 | 0.14623 | 0.13297 | 0.11961 | 0.10648 | 0.1584 | 0.15832 | 0.15825 | 0.15825 | 0.15825 | 0.15825 | 0.15825 | 0.14977 | 0.14876 | 0.14776 | 0.14676 | 0.13349 | 0.12013 | 0.10699
|  | TARBERT JURA | CT |  |  |  | 0.16302 | 0.16302 | 0.16302 | 0.16302 | 0.16302 | 0.16302 | 0.16302 | 0.16302 | 0.16302 | 0.16302 | 0.16302 | 0.14677 | 0.13864 | 0.13061 | 0.15712 | 0.15696 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.14988 | 0.14918 | 0.13966 | 0.13006 | 0.12059 | 0.15841 | 0.15835 | 0.15828 | 0.15825 | 0.15825 | 0.15825 | 0.15825 | 0.15825 | 0.15825 | 0.15825 | 0.14971 | 0.14018 | 0.13058 | 0.12111
|  | TARBERT JURA | LW |  |  |  | 0.16302 | 0.16302 | 0.16302 | 0.16302 | 0.16302 | 0.16302 | 0.16302 | 0.16302 | 0.16302 | 0.16302 | 0.16302 | 0.1411 | 0.12978 | 0.11865 | 0.15711 | 0.15689 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.14925 | 0.14823 | 0.14723 | 0.14623 | 0.13297 | 0.11961 | 0.10648 | 0.1584 | 0.15832 | 0.15825 | 0.15825 | 0.15825 | 0.15825 | 0.15825 | 0.14977 | 0.14876 | 0.14776 | 0.14676 | 0.13349 | 0.12013 | 0.10699
|  | TARBERT JURA | ST |  |  |  | 0.16302 | 0.16302 | 0.16302 | 0.16302 | 0.16302 | 0.16302 | 0.16302 | 0.16302 | 0.16302 | 0.16302 | 0.16302 | 0.14752 | 0.14254 | 0.13759 | 0.15722 | 0.15711 | 0.15701 | 0.15689 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.14897 | 0.14772 | 0.1465 | 0.14055 | 0.13467 | 0.12882 | 0.15843 | 0.1584 | 0.15837 | 0.15832 | 0.15825 | 0.15825 | 0.15825 | 0.15825 | 0.14949 | 0.14825 | 0.14703 | 0.14107 | 0.13519 | 0.12934
|  | TARBERT JURA | FS |  |  |  | 0.16302 | 0.16302 | 0.16302 | 0.16302 | 0.16302 | 0.16302 | 0.16302 | 0.16302 | 0.16302 | 0.16302 | 0.16302 | 0.16302 | 0.16302 | 0.16302 | 0.15729 | 0.15729 | 0.15723 | 0.15717 | 0.15704 | 0.15694 | 0.15681 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.14851 | 0.14652 | 0.15845 | 0.15844 | 0.15843 | 0.15841 | 0.15838 | 0.15834 | 0.1583 | 0.15825 | 0.15825 | 0.15825 | 0.15825 | 0.15825 | 0.14904 | 0.14704
| PORT ANN | TARBERT LOCH FYNE | MINIMUM HEADROOM | NR 86003 68479 | NO | YES | 3.1603 | 3.1603 | 3.1603 | 3.1603 | 3.1603 | 3.1603 | 3.1603 | 3.1603 | 3.1603 | 3.1603 | 3.1522 | 3.0545 | 2.9464 | 2.8313 | 3.1066 | 3.1066 | 3.1066 | 3.1066 | 3.1066 | 3.1066 | 3.1066 | 3.1066 | 3.1066 | 3.1066 | 3.1066 | 3.0408 | 2.9056 | 2.7722 | 3.0019 | 2.991 | 2.9778 | 2.9675 | 2.9572 | 2.947 | 2.9368 | 2.9268 | 2.9173 | 2.908 | 2.8988 | 2.8239 | 2.7485 | 2.6741
|  | TARBERT LOCH FYNE | CT |  |  |  | 3.1603 | 3.1603 | 3.1603 | 3.1603 | 3.1603 | 3.1603 | 3.1603 | 3.1603 | 3.1603 | 3.1603 | 3.1603 | 3.1016 | 3.0183 | 2.923 | 3.1066 | 3.1066 | 3.1066 | 3.1066 | 3.1066 | 3.1066 | 3.1066 | 3.1066 | 3.1066 | 3.1066 | 3.1066 | 3.1055 | 2.9912 | 2.8785 | 3.0033 | 2.9948 | 2.9851 | 2.9777 | 2.9698 | 2.9613 | 2.9528 | 2.9446 | 2.9374 | 2.9304 | 2.9237 | 2.86 | 2.7962 | 2.7334
|  | TARBERT LOCH FYNE | LW |  |  |  | 3.1603 | 3.1603 | 3.1603 | 3.1603 | 3.1603 | 3.1603 | 3.1603 | 3.1603 | 3.1603 | 3.1603 | 3.1522 | 3.0545 | 2.9464 | 2.8313 | 3.1066 | 3.1066 | 3.1066 | 3.1066 | 3.1066 | 3.1066 | 3.1066 | 3.1066 | 3.1066 | 3.1066 | 3.1066 | 3.0408 | 2.9056 | 2.7722 | 3.0019 | 2.991 | 2.9778 | 2.9675 | 2.9572 | 2.947 | 2.9368 | 2.9268 | 2.9173 | 2.908 | 2.8988 | 2.8239 | 2.7485 | 2.6741
|  | TARBERT LOCH FYNE | ST |  |  |  | 3.1603 | 3.1603 | 3.1603 | 3.1603 | 3.1603 | 3.1603 | 3.1603 | 3.1603 | 3.1603 | 3.1603 | 3.1603 | 3.1603 | 3.1251 | 3.0848 | 3.1066 | 3.1066 | 3.1066 | 3.1066 | 3.1066 | 3.1066 | 3.1066 | 3.1066 | 3.1066 | 3.1066 | 3.1066 | 3.1066 | 3.1066 | 3.0825 | 3.0078 | 3.0037 | 2.998 | 2.9931 | 2.9855 | 2.9775 | 2.9695 | 2.9615 | 2.9543 | 2.9473 | 2.9407 | 2.9089 | 2.878 | 2.8471
|  | TARBERT LOCH FYNE | FS |  |  |  | 3.1603 | 3.1603 | 3.1603 | 3.1603 | 3.1603 | 3.1603 | 3.1603 | 3.1603 | 3.1603 | 3.1603 | 3.1603 | 3.1603 | 3.1603 | 3.1603 | 3.1066 | 3.1066 | 3.1066 | 3.1066 | 3.1066 | 3.1066 | 3.1066 | 3.1066 | 3.1066 | 3.1066 | 3.1066 | 3.1066 | 3.1066 | 3.1066 | 3.0115 | 3.0102 | 3.008 | 3.0063 | 3.0036 | 3.0009 | 2.9976 | 2.9945 | 2.9916 | 2.9887 | 2.986 | 2.9735 | 2.9621 | 2.9516
| TAYNUILT | TAYNUILT | MINIMUM HEADROOM | NN 01856 31079 | NO | YES | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 1.7621 | 1.6337 | 2.233 | 2.2326 | 2.2321 | 2.2316 | 2.2312 | 2.2305 | 2.2295 | 2.2285 | 2.2274 | 2.2264 | 2.2253 | 2.2177 | 1.6949 | 1.5815
|  | TAYNUILT | CT |  |  |  | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 1.7626 | 2.233 | 2.2327 | 2.2324 | 2.2321 | 2.2317 | 2.2314 | 2.2311 | 2.2308 | 2.2304 | 2.2301 | 2.2297 | 2.2222 | 1.7761 | 1.6954
|  | TAYNUILT | LW |  |  |  | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 1.7621 | 1.6337 | 2.233 | 2.2326 | 2.2321 | 2.2316 | 2.2312 | 2.2307 | 2.2303 | 2.2298 | 2.2293 | 2.2288 | 2.2283 | 2.2177 | 1.6949 | 1.5815
|  | TAYNUILT | ST |  |  |  | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2331 | 2.233 | 2.2328 | 2.2326 | 2.2316 | 2.2305 | 2.2295 | 2.2285 | 2.2274 | 2.2264 | 2.2253 | 2.2203 | 1.785 | 1.7318
|  | TAYNUILT | FS |  |  |  | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.4418 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2974 | 2.2332 | 2.2332 | 2.2331 | 2.2331 | 2.2327 | 2.2324 | 2.232 | 2.2316 | 2.2313 | 2.2309 | 2.2305 | 2.2287 | 2.227 | 2.2255
| BURGHMUIR | THIMBLEROW | MINIMUM HEADROOM | NO 11356 23764 | NO | YES | 21.2829 | 21.197 | 19.9975 | 19.7936 | 19.5921 | 19.3978 | 19.2081 | 19.0437 | 18.9021 | 18.7593 | 18.6153 | 17.6787 | 16.6502 | 15.6457 | 20.8196 | 20.7289 | 20.68 | 19.8883 | 19.6835 | 19.4858 | 19.2922 | 19.1141 | 18.9421 | 18.716 | 18.488 | 17.3268 | 16.1664 | 15.0363 | 25.3242 | 25.2126 | 25.1064 | 25.0032 | 24.9028 | 24.8062 | 24.7129 | 24.6504 | 24.6082 | 24.5659 | 24.5236 | 24.329 | 24.222 | 19.3115
|  | THIMBLEROW | CT |  |  |  | 21.2829 | 21.197 | 19.9975 | 19.7936 | 19.5921 | 19.3978 | 19.2081 | 19.0437 | 18.9021 | 18.7593 | 18.6153 | 17.9629 | 17.3198 | 16.6917 | 20.8196 | 20.7289 | 20.68 | 19.8883 | 19.6835 | 19.4858 | 19.2922 | 19.1141 | 18.9542 | 18.7928 | 18.6299 | 17.8933 | 17.169 | 16.4651 | 25.3242 | 25.2126 | 25.1064 | 25.0032 | 24.9028 | 24.8062 | 24.7129 | 24.6504 | 24.6082 | 24.5659 | 24.5236 | 24.329 | 24.222 | 24.1223
|  | THIMBLEROW | LW |  |  |  | 21.435 | 21.4222 | 21.4076 | 21.3917 | 19.8624 | 19.6787 | 19.4959 | 19.2979 | 19.101 | 18.9023 | 18.7017 | 17.6787 | 16.6502 | 15.6457 | 20.9404 | 20.8728 | 20.8562 | 20.8465 | 19.81 | 19.6001 | 19.3918 | 19.166 | 18.9421 | 18.716 | 18.488 | 17.3268 | 16.1664 | 15.0363 | 25.4861 | 25.4466 | 25.3995 | 25.3511 | 25.3012 | 25.2508 | 25.1998 | 25.1445 | 25.0889 | 25.0325 | 24.9755 | 24.8289 | 24.6827 | 19.3115
|  | THIMBLEROW | ST |  |  |  | 21.4571 | 21.452 | 21.447 | 21.4421 | 21.4362 | 21.4304 | 21.4249 | 21.4197 | 19.9739 | 19.8755 | 19.777 | 19.29 | 18.8272 | 18.3742 | 20.9802 | 20.9578 | 20.9257 | 20.8879 | 20.8736 | 20.8701 | 20.8667 | 20.8636 | 19.9245 | 19.8107 | 19.6968 | 19.1353 | 18.6006 | 18.0788 | 25.5189 | 25.5058 | 25.4887 | 25.4694 | 25.4464 | 25.4241 | 25.4023 | 25.3796 | 25.3547 | 25.33 | 25.3054 | 25.181 | 25.0645 | 25.0014
|  | THIMBLEROW | FS |  |  |  | 21.452 | 21.4468 | 21.4392 | 21.4317 | 21.4243 | 21.417 | 21.4099 | 21.4028 | 21.3958 | 21.3889 | 21.3821 | 21.3413 | 19.9139 | 19.7327 | 20.987 | 20.9809 | 20.9659 | 20.9494 | 20.931 | 20.913 | 20.8918 | 20.8708 | 20.8562 | 20.8481 | 20.8406 | 20.8158 | 19.9077 | 19.7115 | 25.518 | 25.5116 | 25.4998 | 25.4874 | 25.4743 | 25.4615 | 25.4474 | 25.4334 | 25.4198 | 25.4062 | 25.3927 | 25.319 | 25.2461 | 25.1771
| TAYNUILT | TIRORAN BRIDGE | MINIMUM HEADROOM | NM 48666 28729 | YES | YES | 0.28122 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.191 | 0.22512 | 0.22469 | 0.22437 | 0.22405 | 0.22375 | 0.22355 | 0.22355 | 0.22355 | 0.22355 | 0.22355 | 0.22355 | 0.19566 | 0.18104 | 0.16669 | 0.22927 | 0.22918 | 0.22907 | 0.22896 | 0.22885 | 0.22875 | 0.22864 | 0.22864 | 0.22864 | 0.22864 | 0.22864 | 0.19749 | 0.18287 | 0.16851
|  | TIRORAN BRIDGE | CT |  |  |  | 0.28122 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.22515 | 0.22477 | 0.22454 | 0.22432 | 0.22411 | 0.2239 | 0.22369 | 0.22355 | 0.22355 | 0.22355 | 0.22355 | 0.22355 | 0.19229 | 0.18167 | 0.22927 | 0.22921 | 0.22913 | 0.22905 | 0.22898 | 0.2289 | 0.22883 | 0.22875 | 0.22868 | 0.22864 | 0.22864 | 0.22864 | 0.19412 | 0.1835
|  | TIRORAN BRIDGE | LW |  |  |  | 0.28122 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.191 | 0.22512 | 0.22469 | 0.22437 | 0.22405 | 0.22375 | 0.22355 | 0.22355 | 0.22355 | 0.22355 | 0.22355 | 0.22355 | 0.19566 | 0.18104 | 0.16669 | 0.22927 | 0.22918 | 0.22907 | 0.22896 | 0.22885 | 0.22875 | 0.22864 | 0.22864 | 0.22864 | 0.22864 | 0.22864 | 0.19749 | 0.18287 | 0.16851
|  | TIRORAN BRIDGE | ST |  |  |  | 0.28122 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.22528 | 0.22513 | 0.22489 | 0.22469 | 0.22434 | 0.224 | 0.22367 | 0.22355 | 0.22355 | 0.22355 | 0.22355 | 0.22355 | 0.19901 | 0.19278 | 0.22932 | 0.22927 | 0.22923 | 0.22918 | 0.22906 | 0.22894 | 0.22882 | 0.2287 | 0.22864 | 0.22864 | 0.22864 | 0.22864 | 0.22864 | 0.19461
|  | TIRORAN BRIDGE | FS |  |  |  | 0.28122 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.24522 | 0.22536 | 0.22535 | 0.22529 | 0.22521 | 0.22499 | 0.22477 | 0.22462 | 0.22448 | 0.22434 | 0.2242 | 0.22407 | 0.22355 | 0.22355 | 0.22355 | 0.22936 | 0.22935 | 0.22932 | 0.22929 | 0.22925 | 0.22921 | 0.22916 | 0.22911 | 0.22906 | 0.22901 | 0.22896 | 0.22874 | 0.22864 | 0.22864
| BOAT OF GARTEN | TOMATIN | MINIMUM HEADROOM | NH 79106 29734 | YES | YES | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.4945 | 1.4934 | 1.4921 | 1.4908 | 1.4699 | 1.4684 | 1.4489 | 1.4442 | 1.4442 | 1.4442 | 1.4442 | 1.4442 | 1.4442 | 1.4442 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124
|  | TOMATIN | CT |  |  |  | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.4945 | 1.4937 | 1.4928 | 1.4919 | 1.4734 | 1.4726 | 1.4538 | 1.4454 | 1.4442 | 1.4442 | 1.4442 | 1.4442 | 1.4442 | 1.4442 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124
|  | TOMATIN | LW |  |  |  | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.4945 | 1.4934 | 1.4921 | 1.4908 | 1.4699 | 1.4684 | 1.4489 | 1.4442 | 1.4442 | 1.4442 | 1.4442 | 1.4442 | 1.4442 | 1.4442 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124
|  | TOMATIN | ST |  |  |  | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.4948 | 1.4945 | 1.494 | 1.4934 | 1.4784 | 1.4751 | 1.4599 | 1.4499 | 1.4448 | 1.4442 | 1.4442 | 1.4442 | 1.4442 | 1.4442 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124
|  | TOMATIN | FS |  |  |  | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.6983 | 1.495 | 1.495 | 1.4948 | 1.4947 | 1.4888 | 1.4875 | 1.4802 | 1.4734 | 1.4669 | 1.465 | 1.4628 | 1.4535 | 1.4506 | 1.4483 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124 | 1.4124
| LAIRG | TORBOLL | MINIMUM HEADROOM | NC 75779 00296 | YES | YES | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.099725 | 0.10188 | 0.10185 | 0.10182 | 0.10178 | 0.10176 | 0.10173 | 0.10171 | 0.1017 | 0.10169 | 0.10169 | 0.10168 | 0.099859 | 0.098826 | 0.097826 | 0.10213 | 0.10211 | 0.1021 | 0.1021 | 0.1021 | 0.1021 | 0.1021 | 0.1021 | 0.1021 | 0.1021 | 0.1021 | 0.1021 | 0.099198 | 0.098197
|  | TORBOLL | CT |  |  |  | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10188 | 0.10186 | 0.10184 | 0.10181 | 0.10179 | 0.10177 | 0.10175 | 0.10173 | 0.10172 | 0.1017 | 0.1017 | 0.10168 | 0.099613 | 0.098888 | 0.10213 | 0.10212 | 0.1021 | 0.1021 | 0.1021 | 0.1021 | 0.1021 | 0.1021 | 0.1021 | 0.1021 | 0.1021 | 0.1021 | 0.099967 | 0.09926
|  | TORBOLL | LW |  |  |  | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.099725 | 0.10188 | 0.10185 | 0.10182 | 0.10178 | 0.10176 | 0.10173 | 0.10171 | 0.1017 | 0.10169 | 0.10169 | 0.10168 | 0.099859 | 0.098826 | 0.097826 | 0.10213 | 0.10211 | 0.1021 | 0.1021 | 0.1021 | 0.1021 | 0.1021 | 0.1021 | 0.1021 | 0.1021 | 0.1021 | 0.1021 | 0.099198 | 0.098197
|  | TORBOLL | ST |  |  |  | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10189 | 0.10188 | 0.10187 | 0.10185 | 0.1018 | 0.10176 | 0.10173 | 0.1017 | 0.10169 | 0.10169 | 0.10168 | 0.10168 | 0.099927 | 0.09949 | 0.10213 | 0.10213 | 0.10212 | 0.10211 | 0.1021 | 0.1021 | 0.1021 | 0.1021 | 0.1021 | 0.1021 | 0.1021 | 0.1021 | 0.1021 | 0.099847
|  | TORBOLL | FS |  |  |  | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10333 | 0.10189 | 0.10189 | 0.10189 | 0.10188 | 0.10187 | 0.10185 | 0.10183 | 0.10182 | 0.1018 | 0.10178 | 0.10176 | 0.1017 | 0.10169 | 0.10168 | 0.10213 | 0.10213 | 0.10213 | 0.10213 | 0.10212 | 0.10211 | 0.1021 | 0.1021 | 0.1021 | 0.1021 | 0.1021 | 0.1021 | 0.1021 | 0.1021
| KINTORE | TORRYBURN | MINIMUM HEADROOM | NJ 79129 15653 | NO | YES | 29.7968 | 29.5764 | 29.3941 | 29.2707 | 29.1503 | 29.0326 | 28.9331 | 28.8916 | 28.871 | 28.8505 | 28.8304 | 28.3473 | 22.6349 | 21.5037 | 25.7789 | 25.6486 | 25.5678 | 25.5244 | 25.4825 | 21.8108 | 21.4091 | 20.9744 | 20.5454 | 20.1143 | 19.6862 | 18.1212 | 16.4998 | 15.2413 | 26.4624 | 26.3735 | 26.2901 | 26.2097 | 26.1322 | 26.0578 | 21.907 | 21.5256 | 21.1489 | 20.7485 | 20.3246 | 18.6559 | 16.9145 | 15.643
|  | TORRYBURN | CT |  |  |  | 29.7968 | 29.5764 | 29.3941 | 29.2707 | 29.1503 | 29.0326 | 28.9331 | 28.8916 | 28.871 | 28.8505 | 28.8304 | 28.3473 | 27.818 | 27.7097 | 25.7789 | 25.6486 | 25.5678 | 25.5244 | 25.4825 | 25.4422 | 25.4036 | 22.0064 | 21.7953 | 21.5819 | 21.3707 | 20.1925 | 18.9727 | 18.1135 | 26.4624 | 26.3735 | 26.2901 | 26.2097 | 26.1322 | 26.0578 | 25.9863 | 25.9457 | 22.0053 | 21.8147 | 21.626 | 20.4309 | 19.1813 | 18.3253
|  | TORRYBURN | LW |  |  |  | 29.9036 | 29.6824 | 29.5897 | 29.5347 | 29.5164 | 29.4968 | 29.4761 | 29.4529 | 29.429 | 29.4045 | 29.3798 | 28.8628 | 22.6349 | 21.5037 | 25.8761 | 25.746 | 25.7373 | 25.7276 | 25.7172 | 21.8108 | 21.4091 | 20.9744 | 20.5454 | 20.1143 | 19.6862 | 18.1212 | 16.4998 | 15.2413 | 26.6199 | 26.6066 | 26.5916 | 26.575 | 26.5571 | 26.5379 | 21.907 | 21.5256 | 21.1489 | 20.7485 | 20.3246 | 18.6559 | 16.9145 | 15.643
|  | TORRYBURN | ST |  |  |  | 30.0053 | 29.9139 | 29.7745 | 29.6878 | 29.6544 | 29.6317 | 29.6105 | 29.5884 | 29.5643 | 29.5482 | 29.5404 | 29.3052 | 29.052 | 29.0091 | 25.9308 | 25.8862 | 25.8191 | 25.758 | 25.7544 | 25.751 | 25.7476 | 25.7444 | 25.7398 | 25.7353 | 25.7309 | 21.8617 | 21.1252 | 20.5697 | 26.6428 | 26.6374 | 26.6323 | 26.6272 | 26.6211 | 26.6151 | 26.6094 | 26.6039 | 26.5959 | 26.5882 | 26.5806 | 26.3504 | 21.5008 | 21.0083
|  | TORRYBURN | FS |  |  |  | 30.2291 | 30.1591 | 30.1152 | 30.0646 | 30.0284 | 29.9922 | 29.949 | 29.9063 | 29.8649 | 29.8234 | 29.7826 | 29.6134 | 29.523 | 29.4407 | 26.0346 | 26 | 25.9771 | 25.9509 | 25.9316 | 25.9123 | 25.8897 | 25.8675 | 25.8458 | 25.8241 | 25.8028 | 25.6974 | 25.6718 | 25.647 | 26.6374 | 26.6321 | 26.6243 | 26.6165 | 26.6088 | 26.6013 | 26.5938 | 26.5865 | 26.5793 | 26.5721 | 26.5651 | 26.5229 | 26.4788 | 26.4362
| LAIRG | TRESSADY | MINIMUM HEADROOM | NC 70537 03678 | YES | YES | 0.67183 | 0.67183 | 1.1718 | 1.1718 | 1.1718 | 1.1718 | 1.1718 | 1.1718 | 1.1718 | 1.1718 | 1.1718 | 1.1718 | 0.99017 | 0.92179 | 0.59377 | 0.59276 | 1.0915 | 1.0903 | 1.089 | 1.0863 | 1.0847 | 1.084 | 1.0839 | 1.0839 | 1.0839 | 0.9713 | 0.8894 | 0.80911 | 0.60596 | 0.60547 | 1.1049 | 1.1043 | 1.1043 | 1.1043 | 1.1043 | 1.1043 | 1.1043 | 1.1043 | 1.1043 | 0.98918 | 0.90788 | 0.82757
|  | TRESSADY | CT |  |  |  | 0.67183 | 0.67183 | 1.1718 | 1.1718 | 1.1718 | 1.1718 | 1.1718 | 1.1718 | 1.1718 | 1.1718 | 1.1718 | 1.1718 | 1.1718 | 0.95548 | 0.59383 | 0.59307 | 1.0922 | 1.0913 | 1.0905 | 1.0896 | 1.0888 | 1.088 | 1.0873 | 1.0866 | 1.086 | 0.98956 | 0.91853 | 0.84867 | 0.60599 | 0.60562 | 1.1052 | 1.1048 | 1.1044 | 1.1043 | 1.1043 | 1.1043 | 1.1043 | 1.1043 | 1.1043 | 1.1043 | 0.93702 | 0.86713
|  | TRESSADY | LW |  |  |  | 0.67183 | 0.67183 | 1.1718 | 1.1718 | 1.1718 | 1.1718 | 1.1718 | 1.1718 | 1.1718 | 1.1718 | 1.1718 | 1.1718 | 0.99017 | 0.92179 | 0.59377 | 0.59276 | 1.0915 | 1.0903 | 1.089 | 1.0879 | 1.087 | 1.0861 | 1.0851 | 1.0848 | 1.0845 | 0.9713 | 0.8894 | 0.80911 | 0.60596 | 0.60547 | 1.1049 | 1.1043 | 1.1043 | 1.1043 | 1.1043 | 1.1043 | 1.1043 | 1.1043 | 1.1043 | 0.98918 | 0.90788 | 0.82757
|  | TRESSADY | ST |  |  |  | 0.67183 | 0.67183 | 1.1718 | 1.1718 | 1.1718 | 1.1718 | 1.1718 | 1.1718 | 1.1718 | 1.1718 | 1.1718 | 1.1718 | 1.1718 | 1.1718 | 0.59409 | 0.59379 | 1.0933 | 1.0927 | 1.0892 | 1.0863 | 1.0847 | 1.084 | 1.0839 | 1.0839 | 1.0839 | 0.98944 | 0.95467 | 0.9201 | 0.60612 | 0.60597 | 1.1057 | 1.1055 | 1.1043 | 1.1043 | 1.1043 | 1.1043 | 1.1043 | 1.1043 | 1.1043 | 1.1043 | 0.97299 | 0.93859
|  | TRESSADY | FS |  |  |  | 0.67183 | 0.67183 | 1.1718 | 1.1718 | 1.1718 | 1.1718 | 1.1718 | 1.1718 | 1.1718 | 1.1718 | 1.1718 | 1.1718 | 1.1718 | 1.1718 | 0.59426 | 0.59424 | 1.0941 | 1.094 | 1.0928 | 1.0916 | 1.0901 | 1.0887 | 1.0875 | 1.0864 | 1.0854 | 1.0839 | 1.0839 | 1.0839 | 0.6062 | 0.60619 | 1.1061 | 1.1061 | 1.1055 | 1.1049 | 1.1043 | 1.1043 | 1.1043 | 1.1043 | 1.1043 | 1.1043 | 1.1043 | 1.1043
| SHETLAND | TUMBLIN | MINIMUM HEADROOM | HU3334053363 | YES | YES | 7.3322 | 7.261 | 7.1964 | 7.1342 | 7.0743 | 7.0167 | 6.9614 | 6.9314 | 6.9165 | 6.9018 | 6.8872 | 6.8189 | 5.8377 | 5.6442 | 6.8109 | 6.7468 | 6.6902 | 6.655 | 6.6212 | 6.5886 | 6.5573 | 6.5397 | 6.5305 | 6.5219 | 6.5145 | 6.48 | 5.8327 | 5.6543 | 6.8945 | 6.8163 | 6.7453 | 6.6768 | 6.6109 | 6.5476 | 6.4867 | 6.4535 | 6.4369 | 5.9876 | 5.9684 | 5.7744 | 5.5778 | 5.3789
|  | TUMBLIN | CT |  |  |  | 7.3322 | 7.261 | 7.1964 | 7.1342 | 7.0743 | 7.0167 | 6.9614 | 6.9314 | 6.9165 | 6.9018 | 6.8872 | 6.8189 | 5.8377 | 5.6442 | 6.8109 | 6.7468 | 6.6902 | 6.655 | 6.6212 | 6.5886 | 6.5573 | 6.5397 | 6.5305 | 6.5219 | 6.5145 | 6.48 | 5.8327 | 5.6543 | 6.8945 | 6.8163 | 6.7453 | 6.6768 | 6.6109 | 6.5476 | 6.4867 | 6.4535 | 6.4369 | 5.9876 | 5.9684 | 5.7744 | 5.5778 | 5.3789
|  | TUMBLIN | LW |  |  |  | 7.4582 | 7.4475 | 7.4355 | 7.4222 | 7.4079 | 7.3926 | 7.3764 | 7.359 | 7.3411 | 7.3228 | 7.3043 | 7.2063 | 7.0966 | 5.9094 | 6.9212 | 6.9096 | 6.8961 | 6.8816 | 6.8664 | 6.8503 | 6.8335 | 6.8155 | 6.7972 | 6.7786 | 6.7599 | 6.6758 | 6.6203 | 5.7929 | 7.0324 | 7.0203 | 7.0066 | 6.9916 | 6.9754 | 6.9581 | 6.9399 | 6.9204 | 6.9004 | 6.8799 | 6.8591 | 6.737 | 5.8775 | 5.6073
|  | TUMBLIN | ST |  |  |  | 7.4765 | 7.4722 | 7.4681 | 7.464 | 7.4591 | 7.4544 | 7.4497 | 7.4455 | 7.4393 | 7.4333 | 7.4275 | 7.3958 | 7.3675 | 7.3375 | 6.938 | 6.9336 | 6.9288 | 6.9239 | 6.9123 | 6.9008 | 6.8896 | 6.8782 | 6.8654 | 6.8528 | 6.8405 | 6.7775 | 6.7573 | 6.7421 | 7.0526 | 7.0478 | 7.043 | 7.0384 | 7.0317 | 7.0251 | 7.0187 | 7.0127 | 7.0046 | 6.9967 | 6.989 | 6.9478 | 6.9105 | 6.8714
|  | TUMBLIN | FS |  |  |  | 7.4722 | 7.468 | 7.4617 | 7.4555 | 7.4493 | 7.4433 | 7.4373 | 7.4314 | 7.4256 | 7.4199 | 7.4143 | 7.3806 | 7.3457 | 7.3121 | 6.9346 | 6.9308 | 6.925 | 6.9191 | 6.9113 | 6.9036 | 6.8953 | 6.8871 | 6.879 | 6.8711 | 6.8634 | 6.8203 | 6.7772 | 6.7359 | 7.048 | 7.0433 | 7.0363 | 7.0295 | 7.0223 | 7.0153 | 7.0082 | 7.0012 | 6.9943 | 6.9875 | 6.9808 | 6.9414 | 6.901 | 6.862
| TUMMEL BRIDGE | TUMMEL BRIDGE | MINIMUM HEADROOM | NN 75906 59080 | YES | YES | 0.41704 | 0.010639 | -0.40235 | -0.80064 | -1.1842 | -1.5531 | -1.9074 | -2.0615 | -2.1406 | -2.219 | -2.2963 | -2.6938 | -3.0281 | -3.3589 | 0.54038 | 0.20314 | -0.12565 | -0.44276 | -0.7482 | -1.042 | -1.3251 | -1.4505 | -1.5157 | -1.5803 | -1.6439 | -1.9751 | -2.2555 | -2.533 | 0.28207 | -0.12932 | -0.54592 | -0.94796 | -1.3352 | -1.7075 | -2.065 | -2.2203 | -2.2999 | -2.3786 | -2.4562 | -2.8546 | -3.189 | -3.5245
|  | TUMMEL BRIDGE | CT |  |  |  | 0.41704 | 0.010639 | -0.40235 | -0.80064 | -1.1842 | -1.5531 | -1.9074 | -2.0615 | -2.1406 | -2.219 | -2.2963 | -2.6938 | -3.0281 | -3.3589 | 0.54038 | 0.20314 | -0.12565 | -0.44276 | -0.7482 | -1.042 | -1.3251 | -1.4505 | -1.5157 | -1.5803 | -1.6439 | -1.9751 | -2.2555 | -2.533 | 0.28207 | -0.12932 | -0.54592 | -0.94796 | -1.3352 | -1.7075 | -2.065 | -2.2203 | -2.2999 | -2.3786 | -2.4562 | -2.8546 | -3.189 | -3.5245
|  | TUMMEL BRIDGE | LW |  |  |  | 1.4413 | 1.3826 | 0.95231 | 0.88367 | 0.80932 | 0.7299 | 0.64604 | 0.5649 | 0.47475 | 0.38289 | 0.28998 | -0.21768 | -0.67432 | -1.1579 | 1.3676 | 1.3277 | 0.99523 | 0.92891 | 0.85798 | 0.783 | 0.7025 | 0.63098 | 0.55762 | 0.4829 | 0.40736 | -0.0091012 | -0.38519 | -0.78852 | 0.99586 | 0.93288 | 0.86171 | 0.78365 | 0.6994 | 0.60968 | 0.50736 | 0.41905 | 0.32842 | 0.2361 | 0.14276 | -0.37203 | -0.83593 | -1.3268
|  | TUMMEL BRIDGE | ST |  |  |  | 1.5419 | 1.5185 | 1.4957 | 1.4735 | 1.4465 | 1.4203 | 1.3949 | 1.3699 | 0.96831 | 0.93492 | 0.90247 | 0.76373 | 0.60176 | 0.46061 | 1.4294 | 1.414 | 1.3981 | 1.3821 | 1.362 | 1.3425 | 1.3234 | 1.3044 | 0.98702 | 0.95293 | 0.91972 | 0.77509 | 0.64449 | 0.52927 | 1.341 | 1.3209 | 1.3012 | 1.282 | 0.99661 | 0.96758 | 0.93937 | 0.91151 | 0.87184 | 0.83324 | 0.79556 | 0.61183 | 0.4467 | 0.30214
|  | TUMMEL BRIDGE | FS |  |  |  | 1.5185 | 1.4951 | 1.4604 | 1.4263 | 1.3925 | 0.99267 | 0.96179 | 0.93133 | 0.90131 | 0.87172 | 0.84256 | 0.66773 | 0.52583 | 0.37336 | 1.4162 | 1.4021 | 1.3807 | 1.3595 | 1.338 | 1.3168 | 1.2955 | 0.9862 | 0.95858 | 0.93135 | 0.90453 | 0.74286 | 0.60578 | 0.48179 | 1.3211 | 1.3011 | 1.2715 | 0.98083 | 0.94542 | 0.91049 | 0.87585 | 0.84168 | 0.80801 | 0.77483 | 0.74212 | 0.54704 | 0.38526 | 0.23024
| MACDUFF | TURRIFF | MINIMUM HEADROOM | NJ 72407 50271 | NO | YES | 24.6169 | 24.5964 | 24.5726 | 24.5486 | 24.5247 | 24.5008 | 24.4772 | 24.4517 | 24.4275 | 24.4275 | 23.7116 | 14.2536 | 11.3103 | 11.3103 | 21.0123 | 20.9415 | 20.8592 | 20.7767 | 20.7096 | 20.7096 | 20.7096 | 20.7096 | 20.7096 | 20.7096 | 20.3454 | 12.1929 | 8.8183 | 8.2023 | 21.0049 | 20.9583 | 20.9042 | 20.8613 | 20.8267 | 20.7919 | 20.7578 | 20.7209 | 20.6848 | 20.6483 | 19.9459 | 13.7086 | 9.6402 | 8.9961
|  | TURRIFF | CT |  |  |  | 24.6169 | 24.5964 | 24.5726 | 24.5486 | 24.5247 | 24.5008 | 24.4772 | 24.4517 | 24.4275 | 24.4275 | 23.7116 | 14.2536 | 11.3103 | 11.3103 | 21.0123 | 20.9415 | 20.8592 | 20.7767 | 20.7096 | 20.7096 | 20.7096 | 20.7096 | 20.7096 | 20.7096 | 20.3454 | 12.1929 | 8.8183 | 8.2023 | 21.0049 | 20.9583 | 20.9042 | 20.8613 | 20.8267 | 20.7919 | 20.7578 | 20.7209 | 20.6848 | 20.6483 | 19.9459 | 13.7086 | 9.6402 | 8.9961
|  | TURRIFF | LW |  |  |  | 24.6235 | 24.612 | 24.5974 | 24.5826 | 24.5676 | 24.5522 | 24.5371 | 24.5209 | 24.5052 | 24.4891 | 23.8045 | 14.2536 | 11.3103 | 11.3103 | 21.0349 | 20.9951 | 20.945 | 20.8939 | 20.842 | 20.7891 | 20.737 | 20.7096 | 20.7096 | 20.7096 | 20.3454 | 12.6389 | 9.1334 | 8.3896 | 21.0198 | 20.9936 | 20.9607 | 20.927 | 20.8929 | 20.8665 | 20.8446 | 20.8211 | 20.7984 | 20.775 | 20.0857 | 18.4664 | 9.9696 | 9.192
|  | TURRIFF | ST |  |  |  | 24.6275 | 24.6245 | 24.6198 | 24.6139 | 24.6031 | 24.5922 | 24.5815 | 24.57 | 24.5588 | 24.5475 | 24.2021 | 23.4031 | 13.8657 | 13.8657 | 21.0489 | 21.0384 | 21.022 | 21.0018 | 20.9646 | 20.927 | 20.8901 | 20.8502 | 20.8119 | 20.7727 | 20.528 | 20.1219 | 12.7727 | 12.4639 | 21.029 | 21.0221 | 21.0113 | 20.998 | 20.9735 | 20.9488 | 20.9245 | 20.8983 | 20.8761 | 20.8596 | 20.5104 | 19.6897 | 18.1532 | 18.1117
|  | TURRIFF | FS |  |  |  | 24.6791 | 24.6787 | 24.6772 | 24.6753 | 24.6716 | 24.6678 | 24.6631 | 24.6585 | 24.654 | 24.6494 | 24.6449 | 24.6232 | 24.6025 | 24.583 | 21.2268 | 21.2254 | 21.2201 | 21.2137 | 21.2008 | 21.1878 | 21.1716 | 21.1555 | 21.1399 | 21.1242 | 21.1088 | 21.0339 | 20.9626 | 20.8952 | 21.1461 | 21.1452 | 21.1417 | 21.1375 | 21.129 | 21.1204 | 21.1098 | 21.0992 | 21.0889 | 21.0786 | 21.0684 | 21.0191 | 20.9722 | 20.9279
| RANNOCH | TYNDRUM | MINIMUM HEADROOM | NN 32894 30860 | YES | YES | 3.2292 | 3.2289 | 3.2286 | 3.2283 | 3.2279 | 3.2275 | 3.2272 | 3.2268 | 3.2264 | 3.226 | 3.226 | 3.226 | 3.226 | 3.226 | 2.9152 | 2.9151 | 2.9149 | 2.9146 | 2.9144 | 2.9142 | 2.914 | 2.9137 | 2.9135 | 2.9132 | 2.913 | 2.9117 | 2.9104 | 2.9091 | 3.0466 | 3.0459 | 3.0449 | 3.0439 | 3.0429 | 3.0419 | 3.0409 | 3.0398 | 3.0387 | 3.0376 | 3.0365 | 3.0309 | 3.0252 | 3.0194
|  | TYNDRUM | CT |  |  |  | 3.2292 | 3.229 | 3.2288 | 3.2285 | 3.2283 | 3.228 | 3.2278 | 3.2275 | 3.2272 | 3.2269 | 3.2266 | 3.226 | 3.226 | 3.226 | 2.9152 | 2.9151 | 2.915 | 2.9148 | 2.9146 | 2.9145 | 2.9143 | 2.9142 | 2.914 | 2.9138 | 2.9136 | 2.9127 | 2.9117 | 2.9108 | 3.0467 | 3.0461 | 3.0454 | 3.0447 | 3.044 | 3.0433 | 3.0426 | 3.0418 | 3.041 | 3.0402 | 3.0394 | 3.0352 | 3.031 | 3.0268
|  | TYNDRUM | LW |  |  |  | 3.2292 | 3.2289 | 3.2286 | 3.2283 | 3.2279 | 3.2275 | 3.2272 | 3.2268 | 3.2264 | 3.226 | 3.226 | 3.226 | 3.226 | 3.226 | 2.9152 | 2.9151 | 2.9149 | 2.9146 | 2.9144 | 2.9142 | 2.914 | 2.9137 | 2.9135 | 2.9132 | 2.913 | 2.9117 | 2.9104 | 2.9091 | 3.0466 | 3.0459 | 3.0449 | 3.0439 | 3.0429 | 3.0419 | 3.0409 | 3.0398 | 3.0387 | 3.0376 | 3.0365 | 3.0309 | 3.0252 | 3.0194
|  | TYNDRUM | ST |  |  |  | 3.2293 | 3.2292 | 3.2291 | 3.2289 | 3.2288 | 3.2286 | 3.2284 | 3.2282 | 3.228 | 3.2279 | 3.2277 | 3.2267 | 3.226 | 3.226 | 2.9153 | 2.9152 | 2.9152 | 2.9151 | 2.9149 | 2.9148 | 2.9147 | 2.9146 | 2.9145 | 2.9144 | 2.9143 | 2.9136 | 2.9131 | 2.9125 | 3.0469 | 3.0466 | 3.0463 | 3.0458 | 3.0453 | 3.0448 | 3.0444 | 3.0439 | 3.0433 | 3.0428 | 3.0423 | 3.0395 | 3.0369 | 3.0342
|  | TYNDRUM | FS |  |  |  | 3.2293 | 3.2293 | 3.2293 | 3.2293 | 3.2292 | 3.2291 | 3.2291 | 3.229 | 3.2289 | 3.2289 | 3.2288 | 3.2284 | 3.228 | 3.2277 | 2.9153 | 2.9153 | 2.9153 | 2.9153 | 2.9152 | 2.9152 | 2.9151 | 2.9151 | 2.9151 | 2.915 | 2.915 | 2.9147 | 2.9145 | 2.9143 | 3.047 | 3.047 | 3.0469 | 3.0467 | 3.0466 | 3.0464 | 3.0462 | 3.046 | 3.0458 | 3.0456 | 3.0454 | 3.0443 | 3.0433 | 3.0422
| DUNVEGAN | UIG | MINIMUM HEADROOM | NG 39131 64412 | YES | YES | 3.1927 | 3.0762 | 2.9657 | 2.4587 | 2.3624 | 2.2687 | 2.1522 | 2.0873 | 2.0448 | 2.0023 | 1.9564 | 1.7401 | 1.5359 | 1.3323 | 3.1676 | 3.0965 | 3.0287 | 2.9633 | 2.4434 | 2.3353 | 2.2309 | 2.169 | 2.1257 | 2.0827 | 2.0403 | 1.8413 | 1.6514 | 1.4539 | 3.0474 | 2.9324 | 2.4164 | 2.275 | 2.1383 | 2.0063 | 1.8791 | 1.8058 | 1.7561 | 1.7068 | 1.6581 | 1.4291 | 1.212 | 0.99572
|  | UIG | CT |  |  |  | 3.1927 | 3.0762 | 2.9657 | 2.4587 | 2.3624 | 2.2687 | 2.1522 | 2.0873 | 2.0448 | 2.0023 | 1.9564 | 1.7401 | 1.5359 | 1.3323 | 3.1676 | 3.0965 | 3.0287 | 2.9633 | 2.4434 | 2.3353 | 2.2309 | 2.169 | 2.1257 | 2.0827 | 2.0403 | 1.8413 | 1.6514 | 1.4539 | 3.0474 | 2.9324 | 2.4164 | 2.275 | 2.1383 | 2.0063 | 1.8791 | 1.8058 | 1.7561 | 1.7068 | 1.6581 | 1.4291 | 1.212 | 0.99572
|  | UIG | LW |  |  |  | 3.3987 | 3.3813 | 3.3616 | 3.3399 | 3.3165 | 3.2914 | 3.2649 | 3.241 | 3.2164 | 3.1913 | 3.1658 | 2.3446 | 2.0757 | 1.8043 | 3.2983 | 3.279 | 3.2651 | 3.25 | 3.2339 | 3.2168 | 3.199 | 3.1825 | 3.1656 | 3.1484 | 3.1311 | 2.2592 | 1.9979 | 1.7354 | 3.2509 | 3.2336 | 3.2142 | 3.1928 | 3.1696 | 3.1449 | 3.1188 | 3.0952 | 2.4402 | 2.3746 | 2.309 | 2.0205 | 1.7295 | 1.4337
|  | UIG | ST |  |  |  | 3.4286 | 3.4216 | 3.4149 | 3.4083 | 3.4003 | 3.3925 | 3.3849 | 3.3777 | 3.3671 | 3.3568 | 3.3468 | 3.3012 | 3.261 | 3.2245 | 3.3223 | 3.315 | 3.3063 | 3.2971 | 3.2899 | 3.2845 | 3.2793 | 3.2742 | 3.2672 | 3.2603 | 3.2536 | 3.2229 | 3.1954 | 3.1702 | 3.2804 | 3.2735 | 3.2668 | 3.2603 | 3.2524 | 3.2447 | 3.2372 | 3.2301 | 3.2196 | 3.2095 | 3.1996 | 3.1546 | 3.1149 | 2.4436
|  | UIG | FS |  |  |  | 3.4216 | 3.4147 | 3.4044 | 3.3942 | 3.3842 | 3.3743 | 3.3646 | 3.355 | 3.3455 | 3.3362 | 3.327 | 3.2718 | 3.2236 | 3.1791 | 3.3188 | 3.3137 | 3.3054 | 3.2969 | 3.2886 | 3.2805 | 3.2721 | 3.2642 | 3.2583 | 3.2524 | 3.2466 | 3.2121 | 3.182 | 3.1541 | 3.2735 | 3.2666 | 3.2565 | 3.2465 | 3.2366 | 3.2268 | 3.2172 | 3.2077 | 3.1983 | 3.1891 | 3.18 | 3.1255 | 3.0779 | 3.034
| GRUDIE BRIDGE | ULLAPOOL | MINIMUM HEADROOM | NH 13018 94588 | NO | YES | 2.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 2.2549 | 5.233 | 5.2061 | 5.1796 | 5.1536 | 5.128 | 5.1028 | 5.0756 | 5.0608 | 5.0608 | 5.0608 | 5.0608 | 3.8316 | 3.6078 | 2.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218 | 3.838 | 3.6146
|  | ULLAPOOL | CT |  |  |  | 2.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 2.2572 | 5.2423 | 5.2254 | 5.2087 | 5.1922 | 5.176 | 5.16 | 5.1428 | 5.1257 | 5.1086 | 5.0918 | 5.0608 | 5.0608 | 5.0608 | 2.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218
|  | ULLAPOOL | LW |  |  |  | 2.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 2.2549 | 5.233 | 5.2061 | 5.1796 | 5.1536 | 5.128 | 5.1028 | 5.0756 | 5.0608 | 5.0608 | 5.0608 | 5.0608 | 3.8316 | 3.6078 | 2.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218 | 3.838 | 3.6146
|  | ULLAPOOL | ST |  |  |  | 2.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 2.262 | 5.2555 | 5.2454 | 5.2333 | 5.2237 | 5.2143 | 5.2051 | 5.1951 | 5.1853 | 5.1756 | 5.1662 | 5.1197 | 5.072 | 5.0608 | 2.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218
|  | ULLAPOOL | FS |  |  |  | 2.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 5.5383 | 2.2657 | 5.2652 | 5.2623 | 5.2588 | 5.2556 | 5.2525 | 5.2484 | 5.2444 | 5.2404 | 5.2366 | 5.2328 | 5.2148 | 5.1973 | 5.1804 | 2.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218 | 5.218
| SHETLAND | UNST | MINIMUM HEADROOM | HP6398113411 | YES | YES | 2.162 | 2.1617 | 2.1614 | 2.161 | 2.1607 | 2.1603 | 2.1596 | 2.1589 | 2.1582 | 2.1575 | 2.1569 | 2.1511 | 2.1434 | 2.1358 | 1.7117 | 1.7102 | 1.7083 | 1.7063 | 1.7045 | 1.7023 | 1.6985 | 1.6944 | 1.6905 | 1.6905 | 1.6905 | 1.6905 | 1.6905 | 1.6905 | 1.9094 | 1.9093 | 1.9091 | 1.909 | 1.9089 | 1.9087 | 1.9085 | 1.9082 | 1.9079 | 1.9076 | 1.9073 | 1.9051 | 1.902 | 1.899
|  | UNST | CT |  |  |  | 2.162 | 2.1618 | 2.1616 | 2.1613 | 2.1611 | 2.1609 | 2.1606 | 2.1604 | 2.1602 | 2.16 | 2.1598 | 2.1522 | 2.1445 | 2.137 | 1.7118 | 1.7107 | 1.7093 | 1.7079 | 1.7066 | 1.7054 | 1.7041 | 1.7028 | 1.7016 | 1.7003 | 1.6991 | 1.6905 | 1.6905 | 1.6905 | 1.9094 | 1.9093 | 1.9092 | 1.9091 | 1.909 | 1.9089 | 1.9088 | 1.9088 | 1.9087 | 1.9086 | 1.9085 | 1.9055 | 1.9024 | 1.8995
|  | UNST | LW |  |  |  | 2.162 | 2.1617 | 2.1614 | 2.161 | 2.1607 | 2.1604 | 2.1601 | 2.1598 | 2.1594 | 2.1591 | 2.1588 | 2.1511 | 2.1434 | 2.1358 | 1.7117 | 1.7102 | 1.7083 | 1.7063 | 1.7045 | 1.7027 | 1.701 | 1.6991 | 1.6973 | 1.6955 | 1.6938 | 1.6905 | 1.6905 | 1.6905 | 1.9094 | 1.9093 | 1.9091 | 1.909 | 1.9089 | 1.9087 | 1.9086 | 1.9085 | 1.9084 | 1.9082 | 1.9081 | 1.9051 | 1.902 | 1.899
|  | UNST | ST |  |  |  | 2.1621 | 2.162 | 2.1619 | 2.1617 | 2.161 | 2.1603 | 2.1596 | 2.1589 | 2.1582 | 2.1575 | 2.1569 | 2.1535 | 2.1503 | 2.147 | 1.7122 | 1.7118 | 1.711 | 1.7101 | 1.7061 | 1.7023 | 1.6985 | 1.6944 | 1.6905 | 1.6905 | 1.6905 | 1.6905 | 1.6905 | 1.6905 | 1.9094 | 1.9094 | 1.9093 | 1.9093 | 1.909 | 1.9087 | 1.9085 | 1.9082 | 1.9079 | 1.9076 | 1.9073 | 1.906 | 1.9047 | 1.9034
|  | UNST | FS |  |  |  | 2.1621 | 2.1621 | 2.1621 | 2.162 | 2.1618 | 2.1616 | 2.1613 | 2.161 | 2.1607 | 2.1604 | 2.1602 | 2.1589 | 2.1577 | 2.1566 | 1.7125 | 1.7125 | 1.7122 | 1.712 | 1.7107 | 1.7094 | 1.7077 | 1.7061 | 1.7045 | 1.703 | 1.7015 | 1.6942 | 1.6905 | 1.6905 | 1.9094 | 1.9094 | 1.9094 | 1.9094 | 1.9093 | 1.9092 | 1.9091 | 1.909 | 1.9089 | 1.9088 | 1.9087 | 1.9082 | 1.9077 | 1.9072
| SHETLAND | VOE | MINIMUM HEADROOM | HU4117663079 | YES | YES | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 9.6261 | 9.5753 | 9.517 | 9.4595 | 9.4033 | 9.3909 | 9.3909 | 9.3909 | 9.3909 | 9.3909 | 9.3909 | 9.3909 | 7.738 | 7.3787 | 9.9411 | 9.9375 | 9.9334 | 9.9294 | 9.9254 | 9.9214 | 9.9174 | 9.9131 | 9.9088 | 9.9044 | 9.9003 | 9.8811 | 9.8604 | 7.8836
|  | VOE | CT |  |  |  | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 9.6261 | 9.5753 | 9.517 | 9.4595 | 9.4033 | 9.3909 | 9.3909 | 9.3909 | 9.3909 | 9.3909 | 9.3909 | 9.3909 | 7.8817 | 7.607 | 9.9411 | 9.9375 | 9.9334 | 9.9294 | 9.9254 | 9.9214 | 9.9174 | 9.9131 | 9.9088 | 9.9044 | 9.9003 | 9.8844 | 9.8686 | 9.853
|  | VOE | LW |  |  |  | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 9.6332 | 9.5868 | 9.5295 | 9.4731 | 9.418 | 9.3909 | 9.3909 | 9.3909 | 9.3909 | 9.3909 | 9.3909 | 9.3909 | 7.738 | 7.3787 | 9.9416 | 9.9383 | 9.9343 | 9.9303 | 9.9265 | 9.9224 | 9.9185 | 9.9142 | 9.9099 | 9.9057 | 9.9017 | 9.8811 | 9.8604 | 7.8836
|  | VOE | ST |  |  |  | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 9.6485 | 9.6351 | 9.6142 | 9.5891 | 9.5656 | 9.5408 | 9.5166 | 9.4904 | 9.4645 | 9.4385 | 9.4149 | 9.3909 | 9.3909 | 9.3909 | 9.9427 | 9.9417 | 9.9403 | 9.9385 | 9.9368 | 9.9351 | 9.9334 | 9.9316 | 9.9297 | 9.9279 | 9.9262 | 9.9182 | 9.9103 | 9.9024
|  | VOE | FS |  |  |  | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 10.6211 | 9.656 | 9.655 | 9.6489 | 9.6417 | 9.6336 | 9.6249 | 9.614 | 9.6032 | 9.5925 | 9.5818 | 9.5721 | 9.5259 | 9.4832 | 9.4432 | 9.9432 | 9.9431 | 9.9427 | 9.9422 | 9.9416 | 9.941 | 9.9402 | 9.9395 | 9.9387 | 9.938 | 9.9373 | 9.934 | 9.931 | 9.9282
| DUDHOPE | WALTON | MINIMUM HEADROOM | NO 38995 30333 | NO | NO | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 25.0961 | 25.0649 | 25.026 | 24.988 | 24.9494 | 24.9102 | 24.8719 | 24.8292 | 24.821 | 24.821 | 24.821 | 24.821 | 24.821 | 24.821
|  | WALTON | CT |  |  |  | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 25.1004 | 25.0813 | 25.0591 | 25.0371 | 25.0151 | 24.994 | 24.9733 | 24.9502 | 24.9241 | 24.8972 | 24.8703 | 24.821 | 24.821 | 24.821
|  | WALTON | LW |  |  |  | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 25.0961 | 25.0649 | 25.026 | 24.988 | 24.9494 | 24.9102 | 24.8719 | 24.8292 | 24.821 | 24.821 | 24.821 | 24.821 | 24.821 | 24.821
|  | WALTON | ST |  |  |  | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 25.1056 | 25.0961 | 25.081 | 25.0629 | 25.0076 | 24.9538 | 24.9011 | 24.8437 | 24.821 | 24.821 | 24.821 | 24.821 | 24.821 | 24.821
|  | WALTON | FS |  |  |  | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 26.4573 | 24.2628 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 24.2592 | 25.1838 | 25.1103 | 25.1063 | 25.1016 | 25.0869 | 25.0723 | 25.0534 | 25.0345 | 25.0155 | 24.9968 | 24.9782 | 24.8879 | 24.821 | 24.821
| INVERNESS | WATERLOO PLACE | MINIMUM HEADROOM | NH 66301 45800 | NO | YES | 35.6999 | 35.65 | 35.6009 | 35.5527 | 35.5053 | 35.4586 | 35.3808 | 35.33 | 35.2794 | 35.2299 | 35.1809 | 34.9116 | 34.6352 | 34.3933 | 29.3617 | 29.3033 | 29.2458 | 29.1895 | 29.1341 | 29.0794 | 28.9885 | 28.9291 | 28.8699 | 28.812 | 28.7548 | 28.4398 | 28.1189 | 27.8906 | 31.9348 | 31.8809 | 31.8279 | 31.7759 | 31.7248 | 31.6743 | 31.5904 | 31.5356 | 31.481 | 31.4275 | 31.3747 | 31.0841 | 30.7857 | 30.492
|  | WATERLOO PLACE | CT |  |  |  | 35.7064 | 35.6682 | 35.635 | 35.6014 | 35.5657 | 35.5267 | 35.4651 | 35.4272 | 35.391 | 35.3545 | 35.3184 | 35.139 | 34.9572 | 34.777 | 29.3692 | 29.3246 | 29.2858 | 29.2465 | 29.2046 | 29.159 | 29.087 | 29.0427 | 29.0004 | 28.9578 | 28.9155 | 28.7057 | 28.493 | 28.2824 | 31.9418 | 31.9005 | 31.8647 | 31.8285 | 31.7899 | 31.7478 | 31.6814 | 31.6405 | 31.6014 | 31.562 | 31.523 | 31.3294 | 31.1332 | 30.9388
|  | WATERLOO PLACE | LW |  |  |  | 35.6999 | 35.65 | 35.6009 | 35.5527 | 35.5053 | 35.4586 | 35.3808 | 35.33 | 35.2794 | 35.2299 | 35.1809 | 34.9116 | 34.6352 | 34.3933 | 29.3617 | 29.3033 | 29.2458 | 29.1895 | 29.1341 | 29.0794 | 28.9885 | 28.9291 | 28.8699 | 28.812 | 28.7548 | 28.4398 | 28.1189 | 27.8906 | 31.9348 | 31.8809 | 31.8279 | 31.7759 | 31.7248 | 31.6743 | 31.5904 | 31.5356 | 31.481 | 31.4275 | 31.3747 | 31.0841 | 30.7857 | 30.492
|  | WATERLOO PLACE | ST |  |  |  | 35.7259 | 35.7083 | 35.6907 | 35.6689 | 35.6425 | 35.614 | 35.5705 | 35.5426 | 35.516 | 35.4893 | 35.4631 | 35.3379 | 35.2145 | 35.0913 | 29.3921 | 29.3715 | 29.3509 | 29.3254 | 29.2945 | 29.2612 | 29.2103 | 29.1776 | 29.1465 | 29.1154 | 29.0847 | 28.9383 | 28.794 | 28.6499 | 31.9629 | 31.9438 | 31.9248 | 31.9013 | 31.8728 | 31.8421 | 31.7951 | 31.765 | 31.7362 | 31.7075 | 31.6792 | 31.5441 | 31.4109 | 31.278
|  | WATERLOO PLACE | FS |  |  |  | 35.7412 | 35.7365 | 35.7311 | 35.7245 | 35.7157 | 35.7073 | 35.6898 | 35.679 | 35.6682 | 35.6574 | 35.6471 | 35.5995 | 35.5551 | 35.5127 | 29.41 | 29.4045 | 29.3981 | 29.3904 | 29.3801 | 29.3703 | 29.3498 | 29.3371 | 29.3246 | 29.3119 | 29.2999 | 29.2442 | 29.1923 | 29.1427 | 31.9794 | 31.9743 | 31.9684 | 31.9613 | 31.9518 | 31.9427 | 31.9238 | 31.9121 | 31.9006 | 31.8889 | 31.8778 | 31.8264 | 31.7784 | 31.7327
| LYNDHURST | WEST KIRKTON | MINIMUM HEADROOM | NO 39194 33796 | NO | YES | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 26.0132 | 25.927 | 25.8289 | 25.7403 | 25.7078 | 25.7078 | 25.7078 | 25.7078 | 25.7078 | 25.7078 | 25.7078 | 25.7078 | 25.7078 | 21.0499 | 25.9751 | 25.8701 | 25.7507 | 25.6428 | 25.5308 | 25.4254 | 25.3313 | 25.3222 | 25.3222 | 25.3222 | 25.3222 | 25.3222 | 25.3222 | 25.3222
|  | WEST KIRKTON | CT |  |  |  | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 26.0132 | 25.9283 | 25.84 | 25.7594 | 25.7078 | 25.7078 | 25.7078 | 25.7078 | 25.7078 | 25.7078 | 25.7078 | 25.7078 | 25.7078 | 25.7078 | 25.9751 | 25.8717 | 25.7642 | 25.6661 | 25.565 | 25.4701 | 25.3805 | 25.3222 | 25.3222 | 25.3222 | 25.3222 | 25.3222 | 25.3222 | 25.3222
|  | WEST KIRKTON | LW |  |  |  | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 26.0162 | 25.927 | 25.8289 | 25.7403 | 25.7078 | 25.7078 | 25.7078 | 25.7078 | 25.7078 | 25.7078 | 25.7078 | 25.7078 | 25.7078 | 21.0499 | 25.9787 | 25.8701 | 25.7507 | 25.6428 | 25.5308 | 25.4254 | 25.3313 | 25.3222 | 25.3222 | 25.3222 | 25.3222 | 25.3222 | 25.3222 | 25.3222
|  | WEST KIRKTON | ST |  |  |  | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 26.0451 | 26.014 | 25.9784 | 25.9427 | 25.8904 | 25.8416 | 25.7958 | 25.7464 | 25.7078 | 25.7078 | 25.7078 | 25.7078 | 25.7078 | 25.7078 | 26.0139 | 25.9761 | 25.9327 | 25.8892 | 25.8255 | 25.7661 | 25.7104 | 25.6502 | 25.5851 | 25.5205 | 25.4592 | 25.3222 | 25.3222 | 25.3222
|  | WEST KIRKTON | FS |  |  |  | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 28.9136 | 26.0573 | 26.0467 | 26.0317 | 26.0177 | 25.9991 | 25.9823 | 25.9635 | 25.9441 | 25.924 | 25.9041 | 25.8847 | 25.7926 | 25.7139 | 25.7078 | 26.0287 | 26.0158 | 25.9976 | 25.9806 | 25.9579 | 25.9374 | 25.9146 | 25.8909 | 25.8665 | 25.8423 | 25.8187 | 25.7065 | 25.6106 | 25.5246
| KILLIN | WESTER DRUMMOND | MINIMUM HEADROOM | NN 72155 44784 | YES | YES | -0.14676 | -0.26929 | -0.38535 | -0.49729 | -0.60509 | -0.70876 | -0.8083 | -0.85334 | -0.87632 | -0.89907 | -0.92148 | -1.0441 | -1.1536 | -1.2631 | -0.10089 | -0.1995 | -0.29307 | -0.38333 | -0.47026 | -0.55388 | -0.63419 | -0.67107 | -0.69033 | -0.70941 | -0.72821 | -0.8346 | -0.92946 | -1.0243 | -0.15326 | -0.27666 | -0.39361 | -0.50641 | -0.61504 | -0.71951 | -0.81983 | -0.86543 | -0.88886 | -0.91206 | -0.93491 | -1.0591 | -1.17 | -1.2813
|  | WESTER DRUMMOND | CT |  |  |  | -0.14676 | -0.26929 | -0.38535 | -0.49729 | -0.60509 | -0.70876 | -0.8083 | -0.85334 | -0.87632 | -0.89907 | -0.92148 | -1.0441 | -1.1536 | -1.2631 | -0.10089 | -0.1995 | -0.29307 | -0.38333 | -0.47026 | -0.55388 | -0.63419 | -0.67107 | -0.69033 | -0.70941 | -0.72821 | -0.8346 | -0.92946 | -1.0243 | -0.15326 | -0.27666 | -0.39361 | -0.50641 | -0.61504 | -0.71951 | -0.81983 | -0.86543 | -0.88886 | -0.91206 | -0.93491 | -1.0591 | -1.17 | -1.2813
|  | WESTER DRUMMOND | LW |  |  |  | 0.065038 | 0.038492 | 0.0077516 | -0.024888 | -0.059208 | -0.095012 | -0.13209 | -0.16685 | -0.20228 | -0.23817 | -0.27431 | -0.44196 | -0.60172 | -0.76307 | 0.066772 | 0.042668 | 0.014351 | -0.015408 | -0.046434 | -0.078575 | -0.11166 | -0.1432 | -0.17525 | -0.20764 | -0.2402 | -0.38488 | -0.52345 | -0.66309 | 0.058725 | 0.030934 | -0.0015556 | -0.035907 | -0.071902 | -0.10935 | -0.14803 | -0.18454 | -0.22172 | -0.2594 | -0.29733 | -0.46975 | -0.63454 | -0.80082
|  | WESTER DRUMMOND | ST |  |  |  | 0.09865 | 0.089108 | 0.078243 | 0.066807 | 0.055687 | 0.044858 | 0.034323 | 0.023934 | 0.010152 | -0.0032777 | -0.01636 | -0.076384 | -0.13053 | -0.18012 | 0.094751 | 0.086189 | 0.076113 | 0.0653 | 0.055407 | 0.045767 | 0.036383 | 0.027034 | 0.015006 | 0.0032778 | -0.0081563 | -0.060928 | -0.109 | -0.15343 | 0.092799 | 0.082882 | 0.071447 | 0.059228 | 0.047642 | 0.036355 | 0.025372 | 0.014496 | 0.0002458 | -0.013644 | -0.027179 | -0.089427 | -0.1458 | -0.19763
|  | WESTER DRUMMOND | FS |  |  |  | 0.092347 | 0.085238 | 0.073694 | 0.062029 | 0.050713 | 0.039556 | 0.028273 | 0.017158 | 0.0062024 | -0.0045912 | -0.015219 | -0.077624 | -0.13195 | -0.18206 | 0.090539 | 0.084553 | 0.074771 | 0.064877 | 0.055496 | 0.046249 | 0.036814 | 0.027524 | 0.018367 | 0.0093472 | 0.00046768 | -0.05129 | -0.09646 | -0.13814 | 0.086988 | 0.079544 | 0.06768 | 0.05575 | 0.044329 | 0.03307 | 0.021677 | 0.010448 | -0.00066212 | -0.011607 | -0.022384 | -0.085524 | -0.14053 | -0.19127
| THURSO | WESTRAY | MINIMUM HEADROOM | HY 50213 39413 | YES | YES | -1.1393 | -1.1472 | -1.1569 | -1.1665 | -1.1759 | -1.1851 | -1.1941 | -1.2041 | -1.2138 | -1.2235 | -1.2332 | -3.0032 | -3.0447 | -3.0862 | -1.7929 | -1.8083 | -1.8273 | -1.8459 | -1.8643 | -1.8822 | -1.8998 | -1.9191 | -1.9381 | -1.957 | -1.9758 | -3.4138 | -3.4653 | -3.517 | -2.131 | -2.1415 | -2.1544 | -2.1671 | -2.1796 | -2.1918 | -2.2038 | -2.2169 | -2.2299 | -2.2427 | -2.2556 | -3.9963 | -4.0314 | -4.0667
|  | WESTRAY | CT |  |  |  | -1.1388 | -1.1447 | -1.1515 | -1.1582 | -1.1648 | -1.1712 | -1.1775 | -1.1844 | -1.1913 | -1.198 | -1.2048 | -2.9527 | -2.988 | -3.0231 | -1.792 | -1.8035 | -1.8167 | -1.8298 | -1.8426 | -1.8551 | -1.8674 | -1.8809 | -1.8942 | -1.9074 | -1.9206 | -3.3509 | -3.3949 | -3.4385 | -2.1304 | -2.1382 | -2.1472 | -2.1561 | -2.1649 | -2.1734 | -2.1817 | -2.1909 | -2.2 | -2.209 | -2.218 | -3.9535 | -3.9834 | -4.0132
|  | WESTRAY | LW |  |  |  | -1.1393 | -1.1472 | -1.1569 | -1.1665 | -1.1759 | -1.1851 | -1.1941 | -1.2041 | -1.2138 | -1.2235 | -1.2332 | -3.0032 | -3.0447 | -3.0862 | -1.7929 | -1.8083 | -1.8273 | -1.8459 | -1.8643 | -1.8822 | -1.8998 | -1.9191 | -1.9381 | -1.957 | -1.9758 | -3.4138 | -3.4653 | -3.517 | -2.131 | -2.1415 | -2.1544 | -2.1671 | -2.1796 | -2.1918 | -2.2038 | -2.2169 | -2.2299 | -2.2427 | -2.2556 | -3.9963 | -4.0314 | -4.0667
|  | WESTRAY | ST |  |  |  | -1.1367 | -1.139 | -1.1427 | -1.147 | -1.1494 | -1.1517 | -1.154 | -1.1565 | -1.159 | -1.1613 | -1.1637 | -2.0065 | -2.0243 | -2.042 | -1.7879 | -1.7924 | -1.7995 | -1.808 | -1.8127 | -1.8172 | -1.8216 | -1.8265 | -1.8313 | -1.8359 | -1.8406 | -2.5565 | -2.5786 | -2.6006 | -2.1276 | -2.1307 | -2.1355 | -2.1413 | -2.1445 | -2.1476 | -2.1506 | -2.1539 | -2.1571 | -2.1603 | -2.1635 | -3.0317 | -3.0468 | -3.0618
|  | WESTRAY | FS |  |  |  | -1.1354 | -1.1355 | -1.1366 | -1.1378 | -1.1386 | -1.1394 | -1.1404 | -1.1414 | -1.1424 | -1.1434 | -1.1443 | -1.1489 | -1.1533 | -1.1574 | -1.7853 | -1.7856 | -1.7877 | -1.7901 | -1.7917 | -1.7932 | -1.7951 | -1.7971 | -1.799 | -1.8009 | -1.8028 | -1.8118 | -1.8202 | -1.8282 | -2.1258 | -2.1261 | -2.1274 | -2.1291 | -2.1302 | -2.1312 | -2.1325 | -2.1339 | -2.1352 | -2.1364 | -2.1377 | -2.1438 | -2.1496 | -2.155
| TARLAND | WHITEHOUSE | MINIMUM HEADROOM | NJ 61658 15058 | NO | YES | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 7.6087 | 7.0726 | 6.5409 | 9.0709 | 9.0083 | 8.9792 | 8.9792 | 8.9792 | 8.9792 | 8.9792 | 7.2045 | 7.0442 | 6.8834 | 6.7238 | 6.0736 | 5.419 | 4.7783 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 7.3257 | 7.1648 | 7.0051 | 6.3547 | 5.6999 | 5.059
|  | WHITEHOUSE | CT |  |  |  | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 7.7103 | 7.3583 | 9.0737 | 9.0253 | 8.9792 | 8.9792 | 8.9792 | 8.9792 | 8.9792 | 8.9792 | 8.9792 | 7.2611 | 7.1451 | 6.683 | 6.2183 | 5.7634 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 6.9643 | 6.4994 | 6.0444
|  | WHITEHOUSE | LW |  |  |  | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 7.6087 | 7.0726 | 6.5409 | 9.0709 | 9.0083 | 8.9792 | 8.9792 | 8.9792 | 8.9792 | 8.9792 | 7.2045 | 7.0442 | 6.8834 | 6.7238 | 6.0736 | 5.419 | 4.7783 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 7.3257 | 7.1648 | 7.0051 | 6.3547 | 5.6999 | 5.059
|  | WHITEHOUSE | ST |  |  |  | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 9.0923 | 9.0755 | 9.0492 | 9.0174 | 8.9878 | 8.9792 | 8.9792 | 8.9792 | 8.9792 | 8.9792 | 8.9792 | 8.9792 | 7.1426 | 6.8557 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 7.1371
|  | WHITEHOUSE | FS |  |  |  | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 10.4016 | 9.1016 | 9.1 | 9.0917 | 9.0817 | 9.0721 | 9.0624 | 9.0502 | 9.0381 | 9.0263 | 9.0146 | 9.0031 | 8.9792 | 8.9792 | 8.9792 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593 | 9.4593
| PERSLEY | WHITESTRIPES | MINIMUM HEADROOM | NJ 92850 11054 | NO | YES | 19.6748 | 19.5467 | 19.4209 | 19.2995 | 19.1826 | 19.0703 | 18.9624 | 14.0334 | 13.3168 | 12.5844 | 11.8329 | 9.343 | 7.5719 | 6.0047 | 17.3698 | 17.1942 | 17.1239 | 17.0561 | 16.9908 | 13.1166 | 12.372 | 11.5643 | 10.747 | 9.9118 | 9.0545 | 6.2441 | 4.2835 | 2.563 | 17.6576 | 17.4589 | 17.2565 | 17.0572 | 16.9022 | 13.3298 | 12.5698 | 11.7445 | 10.9094 | 10.056 | 9.18 | 6.2916 | 4.2547 | 2.4642
|  | WHITESTRIPES | CT |  |  |  | 19.6748 | 19.5467 | 19.4209 | 19.2995 | 19.1826 | 19.0703 | 18.9624 | 14.4351 | 13.8962 | 13.338 | 12.78 | 11.3581 | 10.2395 | 9.1567 | 17.3698 | 17.1942 | 17.1239 | 17.0561 | 16.9908 | 13.5946 | 12.9853 | 12.3628 | 11.7504 | 11.1154 | 10.4805 | 8.894 | 7.6666 | 6.4861 | 17.6576 | 17.4589 | 17.2565 | 17.0572 | 16.9022 | 13.6246 | 12.9961 | 12.3655 | 11.7385 | 11.0887 | 10.4391 | 8.7978 | 7.516 | 6.2786
|  | WHITESTRIPES | LW |  |  |  | 19.9014 | 19.8822 | 19.8606 | 19.8367 | 19.8109 | 19.7834 | 19.7543 | 14.0334 | 13.3168 | 12.5844 | 11.8329 | 9.343 | 7.5719 | 6.0047 | 17.5258 | 17.3816 | 17.3696 | 17.3563 | 17.3418 | 13.1166 | 12.372 | 11.5643 | 10.747 | 9.9118 | 9.0545 | 6.2441 | 4.2835 | 2.563 | 17.8784 | 17.7678 | 17.6369 | 17.5537 | 17.528 | 13.3298 | 12.5698 | 11.7445 | 10.9094 | 10.056 | 9.18 | 6.2916 | 4.2547 | 2.4642
|  | WHITESTRIPES | ST |  |  |  | 19.9342 | 19.9266 | 19.9191 | 19.9119 | 19.9031 | 19.8945 | 19.8862 | 19.8779 | 19.8659 | 19.8542 | 19.8428 | 19.7794 | 19.7191 | 14.0546 | 17.6536 | 17.549 | 17.4121 | 17.3982 | 17.3933 | 17.3885 | 17.3839 | 17.3793 | 17.3725 | 17.366 | 17.3596 | 13.0957 | 12.3428 | 11.6173 | 17.9615 | 17.9057 | 17.85 | 17.7882 | 17.7463 | 17.7035 | 17.659 | 17.6104 | 17.5827 | 17.5711 | 17.5597 | 13.3078 | 12.5323 | 11.7822
|  | WHITESTRIPES | FS |  |  |  | 19.9266 | 19.9189 | 19.9076 | 19.8965 | 19.8854 | 19.8746 | 19.8639 | 19.8533 | 19.8429 | 19.8326 | 19.8225 | 19.7618 | 19.6973 | 19.6346 | 17.7966 | 17.6814 | 17.6242 | 17.5598 | 17.5119 | 17.4629 | 17.409 | 17.3655 | 17.3597 | 17.3539 | 17.3483 | 17.3144 | 17.2783 | 17.2433 | 18.026 | 17.9652 | 17.9301 | 17.8917 | 17.8614 | 17.8361 | 17.8102 | 17.7837 | 17.7567 | 17.7292 | 17.7013 | 17.5497 | 17.4194 | 17.3523
| CARRADALE | WHITING BAY | MINIMUM HEADROOM | NS 04169 26277 | YES | YES | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.0416 | 9.0388 | 9.0354 | 9.032 | 9.0287 | 9.0249 | 9.0181 | 9.0109 | 9.0037 | 8.9967 | 8.9898 | 8.9283 | 8.8589 | 8.8329 | 9.0557 | 9.0544 | 9.0528 | 9.0512 | 9.0497 | 9.048 | 9.0449 | 9.0416 | 9.0383 | 9.0351 | 9.0319 | 9.0211 | 9.0211 | 9.0211
|  | WHITING BAY | CT |  |  |  | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.0418 | 9.0397 | 9.0373 | 9.0349 | 9.0326 | 9.0303 | 9.0281 | 9.0257 | 9.0233 | 9.021 | 9.0186 | 8.9371 | 8.8614 | 8.835 | 9.0557 | 9.0548 | 9.0537 | 9.0526 | 9.0515 | 9.0505 | 9.0495 | 9.0484 | 9.0473 | 9.0462 | 9.0451 | 9.0211 | 9.0211 | 9.0211
|  | WHITING BAY | LW |  |  |  | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.0416 | 9.0388 | 9.0354 | 9.032 | 9.0287 | 9.0254 | 9.0223 | 9.0189 | 9.0155 | 9.0121 | 9.0088 | 8.9283 | 8.8589 | 8.8329 | 9.0557 | 9.0544 | 9.0528 | 9.0512 | 9.0497 | 9.0483 | 9.0468 | 9.0452 | 9.0437 | 9.0421 | 9.0406 | 9.0211 | 9.0211 | 9.0211
|  | WHITING BAY | ST |  |  |  | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.0425 | 9.0417 | 9.0404 | 9.0388 | 9.0318 | 9.0249 | 9.0181 | 9.0109 | 9.0037 | 8.9967 | 8.9898 | 8.9561 | 8.9227 | 8.8895 | 9.0561 | 9.0557 | 9.0551 | 9.0544 | 9.0511 | 9.048 | 9.0449 | 9.0416 | 9.0383 | 9.0351 | 9.0319 | 9.0211 | 9.0211 | 9.0211
|  | WHITING BAY | FS |  |  |  | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.3385 | 9.043 | 9.043 | 9.0426 | 9.0422 | 9.0398 | 9.0375 | 9.0346 | 9.0317 | 9.0288 | 9.026 | 9.0233 | 9.0101 | 8.9979 | 8.9864 | 9.0563 | 9.0563 | 9.0561 | 9.0559 | 9.0548 | 9.0538 | 9.0524 | 9.0511 | 9.0498 | 9.0485 | 9.0473 | 9.0412 | 9.0356 | 9.0304
| MYBSTER | WICK | MINIMUM HEADROOM | ND 35583 50947 | NO | YES | 22.455 | 22.4519 | 22.4485 | 22.4452 | 22.442 | 22.4384 | 22.4347 | 22.4313 | 22.428 | 22.4247 | 22.4216 | 22.4038 | 22.384 | 22.3648 | 20.9029 | 20.8801 | 20.854 | 20.8298 | 20.8061 | 20.7792 | 20.7514 | 20.7261 | 20.7013 | 20.6767 | 20.6531 | 20.5206 | 20.372 | 20.2288 | 20.883 | 20.874 | 20.8637 | 20.8542 | 20.8449 | 20.8343 | 20.8234 | 20.8134 | 20.8036 | 20.794 | 20.7847 | 20.7326 | 20.6741 | 20.6177
|  | WICK | CT |  |  |  | 22.4553 | 22.4529 | 22.4504 | 22.4481 | 22.4458 | 22.443 | 22.4402 | 22.4376 | 22.4351 | 22.4327 | 22.4303 | 22.4182 | 22.404 | 22.3899 | 20.9049 | 20.8873 | 20.8688 | 20.8516 | 20.8342 | 20.8134 | 20.7919 | 20.7728 | 20.7544 | 20.736 | 20.7187 | 20.6279 | 20.5217 | 20.4167 | 20.8838 | 20.8769 | 20.8696 | 20.8628 | 20.856 | 20.8478 | 20.8393 | 20.8318 | 20.8245 | 20.8173 | 20.8105 | 20.7748 | 20.733 | 20.6917
|  | WICK | LW |  |  |  | 22.455 | 22.4519 | 22.4485 | 22.4452 | 22.442 | 22.4384 | 22.4347 | 22.4313 | 22.428 | 22.4247 | 22.4216 | 22.4038 | 22.384 | 22.3648 | 20.9029 | 20.8801 | 20.854 | 20.8298 | 20.8061 | 20.7792 | 20.7514 | 20.7261 | 20.7013 | 20.6767 | 20.6531 | 20.5206 | 20.372 | 20.2288 | 20.883 | 20.874 | 20.8637 | 20.8542 | 20.8449 | 20.8343 | 20.8234 | 20.8134 | 20.8036 | 20.794 | 20.7847 | 20.7326 | 20.6741 | 20.6177
|  | WICK | ST |  |  |  | 22.4563 | 22.4553 | 22.4539 | 22.4524 | 22.4508 | 22.4489 | 22.447 | 22.4452 | 22.4436 | 22.4419 | 22.4404 | 22.4326 | 22.4237 | 22.415 | 20.9126 | 20.9048 | 20.8945 | 20.8833 | 20.8715 | 20.8574 | 20.8429 | 20.83 | 20.8176 | 20.8052 | 20.7938 | 20.7358 | 20.6693 | 20.6041 | 20.8868 | 20.8837 | 20.8797 | 20.8753 | 20.8706 | 20.8651 | 20.8594 | 20.8543 | 20.8494 | 20.8446 | 20.84 | 20.8172 | 20.7911 | 20.7654
|  | WICK | FS |  |  |  | 22.4571 | 22.4568 | 22.4564 | 22.4559 | 22.4554 | 22.4548 | 22.4539 | 22.4533 | 22.4526 | 22.4519 | 22.4513 | 22.4483 | 22.4451 | 22.4418 | 20.9184 | 20.9167 | 20.9133 | 20.9099 | 20.9059 | 20.901 | 20.895 | 20.8899 | 20.8848 | 20.8798 | 20.8752 | 20.8531 | 20.8292 | 20.804 | 20.8891 | 20.8884 | 20.8871 | 20.8857 | 20.8842 | 20.8822 | 20.8799 | 20.8779 | 20.8759 | 20.8739 | 20.8721 | 20.8634 | 20.854 | 20.8441
| WOODHILL | WOODHILL | MINIMUM HEADROOM | NJ 91259 07053 | NO | NO | 10.6082 | 10.6048 | 10.6007 | 10.5967 | 10.5927 | 10.5887 | 10.5847 | 10.5805 | 10.5763 | 10.5722 | 10.566 | 10.5121 | 10.4552 | 10.3993 | 21.3279 | 21.3098 | 21.2881 | 21.2665 | 21.2451 | 21.2238 | 21.2028 | 21.1801 | 21.1581 | 21.1362 | 21.1031 | 20.9444 | 20.9444 | 20.9444 | 11.2632 | 11.2526 | 11.2397 | 11.227 | 11.2144 | 11.2019 | 11.1895 | 11.1762 | 11.1632 | 11.1503 | 11.1308 | 10.962 | 10.7469 | 10.4177
|  | WOODHILL | CT |  |  |  | 10.6089 | 10.6068 | 10.6045 | 10.6021 | 10.5996 | 10.5973 | 10.5949 | 10.5924 | 10.59 | 10.5875 | 10.5849 | 10.5427 | 10.4991 | 10.458 | 21.3315 | 21.3204 | 21.3082 | 21.2953 | 21.2822 | 21.2697 | 21.2572 | 21.2437 | 21.2307 | 21.2176 | 21.2039 | 20.979 | 20.9444 | 20.9444 | 11.2653 | 11.2588 | 11.2516 | 11.244 | 11.2363 | 11.2289 | 11.2216 | 11.2136 | 11.2059 | 11.1983 | 11.1902 | 11.0578 | 10.9212 | 10.764
|  | WOODHILL | LW |  |  |  | 10.6082 | 10.6048 | 10.6007 | 10.5967 | 10.5927 | 10.5887 | 10.5847 | 10.5805 | 10.5763 | 10.5722 | 10.566 | 10.5121 | 10.4552 | 10.3993 | 21.3279 | 21.3098 | 21.2881 | 21.2665 | 21.2451 | 21.2238 | 21.2028 | 21.1801 | 21.1581 | 21.1362 | 21.1031 | 20.9444 | 20.9444 | 20.9444 | 11.2632 | 11.2526 | 11.2397 | 11.227 | 11.2144 | 11.2019 | 11.1895 | 11.1762 | 11.1632 | 11.1503 | 11.1308 | 10.962 | 10.7469 | 10.4177
|  | WOODHILL | ST |  |  |  | 10.6105 | 10.6094 | 10.6078 | 10.6058 | 10.6016 | 10.5975 | 10.5935 | 10.5891 | 10.5849 | 10.5807 | 10.5764 | 10.548 | 10.5196 | 10.4933 | 21.34 | 21.334 | 21.3255 | 21.315 | 21.2926 | 21.2709 | 21.2495 | 21.2263 | 21.2037 | 21.1814 | 21.1588 | 21.0071 | 20.9444 | 20.9444 | 11.2703 | 11.2668 | 11.2618 | 11.2556 | 11.2424 | 11.2296 | 11.217 | 11.2034 | 11.19 | 11.1769 | 11.1636 | 11.0743 | 10.9855 | 10.9032
|  | WOODHILL | FS |  |  |  | 10.6262 | 10.6175 | 10.6169 | 10.6164 | 10.615 | 10.6137 | 10.612 | 10.6103 | 10.6087 | 10.6071 | 10.6055 | 10.5977 | 10.5886 | 10.5787 | 21.4238 | 21.3772 | 21.3742 | 21.3712 | 21.3641 | 21.3569 | 21.3479 | 21.3389 | 21.3303 | 21.3218 | 21.3136 | 21.2721 | 21.2237 | 21.1706 | 11.3197 | 11.2922 | 11.2905 | 11.2887 | 11.2845 | 11.2803 | 11.275 | 11.2697 | 11.2646 | 11.2596 | 11.2548 | 11.2303 | 11.2018 | 11.1706

## Local Authority Reference
Local Authority | Grid Supply Point | Primary Substation
Aberdeen City | CLAYHILLS | BALNAGASK
Aberdeen City | CLAYHILLS | CLAYHILLS
Aberdeen City | CLAYHILLS | COMMERCE STREET
Aberdeen City | CLAYHILLS | CRAIGINCHES
Aberdeen City | CRAIGIEBUCKLER | CRAIGIEBUCKLER
Aberdeen City | CRAIGIEBUCKLER | CRAIGTON
Aberdeen City | CRAIGIEBUCKLER | CULTER
Aberdeen City | CRAIGIEBUCKLER | RUTHRIESTON
Aberdeen City | DYCE | DYCE NORTH
Aberdeen City | DYCE | HARVEST AVENUE
Aberdeen City | KINTORE | PARK
Aberdeen City | KINTORE | SKENE
Aberdeen City | KINTORE | TORRYBURN
Aberdeen City | PERSLEY | BRIDGE OF DON
Aberdeen City | PERSLEY | HAUDAGAIN
Aberdeen City | PERSLEY | NORTHFIELD
Aberdeen City | PERSLEY | ST MACHAR
Aberdeen City | PERSLEY | STONEYWOOD T1&T2
Aberdeen City | PERSLEY | STONEYWOOD T3
Aberdeen City | PERSLEY | WHITESTRIPES
Aberdeen City | REDMOSS | KINCORTH
Aberdeen City | REDMOSS | REDMOSS
Aberdeen City | WILLOWDALE | DENBURN
Aberdeen City | WILLOWDALE | GREYFRIARS
Aberdeen City | WILLOWDALE | HAYTON
Aberdeen City | WILLOWDALE | ST NICHOLAS
Aberdeen City | WOODHILL | QUEENS LANE NORTH
Aberdeen City | WOODHILL | SPRINGHILL
Aberdeen City | WOODHILL | WOODHILL
Aberdeenshire | BOAT OF GARTEN | AVIEMORE
Aberdeenshire | BOAT OF GARTEN | BALLINDALLOCH
Aberdeenshire | BRIDGE OF DUN | INCHBARE
Aberdeenshire | BRIDGE OF DUN | LOGIE PERT
Aberdeenshire | BRIDGE OF DUN | MONTROSE NORTH
Aberdeenshire | BRIDGE OF DUN | ST CYRUS
Aberdeenshire | COUPAR ANGUS | DALRULZION
Aberdeenshire | CRAIGIEBUCKLER | CRAIGTON
Aberdeenshire | CRAIGIEBUCKLER | CULTER
Aberdeenshire | CRAIGIEBUCKLER | RUTHRIESTON
Aberdeenshire | DYCE | BALMEDIE
Aberdeenshire | DYCE | DYCE NORTH
Aberdeenshire | DYCE | ELLON 11 kV
Aberdeenshire | DYCE | KINGSEAT
Aberdeenshire | FIDDES | EDZELL
Aberdeenshire | FIDDES | INVERBERVIE
Aberdeenshire | FIDDES | LAURENCEKIRK
Aberdeenshire | FIDDES | STONEHAVEN
Aberdeenshire | FRASERBURGH | FRASERBURGH
Aberdeenshire | KEITH | CULLEN
Aberdeenshire | KEITH | DUFFTOWN
Aberdeenshire | KEITH | HUNTLY
Aberdeenshire | KEITH | INSCH
Aberdeenshire | KEITH | KEITH
Aberdeenshire | KEITH | LIMEHILLOCKS
Aberdeenshire | KEITH | MARNOCH
Aberdeenshire | KINTORE | BANCHORY
Aberdeenshire | KINTORE | FYVIE
Aberdeenshire | KINTORE | INVERURIE
Aberdeenshire | KINTORE | KEMNAY
Aberdeenshire | KINTORE | METHLICK
Aberdeenshire | KINTORE | MIDMAR
Aberdeenshire | KINTORE | OLDMELDRUM
Aberdeenshire | KINTORE | PARK
Aberdeenshire | KINTORE | SKENE
Aberdeenshire | KINTORE | TORRYBURN
Aberdeenshire | LUNANHEAD | MARYTON
Aberdeenshire | MACDUFF | MACDUFF
Aberdeenshire | MACDUFF | PORTSOY
Aberdeenshire | MACDUFF | TURRIFF
Aberdeenshire | PERSLEY | BRIDGE OF DON
Aberdeenshire | PERSLEY | WHITESTRIPES
Aberdeenshire | PETERHEAD GRANGE | PETERHEAD GRANGE 11kV
Aberdeenshire | PETERHEAD GRANGE | PHEAD NORTH ST
Aberdeenshire | PETERHEAD SHELL | BODDAM
Aberdeenshire | REDMOSS | KINCORTH
Aberdeenshire | REDMOSS | NEWTONHILL
Aberdeenshire | REDMOSS | REDMOSS
Aberdeenshire | ST FERGUS GAS | ST FERGUS GAS TERM
Aberdeenshire | STRICHEN | HATTON
Aberdeenshire | STRICHEN | MAUD
Aberdeenshire | STRICHEN | MINTLAW
Aberdeenshire | STRICHEN | NEW PITSLIGO
Aberdeenshire | STRICHEN | STONEYHILL
Aberdeenshire | STRICHEN | STRICHEN
Aberdeenshire | TARLAND | ABOYNE
Aberdeenshire | TARLAND | BALLATER
Aberdeenshire | TARLAND | MOSSAT
Aberdeenshire | TARLAND | STRATHDON
Aberdeenshire | TARLAND | WHITEHOUSE
Aberdeenshire | TUMMEL BRIDGE | BONSKEID
Aberdeenshire | WOODHILL | SPRINGHILL
Angus | ABERNETHY | BALBEGGIE
Angus | ARBROATH | CARNOUSTIE
Angus | ARBROATH | CHARLES AVENUE
Angus | ARBROATH | ELLIOT DEPOT
Angus | ARBROATH | HUME STREET
Angus | ARBROATH | REDFORD
Angus | BRIDGE OF DUN | BRECHIN
Angus | BRIDGE OF DUN | BRIDGE OF DUN 11kV
Angus | BRIDGE OF DUN | INCHBARE
Angus | BRIDGE OF DUN | LOGIE PERT
Angus | BRIDGE OF DUN | MILL RD MONTROSE
Angus | BRIDGE OF DUN | MONTROSE NORTH
Angus | BRIDGE OF DUN | ST CYRUS
Angus | CHARLESTON | GOURDIE
Angus | COUPAR ANGUS | ALYTH
Angus | COUPAR ANGUS | COUPAR ANGUS
Angus | COUPAR ANGUS | DALRULZION
Angus | COUPAR ANGUS | LEOCH
Angus | FIDDES | EDZELL
Angus | FIDDES | LAURENCEKIRK
Angus | KINTORE | BANCHORY
Angus | LUNANHEAD | FRIOCKHEIM
Angus | LUNANHEAD | INVERARITY
Angus | LUNANHEAD | LOCHSIDE
Angus | LUNANHEAD | LUNANHEAD
Angus | LUNANHEAD | MARYTON
Angus | LYNDHURST | MACALPINE ROAD
Angus | LYNDHURST | WEST KIRKTON
Angus | MILTON OF CRAIGIE | ASHLUDIE
Angus | MILTON OF CRAIGIE | BALDOVIE
Angus | MILTON OF CRAIGIE | BROUGHTY FERRY
Angus | MILTON OF CRAIGIE | EDZELL STREET
Angus | MILTON OF CRAIGIE | LONGHAUGH
Angus | TARLAND | BALLATER
Argyll and Bute | CARRADALE | BALLURE
Argyll and Bute | CARRADALE | CAMPBELTOWN
Argyll and Bute | CARRADALE | CLAONAIG
Argyll and Bute | CARRADALE | DIPPEN
Argyll and Bute | CARRADALE | WESTPARK FERGUS
Argyll and Bute | CLACHAN | BUTTERBRIDGE
Argyll and Bute | CLACHAN | DOUGLAS PIER
Argyll and Bute | CLACHAN | INVERARAY
Argyll and Bute | CLACHAN | LOCHGOILHEAD
Argyll and Bute | CLACHAN | STRACHUR
Argyll and Bute | DUNOON | BRUCHAG
Argyll and Bute | DUNOON | COLINTRAIVE
Argyll and Bute | DUNOON | DUNOON
Argyll and Bute | DUNOON | GLENDARUEL
Argyll and Bute | DUNOON | INNELLAN
Argyll and Bute | DUNOON | KAMES
Argyll and Bute | DUNOON | NEWTON
Argyll and Bute | DUNOON | OTTER FERRY
Argyll and Bute | DUNOON | ROTHESAY
Argyll and Bute | DUNOON | SANDBANK
Argyll and Bute | FORT WILLIAM | SALEN
Argyll and Bute | KILLIN | CASHLIE
Argyll and Bute | PORT ANN | AIRIGH-NA-BRODAIG
Argyll and Bute | PORT ANN | BOWMORE
Argyll and Bute | PORT ANN | CRINAN
Argyll and Bute | PORT ANN | CROMALT
Argyll and Bute | PORT ANN | INVERNEIL
Argyll and Bute | PORT ANN | LOCHGILPHEAD
Argyll and Bute | PORT ANN | LUSSAGIVEN
Argyll and Bute | PORT ANN | PORT ASKAIG
Argyll and Bute | PORT ANN | PORT ELLEN
Argyll and Bute | PORT ANN | STONEFIELD
Argyll and Bute | PORT ANN | TARBERT JURA
Argyll and Bute | PORT ANN | TARBERT LOCH FYNE
Argyll and Bute | RANNOCH | BLACKMOUNT
Argyll and Bute | RANNOCH | GLENETIVE
Argyll and Bute | RANNOCH | TYNDRUM
Argyll and Bute | STRATHLEVEN | DRYMEN
Argyll and Bute | TAYNUILT | BARCALDINE
Argyll and Bute | TAYNUILT | CONNEL
Argyll and Bute | TAYNUILT | DALMALLY
Argyll and Bute | TAYNUILT | DERVAIG
Argyll and Bute | TAYNUILT | EREDINE
Argyll and Bute | TAYNUILT | KENMORE
Argyll and Bute | TAYNUILT | KERRERA
Argyll and Bute | TAYNUILT | KILCHRENAN
Argyll and Bute | TAYNUILT | KILMELFORD PS
Argyll and Bute | TAYNUILT | KILNINVER
Argyll and Bute | TAYNUILT | KINLOCH
Argyll and Bute | TAYNUILT | LOCHDONHEAD
Argyll and Bute | TAYNUILT | OBAN
Argyll and Bute | TAYNUILT | SCAMMADALE
Argyll and Bute | TAYNUILT | TAYNUILT
Argyll and Bute | TAYNUILT | TIRORAN BRIDGE
Argyll and Bute | TUMMEL BRIDGE | KINLOCH RANNOCH
Clackmannanshire | ABERNETHY | GLENDEVON
Clackmannanshire | ABERNETHY | MILNATHORT
Clackmannanshire | BRACO | GLENEAGLES
Dundee City | CHARLESTON | CHARLESTON
Dundee City | CHARLESTON | GOURDIE
Dundee City | CHARLESTON | MENZIESHILL
Dundee City | CHARLESTON | NINEWELLS
Dundee City | COUPAR ANGUS | LEOCH
Dundee City | DUDHOPE | CONSTABLE STREET
Dundee City | DUDHOPE | ROSEBANK STREET
Dundee City | GLENAGNES | OVERGATE
Dundee City | GLENAGNES | WALTON
Dundee City | LYNDHURST | LOCHEE
Dundee City | LYNDHURST | LYNDHURST
Dundee City | LYNDHURST | MACALPINE ROAD
Dundee City | LYNDHURST | WEST KIRKTON
Dundee City | MILTON OF CRAIGIE | ASHLUDIE
Dundee City | MILTON OF CRAIGIE | BALDOVIE
Dundee City | MILTON OF CRAIGIE | BROUGHTY FERRY
Dundee City | MILTON OF CRAIGIE | EDZELL STREET
Dundee City | MILTON OF CRAIGIE | LONGHAUGH
Dundee City | MILTON OF CRAIGIE | MILTON OF CRAIGIE
Dundee City | MILTON OF CRAIGIE | OLD CRAIGIE ROAD
East Dunbartonshire | BRACO | KIPPEN
East Dunbartonshire | STRATHLEVEN | KEPCULLOCH
East Dunbartonshire | STRATHLEVEN | KILLEARN
Eilean Siar | ARDMORE | AIRD
Eilean Siar | ARDMORE | CLACHAN
Eilean Siar | ARDMORE | DRIMORE
Eilean Siar | ARDMORE | LOCH CARNAN
Eilean Siar | ARDMORE | POLLACHAR
Eilean Siar | ARDMORE | STOCKINISH
Eilean Siar | ARDMORE | TARBERT
Eilean Siar | STORNOWAY | ARNISH
Eilean Siar | STORNOWAY | BARVAS
Eilean Siar | STORNOWAY | BATTERY POINT
Eilean Siar | STORNOWAY | CALLANISH
Eilean Siar | STORNOWAY | COLL
Eilean Siar | STORNOWAY | GISLA
Eilean Siar | STORNOWAY | HARRIS GRID
Eilean Siar | STORNOWAY | LAXAY
Eilean Siar | STORNOWAY | MAARUIG
Fife | ABERNETHY | ABERNETHY
Fife | ABERNETHY | BRIDGE OF EARN
Fife | ABERNETHY | GLENDEVON
Fife | ABERNETHY | MILNATHORT
Highland | ALNESS | BALALDIE
Highland | ALNESS | CONTULLICH
Highland | ALNESS | CROSSHILLS
Highland | ALNESS | GLASTULLICH
Highland | ALNESS | INVERGORDON
Highland | ALNESS | NIGG
Highland | ALNESS | PEDDIESTON
Highland | ALNESS | TAIN
Highland | BEAULY | AIGAS
Highland | BEAULY | BLACKSTAND
Highland | BEAULY | CONON BRIDGE
Highland | BEAULY | DINGWALL
Highland | BEAULY | KILTARLITY
Highland | BEAULY | MARYBANK
Highland | BEAULY | MUIR OF ORD
Highland | BEAULY | MUIREND
Highland | BOAT OF GARTEN | AVIEMORE
Highland | BOAT OF GARTEN | BALLINDALLOCH
Highland | BOAT OF GARTEN | BOAT OF GARTEN 11 kV
Highland | BOAT OF GARTEN | DALWHINNIE
Highland | BOAT OF GARTEN | GRANTOWN
Highland | BOAT OF GARTEN | KINGUSSIE
Highland | BOAT OF GARTEN | TOMATIN
Highland | BROADFORD | ACHINTEE
Highland | BROADFORD | BROADFORD
Highland | BROADFORD | KALNAKIL
Highland | BROADFORD | KISHORNHILL
Highland | BROADFORD | KYLE
Highland | BROADFORD | LOWER OLLACH
Highland | BROADFORD | NOSTIE BRIDGE
Highland | BROADFORD | SHIELDAIG
Highland | BROADFORD | SKULAMUS
Highland | BRORA | DORNOCH
Highland | BRORA | GOLSPIE
Highland | BRORA | HELMSDALE
Highland | CASSLEY | OVERSCAIG
Highland | CASSLEY | RHICONICH
Highland | CEANNACROC | DRUMNADROCHIT
Highland | DOUNREAY | BETTYHILL
Highland | DOUNREAY | COLDBACKIE
Highland | DOUNREAY | DOUNREAY
Highland | DOUNREAY | FORSS
Highland | DUNOON | DUNOON
Highland | DUNVEGAN | DRYNOCH
Highland | DUNVEGAN | DUNVEGAN GRID
Highland | DUNVEGAN | PORTREE
Highland | DUNVEGAN | UIG
Highland | FORT AUGUSTUS | ABERCHALDER
Highland | FORT AUGUSTUS | ARDOCHY
Highland | FORT AUGUSTUS | BUNOICH
Highland | FORT AUGUSTUS | GLEN LAOGH
Highland | FORT AUGUSTUS | GLENDOE PRIMARY
Highland | FORT AUGUSTUS | INVERGARRY
Highland | FORT WILLIAM | ANNAT
Highland | FORT WILLIAM | ARISAIG
Highland | FORT WILLIAM | CORRAN
Highland | FORT WILLIAM | FISHNISH
Highland | FORT WILLIAM | GLENUIG
Highland | FORT WILLIAM | INVERLOCHY
Highland | FORT WILLIAM | KINGAIRLOCH
Highland | FORT WILLIAM | KINLOCHMOIDART
Highland | FORT WILLIAM | LIDDESDALE
Highland | FORT WILLIAM | LOCHALINE
Highland | FORT WILLIAM | MALLAIG
Highland | FORT WILLIAM | PINEGROVE
Highland | FORT WILLIAM | POOR HOUSE
Highland | FORT WILLIAM | RAHOY
Highland | FORT WILLIAM | SHONA BEAG
Highland | FORT WILLIAM | STRONTIAN
Highland | GRUDIE BRIDGE | ACHILTIBUIE
Highland | GRUDIE BRIDGE | AULTBEA
Highland | GRUDIE BRIDGE | BIDEN CLAN RAONAILD
Highland | GRUDIE BRIDGE | CONON FALLS
Highland | GRUDIE BRIDGE | DRUMRUNIE
Highland | GRUDIE BRIDGE | GARBAT FOREST
Highland | GRUDIE BRIDGE | GRUDIE BRIDGE
Highland | GRUDIE BRIDGE | INVERBROOM
Highland | GRUDIE BRIDGE | KERRY FALLS
Highland | GRUDIE BRIDGE | KINLOCHEWE
Highland | GRUDIE BRIDGE | LETTEREWE
Highland | GRUDIE BRIDGE | LOCH GLASCARNOCH
Highland | GRUDIE BRIDGE | LOCHINVER
Highland | GRUDIE BRIDGE | ULLAPOOL
Highland | INVERNESS | CULLODEN
Highland | INVERNESS | DALNEIGH
Highland | INVERNESS | ERROGIE
Highland | INVERNESS | FOYERS
Highland | INVERNESS | HILTON
Highland | INVERNESS | INVERARNIE
Highland | INVERNESS | INVERNESS 11 kV
Highland | INVERNESS | RAIGMORE
Highland | INVERNESS | WATERLOO PLACE
Highland | KEITH | ABERLOUR
Argyll and Bute | KILLIN | CHAORACH
Highland | KILLIN | WESTER DRUMMOND
Highland | KINLOCHLEVEN | GLENCOE
Highland | KINLOCHLEVEN | KINLOCHLEVEN
Highland | LAIRG | LAIRG GRID
Highland | LAIRG | TORBOLL
Highland | LAIRG | TRESSADY
Highland | MYBSTER | LATHERON
Highland | MYBSTER | MELVICH
Highland | MYBSTER | WICK
Highland | NAIRN | ARDERSIER
Highland | NAIRN | DALCROSS
Highland | NAIRN | FORRES
Highland | NAIRN | LETHEN
Highland | NAIRN | NAIRN CENTRAL
Highland | QUOICH | QUOICH PRIMARY
Highland | RANNOCH | BLACKMOUNT
Highland | RANNOCH | BRIDGE OF GAUR
Highland | RANNOCH | GLENETIVE
Highland | SHIN | GLEDFIELD
Highland | SHIN | SHIN
Highland | ST FILLANS | COMRIE
Highland | TAYNUILT | BARCALDINE
Highland | TAYNUILT | SALEN 2
Highland | THURSO | HALKIRK
Highland | THURSO | HASTIGROW
Highland | THURSO | MOUNT PLEASANT
Highland | THURSO | ORMLIE
Highland | TUMMEL BRIDGE | BONSKEID
Highland | TUMMEL BRIDGE | CALVINE
Highland | TUMMEL BRIDGE | KINLOCH RANNOCH
Moray | BOAT OF GARTEN | AVIEMORE
Moray | BOAT OF GARTEN | BALLINDALLOCH
Moray | BOAT OF GARTEN | GRANTOWN
Moray | ELGIN | ASHGROVE
Moray | ELGIN | BILBOHALL
Moray | ELGIN | BURGHEAD
Moray | ELGIN | CUMMING STREET
Moray | ELGIN | ELGIN
Moray | ELGIN | FOCHABERS
Moray | ELGIN | KINLOSS
Moray | ELGIN | LHANBRYDE
Moray | ELGIN | LOSSIEMOUTH
Moray | KEITH | ABERLOUR
Moray | KEITH | BUCKIE
Moray | KEITH | CULLEN
Moray | KEITH | DUFFTOWN
Moray | KEITH | HUNTLY
Moray | KEITH | KEITH
Moray | KEITH | LIMEHILLOCKS
Moray | KEITH | MARNOCH
Moray | KEITH | ROTHES
Moray | MACDUFF | PORTSOY
Moray | NAIRN | FORRES
Moray | NAIRN | LETHEN
Moray | NAIRN | NAIRN CENTRAL
Moray | TARLAND | BALLATER
Moray | TARLAND | MOSSAT
Moray | TARLAND | STRATHDON
North Ayrshire | CARRADALE | BALLIEKINE
North Ayrshire | CARRADALE | BRODICK
North Ayrshire | CARRADALE | MACHRIE
North Ayrshire | CARRADALE | WHITING BAY
North Ayrshire | DUNOON | BRUCHAG
North Lanarkshire | BRACO | KIPPEN
Orkney Islands | THURSO | BURGARHILL
Orkney Islands | THURSO | EDAY
Orkney Islands | THURSO | EDAY TIDAL
Orkney Islands | THURSO | FLOTTA
Orkney Islands | THURSO | KIRKWALL
Orkney Islands | THURSO | LYNESS
Orkney Islands | THURSO | NORTH HOY
Orkney Islands | THURSO | RACKWICK
Orkney Islands | THURSO | ROUSAY
Orkney Islands | THURSO | SANDAY
Orkney Islands | THURSO | SHAPINSAY
Orkney Islands | THURSO | ST MARYS
Orkney Islands | THURSO | STROMNESS
Orkney Islands | THURSO | STRONSAY
Orkney Islands | THURSO | WESTRAY
Perth and Kinross | ABERNETHY | ABERNETHY
Perth and Kinross | ABERNETHY | BALBEGGIE
Perth and Kinross | ABERNETHY | BRIDGE OF EARN
Perth and Kinross | ABERNETHY | ERROL
Perth and Kinross | ABERNETHY | GLENDEVON
Perth and Kinross | ABERNETHY | HARBOUR
Perth and Kinross | ABERNETHY | MILNATHORT
Perth and Kinross | ABERNETHY | SCONE
Perth and Kinross | BOAT OF GARTEN | AVIEMORE
Perth and Kinross | BOAT OF GARTEN | DALWHINNIE
Perth and Kinross | BOAT OF GARTEN | KINGUSSIE
Perth and Kinross | BRACO | CALLANDER
Perth and Kinross | BRACO | CRIEFF
Perth and Kinross | BRACO | DUNBLANE
Perth and Kinross | BRACO | FORTEVIOT
Perth and Kinross | BRACO | GLENEAGLES
Perth and Kinross | BURGHMUIR | BURGHMUIR
Perth and Kinross | BURGHMUIR | GOODLYBURN
Perth and Kinross | BURGHMUIR | INVERALMOND
Perth and Kinross | BURGHMUIR | REDGORTON
Perth and Kinross | BURGHMUIR | THIMBLEROW
Perth and Kinross | CHARLESTON | GOURDIE
Perth and Kinross | CHARLESTON | NINEWELLS
Perth and Kinross | COUPAR ANGUS | ALYTH
Perth and Kinross | COUPAR ANGUS | BLAIRGOWRIE
Perth and Kinross | COUPAR ANGUS | CAPUTH
Perth and Kinross | COUPAR ANGUS | COUPAR ANGUS
Perth and Kinross | COUPAR ANGUS | DALRULZION
Perth and Kinross | COUPAR ANGUS | LEOCH
Perth and Kinross | FORT WILLIAM | INVERLOCHY
Perth and Kinross | KILLIN | CASHLIE
Perth and Kinross | KILLIN | CHAORACH
Perth and Kinross | KILLIN | COSHIEVILLE
Perth and Kinross | KILLIN | KILLIN TOWN
Perth and Kinross | KILLIN | LOCHEARNHEAD
Perth and Kinross | LUNANHEAD | MARYTON
Perth and Kinross | RANNOCH | BLACKMOUNT
Perth and Kinross | RANNOCH | BRIDGE OF GAUR
Perth and Kinross | RANNOCH | GLENETIVE
Perth and Kinross | RANNOCH | TYNDRUM
Perth and Kinross | ST FILLANS | DALCHONZIE
Perth and Kinross | ST FILLANS | ST FILLANS P S
Perth and Kinross | TARLAND | BALLATER
Perth and Kinross | TUMMEL BRIDGE | ABERFELDY
Perth and Kinross | TUMMEL BRIDGE | BONSKEID
Perth and Kinross | TUMMEL BRIDGE | CALVINE
Perth and Kinross | TUMMEL BRIDGE | FINCASTLE
Perth and Kinross | TUMMEL BRIDGE | KINLOCH RANNOCH
Perth and Kinross | TUMMEL BRIDGE | PITLOCHRY
Shetland Islands | SHETLAND | FIRTH
Shetland Islands | SHETLAND | GUTCHER
Shetland Islands | SHETLAND | MID YELL
Shetland Islands | SHETLAND | SANDWICK
Shetland Islands | SHETLAND | SCALLOWAY
Shetland Islands | SHETLAND | SUMBURGH
Shetland Islands | SHETLAND | TUMBLIN
Shetland Islands | SHETLAND | UNST
Shetland Islands | SHETLAND | VOE
Shetland Islands | WOODHILL | BRAE
Stirling | BRACO | CALLANDER
Stirling | BRACO | DUNBLANE
Stirling | BRACO | GLENEAGLES
Stirling | BRACO | KIPPEN
Stirling | KILLIN | ARCHYLE
Stirling | KILLIN | CASHLIE
Stirling | KILLIN | CHAORACH
Stirling | KILLIN | COSHIEVILLE
Stirling | KILLIN | KILLIN TOWN
Stirling | KILLIN | LOCHEARNHEAD
Stirling | KILLIN | LUBNAIG
Stirling | RANNOCH | TYNDRUM
Stirling | ST FILLANS | DALCHONZIE
Stirling | ST FILLANS | ST FILLANS P S
Stirling | STRATHLEVEN | ABERFOYLE
Stirling | STRATHLEVEN | DRYMEN
Stirling | STRATHLEVEN | KEPCULLOCH
Stirling | STRATHLEVEN | KILLEARN
Stirling | TAYNUILT | DALMALLY
West Dunbartonshire | STRATHLEVEN | BLAIRLINNANS
West Dunbartonshire | STRATHLEVEN | DRYMEN
West Dunbartonshire | STRATHLEVEN | KILLEARN

## EISD
| GSPs in November 2023 LTDS | Demand |  | Generation |  | Comments (optional)
|  | EISD | Under review at freeze date? | EISD | Under review at freeze date?
| Abernethy | 2028 | Under active review | 2028 | Under active review
| Braco | 2024 | Under active review | 2035 | Under active review
| Burghmuir | 2028 | Under active review | 2028 | Under active review
| Coupar Angus | NA |  | 2028 | Under active review
| Killin | 2024 | Under active review | 2030 | Under active review
| Rannoch | 2024 | Under active review | 2025 | Under active review
| St Fillans | 2024 | Under active review | 2028 | Under active review
| Tummel Bridge | 2024 | Under active review | 2025 | Under active review
| Redmoss | NA |  | NA
| Woodhill | NA |  | NA
| Ardkinglas | 2024 | Under active review | 2030 | Under active review
| Ardmore | NA | Under active review | 2026 | Under active review
| Cassley | NA | Under active review | 2028 | Under active review
| Charleston | 2030 | Under active review | 2028 | Under active review
| Clayhills | NA |  | 2030 | Under active review
| Lyndhurst | 2032 | Under active review | 2030 | Under active review
| Peterhead Grange | 2033 | Under active review | 2026 | Under active review
| Dunbeath | NA |  | 2028 | Under active review
| Alness | NA |  | 2030 | Under active review
| Beauly | NA |  | 2030 | Under active review
| Broadford | 2026 | Under active review | 2026 | Under active review
| Brora | NA |  | 2030 | Under active review
| Dunvegan | NA |  | 2026 | Under active review
| Fasnakyle | 2024 | Under active review | 2027 | Under active review
| Grudie Bridge | NA |  | NA
| Lairg | NA |  | 2030 | Under active review
| Shin | NA |  | 2027 | Under active review
| Orrin | NA |  | NA
| Dounreay | NA |  | 2027 | Under active review
| Fraserburgh | 2033 | Under active review | 2033 | Under active review
| Dallas | 2024 | Under active review | NA
| Kinlochleven | 2024 | Under active review | NA
| Glenfarclas | 2024 | Under active review | NA
| Berryburn | 2024 | Under active review | 2030 | Under active review
| Fetteresso | NA |  | 2028 | Under active review
| Craigiebuckler | NA |  | NA
| Kintore | 2032 | Under active review | 2032 | Under active review
| Tarland | NA |  | 2032 | Under active review
| Willowdale | NA |  | NA
| Dyce | 2025 | Under active review | 2025 | Under active review
| Persley | NA |  | NA
| Peterhead Shell | NA |  | NA
| Strichen | 2033 | Under active review | 2033 | Under active review
| Arbroath | 2026 | Under active review | 2032 | Under active review
| Bridge of Dun | NA |  | 2032 | Under active review
| Fiddes | NA |  | 2032 | Under active review
| Lunanhead | 2028 | Under active review | 2028 | Under active review
| Milton of Craigie | NA |  | 2030 | Under active review
| Ceannacroc | NA |  | NA
| Fort Augustus | 2029 | Under active review | 2029 | Under active review
| Quoich | NA |  | NA
| Boat of Garten | 2024 | Under active review | 2028 | Under active review
| Inverness | NA |  | 2024 | Under active review
| Nairn | 2027 | Under active review | 2027 | Under active review
| Rothienorman | 2033 | Under active review | 2033 | Under active review
| Cairnford | NA |  | NA
| Elgin | 2024 | Under active review | 2027 | Under active review
| Keith 1 | 2028 | Under active review | 2028 | Under active review
| Keith 2 | 2028 | Under active review | 2028 | Under active review
| MacDuff | NA |  | 2028 | Under active review
| Carradale 1 | 2024 | Under active review | 2034 | Under active review
| Carradale 2 | 2024 | Under active review | 2034 | Under active review
| Clachan | 2024 | Under active review | 2030 | Under active review
| Dunoon | 2024 | Under active review | 2028 | Under active review
| Fort William | 2024 | Under active review | 2024 | Under active review
| Port Ann | 2027 | Under active review | 2034 | Under active review
| Taynuilt | 2024 | Under active review | 2034 | Under active review
| Dudhope | NA |  | 2028 | Under active review
| Mybster 1 | NA |  | NA
| Mybster 2 | NA |  | NA
| Thurso | NA |  | NA
| Sloy | 2024 | Under active review | 2030 | Under active review
| St Fergus Gas | NA |  | 2033 | Under active review
Links to additional public-domain information related to the EISDs, provided by the Transmission Owner
https://www.ssen-transmission.co.uk/customer-connections/transmission-owner-reinforcement-instruction-tori-quarterly-update-reports/
2023-03-01 | Transmission Owner's freeze date
SHEPD | DNO Licence area
SSEN Transmisson | Transmision Owner providing
2023-03-01 | Last update (version, date)
Notes
1 Earliest in service dates (EISDs) represent a snapshot of the Transmission Owner's view at the 'freeze date' of the earliest date for connection for NEW applications for demand and generation of significant size (>1MW)
For customers which already have accepted connections with a DNO, DNOs may already have agreed with transmission for earlier connection dates for demand and generation customers
2 For storage, both the demand and generation EISDs may be relevant.
3 Where an EISD has not been established for a GSP, this is shown as N/A.
There is likely to be some headroom for connection because there is no constraint yet defined with defined construction works affecting connnection, this is shown as "no date restriction identified".
4 Where the tranmission owner is actively reviewing construction works and earliest in service dates for new applications may be revised e.g. due to an application for capacity affecting that GSP, this is shown as "under active review"
5 The EISDs reflect both works at a Grid Supply Point and in wider tranmission network.
6 Unlike the rest of the DNO Network Scenario Headroom Reports, this is a snapshot of current status based on connection applications, not a scenario based output.
7 The list of GSPs includes at a minimum the GSPs associated with the primary substations and Bulk Supply Points in the DNO's last Long Term Development Statement Table 3. Future new GSPs may not be included.