## Contents
SEPD Network Scenario Headroom Report 2025 Summary
Our Network Scenario Headroom Report (NSHR) is published to enable customers, developers, generators, local authorities and other interested third parties to view the possible headroom capacity at our Primary Substations and Bulk Supply Points (BSP) up to 2050. SSEN have used the latest Distribution Future Energy Scenarios (DFES) data to inform four scenarios of demand and generation forecasts. SSEN's best view of the future demand and generation needs on our network is aligned to the Holistic Transition scenario, moving from Consumer Transformation which was our best view in the 2024 NSHR. Although the NSHR provides a view of the future in terms of our potential available capacity and constraints on our network, we would encourage any party using this information in their decision-making process to engage with us ahead of making an application to connect or offer flexible services.
Network Headroom Report Contents
Tab | Description
Key Information | This tab provides some additional detail to assist users with how to read the data presented within this report.
Primary Headroom Dem | This tab provides the demand headroom capacity at each of our Primary substations, grid references, connectivity upto the Grid Supply Point and upstream constraints.
Primary Headroom Gen | This tab provides the generation headroom capacity at each of our Primary substations, grid references, connectivity upto the Grid Supply Point and upstream constraints.
BSP Headroom Dem | This tab provides the demand headroom capacity at each of our BSP, grid references, connectivity upto the Grid Supply Point and upstream constraints.
BSP Headroom Gen | This tab provides the demand headroom capacity at each of our BSP, grid references, connectivity upto the Grid Supply Point and upstream constraints.
LEP Reference | This tab provides information on the LEPs, local authorities and the connected GSPs, BSPs and Primaries that support those areas
ESID | To indicate potential transmission constraints by 'Earliest in Service Date' per Grid Supply Point (GSP)
May 2025 Version 1.1

## Key Information
SEPD Network Scenario Headroom Report 2025 Key Information
Our Network Scenario Headroom Report (NSHR) has been developed to be used in conjunction with our other documents that combine to make the full Network Development Plan; the other documents to reference are the Network Development Plan Methodology & Assumptions and Network Development Report. The capacity that demand and generation growth is measured against is the firm capacity of the primary substation or BSP as per our Load Indices submission to Ofgem and as indicated by our Long Term Development Statement. Firm capacity means the available capacity on the network with a single feed on outage; for instance a twin transformer sites firm capacity would be the lowest capacity available on a single transformer. For single transformer sites, the firm capacity is based on the backfeed supply available to restore supplies; this may be limited by the backfeed circuit capacity rather than the transformer providing the backfeed. In order to identify future overloaded network assets, forecasts are created which combine our long term DFES projections with the estimated contribution from our connections pipeline after appropriate diversity factors have been applied. When reviewing the headroom reports for demand and generation the following applies: GREEN and POSTIVE VALUES = Capacity is forecast to be available RED and NEGATIVE VALUES = There are constraints forecast It must be noted that forecasts in RED do not mean that connections cannot be made; there are opportunities through flexible services that can enable connections without triggering network reinforcement. We would encourage any developer, generator or customer to contact us to discuss their connection and available opportuinites to connect. The data shown within this NSHR is used by us to identify long term investment opportunities where there are constraints highlighted. As the forecast is scenario based, these constraints are subject to change and will be reviewed and published annually by SEPD. Please note that our DFES scenario naming convention has been updated since 2024 to more closely align with the updated NESO Future Energy Scenario (FES) pathways framework. Published annually, the FES framework outlines different scenarios for the future of the whole energy system. SSEN's DFES builds on the FES scenarios by engaging a diverse and expert range of stakeholders, undertaking detailed investigations into the pipeline of projects seeking to connect, and reflecting extensive industry and local area insight to forecast future load on SSEN’s network.
New DFES Scenario | Previous DFES Scenario | FES Pathway Description
Electric Engagement (EE) | Consumer Transformation (CT) | Net zero met through mainly electrified demand. Consumers are highly engaged in the energy transition through smart technologies that reduce energy demands, utilising technologies such as electric heat pumps and electric vehicles.
Holistic Transition (HT) | Leading the Way (LW) | Net zero met through a mix of electrification and hydrogen, with hydrogen mainly around industrial clusters. Consumer engagement in the transition is very strong with demand shifting, with smart homes and electric vehicles providing flexibility to the grid.
Hydrogen Evolution (HE) | System Transformation (ST) | Net zero met through fast progress for hydrogen in industry and heat. Many consumers will have hydrogen boilers, though energy efficiency will be key to reducing cost. There are low levels of consumer engagement. Hydrogen will be prevalent for heavy goods vehicles but electric car uptake is strong.
Counterfactual (CF) | Falling Short (FS) | Net zero missed, though some progress is made for decarbonisation compared to today. While home insulation improves, there is still a heavy reliance on gas across all sectors, particularly power and space heating. Electric vehicle uptake is slower than the net zero pathways, but still displaces petrol and diesel.
May 2025
Version 1.1

## Primary Headroom Dem
Grid Supply Point | Bulk Supply Point | Primary Substation | Scenario | Grid Reference | Upstream Constraint (YES / NO) | Outstanding Contracted Demand (MVA) | Demand Headroom Winter (MVA) | [12 empty] | Demand Headroom Summer (MVA) | [12 empty] | Demand Headroom Spring/Autumn (MVA)
[7 empty] | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050
MANNINGTON GSP | BOURNEMOUTH | ALDERNEY | MINIMUM HEADROOM | SZ 04270 95141 | YES | 8.378 | 1.36 | -1.0659 | -1.4526 | -2.0383 | -2.7159 | -3.5506 | -4.5322 | -5.7118 | -6.8485 | -7.7934 | -12.9067 | -15.5261 | -16.223 | 4.1552 | 1.7609 | 1.414 | 0.96191 | 0.56396 | 0.055792 | -0.52584 | -1.2799 | -2.1095 | -2.7911 | -6.5462 | -8.3769 | -13.8289 | 1.1047 | -1.407 | -1.8917 | -2.5304 | -3.1059 | -3.8243 | -4.6549 | -5.7498 | -6.8345 | -7.7325 | -12.6223 | -15.0886 | -15.7294
|  | ALDERNEY | EE |  |  |  | 1.36 | -1.0659 | -1.4526 | -2.0383 | -2.7159 | -3.5506 | -4.5322 | -5.7118 | -6.8485 | -7.7934 | -11.1567 | -12.3975 | -13.3639 | 4.1552 | 1.7609 | 1.414 | 0.96191 | 0.56396 | 0.055792 | -0.52584 | -1.2799 | -2.1095 | -2.7911 | -5.0901 | -6.6065 | -9.9779 | 1.1047 | -1.407 | -1.8917 | -2.5304 | -3.1059 | -3.8243 | -4.6549 | -5.7498 | -6.8345 | -7.7325 | -10.8998 | -11.8804 | -12.4019
|  | ALDERNEY | HT |  |  |  | 1.6457 | -0.67814 | -0.93222 | -1.3792 | -1.723 | -2.2169 | -2.9649 | -3.7241 | -4.6475 | -5.6047 | -10.022 | -12.4843 | -13.5312 | 4.4378 | 2.1538 | 1.9344 | 1.5997 | 1.3068 | 0.95375 | 0.54049 | 0.13844 | -0.38502 | -1.0044 | -4.0503 | -5.3911 | -5.7922 | 1.4924 | -0.87839 | -1.1988 | -1.6886 | -2.1151 | -2.6284 | -3.2427 | -3.8631 | -4.6927 | -5.6049 | -9.7896 | -11.7457 | -12.4039
|  | ALDERNEY | HE |  |  |  | 1.5692 | -0.79344 | -1.1016 | -1.5506 | -2.1067 | -2.8924 | -3.8047 | -4.7904 | -5.9751 | -7.2077 | -12.9067 | -15.5261 | -16.223 | 4.3562 | 2.0221 | 1.7395 | 1.3578 | 0.95171 | 0.47416 | -0.066657 | -0.63502 | -1.4575 | -2.3718 | -6.5462 | -8.3769 | -10.4616 | 1.3843 | -1.0457 | -1.4447 | -1.9855 | -2.5641 | -3.2366 | -4.007 | -4.8631 | -5.9937 | -7.1743 | -12.6223 | -15.0886 | -15.7294
|  | ALDERNEY | CF |  |  |  | 1.7825 | -0.47303 | -0.6363 | -0.8363 | -1.0659 | -1.323 | -1.6108 | -2.1067 | -2.7781 | -3.3526 | -7.5924 | -11.373 | -13.8506 | 4.5338 | 2.2864 | 2.1466 | 1.9558 | 1.7354 | 1.4915 | 1.215 | 0.84049 | 0.41498 | 0.064976 | -2.8371 | -7.1044 | -13.8289 | 1.6516 | -0.63247 | -0.84472 | -1.1039 | -1.4039 | -1.7315 | -2.0998 | -2.6121 | -3.1927 | -3.6855 | -7.5692 | -11.1692 | -13.5008
BRAMLEY (FLEE) | ALDERSHOT BSP | ALDERSHOT | MINIMUM HEADROOM | SU 85976 48834 | YES | 1.939 | 6.1663 | 5.6684 | 5.051 | 4.701 | 3.9724 | 3.1724 | 2.0653 | 0.82653 | -0.37857 | -1.2714 | -6.9653 | -9.9908 | -10.5724 | 9.0939 | 8.6959 | 8.1898 | 7.9102 | 7.3316 | 6.6949 | 5.901 | 4.9827 | 4.0776 | 3.401 | -0.32755 | -4.7235 | -14.8541 | 7.5888 | 7.1265 | 6.5235 | 6.098 | 5.2684 | 4.3612 | 3.2898 | 2.0204 | 0.80816 | -0.17857 | -5.8878 | -8.7378 | -9.2735
|  | ALDERSHOT | EE |  |  |  | 6.1663 | 5.6684 | 5.051 | 4.701 | 3.9724 | 3.1724 | 2.0653 | 0.82653 | -0.37857 | -1.2714 | -5.3041 | -7.6969 | -8.8837 | 9.0939 | 8.6959 | 8.1898 | 7.9102 | 7.3316 | 6.6949 | 5.901 | 4.9827 | 4.0776 | 3.401 | 0.020408 | -3.2571 | -8.0449 | 7.5888 | 7.1265 | 6.5235 | 6.098 | 5.2684 | 4.3612 | 3.2898 | 2.0204 | 0.80816 | -0.17857 | -3.6061 | -5.0765 | -6.098
|  | ALDERSHOT | HT |  |  |  | 6.5286 | 6.1602 | 5.7122 | 5.2306 | 4.6051 | 3.9051 | 3.3806 | 2.4194 | 1.4173 | 0.38061 | -4.7 | -7.7143 | -8.9163 | 9.4296 | 9.1949 | 8.8959 | 8.5806 | 8.1765 | 7.7173 | 7.4857 | 6.9092 | 6.2949 | 5.6531 | 2.7082 | 1.1684 | 0.61429 | 7.9673 | 7.6276 | 7.2051 | 6.7714 | 6.1878 | 5.5296 | 5.1133 | 4.2184 | 3.2857 | 2.3194 | -2.3633 | -5.0694 | -6.0827
|  | ALDERSHOT | HE |  |  |  | 6.4622 | 6.0724 | 5.5878 | 5.0806 | 4.4286 | 3.6765 | 3.1071 | 2.1 | 0.91327 | -0.49388 | -6.9653 | -9.9908 | -10.5724 | 9.3265 | 9.0122 | 8.6143 | 8.2031 | 7.6857 | 7.0867 | 6.6959 | 5.9357 | 5.1265 | 4.2694 | -0.32755 | -4.1316 | -8.8163 | 7.9031 | 7.5459 | 7.0908 | 6.6255 | 5.8806 | 4.9918 | 4.1265 | 2.9235 | 1.6398 | 0.28878 | -5.8878 | -8.7378 | -9.2735
|  | ALDERSHOT | CF |  |  |  | 6.7061 | 6.4969 | 6.2194 | 5.9582 | 5.6337 | 5.2714 | 4.8643 | 4.7224 | 4.2031 | 3.6571 | -0.74796 | -4.9469 | -7.6 | 9.4684 | 9.249 | 8.9592 | 8.6745 | 8.3286 | 7.9133 | 7.4347 | 7.152 | 6.5633 | 5.9347 | 1.5673 | -4.7235 | -14.8541 | 8.1143 | 7.9071 | 7.6316 | 7.3878 | 7.0653 | 6.7112 | 6.3143 | 5.9245 | 5.2337 | 4.502 | 0.013265 | -3.9765 | -6.4592
MELKSHAM GSP | CHIPPENHAM | ALDERTON | MINIMUM HEADROOM | ST 84609 84059 | YES | 0.104 | 0.97041 | 0.87857 | 0.75714 | 0.65816 | 0.51633 | 10.6403 | 10.5087 | 10.2607 | 9.9934 | 9.8883 | 9.3852 | 9.1893 | 8.9923 | 1.6796 | 1.6133 | 1.5265 | 1.4561 | 1.349 | 10.8398 | 10.7408 | 10.5673 | 10.3867 | 10.3133 | 9.9765 | 9.5949 | 8.6398 | 1.2357 | 1.152 | 1.0378 | 0.94898 | 0.82041 | 10.5837 | 10.4551 | 10.2286 | 9.9888 | 9.8888 | 9.4153 | 9.2439 | 9.0765
|  | ALDERTON | EE |  |  |  | 0.97041 | 0.87857 | 0.75714 | 0.65816 | 0.51633 | 10.6403 | 10.5087 | 10.2607 | 9.9934 | 9.8883 | 9.3852 | 9.1893 | 9.0872 | 1.6796 | 1.6133 | 1.5265 | 1.4561 | 1.349 | 10.8398 | 10.7408 | 10.5673 | 10.3867 | 10.3133 | 9.9765 | 9.6949 | 9.2429 | 1.2357 | 1.152 | 1.0378 | 0.94898 | 0.82041 | 10.5837 | 10.4551 | 10.2286 | 9.9888 | 9.8888 | 9.4153 | 9.2439 | 9.1582
|  | ALDERTON | HT |  |  |  | 1.0347 | 0.95612 | 0.85714 | 0.77959 | 0.68776 | 10.8464 | 10.6842 | 10.4832 | 10.3168 | 10.2056 | 9.4862 | 9.2015 | 8.9923 | 1.7388 | 1.6908 | 1.6245 | 1.5755 | 1.5184 | 11.0418 | 10.9561 | 10.8327 | 10.7235 | 10.648 | 10.1959 | 10.048 | 9.9469 | 1.298 | 1.2235 | 1.1296 | 1.0582 | 0.97245 | 10.7643 | 10.6194 | 10.4378 | 10.2857 | 10.1714 | 9.5102 | 9.2541 | 9.0765
|  | ALDERTON | HE |  |  |  | 1.0316 | 0.9551 | 0.85816 | 0.78163 | 0.69184 | 10.8536 | 10.7556 | 10.5607 | 10.3342 | 10.224 | 9.4454 | 9.2566 | 9.1617 | 1.7327 | 1.6796 | 1.6092 | 1.5602 | 1.4918 | 11.0122 | 10.9449 | 10.8214 | 10.6735 | 10.5918 | 10.0265 | 9.7388 | 9.2929 | 1.2949 | 1.2214 | 1.1296 | 1.0612 | 0.97551 | 10.7704 | 10.6796 | 10.5061 | 10.302 | 10.1918 | 9.4776 | 9.3071 | 9.2276
|  | ALDERTON | CF |  |  |  | 1.0388 | 0.97449 | 0.90918 | 0.84694 | 0.76224 | 10.9556 | 10.8577 | 10.7872 | 10.6679 | 10.5362 | 9.9056 | 9.525 | 9.2444 | 1.7347 | 1.6898 | 1.6408 | 1.5969 | 1.5357 | 11.0745 | 10.9959 | 10.9378 | 10.8398 | 10.7347 | 10.1724 | 9.5949 | 8.6398 | 1.3041 | 1.2449 | 1.1796 | 1.1235 | 1.049 | 10.8735 | 10.7857 | 10.7224 | 10.6163 | 10.499 | 9.9235 | 9.5673 | 9.3031
BRAMLEY (FLEE) | ALTON | ALRESFORD | MINIMUM HEADROOM | SU 59684 32511 | YES | 5.799 | -2.221 | -2.6261 | -3.1547 | 13.9606 | 13.7433 | 13.1402 | 12.3902 | 11.6208 | 10.8861 | 10.3749 | 7.7035 | 5.8902 | 4.7392 | 1.129 | 0.84838 | 0.46165 | 12.1423 | 12.0994 | 11.6912 | 11.2025 | 10.6668 | 10.1341 | 9.8065 | 7.9219 | 5.6616 | 0.25961 | -1.6414 | -2.0169 | -2.521 | 12.4198 | 12.3259 | 11.7729 | 11.0821 | 10.3606 | 9.6657 | 9.2014 | 6.8259 | 5.2504 | 4.2188
|  | ALRESFORD | EE |  |  |  | -2.221 | -2.6261 | -3.1547 | 13.9606 | 13.7433 | 13.1402 | 12.3902 | 11.6208 | 10.8861 | 10.3749 | 7.7035 | 6.1525 | 5.0994 | 1.129 | 0.84838 | 0.46165 | 12.1423 | 12.0994 | 11.6912 | 11.2025 | 10.6668 | 10.1341 | 9.8065 | 7.9219 | 6.0321 | 3.2647 | -1.6414 | -2.0169 | -2.521 | 12.4198 | 12.3259 | 11.7729 | 11.0821 | 10.3606 | 9.6657 | 9.2014 | 6.8259 | 5.4698 | 4.5331
|  | ALRESFORD | HT |  |  |  | -2.0404 | -2.373 | -2.8108 | 14.4606 | 13.9412 | 13.3698 | 13.027 | 12.3739 | 11.7361 | 11.0606 | 7.78 | 5.8902 | 4.7392 | 1.3157 | 1.129 | 0.86063 | 12.7157 | 12.4014 | 12.0565 | 12.0147 | 11.6463 | 11.2719 | 10.8729 | 9.0545 | 8.1372 | 7.6157 | -1.4384 | -1.7312 | -2.1312 | 12.9902 | 12.5168 | 11.9933 | 11.7239 | 11.1259 | 10.531 | 9.9055 | 6.9096 | 5.2504 | 4.2188
|  | ALRESFORD | HE |  |  |  | -2.0373 | -2.3639 | -2.7873 | 14.5025 | 14.0004 | 13.4494 | 13.1749 | 12.6004 | 12.0361 | 11.4392 | 8.3086 | 6.7657 | 6.0147 | 1.2953 | 1.0821 | 0.7892 | 12.629 | 12.2912 | 11.9198 | 11.8229 | 11.4463 | 11.0606 | 10.6361 | 8.2647 | 6.2892 | 3.6372 | -1.4343 | -1.7241 | -2.1118 | 13.0229 | 12.5678 | 12.0616 | 11.8596 | 11.327 | 10.7994 | 10.2453 | 7.3545 | 5.7933 | 5.0147
|  | ALRESFORD | CF |  |  |  | -1.9414 | -2.2241 | -2.5159 | 14.8361 | 14.5035 | 14.0994 | 13.7065 | 13.3106 | 13.3647 | 13.0341 | 10.8545 | 8.8912 | 7.1963 | 1.3423 | 1.1361 | 0.92389 | 12.7688 | 12.5321 | 12.228 | 11.8963 | 11.528 | 11.5514 | 11.2259 | 8.9249 | 5.6616 | 0.25961 | -1.3526 | -1.6098 | -1.8741 | 13.3045 | 13.0086 | 12.6361 | 12.2688 | 11.877 | 12.0188 | 11.7076 | 9.6739 | 7.9025 | 6.3035
BRAMLEY (FLEE) | ALTON | ALTON LOCAL | MINIMUM HEADROOM | SU 72434 39606 | YES | 4.156 | 21.5655 | 20.5431 | 19.2563 | 17.8349 | 16.8757 | 15.8533 | 14.4288 | 12.8063 | 11.2002 | 9.9839 | 3.1655 | -1.8814 | -4.6641 | 30.6482 | 29.9584 | 29.1298 | 28.0216 | 27.289 | 26.5002 | 25.5022 | 24.3227 | 23.1502 | 22.3176 | 17.792 | 13.1839 | 0.41143 | 22.9614 | 22.0563 | 20.938 | 19.6155 | 18.7196 | 17.7543 | 16.4257 | 14.9033 | 13.3982 | 12.29 | 6.2727 | 1.8155 | -0.52735
|  | ALTON LOCAL | EE |  |  |  | 21.5655 | 20.5431 | 19.2563 | 17.8349 | 16.8757 | 15.8533 | 14.4288 | 12.8063 | 11.2002 | 9.9839 | 3.5635 | -0.76204 | -3.9641 | 30.6482 | 29.9584 | 29.1298 | 28.0216 | 27.289 | 26.5002 | 25.5022 | 24.3227 | 23.1502 | 22.3176 | 17.792 | 13.2808 | 6.5124 | 22.9614 | 22.0563 | 20.938 | 19.6155 | 18.7196 | 17.7543 | 16.4257 | 14.9033 | 13.3982 | 12.29 | 6.5614 | 2.8084 | 0.070612
|  | ALTON LOCAL | HT |  |  |  | 21.89 | 20.9829 | 19.5063 | 18.1461 | 17.6502 | 16.79 | 15.5073 | 14.0839 | 12.6114 | 11.0869 | 3.1655 | -1.8814 | -4.6641 | 31.0073 | 30.4941 | 29.5635 | 28.5982 | 28.4012 | 27.8706 | 27.1635 | 26.3359 | 25.4798 | 24.5788 | 20.2573 | 17.9022 | 16.7216 | 23.2849 | 22.5002 | 21.1941 | 19.939 | 19.5084 | 18.7155 | 17.541 | 16.2288 | 14.8737 | 13.4696 | 6.2727 | 1.8155 | -0.52735
|  | ALTON LOCAL | HE |  |  |  | 21.8992 | 21.039 | 19.6135 | 18.3124 | 17.892 | 17.1135 | 16.0818 | 14.9124 | 13.7063 | 12.4451 | 5.7155 | 1.4767 | -0.56612 | 30.9492 | 30.4053 | 29.4227 | 28.4135 | 28.1696 | 27.591 | 26.8788 | 26.0369 | 25.1553 | 24.2084 | 19.0002 | 14.39 | 8.1043 | 23.292 | 22.5512 | 21.29 | 20.0869 | 19.7267 | 19.0043 | 18.0543 | 16.9676 | 15.8471 | 14.6788 | 8.5614 | 4.8614 | 3.1798
|  | ALTON LOCAL | CF |  |  |  | 22.3257 | 22.0033 | 21.0461 | 19.8839 | 19.2012 | 18.8431 | 18.2686 | 17.7033 | 17.1594 | 16.5839 | 12.1869 | 7.4461 | 3.14 | 31.1431 | 30.8441 | 30.0665 | 29.1329 | 28.5859 | 28.3206 | 27.7451 | 27.1043 | 26.4533 | 25.7522 | 20.6594 | 13.1839 | 0.41143 | 23.6451 | 23.3492 | 22.488 | 21.4471 | 20.841 | 20.5614 | 20.0441 | 19.5084 | 18.9869 | 18.4369 | 14.3359 | 10.0737 | 6.2737
MELKSHAM GSP | ANDOVER BSP | ANDOVER | MINIMUM HEADROOM | SU 35240 46643 | YES | 2.913 | 15.1015 | 14.876 | 14.625 | 14.2903 | 13.7852 | 13.4832 | 12.6883 | 11.8454 | 11.072 | 10.2903 | 6.9505 | 4.7934 | 3.5056 | 17.524 | 17.3424 | 17.125 | 16.8403 | 16.4699 | 16.3424 | 15.8822 | 15.3444 | 14.7485 | 14.272 | 12.0801 | 9.6811 | 3.7985 | 15.5883 | 15.3566 | 15.0832 | 14.723 | 14.2352 | 14.0944 | 13.4393 | 12.6832 | 11.8515 | 11.1913 | 8.4475 | 6.6015 | 5.4873
|  | ANDOVER | EE |  |  |  | 15.1015 | 14.876 | 14.625 | 14.2903 | 13.7852 | 13.5536 | 12.8311 | 12.0046 | 11.072 | 10.2903 | 7.1056 | 5.1628 | 3.7128 | 17.524 | 17.3424 | 17.125 | 16.8403 | 16.4699 | 16.3424 | 15.8822 | 15.3444 | 14.7485 | 14.272 | 12.0801 | 10.0291 | 6.9811 | 15.5883 | 15.3566 | 15.0832 | 14.723 | 14.2352 | 14.0944 | 13.4403 | 12.6873 | 11.8515 | 11.1913 | 8.5362 | 6.922 | 5.6587
|  | ANDOVER | HT |  |  |  | 15.2403 | 15.0271 | 14.8168 | 14.524 | 14.0536 | 13.4832 | 12.6883 | 11.8454 | 11.3301 | 10.5077 | 6.9505 | 4.7934 | 3.5056 | 17.6842 | 17.5464 | 17.4117 | 17.224 | 16.9597 | 16.6362 | 16.2158 | 15.7515 | 15.575 | 15.1342 | 13.2811 | 12.276 | 11.7066 | 15.7352 | 15.5587 | 15.3505 | 15.0617 | 14.6505 | 14.1362 | 13.4393 | 12.6832 | 12.3403 | 11.6148 | 8.4475 | 6.6015 | 5.4873
|  | ANDOVER | HE |  |  |  | 15.2373 | 15.0424 | 14.8485 | 14.5913 | 14.2281 | 13.7597 | 13.1311 | 12.4015 | 11.9077 | 11.1087 | 7.822 | 5.923 | 5.0964 | 17.6495 | 17.4944 | 17.3373 | 17.1291 | 16.874 | 16.5495 | 16.1454 | 15.6668 | 15.425 | 14.9117 | 12.4781 | 10.4097 | 7.6117 | 15.7291 | 15.5658 | 15.3771 | 15.1189 | 14.7924 | 14.3617 | 13.7975 | 13.1322 | 12.8117 | 12.1138 | 9.2301 | 7.6087 | 6.9066
|  | ANDOVER | CF |  |  |  | 15.3291 | 15.2352 | 15.1026 | 14.9771 | 14.8209 | 14.6822 | 14.4964 | 14.2291 | 13.9158 | 13.5424 | 10.5046 | 8.4852 | 6.4158 | 17.6944 | 17.5903 | 17.4444 | 17.3107 | 17.1311 | 16.9485 | 16.7077 | 16.4046 | 16.0648 | 15.6883 | 13.0607 | 9.6811 | 3.7985 | 15.8128 | 15.7352 | 15.5954 | 15.4771 | 15.3046 | 15.1617 | 14.9628 | 14.6852 | 14.372 | 14.0138 | 11.4995 | 9.7505 | 8.0015
MELKSHAM GSP | ANDOVER BSP | ANDOVER EAST | MINIMUM HEADROOM | SU 37953 46433 | YES | 4.67 | 8.2982 | 7.7186 | 6.8584 | 5.8451 | 5.1778 | 4.3186 | 3.3482 | 2.3104 | 1.2747 | 0.46555 | -3.9589 | -7.8498 | -10.1651 | 10.1584 | 9.7829 | 9.1002 | 8.3594 | 7.8553 | 7.2115 | 6.5941 | 5.886 | 5.1543 | 4.588 | 1.4768 | -1.8334 | -10.3069 | 8.0982 | 7.588 | 6.8553 | 6.0258 | 5.3972 | 4.6707 | 3.8604 | 3.0013 | 2.0625 | 1.3207 | -2.7079 | -6.0896 | -8.0304
|  | ANDOVER EAST | EE |  |  |  | 8.2982 | 7.7809 | 6.8584 | 5.8451 | 5.1778 | 4.3186 | 3.3482 | 2.3104 | 1.2747 | 0.46555 | -3.8324 | -7.2926 | -9.8426 | 10.1584 | 9.7829 | 9.1002 | 8.3594 | 7.8553 | 7.2115 | 6.5941 | 5.886 | 5.1543 | 4.588 | 1.4768 | -1.8334 | -6.5151 | 8.0982 | 7.6676 | 6.8809 | 6.0258 | 5.3972 | 4.6707 | 3.8604 | 3.0013 | 2.0625 | 1.3207 | -2.6589 | -5.6202 | -7.7926
|  | ANDOVER EAST | HT |  |  |  | 8.4472 | 7.7186 | 6.8839 | 6.036 | 5.239 | 4.6645 | 3.7758 | 3.188 | 2.3135 | 1.4247 | -3.9589 | -7.8498 | -10.1651 | 10.3441 | 9.8319 | 9.2737 | 8.7084 | 8.1819 | 7.8217 | 7.3431 | 7.1115 | 6.6247 | 6.1196 | 3.3237 | 1.5237 | 0.55433 | 8.2339 | 7.588 | 6.8553 | 6.1115 | 5.4074 | 4.9125 | 4.1421 | 3.6145 | 2.8462 | 2.0686 | -2.7079 | -6.0896 | -8.0304
|  | ANDOVER EAST | HE |  |  |  | 8.4472 | 8.0074 | 7.1951 | 6.3737 | 5.5319 | 4.7992 | 4.037 | 3.5676 | 2.8207 | 2.0594 | -2.2916 | -5.6344 | -7.1722 | 10.3002 | 10.0023 | 9.4002 | 8.8002 | 8.1604 | 7.5911 | 7.0849 | 6.8207 | 6.289 | 5.7319 | 2.4329 | -0.89159 | -5.1487 | 8.2339 | 7.8737 | 7.1553 | 6.4298 | 5.6758 | 5.0145 | 4.3502 | 3.9217 | 3.2604 | 2.587 | -1.2589 | -4.1212 | -5.3987
|  | ANDOVER EAST | CF |  |  |  | 8.6247 | 8.336 | 7.9533 | 7.2737 | 6.6237 | 5.9788 | 5.4604 | 5.14 | 5.1002 | 4.7594 | 1.9482 | -1.2365 | -4.2651 | 10.3911 | 10.1513 | 9.8564 | 9.2921 | 8.7411 | 8.1482 | 7.6023 | 7.2064 | 7.0329 | 6.6135 | 3.4227 | -1.7396 | -10.3069 | 8.389 | 8.1625 | 7.8564 | 7.2615 | 6.687 | 6.1074 | 5.6421 | 5.3707 | 5.3135 | 5.0472 | 2.7013 | -0.14976 | -2.8232
MELKSHAM GSP | ANDOVER BSP | ANDOVER TOWN | MINIMUM HEADROOM | SU 36207 45078 | YES | 0.29 | 6.2362 | 6.0383 | 5.8107 | 5.5342 | 5.2372 | 5.2087 | 4.7128 | 4.174 | 3.6117 | 3.1862 | 0.60867 | -1.5403 | -2.8342 | 7.6469 | 7.4571 | 7.2276 | 6.9439 | 6.6255 | 6.6071 | 6.2224 | 5.7827 | 5.3296 | 5.0153 | 3.2449 | 0.58367 | -5.5643 | 6.1327 | 5.9306 | 5.7041 | 5.4194 | 5.0633 | 5.0755 | 4.5786 | 4.0122 | 3.4459 | 3.0663 | 0.97347 | -0.8551 | -1.9143
|  | ANDOVER TOWN | EE |  |  |  | 6.2362 | 6.0383 | 5.8107 | 5.5342 | 5.2372 | 5.2087 | 4.7128 | 4.174 | 3.6117 | 3.1862 | 0.81582 | -1.1332 | -2.627 | 7.6469 | 7.4571 | 7.2276 | 6.9439 | 6.6255 | 6.6071 | 6.2224 | 5.7827 | 5.3296 | 5.0153 | 3.2449 | 1.1163 | -2.1704 | 6.1327 | 5.9306 | 5.7041 | 5.4194 | 5.0633 | 5.0755 | 4.5786 | 4.0122 | 3.4459 | 3.0663 | 1.0918 | -0.49796 | -1.751
|  | ANDOVER TOWN | HT |  |  |  | 6.3526 | 6.1617 | 5.977 | 5.7556 | 5.5515 | 5.3026 | 4.7985 | 4.2556 | 4.0046 | 3.4903 | 0.60867 | -1.5403 | -2.8342 | 7.8184 | 7.6796 | 7.549 | 7.3755 | 7.2245 | 7.0224 | 6.7214 | 6.3776 | 6.3643 | 6.05 | 4.5163 | 3.5857 | 3.0663 | 6.2673 | 6.0847 | 5.9041 | 5.6857 | 5.4898 | 5.2388 | 4.7755 | 4.2633 | 4.0796 | 3.598 | 0.97347 | -0.8551 | -1.9143
|  | ANDOVER TOWN | HE |  |  |  | 6.3607 | 6.1893 | 6.0189 | 5.8148 | 5.6311 | 5.4056 | 5.0046 | 4.5587 | 4.4097 | 3.9995 | 1.6495 | -0.25255 | -1.2107 | 7.7908 | 7.6327 | 7.4704 | 7.2694 | 7.0857 | 6.849 | 6.5316 | 6.1633 | 6.1204 | 5.7653 | 3.7398 | 1.5969 | -1.5 | 6.2714 | 6.1041 | 5.9378 | 5.7357 | 5.5592 | 5.3347 | 4.9551 | 4.5214 | 4.4367 | 4.0429 | 1.9102 | 0.32653 | -0.4551
|  | ANDOVER TOWN | CF |  |  |  | 6.4342 | 6.3566 | 6.2434 | 6.1383 | 5.9934 | 5.8679 | 5.7036 | 5.5219 | 5.3321 | 5.1301 | 4.0066 | 2.227 | 0.48112 | 7.8204 | 7.7112 | 7.5551 | 7.4153 | 7.2255 | 7.0367 | 6.7816 | 6.4959 | 6.1837 | 5.85 | 4.0327 | 0.58367 | -5.5643 | 6.3388 | 6.2592 | 6.1418 | 6.0378 | 5.8959 | 5.7786 | 5.6163 | 5.4255 | 5.1878 | 4.9357 | 3.8571 | 2.3429 | 0.93163
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | ARBORFIELD | MINIMUM HEADROOM | SU 75949 65766 | YES | 8.32 | 8.5263 | 8.1529 | 7.7131 | 7.2712 | 6.561 | 5.9049 | 5.4202 | 4.5845 | 3.6192 | 3.0692 | -2.4971 | -7.2543 | -10.8104 | 11.3675 | 11.1308 | 10.842 | 10.5543 | 10.1165 | 9.6982 | 9.5226 | 9.039 | 8.4441 | 7.9359 | 4.9778 | 2.0257 | -3.0141 | 9.4253 | 9.0865 | 8.6886 | 8.2835 | 7.6406 | 7.0426 | 6.5324 | 5.7641 | 4.8804 | 4.3345 | -0.37368 | -4.3033 | -7.1645
|  | ARBORFIELD | EE |  |  |  | 8.5263 | 8.1529 | 7.7131 | 7.2712 | 6.561 | 5.9049 | 5.6324 | 4.8824 | 3.9294 | 3.1192 | -2.0257 | -6.7298 | -10.5645 | 11.3675 | 11.1308 | 10.842 | 10.5543 | 10.1165 | 9.6982 | 9.5226 | 9.039 | 8.4441 | 7.9359 | 4.9778 | 2.0257 | -1.2457 | 9.4253 | 9.0865 | 8.6886 | 8.2835 | 7.6406 | 7.0426 | 6.6937 | 5.9978 | 5.1192 | 4.3457 | -0.031841 | -3.8655 | -6.9614
|  | ARBORFIELD | HT |  |  |  | 8.66 | 8.1978 | 7.8753 | 7.4845 | 6.7937 | 6.2029 | 5.4202 | 4.5845 | 3.6192 | 3.0692 | -2.4971 | -7.2543 | -10.8104 | 11.4788 | 11.2206 | 11.0359 | 10.8196 | 10.4359 | 10.1002 | 9.6624 | 9.191 | 8.6431 | 8.3716 | 5.5788 | 3.3104 | 1.6318 | 9.5345 | 9.1161 | 8.8131 | 8.4457 | 7.8151 | 7.2559 | 6.5324 | 5.7641 | 4.8804 | 4.3345 | -0.37368 | -4.3033 | -7.1645
|  | ARBORFIELD | HE |  |  |  | 8.661 | 8.3406 | 7.9753 | 7.6171 | 7.01 | 6.508 | 5.908 | 5.212 | 4.2988 | 3.8804 | -1.49 | -6.1512 | -9.5808 | 11.4594 | 11.2584 | 11.0288 | 10.8012 | 10.4369 | 10.1257 | 9.7461 | 9.3043 | 8.739 | 8.4482 | 5.2971 | 2.3318 | -0.79062 | 9.5375 | 9.2396 | 8.9029 | 8.5682 | 8.0141 | 7.5375 | 6.9865 | 6.3508 | 5.5202 | 5.0324 | 0.54061 | -3.2767 | -6.0533
|  | ARBORFIELD | CF |  |  |  | 8.8926 | 8.7161 | 8.5335 | 8.3722 | 8.0529 | 7.8151 | 7.658 | 7.3335 | 6.9314 | 6.4886 | 3.4386 | -2.3359 | -8.4125 | 11.589 | 11.4635 | 11.3226 | 11.1931 | 10.9675 | 10.7726 | 10.6084 | 10.3339 | 10.0114 | 9.6584 | 7.2645 | 2.8431 | -3.0141 | 9.7416 | 9.5804 | 9.4151 | 9.2671 | 8.9845 | 8.7753 | 8.6324 | 8.3498 | 7.9957 | 7.609 | 4.7406 | -0.14511 | -5.0645
LOVEDEAN GSP | CHICHESTER & HUNSTON | ARGYLE ROAD | MINIMUM HEADROOM | SZ 93193 99152 | YES | 1.433 | 12.0445 | 11.6588 | 11.2578 | 10.7731 | 10.2384 | 10.018 | 9.1333 | 8.1312 | 7.122 | 6.3659 | 2.2904 | -1.6382 | -4.031 | 15.8445 | 15.4935 | 15.1088 | 14.6455 | 14.1139 | 13.8598 | 13.1863 | 12.4118 | 11.6231 | 10.9976 | 7.4118 | 2.6057 | -9.3708 | 12.2863 | 11.9016 | 11.4731 | 10.9333 | 10.3261 | 10.1884 | 9.3608 | 8.42 | 7.4833 | 6.7731 | 3.1996 | -0.23 | -2.1371
|  | ARGYLE ROAD | EE |  |  |  | 12.0445 | 11.6588 | 11.2578 | 10.7731 | 10.2384 | 10.018 | 9.1333 | 8.1312 | 7.122 | 6.3659 | 2.4027 | -0.6749 | -3.5331 | 15.8445 | 15.4935 | 15.1088 | 14.6455 | 14.1139 | 13.8598 | 13.1863 | 12.4118 | 11.6231 | 10.9976 | 7.4118 | 3.321 | -3.1382 | 12.2863 | 11.9016 | 11.4731 | 10.9333 | 10.3261 | 10.1884 | 9.3608 | 8.42 | 7.4833 | 6.7731 | 3.2108 | 0.59041 | -1.7616
|  | ARGYLE ROAD | HT |  |  |  | 12.2424 | 11.9343 | 11.6241 | 11.2567 | 10.9027 | 10.469 | 9.6914 | 9.1618 | 8.3404 | 7.4802 | 2.2904 | -1.6382 | -4.031 | 16.0792 | 15.868 | 15.6506 | 15.3833 | 15.1159 | 14.7843 | 14.3159 | 14.0649 | 13.5516 | 13.0129 | 10.1139 | 8.119 | 7.0547 | 12.4853 | 12.2037 | 11.9129 | 11.5608 | 11.1965 | 10.7465 | 10.0067 | 9.5333 | 8.7384 | 7.9067 | 3.1996 | -0.23 | -2.1371
|  | ARGYLE ROAD | HE |  |  |  | 12.2373 | 11.9578 | 11.6771 | 11.3496 | 11.0404 | 10.6598 | 10.0139 | 9.618 | 8.9537 | 8.2608 | 4.3047 | 1.1884 | -0.46469 | 16.019 | 15.7669 | 15.5047 | 15.1904 | 14.8649 | 14.4731 | 13.9557 | 13.6424 | 13.068 | 12.4598 | 8.6894 | 4.5445 | -1.4178 | 12.4782 | 12.222 | 11.9598 | 11.6486 | 11.3292 | 10.9394 | 10.319 | 9.9751 | 9.3251 | 8.6527 | 5.0373 | 2.4557 | 1.172
|  | ARGYLE ROAD | CF |  |  |  | 12.3873 | 12.2271 | 12.07 | 11.8802 | 11.6751 | 11.4924 | 11.2506 | 10.9547 | 10.6302 | 10.6292 | 8.2608 | 5.4965 | 2.5843 | 16.1016 | 15.8976 | 15.6833 | 15.4261 | 15.1251 | 14.8006 | 14.3873 | 13.8965 | 13.37 | 13.0955 | 9.2057 | 2.6057 | -9.3708 | 12.619 | 12.4659 | 12.32 | 12.1404 | 11.9047 | 11.7149 | 11.4424 | 11.1016 | 10.7312 | 10.8322 | 8.57 | 6.0853 | 3.5802
COWLEY GSP | HEADINGTON BSP | ARNCOTT | MINIMUM HEADROOM | SP 60730 18095 | YES | 11.771 | 7.7284 | 7.3927 | 1.7876 | 0.88559 | -0.30931 | -1.7909 | -4.7134 | -7.3542 | -9.8899 | -15.1971 | -19.3654 | -20.8501 | -21.4042 | 6.438 | 6.2299 | 0.80845 | 0.36559 | -0.15788 | -0.97216 | -3.3671 | -5.6762 | -7.8569 | -13.1018 | -15.5773 | -16.2497 | -18.0783 | 6.2274 | 5.9142 | 0.37437 | -0.3491 | -1.1593 | -2.4052 | -5.0073 | -7.4022 | -9.7083 | -14.8236 | -18.3011 | -19.4991 | -19.9573
|  | ARNCOTT | EE |  |  |  | 7.7284 | 7.3927 | 1.7876 | 0.88559 | -0.13278 | -1.6144 | -4.1154 | -6.3389 | -8.2236 | -11.8328 | -19.3654 | -20.8073 | -21.2532 | 6.438 | 6.2299 | 0.80845 | 0.36559 | -0.10584 | -0.89971 | -2.763 | -4.616 | -6.2742 | -9.6946 | -15.4456 | -16.065 | -17.0589 | 6.2274 | 5.9142 | 0.37437 | -0.3491 | -1.1297 | -2.293 | -4.4869 | -6.4624 | -8.1205 | -11.5369 | -18.3011 | -19.4624 | -19.8205
|  | ARNCOTT | HT |  |  |  | 7.7774 | 7.4693 | 1.8866 | 1.0182 | -0.30931 | -1.7909 | -4.7134 | -7.3542 | -9.8899 | -15.1971 | -19.2511 | -20.8501 | -21.4042 | 6.5023 | 6.3411 | 0.96253 | 0.56049 | -0.15788 | -0.97216 | -3.3671 | -5.6762 | -7.8569 | -13.1018 | -15.3528 | -16.0211 | -16.2762 | 6.3172 | 6.0254 | 0.52233 | -0.15624 | -1.1593 | -2.4052 | -5.0073 | -7.4022 | -9.7083 | -14.8236 | -18.1991 | -19.4991 | -19.9573
|  | ARNCOTT | HE |  |  |  | 7.7764 | 7.4693 | 1.8948 | 1.0295 | 0.050898 | -1.3858 | -3.8022 | -5.9124 | -8.0011 | -11.6236 | -19.1501 | -20.6022 | -20.9471 | 6.4962 | 6.3227 | 0.936 | 0.53702 | 0.10233 | -0.67522 | -2.5324 | -4.3018 | -6.0558 | -9.4926 | -15.5773 | -16.2497 | -16.9722 | 6.3131 | 6.0244 | 0.52743 | -0.14502 | -0.87461 | -2.0287 | -4.1573 | -6.046 | -7.9124 | -11.3379 | -18.1297 | -19.3113 | -19.594
|  | ARNCOTT | CF |  |  |  | 8.1182 | 7.8254 | 2.4662 | 2.0999 | 1.557 | 0.85294 | -1.0001 | -2.7736 | -4.444 | -6.8552 | -17.5664 | -19.293 | -20.3756 | 6.737 | 6.5084 | 1.2023 | 0.98906 | 0.71049 | 0.38498 | -0.99767 | -2.312 | -3.5569 | -5.6467 | -14.7344 | -16.0079 | -18.0783 | 6.6101 | 6.3397 | 0.99171 | 0.66824 | 0.24171 | -0.28584 | -1.8124 | -3.3501 | -4.793 | -6.9879 | -16.7175 | -18.1409 | -19.0797
BRAMLEY (FLEE) | BRACKNELL | ASCOT | MINIMUM HEADROOM | SU 91615 68855 | YES | 2.055 | 18.1635 | 17.8645 | 17.5533 | 17.0666 | 16.489 | 16.2992 | 15.5492 | 14.836 | 14.1186 | 13.6002 | 11.1186 | 9.1982 | 8.4809 | 18.8247 | 18.5604 | 18.2758 | 17.8839 | 17.4227 | 17.3196 | 16.7951 | 16.2431 | 15.6717 | 15.2768 | 13.1247 | 9.6084 | 1.7992 | 17.5084 | 17.2023 | 16.8911 | 16.4186 | 15.8645 | 15.7543 | 15.0676 | 14.3809 | 13.6921 | 13.2258 | 11.1023 | 9.4564 | 8.8604
|  | ASCOT | EE |  |  |  | 18.1635 | 17.8645 | 17.5533 | 17.0666 | 16.489 | 16.2992 | 15.5492 | 14.836 | 14.1186 | 13.6002 | 11.1186 | 9.4604 | 8.9492 | 18.8247 | 18.5604 | 18.2758 | 17.8839 | 17.4227 | 17.3196 | 16.7951 | 16.2431 | 15.6717 | 15.2768 | 13.1247 | 10.7247 | 7.0196 | 17.5084 | 17.2023 | 16.8911 | 16.4186 | 15.8645 | 15.7543 | 15.0676 | 14.3809 | 13.6921 | 13.2258 | 11.1023 | 9.6921 | 9.2615
|  | ASCOT | HT |  |  |  | 18.3196 | 18.0829 | 17.8451 | 17.3604 | 16.9033 | 16.4135 | 15.8472 | 15.5839 | 14.9931 | 14.3829 | 11.2084 | 9.1982 | 8.4809 | 19.0053 | 18.8421 | 18.6788 | 18.3788 | 18.1033 | 17.787 | 17.4349 | 17.3737 | 17.0074 | 16.636 | 14.8278 | 13.8278 | 13.4594 | 17.6849 | 17.4482 | 17.2196 | 16.7839 | 16.3778 | 15.9206 | 15.387 | 15.2074 | 14.6543 | 14.086 | 11.2084 | 9.4564 | 8.8604
|  | ASCOT | HE |  |  |  | 18.3206 | 18.1023 | 17.888 | 17.5166 | 17.2176 | 16.7666 | 16.1421 | 15.8125 | 15.2615 | 14.7033 | 12.0655 | 10.3911 | 9.839 | 18.9625 | 18.7696 | 18.5635 | 18.2717 | 18.0186 | 17.6553 | 17.2064 | 17.038 | 16.5951 | 16.137 | 13.6176 | 11.1053 | 7.3962 | 17.6809 | 17.4655 | 17.2513 | 16.9053 | 16.6268 | 16.2033 | 15.6288 | 15.4053 | 14.889 | 14.3635 | 11.9502 | 10.5176 | 10.0645
|  | ASCOT | CF |  |  |  | 18.438 | 18.3125 | 18.1951 | 18.0145 | 17.7472 | 17.4166 | 17.0604 | 16.7594 | 16.789 | 16.5268 | 14.6329 | 12.49 | 10.5002 | 19.0206 | 18.8666 | 18.7043 | 18.4911 | 18.2421 | 17.9217 | 17.5462 | 17.1635 | 17.0696 | 16.6931 | 13.9686 | 9.6084 | 1.7992 | 17.788 | 17.6584 | 17.5349 | 17.3523 | 17.1145 | 16.8104 | 16.4788 | 16.1758 | 16.2482 | 15.987 | 14.1635 | 12.2839 | 10.6074
LOVEDEAN GSP | CHICHESTER & HUNSTON | ASHLING ROAD | MINIMUM HEADROOM | SU 84085 06737 | YES | 9.463 | -2.8177 | -3.9412 | 0.22922 | -1.033 | -2.4851 | -4.1381 | -6.4075 | -8.8922 | -11.0524 | -12.6993 | -20.6024 | -26.3004 | -29.5412 | 4.8833 | 4.1211 | 8.6476 | 7.7894 | 6.8078 | 5.7078 | 4.2996 | 2.7098 | 1.2486 | 0.16596 | -5.2544 | -10.4136 | -23.4493 | -1.6228 | -2.6187 | 1.6874 | 0.55269 | -0.75955 | -2.2453 | -4.2708 | -6.5126 | -8.5096 | -9.9544 | -16.9085 | -21.6647 | -24.2657
|  | ASHLING ROAD | EE |  |  |  | -2.8177 | -3.9412 | 0.22922 | -1.033 | -2.4851 | -4.1381 | -6.4075 | -8.8922 | -11.0524 | -12.6993 | -20.6024 | -25.4381 | -29.0402 | 4.8833 | 4.1211 | 8.6476 | 7.7894 | 6.8078 | 5.7078 | 4.2996 | 2.7098 | 1.2486 | 0.16596 | -5.2544 | -10.0136 | -16.7453 | -1.6228 | -2.6187 | 1.6874 | 0.55269 | -0.75955 | -2.2453 | -4.2708 | -6.5126 | -8.5096 | -9.9544 | -16.9085 | -20.93 | -23.8881
|  | ASHLING ROAD | HT |  |  |  | -2.3555 | -3.2759 | 0.69759 | -0.45649 | -1.3544 | -2.7779 | -4.8085 | -6.9708 | -8.9024 | -10.8493 | -20.4779 | -26.3004 | -29.5412 | 5.3139 | 4.7915 | 9.2435 | 8.5711 | 8.1404 | 7.3404 | 6.2772 | 5.1088 | 4.0221 | 2.9058 | -2.3269 | -5.1238 | -6.5085 | -1.1647 | -1.9544 | 2.1578 | 1.1384 | 0.38739 | -0.86159 | -2.6381 | -4.5453 | -6.282 | -8.0391 | -16.681 | -21.6647 | -24.2657
|  | ASHLING ROAD | HE |  |  |  | -2.4085 | -3.3136 | 0.66086 | -0.47588 | -1.3626 | -2.7779 | -4.6473 | -6.6871 | -8.482 | -10.2973 | -19.3993 | -24.7565 | -27.0749 | 5.2078 | 4.62 | 8.9864 | 8.2272 | 7.7017 | 6.7884 | 5.6507 | 4.369 | 3.1527 | 1.8874 | -4.7973 | -10.0718 | -16.3208 | -1.2177 | -2.0004 | 2.1109 | 1.1007 | 0.35065 | -0.89833 | -2.5412 | -4.3493 | -5.9759 | -7.6279 | -15.8514 | -20.4034 | -22.2544
|  | ASHLING ROAD | CF |  |  |  | -2.0902 | -2.7728 | 1.5425 | 0.76188 | -0.16159 | -0.80037 | -1.8698 | -3.1044 | -4.1014 | -5.1106 | -11.5106 | -17.3198 | -22.3861 | 5.3874 | 4.8956 | 9.4404 | 8.8588 | 8.1874 | 7.7333 | 6.9037 | 5.9374 | 5.0456 | 4.1129 | -2.134 | -10.4136 | -23.4493 | -0.92078 | -1.5004 | 2.9282 | 2.2404 | 1.4323 | 0.9231 | 0.0057551 | -1.0677 | -1.9647 | -2.88 | -8.7106 | -13.9391 | -18.4014
MELKSHAM GSP | NORRINGTON | ASHTON PARK | MINIMUM HEADROOM | ST 87141 57741 | YES | 17.124 | -8.6216 | -9.4339 | -10.1737 | -11.4318 | -12.8982 | -14.6727 | -16.938 | -19.689 | -22.6329 | -24.8859 | -34.539 | -41.3073 | -44.24 | -2.8308 | -3.4267 | -3.9114 | -4.8512 | -5.8706 | -6.991 | -8.3757 | -10.0655 | -11.8502 | -13.1676 | -18.8635 | -24.3267 | -36.8992 | -8.389 | -9.1951 | -9.8033 | -10.9849 | -12.3349 | -13.9135 | -15.9196 | -18.3512 | -20.9278 | -22.8114 | -30.6614 | -36.2798 | -38.7686
|  | ASHTON PARK | EE |  |  |  | -8.6216 | -9.4339 | -10.1737 | -11.4318 | -12.8982 | -14.6727 | -16.938 | -19.689 | -22.6329 | -24.8859 | -34.0859 | -40.3063 | -43.7012 | -2.8308 | -3.4267 | -3.9114 | -4.8512 | -5.8706 | -6.991 | -8.3757 | -10.0655 | -11.8502 | -13.1676 | -18.8635 | -24.0747 | -30.7206 | -8.389 | -9.1951 | -9.8033 | -10.9849 | -12.3349 | -13.9135 | -15.9196 | -18.3512 | -20.9278 | -22.8114 | -30.3869 | -35.4176 | -38.3461
|  | ASHTON PARK | HT |  |  |  | -8.3227 | -9.0318 | -10.041 | -11.2522 | -12.3227 | -14.1849 | -16.4829 | -19.1676 | -21.738 | -24.1359 | -34.539 | -41.3073 | -44.24 | -2.4849 | -2.892 | -3.5012 | -4.2982 | -4.7951 | -5.7839 | -6.9727 | -8.4002 | -9.7767 | -11.0553 | -16.338 | -19.391 | -20.6369 | -8.0165 | -8.6471 | -9.5573 | -10.6604 | -11.4992 | -13.0767 | -15.038 | -17.3298 | -19.5512 | -21.638 | -30.6614 | -36.2798 | -38.7686
|  | ASHTON PARK | HE |  |  |  | -8.3135 | -8.9461 | -9.9012 | -11.0767 | -12.0686 | -13.6512 | -15.5461 | -17.9104 | -20.4553 | -22.7716 | -32.3951 | -38.7665 | -41.0451 | -2.5471 | -2.9829 | -3.642 | -4.4961 | -5.0839 | -6.0318 | -7.1594 | -8.5727 | -10.089 | -11.5257 | -18.04 | -23.5073 | -29.7104 | -8.0145 | -8.5859 | -9.4543 | -10.5237 | -11.3012 | -12.6584 | -14.2859 | -16.3124 | -18.4931 | -20.5022 | -28.8288 | -34.0594 | -36.0053
|  | ASHTON PARK | CF |  |  |  | -8.0645 | -8.5002 | -9.0982 | -9.9369 | -10.7247 | -11.1941 | -11.9441 | -13.0563 | -14.4104 | -15.9094 | -25.1859 | -31.8778 | -36.742 | -2.4176 | -2.7778 | -3.2614 | -3.9686 | -4.6267 | -5.0002 | -5.6829 | -6.5961 | -7.6482 | -8.788 | -16.1104 | -24.3267 | -36.8992 | -7.7839 | -8.192 | -8.741 | -9.5094 | -10.239 | -10.5584 | -11.2329 | -12.2227 | -13.4043 | -14.7073 | -22.6971 | -28.3329 | -32.4022
BRAMLEY (FLEE) | BRACKNELL | BAGSHOT | MINIMUM HEADROOM | SU 91122 63523 | YES | 5.287 | 8.1271 | 7.8639 | 7.5384 | 7.3731 | 7.0302 | 6.6353 | 5.8149 | 4.8884 | 3.9608 | 3.3496 | -0.17286 | -2.98 | -4.5351 | 11.6935 | 11.4067 | 11.02 | 10.9292 | 10.5435 | 10.12 | 9.5476 | 8.8792 | 8.2016 | 7.7537 | 5.1976 | 1.3822 | -7.2259 | 8.2904 | 7.9516 | 7.5047 | 7.4169 | 6.9812 | 6.5067 | 5.7424 | 4.8731 | 4.0037 | 3.4445 | 0.40571 | -2.0269 | -3.3137
|  | BAGSHOT | EE |  |  |  | 8.1271 | 7.8639 | 7.5384 | 7.3731 | 7.0302 | 6.6353 | 5.8149 | 4.8884 | 3.9608 | 3.3496 | 0.12102 | -2.4167 | -4.2637 | 11.6935 | 11.4067 | 11.02 | 10.9292 | 10.5435 | 10.12 | 9.5476 | 8.8792 | 8.2016 | 7.7537 | 5.1976 | 2.321 | -2.1331 | 8.2904 | 7.9516 | 7.5047 | 7.4169 | 6.9812 | 6.5067 | 5.7424 | 4.8731 | 4.0037 | 3.4445 | 0.63122 | -1.5096 | -3.0688
|  | BAGSHOT | HT |  |  |  | 8.2455 | 7.9965 | 7.7118 | 7.4322 | 7.0935 | 6.7292 | 6.2047 | 5.4547 | 4.7169 | 3.9578 | -0.17286 | -2.98 | -4.5351 | 11.919 | 11.7353 | 11.5016 | 11.2771 | 10.9935 | 10.6741 | 10.5853 | 10.1404 | 9.6812 | 9.2037 | 6.972 | 5.7547 | 5.1516 | 8.5129 | 8.2404 | 7.9006 | 7.5761 | 7.169 | 6.7241 | 6.4333 | 5.7016 | 4.9608 | 4.1924 | 0.40571 | -2.0269 | -3.3137
|  | BAGSHOT | HE |  |  |  | 8.2588 | 8.0373 | 7.8006 | 7.5231 | 7.218 | 6.8812 | 6.5108 | 5.8996 | 5.2761 | 4.6618 | 1.1139 | -1.6994 | -3.0014 | 11.872 | 11.6588 | 11.4057 | 11.1098 | 10.77 | 10.3904 | 10.2782 | 9.7843 | 9.2588 | 8.7149 | 5.6241 | 2.6343 | -1.5739 | 8.5118 | 8.2639 | 7.9853 | 7.6455 | 7.271 | 6.8496 | 6.6873 | 6.0639 | 5.4159 | 4.7659 | 1.4894 | -0.70143 | -1.7167
|  | BAGSHOT | CF |  |  |  | 8.4251 | 8.2894 | 8.1465 | 8.0373 | 7.8873 | 7.7241 | 7.521 | 7.4935 | 7.2588 | 7.0139 | 4.5527 | 1.9802 | -0.43102 | 11.972 | 11.7731 | 11.5435 | 11.3404 | 11.0761 | 10.7669 | 10.3945 | 10.319 | 9.9057 | 9.4649 | 6.2659 | 1.3822 | -7.2259 | 8.6812 | 8.4996 | 8.2976 | 8.1343 | 7.9118 | 7.6527 | 7.3435 | 7.4812 | 7.1782 | 6.8578 | 4.5394 | 2.2078 | 0.15367
BRAMLEY (ANDO-THAT) | THATCHAM BSP | BALL HILL | MINIMUM HEADROOM | SU 42417 63142 | YES | 0.519 | 10.2026 | 10.0423 | 9.8934 | 9.6954 | 9.5332 | 9.1383 | 8.7964 | 8.4648 | 7.6372 | 6.9913 | 5.4209 | 4.1352 | 2.7015 | 11.9102 | 11.7949 | 11.6827 | 11.5214 | 11.3898 | 10.9082 | 10.5929 | 10.2867 | 9.3755 | 8.6867 | 7.1337 | 5.25 | 2.5939 | 10.1908 | 10.0357 | 9.8888 | 9.6939 | 9.5337 | 9.0541 | 8.6929 | 8.3418 | 7.3796 | 6.6429 | 4.9888 | 3.4663 | 1.7082
|  | BALL HILL | EE |  |  |  | 10.2026 | 10.0423 | 9.8934 | 9.6954 | 9.5332 | 9.2372 | 8.8811 | 8.5617 | 8.5077 | 8.274 | 6.9679 | 5.1974 | 4.5403 | 11.9102 | 11.7949 | 11.6827 | 11.5286 | 11.4031 | 11.1286 | 10.8163 | 10.5622 | 10.5327 | 10.3245 | 9.0918 | 6.6153 | 4.9663 | 10.1908 | 10.0357 | 9.8888 | 9.6939 | 9.5337 | 9.2173 | 8.8408 | 8.5184 | 8.5204 | 8.2837 | 6.9398 | 4.8143 | 4.0429
|  | BALL HILL | HT |  |  |  | 10.2883 | 10.173 | 10.0097 | 9.8046 | 9.6862 | 9.2954 | 8.9546 | 8.6168 | 8.3362 | 7.9005 | 6.6189 | 4.823 | 3.4995 | 11.9898 | 11.9276 | 11.8102 | 11.6439 | 11.5704 | 11.1796 | 10.8806 | 10.5837 | 10.3776 | 9.9827 | 8.9255 | 6.9765 | 5.5459 | 10.2796 | 10.1755 | 10.0112 | 9.7959 | 9.6898 | 9.251 | 8.8867 | 8.5296 | 8.249 | 7.7765 | 6.4408 | 4.3286 | 2.7806
|  | BALL HILL | HE |  |  |  | 10.2832 | 10.1679 | 9.9934 | 9.7454 | 9.5903 | 9.1383 | 8.7964 | 8.4648 | 7.6372 | 6.9913 | 5.4209 | 4.1352 | 2.7015 | 11.9745 | 11.8969 | 11.752 | 11.5214 | 11.3898 | 10.9082 | 10.5929 | 10.2867 | 9.3755 | 8.6867 | 7.1337 | 5.25 | 2.5939 | 10.2735 | 10.1724 | 9.9918 | 9.7235 | 9.5724 | 9.0541 | 8.6929 | 8.3418 | 7.3796 | 6.6429 | 4.9888 | 3.4663 | 1.7082
|  | BALL HILL | CF |  |  |  | 10.3026 | 10.1944 | 10.0954 | 9.9842 | 9.826 | 9.6964 | 9.5026 | 9.3056 | 9.1444 | 8.9189 | 7.5821 | 6.8403 | 5.7587 | 11.9847 | 11.9102 | 11.8388 | 11.751 | 11.6102 | 11.4847 | 11.2969 | 11.1071 | 10.9398 | 10.7143 | 9.2092 | 7.6204 | 4.7765 | 10.2918 | 10.1888 | 10.0969 | 9.9878 | 9.8276 | 9.7 | 9.498 | 9.2929 | 9.1357 | 8.901 | 7.4786 | 6.7071 | 5.5133
MELKSHAM GSP | ANDOVER BSP | BARTON STACEY | MINIMUM HEADROOM | SU 42075 42720 | YES | 1.005 | 12.5964 | 12.4668 | 12.3383 | 12.175 | 11.9944 | 11.6362 | 11.3301 | 10.9872 | 10.2332 | 9.626 | 7.8321 | 6.4872 | 4.9515 | 13.7694 | 13.6704 | 13.5776 | 13.4082 | 13.2602 | 12.8163 | 12.5194 | 12.1878 | 11.3347 | 10.6663 | 8.8867 | 7.0051 | 4.3867 | 12.6765 | 12.5582 | 12.4408 | 12.2571 | 12.0847 | 11.6224 | 11.2949 | 10.9367 | 10.0378 | 9.3418 | 7.4408 | 5.8786 | 4.0214
|  | BARTON STACEY | EE |  |  |  | 12.5964 | 12.4668 | 12.3383 | 12.175 | 11.9944 | 11.7791 | 11.4607 | 11.1923 | 10.7852 | 10.5719 | 9.3964 | 7.5597 | 6.8617 | 13.7694 | 13.6704 | 13.5776 | 13.4429 | 13.302 | 13.0959 | 12.8102 | 12.6 | 12.2153 | 12.0245 | 10.8827 | 8.3949 | 6.8347 | 12.6765 | 12.5582 | 12.4408 | 12.2939 | 12.1316 | 11.8969 | 11.5776 | 11.3194 | 10.8724 | 10.6541 | 9.4184 | 7.2418 | 6.4367
|  | BARTON STACEY | HT |  |  |  | 12.6597 | 12.5587 | 12.4301 | 12.2556 | 12.1219 | 11.7934 | 11.4791 | 11.124 | 10.9342 | 10.5393 | 8.9607 | 7.1087 | 5.7709 | 13.8316 | 13.7622 | 13.6673 | 13.5184 | 13.4194 | 13.0714 | 12.7847 | 12.4561 | 12.3265 | 11.948 | 10.5459 | 8.5469 | 7.101 | 12.7306 | 12.6367 | 12.5061 | 12.3286 | 12.2031 | 11.8235 | 11.4898 | 11.1143 | 10.9214 | 10.4939 | 8.8133 | 6.6684 | 5.1224
|  | BARTON STACEY | HE |  |  |  | 12.6546 | 12.5587 | 12.4199 | 12.1995 | 12.0281 | 11.6362 | 11.3301 | 10.9872 | 10.2332 | 9.626 | 7.8321 | 6.4872 | 4.9515 | 13.8194 | 13.748 | 13.6296 | 13.4082 | 13.2602 | 12.8163 | 12.5194 | 12.1878 | 11.3347 | 10.6663 | 8.8867 | 7.0051 | 4.3867 | 12.7276 | 12.6378 | 12.4939 | 12.2571 | 12.0847 | 11.6224 | 11.2949 | 10.9367 | 10.0378 | 9.3418 | 7.4408 | 5.8786 | 4.0214
|  | BARTON STACEY | CF |  |  |  | 12.6821 | 12.6005 | 12.5199 | 12.4179 | 12.2862 | 12.1321 | 11.9954 | 11.8301 | 11.6526 | 11.5015 | 10.327 | 9.2342 | 8.2434 | 13.8388 | 13.7776 | 13.7153 | 13.6347 | 13.5173 | 13.3673 | 13.2286 | 13.0571 | 12.8786 | 12.702 | 11.3327 | 9.5255 | 6.9867 | 12.7551 | 12.6755 | 12.6 | 12.5051 | 12.3745 | 12.2224 | 12.0796 | 11.9163 | 11.7398 | 11.5745 | 10.3541 | 9.152 | 8.0878
BRAMLEY (BASI) | BASINGSTOKE T1A & T2A | BASINGSTOKE | MINIMUM HEADROOM | SU 65155 52705 | YES | 3.613 | 18.2308 | 17.8859 | 17.4063 | 16.9369 | 16.391 | 15.7135 | 15.0053 | 13.8543 | 12.6267 | 11.5288 | 7.79 | 5.9573 | 4.9584 | 17.3073 | 17.1227 | 16.8308 | 16.5992 | 16.2982 | 15.8522 | 15.4267 | 14.7369 | 13.9573 | 13.242 | 10.9471 | 9.2176 | 4.0165 | 17.1267 | 16.8349 | 16.4267 | 16.0318 | 15.5563 | 14.9533 | 14.3543 | 13.3869 | 12.3155 | 11.3257 | 8.0257 | 6.2543 | 5.2869
|  | BASINGSTOKE | EE |  |  |  | 18.2308 | 17.8859 | 17.4063 | 16.9369 | 16.391 | 15.7135 | 15.0053 | 13.8543 | 12.6267 | 11.5288 | 7.9737 | 6.7543 | 6.0298 | 17.3073 | 17.1227 | 16.8308 | 16.5992 | 16.2982 | 15.8522 | 15.4267 | 14.7369 | 13.9573 | 13.242 | 11.1859 | 9.4094 | 6.7359 | 17.1267 | 16.8349 | 16.4267 | 16.0318 | 15.5563 | 14.9533 | 14.3543 | 13.3869 | 12.3155 | 11.3257 | 8.039 | 6.7267 | 5.8992
|  | BASINGSTOKE | HT |  |  |  | 18.4808 | 18.1594 | 17.8471 | 17.4798 | 16.9706 | 16.3614 | 15.3778 | 14.239 | 13.2165 | 12.1441 | 8.1124 | 6.2471 | 5.2482 | 17.439 | 17.2686 | 17.1298 | 16.9553 | 16.6533 | 16.2124 | 15.6676 | 15.0033 | 14.4176 | 13.8206 | 11.4869 | 10.4451 | 9.8818 | 17.3206 | 17.0349 | 16.7686 | 16.4553 | 16.0216 | 15.4992 | 14.5869 | 13.5461 | 12.6308 | 11.6645 | 8.0635 | 6.2686 | 5.2869
|  | BASINGSTOKE | HE |  |  |  | 18.4655 | 18.1951 | 17.8237 | 17.44 | 17.0022 | 16.4431 | 15.691 | 14.64 | 13.6053 | 12.439 | 7.79 | 5.9573 | 4.9584 | 17.4145 | 17.2757 | 17.0635 | 16.8706 | 16.6431 | 16.3267 | 15.8645 | 15.2339 | 14.6012 | 13.8441 | 10.9471 | 9.7727 | 7.2288 | 17.3114 | 17.0808 | 16.7635 | 16.4461 | 16.0818 | 15.6094 | 14.9635 | 14.039 | 13.142 | 12.1186 | 8.0257 | 6.2543 | 5.3145
|  | BASINGSTOKE | CF |  |  |  | 18.6951 | 18.5563 | 18.3808 | 18.142 | 17.9084 | 17.642 | 17.3216 | 16.8502 | 16.2818 | 15.6624 | 11.5318 | 8.6012 | 6.4604 | 17.4829 | 17.3747 | 17.242 | 17.0665 | 16.9002 | 16.7043 | 16.4747 | 16.1359 | 15.739 | 15.2992 | 12.4237 | 9.2176 | 4.0165 | 17.4329 | 17.3369 | 17.2104 | 17.0349 | 16.8431 | 16.6278 | 16.3522 | 15.9288 | 15.4196 | 14.8614 | 11.3757 | 8.8298 | 6.8553
NURSLING GSP | VELMORE BSP | BASSETT | MINIMUM HEADROOM | SU 42193 15958 | YES | 2.306 | 12.0936 | 11.8089 | 11.3079 | 10.9038 | 10.8018 | 10.3211 | 9.4915 | 8.5977 | 7.713 | 7.0773 | 3.564 | 0.58747 | -1.1268 | 15.662 | 15.4089 | 14.9222 | 14.5507 | 14.4334 | 14.0191 | 13.3966 | 12.6956 | 11.9875 | 11.4895 | 8.6813 | 4.2191 | -5.8309 | 13.2977 | 12.9854 | 12.4048 | 11.9283 | 11.8528 | 11.3528 | 10.5579 | 9.6885 | 8.8303 | 8.2497 | 5.2936 | 2.7426 | 1.4007
|  | BASSETT | EE |  |  |  | 12.0936 | 11.8089 | 11.3079 | 10.9038 | 10.8018 | 10.3211 | 9.4915 | 8.5977 | 7.713 | 7.0773 | 3.7477 | 1.1905 | -0.91253 | 15.662 | 15.4089 | 14.9222 | 14.5507 | 14.4334 | 14.0191 | 13.3966 | 12.6956 | 11.9875 | 11.4895 | 8.6813 | 5.2303 | -0.11253 | 13.2977 | 12.9854 | 12.4048 | 11.9283 | 11.8528 | 11.3528 | 10.5579 | 9.6885 | 8.8303 | 8.2497 | 5.364 | 3.2364 | 1.5405
|  | BASSETT | HT |  |  |  | 12.2364 | 11.8599 | 11.5742 | 11.2844 | 10.9303 | 10.5232 | 10.0691 | 9.3477 | 8.6099 | 7.8487 | 3.564 | 0.58747 | -1.1268 | 15.8528 | 15.5466 | 15.3558 | 15.1691 | 14.9079 | 14.5926 | 14.4324 | 14.0334 | 13.615 | 13.1711 | 10.8599 | 9.5211 | 8.8569 | 13.5007 | 13.0854 | 12.7885 | 12.4936 | 12.1069 | 11.6528 | 11.2905 | 10.5987 | 9.8854 | 9.1477 | 5.2936 | 2.7426 | 1.4007
|  | BASSETT | HE |  |  |  | 12.2426 | 12.0344 | 11.6303 | 11.3732 | 11.0732 | 10.7222 | 10.3742 | 9.7895 | 9.1915 | 8.5773 | 5.1038 | 2.4844 | 1.2579 | 15.8069 | 15.613 | 15.212 | 14.9783 | 14.6844 | 14.3262 | 14.0875 | 13.614 | 13.1171 | 12.5936 | 9.4252 | 5.9181 | 0.94461 | 13.4997 | 13.2803 | 12.8293 | 12.566 | 12.2436 | 11.8538 | 11.5752 | 10.9936 | 10.3936 | 9.7762 | 6.6262 | 4.4844 | 3.5334
|  | BASSETT | CF |  |  |  | 12.3671 | 12.2354 | 12.115 | 11.816 | 11.6803 | 11.5048 | 11.2905 | 10.9997 | 11.0058 | 10.7558 | 8.5466 | 6.0773 | 3.6936 | 15.8711 | 15.6926 | 15.512 | 15.1334 | 14.9191 | 14.6273 | 14.2671 | 13.815 | 13.6171 | 13.1691 | 9.863 | 4.2191 | -5.8309 | 13.6252 | 13.4691 | 13.3303 | 12.9783 | 12.8222 | 12.6181 | 12.3722 | 12.0222 | 12.0579 | 11.7732 | 9.6313 | 7.4783 | 5.3956
NORTH HYDE GSP | NORTH HYDE 22kV | BATH ROAD EAST | MINIMUM HEADROOM | TQ 09097 76885 | YES | 3.717 | 3.057 | 2.358 | 2.0315 | 1.8019 | 1.5437 | 26.408 | 26.0764 | 25.6295 | 25.1968 | 24.9897 | 22.9346 | 22.1478 | 21.7988 | 4.4529 | 3.8458 | 3.5907 | 3.3876 | 3.159 | 28.5509 | 28.2835 | 27.9784 | 27.6672 | 27.6846 | 26.2131 | 22.9335 | 16.9509 | 3.4101 | 2.7652 | 2.4203 | 2.1846 | 1.9213 | 26.7927 | 26.4917 | 26.1315 | 25.7764 | 25.7458 | 23.7999 | 23.0641 | 22.7335
|  | BATH ROAD EAST | EE |  |  |  | 3.057 | 2.4274 | 2.0315 | 1.8019 | 1.5437 | 26.408 | 26.0764 | 25.6295 | 25.1968 | 24.9897 | 23.805 | 23.4315 | 23.5356 | 4.4529 | 3.9325 | 3.5907 | 3.3876 | 3.159 | 28.5509 | 28.2835 | 27.9784 | 27.6672 | 27.6846 | 26.3458 | 24.6141 | 21.8182 | 3.4101 | 2.7958 | 2.4203 | 2.1846 | 1.9213 | 26.7927 | 26.4917 | 26.1315 | 25.7764 | 25.7458 | 24.6631 | 24.3305 | 24.4182
|  | BATH ROAD EAST | HT |  |  |  | 3.1458 | 2.358 | 2.2264 | 2.0723 | 1.9295 | 26.8468 | 26.6223 | 26.3999 | 26.1427 | 25.8611 | 24.4192 | 23.6999 | 23.4754 | 4.5284 | 3.8458 | 3.7897 | 3.7203 | 3.6499 | 29.1315 | 28.9917 | 28.8529 | 28.6866 | 28.505 | 27.7723 | 27.3437 | 27.1539 | 3.5162 | 2.7652 | 2.6376 | 2.4876 | 2.357 | 27.2744 | 27.0539 | 26.8427 | 26.5835 | 26.307 | 25.2488 | 24.5856 | 24.3723
|  | BATH ROAD EAST | HE |  |  |  | 3.1346 | 2.555 | 2.2182 | 2.0662 | 1.8988 | 26.8305 | 26.4754 | 26.0284 | 25.5723 | 25.0795 | 22.9346 | 22.1478 | 22.1264 | 4.4937 | 3.9978 | 3.6968 | 3.5825 | 3.4315 | 28.8754 | 28.6672 | 28.4305 | 28.206 | 27.9356 | 26.3641 | 24.8386 | 21.9988 | 3.507 | 2.9468 | 2.6325 | 2.4876 | 2.3254 | 27.2825 | 27.0519 | 26.6856 | 26.3039 | 25.8488 | 23.7999 | 23.0641 | 23.0448
|  | BATH ROAD EAST | CF |  |  |  | 3.2121 | 2.6886 | 2.609 | 2.3019 | 2.1927 | 27.1723 | 27.0927 | 26.9733 | 26.8437 | 26.5529 | 24.7682 | 23.0723 | 21.7988 | 4.5437 | 4.0703 | 4.008 | 3.6937 | 3.5448 | 28.9692 | 28.7937 | 28.5652 | 28.3244 | 28.0621 | 26.2131 | 22.9335 | 16.9509 | 3.5784 | 3.0672 | 2.9907 | 2.6988 | 2.5927 | 27.5744 | 27.5019 | 27.3774 | 27.2376 | 27.0641 | 25.5295 | 23.9233 | 22.7335
IVER 132KV | LONGFORD | BATH ROAD WEST | MINIMUM HEADROOM | TQ 05814 76820 | YES | 9.354 | -0.20573 | -2.0751 | -2.569 | -3.1679 | -3.8434 | -4.62 | -5.4557 | -6.4618 | -7.4353 | -8.2598 | -11.3179 | -13.0486 | -13.8812 | 1.1198 | -0.48018 | -0.6608 | -0.88324 | -1.319 | -1.8873 | -2.4812 | -3.2088 | -3.9067 | -4.4975 | -6.7567 | -8.02 | -8.6261 | 0.85754 | -0.971 | -1.4169 | -1.9547 | -2.5669 | -3.2679 | -4.0149 | -4.9241 | -5.7996 | -6.5383 | -9.3934 | -10.9822 | -11.6914
|  | BATH ROAD WEST | EE |  |  |  | -0.20573 | -2.0751 | -2.569 | -3.1679 | -3.8434 | -4.62 | -5.4557 | -6.4618 | -7.4353 | -8.2598 | -10.8322 | -11.2169 | -11.1924 | 1.1198 | -0.48018 | -0.6608 | -0.88324 | -1.319 | -1.8873 | -2.4812 | -3.2088 | -3.9067 | -4.4975 | -6.3037 | -6.5312 | -6.5853 | 0.85754 | -0.971 | -1.4169 | -1.9547 | -2.5669 | -3.2679 | -4.0149 | -4.9241 | -5.7996 | -6.5383 | -8.8281 | -9.1332 | -9.1455
|  | BATH ROAD WEST | HT |  |  |  | 0.15448 | -1.5751 | -1.8771 | -2.2312 | -2.6496 | -3.1363 | -3.6894 | -4.3924 | -5.1394 | -5.9241 | -9.4047 | -10.7751 | -11.3128 | 1.2218 | -0.32916 | -0.41182 | -0.51182 | -0.65467 | -0.8261 | -1.1465 | -1.6373 | -2.1618 | -2.7128 | -5.1496 | -6.0965 | -6.4751 | 1.1841 | -0.51488 | -0.78427 | -1.1006 | -1.473 | -1.9077 | -2.3986 | -3.02 | -3.6863 | -4.3812 | -7.4812 | -8.6945 | -9.1771
|  | BATH ROAD WEST | HE |  |  |  | 0.089171 | -1.6802 | -2.0404 | -2.4598 | -2.9537 | -3.5281 | -4.2159 | -5.0639 | -5.9832 | -6.9577 | -11.3179 | -13.0486 | -13.8812 | 1.1994 | -0.371 | -0.48018 | -0.62508 | -0.80978 | -1.0986 | -1.5863 | -2.1996 | -2.8618 | -3.572 | -6.7567 | -8.02 | -8.6261 | 1.1218 | -0.62202 | -0.94651 | -1.3261 | -1.7741 | -2.2986 | -2.9169 | -3.6853 | -4.5159 | -5.4006 | -9.3934 | -10.9822 | -11.6914
|  | BATH ROAD WEST | CF |  |  |  | 0.26774 | -1.2822 | -1.4741 | -1.7057 | -1.9679 | -2.2741 | -2.6179 | -3.0904 | -3.6108 | -4.1832 | -7.6434 | -10.6434 | -12.5353 | 1.2667 | -0.2659 | -0.33222 | -0.41386 | -0.49855 | -0.6108 | -0.74651 | -0.93222 | -1.1883 | -1.6098 | -4.1475 | -6.321 | -7.72 | 1.2984 | -0.26794 | -0.44141 | -0.65059 | -0.89243 | -1.1741 | -1.4843 | -1.9149 | -2.3904 | -2.9139 | -6.073 | -8.7924 | -10.5026
IVER 132KV | UPTON BSP | BEACONSFIELD | MINIMUM HEADROOM | SU 93668 91219 | YES | 3.498 | 10.1909 | 9.7317 | 9.1939 | 8.6031 | 10.7909 | 10.1664 | 9.2715 | 8.6358 | 8.0766 | 7.3939 | 3.8848 | 1.0072 | -0.66219 | 10.9664 | 10.7511 | 10.2052 | 9.6348 | 12.0378 | 11.5807 | 10.9684 | 10.6072 | 10.1623 | 9.6572 | 7.1103 | 5.7705 | 5.1133 | 10.3878 | 9.9643 | 9.4623 | 8.9052 | 11.1194 | 10.497 | 9.6348 | 9.0817 | 8.6388 | 8.0276 | 4.9225 | 2.3858 | 0.97659
|  | BEACONSFIELD | EE |  |  |  | 10.1909 | 9.7317 | 9.1939 | 8.6031 | 10.7909 | 10.1664 | 9.2715 | 8.6358 | 8.0766 | 7.3939 | 3.9715 | 1.4174 | -0.51831 | 13.6399 | 13.4011 | 13.098 | 12.7123 | 15.147 | 14.7082 | 14.1388 | 13.7041 | 13.3643 | 12.8684 | 10.897 | 9.7858 | 9.1296 | 10.3878 | 9.9643 | 9.4623 | 8.9052 | 11.1194 | 10.497 | 9.6348 | 9.0817 | 8.6388 | 8.0276 | 4.9715 | 2.745 | 1.095
|  | BEACONSFIELD | HT |  |  |  | 10.4225 | 10.0154 | 9.5745 | 9.0511 | 11.4082 | 10.947 | 10.1735 | 9.3582 | 8.4603 | 7.5205 | 3.8848 | 1.0072 | -0.66219 | 10.9664 | 10.7511 | 10.2052 | 9.6348 | 12.0378 | 11.5807 | 10.9684 | 10.6072 | 10.1623 | 9.6572 | 7.1103 | 5.7705 | 5.1133 | 10.6256 | 10.2613 | 9.8613 | 9.3745 | 11.7837 | 11.3511 | 10.6378 | 9.8817 | 9.045 | 8.1582 | 4.9225 | 2.3858 | 0.97659
|  | BEACONSFIELD | HE |  |  |  | 10.4113 | 10.0439 | 9.597 | 9.1245 | 11.4909 | 10.996 | 10.3307 | 9.6092 | 8.8082 | 8.047 | 3.9348 | 1.6725 | 0.8174 | 13.7939 | 13.6194 | 13.397 | 13.1521 | 15.7409 | 15.4174 | 14.9827 | 14.4276 | 13.7888 | 13.2276 | 10.549 | 9.2654 | 8.845 | 10.6154 | 10.2868 | 9.8756 | 9.4521 | 11.8694 | 11.3929 | 10.7674 | 10.0878 | 9.3164 | 8.9082 | 5.149 | 3.0562 | 2.2919
|  | BEACONSFIELD | CF |  |  |  | 10.5643 | 10.3164 | 10.0256 | 9.6899 | 12.1929 | 11.9378 | 11.648 | 11.3225 | 10.9705 | 10.5531 | 8.0062 | 4.9235 | 2.0868 | 13.8735 | 13.7531 | 13.6082 | 13.4358 | 16.0827 | 15.9092 | 15.6899 | 15.4603 | 15.2041 | 14.8909 | 13.0603 | 11.0674 | 9.3286 | 10.7531 | 10.5307 | 10.2654 | 9.9592 | 12.4909 | 12.2409 | 11.9429 | 11.6205 | 11.2664 | 10.845 | 8.9419 | 6.0562 | 3.4092
BRAMLEY (ANDO-THAT) | THATCHAM BSP | BEENHAM | MINIMUM HEADROOM | SU 58204 69025 | YES | 0.832 | 6.2082 | 6.0847 | 5.9143 | 5.7653 | 5.5612 | 5.3469 | 5.1265 | 4.8173 | 4.5102 | 4.3224 | 3.248 | 2.7092 | 2.5796 | 8.6061 | 8.5224 | 8.3898 | 8.2847 | 8.1296 | 7.9612 | 7.8051 | 7.5663 | 7.3265 | 7.1949 | 6.5194 | 5.6541 | 3.8337 | 6.9939 | 6.8745 | 6.7061 | 6.5633 | 6.3704 | 6.1612 | 5.952 | 5.6551 | 5.3592 | 5.1827 | 4.3714 | 3.8582 | 3.7347
|  | BEENHAM | EE |  |  |  | 6.2082 | 6.0847 | 5.9143 | 5.7653 | 5.5612 | 5.3469 | 5.1265 | 4.8173 | 4.5102 | 4.3224 | 3.4908 | 3.2286 | 3.1173 | 8.6061 | 8.5224 | 8.3898 | 8.2847 | 8.1296 | 7.9612 | 7.8051 | 7.5663 | 7.3265 | 7.1949 | 6.5449 | 6.0122 | 5.1878 | 6.9939 | 6.8745 | 6.7061 | 6.5633 | 6.3704 | 6.1612 | 5.952 | 5.6551 | 5.3592 | 5.1827 | 4.4224 | 4.1969 | 4.098
|  | BEENHAM | HT |  |  |  | 6.2969 | 6.1908 | 6.0786 | 5.949 | 5.8051 | 5.6816 | 5.4816 | 5.25 | 5.049 | 4.801 | 3.7031 | 3.2459 | 3.0235 | 8.6939 | 8.6276 | 8.5582 | 8.4765 | 8.3755 | 8.2969 | 8.1694 | 8.0133 | 7.9 | 7.7316 | 7.0224 | 6.7571 | 6.65 | 7.0898 | 6.9857 | 6.8806 | 6.7571 | 6.6163 | 6.498 | 6.3061 | 6.0827 | 5.8949 | 5.6571 | 4.6163 | 4.1949 | 4.0112
|  | BEENHAM | HE |  |  |  | 6.2847 | 6.1776 | 6.0602 | 5.9286 | 5.7776 | 5.6367 | 5.4327 | 5.1908 | 4.9337 | 4.6439 | 3.248 | 2.7092 | 2.5796 | 8.6786 | 8.602 | 8.5286 | 8.4296 | 8.3153 | 8.2163 | 8.0704 | 7.8929 | 7.7347 | 7.5378 | 6.5194 | 5.8755 | 5.0663 | 7.0796 | 6.9724 | 6.8643 | 6.7347 | 6.5908 | 6.4694 | 6.2724 | 6.0429 | 5.8418 | 5.5929 | 4.3714 | 3.8582 | 3.7347
|  | BEENHAM | CF |  |  |  | 6.3235 | 6.2388 | 6.1347 | 6.0449 | 5.9408 | 5.8214 | 5.7296 | 5.5847 | 5.4245 | 5.2582 | 4.35 | 3.4663 | 2.7929 | 8.702 | 8.6418 | 8.5571 | 8.498 | 8.4143 | 8.3143 | 8.2276 | 8.0929 | 7.949 | 7.7969 | 6.852 | 5.6541 | 3.8337 | 7.1133 | 7.0347 | 6.9327 | 6.852 | 6.752 | 6.6378 | 6.552 | 6.4102 | 6.2541 | 6.0898 | 5.2245 | 4.5653 | 3.9357
MANNINGTON GSP | SALISBURY | BEMERTON | MINIMUM HEADROOM | SU 11583 31233 | YES | 2.603 | 19.3508 | 19.0304 | 18.363 | 17.6324 | 16.7263 | 16.412 | 15.513 | 14.6008 | 13.8997 | 13.3824 | 10.5538 | 8.3263 | 7.1436 | 20.661 | 20.4059 | 19.8446 | 19.2324 | 18.5987 | 18.5467 | 18.0028 | 17.414 | 16.9059 | 16.5457 | 14.4906 | 12.2844 | 6.1967 | 19.2375 | 18.9324 | 18.2936 | 17.5997 | 16.7783 | 16.5599 | 15.7569 | 14.9181 | 14.2406 | 13.7793 | 11.3304 | 9.3732 | 8.3855
|  | BEMERTON | EE |  |  |  | 19.3508 | 19.0304 | 18.363 | 17.6324 | 16.7263 | 16.412 | 15.513 | 14.6008 | 13.8997 | 13.3824 | 10.6395 | 8.7467 | 7.5242 | 20.661 | 20.4059 | 19.8446 | 19.2324 | 18.5987 | 18.5467 | 18.0028 | 17.414 | 16.9059 | 16.5457 | 14.4906 | 12.3436 | 9.2385 | 19.2375 | 18.9324 | 18.2936 | 17.5997 | 16.7783 | 16.5599 | 15.7569 | 14.9181 | 14.2406 | 13.7793 | 11.3814 | 9.7375 | 8.7028
|  | BEMERTON | HT |  |  |  | 19.515 | 19.2671 | 18.665 | 18.0201 | 17.3487 | 16.6824 | 15.7977 | 15.2722 | 14.6518 | 14.012 | 10.5538 | 8.3263 | 7.1436 | 20.8181 | 20.6691 | 20.1926 | 19.7038 | 19.3079 | 18.9293 | 18.4446 | 18.2395 | 17.9079 | 17.5712 | 15.7334 | 14.6589 | 14.1089 | 19.4048 | 19.1712 | 18.6171 | 18.0212 | 17.4426 | 16.8477 | 16.064 | 15.6477 | 15.0732 | 14.4804 | 11.3304 | 9.3732 | 8.3855
|  | BEMERTON | HE |  |  |  | 19.5191 | 19.2906 | 18.7099 | 18.0875 | 17.3579 | 16.765 | 15.9824 | 15.5497 | 15.0283 | 14.4936 | 11.6671 | 9.8967 | 9.0804 | 20.7957 | 20.6416 | 20.1283 | 19.6222 | 19.0977 | 18.7344 | 18.2722 | 18.0263 | 17.6783 | 17.312 | 15.0987 | 12.9406 | 10.0334 | 19.4059 | 19.1926 | 18.6528 | 18.0844 | 17.4579 | 16.9283 | 16.2355 | 15.9028 | 15.4181 | 14.9181 | 12.3375 | 10.8028 | 10.1436
|  | BEMERTON | CF |  |  |  | 19.6977 | 19.4967 | 19.012 | 18.5079 | 17.8885 | 17.4844 | 17.013 | 16.565 | 16.2824 | 16.3385 | 14.5191 | 12.4804 | 10.5038 | 20.9263 | 20.7365 | 20.2599 | 19.8028 | 19.312 | 19.0191 | 18.6589 | 18.2926 | 18.0018 | 17.9222 | 15.8048 | 12.2844 | 6.1967 | 19.5752 | 19.3814 | 18.9355 | 18.4742 | 17.9416 | 17.5967 | 17.1844 | 16.7742 | 16.4895 | 16.5916 | 14.8426 | 13.0518 | 11.3324
COWLEY GSP | COWLEY LOCAL (2 X 45) | BERINSFIELD | MINIMUM HEADROOM | SU 58382 95467 | YES | 1.293 | 12.4601 | 12.1407 | 11.4877 | 9.8111 | 8.1428 | 3.9223 | 0.42234 | -3.4807 | -5.9644 | -11.6001 | -29.0991 | -43.9328 | -52.6644 | 15.456 | 15.2264 | 14.6601 | 13.3152 | 12.3142 | 8.6346 | 6.0683 | 3.2295 | 2.0162 | -3.0103 | -16.3675 | -29.7399 | -40.4144 | 12.8417 | 12.3509 | 11.6611 | 9.9866 | 8.5121 | 4.1611 | 0.88255 | -2.7603 | -4.7062 | -10.5134 | -27.094 | -42.5766 | -53.1226
|  | BERINSFIELD | EE |  |  |  | 12.4601 | 12.1407 | 11.5285 | 10.5091 | 9.0152 | 6.5662 | 3.2754 | 0.23663 | -3.7062 | -7.0807 | -22.6501 | -39.9613 | -45.1848 | 15.456 | 15.2264 | 14.905 | 14.4285 | 13.6489 | 12.0325 | 9.7805 | 8.0713 | 5.2193 | 3.0091 | -7.8481 | -25.5715 | -33.0409 | 12.8417 | 12.3509 | 11.7856 | 10.9315 | 9.6938 | 7.5234 | 4.5397 | 1.9999 | -1.6705 | -4.6756 | -18.8277 | -37.7032 | -43.8481
|  | BERINSFIELD | HT |  |  |  | 12.5305 | 12.2274 | 11.5489 | 10.1815 | 8.7795 | 5.0111 | 1.3642 | -2.7521 | -5.646 | -9.9297 | -27.0879 | -43.9328 | -52.6644 | 15.5213 | 15.3438 | 14.8285 | 13.904 | 13.2948 | 10.2315 | 7.5948 | 4.6091 | 3.0101 | -0.20317 | -12.3736 | -28.5123 | -38.6685 | 12.954 | 12.4989 | 11.7519 | 10.4683 | 9.3336 | 5.556 | 2.1203 | -1.7532 | -4.1787 | -8.2715 | -24.3246 | -42.5766 | -53.1226
|  | BERINSFIELD | HE |  |  |  | 12.5315 | 12.2305 | 11.4877 | 9.8111 | 8.1428 | 3.9223 | 0.42234 | -3.4807 | -5.9644 | -11.6001 | -29.0991 | -42.8817 | -50.4328 | 15.5132 | 15.3162 | 14.6601 | 13.3152 | 12.3142 | 8.6346 | 6.0683 | 3.2295 | 2.0162 | -3.0103 | -16.3675 | -29.7399 | -40.4144 | 12.9591 | 12.5162 | 11.6611 | 9.9866 | 8.5121 | 4.1611 | 0.88255 | -2.7603 | -4.7062 | -10.5134 | -27.094 | -41.5787 | -50.7583
|  | BERINSFIELD | CF |  |  |  | 12.5764 | 12.3254 | 12.0611 | 11.2968 | 9.8825 | 7.8601 | 5.3764 | 2.6652 | -0.073573 | -2.6185 | -16.1838 | -26.9664 | -33.2511 | 15.5407 | 15.3938 | 15.1407 | 14.7611 | 13.9132 | 12.6693 | 11.0121 | 9.2785 | 7.5397 | 5.8764 | -3.7409 | -13.7164 | -23.2093 | 13.0295 | 12.6897 | 12.3009 | 11.6774 | 10.4621 | 8.7377 | 6.5877 | 4.2917 | 1.9723 | -0.21235 | -12.3562 | -22.8705 | -29.8123
NURSLING GSP | SOUTHAMPTON (2 X 60) | BEVOIS VALLEY | MINIMUM HEADROOM | SU 42648 13187 | YES | 2.237 | 14.0972 | 13.6002 | 13.1625 | 12.6982 | 11.9584 | 11.2951 | 10.6992 | 9.9492 | 9.2053 | 8.6584 | 5.9115 | 3.5921 | 2.1758 | 16.888 | 16.588 | 16.3043 | 16.0013 | 15.5523 | 15.0982 | 14.536 | 13.8319 | 13.1145 | 12.5064 | 9.038 | 2.9502 | -10.2467 | 15.2951 | 14.8431 | 14.4268 | 13.986 | 13.2972 | 12.6502 | 12.0727 | 11.3319 | 10.5911 | 10.0298 | 7.487 | 5.5033 | 4.2829
|  | BEVOIS VALLEY | EE |  |  |  | 14.0972 | 13.6002 | 13.1625 | 12.6982 | 11.9584 | 11.2951 | 10.6992 | 9.9492 | 9.2053 | 8.6584 | 5.9115 | 4.04 | 2.336 | 16.888 | 16.588 | 16.3043 | 16.0013 | 15.5523 | 15.0982 | 14.536 | 13.8319 | 13.1145 | 12.5064 | 9.038 | 5.0217 | -1.8712 | 15.2951 | 14.8431 | 14.4268 | 13.986 | 13.2972 | 12.6502 | 12.0727 | 11.3319 | 10.5911 | 10.0298 | 7.487 | 5.8502 | 4.3553
|  | BEVOIS VALLEY | HT |  |  |  | 14.2584 | 13.8911 | 13.6002 | 13.2421 | 12.6156 | 12.1788 | 11.7247 | 11.1911 | 10.6135 | 10.0615 | 6.4166 | 3.5921 | 2.1758 | 17.0411 | 16.839 | 16.6931 | 16.5237 | 16.1809 | 15.9441 | 15.7247 | 15.4635 | 15.1656 | 14.7737 | 12.4727 | 10.8727 | 10.2023 | 15.5207 | 15.1513 | 14.8707 | 14.538 | 13.9564 | 13.539 | 13.1064 | 12.5768 | 12.0094 | 11.4615 | 8.0758 | 5.5033 | 4.2829
|  | BEVOIS VALLEY | HE |  |  |  | 14.2319 | 13.8523 | 13.5727 | 13.2533 | 12.7053 | 12.2431 | 11.8533 | 11.3645 | 10.8472 | 10.339 | 7.4247 | 5.5339 | 4.7992 | 16.9758 | 16.7156 | 16.49 | 16.2411 | 15.8686 | 15.4941 | 15.1533 | 14.7574 | 14.3288 | 13.7972 | 10.1737 | 5.9778 | -0.47322 | 15.4921 | 15.1298 | 14.8584 | 14.539 | 14.0431 | 13.5921 | 13.1972 | 12.7053 | 12.1839 | 11.69 | 9.0074 | 7.3472 | 6.7298
|  | BEVOIS VALLEY | CF |  |  |  | 14.5645 | 14.4533 | 14.2237 | 13.94 | 13.5829 | 13.1625 | 12.8543 | 12.5686 | 12.3349 | 12.0441 | 10.2053 | 8.2584 | 6.4268 | 17.1513 | 17.0013 | 16.7707 | 16.5196 | 16.2074 | 15.8278 | 15.4472 | 15.0513 | 14.6564 | 14.1462 | 10.1696 | 2.9502 | -10.2467 | 15.8013 | 15.6707 | 15.4196 | 15.1502 | 14.8258 | 14.4462 | 14.1553 | 13.8788 | 13.6462 | 13.3645 | 11.6115 | 9.7472 | 8.0962
EAST CLAYDON GSP | BICESTER NORTH BSP | BICESTER | MINIMUM HEADROOM | SP 58381 21988 | YES | 20.148 | 4.5241 | 3.9894 | 2.5494 | 1.7535 | 0.53611 | -0.83021 | -2.8914 | -4.9996 | -6.9333 | -8.4874 | -16.1567 | -21.6659 | -24.3588 | 10.6037 | 10.2016 | 9.0341 | 8.5943 | 7.8453 | 7.0228 | 5.7075 | 4.3575 | 3.0902 | 2.1259 | -2.2751 | -6.2129 | -14.4027 | 4.5924 | 4.0659 | 2.6739 | 2.0677 | 0.98918 | -0.21287 | -2.0108 | -3.8812 | -5.6098 | -6.9343 | -12.9037 | -17.469 | -19.6629
|  | BICESTER | EE |  |  |  | 4.5241 | 3.9894 | 2.5494 | 1.7535 | 0.53611 | -0.83021 | -2.8914 | -4.9996 | -6.9333 | -8.4874 | -15.9333 | -21.0527 | -24.0608 | 10.6037 | 10.2016 | 9.0341 | 8.5943 | 7.8453 | 7.0228 | 5.7075 | 4.3575 | 3.0902 | 2.1259 | -2.2751 | -6.2129 | -10.8149 | 4.5924 | 4.0659 | 2.6739 | 2.0677 | 0.98918 | -0.21287 | -2.0108 | -3.8812 | -5.6098 | -6.9343 | -12.8506 | -16.9588 | -19.468
|  | BICESTER | HT |  |  |  | 4.7455 | 4.2618 | 2.9535 | 1.9126 | 0.73918 | -0.24348 | -2.3251 | -4.3863 | -6.2598 | -7.9251 | -16.1567 | -21.6659 | -24.3588 | 10.819 | 10.5639 | 9.6198 | 9.0535 | 8.4218 | 8.0065 | 6.7249 | 5.4728 | 4.3524 | 3.4596 | -0.55368 | -3.1618 | -4.4649 | 4.8731 | 4.4363 | 3.2269 | 2.33 | 1.3177 | 0.5953 | -1.1394 | -2.8874 | -4.5016 | -5.9506 | -12.9037 | -17.469 | -19.6629
|  | BICESTER | HE |  |  |  | 4.7414 | 4.2955 | 3.0218 | 2.0137 | 0.87591 | -0.072049 | -1.8629 | -3.6537 | -5.3047 | -6.9037 | -14.5384 | -19.7578 | -21.8333 | 10.7588 | 10.4628 | 9.4637 | 8.8514 | 8.178 | 7.7167 | 6.5371 | 5.3718 | 4.278 | 3.2361 | -1.6445 | -5.719 | -9.8669 | 4.8618 | 4.4547 | 3.2728 | 2.4045 | 1.4208 | 0.73101 | -0.76797 | -2.2996 | -3.7333 | -5.1333 | -11.5731 | -15.818 | -17.4853
|  | BICESTER | CF |  |  |  | 5.0006 | 4.7353 | 3.7953 | 3.4024 | 2.8606 | 2.1208 | 1.1984 | -0.1047 | -1.3272 | -2.4282 | -9.0006 | -14.8292 | -18.9241 | 10.8894 | 10.6608 | 9.7963 | 9.4667 | 9.0606 | 8.529 | 7.8708 | 6.9106 | 5.9953 | 5.1443 | 0.043257 | -5.9955 | -14.4027 | 5.0914 | 4.8384 | 3.9198 | 3.5586 | 3.0606 | 2.4055 | 1.7473 | 0.64632 | -0.3996 | -1.3578 | -7.0353 | -11.7792 | -15.0139
EAST CLAYDON GSP | BICESTER NORTH BSP | BICESTER NORTH | MINIMUM HEADROOM | SP 59720 23735 | YES | 17.221 | 19.1611 | 18.8591 | 18.4284 | 17.958 | 16.5478 | 14.5366 | 13.9662 | 13.2938 | 12.6172 | 12.3836 | 10.457 | 2.15 | 0.81526 | 22.4203 | 22.3182 | 22.1856 | 22.0427 | 20.4458 | 18.6417 | 18.2336 | 17.7733 | 17.304 | 17.0427 | 15.8203 | 8.8163 | 8.0408 | 20.8682 | 20.6836 | 20.4611 | 20.2223 | 18.5591 | 16.7254 | 16.2162 | 15.6162 | 14.9978 | 14.5203 | 11.5876 | 3.2704 | 2.0357
|  | BICESTER NORTH | EE |  |  |  | 19.1611 | 18.8591 | 18.4284 | 17.958 | 16.5478 | 14.5366 | 13.9662 | 13.2938 | 12.6172 | 12.3836 | 10.6244 | 2.452 | 0.89689 | 22.4203 | 22.3182 | 22.1856 | 22.0427 | 20.4458 | 18.6417 | 18.2336 | 17.7733 | 17.304 | 17.0427 | 15.8203 | 8.8163 | 8.0408 | 20.8682 | 20.6836 | 20.4611 | 20.2223 | 18.5723 | 16.7346 | 16.2162 | 15.6162 | 14.9978 | 14.5203 | 11.808 | 3.5948 | 2.0979
|  | BICESTER NORTH | HT |  |  |  | 19.4274 | 19.2305 | 18.9489 | 18.7101 | 16.7774 | 14.8142 | 14.8223 | 14.3427 | 13.8244 | 13.2938 | 10.457 | 2.15 | 0.81526 | 22.4693 | 22.3876 | 22.2856 | 22.1948 | 20.4642 | 18.7305 | 18.5978 | 18.3387 | 18.0529 | 17.6825 | 15.905 | 8.8326 | 8.3734 | 20.9315 | 20.7611 | 20.5662 | 20.3876 | 18.5591 | 16.7254 | 16.3662 | 15.8529 | 15.3325 | 14.8152 | 11.5876 | 3.2704 | 2.0357
|  | BICESTER NORTH | HE |  |  |  | 19.4315 | 19.2366 | 18.9601 | 18.7315 | 16.8203 | 14.8642 | 14.9713 | 14.5529 | 14.106 | 13.6356 | 11.4713 | 3.402 | 2.4755 | 22.4764 | 22.3968 | 22.2958 | 22.2111 | 20.4989 | 18.7652 | 18.6733 | 18.4631 | 18.2468 | 17.9203 | 16.4019 | 9.4142 | 8.901 | 20.9448 | 20.7897 | 20.6101 | 20.4489 | 18.655 | 16.8356 | 16.5887 | 16.1825 | 15.7703 | 15.357 | 12.7876 | 4.6867 | 3.8051
|  | BICESTER NORTH | CF |  |  |  | 19.4958 | 19.3315 | 19.1713 | 18.9662 | 17.204 | 15.3703 | 15.0856 | 14.7366 | 15.0427 | 14.7672 | 12.9876 | 5.8122 | 4.5204 | 22.5193 | 22.4601 | 22.4131 | 22.3499 | 20.7029 | 19.0284 | 18.9254 | 18.8101 | 18.8448 | 18.7529 | 17.554 | 10.3193 | 9.2346 | 20.9968 | 20.9468 | 20.8621 | 20.7631 | 19.0805 | 17.3713 | 17.2254 | 17.057 | 17.0805 | 16.9427 | 15.5101 | 7.5326 | 5.7326
LOVEDEAN GSP | CHICHESTER & HUNSTON | BILLINGSHURST | MINIMUM HEADROOM | TQ 08305 26315 | YES | 1.995 | 3.7678 | 3.5239 | 3.2055 | 2.9076 | 2.5851 | 2.2514 | 2.0841 | 1.5453 | 1.0106 | 0.60653 | -1.7078 | -3.3669 | -4.3751 | 6.8743 | 6.6916 | 6.4406 | 6.212 | 5.9498 | 5.6692 | 5.5978 | 5.2161 | 4.8345 | 4.5467 | 2.9406 | 0.87837 | -3.7471 | 5.5161 | 5.2845 | 4.9712 | 4.6957 | 4.3702 | 4.0304 | 3.9733 | 3.4773 | 2.9773 | 2.6273 | 0.7202 | -0.69612 | -1.5176
|  | BILLINGSHURST | EE |  |  |  | 3.7678 | 3.5239 | 3.2055 | 2.9076 | 2.5851 | 2.2514 | 2.0841 | 1.5453 | 1.0106 | 0.60653 | -1.4802 | -2.92 | -4.0016 | 6.8743 | 6.6916 | 6.4406 | 6.212 | 5.9498 | 5.6692 | 5.5978 | 5.2161 | 4.8345 | 4.5467 | 2.9406 | 1.2416 | -1.2624 | 5.5161 | 5.2845 | 4.9712 | 4.6957 | 4.3702 | 4.0304 | 3.9733 | 3.4773 | 2.9773 | 2.6273 | 0.88041 | -0.32878 | -1.2318
|  | BILLINGSHURST | HT |  |  |  | 3.8708 | 3.6473 | 3.3769 | 3.132 | 2.8545 | 2.6106 | 2.1484 | 1.6116 | 1.0586 | 0.86367 | -1.7078 | -3.3669 | -4.3751 | 6.9886 | 6.8457 | 6.6661 | 6.5151 | 6.3386 | 6.1835 | 5.9253 | 5.611 | 5.2855 | 5.2467 | 3.8671 | 3.0518 | 2.5671 | 5.6396 | 5.4427 | 5.1906 | 4.9692 | 4.7059 | 4.4896 | 4.0784 | 3.5896 | 3.0773 | 2.9845 | 0.7202 | -0.69612 | -1.5176
|  | BILLINGSHURST | HE |  |  |  | 3.8769 | 3.6769 | 3.4535 | 3.1933 | 2.9514 | 2.7463 | 2.3647 | 1.9116 | 1.4412 | 1.3382 | -0.85878 | -2.2812 | -3.0414 | 6.9631 | 6.812 | 6.6376 | 6.4427 | 6.2447 | 6.0733 | 5.808 | 5.4784 | 5.1345 | 5.0743 | 3.2886 | 1.5702 | -0.79408 | 5.6416 | 5.4631 | 5.258 | 5.0182 | 4.7865 | 4.6008 | 4.2539 | 3.8365 | 3.3998 | 3.3804 | 1.4488 | 0.25286 | -0.35735
|  | BILLINGSHURST | CF |  |  |  | 3.9535 | 3.8065 | 3.6229 | 3.4524 | 3.2861 | 3.1269 | 2.981 | 2.7361 | 2.479 | 2.2157 | 1.0065 | -0.50163 | -1.868 | 7.0049 | 6.8712 | 6.7039 | 6.5518 | 6.3916 | 6.2192 | 6.0376 | 5.7794 | 5.5008 | 5.21 | 3.6304 | 0.87837 | -3.7471 | 5.71 | 5.5733 | 5.3988 | 5.2447 | 5.0824 | 4.9202 | 4.7896 | 4.5508 | 4.2998 | 4.0386 | 3.0273 | 1.7478 | 0.6202
LOVEDEAN GSP | CHICHESTER & HUNSTON | BILSHAM | MINIMUM HEADROOM | SU 97366 01594 | YES | 14.912 | 10.1234 | 9.1581 | 7.905 | 6.0642 | 3.7968 | 33.5734 | 27.1017 | 24.9701 | 23.0986 | 21.415 | 11.7752 | 8.3058 | 6.2007 | 0.46622 | -0.24603 | -1.2083 | -1.996 | -2.9817 | 26.7274 | 21.6333 | 20.6538 | 19.7742 | 18.9742 | 14.2731 | 11.715 | 5.2925 | 2.1366 | 0.98662 | -0.49093 | -1.9491 | -3.7226 | 25.8825 | 19.9823 | 18.3405 | 16.8966 | 15.5619 | 7.8129 | 4.9527 | 3.2333
|  | BILSHAM | EE |  |  |  | 10.1234 | 9.1754 | 7.905 | 6.0642 | 3.7968 | 33.5734 | 27.1017 | 24.9701 | 23.0986 | 21.415 | 12.0303 | 8.9854 | 6.6895 | 0.46622 | -0.22052 | -1.2083 | -1.996 | -2.9817 | 26.7274 | 21.6333 | 20.6538 | 19.7742 | 18.9742 | 14.2731 | 11.715 | 8.1711 | 2.1366 | 1.0183 | -0.49093 | -1.9491 | -3.7226 | 25.8825 | 19.9823 | 18.3405 | 16.8966 | 15.5619 | 8.0078 | 5.4364 | 3.5864
|  | BILSHAM | HT |  |  |  | 10.2356 | 9.1581 | 8.1081 | 6.2091 | 3.9805 | 33.6999 | 27.4558 | 25.3221 | 23.5507 | 21.766 | 11.7752 | 8.3058 | 6.2007 | 0.58152 | -0.24603 | -0.95317 | -1.7848 | -2.7052 | 27.0295 | 22.1191 | 21.2129 | 20.4446 | 19.668 | 15.4272 | 13.9619 | 13.067 | 2.2489 | 0.98662 | -0.29501 | -1.8532 | -3.6052 | 25.9519 | 20.1619 | 18.4935 | 17.0925 | 15.6844 | 7.8129 | 4.9527 | 3.2333
|  | BILSHAM | HE |  |  |  | 10.2376 | 9.3417 | 8.1336 | 6.304 | 4.1081 | 33.9478 | 27.9589 | 26.0527 | 24.3874 | 22.7119 | 13.2711 | 10.3262 | 8.7925 | 0.56316 | -0.078682 | -1.0134 | -1.8634 | -2.8144 | 26.9244 | 22.0629 | 21.1813 | 20.3854 | 19.5691 | 14.7813 | 12.2109 | 9.0456 | 2.2509 | 1.1917 | -0.24705 | -1.7828 | -3.5154 | 26.1264 | 20.5405 | 19.0446 | 17.7323 | 16.4058 | 8.8762 | 6.3221 | 5.0109
|  | BILSHAM | CF |  |  |  | 10.3438 | 9.6866 | 8.7336 | 7.3652 | 5.5642 | 36.0703 | 30.4578 | 29.5119 | 28.5364 | 27.5078 | 18.5956 | 15.0691 | 11.5721 | 0.64275 | 0.16418 | -0.51031 | -1.4358 | -2.2297 | 27.7652 | 22.9997 | 22.5017 | 21.966 | 21.3905 | 16.4691 | 12.4109 | 5.2925 | 2.3499 | 1.6652 | 0.56009 | -0.85521 | -2.2358 | 27.9723 | 22.7772 | 22.0211 | 21.2803 | 20.4976 | 13.6772 | 10.6201 | 7.6048
FAWLEY GSP | COWES & WOOTTON COMMON BSP | BINSTEAD | MINIMUM HEADROOM | SZ 56409 91399 | YES | 0.204 | 14.001 | 13.7357 | 13.4204 | 13.0327 | 12.5969 | 12.1276 | 11.9214 | 11.2459 | 10.5918 | 10.0745 | 6.7224 | 4.9622 | 4.6827 | 14.7551 | 14.5561 | 14.3102 | 14.0031 | 13.652 | 13.2735 | 13.1643 | 12.6796 | 12.199 | 11.8602 | 9.4653 | 8.0357 | 3.8888 | 14.302 | 14.0469 | 13.7439 | 13.3704 | 12.95 | 12.4959 | 12.3224 | 11.6878 | 11.0673 | 10.6316 | 7.601 | 5.95 | 5.7041
|  | BINSTEAD | EE |  |  |  | 14.001 | 13.7357 | 13.4204 | 13.0327 | 12.5969 | 12.1276 | 11.9214 | 11.2459 | 10.5918 | 10.0745 | 7.8541 | 6.3878 | 5.2622 | 14.7551 | 14.5561 | 14.3102 | 14.0031 | 13.652 | 13.2735 | 13.1643 | 12.6796 | 12.199 | 11.8602 | 10.1878 | 8.6551 | 6.4633 | 14.302 | 14.0469 | 13.7439 | 13.3704 | 12.95 | 12.4959 | 12.3224 | 11.6878 | 11.0673 | 10.6316 | 8.6112 | 7.3541 | 6.4265
|  | BINSTEAD | HT |  |  |  | 14.2235 | 14.0306 | 13.8153 | 13.5469 | 13.2459 | 12.9612 | 12.4204 | 11.8041 | 11.5398 | 10.9398 | 8.0265 | 6.2031 | 5.2673 | 14.9449 | 14.8245 | 14.6837 | 14.5051 | 14.2969 | 14.1031 | 13.7776 | 13.399 | 13.3102 | 12.952 | 11.3051 | 10.4102 | 10.0224 | 14.5204 | 14.3378 | 14.1337 | 13.8786 | 13.5918 | 13.3245 | 12.8204 | 12.248 | 12.0296 | 11.4776 | 8.8235 | 7.2296 | 6.4694
|  | BINSTEAD | HE |  |  |  | 14.2051 | 13.9776 | 13.7388 | 13.4429 | 13.1092 | 12.7847 | 12.2622 | 11.5735 | 10.9724 | 10.2255 | 6.7224 | 4.9622 | 4.6827 | 14.9051 | 14.7357 | 14.548 | 14.3194 | 14.05 | 13.7857 | 13.4133 | 12.9673 | 12.5449 | 11.9949 | 9.4653 | 8.0357 | 5.9959 | 14.501 | 14.2857 | 14.0582 | 13.7745 | 13.4531 | 13.1459 | 12.6622 | 12.0888 | 11.6541 | 10.9388 | 7.601 | 5.95 | 5.7041
|  | BINSTEAD | CF |  |  |  | 14.3092 | 14.1888 | 14.0286 | 13.8786 | 13.6714 | 13.4388 | 13.2306 | 12.9296 | 12.599 | 12.252 | 10.0561 | 7.8041 | 6.3847 | 14.9745 | 14.8622 | 14.7153 | 14.5724 | 14.3837 | 14.1541 | 13.9388 | 13.6347 | 13.3031 | 12.95 | 11.1122 | 8.2214 | 3.8888 | 14.6051 | 14.4867 | 14.3296 | 14.1867 | 13.9898 | 13.7694 | 13.5745 | 13.2837 | 12.9663 | 12.6327 | 10.7653 | 8.6316 | 7.3071
LOVEDEAN GSP | CHICHESTER & HUNSTON | BIRDHAM | MINIMUM HEADROOM | SZ 81965 99422 | YES | 2.888 | 2.5561 | 2.2439 | 1.8714 | 1.3867 | 16.5663 | 16.0439 | 15.2908 | 14.4551 | 13.6643 | 13.1255 | 10.201 | 7.9714 | 6.7622 | 4.3367 | 4.1041 | 3.8133 | 3.4408 | 3.3306 | 17.1408 | 16.6429 | 16.0745 | 15.5163 | 15.1347 | 13.052 | 10.3735 | 4.2173 | 3.4235 | 3.1163 | 2.749 | 2.2776 | 2.1378 | 16.2469 | 15.5561 | 14.7878 | 14.0571 | 13.5633 | 11.0143 | 9.1214 | 8.149
|  | BIRDHAM | EE |  |  |  | 2.5561 | 2.2439 | 1.8714 | 1.3867 | 16.5663 | 16.0439 | 15.2908 | 14.4551 | 13.6643 | 13.1255 | 10.401 | 8.4633 | 7.0755 | 4.3367 | 4.1041 | 3.8133 | 3.4408 | 3.3306 | 17.1408 | 16.6429 | 16.0745 | 15.5163 | 15.1347 | 13.052 | 10.901 | 7.7622 | 3.4235 | 3.1163 | 2.749 | 2.2776 | 2.1378 | 16.2469 | 15.5561 | 14.7878 | 14.0571 | 13.5633 | 11.1357 | 9.551 | 8.4082
|  | BIRDHAM | HT |  |  |  | 2.699 | 2.4367 | 2.1194 | 1.7429 | 16.6827 | 16.1878 | 15.4367 | 14.999 | 14.2867 | 13.6031 | 10.201 | 7.9714 | 6.7622 | 4.498 | 4.348 | 4.1602 | 3.9316 | 3.6673 | 17.5622 | 17.1449 | 16.9959 | 16.5888 | 16.1867 | 14.3163 | 13.2633 | 12.7378 | 3.5439 | 3.3112 | 3.0418 | 2.7061 | 2.3194 | 16.4561 | 15.7755 | 15.4255 | 14.7673 | 14.1255 | 11.0143 | 9.1214 | 8.149
|  | BIRDHAM | HE |  |  |  | 2.701 | 2.4867 | 2.1653 | 1.8133 | 16.7776 | 16.3102 | 15.6765 | 15.3439 | 14.7449 | 14.1735 | 11.099 | 9.0388 | 8.0755 | 4.4837 | 4.3245 | 4.0776 | 3.8296 | 3.5367 | 17.3878 | 16.9541 | 16.7786 | 16.3327 | 15.8857 | 13.3847 | 11.102 | 8.1286 | 3.5469 | 3.3582 | 3.0806 | 2.7612 | 2.399 | 16.5592 | 15.9714 | 15.7112 | 15.1469 | 14.5969 | 11.7776 | 10.0592 | 9.2898
|  | BIRDHAM | CF |  |  |  | 2.8122 | 2.6612 | 2.4582 | 2.1969 | 17.3194 | 16.9969 | 16.6673 | 16.2878 | 16.2735 | 16.0051 | 13.9337 | 11.6867 | 9.6602 | 4.5347 | 4.3969 | 4.2265 | 4.0041 | 3.7939 | 17.7031 | 17.3816 | 16.9939 | 16.9041 | 16.5592 | 14.0878 | 10.3735 | 4.2173 | 3.648 | 3.5133 | 3.3469 | 3.1173 | 2.9031 | 17.2061 | 16.8959 | 16.5306 | 16.5388 | 16.2653 | 14.3173 | 12.298 | 10.5316
BOTLEY WOOD GSP | NETLEY COMMON BSP | BISHOPS WALTHAM | MINIMUM HEADROOM | SU 56691 16683 | YES | 1.813 | 5.4757 | 20.1182 | 19.4794 | 19.1243 | 18.4345 | 17.7671 | 16.761 | 15.6304 | 14.4967 | 13.6651 | 9.4008 | 6.4702 | 4.8151 | 10.2567 | 24.1447 | 23.6651 | 23.4365 | 22.9294 | 22.41 | 21.7233 | 20.9284 | 20.1233 | 19.5488 | 16.4988 | 13.0539 | 5.2039 | 6.1798 | 20.4345 | 19.8039 | 19.5365 | 18.8794 | 18.2222 | 17.2763 | 16.1927 | 15.111 | 14.3702 | 10.7457 | 8.3049 | 6.8957
|  | BISHOPS WALTHAM | EE |  |  |  | 5.4757 | 20.1182 | 19.4794 | 19.1243 | 18.4345 | 17.7671 | 16.761 | 15.6304 | 14.4967 | 13.6651 | 9.4008 | 6.8641 | 5.1171 | 10.2567 | 24.1447 | 23.6651 | 23.4365 | 22.9294 | 22.41 | 21.7233 | 20.9284 | 20.1233 | 19.5488 | 16.4988 | 13.7059 | 9.7202 | 6.1798 | 20.4345 | 19.8039 | 19.5365 | 18.8794 | 18.2222 | 17.2763 | 16.1927 | 15.111 | 14.3702 | 10.7457 | 8.6508 | 7.1447
|  | BISHOPS WALTHAM | HT |  |  |  | 5.7635 | 20.5069 | 20.0529 | 19.4661 | 18.861 | 18.6416 | 17.7835 | 16.8345 | 15.8427 | 14.8029 | 9.6069 | 6.4702 | 4.8151 | 10.4894 | 24.5447 | 24.2671 | 23.91 | 23.5294 | 23.4386 | 22.9651 | 22.4233 | 21.8416 | 21.2304 | 18.3559 | 16.8151 | 16.0763 | 6.491 | 20.8569 | 20.4284 | 19.8824 | 19.31 | 19.162 | 18.3814 | 17.509 | 16.5886 | 15.6294 | 10.9631 | 8.3049 | 6.8957
|  | BISHOPS WALTHAM | HE |  |  |  | 5.7369 | 20.4835 | 20.0263 | 19.4355 | 18.8273 | 18.5967 | 17.8243 | 16.9549 | 16.0376 | 15.0692 | 9.9457 | 7.0641 | 5.9182 | 10.4424 | 24.4376 | 24.1018 | 23.6814 | 23.2355 | 23.0712 | 22.5396 | 21.9284 | 21.2671 | 20.558 | 16.6559 | 13.5406 | 9.8049 | 6.4635 | 20.8314 | 20.4008 | 19.8518 | 19.2712 | 19.1202 | 18.408 | 17.5957 | 16.7365 | 15.8314 | 11.2192 | 8.7835 | 7.812
|  | BISHOPS WALTHAM | CF |  |  |  | 5.9094 | 20.7937 | 20.4549 | 20.0753 | 19.6661 | 19.2855 | 19.2314 | 18.811 | 18.3569 | 17.858 | 14.4304 | 11.058 | 8.1661 | 10.5292 | 24.5967 | 24.31 | 24.011 | 23.6671 | 23.2978 | 23.1692 | 22.7324 | 22.258 | 21.7324 | 18.0927 | 13.0539 | 5.2039 | 6.6267 | 21.1151 | 20.7845 | 20.4437 | 20.0518 | 19.6743 | 19.6835 | 19.2733 | 18.8294 | 18.3447 | 15.108 | 12.1355 | 9.6865
NURSLING GSP | VELMORE BSP | BISHOPSTOKE | MINIMUM HEADROOM | SU 46463 18472 | YES | 3.005 | 8.9495 | 6.4781 | 6.373 | 6.2464 | 6.1046 | 5.9444 | 5.7566 | 5.526 | 5.3036 | 5.1087 | 3.9699 | 3.476 | 3.3913 | 7.302 | 4.8612 | 4.7878 | 4.702 | 4.6031 | 4.4949 | 4.3653 | 4.1867 | 4.0163 | 3.8673 | 2.9949 | 2.6173 | 2.552 | 7.7918 | 5.349 | 5.248 | 5.1276 | 4.9867 | 4.8337 | 4.6531 | 4.4296 | 4.2153 | 4.0276 | 2.9265 | 2.448 | 2.3684
|  | BISHOPSTOKE | EE |  |  |  | 8.9495 | 6.4781 | 6.373 | 6.2464 | 6.1046 | 5.9444 | 5.7566 | 5.526 | 5.3036 | 5.1087 | 4.4454 | 4.3372 | 4.3291 | 7.302 | 4.8612 | 4.7878 | 4.702 | 4.6031 | 4.4949 | 4.3653 | 4.1867 | 4.0163 | 3.8673 | 3.3571 | 3.2776 | 3.2735 | 7.7918 | 5.349 | 5.248 | 5.1276 | 4.9867 | 4.8337 | 4.6531 | 4.4296 | 4.2153 | 4.0276 | 3.3867 | 3.2827 | 3.2765
|  | BISHOPSTOKE | HT |  |  |  | 9.0444 | 6.5821 | 6.5219 | 6.4423 | 6.3464 | 6.2311 | 6.1026 | 5.9352 | 5.7526 | 5.5638 | 4.7056 | 4.3393 | 4.2668 | 7.3714 | 4.9276 | 4.8929 | 4.8398 | 4.7714 | 4.6939 | 4.6071 | 4.4939 | 4.3694 | 4.2245 | 3.5673 | 3.2898 | 3.2367 | 7.8531 | 5.4143 | 5.3837 | 5.3153 | 5.2204 | 5.1102 | 4.9837 | 4.8224 | 4.648 | 4.4643 | 3.6357 | 3.2827 | 3.2133
|  | BISHOPSTOKE | HE |  |  |  | 9.023 | 6.5444 | 6.4668 | 6.3638 | 6.2372 | 6.0883 | 5.9138 | 5.6903 | 5.4454 | 5.1852 | 3.9699 | 3.476 | 3.3913 | 7.3571 | 4.902 | 4.851 | 4.7827 | 4.6949 | 4.5929 | 4.4724 | 4.3153 | 4.1276 | 3.9265 | 2.9949 | 2.6173 | 2.552 | 7.8388 | 5.3908 | 5.3378 | 5.2357 | 5.1153 | 4.9714 | 4.8031 | 4.5888 | 4.351 | 4.101 | 2.9265 | 2.448 | 2.3684
|  | BISHOPSTOKE | CF |  |  |  | 9.0821 | 6.6372 | 6.5852 | 6.5444 | 6.4811 | 6.4036 | 6.3199 | 6.2026 | 6.0668 | 5.9179 | 5.0077 | 4.1668 | 3.5832 | 7.3969 | 4.9643 | 4.9255 | 4.9051 | 4.8612 | 4.8082 | 4.749 | 4.6684 | 4.5755 | 4.4745 | 3.7908 | 3.1449 | 2.6969 | 7.8745 | 5.4459 | 5.4112 | 5.3939 | 5.351 | 5.2765 | 5.1969 | 5.0827 | 4.952 | 4.8061 | 3.9286 | 3.1153 | 2.5531
BOTLEY WOOD GSP | NETLEY COMMON BSP | BITTERNE | MINIMUM HEADROOM | SU 45116 13082 | YES | 0.471 | 2.9388 | 2.6071 | 2.1867 | 2.0816 | 1.6724 | 1.2276 | 0.44184 | -0.39898 | -1.2459 | -1.8276 | -5.4041 | -8.2296 | -9.9082 | 4.5449 | 4.2592 | 3.8776 | 3.7306 | 3.3204 | 2.8612 | 2.2337 | 1.5398 | 0.81735 | 0.27755 | -3.3418 | -11.2235 | -26.6755 | 3.8418 | 3.5704 | 3.2306 | 3.1582 | 2.8367 | 2.4408 | 1.699 | 0.88878 | 0.071429 | -0.44796 | -3.5184 | -6.1653 | -7.6776
|  | BITTERNE | EE |  |  |  | 2.9388 | 2.6071 | 2.1867 | 2.0816 | 1.6724 | 1.2276 | 0.44184 | -0.39898 | -1.2459 | -1.8276 | -5.1 | -7.6582 | -9.6888 | 4.5449 | 4.2592 | 3.8776 | 3.7306 | 3.3204 | 2.8612 | 2.2337 | 1.5398 | 0.81735 | 0.27755 | -3.3418 | -8.2418 | -16.3418 | 3.8418 | 3.5704 | 3.2306 | 3.1582 | 2.8367 | 2.4408 | 1.699 | 0.88878 | 0.071429 | -0.44796 | -3.2816 | -5.6612 | -7.499
|  | BITTERNE | HT |  |  |  | 3.1306 | 2.8714 | 2.5449 | 2.2316 | 1.8561 | 1.4571 | 1.0929 | 0.36122 | -0.40102 | -1.1939 | -5.4041 | -8.2296 | -9.9082 | 4.7408 | 4.598 | 4.3969 | 4.2143 | 3.9724 | 3.6929 | 3.5898 | 3.1847 | 2.7622 | 2.3102 | 0.09898 | -1.2143 | -1.9592 | 3.9827 | 3.7602 | 3.4847 | 3.2276 | 2.9204 | 2.5929 | 2.2429 | 1.5969 | 0.92959 | 0.23878 | -3.5184 | -6.1653 | -7.6776
|  | BITTERNE | HE |  |  |  | 3.1398 | 2.9051 | 2.6082 | 2.3327 | 1.9949 | 1.6173 | 1.3796 | 0.8 | 0.19796 | -0.42143 | -3.8051 | -6.2643 | -7.4908 | 4.6765 | 4.4602 | 4.1745 | 3.9031 | 3.5622 | 3.1684 | 2.948 | 2.4347 | 1.8755 | 1.2735 | -2.6541 | -7.5745 | -15.3551 | 3.9949 | 3.7918 | 3.5439 | 3.3173 | 3.0398 | 2.7347 | 2.5122 | 2.0102 | 1.4908 | 0.95918 | -2.101 | -4.4296 | -5.551
|  | BITTERNE | CF |  |  |  | 3.2694 | 3.1327 | 2.9602 | 2.8143 | 2.6255 | 2.4184 | 2.1724 | 2.2255 | 1.9765 | 1.7173 | -0.38673 | -2.7796 | -5.0357 | 4.7204 | 4.5316 | 4.2837 | 4.0408 | 3.7296 | 3.3469 | 2.8796 | 2.5959 | 2.0704 | 1.501 | -2.948 | -11.2235 | -26.6755 | 4.1061 | 4 | 3.8612 | 3.7449 | 3.5939 | 3.4316 | 3.2347 | 3.2888 | 3.0949 | 2.8918 | 0.85816 | -1.2245 | -3.1918
MINETY GSP | STRATTON (2 X 60) | BLACK BOURTON | MINIMUM HEADROOM | SP 28349 03818 | YES | 0.352 | 7.8827 | 7.6102 | 7.2929 | 6.9122 | 6.501 | 6.0337 | 5.4796 | 4.7469 | 4.0418 | 3.602 | 0.81837 | -0.58878 | -1.4082 | 9.2306 | 9.0847 | 8.8561 | 8.5796 | 8.2755 | 7.9327 | 7.5398 | 7.0224 | 6.5031 | 6.1939 | 4.1908 | 3.2194 | 2.6102 | 8.2908 | 8.1255 | 7.7969 | 7.4 | 6.9714 | 6.4878 | 5.9071 | 5.2082 | 4.5388 | 4.1276 | 1.4898 | 0.16837 | -0.60204
|  | BLACK BOURTON | EE |  |  |  | 7.8827 | 7.6102 | 7.2929 | 6.9122 | 6.501 | 6.0337 | 5.4796 | 4.7469 | 4.0418 | 3.602 | 1.5357 | 0.99082 | 0.69694 | 9.2306 | 9.0847 | 8.8561 | 8.5796 | 8.2755 | 7.9327 | 7.5398 | 7.0224 | 6.5031 | 6.1939 | 4.8112 | 4.5367 | 4.3857 | 8.2908 | 8.1255 | 7.7969 | 7.4 | 6.9714 | 6.4878 | 5.9071 | 5.2082 | 4.5388 | 4.1276 | 2.1908 | 1.7051 | 1.4459
|  | BLACK BOURTON | HT |  |  |  | 8.0643 | 7.9245 | 7.701 | 7.4357 | 7.1337 | 6.7806 | 6.3541 | 5.8296 | 5.2102 | 4.5684 | 1.7939 | 0.53571 | -0.15816 | 9.3224 | 9.2357 | 9.1561 | 8.9724 | 8.7592 | 8.5061 | 8.2082 | 7.8449 | 7.4449 | 6.9765 | 5.0235 | 4.2031 | 3.7571 | 8.3867 | 8.2633 | 8.1449 | 7.9296 | 7.6204 | 7.252 | 6.7939 | 6.2561 | 5.6704 | 5.0592 | 2.4398 | 1.2714 | 0.62755
|  | BLACK BOURTON | HE |  |  |  | 8.0704 | 7.8724 | 7.6255 | 7.3286 | 6.9929 | 6.5969 | 6.1143 | 5.5163 | 4.8204 | 4.0888 | 0.81837 | -0.58878 | -1.4082 | 9.3112 | 9.2112 | 9.1051 | 8.8888 | 8.648 | 8.3633 | 8.0173 | 7.5908 | 7.1041 | 6.5571 | 4.1908 | 3.2194 | 2.6102 | 8.3918 | 8.2622 | 8.1357 | 7.8245 | 7.4796 | 7.0684 | 6.5602 | 5.952 | 5.2898 | 4.5898 | 1.4898 | 0.16837 | -0.60204
|  | BLACK BOURTON | CF |  |  |  | 8.1163 | 8.0306 | 7.9459 | 7.8378 | 7.6439 | 7.4347 | 7.1908 | 6.8592 | 6.4816 | 6.098 | 3.4745 | 1.3143 | -0.22551 | 9.3418 | 9.2735 | 9.1969 | 9.1061 | 8.9949 | 8.9051 | 8.7653 | 8.5378 | 8.2602 | 7.9694 | 6.0459 | 4.4806 | 3.1439 | 8.4357 | 8.3541 | 8.2735 | 8.1776 | 8.0592 | 7.9367 | 7.6796 | 7.3337 | 6.9469 | 6.5469 | 3.9969 | 1.9541 | 0.50918
MANNINGTON GSP | LYTCHETT | BLANDFORD | MINIMUM HEADROOM | ST 88810 05536 | YES | 6.199 | 18.9156 | 18.5432 | 17.8779 | 17.534 | 16.7932 | 15.983 | 14.6452 | 13.5707 | 12.4942 | 11.6758 | 7.4228 | 4.1983 | 2.386 | 23.4595 | 23.2942 | 23.0309 | 22.8534 | 22.5473 | 22.2156 | 21.3024 | 20.5432 | 19.7758 | 19.2309 | 16.3493 | 13.2197 | 5.0585 | 20.2942 | 19.8962 | 19.2667 | 19.0024 | 18.3207 | 17.5707 | 16.3575 | 15.3422 | 14.3258 | 13.6054 | 9.9248 | 7.0503 | 5.4064
|  | BLANDFORD | EE |  |  |  | 18.9156 | 18.5432 | 17.8779 | 17.534 | 16.7932 | 15.983 | 14.6452 | 13.5707 | 12.4942 | 11.6758 | 7.4973 | 4.7789 | 2.7228 | 23.4595 | 23.2942 | 23.0309 | 22.8534 | 22.5473 | 22.2156 | 21.3024 | 20.5432 | 19.7758 | 19.2309 | 16.3493 | 13.4289 | 9.083 | 20.2942 | 19.8962 | 19.2667 | 19.0024 | 18.3207 | 17.5707 | 16.3575 | 15.3422 | 14.3258 | 13.6054 | 9.9687 | 7.5697 | 5.6962
|  | BLANDFORD | HT |  |  |  | 19.0881 | 18.8381 | 18.283 | 17.7667 | 17.0881 | 16.334 | 15.4187 | 14.4942 | 13.533 | 12.5473 | 7.4228 | 4.1983 | 2.386 | 23.5911 | 23.4738 | 23.2758 | 23.085 | 22.8371 | 22.5636 | 21.9779 | 21.5901 | 21.185 | 20.7503 | 18.0126 | 16.534 | 15.7809 | 20.536 | 20.2248 | 19.7197 | 19.2544 | 18.6381 | 17.9452 | 17.2105 | 16.3646 | 15.4881 | 14.585 | 9.9248 | 7.0503 | 5.4064
|  | BLANDFORD | HE |  |  |  | 19.0728 | 18.8524 | 18.3207 | 17.8299 | 17.1779 | 16.4544 | 15.6646 | 14.8656 | 14.036 | 13.183 | 8.7391 | 6.0064 | 4.7575 | 23.5758 | 23.4503 | 23.2401 | 23.0422 | 22.7789 | 22.485 | 21.8769 | 21.4626 | 21.0207 | 20.4085 | 17.0442 | 13.9748 | 9.9748 | 20.5279 | 20.2391 | 19.7513 | 19.3126 | 18.7197 | 18.0575 | 17.432 | 16.7003 | 15.9401 | 15.1585 | 11.1207 | 8.6503 | 7.5177
|  | BLANDFORD | CF |  |  |  | 19.2248 | 19.1013 | 18.7687 | 18.4371 | 17.984 | 17.4779 | 16.735 | 16.633 | 16.2187 | 15.7891 | 12.7962 | 9.8513 | 7.1075 | 23.6616 | 23.5799 | 23.4473 | 23.3156 | 23.1432 | 22.9493 | 22.4024 | 22.2422 | 21.8187 | 21.3646 | 18.0656 | 13.2197 | 5.0585 | 20.6452 | 20.4677 | 20.1636 | 19.8656 | 19.4585 | 19.0034 | 18.3299 | 18.2942 | 17.9013 | 17.4911 | 14.6922 | 12.0993 | 9.6728
COWLEY GSP | WITNEY BSP | BLEDINGTON | MINIMUM HEADROOM | SP 25641 22580 | YES | 1.051 | 0.02011 | -0.090094 | -0.23499 | -0.35132 | -0.51356 | -0.69213 | -0.86867 | -1.1268 | -1.383 | -1.5289 | -2.2309 | -2.5462 | -2.8146 | 1.4507 | 1.3762 | 1.265 | 1.1803 | 1.0528 | 0.91093 | 0.78031 | 0.59256 | 0.39766 | 0.28542 | -0.29009 | -1.1176 | -2.937 | 0.2895 | 0.18848 | 0.046641 | -0.066624 | -0.23295 | -0.4105 | -0.57887 | -0.83703 | -1.0932 | -1.2238 | -1.8105 | -2.0911 | -2.3207
|  | BLEDINGTON | EE |  |  |  | 0.02011 | -0.090094 | -0.23499 | -0.35132 | -0.51356 | -0.69213 | -0.86867 | -1.1268 | -1.383 | -1.5289 | -2.2309 | -2.5268 | -2.7136 | 1.4507 | 1.3762 | 1.265 | 1.1803 | 1.0528 | 0.91093 | 0.78031 | 0.59256 | 0.39766 | 0.28542 | -0.29009 | -0.84418 | -1.7278 | 0.2895 | 0.18848 | 0.046641 | -0.066624 | -0.23295 | -0.4105 | -0.57887 | -0.83703 | -1.0932 | -1.2238 | -1.8105 | -2.0666 | -2.2299
|  | BLEDINGTON | HT |  |  |  | 0.073171 | -0.011522 | -0.10234 | -0.20642 | -0.32989 | -0.42989 | -0.6054 | -0.80642 | -0.96867 | -1.1789 | -2.1176 | -2.5462 | -2.8146 | 1.5181 | 1.463 | 1.4068 | 1.3354 | 1.2538 | 1.1926 | 1.0875 | 0.95889 | 0.85991 | 0.72623 | 0.15072 | -0.076829 | -0.21152 | 0.36909 | 0.28338 | 0.19358 | 0.091539 | -0.028869 | -0.12071 | -0.28703 | -0.47989 | -0.62989 | -0.82989 | -1.7136 | -2.0911 | -2.3207
|  | BLEDINGTON | HE |  |  |  | 0.073171 | -0.012543 | -0.1003 | -0.19826 | -0.31458 | -0.40846 | -0.57377 | -0.76254 | -0.91458 | -1.1136 | -2.0778 | -2.3799 | -2.5248 | 1.5109 | 1.4497 | 1.3793 | 1.3028 | 1.2119 | 1.1395 | 1.0191 | 0.88133 | 0.76705 | 0.61297 | -0.18091 | -0.75336 | -1.6125 | 0.36705 | 0.28338 | 0.19562 | 0.097661 | -0.014584 | -0.1003 | -0.25846 | -0.44009 | -0.57683 | -0.7656 | -1.6615 | -1.9278 | -2.0513
|  | BLEDINGTON | CF |  |  |  | 0.092559 | 0.025212 | -0.0554 | -0.12275 | -0.2054 | -0.29826 | -0.40744 | -0.48601 | -0.60948 | -0.73805 | -1.4217 | -1.9391 | -2.3523 | 1.5262 | 1.4722 | 1.4017 | 1.3487 | 1.2691 | 1.1834 | 1.0803 | 0.99358 | 0.87419 | 0.7446 | -0.051318 | -1.1176 | -2.937 | 0.39154 | 0.32521 | 0.24052 | 0.17929 | 0.096641 | 0.00072245 | -0.1054 | -0.18193 | -0.30642 | -0.43907 | -1.1023 | -1.5687 | -1.9136
BRAMLEY (FLEE) | ALTON | BORDON | MINIMUM HEADROOM | SU 82256 35269 | YES | 6.536 | 2.0775 | 0.65399 | -0.26846 | -1.9021 | -3.2552 | -4.6715 | -6.5562 | -8.696 | -10.6266 | -11.9909 | -18.9562 | -24.2348 | -27.1756 | 7.5642 | 6.6632 | 6.0734 | 4.754 | 3.8173 | 2.8836 | 1.704 | 0.3142 | -0.99091 | -1.8766 | -6.6287 | -11.6205 | -24.247 | 3.7826 | 2.5642 | 1.6877 | -0.028661 | -1.2603 | -2.5368 | -4.2287 | -6.1603 | -7.9195 | -9.1429 | -15.2062 | -19.7062 | -22.2134
|  | BORDON | EE |  |  |  | 2.0775 | 0.65399 | -0.26846 | -1.9021 | -3.2552 | -4.6715 | -6.5562 | -8.696 | -10.6266 | -11.9909 | -18.7429 | -23.3032 | -26.7236 | 7.5642 | 6.6632 | 6.0734 | 4.754 | 3.8173 | 2.8836 | 1.704 | 0.3142 | -0.99091 | -1.8766 | -6.6287 | -11.2113 | -17.8838 | 3.7826 | 2.5642 | 1.6877 | -0.028661 | -1.2603 | -2.5368 | -4.2287 | -6.1603 | -7.9195 | -9.1429 | -15.1001 | -18.9083 | -21.8583
|  | BORDON | HT |  |  |  | 2.4571 | 1.1703 | 0.084604 | -1.4644 | -2.3389 | -3.5644 | -5.2654 | -7.1634 | -8.9134 | -10.5491 | -18.9562 | -24.2348 | -27.1756 | 7.955 | 7.2387 | 6.5693 | 5.3846 | 4.9305 | 4.2754 | 3.4081 | 2.3754 | 1.4173 | 0.48664 | -3.9766 | -6.4052 | -7.6297 | 4.1601 | 3.0826 | 2.0428 | 0.41624 | -0.33376 | -1.4154 | -2.9113 | -4.5919 | -6.1593 | -7.644 | -15.2062 | -19.7062 | -22.2134
|  | BORDON | HE |  |  |  | 2.4315 | 1.1591 | 0.080522 | -1.4511 | -2.3083 | -3.5164 | -5.0378 | -6.7664 | -8.3491 | -9.8297 | -17.3858 | -22.295 | -24.4491 | 7.8744 | 7.104 | 6.3601 | 5.0897 | 4.5397 | 3.7836 | 2.853 | 1.7571 | 0.69991 | -0.34499 | -6.0562 | -11.0572 | -17.2246 | 4.1326 | 3.0662 | 2.0336 | 0.4193 | -0.31846 | -1.3899 | -2.7307 | -4.2705 | -5.6991 | -7.0501 | -13.8807 | -18.0583 | -19.8919
|  | BORDON | CF |  |  |  | 3.1468 | 2.7652 | 2.1979 | 1.2315 | 0.47542 | 0.019298 | -0.96948 | -2.2185 | -3.3072 | -4.2848 | -10.246 | -15.3256 | -19.8409 | 8.2183 | 7.8734 | 7.3622 | 6.3764 | 5.7571 | 5.3897 | 4.6234 | 3.6652 | 2.7754 | 1.8979 | -3.895 | -11.6205 | -24.247 | 4.6999 | 4.3509 | 3.7591 | 2.6438 | 1.9642 | 1.606 | 0.77134 | -0.29805 | -1.247 | -2.1154 | -7.4736 | -12.047 | -16.0338
MELKSHAM GSP | AMESBURY | BOSCOMBE DOWN | MINIMUM HEADROOM | SU 17186 41044 | YES | 4.191 | 4.5987 | 4.4875 | 4.3508 | 4.2314 | 4.0763 | 3.911 | 3.8416 | 3.6151 | 3.3896 | 3.2222 | 2.3467 | 1.6967 | 1.3324 | 4.261 | 4.1589 | 4.0253 | 3.914 | 3.7681 | 3.613 | 3.5569 | 3.3528 | 3.1447 | 2.9824 | 2.0487 | 1.0804 | -1.4941 | 3.8212 | 3.7018 | 3.4702 | 3.2579 | 2.9732 | 2.6681 | 2.7528 | 2.3865 | 2.0181 | 1.811 | 0.71813 | -0.14513 | -0.59309
|  | BOSCOMBE DOWN | EE |  |  |  | 4.5987 | 4.4875 | 4.3508 | 4.2314 | 4.0763 | 3.911 | 3.8416 | 3.6151 | 3.3896 | 3.2222 | 2.3732 | 1.8059 | 1.5181 | 4.261 | 4.1589 | 4.0253 | 3.914 | 3.7681 | 3.613 | 3.5569 | 3.3528 | 3.1447 | 2.9824 | 2.0487 | 1.0804 | -0.15942 | 3.8212 | 3.7018 | 3.4702 | 3.2579 | 2.9732 | 2.6681 | 2.7528 | 2.3865 | 2.0181 | 1.811 | 0.77936 | -0.027788 | -0.4135
|  | BOSCOMBE DOWN | HT |  |  |  | 4.6559 | 4.5579 | 4.4447 | 4.3416 | 4.2181 | 4.1059 | 3.91 | 3.6947 | 3.4681 | 3.3987 | 2.3467 | 1.6967 | 1.3324 | 4.3212 | 4.2457 | 4.1559 | 4.0732 | 3.9722 | 3.8855 | 3.7334 | 3.562 | 3.3845 | 3.3589 | 2.564 | 2.0753 | 1.8202 | 3.8743 | 3.7589 | 3.611 | 3.4763 | 3.3192 | 3.1447 | 2.8273 | 2.4702 | 2.0926 | 2.2049 | 0.71813 | -0.14513 | -0.59309
|  | BOSCOMBE DOWN | HE |  |  |  | 4.6569 | 4.5661 | 4.4579 | 4.363 | 4.2436 | 4.1334 | 3.963 | 3.7651 | 3.5579 | 3.514 | 2.6069 | 2.0569 | 1.7222 | 4.311 | 4.2263 | 4.1212 | 4.0283 | 3.912 | 3.812 | 3.6549 | 3.4773 | 3.2865 | 3.2447 | 2.2396 | 1.264 | 0.014049 | 3.8722 | 3.7753 | 3.6396 | 3.5181 | 3.3681 | 3.2069 | 2.9345 | 2.612 | 2.2743 | 2.4385 | 1.1916 | 0.31813 | -0.1084
|  | BOSCOMBE DOWN | CF |  |  |  | 4.7069 | 4.6487 | 4.5855 | 4.5294 | 4.4579 | 4.3753 | 4.312 | 4.2171 | 4.1161 | 4.0079 | 3.5028 | 2.7896 | 2.1253 | 4.3457 | 4.2783 | 4.2049 | 4.1314 | 4.0457 | 3.9457 | 3.8579 | 3.7324 | 3.5998 | 3.4528 | 2.6406 | 1.1171 | -1.4941 | 3.9089 | 3.8681 | 3.8089 | 3.7406 | 3.6518 | 3.513 | 3.412 | 3.2406 | 3.0569 | 2.861 | 2.2967 | 1.4161 | 0.62323
MANNINGTON GSP | CHRISTCHURCH BSP | BOSCOMBE EAST | MINIMUM HEADROOM | SZ 11636 92447 | YES | 10.927 | 10.0188 | 9.5749 | 9.0086 | 8.429 | 7.7769 | 7.5514 | 6.6514 | 5.6208 | 4.5912 | 3.8106 | 0.62592 | -1.4282 | -1.7659 | 13.2871 | 12.9351 | 12.5127 | 12.0351 | 11.4831 | 11.2198 | 10.5361 | 9.7382 | 8.929 | 8.2831 | 5.0249 | 0.20143 | -11.0047 | 10.2984 | 9.9076 | 9.3953 | 8.8555 | 8.2494 | 8.0055 | 7.1647 | 6.2004 | 5.2382 | 4.4994 | 1.5718 | -0.19551 | -0.46388
|  | BOSCOMBE EAST | EE |  |  |  | 10.0188 | 9.5749 | 9.0086 | 8.429 | 7.7769 | 7.5514 | 6.6514 | 5.6208 | 4.5912 | 3.8106 | 0.62592 | -1.0822 | -1.0465 | 13.2871 | 12.9351 | 12.5127 | 12.0351 | 11.4831 | 11.2198 | 10.5361 | 9.7382 | 8.929 | 8.2831 | 5.0249 | 1.6729 | -3.3098 | 10.2984 | 9.9076 | 9.3953 | 8.8555 | 8.2494 | 8.0055 | 7.1647 | 6.2004 | 5.2382 | 4.4994 | 1.5718 | 0.092245 | 0.1249
|  | BOSCOMBE EAST | HT |  |  |  | 10.2545 | 9.9249 | 9.5045 | 9.1178 | 8.7106 | 8.2086 | 7.4463 | 6.9708 | 6.13 | 5.2576 | 1.0412 | -1.4282 | -1.7659 | 13.5331 | 13.3178 | 13.0586 | 12.7984 | 12.5453 | 12.1963 | 11.73 | 11.4688 | 10.9453 | 10.3922 | 7.8178 | 6.4096 | 6.1433 | 10.4698 | 10.2229 | 9.8902 | 9.5086 | 9.128 | 8.6596 | 7.9555 | 7.5076 | 6.731 | 5.9198 | 2.031 | -0.19551 | -0.46388
|  | BOSCOMBE EAST | HE |  |  |  | 10.2443 | 9.9392 | 9.5463 | 9.1912 | 8.8178 | 8.3514 | 7.6586 | 7.2422 | 6.4861 | 5.6882 | 2.2912 | 0.55551 | 0.25245 | 13.4616 | 13.2014 | 12.8759 | 12.5576 | 12.2239 | 11.8188 | 11.2729 | 10.9208 | 10.2943 | 9.6198 | 5.9912 | 2.4769 | -2.6567 | 10.4627 | 10.228 | 9.9218 | 9.5637 | 9.2096 | 8.7729 | 8.129 | 7.7382 | 7.028 | 6.282 | 3.1351 | 1.5922 | 1.3555
|  | BOSCOMBE EAST | CF |  |  |  | 10.4127 | 10.2341 | 9.9861 | 9.7882 | 9.5392 | 9.3035 | 8.9841 | 8.5882 | 8.1606 | 8.1443 | 5.6984 | 2.9963 | 0.48612 | 13.5535 | 13.3433 | 13.081 | 12.8239 | 12.529 | 12.2045 | 11.7851 | 11.2882 | 10.7361 | 10.4392 | 6.5922 | 0.20143 | -11.0047 | 10.6045 | 10.479 | 10.2973 | 10.1239 | 9.8912 | 9.6708 | 9.3841 | 9.0178 | 8.6249 | 8.578 | 6.2892 | 3.7627 | 1.5239
EALING GSP |  | BOSTON MANOR ROAD | MINIMUM HEADROOM | TQ 17043 78092 | YES | 5.536 | 9.0502 | 8.391 | 7.9808 | 44.1308 | 43.6043 | 42.992 | 42.4002 | 41.7686 | 41.3747 | 40.9941 | 39.7247 | 39.0594 | 38.6676 | 9.1124 | 8.5451 | 8.2696 | 41.2522 | 40.9298 | 40.4614 | 39.9747 | 39.4512 | 39.1584 | 38.8604 | 37.1686 | 32.4114 | 23.1247 | 8.4002 | 7.7288 | 7.2492 | 41.1818 | 40.3951 | 39.6492 | 39.192 | 38.6737 | 38.3961 | 38.1502 | 37.1931 | 36.3645 | 35.9298
|  | BOSTON MANOR ROAD | EE |  |  |  | 9.0502 | 8.391 | 7.9808 | 44.1308 | 43.7267 | 42.992 | 42.4002 | 41.7686 | 41.3747 | 40.9941 | 39.7247 | 39.2573 | 39.1145 | 9.1124 | 8.5451 | 8.2696 | 41.2522 | 41.0104 | 40.4614 | 39.9747 | 39.4512 | 39.1584 | 38.8604 | 37.2084 | 34.5951 | 30.0278 | 8.4002 | 7.7288 | 7.2757 | 41.2798 | 40.7971 | 39.9584 | 39.3084 | 38.6737 | 38.3961 | 38.1502 | 37.1931 | 36.3645 | 36.1237
|  | BOSTON MANOR ROAD | HT |  |  |  | 9.1778 | 8.5053 | 8.0839 | 44.2451 | 43.6043 | 43.0502 | 42.639 | 42.3349 | 42.0124 | 41.6992 | 40.2533 | 39.3563 | 38.9676 | 9.1992 | 8.6482 | 8.3849 | 41.4043 | 40.9298 | 40.5716 | 40.3267 | 40.1522 | 39.9543 | 39.7767 | 39.1002 | 38.4737 | 38.1961 | 8.4829 | 7.7696 | 7.2492 | 41.1818 | 40.3951 | 39.6492 | 39.192 | 38.9696 | 38.7216 | 38.489 | 37.4635 | 36.3676 | 35.9298
|  | BOSTON MANOR ROAD | HE |  |  |  | 9.1614 | 8.5471 | 8.1829 | 44.3982 | 44.0614 | 43.4104 | 42.8971 | 42.3737 | 41.9349 | 41.5451 | 39.8839 | 39.0594 | 38.6676 | 9.1737 | 8.6349 | 8.3818 | 41.4033 | 41.1992 | 40.7053 | 40.2716 | 39.8329 | 39.4665 | 39.1492 | 37.5288 | 34.9798 | 30.4155 | 8.4757 | 7.841 | 7.4155 | 41.4624 | 41.0216 | 40.238 | 39.6676 | 39.1533 | 38.8022 | 38.54 | 37.7155 | 36.9237 | 36.6288
|  | BOSTON MANOR ROAD | CF |  |  |  | 9.2522 | 8.7227 | 8.5186 | 44.9145 | 44.791 | 44.6696 | 44.4186 | 44.0747 | 43.6727 | 43.2604 | 41.2737 | 40.1206 | 39.1278 | 9.2094 | 8.7053 | 8.5267 | 41.6318 | 41.5186 | 41.4002 | 41.1318 | 40.8165 | 40.438 | 39.9737 | 37.1686 | 32.4114 | 23.1247 | 8.5451 | 8.0104 | 7.789 | 42.0829 | 41.9665 | 41.8624 | 41.6594 | 41.3563 | 40.9665 | 40.5737 | 38.8257 | 38.0818 | 37.1839
MANNINGTON GSP | BOURNEMOUTH | BOURNE VALLEY | MINIMUM HEADROOM | SZ 06207 92415 | YES | 2.827 | 5.2224 | 4.3714 | 3.8541 | 2.9367 | 1.9337 | 0.93878 | -0.69592 | -2.5541 | -4.4173 | -5.7959 | -12.8612 | -18.5837 | -21.3714 | 10.0398 | 9.3469 | 8.9255 | 8.1398 | 7.2765 | 6.4163 | 5.2612 | 3.9102 | 2.5306 | 1.5418 | -3.7112 | -10.5133 | -27.2827 | 5.5857 | 4.7408 | 4.2969 | 3.3929 | 2.4235 | 1.4643 | -0.064286 | -1.8133 | -3.5643 | -4.8265 | -10.8592 | -15.9296 | -18.251
|  | BOURNE VALLEY | EE |  |  |  | 5.2224 | 4.3714 | 3.8541 | 2.9367 | 1.9337 | 0.93878 | -0.69592 | -2.5541 | -4.4173 | -5.7959 | -12.5571 | -17.352 | -20.5429 | 10.0398 | 9.3469 | 8.9255 | 8.1398 | 7.2765 | 6.4163 | 5.2612 | 3.9102 | 2.5306 | 1.5418 | -3.7112 | -9.5551 | -18.1837 | 5.5857 | 4.7408 | 4.2969 | 3.3929 | 2.4235 | 1.4643 | -0.064286 | -1.8133 | -3.5643 | -4.8265 | -10.7204 | -14.8847 | -17.601
|  | BOURNE VALLEY | HT |  |  |  | 5.599 | 4.952 | 4.199 | 3.3867 | 2.9969 | 2.2276 | 0.79388 | -0.80204 | -2.498 | -4.2235 | -12.8612 | -18.5837 | -21.3714 | 10.3551 | 9.9255 | 9.4337 | 8.9061 | 8.6939 | 8.1898 | 7.4143 | 6.5031 | 5.5143 | 4.4959 | -0.094898 | -2.7959 | -3.9745 | 6.0255 | 5.4112 | 4.6776 | 3.8837 | 3.5704 | 2.8296 | 1.5357 | 0.081633 | -1.4704 | -3.0551 | -10.8592 | -15.9296 | -18.251
|  | BOURNE VALLEY | HE |  |  |  | 5.6102 | 5.0184 | 4.3245 | 3.5776 | 3.2041 | 2.55 | 1.3949 | 0.1 | -1.2633 | -2.702 | -9.7918 | -14.4816 | -16.5337 | 10.2765 | 9.7898 | 9.2194 | 8.6173 | 8.2459 | 7.7184 | 6.9378 | 6.0235 | 5.001 | 3.898 | -2.1286 | -8.0684 | -16.152 | 6.0224 | 5.4643 | 4.7796 | 4.048 | 3.7449 | 3.1112 | 2.0551 | 0.85612 | -0.41531 | -1.7531 | -8.1429 | -12.2418 | -13.9071
|  | BOURNE VALLEY | CF |  |  |  | 5.951 | 5.4816 | 5.0622 | 4.5867 | 4.0867 | 3.9949 | 3.5347 | 2.9694 | 2.349 | 1.701 | -2.8571 | -7.9235 | -12.898 | 10.4878 | 9.9796 | 9.5276 | 9.0245 | 8.4867 | 8.1878 | 7.6061 | 6.9245 | 6.1592 | 5.3082 | -0.70918 | -10.5133 | -27.2827 | 6.3153 | 5.852 | 5.4357 | 4.952 | 4.4286 | 4.4255 | 3.9827 | 3.4327 | 2.8388 | 2.2194 | -2.0796 | -6.6327 | -10.8939
MANNINGTON GSP | SHAFTESBURY BSP | BOURTON | MINIMUM HEADROOM | ST 77363 30262 | YES | 2.613 | 1.4949 | 1.1163 | 0.43878 | -0.053061 | -0.15 | -0.61939 | -1.3143 | -2.098 | -2.8796 | -3.4112 | -6.1337 | -8.0745 | -9.2735 | 2.9939 | 2.7173 | 2.1612 | 1.7694 | 1.7724 | 1.401 | 0.91837 | 0.3602 | -0.2102 | -0.56327 | -2.5602 | -5.1786 | -11.148 | 2.0071 | 1.652 | 0.98878 | 0.5 | 0.48367 | 0.037755 | -0.61735 | -1.3561 | -2.098 | -2.5867 | -5.0306 | -6.7214 | -7.6918
|  | BOURTON | EE |  |  |  | 1.4949 | 1.1163 | 0.43878 | -0.053061 | -0.15 | -0.61939 | -1.3143 | -2.098 | -2.8796 | -3.4112 | -6.1337 | -7.8449 | -9.1214 | 2.9939 | 2.7173 | 2.1612 | 1.7694 | 1.7724 | 1.401 | 0.91837 | 0.3602 | -0.2102 | -0.56327 | -2.5602 | -4.5571 | -7.6163 | 2.0071 | 1.652 | 0.98878 | 0.5 | 0.48367 | 0.037755 | -0.61735 | -1.3561 | -2.098 | -2.5867 | -5.0306 | -6.5235 | -7.5735
|  | BOURTON | HT |  |  |  | 1.7092 | 1.4153 | 0.8449 | 0.53367 | 0.14592 | -0.27347 | -0.57143 | -1.2133 | -1.8806 | -2.5755 | -5.9959 | -8.0745 | -9.2735 | 3.202 | 3.0316 | 2.6031 | 2.4061 | 2.1449 | 1.8582 | 1.8469 | 1.4847 | 1.0959 | 0.68878 | -1.1786 | -2.1418 | -2.6265 | 2.2255 | 1.9602 | 1.4214 | 1.1296 | 0.77653 | 0.36837 | 0.11531 | -0.47755 | -1.0959 | -1.7408 | -4.8806 | -6.7214 | -7.6918
|  | BOURTON | HE |  |  |  | 1.7 | 1.402 | 0.83163 | 0.52041 | 0.13163 | -0.29286 | -0.8898 | -1.1245 | -1.7418 | -2.3837 | -5.7449 | -7.6847 | -8.5316 | 3.1765 | 2.9694 | 2.5112 | 2.2816 | 1.9786 | 1.6418 | 1.2102 | 1.151 | 0.69286 | 0.20816 | -2.4316 | -4.6602 | -7.5459 | 2.2163 | 1.9439 | 1.4041 | 1.1102 | 0.75102 | 0.35816 | -0.20204 | -0.41633 | -0.99286 | -1.5959 | -4.6939 | -6.4153 | -7.1051
|  | BOURTON | CF |  |  |  | 1.8173 | 1.5908 | 1.1714 | 0.93469 | 0.72449 | 0.45408 | 0.15918 | -0.1949 | -0.14796 | -0.47041 | -2.7051 | -4.8939 | -6.8388 | 3.2306 | 3.051 | 2.6806 | 2.4704 | 2.2755 | 2.0092 | 1.7031 | 1.3327 | 1.3469 | 0.98265 | -1.5612 | -5.1786 | -11.148 | 2.3265 | 2.1173 | 1.7153 | 1.4806 | 1.2847 | 1.0173 | 0.72551 | 0.37245 | 0.48265 | 0.18061 | -1.9265 | -3.9276 | -5.6449
MANNINGTON GSP | WAREHAM | BOVINGTON | MINIMUM HEADROOM | SY 83933 87831 | YES | 0.204 | 4.8184 | 4.7408 | 4.6214 | 4.5173 | 4.2602 | 4.0224 | 3.7245 | 3.1051 | 2.8439 | 2.3786 | 0.62041 | -0.2398 | -0.74592 | 3.9061 | 3.8439 | 3.7582 | 3.6745 | 3.4265 | 3.2459 | 3.05 | 2.7306 | 2.6031 | 2.3602 | 1.3347 | 0.5602 | -1.5102 | 4.1265 | 4.0357 | 3.9 | 3.7888 | 3.4653 | 3.1561 | 2.8031 | 2.3347 | 2.0806 | 1.7153 | 0.22449 | -0.5051 | -0.93571
|  | BOVINGTON | EE |  |  |  | 4.8184 | 4.7408 | 4.6214 | 4.5173 | 4.2602 | 4.0224 | 3.7245 | 3.1051 | 2.8439 | 2.3908 | 0.70918 | -0.083673 | -0.64184 | 3.9061 | 3.8439 | 3.7582 | 3.6745 | 3.4265 | 3.2459 | 3.05 | 2.7306 | 2.6031 | 2.3602 | 1.3347 | 0.57041 | -0.52041 | 4.1265 | 4.0357 | 3.9 | 3.7888 | 3.4653 | 3.1561 | 2.8031 | 2.3347 | 2.0806 | 1.7153 | 0.29796 | -0.37755 | -0.83571
|  | BOVINGTON | HT |  |  |  | 4.8633 | 4.8092 | 4.7122 | 4.6337 | 4.4878 | 4.2796 | 3.9878 | 3.4816 | 2.951 | 2.3786 | 0.62041 | -0.2398 | -0.74592 | 3.9439 | 3.898 | 3.8316 | 3.7755 | 3.6776 | 3.5245 | 3.3582 | 3.1469 | 2.901 | 2.599 | 1.7276 | 1.348 | 1.1224 | 4.1612 | 4.0847 | 3.9582 | 3.8602 | 3.6714 | 3.3796 | 3.0408 | 2.6173 | 2.2051 | 1.7439 | 0.22449 | -0.5051 | -0.93571
|  | BOVINGTON | HE |  |  |  | 4.8643 | 4.8071 | 4.7092 | 4.6286 | 4.3959 | 4.1837 | 3.9704 | 3.5143 | 3.0337 | 2.5418 | 1.0122 | 0.22449 | -0.15714 | 3.9408 | 3.8908 | 3.8194 | 3.7551 | 3.5204 | 3.3582 | 3.1908 | 2.9837 | 2.7133 | 2.4357 | 1.4541 | 0.67551 | -0.33878 | 4.1704 | 4.0929 | 3.9735 | 3.8827 | 3.5806 | 3.2929 | 2.9908 | 2.6 | 2.2214 | 1.8357 | 0.49184 | -0.22041 | -0.57551
|  | BOVINGTON | CF |  |  |  | 4.899 | 4.8673 | 4.7969 | 4.7582 | 4.5449 | 4.302 | 4.1622 | 3.9418 | 3.6796 | 3.3633 | 1.9959 | 1.402 | 0.57755 | 3.9602 | 3.9265 | 3.8704 | 3.8255 | 3.6041 | 3.4194 | 3.298 | 3.1224 | 2.9224 | 2.7163 | 1.6214 | 0.5602 | -1.5102 | 4.2051 | 4.1673 | 4.0857 | 4.0327 | 3.7694 | 3.499 | 3.3194 | 3.0347 | 2.7765 | 2.5388 | 1.4786 | 0.87245 | 0.15204
AMERSHAM | LOUDWATER BSP | BOWERDEAN | MINIMUM HEADROOM | SU 87718 93880 | YES | 4.333 | 5.502 | 3.2498 | 1.9294 | 0.69371 | -0.59506 | -1.8838 | -3.5787 | -5.3308 | -6.943 | -8.0757 | -15.1114 | -20.3206 | -23.1655 | 10.0663 | 8.1764 | 7.3662 | 6.558 | 5.6917 | 4.8039 | 3.7019 | 2.4978 | 1.3315 | 0.58249 | -3.6828 | -9.2349 | -23.0593 | 5.3765 | 3.3356 | 2.1519 | 1.0223 | -0.17261 | -1.391 | -2.9665 | -4.6481 | -6.2257 | -7.194 | -12.8614 | -17.3481 | -19.8165
|  | BOWERDEAN | EE |  |  |  | 5.502 | 3.2498 | 1.9294 | 0.69371 | -0.59506 | -1.8838 | -3.5787 | -5.3308 | -6.943 | -8.0757 | -14.2042 | -19.1379 | -22.7471 | 10.0663 | 8.1764 | 7.3662 | 6.558 | 5.6917 | 4.8039 | 3.7019 | 2.4978 | 1.3315 | 0.58249 | -3.6828 | -8.6093 | -16.0298 | 5.3765 | 3.3356 | 2.1519 | 1.0223 | -0.17261 | -1.391 | -2.9665 | -4.6481 | -6.2257 | -7.194 | -12.1685 | -16.294 | -19.4522
|  | BOWERDEAN | HT |  |  |  | 5.7622 | 3.3162 | 2.0019 | 1.1407 | 0.010041 | -1.1175 | -2.7206 | -4.3073 | -5.7859 | -7.2961 | -15.1114 | -20.3206 | -23.1655 | 10.3622 | 8.4111 | 7.7141 | 7.3509 | 6.7702 | 6.1907 | 5.4039 | 4.559 | 3.7325 | 2.8743 | -1.1022 | -3.2298 | -4.34 | 5.7908 | 3.4825 | 2.3131 | 1.7325 | 0.74065 | -0.27567 | -1.6696 | -3.0981 | -4.4726 | -5.891 | -12.8614 | -17.3481 | -19.8165
|  | BOWERDEAN | HE |  |  |  | 5.799 | 3.4182 | 2.1702 | 1.3825 | 0.32433 | -0.72771 | -1.9859 | -3.2277 | -4.3665 | -5.5665 | -11.994 | -16.8471 | -19.1634 | 10.3041 | 8.307 | 7.5519 | 7.1304 | 6.4794 | 5.8182 | 5.0396 | 4.2029 | 3.3407 | 2.4304 | -2.6481 | -7.6175 | -14.5165 | 5.8082 | 3.5529 | 2.4335 | 1.9182 | 0.98759 | 0.038612 | -1.091 | -2.2593 | -3.3706 | -4.5165 | -10.2502 | -14.2491 | -16.2614
|  | BOWERDEAN | CF |  |  |  | 6.0449 | 3.9121 | 2.958 | 2.1437 | 1.6743 | 0.95494 | 0.3682 | -0.22465 | -0.7318 | -1.2685 | -5.5481 | -10.2838 | -14.7298 | 10.4133 | 8.507 | 7.8611 | 7.2794 | 6.9631 | 6.3845 | 5.7907 | 5.1611 | 4.5162 | 3.808 | -1.39 | -9.2349 | -23.0593 | 6.0235 | 3.9804 | 3.1172 | 2.3519 | 2.1141 | 1.457 | 0.88249 | 0.28861 | -0.24812 | -0.81853 | -5.0002 | -9.0104 | -12.5747
BRAMLEY (FLEE) | BRACKNELL | BRACKNELL | MINIMUM HEADROOM | SU 86075 69397 | YES | 19.238 | 34.636 | 33.7024 | 32.4493 | 31.5901 | 30.2769 | 23.6432 | 21.2973 | 18.3105 | 15.4534 | 13.0238 | 4.7922 | -1.2048 | -4.7078 | 36.8279 | 36.1575 | 35.3075 | 34.7218 | 33.8065 | 27.686 | 25.8116 | 23.5207 | 21.3922 | 19.4983 | 12.5605 | 7.0024 | -5.2446 | 34.0432 | 33.2105 | 32.1126 | 31.3656 | 30.183 | 23.734 | 21.4616 | 18.636 | 15.9922 | 13.7299 | 6.0646 | 0.30543 | -3.0405
|  | BRACKNELL | EE |  |  |  | 34.636 | 33.7024 | 32.4493 | 31.5901 | 30.2769 | 23.6432 | 21.2973 | 18.3105 | 15.4534 | 13.0238 | 5.1371 | 0.67992 | -3.2364 | 36.8279 | 36.1575 | 35.3075 | 34.7218 | 33.8065 | 27.686 | 25.8116 | 23.5207 | 21.3922 | 19.4983 | 12.5605 | 7.0024 | -1.1874 | 34.0432 | 33.2105 | 32.1126 | 31.3656 | 30.183 | 23.734 | 21.4616 | 18.636 | 15.9922 | 13.7299 | 6.4411 | 2.3197 | -1.3976
|  | BRACKNELL | HT |  |  |  | 34.9809 | 34.1871 | 33.1503 | 32.1656 | 30.683 | 24.5616 | 22.4993 | 19.8422 | 17.2197 | 14.6932 | 4.7922 | -1.2048 | -4.7078 | 37.1677 | 36.6707 | 36.083 | 35.5167 | 34.5299 | 28.9299 | 27.4452 | 25.5942 | 23.8483 | 22.0973 | 14.7126 | 10.9524 | 8.9136 | 34.4126 | 33.7054 | 32.8187 | 31.9462 | 30.6187 | 24.682 | 22.6891 | 20.1891 | 17.7779 | 15.4167 | 6.0646 | 0.30543 | -3.0405
|  | BRACKNELL | HE |  |  |  | 34.9473 | 34.1687 | 33.1462 | 32.1809 | 31.0279 | 24.8748 | 23.0248 | 20.5728 | 18.2493 | 15.8228 | 5.2799 | 0.14625 | -2.8272 | 37.0738 | 36.5116 | 35.8381 | 35.185 | 34.4116 | 28.6554 | 27.2034 | 25.3687 | 23.735 | 22.1126 | 14.1116 | 8.5738 | 0.89931 | 34.3758 | 33.683 | 32.8054 | 31.9483 | 30.9258 | 24.9524 | 23.2003 | 20.9289 | 18.8667 | 16.8228 | 6.5595 | 1.682 | -1.3303
|  | BRACKNELL | CF |  |  |  | 35.2483 | 34.6962 | 33.9258 | 33.2983 | 32.5075 | 26.735 | 25.5799 | 24.1442 | 22.3248 | 20.6758 | 13.6003 | 7.3024 | 2.8197 | 37.2462 | 36.7809 | 36.2207 | 35.7289 | 35.1289 | 29.5809 | 28.4554 | 27.1452 | 25.586 | 24.1238 | 17.0962 | 8.5534 | -5.2446 | 34.6585 | 34.1697 | 33.5207 | 32.9779 | 32.2891 | 26.6473 | 25.5575 | 24.2616 | 22.6238 | 21.1514 | 14.6544 | 8.6289 | 4.3881
MELKSHAM GSP | NORRINGTON | BRADFORD-ON-AVON | MINIMUM HEADROOM | ST 81260 60564 | YES | 1.902 | 9.1483 | 8.8034 | 8.3381 | 8.2218 | 7.7718 | 7.2942 | 6.5013 | 5.6146 | 4.7258 | 4.1187 | 0.67686 | -2.3048 | -4.0303 | 13.0177 | 12.7279 | 12.3258 | 12.282 | 11.9024 | 11.4922 | 10.9381 | 10.2942 | 9.6371 | 9.233 | 6.8136 | 3.8809 | -3.5578 | 9.6952 | 9.3564 | 8.9126 | 8.8105 | 8.3789 | 7.9156 | 7.1748 | 6.3391 | 5.4973 | 4.9381 | 1.9269 | -0.63131 | -2.1038
|  | BRADFORD-ON-AVON | EE |  |  |  | 9.1483 | 8.8034 | 8.3381 | 8.2218 | 7.7718 | 7.2942 | 6.5013 | 5.6146 | 4.7258 | 4.1187 | 0.8238 | -1.7466 | -3.7078 | 13.0177 | 12.7279 | 12.3258 | 12.282 | 11.9024 | 11.4922 | 10.9381 | 10.2942 | 9.6371 | 9.233 | 6.8136 | 4.1483 | 0.10645 | 9.6952 | 9.3564 | 8.9126 | 8.8105 | 8.3789 | 7.9156 | 7.1748 | 6.3391 | 5.4973 | 4.9381 | 2.0177 | -0.13437 | -1.8323
|  | BRADFORD-ON-AVON | HT |  |  |  | 9.3789 | 9.0973 | 8.7452 | 8.4258 | 8.0279 | 7.5922 | 7.2656 | 6.5228 | 5.7524 | 4.9422 | 0.67686 | -2.3048 | -4.0303 | 13.2524 | 13.0707 | 12.8248 | 12.6064 | 12.3228 | 12.0013 | 11.9871 | 11.5605 | 11.1116 | 10.6371 | 8.3697 | 7.0238 | 6.2922 | 9.9197 | 9.6544 | 9.3218 | 9.0177 | 8.6391 | 8.2228 | 7.9493 | 7.2575 | 6.5422 | 5.7901 | 1.9269 | -0.63131 | -2.1038
|  | BRADFORD-ON-AVON | HE |  |  |  | 9.3789 | 9.1167 | 8.786 | 8.4901 | 8.1218 | 7.7177 | 7.5146 | 6.8983 | 6.2544 | 5.5922 | 2.0371 | -0.45886 | -1.6884 | 13.2187 | 13.0105 | 12.7279 | 12.4871 | 12.1687 | 11.8167 | 11.7656 | 11.3218 | 10.8473 | 10.3473 | 7.4911 | 4.8044 | 1.084 | 9.9156 | 9.6697 | 9.3564 | 9.0758 | 8.7238 | 8.3381 | 8.1769 | 7.6013 | 6.9993 | 6.3769 | 3.1248 | 1.035 | 0.0013469
|  | BRADFORD-ON-AVON | CF |  |  |  | 9.4932 | 9.3462 | 9.136 | 8.9616 | 8.7309 | 8.4697 | 8.1697 | 8.2462 | 7.9524 | 7.6452 | 5.3462 | 2.8881 | 0.56869 | 13.2748 | 13.1177 | 12.8973 | 12.7003 | 12.4483 | 12.1524 | 11.8034 | 11.7809 | 11.4156 | 11.0218 | 8.1809 | 3.8809 | -3.5578 | 10.0279 | 9.8871 | 9.684 | 9.5167 | 9.2973 | 9.0442 | 8.7534 | 8.836 | 8.5513 | 8.2564 | 6.084 | 3.8636 | 1.8554
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | BRAMLEY GREEN | MINIMUM HEADROOM | SU 67431 58511 | YES | 0.299 | 11.7189 | 11.5066 | 11.2709 | 10.976 | 10.7964 | 10.5689 | 10.2536 | 9.8903 | 9.9056 | 9.6117 | 8.4536 | 7.523 | 6.9485 | 12.0816 | 11.9337 | 11.7745 | 11.5653 | 11.4296 | 11.2459 | 11.0061 | 10.7214 | 10.8745 | 10.749 | 10.0653 | 9.3378 | 7.4939 | 11.5663 | 11.3714 | 11.1592 | 10.8857 | 10.7122 | 10.4837 | 10.1643 | 9.7867 | 9.8898 | 9.6347 | 8.6429 | 7.8561 | 7.4031
|  | BRAMLEY GREEN | EE |  |  |  | 11.7189 | 11.5066 | 11.2709 | 10.976 | 10.7964 | 10.5689 | 10.2536 | 9.8903 | 9.9056 | 9.6944 | 8.5454 | 7.6974 | 7.0423 | 12.0816 | 11.9337 | 11.7745 | 11.5653 | 11.4296 | 11.2459 | 11.0061 | 10.7214 | 10.8745 | 10.749 | 10.0653 | 9.3378 | 8.2959 | 11.5663 | 11.3714 | 11.1592 | 10.8857 | 10.7122 | 10.4837 | 10.1643 | 9.7867 | 9.8898 | 9.7041 | 8.7173 | 8.0184 | 7.4857
|  | BRAMLEY GREEN | HT |  |  |  | 11.7832 | 11.6087 | 11.3811 | 11.1179 | 10.9791 | 10.7934 | 10.5485 | 10.2474 | 9.9332 | 9.6117 | 8.4536 | 7.523 | 6.9485 | 12.1622 | 12.0694 | 11.9347 | 11.7796 | 11.699 | 11.5714 | 11.4439 | 11.2541 | 11.0531 | 10.8469 | 10.4296 | 10.0357 | 9.8051 | 11.6429 | 11.4908 | 11.2918 | 11.0561 | 10.9255 | 10.7459 | 10.5255 | 10.2408 | 9.9408 | 9.6347 | 8.6429 | 7.8561 | 7.4031
|  | BRAMLEY GREEN | HE |  |  |  | 11.7872 | 11.623 | 11.4015 | 11.1495 | 11.0219 | 10.8485 | 10.6566 | 10.4046 | 10.1444 | 9.873 | 8.9209 | 8.0934 | 7.674 | 12.15 | 12.052 | 11.9112 | 11.748 | 11.6602 | 11.5265 | 11.401 | 11.2112 | 11.0153 | 10.799 | 10.2541 | 9.5163 | 8.5694 | 11.6418 | 11.5 | 11.3061 | 11.0816 | 10.9612 | 10.7929 | 10.6163 | 10.3724 | 10.1184 | 9.8531 | 9.0622 | 8.3663 | 8.0378
|  | BRAMLEY GREEN | CF |  |  |  | 11.8332 | 11.7607 | 11.6597 | 11.5107 | 11.3801 | 11.2066 | 11.0556 | 10.9219 | 10.8291 | 10.6944 | 10.0862 | 9.2454 | 8.4699 | 12.1735 | 12.1051 | 12.0235 | 11.9122 | 11.8194 | 11.6898 | 11.5582 | 11.4143 | 11.3122 | 11.1571 | 10.551 | 9.3918 | 7.4939 | 11.6847 | 11.6133 | 11.5235 | 11.3888 | 11.2755 | 11.1173 | 10.9724 | 10.8367 | 10.7469 | 10.6031 | 10.0602 | 9.3245 | 8.6622
LOVEDEAN GSP | PORTSMOUTH BSP | BRANDON ROAD | MINIMUM HEADROOM | SZ 64712 98665 | YES | 1.577 | 6.6855 | 6.0824 | 5.312 | 4.4763 | 3.4936 | 2.4569 | 1.4375 | -0.12166 | -1.6686 | -2.9421 | -7.4257 | -10.5512 | -10.3757 | 11.7834 | 11.2661 | 10.5845 | 9.8416 | 8.9579 | 8.0049 | 7.1243 | 5.8365 | 4.5141 | 3.3641 | -2.4298 | -11.8033 | -33.8002 | 7.4579 | 6.8834 | 6.1477 | 5.3436 | 4.3926 | 3.3732 | 2.4232 | 0.93344 | -0.54717 | -1.7543 | -5.94 | -8.7359 | -8.5594
|  | BRANDON ROAD | EE |  |  |  | 6.6855 | 6.0824 | 5.312 | 4.4763 | 3.4936 | 2.4569 | 1.4375 | -0.12166 | -1.6686 | -2.9421 | -7.4257 | -9.2635 | -8.8339 | 11.7834 | 11.2661 | 10.5845 | 9.8416 | 8.9579 | 8.0049 | 7.1243 | 5.8365 | 4.5141 | 3.3641 | -2.4298 | -8.6308 | -18.591 | 7.4579 | 6.8834 | 6.1477 | 5.3436 | 4.3926 | 3.3732 | 2.4232 | 0.93344 | -0.54717 | -1.7543 | -5.94 | -7.5533 | -7.2298
|  | BRANDON ROAD | HT |  |  |  | 7.0804 | 6.6345 | 6.0834 | 5.4988 | 4.812 | 4.1202 | 3.0681 | 1.8569 | 0.57018 | -0.40125 | -6.837 | -10.5512 | -10.3757 | 12.1457 | 11.8681 | 11.5171 | 11.1161 | 10.6304 | 10.1253 | 9.462 | 8.6753 | 7.8283 | 7.2028 | 3.0314 | 0.60896 | 0.4661 | 7.8477 | 7.4334 | 6.9171 | 6.3651 | 5.709 | 5.0416 | 4.0498 | 2.9008 | 1.6783 | 0.7763 | -5.2859 | -8.7359 | -8.5594
|  | BRANDON ROAD | HE |  |  |  | 7.0488 | 6.6498 | 6.159 | 5.6508 | 5.061 | 4.4865 | 3.6069 | 2.5885 | 1.5253 | 0.82018 | -3.24 | -4.9166 | -4.9625 | 12.0202 | 11.6528 | 11.2028 | 10.7253 | 10.1355 | 9.5273 | 8.7498 | 7.8477 | 6.8732 | 6.109 | 0.43038 | -5.84 | -15.8533 | 7.8171 | 7.4447 | 6.9865 | 6.5079 | 5.9457 | 5.3916 | 4.5651 | 3.6008 | 2.5947 | 1.9416 | -1.9094 | -3.4308 | -3.4441
|  | BRANDON ROAD | CF |  |  |  | 7.2824 | 7.0416 | 6.7141 | 6.3681 | 6.0396 | 5.6743 | 5.31 | 4.8794 | 4.3641 | 3.8161 | 0.89467 | -2.8012 | -6.2074 | 12.1283 | 11.8079 | 11.4039 | 10.961 | 10.4834 | 9.9018 | 9.211 | 8.4212 | 7.5396 | 6.5865 | 0.111 | -11.8033 | -33.8002 | 8.0375 | 7.8151 | 7.509 | 7.1753 | 6.8549 | 6.4906 | 6.1294 | 5.711 | 5.1977 | 4.6518 | 1.862 | -1.5594 | -4.639
BRAMLEY (FLEE) | MAIDENHEAD BSP | BRAYWICK ROAD | MINIMUM HEADROOM | SU 88887 80726 | YES | 5.271 | 4.7873 | 3.5863 | 2.071 | 0.14954 | -2.0841 | -4.1821 | -6.1107 | -7.7362 | -8.6505 | -9.377 | -12.68 | -15.0913 | -16.0658 | 10.0832 | 9.0393 | 8.0557 | 7.2108 | 6.2322 | 5.1108 | 3.9802 | 2.9791 | 2.3332 | 1.8097 | -0.87291 | -4.1219 | -11.9382 | 4.1444 | 3.0016 | 1.6465 | 0.019951 | -1.8596 | -3.5545 | -5.23 | -6.6658 | -7.5535 | -8.2198 | -11.1423 | -13.1821 | -13.9852
|  | BRAYWICK ROAD | EE |  |  |  | 4.7873 | 3.5863 | 2.071 | 0.14954 | -2.0841 | -4.1821 | -6.1107 | -7.7362 | -8.6505 | -9.377 | -12.68 | -14.7035 | -15.6586 | 10.0832 | 9.0393 | 8.0557 | 7.2108 | 6.2322 | 5.1108 | 3.9802 | 2.9791 | 2.3332 | 1.8097 | -0.87291 | -3.4229 | -7.0188 | 4.1444 | 3.0016 | 1.6465 | 0.019951 | -1.8596 | -3.5545 | -5.23 | -6.6658 | -7.5535 | -8.2198 | -11.1423 | -12.8545 | -13.6678
|  | BRAYWICK ROAD | HT |  |  |  | 4.9995 | 3.6291 | 2.1802 | 0.34852 | -1.7596 | -4.1239 | -5.6433 | -6.8596 | -7.6464 | -8.4525 | -12.527 | -15.0913 | -16.0658 | 10.274 | 9.2424 | 8.3587 | 7.6353 | 6.7812 | 5.5863 | 4.7618 | 4.1526 | 3.7148 | 3.2455 | 0.90464 | -0.37189 | -0.84229 | 4.4026 | 3.1557 | 1.8802 | 0.36179 | -1.3954 | -3.3862 | -4.7117 | -5.7239 | -6.4413 | -7.1913 | -10.9209 | -13.1821 | -13.9852
|  | BRAYWICK ROAD | HE |  |  |  | 4.9802 | 3.8353 | 2.5332 | 0.90771 | -1.0188 | -3.1698 | -4.8107 | -6.1627 | -7.076 | -8.0147 | -12.0698 | -14.43 | -15.2423 | 10.2261 | 9.2312 | 8.3393 | 7.6128 | 6.8393 | 5.673 | 4.6914 | 3.9169 | 3.2975 | 2.6393 | -0.81474 | -3.5627 | -7.0862 | 4.3444 | 3.2975 | 2.1291 | 0.77097 | -0.84331 | -2.6678 | -4.0862 | -5.2066 | -6.028 | -6.88 | -10.5872 | -12.6566 | -13.3811
|  | BRAYWICK ROAD | CF |  |  |  | 5.2332 | 4.3873 | 3.6312 | 2.7812 | 1.7006 | 0.077094 | -1.8831 | -3.6943 | -4.0841 | -4.6454 | -7.8341 | -10.9015 | -13.6831 | 10.373 | 9.4955 | 8.7904 | 8.3036 | 7.7934 | 7.1281 | 5.9526 | 4.8628 | 4.5046 | 3.9975 | 0.66689 | -4.1219 | -11.9382 | 4.5597 | 3.7383 | 3.0251 | 2.2904 | 1.3873 | 0.049543 | -1.5556 | -3.0607 | -3.3658 | -3.8739 | -6.8403 | -9.5903 | -12.0137
EALING GSP | EALING 22kV | BRENTFORD | MINIMUM HEADROOM | TQ 17659 78277 | YES | 15.436 | 7.7467 | 4.9204 | 3.601 | 2.2031 | 0.57143 | -1.6602 | -3.5051 | -5.7714 | -7.999 | -9.7245 | -15.0347 | -18.6571 | -19.6735 | 12.4559 | 10.1133 | 9.1347 | 8.0969 | 6.9194 | 5.2765 | 3.5949 | 1.6898 | -0.24082 | -1.8429 | -8.6622 | -19.6102 | -42.9867 | 9.7763 | 7.15 | 5.9673 | 4.6714 | 3.1939 | 1.1673 | -0.65 | -2.7867 | -4.8878 | -6.5143 | -11.4765 | -14.7061 | -15.5622
|  | BRENTFORD | EE |  |  |  | 7.7467 | 4.9204 | 3.601 | 2.2031 | 0.5949 | -1.4806 | -3.5051 | -5.7714 | -7.999 | -9.7245 | -15.0347 | -17.702 | -18.602 | 12.4559 | 10.1133 | 9.1347 | 8.0969 | 6.9194 | 5.2765 | 3.5949 | 1.6898 | -0.24082 | -1.8429 | -8.6622 | -15.499 | -26.8296 | 9.7763 | 7.15 | 5.9673 | 4.6714 | 3.1939 | 1.252 | -0.65 | -2.7867 | -4.8878 | -6.5143 | -11.4765 | -13.8337 | -14.6551
|  | BRENTFORD | HT |  |  |  | 8.1447 | 5.2551 | 4.0857 | 2.7612 | 0.57143 | -1.6602 | -3.4133 | -5.1173 | -6.4306 | -7.9347 | -14.2133 | -18.6571 | -19.6735 | 12.8753 | 10.6337 | 9.9827 | 9.2245 | 7.6776 | 6.1337 | 4.8969 | 3.6071 | 2.6286 | 1.5173 | -2.7643 | -5.3602 | -5.9378 | 10.1824 | 7.5316 | 6.5122 | 5.3265 | 3.2786 | 1.1673 | -0.46224 | -2.0704 | -3.3561 | -4.7704 | -10.6286 | -14.7061 | -15.5622
|  | BRENTFORD | HE |  |  |  | 8.1049 | 5.4939 | 4.3918 | 3.298 | 2.1051 | -0.0040816 | -1.6286 | -3.45 | -4.7847 | -6.3704 | -11.651 | -14.1918 | -14.7265 | 12.7365 | 10.5643 | 9.7653 | 8.9745 | 8.1276 | 6.4643 | 5.0755 | 3.5041 | 2.2102 | 0.67449 | -6.3888 | -13.4847 | -24.5918 | 10.1427 | 7.7337 | 6.752 | 5.7622 | 4.6949 | 2.7163 | 1.1929 | -0.50918 | -1.801 | -3.3 | -8.2449 | -10.5245 | -10.9622
|  | BRENTFORD | CF |  |  |  | 8.4182 | 6.1398 | 5.6122 | 4.9429 | 4.3663 | 3.7969 | 3.052 | 2.001 | 0.74694 | -0.1102 | -7.2857 | -10.9306 | -14.2153 | 12.8865 | 10.8541 | 10.3439 | 9.6633 | 9.049 | 8.3561 | 7.2776 | 5.9398 | 4.4469 | 3.2214 | -6.7765 | -19.6102 | -42.9867 | 10.4141 | 8.2867 | 7.8184 | 7.199 | 6.6633 | 6.1378 | 5.4051 | 4.3939 | 3.2102 | 2.4255 | -4.1622 | -7.5449 | -10.5867
EALING GSP | EALING 22kV | BRIDGE ROAD | MINIMUM HEADROOM | TQ 14778 75741 | YES | 25.214 | 33.5159 | 23.876 | 21.5995 | 19.8597 | 17.1933 | 91.0219 | 88.1882 | 84.6984 | 80.827 | 77.6056 | 69.1495 | 64.8535 | 64.4821 | 44.4996 | 35.1331 | 33.3831 | 32.0413 | 30.4168 | 105.0382 | 102.778 | 100.1403 | 97.2362 | 94.828 | 85.5586 | 72.3842 | 43.6811 | 35.4251 | 25.8597 | 23.8933 | 22.2046 | 20.126 | 94.1178 | 91.2464 | 87.9923 | 84.4291 | 81.578 | 74.126 | 70.4974 | 70.2127
|  | BRIDGE ROAD | EE |  |  |  | 33.5159 | 23.876 | 21.7097 | 19.8617 | 17.5648 | 91.3086 | 88.1882 | 84.6984 | 80.827 | 77.6056 | 69.1495 | 65.8209 | 66.4148 | 44.4996 | 35.1331 | 33.3831 | 32.0413 | 30.4168 | 105.0382 | 102.778 | 100.1403 | 97.2362 | 94.828 | 85.5586 | 77.1525 | 64.1791 | 35.4251 | 25.8597 | 23.8933 | 22.2046 | 20.126 | 94.1178 | 91.2464 | 87.9923 | 84.4291 | 81.578 | 74.126 | 71.3658 | 71.7403
|  | BRIDGE ROAD | HT |  |  |  | 34.1129 | 24.2025 | 21.5995 | 19.8597 | 17.1933 | 91.0219 | 88.3444 | 85.4107 | 82.3178 | 79.3842 | 70.125 | 64.8535 | 64.4821 | 45.1506 | 35.8923 | 34.0729 | 33.2535 | 31.675 | 106.6995 | 105.0444 | 103.1178 | 101.0291 | 99.0668 | 92.7372 | 89.5393 | 89.0219 | 36.0639 | 26.3852 | 24.0311 | 22.6199 | 20.2474 | 94.4076 | 92.0097 | 89.3291 | 86.4974 | 83.8362 | 75.2015 | 70.4974 | 70.2127
|  | BRIDGE ROAD | HE |  |  |  | 34.0904 | 24.8025 | 22.5668 | 21.0515 | 19.5617 | 93.824 | 91.427 | 88.7097 | 85.5842 | 82.5158 | 74.2199 | 71.1699 | 70.5974 | 44.9996 | 35.9464 | 34.0923 | 33.026 | 32.1546 | 107.1791 | 105.425 | 103.3842 | 101.0097 | 98.5944 | 88.7923 | 80.2699 | 66.8015 | 36.0373 | 26.8515 | 24.774 | 23.425 | 22.2352 | 96.7729 | 94.6362 | 92.1842 | 89.374 | 86.6148 | 78.9403 | 76.3117 | 75.8668
|  | BRIDGE ROAD | CF |  |  |  | 34.5843 | 25.7678 | 24.5046 | 23.824 | 23.1699 | 99.6923 | 98.8311 | 97.5505 | 95.9893 | 94.228 | 80.1046 | 74.0342 | 69.1199 | 45.2496 | 36.3607 | 34.9862 | 34.2035 | 33.4046 | 109.6637 | 108.5097 | 107.0342 | 105.3168 | 103.3954 | 88.675 | 72.3842 | 43.6811 | 36.4751 | 27.677 | 26.424 | 25.7699 | 25.1413 | 101.725 | 100.8913 | 99.674 | 98.2076 | 96.5791 | 84.2321 | 78.7933 | 74.5597
LOVEDEAN GSP | HAVANT | BROCKHAMPTON | MINIMUM HEADROOM | SU 70868 05828 | YES | 1.911 | 13.1102 | 12.7561 | 12.2357 | 11.6245 | 10.9194 | 10.1541 | 9.3622 | 8.5847 | 7.9582 | 7.2112 | 4.6765 | 3.3755 | 2.6592 | 12.8969 | 12.5837 | 12.1398 | 11.6184 | 10.9929 | 10.3214 | 9.6439 | 9.0102 | 8.4347 | 7.8214 | 5.8051 | 4.8857 | 3.7755 | 12.5092 | 12.201 | 11.5418 | 10.7878 | 10.0255 | 9.2041 | 8.3367 | 7.4694 | 6.7622 | 6.0296 | 3.5612 | 2.3337 | 1.649
|  | BROCKHAMPTON | EE |  |  |  | 13.1102 | 12.9327 | 12.3388 | 11.6245 | 10.9194 | 10.1541 | 9.3622 | 8.5847 | 7.9582 | 7.2112 | 5.1265 | 4.5224 | 4.5296 | 12.8969 | 12.7704 | 12.2429 | 11.6184 | 10.9929 | 10.3214 | 9.6439 | 9.0102 | 8.4347 | 7.8214 | 6.2439 | 5.9082 | 5.8612 | 12.5092 | 12.2173 | 11.5418 | 10.7878 | 10.0255 | 9.2041 | 8.3367 | 7.4694 | 6.7622 | 6.0296 | 4.0184 | 3.4673 | 3.4735
|  | BROCKHAMPTON | HT |  |  |  | 13.198 | 12.7561 | 12.2357 | 11.6643 | 11.1133 | 10.4796 | 9.9163 | 9.2857 | 8.6061 | 8.0745 | 5.4061 | 4.1184 | 3.6031 | 12.9888 | 12.5837 | 12.1398 | 11.6337 | 11.0847 | 10.5276 | 10.0673 | 9.549 | 8.9949 | 8.5959 | 6.499 | 5.6306 | 5.2429 | 12.6388 | 12.201 | 11.6316 | 10.9857 | 10.3347 | 9.6571 | 9.0388 | 8.3327 | 7.5776 | 6.9551 | 4.2827 | 3.0776 | 2.5898
|  | BROCKHAMPTON | HE |  |  |  | 13.2031 | 13.0684 | 12.5541 | 11.9867 | 11.3663 | 10.6714 | 9.95 | 9.2684 | 8.5347 | 7.752 | 4.6765 | 3.3755 | 2.6592 | 12.9796 | 12.8857 | 12.4306 | 11.9133 | 11.3449 | 10.7276 | 10.1031 | 9.5398 | 8.9378 | 8.2408 | 5.8051 | 4.8857 | 4.3102 | 12.6398 | 12.499 | 11.8918 | 11.2245 | 10.549 | 9.8041 | 9.0153 | 8.2459 | 7.4194 | 6.5592 | 3.5612 | 2.3337 | 1.649
|  | BROCKHAMPTON | CF |  |  |  | 13.2888 | 13.2143 | 13.0888 | 12.6184 | 12.199 | 11.7755 | 11.2327 | 10.65 | 10.1704 | 9.648 | 7.4112 | 5.2082 | 3.549 | 13.0408 | 12.9796 | 12.8959 | 12.4673 | 12.048 | 11.6204 | 11.1337 | 10.6082 | 10.1898 | 9.7388 | 7.8796 | 6.1357 | 3.7755 | 12.7235 | 12.652 | 12.5459 | 12.0888 | 11.5776 | 11.0429 | 10.4776 | 9.8561 | 9.3276 | 8.75 | 6.2 | 4.0347 | 2.498
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | BROCKHURST | MINIMUM HEADROOM | SU 59381 02061 | YES | 3.832 | 19.9843 | 19.4516 | 18.9067 | 18.5976 | 17.9129 | 17.0965 | 54.1639 | 52.8731 | 51.5424 | 50.4802 | 46.0537 | 42.669 | 40.5282 | 21.7169 | 21.2465 | 20.7659 | 20.5363 | 19.9914 | 19.3812 | 55.2445 | 54.3424 | 53.3955 | 52.6537 | 48.8037 | 43.5557 | 32.1802 | 19.9547 | 19.4231 | 18.8547 | 18.5935 | 17.9557 | 17.2118 | 53.469 | 52.2965 | 51.1006 | 50.1741 | 46.2802 | 43.3761 | 41.668
|  | BROCKHURST | EE |  |  |  | 19.9843 | 19.4516 | 18.9067 | 18.6108 | 17.9129 | 17.0965 | 54.1639 | 52.8731 | 51.5424 | 50.4802 | 46.0537 | 43.1006 | 40.672 | 21.7169 | 21.2465 | 20.7659 | 20.5363 | 19.9914 | 19.3812 | 55.2445 | 54.3424 | 53.3955 | 52.6537 | 48.8037 | 44.9333 | 38.9567 | 19.9547 | 19.4231 | 18.8547 | 18.5935 | 17.9557 | 17.2118 | 53.469 | 52.2965 | 51.1006 | 50.1741 | 46.2802 | 43.7853 | 41.7935
|  | BROCKHURST | HT |  |  |  | 20.1771 | 19.6486 | 19.1139 | 18.5976 | 17.9251 | 17.122 | 54.6333 | 53.5414 | 52.5659 | 51.4833 | 46.1241 | 42.669 | 40.5282 | 21.97 | 21.6067 | 21.2618 | 20.9384 | 20.52 | 20.0261 | 56.4098 | 55.7884 | 55.1986 | 54.5435 | 51.5047 | 49.8751 | 49.0302 | 20.2067 | 19.718 | 19.2169 | 18.7353 | 18.1067 | 17.3578 | 54.0996 | 53.1129 | 52.1986 | 51.218 | 46.3884 | 43.3761 | 41.668
|  | BROCKHURST | HE |  |  |  | 20.1629 | 19.7016 | 19.2527 | 18.818 | 18.2414 | 17.5363 | 55.1282 | 54.119 | 53.0771 | 51.9792 | 47.2486 | 44.1629 | 42.7649 | 21.9057 | 21.519 | 21.1465 | 20.7945 | 20.3251 | 19.7771 | 56.07 | 55.3578 | 54.5873 | 53.7741 | 49.4567 | 45.4353 | 39.8741 | 20.1853 | 19.7537 | 19.319 | 18.9037 | 18.3527 | 17.6863 | 54.4976 | 53.5802 | 52.6261 | 51.6496 | 47.3782 | 44.7924 | 43.6618
|  | BROCKHURST | CF |  |  |  | 20.3822 | 20.0976 | 19.9149 | 19.7435 | 19.5363 | 19.2486 | 57.071 | 56.9792 | 56.521 | 55.8812 | 51.421 | 48.2884 | 45.7292 | 22.022 | 21.7037 | 21.4527 | 21.2118 | 20.9016 | 20.4884 | 56.6476 | 56.3904 | 55.8302 | 55.1547 | 50.2996 | 43.5557 | 32.1802 | 20.3853 | 20.1047 | 19.8986 | 19.7129 | 19.4761 | 19.169 | 56.0741 | 56.0129 | 55.5976 | 55.0394 | 51.1557 | 48.3047 | 46.0231
MELKSHAM GSP | NORRINGTON | BROMHAM | MINIMUM HEADROOM | ST 98670 65994 | YES | 0.178 | 3.398 | 3.3204 | 3.2204 | 3.1418 | 3.0143 | 2.8735 | 2.7276 | 2.4796 | 2.248 | 2.1347 | 1.5571 | 1.1265 | 0.8602 | 4.0418 | 3.9827 | 3.902 | 3.8378 | 3.7378 | 3.6357 | 3.5388 | 3.3714 | 3.2122 | 3.1347 | 2.7296 | 2.2765 | 1.1867 | 3.3561 | 3.2776 | 3.1673 | 3.0837 | 2.9551 | 2.8194 | 2.6847 | 2.452 | 2.2296 | 2.1255 | 1.6204 | 1.2684 | 1.052
|  | BROMHAM | EE |  |  |  | 3.398 | 3.3204 | 3.2204 | 3.1418 | 3.0143 | 2.8735 | 2.7276 | 2.4796 | 2.248 | 2.1347 | 1.5571 | 1.1837 | 0.93163 | 4.0418 | 3.9827 | 3.902 | 3.8378 | 3.7378 | 3.6357 | 3.5388 | 3.3714 | 3.2122 | 3.1347 | 2.7296 | 2.3357 | 1.7673 | 3.3561 | 3.2776 | 3.1673 | 3.0837 | 2.9551 | 2.8194 | 2.6847 | 2.452 | 2.2296 | 2.1255 | 1.6204 | 1.3224 | 1.1122
|  | BROMHAM | HT |  |  |  | 3.4469 | 3.3806 | 3.2959 | 3.2286 | 3.1439 | 3.0449 | 2.8724 | 2.7071 | 2.5337 | 2.3918 | 1.5704 | 1.1265 | 0.8602 | 4.0969 | 4.0541 | 3.9959 | 3.9541 | 3.8939 | 3.8235 | 3.7378 | 3.6367 | 3.5224 | 3.451 | 2.9724 | 2.7755 | 2.6653 | 3.4224 | 3.3531 | 3.2653 | 3.201 | 3.1143 | 3.0112 | 2.8612 | 2.6969 | 2.5224 | 2.402 | 1.6306 | 1.2684 | 1.052
|  | BROMHAM | HE |  |  |  | 3.448 | 3.3837 | 3.3051 | 3.2418 | 3.1633 | 3.0684 | 2.9694 | 2.8061 | 2.6204 | 2.501 | 1.7194 | 1.3571 | 1.1765 | 4.0908 | 4.0439 | 3.9796 | 3.9347 | 3.8684 | 3.7949 | 3.7265 | 3.6102 | 3.4806 | 3.401 | 2.8173 | 2.4214 | 1.8796 | 3.4235 | 3.3571 | 3.2714 | 3.2112 | 3.1296 | 3.0316 | 2.9388 | 2.7786 | 2.5939 | 2.4929 | 1.7673 | 1.4765 | 1.3327
|  | BROMHAM | CF |  |  |  | 3.4612 | 3.4184 | 3.3704 | 3.3276 | 3.2663 | 3.2082 | 3.1347 | 3.0847 | 2.9918 | 2.8837 | 2.3031 | 1.8582 | 1.4663 | 4.0959 | 4.0582 | 4.0163 | 3.9796 | 3.9224 | 3.8633 | 3.7929 | 3.7367 | 3.6459 | 3.55 | 2.9765 | 2.2765 | 1.1867 | 3.4337 | 3.3867 | 3.3337 | 3.2929 | 3.2286 | 3.1663 | 3.0878 | 3.0357 | 2.9378 | 2.8357 | 2.2867 | 1.8684 | 1.5459
BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | BROOK STREET | MINIMUM HEADROOM | SU 63480 52228 | YES | 2.038 | 16.6622 | 15.9538 | 15.7629 | 15.5436 | 15.3099 | 15.0517 | 14.716 | 14.1895 | 13.6232 | 13.0252 | 10.2629 | 8.9976 | 8.8732 | 17.649 | 17.0038 | 16.8885 | 16.7558 | 16.6201 | 16.4619 | 16.2476 | 15.8752 | 15.4629 | 15.1272 | 13.1915 | 9.0527 | 1.3099 | 16.602 | 15.9405 | 15.7609 | 15.5344 | 15.3078 | 15.0344 | 14.6629 | 14.2691 | 13.8446 | 13.3201 | 10.6783 | 9.4813 | 9.3691
|  | BROOK STREET | EE |  |  |  | 16.6622 | 15.9538 | 15.7629 | 15.5436 | 15.3099 | 15.0517 | 14.7364 | 14.3374 | 13.9129 | 13.5925 | 12.2915 | 11.4017 | 10.6221 | 17.649 | 17.0038 | 16.8885 | 16.7558 | 16.6201 | 16.4619 | 16.2476 | 15.8752 | 15.4629 | 15.1272 | 13.1915 | 10.8793 | 6.9385 | 16.602 | 15.9405 | 15.7609 | 15.5344 | 15.3078 | 15.0344 | 14.6629 | 14.2691 | 13.8446 | 13.514 | 12.0987 | 11.3089 | 10.6089
|  | BROOK STREET | HT |  |  |  | 16.8 | 16.1762 | 16.0915 | 15.9987 | 15.8783 | 15.7303 | 15.5517 | 15.3283 | 15.0364 | 14.6385 | 12.6334 | 11.2793 | 10.665 | 17.751 | 17.1599 | 17.1089 | 17.0558 | 16.9936 | 16.915 | 16.8354 | 16.7262 | 16.6089 | 16.4834 | 15.3272 | 14.5527 | 14.2456 | 16.7163 | 16.1048 | 16.0078 | 15.8813 | 15.7242 | 15.5415 | 15.2956 | 14.9823 | 14.6538 | 14.3109 | 12.4905 | 11.2466 | 10.714
|  | BROOK STREET | HE |  |  |  | 16.7194 | 16.015 | 15.8252 | 15.614 | 15.3629 | 15.0732 | 14.716 | 14.1895 | 13.6232 | 13.0252 | 10.2629 | 8.9976 | 8.8732 | 17.6908 | 17.0517 | 16.9436 | 16.8313 | 16.6956 | 16.5395 | 16.366 | 16.1415 | 15.7527 | 15.314 | 13.2905 | 10.8987 | 7.1905 | 16.6571 | 16.0017 | 15.8844 | 15.7538 | 15.5956 | 15.3191 | 14.9334 | 14.4323 | 13.8905 | 13.3201 | 10.6783 | 9.4813 | 9.3691
|  | BROOK STREET | CF |  |  |  | 16.85 | 16.2548 | 16.1732 | 16.0691 | 15.9252 | 15.7589 | 15.5813 | 15.3344 | 15.0691 | 14.7762 | 12.615 | 10.5772 | 9.0487 | 17.7663 | 17.166 | 17.0895 | 17.0027 | 16.9058 | 16.7885 | 16.6629 | 16.5007 | 16.2068 | 15.8568 | 13.3752 | 9.0527 | 1.3099 | 16.7582 | 16.167 | 16.0997 | 16.017 | 15.9313 | 15.8262 | 15.7038 | 15.5395 | 15.3058 | 15.0068 | 12.9048 | 10.9558 | 9.5099
MELKSHAM GSP | FROME BSP | BRUTON | MINIMUM HEADROOM | ST 69094 35148 | YES | 0.91 | 2.6569 | 2.5641 | 2.4314 | 2.3222 | 2.1733 | 2.0141 | 1.8273 | 1.5702 | 1.308 | 1.1539 | 0.35898 | -0.17367 | -0.51755 | 3.1649 | 3.0986 | 2.9802 | 2.8914 | 2.7578 | 2.6149 | 2.4822 | 2.2741 | 2.069 | 1.9649 | 1.4384 | 0.8598 | -0.71061 | 2.3529 | 2.262 | 2.1182 | 2.009 | 1.8447 | 1.6682 | 1.4937 | 1.2294 | 0.96918 | 0.83041 | 0.19163 | -0.23796 | -0.52265
|  | BRUTON | EE |  |  |  | 2.6569 | 2.5641 | 2.4314 | 2.3222 | 2.1733 | 2.0141 | 1.8273 | 1.5702 | 1.308 | 1.1539 | 0.35898 | -0.10939 | -0.43082 | 3.1649 | 3.0986 | 2.9802 | 2.8914 | 2.7578 | 2.6149 | 2.4822 | 2.2741 | 2.069 | 1.9649 | 1.4384 | 0.94245 | 0.13224 | 2.3529 | 2.262 | 2.1182 | 2.009 | 1.8447 | 1.6682 | 1.4937 | 1.2294 | 0.96918 | 0.83041 | 0.19163 | -0.17265 | -0.44714
|  | BRUTON | HT |  |  |  | 2.7243 | 2.6406 | 2.5569 | 2.4559 | 2.3427 | 2.2539 | 2.0702 | 1.8641 | 1.6896 | 1.4753 | 0.41 | -0.17367 | -0.51755 | 3.2445 | 3.1894 | 3.1302 | 3.0629 | 2.9751 | 2.9169 | 2.7976 | 2.6618 | 2.5547 | 2.4129 | 1.769 | 1.5067 | 1.3669 | 2.4437 | 2.358 | 2.2773 | 2.1773 | 2.059 | 1.9733 | 1.7967 | 1.5947 | 1.4365 | 1.2233 | 0.23653 | -0.23796 | -0.52265
|  | BRUTON | HE |  |  |  | 2.7222 | 2.6427 | 2.5631 | 2.4692 | 2.359 | 2.2784 | 2.1151 | 1.9294 | 1.7753 | 1.5824 | 0.59061 | 0.13041 | -0.079796 | 3.2373 | 3.1771 | 3.1139 | 3.0384 | 2.9465 | 2.8802 | 2.7588 | 2.6139 | 2.5057 | 2.3516 | 1.5833 | 1.0792 | 0.3149 | 2.4406 | 2.36 | 2.2835 | 2.1886 | 2.0773 | 1.9978 | 1.8376 | 1.6569 | 1.5151 | 1.3222 | 0.40796 | 0.047755 | -0.12878
|  | BRUTON | CF |  |  |  | 2.7529 | 2.6988 | 2.6284 | 2.5763 | 2.508 | 2.4273 | 2.3365 | 2.2702 | 2.1631 | 2.0518 | 1.3814 | 0.79163 | 0.27837 | 3.2567 | 3.2088 | 3.1384 | 3.0924 | 3.0271 | 2.9465 | 2.8496 | 2.7761 | 2.6608 | 2.5373 | 1.7904 | 0.8598 | -0.71061 | 2.4712 | 2.4151 | 2.3324 | 2.2845 | 2.212 | 2.1284 | 2.0365 | 1.9671 | 1.8498 | 1.7304 | 1.0549 | 0.54061 | 0.14571
COWLEY GSP | WITNEY BSP | BURFORD | MINIMUM HEADROOM | SP 25671 12529 | YES | 1.348 | 3.5778 | 3.5053 | 3.4278 | 3.3257 | 3.2073 | 3.1206 | 2.9737 | 2.7982 | 2.6237 | 2.5247 | 2.1624 | 2.0012 | 1.8594 | 4.8066 | 4.7444 | 4.6903 | 4.6097 | 4.5199 | 4.4454 | 4.3352 | 4.2026 | 4.0668 | 3.9842 | 3.6403 | 3.0954 | 1.8087 | 4.5329 | 4.4553 | 4.3798 | 4.2808 | 4.1676 | 4.0849 | 3.939 | 3.7696 | 3.6002 | 3.5094 | 3.1788 | 3.0257 | 2.891
|  | BURFORD | EE |  |  |  | 3.5778 | 3.5053 | 3.4278 | 3.3257 | 3.2073 | 3.1206 | 2.9737 | 2.7982 | 2.6237 | 2.5247 | 2.1624 | 2.0155 | 1.9196 | 4.8066 | 4.7444 | 4.6903 | 4.6097 | 4.5199 | 4.4454 | 4.3352 | 4.2026 | 4.0668 | 3.9842 | 3.6403 | 3.2852 | 2.6995 | 4.5329 | 4.4553 | 4.3798 | 4.2808 | 4.1676 | 4.0849 | 3.939 | 3.7696 | 3.6002 | 3.5094 | 3.1788 | 3.0369 | 2.9482
|  | BURFORD | HT |  |  |  | 3.638 | 3.5859 | 3.5186 | 3.4369 | 3.3757 | 3.2849 | 3.1788 | 3.0482 | 2.9533 | 2.8124 | 2.2563 | 2.0012 | 1.8594 | 4.8556 | 4.8168 | 4.775 | 4.723 | 4.6791 | 4.6199 | 4.5515 | 4.4638 | 4.4026 | 4.3066 | 3.9536 | 3.7954 | 3.7189 | 4.5818 | 4.5308 | 4.4706 | 4.392 | 4.3339 | 4.2461 | 4.1441 | 4.0196 | 3.9288 | 3.7941 | 3.2686 | 3.0257 | 2.891
|  | BURFORD | HE |  |  |  | 3.6359 | 3.5839 | 3.5186 | 3.438 | 3.3808 | 3.2951 | 3.1931 | 3.0665 | 2.9767 | 2.841 | 2.2747 | 2.1114 | 2.0512 | 4.8464 | 4.8046 | 4.7587 | 4.6974 | 4.6536 | 4.5832 | 4.5046 | 4.4097 | 4.3362 | 4.2301 | 3.7332 | 3.3556 | 2.7974 | 4.5798 | 4.5267 | 4.4696 | 4.3941 | 4.34 | 4.2584 | 4.1594 | 4.039 | 3.9543 | 3.8267 | 3.29 | 3.1257 | 3.0716
|  | BURFORD | CF |  |  |  | 3.6522 | 3.6124 | 3.5512 | 3.4982 | 3.4298 | 3.3839 | 3.3145 | 3.238 | 3.1471 | 3.0584 | 2.6012 | 2.3318 | 2.09 | 4.8566 | 4.823 | 4.7781 | 4.7332 | 4.676 | 4.6332 | 4.5679 | 4.4923 | 4.4066 | 4.3148 | 3.773 | 3.0954 | 1.8087 | 4.5961 | 4.5502 | 4.5002 | 4.4492 | 4.3859 | 4.3451 | 4.2798 | 4.2053 | 4.1216 | 4.0308 | 3.592 | 3.341 | 3.1012
MANNINGTON GSP | WAREHAM | BUSHEY | MINIMUM HEADROOM | SY 97671 83532 | YES | 0.161 | 4.899 | 4.8653 | 4.8214 | 4.7173 | 4.6755 | 4.6071 | 4.5296 | 4.4306 | 4.3735 | 4.3245 | 4.0755 | 3.9255 | 3.8204 | 4.902 | 4.8796 | 4.8469 | 4.7837 | 4.7541 | 4.7041 | 4.65 | 4.5796 | 4.5398 | 4.5082 | 4.3633 | 4.2469 | 4.001 | 4.6347 | 4.601 | 4.5592 | 4.4653 | 4.4235 | 4.3571 | 4.2837 | 4.1888 | 4.1337 | 4.0888 | 3.8633 | 3.7276 | 3.6337
|  | BUSHEY | EE |  |  |  | 4.899 | 4.8653 | 4.8214 | 4.7173 | 4.6755 | 4.6071 | 4.5296 | 4.4306 | 4.3735 | 4.3245 | 4.0755 | 3.9378 | 3.8398 | 4.902 | 4.8796 | 4.8469 | 4.7837 | 4.7541 | 4.7041 | 4.65 | 4.5796 | 4.5398 | 4.5082 | 4.3633 | 4.2469 | 4.0796 | 4.6347 | 4.601 | 4.5592 | 4.4653 | 4.4235 | 4.3571 | 4.2837 | 4.1888 | 4.1337 | 4.0888 | 3.8633 | 3.7408 | 3.652
|  | BUSHEY | HT |  |  |  | 4.9337 | 4.9051 | 4.8612 | 4.7929 | 4.7531 | 4.7031 | 4.6347 | 4.5837 | 4.5082 | 4.4378 | 4.1112 | 3.9255 | 3.8204 | 4.9306 | 4.9133 | 4.8816 | 4.8459 | 4.8204 | 4.7847 | 4.7429 | 4.7143 | 4.6643 | 4.6194 | 4.4286 | 4.3357 | 4.2939 | 4.6684 | 4.6398 | 4.599 | 4.5388 | 4.5031 | 4.452 | 4.3888 | 4.3418 | 4.2673 | 4.2031 | 3.8949 | 3.7276 | 3.6337
|  | BUSHEY | HE |  |  |  | 4.9296 | 4.9051 | 4.8622 | 4.7929 | 4.7582 | 4.7092 | 4.648 | 4.6031 | 4.5306 | 4.4694 | 4.1643 | 4.0327 | 3.9816 | 4.9276 | 4.9112 | 4.8806 | 4.8439 | 4.8204 | 4.7857 | 4.7439 | 4.7163 | 4.6643 | 4.6224 | 4.4245 | 4.3041 | 4.1612 | 4.6643 | 4.6408 | 4.6 | 4.5408 | 4.5071 | 4.4592 | 4.401 | 4.3582 | 4.2908 | 4.2327 | 3.948 | 3.8286 | 3.7837
|  | BUSHEY | CF |  |  |  | 4.9459 | 4.9173 | 4.8918 | 4.8378 | 4.8031 | 4.7663 | 4.7418 | 4.699 | 4.651 | 4.6347 | 4.3796 | 4.2316 | 4.0867 | 4.9357 | 4.9184 | 4.901 | 4.8704 | 4.8449 | 4.8173 | 4.8 | 4.7653 | 4.7276 | 4.7122 | 4.498 | 4.3082 | 4.001 | 4.6786 | 4.6531 | 4.6286 | 4.5806 | 4.548 | 4.5122 | 4.4898 | 4.449 | 4.4041 | 4.3888 | 4.1408 | 4.0061 | 3.8755
FAWLEY GSP | LANGLEY BSP | BUTTS ASH | MINIMUM HEADROOM | SU 41923 05772 | YES | 1.541 | 7.8392 | 7.3331 | 7.0718 | 6.5473 | 5.9422 | 5.2953 | 4.1422 | 2.8637 | 1.58 | 0.66776 | -4.671 | -8.821 | -11.1924 | 11.2933 | 10.9382 | 10.7382 | 10.328 | 9.829 | 9.2933 | 8.5137 | 7.6249 | 6.7178 | 6.0933 | 2.529 | -1.9914 | -12.9016 | 7.4494 | 6.9402 | 6.6892 | 6.1616 | 5.5841 | 4.9637 | 3.8973 | 2.6882 | 1.4657 | 0.65755 | -3.9904 | -7.4955 | -9.4771
|  | BUTTS ASH | EE |  |  |  | 7.8392 | 7.3331 | 7.0718 | 6.5473 | 5.9422 | 5.2953 | 4.1422 | 2.8637 | 1.58 | 0.66776 | -4.1496 | -7.969 | -10.8771 | 11.2933 | 10.9382 | 10.7382 | 10.328 | 9.829 | 9.2933 | 8.5137 | 7.6249 | 6.7178 | 6.0933 | 2.529 | -1.3455 | -7.1078 | 7.4494 | 6.9402 | 6.6892 | 6.1616 | 5.5841 | 4.9637 | 3.8973 | 2.6882 | 1.4657 | 0.65755 | -3.6282 | -6.7629 | -9.219
|  | BUTTS ASH | HT |  |  |  | 8.0433 | 7.6096 | 7.179 | 6.6943 | 6.4922 | 6.0035 | 4.9708 | 3.8698 | 2.731 | 1.5688 | -4.671 | -8.821 | -11.1924 | 11.4943 | 11.2484 | 11.0055 | 10.7269 | 10.6494 | 10.3698 | 9.8371 | 9.2392 | 8.6045 | 7.9484 | 4.7361 | 2.9167 | 1.9678 | 7.6912 | 7.2882 | 6.8718 | 6.3943 | 6.2218 | 5.7422 | 4.8014 | 3.7841 | 2.7249 | 1.6382 | -3.9904 | -7.4955 | -9.4771
|  | BUTTS ASH | HE |  |  |  | 8.0831 | 7.6882 | 7.2759 | 6.8239 | 6.6586 | 6.2076 | 5.3912 | 4.4902 | 3.5392 | 2.5514 | -2.7578 | -6.7322 | -8.5863 | 11.4678 | 11.1902 | 10.8769 | 10.5402 | 10.3933 | 10.0341 | 9.48 | 8.83 | 8.131 | 7.3912 | 3.1494 | -0.92714 | -6.3088 | 7.73 | 7.3504 | 6.9433 | 6.4963 | 6.3535 | 5.9086 | 5.1463 | 4.2953 | 3.4024 | 2.481 | -2.3731 | -5.6924 | -7.222
|  | BUTTS ASH | CF |  |  |  | 8.2688 | 8.0739 | 7.8667 | 7.5963 | 7.3249 | 7.3433 | 7.0647 | 6.7086 | 6.3096 | 5.8922 | 2.4535 | -1.372 | -4.9598 | 11.5463 | 11.3596 | 11.1453 | 10.8698 | 10.578 | 10.4576 | 10.0922 | 9.6239 | 9.1096 | 8.5545 | 4.4024 | -1.9914 | -12.9016 | 7.8902 | 7.6984 | 7.482 | 7.2045 | 6.9157 | 6.9443 | 6.6565 | 6.3055 | 5.9259 | 5.5198 | 2.2708 | -1.1506 | -4.2924
MELKSHAM GSP | CHIPPENHAM | CALNE | MINIMUM HEADROOM | SU 00521 72497 | YES | 0.795 | 8.3602 | 7.9398 | 7.3745 | 7.1031 | 6.4041 | 5.5357 | 4.3184 | 3.0276 | 1.6378 | 0.38469 | -4.3112 | -8.1357 | -10.3143 | 9.7296 | 9.3622 | 8.8398 | 8.7398 | 8.1898 | 7.551 | 6.7592 | 5.8602 | 4.9122 | 4.2265 | 1.3071 | -1.9643 | -10.4541 | 8.8561 | 8.4 | 7.7673 | 7.549 | 6.8357 | 5.9888 | 4.848 | 3.598 | 2.2714 | 1.2102 | -2.6031 | -5.6612 | -7.4214
|  | CALNE | EE |  |  |  | 8.3602 | 7.9398 | 7.3745 | 7.1031 | 6.4041 | 5.5357 | 4.3184 | 3.0276 | 1.6378 | 0.38469 | -4.2541 | -7.5429 | -9.9786 | 9.7296 | 9.3622 | 8.8398 | 8.7398 | 8.1898 | 7.551 | 6.7592 | 5.8602 | 4.9122 | 4.2265 | 1.3071 | -1.7612 | -6.1806 | 8.8561 | 8.4 | 7.7673 | 7.549 | 6.8357 | 5.9888 | 4.848 | 3.598 | 2.2714 | 1.2102 | -2.6031 | -5.1296 | -7.1643
|  | CALNE | HT |  |  |  | 8.5806 | 8.1878 | 7.7714 | 7.3296 | 6.5929 | 5.9796 | 4.7898 | 3.6704 | 2.5122 | 1.3255 | -4.3112 | -8.1357 | -10.3143 | 10.0408 | 9.7867 | 9.5041 | 9.1724 | 8.6959 | 8.549 | 7.9551 | 7.3429 | 6.6857 | 6.0051 | 3.05 | 1.3704 | 0.48061 | 9.1694 | 8.7878 | 8.3663 | 7.902 | 7.1969 | 6.7541 | 5.7173 | 4.6918 | 3.6173 | 2.5082 | -2.5571 | -5.6612 | -7.4214
|  | CALNE | HE |  |  |  | 8.5653 | 8.2286 | 7.8153 | 7.3408 | 6.7061 | 6.2041 | 5.2286 | 4.2051 | 3.0541 | 1.7888 | -3.3469 | -6.9194 | -8.4847 | 9.9888 | 9.7255 | 9.4031 | 9.0143 | 8.5347 | 8.3745 | 7.7857 | 7.1235 | 6.3786 | 5.5643 | 1.7214 | -1.6439 | -5.7418 | 9.149 | 8.8061 | 8.3959 | 7.9071 | 7.2816 | 6.9296 | 6.0531 | 5.102 | 4.0398 | 2.8755 | -1.7582 | -4.5786 | -5.8837
|  | CALNE | CF |  |  |  | 8.7531 | 8.5643 | 8.3276 | 8.0704 | 7.7551 | 7.449 | 7.102 | 6.9827 | 6.5378 | 5.8867 | 1.7418 | -1.9082 | -5.3071 | 10.0949 | 9.8949 | 9.6286 | 9.3755 | 9.048 | 8.6796 | 8.2582 | 8.2041 | 7.7194 | 7.1347 | 3.2867 | -1.9643 | -10.4541 | 9.3276 | 9.1235 | 8.852 | 8.5898 | 8.25 | 7.9031 | 7.5163 | 7.4816 | 7.0163 | 6.3939 | 2.5143 | -0.65918 | -3.4133
BRAMLEY (FLEE) | CAMBERLEY MAIN | CAMBERLEY | MINIMUM HEADROOM | SU 86584 59452 | YES | 3.322 | 52.171 | 51.5128 | 50.9435 | 50.3965 | 49.67 | 48.8261 | 47.7904 | 46.5639 | 45.3781 | 44.373 | 39.3639 | 35.9986 | 34.2965 | 52.4077 | 51.7741 | 51.3292 | 50.9322 | 50.3894 | 49.7557 | 49.0271 | 48.0802 | 47.1139 | 46.3608 | 42.2588 | 36.1853 | 22.9047 | 51.8914 | 51.122 | 50.469 | 50.1894 | 49.5353 | 48.8016 | 47.7577 | 46.5628 | 45.3751 | 44.5159 | 40.4884 | 37.2741 | 35.6679
|  | CAMBERLEY | EE |  |  |  | 52.171 | 51.5128 | 50.9435 | 50.3965 | 49.67 | 48.8261 | 47.7904 | 46.5639 | 45.3781 | 44.373 | 40.0914 | 37.1435 | 34.5465 | 52.4077 | 51.7741 | 51.3292 | 50.9322 | 50.3894 | 49.7557 | 49.0271 | 48.0802 | 47.1139 | 46.3608 | 42.2588 | 37.869 | 31.0312 | 51.8914 | 51.122 | 50.469 | 50.1894 | 49.5353 | 48.8016 | 47.7577 | 46.5628 | 45.3751 | 44.5159 | 40.4884 | 37.8618 | 35.8628
|  | CAMBERLEY | HT |  |  |  | 52.5169 | 51.9822 | 51.5955 | 51.1639 | 50.57 | 49.919 | 49.2302 | 48.269 | 47.2547 | 46.2067 | 40.4996 | 36.4588 | 34.2965 | 52.7108 | 52.2016 | 51.8955 | 51.5649 | 51.1343 | 50.6649 | 50.2281 | 49.5741 | 48.8812 | 48.1598 | 44.8322 | 43.2537 | 42.4598 | 52.2077 | 51.5496 | 51.0506 | 50.6006 | 50.022 | 49.3955 | 48.9108 | 47.9424 | 46.9292 | 45.8812 | 40.5853 | 37.2741 | 35.6679
|  | CAMBERLEY | HE |  |  |  | 52.4486 | 51.8771 | 51.4373 | 50.9241 | 50.2914 | 49.521 | 48.7353 | 47.6312 | 46.4557 | 45.223 | 39.3639 | 35.9986 | 34.6649 | 52.6465 | 52.0924 | 51.7363 | 51.3424 | 50.872 | 50.2935 | 49.7516 | 48.9567 | 48.1016 | 47.2047 | 42.7312 | 37.9547 | 31.5118 | 52.1822 | 51.5384 | 51.0496 | 50.6057 | 50.0598 | 49.4332 | 49.0465 | 48.1608 | 47.2353 | 46.0577 | 40.4884 | 37.7037 | 36.4873
|  | CAMBERLEY | CF |  |  |  | 52.7006 | 52.2904 | 52.0404 | 51.7935 | 51.4904 | 51.1475 | 50.723 | 50.2904 | 49.671 | 49.0067 | 44.7281 | 40.5965 | 37.371 | 52.7761 | 52.3384 | 52.0445 | 51.7506 | 51.3863 | 50.9475 | 50.4292 | 50.1026 | 49.4975 | 48.8312 | 43.9792 | 36.1853 | 22.9047 | 52.3873 | 51.8935 | 51.5873 | 51.3302 | 51.0067 | 50.6475 | 50.2526 | 50.2118 | 49.7628 | 49.2884 | 45.5384 | 41.6322 | 38.7567
WILLESDEN GSP | CANAL BANK | CANAL BANK 11kV | MINIMUM HEADROOM | TQ 20927 83082 | YES | 11.896 | 33.1764 | 32.3264 | 31.0723 | 29.6642 | 27.5928 | 25.0356 | 21.5448 | 17.6132 | 13.6407 | 8.6999 | -7.7848 | -12.8277 | -17.1042 | 27.1729 | 26.5463 | 25.7871 | 24.9055 | 23.2841 | 21.3045 | 17.4576 | 12.8473 | 8.5188 | 2.8188 | -18.2486 | -23.9445 | -28.3894 | 27.3076 | 26.5198 | 25.4586 | 24.2341 | 22.1953 | 19.6841 | 15.7667 | 11.2167 | 6.8412 | 1.2178 | -18.3037 | -24.0527 | -28.7812
|  | CANAL BANK 11kV | EE |  |  |  | 33.1764 | 32.4968 | 31.4917 | 30.2652 | 28.7846 | 26.553 | 23.403 | 19.7356 | 16.0652 | 12.1193 | -5.7787 | -8.8981 | -13.0746 | 27.1749 | 26.6065 | 25.9576 | 25.1718 | 24.2576 | 22.6116 | 19.1688 | 15.0627 | 11.4218 | 7.3096 | -15.7588 | -19.1496 | -23.4322 | 27.3076 | 26.6453 | 25.7555 | 24.6708 | 23.3749 | 21.2392 | 17.682 | 13.5024 | 9.6433 | 5.3759 | -15.8098 | -19.2057 | -23.7955
|  | CANAL BANK 11kV | HT |  |  |  | 33.1815 | 32.3264 | 31.0723 | 29.6642 | 27.5928 | 25.0356 | 21.5448 | 17.6132 | 13.6407 | 8.6999 | -7.7848 | -12.8277 | -17.1042 | 27.1759 | 26.5463 | 25.7871 | 24.9055 | 23.2841 | 21.3045 | 17.4576 | 12.8473 | 8.5188 | 2.8188 | -18.2486 | -23.9445 | -28.3894 | 27.3147 | 26.5198 | 25.4586 | 24.2341 | 22.1953 | 19.6841 | 15.7667 | 11.2167 | 6.8412 | 1.2178 | -18.3037 | -24.0527 | -28.7812
|  | CANAL BANK 11kV | HE |  |  |  | 33.1795 | 32.5213 | 31.5264 | 30.3019 | 28.8356 | 26.6254 | 24.0815 | 20.9642 | 18.1917 | 15.2948 | -1.8879 | -5.094 | -9.2113 | 27.1729 | 26.6269 | 25.9831 | 25.2127 | 24.3116 | 22.6933 | 19.9831 | 16.5586 | 14.032 | 11.1871 | -11.1078 | -14.6302 | -18.9557 | 27.3116 | 26.6688 | 25.7871 | 24.7065 | 23.4249 | 21.3106 | 18.4861 | 14.9984 | 12.2678 | 9.2963 | -11.0608 | -14.57 | -19.1404
|  | CANAL BANK 11kV | CF |  |  |  | 33.4162 | 33.0652 | 32.6346 | 32.1142 | 31.5326 | 30.7887 | 29.1642 | 26.7856 | 24.4785 | 22.1285 | 7.8672 | -1.5338 | -1.4644 | 27.2984 | 26.8851 | 26.429 | 25.9596 | 25.4667 | 24.9116 | 23.0871 | 20.4351 | 18.1178 | 15.8698 | 3.8116 | -8.9404 | -9.1384 | 27.5259 | 27.1249 | 26.6606 | 26.1708 | 25.6147 | 24.8412 | 22.9759 | 20.2371 | 17.7024 | 15.2759 | 1.7504 | -9.6435 | -9.3955
COWLEY GSP | WITNEY BSP | CARTERTON | MINIMUM HEADROOM | SP 28261 07823 | YES | 1.169 | 15.902 | 14.952 | 14.1173 | 13.6959 | 13.0061 | 12.3276 | 11.7092 | 11.0194 | 10.2939 | 9.7878 | 6.698 | 3.9663 | 2.2541 | 19.2949 | 18.7469 | 18.2439 | 18.0316 | 17.601 | 17.1622 | 16.7214 | 16.2194 | 15.699 | 15.3255 | 13.0571 | 9.8082 | 2.2969 | 16.4429 | 15.651 | 14.9041 | 14.5541 | 13.9092 | 13.2653 | 12.648 | 11.9459 | 11.2449 | 10.7796 | 8.1255 | 5.8092 | 4.4367
|  | CARTERTON | EE |  |  |  | 15.902 | 14.952 | 14.1173 | 13.6959 | 13.0061 | 12.3276 | 11.7092 | 11.0194 | 10.2939 | 9.7878 | 7.0092 | 4.5531 | 2.5551 | 19.2949 | 18.7469 | 18.2439 | 18.0316 | 17.601 | 17.1622 | 16.7214 | 16.2194 | 15.699 | 15.3255 | 13.0571 | 10.3173 | 6.2071 | 16.4429 | 15.651 | 14.9041 | 14.5541 | 13.9092 | 13.2653 | 12.648 | 11.9459 | 11.2449 | 10.7796 | 8.3418 | 6.3316 | 4.6898
|  | CARTERTON | HT |  |  |  | 16.0541 | 15.1418 | 14.3745 | 13.7694 | 13.0969 | 12.4327 | 12.1429 | 11.5378 | 10.9102 | 10.2602 | 6.698 | 3.9663 | 2.2541 | 19.4602 | 18.9918 | 18.5959 | 18.2959 | 17.9449 | 17.5918 | 17.5184 | 17.1837 | 16.8357 | 16.4714 | 14.6204 | 13.3643 | 12.6092 | 16.6224 | 15.8918 | 15.2316 | 14.7 | 14.0898 | 13.4776 | 13.2439 | 12.6643 | 12.0592 | 11.4286 | 8.1255 | 5.8092 | 4.4367
|  | CARTERTON | HE |  |  |  | 16.0643 | 15.1816 | 14.4429 | 13.8724 | 13.2337 | 12.6071 | 12.4704 | 12.0133 | 11.5378 | 11.0449 | 8.1827 | 5.7184 | 4.4061 | 19.4255 | 18.9327 | 18.5051 | 18.1714 | 17.7827 | 17.3847 | 17.299 | 16.9459 | 16.5643 | 16.1602 | 13.6602 | 10.8643 | 7.0449 | 16.6276 | 15.9224 | 15.2888 | 14.7857 | 14.2092 | 13.6347 | 13.5316 | 13.0796 | 12.6051 | 12.1102 | 9.4398 | 7.398 | 6.349
|  | CARTERTON | CF |  |  |  | 16.2082 | 15.4531 | 14.9112 | 14.4745 | 14.0449 | 13.6112 | 13.4071 | 13.4847 | 13.2898 | 13.0888 | 11.1439 | 8.8776 | 6.5888 | 19.4867 | 19.0347 | 18.698 | 18.3939 | 18.098 | 17.7541 | 17.4663 | 17.3878 | 17.0796 | 16.75 | 14.1347 | 9.8082 | 2.2969 | 16.7582 | 16.1592 | 15.7112 | 15.3235 | 14.9449 | 14.55 | 14.3337 | 14.4102 | 14.1929 | 13.9673 | 12.0388 | 9.998 | 8.0827
AXMINSTER | YEOVIL BSP | CASTLE CARY | MINIMUM HEADROOM | ST 64534 31039 | YES | 2.075 | 7.85 | 7.697 | 7.4898 | 7.2184 | 6.9092 | 6.6419 | 6.3194 | 5.9562 | 5.5888 | 5.7847 | 4.6735 | 3.896 | 3.4123 | 9.0067 | 8.8914 | 8.7495 | 8.5587 | 8.3424 | 8.1577 | 7.923 | 7.6516 | 7.375 | 7.625 | 6.8546 | 5.9322 | 3.6638 | 8.0536 | 7.9118 | 7.7199 | 7.4699 | 7.1761 | 6.925 | 6.6159 | 6.2659 | 5.9128 | 6.2036 | 5.324 | 4.6924 | 4.2995
|  | CASTLE CARY | EE |  |  |  | 7.85 | 7.697 | 7.4898 | 7.2184 | 6.9092 | 6.6419 | 6.3194 | 5.9562 | 5.5888 | 5.7847 | 4.6735 | 3.9949 | 3.5113 | 9.0067 | 8.8914 | 8.7495 | 8.5587 | 8.3424 | 8.1577 | 7.923 | 7.6516 | 7.375 | 7.625 | 6.8546 | 6.0567 | 4.8863 | 8.0536 | 7.9118 | 7.7199 | 7.4699 | 7.1761 | 6.925 | 6.6159 | 6.2659 | 5.9128 | 6.2057 | 5.324 | 4.7914 | 4.3873
|  | CASTLE CARY | HT |  |  |  | 7.9205 | 7.8092 | 7.6276 | 7.398 | 7.1786 | 6.898 | 6.6337 | 6.3949 | 6.1092 | 5.8164 | 4.7092 | 3.896 | 3.4123 | 9.073 | 9.0077 | 8.9077 | 8.7699 | 8.6526 | 8.4893 | 8.3281 | 8.1873 | 8.0006 | 7.8016 | 7.3373 | 6.9587 | 6.7669 | 8.1291 | 8.023 | 7.8669 | 7.6659 | 7.4761 | 7.2301 | 6.9791 | 6.7669 | 6.4904 | 6.2036 | 5.3546 | 4.6924 | 4.2995
|  | CASTLE CARY | HE |  |  |  | 7.9256 | 7.8092 | 7.6317 | 7.4123 | 7.1929 | 6.9225 | 6.6898 | 6.4766 | 6.2184 | 5.9551 | 4.9582 | 4.2817 | 3.9949 | 9.0669 | 8.9873 | 8.8781 | 8.7373 | 8.6036 | 8.4342 | 8.2679 | 8.1199 | 7.923 | 7.7128 | 7.0087 | 6.1904 | 5.1067 | 8.1352 | 8.024 | 7.872 | 7.6771 | 7.4924 | 7.2567 | 7.0332 | 6.8444 | 6.5934 | 6.3342 | 5.5883 | 5.072 | 4.8271
|  | CASTLE CARY | CF |  |  |  | 7.9654 | 7.896 | 7.7562 | 7.5909 | 7.398 | 7.2235 | 7.1021 | 6.9705 | 6.8245 | 6.7215 | 5.7317 | 5.2827 | 4.5623 | 9.0873 | 9.0342 | 8.9404 | 8.8261 | 8.6955 | 8.575 | 8.4587 | 8.3169 | 8.1628 | 8.0465 | 6.9985 | 5.9322 | 3.6638 | 8.1689 | 8.1016 | 7.9822 | 7.8363 | 7.6679 | 7.521 | 7.4016 | 7.2618 | 7.1108 | 7.0169 | 6.0546 | 5.825 | 5.2679
LALEHAM | STAINES | CAUSEWAY | MINIMUM HEADROOM | TQ 02763 71680 | YES | 13.382 | 27.4369 | 27.1604 | 26.7482 | 26.2359 | 25.7849 | 25.1788 | 24.3063 | 23.2839 | 22.1992 | 21.0522 | 17.9451 | 15.1451 | 13.5727 | 29.1608 | 29.0047 | 28.7792 | 28.4965 | 28.3139 | 27.8373 | 27.12 | 26.322 | 25.421 | 24.5149 | 21.4792 | 17.0016 | 7.2394 | 27.6869 | 27.4247 | 27.0359 | 26.5563 | 26.1471 | 25.5818 | 24.8594 | 24.0298 | 23.1165 | 21.9298 | 18.7237 | 16.2543 | 14.8971
|  | CAUSEWAY | EE |  |  |  | 27.4369 | 27.1604 | 26.7482 | 26.2359 | 25.7849 | 25.1788 | 24.3063 | 23.2839 | 22.1992 | 21.0522 | 17.9553 | 15.6543 | 13.8196 | 29.1608 | 29.0047 | 28.7792 | 28.4965 | 28.3139 | 27.8373 | 27.12 | 26.322 | 25.421 | 24.5149 | 21.4792 | 18.1782 | 13.0833 | 27.6869 | 27.4247 | 27.0359 | 26.5563 | 26.1471 | 25.5818 | 24.8594 | 24.0298 | 23.1165 | 21.9298 | 18.8043 | 16.6798 | 15.089
|  | CAUSEWAY | HT |  |  |  | 27.6237 | 27.4124 | 27.0808 | 26.6655 | 26.2104 | 25.6706 | 24.8329 | 24.0124 | 22.8839 | 21.6992 | 17.9451 | 15.1451 | 13.5727 | 29.27 | 29.1751 | 29.02 | 28.821 | 28.6159 | 28.3353 | 27.8333 | 27.4108 | 26.5924 | 25.7955 | 23.7271 | 22.4251 | 21.7435 | 27.8614 | 27.6665 | 27.3594 | 26.9727 | 26.5441 | 26.0441 | 25.3359 | 24.5931 | 23.438 | 22.2094 | 18.7237 | 16.2543 | 14.8971
|  | CAUSEWAY | HE |  |  |  | 27.6114 | 27.39 | 27.0492 | 26.6176 | 26.1431 | 25.5931 | 24.8155 | 24.0349 | 23.0165 | 21.7859 | 17.989 | 15.9522 | 14.9665 | 29.2476 | 29.1271 | 28.9465 | 28.7169 | 28.4751 | 28.1078 | 27.4669 | 27.0282 | 26.2486 | 25.3149 | 22.0506 | 18.6924 | 13.872 | 27.8492 | 27.6471 | 27.3318 | 26.9329 | 26.49 | 25.9767 | 25.3216 | 24.6951 | 23.8502 | 22.8339 | 19.591 | 17.5676 | 16.5696
|  | CAUSEWAY | CF |  |  |  | 27.7696 | 27.6553 | 27.4971 | 27.2829 | 27.0094 | 26.5512 | 26.0971 | 25.5971 | 25.1502 | 24.4114 | 21.5869 | 18.8869 | 16.6553 | 29.3016 | 29.2159 | 29.1067 | 28.9588 | 28.7812 | 28.4261 | 27.9261 | 27.3169 | 26.8904 | 26.07 | 22.5404 | 17.0016 | 7.2394 | 27.9971 | 27.892 | 27.7441 | 27.5461 | 27.288 | 26.8614 | 26.441 | 25.9737 | 25.5594 | 24.8798 | 22.4594 | 20.3665 | 18.3512
BRAMLEY (FLEE) | READING TOWN BSP | CAVERSHAM | MINIMUM HEADROOM | SU 71512 75747 | YES | 0.643 | 14.9061 | 14.4571 | 13.851 | 13.8061 | 13.2459 | 12.6408 | 11.6561 | 10.5388 | 9.4194 | 8.7112 | 5.0255 | 2.0939 | 1.0653 | 18.1816 | 17.8194 | 17.3398 | 17.2163 | 16.7408 | 16.2235 | 15.5082 | 14.6837 | 13.8429 | 13.2724 | 9.9735 | 4.9367 | -6.398 | 15.7245 | 15.3143 | 14.7316 | 14.6867 | 14.1571 | 13.5663 | 12.6408 | 11.5806 | 10.5204 | 9.8643 | 6.4092 | 3.8653 | 3.0245
|  | CAVERSHAM | EE |  |  |  | 14.9061 | 14.4571 | 13.851 | 13.8061 | 13.2459 | 12.6408 | 11.6561 | 10.5388 | 9.4194 | 8.7112 | 5.1612 | 2.6357 | 1.6959 | 18.1816 | 17.8194 | 17.3398 | 17.2163 | 16.7408 | 16.2235 | 15.5082 | 14.6837 | 13.8429 | 13.2724 | 9.9735 | 6.402 | 1.0143 | 15.7245 | 15.3143 | 14.7316 | 14.6867 | 14.1571 | 13.5663 | 12.6408 | 11.5806 | 10.5204 | 9.8643 | 6.5031 | 4.3724 | 3.5592
|  | CAVERSHAM | HT |  |  |  | 15.2153 | 14.8592 | 14.4694 | 14.002 | 13.4878 | 13.4837 | 12.6735 | 11.7816 | 10.852 | 9.8776 | 5.0255 | 2.0939 | 1.0653 | 18.4612 | 18.2378 | 17.9878 | 17.6806 | 17.3398 | 17.3245 | 16.8612 | 16.3337 | 15.7745 | 15.1929 | 12.3898 | 11.0194 | 10.5327 | 16.0102 | 15.6857 | 15.3367 | 14.9041 | 14.4092 | 14.3806 | 13.6082 | 12.7571 | 11.8714 | 10.9551 | 6.4092 | 3.8653 | 3.0245
|  | CAVERSHAM | HE |  |  |  | 15.2184 | 14.9 | 14.5449 | 14.1163 | 13.6459 | 13.6959 | 13.0204 | 12.2541 | 11.4551 | 10.6306 | 6.6592 | 4.2592 | 3.2878 | 18.401 | 18.1337 | 17.8286 | 17.4663 | 17.0673 | 16.9918 | 16.4796 | 15.8908 | 15.2571 | 14.5867 | 10.7561 | 7.1418 | 1.7806 | 16.0112 | 15.7204 | 15.402 | 15.0051 | 14.552 | 14.5837 | 13.9398 | 13.2143 | 12.4551 | 11.6704 | 7.8806 | 5.8173 | 5.0286
|  | CAVERSHAM | CF |  |  |  | 15.3786 | 15.1847 | 14.9673 | 14.698 | 14.4031 | 14.0765 | 14.2408 | 13.8908 | 13.5041 | 13.102 | 10.1337 | 7.3327 | 4.6439 | 18.4806 | 18.2663 | 18.0184 | 17.7214 | 17.3918 | 17.0061 | 16.9 | 16.4286 | 15.9163 | 15.3684 | 11.2316 | 4.9367 | -6.398 | 16.1571 | 15.9816 | 15.7888 | 15.5439 | 15.2561 | 14.9347 | 15.0969 | 14.7653 | 14.3929 | 14 | 11.1184 | 8.5041 | 6.0663
MANNINGTON GSP | BOURNEMOUTH | CENTRAL | MINIMUM HEADROOM | SZ 10293 91931 | YES | 3.996 | 4.3765 | 3.6582 | 1.0745 | 0.056122 | -1.1092 | -1.8184 | -3.4735 | -5.3939 | -7.2918 | -8.8816 | -14.5888 | -18.2337 | -18.3867 | 10.6408 | 9.9847 | 7.5398 | 6.6214 | 5.55 | 4.748 | 3.4031 | 1.8214 | 0.22245 | -1.1357 | -7.5337 | -16.3816 | -38.8796 | 4.7051 | 3.9908 | 1.4357 | 0.42755 | -0.72551 | -1.5265 | -3.1051 | -4.952 | -6.7765 | -8.2582 | -13.4388 | -16.5133 | -16.6163
|  | CENTRAL | EE |  |  |  | 4.3765 | 3.6582 | 1.0745 | 0.056122 | -1.1092 | -1.8184 | -3.4735 | -5.3939 | -7.2918 | -8.8816 | -14.5888 | -17.0184 | -16.7827 | 10.6408 | 9.9847 | 7.5398 | 6.6214 | 5.55 | 4.748 | 3.4031 | 1.8214 | 0.22245 | -1.1357 | -7.5337 | -13.8051 | -23.8918 | 4.7051 | 3.9908 | 1.4357 | 0.42755 | -0.72551 | -1.5265 | -3.1051 | -4.952 | -6.7765 | -8.2582 | -13.4388 | -15.4643 | -15.3888
|  | CENTRAL | HT |  |  |  | 4.8878 | 4.4 | 2.0857 | 1.4041 | 0.68571 | -0.19388 | -1.4622 | -2.6306 | -4.1735 | -5.7888 | -13.6663 | -18.2337 | -18.3867 | 11.1378 | 10.7694 | 8.6653 | 8.1541 | 7.6071 | 6.9316 | 6.0878 | 5.399 | 4.3714 | 3.2867 | -1.8571 | -4.7531 | -5.0663 | 5.2041 | 4.7194 | 2.4357 | 1.7633 | 1.048 | 0.17653 | -1.0367 | -2.0684 | -3.5133 | -5.0316 | -12.3551 | -16.5133 | -16.6163
|  | CENTRAL | HE |  |  |  | 4.8469 | 4.4092 | 2.1592 | 1.5571 | 0.92857 | 0.14796 | -0.97755 | -2.2837 | -3.2643 | -4.648 | -10.2541 | -12.6694 | -12.8204 | 11 | 10.5561 | 8.3633 | 7.7633 | 7.102 | 6.3184 | 5.3622 | 4.2367 | 3.3908 | 2.15 | -4.5571 | -11.1122 | -21.1102 | 5.1571 | 4.7122 | 2.4796 | 1.8714 | 1.2347 | 0.46531 | -0.58673 | -1.8306 | -2.6745 | -3.9704 | -9.1969 | -11.3051 | -11.3898
|  | CENTRAL | CF |  |  |  | 5.0837 | 4.8357 | 2.7388 | 2.398 | 1.9704 | 1.5255 | 1.0112 | 0.35306 | -0.34898 | -1.0898 | -4.699 | -9.3735 | -13.6071 | 11.1602 | 10.8143 | 8.699 | 8.2418 | 7.6653 | 6.9939 | 6.199 | 5.2378 | 4.2092 | 3.102 | -3.9571 | -16.3816 | -38.8796 | 5.4184 | 5.1735 | 3.1112 | 2.7776 | 2.3582 | 1.9173 | 1.4306 | 0.7949 | 0.11224 | -0.6102 | -4.249 | -8.501 | -12.1878
NURSLING GSP | SOUTHAMPTON (2 X 60) | CENTRAL BRIDGE | MINIMUM HEADROOM | SU 42591 11255 | YES | 6.813 | 23.4214 | 23.0327 | 22.601 | 21.7194 | 19.4612 | 16.7735 | 14.5378 | 12.5633 | 11.4857 | 9.3408 | 2.0092 | -5.9235 | -13.0796 | 28.6214 | 28.3439 | 27.9408 | 26.9408 | 24.7357 | 22.0867 | 20.6816 | 18.8582 | 18.0071 | 14.4071 | 5.9418 | -4.4235 | -18.9969 | 24.6837 | 24.3378 | 23.9469 | 22.898 | 20.6235 | 17.9224 | 15.7918 | 13.7684 | 12.7643 | 9.65 | 1.6969 | -7.2765 | -16.5561
|  | CENTRAL BRIDGE | EE |  |  |  | 23.4214 | 23.0327 | 22.601 | 22.0898 | 19.9235 | 18.6327 | 17.4571 | 15.7 | 13.2224 | 11.599 | 6.4347 | -3.0153 | -6.8633 | 28.6214 | 28.3439 | 28.0347 | 27.6653 | 25.6367 | 24.3592 | 23.1602 | 21.998 | 19.9031 | 18.5398 | 12.3112 | -1.3582 | -10.2214 | 24.6837 | 24.3378 | 23.9469 | 23.4806 | 21.3612 | 19.9918 | 18.7337 | 17.1878 | 14.7337 | 13.1765 | 7.6214 | -3.8582 | -8.3633
|  | CENTRAL BRIDGE | HT |  |  |  | 23.5694 | 23.2388 | 22.7286 | 22.0041 | 19.7286 | 16.7735 | 14.5378 | 12.5633 | 11.4857 | 9.5367 | 3.6031 | -5.9235 | -12.3449 | 28.7643 | 28.5898 | 28.2143 | 27.6031 | 25.5 | 22.8888 | 21.1347 | 19.4398 | 18.702 | 16.9143 | 11.0714 | 0.15 | -7.5051 | 24.8255 | 24.548 | 24.0469 | 23.2929 | 21.05 | 17.9796 | 15.7918 | 13.7684 | 12.7643 | 10.6929 | 4.1122 | -7.2765 | -15.0765
|  | CENTRAL BRIDGE | HE |  |  |  | 23.55 | 23.2378 | 22.6724 | 21.7194 | 19.4612 | 17.148 | 15.8745 | 13.898 | 12.6816 | 9.3408 | 2.0092 | -4.9612 | -13.0796 | 28.7041 | 28.4765 | 27.9408 | 26.9408 | 24.7357 | 22.0867 | 20.6816 | 18.8582 | 18.0071 | 14.4071 | 5.9418 | -4.4235 | -18.9969 | 24.8061 | 24.5388 | 23.9531 | 22.898 | 20.6235 | 17.9224 | 16.5 | 14.4622 | 13.4031 | 9.65 | 1.6969 | -6.5541 | -16.5561
|  | CENTRAL BRIDGE | CF |  |  |  | 23.9153 | 23.801 | 23.5735 | 23.3235 | 21.2612 | 20.6694 | 19.948 | 19.2378 | 17.9408 | 16.4408 | 11.1061 | 6.1194 | 1.75 | 28.9 | 28.7541 | 28.5337 | 28.2898 | 26.1918 | 25.5592 | 24.7031 | 23.8704 | 22.7102 | 21.3663 | 14.6551 | 5.0827 | -8.7898 | 25.0939 | 24.9908 | 24.7969 | 24.5786 | 22.501 | 21.898 | 21.1398 | 20.4204 | 19.2071 | 17.798 | 12.3316 | 6.7827 | 1.7735
CHICKERELL GSP | CHICKERELL BSP | CERNE ABBAS | MINIMUM HEADROOM | ST 66140 01039 | YES | 0 | 2.4163 | 2.3918 | 2.3459 | 2.3112 | 2.2582 | 2.2327 | 2.1704 | 2.1051 | 2.0316 | 2.0102 | 1.8959 | 1.85 | 1.8133 | 3.1612 | 3.1418 | 3.1092 | 3.0847 | 3.0449 | 3.0235 | 2.9816 | 2.9327 | 2.8816 | 2.851 | 2.7224 | 2.5184 | 2.102 | 2.6714 | 2.65 | 2.6133 | 2.5837 | 2.5347 | 2.5092 | 2.45 | 2.3888 | 2.3184 | 2.2969 | 2.1816 | 2.1347 | 2.1031
|  | CERNE ABBAS | EE |  |  |  | 2.4163 | 2.3918 | 2.3459 | 2.3112 | 2.2582 | 2.2327 | 2.1704 | 2.1051 | 2.0316 | 2.0102 | 1.8959 | 1.8561 | 1.8337 | 3.1612 | 3.1418 | 3.1092 | 3.0847 | 3.0449 | 3.0235 | 2.9816 | 2.9327 | 2.8816 | 2.851 | 2.7224 | 2.599 | 2.3939 | 2.6714 | 2.65 | 2.6133 | 2.5837 | 2.5347 | 2.5092 | 2.45 | 2.3888 | 2.3184 | 2.2969 | 2.1816 | 2.1439 | 2.1235
|  | CERNE ABBAS | HT |  |  |  | 2.4398 | 2.4163 | 2.3939 | 2.3755 | 2.3378 | 2.3143 | 2.2684 | 2.2173 | 2.1898 | 2.1378 | 1.9255 | 1.85 | 1.8133 | 3.1816 | 3.1622 | 3.1469 | 3.1347 | 3.1061 | 3.0898 | 3.0592 | 3.0224 | 3.0071 | 2.9704 | 2.8306 | 2.7837 | 2.7633 | 2.6806 | 2.6643 | 2.6469 | 2.6265 | 2.5939 | 2.5714 | 2.5296 | 2.4827 | 2.4571 | 2.4061 | 2.2041 | 2.1347 | 2.1031
|  | CERNE ABBAS | HE |  |  |  | 2.4398 | 2.4214 | 2.3918 | 2.3735 | 2.3378 | 2.3133 | 2.2684 | 2.2429 | 2.1918 | 2.1357 | 1.9327 | 1.8878 | 1.8755 | 3.1776 | 3.1612 | 3.1378 | 3.1224 | 3.0959 | 3.0765 | 3.0439 | 3.0194 | 2.9837 | 2.9398 | 2.751 | 2.6235 | 2.4245 | 2.6806 | 2.6663 | 2.6459 | 2.6276 | 2.5959 | 2.5735 | 2.5357 | 2.5082 | 2.4663 | 2.4173 | 2.2143 | 2.1765 | 2.1673
|  | CERNE ABBAS | CF |  |  |  | 2.4429 | 2.4276 | 2.4112 | 2.3857 | 2.3745 | 2.349 | 2.3306 | 2.2959 | 2.2571 | 2.2449 | 2.048 | 1.9561 | 1.8847 | 3.1786 | 3.1653 | 3.151 | 3.1265 | 3.1133 | 3.0898 | 3.0714 | 3.0398 | 3.0031 | 2.9857 | 2.7776 | 2.5184 | 2.102 | 2.6847 | 2.6714 | 2.6592 | 2.6367 | 2.6235 | 2.599 | 2.5857 | 2.5531 | 2.5153 | 2.502 | 2.3235 | 2.2245 | 2.1694
LOVEDEAN GSP | CHICHESTER & HUNSTON | CHALCRAFT LANE | MINIMUM HEADROOM | TBC | YES | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 0 | 0 | 0 | 0 | 0 | 0 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 0 | 0 | 0 | 0 | 0 | 0 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8
|  | CHALCRAFT LANE | EE |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 0 | 0 | 0 | 0 | 0 | 0 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 0 | 0 | 0 | 0 | 0 | 0 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8
|  | CHALCRAFT LANE | HT |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 0 | 0 | 0 | 0 | 0 | 0 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 0 | 0 | 0 | 0 | 0 | 0 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8
|  | CHALCRAFT LANE | HE |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 0 | 0 | 0 | 0 | 0 | 0 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 0 | 0 | 0 | 0 | 0 | 0 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8
|  | CHALCRAFT LANE | CF |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | 0 | 0 | 0 | 0 | 0 | 0 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 0 | 0 | 0 | 0 | 0 | 0 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 36.8
IVER 132KV | CHALVEY BSP | CHALVEY | MINIMUM HEADROOM | SU 96669 79364 | YES | 10.228 | 35.2687 | 32.1013 | 29.7452 | 27.7901 | 25.5921 | 23.0329 | 19.8309 | 16.5789 | 13.5391 | 11.0431 | 1.5687 | -5.6793 | -7.8273 | 43.0238 | 40.4289 | 38.7299 | 37.3901 | 35.8533 | 34.1003 | 31.637 | 28.9605 | 26.4676 | 24.3411 | 15.1523 | 6.7666 | -17.0793 | 35.8003 | 32.9023 | 30.7727 | 28.9962 | 26.9952 | 24.6748 | 21.5942 | 18.3615 | 15.3727 | 12.9666 | 4.2472 | -2.613 | -4.7477
|  | CHALVEY | EE |  |  |  | 35.2687 | 32.1013 | 29.7452 | 27.7901 | 25.5921 | 23.0329 | 19.8309 | 16.5789 | 13.5391 | 11.0431 | 1.5687 | -3.516 | -5.1048 | 43.0238 | 40.4289 | 38.7299 | 37.3901 | 35.8533 | 34.1003 | 31.637 | 28.9605 | 26.4676 | 24.3411 | 15.1523 | 6.7666 | -5.3069 | 35.8003 | 32.9023 | 30.7727 | 28.9962 | 26.9952 | 24.6748 | 21.5942 | 18.3615 | 15.3727 | 12.9666 | 4.2472 | -0.34665 | -2.0375
|  | CHALVEY | HT |  |  |  | 35.9064 | 32.688 | 30.5125 | 29.1319 | 27.285 | 25.1115 | 22.3799 | 19.6778 | 17.0625 | 14.3125 | 1.6911 | -5.6793 | -7.8273 | 43.6452 | 41.1401 | 39.7289 | 39.0115 | 37.9584 | 36.7299 | 34.8819 | 32.9084 | 31.0544 | 29.0584 | 20.4084 | 15.5115 | 13.6523 | 36.4738 | 33.5074 | 31.5636 | 30.4299 | 28.8115 | 26.9044 | 24.3156 | 21.6676 | 19.1319 | 16.435 | 4.3523 | -2.613 | -4.7477
|  | CHALVEY | HE |  |  |  | 35.8799 | 32.7248 | 30.6115 | 29.2993 | 27.5493 | 25.4636 | 23.086 | 20.738 | 18.5993 | 16.3656 | 6.5289 | 1.3197 | -0.69971 | 43.5074 | 40.9156 | 39.4033 | 38.5758 | 37.3931 | 36.0125 | 34.2197 | 32.2687 | 30.5401 | 28.6748 | 18.7809 | 10.0278 | -2.013 | 36.4442 | 33.534 | 31.6452 | 30.5748 | 29.0431 | 27.2248 | 25.0156 | 22.738 | 20.7187 | 18.5891 | 9.2401 | 4.4248 | 2.4084
|  | CHALVEY | CF |  |  |  | 36.8125 | 34.7768 | 33.5401 | 32.6115 | 31.8136 | 30.3033 | 28.4023 | 25.8799 | 24.585 | 23.2523 | 16.3207 | 9.0391 | 2.6493 | 43.9993 | 41.9268 | 40.8166 | 40.0238 | 39.3421 | 38.138 | 36.4921 | 34.3819 | 32.8197 | 31.2187 | 21.7084 | 7.2503 | -17.0793 | 37.2176 | 35.188 | 34.0503 | 33.2166 | 32.5962 | 31.3095 | 29.6278 | 27.3615 | 26.0636 | 24.7482 | 18.0799 | 11.5676 | 6.0258
NURSLING GSP | VELMORE BSP | CHANDLERS FORD | MINIMUM HEADROOM | SU 43494 21552 | YES | 0.382 | 14.3143 | 13.5051 | 12.8439 | 11.749 | 10.6235 | 9.2398 | 7.3255 | 5.0633 | 2.9408 | 1.1898 | -9.2276 | -14.3224 | -15.2245 | 16.8939 | 16.2582 | 15.7469 | 14.9224 | 14.0357 | 13.0571 | 11.8112 | 10.1806 | 8.6367 | 7.3847 | -0.27959 | -3.8867 | -15.5398 | 14.0704 | 13.2878 | 12.7163 | 11.7 | 10.6306 | 9.4551 | 7.6867 | 5.5296 | 3.498 | 1.8337 | -8.1204 | -12.9276 | -13.7347
|  | CHANDLERS FORD | EE |  |  |  | 14.3143 | 13.5051 | 12.8439 | 11.749 | 10.6235 | 9.2398 | 7.3255 | 5.0633 | 2.9408 | 1.1898 | -4.5571 | -7.5694 | -10.3327 | 16.8939 | 16.2582 | 15.7469 | 14.9224 | 14.0357 | 13.0571 | 11.8112 | 10.1806 | 8.6367 | 7.3847 | 3.0786 | -1.2214 | -7.5694 | 14.0704 | 13.2878 | 12.7163 | 11.7 | 10.6306 | 9.4551 | 7.6867 | 5.5296 | 3.498 | 1.8337 | -3.5602 | -5.848 | -8.2296
|  | CHANDLERS FORD | HT |  |  |  | 14.8878 | 14.3327 | 13.6408 | 12.7663 | 12.2418 | 11.3214 | 9.8408 | 8.1959 | 6.5704 | 4.8571 | -3.0449 | -7.6765 | -9.9327 | 17.4071 | 17.0531 | 16.6071 | 16.0439 | 15.7418 | 15.1357 | 14.2939 | 13.3153 | 12.3276 | 11.2878 | 6.2531 | 3.9316 | 3.3541 | 14.6398 | 14.1204 | 13.4806 | 12.6714 | 12.25 | 11.402 | 10.0878 | 8.6102 | 7.1245 | 5.551 | -1.6786 | -5.8439 | -7.7633
|  | CHANDLERS FORD | HE |  |  |  | 14.7776 | 14.1184 | 13.3327 | 12.3439 | 11.6776 | 10.4571 | 8.648 | 6.4408 | 4.1286 | 1.6939 | -9.2276 | -14.3224 | -15.2245 | 17.2551 | 16.7378 | 16.1276 | 15.3816 | 14.8592 | 14.001 | 12.8296 | 11.2143 | 9.5071 | 7.7112 | -0.27959 | -3.8867 | -9.3929 | 14.5408 | 13.9143 | 13.1857 | 12.2714 | 11.7153 | 10.6888 | 8.9643 | 6.8571 | 4.6449 | 2.3102 | -8.1204 | -12.9276 | -13.7347
|  | CHANDLERS FORD | CF |  |  |  | 15.1316 | 14.7867 | 14.3255 | 13.7143 | 13.1102 | 12.7735 | 12.0622 | 11.2184 | 10.3765 | 9.2224 | 1.4602 | -5.1653 | -8.8204 | 17.4704 | 17.1357 | 16.7082 | 16.1765 | 15.6173 | 15.2367 | 14.5357 | 13.6939 | 12.8153 | 11.8735 | 5.5378 | -2.8847 | -15.5398 | 14.8561 | 14.5194 | 14.0878 | 13.5173 | 12.9388 | 12.6908 | 12.0388 | 11.2531 | 10.4541 | 9.5 | 2.0612 | -4.2347 | -7.6469
NURSLING GSP | SOUTHAMPTON (2 X 60) | CHAPEL | MINIMUM HEADROOM | SU 42849 11983 | YES | 3.19 | 9.8208 | 9.6759 | 9.5055 | 9.2963 | 9.0647 | 8.629 | 7.981 | 7.4596 | 6.7106 | 6.2892 | 3.78 | 2.3994 | 2.0606 | 12.1692 | 11.9947 | 11.7855 | 11.5304 | 11.2284 | 10.8304 | 10.4151 | 9.7671 | 9.1814 | 8.7518 | 6.6692 | 2.8569 | -6.5533 | 10.4392 | 10.3024 | 10.1412 | 9.9178 | 9.6249 | 9.2545 | 8.779 | 7.9688 | 7.2137 | 6.781 | 4.2147 | 2.9024 | 2.5871
|  | CHAPEL | EE |  |  |  | 9.8208 | 9.6759 | 9.5055 | 9.2963 | 9.0647 | 8.7576 | 8.3831 | 7.4596 | 6.7106 | 6.2892 | 4.7739 | 4.0178 | 3.2596 | 12.1692 | 11.9947 | 11.7855 | 11.5304 | 11.2284 | 10.8304 | 10.4151 | 9.7671 | 9.1814 | 8.7518 | 7.0141 | 4.662 | 0.31816 | 10.4392 | 10.3024 | 10.1412 | 9.9178 | 9.6249 | 9.2545 | 8.8392 | 7.9688 | 7.2137 | 6.781 | 5.1882 | 4.7402 | 4.1249
|  | CHAPEL | HT |  |  |  | 9.9484 | 9.8576 | 9.7463 | 9.6106 | 9.3984 | 8.629 | 7.981 | 7.5994 | 7.231 | 6.9739 | 5.3657 | 4.0239 | 3.3157 | 12.3335 | 12.2396 | 12.112 | 11.9569 | 11.7222 | 11.3263 | 10.9314 | 10.5743 | 10.1927 | 9.8386 | 8.2182 | 7.4416 | 7.2049 | 10.5637 | 10.4841 | 10.381 | 10.2484 | 10.0433 | 9.3759 | 8.779 | 8.3851 | 7.978 | 7.6535 | 5.9269 | 4.6759 | 4.1871
|  | CHAPEL | HE |  |  |  | 9.9065 | 9.7892 | 9.6473 | 9.479 | 9.282 | 9.0127 | 8.678 | 7.9524 | 7.2412 | 6.6892 | 3.78 | 2.3994 | 2.0606 | 12.2682 | 12.1324 | 11.9671 | 11.7569 | 11.5131 | 11.1549 | 10.7753 | 10.2059 | 9.6059 | 9.0345 | 6.6692 | 4.4365 | 0.50796 | 10.5239 | 10.4147 | 10.28 | 10.1229 | 9.93 | 9.6708 | 9.3627 | 8.7249 | 7.9892 | 7.2463 | 4.2147 | 2.9024 | 2.5871
|  | CHAPEL | CF |  |  |  | 9.9902 | 9.9147 | 9.83 | 9.7351 | 9.628 | 9.5014 | 9.3586 | 9.1769 | 8.6943 | 8.1831 | 6.6453 | 4.7198 | 3.3902 | 12.3253 | 12.211 | 12.0784 | 11.9284 | 11.7518 | 11.5284 | 11.2569 | 10.9416 | 10.4386 | 9.9233 | 7.2273 | 2.8569 | -6.5533 | 10.6055 | 10.5341 | 10.4535 | 10.3637 | 10.2616 | 10.1422 | 10.0055 | 9.8331 | 9.4086 | 8.9586 | 7.0147 | 5.0892 | 3.83
COWLEY GSP | YARNTON BSP | CHARLBURY | MINIMUM HEADROOM | SP 36034 18376 | YES | 0.587 | 8.6709 | 8.5005 | 8.2577 | 8.0474 | 7.776 | 7.4189 | 7.3679 | 6.9505 | 6.5321 | 6.2526 | 4.7148 | 3.4128 | 2.6097 | 9.9265 | 9.7847 | 9.5827 | 9.4041 | 9.1704 | 8.8888 | 8.9449 | 8.6429 | 8.3337 | 8.15 | 7.0561 | 5.6296 | 2.1929 | 8.6306 | 8.4633 | 8.2143 | 8.0031 | 7.7194 | 7.3684 | 7.4133 | 7.0153 | 6.6184 | 6.3776 | 5.049 | 3.9184 | 3.249
|  | CHARLBURY | EE |  |  |  | 8.6709 | 8.5005 | 8.2577 | 8.0474 | 7.776 | 7.4189 | 7.3679 | 6.9505 | 6.5321 | 6.2526 | 4.7495 | 3.6403 | 2.775 | 9.9265 | 9.7847 | 9.5827 | 9.4041 | 9.1704 | 8.8888 | 8.9449 | 8.6429 | 8.3337 | 8.15 | 7.0561 | 5.8541 | 4.0102 | 8.6306 | 8.4633 | 8.2143 | 8.0031 | 7.7194 | 7.3684 | 7.4133 | 7.0153 | 6.6184 | 6.3776 | 5.0673 | 4.1224 | 3.3888
|  | CHARLBURY | HT |  |  |  | 8.773 | 8.6332 | 8.4546 | 8.3066 | 8.1087 | 7.8689 | 7.5005 | 7.0934 | 6.6648 | 6.6179 | 4.7148 | 3.4128 | 2.6097 | 10.0408 | 9.9571 | 9.8255 | 9.7214 | 9.5765 | 9.4327 | 9.2122 | 8.9582 | 8.6816 | 8.8061 | 7.7939 | 7.2122 | 6.8724 | 8.75 | 8.6224 | 8.449 | 8.301 | 8.101 | 7.8847 | 7.5388 | 7.1531 | 6.7459 | 6.7724 | 5.049 | 3.9184 | 3.249
|  | CHARLBURY | HE |  |  |  | 8.773 | 8.6413 | 8.4719 | 8.3342 | 8.1464 | 7.923 | 7.6138 | 7.2628 | 6.8923 | 6.9219 | 5.2526 | 4.1628 | 3.5964 | 10.0255 | 9.9245 | 9.7806 | 9.6633 | 9.5031 | 9.3429 | 9.1163 | 8.852 | 8.5622 | 8.6541 | 7.3265 | 6.1071 | 4.3908 | 8.748 | 8.6296 | 8.4602 | 8.3245 | 8.1357 | 7.9306 | 7.6357 | 7.2959 | 6.9337 | 7.0347 | 5.5204 | 4.5959 | 4.1255
|  | CHARLBURY | CF |  |  |  | 8.8311 | 8.7434 | 8.6393 | 8.5515 | 8.4219 | 8.2311 | 8.1148 | 7.9372 | 7.7454 | 7.5454 | 6.7495 | 5.6444 | 4.5607 | 10.0571 | 9.9714 | 9.8622 | 9.7704 | 9.6388 | 9.4643 | 9.3306 | 9.1286 | 8.9143 | 8.6816 | 7.6153 | 5.6296 | 2.1929 | 8.8031 | 8.7163 | 8.6092 | 8.5194 | 8.3867 | 8.201 | 8.0867 | 7.901 | 7.701 | 7.4908 | 6.8184 | 5.8469 | 4.9398
CHICKERELL GSP | CHICKERELL BSP | CHARMINSTER | MINIMUM HEADROOM | SY 67309 93186 | YES | 4.287 | 4.0538 | 3.5987 | 3.0079 | 2.564 | 2.0436 | 1.5701 | 1.4405 | 0.53849 | -0.61253 | -1.6207 | -6.4697 | -11.0564 | -14.8799 | 5.5308 | 5.2349 | 4.8635 | 4.5747 | 4.2135 | 3.8584 | 3.8635 | 3.2655 | 2.6033 | 2.0492 | -0.79977 | -3.6161 | -9.0539 | 4.4064 | 3.9951 | 3.4594 | 3.0594 | 2.5635 | 2.1012 | 2.0482 | 1.2288 | 0.23492 | -0.59467 | -4.6304 | -8.3804 | -11.4283
|  | CHARMINSTER | EE |  |  |  | 4.0538 | 3.5987 | 3.0079 | 2.564 | 2.0436 | 1.5701 | 1.4405 | 0.53849 | -0.61253 | -1.6207 | -6.4697 | -10.8207 | -14.6789 | 5.5308 | 5.2349 | 4.8635 | 4.5747 | 4.2135 | 3.8584 | 3.8635 | 3.2655 | 2.6033 | 2.0492 | -0.79977 | -3.6161 | -7.113 | 4.4064 | 3.9951 | 3.4594 | 3.0594 | 2.5635 | 2.1012 | 2.0482 | 1.2288 | 0.23492 | -0.59467 | -4.6304 | -8.1488 | -11.2498
|  | CHARMINSTER | HT |  |  |  | 4.1967 | 3.7844 | 3.2946 | 2.8905 | 2.463 | 2.1365 | 1.6916 | 0.81298 | -0.31967 | -1.086 | -6.4421 | -11.0564 | -14.8799 | 5.6676 | 5.4278 | 5.1706 | 4.9482 | 4.7074 | 4.5206 | 4.2492 | 3.7268 | 3.141 | 2.8533 | 0.10329 | -2.0651 | -3.7661 | 4.5543 | 4.1951 | 3.7798 | 3.4155 | 3.0237 | 2.7247 | 2.3053 | 1.5247 | 0.55023 | 0.006351 | -4.5845 | -8.3804 | -11.4283
|  | CHARMINSTER | HE |  |  |  | 4.1905 | 3.7905 | 3.312 | 2.9211 | 2.5079 | 2.2018 | 1.8089 | 0.99053 | -0.084976 | -0.78702 | -5.8768 | -10.1707 | -13.5544 | 5.6431 | 5.39 | 5.1155 | 4.8747 | 4.6196 | 4.4145 | 4.1461 | 3.6125 | 2.9992 | 2.6829 | -0.37018 | -3.2243 | -6.5406 | 4.5492 | 4.2002 | 3.7961 | 3.4421 | 3.0686 | 2.788 | 2.4166 | 1.6859 | 0.75941 | 0.28084 | -4.0273 | -7.5151 | -10.1957
|  | CHARMINSTER | CF |  |  |  | 4.2752 | 3.9405 | 3.5334 | 3.2681 | 2.963 | 2.7232 | 2.5671 | 1.9875 | 1.1854 | 0.36196 | -3.4646 | -7.7819 | -12.2238 | 5.689 | 5.4604 | 5.2084 | 5.0349 | 4.8217 | 4.6268 | 4.4594 | 4.0104 | 3.5002 | 2.9655 | 0.23186 | -3.559 | -9.0539 | 4.6288 | 4.339 | 3.989 | 3.7543 | 3.4717 | 3.2349 | 3.091 | 2.5727 | 1.8839 | 1.1808 | -1.9079 | -5.5028 | -9.1141
LOVEDEAN GSP | CHICHESTER & HUNSTON | CHICHESTER | MINIMUM HEADROOM | SU 92198 07420 | YES | 10.737 | 0.54749 | -0.6821 | -1.8045 | 14.1176 | 13.1564 | 8.4765 | 7.1683 | 5.6786 | 4.1877 | 3.1571 | -1.7847 | -5.3296 | -7.4643 | -3.4522 | -3.9961 | -4.491 | 12.8411 | 12.3737 | 8.2643 | 7.6428 | 6.8979 | 6.1255 | 5.4898 | 2.2459 | -1.0939 | -9.851 | -3.0928 | -4.1836 | -5.2163 | -5.5877 | 10.4584 | 5.8663 | 4.6592 | 3.2765 | 1.8928 | 0.96222 | -3.3919 | -6.5388 | -8.3939
|  | CHICHESTER | EE |  |  |  | 0.54749 | -0.6821 | -1.8045 | 14.1176 | 13.1564 | 8.4765 | 7.1683 | 5.6786 | 4.1877 | 3.1571 | -1.5786 | -4.6051 | -6.9592 | -3.4522 | -3.9961 | -4.491 | 12.8411 | 12.3737 | 8.2643 | 7.6428 | 6.8979 | 6.1255 | 5.4898 | 2.2755 | -0.93165 | -5.5786 | -3.0928 | -4.1836 | -5.2163 | -5.5877 | 10.4584 | 5.8663 | 4.6592 | 3.2765 | 1.8928 | 0.96222 | -3.2572 | -5.9082 | -7.9663
|  | CHICHESTER | HT |  |  |  | 0.88831 | -0.24128 | -1.1352 | 14.3758 | 13.4686 | 9.3939 | 8.253 | 6.9847 | 5.6622 | 4.3561 | -1.7847 | -5.3296 | -7.4643 | -3.2685 | -3.7359 | -4.1093 | 13.1656 | 12.787 | 8.9275 | 8.4337 | 7.8459 | 7.202 | 6.5745 | 3.5428 | 1.749 | 0.71835 | -2.752 | -3.7418 | -4.5408 | -5.3234 | 10.7839 | 6.7949 | 5.7602 | 4.602 | 3.3949 | 2.2 | -3.3919 | -6.5388 | -8.3939
|  | CHICHESTER | HE |  |  |  | 0.87811 | -0.23516 | -1.1107 | 14.4145 | 13.5268 | 9.4673 | 8.4561 | 7.2969 | 6.0959 | 4.9112 | -0.6439 | -3.8245 | -5.4143 | -3.3134 | -3.8155 | -4.2308 | 12.9962 | 12.5564 | 8.6296 | 8.1 | 7.4643 | 6.7622 | 6.0541 | 2.2459 | -1.0939 | -5.4429 | -2.7632 | -3.7377 | -4.5265 | -5.2928 | 10.8268 | 6.849 | 5.9296 | 4.8663 | 3.7622 | 2.6704 | -2.4123 | -5.451 | -7.0561
|  | CHICHESTER | CF |  |  |  | 1.1148 | 0.14647 | -0.5821 | 15.2441 | 14.7064 | 10.4847 | 10.3571 | 9.651 | 8.8979 | 8.1418 | 4.0112 | 0.51018 | -2.7255 | -3.1236 | -3.6308 | -3.9736 | 13.3788 | 13.0931 | 9.1673 | 8.9449 | 8.5081 | 8.0418 | 7.553 | 4.3734 | -1.0459 | -9.851 | -2.5449 | -3.3877 | -4.0438 | -4.5316 | 11.9084 | 7.7377 | 7.6581 | 7.0081 | 6.3214 | 5.6265 | 1.7928 | -1.3919 | -4.2623
CHICKERELL GSP | CHICKERELL BSP | CHICKERELL | MINIMUM HEADROOM | SY 65479 80511 | YES | 0.632 | 30.5882 | 30.4239 | 30.1831 | 29.9453 | 29.6382 | 29.2453 | 28.8453 | 28.2667 | 27.729 | 27.1841 | 24.6565 | 23.2739 | 22.5718 | 30.2724 | 30.149 | 29.9663 | 29.7898 | 29.5541 | 29.2031 | 28.9959 | 28.5694 | 28.1633 | 27.8 | 26.152 | 24.7776 | 21.2204 | 30.5586 | 30.3647 | 30.0708 | 29.78 | 29.3851 | 28.8973 | 28.4953 | 27.9116 | 27.3698 | 26.8545 | 24.6341 | 23.4208 | 22.8188
|  | CHICKERELL | EE |  |  |  | 30.5882 | 30.4239 | 30.1831 | 29.9453 | 29.6382 | 29.2453 | 28.8453 | 28.2667 | 27.729 | 27.1841 | 24.7259 | 23.4984 | 22.7555 | 30.2724 | 30.149 | 29.9663 | 29.7898 | 29.5541 | 29.2031 | 28.9959 | 28.5694 | 28.1633 | 27.8 | 26.152 | 24.8551 | 23.0908 | 30.5586 | 30.3647 | 30.0708 | 29.78 | 29.3851 | 28.8973 | 28.4953 | 27.9116 | 27.3698 | 26.8545 | 24.6831 | 23.6014 | 22.981
|  | CHICKERELL | HT |  |  |  | 30.678 | 30.5422 | 30.3402 | 30.1433 | 29.8861 | 29.481 | 28.9484 | 28.3882 | 27.8504 | 27.3831 | 24.6565 | 23.2739 | 22.5718 | 30.3418 | 30.2449 | 30.1 | 29.9633 | 29.7745 | 29.5612 | 29.2633 | 28.8939 | 28.5357 | 28.3755 | 26.9061 | 26.249 | 25.9235 | 30.6331 | 30.4504 | 30.1861 | 29.9198 | 29.5616 | 29.1341 | 28.5912 | 28.0229 | 27.479 | 27.079 | 24.6341 | 23.4208 | 22.8188
|  | CHICKERELL | HE |  |  |  | 30.6667 | 30.531 | 30.3249 | 30.1229 | 29.8555 | 29.5045 | 29.0147 | 28.4871 | 27.982 | 27.6116 | 25.0831 | 23.7627 | 23.1627 | 30.3316 | 30.2276 | 30.0684 | 29.9173 | 29.7102 | 29.4816 | 29.1398 | 28.75 | 28.3633 | 28.1724 | 26.3633 | 25.0071 | 23.3061 | 30.6249 | 30.4637 | 30.2035 | 29.9443 | 29.5912 | 29.1688 | 28.6749 | 28.1484 | 27.6422 | 27.281 | 25.0157 | 23.8443 | 23.3198
|  | CHICKERELL | CF |  |  |  | 30.7412 | 30.6433 | 30.4963 | 30.3565 | 30.1637 | 29.93 | 29.679 | 29.3688 | 29.0555 | 28.6984 | 27.2004 | 25.7351 | 24.3147 | 30.3745 | 30.2969 | 30.1755 | 30.0622 | 29.901 | 29.7041 | 29.4551 | 29.1745 | 28.8765 | 28.5398 | 26.9704 | 24.7776 | 21.2204 | 30.6831 | 30.6014 | 30.4208 | 30.2433 | 29.9922 | 29.6708 | 29.3739 | 29.0759 | 28.7729 | 28.4269 | 26.9371 | 25.5953 | 24.3249
AXMINSTER | YEOVIL BSP | CHILTON CANTELO | MINIMUM HEADROOM | ST 57910 21616 | YES | 0.363 | 10.1194 | 9.7857 | 9.4214 | 8.7786 | 7.9827 | 7.0408 | 6.2551 | 5.5429 | 5.2041 | 4.6694 | 2.5214 | 1.3398 | 0.91224 | 11.8286 | 11.548 | 11.2276 | 10.8582 | 10.4408 | 9.9459 | 9.5092 | 9.0939 | 8.8622 | 8.4847 | 6.6714 | 5.8235 | 4.1571 | 10.7388 | 10.4051 | 9.949 | 9.3888 | 8.7306 | 7.952 | 7.3235 | 6.752 | 6.3867 | 5.9255 | 3.6714 | 2.5592 | 2.1582
|  | CHILTON CANTELO | EE |  |  |  | 10.1194 | 9.7857 | 9.4214 | 8.7786 | 7.9827 | 7.0408 | 6.2551 | 5.5429 | 5.2041 | 4.6694 | 3.2633 | 2.7357 | 2.4255 | 11.8286 | 11.548 | 11.2276 | 10.8582 | 10.4408 | 9.9459 | 9.5092 | 9.0939 | 8.8622 | 8.4847 | 7.4694 | 6.8429 | 5.7918 | 10.7388 | 10.4051 | 9.949 | 9.3888 | 8.7306 | 7.952 | 7.3235 | 6.752 | 6.3867 | 5.9255 | 4.5429 | 4.1551 | 3.9092
|  | CHILTON CANTELO | HT |  |  |  | 10.252 | 9.9786 | 9.6673 | 9.0867 | 8.3694 | 7.4827 | 6.7786 | 6.2204 | 5.6112 | 4.998 | 3.5806 | 2.7622 | 2.3184 | 11.9276 | 11.699 | 11.4245 | 11.1153 | 10.7561 | 10.3327 | 9.9745 | 9.6806 | 9.3561 | 9.0235 | 7.8949 | 7.3143 | 7.1071 | 10.9204 | 10.5694 | 10.1388 | 9.6337 | 9.0316 | 8.3092 | 7.7459 | 7.2816 | 6.7827 | 6.2796 | 4.9347 | 4.1316 | 3.7224
|  | CHILTON CANTELO | HE |  |  |  | 10.2163 | 9.9173 | 9.5786 | 9.0194 | 8.2806 | 7.3704 | 6.649 | 6.0592 | 5.4173 | 4.7653 | 2.5214 | 1.3398 | 0.91224 | 11.9031 | 11.648 | 11.349 | 11.0122 | 10.6194 | 10.1551 | 9.7561 | 9.4102 | 9.0235 | 8.6102 | 6.6714 | 5.8235 | 5.3276 | 10.8776 | 10.5327 | 10.0847 | 9.5592 | 8.9316 | 8.1816 | 7.5929 | 7.0908 | 6.551 | 6.002 | 3.6714 | 2.5592 | 2.1582
|  | CHILTON CANTELO | CF |  |  |  | 10.3602 | 10.1939 | 9.9806 | 9.7378 | 9.2245 | 8.5469 | 7.9163 | 7.3673 | 6.8459 | 6.2827 | 4.8837 | 3.2245 | 1.9214 | 11.9908 | 11.8357 | 11.6347 | 11.4061 | 11.0939 | 10.7255 | 10.3653 | 10.0378 | 9.7143 | 9.3653 | 8.1194 | 6.5082 | 4.1571 | 11.0265 | 10.8112 | 10.5316 | 10.2 | 9.7469 | 9.1857 | 8.698 | 8.2633 | 7.8378 | 7.3816 | 6.0806 | 4.3255 | 3.1082
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | CHINEHAM | MINIMUM HEADROOM | SU 65105 55805 | YES | 7.496 | 14.5986 | 14.3251 | 13.9128 | 13.3333 | 12.5404 | 11.9782 | 10.4894 | 8.822 | 7.4128 | 6.0169 | 1.6098 | -0.82082 | -2.2065 | 16.768 | 16.5251 | 16.1639 | 15.7282 | 15.1914 | 14.9322 | 14.3098 | 13.4118 | 12.3965 | 11.621 | 8.5424 | 6.4435 | 0.12918 | 14.8751 | 14.621 | 14.218 | 13.6659 | 12.9414 | 12.5037 | 11.3047 | 9.8669 | 8.6649 | 7.422 | 3.3782 | 1.2118 | 0.017951
|  | CHINEHAM | EE |  |  |  | 14.5986 | 14.3251 | 13.9128 | 13.3333 | 12.5404 | 11.9782 | 11.0231 | 9.5506 | 7.8424 | 6.4894 | 1.7598 | -0.37593 | -2.0045 | 16.768 | 16.5251 | 16.1639 | 15.7282 | 15.1914 | 14.9322 | 14.3098 | 13.4118 | 12.3965 | 11.621 | 8.5424 | 6.4435 | 3.2598 | 14.8751 | 14.621 | 14.218 | 13.6659 | 12.9414 | 12.5037 | 11.6231 | 10.3159 | 8.8159 | 7.6506 | 3.4771 | 1.5955 | 0.18326
|  | CHINEHAM | HT |  |  |  | 14.7986 | 14.5751 | 14.1343 | 13.6098 | 12.9261 | 12.0771 | 10.4894 | 8.822 | 7.4128 | 6.0169 | 1.6098 | -0.82082 | -2.2065 | 16.9598 | 16.7792 | 16.5231 | 16.2128 | 15.8455 | 15.3333 | 14.5251 | 13.6414 | 13.0373 | 12.2639 | 9.8465 | 8.7312 | 8.1761 | 15.0067 | 14.7741 | 14.4159 | 13.9822 | 13.4118 | 12.6547 | 11.3047 | 9.8669 | 8.6649 | 7.422 | 3.3782 | 1.2118 | 0.017951
|  | CHINEHAM | HE |  |  |  | 14.77 | 14.5424 | 14.1618 | 13.6506 | 12.9792 | 12.2353 | 11.3884 | 10.219 | 9.2271 | 8.219 | 3.4782 | 0.33734 | -0.75756 | 16.921 | 16.719 | 16.4292 | 16.0812 | 15.6833 | 15.219 | 14.671 | 13.9353 | 13.4598 | 12.7771 | 9.3669 | 6.7098 | 3.7333 | 15.0026 | 14.7812 | 14.4333 | 14.0108 | 13.4547 | 12.8169 | 12.0577 | 11.0312 | 10.1863 | 9.2649 | 4.9006 | 2.2098 | 1.271
|  | CHINEHAM | CF |  |  |  | 14.9251 | 14.8159 | 14.6526 | 14.468 | 14.1343 | 13.5139 | 12.8955 | 12.2843 | 11.6282 | 11.1373 | 7.7057 | 4.0802 | 1.2557 | 16.9761 | 16.8465 | 16.6445 | 16.4567 | 16.1792 | 15.7741 | 15.321 | 14.821 | 14.269 | 13.768 | 10.6231 | 6.4465 | 0.12918 | 15.1098 | 15.0149 | 14.8547 | 14.6924 | 14.42 | 13.9292 | 13.4128 | 12.8567 | 12.2486 | 11.7486 | 8.5026 | 5.4669 | 3.0292
COWLEY GSP | YARNTON BSP | CHIPPING NORTON | MINIMUM HEADROOM | SP 31382 26792 | YES | 1.489 | 3.7577 | 3.5485 | 3.2352 | 2.924 | 2.5862 | 1.9536 | 1.2158 | 0.42092 | -0.55663 | -1.523 | -4.1801 | -5.7607 | -6.7648 | 6.0153 | 5.848 | 5.6051 | 5.3694 | 5.0929 | 4.6061 | 4.1061 | 3.8602 | 3.2357 | 2.7194 | 0.92245 | -0.62551 | -4.6592 | 3.75 | 3.5327 | 3.2204 | 2.9204 | 2.5561 | 1.9561 | 1.2673 | 0.85816 | 0.02551 | -0.80306 | -3.1306 | -4.498 | -5.3245
|  | CHIPPING NORTON | EE |  |  |  | 3.7577 | 3.5485 | 3.2352 | 2.924 | 2.5862 | 1.9536 | 1.2158 | 0.64031 | -0.40867 | -1.3617 | -4.1801 | -5.5393 | -6.5679 | 6.0153 | 5.848 | 5.6051 | 5.3694 | 5.0929 | 4.6061 | 4.1061 | 3.8602 | 3.2357 | 2.7194 | 0.92245 | -0.51837 | -2.6653 | 3.75 | 3.5327 | 3.2204 | 2.9204 | 2.5561 | 1.9561 | 1.2673 | 0.93163 | 0.028571 | -0.75714 | -3.1306 | -4.2857 | -5.1541
|  | CHIPPING NORTON | HT |  |  |  | 3.8495 | 3.6617 | 3.4117 | 3.1577 | 2.6403 | 2.1342 | 1.3832 | 0.42092 | -0.55663 | -1.523 | -4.1362 | -5.7607 | -6.7648 | 6.1388 | 6.0153 | 5.8571 | 5.7031 | 5.3429 | 5.0327 | 4.6327 | 4.1214 | 3.6 | 3.0776 | 1.8357 | 1.0755 | 0.66224 | 3.8735 | 3.701 | 3.4673 | 3.2337 | 2.7694 | 2.3296 | 1.6806 | 0.85816 | 0.02551 | -0.80306 | -3.0806 | -4.498 | -5.3245
|  | CHIPPING NORTON | HE |  |  |  | 3.8474 | 3.6679 | 3.423 | 3.177 | 2.9189 | 2.3709 | 1.7934 | 0.96888 | -0.029082 | -1.0199 | -3.5944 | -4.9168 | -5.5556 | 6.1163 | 5.9857 | 5.8061 | 5.6357 | 5.4347 | 5.0357 | 4.6847 | 4.1867 | 3.6061 | 3.0163 | 1.3224 | -0.13776 | -2.1112 | 3.8704 | 3.7082 | 3.4816 | 3.2592 | 3.0092 | 2.5276 | 2.0296 | 1.3204 | 0.47653 | -0.36837 | -2.5592 | -3.6847 | -4.2082
|  | CHIPPING NORTON | CF |  |  |  | 3.9179 | 3.7944 | 3.6168 | 3.4179 | 3.2995 | 3.1454 | 2.8913 | 2.6087 | 2.2495 | 1.8383 | -1.4801 | -2.926 | -4.3464 | 6.1582 | 6.05 | 5.902 | 5.7357 | 5.6173 | 5.448 | 5.1867 | 4.9143 | 4.5857 | 4.2194 | 1.7847 | -0.62551 | -4.6592 | 3.9378 | 3.8235 | 3.6531 | 3.4592 | 3.3439 | 3.1837 | 2.9398 | 2.6806 | 2.3357 | 1.949 | -0.7 | -1.9918 | -3.2245
COWLEY GSP | HIGH WYCOMBE BSP | CHISBRIDGE | MINIMUM HEADROOM | SU 80226 89155 | YES | 0.713 | 3.3316 | 3.2959 | 3.2602 | 3.2041 | 3.1296 | 3.0612 | 2.9633 | 2.8469 | 2.7398 | 2.649 | 2.1867 | 1.9796 | 1.8306 | 4.8791 | 4.8219 | 4.7628 | 4.6923 | 4.6046 | 4.5464 | 4.4352 | 4.3066 | 4.224 | 4.1587 | 3.7954 | 3.4015 | 2.473 | 4.0061 | 3.9316 | 3.8582 | 3.7653 | 3.6561 | 3.5806 | 3.4378 | 3.2724 | 3.152 | 3.0582 | 2.598 | 2.4153 | 2.2816
|  | CHISBRIDGE | EE |  |  |  | 3.3316 | 3.2959 | 3.2602 | 3.2041 | 3.1296 | 3.0612 | 2.9633 | 2.8469 | 2.7398 | 2.649 | 2.1867 | 1.9867 | 1.8918 | 4.8791 | 4.8219 | 4.7628 | 4.6923 | 4.6046 | 4.5464 | 4.4352 | 4.3066 | 4.224 | 4.1587 | 3.7954 | 3.4913 | 3.0495 | 4.0061 | 3.9316 | 3.8582 | 3.7653 | 3.6561 | 3.5806 | 3.4378 | 3.2724 | 3.152 | 3.0582 | 2.598 | 2.4204 | 2.3347
|  | CHISBRIDGE | HT |  |  |  | 3.351 | 3.3255 | 3.2918 | 3.2541 | 3.2102 | 3.1449 | 3.0622 | 2.9724 | 2.8684 | 2.7602 | 2.252 | 1.9796 | 1.8306 | 4.9209 | 4.8842 | 4.8413 | 4.7832 | 4.7485 | 4.6913 | 4.6117 | 4.5505 | 4.4597 | 4.3607 | 4.0117 | 3.877 | 3.8046 | 4.051 | 3.9939 | 3.9276 | 3.852 | 3.7908 | 3.7092 | 3.5939 | 3.4949 | 3.3602 | 3.2204 | 2.6582 | 2.4153 | 2.2816
|  | CHISBRIDGE | HE |  |  |  | 3.3531 | 3.3255 | 3.2939 | 3.2571 | 3.2071 | 3.1429 | 3.0592 | 2.9704 | 2.8633 | 2.7541 | 2.2378 | 2.0776 | 2.0051 | 4.9179 | 4.8791 | 4.8281 | 4.7699 | 4.7301 | 4.6699 | 4.5893 | 4.5281 | 4.4311 | 4.327 | 3.8587 | 3.5515 | 3.1219 | 4.052 | 3.9959 | 3.9306 | 3.8561 | 3.799 | 3.7235 | 3.6122 | 3.5245 | 3.3969 | 3.2663 | 2.6847 | 2.5153 | 2.449
|  | CHISBRIDGE | CF |  |  |  | 3.3673 | 3.348 | 3.3265 | 3.302 | 3.2765 | 3.2531 | 3.2204 | 3.1622 | 3.099 | 3.0449 | 2.6592 | 2.3184 | 2.0633 | 4.9301 | 4.8964 | 4.8597 | 4.8128 | 4.7587 | 4.7281 | 4.674 | 4.6015 | 4.524 | 4.476 | 3.9995 | 3.4015 | 2.473 | 4.0694 | 4.0276 | 3.9796 | 3.9204 | 3.8602 | 3.8194 | 3.7602 | 3.6786 | 3.5949 | 3.5449 | 3.1092 | 2.7745 | 2.5235
MINETY GSP | TOOTHILL BSP | CHISLEDON | MINIMUM HEADROOM | SU 18894 79934 | YES | 0.468 | 10.0505 | 9.5515 | 8.6893 | 7.3362 | 5.4862 | 3.0352 | 0.2852 | -2.3801 | -4.8403 | -6.9046 | -12.1138 | -14.0342 | -15.3332 | 9.1041 | 8.8184 | 8.3745 | 7.6918 | 6.7347 | 5.3337 | 3.449 | 1.5622 | -0.073469 | -1.4541 | -5.1061 | -6.8184 | -8.3122 | 9.4051 | 9.0429 | 8.3592 | 7.2786 | 5.7633 | 3.6939 | 1.2173 | -1.2184 | -3.4163 | -5.2878 | -10.1908 | -12.2469 | -13.648
|  | CHISLEDON | EE |  |  |  | 10.0505 | 9.5515 | 8.6893 | 7.3362 | 5.6923 | 3.474 | 0.88112 | -1.8781 | -4.4709 | -6.6893 | -11.5342 | -12.9148 | -14.224 | 9.1041 | 8.8184 | 8.3745 | 7.6918 | 6.8806 | 5.6673 | 3.9143 | 1.9286 | 0.1551 | -1.4082 | -4.8653 | -6.3592 | -8.3122 | 9.4051 | 9.0429 | 8.3592 | 7.2786 | 5.949 | 4.0969 | 1.7694 | -0.75918 | -3.0806 | -5.0949 | -9.5061 | -10.9184 | -12.3224
|  | CHISLEDON | HT |  |  |  | 10.1046 | 9.625 | 8.7811 | 7.4587 | 5.4862 | 3.0352 | 0.2852 | -2.3801 | -4.8403 | -6.9046 | -12.1138 | -14.0342 | -15.3332 | 9.1643 | 8.9061 | 8.4878 | 7.8398 | 6.7347 | 5.3337 | 3.449 | 1.5622 | -0.073469 | -1.4541 | -5.1061 | -6.8184 | -8.0408 | 9.4908 | 9.1153 | 8.452 | 7.4031 | 5.7633 | 3.6939 | 1.2173 | -1.2184 | -3.4163 | -5.2878 | -10.1908 | -12.2469 | -13.648
|  | CHISLEDON | HE |  |  |  | 10.1087 | 9.6413 | 8.8046 | 7.4883 | 5.9158 | 3.7077 | 1.326 | -1.1832 | -3.4781 | -5.4964 | -10.3781 | -11.8321 | -13.0352 | 9.1592 | 8.901 | 8.4633 | 7.799 | 7.0378 | 5.8357 | 4.3 | 2.5551 | 1.099 | -0.20102 | -3.6612 | -5.2378 | -7.1786 | 9.4939 | 9.1306 | 8.4724 | 7.4296 | 6.1673 | 4.3265 | 2.2408 | -0.0091837 | -1.9816 | -3.7367 | -8.1602 | -9.6459 | -10.9643
|  | CHISLEDON | CF |  |  |  | 10.1628 | 9.7546 | 9.025 | 7.8883 | 6.5117 | 4.9495 | 3.1026 | 1.076 | -1.0577 | -2.8607 | -7.9903 | -9.0566 | -10.2852 | 9.1878 | 8.951 | 8.5643 | 7.9714 | 7.2796 | 6.5122 | 5.3592 | 3.9724 | 2.5092 | 1.2918 | -2.3429 | -3.6265 | -5.7592 | 9.5429 | 9.2327 | 8.6724 | 7.7867 | 6.698 | 5.4531 | 3.8857 | 2.1 | 0.23061 | -1.3327 | -5.8316 | -6.7827 | -7.8765
BRAMLEY (FLEE) | BRACKNELL | CHOBHAM | MINIMUM HEADROOM | SU 97173 63223 | YES | 3.467 | 11.8963 | 11.279 | 10.6382 | 9.9514 | 7.9902 | 7.7239 | 7.2178 | 6.6167 | 6.0545 | 5.6933 | 3.6698 | 1.982 | 1.1167 | 14.0835 | 13.6865 | 13.2835 | 12.8355 | 11.1498 | 11.0345 | 10.662 | 10.2182 | 9.7784 | 9.5008 | 7.9131 | 5.3865 | -0.082857 | 12.279 | 11.7331 | 11.1708 | 10.5494 | 8.6576 | 8.5524 | 8.078 | 7.5127 | 6.9749 | 6.6657 | 4.9269 | 3.3484 | 2.5382
|  | CHOBHAM | EE |  |  |  | 11.8963 | 11.279 | 10.6382 | 9.9514 | 7.9902 | 7.7239 | 7.2178 | 6.6167 | 6.0545 | 5.6933 | 3.8484 | 2.3535 | 1.3178 | 14.0835 | 13.6865 | 13.2835 | 12.8355 | 11.1498 | 11.0345 | 10.662 | 10.2182 | 9.7784 | 9.5008 | 7.9131 | 6.0529 | 3.2416 | 12.279 | 11.7331 | 11.1708 | 10.5494 | 8.6576 | 8.5524 | 8.078 | 7.5127 | 6.9749 | 6.6657 | 5.0882 | 3.6851 | 2.7208
|  | CHOBHAM | HT |  |  |  | 12.0402 | 11.4729 | 10.8984 | 10.2749 | 8.4422 | 7.8096 | 7.2902 | 7.1086 | 6.6188 | 6.1127 | 3.6698 | 1.982 | 1.1167 | 14.2273 | 13.909 | 13.5988 | 13.2539 | 11.7182 | 11.3631 | 11.0529 | 11.0273 | 10.7314 | 10.4202 | 9.0437 | 8.2876 | 7.9222 | 12.4147 | 11.9565 | 11.4729 | 10.9331 | 9.1984 | 8.6402 | 8.1524 | 8.0198 | 7.5831 | 7.132 | 4.9269 | 3.3484 | 2.5382
|  | CHOBHAM | HE |  |  |  | 12.0392 | 11.4922 | 10.932 | 10.3412 | 8.5443 | 7.932 | 7.5096 | 7.4127 | 7.0014 | 6.5769 | 4.4524 | 2.8831 | 2.1851 | 14.1967 | 13.8539 | 13.5131 | 13.1427 | 11.5876 | 11.1947 | 10.8651 | 10.8049 | 10.4671 | 10.1151 | 8.1447 | 6.2059 | 3.5314 | 12.4178 | 11.9718 | 11.4973 | 10.9841 | 9.2759 | 8.7371 | 8.3259 | 8.2963 | 7.9361 | 7.5647 | 5.6341 | 4.1627 | 3.5055
|  | CHOBHAM | CF |  |  |  | 12.1422 | 11.6922 | 11.2392 | 10.7953 | 9.1596 | 8.7371 | 8.5565 | 8.3065 | 8.4147 | 8.1851 | 6.5616 | 4.9535 | 3.478 | 14.2437 | 13.9457 | 13.6478 | 13.3416 | 11.8467 | 11.5284 | 11.2896 | 10.9886 | 10.9712 | 10.6753 | 8.5631 | 5.3865 | -0.082857 | 12.5147 | 12.1463 | 11.7627 | 11.3739 | 9.8076 | 9.431 | 9.2351 | 8.9718 | 9.1535 | 8.9249 | 7.3933 | 6.028 | 4.7178
COWLEY GSP | DRAYTON BSP | CHOLSEY | MINIMUM HEADROOM | SU 58223 84685 | YES | 0.514 | 13.0694 | 12.85 | 12.6255 | 12.2663 | 11.9714 | 10.9827 | 10.3898 | 9.7071 | 7.802 | 6.3816 | 3.1959 | -0.49388 | -4.6173 | 14.8418 | 14.6867 | 14.499 | 14.0847 | 13.801 | 12.6531 | 12.05 | 11.3459 | 9.1204 | 7.5204 | 4.1888 | -0.32857 | -6.4592 | 13.9459 | 13.7408 | 13.5031 | 13.1 | 12.7776 | 11.5898 | 10.9398 | 10.1673 | 7.8786 | 6.2102 | 2.7327 | -1.5367 | -6.5194
|  | CHOLSEY | EE |  |  |  | 13.0694 | 12.85 | 12.6255 | 12.4184 | 12.1378 | 11.6173 | 10.9765 | 10.9724 | 10.2337 | 9.7745 | 7.0796 | 2.0643 | -0.078571 | 14.8418 | 14.6867 | 14.499 | 14.3316 | 14.1163 | 13.602 | 13.0245 | 13.0867 | 12.351 | 11.9418 | 9.3745 | 3.2367 | -0.19898 | 13.9459 | 13.7408 | 13.5031 | 13.2969 | 13.0255 | 12.4602 | 11.7888 | 11.8418 | 11.0255 | 10.55 | 7.7398 | 1.8255 | -0.58673
|  | CHOLSEY | HT |  |  |  | 13.1541 | 12.9531 | 12.702 | 12.3888 | 12.1888 | 11.3602 | 10.7153 | 9.9571 | 9.4939 | 8.6163 | 5.5041 | 0.6398 | -2.7541 | 14.9439 | 14.8296 | 14.6214 | 14.3316 | 14.1949 | 13.2776 | 12.6878 | 11.9612 | 11.6122 | 10.7582 | 8.1153 | 2.9367 | -0.77653 | 14.0531 | 13.8735 | 13.6071 | 13.2694 | 13.0684 | 12.0867 | 11.3969 | 10.5561 | 10.0857 | 9.102 | 5.7939 | 0.11327 | -3.8816
|  | CHOLSEY | HE |  |  |  | 13.1531 | 12.9622 | 12.6878 | 12.2663 | 11.9714 | 10.9827 | 10.3898 | 9.7071 | 7.802 | 6.3816 | 3.1959 | -0.49388 | -4.6173 | 14.9235 | 14.8 | 14.5378 | 14.0847 | 13.801 | 12.6531 | 12.05 | 11.3459 | 9.1204 | 7.5204 | 4.1888 | -0.32857 | -6.4592 | 14.048 | 13.8776 | 13.5776 | 13.1 | 12.7776 | 11.5898 | 10.9398 | 10.1673 | 7.8786 | 6.2102 | 2.7327 | -1.5367 | -6.5194
|  | CHOLSEY | CF |  |  |  | 13.2153 | 13.0745 | 12.9592 | 12.8357 | 12.6622 | 12.4214 | 12.1367 | 11.9214 | 11.6306 | 11.2847 | 9.5306 | 6.9898 | 4.5357 | 14.9571 | 14.852 | 14.7459 | 14.6286 | 14.4357 | 14.1663 | 13.8367 | 13.5704 | 13.2429 | 12.849 | 10.6041 | 6.9286 | 1.9633 | 14.1051 | 13.9806 | 13.8592 | 13.7296 | 13.5378 | 13.2643 | 12.9469 | 12.7051 | 12.3908 | 12.0112 | 10.0857 | 7.299 | 4.6153
MANNINGTON GSP | CHRISTCHURCH BSP | CHRISTCHURCH | MINIMUM HEADROOM | SZ 15698 93141 | YES | 5.441 | 3.8685 | 3.1532 | 2.7502 | 1.9788 | 1.1543 | 0.27365 | -1.1498 | -2.7386 | -4.3233 | -5.4957 | -11.7539 | -16.7774 | -19.4559 | 8.0828 | 7.5114 | 7.191 | 6.5818 | 5.9277 | 5.2124 | 4.2359 | 3.1155 | 1.9767 | 1.1563 | -3.3559 | -8.6264 | -21.6457 | 5.0441 | 4.3236 | 3.9277 | 3.1849 | 2.3992 | 1.5583 | 0.23589 | -1.2529 | -2.7366 | -3.8029 | -9.2825 | -13.609 | -15.8294
|  | CHRISTCHURCH | EE |  |  |  | 3.8685 | 3.1532 | 2.7502 | 1.9788 | 1.1543 | 0.27365 | -1.1498 | -2.7386 | -4.3233 | -5.4957 | -11.5141 | -15.9019 | -18.9825 | 8.0828 | 7.5114 | 7.191 | 6.5818 | 5.9277 | 5.2124 | 4.2359 | 3.1155 | 1.9767 | 1.1563 | -3.3559 | -8.0559 | -14.8447 | 5.0441 | 4.3236 | 3.9277 | 3.1849 | 2.3992 | 1.5583 | 0.23589 | -1.2529 | -2.7366 | -3.8029 | -9.16 | -12.859 | -15.458
|  | CHRISTCHURCH | HT |  |  |  | 4.1726 | 3.5981 | 2.9655 | 2.2971 | 1.9736 | 1.3114 | 0.068547 | -1.2825 | -2.7131 | -4.1845 | -11.7539 | -16.7774 | -19.4559 | 8.4308 | 8.0726 | 7.6583 | 7.2032 | 7.0634 | 6.6226 | 5.9522 | 5.1961 | 4.3849 | 3.543 | -0.49574 | -2.7978 | -3.911 | 5.3992 | 4.8502 | 4.2267 | 3.5645 | 3.2798 | 2.6318 | 1.4961 | 0.24814 | -1.0621 | -2.41 | -9.2825 | -13.609 | -15.8294
|  | CHRISTCHURCH | HE |  |  |  | 4.1736 | 3.6369 | 3.042 | 2.4104 | 2.1247 | 1.5022 | 0.48283 | -0.66002 | -1.859 | -3.1151 | -9.6335 | -14.108 | -16.0804 | 8.3624 | 7.9563 | 7.4747 | 6.9573 | 6.7349 | 6.2053 | 5.49 | 4.6726 | 3.7941 | 2.8532 | -2.3957 | -7.2764 | -13.5957 | 5.393 | 4.8757 | 4.2849 | 3.6553 | 3.4053 | 2.793 | 1.8441 | 0.78079 | -0.32839 | -1.4937 | -7.4325 | -11.2355 | -12.8672
|  | CHRISTCHURCH | CF |  |  |  | 4.4247 | 4.0859 | 3.7543 | 3.3808 | 2.9951 | 2.9277 | 2.5267 | 2.0236 | 1.4951 | 0.93691 | -3.21 | -7.8325 | -12.0355 | 8.4869 | 8.1522 | 7.8063 | 7.4073 | 6.9828 | 6.789 | 6.2716 | 5.6573 | 5.0032 | 4.2971 | -0.79064 | -8.6264 | -21.6457 | 5.6247 | 5.2798 | 4.94 | 4.5492 | 4.1543 | 4.1073 | 3.7185 | 3.243 | 2.74 | 2.2094 | -1.6825 | -5.8417 | -9.5549
LALEHAM | EAST BEDFONT A | CHURCH ROAD | MINIMUM HEADROOM | TQ 06820 71722 | YES | 2.109 | 4.4681 | 3.8824 | 3.2375 | 3.0263 | 2.4732 | 1.8824 | 0.96709 | -0.29515 | -1.4523 | -2.1717 | -6.1503 | -9.5339 | -11.5298 | 7.1265 | 6.701 | 6.1459 | 5.9908 | 5.5194 | 5.0112 | 4.3316 | 3.4408 | 2.5806 | 2.001 | -1.4347 | -7.1235 | -19.2306 | 4.55 | 4.0143 | 3.3816 | 3.2571 | 2.7184 | 2.1408 | 1.301 | 0.16122 | -0.89898 | -1.5398 | -5.0082 | -7.9398 | -9.5347
|  | CHURCH ROAD | EE |  |  |  | 4.4681 | 3.8824 | 3.2375 | 3.0263 | 2.4732 | 1.8824 | 0.96709 | -0.29515 | -1.4523 | -2.1717 | -5.988 | -8.9268 | -11.3462 | 7.1265 | 6.701 | 6.1459 | 5.9908 | 5.5194 | 5.0112 | 4.3316 | 3.4408 | 2.5806 | 2.001 | -1.4347 | -5.4255 | -11.6796 | 4.55 | 4.0143 | 3.3816 | 3.2571 | 2.7184 | 2.1408 | 1.301 | 0.16122 | -0.89898 | -1.5398 | -4.9327 | -7.4367 | -9.4092
|  | CHURCH ROAD | HT |  |  |  | 4.6538 | 4.0671 | 3.6936 | 3.2691 | 2.7763 | 2.5997 | 1.7987 | 0.69158 | -0.34617 | -1.2686 | -6.1503 | -9.5339 | -11.5298 | 7.3908 | 7.0204 | 6.7745 | 6.4867 | 6.1582 | 6.1 | 5.6673 | 5.0633 | 4.4827 | 3.9418 | 1.301 | -0.27041 | -1.0755 | 4.8184 | 4.3173 | 3.9551 | 3.5255 | 3.0531 | 2.9276 | 2.1959 | 1.2122 | 0.27347 | -0.57857 | -5.0082 | -7.9398 | -9.5347
|  | CHURCH ROAD | HE |  |  |  | 4.6548 | 4.1834 | 3.7304 | 3.3242 | 2.8548 | 2.6946 | 2.0344 | 1.0569 | 0.1477 | -0.64413 | -4.9176 | -7.9839 | -9.4554 | 7.3214 | 6.9796 | 6.5867 | 6.2265 | 5.8184 | 5.6571 | 5.149 | 4.452 | 3.7561 | 3.0847 | -0.92653 | -5.0898 | -10.9918 | 4.8163 | 4.4 | 3.9745 | 3.5633 | 3.1092 | 3 | 2.3898 | 1.5184 | 0.69082 | -0.05102 | -3.951 | -6.601 | -7.751
|  | CHURCH ROAD | CF |  |  |  | 4.9416 | 4.7967 | 4.512 | 4.1497 | 3.8048 | 3.4232 | 3.4048 | 2.8651 | 2.3875 | 2.0263 | -0.8074 | -3.8809 | -6.7411 | 7.4684 | 7.2643 | 6.9561 | 6.5816 | 6.2184 | 5.7888 | 5.5878 | 5.001 | 4.4184 | 3.8592 | -0.32449 | -7.1235 | -19.2306 | 5.0449 | 4.8929 | 4.5827 | 4.248 | 3.9112 | 3.5429 | 3.6 | 3.1153 | 2.6673 | 2.302 | -0.34184 | -3.0235 | -5.5561
MINETY GSP | CIRENCESTER BSP | CIRENCESTER TOWN | MINIMUM HEADROOM | SP 02761 00827 | YES | 10.925 | 18.8276 | 15.1346 | 14.7969 | 14.1744 | 13.6448 | 11.9336 | 10.8162 | 9.5377 | 6.3724 | 3.906 | -3.3001 | -10.0491 | -17.2042 | 21.8316 | 18.2489 | 18.0234 | 17.2724 | 16.806 | 14.8775 | 13.7785 | 12.5367 | 8.8887 | 6.1785 | -0.38069 | -8.1633 | -18.9164 | 18.1469 | 14.4928 | 14.2295 | 13.4458 | 12.9877 | 11.0479 | 9.8132 | 8.4183 | 4.6367 | 1.7611 | -5.6317 | -13.1113 | -21.6991
|  | CIRENCESTER TOWN | EE |  |  |  | 18.8276 | 15.1346 | 14.7969 | 14.3969 | 13.9458 | 13.2316 | 12.254 | 11.5275 | 10.2193 | 9.2897 | 4.1703 | -4.7276 | -8.9256 | 21.8316 | 18.2489 | 18.0367 | 17.7448 | 17.4101 | 16.6999 | 15.8152 | 15.302 | 14.0489 | 13.253 | 8.652 | -2.1552 | -8.4725 | 18.1469 | 14.4928 | 14.2295 | 13.903 | 13.5397 | 12.7938 | 11.7581 | 11.0703 | 9.6469 | 8.702 | 3.3652 | -7.1205 | -11.6246
|  | CIRENCESTER TOWN | HT |  |  |  | 19.0296 | 15.4122 | 15.0428 | 14.4948 | 14.1622 | 12.7652 | 11.6683 | 10.3928 | 9.755 | 8.2816 | 1.705 | -7.3817 | -13.6297 | 21.9776 | 18.452 | 18.155 | 17.654 | 17.4316 | 15.8928 | 14.8275 | 13.5856 | 13.0918 | 11.653 | 5.9897 | -3.0419 | -9.446 | 18.2755 | 14.6713 | 14.3071 | 13.7377 | 13.4856 | 11.9152 | 10.6407 | 9.1826 | 8.6713 | 7.053 | 0.085633 | -10.1644 | -17.2736
|  | CIRENCESTER TOWN | HE |  |  |  | 19.0031 | 15.3764 | 14.9377 | 14.1744 | 13.6448 | 11.9336 | 10.8162 | 9.5377 | 6.3724 | 3.906 | -3.3001 | -10.0491 | -17.2042 | 21.9541 | 18.4111 | 18.0234 | 17.2724 | 16.806 | 14.8775 | 13.7785 | 12.5367 | 8.8887 | 6.1785 | -0.38069 | -8.1633 | -18.9164 | 18.2704 | 14.6764 | 14.2509 | 13.4458 | 12.9877 | 11.0479 | 9.8132 | 8.4183 | 4.6367 | 1.7611 | -5.6317 | -13.1113 | -21.6991
|  | CIRENCESTER TOWN | CF |  |  |  | 19.1724 | 15.6673 | 15.5275 | 15.3683 | 15.0489 | 14.6734 | 14.1969 | 13.7122 | 13.1693 | 12.5275 | 8.356 | 3.1346 | -1.6287 | 22.0133 | 18.5213 | 18.3969 | 18.2673 | 17.9438 | 17.5744 | 17.0683 | 16.6111 | 16.1122 | 15.5009 | 11.205 | 4.1979 | -5.1123 | 18.3735 | 14.8836 | 14.755 | 14.6356 | 14.3193 | 13.9785 | 13.5009 | 13.0754 | 12.5775 | 11.8887 | 7.4234 | 1.9101 | -2.9991
IVER 132KV | CIPPENHAM | CLARENCE ROAD | MINIMUM HEADROOM | SU 95654 76652 | YES | 9.053 | 7.4041 | 5.1409 | 3.4093 | 1.7738 | 0.22992 | -1.2568 | -3.1538 | -5.314 | -7.3425 | -8.9262 | -15.868 | -20.6936 | -22.1936 | 15.0398 | 13.0521 | 11.595 | 10.4064 | 9.4105 | 8.3871 | 7.1769 | 5.7656 | 4.3962 | 3.2381 | -2.7191 | -9.317 | -25.768 | 7.7418 | 5.5572 | 3.9419 | 2.484 | 1.1626 | -0.15478 | -1.8589 | -3.8793 | -5.8038 | -7.2884 | -13.6497 | -17.8752 | -19.1517
|  | CLARENCE ROAD | EE |  |  |  | 7.4041 | 5.1409 | 3.4093 | 1.7738 | 0.22992 | -1.2568 | -3.1538 | -5.314 | -7.3425 | -8.9262 | -15.868 | -19.7793 | -20.8619 | 15.0398 | 13.0521 | 11.595 | 10.4064 | 9.4105 | 8.3871 | 7.1769 | 5.7656 | 4.3962 | 3.2381 | -2.7191 | -8.2415 | -15.9058 | 7.7418 | 5.5572 | 3.9419 | 2.484 | 1.1626 | -0.15478 | -1.8589 | -3.8793 | -5.8038 | -7.2884 | -13.6497 | -17.0844 | -17.9844
|  | CLARENCE ROAD | HT |  |  |  | 7.7929 | 5.6766 | 3.8409 | 2.282 | 1.235 | 0.049306 | -1.4262 | -3.2058 | -4.9619 | -6.7619 | -15.4578 | -20.6936 | -22.1936 | 15.398 | 13.6062 | 12.1634 | 11.1258 | 10.5391 | 9.8258 | 8.9932 | 7.9687 | 6.9258 | 5.8656 | 1.1197 | -1.5915 | -2.4405 | 8.1286 | 6.0909 | 4.3593 | 2.9493 | 2.0473 | 0.96767 | -0.37824 | -1.9946 | -3.6007 | -5.2415 | -13.1874 | -17.8752 | -19.1517
|  | CLARENCE ROAD | HE |  |  |  | 7.8 | 5.696 | 3.9001 | 2.483 | 1.6534 | 0.54114 | -0.86294 | -2.5854 | -4.1384 | -5.7323 | -12.9589 | -16.8456 | -18.0538 | 15.3163 | 13.444 | 11.9154 | 10.836 | 10.2718 | 9.4513 | 8.5054 | 7.3391 | 6.2258 | 5.0411 | -1.2568 | -6.8711 | -14.5017 | 8.1255 | 6.1052 | 4.4042 | 3.1064 | 2.4095 | 1.3932 | 0.11971 | -1.4323 | -2.8527 | -4.316 | -10.9589 | -14.515 | -15.5527
|  | CLARENCE ROAD | CF |  |  |  | 8.1724 | 6.4481 | 5.044 | 4.0677 | 3.1228 | 2.5309 | 1.7422 | 0.89114 | 0.19624 | -0.56396 | -5.9058 | -11.3854 | -16.3578 | 15.502 | 13.8062 | 12.447 | 11.5554 | 10.8279 | 10.2942 | 9.5218 | 8.6718 | 7.8758 | 7.0003 | 0.54318 | -9.317 | -25.768 | 8.45 | 6.7613 | 5.4072 | 4.5034 | 3.6952 | 3.2238 | 2.534 | 1.7891 | 1.1646 | 0.47992 | -4.5731 | -9.5446 | -13.9629
MELKSHAM GSP | CHIPPENHAM | COCKLEBURY | MINIMUM HEADROOM | ST 92447 73890 | YES | 4.969 | 17.4148 | 16.927 | 16.028 | 15.1413 | 14.5474 | 13.5719 | 12.3913 | 11.2393 | 10.1964 | 9.4148 | 5.9474 | 2.9495 | 1.0893 | 22.3801 | 21.9882 | 21.324 | 20.7127 | 20.4168 | 19.7882 | 19.0454 | 18.2638 | 17.5168 | 16.9852 | 14.4352 | 11.4127 | 3.7933 | 16.826 | 16.3607 | 15.5301 | 14.7291 | 14.3658 | 13.4984 | 12.4525 | 11.4015 | 10.4372 | 9.7566 | 6.8964 | 4.3719 | 2.8464
|  | COCKLEBURY | EE |  |  |  | 17.4148 | 16.927 | 16.028 | 15.1413 | 14.5474 | 13.5719 | 12.3913 | 11.2393 | 10.1964 | 9.4148 | 6.1495 | 3.5678 | 1.4209 | 22.3801 | 21.9882 | 21.324 | 20.7127 | 20.4168 | 19.7882 | 19.0454 | 18.2638 | 17.5168 | 16.9852 | 14.4352 | 11.6872 | 7.6015 | 16.826 | 16.3607 | 15.5301 | 14.7291 | 14.3658 | 13.4984 | 12.4525 | 11.4015 | 10.4372 | 9.7566 | 6.9913 | 4.9015 | 3.0944
|  | COCKLEBURY | HT |  |  |  | 17.5719 | 17.0556 | 16.2444 | 15.6066 | 14.7984 | 13.8546 | 12.9882 | 11.975 | 11.0546 | 10.1331 | 5.9474 | 2.9495 | 1.0893 | 22.6199 | 22.2974 | 21.7678 | 21.4046 | 20.926 | 20.3882 | 20.078 | 19.5219 | 18.9811 | 18.4209 | 16.0617 | 14.6944 | 13.925 | 17.0627 | 16.6127 | 15.8923 | 15.3505 | 14.6362 | 13.8066 | 13.2413 | 12.3454 | 11.4995 | 10.6403 | 6.8964 | 4.3719 | 2.8464
|  | COCKLEBURY | HE |  |  |  | 17.5729 | 17.1566 | 16.4117 | 15.7638 | 14.8648 | 13.9831 | 13.2638 | 12.4005 | 11.6229 | 10.8546 | 7.3923 | 4.7382 | 3.3495 | 22.5801 | 22.2699 | 21.7423 | 21.3189 | 20.726 | 20.1658 | 19.8301 | 19.2474 | 18.6791 | 18.0903 | 15.1352 | 12.3158 | 8.5393 | 17.0617 | 16.6882 | 16.0209 | 15.478 | 14.7127 | 13.9382 | 13.4709 | 12.7015 | 11.978 | 11.2464 | 8.1362 | 5.9954 | 4.827
|  | COCKLEBURY | CF |  |  |  | 17.7301 | 17.4117 | 16.8933 | 16.3862 | 15.7362 | 15.0199 | 14.3954 | 13.8148 | 13.6648 | 13.1811 | 10.6719 | 8.2229 | 5.9117 | 22.6566 | 22.3719 | 21.9658 | 21.5842 | 21.1209 | 20.6199 | 20.1087 | 19.5801 | 19.3954 | 18.9087 | 15.8872 | 11.4127 | 3.7933 | 17.1923 | 16.8893 | 16.4311 | 15.974 | 15.4525 | 14.8311 | 14.2658 | 13.7209 | 13.7505 | 13.3117 | 10.9668 | 8.825 | 6.8944
MELKSHAM GSP | FROME BSP | CODFORD | MINIMUM HEADROOM | ST 97372 39559 | YES | 1.756 | 2.199 | 2.1429 | 2.0857 | 2.0031 | 1.9194 | 1.8224 | 1.7531 | 1.6194 | 1.4816 | 1.4429 | 1.1867 | 1.0776 | 1.0143 | 1.4163 | 1.3969 | 1.3776 | 1.3531 | 1.3224 | 1.2908 | 1.2653 | 1.2133 | 1.1122 | 1.0847 | 0.93571 | 0.59694 | -0.15816 | 1.802 | 1.7459 | 1.6918 | 1.6133 | 1.5327 | 1.4378 | 1.3684 | 1.2378 | 1.102 | 1.0633 | 0.82347 | 0.72449 | 0.66939
|  | CODFORD | EE |  |  |  | 2.199 | 2.1429 | 2.0857 | 2.0031 | 1.9194 | 1.8224 | 1.7531 | 1.6194 | 1.4816 | 1.4429 | 1.1867 | 1.0776 | 1.0173 | 1.4163 | 1.3969 | 1.3776 | 1.3531 | 1.3224 | 1.2908 | 1.2653 | 1.2133 | 1.1122 | 1.0847 | 0.93571 | 0.71735 | 0.34796 | 1.802 | 1.7459 | 1.6918 | 1.6133 | 1.5327 | 1.4378 | 1.3684 | 1.2378 | 1.102 | 1.0633 | 0.82347 | 0.72449 | 0.66939
|  | CODFORD | HT |  |  |  | 2.2327 | 2.1908 | 2.1459 | 2.0888 | 2.0469 | 1.9867 | 1.9133 | 1.8235 | 1.7643 | 1.6704 | 1.2418 | 1.0867 | 1.0143 | 1.4337 | 1.4214 | 1.4051 | 1.3888 | 1.3755 | 1.3571 | 1.3347 | 1.302 | 1.2847 | 1.2551 | 1.0347 | 0.99592 | 0.99592 | 1.8439 | 1.8041 | 1.7582 | 1.698 | 1.6643 | 1.5969 | 1.5245 | 1.4316 | 1.3776 | 1.2827 | 0.87245 | 0.72959 | 0.6949
|  | CODFORD | HE |  |  |  | 2.2316 | 2.1908 | 2.1459 | 2.0918 | 2.051 | 1.9929 | 1.9245 | 1.8357 | 1.7786 | 1.6918 | 1.2398 | 1.1276 | 1.0745 | 1.4306 | 1.4163 | 1.399 | 1.3806 | 1.3653 | 1.3418 | 1.3153 | 1.2816 | 1.2582 | 1.2224 | 0.97755 | 0.74592 | 0.37959 | 1.8429 | 1.8041 | 1.7571 | 1.701 | 1.6673 | 1.6041 | 1.5347 | 1.4459 | 1.3939 | 1.3041 | 0.87653 | 0.77857 | 0.73265
|  | CODFORD | CF |  |  |  | 2.2378 | 2.201 | 2.1673 | 2.1316 | 2.0888 | 2.0388 | 2.0071 | 1.949 | 1.8969 | 1.8378 | 1.5194 | 1.299 | 1.1408 | 1.4316 | 1.4204 | 1.4071 | 1.3918 | 1.3745 | 1.3541 | 1.3398 | 1.3122 | 1.2847 | 1.2582 | 1.0469 | 0.59694 | -0.15816 | 1.848 | 1.8092 | 1.7786 | 1.7429 | 1.6959 | 1.6449 | 1.6204 | 1.5582 | 1.5031 | 1.4388 | 1.1327 | 0.92755 | 0.78367
IVER 132KV | DENHAM | COKES LANE | MINIMUM HEADROOM | SU 99240 97483 | YES | 0.911 | 8.4875 | 8.2671 | 8.0314 | 7.763 | 7.5906 | 7.3906 | 7.1018 | 6.7732 | 6.7242 | 6.4283 | 5.2926 | 4.364 | 3.8457 | 9.8592 | 9.701 | 9.5388 | 9.3439 | 9.2041 | 9.0276 | 8.8071 | 8.55 | 8.6082 | 8.4694 | 7.6194 | 6.0969 | 2.9612 | 9.5724 | 9.3531 | 9.1286 | 8.8561 | 8.6816 | 8.4531 | 8.1541 | 7.8092 | 7.9398 | 7.6408 | 6.7918 | 6.0112 | 5.5776
|  | COKES LANE | EE |  |  |  | 8.4875 | 8.2671 | 8.0314 | 7.763 | 7.5906 | 7.3906 | 7.1018 | 6.7732 | 6.7885 | 6.5946 | 5.4702 | 4.5875 | 3.9263 | 9.8592 | 9.701 | 9.5388 | 9.3439 | 9.2041 | 9.0276 | 8.8071 | 8.55 | 8.6082 | 8.4694 | 7.6194 | 6.549 | 4.8888 | 9.5724 | 9.3531 | 9.1286 | 8.8561 | 8.6816 | 8.4531 | 8.1541 | 7.8092 | 7.9531 | 7.7878 | 6.9224 | 6.2082 | 5.649
|  | COKES LANE | HT |  |  |  | 8.5324 | 8.3365 | 8.0987 | 7.8487 | 7.7008 | 7.5242 | 7.2599 | 7.011 | 6.7242 | 6.4283 | 5.2926 | 4.364 | 3.8457 | 9.9388 | 9.8337 | 9.702 | 9.5561 | 9.4735 | 9.3602 | 9.2051 | 9.0745 | 8.8939 | 8.7071 | 8.2653 | 7.8949 | 7.6949 | 9.6551 | 9.4786 | 9.2633 | 9.0306 | 8.8929 | 8.7071 | 8.448 | 8.2286 | 7.9398 | 7.6408 | 6.7918 | 6.0112 | 5.5776
|  | COKES LANE | HE |  |  |  | 8.5406 | 8.3528 | 8.1242 | 7.8885 | 7.7508 | 7.5855 | 7.3804 | 7.1916 | 6.9671 | 6.7314 | 5.8191 | 4.9395 | 4.5089 | 9.9235 | 9.802 | 9.649 | 9.4878 | 9.3847 | 9.2469 | 9.0806 | 8.9347 | 8.7337 | 8.5265 | 7.7592 | 6.6806 | 5.1041 | 9.6561 | 9.4867 | 9.2806 | 9.0561 | 8.9255 | 8.75 | 8.5337 | 8.3582 | 8.1112 | 7.8531 | 7.2214 | 6.5133 | 6.152
|  | COKES LANE | CF |  |  |  | 8.5783 | 8.4324 | 8.2712 | 8.0987 | 8.0151 | 7.9059 | 7.8253 | 7.7304 | 7.6589 | 7.5426 | 7.011 | 6.1916 | 5.3467 | 9.9327 | 9.8214 | 9.7 | 9.5653 | 9.4827 | 9.3592 | 9.2265 | 9.0673 | 8.9398 | 8.7633 | 7.8612 | 6.0969 | 2.9612 | 9.6847 | 9.5449 | 9.398 | 9.2357 | 9.1531 | 9.0327 | 8.9224 | 8.7878 | 8.7082 | 8.5643 | 8.1276 | 7.4429 | 6.8122
LOVEDEAN GSP | WYMERING BSP | COLLEGE PARK | MINIMUM HEADROOM | SU 65893 02686 | YES | 0.592 | 9.5638 | 9.275 | 8.8811 | 8.475 | 7.9801 | 7.4372 | 6.9658 | 6.1005 | 5.2403 | 4.5536 | 1.9577 | 0.14847 | 0.17296 | 11.4367 | 11.148 | 10.7724 | 10.3806 | 9.898 | 9.3673 | 8.9765 | 8.252 | 7.5112 | 6.8929 | 3.5531 | -2.7765 | -16.2745 | 9.6296 | 9.3602 | 9.0102 | 8.649 | 8.1643 | 7.6378 | 7.2112 | 6.3918 | 5.5765 | 4.9357 | 2.5622 | 0.97551 | 1.0235
|  | COLLEGE PARK | EE |  |  |  | 9.5638 | 9.275 | 8.8811 | 8.475 | 7.9801 | 7.4372 | 6.9658 | 6.1005 | 5.2403 | 4.5536 | 1.9577 | 0.71173 | 1.077 | 11.4367 | 11.148 | 10.7724 | 10.3806 | 9.898 | 9.3673 | 8.9765 | 8.252 | 7.5112 | 6.8929 | 3.5531 | -0.28673 | -6.3663 | 9.6296 | 9.3602 | 9.0102 | 8.649 | 8.1643 | 7.6378 | 7.2112 | 6.3918 | 5.5765 | 4.9357 | 2.5622 | 1.4786 | 1.7939
|  | COLLEGE PARK | HT |  |  |  | 9.724 | 9.523 | 9.2709 | 8.9923 | 8.6444 | 8.2893 | 7.6648 | 6.9546 | 6.2107 | 5.776 | 2.1883 | 0.14847 | 0.17296 | 11.6653 | 11.5051 | 11.298 | 11.0949 | 10.8388 | 10.5776 | 10.1898 | 9.7408 | 9.2551 | 9.0306 | 6.8082 | 5.5673 | 5.4337 | 9.8112 | 9.6112 | 9.3561 | 9.1082 | 8.802 | 8.4918 | 7.9092 | 7.2429 | 6.5378 | 6.151 | 2.8276 | 0.97551 | 1.0235
|  | COLLEGE PARK | HE |  |  |  | 9.7128 | 9.5332 | 9.3046 | 9.0638 | 8.7546 | 8.4505 | 7.8913 | 7.2536 | 6.5934 | 6.2648 | 3.7546 | 2.5852 | 2.4219 | 11.5898 | 11.3806 | 11.1112 | 10.8459 | 10.5122 | 10.1673 | 9.6847 | 9.1255 | 8.5245 | 8.1724 | 4.7265 | 0.83878 | -5.3694 | 9.7969 | 9.6194 | 9.3867 | 9.1673 | 8.8929 | 8.6255 | 8.1204 | 7.5235 | 6.9 | 6.6102 | 4.2582 | 3.2163 | 3.099
|  | COLLEGE PARK | CF |  |  |  | 9.8454 | 9.7597 | 9.6372 | 9.526 | 9.3515 | 9.1607 | 8.9689 | 8.6821 | 8.3719 | 8.0413 | 6.4138 | 4.0934 | 1.9342 | 11.6602 | 11.4796 | 11.2469 | 11.0173 | 10.7235 | 10.3673 | 9.9663 | 9.4612 | 8.9163 | 8.3296 | 4.499 | -2.7765 | -16.2745 | 9.9235 | 9.8337 | 9.702 | 9.5898 | 9.4388 | 9.2724 | 9.1071 | 8.8418 | 8.5408 | 8.2204 | 6.6724 | 4.548 | 2.6194
EALING GSP | EALING 22kV | COPLEY DENE | MINIMUM HEADROOM | TQ 17445 80798 | YES | 12.532 | 4.8678 | 3.3743 | 2.3794 | 1.5437 | 0.24373 | 36.9141 | 35.1254 | 33.1203 | 31.1315 | 29.5723 | 21.9743 | 15.3815 | 12.0284 | 13.2964 | 11.9009 | 11.0101 | 10.4294 | 9.3601 | 46.2825 | 44.9458 | 43.3856 | 41.8141 | 40.6274 | 34.3988 | 26.1968 | 4.4703 | 5.729 | 4.255 | 3.258 | 2.5386 | 1.2825 | 38.0019 | 36.3203 | 34.3886 | 32.4743 | 31.0335 | 24.3601 | 18.5631 | 15.6468
|  | COPLEY DENE | EE |  |  |  | 4.8678 | 3.3743 | 2.3794 | 1.5437 | 0.24373 | 36.9141 | 35.1254 | 33.1203 | 31.1315 | 29.5723 | 21.9743 | 16.5458 | 12.7019 | 13.2964 | 11.9009 | 11.0101 | 10.4294 | 9.3601 | 46.2825 | 44.9458 | 43.3856 | 41.8141 | 40.6274 | 34.3988 | 27.1437 | 15.9152 | 5.729 | 4.255 | 3.258 | 2.5386 | 1.2825 | 38.0019 | 36.3203 | 34.3886 | 32.4743 | 31.0335 | 24.3601 | 19.6192 | 16.1948
|  | COPLEY DENE | HT |  |  |  | 5.3576 | 4.0356 | 3.3448 | 2.4243 | 1.3897 | 38.759 | 37.3488 | 35.7835 | 34.1499 | 32.457 | 22.709 | 15.3815 | 12.0284 | 13.8311 | 12.6958 | 12.2162 | 11.5856 | 10.8713 | 48.6182 | 47.7968 | 46.8356 | 45.8172 | 44.7386 | 39.3397 | 35.9162 | 34.6652 | 6.2699 | 4.9846 | 4.3315 | 3.4682 | 2.4886 | 39.9611 | 38.6641 | 37.1978 | 35.6611 | 34.058 | 25.1723 | 18.5631 | 15.6468
|  | COPLEY DENE | HE |  |  |  | 5.3086 | 4.055 | 3.4346 | 2.5948 | 1.6529 | 39.0682 | 37.808 | 36.4203 | 34.9978 | 33.5315 | 26.1346 | 21.1539 | 19.3723 | 13.7076 | 12.5254 | 11.9774 | 11.2876 | 10.507 | 48.1539 | 47.2519 | 46.208 | 45.1029 | 43.9284 | 37.2917 | 29.9876 | 19.6662 | 6.2219 | 4.9988 | 4.409 | 3.6233 | 2.7376 | 40.2713 | 39.1192 | 37.8264 | 36.4927 | 35.1162 | 28.3784 | 23.9631 | 22.4213
|  | COPLEY DENE | CF |  |  |  | 5.6454 | 4.6335 | 4.2539 | 3.7692 | 3.1948 | 40.6539 | 40.4692 | 39.859 | 39.1846 | 38.4774 | 33.8641 | 28.7213 | 23.4631 | 13.8811 | 12.7917 | 12.3131 | 11.7948 | 11.1611 | 48.5141 | 48.1346 | 47.2754 | 46.3397 | 45.3376 | 38.3427 | 26.1968 | 4.4703 | 6.5188 | 5.4999 | 5.106 | 4.6488 | 4.0886 | 41.5641 | 41.4458 | 40.8356 | 40.158 | 39.4458 | 34.9999 | 30.3754 | 25.8662
BRAMLEY (FLEE) | MAIDENHEAD BSP | CORDWALLIS | MINIMUM HEADROOM | SU 88285 81857 | YES | 7.078 | 7.8797 | 7.342 | 6.6624 | 6.2481 | 5.4777 | 4.8603 | 4.0144 | 3.0573 | 2.0664 | 1.3552 | -1.705 | -3.9519 | -4.3203 | 10.944 | 10.5409 | 10.0134 | 9.7593 | 9.192 | 8.6726 | 8.0287 | 7.2807 | 6.4991 | 5.9511 | 3.1215 | -1.1774 | -11.406 | 7.9715 | 7.496 | 6.8766 | 6.5328 | 5.8379 | 5.2389 | 4.4307 | 3.5032 | 2.5511 | 1.9073 | -0.75294 | -2.6989 | -2.9907
|  | CORDWALLIS | EE |  |  |  | 7.8797 | 7.342 | 6.6624 | 6.2481 | 5.4777 | 4.8603 | 4.0144 | 3.0573 | 2.0664 | 1.3552 | -1.705 | -3.5968 | -3.4774 | 10.944 | 10.5409 | 10.0134 | 9.7593 | 9.192 | 8.6726 | 8.0287 | 7.2807 | 6.4991 | 5.9511 | 3.1215 | 0.047057 | -4.3285 | 7.9715 | 7.496 | 6.8766 | 6.5328 | 5.8379 | 5.2389 | 4.4307 | 3.5032 | 2.5511 | 1.9073 | -0.75294 | -2.3907 | -2.2754
|  | CORDWALLIS | HT |  |  |  | 8.1083 | 7.6491 | 7.0858 | 6.4991 | 5.793 | 5.2328 | 4.892 | 4.1491 | 3.3369 | 2.4981 | -1.5591 | -3.9519 | -4.3203 | 11.1991 | 10.9256 | 10.5766 | 10.2318 | 9.8052 | 9.4246 | 9.3318 | 8.8726 | 8.3675 | 7.8338 | 5.4185 | 4.1726 | 3.895 | 8.2001 | 7.8052 | 7.3052 | 6.792 | 6.1654 | 5.642 | 5.3471 | 4.6593 | 3.9124 | 3.1379 | -0.57131 | -2.6989 | -2.9907
|  | CORDWALLIS | HE |  |  |  | 8.1307 | 7.7399 | 7.2491 | 6.7491 | 6.1481 | 5.4828 | 5.1103 | 4.4369 | 3.7124 | 2.9634 | -0.17029 | -1.8989 | -2.2591 | 11.1542 | 10.8573 | 10.4736 | 10.1001 | 9.643 | 9.1358 | 8.9369 | 8.4042 | 7.8226 | 7.2022 | 3.9634 | 0.87665 | -3.6876 | 8.2154 | 7.8715 | 7.4297 | 6.9879 | 6.446 | 5.844 | 5.5379 | 4.9093 | 4.2369 | 3.542 | 0.66236 | -0.84682 | -1.1285
|  | CORDWALLIS | CF |  |  |  | 8.3154 | 8.0736 | 7.7542 | 7.4287 | 7.0318 | 6.5889 | 6.2256 | 6.2409 | 5.9338 | 5.595 | 3.2358 | 0.47869 | -2.0621 | 11.2501 | 11.0113 | 10.7042 | 10.4011 | 10.0307 | 9.6001 | 9.1552 | 9.0083 | 8.5481 | 8.0481 | 4.4685 | -1.1774 | -11.406 | 8.3848 | 8.1756 | 7.896 | 7.6093 | 7.2552 | 6.8603 | 6.5134 | 6.5552 | 6.2583 | 5.9226 | 3.6297 | 1.2073 | -0.9958
MANNINGTON GSP | LYTCHETT | CORFE MULLEN | MINIMUM HEADROOM | SY 98583 96071 | YES | 1.781 | 16.6333 | 16.2608 | 15.6976 | 15.418 | 14.8547 | 14.2445 | 13.1322 | 11.9424 | 10.9516 | 10.3261 | 5.6271 | 2.4843 | 0.77 | 16.7404 | 16.4302 | 15.9924 | 15.8976 | 15.4629 | 14.9486 | 14.2486 | 13.468 | 12.7639 | 12.3333 | 9.4618 | 5.3159 | -3.9535 | 16.371 | 16.0108 | 15.4853 | 15.3241 | 14.8067 | 14.1853 | 13.1894 | 12.1078 | 11.1792 | 10.6312 | 6.6996 | 4.0271 | 2.6067
|  | CORFE MULLEN | EE |  |  |  | 16.6333 | 16.2608 | 15.6976 | 15.5251 | 14.9588 | 14.2445 | 13.1322 | 11.9424 | 10.9516 | 10.3261 | 6.2027 | 3.1771 | 1.0241 | 16.7404 | 16.4302 | 15.9924 | 15.8976 | 15.4629 | 14.9486 | 14.2486 | 13.468 | 12.7639 | 12.3333 | 9.4618 | 6.1965 | 1.2476 | 16.371 | 16.0108 | 15.4853 | 15.3608 | 14.8414 | 14.1853 | 13.1894 | 12.1078 | 11.1792 | 10.6312 | 7.1445 | 4.6241 | 2.819
|  | CORFE MULLEN | HT |  |  |  | 16.7822 | 16.3965 | 15.8955 | 15.418 | 14.8547 | 14.4649 | 13.3904 | 12.3496 | 11.5231 | 10.6751 | 5.6271 | 2.4843 | 0.77 | 16.9567 | 16.7312 | 16.4373 | 16.1394 | 15.7914 | 15.6914 | 15.171 | 14.6373 | 14.1812 | 13.7078 | 11.2333 | 9.9741 | 9.2853 | 16.5496 | 16.2078 | 15.7669 | 15.3241 | 14.8067 | 14.5149 | 13.5863 | 12.671 | 11.9067 | 11.1251 | 6.6996 | 4.0271 | 2.6067
|  | CORFE MULLEN | HE |  |  |  | 16.8108 | 16.5108 | 16.1149 | 15.7078 | 15.2047 | 14.8802 | 14.0057 | 13.0731 | 12.3486 | 11.6822 | 7.4302 | 4.4955 | 3.0822 | 16.92 | 16.6853 | 16.3863 | 16.0588 | 15.6659 | 15.52 | 14.9792 | 14.3812 | 13.8476 | 13.322 | 10.0027 | 6.7598 | 2.0955 | 16.568 | 16.2924 | 15.9353 | 15.5527 | 15.0904 | 14.8496 | 14.0914 | 13.27 | 12.6078 | 11.9935 | 8.2261 | 5.7792 | 4.6047
|  | CORFE MULLEN | CF |  |  |  | 16.9424 | 16.7843 | 16.572 | 16.421 | 16.1598 | 15.7863 | 15.6731 | 15.2884 | 14.8965 | 14.4863 | 11.0557 | 8.2251 | 5.6557 | 16.9792 | 16.7976 | 16.5537 | 16.3465 | 16.0598 | 15.6822 | 15.5465 | 15.1098 | 14.6618 | 14.1731 | 10.4996 | 5.3159 | -3.9535 | 16.6894 | 16.5363 | 16.3241 | 16.1659 | 15.9231 | 15.5751 | 15.5292 | 15.1863 | 14.819 | 14.4302 | 11.3424 | 8.9057 | 6.718
MELKSHAM GSP | NORRINGTON | CORSHAM | MINIMUM HEADROOM | ST 86766 69583 | YES | 1.458 | 3.4197 | 3.1126 | 2.7248 | 2.2473 | 1.7514 | 1.6401 | 0.77176 | -0.21701 | -1.1231 | -1.8619 | -5.4905 | -8.3099 | -10.066 | 3.9605 | 3.7371 | 3.4697 | 3.1371 | 2.7595 | 2.6809 | 1.9473 | 1.0973 | 0.33911 | -0.30171 | -3.0578 | -5.4588 | -9.864 | 3.584 | 3.3738 | 3.0554 | 2.6626 | 2.2463 | 2.1534 | 1.2697 | 0.2534 | -0.65885 | -1.4129 | -4.9762 | -7.7762 | -9.4415
|  | CORSHAM | EE |  |  |  | 3.4197 | 3.1126 | 2.7248 | 2.2473 | 1.7514 | 1.6401 | 0.77176 | -0.21701 | -1.1231 | -1.8619 | -5.1752 | -7.3915 | -9.318 | 3.9605 | 3.7371 | 3.4697 | 3.1371 | 2.7595 | 2.6809 | 1.9473 | 1.0973 | 0.33911 | -0.30171 | -3.0578 | -5.4588 | -8.9333 | 3.584 | 3.3738 | 3.0554 | 2.6626 | 2.2463 | 2.1534 | 1.2697 | 0.2534 | -0.65885 | -1.4129 | -4.6007 | -6.7782 | -8.6007
|  | CORSHAM | HT |  |  |  | 3.5881 | 3.3463 | 3.0412 | 2.6616 | 2.3248 | 1.9371 | 1.0881 | 0.49319 | -0.33538 | -1.2201 | -5.4905 | -8.3099 | -10.066 | 4.1116 | 3.9656 | 3.7891 | 3.5636 | 3.3718 | 3.136 | 2.4932 | 2.0279 | 1.4105 | 0.73401 | -2.2099 | -4.015 | -5.1058 | 3.7003 | 3.5565 | 3.2983 | 2.982 | 2.6932 | 2.3616 | 1.5146 | 0.86156 | 0.048294 | -0.82007 | -4.9762 | -7.7762 | -9.4415
|  | CORSHAM | HE |  |  |  | 3.5799 | 3.3442 | 3.0463 | 2.6707 | 2.3381 | 1.9544 | 1.2728 | 0.81054 | 0.17789 | -0.49048 | -4.0956 | -6.4966 | -7.8854 | 4.0758 | 3.9044 | 3.6901 | 3.4299 | 3.1942 | 2.9075 | 2.3565 | 1.9371 | 1.4483 | 0.90238 | -2.1762 | -4.7884 | -8.0517 | 3.682 | 3.5544 | 3.3024 | 2.986 | 2.6983 | 2.3677 | 1.7034 | 1.1983 | 0.60952 | -0.015992 | -3.4844 | -5.8354 | -7.1803
|  | CORSHAM | CF |  |  |  | 3.6983 | 3.5626 | 3.3677 | 3.1187 | 2.8809 | 2.6779 | 2.3371 | 1.8871 | 1.4534 | 1.3922 | -0.7466 | -2.9435 | -4.9109 | 4.1412 | 4.0116 | 3.8493 | 3.6452 | 3.4381 | 3.2391 | 2.8565 | 2.3493 | 1.8656 | 1.6636 | -0.79967 | -4.2568 | -9.864 | 3.7585 | 3.6922 | 3.582 | 3.3942 | 3.1952 | 3.0248 | 2.6952 | 2.2483 | 1.8289 | 1.7309 | -0.31905 | -2.3017 | -4.0905
EAST CLAYDON GSP | BICESTER NORTH BSP | COTTISFORD | MINIMUM HEADROOM | SP 59021 31128 | YES | 0.127 | -3.0943 | -3.1708 | -3.2708 | -3.3892 | -3.4759 | -3.6086 | -3.781 | -3.9249 | -4.1137 | -4.2229 | -4.7657 | -5.0014 | -5.228 | -2.8647 | -2.9178 | -2.9943 | -3.0831 | -3.1484 | -3.2453 | -3.3718 | -3.4769 | -3.6167 | -3.6922 | -4.0269 | -4.3351 | -5.2239 | -3.0188 | -3.0922 | -3.181 | -3.2882 | -3.3667 | -3.4841 | -3.6371 | -3.7739 | -3.9433 | -4.0524 | -4.5729 | -4.7912 | -4.9953
|  | COTTISFORD | EE |  |  |  | -3.0943 | -3.1708 | -3.2708 | -3.3892 | -3.4759 | -3.6086 | -3.781 | -3.9249 | -4.1137 | -4.2229 | -4.7657 | -5.0014 | -5.1443 | -2.8647 | -2.9178 | -2.9943 | -3.0831 | -3.1484 | -3.2453 | -3.3718 | -3.4769 | -3.6167 | -3.6922 | -4.0269 | -4.2902 | -4.6678 | -3.0188 | -3.0922 | -3.181 | -3.2882 | -3.3667 | -3.4841 | -3.6371 | -3.7739 | -3.9433 | -4.0524 | -4.5729 | -4.7912 | -4.9157
|  | COTTISFORD | HT |  |  |  | -3.0524 | -3.1198 | -3.1953 | -3.2647 | -3.3565 | -3.4484 | -3.5892 | -3.7014 | -3.8555 | -4.0167 | -4.679 | -4.9984 | -5.228 | -2.8239 | -2.8667 | -2.9137 | -2.9565 | -3.0167 | -3.079 | -3.1657 | -3.2361 | -3.3392 | -3.4473 | -3.8484 | -4.0106 | -4.1239 | -2.981 | -3.0453 | -3.1127 | -3.1759 | -3.2586 | -3.3433 | -3.4718 | -3.5759 | -3.7188 | -3.8657 | -4.4861 | -4.7861 | -4.9953
|  | COTTISFORD | HE |  |  |  | -3.0545 | -3.1188 | -3.1922 | -3.2606 | -3.3484 | -3.4422 | -3.5729 | -3.6831 | -3.831 | -3.9882 | -4.7024 | -4.9331 | -5.0371 | -2.8269 | -2.8739 | -2.9249 | -2.9688 | -3.0341 | -3.0994 | -3.1922 | -3.2627 | -3.3718 | -3.4912 | -3.9831 | -4.2484 | -4.6065 | -2.982 | -3.0443 | -3.1096 | -3.1739 | -3.2535 | -3.3382 | -3.4576 | -3.5586 | -3.6973 | -3.8422 | -4.5127 | -4.7249 | -4.8147
|  | COTTISFORD | CF |  |  |  | -3.0351 | -3.0902 | -3.1494 | -3.2147 | -3.2657 | -3.3371 | -3.4106 | -3.5024 | -3.5667 | -3.6688 | -4.1994 | -4.628 | -5.0361 | -2.8137 | -2.8524 | -2.8963 | -2.9463 | -2.98 | -3.0371 | -3.0984 | -3.18 | -3.228 | -3.3198 | -3.8086 | -4.3351 | -5.2239 | -2.9647 | -3.0147 | -3.0678 | -3.129 | -3.1769 | -3.2402 | -3.3076 | -3.3933 | -3.4494 | -3.5433 | -4.0331 | -4.4402 | -4.828
BRAMLEY (FLEE) | BURGHFIELD MAIN | COURAGES | MINIMUM HEADROOM | SU 70990 69570 | YES | 4.105 | 12.8684 | 12.4276 | 11.0847 | 9.849 | 8.4582 | 6.8888 | 3.3041 | 1.3867 | -0.40102 | -1.7898 | -13.8245 | -17.7796 | -17.9306 | 15.6143 | 15.2827 | 14.2173 | 13.2929 | 12.25 | 11.0694 | 7.599 | 6.15 | 4.7969 | 3.7316 | -6.3112 | -9.4735 | -9.6602 | 12.5092 | 11.7449 | 10.4388 | 9.2612 | 7.9306 | 6.4286 | 3.0786 | 1.2418 | -0.47041 | -1.8082 | -13.4969 | -17.3224 | -17.4643
|  | COURAGES | EE |  |  |  | 12.8684 | 12.4276 | 11.0847 | 9.849 | 8.4582 | 6.8888 | 3.3041 | 1.3867 | -0.40102 | -1.7898 | -9.2806 | -10.3245 | -10.3694 | 15.6143 | 15.2827 | 14.2173 | 13.2929 | 12.25 | 11.0694 | 7.599 | 6.15 | 4.7969 | 3.7316 | -2.7745 | -3.6755 | -3.7939 | 12.5092 | 11.7449 | 10.4388 | 9.2612 | 7.9306 | 6.4286 | 3.0786 | 1.2418 | -0.47041 | -1.8082 | -9.0735 | -10.0653 | -10.1041
|  | COURAGES | HT |  |  |  | 13.2929 | 13.05 | 12.3847 | 11.8122 | 11.0816 | 10.0245 | 7.0031 | 5.7408 | 4.4122 | 2.798 | -5.7041 | -8.3929 | -8.5735 | 15.9622 | 15.7796 | 15.2163 | 14.85 | 14.2673 | 13.4776 | 10.4459 | 9.5031 | 8.5071 | 7.2051 | 0.02551 | -2.1041 | -2.2398 | 13.2918 | 12.95 | 12.0367 | 11.3235 | 10.4694 | 9.4633 | 6.6551 | 5.4531 | 4.1827 | 2.6245 | -5.6102 | -8.1949 | -8.3602
|  | COURAGES | HE |  |  |  | 13.1357 | 12.7908 | 11.8378 | 10.7296 | 9.4357 | 7.8786 | 4.3378 | 2.4133 | 0.37551 | -1.6439 | -13.8245 | -17.7796 | -17.9306 | 15.8173 | 15.5418 | 14.798 | 13.9684 | 13.002 | 11.8337 | 8.3898 | 6.9337 | 5.3847 | 3.8347 | -6.3112 | -9.4735 | -9.6602 | 13.0235 | 12.3694 | 11.1694 | 10.1122 | 8.8745 | 7.3888 | 4.0745 | 2.2296 | 0.27143 | -1.6755 | -13.4969 | -17.3224 | -17.4643
|  | COURAGES | CF |  |  |  | 13.3898 | 13.2031 | 12.601 | 12.1327 | 11.5796 | 10.5418 | 7.7643 | 6.6898 | 5.5173 | 4.3888 | -1.8429 | -10.5122 | -12.4082 | 16.0071 | 15.8398 | 15.2837 | 14.9469 | 14.5551 | 13.7929 | 10.9306 | 10.1133 | 9.2245 | 8.3531 | 3.5245 | -3.9684 | -5.5276 | 13.3816 | 13.1796 | 12.348 | 11.7439 | 11.0439 | 9.952 | 7.3724 | 6.3469 | 5.2255 | 4.1408 | -1.8806 | -10.299 | -12.1153
BRAMLEY (FLEE) | CAMBERLEY RESERVE | COVE | MINIMUM HEADROOM | SU 85415 55937 | YES | 2.796 | 12.3708 | 11.7596 | 10.7188 | 10.03 | 9.5667 | 8.7137 | 7.6178 | 6.3912 | 5.2984 | 4.3994 | 0.26469 | -2.7118 | -4.4445 | 13.1743 | 12.6967 | 11.9518 | 11.458 | 11.2804 | 10.7161 | 9.8416 | 8.8437 | 7.9518 | 7.1804 | 3.7906 | 0.69878 | -6.9992 | 12.2035 | 11.6351 | 10.6963 | 10.0576 | 9.7147 | 8.9555 | 7.8871 | 6.678 | 5.6065 | 4.7443 | 0.8902 | -1.9486 | -3.6088
|  | COVE | EE |  |  |  | 12.3708 | 11.7596 | 10.7188 | 10.03 | 9.5667 | 8.7137 | 7.6178 | 6.3912 | 5.2984 | 4.3994 | 0.62898 | -1.7924 | -3.8139 | 13.1743 | 12.6967 | 11.9518 | 11.458 | 11.2804 | 10.7161 | 9.8416 | 8.8437 | 7.9518 | 7.1804 | 3.7906 | 0.69878 | -3.8502 | 12.2035 | 11.6351 | 10.6963 | 10.0576 | 9.7147 | 8.9555 | 7.8871 | 6.678 | 5.6065 | 4.7443 | 1.2627 | -0.97204 | -2.8822
|  | COVE | HT |  |  |  | 12.5759 | 12.0382 | 11.0596 | 10.5137 | 9.8259 | 9.0198 | 7.9535 | 7.1576 | 6.1463 | 5.0984 | 0.26469 | -2.7118 | -4.4445 | 13.3865 | 13.0273 | 12.4069 | 12.1141 | 11.7273 | 11.2824 | 10.5273 | 10.0222 | 9.3049 | 8.5488 | 5.2835 | 3.4386 | 2.3763 | 12.4076 | 11.9157 | 11.0565 | 10.5861 | 9.9861 | 9.28 | 8.2463 | 7.4769 | 6.5137 | 5.5004 | 0.8902 | -1.9486 | -3.6088
|  | COVE | HE |  |  |  | 12.5657 | 12.0473 | 11.0769 | 10.5422 | 9.8637 | 9.0637 | 8.1678 | 7.528 | 6.7249 | 5.8851 | 1.7473 | -0.87204 | -2.2863 | 13.3447 | 12.9498 | 12.2916 | 11.9559 | 11.5151 | 10.9937 | 10.2824 | 9.758 | 9.1182 | 8.4243 | 4.6151 | 1.3171 | -3.0002 | 12.3973 | 11.9188 | 11.0678 | 10.6065 | 10.0106 | 9.3096 | 8.4473 | 7.8514 | 7.1065 | 6.3147 | 2.4239 | -0.01898 | -1.3935
|  | COVE | CF |  |  |  | 12.7167 | 12.3218 | 11.5198 | 11.1249 | 10.6749 | 10.1076 | 9.6106 | 8.9718 | 8.7392 | 8.2147 | 5.2147 | 2.7984 | 0.70143 | 13.4222 | 13.0794 | 12.4896 | 12.1824 | 11.8702 | 11.4508 | 10.9294 | 10.2539 | 9.8998 | 9.2978 | 5.8029 | 1.0376 | -6.9992 | 12.5392 | 12.1749 | 11.48 | 11.1259 | 10.7443 | 10.2514 | 9.7596 | 9.1198 | 8.9361 | 8.4239 | 5.6453 | 3.482 | 1.5922
FAWLEY GSP | COWES & WOOTTON COMMON BSP | COWES | MINIMUM HEADROOM | SP 56113 03074 | YES | 6.495 | 5.3214 | 4.4449 | 3.7765 | 2.799 | 1.6163 | 0.30102 | -1.3653 | -3.151 | -4.9755 | -6.4337 | -12.9847 | -18.6031 | -21.6878 | 9.9469 | 9.3694 | 8.949 | 8.2929 | 7.5255 | 6.6755 | 5.648 | 4.4214 | 3.1643 | 2.2327 | -2.1592 | -6.202 | -15.748 | 5.3827 | 4.552 | 3.9704 | 3.0245 | 1.9276 | 0.7051 | -0.82143 | -2.4949 | -4.1939 | -5.4847 | -11.2122 | -15.9469 | -18.4327
|  | COWES | EE |  |  |  | 5.3214 | 4.4449 | 3.7765 | 2.799 | 1.6163 | 0.30102 | -1.3653 | -3.151 | -4.9755 | -6.4337 | -12.9847 | -17.601 | -21.2388 | 9.9469 | 9.3694 | 8.949 | 8.2929 | 7.5255 | 6.6755 | 5.648 | 4.4214 | 3.1643 | 2.2327 | -2.1592 | -6.202 | -11.8204 | 5.3827 | 4.552 | 3.9704 | 3.0245 | 1.9276 | 0.7051 | -0.82143 | -2.4949 | -4.1939 | -5.4847 | -11.2122 | -15.0816 | -18.1
|  | COWES | HT |  |  |  | 5.6878 | 4.8388 | 4.0092 | 3.0806 | 2.0214 | 1.2582 | -0.21122 | -1.7163 | -3.2786 | -4.8949 | -12.9255 | -18.6031 | -21.6878 | 10.2857 | 9.8194 | 9.3551 | 8.8286 | 8.2224 | 7.8582 | 7.0867 | 6.2622 | 5.3939 | 4.4898 | 0.1102 | -2.6041 | -3.8551 | 5.8153 | 5.0776 | 4.3245 | 3.4673 | 2.4857 | 1.8867 | 0.58673 | -0.7949 | -2.2388 | -3.7316 | -11.0296 | -15.9469 | -18.4327
|  | COWES | HE |  |  |  | 5.6469 | 4.901 | 4.1439 | 3.2929 | 2.2949 | 1.5316 | 0.26531 | -1.0673 | -2.4898 | -3.9755 | -11.1786 | -16.1735 | -18.3745 | 10.2051 | 9.7316 | 9.2418 | 8.6806 | 8.0204 | 7.5735 | 6.7806 | 5.9082 | 4.9643 | 3.9673 | -1.2163 | -5.6867 | -10.6857 | 5.7735 | 5.1112 | 4.4163 | 3.6245 | 2.6949 | 2.1061 | 0.9602 | -0.27755 | -1.602 | -2.9755 | -9.5316 | -13.7398 | -15.501
|  | COWES | CF |  |  |  | 6.0551 | 5.599 | 5.1643 | 4.7459 | 4.2071 | 3.6122 | 3.3806 | 2.7918 | 2.1 | 1.3408 | -4.2459 | -9.301 | -13.7388 | 10.4265 | 10.0867 | 9.7337 | 9.3878 | 8.9429 | 8.4286 | 8.1531 | 7.5684 | 6.9357 | 6.2357 | 1.2071 | -5.4878 | -15.748 | 6.1286 | 5.7163 | 5.2867 | 4.8847 | 4.3612 | 3.7796 | 3.6388 | 3.0561 | 2.4071 | 1.6949 | -3.399 | -7.8367 | -11.748
COWLEY GSP | COWLEY LOCAL (2 X 90) | COWLEY LOCAL | MINIMUM HEADROOM | SP 56113 03074 | YES | 27.141 | -1.2526 | 33.8111 | 32.3713 | 30.9019 | 29.4081 | 27.2815 | 24.505 | 21.453 | 18.3693 | 15.6764 | 4.4315 | 0.39888 | -0.32561 | 4.1148 | 36.8285 | 35.7417 | 34.5866 | 33.4968 | 31.8132 | 29.7234 | 27.3172 | 24.7713 | 22.4999 | 13.2162 | 9.5948 | -5.5521 | -0.69544 | 33.1744 | 32.1428 | 30.956 | 29.6744 | 27.7938 | 25.0254 | 22.2254 | 19.4224 | 17.2305 | 6.8775 | 3.0407 | 2.3519
|  | COWLEY LOCAL | EE |  |  |  | -1.2526 | 33.8111 | 32.3713 | 30.9019 | 29.4081 | 27.2815 | 24.505 | 21.453 | 18.3693 | 15.6764 | 7.0662 | 5.4172 | 5.3397 | 4.1148 | 36.8285 | 35.7417 | 34.5866 | 33.4968 | 31.8132 | 29.7234 | 27.3172 | 24.7713 | 22.4999 | 15.4193 | 11.4581 | 4.7264 | -0.69544 | 33.1744 | 32.1428 | 30.956 | 29.6744 | 27.7938 | 25.0254 | 22.2254 | 19.4224 | 17.2305 | 9.5203 | 7.204 | 7.1101
|  | COWLEY LOCAL | HT |  |  |  | -0.4434 | 34.5887 | 33.5234 | 32.5336 | 31.1081 | 29.4162 | 26.2377 | 23.6856 | 20.903 | 18.4509 | 9.5846 | 5.5081 | 4.8815 | 4.676 | 37.5377 | 36.7162 | 35.9621 | 34.8091 | 33.3428 | 31.3285 | 29.1285 | 26.5897 | 24.3968 | 17.6928 | 15.3734 | 14.8979 | -0.19544 | 33.7244 | 32.7468 | 31.8448 | 30.5193 | 29.0887 | 26.1632 | 23.7826 | 21.1744 | 18.8958 | 11.0081 | 7.3142 | 6.7438
|  | COWLEY LOCAL | HE |  |  |  | -0.68116 | 34.557 | 33.1826 | 31.8826 | 30.5479 | 28.6836 | 26.0938 | 23.2152 | 20.107 | 16.9377 | 4.4315 | 0.39888 | -0.32561 | 4.5158 | 37.356 | 36.3183 | 35.3438 | 34.3795 | 32.905 | 30.953 | 28.6632 | 26.0897 | 23.4346 | 13.2162 | 10.2407 | 4.5019 | -0.29136 | 33.8132 | 32.6805 | 31.6754 | 30.6203 | 29.3111 | 26.8866 | 24.5172 | 21.7948 | 18.7764 | 6.8775 | 3.0407 | 2.3519
|  | COWLEY LOCAL | CF |  |  |  | -0.10871 | 35.554 | 34.6907 | 33.9407 | 33.2183 | 32.204 | 31.1713 | 29.5938 | 27.7224 | 25.705 | 13.507 | 7.1285 | 3.3826 | 4.8076 | 37.8815 | 37.1611 | 36.5734 | 35.9601 | 35.0775 | 34.3111 | 33.006 | 31.4775 | 29.8264 | 18.7601 | 9.5948 | -5.5521 | 0.080065 | 34.5428 | 33.8183 | 33.2764 | 32.6866 | 31.7979 | 31.1213 | 29.8448 | 28.3121 | 26.6897 | 15.5387 | 9.4621 | 5.9254
BRAMLEY (FLEE) | COXMOOR WOOD BSP | COXMOOR WOOD | MINIMUM HEADROOM | SU 78275 50779 | YES | 0.886 | 10.9388 | 10.6327 | 10.3214 | 10.0765 | 9.7735 | 9.451 | 9.002 | 8.8857 | 8.4551 | 8.051 | 6.249 | 4.7806 | 3.8939 | 12.1673 | 11.9735 | 11.7622 | 11.5847 | 11.3612 | 11.1173 | 10.8082 | 10.7612 | 10.4602 | 10.2418 | 8.9939 | 7.5929 | 4.1337 | 11.2071 | 10.9378 | 10.6418 | 10.4082 | 10.1112 | 9.7898 | 9.3551 | 9.3133 | 8.9061 | 8.5592 | 7.0429 | 5.801 | 5.0643
|  | COXMOOR WOOD | EE |  |  |  | 10.9388 | 10.6327 | 10.3214 | 10.0765 | 9.7735 | 9.451 | 9.002 | 8.8857 | 8.4551 | 8.1367 | 6.4184 | 5.1041 | 4.0867 | 12.1673 | 11.9735 | 11.7622 | 11.5847 | 11.3612 | 11.1173 | 10.8082 | 10.7612 | 10.4602 | 10.2418 | 8.9939 | 7.6663 | 5.7949 | 11.2071 | 10.9378 | 10.6418 | 10.4082 | 10.1112 | 9.7898 | 9.3551 | 9.3133 | 8.9061 | 8.6245 | 7.1694 | 6.0816 | 5.2214
|  | COXMOOR WOOD | HT |  |  |  | 11.0286 | 10.7408 | 10.4765 | 10.2735 | 10.0194 | 9.75 | 9.3898 | 8.9612 | 8.5122 | 8.051 | 6.249 | 4.7806 | 3.8939 | 12.2602 | 12.1041 | 11.9541 | 11.8408 | 11.6878 | 11.5204 | 11.3265 | 11.0786 | 10.8133 | 10.5408 | 9.6755 | 8.9929 | 8.6133 | 11.3071 | 11.0653 | 10.8214 | 10.6357 | 10.398 | 10.1367 | 9.8184 | 9.4163 | 8.9949 | 8.5592 | 7.0429 | 5.801 | 5.0643
|  | COXMOOR WOOD | HE |  |  |  | 11.0316 | 10.7561 | 10.5051 | 10.3204 | 10.0867 | 9.8735 | 9.5541 | 9.199 | 8.8255 | 8.4408 | 6.9898 | 5.701 | 5.0163 | 12.2408 | 12.0724 | 11.9061 | 11.7806 | 11.6112 | 11.4551 | 11.2347 | 10.9796 | 10.7071 | 10.4204 | 9.2908 | 7.9582 | 6.2163 | 11.3102 | 11.0745 | 10.8439 | 10.6755 | 10.4531 | 10.2551 | 9.9561 | 9.6163 | 9.2592 | 8.8878 | 7.6735 | 6.6214 | 6.0551
|  | COXMOOR WOOD | CF |  |  |  | 11.1071 | 10.898 | 10.7214 | 10.5806 | 10.4673 | 10.3112 | 10.1653 | 10.0357 | 9.8531 | 9.6633 | 8.7235 | 7.3796 | 6.1551 | 12.2806 | 12.1398 | 12.001 | 11.8786 | 11.7755 | 11.6306 | 11.4694 | 11.3082 | 11.1051 | 10.8878 | 9.7061 | 7.5929 | 4.1337 | 11.3806 | 11.2031 | 11.0408 | 10.902 | 10.7959 | 10.6459 | 10.498 | 10.3724 | 10.1888 | 9.9939 | 9.1571 | 7.9949 | 6.9755
MANNINGTON GSP | LYTCHETT | CREEKMOOR | MINIMUM HEADROOM | SZ 00552 94121 | YES | 1.458 | 15.3044 | 14.8167 | 14.2728 | 13.933 | 13.3299 | 12.6677 | 11.6881 | 10.6085 | 9.5483 | 8.7208 | 4.1585 | 0.75137 | -1.0711 | 19.5606 | 19.1973 | 18.7616 | 18.5401 | 18.0595 | 17.5299 | 16.8473 | 16.0269 | 15.1993 | 14.6126 | 11.434 | 6.8891 | -3.1323 | 16.6483 | 16.2044 | 15.6912 | 15.4054 | 14.8473 | 14.2361 | 13.3432 | 12.3228 | 11.3157 | 10.5728 | 6.6769 | 3.685 | 2.1187
|  | CREEKMOOR | EE |  |  |  | 15.3044 | 14.8167 | 14.2728 | 13.933 | 13.3299 | 12.6677 | 11.6881 | 10.6085 | 9.5483 | 8.7208 | 4.484 | 1.3575 | -0.92312 | 19.5606 | 19.1973 | 18.7616 | 18.5401 | 18.0595 | 17.5299 | 16.8473 | 16.0269 | 15.1993 | 14.6126 | 11.434 | 7.8912 | 2.6554 | 16.6483 | 16.2044 | 15.6912 | 15.4054 | 14.8473 | 14.2361 | 13.3432 | 12.3228 | 11.3157 | 10.5728 | 6.8738 | 4.1636 | 2.1922
|  | CREEKMOOR | HT |  |  |  | 15.5218 | 15.085 | 14.6534 | 14.035 | 13.5034 | 13.185 | 12.285 | 11.3116 | 10.3259 | 9.3218 | 4.1585 | 0.75137 | -1.0711 | 19.8187 | 19.5636 | 19.3136 | 18.9463 | 18.6177 | 18.4922 | 18.0208 | 17.4912 | 16.9442 | 16.3789 | 13.6718 | 12.1616 | 11.3769 | 16.8667 | 16.4799 | 16.0901 | 15.5452 | 15.0534 | 14.7881 | 13.982 | 13.1044 | 12.2126 | 11.3075 | 6.6769 | 3.685 | 2.1187
|  | CREEKMOOR | HE |  |  |  | 15.5157 | 15.1095 | 14.6993 | 14.1595 | 13.6034 | 13.2748 | 12.5208 | 11.6024 | 10.6238 | 9.6034 | 4.6585 | 1.7963 | 0.35749 | 19.7493 | 19.4514 | 19.1381 | 18.7371 | 18.2973 | 18.0718 | 17.5361 | 16.9095 | 16.2554 | 15.5687 | 11.6514 | 7.8269 | 2.885 | 16.8575 | 16.4912 | 16.1157 | 15.6259 | 15.1167 | 14.8361 | 14.1514 | 13.3779 | 12.5922 | 11.7279 | 7.3626 | 4.5473 | 3.2697
|  | CREEKMOOR | CF |  |  |  | 15.7299 | 15.4942 | 15.2503 | 15.0279 | 14.7554 | 14.3718 | 14.3381 | 13.9259 | 13.4514 | 12.9483 | 9.5779 | 6.0616 | 3.3269 | 19.8616 | 19.635 | 19.382 | 19.1371 | 18.8279 | 18.4095 | 18.2401 | 17.783 | 17.2871 | 16.7534 | 12.9095 | 6.8891 | -3.1323 | 17.0534 | 16.8432 | 16.6146 | 16.4044 | 16.1452 | 15.7922 | 15.7769 | 15.4636 | 15.1116 | 14.6442 | 11.4728 | 8.5401 | 6.1524
MINETY GSP | CIRENCESTER BSP | CRICKLADE | MINIMUM HEADROOM | SU 09400 93270 | YES | 2.413 | 2.4395 | 2.2293 | 1.964 | 1.7262 | 1.4232 | 1.0956 | 0.63541 | 0.56296 | 0.12112 | -0.18296 | -1.8095 | -3.037 | -3.7391 | 5.4604 | 5.3869 | 5.2573 | 5.0788 | 4.8512 | 4.6022 | 4.2849 | 4.2237 | 3.9063 | 3.6778 | 2.3818 | 0.81551 | -3.0018 | 2.8686 | 2.6665 | 2.4033 | 2.1778 | 1.8757 | 1.5482 | 1.1002 | 1.1359 | 0.72265 | 0.45735 | -0.91 | -1.9865 | -2.5814
|  | CRICKLADE | EE |  |  |  | 2.4395 | 2.2293 | 1.964 | 1.7262 | 1.4232 | 1.0956 | 0.63541 | 0.56296 | 0.12112 | -0.18296 | -1.8095 | -2.8268 | -3.5564 | 5.4604 | 5.3869 | 5.2573 | 5.0788 | 4.8512 | 4.6022 | 4.2849 | 4.2237 | 3.9063 | 3.6778 | 2.3818 | 1.088 | -0.86204 | 2.8686 | 2.6665 | 2.4033 | 2.1778 | 1.8757 | 1.5482 | 1.1002 | 1.1359 | 0.72265 | 0.45735 | -0.91 | -1.7967 | -2.4263
|  | CRICKLADE | HT |  |  |  | 2.5538 | 2.3721 | 2.1732 | 1.9915 | 1.765 | 1.513 | 1.1793 | 0.76194 | 0.32418 | -0.13602 | -1.786 | -3.037 | -3.7391 | 5.5155 | 5.4614 | 5.4002 | 5.3451 | 5.2176 | 5.0543 | 4.8686 | 4.6216 | 4.3604 | 4.088 | 3.2308 | 2.6145 | 2.2971 | 2.9951 | 2.8278 | 2.6369 | 2.4665 | 2.2441 | 1.9971 | 1.7043 | 1.3094 | 0.8951 | 0.45837 | -0.87531 | -1.9865 | -2.5814
|  | CRICKLADE | HE |  |  |  | 2.5528 | 2.3823 | 2.1936 | 2.0252 | 1.8119 | 1.5783 | 1.2997 | 0.93643 | 0.55071 | 0.15276 | -1.2677 | -2.2748 | -2.7799 | 5.5063 | 5.4471 | 5.3808 | 5.2982 | 5.1359 | 4.9543 | 4.7584 | 4.4941 | 4.2124 | 3.9135 | 2.7063 | 1.388 | -0.48143 | 2.9931 | 2.8349 | 2.6543 | 2.4931 | 2.2859 | 2.0584 | 1.8124 | 1.4635 | 1.0941 | 0.71041 | -0.40286 | -1.2855 | -1.6906
|  | CRICKLADE | CF |  |  |  | 2.6191 | 2.5007 | 2.3691 | 2.2242 | 2.116 | 1.9558 | 1.7854 | 1.6323 | 1.4232 | 1.2048 | 0.28643 | -0.88092 | -1.9554 | 5.5329 | 5.489 | 5.439 | 5.3829 | 5.2757 | 5.1206 | 4.9451 | 4.7655 | 4.5492 | 4.3094 | 3.0431 | 0.81551 | -3.0018 | 3.0502 | 2.941 | 2.8094 | 2.6635 | 2.5604 | 2.4012 | 2.2288 | 2.088 | 1.8788 | 1.6573 | 0.88286 | -0.12531 | -1.009
MELKSHAM GSP | FROME BSP | CROCKERTON | MINIMUM HEADROOM | ST 87736 43371 | YES | 1.109 | 1.4147 | 1.128 | 0.76265 | 0.26469 | 0.095306 | -0.35163 | -1.0292 | -1.7833 | -2.5414 | -3.0822 | -6.0476 | -8.37 | -9.7353 | 3.6927 | 3.56 | 3.4029 | 3.0886 | 2.9784 | 2.6682 | 2.258 | 1.7671 | 1.261 | 0.88551 | -1.289 | -3.739 | -9.738 | 1.0188 | 0.68816 | 0.32286 | -0.16898 | -0.31388 | -0.75163 | -1.3843 | -2.0945 | -2.8047 | -3.3047 | -5.9047 | -7.8843 | -8.9833
|  | CROCKERTON | EE |  |  |  | 1.4147 | 1.128 | 0.76265 | 0.26469 | 0.095306 | -0.35163 | -1.0292 | -1.7833 | -2.5414 | -3.0822 | -5.9771 | -7.9476 | -9.3792 | 3.6927 | 3.56 | 3.4029 | 3.0886 | 2.9784 | 2.6682 | 2.258 | 1.7671 | 1.261 | 0.88551 | -1.289 | -3.4533 | -6.5839 | 1.0188 | 0.68816 | 0.32286 | -0.16898 | -0.31388 | -0.75163 | -1.3843 | -2.0945 | -2.8047 | -3.3047 | -5.8853 | -7.5037 | -8.6843
|  | CROCKERTON | HT |  |  |  | 1.5647 | 1.3371 | 1.0004 | 0.59224 | 0.21469 | -0.17204 | -0.81082 | -1.1394 | -1.7894 | -2.4669 | -6.0476 | -8.37 | -9.7353 | 3.7865 | 3.6927 | 3.5722 | 3.3937 | 3.2447 | 3.0263 | 2.6876 | 2.5457 | 2.1773 | 1.7906 | -0.072653 | -1.1227 | -1.7431 | 1.1871 | 0.9249 | 0.61878 | 0.24429 | -0.12102 | -0.50367 | -1.1037 | -1.3731 | -1.9873 | -2.6312 | -5.9047 | -7.8843 | -8.9833
|  | CROCKERTON | HE |  |  |  | 1.5524 | 1.3596 | 1.0657 | 0.71265 | 0.32898 | -0.055714 | -0.60469 | -0.84857 | -1.4098 | -2.0353 | -5.2741 | -7.2322 | -8.2037 | 3.7763 | 3.6773 | 3.558 | 3.3773 | 3.1416 | 2.862 | 2.508 | 2.3549 | 1.9712 | 1.5692 | -0.88796 | -3.1431 | -6.0859 | 1.1851 | 0.94224 | 0.67592 | 0.34224 | -0.02102 | -0.39449 | -0.91592 | -1.1118 | -1.6455 | -2.2006 | -5.1445 | -6.8261 | -7.6037
|  | CROCKERTON | CF |  |  |  | 1.6851 | 1.5596 | 1.3984 | 1.1637 | 1.0004 | 0.78204 | 0.52796 | 0.22184 | 0.19837 | -0.10265 | -2.2955 | -4.6037 | -6.5751 | 3.8355 | 3.7722 | 3.709 | 3.5784 | 3.4457 | 3.2304 | 2.9722 | 2.6671 | 2.56 | 2.2416 | -0.11245 | -3.739 | -9.738 | 1.2922 | 1.1341 | 0.98102 | 0.75347 | 0.58612 | 0.36878 | 0.11673 | -0.19041 | -0.18939 | -0.48735 | -2.5312 | -4.5078 | -6.3027
BRAMLEY (FLEE) | PYESTOCK BSP | CROOKHAM | MINIMUM HEADROOM | SU 81702 53403 | YES | 0.542 | 17.4643 | 17.1184 | 16.6612 | 16.5714 | 16.1439 | 15.6714 | 14.8327 | 13.9051 | 12.9724 | 12.3439 | 8.3959 | 5.4949 | 3.801 | 18.7898 | 18.5041 | 18.1143 | 18.0653 | 17.6939 | 17.299 | 16.7347 | 16.0776 | 15.4051 | 14.9653 | 12.4602 | 8.6867 | 0.23265 | 16.9092 | 16.5469 | 16.0551 | 16.0643 | 15.6276 | 15.1602 | 14.3857 | 13.5071 | 12.6296 | 12.0959 | 8.7551 | 6.2316 | 4.7724
|  | CROOKHAM | EE |  |  |  | 17.4643 | 17.1184 | 16.6612 | 16.5714 | 16.1439 | 15.6714 | 14.8327 | 13.9051 | 12.9724 | 12.3439 | 8.9622 | 6.2827 | 4.1663 | 18.7898 | 18.5041 | 18.1143 | 18.0653 | 17.6939 | 17.299 | 16.7347 | 16.0776 | 15.4051 | 14.9653 | 12.4602 | 9.548 | 5.0755 | 16.9092 | 16.5469 | 16.0551 | 16.0643 | 15.6276 | 15.1602 | 14.3857 | 13.5071 | 12.6296 | 12.0959 | 9.2184 | 6.9102 | 5.0653
|  | CROOKHAM | HT |  |  |  | 17.6459 | 17.352 | 17.0286 | 16.6459 | 16.2245 | 16.1347 | 15.3449 | 14.5082 | 13.6418 | 12.7541 | 8.3959 | 5.4949 | 3.801 | 19.0194 | 18.8337 | 18.6316 | 18.3704 | 18.0776 | 18.1122 | 17.7102 | 17.2592 | 16.7776 | 16.2745 | 14.0224 | 12.7582 | 12.0571 | 17.1306 | 16.85 | 16.5378 | 16.1602 | 15.7286 | 15.7224 | 15.0184 | 14.2582 | 13.4653 | 12.651 | 8.7551 | 6.2316 | 4.7724
|  | CROOKHAM | HE |  |  |  | 17.6592 | 17.4 | 17.1071 | 16.7633 | 16.3816 | 16.3357 | 15.7378 | 15.0837 | 14.3939 | 13.6898 | 9.9561 | 7.1847 | 5.7929 | 18.9765 | 18.7561 | 18.5122 | 18.2133 | 17.8776 | 17.8684 | 17.4439 | 16.9653 | 16.4459 | 15.898 | 12.8337 | 9.8367 | 5.6337 | 17.1367 | 16.8837 | 16.599 | 16.2449 | 15.8429 | 15.8867 | 15.3367 | 14.7255 | 14.0796 | 13.4153 | 10.0469 | 7.6939 | 6.5276
|  | CROOKHAM | CF |  |  |  | 17.7939 | 17.652 | 17.452 | 17.2847 | 17.0571 | 16.7959 | 16.8755 | 16.599 | 16.2837 | 15.9531 | 13.4316 | 10.6857 | 8.0388 | 19.0357 | 18.8633 | 18.6255 | 18.4173 | 18.152 | 17.8398 | 17.8204 | 17.448 | 17.0449 | 16.6133 | 13.4704 | 8.6867 | 0.23265 | 17.2612 | 17.1143 | 16.8776 | 16.6959 | 16.4347 | 16.1541 | 16.3316 | 16.0388 | 15.7214 | 15.3857 | 12.998 | 10.6214 | 8.4204
BRAMLEY (FLEE) | CAMBERLEY MAIN | CROWTHORNE | MINIMUM HEADROOM | SU 84470 64352 | YES | 1.891 | 6.1683 | 4.5591 | 3.5979 | 2.2499 | 0.76827 | -0.8501 | -2.4205 | -4.0379 | -5.5623 | -6.6991 | -13.1521 | -17.6185 | -20.0654 | 10.4662 | 9.5091 | 9.0132 | 8.1887 | 7.2968 | 6.2672 | 5.2274 | 4.0897 | 2.9632 | 2.1723 | -2.0093 | -6.7736 | -17.8726 | 6.4866 | 5.1305 | 4.4172 | 3.2713 | 2.005 | 0.55908 | -0.89092 | -2.4246 | -3.9032 | -4.944 | -10.5215 | -14.5083 | -16.6113
|  | CROWTHORNE | EE |  |  |  | 6.1683 | 4.5591 | 3.5979 | 2.2499 | 0.76827 | -0.8501 | -2.4205 | -4.0379 | -5.5623 | -6.6991 | -12.395 | -16.4052 | -19.4266 | 10.4662 | 9.5091 | 9.0132 | 8.1887 | 7.2968 | 6.2672 | 5.2274 | 4.0897 | 2.9632 | 2.1723 | -2.0093 | -6.1042 | -11.9511 | 6.4866 | 5.1305 | 4.4172 | 3.2713 | 2.005 | 0.55908 | -0.89092 | -2.4246 | -3.9032 | -4.944 | -9.9205 | -13.4664 | -16.0909
|  | CROWTHORNE | HT |  |  |  | 6.4468 | 4.8274 | 3.6744 | 2.3356 | 1.1642 | -0.28071 | -1.746 | -3.2368 | -4.7154 | -6.2011 | -13.1521 | -17.6185 | -20.0654 | 10.7866 | 9.9438 | 9.3448 | 8.6346 | 8.1285 | 7.3407 | 6.5479 | 5.6877 | 4.7897 | 3.8907 | 0.12949 | -1.8981 | -2.945 | 6.8101 | 5.4917 | 4.5397 | 3.4162 | 2.5315 | 1.2509 | -0.060306 | -1.4338 | -2.8328 | -4.2368 | -10.5215 | -14.5083 | -16.6113
|  | CROWTHORNE | HE |  |  |  | 6.4734 | 5.0274 | 3.8489 | 2.5764 | 1.5836 | 0.155 | -1.0685 | -2.2909 | -3.4705 | -4.695 | -10.8899 | -15.0001 | -17.0338 | 10.7305 | 9.9213 | 9.2101 | 8.4458 | 7.9999 | 7.1254 | 6.3162 | 5.4499 | 4.5621 | 3.6172 | -1.3817 | -5.6542 | -11.1174 | 6.8223 | 5.657 | 4.6652 | 3.5907 | 2.9009 | 1.6407 | 0.53357 | -0.60418 | -1.7409 | -2.9215 | -8.6542 | -12.2521 | -14.0062
|  | CROWTHORNE | CF |  |  |  | 6.8979 | 5.7489 | 4.9632 | 4.0958 | 3.1387 | 2.5815 | 1.9285 | 1.255 | 0.56929 | -0.145 | -5.096 | -9.5205 | -13.5542 | 10.9295 | 10.2193 | 9.6887 | 9.0897 | 8.4489 | 8.1366 | 7.5223 | 6.8417 | 6.1274 | 5.3652 | 0.051939 | -6.7736 | -17.8726 | 7.1642 | 6.2152 | 5.5591 | 4.8132 | 3.9917 | 3.6581 | 3.0672 | 2.4295 | 1.7703 | 1.0785 | -3.6909 | -7.5623 | -10.9511
COWLEY GSP |  | CULHAM | MINIMUM HEADROOM | SU 50731 95053 | YES | 0 | 33.302 | 33.152 | 33.152 | 33.152 | 33.152 | 33.152 | 33.152 | 33.1449 | 33.1449 | 33.1449 | 33.1449 | 33.1449 | 33.1449 | 32.5122 | 32.3286 | 32.3286 | 32.3286 | 32.3286 | 32.3286 | 32.3286 | 32.3214 | 32.3214 | 32.3214 | 32.3214 | 32.3214 | 32.3204 | 32.9684 | 32.8153 | 32.8153 | 32.8153 | 32.8153 | 32.8153 | 32.8153 | 32.8082 | 32.8082 | 32.8082 | 32.8082 | 32.8082 | 32.8082
|  | CULHAM | EE |  |  |  | 33.302 | 33.152 | 33.152 | 33.152 | 33.152 | 33.152 | 33.152 | 33.1449 | 33.1449 | 33.1449 | 33.1449 | 33.1449 | 33.1449 | 32.5122 | 32.3286 | 32.3286 | 32.3286 | 32.3286 | 32.3286 | 32.3286 | 32.3214 | 32.3214 | 32.3214 | 32.3214 | 32.3214 | 32.3214 | 32.9684 | 32.8153 | 32.8153 | 32.8153 | 32.8153 | 32.8153 | 32.8153 | 32.8082 | 32.8082 | 32.8082 | 32.8082 | 32.8082 | 32.8082
|  | CULHAM | HT |  |  |  | 33.302 | 33.152 | 33.152 | 33.152 | 33.152 | 33.152 | 33.152 | 33.152 | 33.152 | 33.152 | 33.1449 | 33.1449 | 33.1449 | 32.5122 | 32.3286 | 32.3286 | 32.3286 | 32.3286 | 32.3286 | 32.3286 | 32.3286 | 32.3286 | 32.3286 | 32.3214 | 32.3214 | 32.3214 | 32.9684 | 32.8153 | 32.8153 | 32.8153 | 32.8153 | 32.8153 | 32.8153 | 32.8153 | 32.8153 | 32.8153 | 32.8082 | 32.8082 | 32.8082
|  | CULHAM | HE |  |  |  | 33.302 | 33.152 | 33.152 | 33.152 | 33.152 | 33.152 | 33.152 | 33.152 | 33.152 | 33.152 | 33.1449 | 33.1449 | 33.1449 | 32.5122 | 32.3286 | 32.3286 | 32.3286 | 32.3286 | 32.3286 | 32.3286 | 32.3286 | 32.3286 | 32.3286 | 32.3214 | 32.3214 | 32.3214 | 32.9684 | 32.8153 | 32.8153 | 32.8153 | 32.8153 | 32.8153 | 32.8153 | 32.8153 | 32.8153 | 32.8153 | 32.8082 | 32.8082 | 32.8082
|  | CULHAM | CF |  |  |  | 33.3031 | 33.1531 | 33.1531 | 33.1531 | 33.1531 | 33.1531 | 33.1531 | 33.1531 | 33.1531 | 33.1531 | 33.1459 | 33.1459 | 33.1459 | 32.5122 | 32.3286 | 32.3286 | 32.3286 | 32.3286 | 32.3286 | 32.3286 | 32.3286 | 32.3286 | 32.3286 | 32.3214 | 32.3214 | 32.3204 | 32.9694 | 32.8173 | 32.8173 | 32.8173 | 32.8173 | 32.8173 | 32.8173 | 32.8173 | 32.8173 | 32.8173 | 32.8102 | 32.8102 | 32.8102
EALING GSP | EALING 22kV | DEAN GARDENS | MINIMUM HEADROOM | TQ 16546 80368 | YES | 3.053 | 8.758 | 8.4396 | 8.0713 | 7.8243 | 7.5621 | 7.2794 | 7.0672 | 6.7774 | 6.4896 | 6.2825 | 5.6468 | 5.1478 | 5.1886 | 9.4857 | 9.348 | 9.0663 | 8.8245 | 8.5367 | 8.2245 | 7.9265 | 7.552 | 7.1592 | 6.8061 | 3.7459 | -2.9622 | -16.05 | 8.6616 | 8.3922 | 8.0739 | 7.8443 | 7.6004 | 7.3361 | 7.1361 | 6.8657 | 6.5922 | 6.3943 | 5.7922 | 5.3392 | 5.3749
|  | DEAN GARDENS | EE |  |  |  | 8.758 | 8.4396 | 8.0713 | 7.8243 | 7.5621 | 7.2794 | 7.0672 | 6.7774 | 6.4896 | 6.2825 | 5.6468 | 5.3519 | 5.4366 | 9.4857 | 9.348 | 9.0663 | 8.8245 | 8.5367 | 8.2245 | 7.9265 | 7.552 | 7.1592 | 6.8061 | 4.5102 | 0.98469 | -5.4367 | 8.6616 | 8.3922 | 8.0739 | 7.8443 | 7.6004 | 7.3361 | 7.1361 | 6.8657 | 6.5922 | 6.3943 | 5.7922 | 5.529 | 5.5882
|  | DEAN GARDENS | HT |  |  |  | 8.8437 | 8.5621 | 8.2182 | 8.0356 | 7.8284 | 7.6294 | 7.4611 | 7.2539 | 7.0356 | 6.8437 | 5.7876 | 5.1478 | 5.1886 | 9.5357 | 9.452 | 9.3633 | 9.2684 | 9.1357 | 9.0071 | 8.8847 | 8.7245 | 8.5571 | 8.4102 | 7.6173 | 7.151 | 7.0684 | 8.7433 | 8.5065 | 8.2147 | 8.0463 | 7.8524 | 7.6657 | 7.5106 | 7.3188 | 7.1137 | 6.9371 | 5.9392 | 5.3392 | 5.3749
|  | DEAN GARDENS | HE |  |  |  | 8.8356 | 8.5611 | 8.2274 | 8.056 | 7.8621 | 7.6845 | 7.5468 | 7.3713 | 7.1876 | 7.0356 | 6.3692 | 6.0907 | 6.106 | 9.5051 | 9.3939 | 9.1939 | 9.0061 | 8.7755 | 8.5418 | 8.2959 | 8.0082 | 7.6898 | 7.3755 | 5.002 | 1.3898 | -5.0265 | 8.7331 | 8.5045 | 8.2208 | 8.0637 | 7.8841 | 7.7147 | 7.5851 | 7.4218 | 7.2524 | 7.1116 | 6.4882 | 6.23 | 6.2463
|  | DEAN GARDENS | CF |  |  |  | 8.8856 | 8.656 | 8.3937 | 8.2774 | 8.1437 | 8.006 | 7.958 | 7.8672 | 7.7754 | 7.6713 | 7.0641 | 6.4182 | 5.8662 | 9.5163 | 9.4092 | 9.2276 | 9.0327 | 8.7969 | 8.5071 | 8.2031 | 7.8378 | 7.452 | 7.0255 | 3.7459 | -2.9622 | -16.05 | 8.781 | 8.5933 | 8.3769 | 8.2667 | 8.1443 | 8.0157 | 7.9688 | 7.8851 | 7.7994 | 7.7004 | 7.1239 | 6.5198 | 6.0137
COWLEY GSP | YARNTON BSP | DEDDINGTON | MINIMUM HEADROOM | SP 46729 30325 | YES | 0.334 | -0.010204 | -0.11429 | -0.25408 | -0.37551 | -0.54184 | -0.72347 | -0.90714 | -1.1816 | -1.452 | -1.6061 | -2.3643 | -2.848 | -3.2235 | 1.6643 | 1.5867 | 1.4837 | 1.3959 | 1.2673 | 1.1276 | 0.99592 | 0.79592 | 0.58469 | 0.47857 | -0.085714 | -0.80306 | -2.5 | 0.36735 | 0.26633 | 0.12959 | 0.015306 | -0.14592 | -0.32143 | -0.49592 | -0.75816 | -1.0194 | -1.1612 | -1.8194 | -2.2357 | -2.5541
|  | DEDDINGTON | EE |  |  |  | -0.010204 | -0.11429 | -0.25408 | -0.37551 | -0.54184 | -0.72347 | -0.90714 | -1.1816 | -1.452 | -1.6061 | -2.3643 | -2.802 | -3.1286 | 1.6643 | 1.5867 | 1.4837 | 1.3959 | 1.2673 | 1.1276 | 0.99592 | 0.79592 | 0.58469 | 0.47857 | -0.085714 | -0.65714 | -1.5276 | 0.36735 | 0.26633 | 0.12959 | 0.015306 | -0.14592 | -0.32143 | -0.49592 | -0.75816 | -1.0194 | -1.1612 | -1.8194 | -2.1898 | -2.4694
|  | DEDDINGTON | HT |  |  |  | 0.063265 | -0.027551 | -0.12041 | -0.23163 | -0.35102 | -0.45 | -0.63776 | -0.85408 | -1.0786 | -1.2582 | -2.2837 | -2.848 | -3.2235 | 1.7337 | 1.6796 | 1.6194 | 1.552 | 1.4673 | 1.4082 | 1.2918 | 1.1592 | 1.0133 | 0.90714 | 0.29286 | 0.028571 | -0.15306 | 0.45 | 0.36429 | 0.27755 | 0.17347 | 0.055102 | -0.037755 | -0.21327 | -0.42143 | -0.63571 | -0.79796 | -1.75 | -2.2357 | -2.5541
|  | DEDDINGTON | HE |  |  |  | 0.061224 | -0.026531 | -0.11633 | -0.21837 | -0.33673 | -0.42653 | -0.59796 | -0.79388 | -0.99796 | -1.1592 | -2.1592 | -2.5847 | -2.8214 | 1.7214 | 1.6582 | 1.5949 | 1.5184 | 1.4245 | 1.3582 | 1.2357 | 1.099 | 0.9449 | 0.83061 | 0.042857 | -0.53469 | -1.3612 | 0.44796 | 0.36327 | 0.28163 | 0.18367 | 0.068367 | -0.017347 | -0.17857 | -0.36633 | -0.56429 | -0.70918 | -1.6296 | -1.9867 | -2.1857
|  | DEDDINGTON | CF |  |  |  | 0.089796 | 0.018367 | -0.066327 | -0.12959 | -0.20714 | -0.29592 | -0.39694 | -0.47755 | -0.60102 | -0.73469 | -1.4357 | -2.0051 | -2.5235 | 1.7367 | 1.6816 | 1.6133 | 1.5582 | 1.4929 | 1.4092 | 1.3112 | 1.2306 | 1.1163 | 0.9898 | 0.22449 | -0.80306 | -2.5 | 0.47449 | 0.40714 | 0.32143 | 0.26531 | 0.1898 | 0.10306 | 0.0010204 | -0.072449 | -0.19388 | -0.32041 | -0.99286 | -1.5184 | -1.9531
IVER 132KV | DENHAM | DENHAM AVENUE | MINIMUM HEADROOM | TQ 03761 86587 | YES | 1.63 | 3.1245 | 2.9551 | 2.7214 | 2.502 | 2.2265 | 26.7337 | 26.2622 | 26.1041 | 25.6378 | 25.2929 | 23.4592 | 21.9449 | 21.1357 | 4.3735 | 4.2582 | 4.102 | 3.9316 | 3.7296 | 26.6173 | 26.3378 | 26.1449 | 25.8541 | 25.6194 | 24.4082 | 22.7347 | 18.6643 | 3.5041 | 3.3388 | 3.1153 | 2.9061 | 2.6449 | 26.1592 | 25.7184 | 25.5867 | 25.15 | 24.8378 | 23.2245 | 21.9612 | 21.3296
|  | DENHAM AVENUE | EE |  |  |  | 3.1245 | 2.9551 | 2.7214 | 2.502 | 2.2265 | 26.7337 | 26.2622 | 26.1041 | 25.6378 | 25.2929 | 23.549 | 22.2398 | 21.3102 | 4.3735 | 4.2582 | 4.102 | 3.9316 | 3.7296 | 26.6173 | 26.3378 | 26.1449 | 25.8541 | 25.6194 | 24.4082 | 23.0194 | 20.9031 | 3.5041 | 3.3388 | 3.1153 | 2.9061 | 2.6449 | 26.1592 | 25.7184 | 25.5867 | 25.15 | 24.8378 | 23.2745 | 22.2276 | 21.4735
|  | DENHAM AVENUE | HT |  |  |  | 3.2143 | 3.0704 | 2.9082 | 2.7541 | 2.549 | 27.1255 | 26.7663 | 26.3316 | 25.8755 | 25.402 | 23.4592 | 21.9449 | 21.1357 | 4.4439 | 4.3929 | 4.3061 | 4.1949 | 4.0602 | 27.0071 | 26.8204 | 26.5847 | 26.3316 | 26.0663 | 25.0031 | 24.4684 | 24.1316 | 3.6163 | 3.4755 | 3.3092 | 3.1633 | 2.9673 | 26.552 | 26.2255 | 25.8204 | 25.398 | 24.9571 | 23.2245 | 21.9612 | 21.3296
|  | DENHAM AVENUE | HE |  |  |  | 3.2133 | 3.0816 | 2.9276 | 2.7837 | 2.5888 | 27.1786 | 26.8776 | 26.498 | 26.0939 | 25.6735 | 24.0337 | 22.6388 | 22.0357 | 4.4327 | 4.3714 | 4.2653 | 4.1408 | 3.9878 | 26.9143 | 26.7051 | 26.4337 | 26.1449 | 25.8367 | 24.5582 | 23.1582 | 21.1673 | 3.6122 | 3.4816 | 3.3265 | 3.1847 | 3.002 | 26.599 | 26.3255 | 25.9694 | 25.5898 | 25.199 | 23.6541 | 22.4786 | 21.9286
|  | DENHAM AVENUE | CF |  |  |  | 3.2898 | 3.2255 | 3.1367 | 3.0296 | 2.9449 | 27.6214 | 27.4776 | 27.3378 | 27.148 | 26.948 | 25.9173 | 24.5469 | 23.2265 | 4.4704 | 4.4357 | 4.3847 | 4.3316 | 4.2541 | 27.2347 | 27.0959 | 26.9184 | 26.6888 | 26.4398 | 25.1061 | 22.7347 | 18.6643 | 3.6847 | 3.6133 | 3.5163 | 3.4102 | 3.3316 | 27.0112 | 26.8755 | 26.7408 | 26.5592 | 26.3673 | 25.4173 | 24.1133 | 22.9031
MELKSHAM GSP | NORRINGTON | DEVIZES | MINIMUM HEADROOM | SU 00106 60986 | YES | 3.925 | -3.0945 | 14.3013 | 13.1666 | 12.2748 | 11.3176 | 10.3717 | 9.1687 | 7.8819 | 6.584 | 5.6911 | 0.886 | -2.8834 | -5.066 | 1.9127 | 18.4105 | 17.5544 | 16.9401 | 16.2738 | 15.5891 | 14.7533 | 13.8105 | 12.8523 | 12.2125 | 8.6799 | 4.7942 | -5.4732 | -2.9246 | 14.034 | 12.9972 | 12.3207 | 11.4533 | 10.5809 | 9.4911 | 8.2911 | 7.0829 | 6.3115 | 2.1452 | -1.1916 | -3.0579
|  | DEVIZES | EE |  |  |  | -3.0945 | 14.3013 | 13.1666 | 12.2748 | 11.3176 | 10.3717 | 9.1687 | 7.8819 | 6.584 | 5.6911 | 0.9911 | -2.1518 | -4.5813 | 1.9127 | 18.4105 | 17.5544 | 16.9401 | 16.2738 | 15.5891 | 14.7533 | 13.8105 | 12.8523 | 12.2125 | 8.6799 | 5.0564 | -0.27522 | -2.9246 | 14.034 | 12.9972 | 12.3207 | 11.4533 | 10.5809 | 9.4911 | 8.2911 | 7.0829 | 6.3115 | 2.1921 | -0.54359 | -2.6477
|  | DEVIZES | HT |  |  |  | -2.821 | 14.685 | 13.7401 | 12.585 | 11.686 | 11.185 | 10.1227 | 9.0258 | 7.9523 | 6.8319 | 0.886 | -2.8834 | -5.066 | 2.1689 | 18.8268 | 18.1911 | 17.4248 | 16.9033 | 16.6829 | 16.1003 | 15.4748 | 14.8421 | 14.1758 | 10.8748 | 9.037 | 8.0901 | -2.5889 | 14.4789 | 13.6717 | 12.6605 | 11.8636 | 11.537 | 10.585 | 9.6044 | 8.6238 | 7.5829 | 2.1452 | -1.1916 | -3.0579
|  | DEVIZES | HE |  |  |  | -2.818 | 14.7176 | 13.8054 | 12.685 | 11.8513 | 11.4176 | 10.5258 | 9.587 | 8.6146 | 7.6738 | 2.6452 | -0.49563 | -2.0222 | 2.125 | 18.7472 | 18.0646 | 17.2584 | 16.7044 | 16.4421 | 15.8421 | 15.1778 | 14.4717 | 13.7564 | 9.6738 | 6.0033 | 0.96865 | -2.593 | 14.5033 | 13.7238 | 12.7493 | 12.0105 | 11.736 | 10.9401 | 10.1013 | 9.2278 | 8.3503 | 3.7482 | 0.97069 | -0.32216
|  | DEVIZES | CF |  |  |  | -2.6333 | 15.0523 | 14.286 | 13.4207 | 12.8666 | 12.335 | 12.2289 | 11.8217 | 11.3554 | 10.8666 | 7.436 | 3.9911 | 0.84722 | 2.2178 | 18.9054 | 18.2758 | 17.5799 | 17.1666 | 16.7156 | 16.5146 | 16.0289 | 15.4972 | 14.9278 | 10.8493 | 4.7942 | -5.4732 | -2.4256 | 14.7952 | 14.1217 | 13.3829 | 12.8809 | 12.388 | 12.3819 | 11.986 | 11.5391 | 11.0676 | 7.9013 | 4.9207 | 2.1636
MINETY GSP | TOOTHILL BSP | DORCAN SOUTH | MINIMUM HEADROOM | SU 19288 83540 | YES | 6.595 | 12.6692 | 12.5896 | 12.4855 | 12.3886 | 12.1988 | 11.9304 | 11.6549 | 11.2947 | 10.9192 | 10.6784 | 9.8529 | 9.4059 | 9.2947 | 10.9645 | 10.9033 | 10.8308 | 10.7543 | 10.5798 | 10.3369 | 10.1196 | 9.8869 | 9.6094 | 9.391 | 8.5216 | 7.2145 | 4.1788 | 12.0661 | 11.9937 | 11.9069 | 11.8212 | 11.6376 | 11.3722 | 11.1335 | 10.8549 | 10.5386 | 10.2967 | 9.5865 | 9.2671 | 9.1335
|  | DORCAN SOUTH | EE |  |  |  | 12.6692 | 12.5896 | 12.4855 | 12.3886 | 12.2396 | 11.9549 | 11.6794 | 11.2947 | 10.9192 | 10.6784 | 9.8529 | 9.4355 | 9.4824 | 10.9645 | 10.9033 | 10.8308 | 10.7543 | 10.6645 | 10.4073 | 10.1869 | 9.9033 | 9.6094 | 9.391 | 8.5216 | 7.5992 | 6.2186 | 12.0661 | 11.9937 | 11.9069 | 11.8212 | 11.711 | 11.4396 | 11.1824 | 10.8549 | 10.5386 | 10.2967 | 9.5865 | 9.309 | 9.2845
|  | DORCAN SOUTH | HT |  |  |  | 12.7049 | 12.6294 | 12.5549 | 12.461 | 12.1988 | 11.9304 | 11.6549 | 11.3498 | 11.0671 | 10.859 | 9.909 | 9.4059 | 9.2947 | 11.0043 | 10.9522 | 10.8961 | 10.8318 | 10.5798 | 10.3369 | 10.1196 | 9.8869 | 9.6716 | 9.5349 | 8.9716 | 8.7012 | 8.5859 | 12.1039 | 12.0457 | 11.9743 | 11.8957 | 11.6376 | 11.3722 | 11.1335 | 10.8682 | 10.611 | 10.4314 | 9.6488 | 9.2671 | 9.1335
|  | DORCAN SOUTH | HE |  |  |  | 12.7049 | 12.6437 | 12.5733 | 12.4855 | 12.3876 | 12.1457 | 11.9059 | 11.5978 | 11.2906 | 11.0324 | 10.1702 | 9.8396 | 9.7151 | 11.0012 | 10.9553 | 10.9022 | 10.838 | 10.7665 | 10.5339 | 10.3441 | 10.0941 | 9.8441 | 9.639 | 8.8227 | 7.9747 | 6.5512 | 12.1029 | 12.0529 | 11.9886 | 11.9171 | 11.8324 | 11.5947 | 11.3794 | 11.0957 | 10.808 | 10.5692 | 9.7722 | 9.5049 | 9.361
|  | DORCAN SOUTH | CF |  |  |  | 12.7549 | 12.7212 | 12.6824 | 12.6508 | 12.61 | 12.5559 | 12.4202 | 12.2641 | 12.0631 | 11.8784 | 10.9967 | 10.3233 | 9.7406 | 11.0318 | 11.0063 | 10.9716 | 10.942 | 10.9022 | 10.8553 | 10.7278 | 10.5624 | 10.3329 | 10.1022 | 8.8563 | 7.2145 | 4.1788 | 12.1406 | 12.11 | 12.0722 | 12.0416 | 11.9967 | 11.9427 | 11.8131 | 11.6539 | 11.4549 | 11.2671 | 10.4151 | 9.8631 | 9.4437
CHICKERELL GSP | CHICKERELL BSP | DORCHESTER | MINIMUM HEADROOM | SY 69113 90401 | YES | 2.787 | 19.5141 | 18.7641 | 17.7182 | 16.9855 | 16.0998 | 14.9488 | 13.5294 | 11.7957 | 10.1202 | 8.6988 | 0.78857 | -3.8135 | -5.3553 | 24.1559 | 23.5784 | 22.858 | 22.3753 | 21.7151 | 20.9916 | 20.0794 | 18.8896 | 17.71 | 16.7376 | 11.211 | 8.1773 | -1.541 | 19.961 | 19.2447 | 18.3151 | 17.6692 | 16.8324 | 15.9324 | 14.6794 | 13.2508 | 11.8447 | 10.7069 | 3.46 | -0.4002 | -1.4624
|  | DORCHESTER | EE |  |  |  | 19.5141 | 18.7641 | 17.7182 | 16.9855 | 16.0998 | 14.9488 | 13.5294 | 11.7957 | 10.1202 | 8.6988 | 2.7273 | -0.89204 | -3.939 | 24.1559 | 23.5784 | 22.858 | 22.3753 | 21.7151 | 20.9916 | 20.0794 | 18.8896 | 17.71 | 16.7376 | 12.6478 | 8.8263 | 3.4896 | 19.961 | 19.2447 | 18.3151 | 17.6692 | 16.8324 | 15.9324 | 14.6794 | 13.2508 | 11.8447 | 10.7069 | 4.9335 | 1.408 | -1.241
|  | DORCHESTER | HT |  |  |  | 19.8998 | 19.2927 | 18.4559 | 17.6406 | 16.9212 | 16.409 | 15.2865 | 14.0406 | 12.7406 | 11.4059 | 3.7141 | -1.3931 | -4.0951 | 24.5059 | 24.0978 | 23.612 | 23.1233 | 22.6682 | 22.3835 | 21.7559 | 21.0335 | 20.2692 | 19.359 | 14.8171 | 12.7039 | 11.5957 | 20.3427 | 19.7641 | 19.0478 | 18.3161 | 17.6416 | 17.1784 | 16.1457 | 14.9916 | 13.7886 | 12.5498 | 5.5284 | 0.96612 | -1.3584
|  | DORCHESTER | HE |  |  |  | 19.8202 | 19.1824 | 18.3069 | 17.4467 | 16.6702 | 16.011 | 14.6937 | 13.0988 | 11.4049 | 9.6324 | 0.78857 | -3.8135 | -5.3553 | 24.3998 | 23.9151 | 23.3345 | 22.7508 | 22.1784 | 21.7569 | 21.0161 | 19.8998 | 18.6692 | 17.362 | 11.211 | 8.1773 | 3.3437 | 20.262 | 19.658 | 18.8998 | 18.1253 | 17.3967 | 16.8661 | 15.858 | 14.6978 | 13.3243 | 11.6182 | 3.46 | -0.4002 | -1.4624
|  | DORCHESTER | CF |  |  |  | 20.1263 | 19.712 | 19.0835 | 18.5549 | 18.1018 | 17.609 | 17.1345 | 16.8651 | 16.1008 | 15.1376 | 8.96 | 3.3151 | -1.0522 | 24.5763 | 24.2039 | 23.7447 | 23.3386 | 22.9365 | 22.4753 | 21.9712 | 21.612 | 20.9927 | 20.3212 | 15.4906 | 8.7161 | -1.541 | 20.5478 | 20.1508 | 19.6192 | 19.1559 | 18.7273 | 18.2631 | 17.811 | 17.5641 | 17.0069 | 16.4151 | 10.9069 | 5.5845 | 1.9416
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | DOWN GRANGE | MINIMUM HEADROOM | SU 61604 50238 | YES | 2.155 | 11.498 | 10.8419 | 9.8225 | 8.6878 | 7.2929 | 5.7674 | 3.746 | 1.6123 | -0.58767 | -2.302 | -10.6132 | -16.8611 | -20.6632 | 14.8562 | 14.445 | 13.7062 | 12.894 | 11.9133 | 10.845 | 9.5287 | 8.0695 | 6.5552 | 5.4705 | 0.089878 | -6.7877 | -23.7877 | 12.2184 | 11.6593 | 10.7409 | 9.7031 | 8.4225 | 7.0205 | 5.1715 | 3.1797 | 1.1368 | -0.34584 | -7.5275 | -12.8673 | -15.9448
|  | DOWN GRANGE | EE |  |  |  | 11.498 | 10.8419 | 9.8225 | 8.6878 | 7.2929 | 5.7674 | 3.746 | 1.6123 | -0.58767 | -2.302 | -9.8918 | -15.6132 | -20.2285 | 14.8562 | 14.445 | 13.7062 | 12.894 | 11.9133 | 10.845 | 9.5287 | 8.0695 | 6.5552 | 5.4705 | 0.089878 | -5.9397 | -15.0856 | 12.2184 | 11.6593 | 10.7409 | 9.7031 | 8.4225 | 7.0205 | 5.1715 | 3.1797 | 1.1368 | -0.34584 | -6.9407 | -11.7611 | -15.5907
|  | DOWN GRANGE | HT |  |  |  | 11.8572 | 11.0205 | 10.0358 | 9.3287 | 8.1154 | 6.747 | 4.7348 | 2.794 | 0.8062 | -1.0479 | -10.6132 | -16.8611 | -20.6632 | 15.2746 | 14.8011 | 14.2184 | 13.9266 | 13.2644 | 12.496 | 11.4827 | 10.4521 | 9.3827 | 8.3521 | 3.5419 | 0.94294 | -0.48053 | 12.5797 | 11.847 | 10.9715 | 10.3787 | 9.3225 | 8.1031 | 6.3307 | 4.595 | 2.8103 | 1.1256 | -7.5275 | -12.8673 | -15.9448
|  | DOWN GRANGE | HE |  |  |  | 11.8715 | 11.0991 | 10.1715 | 9.5307 | 8.394 | 7.1368 | 5.6093 | 4.0766 | 2.4705 | 0.83376 | -7.1132 | -12.6856 | -15.406 | 15.194 | 14.6674 | 14.0144 | 13.6531 | 12.9031 | 12.0756 | 11.1031 | 10.0593 | 8.9419 | 7.7736 | 1.5491 | -4.4836 | -12.8601 | 12.5899 | 11.9133 | 11.0889 | 10.5582 | 9.5684 | 8.4664 | 7.1062 | 5.7184 | 4.2664 | 2.7838 | -4.3816 | -9.0958 | -11.2938
|  | DOWN GRANGE | CF |  |  |  | 12.3225 | 11.9787 | 11.5542 | 11.0582 | 10.7797 | 9.9531 | 8.5307 | 7.6838 | 6.9562 | 6.2031 | 0.52559 | -4.8316 | -9.8734 | 15.4113 | 15.0399 | 14.6164 | 14.1184 | 13.8603 | 13.144 | 12.0919 | 11.2205 | 10.3633 | 9.4521 | 2.8868 | -6.7877 | -23.7877 | 12.9746 | 12.6501 | 12.2633 | 11.8103 | 11.6031 | 10.894 | 9.7246 | 8.9399 | 8.2409 | 7.5123 | 2.2419 | -2.4418 | -6.8499
MINETY GSP | STRATTON (2 X 90) | DRAKES WAY | MINIMUM HEADROOM | SU 16899 85647 | YES | 0.833 | 13.3061 | 13.2173 | 13.102 | 12.9673 | 12.5816 | 12.0684 | 11.6276 | 11.1571 | 10.6847 | 10.2765 | 9.2551 | 8.8551 | 8.6439 | 13.849 | 13.7908 | 13.7173 | 13.6398 | 13.2 | 12.7286 | 12.3653 | 11.9898 | 11.6408 | 11.3755 | 10.6214 | 8.899 | 5.2571 | 13.5306 | 13.4643 | 13.3827 | 13.2959 | 12.8949 | 12.4306 | 12.0398 | 11.6082 | 11.2235 | 10.8776 | 9.8612 | 9.4214 | 9.2071
|  | DRAKES WAY | EE |  |  |  | 13.3061 | 13.2173 | 13.102 | 12.9673 | 12.802 | 12.2418 | 11.7765 | 11.2204 | 10.6847 | 10.2765 | 9.2878 | 9.0418 | 9.0408 | 13.849 | 13.7908 | 13.7173 | 13.6398 | 13.5418 | 13.0102 | 12.6296 | 12.1714 | 11.7133 | 11.3755 | 10.6214 | 9.6653 | 7.9673 | 13.5306 | 13.4643 | 13.3827 | 13.2959 | 13.1724 | 12.6551 | 12.2327 | 11.7327 | 11.2429 | 10.8776 | 9.9061 | 9.6357 | 9.6837
|  | DRAKES WAY | HT |  |  |  | 13.3765 | 13.3092 | 13.2276 | 13.1327 | 12.5816 | 12.0684 | 11.6276 | 11.1571 | 10.7327 | 10.4398 | 9.3786 | 8.9194 | 8.748 | 13.898 | 13.8551 | 13.8031 | 13.7459 | 13.2 | 12.7286 | 12.3653 | 11.9898 | 11.6408 | 11.4337 | 10.7929 | 10.5245 | 10.4061 | 13.5827 | 13.5316 | 13.4694 | 13.402 | 12.8949 | 12.4306 | 12.0398 | 11.6082 | 11.2235 | 10.9755 | 9.9949 | 9.5071 | 9.3531
|  | DRAKES WAY | HE |  |  |  | 13.3745 | 13.3041 | 13.2194 | 13.1194 | 12.9929 | 12.4704 | 12.0582 | 11.5347 | 11.0163 | 10.5673 | 9.2551 | 8.8551 | 8.6439 | 13.8939 | 13.851 | 13.7929 | 13.7347 | 13.6571 | 13.1582 | 12.8143 | 12.3857 | 11.9439 | 11.5735 | 10.6367 | 9.8398 | 8.0857 | 13.5816 | 13.5306 | 13.4673 | 13.4 | 13.3184 | 12.8541 | 12.4827 | 12.002 | 11.5286 | 11.1276 | 9.8612 | 9.4214 | 9.2071
|  | DRAKES WAY | CF |  |  |  | 13.4286 | 13.3908 | 13.3459 | 13.2929 | 13.2378 | 13.1704 | 12.9071 | 12.5663 | 12.1837 | 11.8245 | 10.2439 | 9.4265 | 8.8551 | 13.9276 | 13.902 | 13.8673 | 13.8276 | 13.7878 | 13.7347 | 13.4469 | 13.1112 | 12.7306 | 12.3857 | 10.8653 | 8.899 | 5.2571 | 13.6204 | 13.5918 | 13.5592 | 13.5184 | 13.4786 | 13.4296 | 13.1898 | 12.8939 | 12.5551 | 12.2214 | 10.802 | 10.0694 | 9.4439
NURSLING GSP | WINCHESTER | DUNBRIDGE | MINIMUM HEADROOM | SU 31520 26244 | YES | 2.075 | 1.1069 | 0.9263 | 0.41711 | -0.69717 | -1.2686 | -4.2594 | -5.741 | -7.3808 | -7.7206 | -8.6819 | -16.5268 | -23.4115 | -29.1451 | 3.3013 | 3.1717 | 2.6156 | 1.3125 | 0.69007 | -2.9467 | -4.6569 | -6.5416 | -6.8018 | -7.5569 | -16.7967 | -25.5416 | -33.4191 | 3.0304 | 2.8579 | 2.2865 | 0.94875 | 0.2865 | -3.3962 | -5.1502 | -7.1084 | -7.441 | -8.5074 | -17.9074 | -26.3115 | -33.1604
|  | DUNBRIDGE | EE |  |  |  | 1.1069 | 0.9263 | 0.61609 | 0.40793 | 0.13038 | -0.94615 | -2.1155 | -2.1441 | -3.7962 | -4.7104 | -10.4819 | -21.7227 | -27.0788 | 3.3013 | 3.1717 | 2.9146 | 2.7625 | 2.5452 | 1.3309 | 0.066604 | 0.11048 | -1.7763 | -2.7814 | -9.3099 | -23.5518 | -31.2191 | 3.0304 | 2.8579 | 2.5538 | 2.3559 | 2.0834 | 0.81405 | -0.54615 | -0.50636 | -2.4686 | -3.5217 | -10.2206 | -24.0482 | -30.6298
|  | DUNBRIDGE | HT |  |  |  | 1.2028 | 0.96813 | 0.53242 | -0.15431 | -0.35738 | -2.7421 | -4.2329 | -5.9706 | -6.6074 | -8.6819 | -15.6951 | -18.9002 | -29.1451 | 3.4023 | 3.2411 | 2.8054 | 2.0472 | 1.9054 | -0.94768 | -2.6171 | -4.5895 | -5.1763 | -7.5569 | -15.4936 | -18.9609 | -31.4395 | 3.1396 | 2.9304 | 2.4385 | 1.6324 | 1.4334 | -1.4859 | -3.2472 | -5.3206 | -6.0166 | -8.5074 | -16.8155 | -20.5227 | -33.1441
|  | DUNBRIDGE | HE |  |  |  | 1.2008 | 1.0518 | 0.41711 | -0.69717 | -1.2686 | -4.2594 | -5.741 | -7.3808 | -7.7206 | -8.0737 | -16.5268 | -23.4115 | -28.9645 | 3.388 | 3.287 | 2.6156 | 1.3125 | 0.69007 | -2.9467 | -4.6569 | -6.5416 | -6.8018 | -7.0793 | -16.7967 | -25.5416 | -33.4191 | 3.1345 | 2.9998 | 2.2865 | 0.94875 | 0.2865 | -3.3962 | -5.1502 | -7.1084 | -7.441 | -7.7839 | -17.9074 | -26.3115 | -33.1604
|  | DUNBRIDGE | CF |  |  |  | 1.2447 | 1.1273 | 0.98854 | 0.75589 | 0.34058 | -0.19513 | -0.86656 | -1.3686 | -1.9472 | -2.6921 | -7.19 | -13.5717 | -19.7523 | 3.4146 | 3.3288 | 3.2227 | 3.0299 | 2.5778 | 1.9748 | 1.1901 | 0.61252 | -0.050743 | -0.92217 | -6.4824 | -14.8191 | -24.1507 | 3.1763 | 3.0671 | 2.9283 | 2.709 | 2.2375 | 1.6151 | 0.81507 | 0.24977 | -0.42064 | -1.2972 | -6.5982 | -14.2951 | -21.7084
EALING GSP |  | EALING 11kV | MINIMUM HEADROOM | SZ 06789 95116 | YES | 16.338 | 4.8161 | 9.2368 | 7.3927 | 6.2723 | 4.4549 | 2.4325 | 0.28351 | -1.8828 | -3.9828 | -5.5175 | -11.443 | -16.6757 | -19.3114 | 12.2539 | 16.896 | 15.3243 | 14.6182 | 13.3866 | 11.7427 | 10.0794 | 8.3641 | 6.6335 | 5.308 | -0.87465 | -10.9522 | -33.7359 | 5.3814 | 9.5123 | 7.7988 | 6.8305 | 5.3039 | 3.406 | 1.4223 | -0.59914 | -2.5767 | -4.0308 | -9.5644 | -14.1553 | -16.443
|  | EALING 11kV | EE |  |  |  | 4.8161 | 9.2368 | 7.3927 | 6.2723 | 4.5998 | 2.4325 | 0.28351 | -1.8828 | -3.9828 | -5.5175 | -11.443 | -15.8114 | -18.5685 | 12.2539 | 16.896 | 15.3243 | 14.6182 | 13.3866 | 11.7427 | 10.0794 | 8.3641 | 6.6335 | 5.308 | -0.87465 | -8.1063 | -19.8124 | 5.3814 | 9.5123 | 7.7988 | 6.8305 | 5.3743 | 3.406 | 1.4223 | -0.59914 | -2.5767 | -4.0308 | -9.5644 | -13.391 | -15.8389
|  | EALING 11kV | HT |  |  |  | 5.1743 | 9.546 | 7.8427 | 6.4009 | 4.4549 | 2.8284 | 1.1009 | -0.35526 | -1.9236 | -3.3614 | -10.7195 | -16.6757 | -19.3114 | 12.7467 | 17.5266 | 16.3325 | 15.4631 | 14.1958 | 13.2835 | 12.1641 | 11.1274 | 9.9978 | 8.9498 | 4.5141 | 1.6417 | 0.57331 | 5.7325 | 9.8623 | 8.3284 | 7.0651 | 5.3039 | 3.8386 | 2.2682 | 0.89168 | -0.57669 | -1.9389 | -8.793 | -14.1553 | -16.443
|  | EALING 11kV | HE |  |  |  | 5.1294 | 9.7307 | 8.1447 | 6.9366 | 5.5366 | 3.9866 | 2.2958 | 0.67841 | -0.88485 | -2.3134 | -8.1746 | -12.092 | -13.5522 | 12.6161 | 17.4368 | 16.1509 | 15.2672 | 14.2611 | 13.2549 | 11.9651 | 10.6815 | 9.3549 | 8.0325 | 1.3427 | -5.9563 | -17.0165 | 5.6916 | 10.0062 | 8.5488 | 7.4764 | 6.2386 | 4.8672 | 3.3335 | 1.8631 | 0.41413 | -0.93077 | -6.4318 | -9.9216 | -11.1767
|  | EALING 11kV | CF |  |  |  | 5.4937 | 10.4051 | 9.3835 | 8.7243 | 8.0764 | 7.3968 | 6.9876 | 6.1631 | 5.1254 | 3.9662 | -2.1563 | -6.3298 | -10.4155 | 12.7978 | 17.7286 | 16.6611 | 15.9794 | 15.259 | 14.4325 | 13.758 | 12.6549 | 11.4335 | 10.1111 | 1.5284 | -10.9522 | -33.7359 | 6.0059 | 10.5888 | 9.608 | 8.9958 | 8.3927 | 7.7529 | 7.3702 | 6.606 | 5.6927 | 4.6896 | -1.0134 | -4.8379 | -8.4889
LALEHAM |  | EAST BEDFONT 11kV | MINIMUM HEADROOM | TQ 08394 73826 | YES | 14.258 | 30.6918 | 80.1949 | 79.4153 | 78.4082 | 77.3204 | 75.802 | 73.7622 | 71.3153 | 69.0459 | 66.9653 | 59.3316 | 54.849 | 45.7 | 35.2367 | 84.9102 | 84.4194 | 83.8561 | 83.048 | 81.8622 | 80.1388 | 78.052 | 76.1653 | 74.3847 | 68.5357 | 64.499 | 46.2163 | 30.2602 | 79.7622 | 79.0153 | 78.1704 | 77.149 | 75.6857 | 73.6133 | 71.1276 | 68.8541 | 66.7429 | 59.3776 | 54.95 | 45.6816
|  | EAST BEDFONT 11kV | EE |  |  |  | 30.6918 | 80.1949 | 79.4153 | 78.4082 | 77.3204 | 75.802 | 73.7622 | 71.3153 | 69.0459 | 66.9653 | 60.2082 | 58.1306 | 48.5071 | 35.2367 | 84.9102 | 84.4194 | 83.8561 | 83.048 | 81.8622 | 80.1388 | 78.052 | 76.1653 | 74.3847 | 68.9163 | 64.499 | 49.7398 | 30.2602 | 79.7622 | 79.0153 | 78.1704 | 77.149 | 75.6857 | 73.6133 | 71.1276 | 68.8541 | 66.7429 | 60.0224 | 57.9561 | 48.0041
|  | EAST BEDFONT 11kV | HT |  |  |  | 31.2367 | 80.9408 | 80.5337 | 80.0816 | 79.3286 | 78.3653 | 76.9082 | 75.0214 | 73.0847 | 71.0827 | 63.2378 | 58.6643 | 48.352 | 35.6122 | 85.4408 | 85.1837 | 84.899 | 84.3745 | 83.7908 | 82.5827 | 80.9327 | 79.2837 | 77.5551 | 71.251 | 68.1051 | 59.0357 | 30.7296 | 80.3939 | 79.9041 | 79.4082 | 78.6602 | 77.8265 | 76.5551 | 74.7031 | 72.7541 | 70.7102 | 62.7847 | 57.8735 | 47.6367
|  | EAST BEDFONT 11kV | HE |  |  |  | 31.052 | 80.6622 | 80.102 | 79.4031 | 78.4796 | 77.1847 | 75.5949 | 73.498 | 71.4633 | 69.2755 | 59.3316 | 54.849 | 45.7 | 35.4786 | 85.2276 | 84.8439 | 84.4245 | 83.9245 | 82.9347 | 81.6122 | 79.8531 | 78.2398 | 76.4776 | 68.5357 | 64.9949 | 50.6541 | 30.6316 | 80.2776 | 79.7316 | 79.1776 | 78.2694 | 77.0224 | 75.4214 | 73.3102 | 71.3204 | 69.1684 | 59.3776 | 54.95 | 45.6816
|  | EAST BEDFONT 11kV | CF |  |  |  | 31.3847 | 81.1929 | 80.8898 | 80.5051 | 80.098 | 79.602 | 78.7571 | 77.6082 | 76.4602 | 75.1806 | 67.7898 | 62.6224 | 51.949 | 35.6765 | 85.5306 | 85.3031 | 85.0122 | 84.6816 | 84.2214 | 83.3939 | 82.3122 | 81.4286 | 80.3714 | 73.7418 | 65.9755 | 46.2163 | 30.9061 | 80.7153 | 80.4224 | 80.0429 | 79.6786 | 79.2316 | 78.4541 | 77.2878 | 76.1143 | 74.8276 | 67.6347 | 62.6878 | 52.201
MANNINGTON GSP | REDHILL BSP | EAST HOWE | MINIMUM HEADROOM | SZ 06789 95116 | YES | 7.779 | 0.082737 | -0.48461 | -1.3632 | -2.3356 | -3.4081 | -4.5418 | -6.1948 | -7.8693 | -9.5377 | -10.7591 | -18.0315 | -23.3652 | -26.2877 | 2.1364 | 1.7507 | 1.1241 | 0.4323 | -0.34831 | -1.1728 | -2.2524 | -3.4116 | -4.5902 | -5.4218 | -10.1463 | -15.5748 | -29.3769 | -0.040376 | -0.5414 | -1.3373 | -2.2271 | -3.2098 | -4.273 | -5.8047 | -7.4016 | -8.9955 | -10.0669 | -16.3322 | -20.8975 | -23.4098
|  | EAST HOWE | EE |  |  |  | 0.082737 | -0.48461 | -1.3632 | -2.3356 | -3.4081 | -4.5418 | -6.1948 | -7.8693 | -9.5377 | -10.7591 | -17.1907 | -22.1397 | -25.7693 | 2.1364 | 1.7507 | 1.1241 | 0.4323 | -0.34831 | -1.1728 | -2.2524 | -3.4116 | -4.5902 | -5.4218 | -10.1463 | -15.2493 | -22.5289 | -0.040376 | -0.5414 | -1.3373 | -2.2271 | -3.2098 | -4.273 | -5.8047 | -7.4016 | -8.9955 | -10.0669 | -15.672 | -19.8618 | -23.0047
|  | EAST HOWE | HT |  |  |  | 0.39804 | -0.34583 | -1.2071 | -1.7877 | -2.6856 | -3.6764 | -5.2122 | -6.7203 | -8.3009 | -9.904 | -18.0315 | -23.3652 | -26.2877 | 2.4752 | 2.0262 | 1.5139 | 1.2425 | 0.72822 | 0.15883 | -0.63403 | -1.4544 | -2.3269 | -3.2157 | -7.4228 | -9.7687 | -10.9932 | 0.29024 | -0.38936 | -1.1618 | -1.6536 | -2.4557 | -3.3475 | -4.721 | -6.0934 | -7.5302 | -8.9924 | -16.3322 | -20.8975 | -23.4098
|  | EAST HOWE | HE |  |  |  | 0.446 | -0.23155 | -1.0203 | -1.5275 | -2.3622 | -3.2571 | -4.4683 | -5.6458 | -6.8775 | -8.1662 | -14.8724 | -19.6805 | -21.9907 | 2.4282 | 1.9486 | 1.3915 | 1.0721 | 0.4823 | -0.15546 | -0.94627 | -1.7779 | -2.6687 | -3.6177 | -8.9575 | -14.0555 | -20.8126 | 0.32391 | -0.29038 | -0.99752 | -1.4251 | -2.173 | -2.9771 | -4.0669 | -5.1506 | -6.2863 | -7.472 | -13.5485 | -17.6394 | -19.6169
|  | EAST HOWE | CF |  |  |  | 0.77151 | 0.22457 | -0.2642 | -0.83461 | -1.1122 | -1.7193 | -2.2642 | -2.7622 | -3.2805 | -3.8224 | -8.0642 | -12.9713 | -17.5969 | 2.617 | 2.1425 | 1.7282 | 1.2466 | 0.9874 | 0.42516 | -0.16464 | -0.79117 | -1.4493 | -2.1606 | -7.381 | -15.5748 | -29.3769 | 0.63207 | 0.12391 | -0.3118 | -0.82303 | -1.0394 | -1.573 | -2.0577 | -2.524 | -3.0128 | -3.5475 | -7.6067 | -11.8771 | -15.9455
MELKSHAM GSP | NORRINGTON | EASTERTON | MINIMUM HEADROOM | SU 01568 54730 | YES | 2.29 | 5.0987 | 4.8915 | 4.5915 | 4.3415 | 3.9946 | 3.6181 | 3.7568 | 3.3436 | 2.913 | 2.6803 | 1.4558 | 1.0364 | 0.64561 | 7.388 | 7.239 | 7.0247 | 6.8431 | 6.589 | 6.3084 | 6.3818 | 6.0727 | 5.7543 | 5.588 | 4.6716 | 3.1737 | -0.095714 | 5.3104 | 5.1104 | 4.8155 | 4.5706 | 4.2308 | 3.8635 | 4.0094 | 3.6114 | 3.2022 | 2.991 | 1.939 | 1.5839 | 1.2594
|  | EASTERTON | EE |  |  |  | 5.0987 | 4.8915 | 4.5915 | 4.3415 | 3.9946 | 3.6181 | 3.7568 | 3.3436 | 2.913 | 2.6803 | 1.4558 | 1.0364 | 0.84969 | 7.388 | 7.239 | 7.0247 | 6.8431 | 6.589 | 6.3084 | 6.3818 | 6.0727 | 5.7543 | 5.588 | 4.6716 | 3.741 | 2.2124 | 5.3104 | 5.1104 | 4.8155 | 4.5706 | 4.2308 | 3.8635 | 4.0094 | 3.6114 | 3.2022 | 2.991 | 1.939 | 1.5839 | 1.4308
|  | EASTERTON | HT |  |  |  | 5.2181 | 5.0599 | 4.864 | 4.6905 | 4.4538 | 4.2038 | 3.8313 | 3.4579 | 3.114 | 3.116 | 1.7201 | 1.0711 | 0.64561 | 7.5094 | 7.4145 | 7.2757 | 7.1676 | 7.0012 | 6.8533 | 6.6155 | 6.3604 | 6.1104 | 6.2624 | 5.4155 | 5.0849 | 4.8941 | 5.4318 | 5.2849 | 5.092 | 4.9308 | 4.7043 | 4.4737 | 4.1196 | 3.7522 | 3.4094 | 3.4686 | 2.1655 | 1.6063 | 1.2594
|  | EASTERTON | HE |  |  |  | 5.213 | 5.0579 | 4.865 | 4.6936 | 4.4701 | 4.2487 | 3.9405 | 3.5701 | 3.1619 | 3.1783 | 1.6354 | 1.213 | 1.0446 | 7.491 | 7.3839 | 7.2288 | 7.1073 | 6.9278 | 6.7696 | 6.5359 | 6.2502 | 5.94 | 6.0676 | 4.8206 | 3.8645 | 2.3206 | 5.4267 | 5.2818 | 5.0931 | 4.9359 | 4.7216 | 4.5124 | 4.2145 | 3.8492 | 3.4594 | 3.5298 | 2.1196 | 1.7533 | 1.6216
|  | EASTERTON | CF |  |  |  | 5.2477 | 5.1119 | 4.9568 | 4.816 | 4.6497 | 4.4701 | 4.316 | 4.1038 | 3.863 | 3.6048 | 2.7038 | 1.9068 | 1.2497 | 7.5155 | 7.4176 | 7.292 | 7.1839 | 7.041 | 6.8737 | 6.7278 | 6.5094 | 6.2696 | 6.0114 | 4.988 | 3.1737 | -0.095714 | 5.4635 | 5.339 | 5.1941 | 5.0676 | 4.9073 | 4.7359 | 4.59 | 4.3818 | 4.1451 | 3.8839 | 3.0716 | 2.3502 | 1.7869
BRAMLEY (FLEE) | BRACKNELL | EASTHAMPSTEAD | MINIMUM HEADROOM | SU 86148 67194 | YES | 4.182 | 9.2122 | 8.5856 | 7.8785 | 7.4673 | 6.6275 | 5.5734 | 3.7856 | 1.8407 | 0.12237 | -1.2827 | -8.7062 | -15.1154 | -18.9531 | 12.2601 | 11.756 | 11.1581 | 10.8224 | 10.1336 | 9.3152 | 7.9918 | 6.4938 | 5.1346 | 3.9979 | -1.7184 | -7.4899 | -21.0909 | 8.8479 | 8.1989 | 7.4254 | 7.155 | 6.3224 | 5.3111 | 3.6183 | 1.7326 | 0.037673 | -1.3062 | -7.995 | -13.8338 | -17.1042
|  | EASTHAMPSTEAD | EE |  |  |  | 9.2122 | 8.5856 | 7.8785 | 7.4673 | 6.6275 | 5.5734 | 3.7856 | 1.8407 | 0.12237 | -1.2827 | -8.347 | -13.6684 | -18.0552 | 12.2601 | 11.756 | 11.1581 | 10.8224 | 10.1336 | 9.3152 | 7.9918 | 6.4938 | 5.1346 | 3.9979 | -1.7184 | -7.4899 | -15.9113 | 8.8479 | 8.1989 | 7.4254 | 7.155 | 6.3224 | 5.3111 | 3.6183 | 1.7326 | 0.037673 | -1.3062 | -7.6674 | -12.3266 | -16.1429
|  | EASTHAMPSTEAD | HT |  |  |  | 9.4897 | 8.952 | 8.4418 | 7.8642 | 7.1897 | 6.6336 | 5.0724 | 3.4183 | 1.9234 | 0.35502 | -8.7062 | -15.1154 | -18.9531 | 12.5867 | 12.2581 | 11.9213 | 11.5254 | 11.0622 | 10.7662 | 9.7754 | 8.6764 | 7.6836 | 6.6162 | 1.2652 | -2.2348 | -4.1236 | 9.2438 | 8.7397 | 8.2295 | 7.6336 | 6.9326 | 6.5285 | 5.0571 | 3.4703 | 2.0244 | 0.48971 | -7.995 | -13.8338 | -17.1042
|  | EASTHAMPSTEAD | HE |  |  |  | 9.502 | 9.0275 | 8.503 | 7.9407 | 7.3091 | 6.8132 | 5.5275 | 4.1509 | 2.9805 | 1.7775 | -5.0817 | -10.394 | -12.997 | 12.5213 | 12.1611 | 11.7428 | 11.2764 | 10.7367 | 10.3693 | 9.4305 | 8.3591 | 7.4458 | 6.4795 | 0.6091 | -5.2348 | -12.8654 | 9.2428 | 8.7958 | 8.2877 | 7.7152 | 7.0693 | 6.7275 | 5.5275 | 4.1969 | 3.0856 | 1.9336 | -4.4338 | -9.0297 | -11.2838
|  | EASTHAMPSTEAD | CF |  |  |  | 9.7499 | 9.4816 | 9.1448 | 8.856 | 8.4836 | 7.952 | 7.6244 | 6.9285 | 6.3571 | 5.7938 | 1.4499 | -3.3011 | -7.6052 | 12.6438 | 12.3652 | 12.0081 | 11.6724 | 11.2367 | 10.6703 | 10.1856 | 9.3367 | 8.5469 | 7.7387 | 2.2162 | -6.4317 | -21.0909 | 9.4622 | 9.1867 | 8.8183 | 8.5081 | 8.0979 | 7.555 | 7.3581 | 6.6407 | 6.0275 | 5.4244 | 1.3407 | -2.8103 | -6.5276
NURSLING GSP | VELMORE BSP | EASTLEIGH NORTH | MINIMUM HEADROOM | SU 45426 18958 | YES | 3.909 | 8.5329 | 7.5135 | 5.7441 | 3.7471 | 2.0951 | 0.2849 | -1.6447 | -3.7967 | -5.9161 | -7.5182 | -16.1314 | -23.4192 | -27.5794 | 15.6982 | 15.0778 | 13.9961 | 12.7941 | 11.6992 | 10.5002 | 9.1982 | 7.7084 | 6.2033 | 5.089 | -0.95694 | -7.3631 | -24.111 | 10.09 | 9.2716 | 7.838 | 6.1982 | 4.7676 | 3.1329 | 1.3604 | -0.63449 | -2.5978 | -4.0437 | -11.4804 | -17.8365 | -21.4171
|  | EASTLEIGH NORTH | EE |  |  |  | 8.5329 | 7.5135 | 5.7441 | 3.7471 | 2.0951 | 0.2849 | -1.6447 | -3.7967 | -5.9161 | -7.5182 | -15.8365 | -22.0947 | -26.8855 | 15.6982 | 15.0778 | 13.9961 | 12.7941 | 11.6992 | 10.5002 | 9.1982 | 7.7084 | 6.2033 | 5.089 | -0.95694 | -7.0376 | -15.9896 | 10.09 | 9.2716 | 7.838 | 6.1982 | 4.7676 | 3.1329 | 1.3604 | -0.63449 | -2.5978 | -4.0437 | -11.3988 | -16.7651 | -20.9049
|  | EASTLEIGH NORTH | HT |  |  |  | 8.9329 | 7.788 | 6.0869 | 4.5267 | 3.1278 | 1.5267 | -0.20388 | -1.9967 | -3.8376 | -5.7376 | -16.1314 | -23.4192 | -27.5794 | 16.1053 | 15.4839 | 14.5696 | 13.8318 | 13.0961 | 12.2482 | 11.3502 | 10.3451 | 9.2747 | 8.1553 | 2.591 | -0.76408 | -2.46 | 10.4461 | 9.5145 | 8.139 | 6.8727 | 5.6645 | 4.2869 | 2.7635 | 1.1767 | -0.45082 | -2.1416 | -11.4804 | -17.8365 | -21.4171
|  | EASTLEIGH NORTH | HE |  |  |  | 8.9063 | 7.7982 | 6.1288 | 4.6022 | 3.2431 | 1.7308 | 0.29 | -1.2906 | -2.8988 | -4.5478 | -13.5824 | -20.058 | -22.9661 | 16.0012 | 15.3063 | 14.3002 | 13.4778 | 12.6329 | 11.691 | 10.7441 | 9.6757 | 8.5165 | 7.2737 | 0.29102 | -6.1937 | -14.3692 | 10.4206 | 9.5186 | 8.1635 | 6.9227 | 5.741 | 4.4267 | 3.1482 | 1.7451 | 0.31245 | -1.1518 | -9.258 | -14.9763 | -17.4253
|  | EASTLEIGH NORTH | CF |  |  |  | 9.2604 | 8.4176 | 7.1686 | 5.7553 | 5.0737 | 4.0961 | 3.5522 | 2.8829 | 2.1124 | 1.2706 | -4.7273 | -11.1161 | -17.0467 | 16.1818 | 15.5849 | 14.7706 | 13.8635 | 13.3931 | 12.6339 | 11.9859 | 11.2104 | 10.3655 | 9.439 | 2.6982 | -7.3631 | -24.111 | 10.7482 | 10.088 | 9.1145 | 7.9829 | 7.4135 | 6.5798 | 6.1124 | 5.5329 | 4.8982 | 4.1237 | -1.3763 | -7.0886 | -12.259
LOVEDEAN GSP | PORTSMOUTH BSP | EASTNEY | MINIMUM HEADROOM | SZ 66357 99040 | YES | 0.52 | 12.4541 | 12.2245 | 11.9276 | 11.6214 | 11.2316 | 10.801 | 10.2449 | 9.548 | 8.8561 | 8.3306 | 6.4439 | 4.9429 | 4.9398 | 14.0694 | 13.8347 | 13.5357 | 13.2245 | 12.8347 | 12.4 | 11.8969 | 11.2796 | 10.649 | 10.102 | 7.1163 | 0.98878 | -11.7541 | 12.9082 | 12.6837 | 12.3939 | 12.0888 | 11.7051 | 11.2796 | 10.751 | 10.0796 | 9.4153 | 8.9061 | 7.0745 | 5.7439 | 5.75
|  | EASTNEY | EE |  |  |  | 12.4541 | 12.2245 | 11.9276 | 11.6214 | 11.2316 | 10.801 | 10.2449 | 9.548 | 8.8561 | 8.3306 | 6.4439 | 5.5459 | 5.6684 | 14.0694 | 13.8347 | 13.5357 | 13.2245 | 12.8347 | 12.4 | 11.8969 | 11.2796 | 10.649 | 10.102 | 7.1163 | 3.5653 | -2.3204 | 12.9082 | 12.6837 | 12.3939 | 12.0888 | 11.7051 | 11.2796 | 10.751 | 10.0796 | 9.4153 | 8.9061 | 7.0745 | 6.301 | 6.3796
|  | EASTNEY | HT |  |  |  | 12.6398 | 12.4704 | 12.2602 | 12.0531 | 11.8 | 11.4929 | 11.0878 | 10.5714 | 10.0276 | 9.4908 | 6.6204 | 4.9429 | 4.9398 | 14.2582 | 14.1388 | 13.9847 | 13.8255 | 13.6357 | 13.4102 | 13.1439 | 12.801 | 12.4367 | 12.0735 | 10.1949 | 9.1245 | 9 | 13.0898 | 12.9255 | 12.7235 | 12.5173 | 12.2653 | 11.9694 | 11.5786 | 11.0847 | 10.5551 | 10.0296 | 7.2776 | 5.7439 | 5.75
|  | EASTNEY | HE |  |  |  | 12.6204 | 12.4673 | 12.2786 | 12.1 | 11.8796 | 11.6235 | 11.2735 | 10.8306 | 10.3663 | 9.9429 | 8.0653 | 7.2071 | 7.0663 | 14.1867 | 14.0122 | 13.7908 | 13.5724 | 13.3061 | 13 | 12.6449 | 12.2071 | 11.7388 | 11.2592 | 8.2337 | 4.6439 | -1.3612 | 13.0714 | 12.9235 | 12.7439 | 12.5673 | 12.35 | 12.098 | 11.7694 | 11.3378 | 10.8888 | 10.4704 | 8.6337 | 7.8694 | 7.7592
|  | EASTNEY | CF |  |  |  | 12.702 | 12.6214 | 12.5051 | 12.4041 | 12.2673 | 12.1255 | 11.9561 | 11.7796 | 11.5459 | 11.3031 | 9.8388 | 8.2041 | 6.6806 | 14.2265 | 14.0714 | 13.8765 | 13.6704 | 13.4214 | 13.1163 | 12.749 | 12.3418 | 11.8806 | 11.3816 | 7.7582 | 0.98878 | -11.7541 | 13.152 | 13.0714 | 12.9612 | 12.8602 | 12.7255 | 12.5837 | 12.4194 | 12.2459 | 12.0184 | 11.7806 | 10.3571 | 8.798 | 7.3857
LALEHAM | STAINES | EGHAM | MINIMUM HEADROOM | TQ 01030 71404 | YES | 4.456 | 2.4052 | 1.2419 | -0.11115 | -1.5428 | -3.0101 | 23.7256 | 21.9419 | 19.8419 | 17.8307 | 16.1368 | 6.4399 | 1.346 | 0.0092571 | 8.5929 | 7.7868 | 6.8327 | 6.0776 | 5.1858 | 30.9113 | 29.6552 | 28.0133 | 26.4501 | 25.1603 | 17.495 | 13.844 | 7.2746 | 3.2256 | 2.1531 | 0.88069 | -0.1387 | -1.256 | 25.1327 | 23.497 | 21.3674 | 19.3327 | 17.646 | 7.6929 | 2.8491 | 1.9358
|  | EGHAM | EE |  |  |  | 2.4052 | 1.2419 | -0.11115 | -1.5428 | -3.0101 | 23.7256 | 21.9419 | 19.8419 | 17.8307 | 16.1368 | 9.9276 | 7.5266 | 5.9429 | 8.5929 | 7.7868 | 6.8327 | 6.0776 | 5.1858 | 30.9113 | 29.6552 | 28.0133 | 26.4501 | 25.1603 | 21.096 | 18.2705 | 13.1001 | 3.2256 | 2.1531 | 0.88069 | -0.1387 | -1.256 | 25.1327 | 23.497 | 21.3674 | 19.3327 | 17.646 | 12.0878 | 10.596 | 8.798
|  | EGHAM | HT |  |  |  | 3.2991 | 2.4684 | 1.4603 | 0.24497 | -0.77442 | 26.3797 | 25.197 | 23.648 | 22.0154 | 20.3297 | 12.3337 | 8.0909 | 6.4011 | 9.098 | 8.5133 | 7.8337 | 7.1286 | 6.5164 | 32.5266 | 32.0909 | 31.248 | 30.347 | 29.1633 | 23.6858 | 21.2184 | 20.6082 | 3.7929 | 2.9235 | 1.9144 | 0.8613 | -0.0070694 | 26.6195 | 25.797 | 24.5797 | 23.3103 | 22.0011 | 15.1082 | 11.1225 | 9.1715
|  | EGHAM | HE |  |  |  | 2.997 | 1.9766 | 0.78579 | -0.60707 | -1.9765 | 24.8133 | 23.3052 | 21.3052 | 19.1848 | 16.9429 | 6.4399 | 1.346 | 0.0092571 | 8.9429 | 8.2582 | 7.4593 | 6.6144 | 5.8358 | 31.6552 | 30.7735 | 29.1735 | 27.4603 | 25.6572 | 17.495 | 13.844 | 11.8521 | 3.6613 | 2.7348 | 1.6572 | 0.5113 | -0.51727 | 25.9378 | 24.9001 | 22.8276 | 20.6195 | 18.3021 | 7.6929 | 2.8491 | 1.9358
|  | EGHAM | CF |  |  |  | 3.6031 | 2.9133 | 2.1827 | 1.2776 | 0.59599 | 28.0909 | 27.3103 | 26.397 | 25.2327 | 23.995 | 16.5195 | 9.9521 | 5.6195 | 9.2511 | 8.6327 | 8.0572 | 7.398 | 6.9011 | 33.0001 | 32.3827 | 31.9419 | 31.1674 | 30.3511 | 24.8256 | 17.5746 | 7.2746 | 4.0633 | 3.2878 | 2.5501 | 1.698 | 1.147 | 28.0919 | 27.5154 | 27.2113 | 26.4909 | 25.497 | 17.847 | 11.2042 | 7.3011
MANNINGTON GSP | BOURNEMOUTH | ELECTRIC HOUSE | MINIMUM HEADROOM | SZ 08757 91379 | YES | 4.272 | 9.2509 | 9.0621 | 8.8417 | 8.2488 | 7.4488 | 6.5488 | 5.8611 | 5.3346 | 4.8366 | 4.404 | 3.0825 | 2.1356 | 2.0693 | 11.7519 | 11.6009 | 11.4233 | 11.0999 | 10.6529 | 10.1499 | 9.704 | 9.2866 | 8.8693 | 8.4784 | 6.3029 | 1.5131 | -8.193 | 11.1244 | 10.9754 | 10.7978 | 10.3244 | 9.6499 | 8.8825 | 8.2917 | 7.7886 | 7.3142 | 6.9019 | 5.6662 | 5.0295 | 5.008
|  | ELECTRIC HOUSE | EE |  |  |  | 9.2509 | 9.0621 | 8.8417 | 8.2488 | 7.4488 | 6.5488 | 5.8611 | 5.3346 | 4.8366 | 4.404 | 3.0825 | 2.6131 | 2.5754 | 11.7519 | 11.6009 | 11.4233 | 11.0999 | 10.6529 | 10.1499 | 9.704 | 9.2866 | 8.8693 | 8.4784 | 6.3029 | 3.6774 | -0.94911 | 11.1244 | 10.9754 | 10.7978 | 10.3244 | 9.6499 | 8.8825 | 8.2917 | 7.7886 | 7.3142 | 6.9019 | 5.6662 | 5.2672 | 5.2254
|  | ELECTRIC HOUSE | HT |  |  |  | 9.3968 | 9.2652 | 9.1162 | 8.6366 | 7.9764 | 7.1927 | 6.657 | 6.2978 | 5.9193 | 5.506 | 3.5325 | 2.2846 | 2.2478 | 11.8795 | 11.8091 | 11.7274 | 11.5091 | 11.2152 | 10.8672 | 10.6213 | 10.4417 | 10.2478 | 10.0407 | 8.958 | 8.0652 | 7.9499 | 11.2478 | 11.1519 | 11.0386 | 10.6886 | 10.156 | 9.4907 | 9.0488 | 8.7397 | 8.4152 | 8.0346 | 6.1968 | 5.0295 | 5.008
|  | ELECTRIC HOUSE | HE |  |  |  | 9.3642 | 9.2376 | 9.0917 | 8.6172 | 7.9652 | 7.1988 | 6.7213 | 6.4264 | 6.1009 | 5.7437 | 3.2754 | 2.1356 | 2.1499 | 11.8193 | 11.7019 | 11.5642 | 11.2846 | 10.9162 | 10.4672 | 10.1295 | 9.8458 | 9.5366 | 9.1682 | 6.9754 | 4.2356 | -0.16748 | 11.2152 | 11.1142 | 10.9917 | 10.6356 | 10.1356 | 9.4866 | 9.0693 | 8.7907 | 8.5029 | 8.1846 | 6.7019 | 5.5978 | 5.6091
|  | ELECTRIC HOUSE | CF |  |  |  | 9.4631 | 9.3856 | 9.2948 | 8.9182 | 8.3917 | 7.7795 | 7.4346 | 7.2754 | 7.106 | 6.8937 | 5.5937 | 3.5713 | 2.0693 | 11.8815 | 11.7805 | 11.658 | 11.4152 | 11.0774 | 10.6611 | 10.3213 | 10.0305 | 9.6846 | 9.306 | 6.6284 | 1.5131 | -8.193 | 11.304 | 11.2407 | 11.1652 | 10.8876 | 10.4917 | 10.0274 | 9.7417 | 9.5795 | 9.408 | 9.2193 | 8.1101 | 6.9652 | 5.5397
BRAMLEY (FLEE) | WOKINGHAM BSP | ELMS ROAD | MINIMUM HEADROOM | SU 81057 68532 | YES | 3.373 | 5.9514 | 5.3392 | 4.4872 | 3.8514 | 2.9627 | 2.0116 | 0.75756 | -0.64244 | -2.1496 | -3.3853 | -9.221 | -12.9547 | -14.9016 | 8.2264 | 7.7978 | 7.1999 | 6.8662 | 6.257 | 5.5692 | 4.7458 | 3.7968 | 2.7948 | 2.0437 | -1.7348 | -5.8859 | -16.0471 | 6.1471 | 5.5777 | 4.7889 | 4.291 | 3.4736 | 2.5798 | 1.4359 | 0.142 | -1.2345 | -2.3019 | -7.1784 | -10.4978 | -12.1713
|  | ELMS ROAD | EE |  |  |  | 5.9514 | 5.3392 | 4.4872 | 3.8514 | 2.9627 | 2.0116 | 0.75756 | -0.64244 | -2.1496 | -3.3853 | -8.8894 | -11.9833 | -14.3588 | 8.2264 | 7.7978 | 7.1999 | 6.8662 | 6.257 | 5.5692 | 4.7458 | 3.7968 | 2.7948 | 2.0437 | -1.7348 | -5.2512 | -10.5542 | 6.1471 | 5.5777 | 4.7889 | 4.291 | 3.4736 | 2.5798 | 1.4359 | 0.142 | -1.2345 | -2.3019 | -6.9927 | -9.6947 | -11.7702
|  | ELMS ROAD | HT |  |  |  | 6.2167 | 5.6535 | 4.9474 | 4.0994 | 3.2116 | 2.6198 | 1.4076 | 0.1096 | -1.2679 | -2.6679 | -9.221 | -12.9547 | -14.9016 | 8.5192 | 8.209 | 7.8223 | 7.3468 | 6.8192 | 6.5948 | 5.9784 | 5.2835 | 4.5478 | 3.7876 | 0.34067 | -1.4226 | -2.2746 | 6.4359 | 5.9359 | 5.3175 | 4.5747 | 3.7593 | 3.3022 | 2.2471 | 1.0991 | -0.11412 | -1.358 | -7.1784 | -10.4978 | -12.1713
|  | ELMS ROAD | HE |  |  |  | 6.1994 | 5.6912 | 5.0188 | 4.2025 | 3.4076 | 2.8821 | 1.9035 | 0.80348 | -0.44142 | -1.7169 | -7.6047 | -10.8833 | -12.2353 | 8.4488 | 8.1121 | 7.6794 | 7.1519 | 6.6192 | 6.3458 | 5.7223 | 5.0009 | 4.1958 | 3.3397 | -1.0736 | -4.8144 | -9.695 | 6.4144 | 5.9593 | 5.3665 | 4.644 | 3.9247 | 3.5134 | 2.6451 | 1.6573 | 0.54812 | -0.58861 | -5.8111 | -8.708 | -9.8621
|  | ELMS ROAD | CF |  |  |  | 6.5984 | 6.3004 | 5.8147 | 5.2821 | 4.781 | 4.2994 | 3.8463 | 3.6729 | 3.1178 | 2.5188 | -2.7679 | -6.3108 | -9.5067 | 8.6417 | 8.3815 | 8.0009 | 7.607 | 7.1999 | 6.7499 | 6.2509 | 6.0509 | 5.4815 | 4.8682 | 0.084551 | -5.8859 | -16.0471 | 6.7471 | 6.4747 | 6.04 | 5.5808 | 5.1247 | 4.6767 | 4.2349 | 4.1481 | 3.6267 | 3.0655 | -1.5917 | -4.7121 | -7.5141
LOVEDEAN GSP | HAVANT | EMSWORTH | MINIMUM HEADROOM | SU 74861 05807 | YES | 7.528 | -1.2304 | -1.6702 | -2.3488 | -2.9988 | 12.0145 | 11.191 | 9.9594 | 8.4992 | 6.8747 | 5.5563 | -1.9049 | -5.9376 | -6.7661 | 1.2043 | 0.83796 | 0.27265 | -0.26816 | 13.69 | 13.0318 | 12.2043 | 11.2094 | 10.142 | 9.3257 | 3.8767 | 0.45939 | -8.4029 | -0.96714 | -1.3927 | -2.0406 | -2.6631 | 11.6318 | 10.7584 | 9.6778 | 8.3706 | 6.9563 | 5.6267 | -1.6294 | -5.2824 | -5.7284
|  | EMSWORTH | EE |  |  |  | -1.2304 | -1.6702 | -2.3488 | -2.9988 | 12.0145 | 11.191 | 9.9594 | 8.4992 | 6.8747 | 5.5563 | -0.43449 | -4.4631 | -6.3682 | 1.2043 | 0.83796 | 0.27265 | -0.26816 | 13.69 | 13.0318 | 12.2043 | 11.2094 | 10.142 | 9.3257 | 5.2676 | 1.6655 | -2.8284 | -0.96714 | -1.3927 | -2.0406 | -2.6631 | 11.6318 | 10.7584 | 9.6778 | 8.3706 | 6.9563 | 5.8053 | 0.66143 | -2.558 | -4.1182
|  | EMSWORTH | HT |  |  |  | -0.89163 | -1.3141 | -1.6967 | -2.0937 | 12.688 | 12.0176 | 11.2145 | 9.9237 | 8.4696 | 7.0196 | -0.063061 | -4.71 | -6.3784 | 1.539 | 1.2349 | 0.95939 | 0.67878 | 14.4676 | 14.0063 | 13.6757 | 12.9573 | 12.1563 | 11.339 | 7.5288 | 5.3278 | 4.6063 | -0.61 | -1.0069 | -1.3845 | -1.7661 | 12.3033 | 11.6869 | 11.0043 | 9.8614 | 8.5839 | 7.3043 | 1.1257 | -2.7324 | -4.0722
|  | EMSWORTH | HE |  |  |  | -0.97735 | -1.3273 | -1.8773 | -2.3324 | 12.441 | 11.5808 | 10.5298 | 9.09 | 7.4696 | 5.8012 | -1.9049 | -5.9376 | -6.7661 | 1.4329 | 1.1451 | 0.68184 | 0.30327 | 14.0288 | 13.4145 | 12.7329 | 11.6941 | 10.541 | 9.3461 | 3.8767 | 0.48898 | -3.7131 | -0.69673 | -1.0335 | -1.5631 | -2.0059 | 12.038 | 11.0788 | 10.09 | 8.7247 | 7.1992 | 5.6267 | -1.6294 | -5.2824 | -5.7284
|  | EMSWORTH | CF |  |  |  | -0.74571 | -0.94571 | -1.159 | -1.562 | 13.4818 | 13.0369 | 12.4941 | 11.8298 | 11.4869 | 10.6247 | 5.0339 | -0.66612 | -3.6927 | 1.5676 | 1.3461 | 1.1084 | 0.71347 | 14.6043 | 14.1747 | 13.6543 | 13.0288 | 12.7043 | 12.0492 | 7.3788 | 0.45939 | -8.4029 | -0.48143 | -0.68551 | -0.89776 | -1.2824 | 13.0308 | 12.6237 | 12.1298 | 11.5227 | 11.0114 | 10.1818 | 4.9012 | -0.38857 | -3.0355
MELKSHAM GSP | AMESBURY | ENFORD | MINIMUM HEADROOM | SU 13728 51712 | YES | 0.2 | 6.7837 | 6.7031 | 6.5867 | 6.4531 | 6.3571 | 6.2071 | 6.0224 | 5.8653 | 5.6582 | 5.5929 | 5.2082 | 5.0337 | 4.8776 | 7.6214 | 7.5704 | 7.4949 | 7.4041 | 7.3459 | 7.249 | 7.1245 | 7.0316 | 6.8929 | 6.8163 | 6.4235 | 5.8827 | 4.6816 | 6.8653 | 6.7847 | 6.6694 | 6.5388 | 6.4449 | 6.3 | 6.1184 | 5.9653 | 5.7582 | 5.6969 | 5.5276 | 5.4296 | 5.2929
|  | ENFORD | EE |  |  |  | 6.7837 | 6.7031 | 6.5867 | 6.4531 | 6.3571 | 6.2071 | 6.0224 | 5.8653 | 5.6582 | 5.5929 | 5.2082 | 5.0378 | 4.9531 | 7.6214 | 7.5704 | 7.4949 | 7.4041 | 7.3459 | 7.249 | 7.1245 | 7.0316 | 6.8929 | 6.8163 | 6.4235 | 6.0582 | 5.4745 | 6.8653 | 6.7847 | 6.6694 | 6.5388 | 6.4449 | 6.3 | 6.1184 | 5.9653 | 5.7582 | 5.6969 | 5.5276 | 5.4367 | 5.3622
|  | ENFORD | HT |  |  |  | 6.85 | 6.8 | 6.7122 | 6.6418 | 6.5541 | 6.4561 | 6.3612 | 6.2214 | 6.0735 | 5.9173 | 5.2949 | 5.0337 | 4.8776 | 7.6694 | 7.6408 | 7.5837 | 7.548 | 7.4939 | 7.4276 | 7.3806 | 7.2918 | 7.1918 | 7.0867 | 6.7276 | 6.5847 | 6.501 | 6.9316 | 6.8847 | 6.799 | 6.7398 | 6.6571 | 6.5571 | 6.4765 | 6.3378 | 6.1878 | 6.0327 | 5.5306 | 5.4296 | 5.2929
|  | ENFORD | HE |  |  |  | 6.8633 | 6.799 | 6.7133 | 6.6439 | 6.5612 | 6.4663 | 6.3776 | 6.2408 | 6.099 | 5.9418 | 5.3051 | 5.1296 | 5.0612 | 7.6796 | 7.6388 | 7.5827 | 7.5469 | 7.4939 | 7.4224 | 7.3592 | 7.2571 | 7.1469 | 7.0347 | 6.4969 | 6.1184 | 5.549 | 6.9439 | 6.8837 | 6.7959 | 6.7398 | 6.6602 | 6.5612 | 6.4837 | 6.3469 | 6.201 | 6.0459 | 5.5551 | 5.4867 | 5.45
|  | ENFORD | CF |  |  |  | 6.8776 | 6.8255 | 6.7653 | 6.698 | 6.6469 | 6.5816 | 6.502 | 6.4112 | 6.3541 | 6.2612 | 5.7704 | 5.4286 | 5.1806 | 7.6827 | 7.6551 | 7.6122 | 7.5653 | 7.5265 | 7.4714 | 7.4092 | 7.3235 | 7.2673 | 7.1724 | 6.6102 | 5.8827 | 4.6816 | 6.9571 | 6.9143 | 6.8643 | 6.801 | 6.7622 | 6.7051 | 6.6306 | 6.5378 | 6.4837 | 6.3867 | 5.8724 | 5.6327 | 5.5316
COWLEY GSP | YARNTON BSP | EYNSHAM | MINIMUM HEADROOM | SP 42236 10266 | YES | 11.74 | 11.6363 | 11.3771 | 11.022 | 10.5527 | 10.0578 | 5.3486 | 4.2843 | 2.8047 | 1.871 | 0.42306 | -6.3239 | -9.1718 | -10.2606 | 12.1939 | 12.0204 | 11.7959 | 11.5 | 11.1449 | 6.6898 | 6.4633 | 5.7571 | 5.0327 | 4.2847 | -0.2398 | -2.5214 | -7.1224 | 11.4047 | 11.1853 | 10.8935 | 10.5016 | 10.0833 | 5.471 | 4.5394 | 3.3078 | 2.571 | 1.3557 | -4.3647 | -6.7198 | -7.6137
|  | EYNSHAM | EE |  |  |  | 11.6363 | 11.3771 | 11.022 | 10.5527 | 10.0578 | 5.3486 | 4.7812 | 3.5751 | 2.2292 | 0.79143 | -5.929 | -8.7902 | -10.0565 | 12.1939 | 12.0204 | 11.7959 | 11.5 | 11.1449 | 6.6898 | 6.4633 | 5.7888 | 5.0327 | 4.2847 | -0.2398 | -2.499 | -4.9265 | 11.4047 | 11.1853 | 10.8935 | 10.5016 | 10.0833 | 5.471 | 4.9608 | 3.9231 | 2.7669 | 1.5894 | -4.0576 | -6.3851 | -7.4412
|  | EYNSHAM | HT |  |  |  | 11.7853 | 11.5404 | 11.2384 | 10.8047 | 10.3404 | 5.5669 | 4.2843 | 2.8047 | 1.871 | 0.42306 | -6.3239 | -9.1718 | -10.2606 | 12.3092 | 12.1714 | 12.0041 | 11.7684 | 11.5235 | 7.1153 | 6.4867 | 5.7571 | 5.3847 | 4.5643 | 0.56531 | -0.73878 | -1.2286 | 11.518 | 11.3078 | 11.0476 | 10.6802 | 10.2812 | 5.6118 | 4.5394 | 3.3078 | 2.571 | 1.3557 | -4.3647 | -6.7198 | -7.6137
|  | EYNSHAM | HE |  |  |  | 11.7914 | 11.5629 | 11.2782 | 10.8955 | 10.5394 | 5.9302 | 5.0476 | 3.8384 | 2.8465 | 1.4537 | -5.2576 | -8.0463 | -8.9076 | 12.2918 | 12.1388 | 11.9531 | 11.7092 | 11.4847 | 7.1204 | 6.6143 | 5.9531 | 5.4888 | 4.7408 | 0.07551 | -2.1714 | -4.4439 | 11.5261 | 11.3322 | 11.0904 | 10.7639 | 10.4567 | 5.9292 | 5.1639 | 4.1516 | 3.3771 | 2.2292 | -3.4392 | -5.7157 | -6.4239
|  | EYNSHAM | CF |  |  |  | 11.9129 | 11.719 | 11.4792 | 11.2578 | 11.0873 | 6.9516 | 6.7731 | 6.4231 | 6.0078 | 5.3394 | 0.98837 | -5.5249 | -7.3647 | 12.3847 | 12.2102 | 12.0347 | 11.8704 | 11.7214 | 7.5786 | 7.3847 | 7.0929 | 6.7602 | 6.2867 | 3.2316 | -2.5214 | -7.1224 | 11.6486 | 11.4771 | 11.2843 | 11.0976 | 10.9557 | 6.8404 | 6.6924 | 6.4057 | 6.0639 | 5.5078 | 1.8751 | -3.5994 | -5.1535
MINETY GSP | CIRENCESTER BSP | FAIRFORD | MINIMUM HEADROOM | SP 14418 00559 | YES | 6.382 | 5.4582 | 5.2653 | 5.0051 | 4.7602 | 4.4582 | 4.1143 | 4.0255 | 3.5806 | 3.1418 | 2.8337 | 1.1133 | -0.092847 | -0.85917 | 7.676 | 7.5322 | 7.3362 | 7.1515 | 6.9168 | 6.6607 | 6.6219 | 6.3046 | 5.9852 | 5.7679 | 4.4801 | 2.8944 | -0.72193 | 5.2995 | 5.1056 | 4.8383 | 4.6015 | 4.2975 | 3.9699 | 3.9271 | 3.4995 | 3.076 | 2.8026 | 1.3424 | 0.33113 | -0.2903
|  | FAIRFORD | EE |  |  |  | 5.4582 | 5.2653 | 5.0051 | 4.7602 | 4.4582 | 4.1143 | 4.0255 | 3.5806 | 3.1418 | 2.8337 | 1.1133 | 0.10307 | -0.58366 | 7.676 | 7.5322 | 7.3362 | 7.1515 | 6.9168 | 6.6607 | 6.6219 | 6.3046 | 5.9852 | 5.7679 | 4.4801 | 3.2026 | 1.3281 | 5.2995 | 5.1056 | 4.8383 | 4.6015 | 4.2975 | 3.9699 | 3.9271 | 3.4995 | 3.076 | 2.8026 | 1.3424 | 0.49338 | -0.068867
|  | FAIRFORD | HT |  |  |  | 5.549 | 5.3827 | 5.1786 | 4.9867 | 4.7551 | 4.5347 | 4.1429 | 3.7102 | 3.2572 | 3.1684 | 1.1469 | -0.092847 | -0.85917 | 7.7781 | 7.6801 | 7.5475 | 7.4332 | 7.2801 | 7.1424 | 6.9189 | 6.6587 | 6.3852 | 6.4036 | 5.2883 | 4.673 | 4.3179 | 5.4036 | 5.2556 | 5.0536 | 4.8719 | 4.6393 | 4.4322 | 4.0679 | 3.6556 | 3.2271 | 3.2128 | 1.3913 | 0.33113 | -0.2903
|  | FAIRFORD | HE |  |  |  | 5.55 | 5.3969 | 5.2041 | 5.0265 | 4.8153 | 4.6163 | 4.2776 | 3.8939 | 3.498 | 3.4633 | 1.5398 | 0.53266 | 0.032663 | 7.7617 | 7.6515 | 7.5036 | 7.373 | 7.2015 | 7.0475 | 6.8138 | 6.5383 | 6.2464 | 6.2383 | 4.7352 | 3.4454 | 1.6577 | 5.4036 | 5.2638 | 5.073 | 4.9066 | 4.6893 | 4.5026 | 4.1832 | 3.8138 | 3.4301 | 3.4628 | 1.7393 | 0.90868 | 0.50868
|  | FAIRFORD | CF |  |  |  | 5.6082 | 5.4918 | 5.3592 | 5.2388 | 5.0939 | 4.9327 | 4.7949 | 4.5867 | 4.3582 | 4.1337 | 3.1235 | 1.8827 | 0.79899 | 7.7913 | 7.6995 | 7.5811 | 7.4771 | 7.3424 | 7.1842 | 7.0311 | 6.8199 | 6.5903 | 6.3505 | 5.0791 | 2.8944 | -0.72193 | 5.4597 | 5.3515 | 5.226 | 5.1148 | 4.9638 | 4.8015 | 4.6689 | 4.4607 | 4.2342 | 4.0066 | 3.1077 | 2.0271 | 1.123
MINETY GSP | STRATTON (2 X 60) | FARINGDON | MINIMUM HEADROOM | SU 28819 94924 | YES | 10.72 | -4.1072 | 18.6471 | 18.1522 | 17.596 | 17.0777 | 17.0032 | 16.4216 | 15.7613 | 15.1022 | 14.6522 | 12.3134 | 10.3767 | 9.1736 | -0.46242 | 20.8797 | 20.545 | 20.1746 | 19.7889 | 19.7399 | 19.3399 | 18.8685 | 18.3848 | 18.0613 | 16.2481 | 14.244 | 9.144 | -3.994 | 18.2011 | 17.7338 | 17.2185 | 16.7277 | 16.6716 | 16.1267 | 15.5032 | 14.8797 | 14.4644 | 12.3532 | 10.7093 | 9.7389
|  | FARINGDON | EE |  |  |  | -4.1072 | 18.6471 | 18.1522 | 17.596 | 17.0777 | 17.0032 | 16.4216 | 15.7613 | 15.1022 | 14.6522 | 12.3134 | 10.6807 | 9.4522 | -0.46242 | 20.8797 | 20.545 | 20.1746 | 19.7889 | 19.7399 | 19.3399 | 18.8685 | 18.3848 | 18.0613 | 16.2481 | 14.4409 | 11.7471 | -3.994 | 18.2011 | 17.7338 | 17.2185 | 16.7277 | 16.6716 | 16.1267 | 15.5032 | 14.8797 | 14.4644 | 12.3532 | 10.996 | 9.9746
|  | FARINGDON | HT |  |  |  | -3.9409 | 18.8838 | 18.4379 | 17.9634 | 17.6338 | 17.2226 | 16.6593 | 16.4164 | 15.8603 | 15.2818 | 12.3164 | 10.3767 | 9.1736 | -0.32364 | 21.0971 | 20.8522 | 20.5767 | 20.3756 | 20.1256 | 19.8032 | 19.7113 | 19.3767 | 19.0318 | 17.3838 | 16.4726 | 15.9491 | -3.8379 | 18.4246 | 18.0318 | 17.5971 | 17.2838 | 16.896 | 16.3716 | 16.1838 | 15.6522 | 15.1052 | 12.3746 | 10.7093 | 9.7389
|  | FARINGDON | HE |  |  |  | -3.9409 | 18.9001 | 18.4726 | 18.0328 | 17.7236 | 17.3175 | 16.8348 | 16.6726 | 16.196 | 15.693 | 13.0767 | 11.5083 | 10.7083 | -0.35018 | 21.0511 | 20.7858 | 20.4991 | 20.2787 | 19.9828 | 19.6471 | 19.5369 | 19.1828 | 18.8113 | 16.7113 | 14.9022 | 12.394 | -3.8379 | 18.4389 | 18.0634 | 17.6603 | 17.3675 | 16.9858 | 16.5338 | 16.4154 | 15.9552 | 15.4818 | 13.0848 | 11.7777 | 11.1369
|  | FARINGDON | CF |  |  |  | -3.8491 | 19.0746 | 18.7583 | 18.4379 | 18.1807 | 17.9685 | 17.7297 | 17.443 | 17.1318 | 17.2297 | 15.4358 | 13.7338 | 12.096 | -0.29609 | 21.142 | 20.9216 | 20.6869 | 20.4685 | 20.2685 | 20.0256 | 19.7338 | 19.4205 | 19.3746 | 17.296 | 14.244 | 9.144 | -3.743 | 18.6144 | 18.3307 | 18.0409 | 17.7909 | 17.5909 | 17.3654 | 17.0889 | 16.7909 | 16.8981 | 15.2052 | 13.646 | 12.2246
LOVEDEAN GSP | WYMERING BSP | FARLINGTON | MINIMUM HEADROOM | SU 67400 04843 | YES | 2.83 | 15.369 | 15.2241 | 15.0639 | 14.8588 | 14.6424 | 13.1924 | 12.8771 | 12.4935 | 12.2414 | 11.9088 | 10.62 | 9.9445 | 9.619 | 18.3092 | 18.2 | 18.0786 | 17.9245 | 17.7571 | 16.3673 | 16.1408 | 15.8653 | 15.7143 | 15.5092 | 14.6786 | 13.5082 | 8.9643 | 15.7924 | 15.668 | 15.5363 | 15.3669 | 15.1782 | 13.7394 | 13.4394 | 13.0822 | 12.8761 | 12.5945 | 11.369 | 10.7363 | 10.4241
|  | FARLINGTON | EE |  |  |  | 15.369 | 15.2241 | 15.0639 | 14.8588 | 14.6424 | 13.1924 | 12.8771 | 12.4935 | 12.2414 | 11.9088 | 10.6598 | 10.2098 | 10.2618 | 18.3092 | 18.2 | 18.0786 | 17.9245 | 17.7571 | 16.3673 | 16.1408 | 15.8653 | 15.7143 | 15.5092 | 14.7643 | 14.4102 | 12.3337 | 15.7924 | 15.668 | 15.5363 | 15.3669 | 15.1782 | 13.7394 | 13.4394 | 13.0822 | 12.8761 | 12.5945 | 11.4322 | 11.0292 | 11.0741
|  | FARLINGTON | HT |  |  |  | 15.4771 | 15.3751 | 15.2465 | 15.0996 | 14.9414 | 13.5496 | 13.3118 | 13.02 | 12.7027 | 12.3271 | 10.7945 | 10.0435 | 9.7924 | 18.398 | 18.3255 | 18.2367 | 18.1265 | 18.0153 | 16.6745 | 16.5112 | 16.3061 | 16.0867 | 15.8561 | 14.9316 | 14.4633 | 14.2684 | 15.8792 | 15.7996 | 15.6955 | 15.5731 | 15.4445 | 14.0843 | 13.8598 | 13.5782 | 13.2812 | 12.97 | 11.5557 | 10.8639 | 10.6282
|  | FARLINGTON | HE |  |  |  | 15.4731 | 15.3649 | 15.2302 | 15.0761 | 14.9108 | 13.5027 | 13.2506 | 12.9363 | 12.5843 | 12.1822 | 10.62 | 9.9445 | 9.619 | 18.3898 | 18.3112 | 18.2112 | 18.0918 | 17.9684 | 16.6133 | 16.4327 | 16.2 | 15.9551 | 15.6929 | 14.6786 | 14.2296 | 12.4827 | 15.8771 | 15.7914 | 15.6822 | 15.5557 | 15.42 | 14.0414 | 13.7996 | 13.4976 | 13.1771 | 12.8373 | 11.369 | 10.7363 | 10.4241
|  | FARLINGTON | CF |  |  |  | 15.5588 | 15.5027 | 15.4322 | 15.3506 | 15.2649 | 13.9578 | 13.8322 | 13.6649 | 13.4853 | 13.2812 | 12.1843 | 10.9149 | 9.9669 | 18.452 | 18.4071 | 18.3531 | 18.2867 | 18.2163 | 16.9276 | 16.8296 | 16.7 | 16.5561 | 16.398 | 15.5531 | 13.5082 | 8.9643 | 15.9282 | 15.8873 | 15.8384 | 15.769 | 15.6965 | 14.4057 | 14.3006 | 14.1598 | 14.0169 | 13.822 | 12.7741 | 11.6373 | 10.7578
BRAMLEY (FLEE) | CAMBERLEY RESERVE | FARNBOROUGH | MINIMUM HEADROOM | SU 88404 53930 | YES | 4.526 | 10.8875 | 10.1692 | 9.1518 | 8.66 | 7.8212 | 6.5692 | 4.9467 | 3.2712 | 1.613 | 0.27631 | -6.3084 | -10.3818 | -12.6951 | 13.6794 | 13.1263 | 12.262 | 11.909 | 11.2375 | 10.3528 | 9.2763 | 8.109 | 6.9263 | 6.0151 | 1.1171 | -4.2451 | -16.6859 | 10.8977 | 10.2345 | 9.2661 | 8.859 | 8.0641 | 6.9304 | 5.4733 | 3.9386 | 2.4141 | 1.2467 | -4.4961 | -8.0727 | -9.9676
|  | FARNBOROUGH | EE |  |  |  | 10.8875 | 10.1692 | 9.1518 | 8.66 | 7.8212 | 6.5692 | 4.9467 | 3.2712 | 1.613 | 0.27631 | -6.3084 | -9.791 | -12.5298 | 13.6794 | 13.1263 | 12.262 | 11.909 | 11.2375 | 10.3528 | 9.2763 | 8.109 | 6.9263 | 6.0151 | 1.1171 | -3.1778 | -9.5716 | 10.8977 | 10.2345 | 9.2661 | 8.859 | 8.0641 | 6.9304 | 5.4733 | 3.9386 | 2.4141 | 1.2467 | -4.4961 | -7.5533 | -9.8441
|  | FARNBOROUGH | HT |  |  |  | 11.2406 | 10.6447 | 9.8396 | 9.1886 | 8.4855 | 7.6988 | 6.2712 | 4.8437 | 3.3651 | 1.8508 | -6.0472 | -10.3818 | -12.6951 | 14.0375 | 13.66 | 13.059 | 12.6314 | 12.162 | 11.7916 | 11.0284 | 10.2222 | 9.3733 | 8.4896 | 4.1763 | 2.0018 | 1.0426 | 11.2682 | 10.7365 | 9.9967 | 9.3896 | 8.7273 | 8.111 | 6.8702 | 5.6008 | 4.2804 | 2.9161 | -4.1798 | -8.0727 | -9.9676
|  | FARNBOROUGH | HE |  |  |  | 11.1977 | 10.6079 | 9.7977 | 9.1467 | 8.4324 | 7.6365 | 6.3059 | 4.962 | 3.562 | 2.1253 | -5.2533 | -9.1533 | -10.7563 | 13.9426 | 13.4988 | 12.8171 | 12.3028 | 11.7314 | 11.2579 | 10.3855 | 9.4528 | 8.4498 | 7.4008 | 1.6008 | -3.089 | -9.0155 | 11.2243 | 10.6957 | 9.9508 | 9.3457 | 8.6712 | 8.0518 | 6.8886 | 5.6896 | 4.4273 | 3.1171 | -3.8502 | -7.3982 | -8.7196
|  | FARNBOROUGH | CF |  |  |  | 11.459 | 11.063 | 10.4406 | 10.0712 | 9.6345 | 8.861 | 8.0743 | 7.6804 | 6.9182 | 6.1202 | 0.87938 | -3.4502 | -7.2206 | 14.0896 | 13.7335 | 13.1212 | 12.76 | 12.3243 | 11.6906 | 10.9845 | 10.5835 | 9.8222 | 9.009 | 3.4171 | -4.2451 | -16.6859 | 11.462 | 11.1059 | 10.5243 | 10.1804 | 9.7651 | 9.0835 | 8.3814 | 8.111 | 7.4171 | 6.6875 | 1.9661 | -2.1186 | -5.6941
BRAMLEY (FLEE) | PYESTOCK BSP | FARNBORO AIRFIELD | MINIMUM HEADROOM | SU 85838 54449 | YES | 5.872 | 5.9921 | 5.9452 | 5.887 | 5.8288 | 5.7666 | 5.689 | 5.6268 | 5.5543 | 5.4819 | 5.4248 | 5.2115 | 4.9064 | 4.6982 | 8.0952 | 8.0676 | 8.0258 | 7.9799 | 7.9166 | 7.8503 | 7.8003 | 7.736 | 7.6737 | 7.6248 | 7.4033 | 7.1554 | 6.5788 | 8.7605 | 8.7196 | 8.6696 | 8.6237 | 8.5717 | 8.5156 | 8.4727 | 8.4207 | 8.3686 | 8.3288 | 8.2207 | 8.0105 | 7.836
|  | FARNBORO AIRFIELD | EE |  |  |  | 5.9921 | 5.9452 | 5.887 | 5.8288 | 5.7666 | 5.689 | 5.6268 | 5.5543 | 5.4819 | 5.4248 | 5.2115 | 4.9064 | 4.6982 | 8.0952 | 8.0676 | 8.0258 | 7.9799 | 7.9166 | 7.8503 | 7.8003 | 7.736 | 7.6737 | 7.6248 | 7.4033 | 7.1554 | 6.8299 | 8.7605 | 8.7196 | 8.6696 | 8.6237 | 8.5717 | 8.5156 | 8.4727 | 8.4207 | 8.3686 | 8.3288 | 8.2207 | 8.0105 | 7.836
|  | FARNBORO AIRFIELD | HT |  |  |  | 6.0094 | 5.9615 | 5.9125 | 5.8594 | 5.8013 | 5.736 | 5.6788 | 5.6248 | 5.5635 | 5.5084 | 5.239 | 4.9268 | 4.7237 | 8.1094 | 8.0829 | 8.0564 | 8.0156 | 7.9666 | 7.9196 | 7.8768 | 7.837 | 7.7901 | 7.7574 | 7.5799 | 7.4543 | 7.3676 | 8.7737 | 8.7339 | 8.6941 | 8.6503 | 8.6033 | 8.5584 | 8.5186 | 8.4839 | 8.4411 | 8.4084 | 8.2717 | 8.0441 | 7.8737
|  | FARNBORO AIRFIELD | HE |  |  |  | 6.0074 | 5.9635 | 5.9176 | 5.8666 | 5.8115 | 5.7492 | 5.6901 | 5.6329 | 5.5717 | 5.5166 | 5.2901 | 5.0676 | 4.9441 | 8.1064 | 8.0809 | 8.0513 | 8.0074 | 7.9513 | 7.9013 | 7.8513 | 7.8054 | 7.7523 | 7.7105 | 7.4788 | 7.2554 | 6.9625 | 8.7727 | 8.735 | 8.6972 | 8.6543 | 8.6084 | 8.5666 | 8.5258 | 8.489 | 8.4472 | 8.4125 | 8.2799 | 8.1492 | 8.0431
|  | FARNBORO AIRFIELD | CF |  |  |  | 6.0237 | 5.9911 | 5.9543 | 5.9135 | 5.8768 | 5.836 | 5.8074 | 5.7758 | 5.7411 | 5.7013 | 5.5339 | 5.3666 | 5.2319 | 8.1135 | 8.0952 | 8.0737 | 8.0339 | 7.9992 | 7.9492 | 7.9227 | 7.8839 | 7.8472 | 7.8064 | 7.5952 | 7.2452 | 6.5788 | 8.7839 | 8.7554 | 8.7258 | 8.689 | 8.6564 | 8.6207 | 8.5992 | 8.5748 | 8.5492 | 8.5196 | 8.4217 | 8.3319 | 8.2574
BRAMLEY (FLEE) | ALDERSHOT BSP | FARNHAM | MINIMUM HEADROOM | SU 84517 47217 | YES | 4.637 | 7.247 | 6.2909 | 5.2705 | 4.0664 | 2.8144 | 1.3133 | -0.26216 | -2.0622 | -3.7764 | -5.1989 | -13.0867 | -16.7336 | -17.3591 | 12.1225 | 11.3603 | 10.6062 | 9.7307 | 8.8368 | 7.7521 | 6.6144 | 5.2868 | 4.0236 | 2.9827 | -2.9183 | -5.606 | -9.7244 | 8.3991 | 7.5542 | 6.746 | 5.7552 | 5.0093 | 3.5878 | 2.0899 | 0.36743 | -1.2724 | -2.6295 | -10.2132 | -13.6928 | -14.2795
|  | FARNHAM | EE |  |  |  | 7.247 | 6.2909 | 5.2705 | 4.0664 | 2.8144 | 1.3133 | -0.26216 | -2.0622 | -3.7764 | -5.1989 | -9.8693 | -10.9877 | -11.1775 | 12.1225 | 11.3603 | 10.6062 | 9.7307 | 8.8368 | 7.7521 | 6.6144 | 5.2868 | 4.0236 | 2.9827 | -0.31522 | -1.003 | -4.352 | 8.3991 | 7.5542 | 6.746 | 5.7552 | 5.0093 | 3.5878 | 2.0899 | 0.36743 | -1.2724 | -2.6295 | -7.053 | -8.0662 | -8.2326
|  | FARNHAM | HT |  |  |  | 7.7909 | 7.2348 | 6.6215 | 5.8001 | 4.8215 | 3.7001 | 2.5715 | 1.4409 | 0.1062 | -1.2764 | -7.4489 | -10.2326 | -10.8183 | 12.5236 | 12.1011 | 11.6715 | 11.1042 | 10.4256 | 9.646 | 8.8582 | 8.0593 | 7.095 | 6.095 | 1.6899 | -0.20298 | -0.58461 | 8.8287 | 8.196 | 7.5521 | 6.8256 | 5.9236 | 4.895 | 3.8858 | 3.3287 | 2.3287 | 1.1633 | -4.7203 | -7.3438 | -7.8816
|  | FARNHAM | HE |  |  |  | 7.6633 | 6.9266 | 6.0409 | 5.0062 | 3.7644 | 2.3184 | 0.82559 | -0.77441 | -2.6071 | -4.5183 | -13.0867 | -16.7336 | -17.3591 | 12.398 | 11.8531 | 11.2031 | 10.4572 | 9.5644 | 8.5256 | 7.445 | 6.2664 | 4.9042 | 3.4746 | -2.9183 | -5.606 | -6.204 | 8.7399 | 8.0613 | 7.3644 | 6.6021 | 5.6419 | 4.5327 | 3.1338 | 1.6062 | -0.14992 | -1.9887 | -10.2132 | -13.6928 | -14.2795
|  | FARNHAM | CF |  |  |  | 7.9562 | 7.497 | 7.1052 | 6.595 | 5.8991 | 5.1093 | 4.4001 | 3.4909 | 2.6001 | 1.5246 | -4.8336 | -10.353 | -13.6285 | 12.6113 | 12.2195 | 11.9266 | 11.548 | 11.0736 | 10.5093 | 9.997 | 9.3011 | 8.6276 | 7.8042 | 2.9868 | -1.5999 | -9.7244 | 9.0093 | 8.4899 | 8.0603 | 7.5521 | 6.994 | 6.3307 | 5.8236 | 5.2287 | 4.8113 | 3.7766 | -2.3346 | -7.605 | -10.6979
IVER 132KV | SLOUGH | FARNHAM ROYAL | MINIMUM HEADROOM | SU 95597 82844 | YES | 9.43 | 7.1555 | 5.8279 | 4.1402 | 3.2187 | 2.1565 | 1.0096 | -0.8078 | -4.8721 | -8.319 | -11.3823 | -22.7976 | -31.5568 | -35.3976 | 15.9177 | 14.7034 | 13.1677 | 12.3922 | 11.532 | 10.5891 | 9.3065 | 5.3473 | 2.134 | -0.98739 | -11.6119 | -20.7894 | -33.0323 | 8.9912 | 7.7279 | 6.0136 | 5.0718 | 4.0402 | 2.9085 | 1.2116 | -3.2302 | -6.8996 | -10.1945 | -22.2517 | -31.4996 | -36.019
|  | FARNHAM ROYAL | EE |  |  |  | 7.1555 | 5.8279 | 4.1402 | 3.2187 | 2.1565 | 1.0096 | -0.8078 | -4.8721 | -8.319 | -11.3823 | -21.4364 | -27.6343 | -30.2843 | 15.9177 | 14.7034 | 13.1677 | 12.3922 | 11.532 | 10.5891 | 9.3065 | 5.3473 | 2.134 | -0.98739 | -11.6119 | -20.7894 | -33.0323 | 8.9912 | 7.7279 | 6.0136 | 5.0718 | 4.0402 | 2.9085 | 1.2116 | -3.2302 | -6.8996 | -10.1945 | -20.5782 | -26.7915 | -30.3639
|  | FARNHAM ROYAL | HT |  |  |  | 7.5463 | 6.0555 | 4.4259 | 4.0055 | 3.2861 | 2.5014 | 1.0983 | -2.4588 | -5.568 | -9.018 | -22.7976 | -31.5568 | -35.3976 | 16.3851 | 15.1483 | 13.8034 | 13.5871 | 13.0973 | 12.5453 | 11.7442 | 8.3259 | 5.5361 | 2.382 | -9.1394 | -16.7721 | -21.2251 | 9.5177 | 8.0596 | 6.4422 | 6.1024 | 5.3738 | 4.5677 | 3.2575 | -0.72208 | -4.0813 | -7.8262 | -22.2517 | -31.4996 | -36.019
|  | FARNHAM ROYAL | HE |  |  |  | 7.5718 | 6.1473 | 4.58 | 4.2238 | 3.5769 | 2.881 | 1.6432 | -1.1884 | -3.1578 | -5.367 | -15.4762 | -21.2813 | -25.1476 | 16.3014 | 15.0034 | 13.58 | 13.2759 | 12.6789 | 12.0136 | 11.1024 | 8.2504 | 6.4922 | 4.483 | -6.3098 | -15.4915 | -28.0894 | 9.534 | 8.13 | 6.5718 | 6.2891 | 5.631 | 4.9065 | 3.7483 | 0.61771 | -1.4058 | -3.6649 | -14.1282 | -20.1098 | -24.5956
|  | FARNHAM ROYAL | CF |  |  |  | 7.9759 | 6.9238 | 5.7575 | 5.331 | 5.2177 | 4.7789 | 4.2932 | 2.5381 | 0.92282 | -0.49147 | -6.1639 | -11.8496 | -16.8517 | 16.5065 | 15.3698 | 14.1157 | 13.6096 | 13.3473 | 12.7381 | 12.0238 | 9.7463 | 7.6851 | 5.8442 | -1.9792 | -13.4884 | -32.6609 | 9.8932 | 8.8075 | 7.584 | 7.0871 | 7.081 | 6.6177 | 6.1044 | 4.0422 | 2.1993 | 0.61771 | -4.9925 | -10.1292 | -14.62
LALEHAM | EAST BEDFONT A | FELTHAM | MINIMUM HEADROOM | TQ 10628 72811 | YES | 1.895 | 10.3466 | 10.0456 | 9.5353 | 8.9353 | 8.1037 | 7.2619 | 6.4088 | 5.6078 | 4.7415 | 4.1404 | 1.37 | -0.3371 | -1.3391 | 13.019 | 12.8813 | 12.6466 | 12.3588 | 11.8568 | 11.3568 | 10.8915 | 10.417 | 9.7976 | 9.2976 | 7.7119 | 6.8139 | 5.7149 | 10.6211 | 10.3792 | 9.9496 | 9.418 | 8.6313 | 7.8537 | 7.0956 | 6.3945 | 5.6476 | 5.1741 | 2.8445 | 1.2956 | 0.33535
|  | FELTHAM | EE |  |  |  | 10.3466 | 10.1098 | 9.6996 | 9.2078 | 8.5353 | 7.6343 | 7.0874 | 6.1262 | 5.017 | 4.1404 | 1.37 | -0.095265 | -1.3391 | 13.019 | 12.8813 | 12.6517 | 12.3762 | 11.9619 | 11.3568 | 11.0782 | 10.47 | 9.7976 | 9.2976 | 7.7119 | 6.8139 | 5.7149 | 10.6211 | 10.3792 | 9.9833 | 9.5282 | 8.969 | 8.1547 | 7.6956 | 6.8598 | 5.917 | 5.1741 | 2.8445 | 1.4935 | 0.33535
|  | FELTHAM | HT |  |  |  | 10.4384 | 10.0456 | 9.5353 | 8.9353 | 8.1037 | 7.2619 | 6.4088 | 5.6078 | 4.7415 | 4.318 | 1.3935 | -0.3371 | -1.3238 | 13.0915 | 12.8915 | 12.6466 | 12.3588 | 11.8568 | 11.3853 | 10.8915 | 10.417 | 9.9027 | 9.7425 | 8.1292 | 7.3098 | 6.9211 | 10.7445 | 10.3956 | 9.9496 | 9.418 | 8.6313 | 7.8537 | 7.0956 | 6.3945 | 5.6476 | 5.3251 | 2.8772 | 1.2956 | 0.36596
|  | FELTHAM | HE |  |  |  | 10.4323 | 10.2292 | 9.8558 | 9.4456 | 8.9384 | 8.218 | 7.5088 | 6.6384 | 5.6302 | 5.0956 | 2.3394 | 0.9578 | 0.36188 | 13.0782 | 12.967 | 12.7609 | 12.5486 | 12.2945 | 11.8558 | 11.4231 | 10.8874 | 10.2813 | 10.0343 | 8.3221 | 7.4333 | 6.6282 | 10.7384 | 10.5466 | 10.2068 | 9.8353 | 9.3731 | 8.6966 | 8.0313 | 7.2782 | 6.4119 | 5.9894 | 3.7078 | 2.4404 | 1.8833
|  | FELTHAM | CF |  |  |  | 10.517 | 10.4476 | 10.3598 | 10.2558 | 10.1537 | 10.0486 | 9.8915 | 9.568 | 9.1292 | 8.5986 | 4.1394 | 2.7088 | 1.6966 | 13.119 | 13.068 | 12.9976 | 12.9098 | 12.8374 | 12.7537 | 12.6088 | 12.3609 | 12.0364 | 11.6558 | 9.0139 | 7.6792 | 6.066 | 10.8221 | 10.7466 | 10.6435 | 10.5343 | 10.4139 | 10.2864 | 10.1037 | 9.7639 | 9.3466 | 8.8935 | 5.3139 | 4.0853 | 3.1558
MANNINGTON GSP | MANNINGTON BSP | FERNDOWN | MINIMUM HEADROOM | SU 06593 00685 | YES | 6.036 | 19.8584 | 19.1706 | 18.5767 | 16.6665 | 15.4757 | 13.1084 | 10.5839 | 7.6757 | 6.0941 | 2.3104 | -14.6314 | -24.459 | -34.157 | 25.8216 | 25.2941 | 24.6349 | 22.6043 | 21.4655 | 18.8992 | 16.3686 | 13.4349 | 12.191 | 8.3043 | -7.4427 | -19.96 | -32.2784 | 21.1073 | 20.5094 | 19.839 | 17.7339 | 16.4777 | 13.7798 | 10.9492 | 7.6777 | 5.9992 | 1.5349 | -17.2825 | -27.6396 | -38.758
|  | FERNDOWN | EE |  |  |  | 19.8584 | 19.1706 | 18.5971 | 17.7747 | 16.7982 | 14.3869 | 12.2073 | 10.7849 | 7.7971 | 5.8155 | -7.6865 | -14.0896 | -23.5927 | 25.8216 | 25.2941 | 24.8726 | 24.2492 | 23.4961 | 21.043 | 19.0084 | 18.0216 | 15.0645 | 13.2573 | -0.32838 | -7.4947 | -22.0906 | 21.1073 | 20.5094 | 20.0267 | 19.2818 | 18.3522 | 15.7624 | 13.4124 | 12.0645 | 8.7553 | 6.639 | -8.4814 | -15.0029 | -25.7284
|  | FERNDOWN | HT |  |  |  | 20.2573 | 19.7094 | 18.8543 | 17.5308 | 17.0318 | 13.1084 | 10.5839 | 7.6757 | 6.0941 | 2.3104 | -14.6314 | -23.1876 | -34.157 | 26.1104 | 25.7379 | 24.9573 | 23.6471 | 23.3196 | 18.8992 | 16.3686 | 13.4349 | 12.191 | 8.3043 | -7.4427 | -13.5723 | -25.0365 | 21.3961 | 20.9869 | 20.1533 | 18.7655 | 18.3165 | 13.7798 | 10.9492 | 7.6777 | 5.9992 | 1.5349 | -17.2825 | -26.0692 | -38.758
|  | FERNDOWN | HE |  |  |  | 20.2002 | 19.6359 | 18.5767 | 16.6665 | 15.4757 | 14.1553 | 11.5849 | 8.7012 | 7.3747 | 5.9941 | -12.1304 | -24.459 | -29.2682 | 26.0635 | 25.6594 | 24.6349 | 22.6043 | 21.4655 | 20.3247 | 17.7002 | 14.7859 | 13.8543 | 12.8757 | -5.2161 | -19.96 | -30.0733 | 21.3635 | 20.9237 | 19.839 | 17.7339 | 16.4777 | 15.2175 | 12.3257 | 9.1012 | 7.8471 | 6.5369 | -13.7672 | -27.6396 | -33.0508
|  | FERNDOWN | CF |  |  |  | 20.5063 | 20.1594 | 19.8165 | 19.4114 | 18.4614 | 16.7053 | 15.6104 | 14.5604 | 13.4022 | 11.9982 | 2.1461 | -11.3049 | -21.8621 | 26.2165 | 25.9492 | 25.7104 | 25.4175 | 24.4777 | 22.639 | 21.5114 | 20.5104 | 19.4104 | 18.0196 | 6.7767 | -11.2804 | -32.2784 | 21.5349 | 21.2604 | 21.0053 | 20.6716 | 19.6879 | 17.8645 | 16.6879 | 15.6298 | 14.4349 | 12.8992 | 2.2206 | -12.6906 | -24.8743
BRAMLEY (FLEE) | FERNHURST | FIVE OAKS | MINIMUM HEADROOM | TQ 10647 29057 | YES | 1.891 | 5.6485 | 5.4342 | 5.1362 | 4.8607 | 4.5005 | 4.0117 | 3.4587 | 3.3372 | 2.9168 | 2.524 | 1.0842 | 0.091327 | -0.53112 | 6.4357 | 6.3112 | 6.1582 | 5.9969 | 5.8143 | 5.6265 | 5.4204 | 5.3724 | 5.202 | 5.0327 | 4.2102 | 3.602 | 2.4673 | 6.5122 | 6.298 | 6.0194 | 5.7276 | 5.3459 | 4.898 | 4.399 | 4.3224 | 3.9429 | 3.6153 | 2.3704 | 1.5327 | 1.0255
|  | FIVE OAKS | EE |  |  |  | 5.6485 | 5.4342 | 5.1362 | 4.8607 | 4.5005 | 4.0117 | 3.4587 | 3.3372 | 2.9168 | 2.6046 | 1.1046 | 0.29031 | -0.26786 | 6.4357 | 6.3112 | 6.1582 | 5.9969 | 5.8143 | 5.6265 | 5.4204 | 5.3724 | 5.202 | 5.0327 | 4.2102 | 3.602 | 2.8827 | 6.5122 | 6.298 | 6.0194 | 5.7276 | 5.3459 | 4.898 | 4.399 | 4.3224 | 3.9429 | 3.6663 | 2.3704 | 1.6878 | 1.2286
|  | FIVE OAKS | HT |  |  |  | 5.7811 | 5.6189 | 5.3934 | 5.0923 | 4.7362 | 4.2821 | 3.826 | 3.4046 | 2.974 | 2.524 | 1.0842 | 0.091327 | -0.53112 | 6.4745 | 6.3592 | 6.2245 | 6.0735 | 5.9306 | 5.7643 | 5.6092 | 5.451 | 5.2837 | 5.0786 | 4.4306 | 4.0122 | 3.7316 | 6.5806 | 6.3959 | 6.15 | 5.8827 | 5.5735 | 5.1827 | 4.7867 | 4.4112 | 4.0235 | 3.6153 | 2.3765 | 1.5327 | 1.0255
|  | FIVE OAKS | HE |  |  |  | 5.7781 | 5.6189 | 5.4097 | 5.1658 | 4.7974 | 4.3556 | 3.9372 | 3.5628 | 3.177 | 2.7821 | 1.4291 | 0.62602 | 0.20867 | 6.4694 | 6.3551 | 6.2184 | 6.0704 | 5.9092 | 5.7398 | 5.5857 | 5.4265 | 5.2612 | 5.0816 | 4.3286 | 3.7122 | 3.0337 | 6.5816 | 6.4071 | 6.1816 | 5.9408 | 5.6235 | 5.2398 | 4.8816 | 4.5439 | 4.1929 | 3.8347 | 2.6735 | 1.998 | 1.6653
|  | FIVE OAKS | CF |  |  |  | 5.8117 | 5.6811 | 5.5158 | 5.3321 | 5.0985 | 4.7434 | 4.423 | 4.2036 | 3.9321 | 3.6577 | 2.6872 | 1.6628 | 0.775 | 6.4847 | 6.3776 | 6.2592 | 6.1276 | 5.9959 | 5.8367 | 5.6939 | 5.5786 | 5.4398 | 5.298 | 4.7684 | 3.8296 | 2.4673 | 6.6051 | 6.4816 | 6.3041 | 6.1051 | 5.8888 | 5.5816 | 5.3082 | 5.1133 | 4.8714 | 4.6235 | 3.7827 | 2.8908 | 2.1337
AMERSHAM | LOUDWATER BSP | FLACKWELL HEATH | MINIMUM HEADROOM | SU 90667 89318 | YES | 2.41 | 17.0567 | 16.7792 | 16.4312 | 16.0537 | 15.968 | 15.6047 | 14.9129 | 14.1557 | 13.3914 | 12.7782 | 9.0782 | 6.37 | 4.9139 | 18.7976 | 18.5333 | 18.1761 | 17.7812 | 17.7945 | 17.422 | 16.9108 | 16.318 | 15.7139 | 15.3292 | 13.2884 | 10.8996 | 4.4445 | 16.1843 | 15.8843 | 15.47 | 15.0016 | 15.019 | 14.5986 | 13.9333 | 13.1557 | 12.37 | 11.8659 | 9.0037 | 6.7516 | 5.5476
|  | FLACKWELL HEATH | EE |  |  |  | 17.0567 | 16.7792 | 16.4312 | 16.0537 | 15.968 | 15.6047 | 14.9129 | 14.1557 | 13.3914 | 12.7782 | 9.3996 | 6.9149 | 5.1476 | 18.7976 | 18.5333 | 18.1761 | 17.7812 | 17.7945 | 17.422 | 16.9108 | 16.318 | 15.7139 | 15.3292 | 13.2884 | 11.1761 | 7.7935 | 16.1843 | 15.8843 | 15.47 | 15.0016 | 15.019 | 14.5986 | 13.9333 | 13.1557 | 12.37 | 11.8659 | 9.2006 | 7.2292 | 5.7465
|  | FLACKWELL HEATH | HT |  |  |  | 17.1812 | 16.9384 | 16.6476 | 16.37 | 16.0445 | 15.6884 | 15.2537 | 14.5445 | 13.8078 | 13.0567 | 9.0782 | 6.37 | 4.9139 | 19.0108 | 18.8373 | 18.6108 | 18.4108 | 18.1465 | 17.8445 | 17.8169 | 17.418 | 16.9924 | 16.5465 | 14.5088 | 13.4629 | 12.9618 | 16.3884 | 16.1496 | 15.8445 | 15.57 | 15.2088 | 14.8037 | 14.6078 | 13.9741 | 13.2945 | 12.5965 | 9.0037 | 6.7516 | 5.5476
|  | FLACKWELL HEATH | HE |  |  |  | 17.1955 | 16.9792 | 16.7169 | 16.468 | 16.1731 | 15.8496 | 15.5659 | 14.9955 | 14.3924 | 13.7669 | 10.4588 | 7.9884 | 6.8608 | 18.9761 | 18.7884 | 18.5343 | 18.3118 | 18.021 | 17.6924 | 17.6598 | 17.2496 | 16.8037 | 16.3302 | 13.822 | 11.6669 | 8.5373 | 16.3914 | 16.1741 | 15.8904 | 15.6424 | 15.3108 | 14.9384 | 14.8465 | 14.3231 | 13.7598 | 13.172 | 10.1955 | 8.2169 | 7.2802
|  | FLACKWELL HEATH | CF |  |  |  | 17.322 | 17.1914 | 17.0659 | 16.9139 | 16.7792 | 16.6037 | 16.3955 | 16.1384 | 16.1588 | 15.8629 | 13.7129 | 11.3639 | 9.069 | 19.0363 | 18.8669 | 18.6996 | 18.4853 | 18.2986 | 18.0333 | 17.7251 | 17.3435 | 17.3904 | 17.0343 | 14.4924 | 10.8996 | 4.4445 | 16.4996 | 16.3414 | 16.1924 | 15.9996 | 15.8486 | 15.621 | 15.3567 | 15.0261 | 15.1965 | 14.9139 | 12.8802 | 10.8955 | 8.9771
NURSLING GSP | ROWNHAMS | FLETCHWOOD | MINIMUM HEADROOM | SU 33800 12142 | YES | 4.638 | 14.5434 | 14.025 | 13.677 | 12.9709 | 12.276 | 11.4822 | 10.1668 | 8.7362 | 7.2301 | 6.0985 | 0.28725 | -3.7025 | -5.9872 | 17.5883 | 17.2546 | 17.0413 | 16.6087 | 16.1648 | 15.6219 | 14.7924 | 13.8475 | 12.8526 | 12.173 | 8.4995 | 4.8219 | -4.4097 | 14.4362 | 13.9505 | 13.6546 | 13.0138 | 12.373 | 11.6393 | 10.4536 | 9.1526 | 7.7934 | 6.8005 | 1.7342 | -1.6423 | -3.5546
|  | FLETCHWOOD | EE |  |  |  | 14.5434 | 14.025 | 13.677 | 12.9709 | 12.276 | 11.4822 | 10.1668 | 8.7362 | 7.2301 | 6.0985 | 0.68623 | -2.9342 | -5.5719 | 17.5883 | 17.2546 | 17.0413 | 16.6087 | 16.1648 | 15.6219 | 14.7924 | 13.8475 | 12.8526 | 12.173 | 8.4995 | 5.0709 | 0.18623 | 14.4362 | 13.9505 | 13.6546 | 13.0138 | 12.373 | 11.6393 | 10.4536 | 9.1526 | 7.7934 | 6.8005 | 2.0413 | -0.95764 | -3.2025
|  | FLETCHWOOD | HT |  |  |  | 14.7607 | 14.3607 | 13.8189 | 13.1495 | 12.8464 | 12.174 | 10.9577 | 9.6638 | 8.2648 | 6.7852 | 0.28725 | -3.7025 | -5.9872 | 17.7689 | 17.5566 | 17.2699 | 16.9117 | 16.7873 | 16.4403 | 15.8464 | 15.2056 | 14.5097 | 13.7209 | 10.3179 | 8.5852 | 7.5873 | 14.6577 | 14.2903 | 13.8046 | 13.2036 | 12.9556 | 12.3505 | 11.2709 | 10.1199 | 8.874 | 7.5495 | 1.7342 | -1.6423 | -3.5546
|  | FLETCHWOOD | HE |  |  |  | 14.8097 | 14.4168 | 13.9158 | 13.2852 | 13.026 | 12.3954 | 11.3852 | 10.2944 | 9.0975 | 7.8964 | 2.1179 | -1.5393 | -3.3138 | 17.7515 | 17.4903 | 17.1648 | 16.7668 | 16.5975 | 16.1873 | 15.5934 | 14.9413 | 14.2168 | 13.4709 | 9.1893 | 5.5995 | 1.0566 | 14.7026 | 14.3383 | 13.8873 | 13.3219 | 13.1087 | 12.5444 | 11.6505 | 10.674 | 9.6066 | 8.5342 | 3.3373 | 0.28419 | -1.2076
|  | FLETCHWOOD | CF |  |  |  | 14.9546 | 14.7444 | 14.4077 | 13.9709 | 13.5689 | 13.424 | 12.8964 | 12.3097 | 11.6209 | 10.9352 | 7.1954 | 3.2434 | -0.074992 | 17.8148 | 17.6342 | 17.3781 | 17.0546 | 16.7342 | 16.5699 | 16.1291 | 15.6301 | 15.0699 | 14.4893 | 10.6352 | 4.8219 | -4.4097 | 14.8332 | 14.6393 | 14.3362 | 13.9526 | 13.5832 | 13.4852 | 13.025 | 12.5036 | 11.9015 | 11.2964 | 7.8791 | 4.3332 | 1.4332
MANNINGTON GSP | MANNINGTON BSP | FORDINGBRIDGE | MINIMUM HEADROOM | SU 14069 15523 | YES | 0.603 | 7.1342 | 6.8515 | 6.4148 | 5.9954 | 5.4138 | 4.7097 | 3.9607 | 3.6638 | 3.0454 | 2.5423 | 0.37194 | -0.88827 | -1.5974 | 8.8327 | 8.6459 | 8.348 | 8.0908 | 7.7316 | 7.3143 | 6.8541 | 6.8449 | 6.4561 | 6.1796 | 4.7398 | 3.5 | 0.23469 | 7.7459 | 7.4857 | 7.0816 | 6.7122 | 6.1918 | 5.5694 | 4.8949 | 4.8 | 4.25 | 3.8143 | 1.9327 | 0.84388 | 0.24694
|  | FORDINGBRIDGE | EE |  |  |  | 7.1342 | 6.8515 | 6.4148 | 5.9954 | 5.4138 | 4.7097 | 3.9607 | 3.6638 | 3.0454 | 2.5423 | 0.42398 | -0.66071 | -1.4485 | 8.8327 | 8.6459 | 8.348 | 8.0908 | 7.7316 | 7.3143 | 6.8541 | 6.8449 | 6.4561 | 6.1796 | 4.7398 | 3.5439 | 1.8357 | 7.7459 | 7.4857 | 7.0816 | 6.7122 | 6.1918 | 5.5694 | 4.8949 | 4.8 | 4.25 | 3.8143 | 1.9663 | 1.052 | 0.37449
|  | FORDINGBRIDGE | HT |  |  |  | 7.227 | 6.9342 | 6.5781 | 6.2117 | 5.6944 | 5.0862 | 4.3985 | 3.7893 | 3.1587 | 2.8403 | 0.37194 | -0.88827 | -1.5974 | 8.9449 | 8.7755 | 8.5755 | 8.3888 | 8.1163 | 7.8173 | 7.4694 | 7.1408 | 6.7827 | 6.702 | 5.4265 | 4.8306 | 4.5143 | 7.8673 | 7.6163 | 7.3041 | 6.9969 | 6.5561 | 6.0663 | 5.4755 | 4.9357 | 4.3755 | 4.1296 | 1.9327 | 0.84388 | 0.24694
|  | FORDINGBRIDGE | HE |  |  |  | 7.2352 | 6.9862 | 6.6138 | 6.2628 | 5.7587 | 5.1719 | 4.5515 | 4.0036 | 3.4393 | 3.1995 | 0.9699 | -0.096429 | -0.61071 | 8.9327 | 8.7806 | 8.549 | 8.3439 | 8.0571 | 7.7378 | 7.3867 | 7.0561 | 6.7092 | 6.6 | 5.0296 | 3.8276 | 2.2327 | 7.8694 | 7.6541 | 7.3306 | 7.0388 | 6.6122 | 6.1388 | 5.6122 | 5.1224 | 4.6122 | 4.4551 | 2.4765 | 1.5755 | 1.1347
|  | FORDINGBRIDGE | CF |  |  |  | 7.3005 | 7.1097 | 6.8423 | 6.5066 | 6.1413 | 5.6454 | 5.2107 | 4.8872 | 4.5077 | 4.1199 | 2.7413 | 1.4556 | 0.31582 | 8.9673 | 8.8408 | 8.6673 | 8.4459 | 8.2245 | 7.9204 | 7.6337 | 7.399 | 7.1184 | 6.8245 | 5.5122 | 3.5 | 0.23469 | 7.9276 | 7.7602 | 7.5255 | 7.2347 | 6.9367 | 6.5245 | 6.149 | 5.8724 | 5.5235 | 5.1673 | 4.0622 | 2.9031 | 1.8969
LOVEDEAN GSP | PORTSMOUTH BSP | FRATTON PARK | MINIMUM HEADROOM | SU 66139 00180 | YES | 5.519 | 0.80204 | -0.18878 | -1.149 | -2.3133 | -3.6561 | -4.7061 | -6.5265 | -8.6224 | -10.6949 | -12.4306 | -18.5245 | -22.6745 | -22.4612 | 7.1235 | 6.3429 | 5.5347 | 4.5582 | 3.4204 | 2.5541 | 1.1673 | -0.46429 | -2.1071 | -3.4806 | -9.6776 | -17.3 | -37.1827 | 2.3194 | 1.4041 | 0.48878 | -0.62041 | -1.902 | -2.8939 | -4.6153 | -6.6061 | -8.5755 | -10.2092 | -15.8561 | -19.5143 | -19.2643
|  | FRATTON PARK | EE |  |  |  | 0.80204 | -0.18878 | -1.149 | -2.3133 | -3.6561 | -4.7061 | -6.5265 | -8.6224 | -10.6949 | -12.4306 | -18.5245 | -21.0878 | -20.3092 | 7.1235 | 6.3429 | 5.5347 | 4.5582 | 3.4204 | 2.5541 | 1.1673 | -0.46429 | -2.1071 | -3.4806 | -9.6776 | -15.4633 | -24.0388 | 2.3194 | 1.4041 | 0.48878 | -0.62041 | -1.902 | -2.8939 | -4.6153 | -6.6061 | -8.5755 | -10.2092 | -15.8561 | -18.0786 | -17.4245
|  | FRATTON PARK | HT |  |  |  | 1.2663 | 0.51327 | -0.15102 | -0.98061 | -1.902 | -2.9551 | -4.3735 | -5.6582 | -7.299 | -9.0592 | -17.7133 | -22.6745 | -22.4612 | 7.6173 | 7.1112 | 6.6316 | 6.0449 | 5.4041 | 4.648 | 3.748 | 2.9939 | 1.9173 | 0.75102 | -4.8 | -7.9061 | -8.0765 | 2.8214 | 2.1276 | 1.4827 | 0.7051 | -0.15714 | -1.1531 | -2.4816 | -3.6776 | -5.2245 | -6.8776 | -14.9541 | -19.5143 | -19.2643
|  | FRATTON PARK | HE |  |  |  | 1.1888 | 0.45816 | -0.17449 | -0.94592 | -1.8051 | -2.7796 | -4.0663 | -5.2194 | -6.699 | -8.2367 | -14.4337 | -17.2429 | -17.5541 | 7.4806 | 6.9082 | 6.3561 | 5.6939 | 4.9663 | 4.1235 | 3.1245 | 2.2602 | 1.0704 | -0.20204 | -6.901 | -13.1214 | -21.7867 | 2.7439 | 2.0786 | 1.4663 | 0.73367 | -0.068367 | -0.98878 | -2.1929 | -3.2602 | -4.6551 | -6.1051 | -11.9643 | -14.5133 | -14.7306
|  | FRATTON PARK | CF |  |  |  | 1.5255 | 1.0765 | 0.69796 | 0.25918 | -0.28673 | -0.82347 | -1.3398 | -2.0122 | -2.75 | -3.1918 | -7.9245 | -13.6276 | -18.751 | 7.6694 | 7.2296 | 6.7857 | 6.2796 | 5.6735 | 5.0092 | 4.2622 | 3.3459 | 2.352 | 1.6041 | -5.5592 | -17.3 | -37.1827 | 3.0653 | 2.6592 | 2.2908 | 1.8592 | 1.3459 | 0.8398 | 0.34184 | -0.30918 | -1.0265 | -1.4459 | -5.9878 | -11.2633 | -15.8847
COWLEY GSP | OXFORD BSP | FRENCHAY ROAD | MINIMUM HEADROOM | SP 50426 08256 | YES | 2.114 | 9.5712 | 9.3355 | 9.0886 | 8.7957 | 8.5192 | 8.1692 | 7.4865 | 6.8386 | 6.6794 | 6.3192 | 4.9141 | 3.9437 | 3.9182 | 11.2508 | 11.0406 | 10.8161 | 10.5447 | 10.2896 | 9.9733 | 9.4937 | 8.9978 | 8.9018 | 8.5998 | 7.0682 | 4.3427 | -1.8727 | 10.0171 | 9.7835 | 9.5386 | 9.2386 | 8.9671 | 8.6222 | 7.9957 | 7.3927 | 7.3069 | 6.9845 | 5.7937 | 4.9467 | 4.9243
|  | FRENCHAY ROAD | EE |  |  |  | 9.5712 | 9.3355 | 9.0886 | 8.7957 | 8.5192 | 8.1692 | 7.4865 | 6.8386 | 6.6794 | 6.3192 | 4.9141 | 4.1824 | 4.3335 | 11.2508 | 11.0406 | 10.8161 | 10.5447 | 10.2896 | 9.9733 | 9.4937 | 8.9978 | 8.9018 | 8.5998 | 7.0682 | 5.3192 | 2.4896 | 10.0171 | 9.7835 | 9.5386 | 9.2386 | 8.9671 | 8.6222 | 7.9957 | 7.3927 | 7.3069 | 6.9845 | 5.7937 | 5.16 | 5.2773
|  | FRENCHAY ROAD | HT |  |  |  | 9.6355 | 9.4569 | 9.2712 | 9.0957 | 8.8712 | 8.6222 | 7.9529 | 7.5478 | 7.1222 | 6.6855 | 5.0508 | 3.9437 | 3.9182 | 11.3916 | 11.2457 | 11.109 | 10.9804 | 10.809 | 10.6171 | 10.2824 | 10.008 | 9.71 | 9.4069 | 8.4773 | 7.8457 | 7.7722 | 10.1559 | 9.9467 | 9.7671 | 9.5937 | 9.3702 | 9.1192 | 8.5722 | 8.1855 | 7.7794 | 7.3549 | 5.9549 | 4.9467 | 4.9243
|  | FRENCHAY ROAD | HE |  |  |  | 9.6324 | 9.5294 | 9.3335 | 9.1712 | 8.9661 | 8.7467 | 8.2498 | 7.809 | 7.412 | 7.0365 | 5.9927 | 5.361 | 5.2906 | 11.3559 | 11.2161 | 11.0335 | 10.8773 | 10.6763 | 10.459 | 10.1437 | 9.8039 | 9.459 | 9.1161 | 7.7559 | 6.0008 | 3.0998 | 10.1518 | 10.0008 | 9.811 | 9.6559 | 9.4518 | 9.2304 | 8.8182 | 8.4151 | 8.0406 | 7.6722 | 6.7896 | 6.26 | 6.2018
|  | FRENCHAY ROAD | CF |  |  |  | 9.6824 | 9.6386 | 9.5988 | 9.4988 | 9.4151 | 9.2947 | 9.1437 | 8.9233 | 8.711 | 8.4427 | 7.4018 | 6.21 | 5.1222 | 11.3957 | 11.2712 | 11.1539 | 11.0008 | 10.862 | 10.6692 | 10.4427 | 10.16 | 9.8865 | 9.5549 | 7.7467 | 4.3427 | -1.8727 | 10.2212 | 10.1212 | 10.0427 | 9.9263 | 9.8355 | 9.7039 | 9.5508 | 9.3396 | 9.1416 | 8.8876 | 7.9314 | 6.9059 | 6.0294
FAWLEY GSP | COWES & WOOTTON COMMON BSP | FRESHWATER | MINIMUM HEADROOM | SZ 34325 86965 | YES | 0.72 | 8.0179 | 7.7505 | 7.4862 | 7.1607 | 6.8015 | 6.775 | 6.2556 | 5.677 | 5.1046 | 4.6903 | 2.2015 | 0.19847 | -0.90867 | 8.5633 | 8.3867 | 8.2082 | 7.9551 | 7.6561 | 7.6653 | 7.3102 | 6.9031 | 6.4898 | 6.2184 | 4.7204 | 3.1204 | -0.78878 | 7.7827 | 7.5276 | 7.2612 | 6.9316 | 6.5633 | 6.5806 | 6.0888 | 5.5367 | 4.9847 | 4.6133 | 2.5347 | 0.78163 | -0.16429
|  | FRESHWATER | EE |  |  |  | 8.0179 | 7.7505 | 7.4862 | 7.1607 | 6.8015 | 6.775 | 6.2556 | 5.677 | 5.1046 | 4.6903 | 2.4066 | 0.67704 | -0.66786 | 8.5633 | 8.3867 | 8.2082 | 7.9551 | 7.6561 | 7.6653 | 7.3102 | 6.9031 | 6.4898 | 6.2184 | 4.7204 | 3.1204 | 0.83061 | 7.7827 | 7.5276 | 7.2612 | 6.9316 | 6.5633 | 6.5806 | 6.0888 | 5.5367 | 4.9847 | 4.6133 | 2.6765 | 1.1969 | 0.029592
|  | FRESHWATER | HT |  |  |  | 8.1719 | 7.925 | 7.724 | 7.4791 | 7.2515 | 6.9607 | 6.4321 | 5.8546 | 5.6301 | 5.077 | 2.2015 | 0.19847 | -0.90867 | 8.6929 | 8.5531 | 8.4388 | 8.2969 | 8.1684 | 7.9857 | 7.6857 | 7.3429 | 7.3235 | 7.0102 | 5.4918 | 4.5878 | 4.1133 | 7.9592 | 7.7286 | 7.5306 | 7.2918 | 7.0735 | 6.7888 | 6.2969 | 5.7561 | 5.6214 | 5.1133 | 2.5347 | 0.78163 | -0.16429
|  | FRESHWATER | HE |  |  |  | 8.175 | 7.9474 | 7.7617 | 7.5342 | 7.326 | 7.0668 | 6.6526 | 6.1903 | 6.0821 | 5.6536 | 3.3056 | 1.6179 | 0.81276 | 8.6735 | 8.5245 | 8.3959 | 8.2327 | 8.0888 | 7.899 | 7.6153 | 7.2837 | 7.2633 | 6.9571 | 5.2265 | 3.6143 | 1.5306 | 7.9602 | 7.7459 | 7.5643 | 7.3408 | 7.1418 | 6.8837 | 6.4929 | 6.049 | 6.0133 | 5.6061 | 3.4949 | 2.0622 | 1.3765
|  | FRESHWATER | CF |  |  |  | 8.2464 | 8.1128 | 7.9699 | 7.8536 | 7.6903 | 7.5495 | 7.3638 | 7.1474 | 6.9199 | 6.6811 | 5.6168 | 3.9474 | 2.377 | 8.7061 | 8.601 | 8.4796 | 8.3714 | 8.2286 | 8.0867 | 7.8969 | 7.6765 | 7.4143 | 7.1398 | 5.8082 | 3.3398 | -0.78878 | 8.0235 | 7.899 | 7.7541 | 7.6388 | 7.4776 | 7.3439 | 7.1571 | 6.9388 | 6.7041 | 6.4602 | 5.4796 | 4.0204 | 2.7082
BRAMLEY (FLEE) | CAMBERLEY RESERVE | FRIMLEY | MINIMUM HEADROOM | SU 87745 57942 | YES | 6.422 | 6.6231 | 5.5394 | 4.5864 | 3.4486 | 2.1955 | 0.92207 | -0.38916 | -1.8555 | -3.3096 | -4.382 | -9.8861 | -14.032 | -16.1902 | 10.3608 | 9.6455 | 9.1129 | 8.369 | 7.5394 | 6.6741 | 5.7598 | 4.7017 | 3.6353 | 2.8864 | -1.0677 | -6.279 | -18.4892 | 7.1425 | 6.1843 | 5.4241 | 4.4098 | 3.2853 | 2.1292 | 0.9088 | -0.47283 | -1.8422 | -2.7922 | -7.4147 | -11.3065 | -13.331
|  | FRIMLEY | EE |  |  |  | 6.6231 | 5.5394 | 4.5864 | 3.4486 | 2.1955 | 0.92207 | -0.38916 | -1.8555 | -3.3096 | -4.382 | -9.679 | -13.3198 | -16.0443 | 10.3608 | 9.6455 | 9.1129 | 8.369 | 7.5394 | 6.6741 | 5.7598 | 4.7017 | 3.6353 | 2.8864 | -1.0677 | -5.1759 | -11.4892 | 7.1425 | 6.1843 | 5.4241 | 4.4098 | 3.2853 | 2.1292 | 0.9088 | -0.47283 | -1.8422 | -2.7922 | -7.3014 | -10.6728 | -13.2177
|  | FRIMLEY | HT |  |  |  | 6.9251 | 5.9608 | 4.8476 | 3.7996 | 2.9894 | 1.8894 | 0.74248 | -0.5116 | -1.8106 | -3.1361 | -9.8861 | -14.032 | -16.1902 | 10.6915 | 10.1649 | 9.568 | 8.9833 | 8.6557 | 8.0578 | 7.4374 | 6.7364 | 5.9904 | 5.219 | 1.6251 | -0.27589 | -1.1698 | 7.467 | 6.6527 | 5.7068 | 4.7813 | 4.1557 | 3.1915 | 2.1598 | 1.0241 | -0.15752 | -1.3708 | -7.4147 | -11.3065 | -13.331
|  | FRIMLEY | HE |  |  |  | 6.9343 | 5.9843 | 4.8894 | 3.8364 | 3.0282 | 1.9221 | 0.93431 | -0.17385 | -1.33 | -2.5187 | -8.6218 | -12.6412 | -14.332 | 10.6282 | 10.0292 | 9.3547 | 8.6782 | 8.2517 | 7.5333 | 6.8404 | 6.0353 | 5.17 | 4.2578 | -0.7065 | -5.181 | -11.0953 | 7.4762 | 6.6588 | 5.7262 | 4.7966 | 4.171 | 3.1986 | 2.2986 | 1.2762 | 0.2037 | -0.90038 | -6.3892 | -10.1198 | -11.7402
|  | FRIMLEY | CF |  |  |  | 7.2047 | 6.5323 | 5.7557 | 5.0415 | 4.2466 | 3.7945 | 3.3721 | 2.867 | 2.3282 | 1.7649 | -2.4902 | -6.8269 | -10.6065 | 10.7578 | 10.2894 | 9.7568 | 9.2262 | 8.6384 | 8.3231 | 7.8159 | 7.2139 | 6.5659 | 5.871 | 0.90574 | -6.279 | -18.4892 | 7.7098 | 7.1425 | 6.4864 | 5.8557 | 5.1527 | 4.8323 | 4.4313 | 3.9425 | 3.42 | 2.87 | -1.1116 | -4.9045 | -8.1218
MELKSHAM GSP | FROME BSP | FROME | MINIMUM HEADROOM | ST 78850 48051 | YES | 5.964 | 18.1007 | 17.1518 | 16.0028 | 14.6956 | 13.4467 | 11.964 | 10.2579 | 8.063 | 5.9069 | 4.3293 | -4.236 | -11.3319 | -14.9503 | 23.7742 | 23.0732 | 22.3456 | 21.4344 | 20.5426 | 19.5395 | 18.364 | 16.8701 | 15.363 | 14.3599 | 8.4987 | 2.5487 | -11.5411 | 19.5824 | 18.5599 | 17.6558 | 16.3436 | 15.0599 | 13.6344 | 11.9875 | 9.8905 | 7.8191 | 6.3487 | -0.97477 | -6.9309 | -9.7686
|  | FROME | EE |  |  |  | 18.1007 | 17.1518 | 16.0028 | 14.6956 | 13.4467 | 11.964 | 10.2579 | 8.063 | 5.9069 | 4.3293 | -4.1993 | -10.4952 | -14.384 | 23.7742 | 23.0732 | 22.3456 | 21.4344 | 20.5426 | 19.5395 | 18.364 | 16.8701 | 15.363 | 14.3599 | 8.4987 | 2.7324 | -4.8003 | 19.5824 | 18.5599 | 17.6558 | 16.3436 | 15.0599 | 13.6344 | 11.9875 | 9.8905 | 7.8191 | 6.3487 | -0.97477 | -6.0778 | -9.2686
|  | FROME | HT |  |  |  | 18.3589 | 17.4263 | 16.1548 | 14.9528 | 14.0181 | 12.7824 | 11.2854 | 9.3834 | 7.4599 | 5.6905 | -4.236 | -11.3319 | -14.9503 | 24.1079 | 23.5018 | 22.7314 | 22.0242 | 21.5854 | 20.8467 | 20.0191 | 18.9365 | 17.7987 | 16.763 | 11.5548 | 8.266 | 6.7548 | 20.0599 | 19.1609 | 17.9528 | 16.8007 | 16.0885 | 14.8967 | 13.4956 | 11.7028 | 9.8426 | 8.115 | -0.9564 | -6.9309 | -9.7686
|  | FROME | HE |  |  |  | 18.3518 | 17.5487 | 16.2477 | 15.0201 | 14.1558 | 12.9467 | 11.6467 | 9.9365 | 8.2273 | 6.6028 | -2.3778 | -8.734 | -11.1513 | 24.0324 | 23.4916 | 22.5987 | 21.7722 | 21.2997 | 20.4793 | 19.6069 | 18.4742 | 17.2875 | 16.1038 | 9.5589 | 3.6579 | -3.2523 | 20.0405 | 19.2956 | 18.0599 | 16.8854 | 16.2589 | 15.1252 | 13.9028 | 12.2936 | 10.6518 | 9.0487 | 0.94768 | -4.1768 | -6.0615
|  | FROME | CF |  |  |  | 18.6824 | 18.1773 | 17.3783 | 16.4936 | 15.5507 | 14.8548 | 14.1793 | 13.2324 | 12.2997 | 11.4467 | 5.2946 | -0.98803 | -6.0176 | 24.2058 | 23.7875 | 23.2058 | 22.4997 | 21.7589 | 21.2875 | 20.614 | 19.7354 | 18.8263 | 17.9109 | 11.5467 | 2.5487 | -11.5411 | 20.3303 | 19.8048 | 19.0569 | 18.1834 | 17.2599 | 16.8579 | 16.1885 | 15.2569 | 14.3099 | 13.4099 | 7.4365 | 2.0222 | -2.2686
COWLEY GSP | HIGH WYCOMBE BSP | FRYERS LANE | MINIMUM HEADROOM | SU 84935 93873 | YES | 0.896 | 12.051 | 11.5714 | 10.949 | 10.7306 | 10.1031 | 9.4265 | 8.3367 | 7.098 | 5.8541 | 4.9633 | 0.33163 | -3.6347 | -5.7061 | 15.75 | 15.3847 | 14.9102 | 14.7071 | 14.201 | 13.6459 | 12.8888 | 11.9847 | 11.0663 | 10.4133 | 6.8194 | 2.5449 | -7.9102 | 12.6276 | 12.1694 | 11.5694 | 11.3714 | 10.7663 | 10.1122 | 9.0908 | 7.9204 | 6.7469 | 5.9235 | 1.8592 | -1.6112 | -3.4112
|  | FRYERS LANE | EE |  |  |  | 12.051 | 11.5714 | 10.949 | 10.7306 | 10.1031 | 9.4265 | 8.3367 | 7.098 | 5.8541 | 4.9633 | 0.39694 | -2.9061 | -5.4224 | 15.75 | 15.3847 | 14.9102 | 14.7071 | 14.201 | 13.6459 | 12.8888 | 11.9847 | 11.0663 | 10.4133 | 6.8194 | 3.0827 | -2.4531 | 12.6276 | 12.1694 | 11.5694 | 11.3714 | 10.7663 | 10.1122 | 9.0908 | 7.9204 | 6.7469 | 5.9235 | 1.8592 | -0.95714 | -3.1714
|  | FRYERS LANE | HT |  |  |  | 12.3643 | 11.9888 | 11.5714 | 11.0847 | 10.5531 | 10.3776 | 9.4551 | 8.4347 | 7.3633 | 6.249 | 0.33163 | -3.6347 | -5.7061 | 16.0265 | 15.801 | 15.5408 | 15.2276 | 14.8806 | 14.7765 | 14.2724 | 13.6867 | 13.0643 | 12.4133 | 9.1908 | 7.2888 | 6.4 | 12.9378 | 12.5888 | 12.1929 | 11.7337 | 11.2224 | 11.0724 | 10.2245 | 9.2796 | 8.2847 | 7.2469 | 1.8816 | -1.6112 | -3.4112
|  | FRYERS LANE | HE |  |  |  | 12.3531 | 12.0041 | 11.6143 | 11.1602 | 10.6622 | 10.5245 | 9.751 | 8.8796 | 7.9582 | 7.001 | 1.9469 | -1.4633 | -2.8755 | 15.9684 | 15.701 | 15.3949 | 15.0388 | 14.6316 | 14.4582 | 13.9143 | 13.2827 | 12.5959 | 11.8684 | 7.6969 | 3.7755 | -1.2724 | 12.9276 | 12.599 | 12.2296 | 11.799 | 11.3204 | 11.2031 | 10.4857 | 9.6755 | 8.8122 | 7.9173 | 3.3 | 0.36224 | -0.8602
|  | FRYERS LANE | CF |  |  |  | 12.5429 | 12.3408 | 12.0714 | 11.8388 | 11.5388 | 11.2112 | 10.8327 | 10.8378 | 10.4133 | 9.9633 | 6.6398 | 3.1867 | -0.042857 | 16.0663 | 15.8633 | 15.6041 | 15.349 | 15.0296 | 14.6541 | 14.2112 | 14.0031 | 13.4837 | 12.9235 | 8.8367 | 2.5449 | -7.9102 | 13.102 | 12.9092 | 12.651 | 12.4265 | 12.1367 | 11.8173 | 11.4561 | 11.4714 | 11.0653 | 10.6347 | 7.5041 | 4.3541 | 1.5551
COWLEY GSP | DRAYTON BSP | FULSCOT | MINIMUM HEADROOM | SU 54413 89511 | YES | 10.205 | 4.098 | 1.5211 | 0.40169 | -0.17382 | -1.1065 | -2.4514 | -4.2626 | -5.4187 | -7.5748 | -9.3789 | -15.4432 | -20.3636 | -26.6068 | 10.6602 | 8.2333 | 7.5425 | 7.0711 | 6.4394 | 5.1619 | 3.419 | 2.4905 | 0.25781 | -1.4708 | -6.9085 | -12.6493 | -22.4078 | 7.4704 | 4.9394 | 3.9741 | 3.4078 | 2.5568 | 1.1119 | -0.69729 | -1.8126 | -4.2544 | -6.182 | -12.185 | -17.1544 | -23.9762
|  | FULSCOT | EE |  |  |  | 4.098 | 1.5211 | 0.40169 | -0.10035 | -1.0167 | -1.9575 | -4.2626 | -5.3391 | -6.7912 | -7.8014 | -12.8993 | -18.8371 | -23.914 | 10.6602 | 8.2333 | 7.5425 | 7.2701 | 6.6935 | 5.9466 | 3.8986 | 3.1609 | 2.0068 | 1.2588 | -2.9667 | -10.0157 | -17.7374 | 7.4704 | 4.9394 | 3.9741 | 3.5609 | 2.7496 | 1.8221 | -0.45239 | -1.4422 | -2.8687 | -3.8167 | -8.6636 | -14.9463 | -20.0415
|  | FULSCOT | HT |  |  |  | 4.3184 | 1.8058 | 0.7374 | -0.12076 | -0.99525 | -2.2269 | -4.1524 | -5.4187 | -6.5208 | -7.9738 | -14.3708 | -20.3636 | -26.2834 | 10.8735 | 8.5537 | 7.9313 | 7.3864 | 6.9037 | 5.8507 | 4.1517 | 3.2343 | 2.5874 | 1.5007 | -2.8636 | -8.0065 | -13.5823 | 7.6908 | 5.2292 | 4.2986 | 3.5058 | 2.7374 | 1.4435 | -0.47382 | -1.7279 | -2.7412 | -4.185 | -10.3973 | -16.6748 | -22.9007
|  | FULSCOT | HE |  |  |  | 4.3173 | 1.8282 | 0.75679 | -0.17382 | -1.1065 | -2.4514 | -4.2493 | -5.3687 | -7.5748 | -9.3789 | -15.4432 | -20.3575 | -26.6068 | 10.8255 | 8.4782 | 7.7843 | 7.0711 | 6.4394 | 5.1619 | 3.419 | 2.4905 | 0.25781 | -1.4708 | -6.9085 | -12.6493 | -22.4078 | 7.6867 | 5.2456 | 4.3017 | 3.4078 | 2.5568 | 1.1119 | -0.69729 | -1.8126 | -4.2544 | -6.182 | -12.185 | -17.1544 | -23.9762
|  | FULSCOT | CF |  |  |  | 4.4592 | 2.0935 | 1.2833 | 0.74149 | 0.034343 | -0.53811 | -2.2779 | -2.4779 | -3.1126 | -3.8024 | -8.0544 | -11.9167 | -17.4823 | 10.901 | 8.6017 | 8.0925 | 7.7241 | 7.2037 | 6.7099 | 4.9486 | 4.6599 | 4.0578 | 3.3782 | -1.1595 | -7.4483 | -18.967 | 7.8184 | 5.4884 | 4.816 | 4.3527 | 3.7139 | 3.166 | 1.4303 | 1.2619 | 0.66496 | 0.0078122 | -4.1218 | -8.0279 | -13.5568
COWLEY GSP | WITNEY BSP | FYFIELD | MINIMUM HEADROOM | SU 42256 99551 | YES | 2.941 | 3.8603 | 3.6685 | 3.4409 | 3.0889 | 2.5185 | 1.8889 | 1.5715 | 0.84908 | 0.12867 | -0.17337 | -1.7499 | -2.8703 | -3.6203 | 5.8833 | 5.7312 | 5.5527 | 5.2986 | 4.9241 | 4.521 | 4.4486 | 4.0057 | 3.5547 | 3.3476 | 2.1537 | 0.51388 | -3.1698 | 4.1322 | 3.9424 | 3.7231 | 3.3955 | 2.8751 | 2.2965 | 2.1047 | 1.4608 | 0.82 | 0.55265 | -0.78816 | -1.7657 | -2.3759
|  | FYFIELD | EE |  |  |  | 3.8603 | 3.6685 | 3.4409 | 3.0889 | 2.5185 | 1.8889 | 1.5715 | 0.84908 | 0.12867 | -0.17337 | -1.7499 | -2.6907 | -3.4162 | 5.8833 | 5.7312 | 5.5527 | 5.2986 | 4.9241 | 4.521 | 4.4486 | 4.0057 | 3.5547 | 3.3476 | 2.1537 | 0.91082 | -0.9902 | 4.1322 | 3.9424 | 3.7231 | 3.3955 | 2.8751 | 2.2965 | 2.1047 | 1.4608 | 0.82 | 0.55265 | -0.78816 | -1.6045 | -2.2055
|  | FYFIELD | HT |  |  |  | 3.9674 | 3.8042 | 3.6338 | 3.3593 | 2.8644 | 2.3521 | 1.6726 | 0.95622 | 0.56337 | 0.16235 | -1.7468 | -2.8703 | -3.6203 | 5.9965 | 5.8986 | 5.7945 | 5.6169 | 5.3343 | 5.0812 | 4.718 | 4.3169 | 4.2353 | 4.0037 | 2.97 | 2.4322 | 2.0945 | 4.2547 | 4.0996 | 3.9333 | 3.6802 | 3.2486 | 2.8108 | 2.222 | 1.5873 | 1.3312 | 0.95776 | -0.78204 | -1.7657 | -2.3759
|  | FYFIELD | HE |  |  |  | 3.9868 | 3.8164 | 3.6562 | 3.396 | 2.9134 | 2.4123 | 1.7919 | 1.1287 | 0.79704 | 0.45827 | -1.3356 | -2.2703 | -2.7836 | 5.9853 | 5.8618 | 5.7394 | 5.5578 | 5.2649 | 4.9771 | 4.6098 | 4.2057 | 4.0649 | 3.8118 | 2.3669 | 1.1098 | -0.69939 | 4.2741 | 4.1088 | 3.9516 | 3.7118 | 3.2924 | 2.8649 | 2.3241 | 1.7353 | 1.5322 | 1.2088 | -0.42184 | -1.2188 | -1.6331
|  | FYFIELD | CF |  |  |  | 4.0307 | 3.9215 | 3.7817 | 3.6164 | 3.2277 | 2.7899 | 2.395 | 1.9256 | 1.4409 | 1.2032 | 0.26643 | -0.9152 | -2.053 | 6.0037 | 5.9118 | 5.7853 | 5.6567 | 5.4037 | 5.118 | 4.8465 | 4.5057 | 4.1547 | 3.9037 | 2.6761 | 0.51388 | -3.1698 | 4.3108 | 4.2088 | 4.0659 | 3.9169 | 3.5833 | 3.2078 | 2.8822 | 2.469 | 2.0312 | 1.7741 | 0.95776 | -0.090204 | -1.0443
LOVEDEAN GSP | HAVANT | GABLE HEAD | MINIMUM HEADROOM | SZ 72204 99904 | YES | 1.997 | 15.9884 | 15.5128 | 14.9802 | 14.8077 | 14.1373 | 13.4037 | 12.3741 | 11.2404 | 10.1241 | 9.3026 | 5.1945 | 2.1782 | 0.37509 | 18.1026 | 17.7547 | 17.3261 | 17.1955 | 16.6914 | 16.1363 | 15.4384 | 14.6414 | 13.8445 | 13.271 | 10.3506 | 6.4037 | -3.0953 | 15.9486 | 15.5179 | 14.9812 | 14.87 | 14.273 | 13.5955 | 12.6649 | 11.619 | 10.5863 | 9.8802 | 6.1588 | 3.4833 | 2.0312
|  | GABLE HEAD | EE |  |  |  | 15.9884 | 15.5128 | 14.9802 | 14.8077 | 14.1373 | 13.4037 | 12.3741 | 11.2404 | 10.1241 | 9.3026 | 5.6965 | 3.0679 | 0.81182 | 18.1026 | 17.7547 | 17.3261 | 17.1955 | 16.6914 | 16.1363 | 15.4384 | 14.6414 | 13.8445 | 13.271 | 10.3506 | 7.0812 | 2.0445 | 15.9486 | 15.5179 | 14.9812 | 14.87 | 14.273 | 13.5955 | 12.6649 | 11.619 | 10.5863 | 9.8802 | 6.5516 | 4.2516 | 2.3894
|  | GABLE HEAD | HT |  |  |  | 16.2241 | 15.8159 | 15.3935 | 14.9822 | 14.3455 | 13.6373 | 13.0822 | 12.0822 | 11.0557 | 9.9894 | 5.1945 | 2.1782 | 0.37509 | 18.319 | 18.0894 | 17.8302 | 17.57 | 17.1782 | 16.7343 | 16.5404 | 15.9863 | 15.4067 | 14.7996 | 12.2118 | 10.8241 | 10.0537 | 16.1435 | 15.7873 | 15.4118 | 15.0373 | 14.4761 | 13.8435 | 13.3322 | 12.422 | 11.4863 | 10.5169 | 6.1588 | 3.4833 | 2.0312
|  | GABLE HEAD | HE |  |  |  | 16.2373 | 15.871 | 15.4873 | 15.1292 | 14.5516 | 13.9118 | 13.5404 | 12.7312 | 11.9057 | 11.0475 | 7.2077 | 4.5945 | 3.1363 | 18.2822 | 18.0261 | 17.7302 | 17.4465 | 17.0169 | 16.5353 | 16.3261 | 15.7588 | 15.1618 | 14.523 | 11.1955 | 7.8935 | 3.1975 | 16.1598 | 15.8424 | 15.5016 | 15.173 | 14.6669 | 14.0761 | 13.7547 | 13.022 | 12.2751 | 11.4965 | 7.9659 | 5.672 | 4.4965
|  | GABLE HEAD | CF |  |  |  | 16.3914 | 16.1486 | 15.9067 | 15.6843 | 15.2802 | 14.8363 | 14.3812 | 14.3179 | 13.873 | 13.4016 | 10.8006 | 8.1149 | 5.472 | 18.3567 | 18.1486 | 17.9169 | 17.6935 | 17.3363 | 16.92 | 16.4577 | 16.27 | 15.7812 | 15.2588 | 11.8261 | 6.4037 | -3.0953 | 16.2975 | 16.0955 | 15.8843 | 15.6833 | 15.3047 | 14.8853 | 14.4506 | 14.5006 | 14.0822 | 13.6394 | 11.1945 | 8.8169 | 6.4333
MINETY GSP |  | GALILEO | MINIMUM HEADROOM | SU 10596 83733 | YES | 4.09 | 32.0593 | 31.9675 | 31.8511 | 31.7379 | 31.5216 | 31.2001 | 30.843 | 30.492 | 30.0399 | 29.6603 | 28.2593 | 27.3409 | 27.1522 | 32.4062 | 32.3297 | 32.2348 | 32.1389 | 31.9205 | 31.5695 | 31.1624 | 30.9399 | 30.5185 | 30.1848 | 28.646 | 25.743 | 19.993 | 32.0103 | 31.8899 | 31.7399 | 31.5869 | 31.3991 | 30.9818 | 30.5746 | 30.2328 | 29.7971 | 29.4583 | 28.3481 | 27.7134 | 27.4338
|  | GALILEO | EE |  |  |  | 32.0593 | 31.9675 | 31.8511 | 31.7379 | 31.594 | 31.2144 | 30.843 | 30.4981 | 30.0399 | 29.6828 | 28.2593 | 27.4062 | 27.5226 | 32.4062 | 32.3297 | 32.2348 | 32.1389 | 31.9838 | 31.5695 | 31.1624 | 30.9399 | 30.5185 | 30.1848 | 28.646 | 26.8664 | 24.245 | 32.0103 | 31.8899 | 31.7399 | 31.5869 | 31.3991 | 30.9818 | 30.5746 | 30.2328 | 29.7971 | 29.4583 | 28.4338 | 27.8348 | 27.9552
|  | GALILEO | HT |  |  |  | 32.1256 | 32.0532 | 31.9654 | 31.8838 | 31.5216 | 31.2001 | 30.9113 | 30.492 | 30.0471 | 29.6603 | 28.3358 | 27.3409 | 27.1522 | 32.4654 | 32.4144 | 32.3471 | 32.2818 | 31.9205 | 31.6134 | 31.3624 | 31.0858 | 30.8318 | 30.644 | 29.9869 | 29.492 | 29.3348 | 32.1011 | 32.0113 | 31.8981 | 31.7848 | 31.4011 | 31.0481 | 30.7103 | 30.3277 | 29.9624 | 29.6552 | 28.5409 | 27.7787 | 27.6389
|  | GALILEO | HE |  |  |  | 32.1216 | 32.0501 | 31.9634 | 31.8807 | 31.7716 | 31.4297 | 31.1491 | 30.7624 | 30.3113 | 29.8869 | 28.5164 | 27.7654 | 27.4889 | 32.4593 | 32.4011 | 32.3297 | 32.2583 | 32.143 | 31.7797 | 31.4797 | 31.1103 | 30.7103 | 30.3256 | 28.8991 | 27.1103 | 24.3705 | 32.094 | 32.0011 | 31.8838 | 31.7685 | 31.6226 | 31.244 | 30.9093 | 30.4838 | 30.0542 | 29.6491 | 28.3481 | 27.7134 | 27.4338
|  | GALILEO | CF |  |  |  | 32.1746 | 32.1348 | 32.0869 | 32.0328 | 31.9838 | 31.9154 | 31.7267 | 31.5154 | 31.2644 | 31.0297 | 29.7848 | 28.7124 | 27.7154 | 32.4981 | 32.4613 | 32.4164 | 32.3573 | 32.2603 | 32.1358 | 31.8634 | 31.5562 | 31.1971 | 30.8369 | 28.9236 | 25.743 | 19.993 | 32.1685 | 32.1216 | 32.0624 | 31.9899 | 31.9216 | 31.8338 | 31.6246 | 31.3818 | 31.0889 | 30.8134 | 29.5399 | 28.5287 | 27.7338
LOVEDEAN GSP | WYMERING BSP | GAMBLE ROAD | MINIMUM HEADROOM | SU 64771 01769 | YES | 12.931 | -0.11922 | -0.71922 | -1.8243 | -3.0856 | -4.5764 | -6.6121 | -8.9253 | -10.9958 | -13.3141 | -15.2947 | -21.1611 | -24.1845 | -23.6753 | 3.0665 | 2.5236 | 1.6696 | 0.71955 | -0.42433 | -1.8468 | -3.4304 | -4.8325 | -6.5345 | -8.0243 | -14.7825 | -23.3896 | -43.3498 | 0.76547 | 0.17465 | -0.83861 | -1.9907 | -3.3692 | -5.1917 | -7.2549 | -9.0386 | -11.1304 | -12.8804 | -18.1151 | -20.7672 | -20.3366
|  | GAMBLE ROAD | EE |  |  |  | -0.11922 | -0.71922 | -1.8243 | -3.0856 | -4.5764 | -6.6121 | -8.9253 | -10.9958 | -13.3141 | -15.2947 | -21.1611 | -22.7253 | -21.7651 | 3.0665 | 2.5236 | 1.6696 | 0.71955 | -0.42433 | -1.8468 | -3.4304 | -4.8325 | -6.5345 | -8.0243 | -14.7825 | -20.4539 | -29.4886 | 0.76547 | 0.17465 | -0.83861 | -1.9907 | -3.3692 | -5.1917 | -7.2549 | -9.0386 | -11.1304 | -12.8804 | -18.1151 | -19.4427 | -18.7794
|  | GAMBLE ROAD | HT |  |  |  | 0.26751 | -0.45086 | -1.357 | -2.3794 | -3.9284 | -5.7162 | -7.556 | -9.5315 | -11.5162 | -13.3325 | -20.5366 | -24.1845 | -23.6753 | 3.4879 | 3.0175 | 2.4542 | 1.8287 | 0.94302 | -0.077388 | -1.1029 | -2.2825 | -3.508 | -4.7488 | -9.6539 | -12.1049 | -12.1284 | 1.19 | 0.54098 | -0.25902 | -1.1631 | -2.5009 | -4.056 | -5.6396 | -7.3876 | -9.158 | -10.8294 | -17.3835 | -20.7672 | -20.3366
|  | GAMBLE ROAD | HE |  |  |  | 0.20935 | -0.16718 | -0.94576 | -1.8182 | -2.8498 | -4.1804 | -5.6753 | -7.308 | -8.9519 | -10.5866 | -16.81 | -18.8753 | -18.8386 | 3.3624 | 2.9798 | 2.3787 | 1.7226 | 0.92669 | -0.038612 | -1.0866 | -2.2937 | -3.558 | -4.8733 | -11.8692 | -18.0284 | -27.107 | 1.1328 | 0.75016 | 0.059347 | -0.70902 | -1.6294 | -2.7998 | -4.0947 | -5.5458 | -7.0131 | -8.4866 | -13.9743 | -15.7845 | -15.7407
|  | GAMBLE ROAD | CF |  |  |  | 0.49404 | 0.27873 | 0.033837 | -0.57841 | -1.2437 | -2.0264 | -2.9213 | -3.8794 | -4.907 | -5.9478 | -11.4529 | -16.9284 | -20.4427 | 3.5308 | 3.2022 | 2.842 | 2.2736 | 1.6349 | 0.84608 | -0.071265 | -1.0968 | -2.21 | -3.3896 | -10.9927 | -23.3896 | -43.3498 | 1.4083 | 1.1675 | 0.91343 | 0.37567 | -0.20596 | -0.90086 | -1.6723 | -2.509 | -3.4264 | -4.357 | -9.2294 | -14.1039 | -17.1968
IVER 132KV | DENHAM | GERRARDS CROSS | MINIMUM HEADROOM | SU 99973 87964 | YES | 1.74 | -1.0191 | -1.2375 | -1.5416 | -1.8712 | -2.2355 | -2.1997 | -2.7242 | -3.3099 | -3.9028 | -4.3079 | -6.762 | -8.6906 | -9.8273 | 1.6974 | 1.5148 | 1.2577 | 0.98418 | 0.67806 | 0.71276 | 0.35561 | -0.054592 | -0.47602 | -0.74949 | -2.2617 | -4.3964 | -9.4189 | -0.82857 | -1.0602 | -1.3663 | -1.7061 | -2.0847 | -1.9694 | -2.4622 | -3.0184 | -3.5837 | -3.9408 | -6.0429 | -7.7561 | -8.7786
|  | GERRARDS CROSS | EE |  |  |  | -1.0191 | -1.2375 | -1.5416 | -1.8712 | -2.2355 | -2.1997 | -2.7242 | -3.3099 | -3.9028 | -4.3079 | -6.5232 | -8.2436 | -9.6365 | 1.6974 | 1.5148 | 1.2577 | 0.98418 | 0.67806 | 0.71276 | 0.35561 | -0.054592 | -0.47602 | -0.74949 | -2.2617 | -4.0311 | -6.6883 | -0.82857 | -1.0602 | -1.3663 | -1.7061 | -2.0847 | -1.9694 | -2.4622 | -3.0184 | -3.5837 | -3.9408 | -5.8439 | -7.3561 | -8.6122
|  | GERRARDS CROSS | HT |  |  |  | -0.86709 | -1.112 | -1.3089 | -1.5497 | -1.7712 | -2.0579 | -2.5936 | -3.1834 | -3.3753 | -3.9304 | -6.762 | -8.6906 | -9.8273 | 1.8689 | 1.6893 | 1.5577 | 1.3852 | 1.2423 | 1.0413 | 0.74133 | 0.39847 | 0.4301 | 0.11786 | -1.3036 | -2.0903 | -2.5291 | -0.64184 | -0.8949 | -1.0969 | -1.35 | -1.5633 | -1.851 | -2.3571 | -2.9235 | -2.9612 | -3.4724 | -6.0429 | -7.7561 | -8.7786
|  | GERRARDS CROSS | HE |  |  |  | -0.86709 | -1.0559 | -1.2753 | -1.4987 | -1.7048 | -1.9722 | -2.4089 | -2.5212 | -2.9538 | -3.3977 | -5.7742 | -7.4804 | -8.3069 | 1.8383 | 1.6832 | 1.4832 | 1.2883 | 1.1179 | 0.88827 | 0.5801 | 0.56071 | 0.24439 | -0.089286 | -1.923 | -3.7107 | -6.1342 | -0.64388 | -0.83878 | -1.0724 | -1.3133 | -1.5082 | -1.7776 | -2.201 | -2.198 | -2.6071 | -3.0286 | -5.1633 | -6.6694 | -7.4184
|  | GERRARDS CROSS | CF |  |  |  | -0.77934 | -0.89362 | -0.99974 | -1.1804 | -1.3416 | -1.4661 | -1.6579 | -1.8997 | -2.1681 | -2.0089 | -3.5589 | -5.1967 | -6.7895 | 1.8811 | 1.7536 | 1.624 | 1.423 | 1.2444 | 1.0913 | 0.86071 | 0.58214 | 0.27908 | 0.32908 | -1.5515 | -4.3964 | -9.4189 | -0.56735 | -0.69592 | -0.81633 | -1.0194 | -1.1929 | -1.3102 | -1.5143 | -1.7694 | -2.051 | -1.8061 | -3.2857 | -4.7245 | -6.0694
MANNINGTON GSP | SHAFTESBURY BSP | GILLINGHAM | MINIMUM HEADROOM | ST 80185 25765 | YES | 10.545 | 26.0748 | 25.4983 | 24.4809 | 23.4462 | 22.7503 | 21.9595 | 21.1983 | 20.3748 | 19.6871 | 19.1105 | 15.3922 | 14.1891 | 13.8279 | 25.3973 | 25.1146 | 24.3054 | 23.5003 | 23.1217 | 22.7095 | 22.2789 | 21.8105 | 21.3993 | 21.0554 | 17.7095 | 16.7003 | 14.4228 | 24.8779 | 24.3993 | 23.5299 | 22.6615 | 22.0646 | 21.3922 | 20.733 | 20.0156 | 19.4044 | 18.9054 | 15.1911 | 13.8717 | 13.7524
|  | GILLINGHAM | EE |  |  |  | 26.0748 | 25.4983 | 24.4809 | 23.4462 | 22.7503 | 21.9595 | 21.1983 | 20.3748 | 19.6871 | 19.1105 | 15.6105 | 14.7544 | 14.1258 | 25.3973 | 25.1146 | 24.3054 | 23.5003 | 23.1217 | 22.7095 | 22.2789 | 21.8105 | 21.3993 | 21.0554 | 18.532 | 17.6085 | 16.2789 | 24.8779 | 24.3993 | 23.5299 | 22.6615 | 22.0646 | 21.3922 | 20.733 | 20.0156 | 19.4044 | 18.9054 | 15.8513 | 15.1258 | 14.5871
|  | GILLINGHAM | HT |  |  |  | 26.2136 | 25.6656 | 24.7177 | 23.7197 | 23.0911 | 22.3666 | 21.6768 | 20.9493 | 20.3666 | 19.6483 | 15.8064 | 14.6544 | 14.1013 | 25.5075 | 25.2564 | 24.5075 | 23.7524 | 23.4452 | 23.0973 | 22.7493 | 22.3748 | 22.0677 | 21.634 | 19.2564 | 18.6789 | 18.432 | 25.0217 | 24.5758 | 23.7901 | 22.9401 | 22.4105 | 21.8034 | 21.2177 | 20.5911 | 20.0871 | 19.4524 | 16.0646 | 15.0381 | 14.5738
|  | GILLINGHAM | HE |  |  |  | 26.1809 | 25.6197 | 24.6503 | 23.6289 | 22.9717 | 22.2105 | 21.5136 | 20.7615 | 20.1503 | 19.4973 | 15.3922 | 14.1891 | 13.8279 | 25.4595 | 25.185 | 24.4126 | 23.6197 | 23.2697 | 22.8728 | 22.4738 | 22.0391 | 21.6452 | 21.1187 | 17.7095 | 16.7003 | 15.7983 | 24.9922 | 24.534 | 23.732 | 22.8534 | 22.2973 | 21.6575 | 21.0615 | 20.4095 | 19.8748 | 19.2962 | 15.1911 | 13.8717 | 13.7524
|  | GILLINGHAM | CF |  |  |  | 26.3044 | 25.8044 | 24.9279 | 24.2258 | 23.5462 | 22.5207 | 22.0493 | 21.5156 | 21.0748 | 20.6177 | 18.0166 | 16.0922 | 14.734 | 25.5615 | 25.2973 | 24.5605 | 24.0238 | 23.5615 | 22.7952 | 22.5013 | 22.1626 | 21.8595 | 21.5391 | 19.6024 | 17.232 | 14.4228 | 25.1034 | 24.6993 | 23.9677 | 23.3922 | 22.8197 | 21.932 | 21.5432 | 21.0911 | 20.7075 | 20.3095 | 18.0411 | 15.7564 | 14.3728
BRAMLEY (FLEE) | ALDERSHOT BSP | GODALMING | MINIMUM HEADROOM | SU 96743 44375 | YES | 1.933 | 9.8184 | 9.0276 | 8.1622 | 7.5969 | 6.6245 | 5.4949 | 3.8888 | 1.9714 | 0.13061 | -1.3857 | -10.0878 | -14.4265 | -15.4398 | 14.548 | 13.9582 | 13.2612 | 12.8551 | 12.0755 | 11.2255 | 10.1704 | 8.9316 | 7.6867 | 6.651 | 0.31429 | -2.7173 | -12.9469 | 10.8439 | 10.1102 | 9.2806 | 8.751 | 7.6684 | 6.349 | 4.8143 | 2.9796 | 1.2194 | -0.22245 | -8.5245 | -12.6092 | -13.5327
|  | GODALMING | EE |  |  |  | 9.8184 | 9.0276 | 8.1622 | 7.5969 | 6.6245 | 5.4949 | 3.8888 | 1.9714 | 0.13061 | -1.3857 | -6.6643 | -9.8592 | -12.4286 | 14.548 | 13.9582 | 13.2612 | 12.8551 | 12.0755 | 11.2255 | 10.1704 | 8.9316 | 7.6867 | 6.651 | 2.4296 | -1.4316 | -7.0163 | 10.8439 | 10.1102 | 9.2806 | 8.751 | 7.6684 | 6.349 | 4.8143 | 2.9796 | 1.2194 | -0.22245 | -5.1816 | -7.3031 | -9.5541
|  | GODALMING | HT |  |  |  | 10.351 | 9.7582 | 9.1949 | 8.5357 | 7.8 | 7.348 | 6.1643 | 4.8071 | 3.3878 | 1.9245 | -5.4153 | -10.0653 | -12.2592 | 15.0347 | 14.6612 | 14.2847 | 13.8245 | 13.3082 | 13.0643 | 12.3694 | 11.548 | 10.6735 | 9.7551 | 5.199 | 3.0694 | 2.2286 | 11.3673 | 10.8296 | 10.2959 | 9.6724 | 8.9704 | 8.5531 | 7.4541 | 6.1918 | 4.8673 | 3.502 | -3.2745 | -7.4582 | -9.3561
|  | GODALMING | HE |  |  |  | 10.2316 | 9.5878 | 8.951 | 8.2071 | 7.3704 | 6.6704 | 5.1816 | 3.3469 | 1.3878 | -0.66633 | -10.0878 | -14.4265 | -15.4398 | 14.8898 | 14.4214 | 13.9245 | 13.3347 | 12.6643 | 12.249 | 11.4092 | 10.1316 | 8.6878 | 7.1694 | 0.31429 | -2.7173 | -7.7122 | 11.248 | 10.6612 | 10.0582 | 9.35 | 8.552 | 7.4888 | 6.0694 | 4.3102 | 2.4306 | 0.46735 | -8.5245 | -12.6092 | -13.5327
|  | GODALMING | CF |  |  |  | 10.5653 | 10.1663 | 9.7755 | 9.3857 | 8.9082 | 8.3816 | 8.1735 | 7.549 | 6.8418 | 5.748 | -0.90714 | -6.7653 | -10.1908 | 15.0969 | 14.7541 | 14.3765 | 13.9959 | 13.5347 | 12.9949 | 12.7224 | 12.0551 | 11.3235 | 10.5449 | 5.248 | -2.0918 | -12.9469 | 11.5663 | 11.2082 | 10.8316 | 10.4571 | 9.999 | 9.4898 | 9.3051 | 8.6265 | 7.6357 | 6.5796 | 0.19388 | -5.3724 | -8.5735
WILLESDEN GSP | ACTON LANE | GOLDSMITHS | MINIMUM HEADROOM | TQ 21089 80758 | YES | 2.027 | 5.1592 | 4.848 | 4.3654 | 3.6174 | 2.2143 | 0.4123 | -1.1897 | -2.8653 | -4.5183 | -5.8306 | -9.1816 | -11.4346 | -12.9612 | 7.6186 | 7.3543 | 6.9757 | 6.5073 | 5.9094 | 4.7624 | 3.6798 | 2.3339 | 0.81449 | -0.40796 | -5.1222 | -9.8824 | -19.9733 | 5.3884 | 5.0924 | 4.6445 | 4.0455 | 2.6547 | 0.90163 | -0.61163 | -2.2688 | -4.0106 | -5.4055 | -8.6545 | -10.6014 | -11.9351
|  | GOLDSMITHS | EE |  |  |  | 5.1592 | 4.848 | 4.3654 | 3.7092 | 2.8541 | 1.4256 | 0.019439 | -1.7285 | -3.3132 | -4.7928 | -9.1816 | -11.0275 | -12.8551 | 7.6186 | 7.3543 | 6.9757 | 6.5073 | 5.9431 | 4.892 | 3.8278 | 2.491 | 1.2482 | -0.083469 | -5.1222 | -8.3641 | -13.8396 | 5.3884 | 5.0924 | 4.6445 | 4.0455 | 3.2782 | 1.8853 | 0.51184 | -1.2014 | -2.6902 | -4.1953 | -8.6545 | -10.2392 | -11.8555
|  | GOLDSMITHS | HT |  |  |  | 5.3317 | 4.9378 | 4.4225 | 3.6174 | 2.2143 | 0.4123 | -1.1897 | -2.8653 | -4.5183 | -5.8306 | -9.0234 | -11.4346 | -12.9612 | 7.8043 | 7.5502 | 7.2645 | 6.8308 | 5.9094 | 4.7624 | 3.6798 | 2.3339 | 0.81449 | -0.40796 | -2.6467 | -3.8141 | -4.4916 | 5.5659 | 5.2047 | 4.7598 | 4.0588 | 2.6547 | 0.90163 | -0.61163 | -2.2688 | -4.0106 | -5.4055 | -8.4351 | -10.6014 | -11.9351
|  | GOLDSMITHS | HE |  |  |  | 5.3154 | 5.0745 | 4.6847 | 4.1419 | 3.4092 | 2.1235 | 0.83168 | -0.79791 | -2.6448 | -4.0785 | -8.0816 | -9.7265 | -10.4979 | 7.7512 | 7.5451 | 7.2492 | 6.8839 | 6.4257 | 5.491 | 4.5716 | 3.3829 | 1.8543 | 0.45327 | -4.4335 | -7.6243 | -12.558 | 5.5496 | 5.3261 | 4.9741 | 4.4935 | 3.8588 | 2.5547 | 1.3149 | -0.21776 | -1.9922 | -3.4576 | -7.5463 | -9.0014 | -9.6657
|  | GOLDSMITHS | CF |  |  |  | 5.4011 | 5.2939 | 5.1827 | 5.0215 | 4.8654 | 4.7337 | 4.3939 | 3.7041 | 2.7276 | 1.6715 | -6.1887 | -7.2448 | -8.4336 | 7.792 | 7.6471 | 7.4859 | 7.2706 | 7.0471 | 6.8104 | 6.3278 | 5.5808 | 4.6318 | 3.6145 | -4.6498 | -9.8824 | -19.9733 | 5.6282 | 5.522 | 5.4139 | 5.2527 | 5.0976 | 4.968 | 4.5935 | 3.8782 | 2.8904 | 1.8292 | -5.8586 | -6.8647 | -7.8912
NURSLING GSP | WINCHESTER | GORDON ROAD | MINIMUM HEADROOM | SU 48217 29991 | YES | 3.251 | 14.9552 | 13.9479 | 13.403 | 12.6958 | 11.8326 | 10.8581 | 9.8499 | 8.6172 | 7.457 | 6.4397 | 1.3928 | -1.3521 | -2.3052 | 22.0726 | 21.2764 | 20.9754 | 20.6213 | 20.1989 | 19.5387 | 18.854 | 17.9703 | 17.1336 | 16.4091 | 12.8774 | 10.5162 | 2.2111 | 15.9236 | 15.0519 | 14.6662 | 14.2152 | 13.6723 | 13.056 | 12.1601 | 10.9897 | 9.8826 | 8.9193 | 4.1264 | 1.555 | 0.67439
|  | GORDON ROAD | EE |  |  |  | 14.9552 | 13.9479 | 13.403 | 12.6958 | 11.8326 | 10.8581 | 9.8499 | 8.6172 | 7.457 | 6.4397 | 2.5428 | 1.0958 | -1.2879 | 22.0726 | 21.2764 | 20.9754 | 20.6213 | 20.1989 | 19.5387 | 18.854 | 17.9703 | 17.1336 | 16.4091 | 13.557 | 10.5162 | 6.1193 | 15.9236 | 15.0519 | 14.6662 | 14.2152 | 13.6723 | 13.056 | 12.1601 | 10.9897 | 9.8826 | 8.9193 | 5.2723 | 3.4468 | 1.3764
|  | GORDON ROAD | HT |  |  |  | 15.294 | 14.4336 | 14.0397 | 13.5815 | 12.9795 | 12.2315 | 11.3326 | 10.3703 | 9.4999 | 8.4764 | 3.4774 | 0.65092 | -1.4828 | 22.2695 | 21.5591 | 21.3621 | 21.1285 | 20.8407 | 20.5142 | 20.0611 | 19.3968 | 18.805 | 18.0877 | 14.7366 | 13.1387 | 12.5172 | 16.1532 | 15.3734 | 15.0897 | 14.7632 | 14.3611 | 13.8979 | 13.3438 | 12.6774 | 11.856 | 10.8826 | 6.1621 | 3.0968 | 1.2591
|  | GORDON ROAD | HE |  |  |  | 15.2317 | 14.3111 | 13.8632 | 13.3366 | 12.6091 | 11.7479 | 10.7142 | 9.5713 | 8.5121 | 7.2693 | 1.3928 | -1.3521 | -2.3052 | 22.2164 | 21.4744 | 21.2326 | 20.9479 | 20.5979 | 20.204 | 19.5295 | 18.7142 | 17.954 | 17.053 | 12.8774 | 10.9785 | 7.0397 | 16.1011 | 15.2958 | 14.9826 | 14.6152 | 14.1652 | 13.6458 | 12.9928 | 11.9081 | 10.8979 | 9.7152 | 4.1264 | 1.555 | 0.67439
|  | GORDON ROAD | CF |  |  |  | 15.4338 | 14.7081 | 14.4713 | 14.1764 | 13.7958 | 13.3479 | 12.8846 | 12.3019 | 11.6703 | 10.9795 | 6.7958 | 2.7632 | -0.18071 | 22.347 | 21.6683 | 21.5019 | 21.3234 | 21.0938 | 20.8193 | 20.5428 | 20.2326 | 19.9009 | 19.5356 | 16.0683 | 10.6999 | 2.2111 | 16.2777 | 15.5734 | 15.3774 | 15.1652 | 14.8826 | 14.5509 | 14.2223 | 13.8846 | 13.5264 | 13.1326 | 9.2223 | 5.3938 | 2.6326
BRAMLEY (FLEE) | BURGHFIELD RESERVE | GORING | MINIMUM HEADROOM | SU 60305 82895 | YES | 0.09 | 10.475 | 10.3505 | 10.2383 | 10.0842 | 9.9117 | 9.7964 | 9.5291 | 9.2219 | 8.9138 | 8.7546 | 7.8883 | 7.1985 | 6.8577 | 10.9143 | 10.8194 | 10.7316 | 10.6102 | 10.4796 | 10.3745 | 10.1918 | 9.9714 | 9.7357 | 9.6184 | 8.948 | 8.1459 | 5.8224 | 10.4235 | 10.3092 | 10.2082 | 10.0622 | 9.9041 | 9.7898 | 9.5418 | 9.252 | 8.9571 | 8.8082 | 8.0327 | 7.4112 | 7.1133
|  | GORING | EE |  |  |  | 10.475 | 10.3505 | 10.2383 | 10.0842 | 9.9117 | 9.7964 | 9.5291 | 9.2219 | 8.9138 | 8.7546 | 7.9546 | 7.3393 | 6.8577 | 10.9143 | 10.8194 | 10.7316 | 10.6102 | 10.4796 | 10.3745 | 10.1918 | 9.9714 | 9.7357 | 9.6184 | 8.948 | 8.1459 | 6.9153 | 10.4235 | 10.3092 | 10.2082 | 10.0622 | 9.9041 | 9.7898 | 9.5418 | 9.252 | 8.9571 | 8.8082 | 8.0929 | 7.5408 | 7.1133
|  | GORING | HT |  |  |  | 10.5372 | 10.4423 | 10.3526 | 10.2464 | 10.1577 | 10.0311 | 9.8015 | 9.6066 | 9.3526 | 9.0893 | 7.8883 | 7.1985 | 7.1423 | 10.9745 | 10.9112 | 10.8602 | 10.7867 | 10.7327 | 10.651 | 10.5214 | 10.4122 | 10.2653 | 10.1071 | 9.4337 | 9.1184 | 9.25 | 10.4837 | 10.3959 | 10.3122 | 10.2122 | 10.1347 | 10.0153 | 9.8031 | 9.6235 | 9.3898 | 9.1469 | 8.0327 | 7.4112 | 7.4571
|  | GORING | HE |  |  |  | 10.5362 | 10.4434 | 10.3607 | 10.2617 | 10.1811 | 10.0607 | 9.8648 | 9.7056 | 9.4872 | 9.2617 | 8.2046 | 8.0495 | 7.7138 | 10.9602 | 10.8857 | 10.8184 | 10.7357 | 10.6704 | 10.5663 | 10.4337 | 10.3122 | 10.1469 | 9.9765 | 9.0684 | 8.5806 | 7.4061 | 10.4816 | 10.398 | 10.3204 | 10.2245 | 10.1551 | 10.0398 | 9.8602 | 9.7122 | 9.5092 | 9.299 | 8.3184 | 8.2173 | 7.952
|  | GORING | CF |  |  |  | 10.5719 | 10.5128 | 10.4566 | 10.3893 | 10.3117 | 10.2648 | 10.1709 | 10.0536 | 9.926 | 9.8617 | 9.0485 | 8.8679 | 8.325 | 10.9765 | 10.9153 | 10.8602 | 10.7898 | 10.7102 | 10.649 | 10.5429 | 10.4143 | 10.2755 | 10.1694 | 9.2041 | 8.1714 | 5.8224 | 10.5163 | 10.4592 | 10.4082 | 10.3459 | 10.2714 | 10.2306 | 10.1439 | 10.0347 | 9.9173 | 9.852 | 9.0786 | 8.9459 | 8.4429
IVER 132KV | DENHAM | GRASSINGHAM ROAD | MINIMUM HEADROOM | TQ 00165 90988 | YES | 0.809 | 1.5184 | 1.2235 | 0.83571 | 0.40714 | 0.41224 | 0.023469 | -0.6551 | -1.4163 | -2.1837 | -2.7041 | -5.899 | -8.2837 | -9.6316 | 10.3347 | 10.1265 | 9.8378 | 9.5184 | 9.5837 | 9.3133 | 8.9235 | 8.4643 | 7.998 | 7.748 | 6.4622 | 5.4878 | 4.9735 | 2.1755 | 1.9041 | 1.5327 | 1.1194 | 1.1367 | 0.76531 | 0.13163 | -0.58367 | -1.3031 | -1.7735 | -4.6235 | -6.7194 | -7.8949
|  | GRASSINGHAM ROAD | EE |  |  |  | 1.5184 | 1.2235 | 0.83571 | 0.40714 | 0.41224 | 0.023469 | -0.6551 | -1.4163 | -2.1837 | -2.7041 | -5.5102 | -7.7255 | -9.4102 | 10.3347 | 10.1265 | 9.8378 | 9.5184 | 9.5837 | 9.3133 | 8.9235 | 8.4643 | 7.998 | 7.748 | 6.5582 | 5.7388 | 5.1133 | 2.1755 | 1.9041 | 1.5327 | 1.1194 | 1.1367 | 0.76531 | 0.13163 | -0.58367 | -1.3031 | -1.7735 | -4.2908 | -6.2214 | -7.6959
|  | GRASSINGHAM ROAD | HT |  |  |  | 1.6898 | 1.4429 | 1.1367 | 0.85816 | 0.5102 | 0.13571 | -0.1551 | -0.83163 | -1.5378 | -2.2643 | -5.899 | -8.2837 | -9.6316 | 10.4959 | 10.349 | 10.149 | 9.9806 | 9.751 | 9.4969 | 9.4684 | 9.1092 | 8.7276 | 8.3224 | 6.4622 | 5.4878 | 4.9735 | 2.3245 | 2.099 | 1.8204 | 1.5643 | 1.2469 | 0.89082 | 0.61735 | -0.010204 | -0.65816 | -1.3255 | -4.6235 | -6.7194 | -7.8949
|  | GRASSINGHAM ROAD | HE |  |  |  | 1.701 | 1.4806 | 1.1969 | 0.94592 | 0.62959 | 0.28673 | 0.14592 | -0.38878 | -0.94694 | -1.5224 | -4.5224 | -6.6633 | -7.7673 | 10.4857 | 10.3357 | 10.1306 | 9.9602 | 9.749 | 9.5122 | 9.5418 | 9.2388 | 8.9163 | 8.5796 | 7 | 6.1735 | 5.7673 | 2.3337 | 2.1337 | 1.8786 | 1.648 | 1.352 | 1.0235 | 0.89898 | 0.40612 | -0.10612 | -0.63571 | -3.401 | -5.2755 | -6.2347
|  | GRASSINGHAM ROAD | CF |  |  |  | 1.8153 | 1.6633 | 1.5255 | 1.3459 | 1.2 | 1.0031 | 0.76531 | 0.47041 | 0.61327 | 0.35612 | -1.6255 | -3.7327 | -5.7102 | 10.5459 | 10.4163 | 10.299 | 10.1429 | 10.0439 | 9.8939 | 9.7235 | 9.5041 | 9.6592 | 9.4765 | 8.25 | 7.2531 | 6.4439 | 2.4398 | 2.3051 | 2.1837 | 2.0214 | 1.8816 | 1.6867 | 1.4561 | 1.1714 | 1.3214 | 1.0776 | -0.78673 | -2.6888 | -4.452
BRAMLEY (FLEE) | BURGHFIELD MAIN | GREEN PARK | MINIMUM HEADROOM | SU 70508 70222 | YES | 21.2 | 13.5527 | 13.4771 | 13.4445 | 13.0118 | 12.9853 | 12.9598 | 12.972 | 12.9863 | 12.9976 | 13.0108 | 13.0414 | 13.0649 | 13.0822 | 11.4353 | 11.3904 | 11.3445 | 10.8445 | 10.8231 | 10.7914 | 10.8108 | 10.8241 | 10.8343 | 10.8435 | 10.8659 | 10.8822 | 10.8965 | 11.5006 | 11.4129 | 11.3578 | 10.8924 | 10.8445 | 10.768 | 10.819 | 10.8465 | 10.869 | 10.8945 | 10.9476 | 10.9924 | 11.0373
|  | GREEN PARK | EE |  |  |  | 13.5527 | 13.4771 | 13.4445 | 13.0118 | 12.9863 | 12.9608 | 12.9731 | 12.9863 | 12.9976 | 13.0108 | 13.0741 | 13.0843 | 13.0822 | 11.4353 | 11.3914 | 11.3445 | 10.8445 | 10.8231 | 10.7914 | 10.8108 | 10.8241 | 10.8343 | 10.8435 | 10.8935 | 10.9006 | 10.8965 | 11.5006 | 11.4129 | 11.3578 | 10.8924 | 10.8455 | 10.769 | 10.819 | 10.8465 | 10.869 | 10.8945 | 11.0169 | 11.0394 | 11.0373
|  | GREEN PARK | HT |  |  |  | 13.5527 | 13.4771 | 13.4445 | 13.0118 | 12.9853 | 12.9598 | 12.972 | 12.9863 | 12.9996 | 13.0118 | 13.0741 | 13.0853 | 13.0833 | 11.4353 | 11.3904 | 11.3445 | 10.8455 | 10.8251 | 10.7935 | 10.8149 | 10.8271 | 10.8373 | 10.8465 | 10.8976 | 10.9057 | 10.9027 | 11.5006 | 11.4129 | 11.3578 | 10.8924 | 10.8445 | 10.768 | 10.819 | 10.8476 | 10.871 | 10.8955 | 11.018 | 11.0404 | 11.0384
|  | GREEN PARK | HE |  |  |  | 13.5527 | 13.4771 | 13.4445 | 13.0118 | 12.9863 | 12.9618 | 12.9731 | 12.9873 | 13.0006 | 13.0139 | 13.0792 | 13.0924 | 13.0924 | 11.4353 | 11.3914 | 11.3445 | 10.8445 | 10.8231 | 10.7914 | 10.8118 | 10.8251 | 10.8353 | 10.8455 | 10.8976 | 10.9078 | 10.9047 | 11.5006 | 11.4129 | 11.3578 | 10.8924 | 10.8455 | 10.769 | 10.819 | 10.8476 | 10.872 | 10.8976 | 11.022 | 11.0465 | 11.0476
|  | GREEN PARK | CF |  |  |  | 13.5578 | 13.4894 | 13.4618 | 13.0384 | 13.019 | 12.9976 | 13.0037 | 13.0078 | 13.0129 | 13.0169 | 13.0414 | 13.0649 | 13.0884 | 11.4394 | 11.4006 | 11.37 | 10.8639 | 10.8486 | 10.8333 | 10.8373 | 10.8404 | 10.8435 | 10.8476 | 10.8659 | 10.8822 | 10.8965 | 11.5108 | 11.4343 | 11.3904 | 10.9373 | 10.9006 | 10.8639 | 10.8731 | 10.8822 | 10.8914 | 10.9016 | 10.9476 | 10.9924 | 11.0394
WILLESDEN GSP |  | GREENFORD | MINIMUM HEADROOM | TQ 14695 83785 | YES | 19.753 | 31.3674 | 29.5133 | 27.2358 | 25.1939 | 23.3603 | 21.3643 | 19.3827 | 17.3205 | 15.4194 | 14.2031 | 9.7011 | 6.8899 | 6.8378 | 35.7041 | 34.2337 | 32.5368 | 31.3409 | 30.2194 | 28.9888 | 27.6143 | 26.0327 | 24.499 | 23.4246 | 18.0246 | 8.498 | -11.8775 | 29.8899 | 28.1654 | 26.0562 | 24.2674 | 22.6113 | 20.8001 | 18.9939 | 17.095 | 15.2848 | 14.1521 | 9.9848 | 7.5246 | 7.5766
|  | GREENFORD | EE |  |  |  | 31.3674 | 29.5133 | 27.2358 | 25.1939 | 23.3603 | 21.3643 | 19.3827 | 17.3205 | 15.4194 | 14.2031 | 9.7011 | 6.8899 | 7.7337 | 35.7041 | 34.2337 | 32.5368 | 31.3409 | 30.2194 | 28.9888 | 27.6143 | 26.0327 | 24.499 | 23.4246 | 18.0246 | 11.8613 | 2.8297 | 29.8899 | 28.1654 | 26.0562 | 24.2674 | 22.6113 | 20.8001 | 18.9939 | 17.095 | 15.2848 | 14.1521 | 9.9848 | 7.5246 | 8.2623
|  | GREENFORD | HT |  |  |  | 32.0011 | 30.0113 | 27.8929 | 26.4766 | 25.0072 | 23.3837 | 21.8909 | 20.4439 | 19.0705 | 17.645 | 10.9592 | 7.0817 | 6.8378 | 36.1378 | 34.7205 | 33.247 | 32.5368 | 31.795 | 30.9715 | 30.2103 | 29.445 | 28.7092 | 27.8603 | 23.6572 | 21.5225 | 21.1909 | 30.4725 | 28.6501 | 26.7031 | 25.5246 | 24.2348 | 22.8001 | 21.4643 | 20.1317 | 18.8409 | 17.497 | 11.2643 | 7.7705 | 7.5766
|  | GREENFORD | HE |  |  |  | 31.949 | 29.9684 | 27.8572 | 26.4276 | 24.9429 | 23.3031 | 21.845 | 20.4011 | 19.0266 | 17.596 | 11.9174 | 8.9572 | 8.5001 | 36.0052 | 34.4786 | 32.8684 | 32.0031 | 31.0735 | 30.0378 | 29.047 | 28.0113 | 26.9684 | 25.8378 | 19.1501 | 12.6348 | 3.2031 | 30.4174 | 28.599 | 26.647 | 25.4572 | 24.148 | 22.697 | 21.3827 | 20.0419 | 18.7419 | 17.3868 | 12.0164 | 9.3531 | 8.9715
|  | GREENFORD | CF |  |  |  | 32.3337 | 30.6786 | 28.947 | 27.6511 | 27.0582 | 25.9888 | 25.2205 | 24.4511 | 23.7072 | 23.0113 | 18.3062 | 13.4684 | 9.1582 | 36.199 | 34.8123 | 33.3592 | 32.5082 | 31.9684 | 31.1154 | 30.3103 | 29.446 | 28.5592 | 27.6541 | 20.3664 | 8.498 | -11.8775 | 30.7786 | 29.2664 | 27.6694 | 26.5715 | 26.0572 | 25.1184 | 24.4439 | 23.7388 | 23.0409 | 22.3929 | 17.9388 | 13.4562 | 9.5674
LOVEDEAN GSP | PORTSMOUTH BSP | GREETHAM STREET | MINIMUM HEADROOM | SU 64445 00178 | YES | 1.001 | 16.1408 | 16.002 | 15.7602 | 15.0888 | 14.2939 | 13.1194 | 12.4306 | 11.7296 | 11.0276 | 10.4286 | 9.35 | 8.5357 | 8.5469 | 17.5765 | 17.3653 | 17.1214 | 16.6592 | 16.1112 | 15.3847 | 14.849 | 14.2786 | 13.6847 | 13.1449 | 10.8163 | 5.9439 | -4.402 | 15.0888 | 14.9031 | 14.6949 | 14.1449 | 13.4806 | 12.4949 | 11.9163 | 11.3163 | 10.6908 | 10.1684 | 9.1622 | 8.598 | 8.5867
|  | GREETHAM STREET | EE |  |  |  | 16.1408 | 16.002 | 15.7602 | 15.0888 | 14.2939 | 13.1194 | 12.4306 | 11.7296 | 11.0276 | 10.4286 | 9.35 | 8.8082 | 8.9224 | 17.5765 | 17.3653 | 17.1214 | 16.6592 | 16.1112 | 15.3847 | 14.849 | 14.2786 | 13.6847 | 13.1449 | 10.8163 | 7.8867 | 2.9092 | 15.0888 | 14.9031 | 14.6949 | 14.1449 | 13.4806 | 12.4949 | 11.9163 | 11.3163 | 10.6908 | 10.1684 | 9.1622 | 8.7327 | 8.749
|  | GREETHAM STREET | HT |  |  |  | 16.2163 | 16.1255 | 16.0133 | 15.4092 | 14.4653 | 13.3561 | 12.8378 | 12.2663 | 11.699 | 11.3429 | 9.701 | 8.5357 | 8.5469 | 17.6939 | 17.6224 | 17.5041 | 17.1735 | 16.6888 | 16.1235 | 15.8357 | 15.4969 | 15.151 | 14.8918 | 13.7163 | 12.9031 | 12.7816 | 15.2061 | 15.0796 | 14.9388 | 14.4551 | 13.6918 | 12.7755 | 12.3561 | 11.8929 | 11.4327 | 11.1398 | 9.6531 | 8.598 | 8.5867
|  | GREETHAM STREET | HE |  |  |  | 16.2102 | 16.1235 | 16.0286 | 15.4765 | 14.8173 | 13.8735 | 13.4929 | 13.0663 | 12.649 | 12.2265 | 11.0561 | 10.7112 | 10.7143 | 17.6582 | 17.5163 | 17.3459 | 16.9602 | 16.5194 | 15.9378 | 15.6051 | 15.2173 | 14.8071 | 14.3745 | 12.0398 | 9.2112 | 4.301 | 15.1959 | 15.0776 | 14.951 | 14.4867 | 13.9398 | 13.151 | 12.8378 | 12.4816 | 12.1306 | 11.7796 | 10.8439 | 10.5745 | 10.5959
|  | GREETHAM STREET | CF |  |  |  | 16.2806 | 16.2255 | 16.1602 | 15.7888 | 15.25 | 14.6367 | 14.3816 | 14.0949 | 13.8133 | 13.5143 | 12.0745 | 11.0878 | 10.2173 | 17.702 | 17.5816 | 17.4184 | 17.0653 | 16.649 | 16.1653 | 15.801 | 15.3908 | 14.9622 | 14.4939 | 11.3786 | 5.9439 | -4.402 | 15.2827 | 15.2122 | 15.1255 | 14.7561 | 14.3163 | 13.8112 | 13.6092 | 13.3765 | 13.149 | 12.9071 | 11.6806 | 10.85 | 10.1531
COWLEY GSP | DRAYTON BSP | GROVE | MINIMUM HEADROOM | SU 39515 89611 | YES | 8.6 | -4.8366 | -6.201 | -7.0826 | -7.9643 | -8.7347 | -12.6969 | -13.9449 | -15.1622 | -16.302 | -17.1541 | -21.898 | -25.8306 | -28.951 | -1.9189 | -3.0536 | -3.6679 | -4.222 | -4.6006 | -8.0383 | -8.7281 | -9.4322 | -10.1077 | -10.6077 | -13.4506 | -16.5496 | -23.2394 | -4.6559 | -5.9295 | -6.7111 | -7.506 | -8.0601 | -11.8499 | -12.9254 | -14.004 | -15.0285 | -15.7325 | -19.7172 | -23.0264 | -25.5458
|  | GROVE | EE |  |  |  | -4.8366 | -6.201 | -7.0826 | -7.9643 | -8.7347 | -12.6969 | -13.9449 | -15.1622 | -16.302 | -17.1541 | -21.7347 | -25.4153 | -28.6765 | -1.9189 | -3.0536 | -3.6679 | -4.222 | -4.6006 | -8.0383 | -8.7281 | -9.4322 | -10.1077 | -10.6077 | -13.4506 | -16.3536 | -20.2751 | -4.6559 | -5.9295 | -6.7111 | -7.506 | -8.0601 | -11.8499 | -12.9254 | -14.004 | -15.0285 | -15.7325 | -19.5836 | -22.6499 | -25.3101
|  | GROVE | HT |  |  |  | -4.7132 | -6.0316 | -6.8653 | -7.6806 | -8.648 | -12.601 | -13.8602 | -14.7163 | -15.8071 | -16.8173 | -21.898 | -25.8306 | -28.951 | -1.7862 | -2.8485 | -3.3812 | -3.8353 | -4.3251 | -7.6975 | -8.321 | -8.6567 | -9.2026 | -9.7465 | -12.2292 | -14.0271 | -15.4312 | -4.5121 | -5.7325 | -6.457 | -7.1509 | -7.9632 | -11.7336 | -12.804 | -13.4928 | -14.4264 | -15.3203 | -19.7172 | -23.0264 | -25.5458
|  | GROVE | HE |  |  |  | -4.7101 | -6.0082 | -6.8224 | -7.5806 | -8.5265 | -12.4888 | -13.6408 | -14.3929 | -15.3714 | -16.2347 | -20.8847 | -24.5439 | -27.2786 | -1.8158 | -2.8996 | -3.4598 | -3.9139 | -4.4332 | -7.871 | -8.5077 | -8.8628 | -9.4332 | -9.9669 | -13.02 | -15.9526 | -19.6577 | -4.51 | -5.7101 | -6.4183 | -7.0621 | -7.854 | -11.6336 | -12.607 | -13.1999 | -14.0366 | -14.7846 | -18.806 | -21.8662 | -24.055
|  | GROVE | CF |  |  |  | -4.5989 | -5.7918 | -6.4806 | -7.1194 | -7.8796 | -11.5786 | -12.3826 | -13.1551 | -13.5561 | -14.1255 | -17.7184 | -21.548 | -25.4602 | -1.7638 | -2.8036 | -3.3169 | -3.7383 | -4.1904 | -7.519 | -8.0455 | -8.5781 | -8.8404 | -9.2883 | -12.3057 | -16.5496 | -23.2394 | -4.409 | -5.5142 | -6.1081 | -6.6438 | -7.2632 | -10.807 | -11.4683 | -12.1142 | -12.403 | -12.8866 | -16.0101 | -19.2315 | -22.5009
MANNINGTON GSP | SHAFTESBURY BSP | GUSSAGE ST MICHAEL | MINIMUM HEADROOM | ST 98638 11417 | YES | 0.05 | 7.2184 | 7.1949 | 7.1551 | 7.1245 | 7.0796 | 7.0571 | 6.999 | 6.9398 | 6.8714 | 6.8551 | 6.7378 | 6.6888 | 6.651 | 6.977 | 6.9607 | 6.9321 | 6.9107 | 6.876 | 6.8648 | 6.8219 | 6.7842 | 6.7342 | 6.7148 | 6.6148 | 6.4546 | 6.1209 | 7.3541 | 7.3316 | 7.2949 | 7.2633 | 7.2153 | 7.1939 | 7.1357 | 7.0776 | 7.0112 | 6.9949 | 6.9071 | 6.8612 | 6.8286
|  | GUSSAGE ST MICHAEL | EE |  |  |  | 7.2184 | 7.1949 | 7.1551 | 7.1245 | 7.0796 | 7.0571 | 6.999 | 6.9398 | 6.8714 | 6.8551 | 6.7378 | 6.6888 | 6.6633 | 6.977 | 6.9607 | 6.9321 | 6.9107 | 6.876 | 6.8648 | 6.8219 | 6.7842 | 6.7342 | 6.7148 | 6.6148 | 6.5066 | 6.3434 | 7.3541 | 7.3316 | 7.2949 | 7.2633 | 7.2153 | 7.1939 | 7.1357 | 7.0776 | 7.0112 | 6.9949 | 6.9071 | 6.8612 | 6.8398
|  | GUSSAGE ST MICHAEL | HT |  |  |  | 7.2418 | 7.2153 | 7.1898 | 7.1714 | 7.1398 | 7.1173 | 7.0755 | 7.0276 | 7.0031 | 6.9551 | 6.7673 | 6.702 | 6.651 | 6.9974 | 6.9781 | 6.9638 | 6.9515 | 6.9301 | 6.9158 | 6.8883 | 6.8546 | 6.8423 | 6.8107 | 6.6934 | 6.6577 | 6.6311 | 7.3724 | 7.3469 | 7.3276 | 7.3112 | 7.2816 | 7.2602 | 7.2235 | 7.1786 | 7.1531 | 7.1082 | 6.9337 | 6.8704 | 6.8286
|  | GUSSAGE ST MICHAEL | HE |  |  |  | 7.2418 | 7.2173 | 7.1918 | 7.1735 | 7.1439 | 7.1224 | 7.0806 | 7.0347 | 7.0133 | 6.9622 | 6.7592 | 6.7153 | 6.6908 | 6.9944 | 6.977 | 6.9607 | 6.9495 | 6.927 | 6.9117 | 6.8801 | 6.8485 | 6.8311 | 6.7964 | 6.6321 | 6.525 | 6.3628 | 7.3724 | 7.349 | 7.3296 | 7.3122 | 7.2847 | 7.2663 | 7.2265 | 7.1857 | 7.1602 | 7.1173 | 6.9276 | 6.8867 | 6.8663
|  | GUSSAGE ST MICHAEL | CF |  |  |  | 7.2459 | 7.2286 | 7.2071 | 7.1827 | 7.1694 | 7.1459 | 7.1163 | 7.098 | 7.0622 | 7.0296 | 6.8837 | 6.7837 | 6.7143 | 6.9974 | 6.9862 | 6.9709 | 6.9536 | 6.9444 | 6.924 | 6.9005 | 6.8821 | 6.8505 | 6.8219 | 6.6648 | 6.4546 | 6.1209 | 7.3765 | 7.3602 | 7.3408 | 7.3224 | 7.3092 | 7.2888 | 7.2643 | 7.2459 | 7.2133 | 7.1827 | 7.0439 | 6.9469 | 6.8857
BOTLEY WOOD GSP | NETLEY COMMON BSP | HAMBLE | MINIMUM HEADROOM | SU 47370 08794 | YES | 0.833 | 13.2815 | 13.0693 | 12.7999 | 12.4458 | 12.054 | 12.0601 | 11.4897 | 10.8325 | 10.1907 | 9.6489 | 7.1121 | 5.1601 | 3.9295 | 14.3631 | 14.1325 | 13.8999 | 13.607 | 13.2764 | 13.3448 | 12.954 | 12.506 | 12.0438 | 11.7499 | 10.158 | 8.0264 | 2.5152 | 12.904 | 12.6611 | 12.4162 | 12.0948 | 11.7152 | 11.6968 | 11.1631 | 10.5478 | 9.9468 | 9.4438 | 7.0876 | 5.3356 | 4.2999
|  | HAMBLE | EE |  |  |  | 13.2815 | 13.0693 | 12.7999 | 12.4458 | 12.054 | 12.0601 | 11.4897 | 10.8325 | 10.1907 | 9.6489 | 7.2642 | 5.6029 | 4.2029 | 14.3631 | 14.1325 | 13.8999 | 13.607 | 13.2764 | 13.3448 | 12.954 | 12.506 | 12.0438 | 11.7499 | 10.158 | 8.5101 | 5.7315 | 12.904 | 12.6611 | 12.4162 | 12.0948 | 11.7152 | 11.6968 | 11.1631 | 10.5478 | 9.9468 | 9.4438 | 7.2693 | 5.7458 | 4.5325
|  | HAMBLE | HT |  |  |  | 13.3754 | 13.1968 | 13.0101 | 12.7999 | 12.5989 | 12.308 | 11.7631 | 11.157 | 10.904 | 10.3417 | 7.2652 | 5.1601 | 3.9295 | 14.5029 | 14.3723 | 14.2305 | 14.0458 | 13.8958 | 13.6733 | 13.3376 | 12.955 | 12.9968 | 12.6499 | 10.9509 | 9.9917 | 9.4499 | 13.0336 | 12.8407 | 12.6468 | 12.4172 | 12.207 | 11.9376 | 11.4223 | 10.856 | 10.6274 | 10.0815 | 7.2019 | 5.3356 | 4.2999
|  | HAMBLE | HE |  |  |  | 13.3795 | 13.208 | 13.0284 | 12.8295 | 12.6376 | 12.3815 | 11.9203 | 11.3254 | 10.8672 | 10.2387 | 7.1121 | 5.3438 | 4.4876 | 14.4917 | 14.3376 | 14.1693 | 13.9662 | 13.7897 | 13.5478 | 13.2101 | 12.8182 | 12.8438 | 12.4754 | 10.505 | 8.5989 | 6.0519 | 13.0336 | 12.8519 | 12.6672 | 12.4489 | 12.2529 | 12.0019 | 11.5733 | 11.0172 | 10.5968 | 10.0029 | 7.0876 | 5.4774 | 4.6968
|  | HAMBLE | CF |  |  |  | 13.4764 | 13.3978 | 13.2927 | 13.2029 | 13.0713 | 12.9478 | 12.7346 | 12.4754 | 12.1887 | 11.8876 | 9.9907 | 7.7387 | 5.9509 | 14.5223 | 14.4295 | 14.2774 | 14.1509 | 13.9805 | 13.8284 | 13.5938 | 13.3111 | 13.005 | 12.6774 | 11.1182 | 8.0264 | 2.5152 | 13.1162 | 13.0325 | 12.905 | 12.806 | 12.6672 | 12.5611 | 12.3754 | 12.1233 | 11.8519 | 11.5621 | 9.7458 | 7.657 | 6.0244
MANNINGTON GSP | POOLE PS (HAMWORTHY) | HAMWORTHY | MINIMUM HEADROOM | SZ 00104 90800 | YES | 0.592 | 7.1296 | 6.2082 | 5.1194 | 4.0347 | 2.6827 | 1.2459 | -0.38469 | -2.3786 | -4.298 | -5.9112 | -14.7592 | -18.901 | -19.8276 | 11.7714 | 11.1245 | 10.3735 | 9.8204 | 8.8265 | 7.7806 | 6.6306 | 5.2173 | 3.8602 | 2.748 | -3.5459 | -7.499 | -18.8684 | 8.6224 | 7.7531 | 6.7327 | 6.0173 | 4.848 | 3.4878 | 1.9418 | 0.055102 | -1.7755 | -3.2745 | -11.652 | -15.5459 | -16.3122
|  | HAMWORTHY | EE |  |  |  | 7.1296 | 6.2082 | 5.1194 | 4.0347 | 2.6827 | 1.2459 | -0.38469 | -2.3786 | -4.298 | -5.9112 | -12.9255 | -16.8898 | -19.8276 | 11.7714 | 11.1245 | 10.3735 | 9.8204 | 8.8265 | 7.7806 | 6.6306 | 5.2173 | 3.8602 | 2.748 | -2.1173 | -6.3245 | -12.4388 | 8.6224 | 7.7531 | 6.7327 | 6.0173 | 4.848 | 3.4878 | 1.9418 | 0.055102 | -1.7755 | -3.2745 | -9.5541 | -12.7143 | -15.1959
|  | HAMWORTHY | HT |  |  |  | 7.5888 | 6.8306 | 6.0439 | 5.0204 | 3.9112 | 2.9959 | 1.4592 | -0.34898 | -2.0806 | -3.8398 | -12.302 | -17.0673 | -19.5041 | 12.1898 | 11.7337 | 11.249 | 10.6316 | 9.9755 | 9.5041 | 8.6878 | 7.701 | 6.7378 | 5.7418 | 1.1653 | -1.1367 | -2.1571 | 9.1469 | 8.4663 | 7.7388 | 6.801 | 5.7806 | 5.0204 | 3.6551 | 2.0398 | 0.46224 | -1.15 | -8.7347 | -12.8031 | -14.8235
|  | HAMWORTHY | HE |  |  |  | 7.4847 | 6.6878 | 5.8378 | 4.8112 | 3.5582 | 2.2867 | 0.76327 | -1.1663 | -3.2 | -5.3204 | -14.7592 | -18.901 | -19.8 | 12.052 | 11.4959 | 10.8898 | 10.1918 | 9.399 | 8.5949 | 7.5122 | 6.1408 | 4.6806 | 3.1602 | -3.5459 | -7.499 | -13.1429 | 9.0357 | 8.3102 | 7.5224 | 6.601 | 5.552 | 4.5 | 3.0551 | 1.2306 | -0.7 | -2.7102 | -11.652 | -15.5459 | -16.3122
|  | HAMWORTHY | CF |  |  |  | 7.8837 | 7.3102 | 6.7459 | 6.2765 | 5.752 | 5.1796 | 4.6327 | 3.6959 | 2.6633 | 1.5602 | -5.9061 | -11.3112 | -14.3847 | 12.3041 | 11.8429 | 11.3765 | 10.9541 | 10.4663 | 9.9429 | 9.6051 | 8.8929 | 8.1071 | 7.2551 | 0.64796 | -7.0867 | -18.8684 | 9.4082 | 8.8929 | 8.3561 | 7.8959 | 7.3653 | 6.8194 | 6.6296 | 5.8153 | 4.8296 | 3.7735 | -3.251 | -8.3755 | -11.2337
IVER 132KV | DENHAM | HAREFIELD | MINIMUM HEADROOM | TQ 04001 91227 | YES | 0.814 | 9.2186 | 9.0747 | 8.9278 | 8.7247 | 8.4971 | 8.3124 | 7.9645 | 7.5676 | 7.1706 | 6.9349 | 6.0186 | 4.9308 | 4.3278 | 10.4441 | 10.3257 | 10.2094 | 10.0522 | 9.8706 | 9.7257 | 9.4798 | 9.1941 | 8.9053 | 8.7441 | 8.2267 | 7.3808 | 5.1471 | 9.8206 | 9.6767 | 9.5339 | 9.339 | 9.1227 | 8.9492 | 8.6206 | 8.2441 | 7.8665 | 7.6471 | 6.9329 | 6.0084 | 5.5012
|  | HAREFIELD | EE |  |  |  | 9.2186 | 9.0747 | 8.9278 | 8.7247 | 8.4971 | 8.3124 | 7.9645 | 7.5676 | 7.1706 | 6.9349 | 6.1267 | 5.1502 | 4.4308 | 10.4441 | 10.3257 | 10.2094 | 10.0522 | 9.8706 | 9.7257 | 9.4798 | 9.1941 | 8.9053 | 8.7441 | 8.2706 | 7.3808 | 6.1002 | 9.8206 | 9.6767 | 9.5339 | 9.339 | 9.1227 | 8.9492 | 8.6206 | 8.2441 | 7.8665 | 7.6471 | 7.0022 | 6.2053 | 5.5849
|  | HAREFIELD | HT |  |  |  | 9.2941 | 9.1808 | 9.0584 | 8.9135 | 8.7839 | 8.6084 | 8.3114 | 8.0329 | 7.7033 | 7.3624 | 6.0186 | 4.9308 | 4.3278 | 10.5227 | 10.4461 | 10.3665 | 10.2676 | 10.1849 | 10.0584 | 9.8839 | 9.7298 | 9.5257 | 9.3114 | 8.7257 | 8.2441 | 7.99 | 9.8992 | 9.79 | 9.6767 | 9.538 | 9.4155 | 9.2461 | 8.9696 | 8.7227 | 8.4135 | 8.09 | 6.9329 | 6.0084 | 5.5012
|  | HAREFIELD | HE |  |  |  | 9.2961 | 9.192 | 9.0818 | 8.9512 | 8.8359 | 8.6757 | 8.4308 | 8.2053 | 7.9288 | 7.6441 | 6.2329 | 5.6573 | 5.2135 | 10.5104 | 10.4288 | 10.3451 | 10.242 | 10.1502 | 10.0206 | 9.8502 | 9.6941 | 9.4931 | 9.2818 | 8.2267 | 7.641 | 6.4635 | 9.9022 | 9.8002 | 9.6961 | 9.5706 | 9.4624 | 9.3063 | 9.0747 | 8.8747 | 8.6104 | 8.339 | 7.0522 | 6.6635 | 6.2859
|  | HAREFIELD | CF |  |  |  | 9.3502 | 9.289 | 9.2247 | 9.141 | 9.0441 | 8.9369 | 8.8573 | 8.7176 | 8.5676 | 8.4655 | 7.441 | 6.9584 | 6.139 | 10.542 | 10.4798 | 10.4135 | 10.3369 | 10.241 | 10.1369 | 10.0492 | 9.9053 | 9.7553 | 9.639 | 8.5767 | 7.489 | 5.1471 | 9.9533 | 9.889 | 9.8257 | 9.7451 | 9.6512 | 9.5482 | 9.4747 | 9.34 | 9.1971 | 9.1033 | 8.1288 | 7.7859 | 7.0512
NURSLING GSP | WINCHESTER | HARESTOCK | MINIMUM HEADROOM | SU 45908 31300 | YES | 8.356 | 7.8214 | 5.8678 | 5.2025 | 4.677 | 2.1249 | -0.81284 | -2.3343 | -3.9506 | -6.773 | -8.8669 | -16.569 | -22.6679 | -27.6322 | 12.6929 | 10.8463 | 10.3208 | 9.8647 | 7.5535 | 4.7259 | 3.5923 | 2.3188 | -0.4159 | -2.4608 | -9.2016 | -15.8179 | -23.9822 | 8.8367 | 6.9045 | 6.28 | 5.7535 | 3.2555 | 0.23512 | -1.219 | -2.822 | -5.8792 | -8.1486 | -15.8312 | -22.1547 | -27.6792
|  | HARESTOCK | EE |  |  |  | 7.8214 | 5.8678 | 5.2025 | 4.677 | 2.1372 | -0.71284 | -2.3343 | -3.9047 | -5.8057 | -6.9924 | -13.2761 | -20.6598 | -24.5251 | 12.6929 | 10.8463 | 10.3208 | 10.0198 | 7.7739 | 5.1984 | 4.0433 | 3.0065 | 1.5463 | 0.65144 | -4.3649 | -12.4853 | -18.4914 | 8.8367 | 6.9045 | 6.28 | 5.8372 | 3.3892 | 0.59022 | -0.9506 | -2.3853 | -4.2281 | -5.3771 | -11.4261 | -19.3077 | -23.0822
|  | HARESTOCK | HT |  |  |  | 8.1418 | 6.2831 | 5.729 | 4.831 | 2.3678 | -0.40264 | -2.0047 | -3.773 | -5.3037 | -6.9843 | -14.6853 | -22.1149 | -26.969 | 13.0153 | 11.2984 | 10.9076 | 10.2729 | 8.1484 | 5.5953 | 4.5157 | 3.2821 | 2.3729 | 1.0749 | -4.2904 | -10.6424 | -14.9363 | 9.1561 | 7.3208 | 6.7902 | 5.9423 | 3.5729 | 0.76369 | -0.77917 | -2.4914 | -3.8924 | -5.5904 | -13.12 | -20.9557 | -26.0628
|  | HARESTOCK | HE |  |  |  | 8.1265 | 6.2821 | 5.6984 | 4.6861 | 2.1249 | -0.81284 | -2.3057 | -3.9506 | -6.773 | -8.8669 | -16.569 | -22.6679 | -27.6322 | 12.952 | 11.1963 | 10.7076 | 9.8647 | 7.5535 | 4.7259 | 3.5923 | 2.3188 | -0.4159 | -2.4608 | -9.2016 | -15.8179 | -23.9822 | 9.1367 | 7.3137 | 6.7433 | 5.7535 | 3.2555 | 0.23512 | -1.219 | -2.822 | -5.8792 | -8.1486 | -15.8312 | -22.1547 | -27.6792
|  | HARESTOCK | CF |  |  |  | 8.3541 | 6.6933 | 6.3719 | 5.8861 | 3.629 | 1.278 | 0.829 | 0.036139 | -0.80876 | -1.4873 | -6.3935 | -11.8935 | -16.9424 | 13.0847 | 11.4157 | 11.1157 | 10.7474 | 8.6147 | 6.3882 | 5.9994 | 5.2984 | 4.5484 | 3.8157 | -1.3496 | -8.5394 | -18.6557 | 9.349 | 7.6974 | 7.3974 | 6.981 | 4.777 | 2.48 | 2.0729 | 1.3361 | 0.54634 | -0.13937 | -5.0077 | -10.4741 | -15.4771
EALING GSP | EALING 22kV | HARVARD LANE | MINIMUM HEADROOM | TQ 20021 78030 | YES | 1.865 | 1.3556 | 0.82806 | 0.071939 | 50.2954 | 49.3168 | 48.1311 | 47.277 | 45.8668 | 44.4638 | 43.4903 | 38.2944 | 33.2913 | 30.1117 | 6.0474 | 5.6005 | 4.976 | 55.3423 | 54.5597 | 53.5903 | 52.9434 | 51.8474 | 50.7444 | 49.9128 | 45.2087 | 39.0495 | 23.5628 | 0.65561 | 0.15255 | -0.56582 | 49.6954 | 48.7679 | 47.623 | 46.7832 | 45.4413 | 44.1189 | 43.1954 | 38.623 | 34.3811 | 31.6291
|  | HARVARD LANE | EE |  |  |  | 1.3556 | 0.82806 | 0.071939 | 50.2954 | 49.3168 | 48.1311 | 47.277 | 45.8668 | 44.4638 | 43.4903 | 38.2944 | 34.0964 | 30.3485 | 6.0474 | 5.6005 | 4.976 | 55.3423 | 54.5597 | 53.5903 | 52.9434 | 51.8474 | 50.7444 | 49.9128 | 45.2087 | 39.8903 | 31.4046 | 0.65561 | 0.15255 | -0.56582 | 49.6954 | 48.7679 | 47.623 | 46.7832 | 45.4413 | 44.1189 | 43.1954 | 38.623 | 35.1158 | 31.8117
|  | HARVARD LANE | HT |  |  |  | 1.6872 | 1.2281 | 0.63418 | 50.9372 | 50.0311 | 49.1801 | 48.1291 | 47.0097 | 45.973 | 45.3015 | 38.876 | 33.2913 | 30.1117 | 6.3801 | 6.073 | 5.6985 | 56.2526 | 55.6321 | 55.0638 | 54.423 | 53.7056 | 53.0015 | 52.6628 | 49.0883 | 46.3138 | 44.9709 | 0.975 | 0.54439 | -0.002551 | 50.3505 | 49.477 | 48.6658 | 47.6903 | 46.6403 | 45.6352 | 45.0638 | 39.2372 | 34.3811 | 31.6291
|  | HARVARD LANE | HE |  |  |  | 1.6342 | 1.2495 | 0.72296 | 51.1372 | 50.4454 | 49.5832 | 48.5607 | 47.4403 | 46.6495 | 45.7311 | 40.7219 | 36.8893 | 35.3138 | 6.277 | 5.9526 | 5.5189 | 56.0434 | 55.4974 | 54.824 | 54.0852 | 53.2281 | 52.6026 | 51.8056 | 46.9923 | 41.6893 | 34.0434 | 0.925 | 0.55561 | 0.061735 | 50.5117 | 49.8628 | 49.0577 | 48.1189 | 47.0791 | 46.4168 | 45.5505 | 41.023 | 37.7668 | 36.4199
|  | HARVARD LANE | CF |  |  |  | 1.8515 | 1.6179 | 1.3291 | 52.0138 | 51.6597 | 51.2668 | 50.8985 | 50.3536 | 49.6842 | 49.0005 | 45.8321 | 42.5434 | 39.1648 | 6.3913 | 6.1199 | 5.7903 | 56.4168 | 56.0066 | 55.5209 | 54.9801 | 54.2801 | 53.4923 | 52.6485 | 47.5332 | 39.0495 | 23.5628 | 1.1291 | 0.90663 | 0.63316 | 51.3383 | 51.0046 | 50.6383 | 50.275 | 49.7464 | 49.1056 | 48.4556 | 45.4383 | 42.4566 | 39.5648
COWLEY GSP |  | HARWELL | MINIMUM HEADROOM | SU 47395 86969 | YES | 18.037 | 18.37 | 18.3619 | 18.3517 | 18.3445 | 18.3323 | 18.3262 | 18.3068 | 18.2904 | 18.27 | 18.2547 | 18.1762 | 18.1313 | 18.1027 | 19.2037 | 19.1945 | 19.1833 | 19.1762 | 19.1619 | 19.1527 | 19.1333 | 19.1088 | 19.0853 | 19.067 | 18.9445 | 18.8323 | 18.5731 | 18.469 | 18.4568 | 18.4394 | 18.4272 | 18.4068 | 18.3956 | 18.3588 | 18.32 | 18.2802 | 18.2466 | 18.0466 | 17.916 | 17.8364
|  | HARWELL | EE |  |  |  | 18.37 | 18.3619 | 18.3517 | 18.3445 | 18.3323 | 18.3262 | 18.3068 | 18.2904 | 18.27 | 18.2588 | 18.1813 | 18.1364 | 18.1047 | 19.2037 | 19.1945 | 19.1833 | 19.1762 | 19.1619 | 19.1527 | 19.1333 | 19.1088 | 19.0853 | 19.067 | 18.9445 | 18.8323 | 18.6833 | 18.469 | 18.4568 | 18.4394 | 18.4272 | 18.4068 | 18.3956 | 18.3588 | 18.32 | 18.2802 | 18.2517 | 18.066 | 17.9333 | 17.8425
|  | HARWELL | HT |  |  |  | 18.3751 | 18.368 | 18.3588 | 18.3537 | 18.3435 | 18.3364 | 18.3211 | 18.3119 | 18.2945 | 18.2547 | 18.1762 | 18.1313 | 18.1027 | 19.2098 | 19.2047 | 19.1966 | 19.1925 | 19.1813 | 19.1751 | 19.1588 | 19.1476 | 19.1313 | 19.0864 | 18.9966 | 18.9445 | 18.9139 | 18.4751 | 18.4629 | 18.4466 | 18.4364 | 18.418 | 18.4068 | 18.3711 | 18.3435 | 18.3068 | 18.2466 | 18.0466 | 17.916 | 17.8364
|  | HARWELL | HE |  |  |  | 18.3751 | 18.369 | 18.3598 | 18.3537 | 18.3466 | 18.3404 | 18.3282 | 18.32 | 18.3058 | 18.2945 | 18.2088 | 18.1731 | 18.1517 | 19.2088 | 19.2017 | 19.1925 | 19.1864 | 19.1772 | 19.167 | 19.1527 | 19.1404 | 19.1221 | 19.1037 | 18.9711 | 18.8639 | 18.7241 | 18.4762 | 18.4649 | 18.4496 | 18.4404 | 18.4251 | 18.4129 | 18.3853 | 18.3649 | 18.3353 | 18.3068 | 18.1211 | 17.9966 | 17.9333
|  | HARWELL | CF |  |  |  | 18.3782 | 18.3731 | 18.368 | 18.3629 | 18.3598 | 18.3527 | 18.3486 | 18.3404 | 18.3323 | 18.3292 | 18.2588 | 18.22 | 18.1874 | 19.2109 | 19.2047 | 19.2007 | 19.1904 | 19.1874 | 19.1762 | 19.169 | 19.1547 | 19.1415 | 19.1333 | 18.9996 | 18.8404 | 18.5731 | 18.4813 | 18.4731 | 18.467 | 18.4578 | 18.4537 | 18.4435 | 18.4374 | 18.4251 | 18.4109 | 18.4098 | 18.2823 | 18.169 | 18.0639
BRAMLEY (FLEE) | FERNHURST | HASLEMERE | MINIMUM HEADROOM | SU 89300 31710 | YES | 2.543 | 9.0908 | 8.4765 | 7.9041 | 7.6571 | 7.0929 | 6.4724 | 5.5112 | 4.4806 | 3.452 | 2.6969 | -1.4786 | -4.8102 | -6.6765 | 13.149 | 12.7286 | 12.2959 | 12.1194 | 11.6796 | 11.1929 | 10.5296 | 9.7786 | 9.0112 | 8.4724 | 5.4347 | 1.7235 | -7.2643 | 10.4367 | 9.8867 | 9.3235 | 9.1633 | 8.6214 | 8.0204 | 7.148 | 6.1857 | 5.2092 | 4.5378 | 0.88469 | -2.0541 | -3.652
|  | HASLEMERE | EE |  |  |  | 9.0908 | 8.4765 | 7.9041 | 7.6571 | 7.0929 | 6.4724 | 5.5112 | 4.4806 | 3.452 | 2.6969 | -1.3398 | -4.15 | -6.248 | 13.149 | 12.7286 | 12.2959 | 12.1194 | 11.6796 | 11.1929 | 10.5296 | 9.7786 | 9.0112 | 8.4724 | 5.4347 | 2.1806 | -2.6245 | 10.4367 | 9.8867 | 9.3235 | 9.1633 | 8.6214 | 8.0204 | 7.148 | 6.1857 | 5.2092 | 4.5378 | 0.97143 | -1.4663 | -3.2888
|  | HASLEMERE | HT |  |  |  | 9.3102 | 8.7469 | 8.3378 | 7.8684 | 7.3592 | 7.1143 | 6.2133 | 5.3378 | 4.4133 | 3.4571 | -1.4786 | -4.8102 | -6.6765 | 13.3694 | 13.0551 | 12.8143 | 12.5204 | 12.199 | 12.0969 | 11.6194 | 11.1286 | 10.6 | 10.05 | 7.3898 | 5.8041 | 4.9724 | 10.6959 | 10.2102 | 9.8408 | 9.398 | 8.9163 | 8.7214 | 7.9092 | 7.102 | 6.2531 | 5.3735 | 0.88469 | -2.0541 | -3.652
|  | HASLEMERE | HE |  |  |  | 9.3102 | 8.7969 | 8.3969 | 7.9541 | 7.4806 | 7.2878 | 6.5694 | 5.8224 | 5.0571 | 4.2633 | 0.027551 | -2.699 | -3.9663 | 13.3245 | 12.9857 | 12.6918 | 12.3551 | 11.9878 | 11.8429 | 11.3582 | 10.8286 | 10.2643 | 9.6612 | 6.2143 | 2.9439 | -1.501 | 10.6929 | 10.2469 | 9.8888 | 9.4735 | 9.0245 | 8.8786 | 8.2255 | 7.5378 | 6.8286 | 6.0959 | 2.2439 | -0.13469 | -1.2133
|  | HASLEMERE | CF |  |  |  | 9.4765 | 9.101 | 8.8327 | 8.5888 | 8.2949 | 7.9755 | 7.6459 | 7.6296 | 7.2582 | 6.8592 | 4.0847 | 1.1612 | -1.551 | 13.4061 | 13.1276 | 12.8714 | 12.6327 | 12.3408 | 12 | 11.6092 | 11.4571 | 11.0061 | 10.5255 | 7.0633 | 1.7235 | -7.2643 | 10.8367 | 10.5092 | 10.2418 | 10.0153 | 9.7235 | 9.4061 | 9.0724 | 9.1388 | 8.7745 | 8.3867 | 5.8051 | 3.2378 | 0.85204
BRAMLEY (FLEE) | FERNHURST | HASLINGBOURNE | MINIMUM HEADROOM | SU 98188 20276 | YES | 0.763 | 6.6582 | 6.4704 | 6.2857 | 6.0408 | 5.8306 | 5.5561 | 5.1847 | 4.752 | 4.7714 | 4.5184 | 3.1949 | 2.2714 | 1.6633 | 8.5918 | 8.452 | 8.3143 | 8.1276 | 7.9673 | 7.7449 | 7.4755 | 7.151 | 7.2153 | 7.0306 | 6.0092 | 4.7653 | 1.7612 | 7.2551 | 7.0714 | 6.8939 | 6.651 | 6.4459 | 6.1704 | 5.8082 | 5.3796 | 5.5102 | 5.2929 | 4.1408 | 3.352 | 2.8367
|  | HASLINGBOURNE | EE |  |  |  | 6.6582 | 6.4704 | 6.2857 | 6.0408 | 5.8306 | 5.5561 | 5.1847 | 4.752 | 4.7714 | 4.5184 | 3.1949 | 2.402 | 1.8684 | 8.5918 | 8.452 | 8.3143 | 8.1276 | 7.9673 | 7.7449 | 7.4755 | 7.151 | 7.2153 | 7.0306 | 6.0092 | 5.0061 | 3.4704 | 7.2551 | 7.0714 | 6.8939 | 6.651 | 6.4459 | 6.1704 | 5.8082 | 5.3796 | 5.5102 | 5.2929 | 4.1408 | 3.4673 | 3.0112
|  | HASLINGBOURNE | HT |  |  |  | 6.7643 | 6.6296 | 6.4684 | 6.2755 | 6.1224 | 5.9071 | 5.6459 | 5.3143 | 4.9592 | 4.5827 | 3.2898 | 2.2714 | 1.6633 | 8.6949 | 8.6133 | 8.5122 | 8.3847 | 8.2898 | 8.1449 | 8.0051 | 7.8 | 7.5806 | 7.3418 | 6.6888 | 6.1888 | 5.9163 | 7.3735 | 7.252 | 7.098 | 6.9173 | 6.7724 | 6.5684 | 6.3347 | 6.0204 | 5.6847 | 5.3286 | 4.2429 | 3.352 | 2.8367
|  | HASLINGBOURNE | HE |  |  |  | 6.7612 | 6.6316 | 6.4745 | 6.2949 | 6.151 | 5.9531 | 5.7276 | 5.4235 | 5.102 | 4.7653 | 3.5541 | 2.7765 | 2.4194 | 8.6776 | 8.5867 | 8.4735 | 8.3408 | 8.2316 | 8.0735 | 7.9235 | 7.7061 | 7.4684 | 7.2112 | 6.2469 | 5.2255 | 3.7704 | 7.3684 | 7.252 | 7.1041 | 6.9327 | 6.799 | 6.6112 | 6.4092 | 6.1204 | 5.8143 | 5.4898 | 4.4837 | 3.8173 | 3.5235
|  | HASLINGBOURNE | CF |  |  |  | 6.799 | 6.699 | 6.598 | 6.4765 | 6.3398 | 6.2378 | 6.0918 | 5.9163 | 5.7786 | 5.5857 | 4.799 | 3.8459 | 2.9827 | 8.698 | 8.6173 | 8.5347 | 8.4337 | 8.3143 | 8.2112 | 8.0653 | 7.8867 | 7.7459 | 7.5459 | 6.5235 | 4.7653 | 1.7612 | 7.4031 | 7.3041 | 7.2102 | 7.0949 | 6.9602 | 6.8653 | 6.7224 | 6.5449 | 6.4143 | 6.2235 | 5.5633 | 4.7561 | 4.001
MELKSHAM GSP | FROME BSP | HAWKERIDGE | MINIMUM HEADROOM | ST 86422 53026 | YES | 0.1 | 4.2408 | 4.1673 | 4.0847 | 3.9837 | 3.8653 | 3.7276 | 3.5633 | 3.3684 | 3.1745 | 2.998 | 2.2439 | 1.9704 | 1.8541 | 3.8469 | 3.8153 | 3.7806 | 3.7347 | 3.6878 | 3.6276 | 3.552 | 3.4378 | 3.2878 | 3.1449 | 2.549 | 2.3378 | 2.2378 | 3.9969 | 3.9418 | 3.8796 | 3.8051 | 3.7153 | 3.6122 | 3.4878 | 3.3398 | 3.1918 | 3.0071 | 2.2347 | 1.952 | 1.8367
|  | HAWKERIDGE | EE |  |  |  | 4.2408 | 4.1673 | 4.0847 | 3.9837 | 3.8653 | 3.7276 | 3.5633 | 3.3684 | 3.1745 | 2.998 | 2.2439 | 2.0296 | 2.001 | 3.8469 | 3.8153 | 3.7806 | 3.7347 | 3.6878 | 3.6276 | 3.552 | 3.4378 | 3.2878 | 3.1449 | 2.5684 | 2.4143 | 2.3888 | 3.9969 | 3.9418 | 3.8796 | 3.8051 | 3.7153 | 3.6122 | 3.4878 | 3.3398 | 3.1918 | 3.0071 | 2.2378 | 2.0255 | 1.9929
|  | HAWKERIDGE | HT |  |  |  | 4.2796 | 4.2235 | 4.1551 | 4.0714 | 3.9755 | 3.8561 | 3.7163 | 3.5418 | 3.3551 | 3.1653 | 2.3102 | 1.9704 | 1.8541 | 3.8643 | 3.8388 | 3.8102 | 3.7724 | 3.7357 | 3.6857 | 3.6224 | 3.5398 | 3.4276 | 3.3102 | 2.6245 | 2.3571 | 2.2643 | 4.0245 | 3.9816 | 3.9306 | 3.8653 | 3.7959 | 3.7031 | 3.5949 | 3.4633 | 3.3194 | 3.1755 | 2.3061 | 1.952 | 1.8367
|  | HAWKERIDGE | HE |  |  |  | 4.2847 | 4.2306 | 4.1684 | 4.0878 | 3.9918 | 3.8735 | 3.7316 | 3.5561 | 3.3633 | 3.1612 | 2.2745 | 1.9918 | 1.8663 | 3.8653 | 3.8429 | 3.8133 | 3.7776 | 3.7398 | 3.6898 | 3.6265 | 3.549 | 3.4327 | 3.2796 | 2.549 | 2.3378 | 2.2378 | 4.0296 | 3.9898 | 3.9418 | 3.8806 | 3.8102 | 3.7224 | 3.6153 | 3.4827 | 3.3367 | 3.1786 | 2.2347 | 1.9673 | 1.848
|  | HAWKERIDGE | CF |  |  |  | 4.3286 | 4.3031 | 4.2684 | 4.2286 | 4.1786 | 4.1224 | 4.0561 | 3.9663 | 3.8633 | 3.7439 | 3.0408 | 2.3745 | 1.8786 | 3.8816 | 3.8694 | 3.851 | 3.8316 | 3.8092 | 3.7867 | 3.752 | 3.7112 | 3.6653 | 3.6133 | 3.1714 | 2.6316 | 2.252 | 4.0622 | 4.0418 | 4.0163 | 3.9867 | 3.949 | 3.9092 | 3.8592 | 3.7908 | 3.7143 | 3.6245 | 3.0469 | 2.35 | 1.8541
BRAMLEY (FLEE) | COXMOOR WOOD BSP | HAWLEY | MINIMUM HEADROOM | SU 85973 57691 | YES | 1.41 | 17.148 | 16.7969 | 16.3531 | 16.1969 | 15.7694 | 15.251 | 14.3541 | 13.3531 | 12.3418 | 11.6378 | 7.2704 | 3.9214 | 2.0878 | 18.6153 | 18.2939 | 17.8735 | 17.7408 | 17.3122 | 16.848 | 16.2 | 15.4551 | 14.6898 | 14.149 | 10.8418 | 5.9929 | -5.3418 | 17.1296 | 16.7582 | 16.2735 | 16.151 | 15.6857 | 15.1857 | 14.35 | 13.4082 | 12.4592 | 11.8153 | 8.1592 | 5.3102 | 3.75
|  | HAWLEY | EE |  |  |  | 17.148 | 16.7969 | 16.3531 | 16.1969 | 15.7694 | 15.251 | 14.3541 | 13.3531 | 12.3418 | 11.6378 | 7.5745 | 4.5 | 2.2663 | 18.6153 | 18.2939 | 17.8735 | 17.7408 | 17.3122 | 16.848 | 16.2 | 15.4551 | 14.6898 | 14.149 | 10.8418 | 7.1643 | 1.2357 | 17.1296 | 16.7582 | 16.2735 | 16.151 | 15.6857 | 15.1857 | 14.35 | 13.4082 | 12.4592 | 11.8153 | 8.348 | 5.8204 | 3.898
|  | HAWLEY | HT |  |  |  | 17.3327 | 17.0296 | 16.6673 | 16.3286 | 15.9306 | 15.498 | 15.0102 | 14.1827 | 13.3214 | 12.4041 | 7.2704 | 3.9214 | 2.0878 | 18.8622 | 18.6663 | 18.4092 | 18.1776 | 17.8827 | 17.551 | 17.4347 | 16.9673 | 16.4653 | 15.9163 | 13.2286 | 11.7908 | 11.0745 | 17.3704 | 17.0776 | 16.7122 | 16.3724 | 15.9602 | 15.502 | 15.1684 | 14.401 | 13.6 | 12.7398 | 8.1592 | 5.3102 | 3.75
|  | HAWLEY | HE |  |  |  | 17.3367 | 17.0602 | 16.7235 | 16.4102 | 16.0418 | 15.6418 | 15.299 | 14.6102 | 13.8939 | 13.1643 | 8.899 | 5.85 | 4.5592 | 18.8102 | 18.5724 | 18.2673 | 17.9776 | 17.6184 | 17.2163 | 17.0429 | 16.5061 | 15.9276 | 15.3153 | 11.5633 | 7.8204 | 2.2449 | 17.3673 | 17.099 | 16.7551 | 16.4408 | 16.0582 | 15.6347 | 15.4163 | 14.7643 | 14.0806 | 13.3776 | 9.5724 | 7.0582 | 5.9551
|  | HAWLEY | CF |  |  |  | 17.4969 | 17.3337 | 17.1724 | 17.0102 | 16.8102 | 16.5888 | 16.3357 | 16.3531 | 16.0857 | 15.7827 | 13.1388 | 10.1337 | 7.3969 | 18.8837 | 18.6735 | 18.4571 | 18.2316 | 17.9439 | 17.5929 | 17.1755 | 17.0173 | 16.5551 | 16.0582 | 12.2806 | 5.9929 | -5.3418 | 17.5122 | 17.3316 | 17.1612 | 16.9857 | 16.7622 | 16.5143 | 16.2316 | 16.2939 | 16 | 15.6908 | 13.2112 | 10.5459 | 8.2816
NORTH HYDE GSP |  | HAYES | MINIMUM HEADROOM | TQ 09519 79541 | YES | 15.518 | 33.6717 | 32.586 | 31.5687 | 30.0452 | 104.733 | 103.1452 | 100.0564 | 96.5391 | 93.5758 | 90.8432 | 81.233 | 73.5228 | 68.3932 | 37.5187 | 36.8442 | 36.1513 | 35.0881 | 107.1758 | 106.0146 | 103.136 | 99.836 | 97.186 | 94.5279 | 84.9748 | 76.9809 | 63.7962 | 32.0258 | 30.9748 | 30.1074 | 28.6554 | 101.5707 | 99.9993 | 96.5962 | 92.6768 | 89.4432 | 86.5258 | 76.5901 | 68.6921 | 63.0472
|  | HAYES | EE |  |  |  | 33.6717 | 32.586 | 31.5687 | 30.0452 | 104.733 | 103.1452 | 100.0564 | 96.5391 | 93.5758 | 90.8432 | 81.6095 | 76.3819 | 72.4799 | 37.5187 | 36.8442 | 36.1513 | 35.0881 | 107.1758 | 106.0146 | 103.136 | 99.836 | 97.186 | 94.5279 | 84.9748 | 76.9809 | 64.2472 | 32.0258 | 30.9748 | 30.1074 | 28.6554 | 101.5707 | 99.9993 | 96.5962 | 92.6768 | 89.4432 | 86.5258 | 77.286 | 72.2626 | 67.5095
|  | HAYES | HT |  |  |  | 34.1197 | 33.1513 | 31.9615 | 30.6054 | 105.8962 | 104.6921 | 101.9809 | 98.9534 | 96.3136 | 93.4268 | 81.233 | 73.5228 | 68.3932 | 37.9095 | 37.3615 | 36.6115 | 35.7819 | 108.4136 | 107.7064 | 105.2452 | 102.4677 | 100.2146 | 97.6697 | 87.5952 | 81.0391 | 75.3728 | 32.5472 | 31.7166 | 30.6064 | 29.3544 | 103.0044 | 101.8626 | 98.8962 | 95.5472 | 92.6891 | 89.5166 | 76.5901 | 68.6921 | 63.0472
|  | HAYES | HE |  |  |  | 34.086 | 33.233 | 32.1442 | 30.8228 | 106.1064 | 104.8442 | 102.6656 | 100.086 | 98.2442 | 96.2299 | 87.1217 | 81.7921 | 76.635 | 37.8023 | 37.2595 | 36.5228 | 35.5911 | 108.0442 | 107.086 | 105.036 | 102.5605 | 101.0105 | 99.2442 | 89.734 | 81.635 | 68.4962 | 32.5146 | 31.7564 | 30.7697 | 29.5472 | 103.1911 | 102.0095 | 99.6809 | 96.8758 | 95.0023 | 92.9146 | 83.4074 | 78.1605 | 72.5472
|  | HAYES | CF |  |  |  | 34.4605 | 33.9432 | 33.334 | 32.4564 | 107.8034 | 107.233 | 105.9707 | 104.3391 | 102.8554 | 101.5666 | 96.0513 | 90.4687 | 83.6401 | 37.9983 | 37.5993 | 37.1319 | 36.4564 | 108.883 | 108.2136 | 106.6523 | 104.6544 | 102.8544 | 101.2738 | 94.1544 | 83.5228 | 63.7962 | 32.8554 | 32.3983 | 31.8268 | 31.0319 | 104.6095 | 104.1523 | 102.7401 | 100.8483 | 99.1513 | 97.7003 | 91.9513 | 86.9421 | 80.9483
COWLEY GSP | HEADINGTON BSP | HEADINGTON | MINIMUM HEADROOM | SP 54440 08085 | YES | 2.688 | 19.6852 | 18.4954 | 17.6709 | 17.3668 | 16.6586 | 15.928 | 13.9617 | 12.8943 | 11.8423 | 11.1556 | 8.2474 | 6.4158 | 6.1872 | 19.4066 | 18.6178 | 18.0392 | 17.7831 | 17.2423 | 16.677 | 15.4647 | 14.6617 | 13.8566 | 13.2923 | 10.3586 | 5.9668 | -4.5373 | 20.7913 | 19.7147 | 18.9545 | 18.6392 | 17.9688 | 17.276 | 15.4821 | 14.4719 | 13.477 | 12.8005 | 9.9974 | 8.3198 | 8.1137
|  | HEADINGTON | EE |  |  |  | 19.6852 | 18.4954 | 17.6709 | 17.3668 | 16.6586 | 15.928 | 13.9617 | 12.8943 | 11.8423 | 11.1556 | 8.2474 | 6.5933 | 6.7862 | 19.4066 | 18.6178 | 18.0392 | 17.7831 | 17.2423 | 16.677 | 15.4647 | 14.6617 | 13.8566 | 13.2923 | 10.3586 | 7.1382 | 2.5576 | 20.7913 | 19.7147 | 18.9545 | 18.6392 | 17.9688 | 17.276 | 15.4821 | 14.4719 | 13.477 | 12.8005 | 9.9974 | 8.4852 | 8.6535
|  | HEADINGTON | HT |  |  |  | 19.9464 | 18.5994 | 18.0637 | 17.5515 | 16.9545 | 16.3015 | 15.0015 | 14.2086 | 13.3872 | 12.5372 | 8.5107 | 6.4158 | 6.1872 | 19.6821 | 18.8627 | 18.5403 | 18.228 | 17.8566 | 17.4423 | 16.7882 | 16.3015 | 15.7943 | 15.2576 | 12.8117 | 11.6229 | 11.4188 | 21.0739 | 19.8372 | 19.33 | 18.8607 | 18.3005 | 17.6892 | 16.4658 | 15.7168 | 14.9423 | 14.1321 | 10.3137 | 8.3198 | 8.1137
|  | HEADINGTON | HE |  |  |  | 19.9443 | 18.9209 | 18.2749 | 17.7454 | 17.1535 | 16.5372 | 15.3147 | 14.6005 | 13.8637 | 13.1025 | 9.976 | 8.4576 | 8.1903 | 19.6198 | 18.9239 | 18.4709 | 18.0841 | 17.6362 | 17.1607 | 16.4229 | 15.8678 | 15.279 | 14.6545 | 11.3219 | 8.079 | 3.3474 | 21.0709 | 20.1076 | 19.5168 | 19.026 | 18.4749 | 17.8964 | 16.7392 | 16.0484 | 15.3413 | 14.6076 | 11.5637 | 10.1443 | 9.9066
|  | HEADINGTON | CF |  |  |  | 20.0964 | 19.3556 | 19.1025 | 18.8015 | 18.5372 | 18.1974 | 16.9494 | 16.9688 | 16.5178 | 16.0403 | 13.1994 | 10.7025 | 8.4729 | 19.7147 | 19.1362 | 18.8872 | 18.5882 | 18.3045 | 17.929 | 17.0454 | 16.83 | 16.3076 | 15.7423 | 11.9096 | 5.9668 | -4.5373 | 21.229 | 20.4954 | 20.2596 | 19.978 | 19.7433 | 19.4249 | 18.328 | 18.3147 | 17.8933 | 17.4484 | 14.7668 | 12.3086 | 10.1474
NURSLING GSP | VELMORE BSP | HEDGE END | MINIMUM HEADROOM | SU 49035 15685 | YES | 10.976 | 19.3816 | 10.8969 | 10.252 | 9.4939 | 8.7857 | 7.9388 | 7.4276 | 7.1633 | 6.7439 | 6.651 | 5.4827 | 4.2102 | 3.3633 | 19.3469 | 11.0765 | 10.7092 | 10.3214 | 9.9255 | 9.4653 | 9.0827 | 9.0714 | 8.7408 | 8.5745 | 7.5449 | 5.5306 | 1.3949 | 18.3316 | 9.9194 | 9.3541 | 8.7296 | 8.1112 | 7.3806 | 6.8745 | 6.8694 | 6.4551 | 6.3235 | 5.3857 | 4.3673 | 3.6908
|  | HEDGE END | EE |  |  |  | 19.3816 | 10.8969 | 10.252 | 9.4939 | 8.7857 | 7.9388 | 7.4276 | 7.2541 | 6.8143 | 6.651 | 5.7541 | 4.5714 | 3.5582 | 19.3469 | 11.0765 | 10.7092 | 10.3214 | 9.9255 | 9.4653 | 9.0827 | 9.0714 | 8.7408 | 8.5745 | 7.5449 | 6.0531 | 3.7643 | 18.3316 | 9.9194 | 9.3541 | 8.7296 | 8.1112 | 7.3806 | 6.8745 | 6.8827 | 6.4663 | 6.3235 | 5.5776 | 4.6561 | 3.8347
|  | HEDGE END | HT |  |  |  | 19.4592 | 10.9806 | 10.3663 | 9.6296 | 8.9571 | 8.1694 | 7.6867 | 7.1633 | 6.7439 | 6.7582 | 5.4827 | 4.2102 | 3.3633 | 19.4571 | 11.2163 | 10.9051 | 10.5612 | 10.2367 | 9.8847 | 9.6041 | 9.2827 | 8.9959 | 9.1429 | 8.3653 | 7.7929 | 7.4163 | 18.4316 | 10.05 | 9.5418 | 8.9602 | 8.4031 | 7.7857 | 7.352 | 6.8694 | 6.4551 | 6.5816 | 5.3857 | 4.3673 | 3.6908
|  | HEDGE END | HE |  |  |  | 19.4684 | 11.0102 | 10.4082 | 9.6918 | 9.0378 | 8.2837 | 7.8969 | 7.4816 | 7.1245 | 7.2357 | 6.3204 | 5.1684 | 4.4531 | 19.4357 | 11.2031 | 10.8796 | 10.5194 | 10.1694 | 9.7867 | 9.5173 | 9.2204 | 8.9378 | 8.9684 | 7.8245 | 6.3265 | 4.1541 | 18.4337 | 10.0735 | 9.5714 | 9.0041 | 8.4602 | 7.8724 | 7.5092 | 7.1082 | 6.7398 | 6.9561 | 6.0704 | 5.1582 | 4.6082
|  | HEDGE END | CF |  |  |  | 19.5582 | 11.1918 | 10.7061 | 10.1265 | 9.6153 | 9.0143 | 8.7878 | 8.5602 | 8.3276 | 8.1663 | 7.4204 | 6.4184 | 5.5255 | 19.4745 | 11.2663 | 10.9969 | 10.6786 | 10.3837 | 10.0296 | 9.8194 | 9.5806 | 9.3337 | 9.1122 | 7.8765 | 5.5306 | 1.3949 | 18.5082 | 10.2133 | 9.8184 | 9.3592 | 8.9357 | 8.4398 | 8.2449 | 8.0051 | 7.7602 | 7.5724 | 6.9765 | 6.1357 | 5.4184
BRAMLEY (FLEE) | READING BSP | HENLEY | MINIMUM HEADROOM | SU 76070 82422 | YES | 2.579 | 6.8333 | 6.4364 | 5.9946 | 5.3925 | 5.1017 | 4.5843 | 3.7823 | 2.8803 | 1.9772 | 1.3037 | -2.2697 | -5.3197 | -7.1146 | 12.7976 | 12.467 | 12.0997 | 11.6364 | 11.4497 | 11.0221 | 10.4486 | 9.7772 | 9.0935 | 8.6088 | 5.9109 | 2.7088 | -5.1534 | 8.0997 | 7.6894 | 7.2425 | 6.6588 | 6.4486 | 5.9374 | 5.1782 | 4.3109 | 3.4466 | 2.8384 | -0.233 | -2.8922 | -4.4044
|  | HENLEY | EE |  |  |  | 6.8333 | 6.4364 | 5.9946 | 5.3925 | 5.1017 | 4.5843 | 3.7823 | 2.8803 | 1.9772 | 1.3037 | -2.2697 | -4.7983 | -6.8208 | 12.7976 | 12.467 | 12.0997 | 11.6364 | 11.4497 | 11.0221 | 10.4486 | 9.7772 | 9.0935 | 8.6088 | 5.9109 | 3.068 | -1.1483 | 8.0997 | 7.6894 | 7.2425 | 6.6588 | 6.4486 | 5.9374 | 5.1782 | 4.3109 | 3.4466 | 2.8384 | -0.233 | -2.3871 | -4.1371
|  | HENLEY | HT |  |  |  | 7.0313 | 6.716 | 6.3843 | 5.9425 | 5.4129 | 4.9486 | 4.5231 | 3.7578 | 2.9558 | 2.1333 | -2.2677 | -5.3197 | -7.1146 | 13.0048 | 12.7752 | 12.5527 | 12.2864 | 11.9599 | 11.6486 | 11.4823 | 11.0405 | 10.5772 | 10.0905 | 7.6823 | 6.2333 | 5.5058 | 8.3292 | 8.0007 | 7.667 | 7.267 | 6.7741 | 6.3201 | 5.9956 | 5.2874 | 4.5456 | 3.7752 | -0.20341 | -2.8922 | -4.4044
|  | HENLEY | HE |  |  |  | 7.0231 | 6.7201 | 6.4027 | 5.9833 | 5.4752 | 5.0405 | 4.7303 | 4.0711 | 3.3905 | 2.6874 | -1.0789 | -3.6003 | -4.7708 | 12.9548 | 12.6976 | 12.4272 | 12.1272 | 11.7507 | 11.3905 | 11.2048 | 10.7292 | 10.2231 | 9.6894 | 6.6129 | 3.7058 | -0.15443 | 8.317 | 8.0048 | 7.6833 | 7.3048 | 6.8323 | 6.4048 | 6.1843 | 5.5711 | 4.9333 | 4.2741 | 0.86802 | -1.2687 | -2.2891
|  | HENLEY | CF |  |  |  | 7.1588 | 6.9384 | 6.7721 | 6.4517 | 6.1384 | 5.8711 | 5.5843 | 5.2272 | 5.2435 | 4.9119 | 2.5323 | -0.025857 | -2.3942 | 13.0221 | 12.7843 | 12.5976 | 12.3211 | 12.0425 | 11.7456 | 11.3986 | 10.9813 | 10.8558 | 10.4354 | 7.3966 | 2.7088 | -5.1534 | 8.4415 | 8.1966 | 8.0262 | 7.7262 | 7.4456 | 7.1772 | 6.8874 | 6.5262 | 6.5935 | 6.268 | 3.9752 | 1.7058 | -0.30545
AXMINSTER | YEOVIL BSP | HENSTRIDGE | MINIMUM HEADROOM | ST 72676 19263 | YES | 5.946 | 14.0618 | 13.5639 | 13.1935 | 12.8282 | 12.3047 | 11.2795 | 11.1224 | 10.6724 | 10.3275 | 10.0734 | 8.7397 | 7.9622 | 7.4336 | 15.3969 | 15.0592 | 14.8 | 14.5755 | 14.2408 | 13.4473 | 13.5044 | 13.1952 | 12.9299 | 12.783 | 11.9034 | 10.6993 | 7.7901 | 15.2312 | 14.772 | 14.4108 | 14.068 | 13.5833 | 12.6132 | 12.5387 | 12.0948 | 11.7346 | 11.505 | 10.3938 | 9.7285 | 9.3112
|  | HENSTRIDGE | EE |  |  |  | 14.0618 | 13.5639 | 13.1935 | 12.8282 | 12.3047 | 11.2795 | 11.1224 | 10.6724 | 10.3275 | 10.0734 | 8.7397 | 8.0275 | 7.5856 | 15.3969 | 15.0592 | 14.8 | 14.5755 | 14.2408 | 13.4473 | 13.5044 | 13.1952 | 12.9299 | 12.783 | 11.9034 | 10.9646 | 9.534 | 15.2312 | 14.772 | 14.4108 | 14.068 | 13.5833 | 12.6132 | 12.5387 | 12.0948 | 11.7346 | 11.505 | 10.3938 | 9.8071 | 9.4397
|  | HENSTRIDGE | HT |  |  |  | 14.1373 | 13.6547 | 13.3261 | 12.9965 | 12.5251 | 11.5897 | 11.1907 | 10.754 | 10.4091 | 10.3458 | 8.8305 | 7.9622 | 7.4336 | 15.5051 | 15.2031 | 15.0133 | 14.8449 | 14.5888 | 13.9228 | 13.6799 | 13.3993 | 13.1534 | 13.3003 | 12.4422 | 12.0595 | 11.8483 | 15.3445 | 14.9149 | 14.6149 | 14.3292 | 13.918 | 13.0652 | 12.6867 | 12.2622 | 11.902 | 11.9244 | 10.4785 | 9.7285 | 9.3112
|  | HENSTRIDGE | HE |  |  |  | 14.1516 | 13.6884 | 13.3445 | 13.0251 | 12.5659 | 11.6387 | 11.2754 | 10.8795 | 10.5744 | 10.5479 | 9.0663 | 8.3601 | 8.0438 | 15.502 | 15.2051 | 14.9939 | 14.8214 | 14.5571 | 13.884 | 13.6432 | 13.3636 | 13.1065 | 13.2514 | 12.1258 | 11.1748 | 9.8065 | 15.3547 | 14.9435 | 14.6333 | 14.3557 | 13.9547 | 13.1152 | 12.7683 | 12.3795 | 12.051 | 12.1061 | 10.7275 | 10.1499 | 9.8989
|  | HENSTRIDGE | CF |  |  |  | 14.2078 | 13.7945 | 13.5159 | 13.2598 | 12.8935 | 12.0418 | 11.7989 | 11.5663 | 11.3846 | 11.1989 | 10.4224 | 9.454 | 8.5683 | 15.5347 | 15.2571 | 15.0857 | 14.9439 | 14.7245 | 14.0554 | 13.8595 | 13.6932 | 13.5024 | 13.3054 | 12.4248 | 10.6993 | 7.7901 | 15.4118 | 15.0465 | 14.7996 | 14.5873 | 14.2731 | 13.4887 | 13.2561 | 13.0407 | 12.8377 | 12.6285 | 11.8795 | 11.0142 | 10.2816
BRAMLEY (FLEE) | ALTON | HERRIARD | MINIMUM HEADROOM | SU 66770 44972 | YES | 0.133 | 2.4857 | 2.4684 | 2.449 | 2.4235 | 2.402 | 2.3755 | 2.3429 | 2.3 | 2.2724 | 2.2469 | 2.1418 | 2.1061 | 2.0724 | 1.5061 | 1.4888 | 1.4684 | 1.4439 | 1.4214 | 1.3949 | 1.3622 | 1.3173 | 1.2878 | 1.2622 | 1.1092 | 0.96429 | 0.61531 | 0.97347 | 0.94184 | 0.90714 | 0.85918 | 0.82653 | 0.77143 | 0.70408 | 0.61531 | 0.56837 | 0.52449 | 0.33673 | 0.27143 | 0.20918
|  | HERRIARD | EE |  |  |  | 2.4857 | 2.4684 | 2.449 | 2.4235 | 2.402 | 2.3755 | 2.3429 | 2.3 | 2.2724 | 2.2469 | 2.1418 | 2.1122 | 2.099 | 1.5061 | 1.4888 | 1.4684 | 1.4439 | 1.4214 | 1.3949 | 1.3622 | 1.3173 | 1.2878 | 1.2622 | 1.1092 | 0.99592 | 0.83571 | 0.97347 | 0.94184 | 0.90714 | 0.85918 | 0.82653 | 0.77143 | 0.70408 | 0.61531 | 0.56837 | 0.52449 | 0.33673 | 0.27653 | 0.24388
|  | HERRIARD | HT |  |  |  | 2.499 | 2.4837 | 2.4694 | 2.449 | 2.4316 | 2.4102 | 2.3888 | 2.3561 | 2.3214 | 2.2878 | 2.1561 | 2.1061 | 2.0724 | 1.5173 | 1.502 | 1.4878 | 1.4704 | 1.4541 | 1.4347 | 1.4143 | 1.3827 | 1.3531 | 1.3214 | 1.1929 | 1.1388 | 1.102 | 1.0031 | 0.97449 | 0.95306 | 0.91939 | 0.8898 | 0.85 | 0.81224 | 0.75 | 0.68878 | 0.61939 | 0.36837 | 0.27143 | 0.20918
|  | HERRIARD | HE |  |  |  | 2.498 | 2.4827 | 2.4684 | 2.451 | 2.4306 | 2.4112 | 2.3898 | 2.3561 | 2.3235 | 2.2878 | 2.1449 | 2.1102 | 2.0867 | 1.5163 | 1.501 | 1.4837 | 1.4653 | 1.4469 | 1.4235 | 1.4031 | 1.3673 | 1.3347 | 1.3 | 1.1184 | 1.0041 | 0.84184 | 1 | 0.97449 | 0.95204 | 0.92041 | 0.89184 | 0.85408 | 0.81837 | 0.7602 | 0.70204 | 0.63265 | 0.37143 | 0.3102 | 0.28163
|  | HERRIARD | CF |  |  |  | 2.5031 | 2.4939 | 2.4806 | 2.4704 | 2.4571 | 2.4449 | 2.4276 | 2.4071 | 2.3949 | 2.3714 | 2.2602 | 2.1735 | 2.1092 | 1.5204 | 1.5092 | 1.4908 | 1.4786 | 1.4602 | 1.4429 | 1.4214 | 1.3959 | 1.3765 | 1.351 | 1.1867 | 0.96429 | 0.61531 | 1.0041 | 0.98776 | 0.96122 | 0.94592 | 0.91633 | 0.89286 | 0.86122 | 0.82041 | 0.80102 | 0.7551 | 0.54898 | 0.4051 | 0.30918
COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE | MINIMUM HEADROOM | SU 84733 92200 | YES | 3.138 | 7.0443 | 6.7351 | 6.3331 | 5.8473 | 5.3024 | 4.8504 | 4.1147 | 3.23 | 2.3759 | 1.629 | -1.7078 | -3.9098 | -4.9527 | 10.5024 | 10.3351 | 10.1453 | 9.9178 | 9.6555 | 9.3627 | 8.8667 | 8.232 | 7.6167 | 7.0902 | 4.8535 | 3.6973 | -1.5486 | 7.6759 | 7.4239 | 7.0535 | 6.5912 | 6.0698 | 5.6402 | 4.9443 | 4.1055 | 3.2912 | 2.5882 | -0.42408 | -2.4292 | -3.3945
|  | HIGH WYCOMBE | EE |  |  |  | 7.0443 | 6.7351 | 6.3331 | 5.8473 | 5.3024 | 4.8504 | 4.1147 | 3.23 | 2.3759 | 1.629 | -1.5843 | -3.1435 | -4.0527 | 10.5024 | 10.3351 | 10.1453 | 9.9178 | 9.6555 | 9.3627 | 8.8667 | 8.232 | 7.6167 | 7.0902 | 5.1341 | 4.5014 | 1.5831 | 7.6759 | 7.4239 | 7.0535 | 6.5912 | 6.0698 | 5.6402 | 4.9443 | 4.1055 | 3.2912 | 2.5882 | -0.21898 | -1.6118 | -2.4129
|  | HIGH WYCOMBE | HT |  |  |  | 7.2535 | 7.0157 | 6.7494 | 6.382 | 5.9718 | 5.4912 | 4.8688 | 4.2443 | 3.4769 | 2.681 | -1.4629 | -3.6833 | -4.7935 | 10.6178 | 10.5024 | 10.3729 | 10.2137 | 10.0504 | 9.8463 | 9.4994 | 9.1065 | 8.5759 | 8.0229 | 5.5065 | 4.2892 | 3.6871 | 7.8065 | 7.6443 | 7.4453 | 7.1106 | 6.7208 | 6.2627 | 5.6729 | 5.0902 | 4.3616 | 3.6065 | -0.096531 | -2.1312 | -3.1404
|  | HIGH WYCOMBE | HE |  |  |  | 7.2392 | 7.0055 | 6.731 | 6.3565 | 5.929 | 5.429 | 4.7892 | 3.9973 | 3.3086 | 2.4463 | -1.7078 | -3.9098 | -4.9527 | 10.6035 | 10.478 | 10.3331 | 10.1637 | 9.978 | 9.7514 | 9.378 | 8.8106 | 8.3198 | 7.6943 | 4.8535 | 3.6973 | 2.0627 | 7.8004 | 7.6443 | 7.429 | 7.0831 | 6.678 | 6.1973 | 5.5892 | 4.8361 | 4.1841 | 3.3667 | -0.42408 | -2.4292 | -3.3945
|  | HIGH WYCOMBE | CF |  |  |  | 7.4218 | 7.2984 | 7.1535 | 6.9759 | 6.7718 | 6.5453 | 6.2524 | 5.8545 | 5.4004 | 5.03 | 1.9922 | -0.88531 | -3.3282 | 10.682 | 10.6065 | 10.5157 | 10.4065 | 10.28 | 10.1453 | 9.9861 | 9.779 | 9.5412 | 9.3912 | 7.1922 | 4.632 | -1.5486 | 7.9086 | 7.829 | 7.731 | 7.6127 | 7.4606 | 7.2565 | 6.9759 | 6.5933 | 6.1555 | 5.8055 | 2.9014 | 0.17592 | -1.9231
COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE TOWN | MINIMUM HEADROOM | SU 86304 92972 | YES | 4.811 | 35.6985 | 35.4271 | 35.1168 | 34.7475 | 34.3342 | 33.8852 | 33.4975 | 32.7577 | 32.0199 | 31.4026 | 28.1587 | 25.3679 | 23.7975 | 37.0883 | 36.9332 | 36.7464 | 36.476 | 36.1546 | 35.7546 | 35.4873 | 34.9189 | 34.3168 | 33.8077 | 30.9434 | 26.7842 | 17.475 | 34.5964 | 34.3424 | 34.0495 | 33.6995 | 33.3066 | 32.8811 | 32.5403 | 31.8546 | 31.173 | 30.6128 | 27.723 | 25.3383 | 23.9811
|  | HIGH WYCOMBE TOWN | EE |  |  |  | 35.6985 | 35.4271 | 35.1168 | 34.7475 | 34.3342 | 33.8852 | 33.4975 | 32.7577 | 32.0199 | 31.4026 | 28.1587 | 25.8117 | 23.9771 | 37.0883 | 36.9332 | 36.7464 | 36.476 | 36.1546 | 35.7546 | 35.4873 | 34.9189 | 34.3168 | 33.8077 | 30.9434 | 27.7883 | 22.8975 | 34.5964 | 34.3424 | 34.0495 | 33.6995 | 33.3066 | 32.8811 | 32.5403 | 31.8546 | 31.173 | 30.6128 | 27.723 | 25.6883 | 24.0924
|  | HIGH WYCOMBE TOWN | HT |  |  |  | 35.8546 | 35.625 | 35.376 | 35.0852 | 34.7648 | 34.4475 | 33.8311 | 33.1454 | 32.7128 | 32.0281 | 28.1771 | 25.3679 | 23.7975 | 37.2117 | 37.1148 | 37.0026 | 36.8638 | 36.7107 | 36.5342 | 36.2373 | 35.8811 | 35.6842 | 35.3046 | 33.2056 | 31.8373 | 31.1699 | 34.7515 | 34.5454 | 34.3179 | 34.0505 | 33.7556 | 33.4617 | 32.9026 | 32.2781 | 31.9107 | 31.2903 | 27.8342 | 25.3383 | 23.9811
|  | HIGH WYCOMBE TOWN | HE |  |  |  | 35.8464 | 35.6199 | 35.3852 | 35.1138 | 34.8138 | 34.5179 | 33.9852 | 33.3801 | 32.9546 | 32.1893 | 28.5862 | 26.8077 | 25.9556 | 37.1699 | 37.0322 | 36.8832 | 36.6924 | 36.4464 | 36.2015 | 35.8464 | 35.3913 | 35.1168 | 34.624 | 31.6362 | 28.4342 | 23.9679 | 34.7424 | 34.5332 | 34.3189 | 34.0638 | 33.7801 | 33.5046 | 33.0158 | 32.4597 | 32.1587 | 31.6056 | 28.6648 | 26.6617 | 25.8975
|  | HIGH WYCOMBE TOWN | CF |  |  |  | 35.9893 | 35.8709 | 35.7301 | 35.5985 | 35.423 | 35.2301 | 35.0475 | 34.7842 | 34.4862 | 34.0913 | 31.7138 | 28.9964 | 26.824 | 37.2556 | 37.1638 | 37.0505 | 36.9036 | 36.7056 | 36.4658 | 36.2168 | 35.8526 | 35.4383 | 34.9944 | 32.0964 | 26.7842 | 17.475 | 34.874 | 34.7628 | 34.6281 | 34.5056 | 34.3383 | 34.1546 | 33.9842 | 33.7383 | 33.4597 | 33.1679 | 31.5903 | 29.0209 | 26.9913
IVER 66KV |  | HILLINGDON | MINIMUM HEADROOM | TQ 07470 82827 | YES | 2.914 | 8.8381 | 7.5371 | 6.23 | 4.8044 | 3.1902 | 1.43 | -1.2772 | -4.3425 | -7.2302 | -9.4649 | -19.02 | -26.7211 | -30.7068 | 16.8065 | 15.9891 | 14.9728 | 13.8861 | 12.6544 | 11.2861 | 9.1432 | 6.6667 | 4.334 | 2.5259 | -5.6078 | -13.2986 | -32.4731 | 9.8932 | 8.8555 | 7.6065 | 6.2596 | 4.7534 | 3.1065 | 0.44833 | -2.5996 | -5.4374 | -7.5588 | -16.0996 | -23.0547 | -26.6496
|  | HILLINGDON | EE |  |  |  | 8.8381 | 7.5371 | 6.23 | 4.8044 | 3.1902 | 1.43 | -1.2772 | -4.3425 | -7.2302 | -9.4649 | -19.02 | -25.5017 | -29.4435 | 16.8065 | 15.9891 | 14.9728 | 13.8861 | 12.6544 | 11.2861 | 9.1432 | 6.6667 | 4.334 | 2.5259 | -5.6078 | -13.2986 | -24.0966 | 9.8932 | 8.8555 | 7.6065 | 6.2596 | 4.7534 | 3.1065 | 0.44833 | -2.5996 | -5.4374 | -7.5588 | -16.0996 | -21.7415 | -25.3425
|  | HILLINGDON | HT |  |  |  | 9.4412 | 7.9606 | 7.1708 | 6.0942 | 4.8922 | 3.6228 | 1.3616 | -1.1231 | -3.5915 | -6.1813 | -18.6874 | -26.7211 | -30.7068 | 17.4514 | 16.5953 | 16.181 | 15.5177 | 14.7565 | 13.9381 | 12.3534 | 10.5442 | 8.8402 | 7.0106 | -1.0211 | -5.718 | -8.1251 | 10.6238 | 9.3698 | 8.7565 | 7.7861 | 6.6912 | 5.5044 | 3.3024 | 0.83098 | -1.5486 | -4.0741 | -15.8119 | -23.0547 | -26.6496
|  | HILLINGDON | HE |  |  |  | 9.3851 | 7.984 | 7.1565 | 6.0983 | 4.93 | 3.6279 | 1.684 | -0.54657 | -2.67 | -4.8904 | -15.7435 | -22.8068 | -26.0527 | 17.2973 | 16.3942 | 15.8034 | 15.0085 | 14.1044 | 13.0718 | 11.5055 | 9.6585 | 7.9963 | 6.2116 | -3.4129 | -11.8088 | -22.3313 | 10.5596 | 9.3677 | 8.7249 | 7.7698 | 6.7065 | 5.484 | 3.5932 | 1.3881 | -0.61902 | -2.7353 | -12.8751 | -19.1425 | -22.1149
|  | HILLINGDON | CF |  |  |  | 9.8442 | 8.8371 | 8.1891 | 7.7565 | 7.0667 | 6.3208 | 5.4289 | 4.2687 | 3.083 | 1.9238 | -5.2996 | -12.6374 | -19.0221 | 17.5473 | 16.8147 | 16.2106 | 15.7861 | 15.1004 | 14.3044 | 13.1718 | 11.784 | 10.3718 | 8.9687 | 0.24935 | -12.169 | -32.4731 | 10.9524 | 10.081 | 9.434 | 9.131 | 8.4728 | 7.7555 | 6.8136 | 5.6116 | 4.4024 | 3.232 | -3.5649 | -10.0415 | -15.4231
LOVEDEAN GSP | WYMERING BSP | HILSEA | MINIMUM HEADROOM | SU 66394 03806 | YES | 0.618 | 11.0131 | 10.9253 | 10.8243 | 10.6488 | 10.4559 | 10.2345 | 9.9763 | 9.662 | 9.359 | 9.1029 | 8.0814 | 7.66 | 7.4212 | 12.1212 | 12.0702 | 12.0131 | 11.9406 | 11.8641 | 11.7763 | 11.6733 | 11.5437 | 11.3182 | 11.1263 | 10.3498 | 10.0355 | 9.8427 | 9.9386 | 9.8192 | 9.6784 | 9.511 | 9.3243 | 9.111 | 8.8661 | 8.5631 | 8.2743 | 8.0273 | 7.0355 | 6.6243 | 6.3927
|  | HILSEA | EE |  |  |  | 11.0131 | 10.9253 | 10.8243 | 10.6488 | 10.4559 | 10.2345 | 9.9763 | 9.662 | 9.359 | 9.1029 | 8.1396 | 7.9049 | 7.8814 | 12.1212 | 12.0702 | 12.0131 | 11.9406 | 11.8641 | 11.7763 | 11.6733 | 11.5437 | 11.3182 | 11.1263 | 10.4161 | 10.261 | 10.2478 | 9.9386 | 9.8192 | 9.6784 | 9.511 | 9.3243 | 9.111 | 8.8661 | 8.5631 | 8.2743 | 8.0273 | 7.111 | 6.8927 | 6.8712
|  | HILSEA | HT |  |  |  | 11.0733 | 11.0049 | 10.9243 | 10.8304 | 10.708 | 10.5314 | 10.3273 | 10.0824 | 9.8182 | 9.5437 | 8.309 | 7.81 | 7.6029 | 12.1549 | 12.1222 | 12.0804 | 12.0335 | 11.9794 | 11.911 | 11.8376 | 11.7478 | 11.6478 | 11.5212 | 10.5988 | 10.2304 | 10.0682 | 10.0161 | 9.9396 | 9.8314 | 9.71 | 9.5651 | 9.3947 | 9.2008 | 8.9651 | 8.71 | 8.4447 | 7.259 | 6.7865 | 6.5906
|  | HILSEA | HE |  |  |  | 11.0712 | 11.0029 | 10.9192 | 10.8263 | 10.6763 | 10.4855 | 10.2682 | 9.9998 | 9.709 | 9.4039 | 8.0814 | 7.66 | 7.4212 | 12.1549 | 12.1151 | 12.0682 | 12.0161 | 11.9529 | 11.8784 | 11.7947 | 11.6967 | 11.5855 | 11.3631 | 10.3498 | 10.0355 | 9.8427 | 10.0161 | 9.9304 | 9.8171 | 9.6886 | 9.5345 | 9.3559 | 9.1457 | 8.8876 | 8.6059 | 8.311 | 7.0355 | 6.6243 | 6.3927
|  | HILSEA | CF |  |  |  | 11.1314 | 11.0927 | 11.0478 | 10.9957 | 10.9335 | 10.861 | 10.7845 | 10.6365 | 10.4641 | 10.2824 | 9.1947 | 8.262 | 7.6427 | 12.1865 | 12.1631 | 12.1355 | 12.1049 | 12.0651 | 12.0222 | 11.9794 | 11.9202 | 11.8529 | 11.7814 | 11.2008 | 10.4957 | 10.0304 | 10.06 | 10.0314 | 9.9916 | 9.9243 | 9.8386 | 9.7437 | 9.6406 | 9.4978 | 9.3304 | 9.1569 | 8.1059 | 7.2018 | 6.608
MANNINGTON GSP | ARNEWOOD | HINCHESLEA | MINIMUM HEADROOM | SU 27805 00447 | YES | 0.282 | 7.7719 | 7.6413 | 7.4709 | 7.3026 | 7.0791 | 6.8403 | 6.4617 | 6.4577 | 6.1097 | 5.7679 | 4.4546 | 3.2821 | 2.5995 | 8.6643 | 8.55 | 8.3878 | 8.2551 | 8.0653 | 7.8653 | 7.5898 | 7.6898 | 7.4449 | 7.3031 | 6.5449 | 5.5061 | 2.8653 | 7.5459 | 7.4102 | 7.2224 | 7.0633 | 6.8459 | 6.6112 | 6.2592 | 6.3041 | 5.9837 | 5.699 | 4.6418 | 3.6806 | 3.1316
|  | HINCHESLEA | EE |  |  |  | 7.7719 | 7.6413 | 7.4709 | 7.3026 | 7.0791 | 6.8403 | 6.4617 | 6.4577 | 6.1097 | 5.8821 | 4.5801 | 3.5128 | 2.7138 | 8.6643 | 8.55 | 8.3878 | 8.2551 | 8.0653 | 7.8653 | 7.5898 | 7.6898 | 7.4449 | 7.3031 | 6.5449 | 5.5184 | 4.0765 | 7.5459 | 7.4102 | 7.2224 | 7.0633 | 6.8459 | 6.6112 | 6.2592 | 6.3041 | 5.9837 | 5.7898 | 4.7296 | 3.8827 | 3.2316
|  | HINCHESLEA | HT |  |  |  | 7.8434 | 7.7311 | 7.5954 | 7.4791 | 7.3291 | 7.1648 | 6.8791 | 6.524 | 6.1546 | 5.7679 | 4.4546 | 3.2821 | 2.5995 | 8.7592 | 8.6786 | 8.5755 | 8.4939 | 8.3735 | 8.2367 | 8.0918 | 7.8724 | 7.6378 | 7.4 | 6.9204 | 6.4684 | 6.2173 | 7.6429 | 7.5327 | 7.3969 | 7.2837 | 7.1235 | 6.949 | 6.7092 | 6.3857 | 6.0469 | 5.699 | 4.6418 | 3.6806 | 3.1316
|  | HINCHESLEA | HE |  |  |  | 7.8485 | 7.7454 | 7.624 | 7.5168 | 7.377 | 7.223 | 7.0066 | 6.7107 | 6.4056 | 6.0862 | 5.0321 | 3.9811 | 3.4495 | 8.7459 | 8.6612 | 8.552 | 8.4643 | 8.3316 | 8.1878 | 8.052 | 7.8357 | 7.6031 | 7.3602 | 6.7459 | 5.7061 | 4.3622 | 7.6449 | 7.5439 | 7.4153 | 7.3112 | 7.1622 | 6.9969 | 6.8112 | 6.5398 | 6.2531 | 5.9561 | 5.1133 | 4.2918 | 3.8653
|  | HINCHESLEA | CF |  |  |  | 7.9036 | 7.8444 | 7.7689 | 7.6872 | 7.627 | 7.5362 | 7.4117 | 7.3056 | 7.1505 | 6.9872 | 6.3587 | 5.3893 | 4.4281 | 8.7776 | 8.7133 | 8.6235 | 8.5255 | 8.4571 | 8.3439 | 8.2112 | 8.101 | 7.9337 | 7.7592 | 7.0786 | 5.5061 | 2.8653 | 7.6939 | 7.6286 | 7.5398 | 7.4459 | 7.3827 | 7.2755 | 7.1541 | 7.0582 | 6.9041 | 6.7429 | 6.199 | 5.3806 | 4.6082
BRAMLEY (FLEE) | ALDERSHOT BSP | HINDHEAD | MINIMUM HEADROOM | SU 88631 36479 | YES | 1.969 | 9.5765 | 9.1286 | 8.802 | 8.3633 | 8.2622 | 7.7776 | 7.1327 | 6.3735 | 5.6643 | 5.1776 | 2.3755 | 0.1602 | -1.1245 | 12.9765 | 12.6531 | 12.3755 | 12.0214 | 12 | 11.6367 | 11.1867 | 10.6408 | 10.1255 | 9.8 | 7.9704 | 5.599 | -0.31122 | 10.4704 | 10.0561 | 9.7429 | 9.3153 | 9.2429 | 8.7786 | 8.1663 | 7.4531 | 6.7898 | 6.3408 | 3.9031 | 1.9398 | 0.86735
|  | HINDHEAD | EE |  |  |  | 9.5765 | 9.1286 | 8.802 | 8.3633 | 8.2622 | 7.7776 | 7.1327 | 6.3735 | 5.6643 | 5.1776 | 2.5235 | 0.60816 | -0.86122 | 12.9765 | 12.6531 | 12.3755 | 12.0214 | 12 | 11.6367 | 11.1867 | 10.6408 | 10.1255 | 9.8 | 7.9704 | 5.8765 | 2.7357 | 10.4704 | 10.0561 | 9.7429 | 9.3153 | 9.2429 | 8.7786 | 8.1663 | 7.4531 | 6.7898 | 6.3408 | 4.0153 | 2.3418 | 1.099
|  | HINDHEAD | HT |  |  |  | 9.7459 | 9.3582 | 9.1051 | 8.7347 | 8.3776 | 7.9 | 7.2918 | 6.9827 | 6.349 | 5.6949 | 2.3755 | 0.1602 | -1.1245 | 13.1469 | 12.9143 | 12.748 | 12.501 | 12.2786 | 11.9663 | 11.6051 | 11.5745 | 11.2133 | 10.8327 | 9.1041 | 8.1806 | 7.6561 | 10.6408 | 10.2878 | 10.05 | 9.7041 | 9.3653 | 8.9133 | 8.3408 | 8.0898 | 7.5092 | 6.9041 | 3.9031 | 1.9398 | 0.86735
|  | HINDHEAD | HE |  |  |  | 9.7449 | 9.3878 | 9.1469 | 8.8286 | 8.5112 | 8.0755 | 7.5367 | 7.3286 | 6.8041 | 6.2684 | 3.399 | 1.5347 | 0.64082 | 13.1184 | 12.8745 | 12.6776 | 12.4265 | 12.1837 | 11.8551 | 11.4643 | 11.4153 | 11.0367 | 10.6378 | 8.4327 | 6.3316 | 3.4327 | 10.6367 | 10.3122 | 10.0857 | 9.7847 | 9.4878 | 9.0735 | 8.5602 | 8.3929 | 7.9051 | 7.4041 | 4.8143 | 3.1878 | 2.4459
|  | HINDHEAD | CF |  |  |  | 9.8551 | 9.5837 | 9.4306 | 9.2429 | 9.0888 | 8.8816 | 8.649 | 8.3031 | 8.3735 | 8.0857 | 6.1245 | 4.1888 | 2.3133 | 13.1786 | 12.9704 | 12.8173 | 12.6276 | 12.4571 | 12.2306 | 11.9571 | 11.5837 | 11.6051 | 11.2796 | 9.0337 | 5.599 | -0.31122 | 10.7378 | 10.4929 | 10.349 | 10.1663 | 10.0204 | 9.8173 | 9.5929 | 9.248 | 9.3459 | 9.0714 | 7.2122 | 5.4612 | 3.8449
MANNINGTON GSP | MANNINGTON BSP | HINTON MARTELL | MINIMUM HEADROOM | SU 00702 06030 | YES | 0.436 | 6.3604 | 6.3043 | 6.2502 | 6.1747 | 6.1012 | 6.0176 | 5.9533 | 5.8349 | 5.7176 | 5.6676 | 5.4278 | 5.338 | 5.2563 | 6.873 | 6.8311 | 6.7944 | 6.7413 | 6.6862 | 6.625 | 6.5801 | 6.4923 | 6.4077 | 6.3679 | 6.1648 | 5.8077 | 5.0872 | 6.5778 | 6.5267 | 6.4757 | 6.4022 | 6.3298 | 6.2492 | 6.1869 | 6.0747 | 5.9594 | 5.9114 | 5.6869 | 5.6043 | 5.5308
|  | HINTON MARTELL | EE |  |  |  | 6.3604 | 6.3043 | 6.2502 | 6.1747 | 6.1012 | 6.0176 | 5.9533 | 5.8349 | 5.7176 | 5.6676 | 5.4278 | 5.338 | 5.292 | 6.873 | 6.8311 | 6.7944 | 6.7413 | 6.6862 | 6.625 | 6.5801 | 6.4923 | 6.4077 | 6.3679 | 6.1648 | 5.9587 | 5.6128 | 6.5778 | 6.5267 | 6.4757 | 6.4022 | 6.3298 | 6.2492 | 6.1869 | 6.0747 | 5.9594 | 5.9114 | 5.6869 | 5.6043 | 5.5635
|  | HINTON MARTELL | HT |  |  |  | 6.3941 | 6.3543 | 6.2982 | 6.2553 | 6.192 | 6.1553 | 6.0859 | 5.9982 | 5.9053 | 5.8543 | 5.4808 | 5.3512 | 5.2563 | 6.9036 | 6.8801 | 6.8454 | 6.8168 | 6.777 | 6.7566 | 6.7138 | 6.6556 | 6.5985 | 6.5679 | 6.3383 | 6.2699 | 6.2209 | 6.6114 | 6.5757 | 6.5216 | 6.4818 | 6.4196 | 6.3869 | 6.3176 | 6.2359 | 6.1451 | 6.0941 | 5.738 | 5.6165 | 5.5308
|  | HINTON MARTELL | HE |  |  |  | 6.3931 | 6.3533 | 6.2982 | 6.2553 | 6.1931 | 6.1584 | 6.089 | 6.0012 | 5.9104 | 5.8604 | 5.4492 | 5.3604 | 5.3155 | 6.8995 | 6.8709 | 6.8301 | 6.8005 | 6.7546 | 6.7301 | 6.6801 | 6.6168 | 6.5495 | 6.5117 | 6.1821 | 5.973 | 5.6291 | 6.6104 | 6.5747 | 6.5206 | 6.4808 | 6.4196 | 6.39 | 6.3216 | 6.238 | 6.1492 | 6.1022 | 5.7063 | 5.6298 | 5.589
|  | HINTON MARTELL | CF |  |  |  | 6.4002 | 6.3584 | 6.3237 | 6.2869 | 6.241 | 6.191 | 6.1645 | 6.1104 | 6.0471 | 5.9818 | 5.6808 | 5.4849 | 5.3543 | 6.9056 | 6.873 | 6.8464 | 6.8179 | 6.7842 | 6.7434 | 6.7158 | 6.6648 | 6.6117 | 6.5515 | 6.226 | 5.8077 | 5.0872 | 6.6176 | 6.5818 | 6.5471 | 6.5135 | 6.4696 | 6.4186 | 6.3941 | 6.342 | 6.2808 | 6.2176 | 5.9247 | 5.74 | 5.6165
BRAMLEY (FLEE) | COXMOOR WOOD BSP | HITCHES LANE | MINIMUM HEADROOM | SU 79461 54769 | YES | 9.263 | -10.25 | -10.9868 | -11.8 | -12.5776 | -13.5429 | -14.6164 | -15.9806 | -17.6347 | -19.2388 | -20.7092 | -28.0092 | -31.7112 | -33.9868 | -4.1194 | -4.6959 | -5.3704 | -5.7837 | -6.4847 | -7.2561 | -8.2572 | -9.4378 | -10.6194 | -11.5653 | -16.347 | -20.7786 | -31.3439 | -8.9827 | -9.6847 | -10.5051 | -10.998 | -11.8102 | -12.7225 | -14.0194 | -15.5276 | -17.0704 | -18.2521 | -24.7398 | -28.7408 | -31.297
|  | HITCHES LANE | EE |  |  |  | -10.25 | -10.9868 | -11.8 | -12.5776 | -13.5429 | -14.6164 | -15.9806 | -17.6347 | -19.2388 | -20.7092 | -26.8735 | -30.7164 | -33.8623 | -4.1194 | -4.6959 | -5.3704 | -5.7837 | -6.4847 | -7.2561 | -8.2572 | -9.4378 | -10.6194 | -11.5653 | -16.347 | -20.7786 | -26.5337 | -8.9827 | -9.6847 | -10.5051 | -10.998 | -11.8102 | -12.7225 | -14.0194 | -15.5276 | -17.0704 | -18.2521 | -24.2061 | -28.3602 | -31.2429
|  | HITCHES LANE | HT |  |  |  | -9.7072 | -10.2684 | -10.8725 | -11.5766 | -12.3408 | -13.0735 | -14.2 | -15.548 | -16.9868 | -18.5102 | -26.0817 | -31.2041 | -33.9868 | -3.7337 | -4.1408 | -4.5633 | -5.0684 | -5.5888 | -5.8643 | -6.5919 | -7.4327 | -8.3347 | -9.2776 | -13.7878 | -16.4857 | -17.8704 | -8.6082 | -9.2051 | -9.8153 | -10.5286 | -11.2419 | -11.6766 | -12.8255 | -14.1082 | -15.4561 | -16.8572 | -24.0174 | -28.7408 | -31.297
|  | HITCHES LANE | HE |  |  |  | -9.7929 | -10.398 | -11.0806 | -11.8735 | -12.7357 | -13.6051 | -14.8561 | -16.401 | -18.0582 | -19.7357 | -28.0092 | -31.7112 | -32.8041 | -3.8194 | -4.2776 | -4.7725 | -5.35 | -5.948 | -6.3123 | -7.1 | -8.0347 | -9.0408 | -10.0827 | -15.75 | -20.2041 | -25.247 | -8.6347 | -9.2174 | -9.8215 | -10.5286 | -11.2347 | -11.6704 | -12.6939 | -13.8776 | -15.2612 | -16.8643 | -24.7398 | -28.197 | -29.1919
|  | HITCHES LANE | CF |  |  |  | -9.3796 | -9.7143 | -10.0898 | -10.5082 | -10.95 | -11.4551 | -11.8827 | -12.6143 | -13.4439 | -14.3347 | -20.1306 | -25.8827 | -30.7715 | -3.6378 | -3.9817 | -4.3725 | -4.7602 | -5.1806 | -5.6674 | -5.9194 | -6.5337 | -7.2102 | -7.9337 | -13.0429 | -20.2561 | -31.3439 | -8.351 | -8.7153 | -9.1184 | -9.5041 | -9.9072 | -10.3796 | -10.4684 | -10.9745 | -11.5582 | -12.1919 | -17.2837 | -22.7347 | -27.3419
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | HOEFORD | MINIMUM HEADROOM | SU 57855 04433 | YES | 0.908 | 5.6939 | 5.4163 | 5.0704 | 4.8408 | 4.4439 | 34.65 | 33.948 | 33.1714 | 32.4041 | 31.6071 | 27.5684 | 24.9398 | 23.4031 | 7.9286 | 7.6908 | 7.3908 | 7.1082 | 6.7122 | 35.5576 | 35.0137 | 34.3545 | 33.6535 | 33.0984 | 29.8586 | 24.9382 | 14.3392 | 5.8571 | 5.4959 | 5.0582 | 4.6602 | 4.1051 | 33.2916 | 32.5427 | 31.6508 | 30.7906 | 30.0784 | 26.5998 | 24.4314 | 23.4651
|  | HOEFORD | EE |  |  |  | 5.6939 | 5.4163 | 5.0704 | 4.8408 | 4.4439 | 34.65 | 33.948 | 33.1714 | 32.4041 | 31.6071 | 27.9316 | 25.4908 | 23.4969 | 7.9286 | 7.6908 | 7.3908 | 7.1082 | 6.7122 | 35.5576 | 35.0137 | 34.3545 | 33.6535 | 33.0984 | 29.8586 | 26.2463 | 20.7637 | 5.8571 | 5.4959 | 5.0582 | 4.6602 | 4.1051 | 33.2916 | 32.5427 | 31.6508 | 30.7906 | 30.0784 | 27.2702 | 25.4712 | 23.7529
|  | HOEFORD | HT |  |  |  | 5.8653 | 5.6367 | 5.3714 | 5.0776 | 4.7612 | 35.0061 | 34.5592 | 33.8878 | 33.198 | 32.4837 | 28.1184 | 25.1143 | 23.4031 | 8.149 | 7.999 | 7.8133 | 7.5776 | 7.3286 | 36.3055 | 36.031 | 35.5555 | 35.0545 | 34.5178 | 31.8127 | 30.4739 | 29.8371 | 6.1449 | 5.898 | 5.5949 | 5.2286 | 4.8357 | 34.1396 | 33.6794 | 32.9927 | 32.2671 | 31.5049 | 27.6345 | 25.2263 | 23.7549
|  | HOEFORD | HE |  |  |  | 5.85 | 5.6194 | 5.3439 | 5.0388 | 4.6806 | 34.9082 | 34.5112 | 33.8806 | 33.2224 | 32.4112 | 27.5684 | 24.9398 | 23.8837 | 8.1031 | 7.9184 | 7.6857 | 7.401 | 7.0551 | 35.9667 | 35.5912 | 35.0096 | 34.3831 | 33.7259 | 30.2331 | 26.4463 | 21.2412 | 6.0908 | 5.8102 | 5.4653 | 5.048 | 4.5622 | 33.7937 | 33.2641 | 32.4763 | 31.6365 | 30.758 | 26.5998 | 24.4314 | 23.4651
|  | HOEFORD | CF |  |  |  | 6.0051 | 5.8755 | 5.7398 | 5.551 | 5.3612 | 35.7316 | 35.5153 | 35.4184 | 35.1439 | 34.8531 | 32.0694 | 28.8 | 26.1469 | 8.2429 | 8.1286 | 7.999 | 7.7602 | 7.4745 | 36.3892 | 35.9963 | 35.782 | 35.3157 | 34.8198 | 31.0953 | 24.9382 | 14.3392 | 6.3102 | 6.1571 | 5.9816 | 5.7469 | 5.4735 | 34.9273 | 34.6233 | 34.3396 | 33.9039 | 33.4355 | 30.3916 | 27.5335 | 25.4927
MANNINGTON GSP | LYTCHETT | HOLES BAY | MINIMUM HEADROOM | SZ 00725 91955 | YES | 1.903 | 5.3392 | 5.18 | 5.0167 | 4.8167 | 4.6065 | 4.4157 | 4.028 | 3.5545 | 3.0953 | 2.7157 | 0.95551 | -0.09551 | -0.58327 | 5.5549 | 5.4294 | 5.2916 | 5.1314 | 4.959 | 4.8059 | 4.5784 | 4.3141 | 3.9886 | 3.66 | 2.1865 | 1.46 | -1.2992 | 4.0922 | 3.9514 | 3.8065 | 3.6249 | 3.43 | 3.2535 | 2.881 | 2.429 | 1.9912 | 1.6249 | -0.074082 | -1.2547 | -1.8292
|  | HOLES BAY | EE |  |  |  | 5.3392 | 5.18 | 5.0167 | 4.8167 | 4.6065 | 4.4157 | 4.028 | 3.5545 | 3.0953 | 2.7157 | 1.3586 | 0.59735 | -0.01898 | 5.5549 | 5.4294 | 5.2916 | 5.1314 | 4.959 | 4.8059 | 4.5784 | 4.3141 | 3.9886 | 3.66 | 2.5243 | 1.8018 | 0.4498 | 4.0922 | 3.9514 | 3.8065 | 3.6249 | 3.43 | 3.2535 | 2.881 | 2.429 | 1.9912 | 1.6249 | 0.29327 | -0.32714 | -0.70571
|  | HOLES BAY | HT |  |  |  | 5.4106 | 5.2739 | 5.1269 | 4.9596 | 4.7892 | 4.6269 | 4.3218 | 3.982 | 3.6535 | 3.2933 | 1.5014 | 0.39531 | -0.2149 | 5.6222 | 5.5345 | 5.4396 | 5.3294 | 5.2212 | 5.1182 | 4.9569 | 4.7671 | 4.5886 | 4.3794 | 2.8569 | 2.2243 | 1.9508 | 4.1729 | 4.0678 | 3.9545 | 3.828 | 3.6841 | 3.5351 | 3.2555 | 2.9412 | 2.6494 | 2.3178 | 0.47388 | -0.6149 | -1.1384
|  | HOLES BAY | HE |  |  |  | 5.4086 | 5.282 | 5.1433 | 4.981 | 4.8065 | 4.6494 | 4.38 | 4.0484 | 3.6198 | 3.1484 | 0.95551 | -0.09551 | -0.58327 | 5.6069 | 5.5039 | 5.3916 | 5.2631 | 5.1202 | 4.9927 | 4.81 | 4.5916 | 4.3784 | 4.0304 | 2.1865 | 1.46 | 0.46204 | 4.1718 | 4.0729 | 3.9698 | 3.829 | 3.6729 | 3.5218 | 3.3004 | 2.9024 | 2.4902 | 2.0382 | -0.074082 | -1.2547 | -1.8292
|  | HOLES BAY | CF |  |  |  | 5.5035 | 5.4137 | 5.3341 | 5.2412 | 5.1443 | 5.0484 | 4.9586 | 4.8208 | 4.6739 | 4.481 | 2.8208 | 1.3249 | 0.083061 | 5.6702 | 5.5784 | 5.4916 | 5.3947 | 5.2947 | 5.1886 | 5.0824 | 4.9386 | 4.7814 | 4.6263 | 3.4549 | 1.7212 | -1.2992 | 4.2249 | 4.1453 | 4.0739 | 3.9871 | 3.9014 | 3.8106 | 3.7422 | 3.6218 | 3.481 | 3.3096 | 1.7116 | 0.27796 | -0.96898
MELKSHAM GSP | FROME BSP | HOLWELL | MINIMUM HEADROOM | ST 72191 44633 | YES | 0.23 | 4.0117 | 3.9434 | 3.8791 | 3.7934 | 3.6974 | 3.5821 | 3.4403 | 3.2893 | 3.176 | 3.0821 | 2.6321 | 2.4821 | 2.373 | 4.7571 | 4.7255 | 4.6898 | 4.65 | 4.6031 | 4.5102 | 4.4337 | 4.3459 | 4.2796 | 4.2214 | 3.9878 | 3.7622 | 3.0245 | 3.3367 | 3.2816 | 3.2245 | 3.1551 | 3.0796 | 2.9694 | 2.849 | 2.7235 | 2.6255 | 2.5449 | 2.1398 | 2.0133 | 1.9214
|  | HOLWELL | EE |  |  |  | 4.0117 | 3.9434 | 3.8791 | 3.7934 | 3.6974 | 3.5821 | 3.4403 | 3.2893 | 3.176 | 3.0821 | 2.6321 | 2.4821 | 2.4219 | 4.7571 | 4.7255 | 4.6898 | 4.65 | 4.6031 | 4.5102 | 4.4337 | 4.3459 | 4.2796 | 4.2214 | 4.0255 | 3.8408 | 3.4898 | 3.3367 | 3.2816 | 3.2245 | 3.1551 | 3.0796 | 2.9694 | 2.849 | 2.7235 | 2.6255 | 2.5449 | 2.1398 | 2.0133 | 1.9684
|  | HOLWELL | HT |  |  |  | 4.0505 | 3.9944 | 3.9352 | 3.8648 | 3.7515 | 3.6546 | 3.5434 | 3.424 | 3.3311 | 3.2148 | 2.7301 | 2.5097 | 2.373 | 4.7806 | 4.7571 | 4.7306 | 4.7 | 4.6112 | 4.548 | 4.4908 | 4.4265 | 4.3724 | 4.3102 | 4.0643 | 3.9592 | 3.8929 | 3.3684 | 3.3204 | 3.2704 | 3.2122 | 3.1071 | 3.0214 | 2.9265 | 2.8265 | 2.7408 | 2.6418 | 2.2306 | 2.0398 | 1.9214
|  | HOLWELL | HE |  |  |  | 4.0485 | 3.9944 | 3.9372 | 3.8658 | 3.8128 | 3.6985 | 3.5821 | 3.4597 | 3.3638 | 3.2444 | 2.6934 | 2.5444 | 2.4862 | 4.7786 | 4.7551 | 4.7245 | 4.6939 | 4.6622 | 4.5745 | 4.5051 | 4.4296 | 4.3663 | 4.2898 | 3.9878 | 3.8694 | 3.5224 | 3.3663 | 3.3194 | 3.2714 | 3.2122 | 3.1653 | 3.0592 | 2.9612 | 2.8551 | 2.7673 | 2.6633 | 2.1796 | 2.05 | 2.0051
|  | HOLWELL | CF |  |  |  | 4.0617 | 4.0168 | 3.9638 | 3.9158 | 3.8556 | 3.8138 | 3.7281 | 3.6454 | 3.5556 | 3.4913 | 3.0444 | 2.7923 | 2.5597 | 4.7918 | 4.7786 | 4.7582 | 4.7398 | 4.7153 | 4.6939 | 4.6418 | 4.5898 | 4.5347 | 4.4878 | 4.198 | 3.7622 | 3.0245 | 3.3765 | 3.3398 | 3.2929 | 3.252 | 3.202 | 3.1612 | 3.0867 | 3.0133 | 2.9347 | 2.8765 | 2.4939 | 2.2765 | 2.0704
MANNINGTON GSP | SALISBURY | HOMINGTON | MINIMUM HEADROOM | SU 11742 26037 | YES | 0 | 7.2352 | 7.1321 | 7.0066 | 6.8913 | 6.7454 | 6.5934 | 6.4281 | 6.1832 | 5.9342 | 5.7995 | 5.0964 | 4.7923 | 4.5668 | 9.7684 | 9.6888 | 9.5827 | 9.4959 | 9.3735 | 9.2378 | 9.1153 | 8.9286 | 8.7398 | 8.6439 | 8.1908 | 7.7653 | 6.5898 | 9.402 | 9.3041 | 9.1684 | 9.0582 | 8.9061 | 8.7429 | 8.5786 | 8.349 | 8.1092 | 7.9878 | 7.3653 | 7.1163 | 6.9296
|  | HOMINGTON | EE |  |  |  | 7.2352 | 7.1321 | 7.0066 | 6.8913 | 6.7454 | 6.5934 | 6.4281 | 6.1832 | 5.9342 | 5.7995 | 5.0964 | 4.7923 | 4.6536 | 9.7684 | 9.6888 | 9.5827 | 9.4959 | 9.3735 | 9.2378 | 9.1153 | 8.9286 | 8.7398 | 8.6439 | 8.1908 | 7.7888 | 7.2204 | 9.402 | 9.3041 | 9.1684 | 9.0582 | 8.9061 | 8.7429 | 8.5786 | 8.349 | 8.1092 | 7.9878 | 7.3653 | 7.1163 | 6.9959
|  | HOMINGTON | HT |  |  |  | 7.2913 | 7.1903 | 7.0974 | 6.9852 | 6.8638 | 6.7607 | 6.5995 | 6.427 | 6.2423 | 6.0923 | 5.2393 | 4.8383 | 4.5668 | 9.8388 | 9.7735 | 9.7112 | 9.6357 | 9.55 | 9.4837 | 9.3776 | 9.251 | 9.1163 | 9.0245 | 8.4592 | 8.2541 | 8.1306 | 9.4755 | 9.3827 | 9.2878 | 9.1806 | 9.0602 | 8.9643 | 8.8082 | 8.6316 | 8.4449 | 8.3031 | 7.4837 | 7.1429 | 6.9296
|  | HOMINGTON | HE |  |  |  | 7.2893 | 7.1974 | 7.1107 | 7.0077 | 6.8964 | 6.774 | 6.6495 | 6.4852 | 6.3107 | 6.174 | 5.2872 | 5.0403 | 4.8781 | 9.8306 | 9.7643 | 9.7031 | 9.6286 | 9.5408 | 9.4408 | 9.3643 | 9.2337 | 9.0929 | 8.9949 | 8.3378 | 7.9592 | 7.402 | 9.4724 | 9.3878 | 9.3 | 9.201 | 9.0898 | 8.9643 | 8.8541 | 8.6898 | 8.5122 | 8.3633 | 7.5041 | 7.2347 | 7.0786
|  | HOMINGTON | CF |  |  |  | 7.3199 | 7.2454 | 7.1587 | 7.0883 | 7.0066 | 6.9117 | 6.8087 | 6.723 | 6.6087 | 6.4903 | 5.8944 | 5.4158 | 5.0128 | 9.852 | 9.798 | 9.7255 | 9.6776 | 9.6092 | 9.5347 | 9.4408 | 9.3724 | 9.2633 | 9.15 | 8.5133 | 7.7653 | 6.5898 | 9.5031 | 9.4327 | 9.349 | 9.2847 | 9.2031 | 9.1122 | 9.0082 | 8.9337 | 8.8184 | 8.6959 | 8.0878 | 7.6265 | 7.2327
BRAMLEY (FLEE) | COXMOOR WOOD BSP | HOOK | MINIMUM HEADROOM | SU 72602 53780 | YES | 4.847 | 13.5596 | 12.7463 | 12.3321 | 11.8229 | 11.6025 | 11.0698 | 10.2259 | 9.1759 | 8.1219 | 7.2168 | 2.5933 | -0.031208 | -1.0577 | 16.0423 | 15.3433 | 15.0953 | 14.7892 | 14.58 | 14.2321 | 13.7841 | 13.0974 | 12.3963 | 11.8739 | 8.6433 | 6.6157 | 0.24226 | 13.3586 | 12.5729 | 12.1535 | 11.6402 | 11.4331 | 10.7423 | 9.8739 | 8.8341 | 7.8259 | 6.9647 | 2.5688 | 0.34226 | -0.41692
|  | HOOK | EE |  |  |  | 13.5596 | 12.7463 | 12.3321 | 11.8229 | 11.6025 | 11.0698 | 10.2259 | 9.1759 | 8.1219 | 7.2168 | 3.479 | 1.5576 | -0.012841 | 16.0423 | 15.3433 | 15.0953 | 14.7892 | 14.58 | 14.2321 | 13.7841 | 13.0974 | 12.3963 | 11.8739 | 9.2423 | 6.9525 | 3.7831 | 13.3586 | 12.5729 | 12.1535 | 11.6402 | 11.4331 | 10.7423 | 9.8739 | 8.8341 | 7.8259 | 6.9647 | 3.6708 | 2.3412 | 1.0076
|  | HOOK | HT |  |  |  | 13.7739 | 13.0637 | 12.7106 | 12.3565 | 11.93 | 11.4545 | 10.6392 | 10.1147 | 9.2453 | 8.3586 | 3.8902 | 1.1137 | -0.27917 | 16.2157 | 15.6065 | 15.429 | 15.2443 | 15.0137 | 14.7484 | 14.3923 | 14.1249 | 13.7055 | 13.2412 | 10.2484 | 8.8361 | 8.2188 | 13.5872 | 12.9219 | 12.578 | 12.2361 | 11.8208 | 11.3555 | 10.5974 | 10.1535 | 9.3423 | 8.5137 | 4.328 | 1.9678 | 0.77593
|  | HOOK | HE |  |  |  | 13.7606 | 13.0586 | 12.7045 | 12.3535 | 11.9239 | 11.4433 | 10.7178 | 10.1014 | 9.0361 | 7.9127 | 2.5933 | -0.031208 | -1.0577 | 16.1759 | 15.5372 | 15.3229 | 15.0974 | 14.8178 | 14.4943 | 14.0851 | 13.7474 | 13.2443 | 12.4963 | 8.6433 | 6.7647 | 3.7912 | 13.5719 | 12.9106 | 12.5668 | 12.2219 | 11.8025 | 11.3321 | 10.5514 | 9.7259 | 8.7065 | 7.6331 | 2.5688 | 0.34226 | -0.41692
|  | HOOK | CF |  |  |  | 13.927 | 13.3351 | 13.1484 | 12.9219 | 12.7106 | 12.4412 | 12.1249 | 11.7372 | 11.6545 | 11.2259 | 7.3055 | 3.577 | 0.85144 | 16.278 | 15.6953 | 15.5688 | 15.4086 | 15.2504 | 15.0494 | 14.8137 | 14.5014 | 14.3229 | 13.9045 | 10.8494 | 6.6157 | 0.24226 | 13.7259 | 13.1586 | 12.977 | 12.7484 | 12.5361 | 12.2647 | 11.9504 | 11.5576 | 11.3831 | 10.7851 | 7.03 | 3.4933 | 0.96165
LALEHAM | EAST BEDFONT A | HOPE AND ANCHOR | MINIMUM HEADROOM | TQ 12710 72057 | YES | 0.046 | 4.2429 | 4.1194 | 4 | 3.8531 | 3.7265 | 3.5612 | 3.3255 | 3.102 | 2.8439 | 2.6653 | 1.7939 | 1.0367 | 0.63776 | 5.1378 | 5 | 4.8622 | 4.6908 | 4.5224 | 4.3163 | 4.0663 | 3.8071 | 3.5061 | 3.2561 | 1.0245 | -3.7653 | -13.0582 | 4.4265 | 4.3102 | 4.2031 | 4.0602 | 3.9398 | 3.7816 | 3.5571 | 3.3459 | 3.1 | 2.9367 | 2.149 | 1.4857 | 1.1388
|  | HOPE AND ANCHOR | EE |  |  |  | 4.2429 | 4.1194 | 4 | 3.8531 | 3.7265 | 3.5612 | 3.3255 | 3.102 | 2.8439 | 2.6653 | 1.7939 | 1.1735 | 0.67857 | 5.1378 | 5 | 4.8622 | 4.6908 | 4.5224 | 4.3163 | 4.0663 | 3.8071 | 3.5061 | 3.2561 | 1.4827 | -1.2265 | -5.9847 | 4.4265 | 4.3102 | 4.2031 | 4.0602 | 3.9398 | 3.7816 | 3.5571 | 3.3459 | 3.1 | 2.9367 | 2.149 | 1.6051 | 1.1704
|  | HOPE AND ANCHOR | HT |  |  |  | 4.298 | 4.1847 | 4.0949 | 4.0031 | 3.8888 | 3.7684 | 3.5816 | 3.4133 | 3.2031 | 2.9816 | 1.801 | 1.0367 | 0.63776 | 5.2255 | 5.1551 | 5.0888 | 5.0276 | 4.9418 | 4.8531 | 4.7347 | 4.6296 | 4.4908 | 4.3408 | 3.652 | 3.2276 | 2.9969 | 4.4704 | 4.3806 | 4.3 | 4.2143 | 4.1051 | 3.9929 | 3.8194 | 3.6612 | 3.4622 | 3.2551 | 2.1673 | 1.4857 | 1.1388
|  | HOPE AND ANCHOR | HE |  |  |  | 4.2939 | 4.2143 | 4.1173 | 4.0306 | 3.9214 | 3.8133 | 3.65 | 3.5041 | 3.3163 | 3.1224 | 2.2102 | 1.6133 | 1.3786 | 5.1776 | 5.0776 | 4.9561 | 4.8367 | 4.6929 | 4.5306 | 4.3286 | 4.1265 | 3.8786 | 3.6112 | 1.749 | -0.97143 | -5.6082 | 4.4673 | 4.402 | 4.3184 | 4.2367 | 4.1357 | 4.0347 | 3.8806 | 3.7459 | 3.5714 | 3.3878 | 2.548 | 2.0235 | 1.8235
|  | HOPE AND ANCHOR | CF |  |  |  | 4.3684 | 4.3316 | 4.2704 | 4.2153 | 4.1459 | 4.0939 | 4.0173 | 3.9337 | 3.8316 | 3.7602 | 3.0918 | 2.4735 | 1.9061 | 5.2031 | 5.1122 | 4.9949 | 4.8653 | 4.7102 | 4.5316 | 4.3 | 4.0357 | 3.7429 | 3.4459 | 1.0245 | -3.7653 | -13.0582 | 4.5276 | 4.499 | 4.45 | 4.401 | 4.3357 | 4.2878 | 4.2184 | 4.1367 | 4.0398 | 3.9745 | 3.351 | 2.7878 | 2.2857
LOVEDEAN GSP | HAVANT | HORNDEAN | MINIMUM HEADROOM | SU 70271 12802 | YES | 9.254 | 6.1442 | 2.2153 | 1.0714 | -0.2694 | -1.549 | -2.8592 | 23.6643 | 21.6888 | 19.7173 | 18.3204 | 10.4388 | 4.6816 | 1.3092 | 9.4452 | 5.7102 | 4.8694 | 3.8939 | 2.9724 | 2.0051 | 27.4826 | 26.1102 | 24.7051 | 23.7673 | 18.6204 | 10.9928 | -6.9837 | 6.3309 | 2.4908 | 1.4184 | 0.18775 | -0.98878 | -2.2051 | 23.7235 | 21.8816 | 20.0439 | 18.8306 | 12.2826 | 7.3857 | 4.5265
|  | HORNDEAN | EE |  |  |  | 6.1442 | 2.2153 | 1.0714 | -0.2694 | -1.549 | -2.8592 | 23.6643 | 21.6888 | 19.7173 | 18.3204 | 11.5235 | 6.148 | 2.0173 | 9.4452 | 5.7102 | 4.8694 | 3.8939 | 2.9724 | 2.0051 | 27.4826 | 26.1102 | 24.7051 | 23.7673 | 18.6204 | 12.7061 | 3.1449 | 6.3309 | 2.4908 | 1.4184 | 0.18775 | -0.98878 | -2.2051 | 23.7235 | 21.8816 | 20.0439 | 18.8306 | 13.0847 | 8.6398 | 5.0939
|  | HORNDEAN | HT |  |  |  | 6.4289 | 2.3051 | 1.1531 | 0.18673 | -0.93062 | -2.0714 | 24.5633 | 22.7826 | 20.95 | 19.1602 | 10.4388 | 4.6816 | 1.3092 | 9.8595 | 6.049 | 5.3622 | 4.9031 | 4.2806 | 3.6245 | 29.4592 | 28.5092 | 27.5153 | 26.5143 | 22.0592 | 19.6439 | 18.2551 | 6.7207 | 2.6704 | 1.6306 | 0.86428 | -0.11736 | -1.1388 | 24.9541 | 23.3561 | 21.702 | 20.0704 | 12.2826 | 7.3857 | 4.5265
|  | HORNDEAN | HE |  |  |  | 6.4625 | 2.401 | 1.3112 | 0.42142 | -0.60817 | -1.6572 | 25.3224 | 23.8775 | 22.398 | 20.9531 | 13.7704 | 8.3877 | 5.6918 | 9.7758 | 5.9092 | 5.1347 | 4.6031 | 3.8908 | 3.1377 | 28.9245 | 27.9143 | 26.8296 | 25.7265 | 19.6765 | 13.6418 | 4.6541 | 6.7401 | 2.7408 | 1.751 | 1.0643 | 0.15203 | -0.79899 | 25.5775 | 24.25 | 22.8775 | 21.5245 | 15.0969 | 10.6388 | 8.3592
|  | HORNDEAN | CF |  |  |  | 6.7758 | 3.0735 | 2.5092 | 1.798 | 1.5286 | 0.9102 | 28.5122 | 27.5918 | 26.6388 | 25.551 | 20.8888 | 15.7337 | 10.7204 | 9.9227 | 6.1949 | 5.649 | 4.9735 | 4.7163 | 4.0765 | 29.9918 | 29.0806 | 28.1153 | 27.0459 | 20.7745 | 10.9928 | -6.9837 | 7.0146 | 3.3122 | 2.7541 | 2.0745 | 1.9133 | 1.3398 | 28.251 | 27.4214 | 26.5561 | 25.5816 | 21.1398 | 16.6602 | 12.4969
NURSLING GSP | WINCHESTER | HOUGHTON | MINIMUM HEADROOM | SU 33784 31741 | YES | 0.835 | 9.4097 | 9.2699 | 9.0474 | 8.4995 | 8.226 | 6.8597 | 6.126 | 5.3689 | 2.6934 | 0.80459 | -3.4117 | -7.9934 | -13.5362 | 11.4653 | 11.3643 | 11.1316 | 10.5122 | 10.2265 | 8.5857 | 7.7663 | 6.9184 | 3.6806 | 1.4276 | -3.3214 | -9.2551 | -16.9653 | 10.0776 | 9.9367 | 9.7051 | 9.0561 | 8.748 | 7.0776 | 6.2133 | 5.3204 | 2.0327 | -0.26633 | -5.1867 | -10.8031 | -17.8245
|  | HOUGHTON | EE |  |  |  | 9.4097 | 9.2699 | 9.1026 | 8.927 | 8.7383 | 8.2342 | 7.6444 | 7.3587 | 6.5087 | 6.0474 | 3.2577 | -3.3617 | -5.3781 | 11.4653 | 11.3643 | 11.2316 | 11.0929 | 10.9418 | 10.3898 | 9.7684 | 9.5418 | 8.6031 | 8.1184 | 5.0673 | -3.3959 | -6.7235 | 10.0776 | 9.9367 | 9.7704 | 9.5918 | 9.3939 | 8.8061 | 8.1214 | 7.8204 | 6.8133 | 6.301 | 3.1776 | -4.9806 | -7.4888
|  | HOUGHTON | HT |  |  |  | 9.4709 | 9.3219 | 9.0985 | 8.7393 | 8.625 | 7.524 | 6.7923 | 5.9913 | 5.6434 | 4.6566 | 1.0454 | -4.9097 | -9.4689 | 11.5296 | 11.4316 | 11.2265 | 10.8551 | 10.7827 | 9.4929 | 8.6908 | 7.8112 | 7.5061 | 6.4092 | 2.5245 | -4.6949 | -10.1918 | 10.151 | 10.0133 | 9.7704 | 9.3571 | 9.248 | 7.9133 | 7.05 | 6.1051 | 5.7286 | 4.5602 | 0.34286 | -6.9673 | -12.5571
|  | HOUGHTON | HE |  |  |  | 9.4679 | 9.3587 | 9.0474 | 8.4995 | 8.226 | 6.8597 | 6.126 | 5.3689 | 2.6934 | 0.80459 | -3.4117 | -7.9934 | -13.5362 | 11.5194 | 11.4469 | 11.1316 | 10.5122 | 10.2265 | 8.5857 | 7.7663 | 6.9184 | 3.6806 | 1.4276 | -3.3214 | -9.2551 | -16.9653 | 10.148 | 10.0429 | 9.7051 | 9.0561 | 8.748 | 7.0776 | 6.2133 | 5.3204 | 2.0327 | -0.26633 | -5.1867 | -10.8031 | -17.8245
|  | HOUGHTON | CF |  |  |  | 9.4985 | 9.4087 | 9.3209 | 9.1811 | 8.9444 | 8.6607 | 8.3556 | 8.0679 | 7.7617 | 7.4148 | 4.9781 | 2.0474 | -0.36071 | 11.5408 | 11.4776 | 11.4112 | 11.302 | 11.0551 | 10.749 | 10.4 | 10.0816 | 9.7429 | 9.348 | 6.4265 | 2.3949 | -1.9765 | 10.1745 | 10.0888 | 10.0102 | 9.8837 | 9.6133 | 9.2908 | 8.9388 | 8.6102 | 8.2582 | 7.8643 | 5.0041 | 1.5582 | -1.3245
BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | HOUNDMILLS | MINIMUM HEADROOM | SU 62187 52886 | YES | 27.769 | 13.3402 | 12.8535 | 12.08 | 11.032 | 9.9076 | 8.5657 | -4.0831 | -5.7096 | -7.3127 | -8.78 | -15.0637 | -17.4871 | -18.0147 | 13.9678 | 13.6127 | 13.0688 | 12.3586 | 11.5963 | 10.6412 | -1.5586 | -2.63 | -3.6606 | -4.5565 | -9.128 | -10.8688 | -14.1627 | 13.3973 | 13.0647 | 12.3831 | 11.3616 | 10.231 | 8.8269 | -3.6086 | -5.0086 | -6.3912 | -7.629 | -13.6167 | -15.9892 | -16.481
|  | HOUNDMILLS | EE |  |  |  | 13.3402 | 12.8535 | 12.08 | 11.032 | 9.9076 | 8.5657 | -4.0831 | -5.7096 | -7.3127 | -8.78 | -15.0157 | -16.7096 | -17.8708 | 13.9678 | 13.6127 | 13.0688 | 12.3586 | 11.5963 | 10.6412 | -1.5586 | -2.63 | -3.6606 | -4.5565 | -7.6647 | -9.2371 | -11.5351 | 13.3973 | 13.0647 | 12.3831 | 11.3616 | 10.231 | 8.8269 | -3.6086 | -5.0086 | -6.3912 | -7.629 | -12.8555 | -14.3392 | -15.3371
|  | HOUNDMILLS | HT |  |  |  | 13.7606 | 13.4259 | 12.8382 | 12.0137 | 10.7116 | 9.3055 | -3.4616 | -4.9494 | -6.4647 | -7.6922 | -14.5086 | -16.7045 | -17.7596 | 14.2147 | 14.0667 | 13.6769 | 13.1463 | 12.4453 | 11.7443 | -0.34429 | -1.1402 | -1.98 | -2.7392 | -6.4667 | -7.7708 | -8.1269 | 13.6086 | 13.3514 | 12.78 | 11.8759 | 10.7433 | 9.5565 | -2.9861 | -4.2392 | -5.5218 | -6.5167 | -12.278 | -14.2524 | -15.1616
|  | HOUNDMILLS | HE |  |  |  | 13.6341 | 13.2269 | 12.5453 | 11.6045 | 10.5749 | 9.1524 | -3.6402 | -5.1729 | -6.7473 | -8.0524 | -15.0637 | -17.4871 | -18.0147 | 14.1473 | 13.9035 | 13.43 | 12.8035 | 12.1147 | 11.2229 | -1.0178 | -2.0535 | -3.1504 | -4.18 | -9.128 | -10.8688 | -11.9586 | 13.5565 | 13.28 | 12.679 | 11.7351 | 10.6933 | 9.3963 | -3.181 | -4.4984 | -5.8473 | -6.931 | -13.6167 | -15.9892 | -16.481
|  | HOUNDMILLS | CF |  |  |  | 13.931 | 13.73 | 13.4218 | 13.0188 | 12.5055 | 11.8341 | -0.36469 | -1.5729 | -2.8616 | -4.179 | -10.7627 | -13.6402 | -16.1565 | 14.281 | 14.1718 | 14.0035 | 13.7514 | 13.3912 | 12.9371 | 0.93224 | 0.13429 | -0.68816 | -1.531 | -5.8831 | -9.2922 | -14.1627 | 13.7249 | 13.5943 | 13.3586 | 13.029 | 12.5678 | 11.882 | -0.32898 | -1.3698 | -2.4371 | -3.53 | -8.9994 | -12.2453 | -14.7239
BRAMLEY (ANDO-THAT) | THATCHAM BSP | HUNGERFORD | MINIMUM HEADROOM | SU 34066 68957 | YES | 1.861 | 6.7143 | 6.5949 | 6.4663 | 6.3082 | 6.1398 | 5.949 | 5.6327 | 5.5112 | 5.1704 | 4.8949 | 3.3806 | 2.2286 | 1.55 | 9.3061 | 9.2449 | 9.1735 | 9.0602 | 8.9378 | 8.8 | 8.6286 | 8.5184 | 8.3357 | 8.1408 | 7.0612 | 5.7408 | 2.4908 | 7.1633 | 7.0143 | 6.8724 | 6.6867 | 6.5214 | 6.3112 | 5.9816 | 5.8857 | 5.5694 | 5.3184 | 3.9561 | 2.9367 | 2.3449
|  | HUNGERFORD | EE |  |  |  | 6.7143 | 6.5949 | 6.4663 | 6.3082 | 6.1398 | 5.949 | 5.6327 | 5.5112 | 5.1704 | 4.898 | 3.3806 | 2.3806 | 1.6796 | 9.3061 | 9.2449 | 9.1735 | 9.0602 | 8.9378 | 8.8 | 8.6286 | 8.5184 | 8.3357 | 8.1408 | 7.0612 | 5.9367 | 4.2561 | 7.1633 | 7.0143 | 6.8724 | 6.6867 | 6.5214 | 6.3112 | 5.9816 | 5.8857 | 5.5694 | 5.3184 | 3.9561 | 3.0786 | 2.4643
|  | HUNGERFORD | HT |  |  |  | 6.7918 | 6.7 | 6.5939 | 6.4827 | 6.348 | 6.1959 | 5.9439 | 5.6051 | 5.2582 | 4.8949 | 3.3918 | 2.2286 | 1.55 | 9.352 | 9.3122 | 9.2643 | 9.2041 | 9.1122 | 9.0051 | 8.8765 | 8.7122 | 8.5398 | 8.3582 | 7.6602 | 7.2204 | 6.9449 | 7.2357 | 7.1235 | 6.9929 | 6.8704 | 6.7214 | 6.552 | 6.2949 | 5.9847 | 5.6612 | 5.3245 | 3.9724 | 2.9367 | 2.3449
|  | HUNGERFORD | HE |  |  |  | 6.7888 | 6.6959 | 6.5857 | 6.4735 | 6.3378 | 6.1816 | 5.9816 | 5.7296 | 5.4398 | 5.1255 | 3.7745 | 2.8112 | 2.3806 | 9.3459 | 9.3041 | 9.252 | 9.1908 | 9.0969 | 8.9847 | 8.851 | 8.6765 | 8.4959 | 8.3 | 7.3306 | 6.1714 | 4.6082 | 7.2367 | 7.1306 | 7.0071 | 6.8918 | 6.7531 | 6.5949 | 6.3796 | 6.1071 | 5.8276 | 5.5327 | 4.3327 | 3.4714 | 3.0969
|  | HUNGERFORD | CF |  |  |  | 6.849 | 6.798 | 6.7418 | 6.6755 | 6.6071 | 6.5245 | 6.4276 | 6.301 | 6.1704 | 6.0204 | 5.1612 | 4.1112 | 3.1204 | 9.3694 | 9.3378 | 9.3031 | 9.2673 | 9.2286 | 9.1765 | 9.1173 | 9.0408 | 8.9194 | 8.7286 | 7.6582 | 5.7408 | 2.4908 | 7.2796 | 7.2071 | 7.1367 | 7.052 | 6.9837 | 6.8867 | 6.7786 | 6.6439 | 6.5378 | 6.3918 | 5.6745 | 4.7092 | 3.7786
LOVEDEAN GSP | CHICHESTER & HUNSTON | HUNSTON | MINIMUM HEADROOM | SU 86949 02632 | YES | 7.721 | 15.3733 | 15.109 | 14.7355 | 14.3049 | 13.7957 | 13.2845 | 12.8039 | 12.1018 | 11.4172 | 10.8182 | 7.8161 | 6.0794 | 5.3774 | 16.5192 | 16.3763 | 16.1712 | 15.9427 | 15.5498 | 15.16 | 15.0018 | 14.5151 | 14.0212 | 13.6427 | 11.7243 | 9.9569 | 5.1478 | 14.7947 | 14.5447 | 14.1916 | 13.7855 | 13.3069 | 12.8243 | 12.3712 | 11.7059 | 11.059 | 10.4957 | 7.7712 | 6.3723 | 5.8631
|  | HUNSTON | EE |  |  |  | 15.3733 | 15.109 | 14.7355 | 14.3049 | 13.7957 | 13.2845 | 12.8039 | 12.1018 | 11.4172 | 10.8182 | 8.1304 | 6.9284 | 6.0172 | 16.5192 | 16.3763 | 16.1712 | 15.9427 | 15.5498 | 15.16 | 15.0018 | 14.5151 | 14.0212 | 13.6427 | 11.7243 | 10.06 | 7.5774 | 14.7947 | 14.5447 | 14.1916 | 13.7855 | 13.3069 | 12.8243 | 12.3712 | 11.7059 | 11.059 | 10.4957 | 8.2672 | 7.4753 | 6.6886
|  | HUNSTON | HT |  |  |  | 15.5774 | 15.3845 | 15.0978 | 14.7753 | 14.3743 | 13.9804 | 13.4967 | 12.9212 | 12.3059 | 11.7784 | 8.4253 | 6.7008 | 5.8314 | 16.6386 | 16.5457 | 16.3967 | 16.2335 | 16.0284 | 15.8335 | 15.5202 | 15.1386 | 14.7263 | 14.6314 | 12.7059 | 11.7131 | 11.2457 | 14.9916 | 14.8131 | 14.5427 | 14.2427 | 13.8702 | 13.4967 | 13.0416 | 12.4998 | 11.9151 | 11.4437 | 8.6518 | 7.3202 | 6.5835
|  | HUNSTON | HE |  |  |  | 15.5396 | 15.3314 | 15.0172 | 14.6631 | 14.2243 | 13.7865 | 13.259 | 12.609 | 11.9141 | 11.3131 | 7.8161 | 6.0794 | 5.3774 | 16.6161 | 16.5049 | 16.3376 | 16.1498 | 15.9212 | 15.6886 | 15.3335 | 14.9161 | 14.4651 | 14.2518 | 11.8886 | 10.1916 | 7.8825 | 14.9559 | 14.7569 | 14.4641 | 14.1325 | 13.7243 | 13.311 | 12.808 | 12.1916 | 11.5304 | 10.9651 | 7.7712 | 6.3723 | 5.8631
|  | HUNSTON | CF |  |  |  | 15.711 | 15.6008 | 15.4151 | 15.2059 | 14.9427 | 14.7029 | 14.4457 | 14.112 | 13.7345 | 13.3192 | 10.86 | 8.5498 | 6.6682 | 16.6988 | 16.6335 | 16.5253 | 16.4049 | 16.2488 | 16.0263 | 15.7743 | 15.5151 | 15.1916 | 14.8457 | 12.8978 | 9.9569 | 5.1478 | 15.1182 | 15.0131 | 14.8416 | 14.6478 | 14.4029 | 14.1774 | 13.9294 | 13.6141 | 13.2539 | 12.8569 | 10.5263 | 8.3427 | 6.7437
MELKSHAM GSP | ANDOVER BSP | HURSTBOURNE TARRANT | MINIMUM HEADROOM | SU 39384 52476 | YES | 1.018 | 2.1657 | 2.0687 | 1.9391 | 1.8371 | 1.6881 | 1.531 | 1.3891 | 1.1544 | 0.91057 | 0.83302 | 0.29731 | 0.11363 | -0.059837 | 3.1534 | 3.0871 | 2.9942 | 2.9187 | 2.8055 | 2.682 | 2.5759 | 2.4096 | 2.2361 | 2.1585 | 1.7922 | 1.3473 | 0.27894 | 2.3024 | 2.2096 | 2.0779 | 1.9749 | 1.8187 | 1.6514 | 1.5055 | 1.2657 | 1.0269 | 0.95649 | 0.53608 | 0.37282 | 0.20955
|  | HURSTBOURNE TARRANT | EE |  |  |  | 2.1657 | 2.0687 | 1.9391 | 1.8371 | 1.6881 | 1.531 | 1.3891 | 1.1544 | 0.91057 | 0.83302 | 0.29731 | 0.11363 | 0.022816 | 3.1534 | 3.0871 | 2.9942 | 2.9187 | 2.8055 | 2.682 | 2.5759 | 2.4096 | 2.2361 | 2.1585 | 1.7922 | 1.4871 | 0.97078 | 2.3024 | 2.2096 | 2.0779 | 1.9749 | 1.8187 | 1.6514 | 1.5055 | 1.2657 | 1.0269 | 0.95649 | 0.53608 | 0.37282 | 0.2871
|  | HURSTBOURNE TARRANT | HT |  |  |  | 2.2371 | 2.1524 | 2.0677 | 1.9616 | 1.8575 | 1.7361 | 1.6269 | 1.4575 | 1.282 | 1.1565 | 0.40751 | 0.13098 | -0.059837 | 3.2187 | 3.1677 | 3.1177 | 3.0524 | 2.983 | 2.8993 | 2.834 | 2.7238 | 2.6024 | 2.5259 | 2.0442 | 1.8912 | 1.7963 | 2.381 | 2.3014 | 2.2238 | 2.1238 | 2.0238 | 1.9065 | 1.8065 | 1.6442 | 1.4708 | 1.3565 | 0.63812 | 0.37894 | 0.20955
|  | HURSTBOURNE TARRANT | HE |  |  |  | 2.2351 | 2.1504 | 2.0677 | 1.9616 | 1.8626 | 1.7442 | 1.6432 | 1.4789 | 1.3075 | 1.1861 | 0.37078 | 0.19118 | 0.11465 | 3.2136 | 3.1575 | 3.1034 | 3.031 | 2.9596 | 2.8677 | 2.7993 | 2.684 | 2.5544 | 2.4677 | 1.8626 | 1.5442 | 1.0432 | 2.3789 | 2.2983 | 2.2238 | 2.1249 | 2.0289 | 1.9147 | 1.8218 | 1.6647 | 1.4973 | 1.3902 | 0.61873 | 0.45445 | 0.3871
|  | HURSTBOURNE TARRANT | CF |  |  |  | 2.2442 | 2.1871 | 2.1014 | 2.0412 | 1.9565 | 1.8616 | 1.7606 | 1.6902 | 1.5789 | 1.4616 | 0.86669 | 0.46976 | 0.17792 | 3.2177 | 3.181 | 3.1147 | 3.0718 | 3.0116 | 2.934 | 2.8493 | 2.7891 | 2.6881 | 2.5861 | 1.9973 | 1.3473 | 0.27894 | 2.384 | 2.331 | 2.2493 | 2.1942 | 2.1126 | 2.0208 | 1.9218 | 1.8565 | 1.7442 | 1.6259 | 1.0555 | 0.68914 | 0.44322
EALING GSP |  | IRONBRIDGE | MINIMUM HEADROOM | TQ 14226 80171 | YES | 10.719 | -2.4916 | -5.3403 | -6.3577 | -7.4587 | -8.9118 | -10.722 | -12.6597 | -14.6199 | -16.6495 | -18.3209 | -25.1791 | -29.5801 | -31.526 | 1.0462 | -1.6658 | -2.4475 | -3.1393 | -4.1607 | -5.4526 | -6.7862 | -8.2485 | -9.7658 | -10.9862 | -16.725 | -23.376 | -41.0516 | -2.0681 | -4.8587 | -5.7699 | -6.7485 | -8.0505 | -9.7128 | -11.4975 | -13.3301 | -15.223 | -16.7495 | -22.8924 | -26.775 | -28.4587
|  | IRONBRIDGE | EE |  |  |  | -2.4916 | -5.3403 | -6.3577 | -7.4587 | -8.9118 | -10.722 | -12.6597 | -14.6199 | -16.6495 | -18.3209 | -25.1791 | -28.976 | -30.924 | 1.0462 | -1.6658 | -2.4475 | -3.1393 | -4.1607 | -5.4526 | -6.7862 | -8.2485 | -9.7658 | -10.9862 | -16.725 | -22.2271 | -30.8393 | -2.0681 | -4.8587 | -5.7699 | -6.7485 | -8.0505 | -9.7128 | -11.4975 | -13.3301 | -15.223 | -16.7495 | -22.8924 | -26.224 | -27.9577
|  | IRONBRIDGE | HT |  |  |  | -2.062 | -4.8352 | -5.7699 | -7.1169 | -8.6791 | -10.1781 | -11.5169 | -13.1005 | -14.7158 | -16.3536 | -24.4005 | -29.5801 | -31.526 | 1.4646 | -1.072 | -1.6383 | -2.3699 | -3.3281 | -4.2424 | -4.8516 | -5.8036 | -6.7985 | -7.7954 | -12.375 | -15.023 | -15.8965 | -1.6681 | -4.3709 | -5.1811 | -6.3383 | -7.7516 | -9.1148 | -10.2924 | -11.7536 | -13.2465 | -14.7434 | -22.0995 | -26.775 | -28.4587
|  | IRONBRIDGE | HE |  |  |  | -2.1038 | -4.7658 | -5.525 | -6.6689 | -7.8689 | -9.4107 | -10.6536 | -12.1393 | -13.7465 | -15.3607 | -22.124 | -25.6771 | -26.7944 | 1.3666 | -1.1914 | -1.7607 | -2.4883 | -3.2995 | -4.3689 | -5.1148 | -6.1975 | -7.375 | -8.5873 | -14.674 | -20.2709 | -28.5393 | -1.7099 | -4.326 | -4.9954 | -5.9832 | -7.0424 | -8.4424 | -9.5209 | -10.8873 | -12.3638 | -13.8383 | -19.9954 | -23.1648 | -24.123
|  | IRONBRIDGE | CF |  |  |  | -1.7303 | -4.172 | -4.4648 | -5.1362 | -5.6444 | -6.2505 | -6.9556 | -7.7322 | -8.1679 | -9.0444 | -15.7128 | -20.1546 | -24.3209 | 1.5595 | -0.91686 | -1.2658 | -1.826 | -2.323 | -2.9567 | -3.7383 | -4.6352 | -5.2332 | -6.2495 | -13.5985 | -23.376 | -41.0516 | -1.3814 | -3.7944 | -4.0618 | -4.6342 | -5.0862 | -5.6301 | -6.273 | -6.9903 | -7.4271 | -8.2383 | -14.2067 | -18.2801 | -22.0128
BRAMLEY (BASI) | BASINGSTOKE T1A & T2A | JAYS CLOSE | MINIMUM HEADROOM | SU 63055 50105 | YES | 25.856 | 4.6192 | 4.2681 | 3.8284 | 3.3365 | 3.1906 | 2.6784 | 1.8059 | 0.82121 | -0.16042 | -0.86451 | -4.7788 | -7.9023 | -9.6921 | 6.0661 | 5.7773 | 5.4049 | 4.9784 | 4.8457 | 4.4141 | 3.8008 | 3.0896 | 2.3671 | 1.8569 | -0.91961 | -4.0206 | -12.0665 | 4.5365 | 4.2059 | 3.7886 | 3.3284 | 3.1967 | 2.7181 | 1.9079 | 0.99366 | 0.087535 | -0.57981 | -4.0268 | -6.8114 | -8.3931
|  | JAYS CLOSE | EE |  |  |  | 4.6192 | 4.2681 | 3.8284 | 3.3365 | 3.1906 | 2.6784 | 1.8059 | 0.82121 | -0.16042 | -0.86451 | -4.6002 | -7.3114 | -9.4063 | 6.0661 | 5.7773 | 5.4049 | 4.9784 | 4.8457 | 4.4141 | 3.8008 | 3.0896 | 2.3671 | 1.8569 | -0.91961 | -3.7635 | -7.9849 | 4.5365 | 4.2059 | 3.7886 | 3.3284 | 3.1967 | 2.7181 | 1.9079 | 0.99366 | 0.087535 | -0.57981 | -3.9063 | -6.29 | -8.1461
|  | JAYS CLOSE | HT |  |  |  | 4.8069 | 4.5069 | 4.1498 | 3.809 | 3.4018 | 2.9396 | 2.4447 | 1.6284 | 0.78549 | -0.07369 | -4.7788 | -7.9023 | -9.6921 | 6.2722 | 6.0865 | 5.8477 | 5.6171 | 5.3345 | 5.0018 | 4.812 | 4.3437 | 3.8498 | 3.3396 | 0.82733 | -0.6043 | -1.3461 | 4.7253 | 4.4467 | 4.1161 | 3.7967 | 3.4181 | 2.9855 | 2.5569 | 1.813 | 1.0406 | 0.2508 | -4.0268 | -6.8114 | -8.3931
|  | JAYS CLOSE | HE |  |  |  | 4.81 | 4.5375 | 4.2079 | 3.8998 | 3.5263 | 3.1192 | 2.7508 | 2.063 | 1.3488 | 0.61407 | -3.339 | -6.0533 | -7.3023 | 6.2345 | 6.0232 | 5.7569 | 5.4977 | 5.1743 | 4.8151 | 4.6008 | 4.0988 | 3.56 | 2.9926 | -0.18389 | -3.1084 | -7.0196 | 4.7243 | 4.4712 | 4.1651 | 3.8784 | 3.5294 | 3.1437 | 2.8263 | 2.1947 | 1.5345 | 0.85488 | -2.7523 | -5.1972 | -6.3114
|  | JAYS CLOSE | CF |  |  |  | 4.9712 | 4.7957 | 4.6355 | 4.4396 | 4.2579 | 4.0284 | 3.761 | 3.4192 | 3.4181 | 3.1049 | 0.51611 | -2.1819 | -4.8145 | 6.3192 | 6.1386 | 5.96 | 5.7406 | 5.5181 | 5.2232 | 4.8763 | 4.4549 | 4.3079 | 3.8784 | 0.73243 | -4.0206 | -12.0665 | 4.8722 | 4.711 | 4.5569 | 4.3671 | 4.2008 | 3.9794 | 3.7243 | 3.4069 | 3.412 | 3.1161 | 0.70896 | -1.7614 | -4.0808
MINETY GSP | CIRENCESTER BSP | KEMBLE RAF | MINIMUM HEADROOM | ST 96064 96012 | YES | 0.282 | 11.5071 | 11.4694 | 11.452 | 11.4041 | 11.352 | 11.2929 | 11.2245 | 11.1398 | 11.0571 | 10.9816 | 10.6612 | 10.5541 | 10.502 | 11.4071 | 11.3765 | 11.3663 | 11.3306 | 11.2898 | 11.2439 | 11.1918 | 11.1265 | 11.0612 | 11 | 10.7459 | 10.6602 | 10.6163 | 11.648 | 11.6112 | 11.5929 | 11.549 | 11.4959 | 11.4378 | 11.3704 | 11.2837 | 11.202 | 11.1235 | 10.8082 | 10.698 | 10.648
|  | KEMBLE RAF | EE |  |  |  | 11.5071 | 11.4694 | 11.452 | 11.4041 | 11.352 | 11.2929 | 11.2245 | 11.1398 | 11.0571 | 10.9816 | 10.6673 | 10.5827 | 10.5765 | 11.4071 | 11.3765 | 11.3663 | 11.3306 | 11.2898 | 11.2439 | 11.1918 | 11.1265 | 11.0612 | 11 | 10.7469 | 10.6816 | 10.6765 | 11.648 | 11.6112 | 11.5929 | 11.549 | 11.4959 | 11.4378 | 11.3704 | 11.2837 | 11.202 | 11.1235 | 10.8082 | 10.7255 | 10.7204
|  | KEMBLE RAF | HT |  |  |  | 11.5316 | 11.502 | 11.4663 | 11.4459 | 11.4061 | 11.3561 | 11.2969 | 11.2245 | 11.1449 | 11.0673 | 10.7 | 10.5541 | 10.5102 | 11.4286 | 11.4031 | 11.3735 | 11.3633 | 11.3316 | 11.2929 | 11.2469 | 11.1908 | 11.1286 | 11.0653 | 10.7724 | 10.6602 | 10.6265 | 11.6724 | 11.6418 | 11.6051 | 11.5878 | 11.5469 | 11.4959 | 11.4367 | 11.3622 | 11.2837 | 11.2041 | 10.8378 | 10.698 | 10.6561
|  | KEMBLE RAF | HE |  |  |  | 11.5337 | 11.5031 | 11.4684 | 11.448 | 11.4071 | 11.3571 | 11.2969 | 11.2204 | 11.1367 | 11.049 | 10.6612 | 10.5592 | 10.5143 | 11.4296 | 11.4051 | 11.3765 | 11.3643 | 11.3327 | 11.2939 | 11.248 | 11.1878 | 11.1245 | 11.0541 | 10.7459 | 10.6653 | 10.6316 | 11.6735 | 11.6449 | 11.6092 | 11.5908 | 11.55 | 11.499 | 11.4398 | 11.3622 | 11.2796 | 11.1918 | 10.8082 | 10.7092 | 10.6694
|  | KEMBLE RAF | CF |  |  |  | 11.5551 | 11.5418 | 11.5214 | 11.4969 | 11.4755 | 11.4643 | 11.4388 | 11.398 | 11.3531 | 11.299 | 10.9918 | 10.7071 | 10.502 | 11.4408 | 11.4357 | 11.4184 | 11.398 | 11.3816 | 11.3765 | 11.3561 | 11.3255 | 11.2888 | 11.249 | 11.0082 | 10.7796 | 10.6163 | 11.6918 | 11.6816 | 11.6622 | 11.6378 | 11.6163 | 11.6061 | 11.5816 | 11.5398 | 11.4949 | 11.4429 | 11.1388 | 10.851 | 10.648
COWLEY GSP | COWLEY LOCAL (2 X 45) | KENNINGTON | MINIMUM HEADROOM | SP 52881 01094 | YES | 0.377 | 1.0378 | 0.77041 | 0.54388 | 0.34082 | 0.091837 | -0.16939 | -0.52653 | -0.56224 | -0.91531 | -1.2786 | -2.4827 | -3.4888 | -4.0929 | 2.9704 | 2.8082 | 2.651 | 2.5061 | 2.3276 | 2.1245 | 1.8612 | 1.9071 | 1.6684 | 1.5184 | 0.62347 | -0.6449 | -3.5316 | 1.4408 | 1.2112 | 1 | 0.80918 | 0.56429 | 0.3051 | -0.047959 | -0.011224 | -0.33571 | -0.67755 | -1.7378 | -2.5827 | -3.0694
|  | KENNINGTON | EE |  |  |  | 1.0378 | 0.77041 | 0.54388 | 0.34082 | 0.091837 | -0.16939 | -0.52653 | -0.55408 | -0.88265 | -1.1092 | -2.3224 | -3.251 | -3.949 | 2.9704 | 2.8082 | 2.651 | 2.5061 | 2.3276 | 2.1245 | 1.8612 | 1.9071 | 1.6684 | 1.5184 | 0.62347 | -0.40306 | -1.9367 | 1.4408 | 1.2112 | 1 | 0.80918 | 0.56429 | 0.3051 | -0.047959 | -0.011224 | -0.32755 | -0.52551 | -1.5959 | -2.3786 | -2.9469
|  | KENNINGTON | HT |  |  |  | 1.1071 | 0.84694 | 0.65408 | 0.48571 | 0.27755 | 0.057143 | -0.22245 | -0.56224 | -0.91531 | -1.2786 | -2.4827 | -3.4888 | -4.0929 | 3.0449 | 2.9092 | 2.801 | 2.7102 | 2.5929 | 2.4612 | 2.3194 | 2.1296 | 1.9153 | 1.6949 | 1.2 | 0.77449 | 0.51122 | 1.5112 | 1.2898 | 1.1133 | 0.95918 | 0.76735 | 0.56224 | 0.30816 | -0.005102 | -0.33571 | -0.67755 | -1.7378 | -2.5827 | -3.0694
|  | KENNINGTON | HE |  |  |  | 1.1143 | 0.86837 | 0.68878 | 0.53776 | 0.34286 | 0.1398 | -0.07449 | -0.35408 | -0.64388 | -0.94388 | -1.9133 | -2.8071 | -3.3061 | 3.0316 | 2.8867 | 2.7663 | 2.6622 | 2.5276 | 2.3816 | 2.2357 | 2.0337 | 1.8112 | 1.5745 | 0.80714 | -0.21939 | -1.6755 | 1.5163 | 1.3082 | 1.1459 | 1.0041 | 0.82449 | 0.63469 | 0.43878 | 0.17959 | -0.10612 | -0.4 | -1.2306 | -1.9959 | -2.3959
|  | KENNINGTON | CF |  |  |  | 1.1714 | 0.98163 | 0.86224 | 0.73265 | 0.63776 | 0.50408 | 0.38265 | 0.28571 | 0.14184 | -0.0071429 | -0.62857 | -1.5622 | -2.4888 | 3.0582 | 2.9367 | 2.8398 | 2.7296 | 2.6449 | 2.5214 | 2.3837 | 2.2592 | 2.0929 | 1.9092 | 1.0286 | -0.6449 | -3.5316 | 1.5684 | 1.4122 | 1.301 | 1.1806 | 1.0929 | 0.96735 | 0.85408 | 0.75714 | 0.60612 | 0.44898 | -0.1051 | -0.92551 | -1.7347
BRAMLEY (FLEE) | BURGHFIELD MAIN | KENTWOOD HILL | MINIMUM HEADROOM | SU 67102 74048 | YES | 0.47 | 8.0712 | 7.708 | 7.0263 | 6.2865 | 5.4733 | 4.4763 | 2.7631 | 1.0182 | -0.72163 | -1.9471 | -9.3931 | -15.1237 | -18.3563 | 11.6159 | 11.3353 | 10.7373 | 10.0792 | 9.3394 | 8.4782 | 7.2884 | 5.9833 | 4.6618 | 3.7802 | -1.4576 | -10.0484 | -28.9249 | 8.2753 | 7.9896 | 7.3192 | 6.5814 | 5.7682 | 4.7947 | 3.2131 | 1.5437 | -0.12469 | -1.2033 | -7.3982 | -12.2655 | -15.1492
|  | KENTWOOD HILL | EE |  |  |  | 8.0712 | 7.708 | 7.0263 | 6.2865 | 5.4733 | 4.4763 | 2.7631 | 1.0182 | -0.72163 | -1.9471 | -8.5155 | -13.892 | -17.9788 | 11.6159 | 11.3353 | 10.7373 | 10.0792 | 9.3394 | 8.4782 | 7.2884 | 5.9833 | 4.6618 | 3.7802 | -1.4576 | -7.8831 | -17.9116 | 8.2753 | 7.9896 | 7.3192 | 6.5814 | 5.7682 | 4.7947 | 3.2131 | 1.5437 | -0.12469 | -1.2033 | -6.7441 | -11.1859 | -14.84
|  | KENTWOOD HILL | HT |  |  |  | 8.3529 | 7.7978 | 7.1529 | 6.8416 | 6.2049 | 5.3722 | 3.7835 | 2.2284 | 0.62939 | -1.0114 | -9.3931 | -15.1237 | -18.3563 | 12.0384 | 11.6822 | 11.2333 | 11.122 | 10.7037 | 10.1833 | 9.3731 | 8.5231 | 7.6384 | 6.719 | 2.4435 | 0.075102 | -1.2106 | 8.6916 | 8.1682 | 7.5263 | 7.2957 | 6.6773 | 5.9008 | 4.4886 | 3.0702 | 1.6029 | 0.089592 | -7.3982 | -12.2655 | -15.1492
|  | KENTWOOD HILL | HE |  |  |  | 8.3957 | 7.912 | 7.3406 | 7.1059 | 6.5406 | 5.7916 | 4.5539 | 3.3427 | 2.0947 | 0.80694 | -6.0522 | -11.3135 | -13.9441 | 11.9557 | 11.5363 | 11.0027 | 10.8047 | 10.2822 | 9.6424 | 8.7761 | 7.8486 | 6.8649 | 5.8139 | -0.27694 | -6.7127 | -16.1637 | 8.711 | 8.2447 | 7.6569 | 7.5049 | 6.958 | 6.2549 | 5.1355 | 4.0039 | 2.8273 | 1.612 | -4.592 | -8.8716 | -11.1767
|  | KENTWOOD HILL | CF |  |  |  | 8.659 | 8.41 | 8.0865 | 7.7161 | 7.7253 | 7.2671 | 6.7559 | 6.2835 | 5.7743 | 5.2437 | 0.76204 | -4.3022 | -9.091 | 12.0741 | 11.7363 | 11.3006 | 10.8343 | 10.6904 | 10.1067 | 9.4129 | 8.6588 | 7.8527 | 6.9833 | 0.48122 | -10.0484 | -28.9249 | 8.9355 | 8.659 | 8.2865 | 7.8947 | 7.9692 | 7.5324 | 7.0457 | 6.558 | 6.0304 | 5.4763 | 1.2253 | -3.1849 | -7.1665
COWLEY GSP | YARNTON BSP | KIDDINGTON | MINIMUM HEADROOM | SP 43362 24301 | YES | 2.37 | 13.3041 | 13.2245 | 13.1398 | 13.0215 | 12.8755 | 12.7245 | 12.4388 | 12.1082 | 11.7766 | 11.6051 | 11.05 | 10.4388 | 9.9857 | 14.1174 | 14.0092 | 13.9072 | 13.7623 | 13.6061 | 13.4806 | 13.2674 | 13.0245 | 12.7694 | 12.6439 | 12.3306 | 11.5735 | 9.448 | 12.3837 | 12.2521 | 12.1286 | 11.9623 | 11.7664 | 11.6143 | 11.3419 | 11.0255 | 10.7051 | 10.5449 | 10.1776 | 9.6806 | 9.3357
|  | KIDDINGTON | EE |  |  |  | 13.3041 | 13.2245 | 13.1398 | 13.0215 | 12.8755 | 12.7245 | 12.4388 | 12.1082 | 11.7766 | 11.6051 | 11.05 | 10.4806 | 10.1102 | 14.1174 | 14.0092 | 13.9072 | 13.7623 | 13.6061 | 13.4806 | 13.2674 | 13.0245 | 12.7694 | 12.6439 | 12.4061 | 11.7806 | 10.7459 | 12.3837 | 12.2521 | 12.1286 | 11.9623 | 11.7664 | 11.6143 | 11.3419 | 11.0255 | 10.7051 | 10.5449 | 10.1776 | 9.7429 | 9.4419
|  | KIDDINGTON | HT |  |  |  | 13.3541 | 13.2898 | 13.2215 | 13.1184 | 13.0225 | 12.897 | 12.6837 | 12.4878 | 12.2572 | 12.0225 | 11.1184 | 10.4388 | 9.9857 | 14.1868 | 14.1174 | 14.0459 | 13.9592 | 13.8939 | 13.7868 | 13.6398 | 13.5164 | 13.3459 | 13.1704 | 12.8327 | 12.5459 | 12.3684 | 12.4521 | 12.35 | 12.251 | 12.1235 | 12.0266 | 11.8857 | 11.6674 | 11.4715 | 11.2286 | 10.9745 | 10.2327 | 9.6806 | 9.3357
|  | KIDDINGTON | HE |  |  |  | 13.35 | 13.2857 | 13.2184 | 13.1327 | 13.0388 | 12.9194 | 12.7317 | 12.5592 | 12.3551 | 12.1449 | 11.2276 | 10.6643 | 10.3908 | 14.1776 | 14.098 | 14.0276 | 13.9266 | 13.848 | 13.7317 | 13.5796 | 13.4459 | 13.2623 | 13.0704 | 12.5245 | 11.8908 | 10.8776 | 12.45 | 12.3521 | 12.2623 | 12.1378 | 12.0459 | 11.9082 | 11.7153 | 11.5398 | 11.3184 | 11.0868 | 10.3745 | 9.9235 | 9.6898
|  | KIDDINGTON | CF |  |  |  | 13.3898 | 13.3459 | 13.3041 | 13.2449 | 13.1623 | 13.0939 | 12.999 | 12.8888 | 12.7725 | 12.6847 | 11.798 | 11.4837 | 10.8061 | 14.2 | 14.1337 | 14.0684 | 13.9949 | 13.9021 | 13.8296 | 13.7164 | 13.5776 | 13.4306 | 13.3215 | 12.3306 | 11.5735 | 9.448 | 12.4878 | 12.4092 | 12.3398 | 12.2582 | 12.1612 | 12.098 | 11.9888 | 11.8612 | 11.7123 | 11.6184 | 10.7378 | 10.5429 | 10.0041
BRAMLEY (FLEE) | READING BSP | KIDMORE END | MINIMUM HEADROOM | SU 69953 78205 | YES | 1.517 | 13.7893 | 13.573 | 13.324 | 12.9005 | 12.5628 | 12.5679 | 12.1117 | 11.6107 | 11.1087 | 10.7597 | 8.7046 | 7.2679 | 6.4536 | 14.9581 | 14.7774 | 14.5621 | 14.2336 | 13.9213 | 14.0091 | 13.6734 | 13.2897 | 12.8928 | 12.654 | 11.1499 | 8.2958 | 2.3234 | 13.6893 | 13.476 | 13.2311 | 12.8342 | 12.4883 | 12.5454 | 12.1158 | 11.6362 | 11.1536 | 10.8485 | 9.1046 | 7.8128 | 7.0403
|  | KIDMORE END | EE |  |  |  | 13.7893 | 13.573 | 13.324 | 12.9005 | 12.5628 | 12.5679 | 12.1117 | 11.6107 | 11.1087 | 10.7597 | 8.875 | 7.5515 | 6.6199 | 14.9581 | 14.7774 | 14.5621 | 14.2336 | 13.9213 | 14.0091 | 13.6734 | 13.2897 | 12.8928 | 12.654 | 11.1499 | 9.2162 | 6.106 | 13.6893 | 13.476 | 13.2311 | 12.8342 | 12.4883 | 12.5454 | 12.1158 | 11.6362 | 11.1536 | 10.8485 | 9.2515 | 8.073 | 7.1842
|  | KIDMORE END | HT |  |  |  | 13.9168 | 13.7066 | 13.5036 | 13.1372 | 12.9076 | 12.6199 | 12.1423 | 11.624 | 11.4811 | 11.0036 | 8.7046 | 7.2679 | 6.4536 | 15.1142 | 14.9805 | 14.854 | 14.6356 | 14.4897 | 14.2856 | 13.9999 | 13.6754 | 13.7887 | 13.5142 | 12.3285 | 11.7468 | 11.3938 | 13.8383 | 13.6372 | 13.4423 | 13.1128 | 12.8954 | 12.6138 | 12.1709 | 11.6811 | 11.6281 | 11.1862 | 9.1046 | 7.8128 | 7.0403
|  | KIDMORE END | HE |  |  |  | 13.924 | 13.7291 | 13.5434 | 13.1934 | 12.9811 | 12.7168 | 12.3291 | 12.2342 | 11.8576 | 11.475 | 9.4393 | 8.1474 | 7.5219 | 15.0866 | 14.9274 | 14.7713 | 14.5234 | 14.3499 | 14.1081 | 13.803 | 13.8203 | 13.5254 | 13.2121 | 11.3897 | 9.4703 | 6.4836 | 13.8413 | 13.6515 | 13.475 | 13.1566 | 12.9556 | 12.6944 | 12.325 | 12.2944 | 11.9403 | 11.576 | 9.7362 | 8.6199 | 8.0332
|  | KIDMORE END | CF |  |  |  | 13.9995 | 13.8719 | 13.7536 | 13.4913 | 13.3219 | 13.1842 | 13.0066 | 12.7913 | 12.5597 | 12.6852 | 11.3505 | 9.9393 | 8.6444 | 15.1152 | 14.9856 | 14.8509 | 14.6356 | 14.4519 | 14.2907 | 14.0458 | 13.754 | 13.4387 | 13.4968 | 11.5387 | 8.2958 | 2.3234 | 13.9117 | 13.7832 | 13.6648 | 13.4291 | 13.2576 | 13.1291 | 12.9434 | 12.723 | 12.4679 | 12.6546 | 11.3648 | 10.1291 | 9.0474
BRAMLEY (FLEE) | CAMBERLEY MAIN | KINGS RIDE | MINIMUM HEADROOM | SU 87551 61530 | YES | 1.423 | 10.4899 | 10.1736 | 9.846 | 9.3409 | 8.7389 | 8.4848 | 7.6409 | 6.6124 | 5.4614 | 4.6777 | 1.092 | -1.1397 | -2.2723 | 12.872 | 12.6241 | 12.3639 | 11.9965 | 11.5649 | 11.3822 | 10.8404 | 10.173 | 9.4394 | 8.923 | 6.4271 | 3.6883 | -3.1953 | 10.3529 | 10.1009 | 9.8458 | 9.4519 | 8.9193 | 8.6764 | 7.9315 | 7.0233 | 5.9938 | 5.306 | 2.1866 | 0.17436 | -0.84809
|  | KINGS RIDE | EE |  |  |  | 10.4899 | 10.1736 | 9.846 | 9.3409 | 8.7389 | 8.4848 | 7.6532 | 6.6124 | 5.4614 | 4.6777 | 1.3399 | -0.62436 | -2.1223 | 12.872 | 12.6241 | 12.3639 | 11.9965 | 11.5649 | 11.3822 | 10.8404 | 10.173 | 9.4394 | 8.923 | 6.4271 | 4.0894 | 0.50059 | 10.3529 | 10.1009 | 9.8458 | 9.4519 | 8.9193 | 8.7182 | 7.9621 | 7.0233 | 5.9938 | 5.306 | 2.3948 | 0.62028 | -0.7236
|  | KINGS RIDE | HT |  |  |  | 10.6573 | 10.4032 | 10.1481 | 9.644 | 9.1216 | 8.492 | 7.6409 | 6.7165 | 6.195 | 5.2828 | 1.092 | -1.1397 | -2.2723 | 13.0302 | 12.872 | 12.7169 | 12.4281 | 12.1343 | 11.773 | 11.3179 | 10.8088 | 10.5945 | 10.1006 | 7.9281 | 6.8863 | 6.4067 | 10.4672 | 10.254 | 10.0448 | 9.6356 | 9.1999 | 8.6764 | 7.9315 | 7.1335 | 6.6346 | 5.8529 | 2.1866 | 0.17436 | -0.84809
|  | KINGS RIDE | HE |  |  |  | 10.6614 | 10.4379 | 10.2134 | 9.8338 | 9.4267 | 8.9011 | 8.2134 | 7.3083 | 6.7644 | 5.993 | 2.4746 | 0.49707 | -0.39069 | 12.9955 | 12.8179 | 12.6332 | 12.3608 | 12.069 | 11.7057 | 11.2536 | 10.6781 | 10.3557 | 9.8261 | 7.1108 | 4.721 | 1.3465 | 10.4733 | 10.2876 | 10.104 | 9.7978 | 9.456 | 9.0203 | 8.4284 | 7.6591 | 7.1356 | 6.4744 | 3.4009 | 1.6091 | 0.81416
|  | KINGS RIDE | CF |  |  |  | 10.7593 | 10.6471 | 10.5165 | 10.3573 | 10.1777 | 10.0307 | 9.8165 | 9.4797 | 8.9869 | 8.8593 | 5.3042 | 3.3205 | 1.4328 | 13.0414 | 12.9169 | 12.769 | 12.5945 | 12.3955 | 12.1904 | 11.9179 | 11.5608 | 11.1159 | 10.9088 | 7.6322 | 3.6883 | -3.1953 | 10.5652 | 10.4774 | 10.3784 | 10.256 | 10.1193 | 10.004 | 9.8427 | 9.5856 | 9.1601 | 9.0672 | 5.9774 | 4.1866 | 2.4917
BRAMLEY (ANDO-THAT) | THATCHAM BSP | KINGSCLERE | MINIMUM HEADROOM | SU 51982 59358 | YES | 0.474 | 4.2837 | 4.1204 | 3.9592 | 3.748 | 3.5633 | 3.3286 | 2.9898 | 2.5969 | 2.6133 | 2.3929 | 1.2673 | 0.58878 | 0.17041 | 5.777 | 5.6577 | 5.5352 | 5.376 | 5.2342 | 5.0505 | 4.8138 | 4.527 | 4.5801 | 4.424 | 3.6291 | 2.6913 | 0.49133 | 4.8194 | 4.6592 | 4.502 | 4.2929 | 4.1153 | 3.8776 | 3.5551 | 3.1755 | 3.2571 | 3.051 | 2.0643 | 1.4602 | 1.0939
|  | KINGSCLERE | EE |  |  |  | 4.2837 | 4.1204 | 3.9592 | 3.748 | 3.5633 | 3.3286 | 2.9898 | 2.5969 | 2.6133 | 2.3929 | 1.2673 | 0.67143 | 0.26531 | 5.777 | 5.6577 | 5.5352 | 5.376 | 5.2342 | 5.0505 | 4.8138 | 4.527 | 4.5801 | 4.424 | 3.6291 | 2.9026 | 1.8005 | 4.8194 | 4.6592 | 4.502 | 4.2929 | 4.1153 | 3.8776 | 3.5551 | 3.1755 | 3.2571 | 3.051 | 2.0643 | 1.5408 | 1.1816
|  | KINGSCLERE | HT |  |  |  | 4.3837 | 4.25 | 4.1286 | 3.9714 | 3.8439 | 3.6684 | 3.3969 | 3.1439 | 2.8357 | 2.5143 | 1.3847 | 0.58878 | 0.17041 | 5.8689 | 5.7821 | 5.7107 | 5.6087 | 5.525 | 5.4056 | 5.2464 | 5.1036 | 4.9087 | 4.7046 | 4.1526 | 3.7689 | 3.5944 | 4.9276 | 4.7959 | 4.6898 | 4.5357 | 4.4163 | 4.2469 | 3.9939 | 3.7653 | 3.4714 | 3.1663 | 2.1714 | 1.4602 | 1.0939
|  | KINGSCLERE | HE |  |  |  | 4.3765 | 4.2633 | 4.1235 | 3.9684 | 3.8418 | 3.6673 | 3.4143 | 3.1776 | 2.8847 | 2.5765 | 1.4449 | 0.75714 | 0.5051 | 5.8526 | 5.776 | 5.673 | 5.5607 | 5.4607 | 5.3291 | 5.1556 | 4.9944 | 4.7801 | 4.5526 | 3.7219 | 2.8974 | 1.8699 | 4.9214 | 4.8143 | 4.6847 | 4.5357 | 4.4173 | 4.248 | 4.0153 | 3.799 | 3.5214 | 3.2276 | 2.2296 | 1.6092 | 1.3959
|  | KINGSCLERE | CF |  |  |  | 4.4173 | 4.3245 | 4.2418 | 4.1408 | 4.0255 | 3.9388 | 3.8092 | 3.649 | 3.5224 | 3.35 | 2.2418 | 1.7684 | 1.0173 | 5.874 | 5.8046 | 5.7362 | 5.6515 | 5.5526 | 5.4699 | 5.3444 | 5.1923 | 5.0689 | 4.9015 | 3.7668 | 2.6913 | 0.49133 | 4.9541 | 4.8653 | 4.7847 | 4.6867 | 4.5755 | 4.4929 | 4.3643 | 4.2061 | 4.0847 | 3.9143 | 2.8439 | 2.4959 | 1.8337
BRAMLEY (ANDO-THAT) | THATCHAM BSP | KINTBURY | MINIMUM HEADROOM | SU 37657 67143 | YES | 0.038 | 4.8143 | 4.7173 | 4.5633 | 4.4439 | 4.2796 | 4.15 | 3.9367 | 3.6827 | 3.4306 | 3.3102 | 2.7806 | 2.5918 | 2.4194 | 5.925 | 5.8505 | 5.726 | 5.6372 | 5.4964 | 5.3923 | 5.2199 | 5.0056 | 4.7923 | 4.7372 | 4.3474 | 3.6372 | 2.1709 | 5.3439 | 5.2531 | 5.1122 | 5.002 | 4.849 | 4.7337 | 4.5388 | 4.3082 | 4.0765 | 3.9643 | 3.4867 | 3.3235 | 3.1714
|  | KINTBURY | EE |  |  |  | 4.8143 | 4.7173 | 4.5633 | 4.4439 | 4.2796 | 4.15 | 3.9367 | 3.6827 | 3.4306 | 3.3102 | 2.7806 | 2.5918 | 2.501 | 5.925 | 5.8505 | 5.726 | 5.6372 | 5.4964 | 5.3923 | 5.2199 | 5.0056 | 4.7923 | 4.7372 | 4.3474 | 3.9066 | 3.1872 | 5.3439 | 5.2531 | 5.1122 | 5.002 | 4.849 | 4.7337 | 4.5388 | 4.3082 | 4.0765 | 3.9643 | 3.4867 | 3.3235 | 3.2439
|  | KINTBURY | HT |  |  |  | 4.9051 | 4.8122 | 4.7214 | 4.6143 | 4.4918 | 4.4031 | 4.2429 | 4.0582 | 3.9173 | 3.7214 | 2.9 | 2.6071 | 2.4194 | 5.9995 | 5.9423 | 5.8893 | 5.8179 | 5.727 | 5.6658 | 5.5505 | 5.4128 | 5.3138 | 5.1668 | 4.627 | 4.5301 | 4.4362 | 5.4255 | 5.3418 | 5.2582 | 5.1582 | 5.0469 | 4.9622 | 4.8153 | 4.6459 | 4.5204 | 4.3398 | 3.5908 | 3.3296 | 3.1714
|  | KINTBURY | HE |  |  |  | 4.899 | 4.8092 | 4.7214 | 4.6163 | 4.499 | 4.4112 | 4.2561 | 4.0755 | 3.9388 | 3.748 | 2.8694 | 2.6776 | 2.599 | 5.9872 | 5.927 | 5.8597 | 5.7862 | 5.6944 | 5.6291 | 5.5158 | 5.3821 | 5.277 | 5.1301 | 4.4199 | 3.9628 | 3.2556 | 5.4214 | 5.3388 | 5.2561 | 5.1592 | 5.052 | 4.9714 | 4.8286 | 4.6633 | 4.5408 | 4.3673 | 3.5776 | 3.4041 | 3.3378
|  | KINTBURY | CF |  |  |  | 4.9245 | 4.848 | 4.75 | 4.6806 | 4.5939 | 4.4959 | 4.4296 | 4.3061 | 4.1796 | 4.0449 | 3.3857 | 2.9643 | 2.6776 | 6.0046 | 5.9474 | 5.875 | 5.823 | 5.7526 | 5.675 | 5.6066 | 5.4995 | 5.3832 | 5.2587 | 4.5413 | 3.6372 | 2.1709 | 5.4449 | 5.3745 | 5.2898 | 5.2255 | 5.1459 | 5.0561 | 4.9959 | 4.8878 | 4.7714 | 4.6469 | 4.0541 | 3.6704 | 3.4184
BRAMLEY (FLEE) | MAIDENHEAD BSP | KNOWL HILL | MINIMUM HEADROOM | SU 82849 79105 | YES | 0.381 | 4.6982 | 4.6247 | 4.5227 | 4.4104 | 4.3318 | 4.2073 | 4.039 | 3.9053 | 3.7145 | 3.6155 | 3.0522 | 2.7298 | 2.5624 | 4.7985 | 4.7454 | 4.6689 | 4.577 | 4.5097 | 4.4087 | 4.2832 | 4.176 | 4.0281 | 3.9515 | 3.5434 | 2.9648 | 1.6719 | 5.3196 | 5.2492 | 5.1492 | 5.041 | 4.9614 | 4.84 | 4.6737 | 4.538 | 4.3522 | 4.2522 | 3.7247 | 3.4278 | 3.292
|  | KNOWL HILL | EE |  |  |  | 4.6982 | 4.6247 | 4.5227 | 4.4104 | 4.3318 | 4.2073 | 4.039 | 3.9053 | 3.7145 | 3.6155 | 3.0941 | 2.8022 | 2.639 | 4.7985 | 4.7454 | 4.6689 | 4.577 | 4.5097 | 4.4087 | 4.2832 | 4.176 | 4.0281 | 3.9515 | 3.5434 | 3.1413 | 2.5321 | 5.3196 | 5.2492 | 5.1492 | 5.041 | 4.9614 | 4.84 | 4.6737 | 4.538 | 4.3522 | 4.2522 | 3.7971 | 3.5747 | 3.4369
|  | KNOWL HILL | HT |  |  |  | 4.741 | 4.6778 | 4.6002 | 4.54 | 4.4604 | 4.3645 | 4.2267 | 4.1237 | 3.9635 | 3.7992 | 3.1655 | 2.8073 | 2.5624 | 4.8403 | 4.8015 | 4.7485 | 4.7097 | 4.6556 | 4.5883 | 4.5005 | 4.4321 | 4.326 | 4.2168 | 3.7791 | 3.5607 | 3.4219 | 5.3645 | 5.3063 | 5.2318 | 5.1737 | 5.0982 | 5.0033 | 4.8737 | 4.7727 | 4.6165 | 4.4573 | 3.8512 | 3.5451 | 3.3339
|  | KNOWL HILL | HE |  |  |  | 4.74 | 4.6747 | 4.6022 | 4.5431 | 4.4645 | 4.3696 | 4.24 | 4.1431 | 3.9931 | 3.839 | 3.0522 | 2.7298 | 2.589 | 4.8332 | 4.7893 | 4.7332 | 4.6862 | 4.623 | 4.5464 | 4.4526 | 4.3801 | 4.2607 | 4.1383 | 3.5832 | 3.1801 | 2.5862 | 5.3614 | 5.3022 | 5.2339 | 5.1747 | 5.1002 | 5.0073 | 4.8829 | 4.7869 | 4.6441 | 4.492 | 3.7247 | 3.4278 | 3.292
|  | KNOWL HILL | CF |  |  |  | 4.7645 | 4.7135 | 4.6584 | 4.588 | 4.5441 | 4.4859 | 4.4053 | 4.3114 | 4.2573 | 4.1584 | 3.6502 | 3.192 | 2.7257 | 4.8505 | 4.8128 | 4.7648 | 4.7056 | 4.6679 | 4.6138 | 4.5372 | 4.4515 | 4.3964 | 4.2964 | 3.725 | 2.9648 | 1.6719 | 5.3839 | 5.341 | 5.2859 | 5.2196 | 5.1767 | 5.1196 | 5.0441 | 4.9533 | 4.8992 | 4.8002 | 4.2992 | 3.8227 | 3.3676
BRAMLEY (FLEE) | ALDERSHOT BSP | LABURNUM ROAD | MINIMUM HEADROOM | SU 86017 50475 | YES | 8.194 | 9.1026 | 8.2608 | 6.7465 | 4.922 | 3.5067 | 2.0485 | 0.83321 | -0.41679 | -1.6372 | -2.576 | -6.6627 | -10.5801 | -12.7831 | 15.3975 | 14.8271 | 13.8863 | 12.7495 | 11.9281 | 10.9883 | 10.0955 | 9.122 | 8.1383 | 7.3526 | 3.3628 | -1.7321 | -14.1107 | 9.6199 | 8.8873 | 7.6036 | 6.0169 | 4.8301 | 3.525 | 2.425 | 1.2638 | 0.12709 | -0.73006 | -4.4484 | -7.9188 | -9.8372
|  | LABURNUM ROAD | EE |  |  |  | 9.1026 | 8.2608 | 6.7465 | 4.922 | 3.5067 | 2.0485 | 0.83321 | -0.41679 | -1.6372 | -2.576 | -6.6627 | -9.8178 | -12.4729 | 15.3975 | 14.8271 | 13.8863 | 12.7495 | 11.9281 | 10.9883 | 10.0955 | 9.122 | 8.1383 | 7.3526 | 3.3628 | -0.90965 | -7.5137 | 9.6199 | 8.8873 | 7.6036 | 6.0169 | 4.8301 | 3.525 | 2.425 | 1.2638 | 0.12709 | -0.73006 | -4.4484 | -7.225 | -9.5658
|  | LABURNUM ROAD | HT |  |  |  | 9.3444 | 8.6128 | 7.2424 | 5.6138 | 4.021 | 2.6863 | 1.6057 | 0.91688 | -0.127 | -1.1892 | -6.4494 | -10.5801 | -12.7831 | 15.6669 | 15.2587 | 14.5097 | 13.6271 | 12.7679 | 12.0352 | 11.373 | 10.9914 | 10.3199 | 9.6271 | 6.3832 | 4.2414 | 3.2832 | 9.8873 | 9.2689 | 8.1322 | 6.7587 | 5.4016 | 4.221 | 3.2322 | 2.622 | 1.6577 | 0.68117 | -4.1872 | -7.9188 | -9.8372
|  | LABURNUM ROAD | HE |  |  |  | 9.3301 | 8.622 | 7.272 | 5.6781 | 4.1179 | 2.8281 | 1.8781 | 1.3097 | 0.43525 | -0.47598 | -4.6668 | -7.7729 | -9.1872 | 15.6016 | 15.1455 | 14.3465 | 13.4067 | 12.4822 | 11.6842 | 10.9638 | 10.5097 | 9.7557 | 8.9679 | 4.6852 | 0.31688 | -5.679 | 9.872 | 9.2771 | 8.1628 | 6.823 | 5.5057 | 4.3771 | 3.5087 | 3.0128 | 2.1771 | 1.3352 | -2.5362 | -5.2903 | -6.4433
|  | LABURNUM ROAD | CF |  |  |  | 9.5485 | 9.0026 | 7.9322 | 6.6148 | 5.4312 | 4.4975 | 3.9628 | 3.4506 | 3.2281 | 2.7026 | -0.37904 | -3.5403 | -6.426 | 15.721 | 15.3189 | 14.6475 | 13.8138 | 13.0546 | 12.3832 | 11.7965 | 11.1587 | 10.7526 | 10.0771 | 5.5148 | -1.7321 | -14.1107 | 10.0791 | 9.624 | 8.7679 | 7.6761 | 6.7016 | 5.9006 | 5.4148 | 4.925 | 4.7424 | 4.2608 | 1.3761 | -1.5362 | -4.1443
BRAMLEY (ANDO-THAT) | THATCHAM BSP | LAMBOURN | MINIMUM HEADROOM | SU 33280 78217 | YES | 0.904 | 0.80612 | 12.4851 | 10.9688 | 9.1382 | 7.0045 | 4.5504 | 1.731 | -1.7669 | -4.9741 | -8.2414 | -25.9802 | -32.2588 | -32.4914 | 2.3158 | 13.308 | 12.1529 | 10.7559 | 9.1233 | 7.2457 | 5.1039 | 2.4345 | -0.0042857 | -2.4931 | -16.0124 | -20.7808 | -20.9859 | 1.4622 | 12.5361 | 11.0729 | 9.3065 | 7.2443 | 4.8718 | 2.1494 | -1.2282 | -4.321 | -7.4771 | -24.5976 | -30.6496 | -30.8629
|  | LAMBOURN | EE |  |  |  | 0.80612 | 12.4851 | 10.9688 | 9.1382 | 7.0045 | 4.5504 | 1.731 | -1.7669 | -4.9741 | -8.2414 | -21.0394 | -27.4302 | -29.2343 | 2.3158 | 13.308 | 12.1529 | 10.7559 | 9.1233 | 7.2457 | 5.1039 | 2.4345 | -0.0042857 | -2.4931 | -12.191 | -17.0308 | -18.4135 | 1.4622 | 12.5361 | 11.0729 | 9.3065 | 7.2443 | 4.8718 | 2.1494 | -1.2282 | -4.321 | -7.4771 | -19.8149 | -25.9741 | -27.7016
|  | LAMBOURN | HT |  |  |  | 2.0714 | 14.1973 | 13.2535 | 11.9871 | 10.4606 | 8.6096 | 6.4484 | 3.7504 | 0.82796 | -2.2976 | -15.5731 | -22.7863 | -25.5037 | 3.3913 | 14.7069 | 13.9192 | 12.9498 | 11.7896 | 10.3773 | 8.7396 | 6.6906 | 4.4712 | 2.0927 | -7.9665 | -13.4073 | -15.4329 | 2.5602 | 14.2953 | 13.2922 | 12.0616 | 10.5892 | 8.8004 | 6.7147 | 4.1096 | 1.2902 | -1.7292 | -14.5312 | -21.4812 | -24.0914
|  | LAMBOURN | HE |  |  |  | 1.7776 | 13.7259 | 12.4188 | 10.7514 | 8.7973 | 6.3749 | 3.5371 | -0.064898 | -3.9731 | -7.7904 | -25.9802 | -32.2588 | -32.4914 | 3.1383 | 14.3008 | 13.2671 | 11.9957 | 10.5059 | 8.6518 | 6.4937 | 3.7416 | 0.75694 | -2.1563 | -16.0124 | -20.7808 | -20.9859 | 2.4122 | 13.7871 | 12.4739 | 10.8667 | 8.982 | 6.6382 | 3.8973 | 0.41878 | -3.3557 | -7.0424 | -24.5976 | -30.6496 | -30.8629
|  | LAMBOURN | CF |  |  |  | 2.6041 | 15.1637 | 14.5667 | 13.8412 | 12.98 | 11.8769 | 10.6259 | 8.9076 | 6.9616 | 4.879 | -7.4904 | -18.6231 | -25.471 | 3.6617 | 15.4233 | 15.0182 | 14.408 | 13.6967 | 12.8498 | 11.8947 | 10.5784 | 9.0835 | 7.4896 | -1.9747 | -10.491 | -15.7645 | 2.8735 | 14.928 | 14.5841 | 13.9208 | 13.0198 | 11.9535 | 10.7453 | 9.0861 | 7.2014 | 5.1912 | -6.7527 | -17.4955 | -24.0935
FAWLEY GSP | LANGLEY BSP | LANGLEY | MINIMUM HEADROOM | SU 45158 01418 | YES | 1.073 | 5.7872 | 5.6719 | 5.5566 | 5.2689 | 5.0464 | 4.2291 | 3.4321 | 2.725 | 1.2964 | -0.068878 | -4.5781 | -8.4158 | -12.0434 | 1.8949 | 1.7622 | 1.6337 | 1.2745 | 1.0602 | 0.18673 | -0.35714 | -0.83367 | -2.5765 | -3.8551 | -7.7786 | -12.0286 | -17.5592 | 2.8327 | 2.6163 | 2.4082 | 2.05 | 1.7816 | 0.84082 | 0.13673 | -0.57653 | -2.3653 | -3.8296 | -8.498 | -12.7184 | -16.9112
|  | LANGLEY | EE |  |  |  | 5.7872 | 5.6719 | 5.5566 | 5.2689 | 5.2423 | 4.7699 | 4.0526 | 3.323 | 2.2587 | 1.4842 | -2.0434 | -6.827 | -9.2077 | 1.8949 | 1.7622 | 1.6337 | 1.4765 | 1.4439 | 1.0837 | 0.62347 | 0.29082 | -0.41122 | -0.89592 | -3.9367 | -9.351 | -12.9173 | 2.8327 | 2.6163 | 2.4082 | 2.1531 | 2.1112 | 1.6735 | 1.0071 | 0.41531 | -0.56327 | -1.2878 | -5.0459 | -10.4296 | -12.8837
|  | LANGLEY | HT |  |  |  | 5.8556 | 5.7689 | 5.625 | 5.3321 | 5.1434 | 4.4219 | 3.4321 | 2.725 | 1.9423 | 0.94133 | -3.425 | -8.127 | -11.2781 | 1.9622 | 1.8633 | 1.7071 | 1.4561 | 1.3592 | 0.66939 | 0.04898 | -0.48673 | -0.85816 | -1.652 | -4.7551 | -9.0204 | -12.0204 | 2.9163 | 2.7265 | 2.4745 | 2.1224 | 1.9357 | 1.1316 | 0.19184 | -0.57653 | -1.2592 | -2.2949 | -6.7143 | -11.8969 | -15.398
|  | LANGLEY | HE |  |  |  | 5.8566 | 5.7699 | 5.6066 | 5.2913 | 5.0464 | 4.2291 | 3.5158 | 3.023 | 1.2964 | -0.068878 | -4.5781 | -8.4158 | -12.0434 | 1.9541 | 1.8459 | 1.6459 | 1.2745 | 1.0602 | 0.18673 | -0.35714 | -0.83367 | -2.5765 | -3.8551 | -7.7786 | -12.0286 | -17.5592 | 2.9306 | 2.7592 | 2.4939 | 2.05 | 1.7816 | 0.84082 | 0.13673 | -0.43673 | -2.3653 | -3.8296 | -8.498 | -12.7184 | -16.9112
|  | LANGLEY | CF |  |  |  | 5.8985 | 5.8485 | 5.7985 | 5.7372 | 5.6117 | 5.4791 | 5.2801 | 4.9995 | 4.6607 | 4.6495 | 1.8413 | -1.3872 | -4.1679 | 1.9908 | 1.9184 | 1.8449 | 1.7582 | 1.5837 | 1.3898 | 1.1245 | 0.87347 | 0.59796 | 0.42347 | -2.0929 | -6.4408 | -12.5898 | 3.0102 | 2.9153 | 2.8224 | 2.7102 | 2.5194 | 2.3306 | 2.0561 | 1.7969 | 1.5041 | 1.4184 | -1.1939 | -4.6469 | -7.6082
BRAMLEY (FLEE) | FERNHURST | LANGLEY COURT | MINIMUM HEADROOM | SU 80847 29056 | YES | 7.371 | 12.2218 | 7.9902 | 7.6882 | 7.4116 | 7.0443 | 6.6535 | 6.579 | 6.0943 | 5.6024 | 5.2453 | 3.3606 | 1.9433 | 1.0157 | 14.6835 | 10.5202 | 10.2896 | 10.0886 | 9.812 | 9.5222 | 9.5049 | 9.159 | 8.7998 | 8.5478 | 7.1467 | 5.4947 | 1.5273 | 12.8667 | 8.6504 | 8.3606 | 8.0963 | 7.7545 | 7.3933 | 7.3259 | 6.8688 | 6.4055 | 6.079 | 4.4076 | 3.1984 | 2.4086
|  | LANGLEY COURT | EE |  |  |  | 12.2218 | 7.9902 | 7.6882 | 7.4116 | 7.0443 | 6.6535 | 6.579 | 6.0943 | 5.6024 | 5.2453 | 3.3606 | 2.1341 | 1.2565 | 14.6835 | 10.5202 | 10.2896 | 10.0886 | 9.812 | 9.5222 | 9.5049 | 9.159 | 8.7998 | 8.5478 | 7.1467 | 5.7304 | 3.708 | 12.8667 | 8.6504 | 8.3606 | 8.0963 | 7.7545 | 7.3933 | 7.3259 | 6.8688 | 6.4055 | 6.079 | 4.4076 | 3.3545 | 2.6055
|  | LANGLEY COURT | HT |  |  |  | 12.3576 | 8.1688 | 7.9239 | 7.7127 | 7.4269 | 7.1718 | 6.7494 | 6.281 | 5.779 | 5.6831 | 3.4024 | 1.9433 | 1.0157 | 14.8151 | 10.7029 | 10.5529 | 10.4253 | 10.2427 | 10.0906 | 9.8437 | 9.561 | 9.2488 | 9.2641 | 7.9804 | 7.2661 | 6.8304 | 13.0035 | 8.8259 | 8.5984 | 8.4004 | 8.1351 | 7.8994 | 7.5045 | 7.0678 | 6.5963 | 6.5351 | 4.4616 | 3.1984 | 2.4086
|  | LANGLEY COURT | HE |  |  |  | 12.3514 | 8.1698 | 7.9729 | 7.7371 | 7.4647 | 7.228 | 6.8535 | 6.4341 | 5.982 | 5.9433 | 3.7759 | 2.5647 | 1.9973 | 14.7876 | 10.6702 | 10.5263 | 10.3539 | 10.1539 | 9.9794 | 9.7161 | 9.411 | 9.0722 | 9.0631 | 7.3702 | 5.9406 | 4.0722 | 12.9973 | 8.828 | 8.6443 | 8.4208 | 8.1678 | 7.9473 | 7.5973 | 7.2014 | 6.7729 | 6.7616 | 4.7871 | 3.7453 | 3.2759
|  | LANGLEY COURT | CF |  |  |  | 12.4759 | 8.3463 | 8.178 | 8.0341 | 7.8443 | 7.6371 | 7.479 | 7.2494 | 6.9984 | 6.7259 | 5.6259 | 4.1994 | 2.8127 | 14.8508 | 10.7498 | 10.6131 | 10.4957 | 10.3324 | 10.1549 | 9.9967 | 9.7641 | 9.5141 | 9.2416 | 7.8845 | 5.4947 | 1.5273 | 13.1045 | 8.9831 | 8.828 | 8.6953 | 8.5178 | 8.3249 | 8.1759 | 7.9565 | 7.7218 | 7.4688 | 6.4422 | 5.1524 | 3.9494
AXMINSTER | YEOVIL BSP | LARKHILL | MINIMUM HEADROOM | ST 53677 16914 | YES | 8.327 | 12.0448 | 11.7162 | 11.3009 | 11.1693 | 10.7693 | 10.3448 | 9.5621 | 8.6948 | 7.8366 | 7.1836 | 3.2244 | 0.3305 | -1.4205 | 14.0968 | 13.8142 | 13.455 | 13.3366 | 12.9611 | 12.5529 | 11.9836 | 11.3305 | 10.6621 | 10.1846 | 7.3478 | 3.1254 | -6.6175 | 11.8815 | 11.5499 | 11.0836 | 10.9927 | 10.5754 | 10.1254 | 9.3795 | 8.5274 | 7.6744 | 7.1111 | 3.8713 | 1.4336 | -0.019502
|  | LARKHILL | EE |  |  |  | 12.0448 | 11.7162 | 11.3009 | 11.1693 | 10.7693 | 10.3448 | 9.5621 | 8.6948 | 7.8366 | 7.1836 | 3.6121 | 0.94274 | -1.1246 | 14.0968 | 13.8142 | 13.455 | 13.3366 | 12.9611 | 12.5529 | 11.9836 | 11.3305 | 10.6621 | 10.1846 | 7.3478 | 4.0866 | -1.0328 | 11.8815 | 11.5499 | 11.0836 | 10.9927 | 10.5754 | 10.1254 | 9.3795 | 8.5274 | 7.6744 | 7.1111 | 4.1448 | 1.956 | 0.22029
|  | LARKHILL | HT |  |  |  | 12.2193 | 11.9285 | 11.5876 | 11.2723 | 10.8948 | 10.4836 | 10.0468 | 9.2693 | 8.4703 | 7.654 | 3.2244 | 0.3305 | -1.4205 | 14.3009 | 14.1274 | 13.9009 | 13.6938 | 13.4325 | 13.1407 | 13.0111 | 12.5887 | 12.1427 | 11.6764 | 9.3672 | 8.1162 | 7.3938 | 12.0764 | 11.8091 | 11.4795 | 11.1734 | 10.8029 | 10.3876 | 10.0478 | 9.3376 | 8.5978 | 7.8387 | 3.8713 | 1.4336 | -0.019502
|  | LARKHILL | HE |  |  |  | 12.2315 | 11.9734 | 11.6642 | 11.3825 | 11.0366 | 10.6642 | 10.3805 | 9.7591 | 9.1193 | 8.4621 | 4.3223 | 1.9825 | 0.71927 | 14.2621 | 14.054 | 13.7927 | 13.5438 | 13.2244 | 12.8734 | 12.7029 | 12.2295 | 11.7193 | 11.1825 | 7.9774 | 4.6713 | -0.24807 | 12.0856 | 11.8448 | 11.5448 | 11.2672 | 10.9274 | 10.5468 | 10.1999 | 9.6091 | 8.8601 | 8.0652 | 4.1785 | 2.0519 | 0.8958
|  | LARKHILL | CF |  |  |  | 12.3815 | 12.2295 | 12.0774 | 11.8948 | 11.7407 | 11.5366 | 11.2968 | 11.3183 | 11.0683 | 10.807 | 8.2999 | 5.2856 | 2.8989 | 14.3336 | 14.155 | 13.9764 | 13.7519 | 13.5234 | 13.2213 | 12.8591 | 12.704 | 12.2958 | 11.8601 | 8.5285 | 3.1254 | -6.6175 | 12.2203 | 12.0662 | 11.9193 | 11.7315 | 11.5642 | 11.3183 | 11.0376 | 11.0509 | 10.7223 | 10.3703 | 7.8366 | 5.0499 | 2.8795
COWLEY GSP | WITNEY BSP | LEAFIELD | MINIMUM HEADROOM | SP 30282 15270 | YES | 0.091 | 2.6214 | 2.4888 | 2.3663 | 2.202 | 2.0184 | 1.8765 | 1.5939 | 1.2714 | 0.95 | 0.76327 | 0.18265 | -0.61224 | -1.0969 | 3.398 | 3.2939 | 3.1888 | 3.05 | 2.8939 | 2.7745 | 2.5622 | 2.3133 | 2.0582 | 1.9316 | 1.6194 | 0.72755 | -1.4184 | 2.6082 | 2.4786 | 2.3612 | 2.201 | 2.0204 | 1.8918 | 1.6184 | 1.2949 | 0.97143 | 0.80612 | 0.38163 | -0.30714 | -0.72449
|  | LEAFIELD | EE |  |  |  | 2.6214 | 2.4888 | 2.3663 | 2.202 | 2.0184 | 1.8765 | 1.5939 | 1.2714 | 0.95 | 0.76327 | 0.18265 | -0.49184 | -0.99898 | 3.398 | 3.2939 | 3.1888 | 3.05 | 2.8939 | 2.7745 | 2.5622 | 2.3133 | 2.0582 | 1.9316 | 1.6194 | 0.87551 | -0.25408 | 2.6082 | 2.4786 | 2.3612 | 2.201 | 2.0204 | 1.8918 | 1.6184 | 1.2949 | 0.97143 | 0.80612 | 0.38163 | -0.19898 | -0.64082
|  | LEAFIELD | HT |  |  |  | 2.6888 | 2.5867 | 2.4888 | 2.3694 | 2.2673 | 2.1286 | 1.8888 | 1.6704 | 1.4 | 1.1214 | 0.18265 | -0.61224 | -1.0969 | 3.4684 | 3.398 | 3.3357 | 3.251 | 3.1857 | 3.0837 | 2.9347 | 2.8102 | 2.6388 | 2.4582 | 2.0806 | 1.7265 | 1.5286 | 2.6765 | 2.5786 | 2.4857 | 2.3735 | 2.2796 | 2.1449 | 1.9194 | 1.7184 | 1.4643 | 1.2031 | 0.38673 | -0.30714 | -0.72449
|  | LEAFIELD | HE |  |  |  | 2.6867 | 2.5908 | 2.499 | 2.3867 | 2.2949 | 2.1612 | 1.9561 | 1.7714 | 1.5367 | 1.2939 | 0.47143 | -0.18776 | -0.52551 | 3.4592 | 3.3837 | 3.3082 | 3.2163 | 3.1429 | 3.0296 | 2.8786 | 2.7469 | 2.5663 | 2.3724 | 1.7673 | 1.0143 | -0.043878 | 2.6735 | 2.5816 | 2.4949 | 2.3878 | 2.3031 | 2.1735 | 1.9816 | 1.8112 | 1.5867 | 1.3561 | 0.64082 | 0.07551 | -0.21735
|  | LEAFIELD | CF |  |  |  | 2.7245 | 2.6622 | 2.6041 | 2.5265 | 2.4367 | 2.3806 | 2.2806 | 2.1592 | 2.0296 | 1.9408 | 1.0816 | 0.73163 | 0.05102 | 3.4786 | 3.4214 | 3.3612 | 3.2888 | 3.201 | 3.1327 | 3.0235 | 2.8929 | 2.749 | 2.6429 | 1.6643 | 0.72755 | -1.4184 | 2.7112 | 2.648 | 2.5918 | 2.5194 | 2.4327 | 2.3786 | 2.2816 | 2.1633 | 2.0347 | 1.9571 | 1.1041 | 0.85204 | 0.28265
WILLESDEN GSP | ACTON LANE | LEAMINGTON PARK | MINIMUM HEADROOM | TQ 20539 81536 | YES | 3.956 | 41.1068 | 39.6874 | 37.7027 | 35.4384 | 33.4476 | 31.0333 | 30.069 | 29.0486 | 28.0568 | 27.1476 | 26.0966 | 24.5813 | 23.1456 | 41.8331 | 40.9515 | 39.7872 | 38.475 | 37.2739 | 35.876 | 34.8362 | 33.7188 | 32.6597 | 31.6505 | 28.8964 | 26.2607 | 19.4903 | 43.2893 | 42.1342 | 40.4903 | 38.5852 | 36.8576 | 34.7484 | 33.7199 | 32.6219 | 31.5821 | 30.5954 | 29.0148 | 27.4219 | 26.1331
|  | LEAMINGTON PARK | EE |  |  |  | 41.1068 | 39.8558 | 37.7742 | 35.4588 | 33.4476 | 31.0466 | 30.069 | 29.0486 | 28.0568 | 27.1476 | 26.0966 | 25.1507 | 23.6221 | 41.8331 | 41.1444 | 39.8342 | 38.475 | 37.2739 | 35.876 | 34.8362 | 33.7188 | 32.6597 | 31.6505 | 28.8964 | 26.4668 | 22.2842 | 43.2893 | 42.3148 | 40.5688 | 38.6321 | 36.8617 | 34.7607 | 33.7199 | 32.6219 | 31.5821 | 30.5954 | 29.0148 | 28.1046 | 26.7137
|  | LEAMINGTON PARK | HT |  |  |  | 41.2027 | 39.6874 | 37.7027 | 35.4384 | 33.467 | 31.0333 | 30.0721 | 29.0752 | 28.219 | 27.4323 | 26.1221 | 24.5813 | 23.1456 | 41.9433 | 40.9515 | 39.7872 | 38.5229 | 37.4015 | 36.0607 | 35.1342 | 34.1321 | 33.2688 | 32.4811 | 30.4678 | 29.1505 | 28.128 | 43.4137 | 42.1342 | 40.4903 | 38.5852 | 36.8576 | 34.7484 | 33.7484 | 32.6862 | 31.7821 | 30.9668 | 29.0382 | 27.4219 | 26.1331
|  | LEAMINGTON PARK | HE |  |  |  | 41.1935 | 39.9721 | 37.9384 | 35.6772 | 33.7384 | 31.4099 | 30.6354 | 29.7476 | 28.9588 | 28.1935 | 27.2201 | 26.3099 | 25.2721 | 41.9025 | 41.2393 | 39.9668 | 38.6525 | 37.5107 | 36.1739 | 35.3311 | 34.3515 | 33.5076 | 32.6658 | 29.9495 | 27.4933 | 23.5178 | 43.4025 | 42.4729 | 40.7842 | 38.878 | 37.1903 | 35.1739 | 34.3658 | 33.4239 | 32.627 | 31.8586 | 30.378 | 29.4627 | 28.4852
|  | LEAMINGTON PARK | CF |  |  |  | 41.3139 | 40.4027 | 39.0293 | 37.168 | 35.6986 | 34.0272 | 33.3303 | 32.4476 | 31.5946 | 30.7058 | 27.6905 | 27.1803 | 27.018 | 41.9556 | 41.4311 | 40.6801 | 39.478 | 38.527 | 37.4566 | 36.6586 | 35.7005 | 34.7688 | 33.8168 | 30.1974 | 26.2607 | 19.4903 | 43.4995 | 42.7974 | 41.7546 | 40.2056 | 38.9168 | 37.4556 | 36.7331 | 35.8321 | 34.9729 | 34.0893 | 31.3178 | 30.5025 | 30.225
MINETY GSP | STRATTON (2 X 60) | LECHLADE | MINIMUM HEADROOM | SP 22074 00496 | YES | 0.64 | 5.1571 | 5.0163 | 4.8786 | 4.7 | 4.501 | 4.3408 | 4.0429 | 3.702 | 3.3612 | 3.152 | 2.0776 | 1.398 | 1.0398 | 6.4337 | 6.3255 | 6.2184 | 6.0735 | 5.9153 | 5.7816 | 5.5612 | 5.299 | 5.0337 | 4.8857 | 4.1082 | 3.1133 | 0.70102 | 5.2092 | 5.0694 | 4.9337 | 4.752 | 4.552 | 4.3939 | 4.1041 | 3.7663 | 3.4296 | 3.2459 | 2.3704 | 1.8031 | 1.5643
|  | LECHLADE | EE |  |  |  | 5.1571 | 5.0163 | 4.8786 | 4.7 | 4.501 | 4.3408 | 4.0429 | 3.702 | 3.3612 | 3.152 | 2.0969 | 1.398 | 1.1959 | 6.4337 | 6.3255 | 6.2184 | 6.0735 | 5.9153 | 5.7816 | 5.5612 | 5.299 | 5.0337 | 4.8857 | 4.1082 | 3.2704 | 2.3051 | 5.2092 | 5.0694 | 4.9337 | 4.752 | 4.552 | 4.3939 | 4.1041 | 3.7663 | 3.4296 | 3.2459 | 2.3796 | 1.8031 | 1.6929
|  | LECHLADE | HT |  |  |  | 5.2194 | 5.1082 | 4.998 | 4.8684 | 4.75 | 4.5929 | 4.3388 | 4.098 | 3.8122 | 3.5112 | 2.0776 | 1.5592 | 1.0398 | 6.502 | 6.4296 | 6.3602 | 6.2704 | 6.201 | 6.0929 | 5.9469 | 5.8092 | 5.6306 | 5.4378 | 4.5969 | 4.5153 | 4.2939 | 5.2878 | 5.1786 | 5.0765 | 4.949 | 4.8378 | 4.6837 | 4.4469 | 4.2306 | 3.9622 | 3.6776 | 2.3704 | 1.9857 | 1.5643
|  | LECHLADE | HE |  |  |  | 5.2214 | 5.1194 | 5.0173 | 4.8959 | 4.7929 | 4.652 | 4.4378 | 4.1929 | 3.9898 | 3.7367 | 2.4408 | 1.752 | 1.7133 | 6.4908 | 6.4133 | 6.3337 | 6.2347 | 6.1551 | 6.0378 | 5.8857 | 5.7051 | 5.5561 | 5.3592 | 4.3122 | 3.4602 | 2.5735 | 5.2878 | 5.1857 | 5.0898 | 4.9735 | 4.8735 | 4.7357 | 4.5327 | 4.298 | 4.1122 | 3.8673 | 2.6908 | 2.1265 | 2.1745
|  | LECHLADE | CF |  |  |  | 5.2633 | 5.1949 | 5.1276 | 5.0469 | 4.9582 | 4.8561 | 4.7878 | 4.6592 | 4.5224 | 4.4276 | 3.498 | 2.6622 | 1.9449 | 6.5173 | 6.448 | 6.3867 | 6.3133 | 6.2235 | 6.1194 | 6.0367 | 5.901 | 5.749 | 5.6296 | 4.5643 | 3.1133 | 0.70102 | 5.3265 | 5.2571 | 5.1908 | 5.1051 | 5.0163 | 4.9153 | 4.848 | 4.7173 | 4.5755 | 4.4867 | 3.5735 | 2.849 | 2.2724
BRAMLEY (ANDO-THAT) | THATCHAM BSP | LECKHAMPSTEAD | MINIMUM HEADROOM | SU 43962 77635 | YES | 0.106 | 3.5971 | 3.4961 | 3.3604 | 3.2512 | 3.0941 | 2.9237 | 2.7686 | 2.5329 | 2.2961 | 2.1808 | 1.6573 | 1.3767 | 1.2441 | 4.3832 | 4.3107 | 4.2077 | 4.126 | 4.0046 | 3.8719 | 3.7587 | 3.577 | 3.3944 | 3.3087 | 2.8883 | 2.225 | 0.78929 | 3.9716 | 3.8778 | 3.7471 | 3.642 | 3.49 | 3.3267 | 3.1778 | 2.9482 | 2.7227 | 2.6145 | 2.0522 | 1.7747 | 1.6267
|  | LECKHAMPSTEAD | EE |  |  |  | 3.5971 | 3.4961 | 3.3604 | 3.2512 | 3.0941 | 2.9237 | 2.7686 | 2.5329 | 2.2961 | 2.1808 | 1.6573 | 1.4859 | 1.4247 | 4.3832 | 4.3107 | 4.2077 | 4.126 | 4.0046 | 3.8719 | 3.7587 | 3.577 | 3.3944 | 3.3087 | 2.8883 | 2.4811 | 1.8219 | 3.9716 | 3.8778 | 3.7471 | 3.642 | 3.49 | 3.3267 | 3.1778 | 2.9482 | 2.7227 | 2.6145 | 2.14 | 1.989 | 1.9318
|  | LECKHAMPSTEAD | HT |  |  |  | 3.6808 | 3.5941 | 3.5073 | 3.4084 | 3.292 | 3.2063 | 3.0522 | 2.8778 | 2.69 | 2.5573 | 1.7788 | 1.5155 | 1.341 | 4.4556 | 4.3995 | 4.3474 | 4.2821 | 4.2046 | 4.1485 | 4.0515 | 3.9342 | 3.8066 | 3.7209 | 3.2209 | 3.0689 | 2.9883 | 4.0533 | 3.9727 | 3.8941 | 3.7982 | 3.6869 | 3.6063 | 3.4614 | 3.2931 | 3.1145 | 2.988 | 2.2512 | 2.0104 | 1.8553
|  | LECKHAMPSTEAD | HE |  |  |  | 3.6778 | 3.59 | 3.5053 | 3.4073 | 3.2961 | 3.2104 | 3.0604 | 2.89 | 2.7043 | 2.5737 | 1.6624 | 1.3767 | 1.2441 | 4.4454 | 4.3852 | 4.325 | 4.2515 | 4.1658 | 4.1005 | 3.9954 | 3.8658 | 3.7219 | 3.626 | 2.9444 | 2.5138 | 1.8577 | 4.0492 | 3.9696 | 3.892 | 3.7971 | 3.692 | 3.6104 | 3.4676 | 3.2982 | 3.1206 | 2.9492 | 2.0522 | 1.7747 | 1.6267
|  | LECKHAMPSTEAD | CF |  |  |  | 3.6982 | 3.6298 | 3.5369 | 3.4737 | 3.392 | 3.2961 | 3.1941 | 3.1165 | 2.9951 | 2.8665 | 2.2359 | 1.8359 | 1.4584 | 4.4597 | 4.4097 | 4.3413 | 4.2934 | 4.225 | 4.1474 | 4.0536 | 3.9821 | 3.8699 | 3.7526 | 3.0781 | 2.225 | 0.78929 | 4.0696 | 4.0073 | 3.9216 | 3.8635 | 3.7859 | 3.6931 | 3.5951 | 3.5237 | 3.4073 | 3.2839 | 2.6778 | 2.1992 | 1.8471
LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | LEE-ON-SOLENT | MINIMUM HEADROOM | SU 56858 00293 | YES | 10.551 | 7.8588 | 7.2516 | 6.4486 | 6.0659 | 5.2465 | 4.4792 | 0.27858 | -0.84183 | -1.9112 | -2.5847 | -6.3541 | -9.352 | -11.1255 | 9.6673 | 9.2133 | 8.5479 | 8.2714 | 7.6265 | 7.0082 | 3.1525 | 2.2974 | 1.4514 | 0.89327 | -2.1445 | -7.6333 | -19.3649 | 7.8935 | 7.3414 | 6.5782 | 6.2782 | 5.523 | 4.8037 | 0.71735 | -0.33163 | -1.3408 | -1.9459 | -5.1857 | -7.801 | -9.2265
|  | LEE-ON-SOLENT | EE |  |  |  | 7.8588 | 7.2516 | 6.4486 | 6.0659 | 5.2465 | 4.4792 | 0.27858 | -0.84183 | -1.9112 | -2.5847 | -5.9031 | -8.6082 | -10.8541 | 9.6673 | 9.2133 | 8.5479 | 8.2714 | 7.6265 | 7.0082 | 3.1525 | 2.2974 | 1.4514 | 0.89327 | -2.1445 | -5.9578 | -12.2037 | 7.8935 | 7.3414 | 6.5782 | 6.2782 | 5.523 | 4.8037 | 0.71735 | -0.33163 | -1.3408 | -1.9459 | -4.8173 | -7.148 | -8.9929
|  | LEE-ON-SOLENT | HT |  |  |  | 8.0465 | 7.3843 | 6.8139 | 6.1863 | 5.3914 | 4.5271 | 0.68062 | -0.30612 | -1.2714 | -2.099 | -6.3541 | -9.352 | -11.1255 | 9.853 | 9.4184 | 9.0663 | 8.6775 | 8.1663 | 7.5704 | 4.1433 | 3.6025 | 3.0474 | 2.5494 | 0.25245 | -1.0955 | -1.8078 | 8.1098 | 7.5302 | 7.0108 | 6.4302 | 5.7067 | 4.9077 | 1.2235 | 0.33368 | -0.54489 | -1.3112 | -5.1857 | -7.801 | -9.2265
|  | LEE-ON-SOLENT | HE |  |  |  | 8.0598 | 7.5465 | 6.9057 | 6.319 | 5.573 | 5.2098 | 1.2612 | 0.43266 | -0.37449 | -1.0714 | -4.5214 | -7.199 | -8.6071 | 9.7959 | 9.4347 | 8.9143 | 8.4653 | 7.8969 | 7.5939 | 3.9157 | 3.3004 | 2.6576 | 2.0269 | -1.4322 | -5.2914 | -11.1945 | 8.119 | 7.6669 | 7.0853 | 6.5394 | 5.8598 | 5.5833 | 1.7449 | 0.99184 | 0.25715 | -0.40204 | -3.5561 | -5.8704 | -6.9918
|  | LEE-ON-SOLENT | CF |  |  |  | 8.2057 | 7.822 | 7.4006 | 6.8894 | 6.323 | 5.8169 | 2.2418 | 2.1622 | 1.7235 | 1.3816 | -1.1265 | -3.751 | -6.1949 | 9.8561 | 9.5357 | 9.15 | 8.6541 | 8.1418 | 7.651 | 4.0627 | 3.7912 | 3.2412 | 2.6963 | -1.2445 | -7.6333 | -19.3649 | 8.2537 | 7.9179 | 7.522 | 7.0598 | 6.5435 | 6.0751 | 2.5531 | 2.5449 | 2.1255 | 1.7827 | -0.64183 | -2.9459 | -5.0143
LOVEDEAN GSP | HAVANT | LEIGH PARK | MINIMUM HEADROOM | SU 72144 07875 | YES | 3.121 | 13.4945 | 13.1354 | 12.5619 | 12.2925 | 11.6996 | 11.0252 | 9.9711 | 8.8374 | 7.7415 | 6.8476 | 1.867 | -1.2238 | -2.3095 | 17.6935 | 17.3843 | 16.8894 | 16.6762 | 16.169 | 15.566 | 14.7956 | 13.9354 | 13.0782 | 12.3996 | 8.1068 | 2.8976 | -9.1197 | 15.0221 | 14.6639 | 14.0945 | 13.8639 | 13.2884 | 12.6313 | 11.6354 | 10.4772 | 9.3405 | 8.5364 | 4.3456 | 1.619 | 0.75372
|  | LEIGH PARK | EE |  |  |  | 13.4945 | 13.1354 | 12.5619 | 12.2925 | 11.6996 | 11.0252 | 9.9711 | 8.8374 | 7.7415 | 6.8476 | 1.9966 | -0.51362 | -1.3136 | 17.6935 | 17.3843 | 16.8894 | 16.6762 | 16.169 | 15.566 | 14.7956 | 13.9354 | 13.0782 | 12.3996 | 8.1068 | 4.2547 | -1.4973 | 15.0221 | 14.6639 | 14.0945 | 13.8639 | 13.2884 | 12.6313 | 11.6354 | 10.4772 | 9.3405 | 8.5364 | 4.3558 | 2.2384 | 1.5588
|  | LEIGH PARK | HT |  |  |  | 13.7037 | 13.3466 | 12.9109 | 12.4425 | 11.8568 | 11.2129 | 10.5925 | 9.6639 | 8.7252 | 7.6262 | 1.867 | -1.2238 | -2.3095 | 17.9364 | 17.6864 | 17.4007 | 17.1129 | 16.7037 | 16.2354 | 15.968 | 15.4211 | 14.8629 | 14.1649 | 10.8088 | 9.2629 | 8.6792 | 15.2384 | 14.9068 | 14.5068 | 14.0792 | 13.5262 | 12.9129 | 12.3966 | 11.5354 | 10.6527 | 9.6241 | 4.3456 | 1.619 | 0.75372
|  | LEIGH PARK | HE |  |  |  | 13.6966 | 13.4231 | 12.9731 | 12.5721 | 12.0629 | 11.4731 | 10.9129 | 10.0517 | 9.1894 | 8.3129 | 3.468 | 1.0435 | 0.2027 | 17.8792 | 17.6456 | 17.2588 | 16.9384 | 16.5119 | 15.9894 | 15.6241 | 14.969 | 14.2894 | 13.5813 | 8.9721 | 5.0323 | -0.65954 | 15.2313 | 14.9782 | 14.5578 | 14.1894 | 13.7149 | 13.1527 | 12.6956 | 11.8935 | 11.0843 | 10.2568 | 5.7986 | 3.7088 | 3.0374
|  | LEIGH PARK | CF |  |  |  | 13.8762 | 13.7313 | 13.5966 | 13.3292 | 13.1272 | 12.8762 | 12.5476 | 12.1241 | 11.9884 | 11.5752 | 8.7456 | 4.866 | 1.6343 | 17.9731 | 17.7792 | 17.5782 | 17.2578 | 16.9711 | 16.6007 | 16.1241 | 15.5476 | 15.2262 | 14.6252 | 10.3874 | 2.8976 | -9.1197 | 15.3966 | 15.2588 | 15.1262 | 14.8609 | 14.6721 | 14.4252 | 14.1058 | 13.6884 | 13.6007 | 13.1986 | 10.4262 | 6.9741 | 4.1956
BRAMLEY (FLEE) | READING BSP | LITTLE HUNGERFORD | MINIMUM HEADROOM | SU 75372 72019 | YES | 3.167 | 12.4033 | 11.9676 | 11.189 | 10.3023 | 9.3472 | 8.2135 | 6.487 | 4.5992 | 2.7635 | 1.4808 | -5.2222 | -10.1845 | -12.3743 | 18.4666 | 18.1502 | 17.5145 | 16.79 | 15.9951 | 15.0298 | 13.7982 | 12.4104 | 11.0298 | 10.1278 | 5.3972 | -1.1937 | -16.2865 | 12.9339 | 12.541 | 11.8135 | 10.987 | 10.0635 | 8.9319 | 7.2941 | 5.4808 | 3.7063 | 2.5574 | -3.16 | -7.5426 | -9.3181
|  | LITTLE HUNGERFORD | EE |  |  |  | 12.4033 | 11.9676 | 11.189 | 10.3023 | 9.3472 | 8.2135 | 6.487 | 4.5992 | 2.7635 | 1.4808 | -4.811 | -9.2722 | -11.2049 | 18.4666 | 18.1502 | 17.5145 | 16.79 | 15.9951 | 15.0298 | 13.7982 | 12.4104 | 11.0298 | 10.1278 | 5.3972 | 0.28084 | -7.1375 | 12.9339 | 12.541 | 11.8135 | 10.987 | 10.0635 | 8.9319 | 7.2941 | 5.4808 | 3.7063 | 2.5574 | -2.9059 | -6.7722 | -8.4008
|  | LITTLE HUNGERFORD | HT |  |  |  | 12.7717 | 12.1104 | 11.3635 | 10.9217 | 10.0645 | 9.1023 | 7.6278 | 6.04 | 4.4166 | 2.7849 | -5.2222 | -10.1845 | -12.3743 | 18.9114 | 18.4972 | 17.9961 | 17.8104 | 17.2206 | 16.5533 | 15.7247 | 14.7992 | 13.841 | 12.8686 | 8.5257 | 6.2635 | 5.3002 | 13.3329 | 12.7217 | 12.0257 | 11.6533 | 10.8359 | 9.9278 | 8.5849 | 7.1247 | 5.6329 | 4.1298 | -3.16 | -7.5426 | -9.3181
|  | LITTLE HUNGERFORD | HE |  |  |  | 12.7921 | 12.2502 | 11.5635 | 11.1921 | 10.49 | 9.6084 | 8.3114 | 6.9023 | 5.4829 | 4.0349 | -2.7692 | -7.2243 | -8.9794 | 18.8237 | 18.3788 | 17.8104 | 17.5543 | 16.9768 | 16.2268 | 15.3023 | 14.2666 | 13.1859 | 12.0594 | 6.2604 | 0.9788 | -6.3008 | 13.34 | 12.8196 | 12.1798 | 11.8676 | 11.2217 | 10.3849 | 9.1849 | 7.8747 | 6.5451 | 5.1839 | -1.0783 | -5.009 | -6.4661
|  | LITTLE HUNGERFORD | CF |  |  |  | 13.1941 | 12.9431 | 12.5482 | 12.0798 | 11.987 | 11.4961 | 10.8829 | 10.1931 | 9.4808 | 8.7635 | 3.8706 | -1.2671 | -5.9212 | 19.0206 | 18.6972 | 18.2523 | 17.7461 | 17.5839 | 17.0145 | 16.2992 | 15.4768 | 14.6196 | 13.7227 | 7.6023 | -1.1937 | -16.2865 | 13.689 | 13.4288 | 13.0584 | 12.6319 | 12.5808 | 12.1461 | 11.5676 | 10.8798 | 10.1645 | 9.4421 | 4.688 | 0.15533 | -3.8804
COWLEY GSP | HIGH WYCOMBE BSP | LITTLE MARLOW | MINIMUM HEADROOM | SU 86037 87794 | YES | 4.555 | 6.5673 | 6.2041 | 5.6929 | 5.4908 | 4.9745 | 4.4112 | 3.5673 | 2.6204 | 1.6694 | 0.98265 | -3.0857 | -6.2306 | -7.9939 | 11.5122 | 11.2571 | 10.9061 | 10.7612 | 10.399 | 10.002 | 9.452 | 8.7745 | 8.0663 | 7.5857 | 4.7449 | 0.85714 | -8.1296 | 5.8367 | 5.4949 | 5.0112 | 4.8408 | 4.3541 | 3.8296 | 3.0439 | 2.1571 | 1.2663 | 0.64388 | -2.9582 | -5.7469 | -7.2735
|  | LITTLE MARLOW | EE |  |  |  | 6.5673 | 6.2041 | 5.6929 | 5.4908 | 4.9745 | 4.4112 | 3.5673 | 2.6204 | 1.6694 | 0.98265 | -2.7418 | -5.5602 | -7.6888 | 11.5122 | 11.2571 | 10.9061 | 10.7612 | 10.399 | 10.002 | 9.452 | 8.7745 | 8.0663 | 7.5857 | 4.7449 | 1.452 | -3.3796 | 5.8367 | 5.4949 | 5.0112 | 4.8408 | 4.3541 | 3.8296 | 3.0439 | 2.1571 | 1.2663 | 0.64388 | -2.6735 | -5.1388 | -6.9969
|  | LITTLE MARLOW | HT |  |  |  | 6.7735 | 6.4745 | 6.0622 | 5.6663 | 5.1898 | 4.6592 | 4.2327 | 3.4061 | 2.5469 | 1.6592 | -3.0857 | -6.2306 | -7.9939 | 11.6918 | 11.5276 | 11.2959 | 11.0806 | 10.8112 | 10.5143 | 10.3551 | 9.9367 | 9.4959 | 9.0388 | 6.6082 | 5.1398 | 4.3316 | 6.0449 | 5.7684 | 5.3867 | 5.0235 | 4.5786 | 4.0878 | 3.7265 | 2.9653 | 2.1745 | 1.3561 | -2.9582 | -5.7469 | -7.2735
|  | LITTLE MARLOW | HE |  |  |  | 6.7776 | 6.5051 | 6.1531 | 5.748 | 5.302 | 4.8051 | 4.5347 | 3.8633 | 3.1571 | 2.4286 | -1.4918 | -4.2755 | -5.5765 | 11.6449 | 11.4449 | 11.1918 | 10.9031 | 10.5786 | 10.2224 | 10.0449 | 9.5918 | 9.1051 | 8.5806 | 5.3551 | 2.0173 | -2.4878 | 6.0469 | 5.7929 | 5.4714 | 5.0959 | 4.6806 | 4.2224 | 3.998 | 3.3735 | 2.7204 | 2.0449 | -1.5276 | -3.9806 | -5.1133
|  | LITTLE MARLOW | CF |  |  |  | 6.9296 | 6.7816 | 6.5337 | 6.3122 | 6.0316 | 5.7224 | 5.4449 | 5.4908 | 5.1929 | 4.8765 | 2.3327 | -0.44388 | -3.0082 | 11.7163 | 11.5643 | 11.3398 | 11.1265 | 10.8673 | 10.5622 | 10.2367 | 10.1031 | 9.7357 | 9.3133 | 6.102 | 0.85714 | -8.1296 | 6.1847 | 6.0439 | 5.8173 | 5.6153 | 5.3541 | 5.0673 | 4.798 | 4.8541 | 4.5684 | 4.2694 | 1.8918 | -0.6102 | -2.8806
NURSLING GSP | ROWNHAMS | LORDSHILL | MINIMUM HEADROOM | SU 38746 16055 | YES | 6.868 | 13.5281 | 13.2322 | 12.9322 | 12.5434 | 12.1128 | 12.1924 | 11.6332 | 11.0016 | 10.371 | 9.97 | 6.9108 | 4.8373 | 3.6343 | 11.07 | 10.8271 | 10.5853 | 10.2567 | 9.8802 | 9.8394 | 9.3792 | 8.8598 | 8.3179 | 7.9322 | 4.5985 | -0.26166 | -9.8494 | 11.5363 | 11.2608 | 10.9792 | 10.62 | 10.223 | 10.2302 | 9.6934 | 9.0873 | 8.4832 | 8.0771 | 4.8373 | 3.1414 | 2.2108
|  | LORDSHILL | EE |  |  |  | 13.5281 | 13.2322 | 12.9322 | 12.5434 | 12.1128 | 12.1924 | 11.6332 | 11.0016 | 10.371 | 9.97 | 7.0649 | 5.221 | 3.8496 | 11.07 | 10.8271 | 10.5853 | 10.2567 | 9.8802 | 9.8394 | 9.3792 | 8.8598 | 8.3179 | 7.9322 | 4.5985 | 1.4618 | -3.5402 | 11.5363 | 11.2608 | 10.9792 | 10.62 | 10.223 | 10.2302 | 9.6934 | 9.0873 | 8.4832 | 8.0771 | 4.919 | 3.4843 | 2.3955
|  | LORDSHILL | HT |  |  |  | 13.7057 | 13.4873 | 13.273 | 12.9894 | 12.7383 | 12.4149 | 11.8965 | 11.3139 | 11.2781 | 10.6383 | 6.9108 | 4.8373 | 3.6343 | 11.2332 | 11.0792 | 10.9373 | 10.7424 | 10.5781 | 10.3496 | 10.0292 | 9.6577 | 9.7016 | 9.2445 | 6.7047 | 5.7445 | 5.223 | 11.6945 | 11.4843 | 11.2812 | 11.0169 | 10.7761 | 10.472 | 9.9771 | 9.4271 | 9.3118 | 8.6567 | 4.8373 | 3.1414 | 2.2108
|  | LORDSHILL | HE |  |  |  | 13.7006 | 13.4996 | 13.2975 | 13.0353 | 12.8077 | 12.5016 | 12.0424 | 11.5271 | 11.2965 | 10.7812 | 7.2679 | 5.7751 | 5.0475 | 11.2036 | 11.0322 | 10.8639 | 10.6343 | 10.4016 | 10.1067 | 9.7179 | 9.2741 | 9.17 | 8.7332 | 5.0536 | 1.8792 | -2.9157 | 11.6883 | 11.4955 | 11.3047 | 11.0588 | 10.8414 | 10.5536 | 10.119 | 9.6292 | 9.472 | 8.9894 | 5.67 | 4.2618 | 3.5934
|  | LORDSHILL | CF |  |  |  | 13.7741 | 13.6649 | 13.5404 | 13.3761 | 13.1904 | 13.0434 | 12.8281 | 12.5598 | 12.272 | 12.4588 | 10.6608 | 7.8363 | 6.269 | 11.2353 | 11.12 | 10.9679 | 10.7812 | 10.5557 | 10.3108 | 9.9843 | 9.5985 | 9.1863 | 9.0598 | 6.0669 | -0.26166 | -9.8494 | 11.769 | 11.6659 | 11.5536 | 11.4057 | 11.2383 | 11.1036 | 10.9077 | 10.6639 | 10.4026 | 10.52 | 8.8506 | 6.1281 | 4.7557
BRAMLEY (ANDO-THAT) | THATCHAM BSP | LOVE LANE | MINIMUM HEADROOM | SU 47334 68495 | YES | 15.775 | 7.3344 | 6.1405 | 4.7773 | 3.1487 | 1.4824 | -0.59212 | -2.9442 | -5.587 | -9.3615 | -13.0584 | -28.0289 | -35.3095 | -39.3972 | 11.6926 | 10.8191 | 9.8109 | 8.6171 | 7.3997 | 5.7548 | 3.9171 | 1.5997 | -2.1962 | -5.4258 | -17.437 | -23.9493 | -28.6431 | 8.9426 | 7.8171 | 6.5201 | 4.9752 | 3.3905 | 1.3416 | -0.96865 | -3.5156 | -7.9013 | -11.7176 | -26.586 | -34.2227 | -39.0329
|  | LOVE LANE | EE |  |  |  | 7.3344 | 6.1405 | 4.7773 | 3.1487 | 1.4824 | -0.59212 | -2.9442 | -5.587 | -8.4248 | -10.9584 | -21.3646 | -29.3023 | -32.0962 | 11.6926 | 10.8191 | 9.8109 | 8.6171 | 7.3997 | 5.7548 | 3.9171 | 1.9426 | -0.32988 | -2.2962 | -10.4136 | -17.9238 | -20.5707 | 8.9426 | 7.8171 | 6.5201 | 4.9752 | 3.3905 | 1.3416 | -0.96865 | -3.5084 | -6.3238 | -8.8033 | -19.0605 | -27.638 | -30.6258
|  | LOVE LANE | HT |  |  |  | 8.2518 | 7.4701 | 6.412 | 5.0895 | 3.7273 | 1.7344 | -0.14722 | -2.5605 | -4.8452 | -7.6166 | -19.4268 | -28.0982 | -32.7299 | 12.3069 | 11.8487 | 11.064 | 10.0497 | 9.0732 | 7.3385 | 5.8324 | 3.8854 | 2.166 | -0.092122 | -9.4095 | -17.2931 | -21.7891 | 9.462 | 8.7895 | 7.9538 | 6.7997 | 5.5099 | 3.4456 | 1.566 | -0.84722 | -3.0605 | -5.8401 | -17.5574 | -26.7656 | -31.8554
|  | LOVE LANE | HE |  |  |  | 8.1416 | 7.1446 | 5.862 | 4.1987 | 2.4905 | 0.0037959 | -2.2748 | -5.2054 | -9.3615 | -13.0584 | -28.0289 | -35.3095 | -39.3972 | 12.2099 | 11.5967 | 10.6109 | 9.2793 | 7.9864 | 5.7916 | 3.9569 | 1.5997 | -2.1962 | -5.4258 | -17.437 | -23.9493 | -28.6431 | 9.3803 | 8.6762 | 7.5477 | 5.9007 | 4.2497 | 1.662 | -0.60335 | -3.5156 | -7.9013 | -11.7176 | -26.586 | -34.2227 | -39.0329
|  | LOVE LANE | CF |  |  |  | 8.5854 | 8.0569 | 7.5109 | 6.7905 | 5.9824 | 5.014 | 3.9528 | 2.5946 | 1.1956 | -0.44416 | -10.6003 | -20.2166 | -26.6972 | 12.4813 | 12.114 | 11.7201 | 11.2273 | 10.6436 | 9.9599 | 9.0916 | 8.012 | 6.9069 | 5.5824 | -2.5411 | -10.4074 | -16.4452 | 9.7742 | 9.3109 | 8.8262 | 8.1936 | 7.464 | 6.7395 | 5.6813 | 4.3477 | 2.9813 | 1.3579 | -8.6656 | -18.2533 | -24.7911
COWLEY GSP | YARNTON BSP | LOVELACE ROAD | MINIMUM HEADROOM | SP 50395 10376 | YES | 12.089 | 6.1848 | 5.797 | 27.7736 | 27.5225 | 27.196 | 22.7797 | 21.9256 | 21.5113 | 20.8256 | 20.2419 | 18.195 | 17.2562 | 17.0879 | 7.847 | 7.5848 | 27.9532 | 27.7307 | 27.4481 | 23.0746 | 22.497 | 22.2756 | 21.7276 | 21.2644 | 19.096 | 16.3113 | 10.5807 | 6.5511 | 6.2072 | 27.1338 | 26.8797 | 26.5562 | 22.143 | 21.3756 | 21.0981 | 20.4623 | 19.9572 | 18.0817 | 17.2399 | 17.0879
|  | LOVELACE ROAD | EE |  |  |  | 6.1848 | 5.797 | 27.7736 | 27.5225 | 27.196 | 22.7797 | 21.9256 | 21.5113 | 20.8256 | 20.293 | 18.195 | 17.4042 | 17.3807 | 7.847 | 7.5848 | 27.9532 | 27.7307 | 27.4481 | 23.0746 | 22.497 | 22.2756 | 21.7276 | 21.2644 | 19.096 | 17.4164 | 14.846 | 6.5511 | 6.2072 | 27.1338 | 26.8797 | 26.5562 | 22.143 | 21.3756 | 21.0981 | 20.4623 | 19.9797 | 18.0817 | 17.3817 | 17.3491
|  | LOVELACE ROAD | HT |  |  |  | 6.3246 | 5.9644 | 28.0164 | 27.8317 | 27.5185 | 23.1358 | 22.1766 | 21.6042 | 20.9174 | 20.2419 | 18.3674 | 17.2562 | 17.0879 | 7.9919 | 7.793 | 28.2572 | 28.1348 | 27.9001 | 23.6103 | 23.1123 | 22.696 | 22.1817 | 21.6736 | 20.5042 | 19.8899 | 19.7746 | 6.6981 | 6.3981 | 27.4072 | 27.2328 | 26.9358 | 22.5756 | 21.7736 | 21.2368 | 20.593 | 19.9572 | 18.2552 | 17.2399 | 17.0879
|  | LOVELACE ROAD | HE |  |  |  | 6.3123 | 5.9603 | 28.0144 | 27.8338 | 27.6083 | 23.2838 | 22.5705 | 21.9348 | 21.3215 | 20.7021 | 18.6419 | 17.7042 | 17.5532 | 7.9521 | 7.7307 | 28.1613 | 28.0011 | 27.8021 | 23.5093 | 23.0756 | 22.597 | 22.0899 | 21.5338 | 19.2889 | 17.4409 | 14.8562 | 6.6879 | 6.394 | 27.4052 | 27.2379 | 27.0154 | 22.7052 | 22.1021 | 21.5236 | 20.947 | 20.3623 | 18.4848 | 17.6276 | 17.493
|  | LOVELACE ROAD | CF |  |  |  | 6.397 | 6.1236 | 28.2634 | 28.1368 | 28.0338 | 23.8817 | 23.695 | 23.4511 | 23.0838 | 22.6879 | 20.3756 | 19.0225 | 17.8093 | 8.0001 | 7.8083 | 28.2756 | 28.1205 | 27.9899 | 23.7991 | 23.5501 | 23.2552 | 22.8634 | 22.4379 | 19.5705 | 16.3113 | 10.5807 | 6.7634 | 6.5348 | 27.6195 | 27.4858 | 27.3828 | 23.2317 | 23.046 | 22.8174 | 22.4725 | 22.1072 | 20.0644 | 18.8164 | 17.7113
MANNINGTON GSP | ARNEWOOD | LYMINGTON | MINIMUM HEADROOM | SZ 31720 96856 | YES | 3.649 | 11.8776 | 11.398 | 10.6694 | 10.3847 | 9.6296 | 8.7918 | 7.4704 | 6.1694 | 4.899 | 4.0112 | -1.0898 | -5.1082 | -7.3194 | 14.9878 | 14.6143 | 14.0214 | 13.8592 | 13.2827 | 12.651 | 11.7898 | 10.8827 | 9.9694 | 9.351 | 5.9694 | 2.4245 | -7.1969 | 12.4265 | 11.9735 | 11.2908 | 11.0388 | 10.3439 | 9.5724 | 8.3704 | 7.1704 | 5.9939 | 5.1551 | 0.61327 | -2.9551 | -4.9735
|  | LYMINGTON | EE |  |  |  | 11.8776 | 11.398 | 10.6694 | 10.3847 | 9.6296 | 8.7918 | 7.4704 | 6.1694 | 4.899 | 4.0112 | -0.83878 | -4.2827 | -6.8878 | 14.9878 | 14.6143 | 14.0214 | 13.8592 | 13.2827 | 12.651 | 11.7898 | 10.8827 | 9.9694 | 9.351 | 5.9694 | 2.5429 | -2.5765 | 12.4265 | 11.9735 | 11.2908 | 11.0388 | 10.3439 | 9.5724 | 8.3704 | 7.1704 | 5.9939 | 5.1551 | 0.80306 | -2.2041 | -4.601
|  | LYMINGTON | HT |  |  |  | 12.1337 | 11.6378 | 11.1714 | 10.5582 | 9.8245 | 9.4357 | 8.2765 | 7.201 | 6.0888 | 4.9429 | -1.0898 | -5.1082 | -7.3194 | 15.2806 | 14.95 | 14.6602 | 14.2684 | 13.8082 | 13.6735 | 13.0643 | 12.4582 | 11.8173 | 11.149 | 7.9163 | 6.0867 | 5.1776 | 12.648 | 12.198 | 11.798 | 11.2408 | 10.5745 | 10.2531 | 9.2122 | 8.2235 | 7.1918 | 6.1296 | 0.61327 | -2.9551 | -4.9735
|  | LYMINGTON | HE |  |  |  | 12.1449 | 11.7888 | 11.2714 | 10.752 | 10.1041 | 9.7612 | 8.7469 | 7.8133 | 6.8776 | 5.9286 | 0.80204 | -2.6653 | -4.2684 | 15.2367 | 14.9663 | 14.5633 | 14.1643 | 13.6745 | 13.4929 | 12.8531 | 12.2082 | 11.5255 | 10.8184 | 6.8612 | 3.3255 | -1.3704 | 12.6582 | 12.3469 | 11.8816 | 11.4031 | 10.8122 | 10.5337 | 9.6296 | 8.7663 | 7.898 | 7.0122 | 2.3194 | -0.78163 | -2.2786
|  | LYMINGTON | CF |  |  |  | 12.3378 | 12.1357 | 11.8714 | 11.5327 | 11.2 | 10.7867 | 10.6878 | 10.2857 | 9.8163 | 9.3224 | 5.7837 | 2.15 | -1.2684 | 15.3398 | 15.1306 | 14.8571 | 14.5296 | 14.1939 | 13.7745 | 13.6306 | 13.1612 | 12.6347 | 12.0694 | 8.1041 | 2.4245 | -7.1969 | 12.8327 | 12.6643 | 12.4265 | 12.1112 | 11.798 | 11.4153 | 11.3531 | 10.9755 | 10.5378 | 10.0776 | 6.8051 | 3.498 | 0.46837
MELKSHAM GSP | CHIPPENHAM | LYNEHAM | MINIMUM HEADROOM | ST 99348 80481 | YES | 0.579 | 5.0439 | 4.7643 | 19.0408 | 18.6633 | 18.1796 | 17.802 | 17.8551 | 17.4531 | 17.052 | 16.8092 | 15.3704 | 14.4531 | 13.7786 | 7.4872 | 7.3117 | 20.6296 | 20.3888 | 20.0898 | 19.8459 | 19.8388 | 19.5694 | 19.2929 | 19.1112 | 18.0867 | 16.8082 | 13.8276 | 6.302 | 6.0459 | 19.6082 | 19.2612 | 18.8112 | 18.45 | 18.5235 | 18.1429 | 17.7612 | 17.5408 | 16.3694 | 15.6214 | 15.0888
|  | LYNEHAM | EE |  |  |  | 5.0439 | 4.7643 | 19.0408 | 18.6633 | 18.1796 | 17.802 | 17.8551 | 17.4531 | 17.052 | 16.8092 | 15.3704 | 14.5347 | 14.0051 | 7.4872 | 7.3117 | 20.6296 | 20.3888 | 20.0898 | 19.8459 | 19.8388 | 19.5694 | 19.2929 | 19.1112 | 18.0867 | 17.0837 | 15.598 | 6.302 | 6.0459 | 19.6082 | 19.2612 | 18.8112 | 18.45 | 18.5235 | 18.1429 | 17.7612 | 17.5408 | 16.3837 | 15.7112 | 15.2755
|  | LYNEHAM | HT |  |  |  | 5.1714 | 4.8378 | 19.1633 | 18.8296 | 18.55 | 18.3163 | 17.9643 | 17.5745 | 17.1643 | 17.1918 | 15.4541 | 14.4531 | 13.7786 | 7.5842 | 7.3985 | 20.7694 | 20.5929 | 20.4388 | 20.302 | 20.1071 | 19.8837 | 19.648 | 19.6918 | 18.749 | 18.2837 | 17.9786 | 6.4316 | 6.1337 | 19.748 | 19.4449 | 19.1816 | 18.9643 | 18.6367 | 18.2673 | 17.8786 | 17.9918 | 16.449 | 15.6296 | 15.0888
|  | LYNEHAM | HE |  |  |  | 5.1694 | 4.9429 | 19.3357 | 19.0776 | 18.7469 | 18.4459 | 18.0378 | 17.6755 | 17.2969 | 17.3622 | 15.6235 | 14.7776 | 14.3459 | 7.5719 | 7.426 | 20.8122 | 20.649 | 20.4418 | 20.251 | 19.9939 | 19.7531 | 19.4959 | 19.5143 | 18.2316 | 17.199 | 15.7245 | 6.4286 | 6.2255 | 19.8918 | 19.6551 | 19.351 | 19.0796 | 18.7041 | 18.3592 | 17.999 | 18.1082 | 16.3694 | 15.6214 | 15.201
|  | LYNEHAM | CF |  |  |  | 5.2245 | 5.0327 | 19.5551 | 19.3551 | 19.1061 | 18.8245 | 18.6041 | 18.3061 | 18.0755 | 17.8337 | 17.05 | 16.0112 | 15.0378 | 7.6015 | 7.4719 | 20.9235 | 20.7929 | 20.6204 | 20.4224 | 20.2459 | 20.0184 | 19.8173 | 19.6031 | 18.5684 | 16.8082 | 13.8276 | 6.4806 | 6.3061 | 20.0908 | 19.9112 | 19.6827 | 19.4255 | 19.2276 | 18.95 | 18.7306 | 18.499 | 17.7786 | 16.698 | 15.8398
BRAMLEY (FLEE) | BRACKNELL | M V E E | MINIMUM HEADROOM | SU 98120 65945 | YES | 0 | 24.3429 | 24.2714 | 24.2112 | 24.1306 | 24.0378 | 23.9837 | 23.8347 | 23.6684 | 23.5531 | 23.4582 | 22.9429 | 22.5459 | 22.3245 | 23.1827 | 23.1163 | 23.0643 | 22.9918 | 22.9041 | 22.85 | 22.7367 | 22.602 | 22.5184 | 22.4837 | 22.2673 | 21.649 | 20.3673 | 24.2541 | 24.1867 | 24.1316 | 24.0612 | 23.9765 | 23.9276 | 23.7959 | 23.6449 | 23.5316 | 23.448 | 22.9714 | 22.6469 | 22.4724
|  | M V E E | EE |  |  |  | 24.3429 | 24.2714 | 24.2112 | 24.1306 | 24.0378 | 23.9837 | 23.8347 | 23.6684 | 23.5531 | 23.4582 | 23.0184 | 22.65 | 22.3694 | 23.1827 | 23.1163 | 23.0643 | 22.9918 | 22.9041 | 22.85 | 22.7367 | 22.602 | 22.5184 | 22.4837 | 22.2673 | 21.8449 | 21.1653 | 24.2541 | 24.1867 | 24.1316 | 24.0612 | 23.9765 | 23.9276 | 23.7959 | 23.6449 | 23.5316 | 23.448 | 23.0367 | 22.7337 | 22.5082
|  | M V E E | HT |  |  |  | 24.3643 | 24.3173 | 24.2673 | 24.2224 | 24.15 | 24.0847 | 23.949 | 23.8439 | 23.6929 | 23.5469 | 22.9429 | 22.5459 | 22.3245 | 23.2224 | 23.1857 | 23.1459 | 23.1122 | 23.0571 | 23.0061 | 22.9276 | 22.8724 | 22.7776 | 22.6806 | 22.401 | 22.3367 | 22.2459 | 24.2806 | 24.2357 | 24.1847 | 24.1408 | 24.0765 | 24.0163 | 23.8939 | 23.799 | 23.6633 | 23.5286 | 22.9714 | 22.6469 | 22.4724
|  | M V E E | HE |  |  |  | 24.3673 | 24.3265 | 24.2806 | 24.2367 | 24.1714 | 24.1092 | 23.998 | 23.9163 | 23.7949 | 23.6663 | 23.1347 | 22.7765 | 22.5714 | 23.2173 | 23.1827 | 23.1408 | 23.1071 | 23.052 | 22.9969 | 22.9173 | 22.8633 | 22.7673 | 22.6643 | 22.3102 | 21.8745 | 21.2265 | 24.2827 | 24.2408 | 24.1949 | 24.1551 | 24.0949 | 24.0378 | 23.9398 | 23.8663 | 23.7541 | 23.6398 | 23.151 | 22.8367 | 22.6745
|  | M V E E | CF |  |  |  | 24.3888 | 24.3653 | 24.3388 | 24.2929 | 24.2714 | 24.2327 | 24.1786 | 24.1102 | 24.0796 | 24.0112 | 23.6 | 23.2092 | 22.8878 | 23.2276 | 23.199 | 23.1653 | 23.1214 | 23.098 | 23.0561 | 23.002 | 22.9327 | 22.8949 | 22.8184 | 22.3827 | 21.649 | 20.3673 | 24.3031 | 24.2765 | 24.248 | 24.2082 | 24.1888 | 24.1531 | 24.1061 | 24.0459 | 24.0173 | 23.9592 | 23.5878 | 23.2286 | 22.9286
CHICKERELL GSP | CHICKERELL BSP | MAIDEN NEWTON | MINIMUM HEADROOM | SY 59138 97747 | YES | 0.669 | 7.102 | 6.951 | 6.802 | 6.6031 | 6.4429 | 6.2204 | 5.9388 | 5.5929 | 5.2439 | 5.7173 | 4.9633 | 4.7224 | 4.5194 | 8.5367 | 8.4276 | 8.3204 | 8.1735 | 8.051 | 7.8755 | 7.6571 | 7.3929 | 7.1255 | 7.4816 | 6.8714 | 6.2469 | 4.6551 | 7.6276 | 7.4745 | 7.3245 | 7.1245 | 6.9602 | 6.7347 | 6.4531 | 6.1133 | 5.7704 | 6.2847 | 5.6286 | 5.4224 | 5.2398
|  | MAIDEN NEWTON | EE |  |  |  | 7.102 | 6.951 | 6.802 | 6.6031 | 6.4429 | 6.2204 | 5.9388 | 5.5929 | 5.2439 | 5.7173 | 4.9633 | 4.7224 | 4.6194 | 8.5367 | 8.4276 | 8.3204 | 8.1735 | 8.051 | 7.8755 | 7.6571 | 7.3929 | 7.1255 | 7.4816 | 6.9439 | 6.4663 | 5.7153 | 7.6276 | 7.4745 | 7.3245 | 7.1245 | 6.9602 | 6.7347 | 6.4531 | 6.1133 | 5.7704 | 6.2847 | 5.6286 | 5.4224 | 5.3276
|  | MAIDEN NEWTON | HT |  |  |  | 7.1959 | 7.0949 | 6.9908 | 6.8602 | 6.752 | 6.6071 | 6.4173 | 6.2418 | 6.0194 | 5.7796 | 5.1449 | 4.7541 | 4.5194 | 8.6082 | 8.5357 | 8.4735 | 8.3796 | 8.3112 | 8.2031 | 8.0684 | 7.9531 | 7.7776 | 7.5908 | 7.3571 | 7.1541 | 7.0398 | 7.7306 | 7.6276 | 7.5337 | 7.4041 | 7.302 | 7.151 | 6.9592 | 6.7959 | 6.5653 | 6.3214 | 5.7827 | 5.4378 | 5.2398
|  | MAIDEN NEWTON | HE |  |  |  | 7.2041 | 7.0929 | 6.9908 | 6.8633 | 6.7622 | 6.6204 | 6.4388 | 6.2694 | 6.0531 | 5.8092 | 5.101 | 4.8551 | 4.7806 | 8.6082 | 8.5214 | 8.452 | 8.35 | 8.2776 | 8.1602 | 8.0194 | 7.899 | 7.7265 | 7.5459 | 7.0571 | 6.5633 | 5.8388 | 7.7398 | 7.6265 | 7.5347 | 7.4041 | 7.3071 | 7.1571 | 6.9714 | 6.8092 | 6.5765 | 6.3357 | 5.7724 | 5.5582 | 5.4949
|  | MAIDEN NEWTON | CF |  |  |  | 7.2245 | 7.1398 | 7.052 | 6.9551 | 6.8469 | 6.7694 | 6.651 | 6.5122 | 6.3684 | 6.2602 | 5.3724 | 5.2582 | 4.8378 | 8.6173 | 8.552 | 8.4847 | 8.4061 | 8.3163 | 8.252 | 8.1408 | 8.0112 | 7.8684 | 7.7663 | 6.8714 | 6.2469 | 4.6551 | 7.7612 | 7.6816 | 7.599 | 7.5041 | 7.398 | 7.3255 | 7.2092 | 7.0714 | 6.9255 | 6.8265 | 5.899 | 5.9041 | 5.5378
BRAMLEY (FLEE) | MAIDENHEAD BSP | MAIDENHEAD | MINIMUM HEADROOM | SU 86485 79800 | YES | 35.695 | 16.9166 | 11.462 | 11.0671 | 10.1926 | 8.9559 | -1.7717 | -3.2982 | -4.9564 | -6.4615 | -7.4992 | -12.5697 | -16.2421 | -17.535 | 17.7688 | 12.457 | 12.204 | 11.5774 | 10.7642 | 0.33049 | -0.68992 | -1.8246 | -2.9083 | -3.6267 | -7.1654 | -11.0307 | -21.4654 | 13.1678 | 7.7285 | 7.4336 | 6.6336 | 5.5397 | -5.1001 | -6.4613 | -7.9644 | -9.3429 | -10.2409 | -14.4807 | -17.6746 | -18.7582
|  | MAIDENHEAD | EE |  |  |  | 16.9166 | 11.462 | 11.0671 | 10.1926 | 8.9559 | -1.7717 | -3.2982 | -4.9564 | -6.4615 | -7.4992 | -12.4564 | -15.6952 | -16.6094 | 17.7688 | 12.457 | 12.204 | 11.5774 | 10.7642 | 0.33049 | -0.68992 | -1.8246 | -2.9083 | -3.6267 | -7.1654 | -10.7134 | -15.5695 | 13.1678 | 7.7285 | 7.4336 | 6.6336 | 5.5397 | -5.1001 | -6.4613 | -7.9644 | -9.3429 | -10.2409 | -14.4368 | -17.1991 | -17.9664
|  | MAIDENHEAD | HT |  |  |  | 17.1707 | 11.8273 | 11.2334 | 10.3977 | 9.4538 | -1.1564 | -2.4646 | -3.8411 | -5.1166 | -6.387 | -12.5697 | -16.2421 | -17.535 | 18.0841 | 12.9325 | 12.5621 | 12.054 | 11.6101 | 1.3784 | 0.66314 | -0.11543 | -0.86849 | -1.6226 | -5.0124 | -6.7338 | -7.3613 | 13.4974 | 8.1805 | 7.6397 | 6.8897 | 6.2111 | -4.2756 | -5.3827 | -6.5776 | -7.7429 | -8.9133 | -14.4807 | -17.6746 | -18.7582
|  | MAIDENHEAD | HE |  |  |  | 17.1993 | 11.9079 | 11.3569 | 10.5783 | 9.8446 | -0.67271 | -1.8543 | -3.1115 | -4.2268 | -5.3492 | -10.4074 | -13.437 | -14.5564 | 18.0341 | 12.8509 | 12.4346 | 11.8846 | 11.5264 | 1.2754 | 0.50498 | -0.34196 | -1.1542 | -1.9899 | -6.1246 | -9.6664 | -14.5001 | 13.5076 | 8.2336 | 7.7316 | 7.0275 | 6.5295 | -3.8756 | -4.8889 | -5.9858 | -6.9889 | -8.0307 | -12.6297 | -15.1807 | -16.1164
|  | MAIDENHEAD | CF |  |  |  | 17.3891 | 12.3977 | 12.1242 | 11.6742 | 10.9803 | 1.1038 | 0.40586 | -0.36557 | -1.0013 | -1.5462 | -5.2931 | -9.1992 | -12.9105 | 18.1158 | 13.0795 | 12.7866 | 12.3825 | 11.8489 | 2.0489 | 1.4387 | 0.73967 | 0.077429 | -0.56747 | -4.9307 | -11.0307 | -21.4654 | 13.6597 | 8.6428 | 8.3713 | 7.9418 | 7.3224 | -2.4164 | -3.0256 | -3.7195 | -4.3174 | -4.8562 | -8.3287 | -11.6501 | -14.747
MELKSHAM GSP | CHIPPENHAM | MALMESBURY | MINIMUM HEADROOM | ST 92288 87493 | YES | 1.997 | 2.1633 | 1.5602 | 1.0296 | 0.59592 | 0.15306 | -0.31429 | -0.45918 | -0.98776 | -1.5092 | -1.8837 | -3.9408 | -5.4541 | -6.5092 | 4.7347 | 4.4398 | 4.1888 | 3.9378 | 3.6694 | 3.3816 | 3.3092 | 2.9857 | 2.6602 | 2.4092 | 0.90102 | -0.73163 | -4.8245 | 3.4939 | 2.9786 | 2.5153 | 2.0969 | 1.6541 | 1.1878 | 1.15 | 0.64286 | 0.14184 | -0.1949 | -1.9592 | -3.2643 | -4.0878
|  | MALMESBURY | EE |  |  |  | 2.1633 | 1.5602 | 1.0296 | 0.59592 | 0.15306 | -0.31429 | -0.45918 | -0.98776 | -1.5092 | -1.8837 | -3.9408 | -5.2673 | -6.2531 | 4.7347 | 4.4398 | 4.1888 | 3.9378 | 3.6694 | 3.3816 | 3.3092 | 2.9857 | 2.6602 | 2.4092 | 0.90102 | -0.60612 | -2.7663 | 3.4939 | 2.9786 | 2.5153 | 2.0969 | 1.6541 | 1.1878 | 1.15 | 0.64286 | 0.14184 | -0.1949 | -1.9592 | -3.0704 | -3.8724
|  | MALMESBURY | HT |  |  |  | 2.2969 | 1.7357 | 1.2663 | 0.90816 | 0.55102 | 0.21735 | -0.22959 | -0.72143 | -0.89184 | -1.3612 | -3.8551 | -5.4541 | -6.5092 | 4.8163 | 4.5582 | 4.349 | 4.1908 | 4.0296 | 3.8755 | 3.6398 | 3.3837 | 3.3367 | 3.0898 | 1.8276 | 1.049 | 0.57143 | 3.648 | 3.1827 | 2.7827 | 2.4561 | 2.1163 | 1.8102 | 1.3918 | 0.92551 | 0.83061 | 0.39082 | -1.8684 | -3.2643 | -4.0878
|  | MALMESBURY | HE |  |  |  | 2.2939 | 1.7408 | 1.2806 | 0.93367 | 0.58469 | 0.26633 | -0.12959 | -0.57143 | -0.69286 | -1.1 | -3.3786 | -4.7378 | -5.3969 | 4.799 | 4.5265 | 4.3031 | 4.1245 | 3.9347 | 3.7357 | 3.4857 | 3.2041 | 3.1286 | 2.852 | 1.1714 | -0.35918 | -2.3969 | 3.6418 | 3.1837 | 2.7939 | 2.4755 | 2.15 | 1.8592 | 1.4857 | 1.0612 | 1.0102 | 0.62755 | -1.4327 | -2.5316 | -3.0449
|  | MALMESBURY | CF |  |  |  | 2.3796 | 1.901 | 1.5082 | 1.2878 | 1.0418 | 0.77755 | 0.60204 | 0.36939 | 0.11531 | -0.14694 | -1.3041 | -2.751 | -4.0949 | 4.8378 | 4.5939 | 4.399 | 4.2724 | 4.1265 | 3.9316 | 3.7602 | 3.549 | 3.3143 | 3.0643 | 1.7051 | -0.73163 | -4.8245 | 3.7204 | 3.3316 | 2.9959 | 2.799 | 2.5684 | 2.3235 | 2.1612 | 1.9204 | 1.6531 | 1.3765 | 0.36939 | -0.90306 | -2.05
MINETY GSP | SWINDON BSP | MANCHESTER ROAD | MINIMUM HEADROOM | SU 15254 85130 | YES | 4.219 | 30.1055 | 29.4667 | 28.7422 | 27.9024 | 27.1759 | 25.2718 | 23.1208 | 20.6045 | 17.7208 | 15.5963 | 8.1229 | 4.2422 | 4.0596 | 31.2259 | 30.6402 | 30.0453 | 29.3698 | 28.7943 | 27.4627 | 26.031 | 24.328 | 22.428 | 20.9596 | 15.0351 | 7.6514 | -7.8373 | 30.1606 | 29.5565 | 28.9269 | 28.1994 | 27.5657 | 25.9637 | 24.1249 | 21.9933 | 19.5229 | 17.7239 | 9.48 | 5.7943 | 5.6382
|  | MANCHESTER ROAD | EE |  |  |  | 30.1055 | 29.4667 | 28.7422 | 27.9024 | 27.1759 | 25.2718 | 23.1208 | 20.6045 | 17.7208 | 15.5963 | 11.4076 | 9.7371 | 10.0953 | 31.2259 | 30.6402 | 30.0453 | 29.3698 | 28.7943 | 27.4627 | 26.031 | 24.328 | 22.428 | 20.9596 | 16.1769 | 11.5984 | 4.5637 | 30.1606 | 29.5565 | 28.9269 | 28.1994 | 27.5657 | 25.9637 | 24.1249 | 21.9933 | 19.5229 | 17.7239 | 14.1963 | 12.8341 | 13.0943
|  | MANCHESTER ROAD | HT |  |  |  | 30.5249 | 29.9953 | 29.3851 | 28.7157 | 27.6504 | 25.5269 | 23.6035 | 21.4147 | 19.5147 | 17.681 | 12.2647 | 9.3137 | 9.1443 | 31.6198 | 31.2076 | 30.8218 | 30.4035 | 29.7065 | 28.5024 | 27.4953 | 26.2494 | 25.1218 | 24.031 | 20.4259 | 18.5647 | 18.2718 | 30.5565 | 30.0627 | 29.5586 | 29.0086 | 28.0882 | 26.3637 | 24.8116 | 22.9841 | 21.382 | 19.8647 | 15.0994 | 12.5055 | 12.4035
|  | MANCHESTER ROAD | HE |  |  |  | 30.3963 | 29.879 | 29.2943 | 28.6647 | 27.8157 | 26.0024 | 24.0667 | 22.0667 | 19.4494 | 17.2933 | 8.1229 | 4.2422 | 4.0596 | 31.4524 | 30.9596 | 30.482 | 29.9708 | 29.3024 | 28.082 | 26.8024 | 25.5086 | 23.781 | 22.1759 | 15.0351 | 11.2218 | 4.0953 | 30.4229 | 29.9116 | 29.4035 | 28.8545 | 28.1157 | 26.5882 | 24.9596 | 23.1882 | 20.682 | 18.2984 | 9.48 | 5.7943 | 5.6382
|  | MANCHESTER ROAD | CF |  |  |  | 30.7953 | 30.4218 | 30.1953 | 29.9065 | 29.6147 | 29.2545 | 28.7749 | 27.8759 | 26.9096 | 25.4902 | 15.2035 | 8.532 | 4.1678 | 31.7484 | 31.2657 | 30.9688 | 30.6116 | 30.2076 | 29.7014 | 29.0473 | 28.1055 | 27.1759 | 25.9331 | 17.1627 | 7.6514 | -7.8373 | 30.8208 | 30.4188 | 30.2076 | 29.9412 | 29.6698 | 29.3392 | 28.8892 | 28.1045 | 27.282 | 25.778 | 16.2167 | 9.8851 | 5.7504
MANNINGTON GSP | MANNINGTON BSP | MANNINGTON | MINIMUM HEADROOM | SU 07592 05256 | YES | 3.17 | 5.2209 | 4.9066 | 4.7546 | 4.5301 | 4.1913 | 3.9597 | 3.5556 | 3.4372 | 3.0291 | 2.8587 | 1.1719 | 0.094388 | -0.48827 | 3.9571 | 3.6724 | 3.5061 | 3.3071 | 3.0031 | 2.7755 | 2.4673 | 2.5602 | 2.2878 | 2.1122 | 1.1316 | -0.11224 | -3.0633 | 3.6449 | 3.3418 | 3.1469 | 2.9214 | 2.5908 | 2.3367 | 1.9398 | 1.9429 | 1.5592 | 1.3449 | -0.09898 | -1.0776 | -1.598
|  | MANNINGTON | EE |  |  |  | 5.2209 | 4.9066 | 4.7546 | 4.5301 | 4.1913 | 3.9597 | 3.5556 | 3.5046 | 3.126 | 2.8587 | 1.375 | 0.34133 | -0.36276 | 3.9571 | 3.6724 | 3.5061 | 3.3071 | 3.0031 | 2.7755 | 2.4673 | 2.5602 | 2.2878 | 2.1122 | 1.1316 | 0.071429 | -1.4429 | 3.6449 | 3.3418 | 3.1469 | 2.9214 | 2.5908 | 2.3367 | 1.9398 | 1.9439 | 1.5878 | 1.3449 | 0.079592 | -0.85408 | -1.4867
|  | MANNINGTON | HT |  |  |  | 5.2852 | 4.9903 | 4.8617 | 4.6556 | 4.3536 | 4.1944 | 3.8301 | 3.4372 | 3.0291 | 2.9311 | 1.1719 | 0.094388 | -0.48827 | 4.0184 | 3.7418 | 3.6612 | 3.5173 | 3.2888 | 3.2051 | 3.0133 | 2.7673 | 2.5071 | 2.5888 | 1.6786 | 1.2296 | 0.97551 | 3.7224 | 3.4245 | 3.2765 | 3.0867 | 2.8041 | 2.648 | 2.3122 | 1.9429 | 1.5592 | 1.5092 | -0.09898 | -1.0776 | -1.598
|  | MANNINGTON | HE |  |  |  | 5.2903 | 5.0015 | 4.8923 | 4.7128 | 4.4383 | 4.2872 | 4.0179 | 3.6985 | 3.3679 | 3.3515 | 1.8066 | 0.78929 | 0.27704 | 4.0133 | 3.7327 | 3.6469 | 3.4959 | 3.2551 | 3.1531 | 2.9459 | 2.7041 | 2.4337 | 2.4939 | 1.301 | 0.25102 | -1.1908 | 3.7337 | 3.4582 | 3.3173 | 3.1439 | 2.8765 | 2.7347 | 2.4663 | 2.1612 | 1.8378 | 1.8551 | 0.45204 | -0.45 | -0.90816
|  | MANNINGTON | CF |  |  |  | 5.3526 | 5.1066 | 5.0444 | 4.9189 | 4.7117 | 4.623 | 4.5332 | 4.3883 | 4.2352 | 4.0709 | 3.2628 | 2.1903 | 1.1168 | 4.0418 | 3.7827 | 3.7204 | 3.5918 | 3.3776 | 3.2755 | 3.1673 | 2.9878 | 2.7929 | 2.5776 | 1.6378 | -0.11224 | -3.0633 | 3.7898 | 3.5561 | 3.4684 | 3.3469 | 3.1398 | 3.0306 | 2.9367 | 2.7878 | 2.6235 | 2.4388 | 1.75 | 0.74898 | -0.15
LOVEDEAN GSP | CHICHESTER & HUNSTON | MARKET | MINIMUM HEADROOM | SU 86479 04732 | YES | 0.999 | 13.1035 | 12.8739 | 12.3933 | 11.9157 | 11.4014 | 10.8494 | 10.433 | 9.5351 | 8.679 | 8.0259 | 4.4565 | 1.2626 | -0.63634 | 13.6665 | 13.4257 | 13.1257 | 12.8033 | 12.4492 | 12.0624 | 11.7237 | 11.1757 | 10.5104 | 9.9533 | 6.7665 | 2.139 | -8.6855 | 11.981 | 11.7667 | 11.4851 | 11.0688 | 10.6137 | 10.1279 | 9.7555 | 8.9677 | 8.1239 | 7.5167 | 4.4769 | 1.7402 | 0.067743
|  | MARKET | EE |  |  |  | 13.1035 | 12.8739 | 12.3933 | 11.9157 | 11.4014 | 10.8494 | 10.433 | 9.5351 | 8.679 | 8.0259 | 4.4565 | 1.8616 | -0.30062 | 13.6665 | 13.4257 | 13.1257 | 12.8033 | 12.4492 | 12.0624 | 11.7237 | 11.1757 | 10.5104 | 9.9533 | 6.7665 | 3.2094 | -2.5478 | 11.981 | 11.7667 | 11.4851 | 11.0688 | 10.6137 | 10.1279 | 9.7555 | 8.9677 | 8.1239 | 7.5167 | 4.4769 | 2.1841 | 0.28917
|  | MARKET | HT |  |  |  | 13.2402 | 13.0616 | 12.779 | 12.3667 | 11.9749 | 11.5851 | 10.9626 | 10.1657 | 9.3637 | 8.9443 | 4.531 | 1.2626 | -0.63634 | 13.8614 | 13.693 | 13.4951 | 13.2584 | 13.0094 | 12.7359 | 12.4094 | 11.9839 | 11.5369 | 11.1941 | 9.0859 | 7.7084 | 6.9073 | 12.1218 | 11.9575 | 11.7688 | 11.4861 | 11.1433 | 10.8035 | 10.2524 | 9.5575 | 8.8575 | 8.4922 | 4.6218 | 1.7402 | 0.067743
|  | MARKET | HE |  |  |  | 13.2239 | 13.0433 | 12.783 | 12.3963 | 12.031 | 11.6769 | 11.1382 | 10.4249 | 9.7188 | 9.3973 | 5.832 | 3.2514 | 2.0433 | 13.8359 | 13.6482 | 13.4247 | 13.1665 | 12.891 | 12.589 | 12.2237 | 11.741 | 11.2359 | 10.8298 | 7.7828 | 4.1063 | -1.307 | 12.1065 | 11.9382 | 11.7433 | 11.4922 | 11.1667 | 10.8494 | 10.3647 | 9.7361 | 9.1126 | 8.8249 | 5.6708 | 3.3933 | 2.3484
|  | MARKET | CF |  |  |  | 13.3341 | 13.2177 | 13.0779 | 12.9218 | 12.7024 | 12.4657 | 12.2922 | 11.9412 | 11.5973 | 11.2933 | 9.2657 | 6.8239 | 4.4984 | 13.9645 | 13.8604 | 13.7196 | 13.5706 | 13.4124 | 13.2145 | 13.0084 | 12.5726 | 12.0757 | 11.5696 | 8.1859 | 2.139 | -8.6855 | 12.2096 | 12.0994 | 11.9667 | 11.8453 | 11.7218 | 11.5596 | 11.4024 | 11.1024 | 10.8075 | 10.5382 | 8.7892 | 6.6494 | 4.6004
MELKSHAM GSP | WEST GRAFTON | MARLBOROUGH SOUTH | MINIMUM HEADROOM | SU 19293 68264 | YES | 4.154 | 0.25459 | -0.051531 | -0.39031 | -0.79745 | -1.3077 | -1.4434 | -1.9852 | -2.576 | -3.1872 | -3.6199 | -6.0209 | -7.9148 | -9.0852 | 3.1163 | 2.8663 | 2.599 | 2.2643 | 1.8643 | 1.8347 | 1.4337 | 0.97653 | 0.5102 | 0.2102 | -1.5031 | -3.6214 | -8.7684 | 0.19082 | -0.11735 | -0.46122 | -0.88776 | -1.4061 | -1.4765 | -2.0163 | -2.6194 | -3.2245 | -3.6153 | -5.6133 | -7.1867 | -8.1439
|  | MARLBOROUGH SOUTH | EE |  |  |  | 0.25459 | -0.051531 | -0.39031 | -0.79745 | -1.3077 | -1.4434 | -1.9852 | -2.576 | -3.1872 | -3.6199 | -6.0209 | -7.623 | -8.8005 | 3.1163 | 2.8663 | 2.599 | 2.2643 | 1.8643 | 1.8347 | 1.4337 | 0.97653 | 0.5102 | 0.2102 | -1.5031 | -3.3316 | -6.0704 | 0.19082 | -0.11735 | -0.46122 | -0.88776 | -1.4061 | -1.4765 | -2.0163 | -2.6194 | -3.2245 | -3.6153 | -5.6133 | -6.9112 | -7.9031
|  | MARLBOROUGH SOUTH | HT |  |  |  | 0.38827 | 0.12704 | -0.1648 | -0.52806 | -0.93622 | -1.2719 | -1.7832 | -2.0362 | -2.5526 | -3.0893 | -5.976 | -7.9148 | -9.0852 | 3.2806 | 3.1122 | 2.9347 | 2.7031 | 2.4714 | 2.2327 | 1.9235 | 1.8939 | 1.5816 | 1.25 | -0.32857 | -1.2469 | -1.75 | 0.32449 | 0.088776 | -0.17347 | -0.50918 | -0.88061 | -1.2245 | -1.7194 | -1.8867 | -2.3857 | -2.9061 | -5.549 | -7.1867 | -8.1439
|  | MARLBOROUGH SOUTH | HE |  |  |  | 0.38622 | 0.14439 | -0.12398 | -0.44745 | -0.81276 | -1.1781 | -1.6332 | -2.1342 | -2.276 | -2.7321 | -5.3107 | -6.8903 | -7.6566 | 3.252 | 3.0714 | 2.8765 | 2.6367 | 2.3959 | 2.1143 | 1.7806 | 1.399 | 1.3776 | 1.0204 | -1.0459 | -2.9122 | -5.4735 | 0.32041 | 0.10204 | -0.13878 | -0.4398 | -0.77653 | -1.1347 | -1.5765 | -2.0786 | -2.1306 | -2.5776 | -4.9092 | -6.2184 | -6.8653
|  | MARLBOROUGH SOUTH | CF |  |  |  | 0.47704 | 0.33214 | 0.1699 | 0.0005102 | -0.18316 | -0.34235 | -0.55867 | -0.83112 | -1.1464 | -1.1556 | -2.9342 | -4.627 | -6.2291 | 3.2929 | 3.1663 | 3.0194 | 2.85 | 2.6582 | 2.4806 | 2.2347 | 1.9276 | 1.5888 | 1.5745 | -0.55102 | -3.6214 | -8.7684 | 0.40102 | 0.27143 | 0.12245 | -0.037755 | -0.22245 | -0.38571 | -0.61224 | -0.89694 | -1.2245 | -1.1673 | -2.9153 | -4.402 | -5.698
NURSLING GSP | ROWNHAMS | MAYBUSH | MINIMUM HEADROOM | SU 38426 14930 | YES | 1.635 | 4.3401 | 3.8329 | 3.1768 | 2.9135 | 2.2319 | 1.4686 | 0.32883 | -1.0773 | -2.4661 | -3.4804 | -8.0691 | -12.1171 | -14.2018 | 17.9883 | 17.5577 | 16.9964 | 16.7393 | 16.1209 | 15.4199 | 14.5219 | 13.4403 | 12.3383 | 11.4842 | 6.9505 | 0.30459 | -15.7872 | 4.95 | 4.4663 | 3.8541 | 3.552 | 2.8969 | 2.1531 | 1.0541 | -0.28571 | -1.6082 | -2.5949 | -6.902 | -10.4714 | -12.3551
|  | MAYBUSH | EE |  |  |  | 4.3401 | 3.8329 | 3.1768 | 2.9135 | 2.2319 | 1.4686 | 0.32883 | -1.0773 | -2.4661 | -3.4804 | -8.0691 | -11.3987 | -14.0222 | 17.9883 | 17.5577 | 16.9964 | 16.7393 | 16.1209 | 15.4199 | 14.5219 | 13.4403 | 12.3383 | 11.4842 | 6.9505 | 1.6628 | -6.775 | 4.95 | 4.4663 | 3.8541 | 3.552 | 2.8969 | 2.1531 | 1.0541 | -0.28571 | -1.6082 | -2.5949 | -6.902 | -9.8173 | -12.2143
|  | MAYBUSH | HT |  |  |  | 4.6768 | 4.2696 | 3.7747 | 3.2778 | 2.6747 | 1.8819 | 1.2747 | 0.16964 | -0.8875 | -1.9457 | -8.0651 | -12.1171 | -14.2018 | 18.3219 | 18.0515 | 17.7056 | 17.3679 | 16.924 | 16.3872 | 16.0913 | 15.4138 | 14.7454 | 14.0719 | 10.5658 | 8.4862 | 7.5546 | 5.1571 | 4.8541 | 4.401 | 3.9357 | 3.348 | 2.601 | 1.9582 | 0.89898 | -0.11939 | -1.1398 | -6.8316 | -10.4714 | -12.3551
|  | MAYBUSH | HE |  |  |  | 4.6625 | 4.3156 | 3.8809 | 3.4625 | 2.9584 | 2.3809 | 2.0441 | 1.1482 | 0.23087 | -0.70893 | -5.3171 | -8.3936 | -9.6589 | 18.2505 | 17.9485 | 17.5658 | 17.1872 | 16.7148 | 16.1638 | 15.8077 | 15.075 | 14.2934 | 13.4781 | 8.7383 | 3.5128 | -4.3903 | 5.1531 | 4.8888 | 4.4939 | 4.0959 | 3.6194 | 3.0612 | 2.6633 | 1.7959 | 0.91122 | 0.0091837 | -4.3316 | -7.052 | -8.1796
|  | MAYBUSH | CF |  |  |  | 4.8717 | 4.6227 | 4.386 | 4.1013 | 3.8421 | 3.5094 | 3.1411 | 2.6737 | 2.6298 | 2.1319 | -1.1518 | -4.1355 | -6.9446 | 18.3679 | 18.0954 | 17.8179 | 17.4801 | 17.1209 | 16.6566 | 16.0985 | 15.4413 | 15.0413 | 14.3107 | 9.0638 | 0.30459 | -15.7872 | 5.3235 | 5.1684 | 5.0041 | 4.7408 | 4.5 | 4.1959 | 3.849 | 3.4163 | 3.3133 | 2.8459 | -0.29694 | -3.2286 | -5.8092
MELKSHAM GSP | NORRINGTON | MELKSHAM TOWN | MINIMUM HEADROOM | ST 90170 64096 | YES | 3.175 | 3.5065 | 2.9677 | 2.4218 | 1.4361 | 0.17689 | -1.269 | -2.8782 | -4.5792 | -6.1527 | -7.1884 | -12.2231 | -16.5384 | -19.0915 | 7.1595 | 6.7085 | 6.3432 | 5.7044 | 4.983 | 4.0555 | 3.0187 | 1.8718 | 0.76158 | 0.029951 | -3.7231 | -8.4527 | -19.7598 | 4.3606 | 3.6075 | 3.2218 | 2.231 | 1.1095 | -0.16903 | -1.6129 | -3.1711 | -4.6343 | -5.4854 | -9.8598 | -13.6507 | -15.8221
|  | MELKSHAM TOWN | EE |  |  |  | 3.5065 | 2.9677 | 2.4218 | 1.4361 | 0.17689 | -1.269 | -2.8782 | -4.5792 | -6.1527 | -7.1884 | -11.9721 | -15.6813 | -18.5558 | 7.1595 | 6.7085 | 6.3432 | 5.7044 | 4.983 | 4.0555 | 3.0187 | 1.8718 | 0.76158 | 0.029951 | -3.7231 | -7.7741 | -13.7241 | 4.3606 | 3.6075 | 3.2218 | 2.231 | 1.1095 | -0.16903 | -1.6129 | -3.1711 | -4.6343 | -5.4854 | -9.6945 | -12.9058 | -15.3854
|  | MELKSHAM TOWN | HT |  |  |  | 3.8136 | 3.3871 | 2.8095 | 1.5963 | 0.64424 | -0.77515 | -2.2109 | -3.5007 | -4.7517 | -6.0109 | -12.2231 | -16.5384 | -19.0915 | 7.4055 | 7.0718 | 6.6667 | 6.0575 | 5.6034 | 4.9014 | 4.1973 | 3.5514 | 2.8667 | 2.1157 | -1.367 | -3.4343 | -4.5803 | 4.7504 | 4.1463 | 3.4565 | 2.3953 | 1.7769 | 0.55954 | -0.70678 | -1.8762 | -3.0282 | -4.1864 | -9.8598 | -13.6507 | -15.8221
|  | MELKSHAM TOWN | HE |  |  |  | 3.7708 | 3.3259 | 2.7544 | 1.831 | 1.0667 | -0.19148 | -1.4568 | -2.7864 | -3.9996 | -5.1527 | -10.6333 | -14.5343 | -16.47 | 7.3493 | 6.9718 | 6.5095 | 5.9116 | 5.4565 | 4.733 | 3.983 | 3.1759 | 2.3504 | 1.4759 | -3.12 | -7.4047 | -13.0119 | 4.7463 | 4.1718 | 3.5055 | 2.5912 | 2.1157 | 1.0248 | -0.090457 | -1.2772 | -2.3823 | -3.4405 | -8.4864 | -11.9058 | -13.5364
|  | MELKSHAM TOWN | CF |  |  |  | 4.0157 | 3.7544 | 3.383 | 2.9146 | 2.3504 | 2.132 | 1.6657 | 1.1014 | 0.38403 | -0.42515 | -5.27 | -9.3466 | -13.0568 | 7.4463 | 7.1626 | 6.7922 | 6.3912 | 5.983 | 5.7279 | 5.282 | 4.7534 | 4.1361 | 3.381 | -1.67 | -8.4527 | -19.7598 | 4.9014 | 4.5371 | 4.0565 | 3.5034 | 2.9626 | 2.93 | 2.4942 | 1.9646 | 1.3085 | 0.57995 | -3.7721 | -7.3394 | -10.5996
NURSLING GSP |  | MARCHWOOD | MINIMUM HEADROOM | SU 39234 11008 | YES | 6.705 | 17.6394 | 17.4894 | 16.3916 | 16.2048 | 16.0722 | 15.8293 | 15.5324 | 15.1906 | 14.8732 | 14.6334 | 13.1518 | 12.3406 | 12.1528 | 17.9129 | 17.7925 | 16.6834 | 16.4987 | 16.3844 | 16.214 | 16.0304 | 15.7946 | 15.5599 | 15.3467 | 14.3242 | 13.0906 | 10.0855 | 17.468 | 17.3037 | 16.2252 | 16.0395 | 15.8875 | 15.661 | 15.4018 | 15.0824 | 14.765 | 14.4824 | 13.0814 | 12.3334 | 12.1681
|  | MARCHWOOD | EE |  |  |  | 17.6394 | 17.5782 | 16.3967 | 16.2048 | 16.0732 | 15.8293 | 15.5324 | 15.1906 | 14.8732 | 14.7089 | 13.8528 | 13.1467 | 12.5783 | 17.9129 | 17.8456 | 16.6834 | 16.4987 | 16.3926 | 16.2334 | 16.0446 | 15.8018 | 15.564 | 15.4283 | 14.6263 | 13.6201 | 12.0385 | 17.468 | 17.3956 | 16.2365 | 16.0406 | 15.8987 | 15.6987 | 15.4569 | 15.1742 | 14.9038 | 14.7538 | 13.9895 | 13.3763 | 12.8844
|  | MARCHWOOD | HT |  |  |  | 17.7047 | 17.4894 | 16.3916 | 16.315 | 16.2181 | 16.0038 | 15.7365 | 15.4314 | 15.1538 | 14.9793 | 13.8304 | 13.0375 | 12.562 | 17.9864 | 17.7925 | 16.7314 | 16.6875 | 16.6324 | 16.512 | 16.3773 | 16.214 | 16.0599 | 15.961 | 15.3222 | 14.9538 | 14.7457 | 17.517 | 17.3037 | 16.2252 | 16.1599 | 16.0814 | 15.913 | 15.6895 | 15.4395 | 15.1957 | 15.0344 | 13.9926 | 13.2967 | 12.8875
|  | MARCHWOOD | HE |  |  |  | 17.6649 | 17.6027 | 16.4242 | 16.2099 | 16.0722 | 15.865 | 15.6069 | 15.2671 | 14.9304 | 14.6334 | 13.1518 | 12.3406 | 12.1528 | 17.9353 | 17.8619 | 16.6926 | 16.4987 | 16.3844 | 16.214 | 16.0304 | 15.7946 | 15.5599 | 15.3467 | 14.3242 | 13.6252 | 12.1436 | 17.5058 | 17.4374 | 16.2589 | 16.0395 | 15.8875 | 15.661 | 15.4018 | 15.0824 | 14.765 | 14.4824 | 13.0814 | 12.3334 | 12.1681
|  | MARCHWOOD | CF |  |  |  | 17.7302 | 17.7068 | 16.7487 | 16.5559 | 16.3844 | 16.2477 | 16.0967 | 15.9324 | 15.7497 | 15.5926 | 14.4538 | 13.3293 | 12.4436 | 17.9853 | 17.9384 | 16.963 | 16.7671 | 16.6059 | 16.4722 | 16.3171 | 16.1671 | 15.9997 | 15.8559 | 14.8161 | 13.0906 | 10.0855 | 17.5486 | 17.518 | 16.563 | 16.3793 | 16.2344 | 16.0916 | 15.9355 | 15.7599 | 15.5661 | 15.3977 | 14.2977 | 13.2385 | 12.4181
LOVEDEAN GSP | HAVANT | MEYRICK ROAD | MINIMUM HEADROOM | SU 70849 06469 | YES | 1.119 | 9.6278 | 8.792 | 7.9829 | 7.1676 | 6.4012 | 5.541 | 4.1655 | 2.6573 | 1.1757 | 0.15224 | -4.4865 | -8.9457 | -10.0437 | 13.4098 | 12.8353 | 12.4118 | 11.8578 | 11.271 | 10.6282 | 9.8067 | 8.7496 | 7.6057 | 6.8261 | 2.57 | -5.6076 | -22.1086 | 10.1247 | 9.3227 | 8.6798 | 7.8818 | 7.1002 | 6.2288 | 4.9553 | 3.5318 | 2.1288 | 1.2298 | -2.609 | -6.2988 | -7.1692
|  | MEYRICK ROAD | EE |  |  |  | 9.6278 | 8.792 | 7.9829 | 7.1676 | 6.4012 | 5.541 | 4.1655 | 2.6573 | 1.1757 | 0.15224 | -4.362 | -8.3539 | -8.8661 | 13.4098 | 12.8353 | 12.4118 | 11.8578 | 11.271 | 10.6282 | 9.8067 | 8.7496 | 7.6057 | 6.8261 | 2.57 | -2.9912 | -10.728 | 10.1247 | 9.3227 | 8.6798 | 7.8818 | 7.1002 | 6.2288 | 4.9553 | 3.5318 | 2.1288 | 1.2298 | -2.609 | -5.8151 | -6.2467
|  | MEYRICK ROAD | HT |  |  |  | 9.89 | 8.9931 | 8.1318 | 7.3431 | 6.9614 | 6.2176 | 5.0665 | 3.8451 | 2.5869 | 1.3594 | -4.4865 | -8.9457 | -10.0437 | 13.7608 | 13.2282 | 12.768 | 12.3169 | 12.2424 | 11.8108 | 11.2669 | 10.6496 | 9.9945 | 9.319 | 6.0955 | 4.0333 | 3.3935 | 10.4502 | 9.6778 | 8.9196 | 8.1778 | 7.9104 | 7.2094 | 6.1757 | 5.0512 | 3.8818 | 2.7206 | -2.6069 | -6.2988 | -7.1692
|  | MEYRICK ROAD | HE |  |  |  | 9.9073 | 9.2114 | 8.2451 | 7.5114 | 7.1931 | 6.5176 | 5.4931 | 4.3941 | 3.2778 | 2.191 | -2.5304 | -6.362 | -7.4171 | 13.7363 | 13.3159 | 12.7231 | 12.2669 | 12.1853 | 11.7476 | 11.0537 | 10.2455 | 9.3843 | 8.4639 | 3.5302 | -2.0943 | -9.9994 | 10.4686 | 9.8573 | 9.0073 | 8.3145 | 8.0971 | 7.4614 | 6.5329 | 5.5114 | 4.4573 | 3.4155 | -0.95694 | -4.0202 | -4.8467
|  | MEYRICK ROAD | CF |  |  |  | 10.1237 | 9.6584 | 9.0818 | 8.4451 | 8.0288 | 7.8971 | 7.4247 | 6.9043 | 6.3604 | 5.8533 | 2.4471 | -2.3998 | -6.2773 | 13.8098 | 13.4853 | 13.0955 | 12.619 | 12.2588 | 12.2159 | 11.62 | 10.9302 | 10.2047 | 9.4476 | 4.0557 | -5.6076 | -22.1086 | 10.6563 | 10.2349 | 9.7257 | 9.1339 | 8.7094 | 8.6808 | 8.2288 | 7.7104 | 7.1624 | 6.6329 | 3.3288 | -0.81612 | -3.9896
MELKSHAM GSP | ANDOVER BSP | MIDDLE WALLOP | MINIMUM HEADROOM | SU 30984 40155 | YES | 0.369 | 2.2997 | 2.2171 | 2.1171 | 2.0253 | 1.9048 | 1.7763 | 1.6304 | 1.4222 | 1.2059 | 1.0814 | 0.37423 | 0.019133 | -0.18189 | 4.226 | 4.1811 | 4.1219 | 4.0709 | 3.9985 | 3.927 | 3.8444 | 3.7321 | 3.6199 | 3.5423 | 3.1066 | 2.7219 | 1.6964 | 3.2735 | 3.2031 | 3.1204 | 3.0327 | 2.9245 | 2.8071 | 2.6684 | 2.4776 | 2.2878 | 2.1439 | 1.4418 | 1.1133 | 0.94082
|  | MIDDLE WALLOP | EE |  |  |  | 2.2997 | 2.2171 | 2.1171 | 2.0253 | 1.9048 | 1.7763 | 1.6304 | 1.4222 | 1.2059 | 1.0814 | 0.4324 | 0.10689 | -0.074745 | 4.226 | 4.1811 | 4.1219 | 4.0709 | 3.9985 | 3.927 | 3.8444 | 3.7321 | 3.6199 | 3.5423 | 3.1066 | 2.7658 | 2.3097 | 3.2735 | 3.2031 | 3.1204 | 3.0327 | 2.9245 | 2.8071 | 2.6684 | 2.4776 | 2.2878 | 2.1439 | 1.5184 | 1.3051 | 1.198
|  | MIDDLE WALLOP | HT |  |  |  | 2.3426 | 2.2651 | 2.1753 | 2.1008 | 2.0079 | 1.9069 | 1.7804 | 1.611 | 1.4355 | 1.2936 | 0.48444 | 0.077296 | -0.18189 | 4.2556 | 4.2199 | 4.175 | 4.1352 | 4.0893 | 4.0352 | 3.975 | 3.8893 | 3.7995 | 3.7301 | 3.323 | 3.1301 | 3.0066 | 3.3255 | 3.2592 | 3.1857 | 3.1184 | 3.0398 | 2.9541 | 2.8398 | 2.6918 | 2.5296 | 2.3694 | 1.5847 | 1.2357 | 1.0184
|  | MIDDLE WALLOP | HE |  |  |  | 2.3446 | 2.2702 | 2.1834 | 2.113 | 2.0242 | 1.9273 | 1.8151 | 1.6599 | 1.4987 | 1.3191 | 0.37423 | 0.019133 | -0.16964 | 4.2536 | 4.2138 | 4.1658 | 4.1209 | 4.0658 | 4.0087 | 3.9393 | 3.8485 | 3.7526 | 3.673 | 3.1281 | 2.7648 | 2.3097 | 3.3214 | 3.2622 | 3.1918 | 3.1235 | 3.0388 | 2.9408 | 2.8337 | 2.6714 | 2.4949 | 2.3265 | 1.4418 | 1.1133 | 0.94082
|  | MIDDLE WALLOP | CF |  |  |  | 2.3589 | 2.3059 | 2.2477 | 2.1926 | 2.1171 | 2.0467 | 1.9671 | 1.9038 | 1.811 | 1.7099 | 1.1293 | 0.50587 | 0.0068878 | 4.2628 | 4.2342 | 4.1974 | 4.1628 | 4.1148 | 4.0658 | 4.0117 | 3.9566 | 3.8872 | 3.8158 | 3.3505 | 2.7219 | 1.6964 | 3.3398 | 3.2949 | 3.2449 | 3.199 | 3.1367 | 3.0786 | 3.0102 | 2.95 | 2.8704 | 2.7837 | 2.1449 | 1.5622 | 1.102
BRAMLEY (FLEE) | FERNHURST | MIDHURST | MINIMUM HEADROOM | SU 88127 19555 | YES | 2.474 | 16.9969 | 16.6551 | 16.3122 | 15.8776 | 15.3969 | 15.3786 | 14.7755 | 14.0847 | 13.3765 | 12.8643 | 10.148 | 8.0673 | 6.8214 | 18.7388 | 18.4684 | 18.1888 | 17.8296 | 17.4306 | 17.4653 | 17.0286 | 16.5092 | 15.9847 | 15.6398 | 13.749 | 11.5061 | 5.8806 | 17.2041 | 16.8765 | 16.5408 | 16.1112 | 15.6306 | 15.6245 | 15.0378 | 14.3673 | 13.6898 | 13.2184 | 10.8571 | 9.0643 | 7.9969
|  | MIDHURST | EE |  |  |  | 16.9969 | 16.6551 | 16.3122 | 15.8776 | 15.3969 | 15.3786 | 14.7755 | 14.0847 | 13.3765 | 12.8643 | 10.148 | 8.4122 | 7.1633 | 18.7388 | 18.4684 | 18.1888 | 17.8296 | 17.4306 | 17.4653 | 17.0286 | 16.5092 | 15.9847 | 15.6398 | 13.749 | 11.7306 | 8.7776 | 17.2041 | 16.8765 | 16.5408 | 16.1112 | 15.6306 | 15.6245 | 15.0378 | 14.3673 | 13.6898 | 13.2184 | 10.8571 | 9.3694 | 8.2857
|  | MIDHURST | HT |  |  |  | 17.1837 | 16.9235 | 16.6653 | 16.3357 | 16.0408 | 15.6602 | 15.0918 | 14.8204 | 14.2071 | 13.5643 | 10.2276 | 8.0673 | 6.8214 | 18.9194 | 18.7459 | 18.5745 | 18.3449 | 18.1449 | 17.8735 | 17.5143 | 17.5082 | 17.1418 | 16.7531 | 14.9408 | 13.9429 | 13.3724 | 17.3857 | 17.1327 | 16.8816 | 16.5663 | 16.2765 | 15.9071 | 15.3561 | 15.148 | 14.5776 | 13.9786 | 10.951 | 9.0643 | 7.9969
|  | MIDHURST | HE |  |  |  | 17.1776 | 16.9286 | 16.6857 | 16.3776 | 16.1102 | 15.7653 | 15.2673 | 15.0694 | 14.5378 | 13.9827 | 10.9918 | 9.2949 | 8.5398 | 18.8939 | 18.7031 | 18.5153 | 18.2673 | 18.048 | 17.7602 | 17.3939 | 17.3633 | 16.9816 | 16.5724 | 14.2776 | 12.2286 | 9.5041 | 17.3786 | 17.1378 | 16.901 | 16.6061 | 16.3388 | 16.0031 | 15.5184 | 15.3735 | 14.8735 | 14.3531 | 11.6571 | 10.1908 | 9.5541
|  | MIDHURST | CF |  |  |  | 17.2714 | 17.0969 | 16.9286 | 16.7184 | 16.4908 | 16.3051 | 16.05 | 15.7439 | 15.4112 | 15.5102 | 13.6061 | 11.6551 | 9.8449 | 18.948 | 18.7949 | 18.6449 | 18.45 | 18.2367 | 18.0367 | 17.7673 | 17.4388 | 17.0847 | 17.1306 | 14.8959 | 11.5061 | 5.8806 | 17.4724 | 17.3061 | 17.1459 | 16.9469 | 16.7265 | 16.5469 | 16.2939 | 15.9827 | 15.65 | 15.7684 | 13.9347 | 12.202 | 10.6663
AXMINSTER | YEOVIL BSP | MILBORNE PORT | MINIMUM HEADROOM | ST 67929 19741 | YES | 0.281 | 3.5724 | 3.4806 | 3.3449 | 3.2459 | 3.0939 | 2.9816 | 2.7561 | 2.4918 | 2.2347 | 2.0898 | 1.3296 | 0.7449 | 0.38571 | 2.0806 | 2.0255 | 1.9541 | 1.8929 | 1.8102 | 1.748 | 1.5867 | 1.3959 | 1.2041 | 1.098 | 0.53571 | -0.23367 | -2.0582 | 2.3918 | 2.3265 | 2.2408 | 2.1694 | 2.0765 | 2.0082 | 1.8469 | 1.6684 | 1.4929 | 1.3684 | 0.63776 | 0.07449 | -0.27449
|  | MILBORNE PORT | EE |  |  |  | 3.5724 | 3.4806 | 3.3449 | 3.2459 | 3.0939 | 2.9816 | 2.7561 | 2.4918 | 2.2347 | 2.0898 | 1.3296 | 0.82551 | 0.45306 | 2.0806 | 2.0255 | 1.9541 | 1.8929 | 1.8102 | 1.748 | 1.5867 | 1.3959 | 1.2041 | 1.098 | 0.53571 | -0.081633 | -1.0429 | 2.3918 | 2.3265 | 2.2408 | 2.1694 | 2.0765 | 2.0082 | 1.8469 | 1.6684 | 1.4929 | 1.3684 | 0.6398 | 0.13367 | -0.22245
|  | MILBORNE PORT | HT |  |  |  | 3.648 | 3.5592 | 3.4786 | 3.3837 | 3.2704 | 3.1939 | 3.0041 | 2.7898 | 2.6184 | 2.3959 | 1.3337 | 0.7449 | 0.38571 | 2.1235 | 2.0857 | 2.0449 | 2.002 | 1.9469 | 1.9092 | 1.8204 | 1.7224 | 1.6459 | 1.5214 | 0.91735 | 0.64082 | 0.48061 | 2.4245 | 2.3643 | 2.3031 | 2.2388 | 2.1643 | 2.102 | 1.952 | 1.7888 | 1.6571 | 1.4908 | 0.63776 | 0.07449 | -0.27449
|  | MILBORNE PORT | HE |  |  |  | 3.6469 | 3.5633 | 3.4847 | 3.3949 | 3.2847 | 3.2133 | 3.05 | 2.8602 | 2.7133 | 2.5184 | 1.5357 | 1.0429 | 0.80816 | 2.1143 | 2.0633 | 2.0163 | 1.9622 | 1.8959 | 1.8459 | 1.749 | 1.6418 | 1.55 | 1.4184 | 0.64592 | 0.010204 | -0.88776 | 2.4224 | 2.3653 | 2.3061 | 2.2439 | 2.1694 | 2.1082 | 1.9816 | 1.8388 | 1.7265 | 1.5816 | 0.7602 | 0.2602 | 0.032653
|  | MILBORNE PORT | CF |  |  |  | 3.6796 | 3.6265 | 3.5541 | 3.5071 | 3.4429 | 3.3694 | 3.3163 | 3.2184 | 3.1143 | 3.0041 | 2.3439 | 1.748 | 1.2367 | 2.1296 | 2.0908 | 2.0429 | 2.0051 | 1.9541 | 1.8969 | 1.8378 | 1.751 | 1.6633 | 1.5704 | 0.83367 | -0.23367 | -2.0582 | 2.4439 | 2.4112 | 2.3684 | 2.3327 | 2.2898 | 2.2408 | 2.1949 | 2.1306 | 2.0643 | 1.9908 | 1.5286 | 1.0071 | 0.50408
BRAMLEY (FLEE) | ALDERSHOT BSP | MILFORD | MINIMUM HEADROOM | SU 94719 43018 | YES | 4.784 | 9.5802 | 9.1455 | 8.62 | 7.9424 | 7.6098 | 6.9965 | 6.2373 | 5.3894 | 4.6292 | 4.1169 | 1.018 | -1.4004 | -2.8157 | 12.9771 | 12.671 | 12.2792 | 11.8088 | 11.7261 | 11.3057 | 10.8088 | 10.2363 | 9.6853 | 9.3537 | 7.2965 | 4.8292 | -1.2759 | 10.0261 | 9.6343 | 9.1496 | 8.5363 | 8.2771 | 7.7149 | 7.0169 | 6.2312 | 5.519 | 5.0516 | 2.4261 | 0.42102 | -0.7698
|  | MILFORD | EE |  |  |  | 9.5802 | 9.1455 | 8.62 | 7.9424 | 7.6098 | 6.9965 | 6.2373 | 5.3894 | 4.6292 | 4.1169 | 1.221 | -0.94327 | -2.579 | 12.9771 | 12.671 | 12.2792 | 11.8088 | 11.7261 | 11.3057 | 10.8088 | 10.2363 | 9.6853 | 9.3537 | 7.2965 | 5.0394 | 1.7904 | 10.0261 | 9.6343 | 9.1496 | 8.5363 | 8.2771 | 7.7149 | 7.0169 | 6.2312 | 5.519 | 5.0516 | 2.5782 | 0.82204 | -0.55959
|  | MILFORD | HT |  |  |  | 9.7598 | 9.3782 | 8.9445 | 8.418 | 7.768 | 7.1771 | 6.7588 | 5.9945 | 5.3067 | 4.6037 | 1.018 | -1.4004 | -2.8157 | 13.1741 | 12.9527 | 12.6833 | 12.3986 | 12.0292 | 11.6741 | 11.5986 | 11.1976 | 10.8159 | 10.4241 | 8.5588 | 7.4782 | 6.8924 | 10.2057 | 9.869 | 9.4792 | 9.0149 | 8.4394 | 7.9037 | 7.5976 | 6.9159 | 6.2853 | 5.6363 | 2.4261 | 0.42102 | -0.7698
|  | MILFORD | HE |  |  |  | 9.7629 | 9.4016 | 8.9822 | 8.4802 | 7.8476 | 7.2833 | 6.9945 | 6.3649 | 5.8057 | 5.2353 | 2.1394 | 0.050612 | -0.96061 | 13.1445 | 12.9027 | 12.6078 | 12.2955 | 11.9006 | 11.5139 | 11.4016 | 10.9935 | 10.5914 | 10.172 | 7.7527 | 5.4935 | 2.4955 | 10.2078 | 9.8894 | 9.5098 | 9.071 | 8.5118 | 7.9986 | 7.7996 | 7.2271 | 6.7047 | 6.17 | 3.3833 | 1.6608 | 0.85469
|  | MILFORD | CF |  |  |  | 9.8669 | 9.5782 | 9.3047 | 8.8955 | 8.4629 | 8.07 | 7.7292 | 7.3322 | 7.4547 | 7.1843 | 5.1965 | 3.069 | 1.0027 | 13.1894 | 12.971 | 12.7588 | 12.4649 | 12.1761 | 11.8588 | 11.5322 | 11.1414 | 11.1506 | 10.8282 | 8.469 | 4.8292 | -1.2759 | 10.3047 | 10.0516 | 9.8098 | 9.4496 | 9.0792 | 8.722 | 8.4067 | 8.0404 | 8.169 | 7.9098 | 6.0363 | 4.1292 | 2.3986
MANNINGTON GSP | ARNEWOOD | MILFORD-ON-SEA | MINIMUM HEADROOM | SZ 28252 93347 | YES | 1.284 | 3.5597 | 28.0148 | 27.4944 | 26.8781 | 26.5903 | 25.973 | 25.0812 | 24.0934 | 23.0587 | 22.3118 | 18.8669 | 16.2342 | 14.7322 | 5.772 | 28.6097 | 28.2169 | 27.7659 | 27.6608 | 27.2189 | 26.6495 | 26.0016 | 25.3189 | 24.8669 | 22.7169 | 19.8669 | 12.8118 | 3.9903 | 27.4444 | 26.9199 | 26.3077 | 26.2006 | 25.624 | 24.823 | 23.9128 | 22.9638 | 22.3128 | 19.3546 | 17.0536 | 15.8067
|  | MILFORD-ON-SEA | EE |  |  |  | 3.5597 | 28.0148 | 27.4944 | 26.8781 | 26.5903 | 25.973 | 25.0812 | 24.0934 | 23.0587 | 22.3118 | 19.1873 | 16.8444 | 14.9954 | 5.772 | 28.6097 | 28.2169 | 27.7659 | 27.6608 | 27.2189 | 26.6495 | 26.0016 | 25.3189 | 24.8669 | 22.7169 | 20.2108 | 16.4954 | 3.9903 | 27.4444 | 26.9199 | 26.3077 | 26.2006 | 25.624 | 24.823 | 23.9128 | 22.9638 | 22.3128 | 19.6148 | 17.5944 | 16.0342
|  | MILFORD-ON-SEA | HT |  |  |  | 3.7271 | 28.2291 | 27.775 | 27.2944 | 26.7261 | 26.1189 | 25.5383 | 24.622 | 23.675 | 22.8128 | 18.8669 | 16.2342 | 14.7322 | 5.9689 | 28.8873 | 28.6097 | 28.3444 | 28.0087 | 27.6454 | 27.5067 | 27.0332 | 26.5393 | 26.0679 | 24.0577 | 22.9271 | 22.3312 | 4.1985 | 27.7281 | 27.3077 | 26.8812 | 26.3618 | 25.7934 | 25.3965 | 24.5791 | 23.7342 | 22.9506 | 19.3546 | 17.0536 | 15.8067
|  | MILFORD-ON-SEA | HE |  |  |  | 3.7373 | 28.2699 | 27.8546 | 27.4026 | 26.8628 | 26.3046 | 25.9057 | 25.1434 | 24.3199 | 23.5567 | 20.2495 | 17.8985 | 16.7373 | 5.9373 | 28.8383 | 28.5424 | 28.2536 | 27.8863 | 27.4934 | 27.3546 | 26.872 | 26.3403 | 25.8199 | 23.2444 | 20.6883 | 17.2536 | 4.2026 | 27.7577 | 27.3648 | 26.9638 | 26.4669 | 25.9434 | 25.7067 | 25.023 | 24.2863 | 23.5903 | 20.5883 | 18.5403 | 17.5924
|  | MILFORD-ON-SEA | CF |  |  |  | 3.8526 | 28.4679 | 28.2179 | 27.871 | 27.5312 | 27.1801 | 26.8424 | 26.7699 | 26.3924 | 25.9791 | 23.5771 | 21.1393 | 18.8261 | 5.9924 | 28.9148 | 28.7057 | 28.4281 | 28.171 | 27.8526 | 27.5077 | 27.424 | 27.0373 | 26.622 | 23.921 | 19.8669 | 12.8118 | 4.3057 | 27.9159 | 27.6781 | 27.3465 | 27.0465 | 26.7046 | 26.3618 | 26.424 | 26.0638 | 25.675 | 23.422 | 21.3067 | 19.325
MANNINGTON GSP | MANNINGTON BSP | MILL LANE | MINIMUM HEADROOM | SU 14691 05633 | YES | 4.11 | 8.3722 | 7.6416 | 16.1324 | 15.2682 | 14.1335 | 12.8141 | 11.2253 | 9.3263 | 7.462 | 5.91 | -2.8247 | -6.7094 | -7.6563 | 12.2988 | 11.8171 | 20.0314 | 19.4171 | 18.5712 | 17.5998 | 16.4784 | 15.1192 | 13.7947 | 12.7049 | 6.2345 | 3.512 | -2.7941 | 8.7876 | 8.2314 | 16.658 | 15.9345 | 14.8447 | 13.5886 | 12.0845 | 10.2824 | 8.5182 | 7.0518 | -1.2288 | -4.888 | -5.7522
|  | MILL LANE | EE |  |  |  | 8.3722 | 7.6416 | 16.1324 | 15.2682 | 14.1335 | 12.8141 | 11.2253 | 9.3263 | 7.462 | 5.91 | 0.00081633 | -1.5727 | -3.5757 | 12.2988 | 11.8171 | 20.0314 | 19.4171 | 18.5712 | 17.5998 | 16.4784 | 15.1192 | 13.7947 | 12.7049 | 8.5692 | 6.6518 | 2.2835 | 8.7876 | 8.2314 | 16.658 | 15.9345 | 14.8447 | 13.5886 | 12.0845 | 10.2824 | 8.5182 | 7.0518 | 1.5376 | -0.082857 | -2.0043
|  | MILL LANE | HT |  |  |  | 9.0365 | 8.4794 | 17.3682 | 16.6906 | 15.8855 | 15.0273 | 13.7733 | 12.3059 | 10.7957 | 9.1386 | 1.9273 | -1.5859 | -3.5645 | 12.762 | 12.3927 | 20.9335 | 20.4937 | 19.9631 | 19.3651 | 18.5284 | 17.5263 | 16.4804 | 15.2896 | 10.2069 | 8.2141 | 7.6396 | 9.1937 | 8.7008 | 17.4345 | 16.859 | 16.1794 | 15.6467 | 14.3539 | 12.9416 | 11.5406 | 10.0314 | 3.2182 | -0.29918 | -1.9563
|  | MILL LANE | HE |  |  |  | 8.8396 | 8.2447 | 16.8916 | 16.0273 | 15.0049 | 13.8855 | 12.4151 | 10.6069 | 8.6569 | 6.6539 | -2.8247 | -6.7094 | -7.6563 | 12.6273 | 12.2447 | 20.5743 | 19.9947 | 19.2447 | 18.4324 | 17.3916 | 16.0906 | 14.6865 | 13.2355 | 6.2345 | 3.512 | 1.5008 | 9.1253 | 8.6814 | 17.3049 | 16.6682 | 15.6865 | 14.6273 | 13.2355 | 11.5222 | 9.6692 | 7.7651 | -1.2288 | -4.888 | -5.7522
|  | MILL LANE | CF |  |  |  | 9.2916 | 8.9753 | 18.0345 | 17.4998 | 16.9743 | 16.3253 | 15.7753 | 14.8702 | 13.8478 | 12.7457 | 5.7335 | -0.33694 | -3.9747 | 12.8886 | 12.6896 | 21.3376 | 20.9396 | 20.5722 | 20.1212 | 19.7478 | 19.0896 | 18.3233 | 17.4957 | 12.3702 | 6.1029 | -2.7941 | 9.3978 | 9.1396 | 18.0202 | 17.6447 | 17.26 | 16.7641 | 16.4141 | 15.5631 | 14.5865 | 13.5365 | 6.8927 | 1.1335 | -2.2808
COWLEY GSP | DRAYTON BSP | MILTON | MINIMUM HEADROOM | SU 49992 92060 | YES | 18.438 | 23.3086 | 21.5035 | 19.7382 | 17.4198 | 14.6239 | 10.8647 | 7.6147 | 4.1831 | 1.5484 | -0.79246 | -9.6833 | -16.2425 | -20.5476 | 24.2677 | 23.0831 | 22.0004 | 20.6269 | 18.6514 | 15.8698 | 13.1708 | 10.23 | 7.9933 | 5.9035 | -1.5863 | -7.3782 | -16.8241 | 21.778 | 20.2341 | 18.7535 | 16.7698 | 14.2657 | 10.8218 | 7.6637 | 4.2851 | 1.7228 | -0.57919 | -9.0598 | -15.3516 | -19.4506
|  | MILTON | EE |  |  |  | 23.3086 | 21.5035 | 19.7382 | 17.5463 | 14.6239 | 10.8647 | 7.6147 | 4.1831 | 1.5484 | -0.79246 | -8.9496 | -14.1802 | -18.8618 | 24.2677 | 23.0831 | 22.0004 | 20.6269 | 18.6514 | 15.8698 | 13.1708 | 10.23 | 7.9933 | 5.9035 | -1.5863 | -7.3782 | -15.4384 | 21.778 | 20.2341 | 18.7535 | 16.8616 | 14.2657 | 10.8218 | 7.6637 | 4.2851 | 1.7228 | -0.57919 | -8.2731 | -13.072 | -17.4853
|  | MILTON | HT |  |  |  | 23.6484 | 21.9545 | 20.0586 | 17.4198 | 14.9708 | 11.4371 | 8.3535 | 5.1718 | 2.6728 | -0.014906 | -9.6833 | -16.2425 | -20.5476 | 24.6126 | 23.5973 | 22.5035 | 20.8055 | 19.2994 | 16.7728 | 14.3188 | 11.7422 | 9.8086 | 7.6249 | 0.11469 | -4.2945 | -7.1649 | 22.1157 | 20.6912 | 19.0851 | 16.7698 | 14.6504 | 11.4371 | 8.4484 | 5.3463 | 2.9269 | 0.29326 | -9.0598 | -15.3516 | -19.4506
|  | MILTON | HE |  |  |  | 23.6382 | 21.9861 | 20.1259 | 18.0453 | 15.981 | 12.329 | 9.5728 | 6.6841 | 4.6116 | 2.5575 | -6.571 | -12.3506 | -16.0731 | 24.5259 | 23.4535 | 22.281 | 20.9841 | 19.8004 | 17.1004 | 14.8341 | 12.3555 | 10.6535 | 8.928 | 0.11775 | -5.8241 | -13.5282 | 22.0994 | 20.7014 | 19.1157 | 17.3249 | 15.5922 | 12.2586 | 9.6361 | 6.8382 | 4.8953 | 2.9667 | -6.1945 | -11.1312 | -14.57
|  | MILTON | CF |  |  |  | 23.9402 | 22.6055 | 21.0912 | 19.431 | 17.0126 | 14.2024 | 12.1953 | 9.9616 | 8.2657 | 6.6637 | -0.41491 | -5.4516 | -9.3874 | 24.6841 | 23.7575 | 22.7351 | 21.628 | 19.9075 | 17.6667 | 15.7984 | 13.6545 | 11.9943 | 10.4157 | 3.3331 | -4.6047 | -16.8241 | 22.3739 | 21.2647 | 19.9943 | 18.5831 | 16.4667 | 13.9208 | 12.03 | 9.8708 | 8.2371 | 6.7208 | 0.34122 | -4.1241 | -7.8363
MANNINGTON GSP | SHAFTESBURY BSP | MINCHINGTON | MINIMUM HEADROOM | ST 96164 14520 | YES | 0.475 | 4.1378 | 4.0755 | 4.0102 | 3.9378 | 3.85 | 3.7888 | 3.6755 | 3.5459 | 3.4571 | 3.3867 | 3.002 | 2.8745 | 2.7776 | 4.6592 | 4.6051 | 4.5551 | 4.4867 | 4.4061 | 4.3582 | 4.2602 | 4.1429 | 4.0684 | 4.0153 | 3.7694 | 3.4398 | 2.6673 | 4.8816 | 4.8122 | 4.7418 | 4.651 | 4.5408 | 4.4724 | 4.3388 | 4.1745 | 4.0714 | 4.0265 | 3.7745 | 3.6735 | 3.5847
|  | MINCHINGTON | EE |  |  |  | 4.1378 | 4.0755 | 4.0102 | 3.9378 | 3.85 | 3.7888 | 3.6755 | 3.5459 | 3.4571 | 3.3867 | 3.002 | 2.8745 | 2.8337 | 4.6592 | 4.6051 | 4.5551 | 4.4867 | 4.4061 | 4.3582 | 4.2602 | 4.1429 | 4.0684 | 4.0153 | 3.7694 | 3.548 | 3.1806 | 4.8816 | 4.8122 | 4.7418 | 4.651 | 4.5408 | 4.4724 | 4.3388 | 4.1745 | 4.0714 | 4.0265 | 3.7745 | 3.6735 | 3.6306
|  | MINCHINGTON | HT |  |  |  | 4.1735 | 4.1214 | 4.0673 | 4.0061 | 3.9561 | 3.8918 | 3.799 | 3.6969 | 3.6214 | 3.5184 | 3.0939 | 2.902 | 2.7776 | 4.7031 | 4.6684 | 4.6316 | 4.5837 | 4.5551 | 4.5082 | 4.4378 | 4.3612 | 4.3173 | 4.2378 | 3.9551 | 3.8582 | 3.8031 | 4.9418 | 4.8929 | 4.8367 | 4.7684 | 4.7224 | 4.6541 | 4.5571 | 4.4459 | 4.3765 | 4.2612 | 3.8439 | 3.6847 | 3.5847
|  | MINCHINGTON | HE |  |  |  | 4.1714 | 4.1235 | 4.0684 | 4.0092 | 3.9612 | 3.898 | 3.8102 | 3.7092 | 3.6378 | 3.5367 | 3.0541 | 2.9327 | 2.8939 | 4.699 | 4.6633 | 4.6235 | 4.5694 | 4.5357 | 4.4857 | 4.4184 | 4.3327 | 4.2827 | 4.1918 | 3.8224 | 3.5959 | 3.2347 | 4.9408 | 4.8929 | 4.8388 | 4.7704 | 4.7276 | 4.6622 | 4.5704 | 4.4612 | 4.3949 | 4.2847 | 3.8388 | 3.7408 | 3.7051
|  | MINCHINGTON | CF |  |  |  | 4.1847 | 4.1429 | 4.0908 | 4.049 | 3.9949 | 3.9561 | 3.901 | 3.8388 | 3.7714 | 3.7265 | 3.3592 | 3.1459 | 2.9459 | 4.7071 | 4.6776 | 4.6347 | 4.601 | 4.5561 | 4.5255 | 4.4724 | 4.4092 | 4.3449 | 4.3031 | 3.8694 | 3.4398 | 2.6673 | 4.9561 | 4.9173 | 4.8612 | 4.8163 | 4.7612 | 4.7265 | 4.6663 | 4.601 | 4.5245 | 4.4878 | 4.0684 | 3.8939 | 3.7408
MINETY GSP | CIRENCESTER BSP | MINETY VILLAGE | MINIMUM HEADROOM | SU 01647 91932 | YES | 0.399 | 11.0985 | 10.774 | 10.275 | 9.673 | 8.873 | 7.9199 | 7.1719 | 6.3852 | 5.6454 | 4.875 | 2.727 | 2.4026 | 2.1281 | 12.6969 | 12.5204 | 12.2541 | 11.95 | 11.5408 | 11.0776 | 10.6898 | 10.2561 | 9.8459 | 9.4551 | 8.2276 | 7.4051 | 5.3898 | 11.8888 | 11.6163 | 11.2 | 10.7071 | 10.0469 | 9.2633 | 8.6469 | 7.9898 | 7.3694 | 6.7378 | 4.95 | 4.6673 | 4.4296
|  | MINETY VILLAGE | EE |  |  |  | 11.0985 | 10.774 | 10.275 | 9.673 | 8.873 | 7.9199 | 7.1719 | 6.3852 | 5.6454 | 4.875 | 2.727 | 2.4026 | 2.2546 | 12.6969 | 12.5204 | 12.2541 | 11.95 | 11.5408 | 11.0776 | 10.6898 | 10.2561 | 9.8459 | 9.4551 | 8.2276 | 7.6184 | 6.6765 | 11.8888 | 11.6163 | 11.2 | 10.7071 | 10.0469 | 9.2633 | 8.6469 | 7.9898 | 7.3694 | 6.7378 | 4.95 | 4.6673 | 4.5418
|  | MINETY VILLAGE | HT |  |  |  | 11.173 | 10.8597 | 10.4015 | 9.8077 | 9.027 | 8.1362 | 7.3883 | 6.6454 | 5.9423 | 5.1607 | 2.9005 | 2.4168 | 2.1281 | 12.7724 | 12.6163 | 12.3918 | 12.1031 | 11.7439 | 11.35 | 10.9878 | 10.6214 | 10.2673 | 9.8929 | 8.7245 | 8.4592 | 8.3245 | 11.9704 | 11.7133 | 11.3408 | 10.849 | 10.2102 | 9.4765 | 8.8633 | 8.249 | 7.6633 | 7.0255 | 5.1082 | 4.6755 | 4.4296
|  | MINETY VILLAGE | HE |  |  |  | 11.1699 | 10.8597 | 10.4066 | 9.8148 | 9.0413 | 8.1556 | 7.4189 | 6.6821 | 5.9893 | 5.2209 | 2.877 | 2.5434 | 2.4138 | 12.7643 | 12.598 | 12.3653 | 12.0673 | 11.6929 | 11.2918 | 10.9173 | 10.5316 | 10.1633 | 9.7684 | 8.3347 | 7.7041 | 6.7735 | 11.9643 | 11.7143 | 11.3449 | 10.8531 | 10.2214 | 9.4969 | 8.8908 | 8.2837 | 7.7071 | 7.0827 | 5.0969 | 4.802 | 4.6929
|  | MINETY VILLAGE | CF |  |  |  | 11.2015 | 10.9281 | 10.5077 | 10.0046 | 9.3464 | 8.574 | 7.9413 | 7.3464 | 6.7546 | 6.0526 | 4.0515 | 3.2832 | 2.6158 | 12.7837 | 12.6357 | 12.4071 | 12.15 | 11.8204 | 11.4408 | 11.1 | 10.7857 | 10.4541 | 10.0582 | 8.648 | 7.4051 | 5.3898 | 11.9969 | 11.7755 | 11.4316 | 11.0296 | 10.498 | 9.8704 | 9.3643 | 8.8847 | 8.4041 | 7.8316 | 6.1469 | 5.45 | 4.8622
BRAMLEY (FLEE) | BURGHFIELD RESERVE | MORTIMER | MINIMUM HEADROOM | SU 62236 64103 | YES | 1.522 | 5.7043 | 5.292 | 4.8788 | 4.4573 | 4.0747 | 4.0237 | 3.5594 | 3.0461 | 2.5073 | 2.1288 | -0.031449 | -1.5406 | -2.41 | 5.6915 | 5.4313 | 5.1558 | 4.8538 | 4.5548 | 4.6048 | 4.3191 | 3.9762 | 3.6303 | 3.4772 | 2.1864 | 0.62824 | -3.3371 | 5.5048 | 5.1476 | 4.7721 | 4.3558 | 3.9456 | 4.0466 | 3.6038 | 3.0997 | 2.5915 | 2.2823 | 0.61804 | -0.66767 | -1.3942
|  | MORTIMER | EE |  |  |  | 5.7043 | 5.292 | 4.8788 | 4.4573 | 4.0747 | 4.0237 | 3.5594 | 3.0461 | 2.5073 | 2.1288 | 0.062429 | -1.2876 | -2.2131 | 5.6915 | 5.4313 | 5.1558 | 4.8538 | 4.5548 | 4.6048 | 4.3191 | 3.9762 | 3.6303 | 3.4772 | 2.1864 | 0.816 | -1.2503 | 5.5048 | 5.1476 | 4.7721 | 4.3558 | 3.9456 | 4.0466 | 3.6038 | 3.0997 | 2.5915 | 2.2823 | 0.69559 | -0.42788 | -1.2156
|  | MORTIMER | HT |  |  |  | 5.8114 | 5.4114 | 5.04 | 4.6757 | 4.393 | 4.0757 | 3.591 | 3.0686 | 2.8798 | 2.3981 | -0.031449 | -1.5406 | -2.41 | 5.8344 | 5.5946 | 5.3772 | 5.1487 | 4.9905 | 4.7884 | 4.5323 | 4.2395 | 4.1987 | 3.9497 | 2.768 | 2.1629 | 1.8109 | 5.6813 | 5.3384 | 5.0221 | 4.6844 | 4.4282 | 4.1109 | 3.6507 | 3.1395 | 3.1701 | 2.7252 | 0.61804 | -0.66767 | -1.3942
|  | MORTIMER | HE |  |  |  | 5.8216 | 5.4349 | 5.0777 | 4.7308 | 4.4655 | 4.1788 | 3.7798 | 3.341 | 3.24 | 2.8369 | 0.64304 | -0.70084 | -1.3263 | 5.8231 | 5.5823 | 5.3629 | 5.1303 | 4.9731 | 4.7752 | 4.5333 | 4.2497 | 4.2344 | 3.9721 | 2.4731 | 1.0782 | -0.86767 | 5.6833 | 5.3517 | 5.0466 | 4.7221 | 4.4833 | 4.1915 | 3.7987 | 3.3517 | 3.4527 | 3.0731 | 1.1976 | 0.10478 | -0.42278
|  | MORTIMER | CF |  |  |  | 5.8859 | 5.5849 | 5.2951 | 5.0298 | 4.8094 | 4.6532 | 4.4747 | 4.2543 | 4.0247 | 4.1022 | 2.689 | 1.2175 | -0.14676 | 5.8466 | 5.6538 | 5.465 | 5.2782 | 5.117 | 5.0048 | 4.8538 | 4.6619 | 4.4507 | 4.5619 | 2.9476 | 0.62824 | -3.3371 | 5.7272 | 5.4833 | 5.2415 | 4.9936 | 4.7721 | 4.6242 | 4.4221 | 4.1752 | 3.9089 | 4.1333 | 2.7599 | 1.5507 | 0.53131
MANNINGTON GSP | SALISBURY | NETHERHAMPTON | MINIMUM HEADROOM | SU 12478 29102 | YES | 5.006 | 5.9939 | 2.3124 | 2.0237 | 1.7706 | 1.3114 | 0.6849 | 0.055306 | -0.66408 | -1.1498 | -1.5824 | -2.8508 | -3.6763 | -3.9988 | 9.7112 | 6.1533 | 5.9767 | 5.7992 | 5.5339 | 5.1788 | 4.8073 | 4.3696 | 4.1941 | 3.9696 | 2.9869 | 1.6961 | -1.21 | 7.3643 | 3.7247 | 3.4696 | 3.2186 | 2.8278 | 2.29 | 1.738 | 1.0992 | 0.81449 | 0.47776 | -0.59878 | -1.2957 | -1.56
|  | NETHERHAMPTON | EE |  |  |  | 5.9939 | 2.3124 | 2.0237 | 1.7706 | 1.3114 | 0.6849 | 0.055306 | -0.66408 | -1.1314 | -1.5049 | -2.8478 | -3.5906 | -3.8682 | 9.7112 | 6.1533 | 5.9767 | 5.7992 | 5.5339 | 5.1788 | 4.8073 | 4.3696 | 4.1941 | 3.9696 | 2.9869 | 2.0124 | 0.64408 | 7.3643 | 3.7247 | 3.4696 | 3.2186 | 2.8278 | 2.29 | 1.738 | 1.0992 | 0.81449 | 0.50429 | -0.59878 | -1.2141 | -1.4498
|  | NETHERHAMPTON | HT |  |  |  | 6.0592 | 2.3788 | 2.1165 | 1.9033 | 1.4461 | 0.80837 | 0.11551 | -0.53449 | -1.1498 | -1.5824 | -2.8508 | -3.6763 | -3.9988 | 9.7806 | 6.2543 | 6.1206 | 6.0002 | 5.7747 | 5.4604 | 5.1145 | 4.7971 | 4.4767 | 4.2329 | 3.6206 | 3.2359 | 3.089 | 7.451 | 3.8308 | 3.5971 | 3.4012 | 3.0318 | 2.5104 | 1.9369 | 1.4022 | 0.87469 | 0.47776 | -0.58959 | -1.2957 | -1.56
|  | NETHERHAMPTON | HE |  |  |  | 6.0582 | 2.4165 | 2.1431 | 1.9298 | 1.5012 | 0.91245 | 0.3451 | -0.24878 | -0.93347 | -1.3937 | -2.5478 | -3.2722 | -3.5304 | 9.7622 | 6.239 | 6.0767 | 5.9359 | 5.7012 | 5.3839 | 5.0604 | 4.7308 | 4.338 | 4.0431 | 3.1033 | 2.1155 | 0.77061 | 7.448 | 3.8584 | 3.6196 | 3.4227 | 3.0798 | 2.5951 | 2.1196 | 1.6329 | 1.0553 | 0.64204 | -0.30796 | -0.91306 | -1.1212
|  | NETHERHAMPTON | CF |  |  |  | 6.1857 | 2.6318 | 2.4696 | 2.3492 | 2.0614 | 1.7645 | 1.4767 | 1.1155 | 0.73082 | 0.45633 | -1.4416 | -2.161 | -3.1212 | 9.8286 | 6.339 | 6.2247 | 6.1247 | 5.941 | 5.7492 | 5.541 | 5.2829 | 5.0206 | 4.79 | 3.1798 | 1.6961 | -1.21 | 7.5357 | 4.0267 | 3.8849 | 3.7737 | 3.5267 | 3.292 | 3.042 | 2.7318 | 2.4155 | 2.1645 | 0.47469 | -0.0059184 | -0.80694
BOTLEY WOOD GSP | NETLEY COMMON BSP | NETLEY COMMON | MINIMUM HEADROOM | SU 47615 12025 | YES | 6.122 | -1.8127 | -2.477 | -3.8107 | -5.3453 | -6.9117 | -8.2964 | -10.2831 | -12.4739 | -14.6729 | -16.2913 | -25.2933 | -32.3566 | -36.1219 | 5.2649 | 4.8016 | 3.871 | 2.8883 | 1.8414 | 0.85567 | -0.48106 | -2.127 | -3.8627 | -5.1066 | -12.3617 | -23.5862 | -48.2321 | -0.30657 | -0.87902 | -2.1433 | -3.5453 | -5.0076 | -6.3535 | -8.227 | -10.329 | -12.4351 | -13.8872 | -21.4035 | -27.4331 | -30.6494
|  | NETLEY COMMON | EE |  |  |  | -1.8127 | -2.477 | -3.8107 | -5.3453 | -6.9117 | -8.2964 | -10.2831 | -12.4739 | -14.6729 | -16.2913 | -24.6402 | -30.7127 | -35.3821 | 5.2649 | 4.8016 | 3.871 | 2.8883 | 1.8414 | 0.85567 | -0.48106 | -2.127 | -3.8627 | -5.1066 | -12.3617 | -20.8096 | -33.8525 | -0.30657 | -0.87902 | -2.1433 | -3.5453 | -5.0076 | -6.3535 | -8.227 | -10.329 | -12.4351 | -13.8872 | -20.9994 | -26.0004 | -30.0586
|  | NETLEY COMMON | HT |  |  |  | -1.329 | -2.1933 | -3.4198 | -4.5209 | -5.7933 | -6.8637 | -8.576 | -10.4331 | -12.3953 | -14.4351 | -25.2933 | -32.3566 | -36.1219 | 5.6771 | 5.1557 | 4.4904 | 3.9485 | 3.274 | 2.6965 | 1.8342 | 0.87098 | -0.15147 | -1.2178 | -7.0678 | -10.5086 | -12.2127 | 0.22812 | -0.60249 | -1.7056 | -2.576 | -3.7178 | -4.729 | -6.277 | -7.9892 | -9.7964 | -11.6821 | -21.4035 | -27.4331 | -30.6494
|  | NETLEY COMMON | HE |  |  |  | -1.3219 | -2.0862 | -3.2739 | -4.2198 | -5.4443 | -6.476 | -7.876 | -9.3984 | -11.0076 | -12.677 | -21.5821 | -27.8545 | -30.7015 | 5.5679 | 5.0251 | 4.171 | 3.5536 | 2.7057 | 1.924 | 0.93833 | -0.15759 | -1.3474 | -2.6168 | -10.7525 | -19.5372 | -31.7943 | 0.2271 | -0.4729 | -1.5882 | -2.33 | -3.4219 | -4.3872 | -5.6719 | -7.0964 | -8.6015 | -10.1729 | -18.2056 | -23.4504 | -25.8739
|  | NETLEY COMMON | CF |  |  |  | -0.96678 | -1.4535 | -2.2433 | -3.1464 | -3.5464 | -4.0964 | -4.627 | -5.3127 | -6.0647 | -6.8668 | -12.9913 | -19.4443 | -25.2964 | 5.7322 | 5.2904 | 4.6526 | 3.8781 | 3.4312 | 2.7608 | 1.9955 | 1.0853 | 0.098531 | -0.9729 | -9.4525 | -23.5862 | -48.2321 | 0.55159 | 0.10261 | -0.60963 | -1.4658 | -1.7474 | -2.28 | -2.8025 | -3.4749 | -4.2188 | -5.0066 | -10.7964 | -16.4647 | -21.3902
MANNINGTON GSP | ARNEWOOD | NEW MILTON | MINIMUM HEADROOM | SZ 23049 94942 | YES | 1.464 | 11.5796 | 10.9388 | 10.5694 | 9.8745 | 9.1031 | 8.2153 | 6.7255 | 5.0684 | 3.4286 | 2.2041 | -4.0133 | -8.7663 | -11.3388 | 14.7276 | 14.2245 | 13.9296 | 13.3622 | 12.7133 | 11.9827 | 10.9602 | 9.7663 | 8.5633 | 7.7041 | 3.0541 | -2.7898 | -16.6633 | 11.3316 | 10.6959 | 10.3776 | 9.6908 | 8.9255 | 8.0551 | 6.6694 | 5.1051 | 3.5571 | 2.4694 | -2.7796 | -6.8265 | -8.9724
|  | NEW MILTON | EE |  |  |  | 11.5796 | 10.9388 | 10.5694 | 9.8745 | 9.1031 | 8.2153 | 6.7255 | 5.0684 | 3.4286 | 2.2041 | -3.6867 | -7.7755 | -10.9969 | 14.7276 | 14.2245 | 13.9296 | 13.3622 | 12.7133 | 11.9827 | 10.9602 | 9.7663 | 8.5633 | 7.7041 | 3.0541 | -1.7582 | -8.9163 | 11.3316 | 10.6959 | 10.3776 | 9.6908 | 8.9255 | 8.0551 | 6.6694 | 5.1051 | 3.5571 | 2.4694 | -2.5837 | -5.9633 | -8.6898
|  | NEW MILTON | HT |  |  |  | 11.9214 | 11.399 | 10.8602 | 10.2469 | 9.9418 | 9.2398 | 7.9122 | 6.4765 | 4.9949 | 3.4633 | -4.0133 | -8.7663 | -11.3388 | 15.0735 | 14.752 | 14.4122 | 14.0041 | 13.85 | 13.4031 | 12.6898 | 11.8867 | 11.0429 | 10.1531 | 6.0582 | 3.7663 | 2.6867 | 11.7082 | 11.2092 | 10.6939 | 10.0949 | 9.8582 | 9.1969 | 8.0061 | 6.701 | 5.352 | 3.9469 | -2.7796 | -6.8265 | -8.9724
|  | NEW MILTON | HE |  |  |  | 11.9194 | 11.4367 | 10.9347 | 10.3541 | 10.0806 | 9.4122 | 8.3 | 7.0663 | 5.7898 | 4.4888 | -2.0551 | -6.4357 | -8.4153 | 14.999 | 14.6224 | 14.2163 | 13.7398 | 13.4908 | 12.9347 | 12.1643 | 11.2796 | 10.3398 | 9.3449 | 3.8327 | -1.2908 | -7.9643 | 11.699 | 11.2357 | 10.752 | 10.1786 | 9.9755 | 9.3408 | 8.3337 | 7.198 | 6.0214 | 4.8082 | -1.1204 | -4.8122 | -6.4255
|  | NEW MILTON | CF |  |  |  | 12.1439 | 11.8969 | 11.6204 | 11.2898 | 10.9204 | 10.8316 | 10.3602 | 9.799 | 9.199 | 8.5745 | 4.3888 | -0.31939 | -4.5459 | 15.1112 | 14.848 | 14.5439 | 14.1847 | 13.7673 | 13.5408 | 12.9796 | 12.3184 | 11.6082 | 10.8439 | 5.5265 | -2.7898 | -16.6633 | 11.9 | 11.6531 | 11.3735 | 11.0367 | 10.6602 | 10.6286 | 10.1837 | 9.6439 | 9.0653 | 8.4592 | 4.452 | 0.29694 | -3.2776
FAWLEY GSP | COWES & WOOTTON COMMON BSP | NEWPORT | MINIMUM HEADROOM | SZ 50076 89544 | YES | 6.723 | 28.3562 | 27.6817 | 26.9266 | 25.9705 | 24.8164 | 23.3786 | 21.7358 | 19.7858 | 17.7103 | 16.0705 | 8.4735 | 2.795 | -0.2979 | 30.2133 | 29.8174 | 29.4235 | 28.8664 | 28.0092 | 26.8837 | 25.6011 | 24.2082 | 22.799 | 21.7092 | 16.348 | 11.3399 | -1.5959 | 27.0348 | 26.5246 | 25.9817 | 25.2225 | 23.9939 | 22.4919 | 20.7256 | 18.8756 | 17.0246 | 15.5756 | 8.9031 | 4.1092 | 1.496
|  | NEWPORT | EE |  |  |  | 28.3562 | 27.6817 | 26.9266 | 25.9705 | 24.8164 | 23.3786 | 21.7358 | 19.7858 | 17.7103 | 16.0705 | 8.4735 | 3.7154 | 0.25414 | 30.2133 | 29.8174 | 29.4235 | 28.8664 | 28.0092 | 26.8837 | 25.6011 | 24.2082 | 22.799 | 21.7092 | 16.348 | 11.5725 | 4.8654 | 27.0348 | 26.5246 | 25.9817 | 25.2225 | 23.9939 | 22.4919 | 20.7256 | 18.8756 | 17.0246 | 15.5756 | 8.9031 | 4.8194 | 1.8633
|  | NEWPORT | HT |  |  |  | 28.8021 | 28.2592 | 27.5205 | 26.6858 | 25.5919 | 24.2409 | 22.4378 | 20.6654 | 18.899 | 17.1725 | 8.5123 | 2.795 | -0.2979 | 30.4827 | 30.1919 | 29.7878 | 29.3358 | 28.6327 | 28.0031 | 27.0562 | 26.0705 | 25.0684 | 24.0643 | 19.299 | 16.4919 | 15.149 | 27.3388 | 26.9113 | 26.3103 | 25.3623 | 24.1194 | 23.0052 | 21.4746 | 19.9205 | 18.3592 | 16.8246 | 9.1164 | 4.1092 | 1.496
|  | NEWPORT | HE |  |  |  | 28.699 | 28.1531 | 27.4286 | 26.5888 | 25.5807 | 24.4225 | 22.9501 | 21.2715 | 19.4939 | 17.7194 | 9.4562 | 4.7103 | 2.5439 | 30.4103 | 30.1031 | 29.6888 | 29.2154 | 28.5276 | 27.8215 | 26.7705 | 25.6429 | 24.448 | 23.2205 | 17.0725 | 11.847 | 5.6939 | 27.2735 | 26.8643 | 26.3052 | 25.645 | 24.5184 | 23.4694 | 22.0286 | 20.5266 | 18.945 | 17.4735 | 10.147 | 5.646 | 3.8388
|  | NEWPORT | CF |  |  |  | 29.0868 | 28.7766 | 28.3878 | 27.9633 | 27.4388 | 26.8521 | 26.3501 | 25.5643 | 24.6654 | 23.6337 | 16.7154 | 10.9756 | 6.5664 | 30.6031 | 30.4011 | 30.147 | 29.8705 | 29.5266 | 29.0541 | 28.6399 | 27.8633 | 27.0011 | 26.0848 | 19.5664 | 11.3399 | -1.5959 | 27.546 | 27.3072 | 27.0052 | 26.6786 | 26.2746 | 25.8225 | 25.496 | 24.8868 | 24.1011 | 23.2766 | 17.0776 | 11.7715 | 7.5725
BRAMLEY (FLEE) | ALDERSHOT BSP | NORMANDY | MINIMUM HEADROOM | SU 93221 52894 | YES | 1.331 | 4.4738 | 4.3698 | 4.2728 | 4.1473 | 4.0034 | 3.8902 | 3.7055 | 3.4983 | 3.3381 | 3.2463 | 2.7432 | 2.3432 | 2.1341 | 5.2085 | 5.1351 | 5.0698 | 4.9881 | 4.8912 | 4.8208 | 4.7014 | 4.5657 | 4.4636 | 4.4024 | 4.0708 | 3.7412 | 2.8994 | 4.6647 | 4.5738 | 4.4851 | 4.3698 | 4.2341 | 4.131 | 3.9555 | 3.7585 | 3.6136 | 3.5351 | 3.0973 | 2.7575 | 2.583
|  | NORMANDY | EE |  |  |  | 4.4738 | 4.3698 | 4.2728 | 4.1473 | 4.0034 | 3.8902 | 3.7055 | 3.4983 | 3.3381 | 3.2463 | 2.781 | 2.4208 | 2.1698 | 5.2085 | 5.1351 | 5.0698 | 4.9881 | 4.8912 | 4.8208 | 4.7014 | 4.5657 | 4.4636 | 4.4024 | 4.0708 | 3.7473 | 3.3075 | 4.6647 | 4.5738 | 4.4851 | 4.3698 | 4.2341 | 4.131 | 3.9555 | 3.7585 | 3.6136 | 3.5351 | 3.131 | 2.8249 | 2.6147
|  | NORMANDY | HT |  |  |  | 4.5045 | 4.4259 | 4.33 | 4.2177 | 4.1187 | 3.9953 | 3.8238 | 3.679 | 3.4912 | 3.3453 | 2.7432 | 2.3432 | 2.1341 | 5.2351 | 5.1912 | 5.1361 | 5.0708 | 5.0157 | 4.9463 | 4.8494 | 4.7728 | 4.6677 | 4.5759 | 4.2361 | 4.0647 | 3.9759 | 4.6922 | 4.6249 | 4.5422 | 4.4432 | 4.3534 | 4.2453 | 4.0932 | 3.9626 | 3.7963 | 3.6626 | 3.0973 | 2.7575 | 2.583
|  | NORMANDY | HE |  |  |  | 4.5045 | 4.433 | 4.3422 | 4.2341 | 4.1412 | 4.0208 | 3.8749 | 3.7524 | 3.5861 | 3.4636 | 2.9279 | 2.5983 | 2.431 | 5.232 | 5.1841 | 5.1259 | 5.0555 | 5.0004 | 4.9228 | 4.831 | 4.7555 | 4.6473 | 4.5545 | 4.1453 | 3.8218 | 3.4136 | 4.6932 | 4.631 | 4.5534 | 4.4585 | 4.3759 | 4.2687 | 4.1412 | 4.033 | 3.8841 | 3.7626 | 3.2749 | 2.981 | 2.8432
|  | NORMANDY | CF |  |  |  | 4.529 | 4.4738 | 4.4075 | 4.3259 | 4.2585 | 4.1626 | 4.083 | 3.982 | 3.8708 | 3.8422 | 3.4371 | 3.0341 | 2.6983 | 5.2473 | 5.2055 | 5.1585 | 5.0994 | 5.0545 | 4.9892 | 4.9249 | 4.8443 | 4.7575 | 4.7177 | 4.2983 | 3.7412 | 2.8994 | 4.7147 | 4.6698 | 4.6136 | 4.5422 | 4.4851 | 4.4014 | 4.33 | 4.233 | 4.129 | 4.0994 | 3.6994 | 3.3473 | 3.0616
NURSLING GSP | ROWNHAMS | NORTH BADDESLEY | MINIMUM HEADROOM | SU 38080 20568 | YES | 15.737 | 7.6723 | 6.0254 | 4.9315 | 4.0182 | 2.5784 | -5.2553 | -7.7961 | -10.9277 | -16.5573 | -21.1348 | -38.7063 | -48.7685 | -56.7685 | 9.5029 | 8.0998 | 7.3356 | 6.3703 | 5.2498 | -2.7318 | -4.9338 | -7.6308 | -13.3859 | -17.8583 | -33.642 | -43.7022 | -53.3236 | 7.6794 | 6.1029 | 5.1009 | 4.0743 | 2.7549 | -5.6002 | -8.2226 | -11.4369 | -17.7389 | -22.743 | -40.7604 | -51.9206 | -61.643
|  | NORTH BADDESLEY | EE |  |  |  | 7.6723 | 6.0254 | 4.9315 | 4.1172 | 2.5784 | -4.4002 | -6.8706 | -9.2889 | -12.2961 | -14.8216 | -27.5685 | -40.0634 | -44.5859 | 9.5029 | 8.0998 | 7.3356 | 6.6692 | 5.5335 | -1.0961 | -3.1206 | -4.9073 | -7.4951 | -9.5491 | -20.8369 | -33.9563 | -38.6624 | 7.6794 | 6.1029 | 5.1009 | 4.2866 | 2.8152 | -4.1951 | -6.6848 | -8.9991 | -12.093 | -14.6226 | -27.5491 | -41.7746 | -46.8604
|  | NORTH BADDESLEY | HT |  |  |  | 8.1743 | 6.6621 | 5.6029 | 4.4213 | 3.3192 | -3.8675 | -5.5859 | -8.0267 | -10.1848 | -13.5216 | -27.5716 | -40.1318 | -47.7481 | 9.96 | 8.7254 | 7.9876 | 7.0713 | 6.3835 | -0.71444 | -2.5828 | -4.9104 | -6.5685 | -9.6257 | -22.1134 | -34.9246 | -43.1502 | 8.1549 | 6.7396 | 5.7509 | 4.5845 | 3.5896 | -3.8012 | -5.6257 | -8.3848 | -10.4971 | -13.9767 | -28.3777 | -42.4961 | -51.3165
|  | NORTH BADDESLEY | HE |  |  |  | 8.1039 | 6.5733 | 5.4274 | 4.0182 | 2.7182 | -5.2553 | -7.7961 | -10.9277 | -16.5573 | -21.1348 | -38.7063 | -48.7685 | -56.7685 | 9.859 | 8.5662 | 7.66 | 6.3703 | 5.2498 | -2.7318 | -4.9338 | -7.6308 | -13.3859 | -17.8583 | -33.642 | -43.7022 | -53.3236 | 8.0886 | 6.6498 | 5.5447 | 4.0743 | 2.7549 | -5.6002 | -8.2226 | -11.4369 | -17.7389 | -22.743 | -40.7604 | -51.9206 | -61.643
|  | NORTH BADDESLEY | CF |  |  |  | 8.508 | 7.258 | 6.6917 | 6.2631 | 5.5907 | -0.0032163 | -0.87669 | -1.6114 | -3.1338 | -4.8297 | -15.3624 | -27.5542 | -35.2951 | 10.1254 | 8.9927 | 8.5672 | 8.2019 | 7.56 | 1.9917 | 1.0794 | 0.42229 | -0.60526 | -1.9655 | -10.8777 | -22.2236 | -33.6695 | 8.4641 | 7.2947 | 6.7856 | 6.3917 | 5.7049 | 0.090661 | -0.82362 | -1.643 | -3.1675 | -4.8746 | -15.5634 | -28.1155 | -36.3195
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | NORTH FAREHAM | MINIMUM HEADROOM | SU 56427 07430 | YES | 8.742 | 0.13776 | -0.2949 | -0.84082 | -0.8898 | -1.3857 | -1.9143 | -2.9112 | -4.0786 | -5.3194 | -6.4765 | -12.0898 | -15.3265 | -17.1612 | 4.0418 | 3.7367 | 3.3439 | 3.2235 | 2.8429 | 2.4276 | 1.6796 | 0.77959 | -0.22143 | -1.0745 | -5.2969 | -9.0337 | -17.9643 | 0.41531 | 0.012245 | -0.51122 | -0.54082 | -1.0133 | -1.5153 | -2.4745 | -3.6051 | -4.8265 | -5.7541 | -10.7724 | -13.5847 | -15.1082
|  | NORTH FAREHAM | EE |  |  |  | 0.13776 | -0.2949 | -0.84082 | -0.8898 | -1.3857 | -1.9143 | -2.9112 | -4.0786 | -5.3194 | -6.2663 | -11.7102 | -14.701 | -16.9122 | 4.0418 | 3.7367 | 3.3439 | 3.2235 | 2.8429 | 2.4276 | 1.6796 | 0.77959 | -0.22143 | -1.0745 | -5.2969 | -8.5092 | -13.2551 | 0.41531 | 0.012245 | -0.51122 | -0.54082 | -1.0133 | -1.5153 | -2.4745 | -3.6051 | -4.8265 | -5.7541 | -10.4949 | -13.0633 | -14.9204
|  | NORTH FAREHAM | HT |  |  |  | 0.35918 | -0.0020408 | -0.33673 | -0.75 | -1.2112 | -1.551 | -2.5684 | -3.7663 | -5.1622 | -6.4765 | -12.0898 | -15.3265 | -17.1612 | 4.2459 | 4.0347 | 3.8224 | 3.5684 | 3.2918 | 2.9939 | 2.3694 | 1.5796 | 0.6102 | -0.26633 | -3.4378 | -4.8612 | -5.6041 | 0.66939 | 0.32959 | -0.0040816 | -0.4051 | -0.84184 | -1.0898 | -2.0306 | -3.1561 | -4.4816 | -5.7031 | -10.7724 | -13.5847 | -15.1082
|  | NORTH FAREHAM | HE |  |  |  | 0.37551 | 0.060204 | -0.26327 | -0.65306 | -1.0827 | -1.0867 | -1.8653 | -2.7755 | -3.8071 | -4.9143 | -10.4796 | -13.4306 | -14.8459 | 4.2082 | 3.9745 | 3.7122 | 3.4163 | 3.0898 | 2.9959 | 2.4092 | 1.6949 | 0.8602 | -0.056122 | -4.6663 | -7.9184 | -12.348 | 0.67551 | 0.36837 | 0.05 | -0.32041 | -0.73163 | -0.69388 | -1.399 | -2.2612 | -3.2541 | -4.3194 | -9.3633 | -11.902 | -13.0694
|  | NORTH FAREHAM | CF |  |  |  | 0.52857 | 0.33878 | 0.090816 | -0.12245 | -0.39082 | -0.67959 | -1.0143 | -0.94796 | -1.4224 | -1.9418 | -6.3888 | -9.3347 | -12.1398 | 4.2847 | 4.1 | 3.8806 | 3.6633 | 3.399 | 3.0939 | 2.7296 | 2.5061 | 1.9347 | 1.2969 | -3.8429 | -9.0337 | -17.9643 | 0.81224 | 0.61531 | 0.37245 | 0.17755 | -0.079592 | -0.35918 | -0.67551 | -0.6051 | -1.0786 | -1.6071 | -5.8684 | -8.4306 | -10.8051
LALEHAM | EAST BEDFONT A | NORTH FELTHAM | MINIMUM HEADROOM | TQ 10987 74875 | YES | 8.857 | 5.8456 | 5.4487 | 4.9232 | 4.3865 | 3.7171 | 2.6365 | 1.8324 | 0.4783 | -0.87578 | -2.0074 | -6.0074 | -8.2431 | -8.885 | 7.7133 | 7.4255 | 7.0419 | 6.6643 | 6.1868 | 5.3368 | 4.6653 | 3.7602 | 2.7133 | 1.8439 | -1.2398 | -7.6367 | -20.3612 | 5.9988 | 5.6509 | 5.1815 | 4.7131 | 4.1274 | 3.1274 | 2.1835 | 0.86208 | -0.41547 | -1.4889 | -5.291 | -7.4073 | -8.0032
|  | NORTH FELTHAM | EE |  |  |  | 5.8456 | 5.4487 | 4.9232 | 4.3865 | 3.7171 | 2.6365 | 1.8324 | 0.4783 | -0.87578 | -2.0074 | -5.6084 | -6.835 | -8.0227 | 7.7133 | 7.4255 | 7.0419 | 6.6643 | 6.1868 | 5.3368 | 4.6653 | 3.7602 | 2.7133 | 1.8439 | -1.2398 | -5.1285 | -11.4622 | 5.9988 | 5.6509 | 5.1815 | 4.7131 | 4.1274 | 3.1274 | 2.1835 | 0.86208 | -0.41547 | -1.4889 | -4.8777 | -5.8328 | -6.2971
|  | NORTH FELTHAM | HT |  |  |  | 6.0477 | 5.6661 | 5.2303 | 4.7803 | 3.9691 | 2.9926 | 2.0232 | 1.0263 | 0.056873 | -0.49109 | -4.2962 | -6.7778 | -7.935 | 7.9051 | 7.6909 | 7.4602 | 7.2204 | 6.6133 | 5.9368 | 5.3347 | 4.7194 | 4.1266 | 3.5817 | 0.69085 | -0.61731 | -1.0408 | 6.1855 | 5.8621 | 5.4958 | 5.107 | 4.3406 | 3.4447 | 2.5815 | 1.6958 | 0.83555 | 0.34779 | -3.3226 | -5.19 | -6.1502
|  | NORTH FELTHAM | HE |  |  |  | 6.0181 | 5.6865 | 5.2497 | 4.8171 | 4.2814 | 3.3763 | 2.462 | 1.4201 | 0.32626 | -0.81558 | -6.0074 | -8.2431 | -8.885 | 7.8317 | 7.5929 | 7.2725 | 6.9562 | 6.5653 | 5.8398 | 5.1174 | 4.297 | 3.4388 | 2.7643 | -1.154 | -4.9989 | -11.1183 | 6.157 | 5.8713 | 5.4866 | 5.1039 | 4.6355 | 3.7988 | 2.9641 | 2.0029 | 0.76004 | -0.34098 | -5.291 | -7.4073 | -8.0032
|  | NORTH FELTHAM | CF |  |  |  | 6.2263 | 6.0365 | 5.8324 | 5.5967 | 5.3477 | 5.0783 | 4.6946 | 4.1916 | 3.561 | 2.9344 | -1.6472 | -5.1462 | -7.6156 | 7.9409 | 7.7562 | 7.5531 | 7.299 | 7.0286 | 6.7021 | 6.1929 | 5.5766 | 4.8643 | 4.15 | -0.4367 | -7.6367 | -20.3612 | 6.3386 | 6.1774 | 5.9978 | 5.7835 | 5.5621 | 5.3233 | 4.96 | 4.4866 | 3.9039 | 3.2182 | -1.143 | -4.4767 | -6.8185
COWLEY GSP | OXFORD BSP | NORTH HINKSEY | MINIMUM HEADROOM | SP 48645 04403 | YES | 2.227 | 2.0032 | 1.8124 | 1.5971 | 1.3267 | 1.0318 | 0.71444 | 0.6573 | 0.18689 | -0.28352 | -0.59372 | -2.4305 | -3.7958 | -4.5774 | 1.3313 | 1.1823 | 1.0068 | 0.79046 | 0.54454 | 0.28536 | 0.2874 | -0.043212 | -0.37995 | -0.59627 | -1.8095 | -3.4432 | -7.3616 | 1.2573 | 1.0655 | 0.85118 | 0.57158 | 0.26444 | -0.064131 | -0.018212 | -0.46821 | -0.91923 | -1.1937 | -2.7539 | -3.959 | -4.6111
|  | NORTH HINKSEY | EE |  |  |  | 2.0032 | 1.8124 | 1.5971 | 1.3267 | 1.0318 | 0.71444 | 0.6573 | 0.18689 | -0.28352 | -0.59372 | -2.2203 | -3.4641 | -4.3713 | 1.3313 | 1.1823 | 1.0068 | 0.79046 | 0.54454 | 0.28536 | 0.2874 | -0.043212 | -0.37995 | -0.59627 | -1.8095 | -3.1861 | -5.2677 | 1.2573 | 1.0655 | 0.85118 | 0.57158 | 0.26444 | -0.064131 | -0.018212 | -0.46821 | -0.91923 | -1.1937 | -2.5743 | -3.6641 | -4.4366
|  | NORTH HINKSEY | HT |  |  |  | 2.1144 | 1.9532 | 1.7797 | 1.5695 | 1.3389 | 1.144 | 0.71138 | 0.23689 | 0.13791 | -0.29372 | -2.4305 | -3.7958 | -4.5774 | 1.4476 | 1.3466 | 1.2384 | 1.1017 | 0.93842 | 0.81495 | 0.56291 | 0.27107 | 0.32107 | 0.073114 | -1.0381 | -1.6402 | -1.985 | 1.3848 | 1.2328 | 1.0604 | 0.85016 | 0.61648 | 0.43689 | 0.026686 | -0.43046 | -0.42433 | -0.8274 | -2.7539 | -3.959 | -4.6111
|  | NORTH HINKSEY | HE |  |  |  | 2.144 | 1.9808 | 1.8267 | 1.6379 | 1.4287 | 1.2553 | 0.90832 | 0.51648 | 0.5073 | 0.16342 | -1.5845 | -2.7947 | -3.4417 | 1.4445 | 1.3139 | 1.1884 | 1.0333 | 0.85781 | 0.71189 | 0.46393 | 0.17618 | 0.19352 | -0.067702 | -1.5095 | -2.884 | -4.8636 | 1.4155 | 1.2542 | 1.1012 | 0.90628 | 0.69403 | 0.53179 | 0.19301 | -0.19168 | -0.10699 | -0.43454 | -2.0121 | -3.0662 | -3.6172
|  | NORTH HINKSEY | CF |  |  |  | 2.1971 | 2.1134 | 1.9889 | 1.9042 | 1.7736 | 1.6318 | 1.5195 | 1.3287 | 1.1226 | 0.9073 | 0.069543 | -1.1743 | -2.3968 | 1.4639 | 1.3752 | 1.2456 | 1.1456 | 1.0098 | 0.85169 | 0.70169 | 0.4823 | 0.24964 | -0.0003551 | -1.2024 | -3.4432 | -7.3616 | 1.4583 | 1.3746 | 1.243 | 1.1522 | 1.0134 | 0.8624 | 0.75832 | 0.55424 | 0.33587 | 0.10526 | -0.60801 | -1.7029 | -2.7131
NORTH HYDE GSP |  | NORTH HYDE 11kV | MINIMUM HEADROOM | TQ 10367 79001 | YES | 6.918 | 24.7429 | 22.2003 | 57.9952 | 55.188 | 52.3401 | 49.5125 | 46.0717 | 42.0931 | 38.5503 | 35.185 | 21.7094 | 14.4941 | 11.2901 | 28.1745 | 26.4003 | 60.7258 | 58.8003 | 56.9258 | 54.888 | 51.5237 | 47.6074 | 44.2829 | 40.7941 | 28.2921 | 17.5523 | -0.55688 | 24.1888 | 22.0645 | 57.1758 | 54.7554 | 52.2962 | 49.6788 | 46.0115 | 41.7594 | 38.0656 | 34.5278 | 19.885 | 12.4768 | 8.7003
|  | NORTH HYDE 11kV | EE |  |  |  | 24.7429 | 22.2003 | 57.9952 | 55.188 | 52.3401 | 49.5125 | 46.0717 | 42.0931 | 38.5503 | 35.185 | 21.7094 | 14.4941 | 11.2901 | 28.1745 | 26.4003 | 60.7258 | 58.8003 | 56.9258 | 54.888 | 51.5237 | 47.6074 | 44.2829 | 40.7941 | 28.2921 | 17.5523 | 3.5584 | 24.1888 | 22.0645 | 57.1758 | 54.7554 | 52.2962 | 49.6788 | 46.0115 | 41.7594 | 38.0656 | 34.5278 | 19.885 | 12.4768 | 8.7003
|  | NORTH HYDE 11kV | HT |  |  |  | 25.4092 | 23.0472 | 58.9727 | 56.4829 | 54.0605 | 51.9503 | 48.9839 | 45.6196 | 42.6033 | 39.3543 | 25.5758 | 16.9686 | 12.9809 | 28.8399 | 27.3472 | 61.9196 | 60.4135 | 59.0962 | 57.9003 | 55.1615 | 51.9941 | 49.2737 | 45.8635 | 31.7992 | 23.5145 | 18.9533 | 24.8031 | 22.8513 | 58.1237 | 56.0156 | 53.9523 | 52.1278 | 49.0554 | 45.4564 | 42.2635 | 38.7819 | 24.1125 | 14.4196 | 9.5196
|  | NORTH HYDE 11kV | HE |  |  |  | 25.3388 | 23.0523 | 58.8799 | 56.3523 | 54.1248 | 51.6992 | 49.1533 | 46.1135 | 43.7268 | 41.239 | 25.5727 | 18.9145 | 16.0186 | 28.6705 | 27.1084 | 61.4462 | 59.7513 | 58.4145 | 56.7176 | 54.2431 | 51.2278 | 49.0094 | 46.3319 | 32.4656 | 23.2288 | 9.2258 | 24.7348 | 22.8411 | 58.0033 | 55.8411 | 53.9605 | 51.8064 | 49.2482 | 46.1411 | 43.7625 | 40.8043 | 24.2931 | 17.3574 | 13.9023
|  | NORTH HYDE 11kV | CF |  |  |  | 25.898 | 24.1258 | 60.5605 | 58.5921 | 56.7972 | 55.3339 | 53.9288 | 52.0288 | 50.239 | 48.5768 | 40.9523 | 31.7952 | 25.6472 | 29.0021 | 27.6911 | 62.3482 | 60.8941 | 59.638 | 58.4401 | 56.6686 | 54.2839 | 52.0258 | 49.8972 | 39.1676 | 24.0299 | -0.55688 | 25.249 | 23.8125 | 59.5278 | 57.8717 | 56.4115 | 55.1666 | 53.7094 | 51.7196 | 49.8748 | 48.1288 | 39.6686 | 30.8105 | 24.9319
MINETY GSP | CIRENCESTER BSP | NORTHLEACH | MINIMUM HEADROOM | SP 10557 14251 | YES | 0.816 | 7.1878 | 7.0255 | 6.8673 | 6.6592 | 6.4296 | 6.249 | 5.9571 | 5.6133 | 5.2704 | 5.0929 | 4.5704 | 4.1714 | 3.8133 | 8.6867 | 8.5673 | 8.451 | 8.2959 | 8.1173 | 7.9776 | 7.7571 | 7.4959 | 7.2316 | 7.0929 | 6.7153 | 5.7235 | 3.552 | 7.7714 | 7.6173 | 7.4663 | 7.2663 | 7.0449 | 6.8735 | 6.5929 | 6.2622 | 5.9327 | 5.7673 | 5.3684 | 5.0357 | 4.752
|  | NORTHLEACH | EE |  |  |  | 7.1878 | 7.0255 | 6.8673 | 6.6592 | 6.4296 | 6.249 | 5.9571 | 5.6133 | 5.2704 | 5.0929 | 4.5704 | 4.1898 | 4.001 | 8.6867 | 8.5673 | 8.451 | 8.2959 | 8.1173 | 7.9776 | 7.7571 | 7.4959 | 7.2316 | 7.0929 | 6.7153 | 6.0316 | 4.9827 | 7.7714 | 7.6173 | 7.4663 | 7.2663 | 7.0449 | 6.8735 | 6.5929 | 6.2622 | 5.9327 | 5.7673 | 5.3684 | 5.0582 | 4.902
|  | NORTHLEACH | HT |  |  |  | 7.2663 | 7.1408 | 7.0102 | 6.8531 | 6.7214 | 6.5398 | 6.3102 | 6.0969 | 5.8306 | 5.5612 | 4.7265 | 4.1714 | 3.8133 | 8.7582 | 8.6796 | 8.6031 | 8.502 | 8.4204 | 8.301 | 8.1531 | 8.0235 | 7.8449 | 7.6612 | 7.2418 | 6.9367 | 6.7633 | 7.849 | 7.7316 | 7.6102 | 7.4663 | 7.3449 | 7.1735 | 6.9582 | 6.7612 | 6.5112 | 6.2571 | 5.5102 | 5.0357 | 4.752
|  | NORTHLEACH | HE |  |  |  | 7.2622 | 7.1439 | 7.0184 | 6.8714 | 6.7459 | 6.5786 | 6.3622 | 6.1602 | 5.9082 | 5.649 | 4.7306 | 4.3571 | 4.1908 | 8.75 | 8.6633 | 8.5786 | 8.4724 | 8.3827 | 8.252 | 8.0959 | 7.9531 | 7.7622 | 7.5551 | 6.8469 | 6.1531 | 5.1276 | 7.8459 | 7.7316 | 7.6184 | 7.4786 | 7.3673 | 7.2071 | 7.0041 | 6.8163 | 6.5806 | 6.3378 | 5.5357 | 5.2276 | 5.0969
|  | NORTHLEACH | CF |  |  |  | 7.2939 | 7.1969 | 7.098 | 6.9878 | 6.8653 | 6.7704 | 6.6316 | 6.4694 | 6.2949 | 6.1714 | 5.1704 | 4.8878 | 4.3316 | 8.7704 | 8.6959 | 8.6255 | 8.5418 | 8.4398 | 8.3571 | 8.2337 | 8.0867 | 7.9255 | 7.8 | 6.7337 | 5.7235 | 3.552 | 7.8724 | 7.7847 | 7.6949 | 7.5898 | 7.4745 | 7.3867 | 7.2571 | 7.101 | 6.9347 | 6.8194 | 5.8622 | 5.6724 | 5.2031
IVER 66KV |  | NORTHOLT | MINIMUM HEADROOM | TQ 11550 83230 | YES | 11.083 | 1.5615 | 0.5911 | -0.49564 | -1.7252 | -3.1089 | -4.6099 | -6.9681 | -9.6538 | -12.3283 | -14.2436 | -21.4936 | -25.9518 | -25.865 | 11.8635 | 10.9605 | 10.0227 | 8.9615 | 7.7268 | 6.3758 | 4.6289 | 2.5666 | 0.46967 | -1.0609 | -8.6548 | -20.3752 | -48.6865 | 5.7952 | 4.836 | 3.7891 | 2.6033 | 1.2697 | -0.17931 | -2.3997 | -4.9436 | -7.4742 | -9.2487 | -15.8609 | -19.6946 | -19.6395
|  | NORTHOLT | EE |  |  |  | 1.5615 | 0.5911 | -0.49564 | -1.7252 | -3.1089 | -4.6099 | -6.9681 | -9.6538 | -12.3283 | -14.2436 | -21.4936 | -25.2375 | -23.8997 | 11.8635 | 10.9605 | 10.0227 | 8.9615 | 7.7268 | 6.3758 | 4.6289 | 2.5666 | 0.46967 | -1.0609 | -8.6548 | -16.6946 | -28.8334 | 5.7952 | 4.836 | 3.7891 | 2.6033 | 1.2697 | -0.17931 | -2.3997 | -4.9436 | -7.4742 | -9.2487 | -15.8609 | -19.0303 | -18.0273
|  | NORTHOLT | HT |  |  |  | 2.2819 | 1.1768 | 0.28906 | -0.21196 | -1.1569 | -2.214 | -3.9875 | -5.9671 | -8.0436 | -10.2007 | -20.4589 | -25.9518 | -25.865 | 12.5513 | 11.6666 | 11.037 | 10.7493 | 10.085 | 9.3289 | 8.2962 | 7.0921 | 5.7982 | 4.4319 | -1.815 | -4.8793 | -5.1548 | 6.4891 | 5.4146 | 4.5666 | 4.1135 | 3.2186 | 2.2146 | 0.57579 | -1.2722 | -3.2171 | -5.2416 | -14.7987 | -19.6946 | -19.6395
|  | NORTHOLT | HE |  |  |  | 2.2574 | 1.2186 | 0.40232 | -0.024208 | -0.87829 | -1.8314 | -3.4324 | -5.2426 | -7.1385 | -9.1018 | -16.9722 | -20.5232 | -20.7885 | 12.4156 | 11.4472 | 10.7176 | 10.3217 | 9.4972 | 8.5799 | 7.3523 | 5.9248 | 4.386 | 2.7493 | -5.8977 | -14.1803 | -26.7303 | 6.4686 | 5.4493 | 4.6656 | 4.2778 | 3.4676 | 2.5646 | 1.0819 | -0.61094 | -2.3844 | -4.2273 | -11.6018 | -14.7416 | -14.9783
|  | NORTHOLT | CF |  |  |  | 2.6472 | 1.8982 | 1.4238 | 0.90232 | 0.8064 | 0.28396 | -0.33543 | -1.1099 | -1.9538 | -2.8467 | -8.7375 | -15.2589 | -21.3569 | 12.6309 | 11.7911 | 11.2227 | 10.5891 | 10.2411 | 9.4411 | 8.4778 | 7.336 | 6.1023 | 4.7707 | -4.766 | -20.3752 | -48.6865 | 6.8401 | 6.1156 | 5.6686 | 5.1748 | 5.0799 | 4.5799 | 3.988 | 3.2421 | 2.4299 | 1.5717 | -4.112 | -10.1109 | -15.4885
BRAMLEY (FLEE) | READING BSP | NORTHUMBERLAND AVENUE | MINIMUM HEADROOM | SU 72207 71092 | YES | 3.782 | 4.1066 | 3.8617 | 3.3617 | 2.779 | 2.3842 | 2.2127 | 1.526 | 0.49129 | -0.44646 | -1.1077 | -3.7944 | -5.0883 | -5.2556 | 5.9364 | 5.6588 | 5.1456 | 4.5609 | 4.2252 | 4.0966 | 3.6537 | 3.015 | 2.4088 | 1.9517 | -0.49422 | -4.2299 | -11.6422 | 4.0542 | 3.7542 | 3.2123 | 2.6358 | 2.2827 | 2.1521 | 1.5613 | 0.70007 | -0.079522 | -0.63156 | -2.8081 | -3.8601 | -3.9805
|  | NORTHUMBERLAND AVENUE | EE |  |  |  | 4.1066 | 3.8617 | 3.3617 | 2.779 | 2.3842 | 2.2127 | 1.526 | 0.49129 | -0.44646 | -1.1077 | -3.7944 | -5.0434 | -4.7995 | 5.9364 | 5.6588 | 5.1456 | 4.5609 | 4.2252 | 4.0966 | 3.6537 | 3.015 | 2.4088 | 1.9517 | -0.49422 | -2.9238 | -6.3422 | 4.0542 | 3.7542 | 3.2123 | 2.6358 | 2.2827 | 2.1521 | 1.5613 | 0.70007 | -0.079522 | -0.63156 | -2.8081 | -3.851 | -3.5846
|  | NORTHUMBERLAND AVENUE | HT |  |  |  | 4.2086 | 3.9995 | 3.5393 | 3.0658 | 2.8525 | 2.3127 | 1.6005 | 0.56782 | 0.16987 | -0.5383 | -3.6658 | -5.0883 | -5.2556 | 6.0568 | 5.8548 | 5.4303 | 4.9446 | 4.816 | 4.517 | 4.1446 | 3.6048 | 3.4517 | 3.0639 | 1.3231 | 0.55987 | 0.39354 | 4.1623 | 3.9052 | 3.4072 | 2.895 | 2.7052 | 2.2562 | 1.6521 | 0.79803 | 0.48476 | -0.10401 | -2.654 | -3.8601 | -3.9805
|  | NORTHUMBERLAND AVENUE | HE |  |  |  | 4.2066 | 4.0005 | 3.5454 | 3.0872 | 2.8719 | 2.4831 | 1.8933 | 0.92701 | 0.4464 | -0.21075 | -2.7669 | -3.8097 | -4.0097 | 6.0293 | 5.8007 | 5.3384 | 4.8211 | 4.5844 | 4.2731 | 3.8844 | 3.2905 | 2.9925 | 2.5252 | 0.062927 | -2.2789 | -5.834 | 4.1715 | 3.9337 | 3.4562 | 2.9674 | 2.7358 | 2.3817 | 1.8756 | 1.0776 | 0.69701 | 0.15007 | -1.8948 | -2.7601 | -2.9152
|  | NORTHUMBERLAND AVENUE | CF |  |  |  | 4.2882 | 4.1433 | 3.7362 | 3.3576 | 3.2046 | 3.1107 | 2.9903 | 2.7903 | 2.4688 | 2.077 | -0.40258 | -2.7505 | -3.9536 | 6.0711 | 5.8874 | 5.4415 | 4.9793 | 4.7568 | 4.5752 | 4.3282 | 3.9976 | 3.6099 | 3.1905 | 0.3568 | -4.2299 | -11.6422 | 4.2623 | 4.1174 | 3.699 | 3.3266 | 3.1674 | 3.0776 | 2.9348 | 2.7052 | 2.4001 | 2.0756 | 0.13068 | -1.7938 | -2.8632
COWLEY GSP | HIGH WYCOMBE BSP | NUFFIELD | MINIMUM HEADROOM | SU 68329 86784 | YES | 1.219 | 2.5429 | 1.9761 | 1.8394 | 1.4935 | 1.2873 | 0.38735 | -0.071837 | -0.60551 | -2.3657 | -3.5729 | -6.3678 | -9.3463 | -13.1392 | 4.0827 | 3.5394 | 3.3924 | 2.9976 | 2.7914 | 1.72 | 1.2047 | 0.61898 | -1.5004 | -2.9351 | -6.0586 | -9.9188 | -15.1433 | 2.8724 | 2.3149 | 2.1598 | 1.7516 | 1.5282 | 0.43327 | -0.10449 | -0.72286 | -2.8759 | -4.3412 | -7.5882 | -11.2463 | -15.9647
|  | NUFFIELD | EE |  |  |  | 2.5429 | 1.9761 | 1.8588 | 1.7292 | 1.6292 | 1.2598 | 0.84959 | 0.68735 | 0.11184 | -0.19633 | -2.031 | -6.332 | -7.8596 | 4.0827 | 3.5394 | 3.4537 | 3.3537 | 3.2751 | 2.8833 | 2.4669 | 2.3516 | 1.7312 | 1.4118 | -0.60245 | -6.1055 | -8.4892 | 2.8724 | 2.3149 | 2.2037 | 2.0792 | 1.9853 | 1.5649 | 1.1078 | 0.9598 | 0.30061 | -0.046327 | -2.1484 | -7.4565 | -9.3382
|  | NUFFIELD | HT |  |  |  | 2.601 | 2.0445 | 1.8751 | 1.6465 | 1.5496 | 0.81694 | 0.35776 | -0.20347 | -0.45449 | -1.1188 | -3.479 | -7.5565 | -10.5147 | 4.1378 | 3.6078 | 3.4547 | 3.2241 | 3.1578 | 2.3088 | 1.8098 | 1.2057 | 0.99041 | 0.26286 | -2.2443 | -7.1473 | -10.7188 | 2.9347 | 2.3853 | 2.2037 | 1.9476 | 1.8547 | 0.9751 | 0.43735 | -0.21469 | -0.47898 | -1.2565 | -3.9902 | -8.9953 | -12.6351
|  | NUFFIELD | HE |  |  |  | 2.6 | 2.0455 | 1.8394 | 1.4935 | 1.2873 | 0.38735 | -0.071837 | -0.60551 | -2.3657 | -3.5729 | -6.3678 | -9.3463 | -13.1392 | 4.1306 | 3.5976 | 3.3924 | 2.9976 | 2.7914 | 1.72 | 1.2047 | 0.61898 | -1.5004 | -2.9351 | -6.0586 | -9.9188 | -15.1433 | 2.9327 | 2.3853 | 2.1598 | 1.7516 | 1.5282 | 0.43327 | -0.10449 | -0.72286 | -2.8759 | -4.3412 | -7.5882 | -11.2463 | -15.9647
|  | NUFFIELD | CF |  |  |  | 2.6122 | 2.071 | 2.0047 | 1.9496 | 1.7863 | 1.6078 | 1.3761 | 1.2108 | 0.99959 | 0.73327 | -0.87898 | -2.8157 | -4.629 | 4.1337 | 3.6118 | 3.5618 | 3.5169 | 3.3516 | 3.1578 | 2.9016 | 2.7159 | 2.4873 | 2.1935 | 0.28939 | -2.3647 | -5.4463 | 2.9439 | 2.4078 | 2.3496 | 2.2986 | 2.122 | 1.9241 | 1.6598 | 1.4771 | 1.2445 | 0.94653 | -0.90041 | -3.1882 | -5.3453
BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | OAKRIDGE | MINIMUM HEADROOM | SU 63496 53664 | YES | 0.755 | 18.4622 | 17.9714 | 17.2816 | 16.5765 | 16.1827 | 15.5765 | 14.6704 | 13.4316 | 12.0714 | 10.9031 | 6.6643 | 3.1653 | 1.0102 | 19.2878 | 18.9153 | 18.3969 | 17.8204 | 17.5439 | 17.0449 | 16.4204 | 15.6061 | 14.7316 | 14.049 | 11.0918 | 8.0806 | -0.0091837 | 18.151 | 17.6939 | 17.0561 | 16.3735 | 16.048 | 15.4561 | 14.601 | 13.4551 | 12.2214 | 11.2163 | 7.4367 | 4.3745 | 2.5367
|  | OAKRIDGE | EE |  |  |  | 18.4622 | 17.9714 | 17.2816 | 16.5765 | 16.1827 | 15.5765 | 14.6704 | 13.4316 | 12.0714 | 10.9031 | 6.6643 | 3.6918 | 1.2582 | 19.2878 | 18.9153 | 18.3969 | 17.8204 | 17.5439 | 17.0449 | 16.4204 | 15.6061 | 14.7316 | 14.049 | 11.0918 | 8.0806 | 3.6173 | 18.151 | 17.6939 | 17.0561 | 16.3735 | 16.048 | 15.4561 | 14.601 | 13.4551 | 12.2214 | 11.2163 | 7.4367 | 4.8714 | 2.7469
|  | OAKRIDGE | HT |  |  |  | 18.6684 | 18.1153 | 17.5357 | 16.9969 | 16.5357 | 16.0082 | 14.8561 | 14.0041 | 12.8235 | 11.9092 | 6.6939 | 3.1653 | 1.0102 | 19.5153 | 19.1459 | 18.7684 | 18.4 | 18.0816 | 17.7041 | 17.0929 | 16.7888 | 16.1612 | 15.6316 | 12.951 | 11.302 | 10.4388 | 18.3582 | 17.8561 | 17.3388 | 16.8418 | 16.4041 | 15.8959 | 14.8745 | 14.151 | 13.102 | 12.2582 | 7.4949 | 4.3745 | 2.5367
|  | OAKRIDGE | HE |  |  |  | 18.651 | 18.2592 | 17.6939 | 17.1388 | 16.6163 | 16.1214 | 15.4051 | 14.8235 | 13.8633 | 12.8847 | 8.2735 | 5.3398 | 4.0878 | 19.4714 | 19.1959 | 18.7847 | 18.352 | 17.9429 | 17.5429 | 17.048 | 16.7857 | 16.1684 | 15.5194 | 12.0888 | 9.0469 | 5.0265 | 18.3408 | 17.9898 | 17.4847 | 16.9724 | 16.4847 | 16.0204 | 15.349 | 14.85 | 13.9878 | 13.1071 | 8.9541 | 6.3694 | 5.248
|  | OAKRIDGE | CF |  |  |  | 18.85 | 18.6724 | 18.4694 | 18.0878 | 17.6724 | 17.1867 | 16.8041 | 16.448 | 16.0439 | 15.998 | 12.4194 | 9.599 | 6.9878 | 19.5704 | 19.3878 | 19.1847 | 18.8265 | 18.4316 | 18.0031 | 17.6051 | 17.1796 | 16.7133 | 16.5908 | 13.049 | 8.2102 | -0.0091837 | 18.5163 | 18.349 | 18.1643 | 17.8082 | 17.4255 | 16.9908 | 16.6367 | 16.2694 | 15.8633 | 15.8755 | 12.649 | 10.102 | 7.7847
COWLEY GSP | HEADINGTON BSP | OLD ROAD | MINIMUM HEADROOM | SP 55274 06426 | YES | 1.645 | 11.5092 | 10.8439 | 10.3153 | 9.7959 | 9.2643 | 8.0837 | 7.1184 | 6.2969 | 5.5684 | 5.1102 | 3.3337 | 2.1214 | 2.0214 | 10.8194 | 10.498 | 9.9643 | 9.6745 | 9.35 | 8.1469 | 7.4755 | 6.8551 | 6.2643 | 5.8459 | 3.6418 | -0.28367 | -8.9643 | 9.9204 | 9.4378 | 8.8704 | 8.4122 | 7.9367 | 6.7408 | 5.8837 | 5.1408 | 4.4735 | 4.0449 | 2.4041 | 1.3541 | 1.2633
|  | OLD ROAD | EE |  |  |  | 11.5092 | 11.0306 | 10.3153 | 9.7959 | 9.2643 | 8.0837 | 7.1184 | 6.2969 | 5.5684 | 5.1102 | 3.3337 | 2.2714 | 2.4837 | 10.8194 | 10.498 | 9.9643 | 9.6745 | 9.35 | 8.1469 | 7.4755 | 6.8551 | 6.2643 | 5.8459 | 3.6418 | 1.0663 | -2.8959 | 9.9204 | 9.5061 | 8.8704 | 8.4122 | 7.9367 | 6.7408 | 5.8837 | 5.1408 | 4.4735 | 4.0449 | 2.4041 | 1.4735 | 1.65
|  | OLD ROAD | HT |  |  |  | 11.649 | 10.8439 | 10.3622 | 10.052 | 9.7184 | 8.2969 | 7.2082 | 6.601 | 6.3949 | 5.8898 | 3.501 | 2.1214 | 2.0214 | 10.9398 | 10.5122 | 10.1265 | 9.9622 | 9.7765 | 8.5327 | 7.9643 | 7.6265 | 7.4663 | 7.2173 | 5.7592 | 4.9796 | 4.8418 | 10.0959 | 9.4378 | 9 | 8.6888 | 8.3561 | 6.9551 | 6.0092 | 5.4551 | 5.2643 | 4.7949 | 2.6031 | 1.3541 | 1.2633
|  | OLD ROAD | HE |  |  |  | 11.6551 | 11.2398 | 10.6102 | 10.249 | 9.9337 | 8.5306 | 7.7061 | 7.0439 | 6.8694 | 6.4265 | 4.75 | 3.951 | 3.848 | 10.902 | 10.6092 | 10.1071 | 9.8714 | 9.6602 | 8.352 | 7.8296 | 7.3827 | 7.15 | 6.7643 | 4.5092 | 2.0316 | -2.0531 | 10.0969 | 9.7306 | 9.1878 | 8.851 | 8.5531 | 7.1663 | 6.4398 | 5.8469 | 5.6847 | 5.2653 | 3.7276 | 3.0092 | 2.9204
|  | OLD ROAD | CF |  |  |  | 11.8878 | 11.599 | 11.2959 | 11.2102 | 11.0582 | 9.8286 | 9.6224 | 9.2531 | 8.7878 | 8.3194 | 6.548 | 5.0908 | 3.7602 | 11.1071 | 10.7582 | 10.3837 | 10.2541 | 10.0969 | 8.8184 | 8.5378 | 8.1714 | 7.748 | 7.2306 | 4.4061 | -0.28367 | -8.9643 | 10.302 | 10.0337 | 9.7429 | 9.6459 | 9.5051 | 8.2929 | 8.0959 | 7.7684 | 7.3622 | 6.9551 | 5.3959 | 4.0469 | 2.8306
COWLEY GSP | OXFORD BSP | OXFORD | MINIMUM HEADROOM | SP 50148 05901 | YES | 1.883 | 16.5807 | 15.6399 | 14.5613 | 13.347 | 11.9684 | 9.9919 | 7.7654 | 5.0705 | 2.2174 | -0.44178 | -12.9244 | -16.4826 | -16.7652 | 22.2613 | 21.7603 | 21.1919 | 20.4929 | 19.449 | 17.8929 | 16.1766 | 14.0633 | 11.8021 | 9.6858 | -0.153 | -2.8846 | -3.2428 | 17.7296 | 17.0245 | 16.0562 | 14.8888 | 13.5643 | 11.6623 | 9.5358 | 6.9429 | 4.2031 | 1.646 | -10.4224 | -13.852 | -14.1224
|  | OXFORD | EE |  |  |  | 16.5807 | 15.6399 | 14.5613 | 13.347 | 11.9684 | 9.9919 | 7.7654 | 5.0705 | 2.2174 | -0.44178 | -8.9714 | -9.802 | -9.8112 | 22.2613 | 21.7603 | 21.1919 | 20.4929 | 19.449 | 17.8929 | 16.1766 | 14.0633 | 11.8021 | 9.6858 | 2.9521 | 2.345 | 2.1582 | 17.7296 | 17.0245 | 16.0562 | 14.8888 | 13.5643 | 11.6623 | 9.5358 | 6.9429 | 4.2031 | 1.646 | -6.555 | -7.3255 | -7.3387
|  | OXFORD | HT |  |  |  | 17.4123 | 16.7501 | 16.1348 | 15.4092 | 14.0154 | 12.2531 | 10.3133 | 7.9552 | 5.0572 | 2.3154 | -5.6183 | -8.1897 | -8.4724 | 22.7256 | 22.3552 | 22.047 | 21.6796 | 20.7725 | 19.5613 | 18.0827 | 16.2041 | 13.8796 | 11.7092 | 5.6654 | 3.798 | 3.5807 | 18.3592 | 17.8296 | 17.3796 | 16.8531 | 15.5541 | 13.8592 | 12.0133 | 9.747 | 6.9541 | 4.3113 | -3.3193 | -5.7734 | -6.0336
|  | OXFORD | HE |  |  |  | 17.1082 | 16.3194 | 15.3837 | 14.3133 | 13.0674 | 11.1603 | 9.0215 | 6.3684 | 3.348 | 0.11638 | -12.9244 | -16.4826 | -16.7652 | 22.546 | 22.1154 | 21.6276 | 21.0715 | 20.298 | 18.797 | 17.1439 | 15.0623 | 12.6643 | 10.099 | -0.153 | -2.8846 | -3.2428 | 18.1327 | 17.5235 | 16.8307 | 15.8266 | 14.6286 | 12.796 | 10.748 | 8.196 | 5.2878 | 2.1664 | -10.4224 | -13.852 | -14.1224
|  | OXFORD | CF |  |  |  | 17.6133 | 17.2113 | 16.7796 | 16.2439 | 15.6031 | 14.8664 | 13.9123 | 12.4807 | 10.746 | 8.8592 | -3.7652 | -9.2183 | -11.7806 | 22.8123 | 22.5735 | 22.3225 | 22.0307 | 21.6837 | 21.2796 | 20.6837 | 19.6827 | 18.296 | 16.7858 | 6.6592 | 2.4582 | -0.19484 | 18.5021 | 18.2021 | 17.8623 | 17.4603 | 16.9878 | 16.3378 | 15.4184 | 14.0399 | 12.3735 | 10.5582 | -1.6071 | -6.8571 | -9.2999
COWLEY GSP | COWLEY LOCAL (2 X 90) | OXFORD SCIENCE PARK | MINIMUM HEADROOM | TBC | YES | 22.91 | -1.288 | 14.9552 | 14.9552 | 14.9552 | 14.9552 | 4.352 | 4.352 | 4.352 | 4.352 | 4.352 | 4.352 | 4.352 | 4.352 | -1.288 | 13.6352 | 13.6352 | 13.6352 | 13.6352 | 3.032 | 3.032 | 3.032 | 3.032 | 3.032 | 3.032 | 3.032 | 3.032 | -1.288 | 14.3552 | 14.3552 | 14.3552 | 14.3552 | 3.752 | 3.752 | 3.752 | 3.752 | 3.752 | 3.752 | 3.752 | 3.752
|  | OXFORD SCIENCE PARK | EE |  |  |  | -1.288 | 14.9552 | 14.9552 | 14.9552 | 14.9552 | 4.352 | 4.352 | 4.352 | 4.352 | 4.352 | 4.352 | 4.352 | 4.352 | -1.288 | 13.6352 | 13.6352 | 13.6352 | 13.6352 | 3.032 | 3.032 | 3.032 | 3.032 | 3.032 | 3.032 | 3.032 | 3.032 | -1.288 | 14.3552 | 14.3552 | 14.3552 | 14.3552 | 3.752 | 3.752 | 3.752 | 3.752 | 3.752 | 3.752 | 3.752 | 3.752
|  | OXFORD SCIENCE PARK | HT |  |  |  | -1.288 | 14.9552 | 14.9552 | 14.9552 | 14.9552 | 4.352 | 4.352 | 4.352 | 4.352 | 4.352 | 4.352 | 4.352 | 4.352 | -1.288 | 13.6352 | 13.6352 | 13.6352 | 13.6352 | 3.032 | 3.032 | 3.032 | 3.032 | 3.032 | 3.032 | 3.032 | 3.032 | -1.288 | 14.3552 | 14.3552 | 14.3552 | 14.3552 | 3.752 | 3.752 | 3.752 | 3.752 | 3.752 | 3.752 | 3.752 | 3.752
|  | OXFORD SCIENCE PARK | HE |  |  |  | -1.288 | 14.9552 | 14.9552 | 14.9552 | 14.9552 | 4.352 | 4.352 | 4.352 | 4.352 | 4.352 | 4.352 | 4.352 | 4.352 | -1.288 | 13.6352 | 13.6352 | 13.6352 | 13.6352 | 3.032 | 3.032 | 3.032 | 3.032 | 3.032 | 3.032 | 3.032 | 3.032 | -1.288 | 14.3552 | 14.3552 | 14.3552 | 14.3552 | 3.752 | 3.752 | 3.752 | 3.752 | 3.752 | 3.752 | 3.752 | 3.752
|  | OXFORD SCIENCE PARK | CF |  |  |  | -1.288 | 14.9552 | 14.9552 | 14.9552 | 14.9552 | 4.352 | 4.352 | 4.352 | 4.352 | 4.352 | 4.352 | 4.352 | 4.352 | -1.288 | 13.6352 | 13.6352 | 13.6352 | 13.6352 | 3.032 | 3.032 | 3.032 | 3.032 | 3.032 | 3.032 | 3.032 | 3.032 | -1.288 | 14.3552 | 14.3552 | 14.3552 | 14.3552 | 3.752 | 3.752 | 3.752 | 3.752 | 3.752 | 3.752 | 3.752 | 3.752
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | OVERTON | MINIMUM HEADROOM | SU 52061 50913 | YES | 20.11 | 16.0924 | 13.0811 | 12.8944 | 12.6505 | 12.4118 | 10.8281 | 9.8352 | 8.5475 | 7.3852 | 6.0271 | 1.2852 | -0.38825 | -0.99335 | 15.3301 | 12.3883 | 12.2526 | 12.076 | 11.9056 | 10.4424 | 10.1362 | 9.5169 | 8.9015 | 8.0883 | 4.6138 | 2.9434 | 0.25053 | 13.4954 | 10.4964 | 10.3148 | 10.0781 | 9.8495 | 8.2924 | 7.4822 | 6.4791 | 5.5311 | 4.4209 | 0.66481 | -0.63009 | -1.124
|  | OVERTON | EE |  |  |  | 16.0924 | 13.0811 | 12.8944 | 12.6505 | 12.4118 | 10.8281 | 10.3689 | 9.3199 | 8.5342 | 7.4669 | 1.8536 | -0.21784 | -0.89233 | 15.3301 | 12.3883 | 12.2526 | 12.076 | 11.9056 | 10.4424 | 10.1362 | 9.5332 | 9.2515 | 8.6944 | 4.6138 | 2.9434 | 1.5169 | 13.4954 | 10.4964 | 10.3148 | 10.0781 | 9.8495 | 8.2924 | 7.8577 | 6.9066 | 6.3607 | 5.5311 | 1.0628 | -0.47396 | -1.0342
|  | OVERTON | HT |  |  |  | 16.1924 | 13.2373 | 13.0607 | 12.873 | 12.6822 | 11.1566 | 9.8352 | 8.5475 | 7.3852 | 6.0271 | 1.2852 | -0.38825 | -0.99335 | 15.424 | 12.5362 | 12.4322 | 12.3148 | 12.2046 | 10.8189 | 10.1434 | 9.5169 | 8.9015 | 8.0883 | 4.9138 | 4.0148 | 3.7464 | 13.6005 | 10.6556 | 10.4924 | 10.3128 | 10.1311 | 8.6311 | 7.4822 | 6.4791 | 5.5311 | 4.4209 | 0.66481 | -0.63009 | -1.124
|  | OVERTON | HE |  |  |  | 16.1913 | 13.2434 | 13.075 | 12.8964 | 12.7158 | 11.2026 | 10.8444 | 10.0556 | 9.0781 | 8.1383 | 3.2995 | 0.7893 | -0.028045 | 15.4077 | 12.5128 | 12.3944 | 12.2689 | 12.1495 | 10.7495 | 10.526 | 10.1005 | 9.5618 | 9.0311 | 5.3811 | 3.4709 | 1.9424 | 13.5975 | 10.6597 | 10.5036 | 10.3332 | 10.1628 | 8.675 | 8.3424 | 7.6444 | 6.8097 | 6.0271 | 2.2097 | 0.34542 | -0.28009
|  | OVERTON | CF |  |  |  | 16.2944 | 13.4015 | 13.2893 | 13.1577 | 12.9934 | 11.6209 | 11.3791 | 11.1107 | 10.9015 | 10.6026 | 7.8628 | 2.0975 | 0.63318 | 15.4607 | 12.5852 | 12.4985 | 12.3903 | 12.2689 | 10.9413 | 10.7536 | 10.5454 | 10.372 | 10.1332 | 8.223 | 3.3352 | 0.25053 | 13.6924 | 10.8005 | 10.6944 | 10.573 | 10.4179 | 9.0577 | 8.8342 | 8.5822 | 8.3934 | 8.1118 | 5.9005 | 1.322 | 0.23624
BRAMLEY (FLEE) | BURGHFIELD RESERVE | PADWORTH | MINIMUM HEADROOM | SU 62243 66052 | YES | 0.137 | 3.9916 | 3.9385 | 3.8906 | 3.8457 | 3.7804 | 3.7202 | 3.6253 | 3.5528 | 3.4518 | 3.3926 | 3.1099 | 2.9028 | 2.7865 | 5.1893 | 5.1474 | 5.1066 | 5.075 | 5.0189 | 4.9648 | 4.8944 | 4.8372 | 4.7526 | 4.7036 | 4.4393 | 4.1454 | 3.4189 | 5.0357 | 4.9837 | 4.9347 | 4.8939 | 4.8255 | 4.7602 | 4.6643 | 4.5949 | 4.4878 | 4.4367 | 4.1582 | 3.9653 | 3.8561
|  | PADWORTH | EE |  |  |  | 3.9916 | 3.9385 | 3.8906 | 3.8457 | 3.7804 | 3.7202 | 3.6253 | 3.5528 | 3.4518 | 3.3926 | 3.1099 | 2.9671 | 2.8732 | 5.1893 | 5.1474 | 5.1066 | 5.075 | 5.0189 | 4.9648 | 4.8944 | 4.8372 | 4.7526 | 4.7036 | 4.4791 | 4.2536 | 3.8903 | 5.0357 | 4.9837 | 4.9347 | 4.8939 | 4.8255 | 4.7602 | 4.6643 | 4.5949 | 4.4878 | 4.4367 | 4.2092 | 4.0939 | 4.0102
|  | PADWORTH | HT |  |  |  | 4.0151 | 3.9763 | 3.9436 | 3.9048 | 3.8548 | 3.8008 | 3.7457 | 3.6661 | 3.5804 | 3.4906 | 3.1273 | 2.9355 | 2.8253 | 5.2117 | 5.1893 | 5.1658 | 5.1423 | 5.1056 | 5.0607 | 5.0311 | 4.9668 | 4.9015 | 4.8281 | 4.5352 | 4.4179 | 4.3505 | 5.0653 | 5.0296 | 4.998 | 4.9622 | 4.9112 | 4.852 | 4.8061 | 4.7296 | 4.6439 | 4.5541 | 4.2214 | 4.0633 | 3.9704
|  | PADWORTH | HE |  |  |  | 4.014 | 3.9773 | 3.9436 | 3.9059 | 3.861 | 3.8099 | 3.7599 | 3.6895 | 3.6079 | 3.5263 | 3.1099 | 2.9028 | 2.7865 | 5.2077 | 5.1832 | 5.1556 | 5.127 | 5.0883 | 5.0413 | 5.0056 | 4.9362 | 4.8607 | 4.7832 | 4.4393 | 4.2781 | 3.923 | 5.0633 | 5.0306 | 4.998 | 4.9643 | 4.9163 | 4.8602 | 4.8194 | 4.751 | 4.6714 | 4.5888 | 4.1582 | 3.9653 | 3.8561
|  | PADWORTH | CF |  |  |  | 4.0283 | 4.0028 | 3.9793 | 3.9477 | 3.9212 | 3.8844 | 3.8446 | 3.8161 | 3.7681 | 3.7253 | 3.463 | 3.1977 | 2.9702 | 5.2179 | 5.1964 | 5.176 | 5.1444 | 5.1199 | 5.0852 | 5.0423 | 5.0056 | 4.9566 | 4.9097 | 4.5832 | 4.1454 | 3.4189 | 5.0765 | 5.052 | 5.0316 | 4.9959 | 4.9714 | 4.9316 | 4.8898 | 4.8643 | 4.8122 | 4.7684 | 4.5041 | 4.2388 | 4.0265
BRAMLEY (FLEE) | BURGHFIELD RESERVE | PANGBOURNE | MINIMUM HEADROOM | SU 62960 76144 | YES | 1.275 | 19.1622 | 18.9887 | 18.7469 | 18.5367 | 18.2602 | 17.9602 | 17.5357 | 17.5928 | 17.2071 | 16.8785 | 15.5132 | 14.4561 | 13.7795 | 19.7918 | 19.6734 | 19.4999 | 19.3408 | 19.1295 | 18.903 | 18.6071 | 18.6173 | 18.3336 | 18.1489 | 17.0938 | 15.8724 | 12.9765 | 18.1887 | 18.0285 | 17.8081 | 17.6122 | 17.3591 | 17.0816 | 16.6826 | 16.6785 | 16.3112 | 16.0408 | 14.8091 | 13.953 | 13.3959
|  | PANGBOURNE | EE |  |  |  | 19.1622 | 18.9887 | 18.7469 | 18.5367 | 18.2602 | 17.9602 | 17.5357 | 17.5928 | 17.2071 | 16.9632 | 15.5132 | 14.5765 | 13.9377 | 19.7918 | 19.6734 | 19.4999 | 19.3408 | 19.1295 | 18.903 | 18.6071 | 18.6173 | 18.3336 | 18.1489 | 17.0938 | 16.0704 | 14.5887 | 18.1887 | 18.0285 | 17.8081 | 17.6122 | 17.3591 | 17.0816 | 16.6826 | 16.6785 | 16.3112 | 16.0693 | 14.8091 | 14.0806 | 13.5377
|  | PANGBOURNE | HT |  |  |  | 19.2316 | 19.0979 | 18.9438 | 18.8051 | 18.601 | 18.3704 | 18.0887 | 17.7122 | 17.3132 | 16.8785 | 15.553 | 14.4561 | 13.7795 | 19.8816 | 19.7979 | 19.6887 | 19.5989 | 19.4653 | 19.3153 | 19.1489 | 18.9204 | 18.6663 | 18.3887 | 17.7326 | 17.2336 | 16.9469 | 18.2877 | 18.154 | 17.9918 | 17.8489 | 17.6571 | 17.4448 | 17.1724 | 16.8193 | 16.4459 | 16.0408 | 14.8499 | 13.953 | 13.3959
|  | PANGBOURNE | HE |  |  |  | 19.2336 | 19.1061 | 18.9602 | 18.8265 | 18.6295 | 18.4102 | 18.1683 | 17.8255 | 17.4642 | 17.0897 | 15.8836 | 14.9591 | 14.5397 | 19.8632 | 19.7663 | 19.6459 | 19.5408 | 19.3938 | 19.2244 | 19.054 | 18.8091 | 18.5418 | 18.2642 | 17.2979 | 16.2693 | 14.8816 | 18.2877 | 18.1591 | 18.004 | 17.8693 | 17.6857 | 17.4836 | 17.252 | 16.9316 | 16.5948 | 16.2459 | 15.1448 | 14.4285 | 14.0857
|  | PANGBOURNE | CF |  |  |  | 19.2857 | 19.203 | 19.0999 | 18.9673 | 18.8683 | 18.7183 | 18.5489 | 18.402 | 18.1908 | 17.9714 | 17.2306 | 16.2102 | 15.2316 | 19.8938 | 19.8173 | 19.7142 | 19.602 | 19.5132 | 19.3816 | 19.2214 | 19.0714 | 18.8693 | 18.652 | 17.6336 | 15.8724 | 12.9765 | 18.3397 | 18.2499 | 18.1387 | 18.0142 | 17.9234 | 17.7857 | 17.6316 | 17.4959 | 17.3051 | 17.102 | 16.3377 | 15.3979 | 14.5714
BOTLEY WOOD GSP | BOTLEY WOOD BSP | PARK GATE | MINIMUM HEADROOM | SU 51369 08259 | YES | 3.305 | 16.9296 | 16.4296 | 15.7918 | 15.5653 | 15.051 | 14.5051 | 13.6031 | 12.6163 | 11.6418 | 10.9347 | 6.8694 | 3.8265 | 2.1061 | 19.0816 | 18.8235 | 18.3449 | 18.2092 | 17.7918 | 17.3408 | 16.6867 | 15.9571 | 15.2194 | 14.7112 | 11.9153 | 7.9378 | -1.3327 | 16.948 | 16.4796 | 15.85 | 15.7194 | 15.2204 | 14.6878 | 13.8418 | 12.9041 | 11.9735 | 11.348 | 7.8939 | 5.2837 | 3.799
|  | PARK GATE | EE |  |  |  | 16.9296 | 16.4296 | 15.7918 | 15.5653 | 15.051 | 14.5051 | 13.6031 | 12.6163 | 11.6418 | 10.9347 | 7.3061 | 4.5408 | 2.4173 | 19.0816 | 18.8235 | 18.3449 | 18.2092 | 17.7918 | 17.3408 | 16.6867 | 15.9571 | 15.2194 | 14.7112 | 11.9153 | 8.7102 | 3.7867 | 16.948 | 16.4796 | 15.85 | 15.7194 | 15.2204 | 14.6878 | 13.8418 | 12.9041 | 11.9735 | 11.348 | 8.2449 | 5.9041 | 4.0561
|  | PARK GATE | HT |  |  |  | 17.1153 | 16.5939 | 16.1102 | 15.651 | 15.1694 | 14.5347 | 14.0612 | 13.1959 | 12.3102 | 11.4255 | 6.8694 | 3.8265 | 2.1061 | 19.201 | 19.0071 | 18.8306 | 18.5429 | 18.2316 | 17.7867 | 17.6531 | 17.1633 | 16.65 | 16.1357 | 13.7347 | 12.3847 | 11.648 | 17.1643 | 16.7112 | 16.2724 | 15.8378 | 15.3735 | 14.7735 | 14.4276 | 13.6388 | 12.8245 | 12.0112 | 7.8939 | 5.2837 | 3.799
|  | PARK GATE | HE |  |  |  | 17.1286 | 16.7153 | 16.2337 | 15.799 | 15.3469 | 15.2031 | 14.5429 | 13.8337 | 13.102 | 12.3663 | 8.5531 | 5.8163 | 4.4265 | 19.1908 | 19.0224 | 18.7357 | 18.3959 | 18.0347 | 17.9439 | 17.4602 | 16.9235 | 16.3561 | 15.7694 | 12.5408 | 9.2837 | 4.652 | 17.1735 | 16.8031 | 16.3714 | 15.9571 | 15.5235 | 15.4418 | 14.8388 | 14.1755 | 13.4918 | 12.802 | 9.3643 | 7.0439 | 5.8541
|  | PARK GATE | CF |  |  |  | 17.3612 | 17.1194 | 16.8092 | 16.6 | 16.3531 | 16.0786 | 15.7969 | 15.7765 | 15.4 | 15.0092 | 12.2633 | 9.4327 | 6.8143 | 19.3122 | 19.2102 | 18.9714 | 18.7418 | 18.4592 | 18.1276 | 17.7449 | 17.6143 | 17.1388 | 16.6418 | 13.1898 | 7.9378 | -1.3327 | 17.3714 | 17.1418 | 16.8469 | 16.6357 | 16.3633 | 16.0684 | 15.75 | 15.8694 | 15.4969 | 15.1051 | 12.5245 | 10.0633 | 7.8551
MELKSHAM GSP | AMESBURY | PARK HOUSE | MINIMUM HEADROOM | SU 23138 43780 | YES | 0.003 | 3.3531 | 3.2867 | 3.2276 | 3.1469 | 3.0571 | 3 | 2.8827 | 2.748 | 2.6102 | 2.5459 | 2.3102 | 2.1908 | 2.0939 | 3.6673 | 3.6214 | 3.5776 | 3.5163 | 3.4469 | 3.4061 | 3.3184 | 3.2184 | 3.1122 | 3.0673 | 2.8908 | 2.5827 | 1.9061 | 3.5143 | 3.4531 | 3.3949 | 3.3163 | 3.2286 | 3.1745 | 3.0612 | 2.9276 | 2.7949 | 2.7337 | 2.5204 | 2.4204 | 2.3347
|  | PARK HOUSE | EE |  |  |  | 3.3531 | 3.2867 | 3.2276 | 3.1469 | 3.0571 | 3 | 2.8827 | 2.748 | 2.6102 | 2.5459 | 2.3102 | 2.1908 | 2.1388 | 3.6673 | 3.6214 | 3.5776 | 3.5163 | 3.4469 | 3.4061 | 3.3184 | 3.2184 | 3.1122 | 3.0673 | 2.8908 | 2.6837 | 2.3531 | 3.5143 | 3.4531 | 3.3949 | 3.3163 | 3.2286 | 3.1745 | 3.0612 | 2.9276 | 2.7949 | 2.7337 | 2.5204 | 2.4204 | 2.3724
|  | PARK HOUSE | HT |  |  |  | 3.3959 | 3.349 | 3.2969 | 3.2286 | 3.1867 | 3.1153 | 3.0347 | 2.9337 | 2.8673 | 2.7612 | 2.3735 | 2.2051 | 2.0939 | 3.7041 | 3.6755 | 3.6439 | 3.599 | 3.5704 | 3.5224 | 3.4714 | 3.4041 | 3.3673 | 3.2939 | 3.052 | 2.9673 | 2.9133 | 3.5541 | 3.5122 | 3.4653 | 3.3969 | 3.3571 | 3.2878 | 3.2092 | 3.1122 | 3.048 | 2.9439 | 2.5806 | 2.4316 | 2.3347
|  | PARK HOUSE | HE |  |  |  | 3.3959 | 3.35 | 3.299 | 3.2347 | 3.1929 | 3.1265 | 3.048 | 2.95 | 2.8878 | 2.7827 | 2.3643 | 2.2531 | 2.2102 | 3.699 | 3.6694 | 3.6357 | 3.5867 | 3.5551 | 3.5061 | 3.451 | 3.3796 | 3.3347 | 3.2582 | 2.9337 | 2.7245 | 2.4041 | 3.5561 | 3.5143 | 3.4663 | 3.402 | 3.3633 | 3.2959 | 3.2224 | 3.1265 | 3.0684 | 2.9684 | 2.5755 | 2.4786 | 2.4408
|  | PARK HOUSE | CF |  |  |  | 3.4071 | 3.3561 | 3.3133 | 3.2765 | 3.2184 | 3.1837 | 3.1265 | 3.0694 | 2.9969 | 2.9214 | 2.5806 | 2.4051 | 2.248 | 3.7092 | 3.6694 | 3.6429 | 3.6122 | 3.5684 | 3.5398 | 3.4929 | 3.4398 | 3.3796 | 3.3133 | 2.9633 | 2.5827 | 1.9061 | 3.5633 | 3.5204 | 3.4816 | 3.4429 | 3.3888 | 3.3582 | 3.302 | 3.2449 | 3.1745 | 3.101 | 2.7714 | 2.6102 | 2.4663
MINETY GSP | STRATTON (2 X 90) | PARK NORTH | MINIMUM HEADROOM | SU 18052 84542 | YES | 2.212 | 10.3061 | 9.4367 | 8.7786 | 7.8898 | 6.9235 | 5.8765 | 4.2459 | 2.3796 | 0.47041 | -0.97449 | -6.349 | -9.5439 | -10.0857 | 11.5867 | 10.8949 | 10.3827 | 9.6296 | 8.7724 | 7.8622 | 6.6898 | 5.3245 | 3.9122 | 2.849 | -1.9163 | -8.1643 | -21.6592 | 10.2949 | 9.4429 | 8.8306 | 7.9286 | 6.9286 | 5.8837 | 4.3663 | 2.6173 | 0.83469 | -0.48878 | -5.9204 | -9.4031 | -9.8918
|  | PARK NORTH | EE |  |  |  | 10.3061 | 9.4367 | 8.7786 | 7.8898 | 6.9235 | 5.8765 | 4.2459 | 2.3796 | 0.47041 | -0.97449 | -6.349 | -8.9694 | -8.9408 | 11.5867 | 10.8949 | 10.3827 | 9.6296 | 8.7724 | 7.8622 | 6.6898 | 5.3245 | 3.9122 | 2.849 | -1.8276 | -6.0286 | -11.8337 | 10.2949 | 9.4429 | 8.8306 | 7.9286 | 6.9286 | 5.8837 | 4.3663 | 2.6173 | 0.83469 | -0.48878 | -5.248 | -7.4643 | -7.3827
|  | PARK NORTH | HT |  |  |  | 10.702 | 10.0204 | 9.3082 | 8.5694 | 8.0163 | 7.25 | 5.8969 | 4.4255 | 2.949 | 1.5122 | -5.3286 | -9.001 | -9.6531 | 12.0163 | 11.5704 | 11.0816 | 10.5531 | 10.1918 | 9.6112 | 8.7949 | 7.8551 | 6.8908 | 5.95 | 1.8051 | -0.24592 | -0.69388 | 10.7449 | 10.1184 | 9.4551 | 8.7337 | 8.2378 | 7.4541 | 6.202 | 4.8031 | 3.3867 | 2 | -4.2214 | -7.4551 | -7.9367
|  | PARK NORTH | HE |  |  |  | 10.6265 | 9.9204 | 9.1653 | 8.3745 | 7.7827 | 6.9602 | 5.6612 | 4.1673 | 2.5551 | 0.93673 | -5.9286 | -9.5439 | -10.0857 | 11.8888 | 11.3571 | 10.7551 | 10.1071 | 9.6296 | 8.8847 | 7.9306 | 6.799 | 5.5551 | 4.2735 | -1.9163 | -6.8786 | -12.8816 | 10.6653 | 10.0122 | 9.3071 | 8.5337 | 8.0102 | 7.1745 | 5.9551 | 4.5265 | 2.9806 | 1.4184 | -5.9204 | -9.4031 | -9.8918
|  | PARK NORTH | CF |  |  |  | 11.0561 | 10.4939 | 10.0184 | 9.5398 | 9.0184 | 8.601 | 8.4194 | 7.8296 | 7.1724 | 6.4551 | 0.87449 | -4.5418 | -8.4316 | 12.1551 | 11.6724 | 11.2214 | 10.7367 | 10.1796 | 9.6367 | 9.2857 | 8.5337 | 7.702 | 6.8102 | 0.51735 | -8.1643 | -21.6592 | 11.0653 | 10.549 | 10.101 | 9.6265 | 9.102 | 8.6439 | 8.4969 | 7.8704 | 7.1714 | 6.4235 | 1.2561 | -3.9571 | -7.2551
WILLESDEN GSP | ACTON LANE | PARK ROYAL | MINIMUM HEADROOM | TQ 20137 82215 | YES | 5.897 | 2.1958 | 1.9316 | 1.554 | 1.0642 | 0.46217 | -0.23783 | -0.8715 | -1.5705 | -2.1144 | -2.6368 | -4.4093 | -5.7144 | -6.2735 | 3.5205 | 3.3429 | 3.0511 | 2.7205 | 2.3654 | 1.9419 | 1.345 | 0.52151 | -0.15298 | -0.81624 | -2.5509 | -3.5826 | -4.253 | 2.4617 | 2.2158 | 1.8638 | 1.4587 | 1.0127 | 0.4209 | -0.22502 | -1.0556 | -1.8393 | -2.5944 | -4.4944 | -5.8454 | -6.5097
|  | PARK ROYAL | EE |  |  |  | 2.1958 | 1.9316 | 1.554 | 1.0642 | 0.46217 | -0.23783 | -0.8715 | -1.5705 | -2.1144 | -2.6368 | -4.2868 | -4.8123 | -5.3123 | 3.5205 | 3.3429 | 3.0511 | 2.7205 | 2.3654 | 1.9419 | 1.345 | 0.52151 | -0.15298 | -0.81624 | -2.5509 | -3.1336 | -3.7418 | 2.4617 | 2.2158 | 1.8638 | 1.4587 | 1.0127 | 0.4209 | -0.22502 | -1.0556 | -1.8393 | -2.5944 | -4.4944 | -5.0975 | -5.7005
|  | PARK ROYAL | HT |  |  |  | 2.3254 | 2.052 | 1.7254 | 1.2581 | 0.71115 | 0.14483 | -0.41028 | -0.99701 | -1.4909 | -2.0001 | -3.4317 | -4.6766 | -5.2654 | 3.6358 | 3.4287 | 3.1838 | 2.9042 | 2.5684 | 2.2797 | 1.7899 | 1.244 | 0.80314 | 0.23988 | -1.9775 | -3.2101 | -3.8581 | 2.6036 | 2.3576 | 2.0791 | 1.777 | 1.2893 | 0.79233 | 0.21886 | -0.40155 | -0.90869 | -1.4434 | -3.7567 | -5.1291 | -5.8179
|  | PARK ROYAL | HE |  |  |  | 2.2816 | 2.0407 | 1.6958 | 1.2061 | 0.63666 | -0.027622 | -0.55619 | -1.1317 | -1.5623 | -1.996 | -4.4093 | -5.7144 | -6.2735 | 3.596 | 3.4399 | 3.1746 | 2.8664 | 2.5144 | 2.1042 | 1.6562 | 1.1297 | 0.60722 | 0.037837 | -2.3969 | -3.5826 | -4.253 | 2.5546 | 2.3372 | 2.0178 | 1.6648 | 1.2362 | 0.62906 | 0.10253 | -0.48727 | -0.98216 | -1.6679 | -4.4781 | -5.8454 | -6.5097
|  | PARK ROYAL | CF |  |  |  | 2.4622 | 2.3999 | 2.2805 | 2.0775 | 1.8418 | 1.5326 | 1.0295 | 0.38564 | -0.21028 | -0.76232 | -2.1307 | -3.5062 | -4.345 | 3.7154 | 3.6633 | 3.5766 | 3.396 | 3.1919 | 2.9256 | 2.5021 | 1.997 | 1.5389 | 1.1225 | -0.36931 | -1.5713 | -3.0622 | 2.7189 | 2.6525 | 2.5413 | 2.3464 | 2.124 | 1.8362 | 1.3801 | 0.8158 | 0.28722 | -0.21584 | -2.072 | -3.5097 | -4.3332
MANNINGTON GSP | BOURNEMOUTH | PARKSTONE NORTH | MINIMUM HEADROOM | SZ 03222 92233 | YES | 2.286 | 0.20204 | -0.59694 | -1.2245 | -2.348 | -3.5 | -4.7316 | -6.3255 | -8.1776 | -10.0143 | -11.3745 | -18.7184 | -25.0439 | -28.5235 | 7.651 | 6.9571 | 6.5 | 5.6173 | 4.6704 | 3.6469 | 2.4378 | 1.0388 | -0.37755 | -1.3816 | -6.8541 | -13.9745 | -31.8612 | 1.198 | 0.4 | -0.17347 | -1.2398 | -2.3602 | -3.5673 | -5.1082 | -6.8418 | -8.5633 | -9.8071 | -16.0878 | -21.4888 | -24.3204
|  | PARKSTONE NORTH | EE |  |  |  | 0.20204 | -0.59694 | -1.2245 | -2.348 | -3.5 | -4.7316 | -6.3255 | -8.1776 | -10.0143 | -11.3745 | -18.3796 | -23.8847 | -28.1704 | 7.651 | 6.9571 | 6.5 | 5.6173 | 4.6704 | 3.6469 | 2.4378 | 1.0388 | -0.37755 | -1.3816 | -6.8541 | -12.8112 | -22.2459 | 1.198 | 0.4 | -0.17347 | -1.2398 | -2.3602 | -3.5673 | -5.1082 | -6.8418 | -8.5633 | -9.8071 | -15.998 | -20.5184 | -24.0755
|  | PARKSTONE NORTH | HT |  |  |  | 0.58163 | -0.04898 | -0.94184 | -1.7827 | -2.6561 | -3.6622 | -5.0878 | -6.6398 | -8.2663 | -9.9286 | -18.7184 | -25.0439 | -28.5235 | 8.1194 | 7.7051 | 7.1224 | 6.7224 | 6.1653 | 5.5214 | 4.7265 | 3.8133 | 2.8367 | 1.8224 | -2.9724 | -5.7724 | -7.1408 | 1.6347 | 1.0408 | 0.22041 | -0.48163 | -1.301 | -2.2459 | -3.5551 | -4.998 | -6.5204 | -8.0847 | -16.0878 | -21.4888 | -24.3204
|  | PARKSTONE NORTH | HE |  |  |  | 0.56939 | -0.012245 | -0.83673 | -1.5255 | -2.4418 | -3.4316 | -4.5898 | -5.8704 | -7.2031 | -8.5939 | -16.0878 | -21.652 | -24.1337 | 8.0184 | 7.5398 | 6.8878 | 6.448 | 5.7388 | 4.9643 | 4.098 | 3.0939 | 2.0173 | 0.86327 | -5.5786 | -11.7571 | -20.5184 | 1.6163 | 1.0602 | 0.2949 | -0.28673 | -1.1327 | -2.0561 | -3.1429 | -4.3612 | -5.6398 | -6.9786 | -13.8327 | -18.4786 | -20.4816
|  | PARKSTONE NORTH | CF |  |  |  | 0.89592 | 0.50612 | 0.02551 | -0.50408 | -0.75 | -1.3388 | -1.7786 | -2.3388 | -2.9561 | -3.5908 | -8.3857 | -13.7286 | -18.7918 | 8.1929 | 7.7724 | 7.2918 | 6.7469 | 6.4633 | 5.8122 | 5.151 | 4.352 | 3.4867 | 2.5612 | -3.9694 | -13.9745 | -31.8612 | 1.9163 | 1.5347 | 1.0816 | 0.57245 | 0.36837 | -0.18571 | -0.63367 | -1.202 | -1.8296 | -2.4827 | -7.0357 | -11.85 | -16.2265
MANNINGTON GSP | BOURNEMOUTH | PARKSTONE SOUTH | MINIMUM HEADROOM | SZ 04762 89848 | YES | 0.988 | 18.8949 | 18.4745 | 17.9724 | 17.3888 | 16.7429 | 16.6102 | 15.7245 | 14.7163 | 13.7133 | 12.948 | 8.9031 | 5.4071 | 3.5612 | 19.9531 | 19.6082 | 19.2071 | 18.7286 | 18.1867 | 18.0673 | 17.4347 | 16.6959 | 15.9459 | 15.3612 | 12.2765 | 8.7531 | -0.65102 | 18.9245 | 18.5173 | 18.0439 | 17.4796 | 16.848 | 16.7561 | 15.9449 | 14.9959 | 14.0469 | 13.3378 | 9.7041 | 6.5694 | 4.9878
|  | PARKSTONE SOUTH | EE |  |  |  | 18.8949 | 18.4745 | 17.9724 | 17.3888 | 16.7429 | 16.6102 | 15.7245 | 14.7163 | 13.7133 | 12.948 | 9.1347 | 6.3265 | 3.9163 | 19.9531 | 19.6082 | 19.2071 | 18.7286 | 18.1867 | 18.0673 | 17.4347 | 16.6959 | 15.9459 | 15.3612 | 12.2765 | 9.0867 | 4.0418 | 18.9245 | 18.5173 | 18.0439 | 17.4796 | 16.848 | 16.7561 | 15.9449 | 14.9959 | 14.0469 | 13.3378 | 9.8612 | 7.4 | 5.299
|  | PARKSTONE SOUTH | HT |  |  |  | 19.1408 | 18.8194 | 18.3776 | 17.9643 | 17.5612 | 17.0663 | 16.2367 | 15.7214 | 14.8276 | 13.902 | 8.9031 | 5.4071 | 3.5612 | 20.1918 | 19.9745 | 19.699 | 19.4112 | 19.1347 | 18.7827 | 18.2908 | 18.1327 | 17.5959 | 17.0347 | 14.2673 | 12.5908 | 11.849 | 19.1653 | 18.8531 | 18.45 | 18.052 | 17.6827 | 17.2082 | 16.4388 | 16.0071 | 15.1765 | 14.3153 | 9.7041 | 6.5694 | 4.9878
|  | PARKSTONE SOUTH | HE |  |  |  | 19.1327 | 18.8398 | 18.4857 | 18.0888 | 17.7194 | 17.2765 | 16.5867 | 16.2265 | 15.5031 | 14.7469 | 10.7755 | 7.95 | 6.6663 | 20.1459 | 19.9041 | 19.6204 | 19.2969 | 18.9847 | 18.5969 | 18.0908 | 17.8694 | 17.3133 | 16.7143 | 13.3143 | 10.0051 | 5.4776 | 19.1561 | 18.8714 | 18.5429 | 18.1622 | 17.8255 | 17.399 | 16.7551 | 16.4776 | 15.8031 | 15.098 | 11.4143 | 8.9163 | 7.8306
|  | PARKSTONE SOUTH | CF |  |  |  | 19.2735 | 19.0898 | 18.9071 | 18.6776 | 18.4755 | 18.199 | 17.8878 | 17.4857 | 17.5235 | 17.152 | 14.6408 | 11.898 | 9.1969 | 20.2214 | 20.0255 | 19.8255 | 19.5786 | 19.3367 | 19.0112 | 18.6327 | 18.1673 | 18.0041 | 17.5224 | 14.102 | 8.7531 | -0.65102 | 19.2878 | 19.1102 | 18.9347 | 18.7122 | 18.5194 | 18.251 | 17.948 | 17.5582 | 17.6122 | 17.25 | 14.8888 | 12.4061 | 9.9673
BRAMLEY (FLEE) | WOKINGHAM BSP | PEACOCK FARM | MINIMUM HEADROOM | SU 84770 68709 | YES | 13.386 | 2.2549 | 2.0181 | 1.8049 | 1.6161 | 1.412 | 1.2365 | 0.53242 | -0.27676 | -0.93084 | -1.5339 | -3.9951 | -6.0257 | -7.3829 | 2.3452 | 2.1758 | 2.0197 | 1.8574 | 1.6768 | 1.5105 | 0.75844 | -0.12217 | -0.81707 | -1.4885 | -3.615 | -5.8528 | -9.1926 | 2.1656 | 1.9442 | 1.7482 | 1.5431 | 1.3207 | 1.1503 | 0.34314 | -0.59564 | -1.3436 | -2.014 | -4.4844 | -6.6456 | -8.1069
|  | PEACOCK FARM | EE |  |  |  | 2.2549 | 2.0181 | 1.8049 | 1.6161 | 1.412 | 1.2365 | 0.53242 | -0.27676 | -0.93084 | -1.5339 | -3.3502 | -4.8615 | -6.3104 | 2.3452 | 2.1758 | 2.0197 | 1.8574 | 1.6768 | 1.5105 | 0.75844 | -0.12217 | -0.81707 | -1.4885 | -3.615 | -5.8528 | -9.1926 | 2.1656 | 1.9442 | 1.7482 | 1.5431 | 1.3207 | 1.1503 | 0.34314 | -0.59564 | -1.3436 | -2.014 | -3.7538 | -5.2916 | -6.8273
|  | PEACOCK FARM | HT |  |  |  | 2.3028 | 2.0865 | 1.8834 | 1.7283 | 1.5794 | 1.3998 | 0.72732 | 0.0089551 | -0.62472 | -1.3145 | -3.9951 | -6.0257 | -7.3829 | 2.4084 | 2.2911 | 2.1819 | 2.0891 | 2.0044 | 1.8921 | 1.2248 | 0.48396 | -0.13339 | -0.82523 | -3.2191 | -4.9579 | -6.1752 | 2.236 | 2.0442 | 1.8666 | 1.7125 | 1.5809 | 1.4003 | 0.63089 | -0.18237 | -0.8987 | -1.6905 | -4.4844 | -6.6456 | -8.1069
|  | PEACOCK FARM | HE |  |  |  | 2.3141 | 2.0998 | 1.9151 | 1.7661 | 1.6324 | 1.462 | 0.97732 | 0.45079 | 0.10079 | -0.28696 | -2.087 | -3.6125 | -4.8094 | 2.3921 | 2.2421 | 2.1095 | 1.9829 | 1.8727 | 1.7238 | 1.2064 | 0.61049 | 0.24824 | -0.17013 | -2.3242 | -4.616 | -7.8722 | 2.2482 | 2.0513 | 1.8942 | 1.7421 | 1.6238 | 1.4523 | 0.89416 | 0.2962 | -0.093596 | -0.52829 | -2.3109 | -3.8742 | -5.1936
|  | PEACOCK FARM | CF |  |  |  | 2.3579 | 2.2018 | 2.0661 | 1.9651 | 1.859 | 1.7671 | 1.4896 | 1.0977 | 0.76202 | 0.5161 | -0.6237 | -1.2155 | -2.0615 | 2.4074 | 2.2819 | 2.1554 | 2.0493 | 1.9258 | 1.8003 | 1.4095 | 0.87171 | 0.39926 | 0.011506 | -1.8089 | -4.1742 | -8.8007 | 2.2809 | 2.1421 | 2.0197 | 1.9197 | 1.8054 | 1.7238 | 1.3819 | 0.9013 | 0.48089 | 0.19518 | -1.0354 | -1.3814 | -2.0885
WILLESDEN GSP |  | PERIVALE | MINIMUM HEADROOM | TQ 17544 82947 | YES | 17.131 | 48.5155 | 47.3767 | 46.1053 | 45.5379 | 44.9543 | 42.9134 | 42.0736 | 40.7073 | 40.09 | 37.2247 | 30.2553 | 22.0838 | 14.8992 | 52.2063 | 51.1736 | 50.041 | 49.2083 | 48.5961 | 46.1747 | 45.1104 | 43.6522 | 43.1287 | 39.7849 | 31.5389 | 21.1604 | 6.5604 | 49.0318 | 47.9961 | 46.8645 | 45.942 | 45.3961 | 43.0563 | 41.8736 | 40.3849 | 39.8512 | 36.492 | 28.6634 | 19.4961 | 10.0665
|  | PERIVALE | EE |  |  |  | 48.5155 | 47.3767 | 46.1053 | 46.0614 | 45.6185 | 44.6838 | 43.4634 | 42.6043 | 40.9849 | 40.0502 | 34.9461 | 24.8032 | 21.443 | 52.2063 | 51.1736 | 50.041 | 49.9706 | 49.5685 | 48.5532 | 47.39 | 46.7145 | 45.0787 | 44.1083 | 38.1624 | 24.3563 | 15.694 | 49.0318 | 47.9961 | 46.891 | 46.7777 | 46.4083 | 45.3757 | 44.0838 | 43.2696 | 41.5094 | 40.49 | 34.8859 | 22.8155 | 18.742
|  | PERIVALE | HT |  |  |  | 48.7838 | 47.7287 | 46.4461 | 45.843 | 45.4655 | 43.7675 | 42.892 | 41.4287 | 40.6012 | 38.9043 | 31.9828 | 22.0838 | 15.6951 | 52.4114 | 51.4614 | 50.2655 | 49.6992 | 49.4583 | 47.592 | 46.7104 | 45.2808 | 44.6583 | 42.9655 | 36.6114 | 25.743 | 18.1747 | 49.1838 | 48.1951 | 46.9798 | 46.3767 | 46.1124 | 44.193 | 43.0369 | 41.4604 | 40.6267 | 38.7185 | 31.1492 | 19.4961 | 11.7389
|  | PERIVALE | HE |  |  |  | 48.7665 | 47.7236 | 46.3787 | 45.5379 | 44.9543 | 42.9134 | 42.0736 | 40.7073 | 40.09 | 37.2247 | 30.2553 | 23.0267 | 14.8992 | 52.3849 | 51.4267 | 50.1226 | 49.2083 | 48.5961 | 46.1747 | 45.1104 | 43.6522 | 43.1287 | 39.7849 | 31.5389 | 21.1604 | 6.5604 | 49.1604 | 48.1747 | 46.8645 | 45.942 | 45.3961 | 43.0563 | 41.8736 | 40.3849 | 39.8512 | 36.492 | 28.6634 | 20.0879 | 10.0665
|  | PERIVALE | CF |  |  |  | 48.8992 | 47.9277 | 46.9665 | 46.7502 | 46.4165 | 45.9604 | 45.3798 | 44.8226 | 44.7879 | 44.1747 | 39.9624 | 34.8083 | 29.7889 | 52.4522 | 51.5114 | 50.5767 | 50.3828 | 49.9318 | 49.3328 | 48.5757 | 47.8543 | 47.4563 | 46.592 | 40.4981 | 30.8226 | 16.5073 | 49.294 | 48.3889 | 47.4849 | 47.344 | 47.0196 | 46.592 | 46.0308 | 45.4543 | 45.2818 | 44.6053 | 39.9461 | 34.0869 | 28.5032
BRAMLEY (FLEE) | FERNHURST | PETERSFIELD | MINIMUM HEADROOM | SU 74173 23420 | YES | 5.398 | 7.1669 | 6.6414 | 5.9649 | 5.7047 | 4.9955 | 4.2353 | 3.118 | 1.8578 | 0.58632 | -0.33409 | -4.8871 | -8.482 | -10.4892 | 12.27 | 11.8629 | 11.3343 | 11.1312 | 10.571 | 9.9598 | 9.169 | 8.2547 | 7.3251 | 6.671 | 3.269 | -0.34633 | -9.732 | 7.2159 | 6.7282 | 6.0853 | 5.8822 | 5.2169 | 4.4873 | 3.4363 | 2.2435 | 1.0414 | 0.19244 | -3.8963 | -6.9259 | -8.6535
|  | PETERSFIELD | EE |  |  |  | 7.1669 | 6.6414 | 5.9649 | 5.7047 | 4.9955 | 4.2353 | 3.118 | 1.8578 | 0.58632 | -0.33409 | -4.8871 | -7.8494 | -10.0412 | 12.27 | 11.8629 | 11.3343 | 11.1312 | 10.571 | 9.9598 | 9.169 | 8.2547 | 7.3251 | 6.671 | 3.269 | 0.064894 | -4.7678 | 7.2159 | 6.7282 | 6.0853 | 5.8822 | 5.2169 | 4.4873 | 3.4363 | 2.2435 | 1.0414 | 0.19244 | -3.8963 | -6.3729 | -8.2933
|  | PETERSFIELD | HT |  |  |  | 7.5078 | 7.1016 | 6.6455 | 6.1098 | 5.4975 | 5.2547 | 4.318 | 3.2904 | 2.1996 | 1.0567 | -4.781 | -8.482 | -10.4892 | 12.5863 | 12.3302 | 12.0353 | 11.6802 | 11.2649 | 11.1537 | 10.6149 | 10.0006 | 9.3394 | 8.6424 | 5.3047 | 3.5098 | 2.6455 | 7.5659 | 7.1955 | 6.7822 | 6.2873 | 5.718 | 5.5139 | 4.6506 | 3.6924 | 2.6782 | 1.6129 | -3.7443 | -6.9259 | -8.6535
|  | PETERSFIELD | HE |  |  |  | 7.4812 | 7.0863 | 6.6373 | 6.119 | 5.5231 | 5.3047 | 4.4782 | 3.5537 | 2.5659 | 1.5241 | -4.1708 | -7.2055 | -8.482 | 12.522 | 12.218 | 11.8751 | 11.4629 | 10.9945 | 10.819 | 10.2384 | 9.5649 | 8.8373 | 8.0608 | 3.82 | 0.31183 | -4.2484 | 7.5241 | 7.1782 | 6.7731 | 6.2935 | 5.7404 | 5.2935 | 4.5475 | 3.6526 | 2.6904 | 1.67 | -3.2249 | -5.9974 | -7.1565
|  | PETERSFIELD | CF |  |  |  | 7.6833 | 7.4139 | 7.0894 | 6.7986 | 6.4384 | 6.0414 | 6.0108 | 5.5639 | 5.0761 | 4.5629 | 0.94142 | -2.7137 | -5.8504 | 12.6363 | 12.3955 | 12.0986 | 11.8159 | 11.469 | 11.0649 | 10.9302 | 10.4404 | 9.9078 | 9.3363 | 5.3067 | -0.34633 | -9.732 | 7.7149 | 7.4649 | 7.1557 | 6.8894 | 6.5465 | 6.1639 | 6.1782 | 5.7588 | 5.2884 | 4.7424 | 1.1894 | -2.1382 | -4.7657
IVER 132KV | CHALVEY BSP | PETERSFIELD AVENUE | MINIMUM HEADROOM | SU 98108 80286 | YES | 2.625 | 34.6922 | 33.4279 | 31.8116 | 29.885 | 28.0871 | 26.1177 | 24.6697 | 23.3962 | 22.1636 | 21.1238 | 17.9524 | 14.9462 | 13.9799 | 37.0096 | 36.3525 | 35.4361 | 34.3474 | 33.4361 | 32.2943 | 30.9606 | 29.6045 | 28.3627 | 27.1882 | 22.7902 | 18.5014 | 7.3351 | 34.4929 | 33.3837 | 32.0112 | 30.3837 | 29.0255 | 27.348 | 25.8306 | 24.3796 | 23.0674 | 21.9592 | 18.5776 | 15.5255 | 14.3827
|  | PETERSFIELD AVENUE | EE |  |  |  | 34.6922 | 33.4279 | 31.8116 | 29.885 | 28.0871 | 26.1177 | 24.6697 | 23.3962 | 22.1636 | 21.1238 | 18.1687 | 16.2493 | 15.8024 | 37.0096 | 36.3525 | 35.4361 | 34.3474 | 33.4361 | 32.2943 | 30.9606 | 29.6045 | 28.3627 | 27.1882 | 22.7902 | 18.5014 | 12.2086 | 34.4929 | 33.3837 | 32.0112 | 30.3837 | 29.0255 | 27.348 | 25.8306 | 24.3796 | 23.0674 | 21.9592 | 18.8806 | 17.0204 | 16.2806
|  | PETERSFIELD AVENUE | HT |  |  |  | 34.935 | 33.7411 | 32.236 | 30.4799 | 28.3524 | 26.4044 | 25.3646 | 24.2687 | 23.183 | 22.0422 | 17.9524 | 14.9462 | 13.9799 | 37.1627 | 36.6657 | 35.931 | 35.077 | 33.978 | 32.9617 | 32.0596 | 30.9739 | 29.9372 | 28.8127 | 25.0892 | 22.6025 | 21.3821 | 34.6663 | 33.7714 | 32.548 | 31.1378 | 29.3817 | 27.7061 | 26.6633 | 25.4714 | 24.3174 | 23.0459 | 18.5776 | 15.5255 | 14.3827
|  | PETERSFIELD AVENUE | HE |  |  |  | 34.9136 | 33.7718 | 32.2983 | 30.583 | 28.5942 | 26.7289 | 25.934 | 25.1024 | 24.4279 | 23.6667 | 20.8371 | 18.9922 | 17.9442 | 37.1351 | 36.5688 | 35.7739 | 34.8627 | 33.7882 | 32.727 | 31.9474 | 30.981 | 30.2198 | 29.3341 | 24.9035 | 20.5463 | 14.0484 | 34.6531 | 33.7959 | 32.6031 | 31.2317 | 29.6051 | 28.001 | 27.2357 | 26.3266 | 25.6439 | 24.8194 | 21.6714 | 19.8306 | 18.5184
|  | PETERSFIELD AVENUE | CF |  |  |  | 35.4228 | 35.2799 | 34.882 | 34.1248 | 32.8932 | 30.7085 | 28.2758 | 27.3289 | 27.0911 | 26.5942 | 23.8667 | 21.6207 | 19.6993 | 37.4157 | 37.3076 | 37.0055 | 36.4841 | 35.7484 | 34.4912 | 32.8566 | 31.8127 | 31.2025 | 30.381 | 25.7168 | 19.0555 | 7.3351 | 35.1041 | 34.9919 | 34.6327 | 33.9745 | 32.9939 | 31.2776 | 29.2612 | 28.2786 | 28.0133 | 27.4276 | 24.6439 | 22.5766 | 20.9092
MANNINGTON GSP | SALISBURY | PETERSFINGER | MINIMUM HEADROOM | SU 15608 29334 | YES | 1.384 | 10.2669 | 9.9241 | 9.4924 | 8.9884 | 8.771 | 8.2139 | 7.4312 | 6.5353 | 5.5649 | 4.9884 | 2.2598 | 0.50163 | -0.29531 | 14.521 | 14.2537 | 13.9067 | 13.5139 | 13.369 | 12.9506 | 12.4149 | 11.7986 | 11.121 | 10.7129 | 8.5139 | 5.7414 | -0.78408 | 11.5506 | 11.1996 | 10.7333 | 10.1924 | 10.1271 | 9.5965 | 8.868 | 8.0271 | 7.1261 | 6.6098 | 4.2731 | 2.7976 | 2.1639
|  | PETERSFINGER | EE |  |  |  | 10.2669 | 9.9241 | 9.4924 | 8.9884 | 8.771 | 8.2139 | 7.4312 | 6.5353 | 5.5649 | 4.9884 | 2.2598 | 0.71082 | 0.26796 | 14.521 | 14.2537 | 13.9067 | 13.5139 | 13.369 | 12.9506 | 12.4149 | 11.7986 | 11.121 | 10.7129 | 8.5139 | 6.3782 | 3.3312 | 11.5506 | 11.1996 | 10.7333 | 10.1924 | 10.1271 | 9.5965 | 8.868 | 8.0271 | 7.1261 | 6.6098 | 4.2731 | 2.9945 | 2.6159
|  | PETERSFINGER | HT |  |  |  | 10.4384 | 10.119 | 9.7863 | 9.3782 | 8.8986 | 8.3669 | 7.9424 | 7.219 | 6.5261 | 5.8537 | 2.471 | 0.50163 | -0.29531 | 14.7016 | 14.5159 | 14.2996 | 14.0537 | 13.7547 | 13.418 | 13.2649 | 12.8445 | 12.4282 | 12.0129 | 10.0598 | 9.0424 | 8.6261 | 11.7792 | 11.4914 | 11.1578 | 10.7843 | 10.3241 | 9.8139 | 9.5424 | 8.8782 | 8.2241 | 7.5761 | 4.4873 | 2.7976 | 2.1639
|  | PETERSFINGER | HE |  |  |  | 10.4363 | 10.1629 | 9.8282 | 9.4741 | 9.0424 | 8.5567 | 7.8986 | 7.521 | 6.7537 | 6.1373 | 3.0812 | 1.4955 | 0.9098 | 14.67 | 14.468 | 14.2098 | 13.9516 | 13.6241 | 13.2567 | 12.7976 | 12.5976 | 12.0639 | 11.5853 | 8.9741 | 6.7414 | 3.6863 | 11.7782 | 11.522 | 11.1873 | 10.8598 | 10.4384 | 9.969 | 9.3537 | 9.1302 | 8.4261 | 7.8322 | 5.0404 | 3.6894 | 3.072
|  | PETERSFINGER | CF |  |  |  | 10.6302 | 10.4578 | 10.2833 | 10.0731 | 9.8935 | 9.6496 | 9.3669 | 9.0006 | 8.8853 | 8.4639 | 5.9282 | 3.7149 | 1.6751 | 14.769 | 14.6037 | 14.4353 | 14.2302 | 14.0292 | 13.7598 | 13.4445 | 13.0527 | 12.9027 | 12.4731 | 9.6669 | 5.7414 | -0.78408 | 11.9333 | 11.7465 | 11.5649 | 11.3363 | 11.1424 | 10.8761 | 10.571 | 10.1792 | 10.2394 | 9.8384 | 7.4935 | 5.5445 | 3.8322
MELKSHAM GSP | AMESBURY | PEWSEY | MINIMUM HEADROOM | SU 14710 59252 | YES | 0.518 | 4.8116 | 4.6259 | 4.3565 | 4.13 | 3.8208 | 3.48 | 3.0453 | 3.2851 | 2.9147 | 2.7892 | 1.6188 | 1.1871 | 0.76673 | 8.01 | 7.8712 | 7.6682 | 7.5018 | 7.2631 | 7.01 | 6.6927 | 6.7947 | 6.511 | 6.3386 | 5.4018 | 4.0865 | 1.1498 | 5.4667 | 5.282 | 5.0086 | 4.779 | 4.4637 | 4.1249 | 3.6994 | 3.9473 | 3.5851 | 3.4667 | 2.5882 | 2.2229 | 1.8841
|  | PEWSEY | EE |  |  |  | 4.8116 | 4.6259 | 4.3565 | 4.13 | 3.8208 | 3.48 | 3.0453 | 3.2851 | 2.9147 | 2.7892 | 1.6188 | 1.1943 | 0.96163 | 8.01 | 7.8712 | 7.6682 | 7.5018 | 7.2631 | 7.01 | 6.6927 | 6.7947 | 6.511 | 6.3386 | 5.4018 | 4.5335 | 3.0988 | 5.4667 | 5.282 | 5.0086 | 4.779 | 4.4637 | 4.1249 | 3.6994 | 3.9473 | 3.5851 | 3.4667 | 2.5882 | 2.228 | 2.0473
|  | PEWSEY | HT |  |  |  | 4.9473 | 4.8229 | 4.6586 | 4.5147 | 4.3096 | 4.1371 | 3.8555 | 3.5229 | 3.1739 | 3.2361 | 1.8535 | 1.1871 | 0.76673 | 8.1386 | 8.0427 | 7.9182 | 7.8141 | 7.6651 | 7.5447 | 7.3406 | 7.1029 | 6.8518 | 6.9845 | 6.1314 | 5.762 | 5.5529 | 5.6249 | 5.4943 | 5.3188 | 5.1749 | 4.9718 | 4.7973 | 4.5167 | 4.1871 | 3.8433 | 4.0331 | 2.78 | 2.2229 | 1.8841
|  | PEWSEY | HE |  |  |  | 4.9433 | 4.8208 | 4.6576 | 4.5157 | 4.3147 | 4.1473 | 3.8769 | 3.5463 | 3.1943 | 3.3229 | 1.8667 | 1.4361 | 1.2422 | 8.1324 | 8.0335 | 7.8998 | 7.7886 | 7.6324 | 7.4937 | 7.2773 | 7.0171 | 6.7518 | 6.8029 | 5.6049 | 4.71 | 3.3069 | 5.6198 | 5.4912 | 5.3188 | 5.178 | 4.9769 | 4.8106 | 4.5402 | 4.2116 | 3.8637 | 4.1045 | 2.8035 | 2.4331 | 2.2861
|  | PEWSEY | CF |  |  |  | 4.9892 | 4.9045 | 4.7871 | 4.6504 | 4.5361 | 4.3902 | 4.2188 | 4.0708 | 3.8463 | 3.6096 | 2.8647 | 2.0933 | 1.4392 | 8.161 | 8.0722 | 7.96 | 7.8386 | 7.7324 | 7.5824 | 7.412 | 7.2498 | 7.0345 | 6.8039 | 5.7804 | 4.0865 | 1.1498 | 5.6667 | 5.5729 | 5.4463 | 5.3096 | 5.2086 | 5.0514 | 4.8749 | 4.7249 | 4.4963 | 4.2596 | 3.6361 | 2.9698 | 2.4514
CHICKERELL GSP | CHICKERELL BSP | PIDDLETRENTHIDE | MINIMUM HEADROOM | SY 70169 99809 | YES | 0.31 | 5.4745 | 5.3776 | 5.3112 | 5.2255 | 5.1245 | 5.0643 | 4.9337 | 4.7847 | 4.6969 | 4.6276 | 4.2857 | 4.1714 | 4.0653 | 5.3056 | 5.2321 | 5.1791 | 5.1179 | 5.0413 | 4.9923 | 4.8964 | 4.7842 | 4.7138 | 4.6617 | 4.424 | 4.1321 | 3.3913 | 4.4286 | 4.3408 | 4.2786 | 4.1969 | 4.1051 | 4.0459 | 3.9276 | 3.7867 | 3.7041 | 3.6378 | 3.3357 | 3.2388 | 3.1439
|  | PIDDLETRENTHIDE | EE |  |  |  | 5.4745 | 5.3776 | 5.3112 | 5.2255 | 5.1245 | 5.0643 | 4.9337 | 4.7847 | 4.6969 | 4.6276 | 4.2857 | 4.1714 | 4.1224 | 5.3056 | 5.2321 | 5.1791 | 5.1179 | 5.0413 | 4.9923 | 4.8964 | 4.7842 | 4.7138 | 4.6617 | 4.424 | 4.225 | 3.9015 | 4.4286 | 4.3408 | 4.2786 | 4.1969 | 4.1051 | 4.0459 | 3.9276 | 3.7867 | 3.7041 | 3.6378 | 3.3357 | 3.2388 | 3.1939
|  | PIDDLETRENTHIDE | HT |  |  |  | 5.5082 | 5.4327 | 5.3816 | 5.3102 | 5.2612 | 5.1908 | 5.0888 | 4.9735 | 4.9061 | 4.7888 | 4.3592 | 4.1847 | 4.0653 | 5.3454 | 5.2883 | 5.2495 | 5.2015 | 5.174 | 5.127 | 5.0587 | 4.9821 | 4.9383 | 4.8597 | 4.5852 | 4.4923 | 4.4342 | 4.4724 | 4.4 | 4.3459 | 4.2796 | 4.2337 | 4.1694 | 4.0765 | 3.9694 | 3.9041 | 3.7949 | 3.399 | 3.2439 | 3.1439
|  | PIDDLETRENTHIDE | HE |  |  |  | 5.5061 | 5.4316 | 5.3806 | 5.3102 | 5.2653 | 5.1969 | 5.0969 | 4.9847 | 4.9173 | 4.8031 | 4.3245 | 4.2133 | 4.1684 | 5.3423 | 5.2832 | 5.2383 | 5.1883 | 5.1566 | 5.1056 | 5.0342 | 4.9536 | 4.9036 | 4.8158 | 4.4577 | 4.2546 | 3.926 | 4.4704 | 4.399 | 4.3469 | 4.2806 | 4.2367 | 4.1745 | 4.0857 | 3.9816 | 3.9163 | 3.8112 | 3.3806 | 3.2837 | 3.2439
|  | PIDDLETRENTHIDE | CF |  |  |  | 5.5184 | 5.449 | 5.398 | 5.3582 | 5.2969 | 5.2622 | 5.1939 | 5.1276 | 5.0439 | 5.0061 | 4.5755 | 4.3796 | 4.198 | 5.3485 | 5.2944 | 5.2536 | 5.2219 | 5.174 | 5.1454 | 5.0872 | 5.0321 | 4.9648 | 4.925 | 4.5077 | 4.1321 | 3.3913 | 4.4847 | 4.4235 | 4.3663 | 4.3265 | 4.2724 | 4.2398 | 4.1796 | 4.1194 | 4.0439 | 4.0071 | 3.6153 | 3.4347 | 3.2745
BRAMLEY (FLEE) | FERNHURST | PLAISTOW | MINIMUM HEADROOM | TQ 02071 29626 | YES | 6.502 | 9.0444 | 8.8964 | 8.7587 | 8.5699 | 8.375 | 8.2138 | 7.9587 | 7.6607 | 7.3474 | 7.1821 | 5.874 | 5.5301 | 5.5668 | 10.4724 | 10.3663 | 10.2643 | 10.1255 | 9.9724 | 9.8571 | 9.6663 | 9.4408 | 9.2153 | 9.1 | 8.3929 | 7.9469 | 6.8531 | 9.1908 | 9.051 | 8.9163 | 8.7327 | 8.5357 | 8.3898 | 8.1429 | 7.8531 | 7.551 | 7.4 | 6.3051 | 6.0112 | 6.1245
|  | PLAISTOW | EE |  |  |  | 9.0444 | 8.8964 | 8.7587 | 8.5699 | 8.375 | 8.2138 | 7.9587 | 7.6607 | 7.3474 | 7.1821 | 5.874 | 5.5301 | 5.7087 | 10.4724 | 10.3663 | 10.2643 | 10.1255 | 9.9724 | 9.8571 | 9.6663 | 9.4408 | 9.2153 | 9.1 | 8.3929 | 7.9469 | 7.6245 | 9.1908 | 9.051 | 8.9163 | 8.7327 | 8.5357 | 8.3898 | 8.1429 | 7.8531 | 7.551 | 7.4 | 6.3051 | 6.0112 | 6.2429
|  | PLAISTOW | HT |  |  |  | 9.1077 | 8.9893 | 8.876 | 8.7291 | 8.6107 | 8.4495 | 8.2434 | 8.0577 | 7.8179 | 7.5679 | 6.025 | 5.5342 | 5.5668 | 10.5357 | 10.4663 | 10.3949 | 10.3061 | 10.2337 | 10.1255 | 9.9949 | 9.8847 | 9.7265 | 9.5592 | 8.6908 | 8.4418 | 8.6255 | 9.2561 | 9.149 | 9.0429 | 8.9061 | 8.8 | 8.6449 | 8.449 | 8.2867 | 8.0592 | 7.8235 | 6.4378 | 6.0122 | 6.1245
|  | PLAISTOW | HE |  |  |  | 9.1026 | 8.9883 | 8.877 | 8.7362 | 8.626 | 8.473 | 8.2781 | 8.0985 | 7.8679 | 7.6311 | 5.9974 | 6.0168 | 5.8832 | 10.5245 | 10.449 | 10.3714 | 10.2786 | 10.2031 | 10.0929 | 9.9561 | 9.8347 | 9.6714 | 9.4949 | 8.4827 | 8.351 | 7.748 | 9.25 | 9.148 | 9.0439 | 8.9122 | 8.8112 | 8.6643 | 8.4765 | 8.3214 | 8.102 | 7.8745 | 6.4184 | 6.5163 | 6.4143
|  | PLAISTOW | CF |  |  |  | 9.1291 | 9.0342 | 8.9403 | 8.8321 | 8.7117 | 8.623 | 8.4964 | 8.3474 | 8.1934 | 8.077 | 6.7781 | 6.5128 | 5.9811 | 10.5439 | 10.4745 | 10.4092 | 10.3296 | 10.2408 | 10.1755 | 10.0724 | 9.949 | 9.8184 | 9.7204 | 8.7163 | 8.1602 | 6.8531 | 9.2755 | 9.1888 | 9.1031 | 8.999 | 8.8806 | 8.8031 | 8.6786 | 8.5306 | 8.3765 | 8.2735 | 7.0776 | 6.9388 | 6.4816
MINETY GSP | STRATTON (2 X 90) | PLESSEY | MINIMUM HEADROOM | SU 16381 86720 | YES | 2.643 | 6.3172 | 6.0468 | 5.7448 | 5.3836 | 4.9234 | 4.0621 | 3.1866 | 2.2121 | 1.1611 | 0.31622 | -2.3001 | -3.6562 | -4.0654 | 8.9019 | 8.6519 | 8.3815 | 8.055 | 7.6764 | 7.1958 | 6.4489 | 5.553 | 4.6683 | 4.0172 | 1.4183 | -2.196 | -10.4297 | 5.9264 | 5.6968 | 5.4458 | 5.105 | 4.6785 | 3.9264 | 3.0642 | 2.3234 | 1.3172 | 0.55194 | -1.9358 | -3.3419 | -3.6756
|  | PLESSEY | EE |  |  |  | 6.3172 | 6.0468 | 5.7448 | 5.3836 | 4.9764 | 4.1999 | 3.306 | 2.2121 | 1.1611 | 0.31622 | -2.3001 | -3.5256 | -3.4491 | 8.9019 | 8.6519 | 8.3815 | 8.055 | 7.6764 | 7.1958 | 6.4489 | 5.553 | 4.6683 | 4.0172 | 1.4183 | -1.244 | -4.9787 | 5.9264 | 5.6968 | 5.4458 | 5.105 | 4.7203 | 4.2377 | 3.3591 | 2.3234 | 1.3172 | 0.55194 | -1.9358 | -3.2583 | -3.2062
|  | PLESSEY | HT |  |  |  | 6.4754 | 6.2703 | 6.0397 | 5.7662 | 4.9234 | 4.0621 | 3.1866 | 2.3764 | 1.5091 | 0.83255 | -2.0185 | -3.6562 | -4.0654 | 9.0621 | 8.9081 | 8.754 | 8.5581 | 7.9285 | 7.2713 | 6.6081 | 6.1417 | 5.5591 | 5.104 | 3.2009 | 2.2642 | 1.8938 | 6.0285 | 5.8479 | 5.655 | 5.4315 | 4.6785 | 3.9264 | 3.0642 | 2.404 | 1.6315 | 1.0346 | -1.7236 | -3.3419 | -3.6756
|  | PLESSEY | HE |  |  |  | 6.4723 | 6.2693 | 6.0397 | 5.7611 | 5.4489 | 4.6132 | 3.806 | 2.7999 | 1.9295 | 1.0193 | -2.0817 | -3.2246 | -3.6879 | 9.0336 | 8.853 | 8.6591 | 8.4244 | 8.1877 | 7.506 | 6.8458 | 6.0428 | 5.5336 | 4.8479 | 2.0723 | -0.52663 | -4.3807 | 6.0387 | 5.8683 | 5.6907 | 5.4815 | 5.2764 | 4.5621 | 3.7989 | 2.8836 | 2.0917 | 1.2183 | -1.746 | -2.8134 | -3.2389
|  | PLESSEY | CF |  |  |  | 6.6315 | 6.5326 | 6.404 | 6.2693 | 6.1009 | 5.9162 | 5.4723 | 4.8887 | 4.1979 | 3.5417 | 0.555 | -1.6766 | -3.4685 | 9.0989 | 8.9703 | 8.803 | 8.6499 | 8.4377 | 8.2142 | 7.7305 | 7.1336 | 6.454 | 5.7979 | 2.5142 | -2.196 | -10.4297 | 6.1509 | 6.0856 | 5.9866 | 5.9009 | 5.7866 | 5.6917 | 5.304 | 4.805 | 4.2305 | 3.6101 | 0.73255 | -1.3736 | -3.043
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | PLESSEY TITCHFIELD | MINIMUM HEADROOM | SU 53390 06922 | YES | 4.028 | 18.1764 | 17.8887 | 17.5734 | 17.204 | 16.7907 | 16.5224 | 15.8519 | 15.0999 | 14.3724 | 13.7611 | 11.0499 | 9.0703 | 8.0009 | 19.2193 | 19.005 | 18.7795 | 18.5091 | 18.2111 | 18.156 | 17.6958 | 17.1989 | 16.6968 | 16.2999 | 14.0326 | 10.5795 | 3.2234 | 18.5285 | 18.2887 | 18.0244 | 17.7081 | 17.354 | 17.1132 | 16.5713 | 15.9489 | 15.353 | 14.8611 | 12.653 | 11.203 | 10.2519
|  | PLESSEY TITCHFIELD | EE |  |  |  | 18.1764 | 17.8887 | 17.5734 | 17.204 | 16.7907 | 16.5224 | 15.8519 | 15.0999 | 14.3724 | 13.7611 | 11.2009 | 9.5591 | 8.4213 | 19.2193 | 19.005 | 18.7795 | 18.5091 | 18.2111 | 18.156 | 17.6958 | 17.1989 | 16.6968 | 16.2999 | 14.0326 | 11.4866 | 7.6744 | 18.5285 | 18.2887 | 18.0244 | 17.7081 | 17.354 | 17.1132 | 16.5713 | 15.9489 | 15.353 | 14.8611 | 12.9938 | 11.6489 | 10.6519
|  | PLESSEY TITCHFIELD | HT |  |  |  | 18.3468 | 18.1193 | 17.8713 | 17.5815 | 17.2785 | 16.8172 | 16.2121 | 15.6938 | 15.0315 | 14.3693 | 11.0499 | 9.0703 | 8.0009 | 19.3468 | 19.205 | 19.0703 | 18.8999 | 18.7468 | 18.454 | 18.0928 | 17.9417 | 17.5917 | 17.2489 | 15.5917 | 14.5938 | 14.0458 | 18.6938 | 18.5111 | 18.3142 | 18.0754 | 17.8254 | 17.4234 | 16.9601 | 16.5581 | 16.0387 | 15.5193 | 12.9775 | 11.203 | 10.2519
|  | PLESSEY TITCHFIELD | HE |  |  |  | 18.3377 | 18.1111 | 17.8621 | 17.5703 | 17.2581 | 16.8866 | 16.2938 | 15.7724 | 15.103 | 14.4172 | 11.1468 | 9.3326 | 8.4346 | 19.3091 | 19.1417 | 18.9642 | 18.755 | 18.553 | 18.2979 | 17.8866 | 17.6795 | 17.2581 | 16.8224 | 14.3101 | 11.6601 | 7.9989 | 18.6764 | 18.4928 | 18.2866 | 18.0377 | 17.7734 | 17.4519 | 16.9621 | 16.5244 | 15.9632 | 15.3826 | 12.653 | 11.2611 | 10.4785
|  | PLESSEY TITCHFIELD | CF |  |  |  | 18.503 | 18.3887 | 18.2662 | 18.1111 | 17.9479 | 17.755 | 17.5305 | 17.1887 | 16.9642 | 16.606 | 14.1999 | 11.7785 | 9.8326 | 19.3672 | 19.2346 | 19.0999 | 18.9305 | 18.7672 | 18.5479 | 18.2846 | 17.9275 | 17.7785 | 17.4213 | 14.8387 | 10.5795 | 3.2234 | 18.8152 | 18.7172 | 18.6101 | 18.4764 | 18.3356 | 18.1652 | 17.9683 | 17.6621 | 17.4489 | 17.1203 | 15.0601 | 13.1428 | 11.7009
MANNINGTON GSP | POOLE PS (HAMWORTHY) | POOLE | MINIMUM HEADROOM | SZ 01091 90595 | YES | 2.274 | 11.0207 | 10.739 | 10.3503 | 9.9666 | 9.6084 | 8.7972 | 8.2196 | 7.6431 | 6.9176 | 6.737 | 5.6227 | 4.0033 | 3.0135 | 12.6288 | 12.4482 | 12.2554 | 12.0543 | 11.6727 | 11.1258 | 10.6431 | 10.0747 | 9.487 | 9.2033 | 7.336 | 2.5288 | -7.1181 | 12.5992 | 12.3441 | 11.9839 | 11.6319 | 11.1849 | 10.4186 | 9.9778 | 9.4176 | 8.7217 | 8.5421 | 7.6472 | 6.2298 | 5.286
|  | POOLE | EE |  |  |  | 11.0207 | 10.7543 | 10.4278 | 10.1013 | 9.789 | 9.1462 | 8.4911 | 7.69 | 6.9176 | 6.737 | 5.6227 | 4.386 | 3.0982 | 12.6288 | 12.4482 | 12.2574 | 12.0645 | 11.6727 | 11.1258 | 10.6431 | 10.0747 | 9.487 | 9.2033 | 7.336 | 4.3156 | -0.87934 | 12.5992 | 12.3452 | 12.039 | 11.7298 | 11.39 | 10.6666 | 10.1421 | 9.4176 | 8.7217 | 8.5421 | 7.6472 | 6.5074 | 5.3166
|  | POOLE | HT |  |  |  | 11.0543 | 10.739 | 10.3503 | 9.9666 | 9.6084 | 8.7972 | 8.2196 | 7.6431 | 7.3819 | 7.2543 | 5.7696 | 4.0033 | 3.0135 | 12.6635 | 12.4676 | 12.2554 | 12.0543 | 11.8676 | 11.439 | 11.1207 | 10.7819 | 10.588 | 10.4615 | 9.6094 | 8.7666 | 8.2819 | 12.64 | 12.3441 | 11.9839 | 11.6319 | 11.1849 | 10.4186 | 9.9778 | 9.538 | 9.2972 | 9.138 | 7.79 | 6.2298 | 5.286
|  | POOLE | HE |  |  |  | 11.0503 | 10.7972 | 10.489 | 10.1911 | 9.8962 | 9.4615 | 8.9319 | 8.1931 | 7.587 | 7.4829 | 6.8247 | 5.6564 | 5.0911 | 12.6543 | 12.487 | 12.3105 | 12.1441 | 11.8962 | 11.4074 | 11.0186 | 10.5054 | 10.0288 | 9.7737 | 7.9696 | 5.1411 | 0.3227 | 12.6349 | 12.3962 | 12.1115 | 11.837 | 11.5645 | 10.9237 | 10.5145 | 9.9513 | 9.4952 | 9.3829 | 8.6482 | 7.6013 | 7.1227
|  | POOLE | CF |  |  |  | 11.1533 | 10.8992 | 10.7319 | 10.5819 | 10.486 | 10.3788 | 10.3054 | 10.1472 | 9.9237 | 9.6798 | 8.0523 | 7.2237 | 6.2747 | 12.7452 | 12.5329 | 12.4278 | 12.3309 | 12.2594 | 12.086 | 11.8074 | 11.4298 | 10.9809 | 10.4758 | 7.4523 | 2.5288 | -7.1181 | 12.7339 | 12.489 | 12.3319 | 12.19 | 12.1023 | 12.0013 | 11.9258 | 11.7737 | 11.5666 | 11.3329 | 9.8237 | 9.0472 | 8.24
LOVEDEAN GSP | WYMERING BSP | PORTCHESTER | MINIMUM HEADROOM | SU 62043 05575 | YES | 3.576 | 12.2931 | 11.4778 | 11.0033 | 10.2238 | 9.4003 | 8.4921 | 7.2595 | 5.8595 | 4.338 | 3.3544 | -1.1691 | -4.7671 | -6.6844 | 13.2533 | 12.6635 | 12.4156 | 11.8431 | 11.2156 | 10.536 | 9.6727 | 8.6717 | 7.5952 | 6.938 | 3.1605 | -4.0293 | -18.9426 | 11.9319 | 11.1768 | 10.8023 | 10.0921 | 9.3289 | 8.4921 | 7.3615 | 6.0727 | 4.686 | 3.8105 | -0.019106 | -3.0701 | -4.714
|  | PORTCHESTER | EE |  |  |  | 12.2931 | 11.4778 | 11.0033 | 10.2238 | 9.4003 | 8.4921 | 7.2595 | 5.8595 | 4.338 | 3.3544 | -0.71196 | -4.0609 | -6.2926 | 13.2533 | 12.6635 | 12.4156 | 11.8431 | 11.2156 | 10.536 | 9.6727 | 8.6717 | 7.5952 | 6.938 | 3.1605 | -1.6497 | -9.3385 | 11.9319 | 11.1768 | 10.8023 | 10.0921 | 9.3289 | 8.4921 | 7.3615 | 6.0727 | 4.686 | 3.8105 | 0.27885 | -2.4538 | -4.3854
|  | PORTCHESTER | HT |  |  |  | 12.5646 | 11.8686 | 11.1615 | 10.3676 | 9.8717 | 9.0319 | 7.8564 | 6.6217 | 5.3584 | 4.3238 | -1.1691 | -4.7671 | -6.6844 | 13.5901 | 13.1778 | 12.7697 | 12.2962 | 12.1942 | 11.735 | 11.136 | 10.4697 | 9.7727 | 9.1533 | 6.2901 | 4.7554 | 3.9064 | 12.2238 | 11.6003 | 10.9697 | 10.2554 | 9.8962 | 9.1452 | 8.1166 | 7.0115 | 5.8727 | 4.8891 | -0.019106 | -3.0701 | -4.714
|  | PORTCHESTER | HE |  |  |  | 12.5799 | 11.9166 | 11.2401 | 10.5299 | 10.1748 | 9.4472 | 8.5278 | 7.485 | 6.2972 | 5.2309 | 0.63089 | -2.7385 | -4.2803 | 13.5258 | 13.0646 | 12.5962 | 12.0758 | 11.8921 | 11.3554 | 10.7013 | 9.9493 | 9.0911 | 8.2656 | 3.7809 | -1.1456 | -8.5558 | 12.2289 | 11.637 | 11.036 | 10.3952 | 10.1309 | 9.4686 | 8.6421 | 7.688 | 6.6135 | 5.6278 | 1.437 | -1.2936 | -2.612
|  | PORTCHESTER | CF |  |  |  | 12.7452 | 12.2778 | 11.786 | 11.3472 | 10.9666 | 10.9697 | 10.6727 | 10.2513 | 9.7646 | 9.1299 | 5.1227 | 1.7748 | -1.3936 | 13.584 | 13.2156 | 12.8146 | 12.4064 | 11.9942 | 11.8809 | 11.4074 | 10.8186 | 10.1809 | 9.4309 | 4.1891 | -4.0293 | -18.9426 | 12.3676 | 11.9676 | 11.536 | 11.1238 | 10.7391 | 10.7952 | 10.5074 | 10.1146 | 9.6615 | 9.0748 | 5.4248 | 2.4115 | -0.25482
CHICKERELL GSP | CHICKERELL BSP | PORTLAND | MINIMUM HEADROOM | SY 68307 73941 | YES | 2.687 | 6.7067 | 6.3159 | 5.8312 | 5.3424 | 4.8088 | 4.5343 | 3.7731 | 2.9118 | 2.0547 | 1.3955 | -2.9984 | -6.5167 | -8.5147 | 9.6924 | 9.4424 | 9.0884 | 8.7751 | 8.3527 | 8.1496 | 7.6047 | 6.9751 | 6.3343 | 5.8435 | 2.6618 | -0.60143 | -9.0443 | 7.1261 | 6.9476 | 6.4659 | 5.9782 | 5.4363 | 5.1996 | 4.4894 | 3.6802 | 2.872 | 2.2588 | -1.5994 | -4.5565 | -6.2759
|  | PORTLAND | EE |  |  |  | 6.7067 | 6.3159 | 5.8312 | 5.3424 | 4.8088 | 4.5343 | 3.7731 | 2.9118 | 2.0547 | 1.3955 | -2.9984 | -6.0586 | -8.2933 | 9.6924 | 9.4424 | 9.0884 | 8.7751 | 8.3527 | 8.1496 | 7.6047 | 6.9751 | 6.3343 | 5.8435 | 2.6618 | -0.4351 | -5.0443 | 7.1261 | 6.9476 | 6.4659 | 5.9782 | 5.4363 | 5.1996 | 4.4894 | 3.6802 | 2.872 | 2.2588 | -1.5994 | -4.131 | -6.081
|  | PORTLAND | HT |  |  |  | 6.869 | 6.5465 | 6.1373 | 5.7476 | 5.37 | 4.869 | 4.1843 | 3.7363 | 3.019 | 2.2792 | -2.9473 | -6.5167 | -8.5147 | 9.822 | 9.6567 | 9.3914 | 9.1853 | 8.9833 | 8.7169 | 8.3782 | 8.1822 | 7.7537 | 7.3016 | 4.5547 | 2.9129 | 2.1057 | 7.2067 | 7.072 | 6.8088 | 6.4516 | 6.0873 | 5.6067 | 4.9608 | 4.572 | 3.8884 | 3.1771 | -1.5014 | -4.5565 | -6.2759
|  | PORTLAND | HE |  |  |  | 6.8578 | 6.5476 | 6.1476 | 5.7751 | 5.4169 | 4.9435 | 4.3465 | 3.6802 | 3.3649 | 2.7282 | -1.6586 | -4.529 | -5.7984 | 9.7853 | 9.5884 | 9.2843 | 9.0404 | 8.7935 | 8.4731 | 8.0935 | 7.6271 | 7.4129 | 6.9088 | 3.571 | 0.41796 | -3.7576 | 7.2037 | 7.072 | 6.819 | 6.4802 | 6.1465 | 5.6986 | 5.1343 | 4.4996 | 4.2373 | 3.6261 | -0.25143 | -2.7137 | -3.7678
|  | PORTLAND | CF |  |  |  | 6.9833 | 6.8088 | 6.5363 | 6.3067 | 6.0608 | 5.7924 | 5.5761 | 5.3006 | 5.0129 | 5.0231 | 2.1312 | -0.57388 | -3.08 | 9.8404 | 9.6955 | 9.4414 | 9.2516 | 9.0292 | 8.7741 | 8.5016 | 8.1802 | 7.8067 | 7.6384 | 4.3537 | -0.60143 | -9.0443 | 7.2649 | 7.1884 | 7.0067 | 6.9057 | 6.7394 | 6.4884 | 6.2639 | 5.9792 | 5.6731 | 5.6914 | 3.0618 | 0.62918 | -1.5157
LOVEDEAN GSP | PORTSMOUTH BSP | PORTSMOUTH | MINIMUM HEADROOM | SZ 63405 99685 | YES | 1.515 | 37.65 | 37.402 | 37.0949 | 36.7582 | 36.3622 | 35.9204 | 35.352 | 34.6561 | 33.9735 | 33.4061 | 31.5276 | 30.3571 | 30.4235 | 39.1235 | 38.8755 | 38.5643 | 38.2316 | 37.8276 | 37.3755 | 36.8704 | 36.2531 | 35.6224 | 35.0806 | 32.2643 | 26.6714 | 14.7214 | 36.7092 | 36.4724 | 36.1735 | 35.85 | 35.4673 | 35.0378 | 34.501 | 33.8408 | 33.1908 | 32.6531 | 30.9122 | 29.9296 | 30
|  | PORTSMOUTH | EE |  |  |  | 37.65 | 37.402 | 37.0949 | 36.7582 | 36.3622 | 35.9204 | 35.352 | 34.6561 | 33.9735 | 33.4061 | 31.5276 | 30.8673 | 31.0163 | 39.1235 | 38.8755 | 38.5643 | 38.2316 | 37.8276 | 37.3755 | 36.8704 | 36.2531 | 35.6224 | 35.0806 | 32.2643 | 28.9888 | 23.4286 | 36.7092 | 36.4724 | 36.1735 | 35.85 | 35.4673 | 35.0378 | 34.501 | 33.8408 | 33.1908 | 32.6531 | 30.9122 | 30.3459 | 30.4663
|  | PORTSMOUTH | HT |  |  |  | 37.7949 | 37.65 | 37.448 | 37.2184 | 36.9449 | 36.652 | 36.2092 | 35.7082 | 35.1704 | 34.6276 | 31.8724 | 30.3571 | 30.4235 | 39.3194 | 39.1816 | 39.0306 | 38.8561 | 38.6418 | 38.4163 | 38.1306 | 37.7929 | 37.4224 | 37.0602 | 35.2112 | 34.1684 | 34.0663 | 36.8867 | 36.7194 | 36.5316 | 36.3184 | 36.0582 | 35.7796 | 35.3704 | 34.901 | 34.3969 | 33.8929 | 31.3306 | 29.9296 | 30
|  | PORTSMOUTH | HE |  |  |  | 37.7806 | 37.649 | 37.4735 | 37.2714 | 37.0357 | 36.7867 | 36.4163 | 35.9878 | 35.5408 | 35.1071 | 33.3449 | 32.7224 | 32.652 | 39.2531 | 39.0776 | 38.8755 | 38.652 | 38.3827 | 38.0959 | 37.7388 | 37.3316 | 36.8837 | 36.4347 | 33.5469 | 30.2153 | 24.5398 | 36.8663 | 36.7163 | 36.548 | 36.3561 | 36.1337 | 35.8939 | 35.549 | 35.1469 | 34.7286 | 34.3204 | 32.6714 | 32.0378 | 31.6071
|  | PORTSMOUTH | CF |  |  |  | 37.85 | 37.7949 | 37.7112 | 37.5827 | 37.448 | 37.2847 | 37.1224 | 36.9245 | 36.6929 | 36.4541 | 35.0459 | 33.5367 | 32.2337 | 39.3133 | 39.1571 | 38.9765 | 38.7684 | 38.5327 | 38.2286 | 37.8857 | 37.499 | 37.0622 | 36.5857 | 33.101 | 26.6714 | 14.7214 | 36.9684 | 36.8806 | 36.7735 | 36.6469 | 36.5143 | 36.3571 | 36.202 | 36.0173 | 35.7908 | 35.5643 | 34.2316 | 32.8439 | 31.6806
MELKSHAM GSP | ANDOVER BSP | PORTWAY | MINIMUM HEADROOM | SU 34402 46001 | YES | 2.685 | 13.7191 | 13.0457 | 12.2304 | 11.2773 | 10.1926 | 9.0018 | 7.8008 | 6.2304 | 4.7365 | 3.4957 | -3.6921 | -6.9043 | -7.5309 | 15.3406 | 14.8875 | 14.3242 | 13.6814 | 12.9436 | 12.0855 | 11.2008 | 10.0232 | 8.9089 | 7.9906 | 2.663 | 0.3518 | -0.13698 | 13.5742 | 12.9273 | 12.1416 | 11.2232 | 10.1783 | 9.0304 | 7.8834 | 6.3702 | 4.9385 | 3.7477 | -3.1768 | -6.2462 | -6.8309
|  | PORTWAY | EE |  |  |  | 13.7191 | 13.0457 | 12.2304 | 11.2773 | 10.1926 | 9.0018 | 7.8008 | 6.2304 | 4.7365 | 3.4957 | -0.45942 | -1.338 | -1.7411 | 15.3406 | 14.8875 | 14.3242 | 13.6814 | 12.9436 | 12.0855 | 11.2008 | 10.0232 | 8.9089 | 7.9906 | 5.1742 | 4.6559 | 4.4038 | 13.5742 | 12.9273 | 12.1416 | 11.2232 | 10.1783 | 9.0304 | 7.8834 | 6.3702 | 4.9385 | 3.7477 | -0.020649 | -0.81963 | -1.1778
|  | PORTWAY | HT |  |  |  | 14.412 | 14.01 | 13.511 | 12.9365 | 12.2579 | 11.4753 | 10.5794 | 9.4804 | 8.314 | 7.2406 | 2.0008 | -0.32269 | -0.96963 | 15.8151 | 15.5447 | 15.2059 | 14.8181 | 14.3579 | 13.8304 | 13.2253 | 12.4804 | 11.6855 | 10.9794 | 7.2294 | 5.6385 | 5.2559 | 14.2487 | 13.8579 | 13.3783 | 12.8273 | 12.1753 | 11.4222 | 10.562 | 9.5069 | 8.3845 | 7.3569 | 2.3355 | 0.13956 | -0.45126
|  | PORTWAY | HE |  |  |  | 14.1773 | 13.6151 | 12.9202 | 12.1079 | 11.1467 | 10.0253 | 8.7773 | 7.2222 | 5.563 | 3.96 | -3.6921 | -6.9043 | -7.5309 | 15.661 | 15.2855 | 14.814 | 14.2722 | 13.6242 | 12.8773 | 11.9528 | 10.7885 | 9.5406 | 8.3426 | 2.663 | 0.3518 | -0.13698 | 14.0171 | 13.4783 | 12.8079 | 12.0263 | 11.0987 | 10.0222 | 8.8212 | 7.3242 | 5.7253 | 4.1845 | -3.1768 | -6.2462 | -6.8309
|  | PORTWAY | CF |  |  |  | 14.614 | 14.3161 | 13.9426 | 13.5028 | 12.9824 | 12.3824 | 11.7773 | 10.9794 | 10.0732 | 9.1151 | 3.6589 | -0.98289 | -3.4053 | 15.8957 | 15.7487 | 15.4998 | 15.2038 | 14.8457 | 14.4385 | 14.0263 | 13.4896 | 12.8722 | 12.1457 | 8.0447 | 4.5804 | 2.7345 | 14.4426 | 14.1528 | 13.7916 | 13.3702 | 12.8671 | 12.2936 | 11.7089 | 10.9385 | 10.0661 | 9.1365 | 3.8773 | -0.57881 | -2.8798
IVER 132KV | LONGFORD | POYLE | MINIMUM HEADROOM | TQ 03425 75555 | YES | 6.967 | 5.6149 | 5.0945 | 4.4424 | 3.5649 | 2.5088 | 1.3537 | 0.18939 | -1.3698 | -2.8555 | -4.2657 | -9.7086 | -12.3749 | -13.431 | 8.0751 | 7.6792 | 7.1802 | 6.5822 | 5.7771 | 4.8904 | 4.0241 | 2.8537 | 1.7333 | 0.69551 | -3.3647 | -5.3229 | -7.0004 | 5.5445 | 5.0455 | 4.4169 | 3.62 | 2.6078 | 1.4945 | 0.38224 | -1.1106 | -2.5382 | -3.8759 | -9.0994 | -11.6433 | -12.5637
|  | POYLE | EE |  |  |  | 5.6149 | 5.0945 | 4.4424 | 3.5649 | 2.5088 | 1.3537 | 0.18939 | -1.3698 | -2.8555 | -4.2657 | -8.8269 | -9.9841 | -10.4718 | 8.0751 | 7.6792 | 7.1802 | 6.5822 | 5.7771 | 4.8904 | 4.0241 | 2.8537 | 1.7333 | 0.69551 | -2.6331 | -3.3718 | -3.6524 | 5.5445 | 5.0455 | 4.4169 | 3.62 | 2.6078 | 1.4945 | 0.38224 | -1.1106 | -2.5382 | -3.8759 | -8.2178 | -9.2494 | -9.6086
|  | POYLE | HT |  |  |  | 6.0618 | 5.719 | 5.2894 | 4.7986 | 4.1333 | 3.3527 | 2.4159 | 1.2537 | 0.014898 | -1.2392 | -7.0178 | -9.6769 | -10.7453 | 8.3863 | 8.1741 | 7.8578 | 7.4935 | 7.0353 | 6.4873 | 5.8108 | 4.9598 | 4.0435 | 3.1435 | -1.0433 | -2.7494 | -3.3361 | 5.9782 | 5.6486 | 5.2363 | 4.7629 | 4.1741 | 3.422 | 2.5261 | 1.4129 | 0.2251 | -0.96163 | -6.4576 | -8.8892 | -9.879
|  | POYLE | HE |  |  |  | 5.9792 | 5.5761 | 5.0771 | 4.4955 | 3.6741 | 2.7455 | 1.6445 | 0.2598 | -1.2218 | -2.7576 | -9.7086 | -12.3749 | -13.431 | 8.3373 | 8.0537 | 7.6761 | 7.2312 | 6.6822 | 5.9771 | 5.1537 | 4.1149 | 2.9955 | 1.8567 | -3.3647 | -5.3229 | -6.1494 | 5.8965 | 5.5118 | 5.0312 | 4.4731 | 3.7322 | 2.8394 | 1.7822 | 0.45571 | -0.9698 | -2.428 | -9.0994 | -11.6433 | -12.5637
|  | POYLE | CF |  |  |  | 6.3149 | 6.1047 | 5.8384 | 5.5333 | 5.1557 | 4.719 | 4.2435 | 3.5312 | 2.7129 | 1.7067 | -3.5208 | -8.2627 | -11.3473 | 8.4986 | 8.3822 | 8.2343 | 8.0037 | 7.7067 | 7.3659 | 7.0027 | 6.521 | 5.8863 | 5.1231 | 1.1251 | -2.4984 | -7.0004 | 6.22 | 6.0159 | 5.7618 | 5.468 | 5.1047 | 4.6853 | 4.2312 | 3.5884 | 2.7976 | 1.8394 | -3.1882 | -7.7331 | -10.6698
MINETY GSP | STRATTON (2 X 90) | PRESSED STEEL SWINDON | MINIMUM HEADROOM | SU 16963 86368 | YES | 3.98 | 35.6662 | 35.3489 | 67.2882 | 66.8769 | 66.4147 | 65.9677 | 64.9994 | 63.7361 | 62.478 | 61.5228 | 58.2565 | 56.7922 | 56.531 | 34.0673 | 33.8316 | 63.0586 | 62.6912 | 62.2749 | 61.98 | 61.2596 | 60.3157 | 59.3443 | 58.5718 | 55.8351 | 52.1239 | 44.5412 | 34.0363 | 33.718 | 64.1463 | 63.731 | 63.2657 | 62.8892 | 61.9769 | 60.7963 | 59.6096 | 58.7402 | 55.6708 | 54.2892 | 54.0514
|  | PRESSED STEEL SWINDON | EE |  |  |  | 35.6662 | 35.3489 | 67.2882 | 66.8769 | 66.4147 | 65.9677 | 64.9994 | 63.7361 | 62.478 | 61.5228 | 58.6188 | 57.3524 | 57.4116 | 34.0673 | 33.8316 | 63.0586 | 62.6912 | 62.2749 | 61.98 | 61.2596 | 60.3157 | 59.3443 | 58.5718 | 55.8351 | 53.4739 | 50.1228 | 34.0363 | 33.718 | 64.1463 | 63.731 | 63.2657 | 62.8892 | 61.9769 | 60.7963 | 59.6096 | 58.7402 | 56.1912 | 55.0882 | 55.1555
|  | PRESSED STEEL SWINDON | HT |  |  |  | 35.8468 | 35.6111 | 67.6392 | 67.3392 | 66.8106 | 65.9973 | 65.0249 | 64.178 | 63.1137 | 62.2371 | 59.0239 | 57.4228 | 57.0851 | 34.2255 | 34.0786 | 63.4086 | 63.2239 | 62.778 | 62.1463 | 61.4616 | 60.731 | 59.9331 | 59.3443 | 57.1922 | 56.2851 | 56.0769 | 34.2384 | 34.0006 | 64.5239 | 64.229 | 63.6922 | 62.9086 | 61.9933 | 61.2718 | 60.278 | 59.48 | 56.5882 | 55.1575 | 54.8882
|  | PRESSED STEEL SWINDON | HE |  |  |  | 35.8397 | 35.6121 | 67.6422 | 67.3402 | 67.0433 | 66.3382 | 65.4524 | 64.5535 | 63.3596 | 62.232 | 58.2565 | 56.7922 | 56.531 | 34.1806 | 33.998 | 63.281 | 63.0422 | 62.7922 | 62.1922 | 61.5075 | 60.8065 | 59.8371 | 58.9341 | 55.8963 | 53.3882 | 49.9024 | 34.2231 | 33.9975 | 64.5198 | 64.2228 | 63.9392 | 63.2524 | 62.4208 | 61.6637 | 60.528 | 59.4535 | 55.6708 | 54.2892 | 54.0514
|  | PRESSED STEEL SWINDON | CF |  |  |  | 35.9785 | 35.8591 | 68.0106 | 67.8463 | 67.6626 | 67.3851 | 66.931 | 66.2331 | 65.4402 | 65.0259 | 61.5208 | 59.0351 | 57.2371 | 34.2571 | 34.1265 | 63.4657 | 63.2902 | 63.0861 | 62.8086 | 62.3514 | 61.7014 | 60.9545 | 60.4371 | 56.6433 | 52.1239 | 44.5412 | 34.3557 | 34.2251 | 64.8545 | 64.6871 | 64.4933 | 64.2453 | 63.8065 | 63.1504 | 62.4035 | 62.079 | 58.7728 | 56.4075 | 54.7239
BRAMLEY (FLEE) | FERNHURST | PRESTON CANDOVER | MINIMUM HEADROOM | SU 60879 41131 | YES | 1.685 | 9.7026 | 9.3903 | 8.9474 | 8.6087 | 8.3607 | 8.1046 | 7.9403 | 7.6893 | 7.4393 | 7.2954 | 4.4148 | 4.177 | 3.9607 | 11.7643 | 11.6 | 11.3327 | 11.1612 | 11.0061 | 10.8388 | 10.7112 | 10.5092 | 10.3122 | 10.2133 | 7.8347 | 7.2367 | 5.8827 | 10.7827 | 10.5235 | 10.1286 | 9.8469 | 9.6133 | 9.3684 | 9.2 | 8.9612 | 8.7214 | 8.5888 | 6.0673 | 5.8582 | 5.6735
|  | PRESTON CANDOVER | EE |  |  |  | 9.7026 | 9.3903 | 8.9474 | 8.6087 | 8.3607 | 8.1046 | 7.9403 | 7.6893 | 7.4393 | 7.2954 | 4.4148 | 4.177 | 4.0638 | 11.7643 | 11.6 | 11.3327 | 11.1612 | 11.0061 | 10.8388 | 10.7112 | 10.5092 | 10.3122 | 10.2133 | 7.8347 | 7.4184 | 6.7673 | 10.7827 | 10.5235 | 10.1286 | 9.8469 | 9.6133 | 9.3684 | 9.2 | 8.9612 | 8.7214 | 8.5888 | 6.0673 | 5.8582 | 5.7633
|  | PRESTON CANDOVER | HT |  |  |  | 9.7658 | 9.4026 | 9.0536 | 8.7179 | 8.5036 | 8.2872 | 8.126 | 7.9423 | 7.7923 | 7.3454 | 4.5638 | 4.2036 | 3.9607 | 11.8286 | 11.6031 | 11.4316 | 11.2694 | 11.1673 | 11.0592 | 10.9694 | 10.8612 | 10.7622 | 10.4112 | 8.1929 | 8.0061 | 7.8837 | 10.8582 | 10.5459 | 10.2643 | 9.9857 | 9.7918 | 9.6092 | 9.448 | 9.2612 | 9.1143 | 8.7 | 6.1908 | 5.8735 | 5.6735
|  | PRESTON CANDOVER | HE |  |  |  | 9.7628 | 9.4577 | 9.0526 | 8.725 | 8.5087 | 8.3128 | 8.1515 | 7.973 | 7.826 | 7.6413 | 4.4985 | 4.2648 | 4.1658 | 11.8235 | 11.6612 | 11.4082 | 11.2388 | 11.1224 | 11.0224 | 10.9214 | 10.7959 | 10.6969 | 10.55 | 7.8857 | 7.4602 | 6.8173 | 10.8571 | 10.6133 | 10.2643 | 9.9908 | 9.798 | 9.6337 | 9.4765 | 9.2939 | 9.15 | 8.9653 | 6.1378 | 5.9265 | 5.8439
|  | PRESTON CANDOVER | CF |  |  |  | 9.9209 | 9.8352 | 9.6413 | 9.3209 | 9.0148 | 8.6842 | 8.4811 | 8.3352 | 8.2077 | 8.0699 | 7.3832 | 4.7005 | 4.2903 | 11.902 | 11.8418 | 11.7306 | 11.5194 | 11.3541 | 11.1724 | 11.0582 | 10.9459 | 10.8408 | 10.7286 | 10.0194 | 7.2367 | 5.8827 | 10.9837 | 10.9041 | 10.7398 | 10.4612 | 10.2133 | 9.9398 | 9.7796 | 9.6357 | 9.5092 | 9.3704 | 8.6857 | 6.3245 | 5.9571
CHICKERELL GSP | CHICKERELL BSP | PUDDLETOWN | MINIMUM HEADROOM | SY 74226 95039 | YES | 0.319 | 5.6869 | 5.5941 | 5.5196 | 5.4196 | 5.3441 | 5.2267 | 5.0778 | 4.8951 | 4.7839 | 4.7104 | 4.3063 | 4.0512 | 3.8696 | 5.9923 | 5.923 | 5.8617 | 5.7832 | 5.724 | 5.6301 | 5.5128 | 5.3679 | 5.2821 | 5.2444 | 4.9597 | 4.5158 | 3.5199 | 5.8522 | 5.7614 | 5.6829 | 5.5839 | 5.5073 | 5.3859 | 5.2359 | 5.0512 | 4.938 | 4.8869 | 4.5441 | 4.3257 | 4.1706
|  | PUDDLETOWN | EE |  |  |  | 5.6869 | 5.5941 | 5.5196 | 5.4196 | 5.3441 | 5.2267 | 5.0778 | 4.8951 | 4.7839 | 4.7104 | 4.3063 | 4.0757 | 3.9267 | 5.9923 | 5.923 | 5.8617 | 5.7832 | 5.724 | 5.6301 | 5.5128 | 5.3679 | 5.2821 | 5.2444 | 4.9597 | 4.6291 | 4.1352 | 5.8522 | 5.7614 | 5.6829 | 5.5839 | 5.5073 | 5.3859 | 5.2359 | 5.0512 | 4.938 | 4.8869 | 4.5441 | 4.3522 | 4.2206
|  | PUDDLETOWN | HT |  |  |  | 5.741 | 5.689 | 5.6237 | 5.5696 | 5.489 | 5.4073 | 5.2869 | 5.191 | 5.0533 | 4.9104 | 4.3512 | 4.0512 | 3.8696 | 6.0393 | 6.0005 | 5.9556 | 5.9189 | 5.8597 | 5.8026 | 5.724 | 5.6679 | 5.573 | 5.4709 | 5.1689 | 5.0413 | 4.9536 | 5.9002 | 5.8482 | 5.7839 | 5.7339 | 5.6573 | 5.5818 | 5.4645 | 5.3778 | 5.2451 | 5.1073 | 4.5808 | 4.3257 | 4.1706
|  | PUDDLETOWN | HE |  |  |  | 5.738 | 5.688 | 5.6257 | 5.5747 | 5.4961 | 5.4206 | 5.3094 | 5.2206 | 5.0951 | 4.9614 | 4.4114 | 4.1849 | 4.0747 | 6.0362 | 5.9995 | 5.9546 | 5.9189 | 5.8597 | 5.8036 | 5.724 | 5.6668 | 5.5699 | 5.4689 | 5.027 | 4.6883 | 4.2117 | 5.8992 | 5.8482 | 5.7859 | 5.738 | 5.6645 | 5.592 | 5.4849 | 5.4033 | 5.2808 | 5.1522 | 4.64 | 4.4522 | 4.3604
|  | PUDDLETOWN | CF |  |  |  | 5.7553 | 5.7196 | 5.6716 | 5.6145 | 5.5757 | 5.5135 | 5.4553 | 5.3727 | 5.3267 | 5.2431 | 4.8012 | 4.4737 | 4.2318 | 6.0474 | 6.0199 | 5.9852 | 5.9434 | 5.9158 | 5.8648 | 5.8077 | 5.7342 | 5.6852 | 5.6056 | 5.1321 | 4.5158 | 3.5199 | 5.9165 | 5.8798 | 5.8318 | 5.7757 | 5.74 | 5.6808 | 5.6237 | 5.5441 | 5.5002 | 5.4186 | 4.9767 | 4.6931 | 4.4778
AXMINSTER | YEOVIL BSP | PULHAM | MINIMUM HEADROOM | ST 71579 09451 | YES | 0 | 6.2745 | 6.1551 | 6.0122 | 5.8949 | 5.7408 | 5.6153 | 5.4112 | 5.1673 | 4.9194 | 4.7765 | 4.0398 | 3.8051 | 3.649 | 7.1561 | 7.0622 | 6.948 | 6.8622 | 6.7347 | 6.6378 | 6.4776 | 6.2857 | 6.0949 | 5.999 | 5.5408 | 5.0704 | 3.8714 | 6.5398 | 6.4224 | 6.2786 | 6.1684 | 6.002 | 5.8704 | 5.6561 | 5.4051 | 5.1561 | 5.0245 | 4.3908 | 4.1908 | 4.0531
|  | PULHAM | EE |  |  |  | 6.2745 | 6.1551 | 6.0122 | 5.8949 | 5.7408 | 5.6153 | 5.4112 | 5.1673 | 4.9194 | 4.7765 | 4.0398 | 3.8051 | 3.7367 | 7.1561 | 7.0622 | 6.948 | 6.8622 | 6.7347 | 6.6378 | 6.4776 | 6.2857 | 6.0949 | 5.999 | 5.5408 | 5.1898 | 4.651 | 6.5398 | 6.4224 | 6.2786 | 6.1684 | 6.002 | 5.8704 | 5.6561 | 5.4051 | 5.1561 | 5.0245 | 4.3908 | 4.1908 | 4.1245
|  | PULHAM | HT |  |  |  | 6.3173 | 6.2204 | 6.1235 | 6.0122 | 5.8898 | 5.7857 | 5.6184 | 5.4327 | 5.2776 | 5.0857 | 4.2143 | 3.8704 | 3.649 | 7.2092 | 7.149 | 7.0898 | 7.0163 | 6.9306 | 6.8684 | 6.7561 | 6.6276 | 6.5337 | 6.398 | 5.8418 | 5.6684 | 5.5704 | 6.5898 | 6.499 | 6.4061 | 6.3 | 6.1776 | 6.0827 | 5.9204 | 5.7367 | 5.5847 | 5.3857 | 4.5398 | 4.2367 | 4.0531
|  | PULHAM | HE |  |  |  | 6.3163 | 6.2214 | 6.1265 | 6.0173 | 5.8969 | 5.798 | 5.6337 | 5.451 | 5.302 | 5.1112 | 4.1214 | 3.9082 | 3.8459 | 7.201 | 7.1367 | 7.0714 | 6.9939 | 6.9051 | 6.8347 | 6.7194 | 6.5786 | 6.4755 | 6.3276 | 5.6163 | 5.2694 | 4.7378 | 6.5878 | 6.5 | 6.4082 | 6.3051 | 6.1878 | 6.0959 | 5.9388 | 5.7582 | 5.6112 | 5.4163 | 4.4816 | 4.3 | 4.2459
|  | PULHAM | CF |  |  |  | 6.3357 | 6.2541 | 6.1755 | 6.0837 | 5.9908 | 5.8908 | 5.8102 | 5.6929 | 5.5653 | 5.4337 | 4.7837 | 4.2827 | 3.8929 | 7.2173 | 7.1612 | 7.1082 | 7.0378 | 6.9694 | 6.8888 | 6.8255 | 6.7214 | 6.6051 | 6.4837 | 5.8143 | 5.0704 | 3.8714 | 6.6102 | 6.5357 | 6.4612 | 6.3735 | 6.2847 | 6.1898 | 6.1194 | 6.0031 | 5.8776 | 5.7449 | 5.0663 | 4.6031 | 4.2694
LOVEDEAN GSP | FORT WIDLEY | PURBROOK | MINIMUM HEADROOM | SU 67047 07819 | YES | 0 | 11.3235 | 11.0724 | 10.7908 | 10.4398 | 9.9898 | 9.6704 | 9.1102 | 8.701 | 8.0541 | 7.5714 | 5.4214 | 3.9531 | 3.1898 | 13.4571 | 13.2306 | 12.9796 | 12.6663 | 12.298 | 12.2531 | 11.8439 | 11.3816 | 10.8837 | 10.5347 | 8.6112 | 4.8908 | -2.6398 | 11.7347 | 11.4694 | 11.1837 | 10.8153 | 10.3796 | 10.298 | 9.7929 | 9.2949 | 8.6959 | 8.2867 | 6.5357 | 5.3429 | 4.751
|  | PURBROOK | EE |  |  |  | 11.3235 | 11.0724 | 10.7908 | 10.4398 | 9.9898 | 9.8786 | 9.3143 | 8.701 | 8.0541 | 7.5714 | 5.5745 | 4.2418 | 3.5969 | 13.4571 | 13.2306 | 12.9796 | 12.6663 | 12.298 | 12.2531 | 11.8439 | 11.3816 | 10.8837 | 10.5347 | 8.6112 | 6.2643 | 2.5602 | 11.7347 | 11.4694 | 11.1837 | 10.8153 | 10.3796 | 10.3714 | 9.8663 | 9.2949 | 8.6959 | 8.2867 | 6.6357 | 5.5857 | 5.0643
|  | PURBROOK | HT |  |  |  | 11.4255 | 11.1531 | 10.8561 | 10.498 | 10.1214 | 9.6704 | 9.1102 | 8.8469 | 8.3337 | 7.8082 | 5.4214 | 3.9531 | 3.1898 | 13.5918 | 13.4265 | 13.2622 | 13.0418 | 12.8265 | 12.5469 | 12.2235 | 12.1827 | 11.8806 | 11.5673 | 10.2276 | 9.5663 | 9.1908 | 11.8806 | 11.6286 | 11.3663 | 11.0337 | 10.7112 | 10.298 | 9.7929 | 9.6367 | 9.1653 | 8.6796 | 6.5357 | 5.3429 | 4.751
|  | PURBROOK | HE |  |  |  | 11.4347 | 11.2367 | 11.0071 | 10.7265 | 10.4306 | 10.0551 | 9.5796 | 9.3735 | 8.8857 | 8.3867 | 6.301 | 5.0633 | 4.4429 | 13.5551 | 13.3867 | 13.201 | 12.9724 | 12.7327 | 12.4286 | 12.0663 | 11.9531 | 11.5714 | 11.1724 | 8.9786 | 6.6418 | 2.9612 | 11.8816 | 11.6898 | 11.4776 | 11.2082 | 10.9449 | 10.5918 | 10.1571 | 10.052 | 9.6041 | 9.1418 | 7.2776 | 6.2857 | 5.801
|  | PURBROOK | CF |  |  |  | 11.5929 | 11.5031 | 11.4245 | 11.3122 | 11.1704 | 11.0582 | 10.8867 | 10.6459 | 10.3867 | 10.4429 | 8.0837 | 6.7245 | 5.3429 | 13.6296 | 13.5051 | 13.3765 | 13.2082 | 13.0041 | 12.8031 | 12.5245 | 12.1857 | 11.8235 | 11.75 | 8.898 | 4.8908 | -2.6398 | 12.0133 | 11.9082 | 11.8143 | 11.6796 | 11.5184 | 11.399 | 11.2092 | 10.9653 | 10.698 | 10.8347 | 8.7857 | 7.6173 | 6.4816
BRAMLEY (FLEE) | PYESTOCK BSP | PYESTOCK | MINIMUM HEADROOM | SU 82940 54553 | YES | 8.2 | 13.52 | 13.4873 | 13.4873 | 13.4863 | 13.4863 | 13.4863 | 13.4863 | 13.4863 | 13.4853 | 13.4863 | 13.4863 | 13.4853 | 13.4853 | 11.6398 | 11.6051 | 11.6051 | 11.6051 | 11.6051 | 11.6051 | 11.6051 | 11.6051 | 11.6051 | 11.6051 | 11.6051 | 11.6051 | 11.6051 | 12.8333 | 12.7996 | 12.7996 | 12.7996 | 12.7986 | 12.7986 | 12.7986 | 12.7986 | 12.7986 | 12.7986 | 12.7986 | 12.7986 | 12.7986
|  | PYESTOCK | EE |  |  |  | 13.52 | 13.4873 | 13.4873 | 13.4873 | 13.4863 | 13.4863 | 13.4863 | 13.4863 | 13.4853 | 13.4863 | 13.4863 | 13.4853 | 13.4853 | 11.6398 | 11.6051 | 11.6051 | 11.6051 | 11.6051 | 11.6051 | 11.6051 | 11.6061 | 11.6051 | 11.6051 | 11.6051 | 11.6051 | 11.6051 | 12.8333 | 12.7996 | 12.7996 | 12.7996 | 12.7996 | 12.7986 | 12.7986 | 12.7986 | 12.7986 | 12.7986 | 12.7986 | 12.7986 | 12.7986
|  | PYESTOCK | HT |  |  |  | 13.52 | 13.4873 | 13.4873 | 13.4863 | 13.4863 | 13.4873 | 13.4863 | 13.4863 | 13.4863 | 13.4863 | 13.4863 | 13.4873 | 13.4873 | 11.6398 | 11.6051 | 11.6051 | 11.6061 | 11.6061 | 11.6061 | 11.6051 | 11.6051 | 11.6061 | 11.6061 | 11.6082 | 11.6082 | 11.6082 | 12.8333 | 12.7996 | 12.7996 | 12.7996 | 12.7986 | 12.7986 | 12.7996 | 12.7996 | 12.7986 | 12.7986 | 12.7996 | 12.7996 | 12.7996
|  | PYESTOCK | HE |  |  |  | 13.52 | 13.4873 | 13.4873 | 13.4873 | 13.4873 | 13.4873 | 13.4863 | 13.4863 | 13.4873 | 13.4873 | 13.4873 | 13.4873 | 13.4884 | 11.6398 | 11.6051 | 11.6051 | 11.6051 | 11.6051 | 11.6051 | 11.6051 | 11.6061 | 11.6061 | 11.6061 | 11.6061 | 11.6071 | 11.6082 | 12.8333 | 12.7996 | 12.7996 | 12.7996 | 12.7996 | 12.7996 | 12.7996 | 12.7986 | 12.7986 | 12.7996 | 12.7996 | 12.7996 | 12.7996
|  | PYESTOCK | CF |  |  |  | 13.52 | 13.4873 | 13.4873 | 13.4873 | 13.4873 | 13.4873 | 13.4873 | 13.4873 | 13.4873 | 13.4873 | 13.4873 | 13.4873 | 13.4884 | 11.6398 | 11.6061 | 11.6061 | 11.6061 | 11.6051 | 11.6051 | 11.6051 | 11.6051 | 11.6051 | 11.6051 | 11.6071 | 11.6071 | 11.6082 | 12.8333 | 12.8006 | 12.7996 | 12.7996 | 12.7996 | 12.7996 | 12.7996 | 12.7996 | 12.7996 | 12.7996 | 12.7996 | 12.8006 | 12.7996
MINETY GSP | TOOTHILL BSP | QUARRY ROAD | MINIMUM HEADROOM | SU 15334 83380 | YES | 2.197 | 6.8971 | 6.5287 | 6.0981 | 5.5348 | 4.8807 | 4.3022 | 3.2042 | 1.9542 | 0.72461 | -0.10702 | -2.605 | -4.3744 | -4.7387 | 10.2134 | 9.9358 | 9.6134 | 9.2175 | 8.7685 | 8.242 | 7.4705 | 6.5807 | 5.6787 | 5.0022 | 2.2869 | -2.3468 | -12.0029 | 7.6797 | 7.3093 | 6.896 | 6.3583 | 5.7318 | 5.243 | 4.2277 | 3.0562 | 1.896 | 1.1256 | -1.1213 | -2.6029 | -2.8754
|  | QUARRY ROAD | EE |  |  |  | 6.8971 | 6.5287 | 6.0981 | 5.5348 | 4.8807 | 4.3022 | 3.2042 | 1.9542 | 0.72461 | -0.10702 | -2.605 | -4.0438 | -4.0489 | 10.2134 | 9.9358 | 9.6134 | 9.2175 | 8.7685 | 8.242 | 7.4705 | 6.5807 | 5.6787 | 5.0022 | 2.2869 | -0.70294 | -5.0836 | 7.6797 | 7.3093 | 6.896 | 6.3583 | 5.7318 | 5.243 | 4.2277 | 3.0562 | 1.896 | 1.1256 | -1.1213 | -2.2968 | -2.3203
|  | QUARRY ROAD | HT |  |  |  | 7.1369 | 6.8726 | 6.544 | 6.096 | 5.3858 | 4.4715 | 3.4297 | 2.7726 | 1.8522 | 1.1246 | -2.2091 | -4.3744 | -4.7387 | 10.4175 | 10.2613 | 10.0715 | 9.8164 | 9.2807 | 8.6613 | 8.0185 | 7.593 | 7.0103 | 6.5818 | 4.7338 | 3.5409 | 3.245 | 7.943 | 7.6848 | 7.3746 | 6.9552 | 6.3134 | 5.4715 | 4.5226 | 3.9654 | 3.096 | 2.3981 | -0.72029 | -2.6029 | -2.8754
|  | QUARRY ROAD | HE |  |  |  | 7.1154 | 6.8613 | 6.5624 | 6.1787 | 5.7715 | 4.9501 | 4.0124 | 3.2858 | 2.2818 | 1.446 | -1.4244 | -3.0325 | -3.4815 | 10.3511 | 10.1399 | 9.893 | 9.593 | 9.2777 | 8.6154 | 7.9266 | 7.3562 | 6.5766 | 5.8828 | 2.8215 | -0.35396 | -4.8897 | 7.9195 | 7.6705 | 7.3889 | 7.0215 | 6.6542 | 5.8971 | 5.043 | 4.444 | 3.5175 | 2.7175 | -0.00090204 | -1.3703 | -1.7193
|  | QUARRY ROAD | CF |  |  |  | 7.2715 | 7.1307 | 6.9889 | 6.8052 | 6.594 | 6.4022 | 6.0277 | 5.495 | 4.8389 | 4.5562 | 1.4389 | -1.058 | -3.2876 | 10.4246 | 10.2542 | 10.0736 | 9.8573 | 9.6164 | 9.3511 | 8.8899 | 8.3083 | 7.6328 | 7.1664 | 3.2113 | -2.3468 | -12.0029 | 8.0562 | 7.9052 | 7.7511 | 7.5593 | 7.3409 | 7.1542 | 6.793 | 6.2807 | 5.6613 | 5.4705 | 2.5266 | 0.2991 | -1.5948
BRAMLEY (FLEE) | CAMBERLEY RESERVE | QUEENSMEAD | MINIMUM HEADROOM | SU 87062 55683 | YES | 4.262 | 3.6041 | 3.1868 | 2.65 | 1.8582 | 1.1531 | 0.39187 | -0.50303 | -1.7112 | -3.0102 | -4.3836 | -10.5938 | -13.5622 | -13.8765 | 4.1225 | 3.8031 | 3.446 | 2.8837 | 2.4153 | 1.9062 | 1.347 | 0.5633 | -0.40609 | -1.4581 | -6.153 | -8.3153 | -11.4194 | 3.2062 | 2.7449 | 2.2306 | 1.5011 | 0.82452 | 0.094931 | -0.75609 | -1.9194 | -3.1673 | -4.4877 | -10.4275 | -13.1806 | -13.4571
|  | QUEENSMEAD | EE |  |  |  | 3.6041 | 3.1868 | 2.65 | 1.8582 | 1.1531 | 0.39187 | -0.45405 | -1.3459 | -2.2898 | -3.0092 | -5.15 | -5.6867 | -6.251 | 4.1225 | 3.8031 | 3.446 | 2.8837 | 2.4153 | 1.9062 | 1.347 | 0.76432 | 0.13677 | -0.35303 | -1.8398 | -2.9734 | -6.2275 | 3.2062 | 2.7449 | 2.2306 | 1.5011 | 0.82452 | 0.094931 | -0.71731 | -1.5673 | -2.4724 | -3.1612 | -5.1734 | -5.651 | -6.0551
|  | QUEENSMEAD | HT |  |  |  | 3.8429 | 3.5582 | 3.3062 | 2.8113 | 2.4949 | 2.1357 | 1.7153 | 1.2123 | 0.67248 | 0.10309 | -2.754 | -4.0949 | -4.9122 | 4.5327 | 4.3817 | 4.2031 | 3.9092 | 3.6735 | 3.3888 | 3.0898 | 2.7021 | 2.2868 | 1.8572 | 0.10309 | -0.66731 | -0.79793 | 3.5582 | 3.3011 | 3.0562 | 2.5868 | 2.2755 | 1.9245 | 1.5419 | 1.0521 | 0.49085 | -0.14997 | -2.8632 | -4.0571 | -4.3612
|  | QUEENSMEAD | HE |  |  |  | 3.7398 | 3.3847 | 2.846 | 2.05 | 1.3123 | 0.45411 | -0.50303 | -1.7112 | -3.0102 | -4.3836 | -10.5938 | -13.5622 | -13.8765 | 4.2684 | 3.9531 | 3.599 | 3.0337 | 2.55 | 1.9857 | 1.3633 | 0.5633 | -0.40609 | -1.4581 | -6.153 | -8.3153 | -8.5234 | 3.4011 | 2.9388 | 2.4215 | 1.6898 | 0.98167 | 0.1582 | -0.75609 | -1.9194 | -3.1673 | -4.4877 | -10.4275 | -13.1806 | -13.4571
|  | QUEENSMEAD | CF |  |  |  | 3.9327 | 3.7235 | 3.5378 | 3.0817 | 2.8664 | 2.3735 | 1.8735 | 1.2 | 0.43677 | -0.3816 | -5.2949 | -9.5989 | -12.5663 | 4.5837 | 4.4388 | 4.2266 | 3.8204 | 3.5408 | 3.2092 | 2.8643 | 2.4082 | 1.8857 | 1.3286 | -2.2877 | -5.6418 | -11.4194 | 3.6368 | 3.446 | 3.2664 | 2.8266 | 2.4735 | 2 | 1.5143 | 0.86432 | 0.12962 | -0.65609 | -5.3632 | -9.4826 | -12.251
MELKSHAM GSP | WEST GRAFTON | RAMSBURY | MINIMUM HEADROOM | SU 27380 72108 | YES | 0.542 | 4.9637 | 4.8392 | 4.6851 | 4.5596 | 4.3933 | 4.2218 | 4.032 | 3.7596 | 3.4871 | 3.3392 | 2.532 | 1.8535 | 1.4402 | 5.3808 | 5.2808 | 5.1645 | 5.0778 | 4.9492 | 4.8104 | 4.6869 | 4.4818 | 4.2747 | 4.1665 | 3.6257 | 2.8808 | 1.0543 | 5.0167 | 4.8984 | 4.7535 | 4.6371 | 4.48 | 4.3127 | 4.1341 | 3.881 | 3.63 | 3.4882 | 2.7637 | 2.1739 | 1.8392
|  | RAMSBURY | EE |  |  |  | 4.9637 | 4.8392 | 4.6851 | 4.5596 | 4.3933 | 4.2218 | 4.032 | 3.7596 | 3.4871 | 3.3392 | 2.5647 | 2.0024 | 1.5555 | 5.3808 | 5.2808 | 5.1645 | 5.0778 | 4.9492 | 4.8104 | 4.6869 | 4.4818 | 4.2747 | 4.1665 | 3.6257 | 2.992 | 2.0278 | 5.0167 | 4.8984 | 4.7535 | 4.6371 | 4.48 | 4.3127 | 4.1341 | 3.881 | 3.63 | 3.4882 | 2.7861 | 2.3076 | 1.9382
|  | RAMSBURY | HT |  |  |  | 5.0341 | 4.9086 | 4.7902 | 4.681 | 4.5637 | 4.4739 | 4.279 | 4.0586 | 3.8759 | 3.6412 | 2.532 | 1.8535 | 1.4402 | 5.4553 | 5.3604 | 5.291 | 5.2176 | 5.1349 | 5.0798 | 4.9604 | 4.8216 | 4.7237 | 4.5767 | 3.9278 | 3.6216 | 3.4461 | 5.0922 | 4.9759 | 4.8688 | 4.7627 | 4.6514 | 4.5667 | 4.3841 | 4.1769 | 4.0086 | 3.7892 | 2.7637 | 2.1739 | 1.8392
|  | RAMSBURY | HE |  |  |  | 5.0341 | 4.9188 | 4.8218 | 4.7116 | 4.5892 | 4.5065 | 4.3361 | 4.1514 | 3.9994 | 3.8004 | 2.8106 | 2.2463 | 1.9422 | 5.4471 | 5.3533 | 5.2859 | 5.2073 | 5.1135 | 5.0553 | 4.9359 | 4.7982 | 4.6941 | 4.5369 | 3.7553 | 3.1053 | 2.1992 | 5.0892 | 4.9831 | 4.8922 | 4.7882 | 4.6739 | 4.5953 | 4.4371 | 4.2606 | 4.1198 | 3.9331 | 3.0157 | 2.5208 | 2.2708
|  | RAMSBURY | CF |  |  |  | 5.0688 | 4.9841 | 4.9218 | 4.8769 | 4.8137 | 4.7382 | 4.6861 | 4.5831 | 4.4688 | 4.3422 | 3.6208 | 2.9892 | 2.429 | 5.4686 | 5.391 | 5.3288 | 5.289 | 5.2278 | 5.1492 | 5.0839 | 4.9757 | 4.8604 | 4.7339 | 3.9594 | 2.8808 | 1.0543 | 5.1249 | 5.0422 | 4.979 | 4.9351 | 4.8739 | 4.8014 | 4.7545 | 4.6555 | 4.5463 | 4.432 | 3.7616 | 3.1708 | 2.68
MELKSHAM GSP | AMESBURY | RATFYN | MINIMUM HEADROOM | SU 16215 42533 | YES | 0.711 | 12.4198 | 12.1259 | 11.7147 | 11.2535 | 11.2157 | 10.8076 | 10.1912 | 9.4943 | 8.8055 | 8.3576 | 6.0606 | 4.2524 | 3.3361 | 14.3478 | 14.158 | 13.9029 | 13.5784 | 13.5345 | 13.2253 | 12.8131 | 12.3365 | 11.8539 | 11.5416 | 9.7569 | 7.5641 | 2.0376 | 12.3861 | 12.1076 | 11.7178 | 11.278 | 11.2586 | 10.8718 | 10.2963 | 9.6392 | 8.9892 | 8.582 | 6.5841 | 5.0973 | 4.3433
|  | RATFYN | EE |  |  |  | 12.4198 | 12.1259 | 11.7147 | 11.2535 | 11.2157 | 10.8076 | 10.1912 | 9.4943 | 8.8055 | 8.3576 | 6.0739 | 4.5147 | 3.7484 | 14.3478 | 14.158 | 13.9029 | 13.5784 | 13.5345 | 13.2253 | 12.8131 | 12.3365 | 11.8539 | 11.5416 | 9.7569 | 7.8661 | 5.1478 | 12.3861 | 12.1076 | 11.7178 | 11.278 | 11.2586 | 10.8718 | 10.2963 | 9.6392 | 8.9892 | 8.582 | 6.5841 | 5.2994 | 4.6688
|  | RATFYN | HT |  |  |  | 12.579 | 12.3535 | 12.03 | 11.7106 | 11.378 | 11.0055 | 10.7922 | 10.2422 | 9.6708 | 9.0698 | 6.0606 | 4.2524 | 3.3361 | 14.4733 | 14.3569 | 14.1835 | 14.0131 | 13.8365 | 13.6233 | 13.5671 | 13.259 | 12.9335 | 12.5876 | 10.958 | 10.0763 | 9.6131 | 12.5678 | 12.3565 | 12.0484 | 11.7535 | 11.4331 | 11.0831 | 10.93 | 10.4208 | 9.8892 | 9.3269 | 6.6157 | 5.0973 | 4.3433
|  | RATFYN | HE |  |  |  | 12.5922 | 12.3831 | 12.0973 | 11.8178 | 11.4861 | 11.1331 | 10.9922 | 10.5127 | 10.0167 | 9.5004 | 6.9198 | 5.4269 | 4.729 | 14.4549 | 14.3069 | 14.1151 | 13.9273 | 13.709 | 13.4641 | 13.3773 | 13.0529 | 12.6947 | 12.3192 | 10.2212 | 8.3365 | 5.6355 | 12.579 | 12.379 | 12.1024 | 11.8392 | 11.5259 | 11.1933 | 11.0994 | 10.6504 | 10.182 | 9.6953 | 7.3565 | 6.1249 | 5.5657
|  | RATFYN | CF |  |  |  | 12.6892 | 12.5402 | 12.3973 | 12.2188 | 12.0627 | 11.8392 | 11.582 | 11.279 | 11.3678 | 11.0973 | 9.2739 | 7.4667 | 5.7371 | 14.5008 | 14.3712 | 14.2457 | 14.0906 | 13.9488 | 13.7467 | 13.4998 | 13.2049 | 13.162 | 12.8661 | 10.7498 | 7.5641 | 2.0376 | 12.6718 | 12.5208 | 12.378 | 12.1963 | 12.0514 | 11.8402 | 11.5963 | 11.3045 | 11.4086 | 11.1545 | 9.4524 | 7.8341 | 6.3871
BRAMLEY (FLEE) | READING BSP | READING | MINIMUM HEADROOM | SU 74591 73788 | YES | 78.893 | 7.6876 | 6.8957 | 6.3835 | 5.3927 | 4.4273 | -3.0604 | -4.688 | -6.5033 | -8.292 | -9.6094 | -15.5563 | -20.0635 | -21.5063 | 10.2929 | 9.6112 | 9.2888 | 8.4745 | 7.6429 | 0.30306 | -0.89184 | -2.2704 | -3.6571 | -4.598 | -9.9653 | -18.4449 | -37.352 | 6.4488 | 5.6437 | 5.1978 | 4.2304 | 3.2896 | -4.1635 | -5.6859 | -7.4033 | -9.1043 | -10.2808 | -15.4186 | -19.2676 | -20.4482
|  | READING | EE |  |  |  | 7.6876 | 6.8957 | 6.3835 | 5.3927 | 4.4273 | -3.0604 | -4.688 | -6.5033 | -8.292 | -9.6094 | -15.5563 | -19.3543 | -20.2206 | 10.2929 | 9.6112 | 9.2888 | 8.4745 | 7.6429 | 0.30306 | -0.89184 | -2.2704 | -3.6571 | -4.598 | -9.9653 | -15.9878 | -24.7316 | 6.4488 | 5.6437 | 5.1978 | 4.2304 | 3.2896 | -4.1635 | -5.6859 | -7.4033 | -9.1043 | -10.2808 | -15.4186 | -18.6686 | -19.438
|  | READING | HT |  |  |  | 8.0263 | 7.3814 | 6.6039 | 5.6671 | 5.1916 | -2.0533 | -3.3951 | -4.8482 | -6.3716 | -7.94 | -15.5124 | -20.0635 | -21.5063 | 10.7255 | 10.3122 | 9.7806 | 9.1531 | 9.0092 | 2.0316 | 1.2755 | 0.41531 | -0.48571 | -1.4418 | -5.7337 | -8.0224 | -8.799 | 6.8743 | 6.2722 | 5.5263 | 4.6427 | 4.2743 | -2.9431 | -4.1624 | -5.5124 | -6.9227 | -8.3727 | -15.2369 | -19.2676 | -20.4482
|  | READING | HE |  |  |  | 8.0365 | 7.4508 | 6.759 | 5.8886 | 5.5182 | -1.6665 | -2.839 | -4.1278 | -5.4716 | -6.8604 | -13.0778 | -16.7614 | -18.0308 | 10.649 | 10.1867 | 9.6071 | 8.9051 | 8.6786 | 1.5755 | 0.70918 | -0.28265 | -1.3602 | -2.502 | -8.6429 | -14.7357 | -23.5765 | 6.8733 | 6.3161 | 5.6427 | 4.8131 | 4.5376 | -2.6257 | -3.7043 | -4.9186 | -6.1829 | -7.4788 | -13.1594 | -16.3237 | -17.3441
|  | READING | CF |  |  |  | 8.3559 | 7.9814 | 7.5794 | 6.9988 | 6.8447 | -0.0093878 | -0.51755 | -1.1176 | -1.7543 | -2.4155 | -6.8839 | -11.8512 | -16.3339 | 10.8061 | 10.4 | 9.9714 | 9.3837 | 9.1796 | 2.1765 | 1.4765 | 0.66327 | -0.1949 | -1.1184 | -7.7194 | -18.4449 | -37.352 | 7.159 | 6.7753 | 6.3722 | 5.8131 | 5.7131 | -1.141 | -1.6471 | -2.2369 | -2.8604 | -3.5124 | -7.7951 | -12.1665 | -16.0329
BRAMLEY (FLEE) | READING TOWN BSP | READING TOWN | MINIMUM HEADROOM | SU 71540 74122 | YES | 33.143 | 51.5024 | 46.5198 | 45.4708 | 44.2198 | 42.38 | 40.2024 | 38.0524 | 35.7963 | 33.0892 | 30.7239 | 28.3453 | 26.7218 | 26.3157 | 53.3973 | 48.4392 | 47.5871 | 46.831 | 45.7637 | 44.531 | 43.2188 | 41.6494 | 39.9912 | 38.5004 | 34.7943 | 29.3882 | 18.4616 | 51.4045 | 46.5422 | 45.88 | 44.8351 | 43.2667 | 41.379 | 39.5331 | 37.6076 | 35.3229 | 33.3851 | 31.0627 | 29.5892 | 29.2586
|  | READING TOWN | EE |  |  |  | 51.5024 | 46.5198 | 45.4708 | 44.2198 | 42.38 | 40.2024 | 38.0524 | 35.7963 | 33.0892 | 30.7239 | 28.3453 | 27.4106 | 27.2218 | 53.3973 | 48.4392 | 47.5871 | 46.831 | 45.7637 | 44.531 | 43.2188 | 41.6494 | 39.9912 | 38.5004 | 34.7943 | 31.6422 | 26.4331 | 51.4045 | 46.5422 | 45.88 | 44.8351 | 43.2667 | 41.379 | 39.5331 | 37.6076 | 35.3229 | 33.3851 | 31.0627 | 30.2535 | 29.9922
|  | READING TOWN | HT |  |  |  | 51.7616 | 46.8718 | 46.0178 | 44.932 | 43.2851 | 41.2188 | 39.0912 | 36.7014 | 34.33 | 32.0239 | 28.882 | 26.7218 | 26.3157 | 53.6565 | 48.8422 | 48.1769 | 47.628 | 46.7912 | 45.7565 | 44.6412 | 43.1188 | 41.8055 | 40.4933 | 37.8014 | 36.4402 | 36.131 | 51.6249 | 46.8402 | 46.3157 | 45.4392 | 44.1076 | 42.3759 | 40.6871 | 38.7024 | 36.7871 | 34.8667 | 31.7014 | 29.5892 | 29.2586
|  | READING TOWN | HE |  |  |  | 51.7127 | 46.7973 | 46.0035 | 44.9361 | 43.3127 | 41.3535 | 39.5443 | 37.2637 | 34.8014 | 32.4831 | 30.1729 | 28.9871 | 28.6198 | 53.5739 | 48.6994 | 47.9586 | 47.332 | 46.4157 | 45.3341 | 44.2433 | 42.6392 | 41.128 | 39.6382 | 35.7912 | 32.3229 | 27.1065 | 51.5841 | 46.7841 | 46.2341 | 45.4065 | 44.08 | 42.4494 | 41.0035 | 39.0933 | 37.1708 | 35.328 | 33.0035 | 31.5841 | 30.8984
|  | READING TOWN | CF |  |  |  | 51.9973 | 47.3137 | 46.7922 | 46.0963 | 44.7953 | 43.3463 | 42.2086 | 40.6443 | 38.9004 | 37.3943 | 31.6024 | 29.8188 | 28.4127 | 53.7739 | 49.0708 | 48.4147 | 47.8422 | 47.0586 | 46.1576 | 45.3198 | 44.0004 | 42.7861 | 41.6504 | 35.6718 | 29.3882 | 18.4616 | 51.8239 | 47.2167 | 46.7657 | 46.3616 | 45.3708 | 44.2055 | 43.3463 | 42.029 | 40.68 | 39.5014 | 34.5188 | 32.6555 | 31.279
MANNINGTON GSP | REDHILL BSP | REDHILL | MINIMUM HEADROOM | SZ 08512 96149 | YES | 5 | 28.0286 | 27.0969 | 26.4184 | 25.5286 | 24.8276 | 24.1296 | 22.9847 | 21.7357 | 20.4878 | 19.5388 | 13.702 | 9.4704 | 7.2255 | 32.7 | 31.9898 | 31.5357 | 30.8449 | 30.2796 | 29.6908 | 28.8888 | 27.9684 | 27.0316 | 26.3837 | 22.6561 | 17.6235 | 5.7051 | 28.4357 | 27.5551 | 26.9806 | 26.1245 | 25.4255 | 24.7143 | 23.6153 | 22.3878 | 21.1704 | 20.3276 | 15.499 | 12.0408 | 10.2745
|  | REDHILL | EE |  |  |  | 28.0286 | 27.0969 | 26.4184 | 25.5286 | 24.8276 | 24.1296 | 22.9847 | 21.7357 | 20.4878 | 19.5388 | 14.4316 | 10.4276 | 7.7347 | 32.7 | 31.9898 | 31.5357 | 30.8449 | 30.2796 | 29.6908 | 28.8888 | 27.9684 | 27.0316 | 26.3837 | 22.6561 | 18.4571 | 12.299 | 28.4357 | 27.5551 | 26.9806 | 26.1245 | 25.4255 | 24.7143 | 23.6153 | 22.3878 | 21.1704 | 20.3276 | 16.0194 | 12.8337 | 10.6776
|  | REDHILL | HT |  |  |  | 28.2163 | 27.3357 | 26.4408 | 25.552 | 25.2071 | 24.6184 | 23.5296 | 22.3796 | 21.1786 | 19.9633 | 13.702 | 9.4704 | 7.2255 | 32.9888 | 32.4265 | 31.8684 | 31.2857 | 31.1786 | 30.8071 | 30.2469 | 29.6102 | 28.9378 | 28.2408 | 25.0143 | 23.2235 | 22.2929 | 28.7071 | 27.9224 | 27.1184 | 26.2908 | 26.0286 | 25.451 | 24.4622 | 23.3918 | 22.2745 | 21.1276 | 15.499 | 12.0408 | 10.2745
|  | REDHILL | HE |  |  |  | 28.2551 | 27.4347 | 26.5918 | 25.7622 | 25.4755 | 24.948 | 24.1357 | 23.2582 | 22.3459 | 21.3786 | 16.202 | 12.2571 | 10.3755 | 32.9388 | 32.3429 | 31.7367 | 31.1122 | 30.9378 | 30.5 | 29.9235 | 29.2633 | 28.5541 | 27.7959 | 23.498 | 19.251 | 13.3908 | 28.7316 | 27.9969 | 27.2388 | 26.4663 | 26.2531 | 25.7316 | 24.9673 | 24.1194 | 23.2327 | 22.3102 | 17.6082 | 14.4337 | 12.9571
|  | REDHILL | CF |  |  |  | 28.5694 | 27.8357 | 27.2102 | 26.6143 | 26.2408 | 26.1867 | 25.8949 | 25.549 | 25.1765 | 24.7898 | 21.6133 | 17.6439 | 13.8143 | 33.1204 | 32.5194 | 31.9969 | 31.4643 | 31.0724 | 30.9337 | 30.4939 | 29.9806 | 29.4306 | 28.8449 | 24.5102 | 17.6235 | 5.7051 | 29.0041 | 28.3582 | 27.7959 | 27.2347 | 26.851 | 26.8398 | 26.5306 | 26.1582 | 25.7673 | 25.3571 | 22.2194 | 18.7459 | 15.55
CHICKERELL GSP | CHICKERELL BSP | REDLANDS | MINIMUM HEADROOM | SY 67131 82321 | YES | 9.197 | 1.9387 | -1.0686 | -1.8788 | -2.6073 | -3.3757 | -4.1216 | -5.0512 | -6.0073 | -6.9155 | -7.5818 | -11.4706 | -14.1971 | -15.6604 | 4.456 | 1.6763 | 1.1233 | 0.61714 | 0.12429 | -0.36959 | -0.96449 | -1.6063 | -2.238 | -2.69 | -5.5359 | -8.7727 | -16.7635 | 2.4254 | -0.50224 | -1.2339 | -1.8288 | -2.5216 | -3.2073 | -4.0533 | -4.9522 | -5.8135 | -6.3971 | -9.739 | -12.09 | -13.3155
|  | REDLANDS | EE |  |  |  | 1.9387 | -1.0686 | -1.8788 | -2.6073 | -3.3757 | -4.1216 | -5.0512 | -6.0073 | -6.9155 | -7.5818 | -11.2308 | -13.7359 | -15.3543 | 4.456 | 1.6763 | 1.1233 | 0.61714 | 0.12429 | -0.36959 | -0.96449 | -1.6063 | -2.238 | -2.69 | -5.5359 | -8.2941 | -12.4635 | 2.4254 | -0.50224 | -1.2339 | -1.8288 | -2.5216 | -3.2073 | -4.0533 | -4.9522 | -5.8135 | -6.3971 | -9.5757 | -11.6808 | -13.0563
|  | REDLANDS | HT |  |  |  | 2.105 | -0.84408 | -1.5614 | -2.5124 | -3.241 | -3.9573 | -4.5145 | -5.3441 | -6.1451 | -7.0737 | -11.4706 | -14.1971 | -15.6604 | 4.6387 | 1.9498 | 1.5222 | 0.91612 | 0.51816 | 0.11714 | -0.060408 | -0.5002 | -0.94204 | -1.49 | -3.8706 | -5.0614 | -5.6665 | 2.6264 | -0.23184 | -0.86347 | -1.69 | -2.3359 | -2.991 | -3.4145 | -4.1676 | -4.9053 | -5.7604 | -9.739 | -12.09 | -13.3155
|  | REDLANDS | HE |  |  |  | 2.1172 | -0.80429 | -1.4941 | -2.4094 | -3.1104 | -3.7859 | -4.2094 | -4.9022 | -5.5624 | -6.2461 | -9.9676 | -12.3584 | -13.4676 | 4.606 | 1.8927 | 1.4294 | 0.79367 | 0.35184 | -0.09102 | -0.29204 | -0.76347 | -1.239 | -1.742 | -4.8594 | -7.6308 | -11.5788 | 2.6356 | -0.19918 | -0.80939 | -1.6033 | -2.2227 | -2.84 | -3.1461 | -3.7808 | -4.3971 | -5.0318 | -8.4073 | -10.4308 | -11.3543
|  | REDLANDS | CF |  |  |  | 2.256 | -0.5502 | -1.0543 | -1.6849 | -2.3104 | -2.8982 | -3.3012 | -3.3676 | -3.6941 | -4.0318 | -6.2216 | -9.0094 | -11.3635 | 4.6682 | 1.9814 | 1.6131 | 1.1396 | 0.6702 | 0.18857 | -0.19816 | -0.34612 | -0.72673 | -1.1339 | -3.9573 | -8.7727 | -16.7635 | 2.7591 | 0.0059184 | -0.42265 | -0.95735 | -1.5094 | -2.04 | -2.4196 | -2.4196 | -2.7339 | -3.0594 | -5.1604 | -7.591 | -9.6073
MANNINGTON GSP | SALISBURY | REDLYNCH | MINIMUM HEADROOM | SU 19073 20576 | YES | 4.494 | 4.0544 | 3.8453 | 3.6085 | 1.9253 | 1.5967 | 1.6457 | 1.2161 | 0.73547 | 0.24976 | -0.066567 | -1.8553 | -3.2921 | -4.1788 | 5.357 | 5.2886 | 5.2029 | 3.7074 | 3.5911 | 3.589 | 3.4044 | 3.1686 | 2.8839 | 2.6646 | 1.2778 | -0.48953 | -4.6456 | 4.1029 | 3.9988 | 3.8866 | 2.2829 | 2.0125 | 2.0401 | 1.6656 | 1.2482 | 0.8319 | 0.5319 | -1.211 | -2.4793 | -3.2436
|  | REDLYNCH | EE |  |  |  | 4.0544 | 3.8453 | 3.6085 | 1.9253 | 1.5967 | 1.6457 | 1.2161 | 0.73547 | 0.24976 | -0.066567 | -1.7819 | -3.0523 | -3.9778 | 5.357 | 5.2886 | 5.2029 | 3.7074 | 3.5911 | 3.589 | 3.4044 | 3.1686 | 2.8839 | 2.6646 | 1.2778 | -0.20993 | -2.361 | 4.1029 | 3.9988 | 3.8866 | 2.2829 | 2.0125 | 2.0401 | 1.6656 | 1.2482 | 0.8319 | 0.5319 | -1.1436 | -2.2722 | -3.0783
|  | REDLYNCH | HT |  |  |  | 4.2065 | 4.0106 | 3.8259 | 2.214 | 2.012 | 1.7579 | 1.3212 | 0.83956 | 0.76302 | 0.32017 | -1.8553 | -3.2921 | -4.1788 | 5.4243 | 5.3703 | 5.3192 | 3.8625 | 3.7982 | 3.7156 | 3.589 | 3.3758 | 3.3166 | 3.1217 | 2.1288 | 1.4523 | 1.0319 | 4.1723 | 4.0764 | 3.9815 | 2.4819 | 2.3207 | 2.1033 | 1.7095 | 1.2809 | 1.1768 | 0.77986 | -1.211 | -2.4793 | -3.2436
|  | REDLYNCH | HE |  |  |  | 4.2065 | 4.0289 | 3.8575 | 2.2549 | 2.0712 | 1.8324 | 1.463 | 1.0477 | 1.0416 | 0.67323 | -1.2931 | -2.5176 | -3.1655 | 5.4121 | 5.3529 | 5.2937 | 3.8268 | 3.7523 | 3.6544 | 3.4972 | 3.285 | 3.2176 | 3.0044 | 1.5084 | 0.014555 | -2.0242 | 4.1723 | 4.0845 | 3.9948 | 2.4992 | 2.3758 | 2.1707 | 1.8452 | 1.4839 | 1.4482 | 1.1227 | -0.6834 | -1.7977 | -2.3528
|  | REDLYNCH | CF |  |  |  | 4.2544 | 4.1514 | 4.0024 | 2.5069 | 2.3518 | 2.2263 | 2.0406 | 1.8212 | 1.5885 | 1.3436 | 0.41711 | -0.8982 | -2.1155 | 5.4305 | 5.3886 | 5.3325 | 3.8931 | 3.8268 | 3.7584 | 3.6666 | 3.5421 | 3.3595 | 3.1288 | 1.8962 | -0.48953 | -4.6456 | 4.2009 | 4.1488 | 4.0743 | 2.6288 | 2.5503 | 2.486 | 2.3707 | 2.188 | 1.9972 | 1.7962 | 0.96864 | -0.25993 | -1.4263
NURSLING GSP | SOUTHAMPTON (2 X 90) | REGENTS PARK | MINIMUM HEADROOM | SU 39267 13050 | YES | 0.36 | 15.3592 | 15.0153 | 14.4755 | 12.8112 | 11.7796 | 10.0082 | 7.7704 | 5.1776 | 3.9541 | 0.97653 | -10.0143 | -19.8755 | -23.9347 | 15.7612 | 15.5367 | 14.9204 | 13.1704 | 12.2673 | 10.1827 | 7.8163 | 5.0163 | 3.9367 | 0.67143 | -10.9786 | -21.1112 | -26.7561 | 14.5224 | 14.152 | 13.5112 | 11.598 | 10.5041 | 8.3561 | 5.8041 | 2.8561 | 1.6224 | -1.8051 | -14.2571 | -25.0224 | -30.7184
|  | REGENTS PARK | EE |  |  |  | 15.3592 | 15.0153 | 14.5245 | 13.951 | 13.298 | 11.5204 | 9.6041 | 8.6092 | 5.9418 | 4.2276 | -4.4092 | -7.0908 | -13.8724 | 15.7612 | 15.5367 | 15.2541 | 14.9316 | 14.5194 | 12.6796 | 10.7612 | 10.0102 | 7.202 | 5.5133 | -3.5714 | -6.6245 | -17.451 | 14.5224 | 14.152 | 13.7071 | 13.1969 | 12.6061 | 10.6622 | 8.5888 | 7.6888 | 4.7184 | 2.8837 | -6.8265 | -9.8398 | -18.1469
|  | REGENTS PARK | HT |  |  |  | 15.5888 | 15.3602 | 14.7776 | 13.8327 | 13.3265 | 10.0082 | 7.7704 | 5.1776 | 3.9541 | 0.97653 | -10.0143 | -14.8806 | -23.9347 | 15.9806 | 15.8398 | 15.2776 | 14.2602 | 13.9378 | 10.1827 | 7.8163 | 5.0163 | 3.9367 | 0.67143 | -10.9786 | -15.9592 | -26.7561 | 14.8286 | 14.6082 | 13.9265 | 12.7724 | 12.2898 | 8.3561 | 5.8041 | 2.8561 | 1.6224 | -1.8051 | -14.2571 | -19.7 | -30.7184
|  | REGENTS PARK | HE |  |  |  | 15.5429 | 15.301 | 14.4755 | 12.8112 | 11.7796 | 11.0439 | 8.6592 | 5.9469 | 4.8194 | 3.6684 | -9.9418 | -19.8755 | -23.4163 | 15.9163 | 15.7337 | 14.9204 | 13.1704 | 12.2673 | 11.7724 | 9.2173 | 6.3551 | 5.5 | 4.6286 | -9.8612 | -21.1112 | -26.2378 | 14.7622 | 14.4612 | 13.5112 | 11.598 | 10.5041 | 9.8378 | 7.1561 | 4.1337 | 3.1092 | 2.0653 | -13.2969 | -25.0224 | -29.3602
|  | REGENTS PARK | CF |  |  |  | 15.7122 | 15.5755 | 15.4163 | 15.2357 | 14.6694 | 13.8857 | 12.8806 | 11.9194 | 10.8296 | 9.5184 | 1.2939 | -8.5439 | -17.1776 | 16.0582 | 15.952 | 15.8245 | 15.6724 | 15.0592 | 14.2929 | 13.2765 | 12.4143 | 11.4306 | 10.0898 | 1.5888 | -10.0071 | -24.0112 | 14.9184 | 14.8102 | 14.651 | 14.4204 | 13.7204 | 12.852 | 11.7286 | 10.7153 | 9.5653 | 8.1469 | -0.87143 | -12.051 | -22.0908
COWLEY GSP | WITNEY BSP | RISSINGTON | MINIMUM HEADROOM | SP 19225 19563 | YES | 4.943 | 0.65531 | 0.50224 | 0.3002 | 0.11857 | -0.11408 | -0.37837 | -0.77633 | -0.86102 | -1.2416 | -1.5569 | -3.0978 | -4.3212 | -5.0682 | 2.7573 | 2.6522 | 2.5012 | 2.3573 | 2.1727 | 1.9716 | 1.6961 | 1.6869 | 1.4298 | 1.2584 | 0.26755 | -0.67735 | -3.01 | 1.1267 | 0.97163 | 0.74612 | 0.54408 | 0.26347 | -0.030408 | -0.41612 | -0.18551 | -0.5151 | -0.78041 | -2.1273 | -3.1539 | -3.7498
|  | RISSINGTON | EE |  |  |  | 0.65531 | 0.50224 | 0.3002 | 0.11857 | -0.11408 | -0.37837 | -0.77633 | -0.86102 | -1.2416 | -1.509 | -3.0386 | -4.0978 | -4.8376 | 2.7573 | 2.6522 | 2.5012 | 2.3573 | 2.1727 | 1.9716 | 1.6961 | 1.6869 | 1.4298 | 1.2584 | 0.26755 | -0.67735 | -1.9682 | 1.1267 | 0.97163 | 0.74612 | 0.54408 | 0.26347 | -0.030408 | -0.41612 | -0.18551 | -0.5151 | -0.75796 | -2.1008 | -2.961 | -3.5682
|  | RISSINGTON | HT |  |  |  | 0.72878 | 0.59102 | 0.42571 | 0.26857 | 0.082857 | -0.12429 | -0.42224 | -0.78959 | -1.1682 | -1.5569 | -3.0978 | -4.3212 | -5.0682 | 2.8308 | 2.7543 | 2.6553 | 2.5635 | 2.4482 | 2.3104 | 2.1471 | 1.9288 | 1.6992 | 1.4645 | 0.73286 | 0.16449 | -0.1651 | 1.2624 | 1.1522 | 1.0053 | 0.88184 | 0.70837 | 0.50837 | 0.29204 | -0.053878 | -0.41204 | -0.78041 | -2.1273 | -3.1539 | -3.7498
|  | RISSINGTON | HE |  |  |  | 0.73184 | 0.60531 | 0.45327 | 0.31143 | 0.14408 | -0.041633 | -0.28755 | -0.59878 | -0.92122 | -1.2569 | -2.61 | -3.6406 | -4.1488 | 2.8176 | 2.7349 | 2.6267 | 2.5298 | 2.4084 | 2.2665 | 2.1084 | 1.892 | 1.6594 | 1.4216 | 0.52061 | -0.43143 | -1.6365 | 1.2584 | 1.1543 | 1.0084 | 0.89306 | 0.72469 | 0.53082 | 0.34714 | 0.055306 | -0.2549 | -0.58245 | -1.6886 | -2.5304 | -2.9304
|  | RISSINGTON | CF |  |  |  | 0.7849 | 0.7002 | 0.59714 | 0.4849 | 0.39612 | 0.27469 | 0.13898 | 0.01551 | -0.14571 | -0.31306 | -1.1722 | -2.2855 | -3.3151 | 2.8461 | 2.7788 | 2.6971 | 2.6022 | 2.5257 | 2.4124 | 2.2859 | 2.1604 | 1.992 | 1.8176 | 0.91857 | -0.58755 | -3.01 | 1.2982 | 1.2206 | 1.1145 | 0.99714 | 0.91551 | 0.78694 | 0.63082 | 0.49714 | 0.29816 | 0.084898 | -0.42939 | -1.411 | -2.2876
BRAMLEY (ANDO-THAT) | THATCHAM BSP | RIVERSIDE | MINIMUM HEADROOM | SU 47846 67187 | YES | 3.93 | 11.7415 | 11.5558 | 11.316 | 11.064 | 10.7619 | 10.3987 | 9.9803 | 9.4885 | 9.0701 | 8.7089 | 7.1885 | 6.3374 | 5.9864 | 13.2869 | 13.1757 | 13.0298 | 12.8777 | 12.691 | 12.492 | 12.2859 | 12.0298 | 11.8043 | 11.6196 | 10.2135 | 8.2808 | 3.7869 | 12.7231 | 12.5589 | 12.3344 | 12.0987 | 11.8119 | 11.4844 | 11.0731 | 10.5844 | 10.165 | 9.814 | 8.2425 | 7.2629 | 6.8303
|  | RIVERSIDE | EE |  |  |  | 11.7415 | 11.5558 | 11.316 | 11.064 | 10.7619 | 10.3987 | 9.9803 | 9.4885 | 9.0701 | 8.7089 | 7.2701 | 6.6956 | 6.368 | 13.2869 | 13.1757 | 13.0298 | 12.8777 | 12.691 | 12.492 | 12.2859 | 12.0298 | 11.8043 | 11.6196 | 10.2135 | 8.6839 | 6.3502 | 12.7231 | 12.5589 | 12.3344 | 12.0987 | 11.8119 | 11.4844 | 11.0731 | 10.5844 | 10.165 | 9.814 | 8.3252 | 7.6038 | 7.1395
|  | RIVERSIDE | HT |  |  |  | 11.8456 | 11.6905 | 11.4997 | 11.2905 | 11.0415 | 10.7813 | 10.4323 | 10.0323 | 9.6731 | 9.2976 | 7.468 | 6.5436 | 6.118 | 13.3563 | 13.2737 | 13.1747 | 13.0624 | 12.9277 | 12.792 | 12.6369 | 12.4532 | 12.3114 | 12.1502 | 11.2788 | 10.6522 | 10.3114 | 12.8038 | 12.6772 | 12.5119 | 12.3191 | 12.0874 | 11.8487 | 11.5078 | 11.1027 | 10.7507 | 10.3772 | 8.4599 | 7.4089 | 6.8538
|  | RIVERSIDE | HE |  |  |  | 11.8344 | 11.6813 | 11.4885 | 11.2742 | 11.0221 | 10.7395 | 10.3711 | 9.9425 | 9.5507 | 9.1323 | 7.1885 | 6.3374 | 5.9864 | 13.342 | 13.2481 | 13.1308 | 13.0012 | 12.8471 | 12.693 | 12.5073 | 12.2941 | 12.1124 | 11.9094 | 10.5308 | 8.9665 | 6.7981 | 12.7987 | 12.6711 | 12.5017 | 12.3017 | 12.065 | 11.814 | 11.4466 | 11.017 | 10.6333 | 10.2211 | 8.2425 | 7.2629 | 6.8303
|  | RIVERSIDE | CF |  |  |  | 11.9282 | 11.8313 | 11.6997 | 11.568 | 11.4089 | 11.2436 | 11.0782 | 10.8711 | 10.6854 | 10.4742 | 8.9895 | 7.5619 | 6.4405 | 13.3839 | 13.3114 | 13.2135 | 13.1175 | 13.0032 | 12.8737 | 12.7512 | 12.593 | 12.4512 | 12.2961 | 10.8767 | 8.2808 | 3.7869 | 12.868 | 12.7864 | 12.6752 | 12.567 | 12.4313 | 12.2782 | 12.1231 | 11.9252 | 11.7466 | 11.5497 | 10.1293 | 8.6915 | 7.5385
MANNINGTON GSP | MANNINGTON BSP | ROCKBOURNE | MINIMUM HEADROOM | SU 11617 17810 | YES | 3.84 | 2.4127 | 0.92776 | 0.86857 | 0.82469 | 0.76347 | 0.6849 | 0.58898 | 0.52469 | 0.42163 | 0.37163 | 0.14102 | 0.058367 | -0.018163 | 3.1871 | 1.7104 | 1.6635 | 1.6298 | 1.5839 | 1.5247 | 1.4512 | 1.4053 | 1.3257 | 1.288 | 1.1022 | 0.83388 | 0.20837 | 2.6637 | 1.1778 | 1.1135 | 1.0696 | 1.0114 | 0.9349 | 0.84306 | 0.78286 | 0.68082 | 0.63796 | 0.43694 | 0.36347 | 0.29816
|  | ROCKBOURNE | EE |  |  |  | 2.4127 | 0.92776 | 0.86857 | 0.82469 | 0.76347 | 0.6849 | 0.58898 | 0.52469 | 0.42163 | 0.37163 | 0.14102 | 0.058367 | 0.017551 | 3.1871 | 1.7104 | 1.6635 | 1.6298 | 1.5839 | 1.5247 | 1.4512 | 1.4053 | 1.3257 | 1.288 | 1.1022 | 0.93796 | 0.63694 | 2.6637 | 1.1778 | 1.1135 | 1.0696 | 1.0114 | 0.9349 | 0.84306 | 0.78286 | 0.68082 | 0.63796 | 0.43694 | 0.36347 | 0.3298
|  | ROCKBOURNE | HT |  |  |  | 2.4331 | 0.9502 | 0.91551 | 0.87776 | 0.83082 | 0.79204 | 0.72776 | 0.65939 | 0.58082 | 0.4951 | 0.18694 | 0.063469 | -0.018163 | 3.2116 | 1.742 | 1.7216 | 1.6951 | 1.6604 | 1.639 | 1.5941 | 1.5451 | 1.491 | 1.4308 | 1.2431 | 1.1747 | 1.1298 | 2.6882 | 1.2073 | 1.1757 | 1.1369 | 1.088 | 1.0543 | 0.98796 | 0.92265 | 0.84204 | 0.76143 | 0.47469 | 0.36551 | 0.29816
|  | ROCKBOURNE | HE |  |  |  | 2.431 | 0.95429 | 0.92061 | 0.88184 | 0.83592 | 0.8002 | 0.73592 | 0.67163 | 0.59714 | 0.51143 | 0.18388 | 0.10224 | 0.070612 | 3.2065 | 1.738 | 1.7165 | 1.6859 | 1.6502 | 1.6257 | 1.5767 | 1.5278 | 1.4665 | 1.4012 | 1.1359 | 0.96653 | 0.66959 | 2.6861 | 1.2094 | 1.1778 | 1.141 | 1.0931 | 1.0614 | 0.99918 | 0.93388 | 0.85735 | 0.77776 | 0.47878 | 0.40837 | 0.3798
|  | ROCKBOURNE | CF |  |  |  | 2.4422 | 0.97163 | 0.94408 | 0.90735 | 0.87776 | 0.84 | 0.79714 | 0.76551 | 0.71653 | 0.67061 | 0.40735 | 0.23082 | 0.10837 | 3.2137 | 1.7543 | 1.7308 | 1.7012 | 1.6788 | 1.6431 | 1.6022 | 1.5767 | 1.5227 | 1.4798 | 1.1971 | 0.83388 | 0.20837 | 2.6994 | 1.2288 | 1.2022 | 1.1655 | 1.1359 | 1.0971 | 1.0522 | 1.0257 | 0.97469 | 0.92878 | 0.68082 | 0.51959 | 0.41245
NURSLING GSP | ROWNHAMS | ROMSEY | MINIMUM HEADROOM | SU 36092 21110 | YES | 0.026 | -0.50816 | 24.0306 | 23.4786 | 23.0786 | 22.6929 | 22.1694 | 21.4429 | 20.6265 | 19.598 | 18.6051 | 13.4388 | 10.448 | 8.7133 | 4.2469 | 27.1163 | 26.699 | 26.4163 | 26.1643 | 25.8051 | 25.3378 | 24.799 | 24.0969 | 23.5071 | 20.198 | 17.5398 | 10.8653 | 0.65306 | 24.1337 | 23.549 | 23.0724 | 22.749 | 22.1214 | 21.1602 | 20.1214 | 19.0816 | 18.2173 | 13.7776 | 11.1857 | 9.7592
|  | ROMSEY | EE |  |  |  | -0.50816 | 24.0337 | 23.4786 | 23.0786 | 22.6929 | 22.1694 | 21.4429 | 20.6265 | 19.598 | 18.6051 | 13.5592 | 10.9663 | 9.0418 | 4.2469 | 27.1643 | 26.699 | 26.4163 | 26.1643 | 25.8051 | 25.3378 | 24.799 | 24.0969 | 23.5071 | 20.198 | 17.6827 | 14.1214 | 0.65306 | 24.1337 | 23.549 | 23.0724 | 22.749 | 22.1214 | 21.1602 | 20.1214 | 19.0816 | 18.2173 | 13.8398 | 11.6714 | 10.05
|  | ROMSEY | HT |  |  |  | -0.34082 | 24.0306 | 23.7622 | 23.4367 | 23.0449 | 22.5959 | 21.9408 | 21.3459 | 20.2602 | 19.05 | 13.4388 | 10.448 | 8.7133 | 4.3806 | 27.1163 | 26.9378 | 26.7245 | 26.4622 | 26.1663 | 25.7633 | 25.4112 | 24.9429 | 24.3347 | 21.5214 | 20.202 | 19.4551 | 0.80918 | 24.1347 | 23.802 | 23.4235 | 22.9276 | 22.3592 | 21.4265 | 20.7806 | 19.8204 | 18.7469 | 13.7776 | 11.1857 | 9.7592
|  | ROMSEY | HE |  |  |  | -0.35612 | 24.2439 | 23.7571 | 23.4367 | 23.0041 | 22.5245 | 21.8612 | 21.25 | 20.4898 | 19.6551 | 14.4776 | 11.8714 | 10.648 | 4.3673 | 27.3286 | 26.9173 | 26.701 | 26.4102 | 26.0867 | 25.6612 | 25.2765 | 24.7755 | 24.251 | 20.7306 | 18.1184 | 14.8449 | 0.8051 | 24.3673 | 23.8643 | 23.5327 | 23.0184 | 22.4561 | 21.6092 | 21.049 | 20.1816 | 19.3031 | 14.7439 | 12.5327 | 11.5265
|  | ROMSEY | CF |  |  |  | -0.20714 | 24.4857 | 24.3673 | 23.9796 | 23.7214 | 23.4173 | 23.0214 | 22.5571 | 22.1806 | 21.6653 | 18.5765 | 15.3939 | 12.7755 | 4.4694 | 27.4908 | 27.401 | 27.052 | 26.8704 | 26.6602 | 26.3949 | 26.0745 | 25.7939 | 25.2633 | 22.0735 | 17.5398 | 10.8653 | 0.92653 | 24.5837 | 24.4418 | 24.0378 | 23.7398 | 23.3643 | 22.8612 | 22.298 | 22.0102 | 21.4429 | 18.3724 | 15.5214 | 13.2735
LOVEDEAN GSP | CHICHESTER & HUNSTON | ROSE GREEN | MINIMUM HEADROOM | SZ 89974 99335 | YES | 4.345 | 14.4643 | 12.801 | 12.4245 | 11.8776 | 11.3449 | 10.898 | 10.3061 | 9.2235 | 8.1316 | 7.0276 | 1.1449 | -2.599 | -4.3143 | 13.5582 | 11.8898 | 11.4112 | 10.998 | 10.3816 | 9.8214 | 9.0745 | 8.2878 | 7.4622 | 6.8102 | 3.0633 | -1.0602 | -9.3633 | 13.6531 | 11.7286 | 10.9724 | 10.1388 | 9.0969 | 8.4316 | 7.402 | 6.2643 | 5 | 4.1112 | -1.0969 | -4.3449 | -5.8388
|  | ROSE GREEN | EE |  |  |  | 14.4643 | 12.8408 | 12.4969 | 12.1949 | 11.7592 | 11.1939 | 10.6337 | 10.0071 | 8.8102 | 7.7765 | 2.0633 | -1.8969 | -3.9684 | 13.5582 | 11.8898 | 11.4112 | 11.1143 | 10.5388 | 9.8214 | 9.0745 | 8.2878 | 7.4622 | 6.8102 | 3.0633 | -0.57347 | -5.0194 | 13.6531 | 11.7286 | 10.9724 | 10.5959 | 9.7163 | 8.6173 | 7.4745 | 6.2643 | 5 | 4.1112 | -0.42347 | -3.6837 | -5.5143
|  | ROSE GREEN | HT |  |  |  | 14.5469 | 12.801 | 12.4245 | 11.8776 | 11.3449 | 10.898 | 10.3061 | 9.2235 | 8.1316 | 7.0276 | 1.1449 | -2.599 | -4.3143 | 13.7418 | 12.0143 | 11.5969 | 10.998 | 10.3816 | 9.9653 | 9.3745 | 8.7878 | 8.1816 | 7.5663 | 4.4633 | 2.6724 | 1.851 | 13.8908 | 11.8531 | 11.151 | 10.1388 | 9.0969 | 8.4316 | 7.402 | 6.3765 | 5.3245 | 4.251 | -1.0969 | -4.3449 | -5.8388
|  | ROSE GREEN | HE |  |  |  | 14.5469 | 12.948 | 12.6561 | 12.2694 | 11.8469 | 11.4082 | 10.9031 | 10.4153 | 9.4949 | 8.5071 | 2.9122 | -1.15 | -2.7153 | 13.7122 | 12.0735 | 11.6939 | 11.2041 | 10.648 | 10.199 | 9.5571 | 8.9173 | 8.2255 | 7.5316 | 3.5214 | -0.16224 | -4.3571 | 13.901 | 12.0602 | 11.502 | 10.748 | 9.901 | 9.3102 | 8.3694 | 7.4337 | 6.4347 | 5.448 | 0.48469 | -2.7418 | -4.0112
|  | ROSE GREEN | CF |  |  |  | 14.6173 | 13.2337 | 13.0133 | 12.9306 | 12.8265 | 12.7143 | 12.5949 | 12.4786 | 12.1765 | 11.849 | 9.052 | 3.148 | 0.22755 | 13.7827 | 12.3316 | 12.0122 | 11.8173 | 11.5622 | 11.2735 | 10.9429 | 10.7673 | 10.2612 | 9.7184 | 5.3663 | -1.0602 | -9.3633 | 14.0449 | 12.5153 | 12.0878 | 11.8612 | 11.5633 | 11.2469 | 10.9378 | 10.9878 | 10.451 | 9.8806 | 5.251 | 0.3 | -1.9092
COWLEY GSP | COWLEY LOCAL (2 X 90) | ROSE HILL | MINIMUM HEADROOM | SP 53637 03027 | YES | 8.179 | 7.3551 | 6.01 | 5.408 | 4.7835 | 4.5366 | 15.8682 | 13.7947 | 12.0723 | 10.4896 | 9.2815 | 4.8927 | 2.4815 | 1.3417 | 10.5429 | 9.3437 | 8.8784 | 8.4182 | 8.2172 | 20.6621 | 19.3907 | 18.1978 | 17.0039 | 16.009 | 11.3958 | 5.5815 | -5.6389 | 8.5633 | 7.3019 | 6.7468 | 6.2029 | 5.9998 | 17.3866 | 15.6182 | 14.0917 | 12.6611 | 11.5672 | 7.6845 | 5.7427 | 4.9284
|  | ROSE HILL | EE |  |  |  | 7.3551 | 6.0407 | 5.408 | 4.7835 | 4.5366 | 15.8682 | 13.7947 | 12.0723 | 10.4896 | 9.2815 | 4.8927 | 2.6274 | 1.9682 | 10.5429 | 9.3437 | 8.8784 | 8.4182 | 8.2172 | 20.6621 | 19.3907 | 18.1978 | 17.0039 | 16.009 | 11.3958 | 7.7162 | 2.3009 | 8.5633 | 7.3019 | 6.7468 | 6.2029 | 5.9998 | 17.3866 | 15.6182 | 14.0917 | 12.6611 | 11.5672 | 7.6845 | 5.8549 | 5.4519
|  | ROSE HILL | HT |  |  |  | 7.5674 | 6.01 | 5.6458 | 5.2958 | 4.657 | 16.0417 | 13.8264 | 12.5529 | 11.1213 | 9.7651 | 5.2243 | 2.4815 | 1.3417 | 10.7419 | 9.506 | 9.2968 | 9.0917 | 8.6029 | 21.1386 | 19.9631 | 19.0794 | 18.006 | 16.9886 | 14.0672 | 12.5692 | 11.858 | 8.7735 | 7.357 | 7.0192 | 6.6968 | 6.0917 | 17.5131 | 15.7162 | 14.5743 | 13.2682 | 12.0325 | 8.0356 | 5.7427 | 4.9284
|  | ROSE HILL | HE |  |  |  | 7.5602 | 6.3315 | 5.8264 | 5.4172 | 4.9876 | 16.4437 | 14.4866 | 13.3172 | 12.0029 | 10.7641 | 6.1692 | 3.8988 | 2.6764 | 10.6827 | 9.557 | 9.2009 | 8.8825 | 8.5202 | 21.0376 | 19.8488 | 19.0305 | 17.9815 | 16.9111 | 11.9907 | 8.2223 | 2.6774 | 8.7653 | 7.5896 | 7.1539 | 6.7886 | 6.3886 | 17.8825 | 16.2376 | 15.26 | 14.0907 | 12.9641 | 8.8376 | 6.9978 | 6.1039
|  | ROSE HILL | CF |  |  |  | 7.7255 | 6.7376 | 6.61 | 6.4437 | 6.2978 | 18.1968 | 17.5151 | 16.5988 | 15.8468 | 14.7794 | 8.656 | 5.4396 | 2.7407 | 10.7663 | 9.7427 | 9.5631 | 9.3335 | 9.0917 | 21.8774 | 21.2386 | 20.4223 | 19.7192 | 18.7478 | 12.0764 | 5.5815 | -5.6389 | 8.9184 | 7.9396 | 7.8141 | 7.656 | 7.5121 | 19.4213 | 18.8407 | 18.058 | 17.4376 | 16.5233 | 11.109 | 8.3958 | 6.1631
MELKSHAM GSP | CHIPPENHAM | ROWDEN | MINIMUM HEADROOM | ST 90805 72608 | YES | 25.26 | -4.5363 | -5.321 | -6.7312 | -8.0325 | -9.1559 | -9.8253 | -11.4662 | -13.1039 | -15.0835 | -16.7202 | -25.1835 | -30.5957 | -32.8131 | -1.8261 | -2.3771 | -3.4689 | -4.4784 | -5.2335 | -6.0743 | -7.1896 | -8.3355 | -9.6345 | -10.6264 | -15.4835 | -19.9621 | -29.4692 | -3.9802 | -4.6475 | -5.9138 | -7.1059 | -8.0662 | -9.3264 | -10.808 | -12.3243 | -14.0906 | -15.4733 | -22.5672 | -27.2182 | -29.1019
|  | ROWDEN | EE |  |  |  | -4.5363 | -5.321 | -6.7312 | -8.0325 | -9.1559 | -9.8253 | -11.4662 | -13.1039 | -15.0835 | -16.7202 | -24.8427 | -29.8774 | -32.4427 | -1.8261 | -2.3771 | -3.4689 | -4.4784 | -5.2335 | -6.0743 | -7.1896 | -8.3355 | -9.6345 | -10.6264 | -15.4835 | -19.6733 | -24.6845 | -3.9802 | -4.6475 | -5.9138 | -7.1059 | -8.0662 | -9.3264 | -10.808 | -12.3243 | -14.0906 | -15.4733 | -22.2998 | -26.6121 | -28.811
|  | ROWDEN | HT |  |  |  | -4.3006 | -5.0302 | -6.2924 | -7.8376 | -8.8621 | -9.2559 | -10.9202 | -12.5774 | -14.5019 | -16.2345 | -25.1835 | -30.5957 | -32.8131 | -1.5669 | -1.9944 | -2.8883 | -4.0366 | -4.6151 | -5.1131 | -6.0988 | -7.0835 | -8.1702 | -9.1141 | -13.5539 | -15.9815 | -16.9141 | -3.7771 | -4.3842 | -5.524 | -6.9325 | -7.8059 | -8.8182 | -10.2978 | -11.7692 | -13.4355 | -14.9213 | -22.5672 | -27.2182 | -29.1019
|  | ROWDEN | HE |  |  |  | -4.3026 | -5.0047 | -6.2475 | -7.7713 | -8.8223 | -9.0784 | -10.4682 | -11.8478 | -13.6059 | -15.2815 | -23.6998 | -28.8947 | -30.5702 | -1.6179 | -2.0812 | -3.022 | -4.2162 | -4.8978 | -5.3672 | -6.2978 | -7.2406 | -8.3682 | -9.4519 | -14.9151 | -19.3386 | -24.008 | -3.7781 | -4.3649 | -5.4883 | -6.8815 | -7.7835 | -8.6682 | -9.9039 | -11.1304 | -12.6508 | -14.0968 | -21.308 | -25.757 | -27.1692
|  | ROWDEN | CF |  |  |  | -4.1057 | -4.6353 | -5.7159 | -6.9682 | -7.757 | -9.0131 | -9.31 | -9.7998 | -10.3794 | -10.9621 | -16.4835 | -23.6804 | -27.2223 | -1.5138 | -1.9067 | -2.7842 | -3.8488 | -4.4141 | -5.8692 | -6.1498 | -6.6631 | -7.2376 | -7.8396 | -12.6631 | -19.9621 | -29.4692 | -3.5965 | -4.0271 | -4.9975 | -6.1519 | -6.8121 | -8.6355 | -8.8743 | -9.2998 | -9.7978 | -10.2937 | -15.009 | -21.06 | -24.2172
LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | ROWNER PARK | MINIMUM HEADROOM | SU 58018 00782 | YES | 9.081 | 12.9039 | 11.6961 | 11.3675 | 10.9573 | 10.4991 | 10.4471 | 9.8216 | 9.1012 | 8.3889 | 7.8848 | 5.4522 | 3.4726 | 2.345 | 14.25 | 13.0849 | 12.8013 | 12.4574 | 12.0594 | 11.9666 | 11.488 | 10.9319 | 10.3676 | 9.9564 | 7.7156 | 4.0074 | -4.0283 | 13.1138 | 11.9141 | 11.5978 | 11.209 | 10.7713 | 10.7131 | 10.1223 | 9.4396 | 8.7631 | 8.2947 | 6.0917 | 4.3162 | 3.3713
|  | ROWNER PARK | EE |  |  |  | 12.9039 | 11.6961 | 11.3675 | 10.9573 | 10.4991 | 10.4471 | 9.8216 | 9.1012 | 8.3889 | 7.8848 | 5.4522 | 3.7624 | 2.3767 | 14.25 | 13.0849 | 12.8013 | 12.4574 | 12.0594 | 11.9666 | 11.488 | 10.9319 | 10.3676 | 9.9564 | 7.7156 | 5.1492 | 1.0502 | 13.1138 | 11.9141 | 11.5978 | 11.209 | 10.7713 | 10.7131 | 10.1223 | 9.4396 | 8.7631 | 8.2947 | 6.0917 | 4.5733 | 3.3937
|  | ROWNER PARK | HT |  |  |  | 13.1478 | 11.9859 | 11.7563 | 11.4736 | 11.2124 | 10.8736 | 10.3175 | 9.6899 | 9.4685 | 8.8644 | 5.5512 | 3.4726 | 2.345 | 14.4806 | 13.3931 | 13.2339 | 13.04 | 12.8584 | 12.6176 | 12.2798 | 11.8849 | 11.8186 | 11.4421 | 9.5656 | 8.5451 | 8.0931 | 13.3526 | 12.2019 | 11.9825 | 11.7151 | 11.4651 | 11.1396 | 10.6182 | 10.0264 | 9.8417 | 9.2713 | 6.2151 | 4.3162 | 3.3713
|  | ROWNER PARK | HE |  |  |  | 13.1203 | 11.9583 | 11.7236 | 11.4379 | 11.1706 | 10.8257 | 10.3093 | 9.7093 | 9.5093 | 8.9338 | 5.9654 | 4.0124 | 3.2563 | 14.4214 | 13.2931 | 13.088 | 12.839 | 12.588 | 12.2758 | 11.8717 | 11.3941 | 11.2237 | 10.7421 | 7.9421 | 5.1309 | 1.2727 | 13.323 | 12.1713 | 11.9488 | 11.6764 | 11.4182 | 11.0896 | 10.6029 | 10.0366 | 9.8672 | 9.3202 | 6.557 | 4.7804 | 4.1672
|  | ROWNER PARK | CF |  |  |  | 13.2937 | 12.1787 | 12.0165 | 11.8828 | 11.694 | 11.4818 | 11.3144 | 11.0359 | 10.7328 | 10.4124 | 8.8032 | 6.8226 | 5.1348 | 14.5408 | 13.4094 | 13.2298 | 13.0635 | 12.84 | 12.5737 | 12.3043 | 11.9411 | 11.5441 | 11.1186 | 8.5707 | 4.0074 | -4.0283 | 13.4924 | 12.3784 | 12.2284 | 12.1019 | 11.9243 | 11.7243 | 11.5611 | 11.2947 | 11.0049 | 10.6998 | 9.158 | 7.3366 | 5.7876
FAWLEY GSP | COWES & WOOTTON COMMON BSP | RYDE | MINIMUM HEADROOM | SZ 59554 91973 | YES | 0.32 | 10.6082 | 9.798 | 8.7194 | 7.9918 | 6.8469 | 5.6908 | 4.1327 | 2.3724 | 0.56939 | -0.83265 | -8.299 | -14.2082 | -17.5745 | 13.5755 | 13.0449 | 12.3327 | 11.8684 | 11.05 | 10.1929 | 9.1347 | 7.902 | 6.6337 | 5.6582 | 0.32245 | -4.7898 | -18.8133 | 11.252 | 10.5184 | 9.5408 | 8.9143 | 7.8684 | 6.7939 | 5.3622 | 3.7398 | 2.0796 | 0.81735 | -5.6561 | -10.8888 | -13.6173
|  | RYDE | EE |  |  |  | 10.6082 | 9.798 | 8.7194 | 7.9918 | 6.8469 | 5.6908 | 4.1327 | 2.3724 | 0.56939 | -0.83265 | -8.1633 | -12.8847 | -16.8908 | 13.5755 | 13.0449 | 12.3327 | 11.8684 | 11.05 | 10.1929 | 9.1347 | 7.902 | 6.6337 | 5.6582 | 0.32245 | -4.7224 | -12.3214 | 11.252 | 10.5184 | 9.5408 | 8.9143 | 7.8684 | 6.7939 | 5.3622 | 3.7398 | 2.0796 | 0.81735 | -5.6408 | -9.7173 | -13.0561
|  | RYDE | HT |  |  |  | 10.9347 | 10.2204 | 9.3551 | 8.4112 | 7.3622 | 6.6776 | 5.2296 | 3.6551 | 2.0173 | 0.37449 | -8.299 | -14.2082 | -17.5745 | 13.8959 | 13.4898 | 13.0133 | 12.4765 | 11.8918 | 11.5673 | 10.7908 | 9.9092 | 8.9827 | 8.0347 | 3.3041 | 0.43061 | -0.94796 | 11.6194 | 10.9857 | 10.2173 | 9.3602 | 8.4173 | 7.8296 | 6.5378 | 5.1184 | 3.6429 | 2.151 | -5.6561 | -10.8888 | -13.6173
|  | RYDE | HE |  |  |  | 10.9163 | 10.2724 | 9.4735 | 8.5969 | 7.6418 | 7.0704 | 5.9102 | 4.6051 | 3.2153 | 1.8173 | -5.6857 | -10.5204 | -12.8224 | 13.8194 | 13.3949 | 12.8724 | 12.2929 | 11.65 | 11.2663 | 10.5122 | 9.6224 | 8.6531 | 7.6418 | 1.8388 | -3.4184 | -10.3653 | 11.5959 | 11.0235 | 10.3122 | 9.5173 | 8.6582 | 8.1673 | 7.1245 | 5.9418 | 4.6867 | 3.4163 | -3.299 | -7.4337 | -9.2796
|  | RYDE | CF |  |  |  | 11.2357 | 10.8316 | 10.2857 | 9.752 | 9.1531 | 8.5786 | 8.398 | 7.8112 | 7.1949 | 6.5755 | 0.99796 | -3.8704 | -8.349 | 13.9857 | 13.6602 | 13.2327 | 12.8092 | 12.3071 | 11.7643 | 11.4408 | 10.799 | 10.1194 | 9.3755 | 3.4878 | -4.7898 | -18.8133 | 11.8837 | 11.5265 | 11.0378 | 10.5592 | 10.0235 | 9.5031 | 9.3694 | 8.8367 | 8.2704 | 7.6959 | 2.702 | -1.6776 | -5.6255
MANNINGTON GSP | SALISBURY | SALISBURY CENTRAL | MINIMUM HEADROOM | SU 14215 30481 | YES | 3.327 | 14.449 | 14.148 | 13.6102 | 13.1469 | 12.0102 | 10.9612 | 9.4837 | 7.6908 | 5.8143 | 4.2643 | -1.5133 | -5.3459 | -6.4367 | 19.8367 | 19.4092 | 18.8878 | 18.4929 | 17.501 | 16.6622 | 15.6082 | 14.2908 | 12.9327 | 11.8163 | 6.8878 | 1.7878 | -11.6082 | 16.0724 | 15.5398 | 14.8898 | 14.4265 | 13.2418 | 12.2653 | 10.8878 | 9.1806 | 7.4194 | 5.9816 | 0.64184 | -2.651 | -3.5378
|  | SALISBURY CENTRAL | EE |  |  |  | 14.449 | 14.148 | 13.6102 | 13.1469 | 12.0102 | 10.9612 | 9.4837 | 7.6908 | 5.8143 | 4.2643 | -1.5133 | -4.4531 | -5.3 | 19.8367 | 19.4092 | 18.8878 | 18.4929 | 17.501 | 16.6622 | 15.6082 | 14.2908 | 12.9327 | 11.8163 | 6.8878 | 2.5786 | -3.7612 | 16.0724 | 15.5398 | 14.8898 | 14.4265 | 13.2418 | 12.2653 | 10.8878 | 9.1806 | 7.4194 | 5.9816 | 0.64184 | -1.8949 | -2.602
|  | SALISBURY CENTRAL | HT |  |  |  | 14.6316 | 14.3806 | 14.1316 | 13.5061 | 12.5245 | 11.9276 | 10.4541 | 8.8082 | 7.1582 | 5.6694 | -1.4704 | -5.3459 | -6.4367 | 20.1031 | 19.8633 | 19.5796 | 19.0796 | 18.4112 | 18.0296 | 17.1816 | 16.1469 | 15.1051 | 14.1469 | 9.9429 | 7.8673 | 7.2398 | 16.2561 | 15.9429 | 15.5408 | 14.8173 | 13.8653 | 13.3102 | 11.9684 | 10.3908 | 8.8276 | 7.3969 | 0.79694 | -2.651 | -3.5378
|  | SALISBURY CENTRAL | HE |  |  |  | 14.6357 | 14.4031 | 14.1714 | 13.7388 | 12.7755 | 12.2959 | 11.2265 | 9.9367 | 8.5592 | 7.1663 | 1.2684 | -1.4847 | -2.4857 | 20.0714 | 19.749 | 19.4061 | 18.8776 | 18.0173 | 17.6327 | 16.8816 | 15.9306 | 14.9255 | 13.8786 | 8.6082 | 4.199 | -2.1429 | 16.2694 | 15.9806 | 15.6316 | 15.0102 | 13.9959 | 13.5878 | 12.6031 | 11.3765 | 10.0888 | 8.7673 | 3.2673 | 0.88061 | 0.072449
|  | SALISBURY CENTRAL | CF |  |  |  | 14.7704 | 14.6378 | 14.4918 | 14.2684 | 13.7816 | 13.3602 | 13.2408 | 12.8776 | 12.348 | 11.7 | 6.3786 | 2.3714 | -1.3663 | 20.1643 | 19.9367 | 19.6449 | 19.2694 | 18.6051 | 17.9918 | 17.6888 | 17.0214 | 16.3071 | 15.5378 | 9.5959 | 1.7878 | -11.6082 | 16.4582 | 16.3112 | 16.1571 | 15.8306 | 15.2041 | 14.702 | 14.6082 | 14.0755 | 13.4847 | 12.851 | 7.851 | 4.251 | 0.98061
BRAMLEY (FLEE) | CAMBERLEY MAIN | SANDHURST | MINIMUM HEADROOM | SU 83597 60930 | YES | 7.971 | 4.7812 | 4.0812 | 3.7802 | 3.0506 | 2.2302 | 1.3547 | -0.14226 | -1.8229 | -3.5035 | -4.6545 | -11.4147 | -16.6647 | -19.7076 | 8.2771 | 7.7108 | 7.471 | 6.8618 | 6.1802 | 5.4384 | 4.3894 | 3.1833 | 1.9567 | 1.1363 | -3.5035 | -10.2882 | -25.3667 | 4.9853 | 4.3006 | 4.0394 | 3.3333 | 2.5506 | 1.7108 | 0.31284 | -1.2647 | -2.8423 | -3.8902 | -9.6994 | -14.2657 | -16.8953
|  | SANDHURST | EE |  |  |  | 4.7812 | 4.0812 | 3.7802 | 3.0506 | 2.2302 | 1.3547 | -0.14226 | -1.8229 | -3.5035 | -4.6545 | -10.8372 | -15.5851 | -19.2321 | 8.2771 | 7.7108 | 7.471 | 6.8618 | 6.1802 | 5.4384 | 4.3894 | 3.1833 | 1.9567 | 1.1363 | -3.5035 | -8.7974 | -16.728 | 4.9853 | 4.3006 | 4.0394 | 3.3333 | 2.5506 | 1.7108 | 0.31284 | -1.2647 | -2.8423 | -3.8902 | -9.2474 | -13.3382 | -16.5137
|  | SANDHURST | HT |  |  |  | 5.1343 | 4.6169 | 4.0128 | 3.6996 | 3.0782 | 2.4067 | 1.0659 | -0.38103 | -1.8872 | -3.4239 | -11.4147 | -16.6647 | -19.7076 | 8.6639 | 8.3455 | 7.9384 | 7.8128 | 7.4067 | 6.9567 | 6.2363 | 5.4282 | 4.572 | 3.6822 | -0.50348 | -2.8351 | -4.1198 | 5.3782 | 4.8853 | 4.2965 | 4.0577 | 3.4679 | 2.8261 | 1.6179 | 0.30162 | -1.078 | -2.4933 | -9.6994 | -14.2657 | -16.8953
|  | SANDHURST | HE |  |  |  | 5.1322 | 4.6506 | 4.069 | 3.7955 | 3.2057 | 2.5649 | 1.4618 | 0.23836 | -1.0463 | -2.3688 | -9.3994 | -14.3698 | -16.7627 | 8.5782 | 8.1986 | 7.7067 | 7.4914 | 6.9965 | 6.4353 | 5.6516 | 4.7516 | 3.7833 | 2.7557 | -2.978 | -8.5606 | -16.0167 | 5.37 | 4.9077 | 4.3353 | 4.1271 | 3.5659 | 2.9486 | 1.9384 | 0.79958 | -0.40144 | -1.6433 | -7.9872 | -12.3474 | -14.3259
|  | SANDHURST | CF |  |  |  | 5.3914 | 5.0873 | 4.7843 | 4.4037 | 4.3935 | 4.0455 | 3.6118 | 3.0833 | 2.4996 | 1.8873 | -2.8514 | -7.8514 | -12.4861 | 8.7067 | 8.3802 | 8.0302 | 7.6077 | 7.4873 | 7.02 | 6.4516 | 5.7792 | 5.0455 | 4.2608 | -1.4872 | -10.2882 | -25.3667 | 5.6037 | 5.2904 | 4.9833 | 4.6088 | 4.6271 | 4.2792 | 3.8649 | 3.3588 | 2.7965 | 2.2067 | -2.2443 | -6.728 | -10.6851
FAWLEY GSP | COWES & WOOTTON COMMON BSP | SANDOWN | MINIMUM HEADROOM | SZ 59877 85052 | YES | 0.254 | 3.9801 | 3.5668 | 3.0311 | 2.4128 | 2.2515 | 1.673 | 0.81888 | -0.16582 | -1.1556 | -1.8903 | -5.4689 | -8.5291 | -10.1097 | 4.1418 | 3.8306 | 3.4286 | 2.9724 | 2.7796 | 2.3061 | 1.6827 | 0.95612 | 0.23061 | -0.31327 | -3.1531 | -6.2806 | -13.9112 | 3.1418 | 2.7408 | 2.2235 | 1.6367 | 1.4571 | 0.89388 | 0.056122 | -0.90408 | -1.851 | -2.5296 | -5.8286 | -8.5939 | -9.998
|  | SANDOWN | EE |  |  |  | 3.9801 | 3.5668 | 3.0311 | 2.4128 | 2.2515 | 1.673 | 0.81888 | -0.16582 | -1.1556 | -1.8903 | -5.4689 | -7.9138 | -9.875 | 4.1418 | 3.8306 | 3.4286 | 2.9724 | 2.7796 | 2.3061 | 1.6827 | 0.95612 | 0.23061 | -0.31327 | -3.1531 | -5.9327 | -9.9837 | 3.1418 | 2.7408 | 2.2235 | 1.6367 | 1.4571 | 0.89388 | 0.056122 | -0.90408 | -1.851 | -2.5296 | -5.8286 | -8.0724 | -9.8071
|  | SANDOWN | HT |  |  |  | 4.2638 | 3.9546 | 3.5515 | 3.175 | 2.7444 | 2.2505 | 1.4342 | 1.0423 | 0.15765 | -0.76071 | -5.4546 | -8.5291 | -10.1097 | 4.3847 | 4.1898 | 3.9388 | 3.6857 | 3.399 | 3.0633 | 2.5806 | 2.351 | 1.8316 | 1.2827 | -1.3857 | -2.9724 | -3.6908 | 3.4163 | 3.1255 | 2.7469 | 2.3735 | 1.9571 | 1.4806 | 0.70306 | 0.29388 | -0.52857 | -1.3816 | -5.7469 | -8.5939 | -9.998
|  | SANDOWN | HE |  |  |  | 4.2362 | 3.9321 | 3.5372 | 3.1505 | 2.7168 | 2.227 | 1.523 | 1.1281 | 0.35459 | -0.4699 | -4.7026 | -7.4903 | -8.8189 | 4.3255 | 4.0959 | 3.7949 | 3.4898 | 3.1347 | 2.7296 | 2.2051 | 1.9112 | 1.3245 | 0.69388 | -2.8173 | -5.9327 | -9.6388 | 3.3847 | 3.0949 | 2.7163 | 2.3388 | 1.9163 | 1.4367 | 0.75 | 0.40102 | -0.33878 | -1.1143 | -5.1276 | -7.7194 | -8.752
|  | SANDOWN | CF |  |  |  | 4.4015 | 4.1832 | 3.9566 | 3.6628 | 3.425 | 3.1087 | 2.7679 | 2.3485 | 2.3577 | 1.9719 | -0.69541 | -3.5923 | -6.1128 | 4.4296 | 4.2367 | 4.0347 | 3.7786 | 3.5306 | 3.2061 | 2.8327 | 2.3929 | 2.2071 | 1.7531 | -1.4541 | -6.2806 | -13.9112 | 3.549 | 3.3459 | 3.1367 | 2.8612 | 2.6316 | 2.3337 | 2.0071 | 1.6122 | 1.6 | 1.2276 | -1.348 | -4.049 | -6.4
LOVEDEAN GSP | CHICHESTER & HUNSTON | SELSEY | MINIMUM HEADROOM | SZ 85667 94289 | YES | 0.356 | 10.9306 | 10.6255 | 10.3316 | 9.9418 | 9.9541 | 9.6071 | 9.0398 | 8.3959 | 7.748 | 7.3224 | 4.6051 | 2.302 | 0.97755 | 11.4378 | 11.2 | 10.9612 | 10.652 | 10.6357 | 10.3459 | 9.9388 | 9.4663 | 8.9878 | 8.6684 | 6.8418 | 4.4694 | -1.3663 | 10.9551 | 10.6602 | 10.3765 | 10.002 | 10.0255 | 9.6918 | 9.1582 | 8.551 | 7.9388 | 7.55 | 5.1041 | 3.2235 | 2.149
|  | SELSEY | EE |  |  |  | 10.9306 | 10.6255 | 10.3316 | 9.9418 | 9.9541 | 9.6071 | 9.0398 | 8.3959 | 7.748 | 7.3224 | 5.0337 | 2.852 | 1.2388 | 11.4378 | 11.2 | 10.9612 | 10.652 | 10.6357 | 10.3459 | 9.9388 | 9.4663 | 8.9878 | 8.6684 | 6.8418 | 4.7684 | 1.6776 | 10.9551 | 10.6602 | 10.3765 | 10.002 | 10.0255 | 9.6918 | 9.1582 | 8.551 | 7.9388 | 7.55 | 5.4061 | 3.6898 | 2.3561
|  | SELSEY | HT |  |  |  | 11.0959 | 10.8602 | 10.6327 | 10.3816 | 10.0776 | 9.7398 | 9.1561 | 8.9847 | 8.4031 | 7.7939 | 4.6051 | 2.302 | 0.97755 | 11.5939 | 11.4378 | 11.2939 | 11.1296 | 10.9245 | 10.6969 | 10.349 | 10.3184 | 9.9765 | 9.6153 | 7.9429 | 6.9918 | 6.4724 | 11.1224 | 10.8959 | 10.6827 | 10.448 | 10.1582 | 9.8378 | 9.2949 | 9.1622 | 8.6031 | 8.0194 | 5.1041 | 3.2235 | 2.149
|  | SELSEY | HE |  |  |  | 11.1061 | 10.8929 | 10.6898 | 10.4735 | 10.201 | 9.9041 | 9.4408 | 9.3796 | 8.9194 | 8.4388 | 5.9612 | 3.8357 | 2.7602 | 11.5714 | 11.401 | 11.2398 | 11.0592 | 10.8286 | 10.5765 | 10.2316 | 10.1847 | 9.8316 | 9.45 | 7.3153 | 5.2286 | 2.3429 | 11.1306 | 10.9245 | 10.7347 | 10.5296 | 10.2704 | 9.9847 | 9.55 | 9.5143 | 9.0837 | 8.6337 | 6.2633 | 4.5765 | 3.7153
|  | SELSEY | CF |  |  |  | 11.2 | 11.0704 | 10.948 | 10.7827 | 10.6541 | 10.4684 | 10.2653 | 10.0092 | 10.151 | 9.9306 | 8.248 | 6.4653 | 4.7122 | 11.6204 | 11.4908 | 11.3643 | 11.198 | 11.0449 | 10.8316 | 10.5786 | 10.2806 | 10.2724 | 9.9776 | 7.8092 | 4.4694 | -1.3663 | 11.2163 | 11.0908 | 10.9724 | 10.8112 | 10.6898 | 10.5112 | 10.3122 | 10.0673 | 10.2133 | 9.998 | 8.4092 | 6.7663 | 5.2184
MANNINGTON GSP | SHAFTESBURY BSP | SHAFTESBURY | MINIMUM HEADROOM | ST 85605 23325 | YES | 1.741 | -0.58245 | -1.0355 | -1.5324 | -2.0253 | -2.4018 | -3.0457 | -3.71 | -4.3906 | -5.0692 | -5.5559 | -8.1661 | -10.2855 | -11.5773 | 2.2769 | 1.9851 | 1.679 | 1.3535 | 1.1586 | 0.75755 | 0.34224 | -0.10061 | -0.55163 | -0.89143 | -2.8496 | -5.0751 | -10.6435 | -0.65388 | -1.0722 | -1.5171 | -1.9927 | -2.2324 | -2.8069 | -3.4202 | -4.0743 | -4.7273 | -5.1671 | -7.4161 | -9.2539 | -10.3008
|  | SHAFTESBURY | EE |  |  |  | -0.58245 | -1.0355 | -1.5324 | -2.0253 | -2.4018 | -3.0457 | -3.71 | -4.3906 | -5.0692 | -5.5559 | -8.162 | -9.9559 | -11.3212 | 2.2769 | 1.9851 | 1.679 | 1.3535 | 1.1586 | 0.75755 | 0.34224 | -0.10061 | -0.55163 | -0.89143 | -2.8496 | -4.8833 | -7.8302 | -0.65388 | -1.0722 | -1.5171 | -1.9927 | -2.2324 | -2.8069 | -3.4202 | -4.0743 | -4.7273 | -5.1671 | -7.4161 | -8.9457 | -10.0804
|  | SHAFTESBURY | HT |  |  |  | -0.44776 | -0.83551 | -1.2539 | -1.6488 | -2.2069 | -2.8131 | -3.4641 | -3.7457 | -4.3406 | -4.959 | -8.1661 | -10.2855 | -11.5773 | 2.4157 | 2.1984 | 1.9708 | 1.7473 | 1.4535 | 1.1208 | 0.77898 | 0.69122 | 0.36571 | 0.03 | -1.6394 | -2.6516 | -3.2373 | -0.47224 | -0.81816 | -1.1824 | -1.5508 | -2.0182 | -2.5518 | -3.1488 | -3.3406 | -3.8957 | -4.4733 | -7.4039 | -9.2539 | -10.3008
|  | SHAFTESBURY | HE |  |  |  | -0.44469 | -0.80898 | -1.2049 | -1.5988 | -2.1335 | -2.7141 | -3.2702 | -3.4661 | -3.9702 | -4.4855 | -7.2865 | -9.0743 | -9.9508 | 2.3871 | 2.1524 | 1.9065 | 1.6494 | 1.331 | 0.96776 | 0.60959 | 0.49837 | 0.15143 | -0.2149 | -2.3863 | -4.4373 | -7.1761 | -0.47429 | -0.80286 | -1.1427 | -1.5039 | -1.9498 | -2.46 | -2.9722 | -3.0927 | -3.5661 | -4.0549 | -6.5988 | -8.1069 | -8.812
|  | SHAFTESBURY | CF |  |  |  | -0.34061 | -0.61306 | -0.90796 | -1.1865 | -1.6263 | -2.0141 | -2.3059 | -2.5845 | -2.8855 | -2.8192 | -4.6641 | -6.6059 | -8.4376 | 2.4422 | 2.2463 | 2.0433 | 1.8341 | 1.5341 | 1.2565 | 0.98 | 0.69735 | 0.38612 | 0.33714 | -1.771 | -5.0751 | -10.6435 | -0.38143 | -0.62837 | -0.88653 | -1.1457 | -1.5294 | -1.8508 | -2.1294 | -2.411 | -2.7192 | -2.5773 | -4.3253 | -6.0376 | -7.6151
FAWLEY GSP | COWES & WOOTTON COMMON BSP | SHALFLEET | MINIMUM HEADROOM | SZ 40828 88643 | YES | 0.137 | 8.2505 | 8.0607 | 7.8781 | 7.6413 | 7.4372 | 7.174 | 6.8128 | 6.7995 | 6.4658 | 6.2403 | 5.0903 | 4.4628 | 4.0505 | 9.1102 | 8.9796 | 8.8551 | 8.6827 | 8.5255 | 8.3235 | 8.0633 | 8.0765 | 7.8327 | 7.6714 | 6.8051 | 5.7724 | 3.3408 | 8.4245 | 8.2684 | 8.1214 | 7.9071 | 7.7214 | 7.4663 | 7.1255 | 7.1276 | 6.8122 | 6.6041 | 5.5541 | 5.0133 | 4.6673
|  | SHALFLEET | EE |  |  |  | 8.2505 | 8.0607 | 7.8781 | 7.6413 | 7.4372 | 7.174 | 6.8128 | 6.7995 | 6.4658 | 6.2403 | 5.0903 | 4.5413 | 4.223 | 9.1102 | 8.9796 | 8.8551 | 8.6827 | 8.5255 | 8.3235 | 8.0633 | 8.0765 | 7.8327 | 7.6714 | 6.8051 | 6.0071 | 4.8031 | 8.4245 | 8.2684 | 8.1214 | 7.9071 | 7.7214 | 7.4663 | 7.1255 | 7.1276 | 6.8122 | 6.6041 | 5.5541 | 5.0837 | 4.8082
|  | SHALFLEET | HT |  |  |  | 8.3372 | 8.2036 | 8.0474 | 7.9117 | 7.7281 | 7.5219 | 7.2791 | 6.9617 | 6.623 | 6.277 | 5.2036 | 4.4628 | 4.0505 | 9.1908 | 9.1112 | 9.0163 | 8.9367 | 8.8255 | 8.6929 | 8.5561 | 8.3571 | 8.1449 | 7.9204 | 7.3704 | 6.9949 | 6.8082 | 8.4867 | 8.3724 | 8.2398 | 8.1214 | 7.9735 | 7.7939 | 7.5714 | 7.2837 | 6.9786 | 6.651 | 5.6694 | 5.0133 | 4.6673
|  | SHALFLEET | HE |  |  |  | 8.3342 | 8.2097 | 8.0597 | 7.9281 | 7.7556 | 7.5658 | 7.3485 | 7.0607 | 6.7587 | 6.4444 | 5.3923 | 4.8495 | 4.626 | 9.1786 | 9.0939 | 8.9847 | 8.8959 | 8.7704 | 8.6296 | 8.4867 | 8.2806 | 8.0561 | 7.8184 | 7.0092 | 6.1918 | 5.0398 | 8.4857 | 8.3776 | 8.25 | 8.1378 | 7.9969 | 7.8347 | 7.6378 | 7.3755 | 7.101 | 6.8031 | 5.8439 | 5.3724 | 5.1847
|  | SHALFLEET | CF |  |  |  | 8.375 | 8.2587 | 8.1617 | 8.0352 | 7.926 | 7.7832 | 7.623 | 7.4372 | 7.2964 | 7.0985 | 6.4148 | 5.6168 | 4.9362 | 9.199 | 9.1184 | 9.0429 | 8.9418 | 8.8561 | 8.7327 | 8.5898 | 8.4265 | 8.2867 | 8.102 | 7.2418 | 5.7724 | 3.3408 | 8.5184 | 8.4204 | 8.3337 | 8.2255 | 8.1337 | 8.0143 | 7.8857 | 7.7286 | 7.598 | 7.4204 | 6.7776 | 6.0469 | 5.449
FAWLEY GSP | COWES & WOOTTON COMMON BSP | SHANKLIN | MINIMUM HEADROOM | SZ 57809 81912 | YES | 2.756 | 16.1006 | 15.7863 | 15.3996 | 14.9384 | 14.8159 | 14.3353 | 13.5057 | 12.5751 | 11.6496 | 10.9629 | 6.9527 | 3.6333 | 1.7639 | 17.0384 | 16.7976 | 16.4833 | 16.12 | 16.018 | 15.6231 | 15.072 | 14.4353 | 13.7822 | 13.3251 | 10.8404 | 8.3761 | 2.4802 | 15.7996 | 15.4618 | 15.0302 | 14.5455 | 14.4282 | 13.9486 | 13.1771 | 12.3057 | 11.4271 | 10.8088 | 7.3067 | 4.4771 | 2.9894
|  | SHANKLIN | EE |  |  |  | 16.1006 | 15.7863 | 15.3996 | 14.9384 | 14.8159 | 14.3353 | 13.5057 | 12.5751 | 11.6496 | 10.9629 | 7.2914 | 4.4496 | 2.1578 | 17.0384 | 16.7976 | 16.4833 | 16.12 | 16.018 | 15.6231 | 15.072 | 14.4353 | 13.7822 | 13.3251 | 10.8404 | 8.3761 | 4.8833 | 15.7996 | 15.4618 | 15.0302 | 14.5455 | 14.4282 | 13.9486 | 13.1771 | 12.3057 | 11.4271 | 10.8088 | 7.5486 | 5.1945 | 3.3251
|  | SHANKLIN | HT |  |  |  | 16.2476 | 15.9761 | 15.6578 | 15.3547 | 14.9935 | 14.5761 | 14.0802 | 13.2812 | 12.4404 | 11.572 | 6.9527 | 3.6333 | 1.7639 | 17.2098 | 17.0465 | 16.8373 | 16.6476 | 16.4067 | 16.1261 | 15.9537 | 15.5037 | 15.021 | 14.5149 | 12.0282 | 10.5159 | 9.768 | 15.9312 | 15.6924 | 15.4016 | 15.0914 | 14.7078 | 14.271 | 13.871 | 13.1159 | 12.3302 | 11.5139 | 7.3067 | 4.4771 | 2.9894
|  | SHANKLIN | HE |  |  |  | 16.2557 | 16.0139 | 15.7241 | 15.4476 | 15.121 | 14.7588 | 14.4322 | 13.818 | 13.172 | 12.4996 | 8.7129 | 5.8465 | 4.4527 | 17.1843 | 17.0047 | 16.7782 | 16.5639 | 16.2955 | 15.9996 | 15.8394 | 15.422 | 14.9547 | 14.4567 | 11.6618 | 9.1394 | 5.9731 | 15.9384 | 15.7241 | 15.4588 | 15.1751 | 14.8271 | 14.4445 | 14.1945 | 13.5914 | 12.9731 | 12.3282 | 8.8853 | 6.5271 | 5.4302
|  | SHANKLIN | CF |  |  |  | 16.3873 | 16.2384 | 16.0924 | 15.8965 | 15.718 | 15.4884 | 15.2251 | 14.9118 | 14.9465 | 14.6639 | 12.4027 | 9.6822 | 7.1047 | 17.2496 | 17.1037 | 16.9506 | 16.7557 | 16.5649 | 16.3088 | 16.0129 | 15.67 | 15.5965 | 15.2486 | 12.6863 | 8.819 | 2.4802 | 16.0506 | 15.9241 | 15.7935 | 15.6016 | 15.4098 | 15.1639 | 14.8894 | 14.5639 | 14.6139 | 14.319 | 12.1618 | 9.7384 | 7.4873
AXMINSTER | YEOVIL BSP | SHERBORNE | MINIMUM HEADROOM | ST 63978 18163 | YES | 1.211 | 5.0779 | 4.8003 | 4.6554 | 4.5126 | 4.234 | 3.8524 | 3.5197 | 2.8452 | 1.9963 | 1.2106 | -1.8731 | -4.0925 | -5.2833 | 7.41 | 7.1345 | 6.8958 | 6.6866 | 6.36 | 6.0233 | 5.9672 | 5.5233 | 5.0049 | 4.556 | 2.56 | 0.74984 | -3.2461 | 5.8702 | 5.5631 | 5.2753 | 5.0304 | 4.6172 | 4.2192 | 4.0723 | 3.4539 | 2.7029 | 2.0651 | -0.49098 | -2.4706 | -3.4767
|  | SHERBORNE | EE |  |  |  | 5.0779 | 4.8003 | 4.6554 | 4.5126 | 4.234 | 3.8524 | 3.5197 | 2.8452 | 1.9963 | 1.2106 | -1.8456 | -3.8017 | -5.1231 | 7.41 | 7.1345 | 6.8958 | 6.6866 | 6.36 | 6.0233 | 5.9672 | 5.5233 | 5.0049 | 4.556 | 2.56 | 0.74984 | -1.5185 | 5.8702 | 5.5631 | 5.2753 | 5.0304 | 4.6172 | 4.2192 | 4.0723 | 3.4539 | 2.7029 | 2.0651 | -0.47567 | -2.2053 | -3.3349
|  | SHERBORNE | HT |  |  |  | 5.1483 | 4.8932 | 4.7789 | 4.6677 | 4.4248 | 4.2514 | 3.7269 | 3.0901 | 2.2565 | 1.6871 | -1.8731 | -4.0925 | -5.2833 | 7.509 | 7.2631 | 7.158 | 7.0641 | 6.8233 | 6.657 | 6.3294 | 5.96 | 5.4968 | 5.3356 | 3.4662 | 2.3529 | 1.8641 | 6.0182 | 5.7641 | 5.5549 | 5.3804 | 5.0304 | 4.81 | 4.2784 | 3.6947 | 2.9519 | 2.6529 | -0.49098 | -2.4706 | -3.4767
|  | SHERBORNE | HE |  |  |  | 5.1452 | 4.8912 | 4.7759 | 4.6636 | 4.4718 | 4.2748 | 3.8759 | 3.3095 | 2.5401 | 2.0299 | -1.0782 | -2.9466 | -3.7201 | 7.4886 | 7.2253 | 7.1009 | 6.9896 | 6.7723 | 6.5825 | 6.2519 | 5.8774 | 5.4049 | 5.1825 | 3.0437 | 1.2468 | -0.78384 | 6.0131 | 5.7702 | 5.5692 | 5.409 | 5.106 | 4.8927 | 4.4182 | 3.8917 | 3.207 | 2.9651 | 0.23657 | -1.4063 | -2.0461
|  | SHERBORNE | CF |  |  |  | 5.2116 | 5.0034 | 4.9432 | 4.884 | 4.7626 | 4.682 | 4.4983 | 4.3177 | 3.8279 | 3.2493 | 1.2503 | -0.5721 | -2.1466 | 7.5284 | 7.2856 | 7.1937 | 7.107 | 6.9529 | 6.8009 | 6.5509 | 6.2958 | 5.9243 | 5.5049 | 3.6243 | 0.90086 | -3.2461 | 6.0825 | 5.8753 | 5.7825 | 5.6876 | 5.4764 | 5.3253 | 5.0447 | 4.7958 | 4.3509 | 3.8417 | 2.2172 | 0.67433 | -0.71649
MINETY GSP | CIRENCESTER BSP | SHIPTON OLIFFE | MINIMUM HEADROOM | SP 03884 19102 | YES | 0.756 | 0.86571 | 0.78102 | 0.70755 | 0.61061 | 0.49939 | 0.41265 | 0.27694 | 0.11265 | -0.034286 | -0.17306 | -0.87 | -1.1486 | -1.3088 | 1.6886 | 1.6243 | 1.5702 | 1.5018 | 1.4141 | 1.3559 | 1.2508 | 1.1294 | 1.0406 | 0.97327 | 0.52837 | 0.19673 | -0.72673 | 1.1045 | 1.0269 | 0.95551 | 0.86673 | 0.75857 | 0.6851 | 0.54633 | 0.37592 | 0.22184 | 0.090204 | -0.55878 | -0.82408 | -0.97306
|  | SHIPTON OLIFFE | EE |  |  |  | 0.86571 | 0.78102 | 0.70755 | 0.61061 | 0.49939 | 0.41265 | 0.27694 | 0.11265 | -0.034286 | -0.17306 | -0.7251 | -0.86082 | -0.90673 | 1.6886 | 1.6243 | 1.5702 | 1.5018 | 1.4141 | 1.3559 | 1.2508 | 1.1294 | 1.0406 | 0.97327 | 0.63449 | 0.34265 | -0.10122 | 1.1045 | 1.0269 | 0.95551 | 0.86673 | 0.75857 | 0.6851 | 0.54633 | 0.37592 | 0.22184 | 0.090204 | -0.42204 | -0.54551 | -0.58735
|  | SHIPTON OLIFFE | HT |  |  |  | 0.90653 | 0.84939 | 0.78714 | 0.70347 | 0.6402 | 0.55959 | 0.44837 | 0.3402 | 0.20245 | 0.057551 | -0.6302 | -0.92306 | -1.1027 | 1.7212 | 1.6876 | 1.6467 | 1.5947 | 1.5539 | 1.5008 | 1.4294 | 1.3702 | 1.2876 | 1.1804 | 0.69673 | 0.50082 | 0.38143 | 1.1412 | 1.0882 | 1.03 | 0.95755 | 0.89633 | 0.82286 | 0.71776 | 0.61469 | 0.47184 | 0.32082 | -0.33735 | -0.60571 | -0.77
|  | SHIPTON OLIFFE | HE |  |  |  | 0.90347 | 0.84837 | 0.78612 | 0.70551 | 0.64224 | 0.54327 | 0.42388 | 0.2902 | 0.13306 | -0.029184 | -0.87 | -1.1486 | -1.3088 | 1.7182 | 1.6773 | 1.6335 | 1.5784 | 1.5314 | 1.4722 | 1.3927 | 1.3304 | 1.2314 | 1.1049 | 0.52837 | 0.32633 | -0.076735 | 1.1382 | 1.0871 | 1.03 | 0.95857 | 0.89735 | 0.81673 | 0.69735 | 0.56163 | 0.39939 | 0.23102 | -0.55878 | -0.82408 | -0.97306
|  | SHIPTON OLIFFE | CF |  |  |  | 0.92082 | 0.87898 | 0.82898 | 0.77286 | 0.71061 | 0.66878 | 0.60653 | 0.52694 | 0.43816 | 0.38714 | -0.20673 | -0.74857 | -1.1373 | 1.7314 | 1.6978 | 1.659 | 1.612 | 1.5661 | 1.5273 | 1.4712 | 1.3978 | 1.3182 | 1.2671 | 0.79163 | 0.19673 | -0.72673 | 1.1545 | 1.1167 | 1.0698 | 1.0178 | 0.96265 | 0.9198 | 0.86469 | 0.78918 | 0.70551 | 0.65347 | 0.062653 | -0.44959 | -0.81082
NURSLING GSP | SOUTHAMPTON (2 X 90) | SHIRLEY | MINIMUM HEADROOM | SU 39988 13808 | YES | 0.432 | 14.4051 | 13.9224 | 13.3112 | 12.9388 | 12.25 | 11.4827 | 10.3061 | 9.0112 | 7.7286 | 6.748 | 1.5704 | -2.9592 | -5.5245 | 14.1908 | 13.7541 | 13.1776 | 12.8663 | 12.2194 | 11.4959 | 10.5745 | 9.5245 | 8.4602 | 7.6378 | 2.9347 | -4.2398 | -20.7541 | 13.7031 | 13.2327 | 12.6061 | 12.3163 | 11.6347 | 10.8735 | 9.7663 | 8.5204 | 7.2878 | 6.3857 | 1.9 | -1.8714 | -3.9643
|  | SHIRLEY | EE |  |  |  | 14.4051 | 13.9224 | 13.3112 | 12.9388 | 12.25 | 11.4827 | 10.3061 | 9.0112 | 7.7286 | 6.748 | 1.5704 | -2.0969 | -5.1102 | 14.1908 | 13.7541 | 13.1776 | 12.8663 | 12.2194 | 11.4959 | 10.5745 | 9.5245 | 8.4602 | 7.6378 | 2.9347 | -2.4214 | -11.0112 | 13.7031 | 13.2327 | 12.6061 | 12.3163 | 11.6347 | 10.8735 | 9.7663 | 8.5204 | 7.2878 | 6.3857 | 1.9 | -1.1194 | -3.6429
|  | SHIRLEY | HT |  |  |  | 14.7388 | 14.3837 | 13.9439 | 13.4765 | 12.9255 | 12.3286 | 11.6847 | 10.6367 | 9.5378 | 8.3704 | 1.8327 | -2.9592 | -5.5245 | 14.4694 | 14.2816 | 13.9806 | 13.6459 | 13.2306 | 12.7673 | 12.5255 | 11.8827 | 11.202 | 10.4704 | 6.7429 | 4.401 | 3.2949 | 14.0694 | 13.7316 | 13.2949 | 12.8653 | 12.3276 | 11.7347 | 11.2173 | 10.2439 | 9.2173 | 8.1296 | 2.2418 | -1.8714 | -3.9643
|  | SHIRLEY | HE |  |  |  | 14.702 | 14.3592 | 13.9408 | 13.501 | 12.9898 | 12.3939 | 11.8357 | 10.9163 | 9.9551 | 8.9633 | 3.5276 | -0.20714 | -1.8265 | 14.4051 | 14.1469 | 13.7429 | 13.3337 | 12.8347 | 12.2582 | 11.8633 | 11.1122 | 10.3041 | 9.4378 | 4.1867 | -1.3735 | -9.4684 | 14.0367 | 13.7153 | 13.302 | 12.8939 | 12.3929 | 11.8133 | 11.3786 | 10.5194 | 9.6194 | 8.6867 | 3.699 | 0.63673 | -0.68878
|  | SHIRLEY | CF |  |  |  | 14.9061 | 14.6704 | 14.452 | 14.1796 | 13.9194 | 13.5959 | 13.2265 | 13.0816 | 12.6357 | 12.1694 | 8.8235 | 5.0316 | 1.4847 | 14.4847 | 14.2806 | 13.9786 | 13.6153 | 13.2398 | 12.7469 | 12.1643 | 11.7776 | 11.0908 | 10.348 | 4.9184 | -4.2398 | -20.7541 | 14.2112 | 13.9673 | 13.7398 | 13.4531 | 13.2041 | 12.8684 | 12.4918 | 12.4592 | 12.0184 | 11.5551 | 8.352 | 4.9786 | 1.952
MINETY GSP | STRATTON (2 X 60) | SHRIVENHAM | MINIMUM HEADROOM | SU 23782 87902 | YES | 0.366 | 8.6832 | 8.3954 | 8.2087 | 7.9974 | 7.723 | 7.4842 | 7.1617 | 6.8026 | 6.4403 | 6.4985 | 5.5566 | 4.8352 | 4.3872 | 10.9143 | 10.7918 | 10.6755 | 10.5337 | 10.351 | 10.1949 | 9.9735 | 9.7204 | 9.4571 | 9.5755 | 8.8663 | 8.049 | 6.0857 | 8.8724 | 8.6265 | 8.4531 | 8.2449 | 7.9898 | 7.7755 | 7.4714 | 7.1265 | 6.7806 | 6.8867 | 6.0306 | 5.3888 | 5.0082
|  | SHRIVENHAM | EE |  |  |  | 8.6832 | 8.3954 | 8.2087 | 7.9974 | 7.723 | 7.4842 | 7.1617 | 6.8026 | 6.4403 | 6.5474 | 5.5699 | 4.9434 | 4.4842 | 10.9143 | 10.7918 | 10.6755 | 10.5337 | 10.351 | 10.1949 | 9.9735 | 9.7204 | 9.4571 | 9.5755 | 8.8663 | 8.1694 | 7.1357 | 8.8724 | 8.6265 | 8.4531 | 8.2449 | 7.9898 | 7.7755 | 7.4714 | 7.1265 | 6.7806 | 6.9633 | 6.0378 | 5.4867 | 5.0908
|  | SHRIVENHAM | HT |  |  |  | 8.7505 | 8.4883 | 8.327 | 8.1077 | 7.9107 | 7.675 | 7.3923 | 7.124 | 6.8138 | 6.4985 | 5.5566 | 4.8352 | 4.3872 | 10.9663 | 10.8816 | 10.802 | 10.6735 | 10.5622 | 10.4224 | 10.2582 | 10.1133 | 9.9286 | 9.7327 | 9.2316 | 8.9418 | 8.7582 | 8.9276 | 8.7102 | 8.5643 | 8.3643 | 8.1796 | 7.9653 | 7.7041 | 7.4653 | 7.1827 | 6.8867 | 6.0306 | 5.3888 | 5.0082
|  | SHRIVENHAM | HE |  |  |  | 8.7587 | 8.4934 | 8.3413 | 8.1689 | 8.023 | 7.7964 | 7.5495 | 7.3168 | 7.0403 | 6.7566 | 5.826 | 5.1821 | 4.8526 | 10.9622 | 10.8612 | 10.7684 | 10.6582 | 10.5633 | 10.4163 | 10.251 | 10.0939 | 9.8969 | 9.7 | 8.9878 | 8.2633 | 7.2755 | 8.9357 | 8.7143 | 8.5765 | 8.4204 | 8.2827 | 8.0755 | 7.85 | 7.6398 | 7.3908 | 7.1347 | 6.2714 | 5.699 | 5.4173
|  | SHRIVENHAM | CF |  |  |  | 8.8026 | 8.5913 | 8.477 | 8.3607 | 8.1923 | 8.0485 | 7.9066 | 7.7372 | 7.5628 | 7.4291 | 6.5158 | 6.1107 | 5.4403 | 10.9898 | 10.9061 | 10.8265 | 10.7408 | 10.6204 | 10.5092 | 10.3796 | 10.2296 | 10.0724 | 9.9408 | 8.9929 | 8.049 | 6.0857 | 8.9755 | 8.8061 | 8.702 | 8.5969 | 8.4459 | 8.3112 | 8.1786 | 8.0276 | 7.8694 | 7.7531 | 6.8622 | 6.5388 | 5.9296
MANNINGTON GSP | SHAFTESBURY BSP | SHROTON | MINIMUM HEADROOM | ST 85356 13659 | YES | 0.692 | 11.0492 | 10.1522 | 9.6788 | 9.1216 | 8.3829 | 8.0829 | 7.5492 | 6.9512 | 6.3512 | 5.9533 | 3.8645 | 2.191 | 1.142 | 11.418 | 10.6516 | 10.4435 | 10.2037 | 9.8812 | 9.7169 | 9.4108 | 9.0608 | 8.7057 | 8.4404 | 6.8424 | 5.0731 | 0.65367 | 10.5237 | 9.6798 | 9.2788 | 8.8084 | 8.1635 | 7.891 | 7.4022 | 6.8543 | 6.3073 | 5.9329 | 3.9655 | 2.5492 | 1.6829
|  | SHROTON | EE |  |  |  | 11.0492 | 10.1522 | 9.6788 | 9.1216 | 8.3829 | 8.0829 | 7.5492 | 6.9512 | 6.3512 | 5.9533 | 3.8645 | 2.3778 | 1.3635 | 11.418 | 10.6516 | 10.4435 | 10.2037 | 9.8812 | 9.7169 | 9.4108 | 9.0608 | 8.7057 | 8.4404 | 6.8424 | 5.2312 | 2.9251 | 10.5237 | 9.6798 | 9.2788 | 8.8084 | 8.1635 | 7.891 | 7.4022 | 6.8543 | 6.3073 | 5.9329 | 3.9655 | 2.7257 | 1.8727
|  | SHROTON | HT |  |  |  | 11.1982 | 10.3573 | 9.9553 | 9.4931 | 8.9084 | 8.2533 | 7.7318 | 7.5084 | 7.0135 | 6.5073 | 3.9002 | 2.191 | 1.142 | 11.4843 | 10.7506 | 10.5833 | 10.3894 | 10.1465 | 9.871 | 9.6557 | 9.5649 | 9.3476 | 9.1139 | 7.8098 | 7.0312 | 6.5588 | 10.64 | 9.84 | 9.488 | 9.0808 | 8.5767 | 8.0012 | 7.5359 | 7.3512 | 6.8859 | 6.4114 | 4.0155 | 2.5492 | 1.6829
|  | SHROTON | HE |  |  |  | 11.1982 | 10.3767 | 9.989 | 9.539 | 8.9716 | 8.338 | 7.89 | 7.7471 | 7.3318 | 6.8931 | 4.488 | 3.0635 | 2.388 | 11.471 | 10.7322 | 10.5506 | 10.3435 | 10.0822 | 9.7914 | 9.568 | 9.4771 | 9.2139 | 8.919 | 7.1629 | 5.5598 | 3.3935 | 10.641 | 9.8563 | 9.5155 | 9.1237 | 8.6369 | 8.0808 | 7.6839 | 7.5665 | 7.1727 | 6.7727 | 4.5716 | 3.3655 | 2.8094
|  | SHROTON | CF |  |  |  | 11.3512 | 10.5441 | 10.242 | 9.8992 | 9.4155 | 8.9614 | 8.7349 | 8.4533 | 8.1512 | 8.2706 | 6.6155 | 5.0604 | 3.589 | 11.5833 | 10.7976 | 10.6486 | 10.4802 | 10.2486 | 10.022 | 9.8741 | 9.6496 | 9.3955 | 9.371 | 7.6904 | 5.0731 | 0.65367 | 10.792 | 10.0124 | 9.7512 | 9.4522 | 9.04 | 8.6573 | 8.4543 | 8.2176 | 7.9655 | 8.0451 | 6.5431 | 5.1033 | 3.7931
LALEHAM | STAINES | SIDNEY ROAD | MINIMUM HEADROOM | TQ 04100 71760 | YES | 5.028 | 12.3633 | 11.8949 | 11.3867 | 10.8928 | 10.7377 | 10.3092 | 9.6643 | 8.9418 | 8.1918 | 7.6459 | 4.4398 | 1.7745 | 0.25101 | 14.4684 | 14.1347 | 13.7786 | 13.4071 | 13.2837 | 12.9306 | 12.4704 | 11.9469 | 11.4102 | 10.9959 | 8.4377 | 4.7357 | -3.5949 | 12.2694 | 11.8337 | 11.3633 | 10.8735 | 10.7367 | 10.299 | 9.6745 | 8.9663 | 8.2633 | 7.7622 | 5.0265 | 2.751 | 1.5133
|  | SIDNEY ROAD | EE |  |  |  | 12.3633 | 11.8949 | 11.3867 | 10.8928 | 10.7377 | 10.3092 | 9.6643 | 8.9418 | 8.1918 | 7.6459 | 4.6184 | 2.2867 | 0.46733 | 14.4684 | 14.1347 | 13.7786 | 13.4071 | 13.2837 | 12.9306 | 12.4704 | 11.9469 | 11.4102 | 10.9959 | 8.4377 | 5.502 | 1.0316 | 12.2694 | 11.8337 | 11.3633 | 10.8735 | 10.7367 | 10.299 | 9.6745 | 8.9663 | 8.2633 | 7.7622 | 5.1224 | 3.2092 | 1.6959
|  | SIDNEY ROAD | HT |  |  |  | 12.5153 | 12.103 | 11.6592 | 11.2867 | 10.9102 | 10.5092 | 9.8704 | 9.5337 | 8.8847 | 8.2184 | 4.4398 | 1.7745 | 0.25101 | 14.6347 | 14.3969 | 14.149 | 13.9408 | 13.7092 | 13.4551 | 13.1082 | 12.9949 | 12.6377 | 12.2612 | 10.302 | 9.0633 | 8.3908 | 12.4377 | 12.0724 | 11.6877 | 11.3377 | 10.9735 | 10.5775 | 9.9796 | 9.703 | 9.0898 | 8.4561 | 5.0265 | 2.751 | 1.5133
|  | SIDNEY ROAD | HE |  |  |  | 12.5153 | 12.1235 | 11.6969 | 11.35 | 11.001 | 10.6275 | 10.102 | 9.8796 | 9.351 | 8.803 | 5.7173 | 3.453 | 2.3918 | 14.5888 | 14.3163 | 14.0275 | 13.7714 | 13.4928 | 13.1857 | 12.799 | 12.6418 | 12.2275 | 11.7867 | 9.049 | 6.0959 | 1.9398 | 12.4357 | 12.0888 | 11.7214 | 11.3959 | 11.0561 | 10.6898 | 10.1908 | 10.0122 | 9.5051 | 8.9775 | 6.1796 | 4.3071 | 3.451
|  | SIDNEY ROAD | CF |  |  |  | 12.6684 | 12.4367 | 12.1612 | 11.9408 | 11.7153 | 11.4306 | 11.1867 | 10.9265 | 10.9786 | 10.749 | 8.8133 | 6.651 | 4.5316 | 14.6643 | 14.4571 | 14.2245 | 14.002 | 13.7765 | 13.4765 | 13.1561 | 12.7908 | 12.6684 | 12.2969 | 9.4745 | 4.7357 | -3.5949 | 12.5724 | 12.3622 | 12.1245 | 11.9082 | 11.6959 | 11.4235 | 11.1806 | 10.9102 | 10.9704 | 10.7255 | 8.8622 | 6.9245 | 5.1357
NURSLING GSP | ROWNHAMS | SILKSTEAD | MINIMUM HEADROOM | SU 44578 24565 | YES | 1.185 | 4.7306 | 3.9378 | 2.9653 | 1.8296 | 0.53776 | -0.88163 | -2.4408 | -4.1827 | -5.9418 | -7.3898 | -16.8204 | -21.0061 | -21.4214 | 6.6082 | 6.0041 | 5.2633 | 4.399 | 3.4112 | 2.3286 | 1.1551 | -0.15204 | -1.4776 | -2.5633 | -9.6816 | -12.7837 | -13.1092 | 5.0184 | 4.2735 | 3.3367 | 2.2398 | 0.99388 | -0.37857 | -1.8806 | -3.5541 | -5.2469 | -6.6378 | -15.7143 | -19.7194 | -20.098
|  | SILKSTEAD | EE |  |  |  | 4.7306 | 3.9378 | 2.9653 | 1.8296 | 0.53776 | -0.88163 | -2.4408 | -4.1827 | -5.9418 | -7.3898 | -11.8194 | -12.6337 | -13.0163 | 6.6082 | 6.0041 | 5.2633 | 4.399 | 3.4112 | 2.3286 | 1.1551 | -0.15204 | -1.4776 | -2.5633 | -5.7786 | -6.2653 | -6.5082 | 5.0184 | 4.2735 | 3.3367 | 2.2398 | 0.99388 | -0.37857 | -1.8806 | -3.5541 | -5.2469 | -6.6378 | -10.8673 | -11.6061 | -11.9398
|  | SILKSTEAD | HT |  |  |  | 5.2622 | 4.9561 | 4.5806 | 3.9918 | 3.2327 | 2.3531 | 1.348 | 0.10918 | -1.2133 | -2.5888 | -8.4082 | -11.0541 | -11.5031 | 7.1622 | 6.9704 | 6.5551 | 6.0724 | 5.5 | 4.8327 | 4.0918 | 3.1745 | 2.1918 | 1.1684 | -3.0939 | -4.9551 | -5.1949 | 5.699 | 5.4 | 4.952 | 4.3337 | 3.6031 | 2.7531 | 1.7898 | 0.6 | -0.67041 | -1.9898 | -7.5612 | -10.0714 | -10.4735
|  | SILKSTEAD | HE |  |  |  | 5.099 | 4.5908 | 3.7439 | 2.748 | 1.5653 | 0.18163 | -1.3337 | -3.2306 | -5.2633 | -7.2714 | -16.8204 | -21.0061 | -21.4214 | 7.0276 | 6.5082 | 5.8643 | 5.1092 | 4.2041 | 3.15 | 2.0071 | 0.57041 | -0.96939 | -2.4888 | -9.6816 | -12.7837 | -13.1092 | 5.4663 | 4.9071 | 4.0918 | 3.1306 | 1.9898 | 0.65306 | -0.80816 | -2.6357 | -4.5939 | -6.5276 | -15.7143 | -19.7194 | -20.098
|  | SILKSTEAD | CF |  |  |  | 5.3776 | 5.1561 | 4.8755 | 4.4367 | 3.8194 | 3.1 | 2.3724 | 1.3969 | 0.3 | -0.86939 | -7.55 | -13.1694 | -15.95 | 7.2092 | 7.0388 | 6.7949 | 6.3806 | 5.9051 | 5.3541 | 4.7969 | 4.0469 | 3.2041 | 2.3031 | -2.7918 | -7.0469 | -9.1796 | 5.8051 | 5.5888 | 5.2143 | 4.7561 | 4.1612 | 3.4653 | 2.7612 | 1.8214 | 0.7602 | -0.37041 | -6.8051 | -12.199 | -14.8459
BRAMLEY (FLEE) | READING BSP | SILVER STREET | MINIMUM HEADROOM | SU 71957 72821 | YES | 2.712 | 8.9784 | 8.4651 | 7.8478 | 6.96 | 5.9947 | 5.0427 | 3.761 | 2.2049 | 1.309 | 0.35184 | -2.2961 | -4.2308 | -4.2073 | 13.9702 | 13.5682 | 13.0437 | 12.3478 | 11.5906 | 10.7896 | 9.7957 | 8.5998 | 7.7865 | 6.911 | 3.0998 | -2.6584 | -16.6104 | 9.3865 | 8.9029 | 8.3161 | 7.4927 | 6.5651 | 5.6457 | 4.4212 | 2.9376 | 1.9978 | 1.0498 | -1.641 | -3.4441 | -3.4033
|  | SILVER STREET | EE |  |  |  | 8.9784 | 8.4651 | 7.8478 | 6.96 | 5.9947 | 5.0427 | 3.761 | 2.2049 | 1.309 | 0.35184 | -2.2961 | -3.442 | -3.2829 | 13.9702 | 13.5682 | 13.0437 | 12.3478 | 11.5906 | 10.7896 | 9.7957 | 8.5998 | 7.7865 | 6.911 | 3.0998 | -0.79102 | -7.2339 | 9.3865 | 8.9029 | 8.3161 | 7.4927 | 6.5651 | 5.6457 | 4.4212 | 2.9376 | 1.9978 | 1.0498 | -1.641 | -2.7196 | -2.5941
|  | SILVER STREET | HT |  |  |  | 9.2661 | 8.8835 | 8.3773 | 7.6692 | 6.8865 | 6.06 | 4.8631 | 3.662 | 2.7059 | 1.7171 | -1.8308 | -4.2308 | -4.2073 | 14.0998 | 13.9488 | 13.6947 | 13.2345 | 12.7396 | 12.1906 | 11.4549 | 10.6773 | 9.9957 | 9.2865 | 6.6039 | 4.912 | 4.7447 | 9.661 | 9.3018 | 8.8314 | 8.1763 | 7.4437 | 6.66 | 5.5478 | 4.4029 | 3.4855 | 2.5355 | -1.1073 | -3.4441 | -3.4033
|  | SILVER STREET | HE |  |  |  | 9.2437 | 8.8763 | 8.4488 | 7.7988 | 7.0876 | 6.4222 | 5.5141 | 4.4396 | 3.4651 | 2.6202 | 0.5549 | -0.45939 | -0.61449 | 14.0682 | 13.8947 | 13.5314 | 13.0263 | 12.4671 | 11.8937 | 11.1824 | 10.3447 | 9.5141 | 8.711 | 5.1355 | 1.1467 | -5.2573 | 9.6376 | 9.2947 | 8.8865 | 8.2855 | 7.6161 | 6.9763 | 6.1182 | 5.0927 | 4.1631 | 3.3478 | 1.109 | 0.092653 | -0.020612
|  | SILVER STREET | CF |  |  |  | 9.4131 | 9.1702 | 8.8631 | 8.3947 | 7.8345 | 7.5427 | 7.2753 | 6.8437 | 6.3039 | 5.7896 | 2.4508 | 0.59571 | -1.4227 | 14.1529 | 14.0222 | 13.7447 | 13.3212 | 12.8212 | 12.4039 | 11.9263 | 11.3182 | 10.6212 | 9.9039 | 4.8018 | -2.6584 | -16.6104 | 9.81 | 9.5957 | 9.3151 | 8.8906 | 8.3824 | 8.0947 | 7.8396 | 7.4376 | 6.9314 | 6.4304 | 3.212 | 1.2273 | -0.7951
MANNINGTON GSP | CHRISTCHURCH BSP | SOMERFORD | MINIMUM HEADROOM | SZ 18262 93590 | YES | 6.723 | 3.0384 | 2.1353 | 1.4343 | 0.29347 | -0.98306 | -1.9392 | -3.2524 | -4.7718 | -6.3045 | -7.4208 | -14.1259 | -19.3382 | -22.2035 | 7.7914 | 7.171 | 6.7333 | 5.9853 | 5.1333 | 4.4098 | 3.4955 | 2.419 | 1.271 | 0.44653 | -4.2739 | -10.8902 | -26.2504 | 4.0159 | 3.2129 | 2.6271 | 1.6241 | 0.49653 | -0.41878 | -1.6933 | -3.1371 | -4.5759 | -5.5912 | -11.3433 | -15.9422 | -18.4137
|  | SOMERFORD | EE |  |  |  | 3.0384 | 2.1353 | 1.4343 | 0.29347 | -0.98306 | -1.9392 | -3.2524 | -4.7718 | -6.3045 | -7.4208 | -13.2973 | -18.0667 | -21.7188 | 7.7914 | 7.171 | 6.7333 | 5.9853 | 5.1333 | 4.4098 | 3.4955 | 2.419 | 1.271 | 0.44653 | -4.2739 | -9.7973 | -18.0137 | 4.0159 | 3.2129 | 2.6271 | 1.6241 | 0.49653 | -0.41878 | -1.6933 | -3.1371 | -4.5759 | -5.5912 | -10.7545 | -14.8453 | -18.0229
|  | SOMERFORD | HT |  |  |  | 3.3067 | 2.522 | 1.5557 | 0.43837 | -0.41265 | -1.2392 | -2.4647 | -3.7943 | -5.1749 | -6.5933 | -14.1259 | -19.3382 | -22.2035 | 8.0904 | 7.668 | 7.1322 | 6.521 | 6.1547 | 5.6904 | 5.0567 | 4.3414 | 3.5863 | 2.8016 | -1.1545 | -3.5137 | -4.7402 | 4.2873 | 3.6067 | 2.7669 | 1.7914 | 1.0935 | 0.33735 | -0.77388 | -1.9841 | -3.2443 | -4.5371 | -11.3433 | -15.9422 | -18.4137
|  | SOMERFORD | HE |  |  |  | 3.3353 | 2.6098 | 1.7057 | 0.65163 | -0.13714 | -0.88714 | -1.8147 | -2.8371 | -3.9035 | -5.0188 | -11.129 | -15.9218 | -18.1729 | 8.0271 | 7.5527 | 6.9445 | 6.2659 | 5.8088 | 5.2455 | 4.5751 | 3.8078 | 2.9802 | 2.0996 | -3.1953 | -8.8269 | -16.4718 | 4.3118 | 3.6822 | 2.8935 | 1.9782 | 1.3343 | 0.64245 | -0.20755 | -1.1535 | -2.1382 | -3.1647 | -8.7422 | -12.9045 | -14.8392
|  | SOMERFORD | CF |  |  |  | 3.6037 | 3.0802 | 2.4853 | 1.7445 | 1.2261 | 0.77 | 0.44449 | 0.04551 | -0.37184 | -0.81878 | -4.7678 | -9.3422 | -13.7504 | 8.1506 | 7.7353 | 7.2731 | 6.7149 | 6.3251 | 5.8343 | 5.32 | 4.7047 | 4.0588 | 3.3567 | -1.9729 | -10.8902 | -26.2504 | 4.5547 | 4.1088 | 3.6027 | 2.97 | 2.5659 | 2.1445 | 1.8424 | 1.4649 | 1.0639 | 0.6251 | -3.1545 | -7.2708 | -11.0402
LOVEDEAN GSP | CHICHESTER & HUNSTON | SOUTH BERSTED | MINIMUM HEADROOM | SU 94025 00705 | YES | 9.481 | 3.2029 | 2.6876 | 2.4192 | 14.8896 | 14.309 | 13.6886 | 12.5212 | 11.2049 | 9.8927 | 8.9284 | 3.0682 | -1.8502 | -4.8451 | 7.2876 | 6.8876 | 6.6784 | 18.7222 | 18.1712 | 17.5671 | 16.7345 | 15.7722 | 14.7927 | 14.112 | 10.2049 | 5.1437 | -7.5665 | 3.4212 | 2.8784 | 2.6365 | 15.0702 | 14.4437 | 13.7641 | 12.6559 | 11.4049 | 10.1569 | 9.3008 | 4.609 | 0.59878 | -1.8104
|  | SOUTH BERSTED | EE |  |  |  | 3.2029 | 2.6876 | 2.4192 | 14.8896 | 14.309 | 13.6886 | 12.5212 | 11.2049 | 9.8927 | 8.9284 | 3.5784 | -0.79714 | -4.2767 | 7.2876 | 6.8876 | 6.6784 | 18.7222 | 18.1712 | 17.5671 | 16.7345 | 15.7722 | 14.7927 | 14.112 | 10.2049 | 5.6518 | -1.2655 | 3.4212 | 2.8784 | 2.6365 | 15.0702 | 14.4437 | 13.7641 | 12.6559 | 11.4049 | 10.1569 | 9.3008 | 4.8447 | 1.4284 | -1.4308
|  | SOUTH BERSTED | HT |  |  |  | 3.4029 | 2.9876 | 2.5498 | 15.0539 | 14.5151 | 14.3151 | 13.2712 | 12.1508 | 10.9906 | 9.8029 | 3.0682 | -1.8502 | -4.8451 | 7.511 | 7.2722 | 7.0151 | 19.2069 | 18.8396 | 18.7957 | 18.2396 | 17.611 | 16.9467 | 16.2518 | 12.7478 | 10.5824 | 9.3039 | 3.6886 | 3.2937 | 2.8631 | 15.358 | 14.8059 | 14.6814 | 13.7427 | 12.7161 | 11.6406 | 10.5284 | 4.609 | 0.59878 | -1.8104
|  | SOUTH BERSTED | HE |  |  |  | 3.4151 | 3.0406 | 2.6447 | 15.1896 | 14.6947 | 14.5447 | 13.7131 | 12.8008 | 11.8549 | 10.8896 | 5.359 | 1.0212 | -1.2461 | 7.4559 | 7.1712 | 6.859 | 18.9927 | 18.5712 | 18.4192 | 17.8498 | 17.1814 | 16.4508 | 15.6722 | 11.1886 | 6.5427 | 0.12837 | 3.6906 | 3.3284 | 2.9324 | 15.4631 | 14.9488 | 14.8651 | 14.0988 | 13.2365 | 12.3345 | 11.4049 | 6.4967 | 3.111 | 1.3263
|  | SOUTH BERSTED | CF |  |  |  | 3.6467 | 3.4273 | 3.209 | 15.9559 | 15.6794 | 15.3835 | 15.3988 | 15.062 | 14.6927 | 14.309 | 10.8876 | 6.9151 | 2.7722 | 7.5784 | 7.3406 | 7.0947 | 19.308 | 18.9763 | 18.5773 | 18.3998 | 17.908 | 17.3763 | 16.7702 | 12.3018 | 5.1437 | -7.5665 | 3.9029 | 3.6784 | 3.4376 | 16.1569 | 15.8467 | 15.51 | 15.5865 | 15.2161 | 14.809 | 14.3835 | 11.1263 | 7.6998 | 4.3722
MANNINGTON GSP | CHRISTCHURCH BSP | SOUTHBOURNE | MINIMUM HEADROOM | SZ 13563 92074 | YES | 4.015 | 4.8816 | 4.4102 | 3.7969 | 3.5765 | 2.951 | 2.2704 | 1.1776 | -0.061224 | -1.2949 | -2.1857 | -5.9959 | -8.8388 | -9.498 | 8.5031 | 8.0939 | 7.55 | 7.3194 | 6.7388 | 6.1071 | 5.2653 | 4.2888 | 3.2969 | 2.5633 | -1.3878 | -7.9959 | -23.1316 | 6.5959 | 6.1286 | 5.499 | 5.3714 | 4.749 | 4.0776 | 3.0571 | 1.8837 | 0.71327 | -0.071429 | -3.5051 | -5.9735 | -6.5102
|  | SOUTHBOURNE | EE |  |  |  | 4.8816 | 4.4102 | 3.7969 | 3.5765 | 2.951 | 2.2704 | 1.1776 | -0.061224 | -1.2949 | -2.1857 | -5.9959 | -8.3235 | -8.5918 | 8.5031 | 8.0939 | 7.55 | 7.3194 | 6.7388 | 6.1071 | 5.2653 | 4.2888 | 3.2969 | 2.5633 | -1.3878 | -5.9112 | -12.9276 | 6.5959 | 6.1286 | 5.499 | 5.3714 | 4.749 | 4.0776 | 3.0571 | 1.8837 | 0.71327 | -0.071429 | -3.5051 | -5.5 | -5.7714
|  | SOUTHBOURNE | HT |  |  |  | 5.2 | 4.8357 | 4.4306 | 3.95 | 3.4204 | 3.2449 | 2.3827 | 1.4143 | 0.39388 | -0.66939 | -5.7786 | -8.8388 | -9.498 | 8.8347 | 8.5908 | 8.3122 | 7.9714 | 7.5959 | 7.502 | 6.9969 | 6.4061 | 5.7776 | 5.1153 | 2.0847 | 0.4449 | 0.036735 | 6.9347 | 6.5969 | 6.2173 | 5.7469 | 5.2224 | 5.1031 | 4.3061 | 3.4051 | 2.4561 | 1.4673 | -3.2531 | -5.9735 | -6.5102
|  | SOUTHBOURNE | HE |  |  |  | 5.2041 | 4.8918 | 4.5378 | 4.1245 | 3.6673 | 3.5653 | 2.8378 | 2.0173 | 1.1653 | 0.26429 | -3.5663 | -5.6163 | -6.1408 | 8.7571 | 8.4724 | 8.1327 | 7.7378 | 7.2888 | 7.1173 | 6.5316 | 5.8622 | 5.1398 | 4.3643 | 0.07449 | -4.4378 | -11.4561 | 6.9337 | 6.6418 | 6.3082 | 5.8969 | 5.4388 | 5.3949 | 4.7204 | 3.9551 | 3.1571 | 2.3184 | -1.2327 | -3.0469 | -3.4867
|  | SOUTHBOURNE | CF |  |  |  | 5.3878 | 5.2163 | 4.9714 | 4.7653 | 4.4959 | 4.1786 | 3.7735 | 3.8031 | 3.4041 | 2.9888 | 0.25102 | -2.8286 | -5.6908 | 8.852 | 8.6133 | 8.3 | 8.0031 | 7.6235 | 7.1592 | 6.6 | 6.3204 | 5.6969 | 5.0255 | 0.22347 | -7.9959 | -23.1316 | 7.0949 | 6.9214 | 6.6714 | 6.4541 | 6.1633 | 5.8306 | 5.4388 | 5.5367 | 5.1378 | 4.7194 | 2.0684 | -0.6102 | -3.1531
BRAMLEY (FLEE) | BURGHFIELD RESERVE | SOUTHCOTE | MINIMUM HEADROOM | SU 68199 71325 | YES | 1.732 | 11.1576 | 10.8668 | 10.576 | 10.2046 | 9.7107 | 9.6352 | 8.9342 | 8.2127 | 7.5178 | 7.0566 | 4.3637 | 2.225 | 0.99742 | 12.2035 | 11.9382 | 11.6648 | 11.3311 | 10.9117 | 10.8464 | 10.3372 | 9.7923 | 9.2382 | 8.8576 | 6.5566 | 2.2913 | -6.7281 | 11.479 | 11.1668 | 10.8627 | 10.4699 | 9.975 | 10.0168 | 9.3688 | 8.6882 | 8.027 | 7.6199 | 5.3393 | 3.4484 | 2.4495
|  | SOUTHCOTE | EE |  |  |  | 11.1576 | 10.8668 | 10.576 | 10.2046 | 9.7107 | 9.6352 | 8.9342 | 8.2127 | 7.5178 | 7.0566 | 4.5923 | 2.6852 | 1.1525 | 12.2035 | 11.9382 | 11.6648 | 11.3311 | 10.9117 | 10.8464 | 10.3372 | 9.7923 | 9.2382 | 8.8576 | 6.5566 | 3.6637 | -1.0199 | 11.479 | 11.1668 | 10.8627 | 10.4699 | 9.975 | 10.0168 | 9.3688 | 8.6882 | 8.027 | 7.6199 | 5.5076 | 3.8607 | 2.5842
|  | SOUTHCOTE | HT |  |  |  | 11.2872 | 11.0627 | 10.8342 | 10.5607 | 10.1882 | 9.7352 | 9.0627 | 8.7852 | 8.1984 | 7.5984 | 4.3637 | 2.225 | 0.99742 | 12.378 | 12.2199 | 12.0668 | 11.8739 | 11.6454 | 11.3607 | 10.976 | 10.9239 | 10.5801 | 10.229 | 8.5056 | 7.5311 | 7.0352 | 11.6515 | 11.4229 | 11.1954 | 10.9076 | 10.5739 | 10.1393 | 9.5178 | 9.3709 | 8.8239 | 8.2658 | 5.3393 | 3.4484 | 2.4495
|  | SOUTHCOTE | HE |  |  |  | 11.2913 | 11.0862 | 10.8842 | 10.6352 | 10.3362 | 9.9484 | 9.3709 | 9.1535 | 8.6617 | 8.176 | 5.5719 | 3.6393 | 2.7311 | 12.3342 | 12.1403 | 11.9454 | 11.7076 | 11.4464 | 11.1148 | 10.6821 | 10.5535 | 10.1362 | 9.7097 | 7.0903 | 4.1372 | -0.28422 | 11.6525 | 11.4444 | 11.2362 | 10.9729 | 10.7035 | 10.3219 | 9.7801 | 9.6831 | 9.227 | 8.7648 | 6.3933 | 4.7382 | 3.9995
|  | SOUTHCOTE | CF |  |  |  | 11.4005 | 11.2862 | 11.177 | 11.0311 | 10.8688 | 10.7423 | 10.5505 | 10.279 | 9.9648 | 10.0505 | 8.1331 | 6.2576 | 4.4842 | 12.3852 | 12.227 | 12.0627 | 11.8637 | 11.6331 | 11.4066 | 11.0862 | 10.6984 | 10.2739 | 10.1607 | 7.2056 | 2.2913 | -6.7281 | 11.7556 | 11.626 | 11.5005 | 11.3352 | 11.1505 | 11.025 | 10.8117 | 10.5311 | 10.2117 | 10.3954 | 8.5995 | 6.9505 | 5.4546
EALING GSP |  | SOUTHFIELD ROAD | MINIMUM HEADROOM | TQ 20533 79746 | YES | 20.697 | 27.3772 | 19.1771 | 17.176 | 14.7607 | 12.5577 | 9.7516 | 7.4709 | 5.0016 | 3.2699 | 1.9107 | -5.4791 | -13.6046 | -18.8515 | 35.2874 | 27.4403 | 26.1118 | 24.524 | 23.2046 | 21.3985 | 19.7434 | 17.873 | 16.275 | 14.9658 | 6.9811 | -6.0138 | -36.1607 | 28.4231 | 20.3556 | 18.6107 | 16.4801 | 14.5516 | 12.0424 | 9.973 | 7.7097 | 6.0393 | 4.7444 | -1.9678 | -8.8321 | -13.2413
|  | SOUTHFIELD ROAD | EE |  |  |  | 27.3772 | 19.1771 | 17.176 | 14.7607 | 12.5577 | 9.7516 | 7.4709 | 5.0016 | 3.2699 | 1.9107 | -5.4791 | -12.2617 | -18.4607 | 35.2874 | 27.4403 | 26.1118 | 24.524 | 23.2046 | 21.3985 | 19.7434 | 17.873 | 16.275 | 14.9658 | 6.9811 | -3.0995 | -19.4852 | 28.4231 | 20.3556 | 18.6107 | 16.4801 | 14.5516 | 12.0424 | 9.973 | 7.7097 | 6.0393 | 4.7444 | -1.9678 | -7.577 | -12.9423
|  | SOUTHFIELD ROAD | HT |  |  |  | 27.8864 | 19.8995 | 18.174 | 16.1465 | 13.9362 | 11.4403 | 9.472 | 7.8016 | 6.4638 | 5.0393 | -4.3597 | -13.6046 | -18.8515 | 35.8221 | 28.3077 | 27.372 | 26.2934 | 25.1016 | 23.7597 | 22.6199 | 21.7903 | 20.8393 | 19.8301 | 14.3097 | 9.9291 | 7.8271 | 28.9098 | 21.076 | 19.6067 | 17.8628 | 15.9271 | 13.7271 | 11.974 | 10.5342 | 9.2362 | 7.8679 | -0.80253 | -8.8321 | -13.2413
|  | SOUTHFIELD ROAD | HE |  |  |  | 27.7956 | 19.8128 | 18.1179 | 16.1352 | 13.9944 | 11.5883 | 9.7138 | 8.1301 | 6.9475 | 5.725 | -1.2515 | -7.2627 | -9.7107 | 35.6384 | 28.0046 | 26.9362 | 25.7281 | 24.4036 | 22.9271 | 21.625 | 20.6281 | 19.4954 | 18.2832 | 10.1852 | 0.19543 | -14.4944 | 28.82 | 20.9954 | 19.5587 | 17.8607 | 15.9944 | 13.8893 | 12.2403 | 10.9342 | 9.8056 | 8.6342 | 2.2495 | -2.8219 | -4.8178
|  | SOUTHFIELD ROAD | CF |  |  |  | 28.0996 | 20.3883 | 19.0087 | 17.3699 | 15.7087 | 13.8118 | 12.6822 | 11.4526 | 11.2209 | 10.624 | 6.5169 | 1.7393 | -3.0974 | 35.7956 | 28.2444 | 27.276 | 26.1475 | 24.9975 | 23.625 | 22.4516 | 21.1199 | 20.3832 | 19.175 | 10.226 | -6.0138 | -36.1607 | 29.117 | 21.526 | 20.3781 | 18.9893 | 17.5669 | 15.9291 | 14.9505 | 13.8618 | 13.6383 | 13.0536 | 9.1148 | 4.6975 | 0.39339
AXMINSTER | YEOVIL BSP | SPARKFORD | MINIMUM HEADROOM | ST 60767 25496 | YES | 1.049 | 2.2367 | 2.1571 | 2.05 | 1.9265 | 1.8367 | 1.7031 | 1.5327 | 1.3888 | 1.202 | 1.1 | 0.61122 | 0.43469 | 0.26837 | 3.3255 | 3.2663 | 3.1878 | 3.0939 | 3.0306 | 2.9276 | 2.8041 | 2.6949 | 2.5541 | 2.4816 | 2.1112 | 1.6439 | 0.64388 | 2.8194 | 2.7439 | 2.6337 | 2.5051 | 2.4153 | 2.2745 | 2.1 | 1.9643 | 1.7663 | 1.7092 | 1.2918 | 1.1357 | 0.98776
|  | SPARKFORD | EE |  |  |  | 2.2367 | 2.1571 | 2.05 | 1.9265 | 1.8367 | 1.7031 | 1.5327 | 1.3888 | 1.202 | 1.1 | 0.61122 | 0.43469 | 0.34694 | 3.3255 | 3.2663 | 3.1878 | 3.0939 | 3.0306 | 2.9276 | 2.8041 | 2.6949 | 2.5541 | 2.4816 | 2.1112 | 1.798 | 1.3286 | 2.8194 | 2.7439 | 2.6337 | 2.5051 | 2.4153 | 2.2745 | 2.1 | 1.9643 | 1.7663 | 1.7092 | 1.2918 | 1.1357 | 1.0592
|  | SPARKFORD | HT |  |  |  | 2.3031 | 2.2306 | 2.1429 | 2.0714 | 1.9806 | 1.8796 | 1.7847 | 1.6418 | 1.4888 | 1.3755 | 0.70816 | 0.45612 | 0.26837 | 3.3796 | 3.3316 | 3.2735 | 3.2337 | 3.1745 | 3.1061 | 3.0541 | 2.9561 | 2.8551 | 2.7847 | 2.3602 | 2.2143 | 2.1102 | 2.8816 | 2.8143 | 2.7296 | 2.6643 | 2.5816 | 2.4816 | 2.3959 | 2.2582 | 2.1143 | 2.0061 | 1.3806 | 1.152 | 0.98776
|  | SPARKFORD | HE |  |  |  | 2.3 | 2.2306 | 2.1418 | 2.0724 | 1.9847 | 1.8847 | 1.7918 | 1.651 | 1.499 | 1.3857 | 0.65102 | 0.48061 | 0.4102 | 3.3724 | 3.3235 | 3.2602 | 3.2112 | 3.149 | 3.0724 | 3.0102 | 2.9051 | 2.7918 | 2.7112 | 2.1459 | 1.8265 | 1.3714 | 2.8776 | 2.8133 | 2.7296 | 2.6663 | 2.5847 | 2.4867 | 2.402 | 2.2653 | 2.1235 | 2.0184 | 1.3316 | 1.1786 | 1.1194
|  | SPARKFORD | CF |  |  |  | 2.3051 | 2.251 | 2.1918 | 2.1378 | 2.0643 | 1.9949 | 1.9082 | 1.8439 | 1.7449 | 1.6398 | 1.1082 | 0.72857 | 0.40204 | 3.3765 | 3.3347 | 3.2898 | 3.25 | 3.1949 | 3.1378 | 3.0622 | 3.0061 | 2.9173 | 2.8245 | 2.2847 | 1.6439 | 0.64388 | 2.8867 | 2.8347 | 2.7786 | 2.7276 | 2.6582 | 2.5929 | 2.5102 | 2.452 | 2.3571 | 2.2582 | 1.75 | 1.398 | 1.1031
MELKSHAM GSP | NORRINGTON | SPRING QUARRY WEST | MINIMUM HEADROOM | ST 84368 68717 | YES | 0.254 | 20.0847 | 19.9378 | 19.7418 | 19.5633 | 19.2755 | 18.9245 | 18.0122 | 17.3653 | 16.6194 | 15.898 | 12.9357 | 10.6592 | 9.0724 | 20.4837 | 20.3898 | 20.2337 | 20.0908 | 19.8684 | 19.6143 | 18.7602 | 18.148 | 17.449 | 16.7786 | 14.4612 | 12.6367 | 10.2684 | 19.7633 | 19.6255 | 19.4286 | 19.2531 | 18.9704 | 18.6367 | 17.649 | 16.9571 | 16.1541 | 15.351 | 12.202 | 9.8418 | 8.1796
|  | SPRING QUARRY WEST | EE |  |  |  | 20.0847 | 19.9378 | 19.7418 | 19.5633 | 19.2755 | 18.9245 | 18.0122 | 17.3653 | 16.6194 | 15.9622 | 13.4908 | 11.8184 | 10.2143 | 20.4837 | 20.3898 | 20.2337 | 20.0908 | 19.8684 | 19.6143 | 18.7602 | 18.148 | 17.449 | 16.7786 | 14.552 | 12.7367 | 10.2684 | 19.7633 | 19.6255 | 19.4286 | 19.2531 | 18.9704 | 18.6367 | 17.649 | 16.9571 | 16.1541 | 15.4214 | 12.8643 | 11.2092 | 9.5388
|  | SPRING QUARRY WEST | HT |  |  |  | 20.1796 | 20.0551 | 19.9092 | 19.7827 | 19.5531 | 19.2622 | 18.4408 | 17.4888 | 16.7112 | 15.898 | 12.9357 | 10.6592 | 9.0724 | 20.549 | 20.4837 | 20.4102 | 20.3429 | 20.2133 | 20.0316 | 19.3051 | 18.4255 | 17.7286 | 16.9531 | 14.4612 | 12.6367 | 11.2898 | 19.8561 | 19.7429 | 19.6051 | 19.4878 | 19.2806 | 19.0112 | 18.1357 | 17.0929 | 16.2551 | 15.351 | 12.202 | 9.8418 | 8.1796
|  | SPRING QUARRY WEST | HE |  |  |  | 20.1776 | 20.0602 | 19.9204 | 19.799 | 19.5796 | 19.2959 | 18.6745 | 17.9082 | 17.4153 | 16.9296 | 14.7959 | 13.0878 | 11.7429 | 20.5367 | 20.4602 | 20.3673 | 20.2827 | 20.1429 | 19.95 | 19.4041 | 18.6888 | 18.2755 | 17.8255 | 15.8755 | 13.9755 | 11.5857 | 19.8551 | 19.7469 | 19.6143 | 19.502 | 19.3031 | 19.0449 | 18.3939 | 17.5673 | 17.0653 | 16.5469 | 14.3602 | 12.65 | 11.201
|  | SPRING QUARRY WEST | CF |  |  |  | 20.2367 | 20.1633 | 20.0745 | 19.9745 | 19.85 | 19.6439 | 19.2316 | 18.7255 | 18.2867 | 17.9439 | 16.9398 | 15.8 | 14.7796 | 20.5612 | 20.5071 | 20.4327 | 20.352 | 20.2582 | 20.1112 | 19.6939 | 19.1531 | 18.6571 | 18.2459 | 17.0439 | 15.3061 | 12.4235 | 19.9082 | 19.8418 | 19.7582 | 19.6612 | 19.5551 | 19.3694 | 18.9306 | 18.3745 | 17.8837 | 17.4888 | 16.4888 | 15.4602 | 14.5582
NORTH HYDE GSP | NORTH HYDE 22kV | SPRINGFIELD ROAD | MINIMUM HEADROOM | TQ 11409 80620 | YES | 5.143 | 15.4791 | 12.7209 | 12.275 | 11.7638 | 27.9806 | 27.4612 | 26.0041 | 24.348 | 22.9255 | 21.6531 | 16.9684 | 13.4204 | 12.1724 | 18.96 | 16.2141 | 15.7794 | 15.311 | 32.6908 | 32.1592 | 30.6724 | 28.9633 | 27.5194 | 26.0898 | 20.1694 | 13.948 | -3.9071 | 15.3598 | 12.5782 | 12.1465 | 11.6343 | 28.751 | 28.251 | 26.6939 | 24.9051 | 23.4122 | 22.0643 | 17.099 | 13.3786 | 11.8755
|  | SPRINGFIELD ROAD | EE |  |  |  | 15.4791 | 12.7209 | 12.275 | 11.7638 | 27.9806 | 27.4612 | 26.0041 | 24.348 | 22.9255 | 21.6531 | 17.5204 | 15.2194 | 14.498 | 18.96 | 16.2141 | 15.7794 | 15.311 | 32.6908 | 32.1592 | 30.6724 | 28.9633 | 27.5194 | 26.0898 | 20.1694 | 14.0133 | 4.3378 | 15.3598 | 12.5782 | 12.1465 | 11.6343 | 28.751 | 28.251 | 26.6939 | 24.9051 | 23.4122 | 22.0643 | 17.7908 | 15.4622 | 14.3918
|  | SPRINGFIELD ROAD | HT |  |  |  | 15.6648 | 12.9689 | 12.7026 | 12.3577 | 28.3796 | 27.9367 | 26.5786 | 25.4857 | 24.2194 | 22.8245 | 16.9684 | 13.4204 | 12.1724 | 19.2039 | 16.5814 | 16.3865 | 16.1386 | 33.5347 | 33.2276 | 31.9929 | 30.8857 | 29.7694 | 28.5031 | 23.5071 | 20.3878 | 18.6939 | 15.4812 | 12.8547 | 12.6251 | 12.2751 | 29.1296 | 28.701 | 27.2276 | 26.0571 | 24.7214 | 23.2306 | 17.099 | 13.3786 | 11.8755
|  | SPRINGFIELD ROAD | HE |  |  |  | 15.6607 | 13.0372 | 12.7515 | 12.4485 | 28.5143 | 28.1265 | 27.0786 | 26.2561 | 25.4357 | 24.5347 | 20.5796 | 18.4704 | 17.0847 | 19.1222 | 16.4651 | 16.1416 | 15.8059 | 33.0867 | 32.6561 | 31.5643 | 30.5449 | 29.6939 | 28.7194 | 22.9276 | 16.7724 | 6.7918 | 15.4792 | 12.9149 | 12.671 | 12.3578 | 29.2541 | 28.8755 | 27.7612 | 26.8949 | 26.0857 | 25.1796 | 21.099 | 18.9041 | 17.2837
|  | SPRINGFIELD ROAD | CF |  |  |  | 15.7821 | 13.2893 | 13.1668 | 12.9566 | 29.1143 | 28.9296 | 28.3653 | 27.5969 | 26.8847 | 26.6551 | 24.2867 | 21.9541 | 19.8224 | 19.1702 | 16.562 | 16.3141 | 15.9692 | 33.249 | 32.8367 | 31.9357 | 30.7663 | 29.6602 | 28.8969 | 23.451 | 13.948 | -3.9071 | 15.5833 | 13.12 | 13.0384 | 12.8251 | 29.7888 | 29.6173 | 28.9837 | 28.1092 | 27.3071 | 27.1031 | 24.7449 | 22.6327 | 20.7418
NURSLING GSP | WINCHESTER | ST CROSS | MINIMUM HEADROOM | SU 47287 28156 | YES | 8.564 | 12.098 | 10.7717 | 9.888 | 4.6003 | 3.9554 | 3.3391 | 2.3493 | 1.2146 | 0.038041 | -0.89971 | -5.8722 | -9.7987 | -12.0813 | 11.6061 | 10.3289 | 9.5707 | 4.2238 | 3.8462 | 3.5472 | 3.0656 | 2.4931 | 1.8615 | 1.2656 | -1.4497 | -3.4191 | -5.5262 | 11.398 | 10.1176 | 9.284 | 4.037 | 3.4238 | 2.8329 | 1.9105 | 0.8462 | -0.25584 | -1.113 | -5.3752 | -8.814 | -10.7528
|  | ST CROSS | EE |  |  |  | 12.098 | 10.7717 | 9.888 | 4.6003 | 3.9554 | 3.3391 | 2.3493 | 1.2146 | 0.038041 | -0.89971 | -5.6518 | -9.0609 | -11.7262 | 11.6061 | 10.3289 | 9.5707 | 4.2238 | 3.8462 | 3.5472 | 3.0656 | 2.4931 | 1.8615 | 1.2656 | -1.4497 | -3.4191 | -5.5262 | 11.398 | 10.1176 | 9.284 | 4.037 | 3.4238 | 2.8329 | 1.9105 | 0.8462 | -0.25584 | -1.113 | -5.2426 | -8.1824 | -10.4803
|  | ST CROSS | HT |  |  |  | 12.3418 | 11.088 | 10.3248 | 4.8401 | 4.3156 | 3.7176 | 3.184 | 2.1656 | 1.0299 | -0.14155 | -5.8722 | -9.7987 | -12.0813 | 11.7133 | 10.4748 | 9.7748 | 4.3758 | 4.1258 | 3.8166 | 3.488 | 2.9268 | 2.2482 | 1.5758 | -0.9538 | -2.5701 | -3.5599 | 11.6418 | 10.4401 | 9.7258 | 4.287 | 3.7942 | 3.2289 | 2.7687 | 1.8391 | 0.80539 | -0.2589 | -5.3752 | -8.814 | -10.7528
|  | ST CROSS | HE |  |  |  | 12.3337 | 11.1176 | 10.386 | 4.9411 | 4.4013 | 3.8931 | 3.5319 | 2.7268 | 1.8523 | 0.89927 | -3.8905 | -7.0905 | -8.6375 | 11.6939 | 10.4503 | 9.738 | 4.3309 | 3.9799 | 3.7187 | 3.4595 | 2.9993 | 2.4687 | 1.8758 | -0.84869 | -2.7732 | -4.516 | 11.6337 | 10.4605 | 9.7778 | 4.3748 | 3.8656 | 3.384 | 3.0768 | 2.3299 | 1.5207 | 0.64416 | -3.6038 | -6.3701 | -7.6701
|  | ST CROSS | CF |  |  |  | 12.7653 | 11.385 | 10.8411 | 5.5064 | 5.1789 | 4.7911 | 4.4584 | 4.4309 | 4.0431 | 3.6013 | 0.32478 | -2.6946 | -5.6528 | 12.1704 | 10.535 | 9.8768 | 4.4942 | 4.2105 | 3.8972 | 3.7136 | 3.6115 | 3.3462 | 3.0421 | 0.73702 | -1.5762 | -4.8875 | 12.0357 | 10.7064 | 10.1931 | 4.888 | 4.5799 | 4.2105 | 3.8911 | 3.884 | 3.5136 | 3.0972 | 0.075796 | -2.6038 | -5.0864
COWLEY GSP | OXFORD BSP | ST EBBES | MINIMUM HEADROOM | SP 51259 05741 | YES | 7.054 | 5.1991 | 4.7828 | 4.6736 | 4.4736 | 4.1858 | 3.6267 | 2.545 | 1.8716 | 1.1297 | 0.55625 | -1.2131 | -2.1305 | -2.3315 | 9.1512 | 8.9563 | 8.8022 | 8.6165 | 8.444 | 8.0134 | 7.3512 | 6.7348 | 6.0675 | 5.4818 | 3.2144 | 0.36544 | -6.0652 | 4.7318 | 4.3869 | 4.295 | 4.1103 | 3.8654 | 3.4634 | 2.7818 | 2.1542 | 1.4624 | 0.92156 | -0.71722 | -1.4876 | -1.6591
|  | ST EBBES | EE |  |  |  | 5.1991 | 4.9767 | 4.695 | 4.4736 | 4.1858 | 3.6267 | 2.6307 | 1.8716 | 1.1297 | 0.55625 | -1.2131 | -1.8846 | -2.0335 | 9.1512 | 9.0083 | 8.8022 | 8.6165 | 8.444 | 8.0277 | 7.3512 | 6.7348 | 6.0675 | 5.4818 | 3.2144 | 1.3134 | -1.8397 | 4.7318 | 4.542 | 4.3022 | 4.1103 | 3.942 | 3.5746 | 2.8471 | 2.1542 | 1.4624 | 0.92156 | -0.71722 | -1.2948 | -1.456
|  | ST EBBES | HT |  |  |  | 5.2665 | 4.7828 | 4.6736 | 4.5614 | 4.2175 | 3.7287 | 2.545 | 2.0073 | 1.3491 | 0.8338 | -1.0101 | -2.1305 | -2.3315 | 9.2185 | 8.9563 | 8.8777 | 8.8032 | 8.4471 | 8.0134 | 7.4175 | 6.9399 | 6.3195 | 5.8981 | 4.9256 | 4.2991 | 4.1501 | 4.7909 | 4.3869 | 4.295 | 4.2001 | 3.8654 | 3.4634 | 2.7818 | 2.2603 | 1.6216 | 1.1491 | -0.43864 | -1.4876 | -1.6591
|  | ST EBBES | HE |  |  |  | 5.2614 | 5.0532 | 4.796 | 4.6226 | 4.4634 | 4.0828 | 3.2542 | 2.6328 | 2.0807 | 1.5654 | -0.065176 | -0.60497 | -0.71722 | 9.1981 | 9.0695 | 8.8828 | 8.7409 | 8.5981 | 8.2246 | 7.7399 | 7.2624 | 6.7256 | 6.1654 | 3.9501 | 2.146 | -0.89171 | 4.7858 | 4.6114 | 4.395 | 4.2471 | 4.1124 | 3.7889 | 3.3073 | 2.8501 | 2.3216 | 1.8124 | 0.3338 | -0.10395 | -0.19783
|  | ST EBBES | CF |  |  |  | 5.3185 | 5.2746 | 5.2287 | 5.1726 | 5.1216 | 5.0593 | 4.9012 | 4.5991 | 4.2042 | 3.7756 | 1.094 | 0.16442 | -0.65395 | 9.2195 | 9.1654 | 9.1001 | 9.0267 | 8.9512 | 8.846 | 8.6175 | 8.2542 | 7.8032 | 7.3103 | 3.7736 | 0.36544 | -6.0652 | 4.8348 | 4.796 | 4.7542 | 4.7063 | 4.6603 | 4.6083 | 4.4552 | 4.1716 | 3.8022 | 3.4012 | 1.1563 | 0.57258 | -0.11926
BRAMLEY (ANDO-THAT) | THATCHAM BSP | ST JOHNS | MINIMUM HEADROOM | SU 47113 66363 | YES | 3.54 | -8.4937 | -9.0641 | -10.1651 | -11.0141 | -12.2294 | -13.5457 | -15.0222 | -16.6202 | -18.1651 | -19.3008 | -23.7008 | -27.3161 | -29.3212 | -2.3396 | -2.7692 | -3.51 | -3.9427 | -4.7192 | -5.5518 | -6.4906 | -7.5355 | -8.5651 | -9.2886 | -12.4978 | -16.5396 | -27.1253 | -7.7978 | -8.3427 | -9.3478 | -9.9682 | -11.0396 | -12.2069 | -13.5457 | -15.012 | -16.4171 | -17.3957 | -21.108 | -24.2233 | -25.859
|  | ST JOHNS | EE |  |  |  | -8.4937 | -9.0641 | -10.1651 | -11.0141 | -12.2294 | -13.5457 | -15.0222 | -16.6202 | -18.1651 | -19.3008 | -23.5427 | -26.7018 | -29.1161 | -2.3396 | -2.7692 | -3.51 | -3.9427 | -4.7192 | -5.5518 | -6.4906 | -7.5355 | -8.5651 | -9.2886 | -12.4978 | -15.9967 | -21.6416 | -7.7978 | -8.3427 | -9.3478 | -9.9682 | -11.0396 | -12.2069 | -13.5457 | -15.012 | -16.4171 | -17.3957 | -21.059 | -23.659 | -25.6835
|  | ST JOHNS | HT |  |  |  | -8.2937 | -8.8059 | -9.7722 | -10.862 | -12.0365 | -12.9824 | -14.3753 | -15.8253 | -17.2263 | -18.5345 | -23.7008 | -27.3161 | -29.3212 | -2.0712 | -2.3661 | -2.8896 | -3.4794 | -4.1131 | -4.4702 | -5.1671 | -5.9284 | -6.6835 | -7.4171 | -10.2141 | -11.8222 | -12.5988 | -7.512 | -7.9651 | -8.7712 | -9.6978 | -10.71 | -11.4631 | -12.66 | -13.9263 | -15.1682 | -16.3508 | -21.108 | -24.2233 | -25.859
|  | ST JOHNS | HE |  |  |  | -8.2937 | -8.7743 | -9.7059 | -10.759 | -11.8947 | -12.7896 | -14.0069 | -15.2814 | -16.4967 | -17.6141 | -21.8406 | -24.8365 | -26.2049 | -2.1284 | -2.459 | -3.0273 | -3.662 | -4.3488 | -4.7498 | -5.4722 | -6.2641 | -7.062 | -7.8437 | -11.4416 | -14.9243 | -20.1396 | -7.5202 | -7.9457 | -8.7222 | -9.61 | -10.5824 | -11.2845 | -12.3284 | -13.4427 | -14.5212 | -15.5304 | -19.4059 | -21.8967 | -23.0039
|  | ST JOHNS | CF |  |  |  | -8.1294 | -8.4671 | -9.2478 | -10.0437 | -10.9212 | -11.8712 | -12.3722 | -13.1845 | -13.9488 | -14.6212 | -17.3784 | -20.412 | -23.3488 | -2.0437 | -2.3243 | -2.8508 | -3.3641 | -3.9457 | -4.5967 | -4.9345 | -5.6069 | -6.2784 | -6.9416 | -10.7294 | -16.5396 | -27.1253 | -7.3702 | -7.6794 | -8.3498 | -9.0049 | -9.7467 | -10.5488 | -10.861 | -11.561 | -12.2406 | -12.8682 | -15.6182 | -18.2886 | -20.7508
COWLEY GSP | WITNEY BSP | STANDLAKE | MINIMUM HEADROOM | SP 38923 02349 | YES | 1.939 | -0.41429 | -0.53265 | -0.66939 | -0.78469 | -0.93469 | -1.0673 | -1.2929 | -1.5612 | -1.8347 | -1.9939 | -2.7408 | -3.1469 | -3.4561 | 1.4092 | 1.3235 | 1.202 | 1.1102 | 0.97449 | 0.86122 | 0.69184 | 0.48163 | 0.27653 | 0.1551 | -0.45204 | -1.2306 | -2.9418 | 0.48367 | 0.38163 | 0.24388 | 0.12041 | -0.045918 | -0.18469 | -0.40816 | -0.66531 | -0.92857 | -1.0765 | -1.752 | -2.0929 | -2.3337
|  | STANDLAKE | EE |  |  |  | -0.41429 | -0.53265 | -0.66939 | -0.78469 | -0.93469 | -1.0673 | -1.2929 | -1.5612 | -1.8347 | -1.9939 | -2.7408 | -3.1265 | -3.351 | 1.4092 | 1.3235 | 1.202 | 1.1102 | 0.97449 | 0.86122 | 0.69184 | 0.48163 | 0.27653 | 0.1551 | -0.45204 | -1.0184 | -1.8663 | 0.48367 | 0.38163 | 0.24388 | 0.12041 | -0.045918 | -0.18469 | -0.40816 | -0.66531 | -0.92857 | -1.0765 | -1.752 | -2.0602 | -2.25
|  | STANDLAKE | HT |  |  |  | -0.36224 | -0.47347 | -0.57245 | -0.68776 | -0.8102 | -0.91735 | -1.099 | -1.298 | -1.4735 | -1.6827 | -2.6694 | -3.1469 | -3.4561 | 1.4806 | 1.4112 | 1.3439 | 1.2673 | 1.1755 | 1.1112 | 0.99082 | 0.84694 | 0.73878 | 0.59082 | -0.039796 | -0.29184 | -0.43571 | 0.53265 | 0.44184 | 0.35408 | 0.25102 | 0.13878 | 0.034694 | -0.1449 | -0.35204 | -0.52041 | -0.73571 | -1.6806 | -2.0929 | -2.3337
|  | STANDLAKE | HE |  |  |  | -0.3602 | -0.46939 | -0.56429 | -0.67347 | -0.79286 | -0.8949 | -1.0561 | -1.2418 | -1.402 | -1.5969 | -2.5898 | -2.9745 | -3.1643 | 1.4704 | 1.3939 | 1.3184 | 1.2347 | 1.1367 | 1.0582 | 0.92959 | 0.77449 | 0.64898 | 0.48265 | -0.35102 | -0.91735 | -1.7429 | 0.53265 | 0.44184 | 0.35408 | 0.25102 | 0.13673 | 0.029592 | -0.12551 | -0.30714 | -0.47857 | -0.67653 | -1.65 | -2.0051 | -2.1806
|  | STANDLAKE | CF |  |  |  | -0.33061 | -0.41429 | -0.50102 | -0.57041 | -0.6551 | -0.74898 | -0.81837 | -0.92347 | -1.0357 | -1.1531 | -1.8612 | -2.451 | -2.9327 | 1.4918 | 1.4255 | 1.352 | 1.2939 | 1.2163 | 1.1255 | 1.0531 | 0.93265 | 0.80612 | 0.67041 | -0.1551 | -1.2306 | -2.9418 | 0.57143 | 0.50918 | 0.44184 | 0.38163 | 0.29694 | 0.2 | 0.13673 | 0.019388 | -0.1051 | -0.23673 | -0.93776 | -1.4959 | -1.9908
MINETY GSP | STRATTON (2 X 60) | STANTON FITZWARREN | MINIMUM HEADROOM | SU 17585 90987 | YES | 5.928 | 11.0482 | 10.4074 | 9.7278 | 9.04 | 8.5135 | 7.3604 | 6.1543 | 5.0104 | 3.4696 | 2.2329 | -2.91 | -5.8692 | -7.3304 | 10.5914 | 10.1088 | 9.4751 | 9.0159 | 8.719 | 7.9445 | 7.1098 | 6.1516 | 5.0221 | 4.1118 | -0.18407 | -2.2739 | -8.1882 | 8.9023 | 8.2686 | 7.5206 | 6.8645 | 6.5318 | 5.4767 | 4.3696 | 3.2798 | 1.8543 | 0.61756 | -5.0233 | -7.6426 | -8.112
|  | STANTON FITZWARREN | EE |  |  |  | 11.0482 | 10.4074 | 9.7278 | 9.04 | 8.5696 | 7.5798 | 6.5002 | 5.0104 | 3.4696 | 2.2329 | -2.6161 | -5.4733 | -7.0682 | 10.5914 | 10.1088 | 9.4751 | 9.0159 | 8.719 | 7.9996 | 7.2312 | 6.1516 | 5.0221 | 4.1159 | 0.58124 | -2.1198 | -5.1708 | 8.9023 | 8.2686 | 7.5206 | 6.8645 | 6.5553 | 5.6472 | 4.6512 | 3.2798 | 1.8543 | 0.75736 | -3.5926 | -6.0222 | -7.3518
|  | STANTON FITZWARREN | HT |  |  |  | 11.2084 | 10.6257 | 10.0196 | 9.4553 | 8.5135 | 7.3604 | 6.1543 | 5.0237 | 3.5839 | 2.391 | -2.7682 | -5.8692 | -7.3304 | 10.7241 | 10.317 | 9.771 | 9.4374 | 8.7833 | 7.9445 | 7.1098 | 6.3251 | 5.3476 | 4.6292 | 1.8465 | 0.19144 | -0.49529 | 9.1023 | 8.5523 | 7.8839 | 7.389 | 6.5318 | 5.4767 | 4.3696 | 3.3349 | 1.9961 | 0.92164 | -3.6457 | -6.3314 | -7.5324
|  | STANTON FITZWARREN | HE |  |  |  | 11.1982 | 10.6349 | 10.04 | 9.4951 | 8.8012 | 7.8594 | 6.9053 | 5.9288 | 4.5655 | 3.0798 | -2.91 | -5.7171 | -6.2528 | 10.6823 | 10.2394 | 9.6557 | 9.2782 | 8.82 | 8.1221 | 7.4088 | 6.5629 | 5.3016 | 4.1118 | -0.18407 | -2.0606 | -4.6973 | 9.0921 | 8.5563 | 7.8931 | 7.4114 | 6.7982 | 5.8635 | 4.8247 | 3.5574 | 2.0584 | 0.61756 | -5.0233 | -7.6426 | -8.112
|  | STANTON FITZWARREN | CF |  |  |  | 11.4206 | 10.9176 | 10.4533 | 10.0176 | 9.5359 | 8.9808 | 8.5135 | 7.7084 | 7.1074 | 6.2206 | 1.189 | -2.8243 | -5.713 | 10.8343 | 10.3965 | 9.87 | 9.5312 | 9.1741 | 8.7516 | 8.317 | 7.6323 | 7.0414 | 6.2476 | 1.8323 | -2.2739 | -8.1882 | 9.2798 | 8.788 | 8.2492 | 7.8543 | 7.44 | 6.9472 | 6.5012 | 5.7574 | 5.2043 | 4.2186 | -1.2192 | -5.0028 | -7.6763
LALEHAM | STAINES | STANWELL | MINIMUM HEADROOM | TQ 06003 72766 | YES | 8.431 | 13.6974 | 13.5168 | 13.2811 | 13.0627 | 12.7862 | 12.4862 | 11.3637 | 10.4454 | 9.4545 | 8.477 | 3.9352 | 0.65761 | -1.4301 | 14.0994 | 13.9586 | 13.776 | 13.6005 | 13.378 | 13.1239 | 11.9627 | 10.9188 | 9.8964 | 8.8413 | 4.7964 | 1.2352 | -4.0036 | 13.1974 | 13.0148 | 12.7576 | 12.5219 | 12.2178 | 11.8872 | 10.6076 | 9.5923 | 8.4801 | 7.4025 | 2.7433 | -0.60566 | -2.874
|  | STANWELL | EE |  |  |  | 13.6974 | 13.5168 | 13.2811 | 13.0627 | 12.7862 | 12.4862 | 11.3637 | 10.4454 | 9.4545 | 8.477 | 4.7423 | 2.3209 | 0.093322 | 14.0994 | 13.9586 | 13.776 | 13.6005 | 13.378 | 13.1239 | 11.9627 | 10.9188 | 9.8964 | 8.8413 | 4.7964 | 1.2352 | -4.0036 | 13.1974 | 13.0148 | 12.7576 | 12.5219 | 12.2178 | 11.8872 | 10.6076 | 9.5923 | 8.4801 | 7.4025 | 3.6545 | 1.3525 | -1.0322
|  | STANWELL | HT |  |  |  | 13.7974 | 13.6454 | 13.4586 | 13.2852 | 13.0719 | 12.8352 | 11.8229 | 10.627 | 9.6107 | 8.5045 | 3.9352 | 0.65761 | -1.4301 | 14.1984 | 14.1137 | 14.0107 | 13.9158 | 13.7903 | 13.6525 | 12.6811 | 11.5321 | 10.6178 | 9.5637 | 5.6413 | 2.8801 | 1.0219 | 13.325 | 13.176 | 12.9892 | 12.8209 | 12.6015 | 12.3556 | 11.2219 | 9.8648 | 8.7352 | 7.4923 | 2.7433 | -0.60566 | -2.874
|  | STANWELL | HE |  |  |  | 13.7984 | 13.6596 | 13.4882 | 13.329 | 13.129 | 12.9137 | 12.1831 | 11.2545 | 10.6433 | 9.977 | 6.7515 | 4.3056 | 2.5372 | 14.1637 | 14.0474 | 13.9076 | 13.7688 | 13.5954 | 13.4005 | 12.6525 | 11.7015 | 11.129 | 10.4627 | 6.8219 | 3.1923 | -1.872 | 13.325 | 13.1882 | 13.0127 | 12.8586 | 12.6545 | 12.4301 | 11.6219 | 10.5739 | 9.927 | 9.2086 | 5.9688 | 3.578 | 1.6066
|  | STANWELL | CF |  |  |  | 13.8913 | 13.8178 | 13.7219 | 13.6209 | 13.5341 | 13.4158 | 12.9943 | 12.4362 | 11.9148 | 11.4658 | 9.9076 | 8.2331 | 6.6964 | 14.2066 | 14.1117 | 13.9943 | 13.8658 | 13.7321 | 13.5515 | 12.978 | 12.2148 | 11.5158 | 10.8658 | 8.1913 | 3.8913 | -3.6352 | 13.4127 | 13.3321 | 13.227 | 13.1127 | 13.026 | 12.8943 | 12.3892 | 11.7188 | 11.0923 | 10.5607 | 8.9984 | 7.5076 | 6.2423
MANNINGTON GSP | SALISBURY | STAPLEFORD | MINIMUM HEADROOM | SU 06871 37078 | YES | 1.672 | 8.43 | 8.2749 | 8.129 | 7.9382 | 7.778 | 7.5596 | 7.279 | 6.9443 | 7.1269 | 6.9524 | 5.9892 | 5.5392 | 5.3137 | 8.5754 | 8.4693 | 8.3652 | 8.2295 | 8.1111 | 7.957 | 7.756 | 7.5162 | 7.6111 | 7.4978 | 6.8111 | 5.9448 | 3.9693 | 8.2142 | 8.0672 | 7.9254 | 7.7417 | 7.5876 | 7.3632 | 7.0815 | 6.7407 | 6.9815 | 6.8203 | 5.9999 | 5.5938 | 5.3713
|  | STAPLEFORD | EE |  |  |  | 8.43 | 8.2749 | 8.129 | 7.9382 | 7.778 | 7.5596 | 7.279 | 6.9443 | 7.1269 | 6.979 | 6.0688 | 5.7065 | 5.4708 | 8.5754 | 8.4693 | 8.3652 | 8.2295 | 8.1111 | 7.957 | 7.756 | 7.5162 | 7.6111 | 7.4978 | 6.8519 | 6.2274 | 5.254 | 8.2142 | 8.0672 | 7.9254 | 7.7417 | 7.5876 | 7.3632 | 7.0815 | 6.7407 | 6.9815 | 6.8448 | 6.0846 | 5.7836 | 5.5907
|  | STAPLEFORD | HT |  |  |  | 8.5096 | 8.3892 | 8.2851 | 8.1412 | 8.0269 | 7.8667 | 7.6473 | 7.4637 | 7.2147 | 6.9524 | 6.2198 | 5.6994 | 5.3177 | 8.6438 | 8.5734 | 8.5091 | 8.4162 | 8.353 | 8.2509 | 8.1142 | 8.005 | 7.8427 | 7.6713 | 7.3111 | 7.0438 | 6.8611 | 8.2927 | 8.1815 | 8.0815 | 7.9458 | 7.8397 | 7.6876 | 7.4785 | 7.3081 | 7.0693 | 6.8203 | 6.2203 | 5.7621 | 5.4458
|  | STAPLEFORD | HE |  |  |  | 8.5198 | 8.3902 | 8.2882 | 8.1473 | 8.0402 | 7.8841 | 7.6769 | 7.5035 | 7.2667 | 7.0177 | 5.9892 | 5.5392 | 5.3137 | 8.6387 | 8.553 | 8.4764 | 8.3785 | 8.2999 | 8.1866 | 8.0387 | 7.9091 | 7.7346 | 7.5509 | 6.9274 | 6.2856 | 5.3295 | 8.3019 | 8.1815 | 8.0836 | 7.9519 | 7.8499 | 7.7009 | 7.506 | 7.3438 | 7.1172 | 6.8815 | 5.9999 | 5.5938 | 5.3713
|  | STAPLEFORD | CF |  |  |  | 8.5494 | 8.4443 | 8.3555 | 8.2535 | 8.1361 | 8.0494 | 7.9157 | 7.7647 | 7.6024 | 7.5004 | 6.579 | 6.2382 | 5.6106 | 8.6652 | 8.5846 | 8.5183 | 8.4407 | 8.3478 | 8.2734 | 8.1581 | 8.0244 | 7.8815 | 7.7703 | 6.8111 | 5.9448 | 3.9693 | 8.3315 | 8.2315 | 8.1509 | 8.056 | 7.9427 | 7.8621 | 7.7356 | 7.5907 | 7.4346 | 7.3417 | 6.4591 | 6.1805 | 5.6203
COWLEY GSP | HIGH WYCOMBE BSP | STOKENCHURCH | MINIMUM HEADROOM | SU 77124 94355 | YES | 4.686 | -1.6225 | -1.8337 | -2.1174 | -2.3704 | -2.698 | -3.0449 | -3.1225 | -3.599 | -4.0827 | -4.4153 | -6.1633 | -7.3521 | -8.0745 | 0.74027 | 0.57803 | 0.34436 | 0.14129 | -0.13013 | -0.42197 | -0.37299 | -0.72095 | -1.0761 | -1.2954 | -2.6158 | -4.2485 | -8.0995 | -1.0449 | -1.2521 | -1.5429 | -1.7898 | -2.1225 | -2.4776 | -2.4419 | -2.8949 | -3.3521 | -3.6347 | -5.1939 | -6.247 | -6.8715
|  | STOKENCHURCH | EE |  |  |  | -1.6225 | -1.8337 | -2.1174 | -2.3704 | -2.698 | -3.0449 | -3.1225 | -3.599 | -4.0827 | -4.4153 | -6.1633 | -7.2215 | -7.9174 | 0.74027 | 0.57803 | 0.34436 | 0.14129 | -0.13013 | -0.42197 | -0.37299 | -0.72095 | -1.0761 | -1.2954 | -2.6158 | -3.9526 | -5.9393 | -1.0449 | -1.2521 | -1.5429 | -1.7898 | -2.1225 | -2.4776 | -2.4419 | -2.8949 | -3.3521 | -3.6347 | -5.1939 | -6.1235 | -6.7317
|  | STOKENCHURCH | HT |  |  |  | -1.4929 | -1.6653 | -1.85 | -2.0704 | -2.3164 | -2.5317 | -2.9378 | -3.3888 | -3.8704 | -3.9225 | -6.0817 | -7.3521 | -8.0745 | 0.85966 | 0.76068 | 0.65252 | 0.4964 | 0.32701 | 0.18721 | -0.059727 | -0.34646 | -0.65667 | -0.5383 | -1.7179 | -2.325 | -2.6454 | -0.90309 | -1.0602 | -1.2347 | -1.4511 | -1.6929 | -1.8908 | -2.2684 | -2.7021 | -3.1623 | -3.1153 | -5.1123 | -6.247 | -6.8715
|  | STOKENCHURCH | HE |  |  |  | -1.496 | -1.6592 | -1.8347 | -2.047 | -2.2786 | -2.4766 | -2.8368 | -3.2429 | -3.6745 | -3.6766 | -5.6521 | -6.6755 | -7.1296 | 0.83619 | 0.72599 | 0.59844 | 0.43517 | 0.25252 | 0.094355 | -0.16381 | -0.46789 | -0.79748 | -0.73524 | -2.3118 | -3.6587 | -5.5261 | -0.90718 | -1.0541 | -1.2215 | -1.4296 | -1.6572 | -1.8398 | -2.1776 | -2.5694 | -2.9878 | -2.8868 | -4.7153 | -5.6184 | -6.0062
|  | STOKENCHURCH | CF |  |  |  | -1.4286 | -1.5439 | -1.6888 | -1.8051 | -1.9633 | -2.1296 | -2.2704 | -2.4888 | -2.7266 | -2.9745 | -3.9939 | -5.2092 | -6.2868 | 0.87089 | 0.78007 | 0.65864 | 0.5566 | 0.4117 | 0.24027 | 0.086192 | -0.1434 | -0.3934 | -0.66279 | -1.9485 | -4.2485 | -8.0995 | -0.84493 | -0.95513 | -1.1 | -1.2102 | -1.3674 | -1.5378 | -1.6725 | -1.8929 | -2.1337 | -2.3878 | -3.2419 | -4.3082 | -5.2878
MINETY GSP | STRATTON (2 X 60) | STRATTON | MINIMUM HEADROOM | SU 16998 88837 | YES | 10.713 | 7.535 | 6.9258 | 6.1697 | 5.3003 | 4.4126 | 2.6758 | 1.1167 | -0.63538 | -2.4854 | -4.0038 | -8.3966 | -11.0435 | -12.2364 | 10.7254 | 10.3183 | 9.8152 | 9.2489 | 8.8673 | 7.7652 | 6.6111 | 5.2407 | 3.9152 | 2.8591 | -0.5062 | -3.7817 | -11.8042 | 9.3075 | 8.7483 | 8.032 | 7.2126 | 6.6911 | 5.1932 | 3.8238 | 2.0748 | 0.40237 | -0.89559 | -4.7038 | -7.014 | -7.9548
|  | STRATTON | EE |  |  |  | 7.535 | 6.9258 | 6.1697 | 5.3003 | 4.6258 | 3.0524 | 1.3105 | -0.63436 | -2.4854 | -4.0038 | -8.3966 | -10.7997 | -11.766 | 10.7254 | 10.3183 | 9.8152 | 9.2489 | 8.8673 | 7.7734 | 6.6111 | 5.2407 | 3.9152 | 2.8591 | -0.5062 | -3.3297 | -7.1174 | 9.3075 | 8.7483 | 8.032 | 7.2126 | 6.7269 | 5.3575 | 3.8238 | 2.0748 | 0.40237 | -0.89559 | -4.5874 | -6.4956 | -7.2905
|  | STRATTON | HT |  |  |  | 7.7187 | 7.1707 | 6.4973 | 5.7575 | 4.4126 | 2.6758 | 1.1167 | -0.63538 | -2.2425 | -3.5701 | -8.2415 | -11.0435 | -12.2364 | 10.9122 | 10.6081 | 10.2295 | 9.8295 | 8.9193 | 7.7652 | 6.8214 | 5.702 | 4.6907 | 3.9285 | 1.4183 | -7.7551e-05 | -0.6562 | 9.5462 | 9.0779 | 8.482 | 7.8503 | 6.6911 | 5.1932 | 3.9422 | 2.4187 | 1.0116 | -0.15885 | -4.3354 | -6.6833 | -7.615
|  | STRATTON | HE |  |  |  | 7.7187 | 7.1871 | 6.5279 | 5.8014 | 4.9432 | 3.4309 | 2.0993 | 0.35441 | -1.3303 | -2.8844 | -7.4752 | -9.9548 | -10.9262 | 10.8714 | 10.5244 | 10.0958 | 9.6448 | 9.1101 | 8.0662 | 7.2071 | 5.9693 | 4.7489 | 3.6346 | -0.10518 | -3.0664 | -6.847 | 9.5432 | 9.085 | 8.4983 | 7.8769 | 7.1279 | 5.834 | 4.7789 | 3.2626 | 1.7799 | 0.40747 | -4.7038 | -7.014 | -7.9548
|  | STRATTON | CF |  |  |  | 7.9034 | 7.5085 | 7.0565 | 6.5146 | 5.9279 | 5.1289 | 4.1738 | 3.0707 | 2.1677 | 1.0585 | -3.2262 | -6.4058 | -9.3578 | 10.9734 | 10.6754 | 10.352 | 9.9683 | 9.5642 | 9.0173 | 8.2703 | 7.3601 | 6.5734 | 5.6162 | 1.1622 | -3.7817 | -11.8042 | 9.7044 | 9.3462 | 8.9544 | 8.4738 | 7.9769 | 7.2952 | 6.4707 | 5.4962 | 4.8269 | 3.8442 | -0.16293 | -3.6548 | -6.4293
LALEHAM | STAINES | SUNBURY CROSS | MINIMUM HEADROOM | TQ 10053 69996 | YES | 6.461 | 36.5924 | 36.0138 | 35.0648 | 33.9995 | 32.7444 | 31.2005 | 28.9128 | 26.3209 | 23.8566 | 22.0536 | 13.0577 | 5.3036 | 1.074 | 44.5893 | 44.0944 | 43.2577 | 42.3118 | 41.2199 | 39.9771 | 38.3781 | 36.525 | 34.7026 | 33.3526 | 26.1056 | 16.8424 | -4.6719 | 36.6903 | 36.1444 | 35.1362 | 33.9964 | 32.6995 | 31.222 | 29.1087 | 26.6873 | 24.3658 | 22.7505 | 15.0403 | 8.8852 | 5.2434
|  | SUNBURY CROSS | EE |  |  |  | 36.5924 | 36.0138 | 35.0648 | 33.9995 | 32.7444 | 31.2005 | 28.9128 | 26.3209 | 23.8566 | 22.0536 | 13.0577 | 6.4332 | 1.4158 | 44.5893 | 44.0944 | 43.2577 | 42.3118 | 41.2199 | 39.9771 | 38.3781 | 36.525 | 34.7026 | 33.3526 | 26.1056 | 18.7373 | 7.7107 | 36.6903 | 36.1444 | 35.1362 | 33.9964 | 32.6995 | 31.222 | 29.1087 | 26.6873 | 24.3658 | 22.7505 | 15.0403 | 9.8515 | 5.4913
|  | SUNBURY CROSS | HT |  |  |  | 37.0515 | 36.373 | 35.4618 | 34.7607 | 33.673 | 32.4822 | 30.5107 | 28.573 | 26.5822 | 24.5536 | 13.0893 | 5.3036 | 1.074 | 45.1444 | 44.6975 | 44.0811 | 43.6954 | 42.9709 | 42.1679 | 41.073 | 39.9158 | 38.6975 | 37.4434 | 31.1475 | 27.5271 | 25.8424 | 37.2944 | 36.622 | 35.7148 | 35.1403 | 34.0964 | 32.9413 | 31.1811 | 29.3709 | 27.4873 | 25.5454 | 15.3158 | 8.8852 | 5.2434
|  | SUNBURY CROSS | HE |  |  |  | 37.0026 | 36.3526 | 35.5026 | 34.8791 | 33.9077 | 32.7444 | 31.0015 | 29.0373 | 27.1403 | 25.2618 | 14.972 | 7.7515 | 4.8015 | 45.0005 | 44.4485 | 43.7301 | 43.2403 | 42.4128 | 41.4352 | 40.1964 | 38.7526 | 37.274 | 35.7403 | 27.0822 | 19.1066 | 8.8107 | 37.2362 | 36.5893 | 35.7301 | 35.2179 | 34.2689 | 33.1464 | 31.5648 | 29.7413 | 27.9383 | 26.1209 | 16.9077 | 10.9638 | 8.4322
|  | SUNBURY CROSS | CF |  |  |  | 37.4271 | 37.0985 | 36.6781 | 36.2138 | 36.0179 | 35.5332 | 34.9546 | 34.1852 | 33.2628 | 32.2118 | 24.8495 | 17.7842 | 11.4189 | 45.2281 | 44.8209 | 44.3046 | 43.7311 | 43.3862 | 42.6781 | 41.8373 | 40.8015 | 39.6434 | 38.4046 | 29.6648 | 16.8424 | -4.6719 | 37.6189 | 37.2546 | 36.7709 | 36.2454 | 36.1097 | 35.573 | 34.9546 | 34.1383 | 33.1913 | 32.1903 | 25.375 | 19.1475 | 13.8148
BRAMLEY (FLEE) | BRACKNELL | SUNNINGHILL | MINIMUM HEADROOM | SU 93757 67606 | YES | 1.715 | 11.9065 | 11.6433 | 11.3647 | 11.1086 | 10.78 | 10.3882 | 9.8555 | 9.7249 | 9.1963 | 8.8249 | 7.1973 | 6.0076 | 5.7106 | 13.8478 | 13.6559 | 13.4243 | 13.2171 | 12.9457 | 12.6069 | 12.21 | 12.1569 | 11.7631 | 11.4947 | 10.1539 | 8.4161 | 4.0386 | 12.2545 | 12.0147 | 11.7443 | 11.5035 | 11.1871 | 10.7933 | 10.2871 | 10.2167 | 9.729 | 9.3861 | 7.8963 | 6.8524 | 6.6055
|  | SUNNINGHILL | EE |  |  |  | 11.9065 | 11.6433 | 11.3647 | 11.1086 | 10.78 | 10.3882 | 9.8555 | 9.7249 | 9.1963 | 8.8249 | 7.1973 | 6.1831 | 6.0963 | 13.8478 | 13.6559 | 13.4243 | 13.2171 | 12.9457 | 12.6069 | 12.21 | 12.1569 | 11.7631 | 11.4947 | 10.1539 | 8.7916 | 6.8549 | 12.2545 | 12.0147 | 11.7443 | 11.5035 | 11.1871 | 10.7933 | 10.2871 | 10.2167 | 9.729 | 9.3861 | 7.8963 | 7.0127 | 6.9412
|  | SUNNINGHILL | HT |  |  |  | 12.031 | 11.8096 | 11.5902 | 11.4004 | 11.1024 | 10.8586 | 10.4484 | 9.9922 | 9.4984 | 9.3973 | 7.2861 | 6.0076 | 5.7106 | 13.9763 | 13.8437 | 13.6978 | 13.5753 | 13.3498 | 13.1824 | 12.9314 | 12.6467 | 12.3284 | 12.3518 | 11.1457 | 10.5182 | 10.3518 | 12.3841 | 12.1912 | 11.9851 | 11.8086 | 11.5127 | 11.28 | 10.9076 | 10.4861 | 10.031 | 9.9453 | 7.9953 | 6.8524 | 6.6055
|  | SUNNINGHILL | HE |  |  |  | 12.0494 | 11.8678 | 11.6229 | 11.4524 | 11.2259 | 10.9861 | 10.6106 | 10.1943 | 9.7494 | 9.7086 | 8.0433 | 7.1188 | 6.8535 | 13.959 | 13.8243 | 13.6355 | 13.4906 | 13.3008 | 13.0916 | 12.8161 | 12.4957 | 12.1539 | 12.1498 | 10.6222 | 9.2396 | 7.2896 | 12.3963 | 12.2341 | 12.0086 | 11.8494 | 11.6341 | 11.4035 | 11.0565 | 10.6667 | 10.2535 | 10.23 | 8.6922 | 7.8637 | 7.6402
|  | SUNNINGHILL | CF |  |  |  | 12.1351 | 12.0106 | 11.8545 | 11.7606 | 11.6229 | 11.4708 | 11.329 | 11.1147 | 10.8851 | 10.6412 | 9.6841 | 8.3514 | 7.1514 | 14.0059 | 13.8886 | 13.7416 | 13.6294 | 13.4784 | 13.3029 | 13.1182 | 12.8641 | 12.5916 | 12.3039 | 10.8876 | 8.4161 | 4.0386 | 12.4718 | 12.3596 | 12.2127 | 12.1188 | 11.9831 | 11.8341 | 11.6953 | 11.481 | 11.2514 | 11.0096 | 10.1494 | 8.9708 | 7.8851
MELKSHAM GSP | CHIPPENHAM | SUTTON BENGER | MINIMUM HEADROOM | ST 93394 80051 | YES | 6.362 | 5.8085 | 5.7085 | 3.974 | 3.8169 | 3.674 | 3.5128 | 3.3495 | 3.2098 | 3.0342 | 2.9353 | 2.4077 | 2.1649 | 1.9281 | 6.8916 | 6.8252 | 5.1377 | 5.0336 | 4.9428 | 4.8316 | 4.7051 | 4.602 | 4.4642 | 4.3949 | 4.0091 | 3.4244 | 2.2204 | 6.334 | 6.2463 | 4.523 | 4.3791 | 4.2557 | 4.1077 | 3.9485 | 3.8108 | 3.6251 | 3.5383 | 3.1026 | 2.8985 | 2.7026
|  | SUTTON BENGER | EE |  |  |  | 5.8085 | 5.7085 | 3.974 | 3.8169 | 3.674 | 3.5128 | 3.3495 | 3.2098 | 3.0342 | 2.9353 | 2.4077 | 2.17 | 2.0312 | 6.8916 | 6.8252 | 5.1377 | 5.0336 | 4.9428 | 4.8316 | 4.7051 | 4.602 | 4.4642 | 4.3949 | 4.0091 | 3.6346 | 3.0459 | 6.334 | 6.2463 | 4.523 | 4.3791 | 4.2557 | 4.1077 | 3.9485 | 3.8108 | 3.6251 | 3.5383 | 3.1026 | 2.8985 | 2.7853
|  | SUTTON BENGER | HT |  |  |  | 5.8575 | 5.7667 | 4.0189 | 3.8791 | 3.7546 | 3.6424 | 3.5465 | 3.4087 | 3.2649 | 3.1118 | 2.4812 | 2.1649 | 1.9281 | 6.9375 | 6.8906 | 5.204 | 5.1316 | 5.0663 | 4.9949 | 4.9469 | 4.8581 | 4.7642 | 4.6591 | 4.2887 | 4.1214 | 4.001 | 6.382 | 6.3034 | 4.573 | 4.4557 | 4.3444 | 4.2393 | 4.1526 | 4.021 | 3.8873 | 3.7424 | 3.171 | 2.8995 | 2.7026
|  | SUTTON BENGER | HE |  |  |  | 5.8554 | 5.7657 | 4.0444 | 3.9322 | 3.7924 | 3.6557 | 3.5598 | 3.423 | 3.2822 | 3.1363 | 2.4495 | 2.2138 | 2.0924 | 6.9293 | 6.8742 | 5.1959 | 5.1285 | 5.0408 | 4.9551 | 4.8908 | 4.7928 | 4.6877 | 4.5693 | 4.0346 | 3.652 | 3.0755 | 6.381 | 6.3024 | 4.5944 | 4.4965 | 4.372 | 4.2516 | 4.1649 | 4.0353 | 3.9036 | 3.7659 | 3.1404 | 2.9393 | 2.8434
|  | SUTTON BENGER | CF |  |  |  | 5.8901 | 5.7891 | 4.1251 | 4.07 | 3.9975 | 3.923 | 3.8424 | 3.772 | 3.6546 | 3.5322 | 2.9404 | 2.5393 | 2.1802 | 6.9579 | 6.8824 | 5.2346 | 5.1938 | 5.1357 | 5.0765 | 5.003 | 4.9387 | 4.8428 | 4.7387 | 4.1438 | 3.4244 | 2.2204 | 6.4116 | 6.3238 | 4.6628 | 4.6108 | 4.5455 | 4.4771 | 4.4026 | 4.3383 | 4.2332 | 4.121 | 3.5659 | 3.2169 | 2.9046
IVER 132KV | UPTON BSP | SUTTON LANE | MINIMUM HEADROOM | TQ 02185 78595 | YES | 6.009 | 14.1292 | 13.9271 | 9.6282 | 9.269 | 8.8088 | 8.3149 | 8.1863 | 7.5853 | 6.9802 | 6.5414 | 4.8016 | 3.7261 | 3.4782 | 16.5853 | 16.3802 | 12.1016 | 11.7965 | 11.4159 | 11.0057 | 10.8527 | 10.3608 | 9.8547 | 9.4659 | 7.3894 | 3.2853 | -4.9718 | 14.9353 | 14.7149 | 10.4159 | 10.0761 | 9.6394 | 9.168 | 9.0302 | 8.4618 | 7.8924 | 7.4833 | 5.5935 | 4.4537 | 4.1435
|  | SUTTON LANE | EE |  |  |  | 14.1292 | 13.9271 | 9.6282 | 9.269 | 8.8088 | 8.3149 | 8.1863 | 7.5853 | 6.9802 | 6.5414 | 4.8016 | 3.92 | 4.1231 | 16.5853 | 16.3802 | 12.1016 | 11.7965 | 11.4159 | 11.0057 | 10.8527 | 10.3608 | 9.8547 | 9.4659 | 7.3894 | 5.0465 | 1.3629 | 14.9353 | 14.7149 | 10.4159 | 10.0761 | 9.6394 | 9.168 | 9.0302 | 8.4618 | 7.8924 | 7.4833 | 5.9353 | 5.1669 | 5.3465
|  | SUTTON LANE | HT |  |  |  | 14.268 | 14.1118 | 9.92 | 9.6659 | 9.3496 | 9.0414 | 8.6261 | 8.1149 | 7.572 | 7.4169 | 5.0231 | 3.7261 | 3.6363 | 16.7639 | 16.6516 | 12.4884 | 12.3169 | 12.0843 | 11.87 | 11.5945 | 11.2567 | 10.8965 | 10.8486 | 9.3588 | 8.6261 | 8.4455 | 15.1159 | 14.9547 | 10.7414 | 10.4986 | 10.1802 | 9.8812 | 9.469 | 8.9894 | 8.4771 | 8.3547 | 6.1629 | 4.9955 | 4.9302
|  | SUTTON LANE | HE |  |  |  | 14.2598 | 14.1088 | 9.9241 | 9.6771 | 9.3629 | 9.0598 | 8.6618 | 8.1873 | 7.6608 | 7.4761 | 5.019 | 3.8047 | 3.4782 | 16.718 | 16.5669 | 12.3659 | 12.1414 | 11.8557 | 11.5822 | 11.2302 | 10.8078 | 10.3496 | 10.1659 | 7.7159 | 5.1996 | 1.3557 | 15.1047 | 14.9506 | 10.7465 | 10.5098 | 10.1996 | 9.9098 | 9.519 | 9.0516 | 8.5527 | 8.1537 | 5.5935 | 4.4537 | 4.1435
|  | SUTTON LANE | CF |  |  |  | 14.368 | 14.2884 | 10.1935 | 10.068 | 9.9424 | 9.6812 | 9.4343 | 9.2384 | 8.969 | 8.6884 | 7.3945 | 5.4629 | 3.8649 | 16.7782 | 16.6496 | 12.4904 | 12.3006 | 12.1169 | 11.8271 | 11.5057 | 11.1894 | 10.8139 | 10.4078 | 7.9088 | 3.2853 | -4.9718 | 15.2047 | 15.1129 | 10.9976 | 10.8496 | 10.722 | 10.4873 | 10.2506 | 10.0629 | 9.7996 | 9.5261 | 8.02 | 6.0608 | 4.5169
MANNINGTON GSP | WAREHAM | SWANAGE | MINIMUM HEADROOM | SZ 02010 79296 | YES | 0.926 | 3.3867 | 27.8214 | 27.4398 | 26.9796 | 26.3949 | 26.098 | 25.2204 | 24.3541 | 23.5133 | 22.8745 | 19.4684 | 16.552 | 15.0082 | 5.3745 | 28.1949 | 27.899 | 27.5357 | 27.0816 | 26.8837 | 26.299 | 25.6806 | 25.0633 | 24.599 | 22.0296 | 19.3153 | 11.9918 | 3.8633 | 27.2959 | 26.9153 | 26.448 | 25.8684 | 25.6551 | 24.8439 | 24.0143 | 23.202 | 22.6173 | 19.7041 | 17.0949 | 15.7643
|  | SWANAGE | EE |  |  |  | 3.3867 | 27.8214 | 27.4398 | 26.9796 | 26.3949 | 26.098 | 25.2204 | 24.3541 | 23.5133 | 22.8745 | 19.5398 | 17.1724 | 15.2622 | 5.3745 | 28.1949 | 27.899 | 27.5357 | 27.0816 | 26.8837 | 26.299 | 25.6806 | 25.0633 | 24.599 | 22.0296 | 19.3735 | 15.3755 | 3.8633 | 27.2959 | 26.9153 | 26.448 | 25.8684 | 25.6551 | 24.8439 | 24.0143 | 23.202 | 22.6173 | 19.7235 | 17.6694 | 15.9898
|  | SWANAGE | HT |  |  |  | 3.5633 | 28.0694 | 27.7745 | 27.4245 | 27.0133 | 26.4429 | 25.6031 | 25.1459 | 24.3969 | 23.6255 | 19.4684 | 16.552 | 15.0082 | 5.552 | 28.4663 | 28.2867 | 28.0571 | 27.8051 | 27.4551 | 26.9929 | 26.8061 | 26.3724 | 25.9235 | 23.6663 | 22.2551 | 21.598 | 4.0602 | 27.5765 | 27.2908 | 26.9469 | 26.5633 | 26.0316 | 25.2663 | 24.9122 | 24.2122 | 23.4857 | 19.7041 | 17.0949 | 15.7643
|  | SWANAGE | HE |  |  |  | 3.5612 | 28.0908 | 27.8245 | 27.5051 | 27.1306 | 26.6092 | 25.8949 | 25.5694 | 24.9643 | 24.3388 | 20.9786 | 18.6827 | 17.652 | 5.5153 | 28.4133 | 28.2071 | 27.9592 | 27.6745 | 27.2959 | 26.8204 | 26.6173 | 26.1684 | 25.6939 | 22.9337 | 20.252 | 16.6714 | 4.0571 | 27.5939 | 27.3357 | 27.0204 | 26.6755 | 26.1867 | 25.5347 | 25.2959 | 24.7255 | 24.1337 | 21.0806 | 19.0816 | 18.2143
|  | SWANAGE | CF |  |  |  | 3.6929 | 28.3296 | 28.1714 | 27.9806 | 27.7031 | 27.3816 | 27.0296 | 26.7071 | 26.3878 | 26.4337 | 24.348 | 22.0061 | 19.752 | 5.5816 | 28.5306 | 28.3673 | 28.1745 | 27.9184 | 27.6184 | 27.2653 | 26.8898 | 26.501 | 26.3857 | 23.6439 | 19.3153 | 11.9918 | 4.1786 | 27.8163 | 27.6561 | 27.4622 | 27.1959 | 26.9092 | 26.5776 | 26.2541 | 25.9245 | 26.0153 | 23.9949 | 21.9071 | 19.9949
MINETY GSP | SWINDON BSP | SWINDON | MINIMUM HEADROOM | SU 12449 86967 | YES | 3.123 | 24.2293 | 23.711 | 22.713 | 21.6069 | 20.4763 | 18.9355 | 16.6355 | 14.0426 | 11.4702 | 9.6212 | 0.45791 | -6.9003 | -10.5145 | 27.8232 | 27.4089 | 26.612 | 25.7314 | 24.7804 | 23.4304 | 21.7804 | 19.8722 | 17.9538 | 16.5895 | 9.5579 | 0.014033 | -22.1003 | 21.7651 | 21.3089 | 20.3375 | 19.2538 | 18.1253 | 16.5804 | 14.4079 | 11.9304 | 9.4753 | 7.8232 | 0.086482 | -6.3309 | -9.3421
|  | SWINDON | EE |  |  |  | 24.2293 | 23.711 | 22.713 | 21.6069 | 20.4763 | 18.9355 | 16.6355 | 14.0426 | 11.4702 | 9.6212 | 0.86607 | -5.6523 | -9.439 | 27.8232 | 27.4089 | 26.612 | 25.7314 | 24.7804 | 23.4304 | 21.7804 | 19.8722 | 17.9538 | 16.5895 | 9.5579 | 1.7589 | -9.4452 | 21.7651 | 21.3089 | 20.3375 | 19.2538 | 18.1253 | 16.5804 | 14.4079 | 11.9304 | 9.4753 | 7.8232 | 0.35995 | -5.24 | -8.4554
|  | SWINDON | HT |  |  |  | 24.7181 | 23.9151 | 23.3079 | 22.4906 | 21.2344 | 19.9406 | 17.8885 | 15.7059 | 13.5008 | 11.3671 | 0.45791 | -6.9003 | -10.5145 | 28.3385 | 27.8559 | 27.5375 | 27.0324 | 26.113 | 25.1844 | 23.9926 | 22.7028 | 21.3967 | 20.1569 | 14.3559 | 10.8263 | 9.1151 | 22.3161 | 21.5702 | 21.0548 | 20.2814 | 19.0651 | 17.8232 | 15.961 | 13.9548 | 11.9171 | 9.9324 | 0.086482 | -6.3309 | -9.3421
|  | SWINDON | HE |  |  |  | 24.7436 | 24.0875 | 23.5967 | 22.8242 | 21.9753 | 20.7875 | 19.0804 | 17.161 | 15.1946 | 13.2487 | 4.1038 | -2.3421 | -5.2115 | 28.2324 | 27.7079 | 27.3048 | 26.6804 | 25.9732 | 24.9059 | 23.6508 | 22.2028 | 20.6916 | 19.1691 | 11.2304 | 3.2906 | -7.4523 | 22.3283 | 21.7028 | 21.2865 | 20.5589 | 19.7528 | 18.5906 | 17.0161 | 15.2263 | 13.3865 | 11.5559 | 3.2528 | -2.2666 | -4.6482
|  | SWINDON | CF |  |  |  | 25.1151 | 24.763 | 24.3151 | 24.164 | 23.6895 | 23.16 | 22.4416 | 21.5783 | 20.614 | 19.6559 | 13.1079 | 6.0712 | -0.66862 | 28.413 | 28.0038 | 27.4936 | 27.212 | 26.6406 | 25.9559 | 25.0161 | 23.9008 | 22.6875 | 21.4283 | 12.8957 | 0.014033 | -22.1003 | 22.6681 | 22.314 | 21.8446 | 21.7477 | 21.2804 | 20.7589 | 20.0457 | 19.1814 | 18.2242 | 17.2702 | 10.9763 | 4.8416 | -0.78801
BRAMLEY (ANDO-THAT) | THATCHAM BSP | TADLEY | MINIMUM HEADROOM | SU 57753 62717 | YES | 0.109 | 18.1686 | 17.9022 | 17.639 | 17.3176 | 16.9665 | 16.9543 | 16.391 | 15.7533 | 15.1114 | 14.6502 | 11.9431 | 9.991 | 8.8869 | 19.2731 | 19.0414 | 18.8108 | 18.5169 | 18.1843 | 18.2118 | 17.8129 | 17.3486 | 16.8802 | 16.5649 | 14.8169 | 12.5363 | 7.0516 | 18.1778 | 17.8961 | 17.6124 | 17.2635 | 16.8747 | 16.9135 | 16.3767 | 15.7665 | 15.1563 | 14.7461 | 12.5461 | 10.8573 | 9.8665
|  | TADLEY | EE |  |  |  | 18.1686 | 17.9022 | 17.639 | 17.3176 | 16.9665 | 16.9543 | 16.391 | 15.7533 | 15.1114 | 14.6502 | 12.1665 | 10.4165 | 9.1237 | 19.2731 | 19.0414 | 18.8108 | 18.5169 | 18.1843 | 18.2118 | 17.8129 | 17.3486 | 16.8802 | 16.5649 | 14.8169 | 12.9863 | 10.168 | 18.1778 | 17.8961 | 17.6124 | 17.2635 | 16.8747 | 16.9135 | 16.3767 | 15.7665 | 15.1563 | 14.7461 | 12.6992 | 11.239 | 10.0798
|  | TADLEY | HT |  |  |  | 18.2808 | 18.0563 | 17.8349 | 17.5716 | 17.339 | 17.042 | 16.4706 | 16.1737 | 15.6022 | 15.0165 | 11.9431 | 9.991 | 8.8869 | 19.4241 | 19.2731 | 19.1322 | 18.9414 | 18.7884 | 18.568 | 18.2435 | 18.1914 | 17.8578 | 17.518 | 15.9078 | 15.0741 | 14.6333 | 18.3237 | 18.1022 | 17.8859 | 17.6176 | 17.3839 | 17.0767 | 16.5441 | 16.3584 | 15.8288 | 15.2798 | 12.5461 | 10.8573 | 9.8665
|  | TADLEY | HE |  |  |  | 18.288 | 18.0818 | 17.8788 | 17.6359 | 17.4237 | 17.1461 | 16.6839 | 16.489 | 16.0186 | 15.5329 | 12.8676 | 11.0543 | 10.2165 | 19.3976 | 19.2312 | 19.0639 | 18.8557 | 18.6659 | 18.4139 | 18.071 | 17.9986 | 17.6424 | 17.2639 | 15.1424 | 13.2322 | 10.572 | 18.3237 | 18.1186 | 17.9186 | 17.6696 | 17.4533 | 17.1665 | 16.7196 | 16.6145 | 16.1655 | 15.6982 | 13.3124 | 11.7869 | 11.0288
|  | TADLEY | CF |  |  |  | 18.389 | 18.2655 | 18.1502 | 18.0073 | 17.8563 | 17.7288 | 17.542 | 17.3145 | 17.0665 | 17.1543 | 15.4155 | 13.5716 | 11.788 | 19.4476 | 19.3139 | 19.1833 | 19.02 | 18.8363 | 18.671 | 18.4231 | 18.121 | 17.7996 | 17.8088 | 15.671 | 12.5363 | 7.0516 | 18.4176 | 18.2859 | 18.1665 | 18.0094 | 17.84 | 17.7033 | 17.5012 | 17.2482 | 16.9727 | 17.1176 | 15.44 | 13.8206 | 12.391
IVER 132KV | SLOUGH | TAPLOW | MINIMUM HEADROOM | SU 91721 81234 | YES | 1.285 | 14.3082 | 13.9622 | 13.5133 | 13.0173 | 12.9163 | 12.4327 | 11.652 | 10.7551 | 9.852 | 9.2153 | 6.3847 | 4.35 | 3.8163 | 17.2918 | 16.9898 | 16.5878 | 16.1418 | 16.0102 | 15.55 | 14.9357 | 14.2173 | 13.4816 | 12.9388 | 9.8755 | 3.9439 | -8.4112 | 14.8367 | 14.499 | 14.0398 | 13.5347 | 13.5224 | 13.0459 | 12.3204 | 11.4765 | 10.6276 | 10.0429 | 7.4908 | 5.6847 | 5.2204
|  | TAPLOW | EE |  |  |  | 14.3082 | 13.9622 | 13.5133 | 13.0173 | 12.9163 | 12.4327 | 11.652 | 10.7551 | 9.852 | 9.2153 | 6.3847 | 4.7296 | 4.3714 | 17.2918 | 16.9898 | 16.5878 | 16.1418 | 16.0102 | 15.55 | 14.9357 | 14.2173 | 13.4816 | 12.9388 | 9.8755 | 6.201 | 0.36735 | 14.8367 | 14.499 | 14.0398 | 13.5347 | 13.5224 | 13.0459 | 12.3204 | 11.4765 | 10.6276 | 10.0429 | 7.4908 | 6.0388 | 5.7102
|  | TAPLOW | HT |  |  |  | 14.5337 | 14.2673 | 13.9327 | 13.6163 | 13.2296 | 12.8061 | 12.4918 | 11.7806 | 11.0337 | 10.2612 | 6.4929 | 4.35 | 3.8163 | 17.5327 | 17.3612 | 17.1286 | 16.9173 | 16.6398 | 16.3337 | 16.2296 | 15.8031 | 15.349 | 14.8663 | 12.6541 | 11.5082 | 11.1837 | 15.0888 | 14.8378 | 14.5071 | 14.2071 | 13.8245 | 13.4031 | 13.1735 | 12.5163 | 11.8194 | 11.099 | 7.6184 | 5.6847 | 5.2204
|  | TAPLOW | HE |  |  |  | 14.5327 | 14.2898 | 13.9796 | 13.6939 | 13.3398 | 12.949 | 12.7163 | 12.0867 | 11.4255 | 10.7388 | 7.6643 | 6.0194 | 5.5551 | 17.4704 | 17.2531 | 16.9643 | 16.6888 | 16.3388 | 15.95 | 15.7541 | 15.2286 | 14.6633 | 14.0592 | 10.599 | 6.848 | 0.95102 | 15.0827 | 14.8531 | 14.5439 | 14.2735 | 13.9204 | 13.5316 | 13.3786 | 12.7929 | 12.1704 | 11.5316 | 8.6816 | 7.2153 | 6.8143
|  | TAPLOW | CF |  |  |  | 14.6694 | 14.5061 | 14.3571 | 14.1602 | 13.9918 | 13.7633 | 13.4847 | 13.1418 | 13.2051 | 12.8816 | 10.6673 | 8.3122 | 6.1929 | 17.5327 | 17.3378 | 17.1224 | 16.8582 | 16.5959 | 16.2418 | 15.8153 | 15.3031 | 15.1061 | 14.5724 | 10.6929 | 3.9439 | -8.4112 | 15.2 | 15.0327 | 14.8755 | 14.6673 | 14.4949 | 14.252 | 13.9694 | 13.6133 | 13.7663 | 13.4469 | 11.352 | 9.2459 | 7.349
MANNINGTON GSP | SHAFTESBURY BSP | TARRANT RUSHTON | MINIMUM HEADROOM | ST 94510 07307 | YES | 0.744 | 3.6641 | 3.5661 | 3.4345 | 3.2967 | 3.1263 | 2.9294 | 2.7376 | 2.4763 | 2.211 | 2.0059 | 1.4478 | 1.1233 | 0.91102 | 4.8702 | 4.8059 | 4.7192 | 4.6273 | 4.5212 | 4.3978 | 4.2876 | 4.1569 | 4.0233 | 3.911 | 3.559 | 3.2722 | 2.4651 | 3.4508 | 3.3406 | 3.1804 | 3.0324 | 2.8447 | 2.6253 | 2.4447 | 2.21 | 1.9753 | 1.8039 | 1.3192 | 1.0386 | 0.86306
|  | TARRANT RUSHTON | EE |  |  |  | 3.6641 | 3.5661 | 3.4345 | 3.2967 | 3.1263 | 2.9294 | 2.7376 | 2.4763 | 2.211 | 2.0059 | 1.4478 | 1.162 | 0.96918 | 4.8702 | 4.8059 | 4.7192 | 4.6273 | 4.5212 | 4.3978 | 4.2876 | 4.1569 | 4.0233 | 3.911 | 3.559 | 3.2794 | 2.8896 | 3.4508 | 3.3406 | 3.1804 | 3.0324 | 2.8447 | 2.6253 | 2.4447 | 2.21 | 1.9753 | 1.8039 | 1.3192 | 1.0794 | 0.91612
|  | TARRANT RUSHTON | HT |  |  |  | 3.7049 | 3.6222 | 3.509 | 3.3824 | 3.2273 | 3.062 | 2.8712 | 2.6365 | 2.3906 | 2.1712 | 1.4631 | 1.1233 | 0.91102 | 4.8927 | 4.8416 | 4.7641 | 4.6855 | 4.5876 | 4.4937 | 4.3906 | 4.2794 | 4.1682 | 4.0631 | 3.7284 | 3.5773 | 3.4824 | 3.4906 | 3.3957 | 3.259 | 3.1161 | 2.9386 | 2.758 | 2.5702 | 2.3661 | 2.1518 | 1.9733 | 1.3365 | 1.0386 | 0.86306
|  | TARRANT RUSHTON | HE |  |  |  | 3.7008 | 3.6151 | 3.4988 | 3.3702 | 3.212 | 3.0416 | 2.8671 | 2.6682 | 2.4376 | 2.2294 | 1.5549 | 1.262 | 1.1161 | 4.8886 | 4.8314 | 4.7539 | 4.6682 | 4.5661 | 4.4651 | 4.36 | 4.2467 | 4.1284 | 4.0161 | 3.5927 | 3.2937 | 2.9131 | 3.4865 | 3.3947 | 3.2631 | 3.1212 | 2.9478 | 2.7702 | 2.5927 | 2.3978 | 2.1967 | 2.0273 | 1.4273 | 1.1773 | 1.0569
|  | TARRANT RUSHTON | CF |  |  |  | 3.7273 | 3.6631 | 3.5824 | 3.4814 | 3.3641 | 3.2324 | 3.109 | 2.9416 | 2.7712 | 2.5927 | 2.0886 | 1.7222 | 1.3804 | 4.8957 | 4.8447 | 4.7814 | 4.709 | 4.6263 | 4.5304 | 4.4488 | 4.3549 | 4.261 | 4.161 | 3.7641 | 3.2722 | 2.4651 | 3.5018 | 3.4222 | 3.3233 | 3.2059 | 3.0671 | 2.908 | 2.7896 | 2.6488 | 2.5049 | 2.3518 | 1.8978 | 1.5631 | 1.2763
MANNINGTON GSP | SALISBURY | TEFFONT | MINIMUM HEADROOM | ST 99837 30994 | YES | 0.145 | 2.951 | 2.8745 | 2.7694 | 2.649 | 2.5602 | 2.4286 | 2.2622 | 2.1204 | 1.9184 | 1.8378 | 1.35 | 1.1724 | 1.0082 | 4.2612 | 4.199 | 4.1122 | 4.0092 | 3.9378 | 3.8224 | 3.6827 | 3.5673 | 3.4061 | 3.3643 | 3.2082 | 2.7694 | 1.6816 | 2.9918 | 2.9531 | 2.898 | 2.801 | 2.7224 | 2.602 | 2.4367 | 2.2888 | 2.0827 | 2.0235 | 1.602 | 1.449 | 1.3082
|  | TEFFONT | EE |  |  |  | 2.951 | 2.8745 | 2.7694 | 2.649 | 2.5602 | 2.4286 | 2.2622 | 2.1204 | 1.9184 | 1.8378 | 1.35 | 1.1724 | 1.0908 | 4.2612 | 4.199 | 4.1122 | 4.0092 | 3.9378 | 3.8224 | 3.6827 | 3.5673 | 3.4061 | 3.3643 | 3.2082 | 2.9316 | 2.4112 | 2.9918 | 2.9531 | 2.898 | 2.801 | 2.7224 | 2.602 | 2.4367 | 2.2888 | 2.0827 | 2.0235 | 1.602 | 1.449 | 1.3776
|  | TEFFONT | HT |  |  |  | 2.9949 | 2.9276 | 2.8459 | 2.7786 | 2.698 | 2.5959 | 2.501 | 2.3622 | 2.2122 | 2.0582 | 1.4449 | 1.1857 | 1.0082 | 4.3286 | 4.2827 | 4.2194 | 4.1765 | 4.1153 | 4.0398 | 3.9837 | 3.8786 | 3.7663 | 3.649 | 3.2847 | 3.2245 | 3.1776 | 3.0163 | 2.9837 | 2.9429 | 2.8918 | 2.8255 | 2.7418 | 2.6561 | 2.5347 | 2.4071 | 2.2612 | 1.6888 | 1.4592 | 1.3082
|  | TEFFONT | HE |  |  |  | 2.9929 | 2.9276 | 2.849 | 2.7857 | 2.7071 | 2.6082 | 2.5194 | 2.3827 | 2.2378 | 2.0857 | 1.4296 | 1.2582 | 1.1816 | 4.3276 | 4.2816 | 4.2184 | 4.1765 | 4.1163 | 4.0398 | 3.9847 | 3.8816 | 3.7684 | 3.648 | 3.2694 | 2.9724 | 2.4531 | 3.0173 | 2.9847 | 2.9449 | 2.8959 | 2.8286 | 2.752 | 2.6673 | 2.55 | 2.4265 | 2.2878 | 1.6786 | 1.5306 | 1.4673
|  | TEFFONT | CF |  |  |  | 2.999 | 2.9459 | 2.8888 | 2.8194 | 2.7714 | 2.7041 | 2.6245 | 2.5337 | 2.4745 | 2.3776 | 1.8806 | 1.5255 | 1.251 | 4.3296 | 4.299 | 4.2582 | 4.2061 | 4.1776 | 4.1306 | 4.0694 | 3.9908 | 3.948 | 3.8684 | 3.4031 | 2.7694 | 1.6816 | 3.0194 | 2.9908 | 2.9602 | 2.9204 | 2.8776 | 2.8224 | 2.7561 | 2.6827 | 2.6265 | 2.5408 | 2.0929 | 1.7663 | 1.5255
BRAMLEY (FLEE) | MAIDENHEAD BSP | TEMPLE FARM | MINIMUM HEADROOM | SU 84178 83872 | YES | 0.258 | 2.3122 | 2.2786 | 2.2378 | 2.1857 | 2.149 | 2.0939 | 2.0286 | 1.9459 | 1.8918 | 1.8347 | 1.5388 | 1.4163 | 1.35 | 3.0857 | 3.0612 | 3.0367 | 3.002 | 2.9796 | 2.9408 | 2.8959 | 2.8418 | 2.798 | 2.7602 | 2.5714 | 2.398 | 1.951 | 2.3531 | 2.3204 | 2.2806 | 2.2316 | 2.1888 | 2.1337 | 2.0714 | 1.9939 | 1.9357 | 1.8796 | 1.6051 | 1.4918 | 1.4316
|  | TEMPLE FARM | EE |  |  |  | 2.3122 | 2.2786 | 2.2378 | 2.1857 | 2.149 | 2.0939 | 2.0286 | 1.9459 | 1.8918 | 1.8347 | 1.6041 | 1.5541 | 1.5378 | 3.0857 | 3.0612 | 3.0367 | 3.002 | 2.9796 | 2.9408 | 2.8959 | 2.8418 | 2.798 | 2.7602 | 2.6173 | 2.4816 | 2.2684 | 2.3531 | 2.3204 | 2.2806 | 2.2316 | 2.1888 | 2.1337 | 2.0714 | 1.9939 | 1.9357 | 1.8796 | 1.6714 | 1.6245 | 1.6092
|  | TEMPLE FARM | HT |  |  |  | 2.3388 | 2.3092 | 2.2806 | 2.2418 | 2.2092 | 2.1673 | 2.1071 | 2.0673 | 2.001 | 1.9418 | 1.652 | 1.5378 | 1.4643 | 3.1061 | 3.0908 | 3.0704 | 3.049 | 3.0296 | 3.0051 | 2.9724 | 2.9367 | 2.8908 | 2.8459 | 2.6541 | 2.5837 | 2.5429 | 2.3816 | 2.3541 | 2.3255 | 2.2908 | 2.2541 | 2.2133 | 2.1602 | 2.1092 | 2.0469 | 1.9837 | 1.7143 | 1.6061 | 1.5408
|  | TEMPLE FARM | HE |  |  |  | 2.3388 | 2.3082 | 2.2786 | 2.2408 | 2.2071 | 2.1643 | 2.1061 | 2.0429 | 1.9694 | 1.8939 | 1.5388 | 1.4163 | 1.35 | 3.102 | 3.0837 | 3.0643 | 3.0378 | 3.0163 | 2.9847 | 2.9459 | 2.9102 | 2.8612 | 2.8071 | 2.5714 | 2.4745 | 2.2612 | 2.3786 | 2.349 | 2.3184 | 2.2806 | 2.2398 | 2.1949 | 2.1378 | 2.0786 | 2.0112 | 1.9367 | 1.6051 | 1.4918 | 1.4316
|  | TEMPLE FARM | CF |  |  |  | 2.3469 | 2.3184 | 2.2898 | 2.2704 | 2.2388 | 2.2122 | 2.1755 | 2.1347 | 2.1112 | 2.0673 | 1.8092 | 1.6041 | 1.4582 | 3.1071 | 3.0898 | 3.0684 | 3.0551 | 3.0286 | 3.0102 | 2.9796 | 2.9469 | 2.9204 | 2.8857 | 2.6582 | 2.398 | 1.951 | 2.3898 | 2.3653 | 2.3378 | 2.3184 | 2.2888 | 2.2653 | 2.2306 | 2.1918 | 2.1673 | 2.1194 | 1.8561 | 1.6643 | 1.5286
MELKSHAM GSP | CHIPPENHAM | TETBURY | MINIMUM HEADROOM | ST 89708 93444 | YES | 2.114 | 5.1986 | 5.0364 | 4.816 | 4.6099 | 4.3354 | 4.0323 | 3.5915 | 3.4833 | 3.068 | 2.7456 | 1.0507 | -0.30136 | -1.1146 | 4.5549 | 4.4263 | 4.2436 | 4.0804 | 3.8538 | 3.6059 | 3.2926 | 3.2814 | 2.9783 | 2.7794 | 1.6426 | 0.42527 | -2.69 | 5.029 | 4.8658 | 4.6229 | 4.4148 | 4.128 | 3.8148 | 3.378 | 3.4178 | 3.0229 | 2.726 | 1.3341 | 0.16272 | -0.49749
|  | TETBURY | EE |  |  |  | 5.1986 | 5.0364 | 4.816 | 4.6099 | 4.3354 | 4.0323 | 3.5915 | 3.4833 | 3.068 | 2.7772 | 1.1262 | -0.023812 | -0.89422 | 4.5549 | 4.4263 | 4.2436 | 4.0804 | 3.8538 | 3.6059 | 3.2926 | 3.2814 | 2.9783 | 2.7794 | 1.6426 | 0.48139 | -1.1727 | 5.029 | 4.8658 | 4.6229 | 4.4148 | 4.128 | 3.8148 | 3.378 | 3.4178 | 3.0229 | 2.776 | 1.378 | 0.39945 | -0.31789
|  | TETBURY | HT |  |  |  | 5.2935 | 5.1476 | 4.9762 | 4.8139 | 4.5884 | 4.3282 | 3.9946 | 3.5915 | 3.1721 | 2.7456 | 1.0507 | -0.30136 | -1.1146 | 4.662 | 4.5702 | 4.4528 | 4.3477 | 4.1977 | 4.0232 | 3.8447 | 3.5987 | 3.3406 | 3.0712 | 2.2834 | 1.662 | 1.3222 | 5.1586 | 5.0209 | 4.8495 | 4.6974 | 4.4729 | 4.2188 | 3.928 | 3.5474 | 3.1423 | 2.726 | 1.3341 | 0.16272 | -0.49749
|  | TETBURY | HE |  |  |  | 5.2935 | 5.1629 | 5.0027 | 4.8578 | 4.6588 | 4.4282 | 4.1466 | 3.8017 | 3.4415 | 3.0813 | 1.6486 | 0.51802 | -0.052384 | 4.6416 | 4.5416 | 4.412 | 4.2998 | 4.1406 | 3.9579 | 3.7753 | 3.5222 | 3.2528 | 2.9712 | 1.9396 | 0.76609 | -0.76555 | 5.1556 | 5.0301 | 4.8709 | 4.7321 | 4.5341 | 4.3015 | 4.0535 | 3.7188 | 3.3658 | 3.0046 | 1.8535 | 0.90353 | 0.44435
|  | TETBURY | CF |  |  |  | 5.3558 | 5.2762 | 5.1711 | 5.0568 | 4.9731 | 4.8497 | 4.7058 | 4.5721 | 4.3854 | 4.1976 | 3.2629 | 2.0497 | 0.96088 | 4.6763 | 4.5998 | 4.4977 | 4.3824 | 4.2926 | 4.1579 | 3.9967 | 3.8436 | 3.6406 | 3.4253 | 2.3202 | 0.42527 | -2.69 | 5.2127 | 5.1311 | 5.0178 | 4.8984 | 4.8107 | 4.676 | 4.5229 | 4.3882 | 4.1811 | 3.9678 | 3.2188 | 2.1862 | 1.276
BRAMLEY (ANDO-THAT) | THATCHAM BSP | THATCHAM | MINIMUM HEADROOM | SU 52758 66466 | YES | 6.311 | 1.5929 | 0.83367 | 0.45816 | -0.24898 | -1.0724 | -1.8776 | -3.2929 | -5.0776 | -7.0714 | -8.498 | -16.4439 | -21.0827 | -23.498 | 11.5929 | 10.9663 | 10.6867 | 10.0959 | 9.4286 | 8.7745 | 7.8469 | 6.6837 | 5.4153 | 4.5684 | -0.018367 | -4.6541 | -15.6051 | 2.2847 | 1.5959 | 1.2714 | 0.64184 | -0.078571 | -0.77143 | -2.0296 | -3.6357 | -5.4071 | -6.651 | -13.698 | -17.8245 | -19.9082
|  | THATCHAM | EE |  |  |  | 1.5929 | 0.83367 | 0.45816 | -0.24898 | -1.0724 | -1.8776 | -3.2929 | -5.0776 | -7.0714 | -8.498 | -15.9051 | -20.2214 | -23.0888 | 11.5929 | 10.9663 | 10.6867 | 10.0959 | 9.4286 | 8.7745 | 7.8469 | 6.6837 | 5.4153 | 4.5684 | -0.018367 | -4.2561 | -10.0918 | 2.2847 | 1.5959 | 1.2714 | 0.64184 | -0.078571 | -0.77143 | -2.0296 | -3.6357 | -5.4071 | -6.651 | -13.1959 | -17.048 | -19.549
|  | THATCHAM | HT |  |  |  | 1.8694 | 1.2092 | 0.6102 | -0.063265 | -0.4898 | -1.1939 | -2.5878 | -4.348 | -6.0857 | -7.7888 | -16.4439 | -21.0827 | -23.498 | 11.9071 | 11.4429 | 11.0388 | 10.5612 | 10.3816 | 9.948 | 9.2337 | 8.3245 | 7.4071 | 6.4878 | 2.1449 | 0.13776 | -0.86633 | 2.5163 | 1.9082 | 1.3673 | 0.75714 | 0.39286 | -0.22449 | -1.4633 | -3.002 | -4.5245 | -6.0194 | -13.698 | -17.8245 | -19.9082
|  | THATCHAM | HE |  |  |  | 1.8918 | 1.2786 | 0.72653 | 0.10714 | -0.21735 | -0.82653 | -1.8888 | -3.302 | -4.9296 | -6.401 | -14.099 | -18.3673 | -20.2582 | 11.8592 | 11.3612 | 10.9102 | 10.3908 | 10.1796 | 9.701 | 9.0224 | 8.1398 | 7.1306 | 6.1612 | 0.9051 | -3.3724 | -8.8143 | 2.5378 | 1.9735 | 1.4745 | 0.91224 | 0.63571 | 0.10204 | -0.83776 | -2.0673 | -3.4735 | -4.7531 | -11.5561 | -15.3786 | -17.0133
|  | THATCHAM | CF |  |  |  | 2.0633 | 1.6582 | 1.2949 | 0.88265 | 0.45918 | 0.47551 | 0.13878 | -0.33469 | -0.92143 | -1.5684 | -7.3286 | -13.0663 | -16.7602 | 11.9327 | 11.5388 | 11.1724 | 10.7459 | 10.301 | 10.2255 | 9.7949 | 9.248 | 8.6276 | 7.95 | 2.6602 | -4.6541 | -15.6051 | 2.702 | 2.3184 | 1.9959 | 1.6214 | 1.2418 | 1.2714 | 0.97653 | 0.57143 | 0.071429 | -0.47449 | -5.449 | -10.4765 | -13.901
NORTH HYDE GSP | NORTH HYDE 22kV | THE GREEN | MINIMUM HEADROOM | TQ 12414 79503 | YES | 3.33 | 5.6446 | 4.1977 | 1.912 | -1.6758 | -7.1363 | -10.2281 | -11.6557 | -12.3537 | -12.0394 | -11.6496 | -9.3628 | -9.4139 | -9.371 | 8.4469 | 7.6398 | 6.3929 | 4.5255 | 0.6813 | -0.85442 | -1.782 | -2.3595 | -2.4483 | -2.485 | -3.4095 | -7.186 | -14.6636 | 6.502 | 5.3337 | 3.4745 | 0.60102 | -4.2922 | -6.8544 | -8.0167 | -8.6044 | -8.3809 | -8.0534 | -6.2697 | -6.3503 | -6.3309
|  | THE GREEN | EE |  |  |  | 5.6446 | 4.1977 | 1.912 | -1.6758 | -7.1363 | -10.2281 | -11.6557 | -12.3537 | -12.0394 | -11.6496 | -9.3628 | -9.2547 | -9.0332 | 8.4469 | 7.6398 | 6.3929 | 4.5255 | 0.6813 | -0.85442 | -1.782 | -2.3595 | -2.4483 | -2.485 | -2.9432 | -4.9738 | -8.6932 | 6.502 | 5.3337 | 3.4745 | 0.60102 | -4.2922 | -6.8544 | -8.0167 | -8.6044 | -8.3809 | -8.0534 | -6.2697 | -6.2197 | -6.1034
|  | THE GREEN | HT |  |  |  | 5.7355 | 4.3161 | 2.0885 | -1.4645 | -6.8588 | -9.8639 | -11.2343 | -11.8363 | -11.4057 | -10.9618 | -9.1322 | -9.4139 | -9.371 | 8.5724 | 7.8357 | 6.6612 | 4.8745 | 1.1435 | -0.24421 | -1.0473 | -1.4565 | -1.3799 | -1.283 | -0.85952 | -1.2095 | -1.2697 | 6.6031 | 5.4673 | 3.6765 | 0.8449 | -3.9748 | -6.4381 | -7.5442 | -8.0269 | -7.7146 | -7.3697 | -6.0116 | -6.3503 | -6.3309
|  | THE GREEN | HE |  |  |  | 5.7355 | 4.3253 | 2.1099 | -1.4329 | -6.8108 | -9.819 | -11.1363 | -11.6985 | -11.2332 | -10.7353 | -8.3108 | -8.1057 | -8.1179 | 8.5378 | 7.7673 | 6.5439 | 4.7122 | 0.9313 | -0.53809 | -1.3891 | -1.8718 | -1.8769 | -1.8789 | -2.2963 | -4.2983 | -8.0769 | 6.602 | 5.4765 | 3.6918 | 0.87245 | -3.9269 | -6.3942 | -7.4452 | -7.8901 | -7.5391 | -7.1524 | -5.2636 | -5.1575 | -5.1748
|  | THE GREEN | CF |  |  |  | 5.8467 | 4.5946 | 2.6385 | -0.45536 | -5.3322 | -7.8251 | -9.2455 | -9.9934 | -9.8292 | -9.67 | -9.1567 | -8.8771 | -8.5843 | 8.5837 | 7.8653 | 6.7357 | 5.0633 | 1.4578 | 0.14967 | -0.79829 | -1.3942 | -1.5636 | -1.7585 | -3.4095 | -7.186 | -14.6636 | 6.701 | 5.7122 | 4.1469 | 1.7133 | -2.6626 | -4.6912 | -5.8187 | -6.4034 | -6.2901 | -6.184 | -5.8024 | -5.6881 | -5.536
BRAMLEY (FLEE) | READING TOWN BSP | THE MALL | MINIMUM HEADROOM | SU 71319 73293 | YES | 5.109 | 12.5561 | 12.3867 | 12.2051 | 11.704 | 9.901 | 8.9204 | 8.354 | 7.6755 | 6.8949 | 6.2408 | 5.2836 | 4.5 | 4.4959 | 15.3928 | 15.2612 | 15.15 | 14.8775 | 13.1316 | 12.5081 | 12.0643 | 11.5255 | 10.9183 | 10.3724 | 8.2377 | 3.3092 | -6.2827 | 13.3745 | 13.2459 | 13.1265 | 12.7581 | 11.101 | 10.2132 | 9.6551 | 8.9479 | 8.1683 | 7.5571 | 6.5296 | 5.8316 | 5.8204
|  | THE MALL | EE |  |  |  | 12.5561 | 12.3867 | 12.2051 | 11.704 | 9.901 | 8.9204 | 8.354 | 7.6755 | 6.8949 | 6.2408 | 5.2836 | 4.7694 | 4.8959 | 15.3928 | 15.2612 | 15.15 | 14.8775 | 13.1316 | 12.5081 | 12.0643 | 11.5255 | 10.9183 | 10.3724 | 8.2377 | 5.5306 | 0.92038 | 13.3745 | 13.2459 | 13.1265 | 12.7581 | 11.101 | 10.2132 | 9.6551 | 8.9479 | 8.1683 | 7.5571 | 6.5296 | 6.0979 | 6.1255
|  | THE MALL | HT |  |  |  | 12.6357 | 12.5265 | 12.4102 | 11.9653 | 10.2602 | 9.2602 | 8.65 | 8.0387 | 7.4663 | 6.8826 | 5.5367 | 4.5 | 4.4959 | 15.4755 | 15.3867 | 15.3398 | 15.1979 | 13.5234 | 13.1714 | 12.8602 | 12.5285 | 12.1877 | 11.8122 | 10.7755 | 10.0724 | 9.9724 | 13.45 | 13.3469 | 13.2734 | 13.0326 | 11.4663 | 10.6285 | 10.1214 | 9.603 | 9.0755 | 8.4826 | 6.8449 | 5.8316 | 5.8204
|  | THE MALL | HE |  |  |  | 12.6306 | 12.5275 | 12.4224 | 11.9928 | 10.3112 | 9.4561 | 8.9979 | 8.4643 | 7.8581 | 7.2551 | 6.4143 | 5.9224 | 5.8714 | 15.451 | 15.3357 | 15.2612 | 15.0908 | 13.3816 | 12.8775 | 12.5326 | 12.1296 | 11.6561 | 11.15 | 9.0163 | 6.2571 | 1.6489 | 13.4428 | 13.3367 | 13.2632 | 13.0245 | 11.5102 | 10.7836 | 10.4 | 9.9459 | 9.4438 | 8.8969 | 7.7571 | 7.2877 | 7.2479
|  | THE MALL | CF |  |  |  | 12.6765 | 12.603 | 12.552 | 12.2357 | 10.6673 | 10.1847 | 10.101 | 9.9387 | 9.704 | 9.4102 | 7.4622 | 6.4592 | 5.5612 | 15.4775 | 15.3704 | 15.2979 | 15.1408 | 13.4602 | 13.0836 | 12.8316 | 12.5214 | 12.1592 | 11.7418 | 8.5183 | 3.3092 | -6.2827 | 13.4979 | 13.4214 | 13.3755 | 13.1857 | 11.7663 | 11.4275 | 11.3357 | 11.1908 | 10.9836 | 10.7316 | 8.8428 | 7.7479 | 6.9357
BRAMLEY (FLEE) | BURGHFIELD RESERVE | THEALE | MINIMUM HEADROOM | SU 64755 71015 | YES | 6.205 | 13.6782 | 13.3567 | 12.9731 | 12.5302 | 12.0435 | 11.4506 | 10.9159 | 10.2782 | 9.6649 | 9.1414 | 6.6924 | 5.57 | 3.8502 | 15.8669 | 15.6486 | 15.3894 | 15.069 | 14.719 | 14.2649 | 13.8465 | 13.3516 | 12.8741 | 12.471 | 10.5853 | 9.7363 | 8.0818 | 14.1629 | 13.8322 | 13.4659 | 13.0486 | 12.5914 | 12.0404 | 11.5312 | 10.922 | 10.3312 | 9.8343 | 7.47 | 6.3904 | 4.688
|  | THEALE | EE |  |  |  | 13.6782 | 13.3567 | 12.9731 | 12.5302 | 12.0435 | 11.4506 | 10.9159 | 10.2782 | 9.6649 | 9.1414 | 7.4567 | 7.119 | 5.8227 | 15.8669 | 15.6486 | 15.3894 | 15.069 | 14.719 | 14.2649 | 13.8465 | 13.3516 | 12.8741 | 12.471 | 11.1914 | 10.9578 | 9.6237 | 14.1629 | 13.8322 | 13.4659 | 13.0486 | 12.5914 | 12.0404 | 11.5312 | 10.922 | 10.3312 | 9.8343 | 8.22 | 7.9088 | 6.6135
|  | THEALE | HT |  |  |  | 13.8649 | 13.6159 | 13.3537 | 13.0394 | 12.5669 | 12.121 | 11.7455 | 11.2669 | 10.7547 | 10.2302 | 7.9067 | 6.9373 | 5.3308 | 15.9578 | 15.8322 | 15.6761 | 15.4771 | 15.1231 | 14.7945 | 14.5078 | 14.1414 | 13.7557 | 13.3567 | 11.6108 | 10.9016 | 9.3757 | 14.3731 | 14.1231 | 13.8435 | 13.5394 | 13.1098 | 12.6965 | 12.3363 | 11.8771 | 11.3914 | 10.8853 | 8.6476 | 7.7231 | 6.1359
|  | THEALE | HE |  |  |  | 13.8343 | 13.5598 | 13.2629 | 12.8976 | 12.4659 | 11.9312 | 11.4659 | 10.8782 | 10.2486 | 9.5894 | 6.6924 | 5.57 | 3.8502 | 15.9435 | 15.7996 | 15.5976 | 15.3567 | 15.0506 | 14.6404 | 14.2771 | 13.818 | 13.3302 | 12.8159 | 10.5853 | 9.7363 | 8.0818 | 14.3404 | 14.0588 | 13.7455 | 13.4047 | 13.0006 | 12.5057 | 12.0618 | 11.4965 | 10.8955 | 10.2639 | 7.47 | 6.3904 | 4.688
|  | THEALE | CF |  |  |  | 13.9751 | 13.7792 | 13.5904 | 13.3863 | 13.1557 | 12.8986 | 12.6363 | 12.2976 | 11.9312 | 11.5312 | 9.1741 | 7.1363 | 4.5145 | 16.0067 | 15.8986 | 15.7955 | 15.6884 | 15.5343 | 15.3669 | 15.1557 | 14.8833 | 14.5904 | 14.2751 | 12.4363 | 10.8731 | 8.5257 | 14.4976 | 14.3108 | 14.1139 | 13.9006 | 13.6608 | 13.4159 | 13.169 | 12.8486 | 12.4996 | 12.1159 | 9.8486 | 7.8924 | 5.3257
MELKSHAM GSP | ANDOVER BSP | THRUXTON | MINIMUM HEADROOM | SU 29134 45674 | YES | 0.234 | 3.5757 | 3.4512 | 3.2951 | 3.1512 | 2.7482 | 2.14 | 1.4604 | 0.76653 | 0.23388 | -0.46 | -2.3529 | -2.6202 | -2.7927 | 4.6138 | 4.523 | 4.4046 | 4.3056 | 4.0709 | 3.826 | 3.5291 | 3.175 | 2.7995 | 2.4923 | 1.2332 | 0.50867 | -1.0332 | 4.2665 | 4.1441 | 3.989 | 3.8522 | 3.492 | 3.0543 | 2.5033 | 1.9339 | 1.4992 | 0.91755 | -0.78245 | -0.98143 | -1.1559
|  | THRUXTON | EE |  |  |  | 3.5757 | 3.4512 | 3.2951 | 3.1512 | 2.7482 | 2.2665 | 1.74 | 1.1278 | 0.46041 | -0.17531 | -2.3437 | -2.5906 | -2.6855 | 4.6138 | 4.523 | 4.4046 | 4.3056 | 4.0709 | 3.826 | 3.5291 | 3.175 | 2.7995 | 2.4923 | 1.2526 | 0.79439 | 0.07398 | 4.2665 | 4.1441 | 3.989 | 3.8522 | 3.492 | 3.092 | 2.6288 | 2.0849 | 1.4992 | 0.98082 | -0.78245 | -0.98143 | -1.0682
|  | THRUXTON | HT |  |  |  | 3.6349 | 3.5359 | 3.4369 | 3.2737 | 2.7553 | 2.14 | 1.4604 | 0.76653 | 0.23388 | -0.46 | -2.1773 | -2.5355 | -2.7927 | 4.673 | 4.6087 | 4.5526 | 4.4546 | 4.1954 | 3.9138 | 3.5913 | 3.2546 | 3.0056 | 2.6362 | 1.6209 | 1.4474 | 1.324 | 4.3288 | 4.2349 | 4.1461 | 3.9971 | 3.5614 | 3.0543 | 2.5033 | 1.9339 | 1.5114 | 0.91755 | -0.65286 | -0.95082 | -1.1559
|  | THRUXTON | HE |  |  |  | 3.6308 | 3.5339 | 3.4318 | 3.2941 | 2.9216 | 2.4645 | 1.9716 | 1.3635 | 0.75122 | 0.032857 | -2.3529 | -2.6202 | -2.7059 | 4.6638 | 4.5954 | 4.5291 | 4.4362 | 4.2342 | 4.0117 | 3.7526 | 3.4342 | 3.1495 | 2.7852 | 1.2332 | 0.74949 | 0.056633 | 4.3257 | 4.2318 | 4.1431 | 4.0145 | 3.6961 | 3.3155 | 2.8931 | 2.389 | 1.9104 | 1.3216 | -0.75796 | -0.97224 | -1.0467
|  | THRUXTON | CF |  |  |  | 3.6553 | 3.5747 | 3.4982 | 3.3961 | 3.2982 | 3.1859 | 3.1053 | 2.889 | 2.6614 | 2.3818 | -1.1376 | -2.0947 | -2.5998 | 4.6801 | 4.6209 | 4.5668 | 4.4954 | 4.4179 | 4.3332 | 4.2658 | 4.1158 | 3.9566 | 3.7679 | 1.7934 | 0.50867 | -1.0332 | 4.3492 | 4.2706 | 4.1992 | 4.1043 | 4.0094 | 3.8992 | 3.8257 | 3.6247 | 3.4196 | 3.1665 | 0.30633 | -0.5702 | -0.97224
MELKSHAM GSP | WEST GRAFTON | TIDWORTH | MINIMUM HEADROOM | SU 24088 49593 | YES | 1.915 | 7.7549 | 7.2069 | 6.4936 | 5.6936 | 4.864 | 4.4171 | 3.3947 | 2.3753 | 0.77118 | -0.40229 | -7.0125 | -9.586 | -10.9135 | 9.7359 | 9.3767 | 8.9379 | 8.4328 | 7.892 | 7.6869 | 7.0961 | 6.4053 | 5.4767 | 4.8216 | 1.0777 | -1.5764 | -7.9876 | 7.5261 | 7.0322 | 6.4118 | 5.6965 | 4.9424 | 4.6251 | 3.7842 | 2.8047 | 1.4302 | 0.45771 | -4.8617 | -7.0821 | -8.1984
|  | TIDWORTH | EE |  |  |  | 7.7549 | 7.2069 | 6.4936 | 5.6936 | 4.864 | 4.4171 | 3.4712 | 2.3753 | 0.77118 | -0.40229 | -6.8788 | -9.14 | -10.5941 | 9.7359 | 9.3767 | 8.9379 | 8.4328 | 7.892 | 7.6869 | 7.0961 | 6.4053 | 5.4767 | 4.8216 | 1.0777 | -1.3274 | -4.71 | 7.5261 | 7.0322 | 6.4118 | 5.6965 | 4.9424 | 4.6251 | 3.7842 | 2.8047 | 1.4302 | 0.45771 | -4.778 | -6.6953 | -7.9341
|  | TIDWORTH | HT |  |  |  | 7.9304 | 7.3579 | 6.7671 | 6.1314 | 5.3947 | 4.4763 | 3.3947 | 2.5834 | 1.2834 | 0.024245 | -7.0125 | -9.586 | -10.9135 | 9.9206 | 9.6042 | 9.2869 | 8.9379 | 8.5644 | 8.0798 | 7.5134 | 7.2053 | 6.5369 | 5.8828 | 2.4114 | 1.1849 | 0.59608 | 7.723 | 7.2383 | 6.7312 | 6.174 | 5.5485 | 4.7557 | 3.824 | 3.2189 | 2.1179 | 1.0455 | -4.8617 | -7.0821 | -8.1984
|  | TIDWORTH | HE |  |  |  | 7.9283 | 7.4732 | 6.9018 | 6.2161 | 5.5447 | 4.7865 | 3.962 | 3.3089 | 1.8783 | 0.70486 | -5.9513 | -8.2421 | -9.1941 | 9.8889 | 9.6042 | 9.2614 | 8.8532 | 8.4624 | 8.0063 | 7.4991 | 7.1879 | 6.393 | 5.6971 | 1.6369 | -0.83657 | -3.9958 | 7.72 | 7.3291 | 6.8414 | 6.2434 | 5.6761 | 5.0118 | 4.2883 | 3.8159 | 2.6312 | 1.6373 | -3.9127 | -5.8402 | -6.6147
|  | TIDWORTH | CF |  |  |  | 8.0293 | 7.76 | 7.3661 | 6.8253 | 6.2783 | 5.9844 | 5.7477 | 5.3763 | 4.8406 | 4.6018 | -1.8564 | -5.2992 | -7.4278 | 9.9389 | 9.7461 | 9.4869 | 9.1379 | 8.7808 | 8.5338 | 8.2573 | 7.8971 | 7.442 | 7.244 | 2.7675 | -1.5764 | -7.9876 | 7.7975 | 7.5669 | 7.2302 | 6.7689 | 6.3036 | 6.0455 | 5.8036 | 5.4465 | 4.9608 | 4.873 | -0.4382 | -3.2943 | -5.1484
MANNINGTON GSP | SHAFTESBURY BSP | TISBURY | MINIMUM HEADROOM | ST 93438 29127 | YES | 3.941 | 4.6404 | 2.4914 | 2.3455 | 2.1455 | 1.9179 | 1.7424 | 1.4618 | 1.1282 | 0.7955 | 0.70162 | 0.21999 | 0.21591 | 0.011824 | 6.1884 | 4.0833 | 3.9771 | 3.8282 | 3.6526 | 3.5139 | 3.3037 | 3.0588 | 2.823 | 2.7108 | 2.3159 | 1.8139 | -0.020829 | 5.173 | 3.0322 | 2.8965 | 2.7006 | 2.4782 | 2.3098 | 2.0343 | 1.7067 | 1.3812 | 1.2894 | 0.88223 | 0.92815 | 0.7506
|  | TISBURY | EE |  |  |  | 4.6404 | 2.4914 | 2.3455 | 2.1455 | 1.9179 | 1.7424 | 1.4618 | 1.1282 | 0.7955 | 0.70162 | 0.44652 | 0.21591 | 0.094478 | 6.1884 | 4.0833 | 3.9771 | 3.8282 | 3.6526 | 3.5139 | 3.3037 | 3.0588 | 2.823 | 2.7108 | 2.5741 | 2.0873 | 1.2159 | 5.173 | 3.0322 | 2.8965 | 2.7006 | 2.4782 | 2.3098 | 2.0343 | 1.7067 | 1.3812 | 1.2894 | 1.1302 | 0.92815 | 0.82203
|  | TISBURY | HT |  |  |  | 4.7435 | 2.6424 | 2.519 | 2.37 | 2.221 | 2.021 | 1.7853 | 1.623 | 1.4118 | 1.1904 | 0.6057 | 0.23529 | 0.011824 | 6.2588 | 4.1924 | 4.1169 | 4.0251 | 3.9384 | 3.8149 | 3.671 | 3.5649 | 3.419 | 3.2598 | 3.0016 | 2.8067 | 2.7026 | 5.2506 | 3.1455 | 3.0322 | 2.8945 | 2.7639 | 2.5792 | 2.3577 | 2.2159 | 2.0108 | 1.7945 | 1.2761 | 0.94244 | 0.7506
|  | TISBURY | HE |  |  |  | 4.7384 | 2.6404 | 2.5282 | 2.3914 | 2.2537 | 2.0669 | 1.8465 | 1.6608 | 1.4486 | 1.2373 | 0.21999 | 0.36693 | 0.27509 | 6.2496 | 4.1751 | 4.0996 | 3.9996 | 3.9098 | 3.7792 | 3.6271 | 3.4975 | 3.3333 | 3.1588 | 2.3159 | 2.1996 | 1.3414 | 5.2445 | 3.1424 | 3.0424 | 2.9139 | 2.7914 | 2.6179 | 2.4139 | 2.2526 | 2.0465 | 1.8404 | 0.88223 | 1.0771 | 0.99958
|  | TISBURY | CF |  |  |  | 4.771 | 2.6884 | 2.6088 | 2.52 | 2.4149 | 2.3037 | 2.2241 | 2.0782 | 1.9047 | 1.7751 | 0.85672 | 0.75978 | 0.39856 | 6.2679 | 4.2026 | 4.1424 | 4.0679 | 3.9792 | 3.8802 | 3.8026 | 3.669 | 3.5159 | 3.3996 | 2.4577 | 1.8139 | -0.020829 | 5.269 | 3.1884 | 3.1128 | 3.0241 | 2.921 | 2.8108 | 2.7384 | 2.5945 | 2.4302 | 2.32 | 1.4435 | 1.423 | 1.0986
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | TITCHFIELD | MINIMUM HEADROOM | SU 54104 05695 | YES | 0.434 | 10.0026 | 9.0546 | 7.9995 | 6.7526 | 5.3515 | 3.6474 | 21.1878 | 19.9122 | 18.3265 | 16.7214 | 10.9245 | 8.4398 | 7.0582 | 10.5582 | 10 | 9.4112 | 8.7041 | 8.199 | 7.3673 | 24.8122 | 23.8765 | 22.8776 | 22.0276 | 18.5827 | 15.8224 | 8.9878 | 10.0378 | 9.2245 | 8.3418 | 7.2694 | 6.3224 | 4.8837 | 22.152 | 21.1041 | 19.6296 | 18.3418 | 13.4418 | 11.2531 | 10.0684
|  | TITCHFIELD | EE |  |  |  | 10.0026 | 9.0546 | 7.9995 | 6.7526 | 5.6444 | 4.0811 | 21.6939 | 20.0724 | 18.3398 | 16.7663 | 11.1612 | 8.9408 | 7.3204 | 10.5582 | 10 | 9.4112 | 8.7041 | 8.199 | 7.3673 | 24.8122 | 23.8765 | 22.8776 | 22.0276 | 18.5827 | 16.1327 | 12.5939 | 10.0378 | 9.2245 | 8.3418 | 7.2694 | 6.5 | 5.1806 | 22.4939 | 21.1041 | 19.6296 | 18.3418 | 13.6276 | 11.698 | 10.2918
|  | TITCHFIELD | HT |  |  |  | 10.1536 | 9.1423 | 8.0628 | 6.8311 | 5.3515 | 3.6474 | 21.1878 | 19.9122 | 18.3265 | 16.7214 | 10.9245 | 8.4398 | 7.0582 | 10.7122 | 10.1704 | 9.6255 | 9.0306 | 8.3265 | 7.4857 | 25 | 24.4235 | 23.6286 | 22.8276 | 19.9592 | 18.7867 | 18.1561 | 10.2286 | 9.399 | 8.5173 | 7.5265 | 6.3224 | 4.8837 | 22.152 | 21.1235 | 19.7867 | 18.4367 | 13.4418 | 11.2531 | 10.0684
|  | TITCHFIELD | HE |  |  |  | 10.1566 | 9.2842 | 8.3097 | 7.2097 | 5.8628 | 4.3066 | 22.0112 | 20.8459 | 19.2663 | 17.6704 | 12.001 | 9.7439 | 8.701 | 10.6949 | 10.2082 | 9.6776 | 9.0827 | 8.3673 | 7.5622 | 25.0663 | 24.4633 | 23.5765 | 22.6745 | 18.9786 | 16.452 | 13.1459 | 10.2245 | 9.5051 | 8.7092 | 7.8204 | 6.7224 | 5.4184 | 22.8245 | 21.8908 | 20.5714 | 19.2367 | 14.3929 | 12.4153 | 11.5224
|  | TITCHFIELD | CF |  |  |  | 10.3689 | 9.7026 | 9.0301 | 8.2454 | 7.3842 | 6.4005 | 24.7071 | 23.7418 | 23.0765 | 22.0643 | 15.8867 | 13.1867 | 10.6755 | 10.8 | 10.4041 | 10.0031 | 9.5388 | 9.0429 | 8.4531 | 26.199 | 25.5378 | 25.1133 | 24.4184 | 19.9704 | 15.8224 | 8.9878 | 10.399 | 9.851 | 9.2939 | 8.6357 | 7.9469 | 7.1296 | 25.0327 | 24.2051 | 23.8235 | 22.9878 | 17.8541 | 15.4398 | 13.2235
BRAMLEY (FLEE) | ALDERSHOT BSP | TONGHAM | MINIMUM HEADROOM | SU 88310 49487 | YES | 2.082 | 16.951 | 16.2031 | 15.2541 | 14.6439 | 13.6949 | 12.698 | 11.3592 | 9.9898 | 8.6327 | 7.5316 | 1.6367 | -2.3602 | -4.4561 | 19.6204 | 19.0867 | 18.3582 | 17.9898 | 17.3194 | 16.5959 | 15.6776 | 14.7051 | 13.7122 | 12.9592 | 8.8051 | 3.8071 | -7.8949 | 17.7673 | 17.1082 | 16.2184 | 15.7163 | 14.8694 | 13.9714 | 12.7571 | 11.5122 | 10.2673 | 9.2796 | 4.099 | 0.54082 | -1.2867
|  | TONGHAM | EE |  |  |  | 16.951 | 16.2031 | 15.2541 | 14.6439 | 13.6949 | 12.698 | 11.3592 | 9.9898 | 8.6327 | 7.5316 | 1.8888 | -1.6847 | -4.2051 | 19.6204 | 19.0867 | 18.3582 | 17.9898 | 17.3194 | 16.5959 | 15.6776 | 14.7051 | 13.7122 | 12.9592 | 8.8051 | 4.7102 | -1.3041 | 17.7673 | 17.1082 | 16.2184 | 15.7163 | 14.8694 | 13.9714 | 12.7571 | 11.5122 | 10.2673 | 9.2796 | 4.2776 | 1.1378 | -1.0714
|  | TONGHAM | HT |  |  |  | 17.1878 | 16.499 | 15.701 | 14.85 | 13.9439 | 13.3357 | 12.0959 | 10.8653 | 9.6 | 8.3173 | 1.6367 | -2.3602 | -4.4561 | 19.8959 | 19.4969 | 18.9837 | 18.499 | 17.9765 | 17.7163 | 17.0459 | 16.3643 | 15.651 | 14.9173 | 11.3959 | 9.5653 | 8.6969 | 18.0041 | 17.4102 | 16.6724 | 15.9316 | 15.1316 | 14.6235 | 13.5173 | 12.4133 | 11.2694 | 10.1092 | 4.099 | 0.54082 | -1.2867
|  | TONGHAM | HE |  |  |  | 17.1898 | 16.5327 | 15.7592 | 14.9327 | 14.052 | 13.4663 | 12.3878 | 11.3133 | 10.199 | 9.0622 | 3.1908 | -0.42347 | -1.9082 | 19.8316 | 19.3929 | 18.8184 | 18.2724 | 17.6735 | 17.3194 | 16.5908 | 15.8378 | 15.0276 | 14.1796 | 9.4561 | 5.2408 | -0.36735 | 18.0031 | 17.4367 | 16.7173 | 15.999 | 15.2224 | 14.7316 | 13.7673 | 12.8 | 11.7888 | 10.7571 | 5.4602 | 2.2622 | 0.97245
|  | TONGHAM | CF |  |  |  | 17.4102 | 17.0071 | 16.4031 | 15.8418 | 15.199 | 14.5796 | 14.3041 | 13.799 | 13.2541 | 12.6939 | 8.8061 | 4.9439 | 1.3265 | 19.9459 | 19.6173 | 19.1071 | 18.6806 | 18.1827 | 17.6439 | 17.3133 | 16.7347 | 16.1153 | 15.448 | 10.7663 | 3.8071 | -7.8949 | 18.2071 | 17.8592 | 17.2959 | 16.8255 | 16.2704 | 15.7286 | 15.5133 | 15.0602 | 14.5663 | 14.0571 | 10.5184 | 7.0204 | 3.7929
MINETY GSP | TOOTHILL BSP | TOOTHILL | MINIMUM HEADROOM | SU 13215 83986 | YES | 2.502 | 15.4955 | 15.1118 | 14.7047 | 14.2037 | 13.6445 | 13.1241 | 12.0435 | 10.6751 | 9.319 | 8.2129 | 3.371 | 1.0537 | 0.67918 | 15.3322 | 14.9894 | 14.6139 | 14.1547 | 13.6241 | 13.218 | 12.3822 | 11.3588 | 10.3047 | 9.4904 | 6.421 | 2.6129 | -5.9382 | 14.7343 | 14.368 | 13.9761 | 13.4955 | 12.9547 | 12.4588 | 11.4445 | 10.2292 | 8.9843 | 8.021 | 3.6802 | 1.4822 | 1.1384
|  | TOOTHILL | EE |  |  |  | 15.4955 | 15.1118 | 14.7047 | 14.2037 | 13.6445 | 13.1241 | 12.0435 | 10.6751 | 9.319 | 8.2129 | 5.1496 | 4.0139 | 4.0986 | 15.3322 | 14.9894 | 14.6139 | 14.1547 | 13.6241 | 13.218 | 12.3822 | 11.3588 | 10.3047 | 9.4904 | 6.6047 | 4.0639 | 0.41898 | 14.7343 | 14.368 | 13.9761 | 13.4955 | 12.9547 | 12.4588 | 11.4445 | 10.2292 | 8.9843 | 8.021 | 5.2761 | 4.069 | 4.2139
|  | TOOTHILL | HT |  |  |  | 15.768 | 15.4935 | 15.2078 | 14.8639 | 14.3057 | 13.4629 | 12.4159 | 11.5955 | 10.5486 | 9.6435 | 6.0455 | 3.9373 | 3.6353 | 15.6057 | 15.4047 | 15.1884 | 14.9231 | 14.4669 | 13.8322 | 13.119 | 12.5894 | 11.8547 | 11.2455 | 8.9027 | 7.6618 | 7.4169 | 15.0016 | 14.7455 | 14.4761 | 14.1486 | 13.5904 | 12.7894 | 11.8129 | 11.0557 | 10.072 | 9.2343 | 5.9078 | 4.0251 | 3.8149
|  | TOOTHILL | HE |  |  |  | 15.7159 | 15.4282 | 15.1149 | 14.7435 | 14.3649 | 13.619 | 12.6547 | 11.4506 | 10.0435 | 8.6649 | 3.371 | 1.0537 | 0.67918 | 15.5271 | 15.2761 | 14.9955 | 14.6588 | 14.3078 | 13.668 | 12.9139 | 12.2516 | 11.2965 | 10.3751 | 6.421 | 3.5904 | -0.16265 | 14.9506 | 14.6782 | 14.3822 | 14.0251 | 13.6659 | 12.9435 | 12.0394 | 11.1088 | 9.8567 | 8.6363 | 3.6802 | 1.4822 | 1.1384
|  | TOOTHILL | CF |  |  |  | 15.8904 | 15.7598 | 15.6006 | 15.4006 | 15.1792 | 14.9669 | 14.5843 | 14.0292 | 13.369 | 12.7016 | 8.1149 | 4.5863 | 2.1108 | 15.6261 | 15.4618 | 15.2659 | 15.0241 | 14.7414 | 14.4465 | 13.9802 | 13.3659 | 12.6486 | 12.1833 | 7.8792 | 2.6129 | -5.9382 | 15.1129 | 14.9873 | 14.8322 | 14.6414 | 14.4241 | 14.219 | 13.8414 | 13.3037 | 12.6588 | 12.1149 | 8.0118 | 4.8424 | 2.5149
NURSLING GSP | ROWNHAMS | TOTTON | MINIMUM HEADROOM | SU 35835 13428 | YES | 5.587 | 8.526 | 8.2301 | 7.6821 | 7.4066 | 6.9903 | 6.5341 | 5.8648 | 5.0801 | 4.2831 | 3.577 | -1.0699 | -4.371 | -6.1556 | 12.2913 | 12.0637 | 11.679 | 11.5362 | 11.2607 | 10.9586 | 10.5239 | 9.8137 | 9.0556 | 8.4699 | 5.2913 | 1.6423 | -6.8924 | 10.2678 | 9.9382 | 9.4056 | 9.2484 | 8.8852 | 8.4944 | 7.6964 | 6.8076 | 5.879 | 5.0974 | 0.93619 | -2.0046 | -3.5873
|  | TOTTON | EE |  |  |  | 8.526 | 8.2301 | 7.6821 | 7.4066 | 6.9903 | 6.5341 | 5.8648 | 5.0801 | 4.2831 | 3.577 | -0.7883 | -3.8056 | -5.9138 | 12.2913 | 12.125 | 11.679 | 11.5362 | 11.2607 | 10.9586 | 10.5239 | 9.8137 | 9.0556 | 8.4699 | 5.2913 | 2.0586 | -2.4832 | 10.2678 | 9.9719 | 9.4056 | 9.2484 | 8.8852 | 8.4944 | 7.6964 | 6.8076 | 5.879 | 5.0974 | 1.1637 | -1.523 | -3.3975
|  | TOTTON | HT |  |  |  | 8.7117 | 8.2882 | 8.0127 | 7.7117 | 7.3648 | 6.9699 | 6.4933 | 5.8188 | 5.0923 | 4.1719 | -1.0699 | -4.371 | -6.1556 | 12.4178 | 12.0637 | 11.9137 | 11.7546 | 11.5627 | 11.3239 | 11.0944 | 10.7209 | 10.3137 | 9.8413 | 7.1005 | 5.5882 | 4.8158 | 10.4076 | 9.9382 | 9.6413 | 9.3535 | 9.0158 | 8.6423 | 8.1035 | 7.3066 | 6.4464 | 5.5403 | 0.93619 | -2.0046 | -3.5873
|  | TOTTON | HE |  |  |  | 8.7025 | 8.479 | 8.0107 | 7.7097 | 7.3535 | 6.9505 | 6.5097 | 5.8444 | 5.1086 | 4.3229 | 0.47496 | -2.4914 | -3.8077 | 12.4066 | 12.2841 | 11.8933 | 11.729 | 11.5229 | 11.2658 | 11.0311 | 10.6341 | 10.0699 | 9.4444 | 5.9362 | 2.677 | -1.5505 | 10.4168 | 10.1811 | 9.6995 | 9.4382 | 9.1229 | 8.779 | 8.3974 | 7.7423 | 7.0188 | 6.2464 | 2.2903 | -0.35769 | -1.5159
|  | TOTTON | CF |  |  |  | 8.877 | 8.7546 | 8.6229 | 8.2648 | 8.0841 | 7.877 | 7.6321 | 7.4362 | 7.0913 | 6.7066 | 3.9127 | 1.1199 | -1.2689 | 12.4944 | 12.4148 | 12.327 | 11.9862 | 11.877 | 11.7392 | 11.4525 | 11.3005 | 10.9066 | 10.4739 | 7.0158 | 1.6423 | -6.8924 | 10.5566 | 10.425 | 10.2933 | 9.927 | 9.7892 | 9.6046 | 9.3903 | 9.3546 | 9.0974 | 8.8117 | 6.1597 | 3.1433 | 0.78721
BOTLEY WOOD GSP | NETLEY COMMON BSP | TOWNHILL PARK | MINIMUM HEADROOM | SU 45156 14783 | YES | 1.639 | 10.5147 | 9.6892 | 9.378 | 8.5606 | 7.6524 | 6.6545 | 5.1422 | 3.4535 | 1.7647 | 0.65551 | -6.0802 | -11.5935 | -14.6363 | 14.1024 | 13.53 | 13.2127 | 12.5708 | 11.7953 | 10.9371 | 9.7933 | 8.4953 | 7.1739 | 6.2371 | 0.84837 | -7.5547 | -26.6629 | 10.1973 | 9.4076 | 9.131 | 8.3433 | 7.4708 | 6.5086 | 5.082 | 3.478 | 1.8729 | 0.85245 | -4.8618 | -9.7384 | -12.2863
|  | TOWNHILL PARK | EE |  |  |  | 10.5147 | 9.6892 | 9.378 | 8.5606 | 7.6524 | 6.6545 | 5.1422 | 3.4535 | 1.7647 | 0.65551 | -5.5945 | -10.3129 | -14.0976 | 14.1024 | 13.53 | 13.2127 | 12.5708 | 11.7953 | 10.9371 | 9.7933 | 8.4953 | 7.1739 | 6.2371 | 0.84837 | -5.4741 | -15.619 | 10.1973 | 9.4076 | 9.131 | 8.3433 | 7.4708 | 6.5086 | 5.082 | 3.478 | 1.8729 | 0.85245 | -4.5761 | -8.6302 | -11.8547
|  | TOWNHILL PARK | HT |  |  |  | 10.9718 | 10.378 | 9.6933 | 8.9504 | 8.7269 | 8.0024 | 6.6851 | 5.2524 | 3.7576 | 2.1953 | -6.0802 | -11.5935 | -14.6363 | 14.4504 | 14.1116 | 13.7269 | 13.2678 | 13.1361 | 12.6963 | 11.9698 | 11.1504 | 10.2688 | 9.3433 | 4.8371 | 2.2688 | 1.0035 | 10.6545 | 10.1035 | 9.4576 | 8.7535 | 8.5759 | 7.8871 | 6.7055 | 5.3871 | 4.0035 | 2.5555 | -4.8618 | -9.7384 | -12.2863
|  | TOWNHILL PARK | HE |  |  |  | 10.9729 | 10.43 | 9.7973 | 9.1239 | 8.9933 | 8.3198 | 7.2514 | 6.0973 | 4.8933 | 3.6382 | -3.0873 | -7.8465 | -10.1271 | 14.3555 | 13.9463 | 13.4678 | 12.9524 | 12.6892 | 12.1096 | 11.332 | 10.4433 | 9.4586 | 8.4065 | 2.2637 | -4.2873 | -13.7741 | 10.6535 | 10.1463 | 9.5453 | 8.9014 | 8.8024 | 8.1606 | 7.1973 | 6.1178 | 4.982 | 3.7984 | -2.2853 | -6.3792 | -8.2598
|  | TOWNHILL PARK | CF |  |  |  | 11.2739 | 10.9249 | 10.5484 | 10.1035 | 9.6167 | 9.6657 | 9.2137 | 8.6678 | 8.0933 | 7.4882 | 3.0943 | -1.4241 | -5.9904 | 14.5137 | 14.1769 | 13.8024 | 13.3739 | 12.878 | 12.5871 | 11.9616 | 11.2259 | 10.4514 | 9.6035 | 3.1576 | -7.5547 | -26.6629 | 10.9259 | 10.5922 | 10.231 | 9.8076 | 9.3361 | 9.4024 | 8.9729 | 8.4463 | 7.8912 | 7.3076 | 3.1463 | -0.94041 | -4.7884
MINETY GSP | SWINDON BSP | TRADING ESTATE | MINIMUM HEADROOM | SU 13490 85868 | YES | 5.019 | 9.3149 | 8.669 | 7.8925 | 6.9782 | 5.8649 | 4.1741 | 2.3404 | -0.0034286 | -2.283 | -4.132 | -12.6136 | -15.9442 | -16.3351 | 11.5996 | 11.0609 | 10.4058 | 9.6384 | 8.7486 | 7.3374 | 5.8476 | 3.9251 | 2.0149 | 0.47412 | -6.1453 | -8.7004 | -9.0993 | 9.9435 | 9.4343 | 8.82 | 7.8517 | 6.7313 | 5.1027 | 3.3343 | 1.0802 | -1.1218 | -2.9065 | -11.1126 | -14.3218 | -14.6942
|  | TRADING ESTATE | EE |  |  |  | 9.3149 | 8.669 | 7.8925 | 6.9782 | 5.8649 | 4.1741 | 2.3404 | -0.0034286 | -2.283 | -4.132 | -9.2187 | -10.0973 | -10.1218 | 11.5996 | 11.0609 | 10.4058 | 9.6384 | 8.7486 | 7.3374 | 5.8476 | 3.9251 | 2.0149 | 0.47412 | -3.5167 | -4.18 | -4.3289 | 9.9435 | 9.4343 | 8.82 | 7.8517 | 6.7313 | 5.1027 | 3.3343 | 1.0802 | -1.1218 | -2.9065 | -7.8024 | -8.6259 | -8.6514
|  | TRADING ESTATE | HT |  |  |  | 9.968 | 9.5792 | 9.1047 | 8.5333 | 7.4109 | 6.0486 | 4.52 | 2.6435 | 0.85473 | -0.62486 | -6.6147 | -9.1616 | -9.5483 | 12.1527 | 11.8333 | 11.4384 | 10.9649 | 9.9221 | 8.6537 | 7.3466 | 5.7588 | 4.2507 | 3.0915 | -1.3912 | -3.282 | -3.5881 | 10.4609 | 10.1537 | 9.7823 | 9.3333 | 8.3384 | 6.9394 | 5.4364 | 3.6292 | 1.8986 | 0.47004 | -5.2963 | -7.7351 | -8.0953
|  | TRADING ESTATE | HE |  |  |  | 9.7527 | 9.2119 | 8.5547 | 7.7629 | 6.819 | 5.2435 | 3.4853 | 1.1853 | -1.2524 | -3.5942 | -12.6136 | -15.9442 | -16.3351 | 11.97 | 11.52 | 10.968 | 10.3047 | 9.5119 | 8.168 | 6.7374 | 4.8476 | 2.816 | 0.89147 | -6.1453 | -8.7004 | -9.0993 | 10.2864 | 9.8629 | 9.3435 | 8.6823 | 7.6843 | 6.1353 | 4.4425 | 2.2282 | -0.12792 | -2.3953 | -11.1126 | -14.3218 | -14.6942
|  | TRADING ESTATE | CF |  |  |  | 10.1456 | 9.8925 | 9.5374 | 9.119 | 8.6251 | 8.0547 | 7.27 | 6.1537 | 4.7241 | 3.2149 | -4.5402 | -10.0157 | -13.1585 | 12.3313 | 12.0874 | 11.7884 | 11.4353 | 11.016 | 10.5333 | 9.8282 | 8.817 | 7.5751 | 6.2925 | -0.082 | -4.2902 | -6.8136 | 10.6211 | 10.3956 | 10.1119 | 9.7823 | 9.3935 | 8.9435 | 8.1904 | 7.0333 | 5.6272 | 4.169 | -3.332 | -8.6065 | -11.6259
BRAMLEY (FLEE) | BURGHFIELD RESERVE | TRASH GREEN | MINIMUM HEADROOM | SU 66254 68745 | YES | 5.195 | 0.59218 | 0.0054408 | -0.62007 | -1.7017 | -3.0139 | -4.5027 | -6.1037 | -8.2017 | -10.2129 | -12.1537 | -22.4946 | -26.3568 | -26.6997 | 2.5978 | 1.9692 | 1.2529 | 0.41105 | -0.58384 | -1.7145 | -2.9104 | -4.493 | -6.0073 | -7.4655 | -15.2757 | -18.1359 | -18.4104 | -0.18589 | -0.99507 | -1.9083 | -2.9838 | -4.2502 | -5.6889 | -7.2257 | -9.2481 | -11.1838 | -13.0522 | -23.0155 | -26.7114 | -27.0216
|  | TRASH GREEN | EE |  |  |  | 0.59218 | 0.0054408 | -0.62007 | -1.7017 | -3.0139 | -4.5027 | -6.1037 | -8.2017 | -10.2129 | -12.1537 | -19.7823 | -23.6201 | -24.8007 | 2.5978 | 1.9692 | 1.2529 | 0.41105 | -0.58384 | -1.7145 | -2.9104 | -4.493 | -6.0073 | -7.4655 | -13.1267 | -15.9553 | -16.8257 | -0.18589 | -0.99507 | -1.9083 | -2.9838 | -4.2502 | -5.6889 | -7.2257 | -9.2481 | -11.1838 | -13.0522 | -20.3767 | -24.0492 | -25.1624
|  | TRASH GREEN | HT |  |  |  | 1.0136 | 0.55646 | 0.10646 | -0.38027 | -0.98436 | -2.0629 | -3.4058 | -5.067 | -6.8527 | -8.6211 | -16.7395 | -21.1078 | -22.7803 | 3.2437 | 2.8039 | 2.3162 | 1.7366 | 1.0253 | 0.18146 | -0.81242 | -2.0512 | -3.3849 | -4.7002 | -10.7308 | -13.9298 | -15.1247 | 0.62024 | 0.048808 | -0.58487 | -1.3318 | -2.244 | -3.3236 | -4.6134 | -6.2124 | -7.9298 | -9.6257 | -17.4308 | -21.6134 | -23.2032
|  | TRASH GREEN | HE |  |  |  | 0.93809 | 0.4483 | -0.074151 | -0.6915 | -1.8813 | -3.3252 | -5.0303 | -7.1874 | -9.516 | -11.6599 | -22.4946 | -26.3568 | -26.6997 | 3.0957 | 2.5723 | 1.9427 | 1.1876 | 0.28758 | -0.80629 | -2.092 | -3.7236 | -5.491 | -7.1032 | -15.2757 | -18.1359 | -18.4104 | 0.44064 | -0.23691 | -1.0451 | -2.0073 | -3.1532 | -4.5451 | -6.19 | -8.2696 | -10.5165 | -12.5757 | -23.0155 | -26.7114 | -27.0216
|  | TRASH GREEN | CF |  |  |  | 1.2514 | 0.9636 | 0.68401 | 0.39013 | 0.021767 | -0.4017 | -0.81803 | -1.8282 | -2.9966 | -4.2364 | -11.5333 | -18.1619 | -22.1742 | 3.4845 | 3.2702 | 2.9804 | 2.6131 | 2.1804 | 1.6641 | 1.0927 | 0.30391 | -0.59099 | -1.54 | -7.09 | -12.1104 | -15.1808 | 0.89473 | 0.63044 | 0.28656 | -0.1818 | -0.73384 | -1.3889 | -2.1104 | -3.1053 | -4.2328 | -5.4318 | -12.4645 | -18.8389 | -22.6767
MELKSHAM GSP | NORRINGTON | TROWBRIDGE TOWN | MINIMUM HEADROOM | ST 84668 58036 | YES | 5.035 | 13.4606 | 11.2308 | 10.6329 | 10.3369 | 9.7614 | 9.1135 | 8.142 | 7.0614 | 5.9369 | 5.0961 | 0.77265 | -2.8998 | -5.0406 | 18.6627 | 16.538 | 16.1216 | 15.9114 | 15.4869 | 15.0124 | 14.3818 | 13.6624 | 12.9135 | 12.3288 | 9.1104 | 5.2492 | -4.2018 | 14.9392 | 12.7522 | 12.2369 | 11.9033 | 11.2971 | 10.6247 | 9.7329 | 8.6941 | 7.6635 | 6.8124 | 3.0094 | 0.12469 | -1.761
|  | TROWBRIDGE TOWN | EE |  |  |  | 13.4606 | 11.2308 | 10.6329 | 10.3369 | 9.7614 | 9.1135 | 8.142 | 7.0614 | 5.9369 | 5.0961 | 0.88592 | -2.2039 | -4.6029 | 18.6627 | 16.538 | 16.1216 | 15.9114 | 15.4869 | 15.0124 | 14.3818 | 13.6624 | 12.9135 | 12.3288 | 9.1104 | 5.6665 | 0.58898 | 14.9392 | 12.7522 | 12.2369 | 11.9033 | 11.2971 | 10.6247 | 9.7329 | 8.6941 | 7.6635 | 6.8124 | 3.2614 | 0.72469 | -1.3896
|  | TROWBRIDGE TOWN | HT |  |  |  | 13.682 | 11.4533 | 10.9686 | 10.5308 | 10.0359 | 9.4308 | 8.8237 | 7.8716 | 6.8839 | 5.9655 | 0.77265 | -2.8998 | -5.0406 | 18.8627 | 16.8043 | 16.5267 | 16.2655 | 15.9716 | 15.6114 | 15.3533 | 14.8451 | 14.3104 | 13.8002 | 11.088 | 9.3359 | 8.3512 | 15.1341 | 12.9635 | 12.5461 | 12.1573 | 11.7176 | 11.1859 | 10.6441 | 9.7961 | 8.8859 | 7.9849 | 3.3869 | 0.12469 | -1.761
|  | TROWBRIDGE TOWN | HE |  |  |  | 13.6769 | 11.5329 | 11.0778 | 10.64 | 10.1471 | 9.5869 | 9.1206 | 8.292 | 7.3941 | 6.5533 | 2.1624 | -0.95082 | -2.4743 | 18.8178 | 16.7584 | 16.44 | 16.1267 | 15.7645 | 15.3482 | 15.0543 | 14.4931 | 13.8798 | 13.2747 | 9.742 | 6.2094 | 1.541 | 15.129 | 13.0196 | 12.6278 | 12.241 | 11.7961 | 11.19 | 10.5573 | 9.6482 | 8.6788 | 7.7012 | 3.0094 | 0.47571 | -0.82224
|  | TROWBRIDGE TOWN | CF |  |  |  | 13.878 | 11.8635 | 11.688 | 11.4512 | 11.2349 | 10.9727 | 10.6706 | 10.5839 | 10.1798 | 9.7124 | 6.5788 | 3.4451 | 0.53286 | 18.9229 | 16.9104 | 16.7308 | 16.4982 | 16.2573 | 15.9563 | 15.59 | 15.3696 | 14.9165 | 14.4135 | 10.8369 | 5.2492 | -4.2018 | 15.3035 | 13.3094 | 13.1553 | 12.9461 | 12.7543 | 12.5216 | 12.2553 | 12.0196 | 11.5267 | 10.9767 | 7.4257 | 4.1084 | 1.4839
BRAMLEY (FLEE) | READING BSP | TWYFORD | MINIMUM HEADROOM | SU 78430 76339 | YES | 3.147 | -1.6717 | -2.0279 | -2.5523 | -3.1146 | -3.2156 | -3.7177 | -4.4258 | -5.2166 | -5.9911 | -6.5074 | -10.0023 | -12.6636 | -14.234 | 3.0737 | 2.8043 | 2.4114 | 1.9818 | 1.9747 | 1.5961 | 1.1022 | 0.53694 | -0.027347 | -0.37735 | -2.4386 | -5.3427 | -12.1355 | -0.21 | -0.51102 | -1.0029 | -1.5304 | -1.6365 | -2.1131 | -2.7937 | -3.5569 | -4.309 | -4.81 | -7.7498 | -10.1294 | -11.4927
|  | TWYFORD | EE |  |  |  | -1.6717 | -2.0279 | -2.5523 | -3.1146 | -3.2156 | -3.7177 | -4.4258 | -5.2166 | -5.9911 | -6.5074 | -9.536 | -11.9748 | -13.834 | 3.0737 | 2.8043 | 2.4114 | 1.9818 | 1.9747 | 1.5961 | 1.1022 | 0.53694 | -0.027347 | -0.37735 | -2.4386 | -4.8202 | -8.4212 | -0.21 | -0.51102 | -1.0029 | -1.5304 | -1.6365 | -2.1131 | -2.7937 | -3.5569 | -4.309 | -4.81 | -7.4212 | -9.5478 | -11.1722
|  | TWYFORD | HT |  |  |  | -1.4728 | -1.8564 | -2.3105 | -2.6942 | -3.1095 | -3.5789 | -3.8881 | -4.6054 | -5.3391 | -6.0911 | -10.0023 | -12.6636 | -14.234 | 3.2747 | 3.0431 | 2.7553 | 2.5155 | 2.2369 | 1.9196 | 1.889 | 1.489 | 1.0706 | 0.64102 | -1.3539 | -2.4243 | -3.0029 | -0.088571 | -0.41918 | -0.80388 | -1.1427 | -1.5171 | -1.961 | -2.2569 | -2.8967 | -3.5773 | -4.2753 | -7.7498 | -10.1294 | -11.4927
|  | TWYFORD | HE |  |  |  | -1.4758 | -1.7605 | -2.1748 | -2.5442 | -2.9697 | -3.4217 | -3.5779 | -4.137 | -4.7105 | -5.3054 | -8.6258 | -11.0646 | -12.1993 | 3.241 | 3.0329 | 2.7308 | 2.4665 | 2.1431 | 1.7961 | 1.7706 | 1.3727 | 0.95429 | 0.51347 | -2.0202 | -4.4447 | -7.7273 | -0.087551 | -0.33449 | -0.68551 | -1.011 | -1.3927 | -1.8202 | -1.9876 | -2.5161 | -3.0712 | -3.6427 | -6.6192 | -8.7508 | -9.7263
|  | TWYFORD | CF |  |  |  | -1.2585 | -1.4268 | -1.5983 | -1.836 | -2.0299 | -2.3074 | -2.6115 | -2.5799 | -2.9238 | -3.284 | -5.685 | -7.8299 | -10.2483 | 3.3543 | 3.1839 | 3.0165 | 2.788 | 2.6002 | 2.3247 | 2.0114 | 2.0124 | 1.6727 | 1.3084 | -1.4222 | -5.3427 | -12.1355 | 0.10327 | -0.024286 | -0.15184 | -0.32633 | -0.51102 | -0.76816 | -1.0508 | -1.0192 | -1.3427 | -1.6824 | -3.9865 | -6.0682 | -8.0324
COWLEY GSP | COWLEY LOCAL (2 X 90) | UNION STREET | MINIMUM HEADROOM | SP 52865 05849 | YES | 6.436 | 7.789 | 7.2757 | 6.8329 | 6.3114 | 5.7247 | 5.089 | 4.4676 | 3.4859 | 2.5645 | 1.9022 | -0.75694 | -2.4845 | -2.4549 | 11.0531 | 10.6684 | 10.2908 | 9.8378 | 9.3286 | 8.7684 | 8.3643 | 7.6071 | 6.8663 | 6.302 | 3.5 | -0.49592 | -10.8092 | 7.0931 | 6.6298 | 6.2033 | 5.7002 | 5.138 | 4.5257 | 3.94 | 3.0043 | 2.1155 | 1.4767 | -0.94367 | -2.4345 | -2.4222
|  | UNION STREET | EE |  |  |  | 7.789 | 7.2757 | 6.8329 | 6.3114 | 5.7247 | 5.089 | 4.4676 | 3.4859 | 2.5645 | 1.9022 | -0.75694 | -2.0478 | -1.6753 | 11.0531 | 10.6684 | 10.2908 | 9.8378 | 9.3286 | 8.7684 | 8.3643 | 7.6071 | 6.8663 | 6.302 | 3.5 | 0.54796 | -3.9153 | 7.0931 | 6.6298 | 6.2033 | 5.7002 | 5.138 | 4.5257 | 3.94 | 3.0043 | 2.1155 | 1.4767 | -0.94367 | -2.0335 | -1.7896
|  | UNION STREET | HT |  |  |  | 8.0288 | 7.5553 | 7.24 | 6.8635 | 6.4471 | 6.04 | 5.0237 | 4.2931 | 3.9257 | 3.1982 | -0.46612 | -2.4845 | -2.4549 | 11.2918 | 11.0061 | 10.7908 | 10.5245 | 10.2224 | 9.9327 | 9.3459 | 8.8622 | 8.6755 | 8.2 | 5.9102 | 4.7388 | 4.6316 | 7.3237 | 6.9033 | 6.6063 | 6.2492 | 5.8533 | 5.4573 | 4.5216 | 3.8227 | 3.4788 | 2.788 | -0.60898 | -2.4345 | -2.4222
|  | UNION STREET | HE |  |  |  | 8.0186 | 7.6278 | 7.3288 | 6.9971 | 6.6329 | 6.29 | 5.5043 | 4.7869 | 4.1043 | 3.8573 | 1.3614 | 0.28082 | 0.17061 | 11.2378 | 10.9449 | 10.6837 | 10.3806 | 10.0459 | 9.7204 | 9.1643 | 8.6 | 8.0276 | 7.8194 | 4.9122 | 1.9898 | -2.5439 | 7.3145 | 6.9645 | 6.6829 | 6.3624 | 6.0155 | 5.6778 | 4.9461 | 4.2635 | 3.6053 | 3.4033 | 1.0716 | 0.12673 | 0.027755
|  | UNION STREET | CF |  |  |  | 8.1727 | 7.9094 | 7.7369 | 7.5767 | 7.3686 | 7.1369 | 6.939 | 6.6063 | 6.2124 | 5.8022 | 3.8778 | 1.792 | -0.21 | 11.3255 | 11.0878 | 10.8684 | 10.6531 | 10.3867 | 10.0663 | 9.7439 | 9.2959 | 8.802 | 8.2735 | 5.099 | -0.49592 | -10.8092 | 7.4665 | 7.2329 | 7.0686 | 6.9196 | 6.7196 | 6.5002 | 6.3094 | 5.9931 | 5.6237 | 5.242 | 3.4227 | 1.4278 | -0.31714
COWLEY GSP | OXFORD BSP | UNIVERSITY PARKS | MINIMUM HEADROOM | SP 51472 07052 | YES | 1.998 | 20.0182 | 19.8722 | 19.7814 | 19.6794 | 19.5733 | 19.462 | 19.3182 | 19.1743 | 19.0233 | 18.8967 | 18.3906 | 18.0896 | 17.9855 | 23.1886 | 23.1161 | 23.0273 | 22.9477 | 22.862 | 22.7743 | 22.661 | 22.5529 | 22.4304 | 22.3284 | 21.8365 | 21.2029 | 18.9824 | 21.0529 | 20.9355 | 20.8539 | 20.76 | 20.6641 | 20.5661 | 20.4375 | 20.311 | 20.1784 | 20.0671 | 19.6314 | 19.3814 | 19.2926
|  | UNIVERSITY PARKS | EE |  |  |  | 20.0182 | 19.912 | 19.7875 | 19.6794 | 19.5733 | 19.462 | 19.3182 | 19.1743 | 19.0233 | 18.8967 | 18.3906 | 18.0896 | 17.9855 | 23.1886 | 23.1161 | 23.0273 | 22.9477 | 22.862 | 22.7743 | 22.661 | 22.5529 | 22.4304 | 22.3284 | 21.8365 | 21.2212 | 20.1498 | 21.0529 | 20.962 | 20.8539 | 20.76 | 20.6641 | 20.5661 | 20.4375 | 20.311 | 20.1784 | 20.0671 | 19.6314 | 19.3814 | 19.2926
|  | UNIVERSITY PARKS | HT |  |  |  | 20.0467 | 19.8722 | 19.7814 | 19.6845 | 19.5845 | 19.4835 | 19.3794 | 19.2692 | 19.1539 | 19.0386 | 18.4947 | 18.161 | 18.0233 | 23.2182 | 23.1171 | 23.06 | 22.9998 | 22.9314 | 22.8712 | 22.8039 | 22.7314 | 22.6559 | 22.5784 | 22.2294 | 22.0018 | 21.9049 | 21.0814 | 20.9355 | 20.8569 | 20.7763 | 20.6886 | 20.6018 | 20.512 | 20.4171 | 20.3171 | 20.2161 | 19.7477 | 19.459 | 19.3396
|  | UNIVERSITY PARKS | HE |  |  |  | 20.0437 | 19.9529 | 19.8518 | 19.7631 | 19.6753 | 19.5937 | 19.5131 | 19.4284 | 19.3375 | 19.2477 | 18.9671 | 18.8773 | 18.7498 | 23.21 | 23.1467 | 23.0753 | 23.01 | 22.9416 | 22.8773 | 22.812 | 22.7426 | 22.6631 | 22.5794 | 22.2426 | 21.8498 | 20.7845 | 21.0784 | 21.0008 | 20.9131 | 20.8375 | 20.762 | 20.6886 | 20.6182 | 20.5426 | 20.462 | 20.3804 | 20.1345 | 20.06 | 19.9886
|  | UNIVERSITY PARKS | CF |  |  |  | 20.0977 | 20.0559 | 20.0131 | 19.9682 | 19.9202 | 19.8682 | 19.8141 | 19.7549 | 19.6743 | 19.5957 | 19.2345 | 18.962 | 18.7365 | 23.2426 | 23.2049 | 23.1651 | 23.1202 | 23.0733 | 23.0182 | 22.959 | 22.8957 | 22.8141 | 22.7314 | 22.2661 | 21.2029 | 18.9824 | 21.1253 | 21.0886 | 21.0518 | 21.01 | 20.9682 | 20.9212 | 20.8743 | 20.8212 | 20.7518 | 20.6835 | 20.3682 | 20.1345 | 19.9447
EAST CLAYDON GSP | BICESTER NORTH BSP | UPPER HEYFORD | MINIMUM HEADROOM | SP 51750 25667 | YES | 4.729 | 4.2519 | 4.0397 | 2.7805 | 2.3764 | 1.9183 | 0.89378 | -0.70724 | -2.3001 | -3.6776 | -4.4756 | -5.7674 | -6.0725 | -6.3736 | 4.8525 | 4.728 | 3.5769 | 3.3484 | 3.1167 | 2.1616 | 1.0412 | -0.34959 | -1.5312 | -2.0404 | -2.8802 | -3.4169 | -4.8139 | 4.0004 | 3.8218 | 2.5984 | 2.2576 | 1.879 | 0.7596 | -0.80673 | -2.3057 | -3.6139 | -4.3047 | -5.4077 | -5.6761 | -5.922
|  | UPPER HEYFORD | EE |  |  |  | 4.2519 | 4.0397 | 2.7805 | 2.3764 | 1.9183 | 0.89378 | -0.55826 | -1.894 | -3.146 | -4.1481 | -5.7674 | -6.0725 | -6.2603 | 4.8525 | 4.728 | 3.5769 | 3.3484 | 3.1167 | 2.28 | 1.1433 | 0.088169 | -0.90877 | -1.6659 | -2.8802 | -3.3169 | -3.9537 | 4.0004 | 3.8218 | 2.5984 | 2.2576 | 1.879 | 0.7596 | -0.64346 | -1.8843 | -3.0384 | -3.9455 | -5.4077 | -5.6761 | -5.822
|  | UPPER HEYFORD | HT |  |  |  | 4.3121 | 4.1121 | 2.8734 | 2.5224 | 2.0642 | 1.0183 | -0.70724 | -2.3001 | -3.6776 | -4.4756 | -5.6307 | -6.0419 | -6.3736 | 4.9086 | 4.8055 | 3.6759 | 3.5055 | 3.28 | 2.4198 | 1.0412 | -0.34959 | -1.5312 | -2.0404 | -2.6016 | -2.8067 | -2.972 | 4.0647 | 3.8943 | 2.6933 | 2.4076 | 2.032 | 0.86674 | -0.80673 | -2.3057 | -3.6139 | -4.3047 | -5.2894 | -5.6486 | -5.922
|  | UPPER HEYFORD | HE |  |  |  | 4.3111 | 4.1111 | 2.8724 | 2.5254 | 2.0713 | 1.0958 | -0.34193 | -1.6725 | -2.9011 | -3.9134 | -5.7276 | -6.0225 | -6.1766 | 4.8994 | 4.7861 | 3.6535 | 3.4698 | 3.2382 | 2.4443 | 1.3535 | 0.2698 | -0.71693 | -1.5047 | -2.8557 | -3.2975 | -3.9118 | 4.0616 | 3.8943 | 2.6943 | 2.4116 | 2.0382 | 0.96572 | -0.42816 | -1.6639 | -2.7965 | -3.7139 | -5.371 | -5.6292 | -5.7455
|  | UPPER HEYFORD | CF |  |  |  | 4.4509 | 4.3683 | 3.2509 | 3.1081 | 2.8958 | 1.407 | 0.44888 | -0.5552 | -1.5205 | -2.4113 | -4.8174 | -5.4542 | -6.1083 | 4.9688 | 4.9137 | 3.8351 | 3.7484 | 3.6239 | 2.1616 | 1.38 | 0.66062 | -0.027137 | -0.63224 | -2.5486 | -3.4169 | -4.8139 | 4.1729 | 4.1004 | 2.9984 | 2.881 | 2.7025 | 0.88613 | 0.024904 | -0.83632 | -1.6629 | -2.4159 | -4.5455 | -5.1241 | -5.6996
IVER 132KV | UPTON BSP | UPTON | MINIMUM HEADROOM | TQ 00800 79434 | YES | 1.741 | 12.3376 | 11.8774 | 11.2896 | 10.8039 | 10.1519 | 9.1825 | 7.7733 | 6.2703 | 4.8529 | 3.7029 | -0.62158 | -3.8114 | -4.4195 | 17.5055 | 17.3127 | 17.0616 | 16.7739 | 16.1933 | 15.4422 | 14.3045 | 13.0147 | 11.8116 | 10.828 | 6.4749 | 1.8341 | -11.1914 | 12.2716 | 11.8196 | 11.2094 | 10.8727 | 10.2278 | 9.3196 | 7.9339 | 6.4176 | 5.0073 | 3.89 | -0.10796 | -3.1233 | -3.8069
|  | UPTON | EE |  |  |  | 12.3376 | 11.8774 | 11.2896 | 10.8039 | 10.1519 | 9.1825 | 7.7733 | 6.2703 | 4.8529 | 3.7029 | -0.62158 | -2.8512 | -2.8746 | 17.5055 | 17.3127 | 17.0616 | 16.7739 | 16.1933 | 15.4422 | 14.3045 | 13.0147 | 11.8116 | 10.828 | 6.4749 | 2.2188 | -4.02 | 12.2716 | 11.8196 | 11.2094 | 10.8727 | 10.2278 | 9.3196 | 7.9339 | 6.4176 | 5.0073 | 3.89 | -0.10796 | -2.0998 | -2.3437
|  | UPTON | HT |  |  |  | 12.6223 | 12.2825 | 11.8488 | 11.2243 | 10.6835 | 9.8182 | 8.9682 | 7.7498 | 6.558 | 5.2937 | -0.5175 | -3.8114 | -4.4195 | 17.6586 | 17.529 | 17.3657 | 17.1422 | 16.9351 | 16.4535 | 15.9453 | 15.0259 | 14.1596 | 13.2157 | 9.1678 | 6.932 | 6.1647 | 12.6186 | 12.2788 | 11.8482 | 11.3002 | 10.7757 | 9.9829 | 9.2278 | 8.0124 | 6.84 | 5.59 | -0.014082 | -3.1233 | -3.8069
|  | UPTON | HE |  |  |  | 12.6223 | 12.3213 | 11.9243 | 11.3498 | 10.8631 | 10.0611 | 9.3692 | 8.3203 | 7.3529 | 6.3335 | 1.9835 | -0.14709 | -0.84505 | 17.6371 | 17.4922 | 17.3045 | 17.0596 | 16.7657 | 16.1494 | 15.6239 | 14.7331 | 13.9453 | 13.0912 | 8.3749 | 3.9382 | -2.5251 | 12.6104 | 12.3124 | 11.9124 | 11.4124 | 10.9359 | 10.2053 | 9.6135 | 8.5788 | 7.6533 | 6.6716 | 2.49 | 0.53694 | -0.42327
|  | UPTON | CF |  |  |  | 12.8305 | 12.6458 | 12.4611 | 12.206 | 11.8958 | 11.4009 | 10.7417 | 10.4703 | 9.9233 | 9.3927 | 6.2743 | 2.9274 | -0.081786 | 17.7341 | 17.6259 | 17.5086 | 17.3688 | 17.1963 | 16.7178 | 16.0127 | 15.5065 | 14.7708 | 14.0371 | 9.3861 | 1.8341 | -11.1914 | 12.791 | 12.5798 | 12.3737 | 12.138 | 11.8186 | 11.3543 | 10.7135 | 10.539 | 9.9645 | 9.4176 | 6.3798 | 3.389 | 0.80735
IVER 132kV |  | UXBRIDGE | MINIMUM HEADROOM | TQ 04984 83484 | YES | 26.135 | 29.5053 | 27.9314 | 26.0498 | 23.9998 | 21.7804 | 19.4641 | 17.0069 | 14.2355 | 11.4437 | 8.9263 | 3.6049 | 0.95694 | -1.1053 | 32.3008 | 30.6024 | 28.7718 | 26.7524 | 24.7943 | 22.8351 | 20.8106 | 18.5463 | 16.2861 | 14.03 | 10.078 | 5.2453 | -6.6088 | 26.6576 | 25.0122 | 23.2153 | 21.2378 | 19.2571 | 17.2592 | 15.1306 | 12.3908 | 9.6898 | 7.2582 | 2.2653 | -1.2133 | -3.0765
|  | UXBRIDGE | EE |  |  |  | 29.5053 | 28.1876 | 26.1069 | 24.1018 | 21.7804 | 19.4641 | 17.0069 | 14.2355 | 11.4437 | 8.9263 | 3.6049 | 1.208 | -0.44102 | 32.3008 | 31.1555 | 29.1637 | 27.2984 | 25.1086 | 22.9831 | 20.8106 | 18.5463 | 16.2861 | 14.03 | 10.078 | 5.3984 | -0.70571 | 26.6576 | 25.4561 | 23.5143 | 21.701 | 19.5704 | 17.4357 | 15.1306 | 12.3908 | 9.6898 | 7.2582 | 2.2653 | -0.88878 | -2.5643
|  | UXBRIDGE | HT |  |  |  | 29.7839 | 27.9314 | 26.0498 | 23.9998 | 21.9508 | 19.8549 | 17.7559 | 15.408 | 13.0498 | 10.9733 | 4.6712 | 0.95694 | -1.1053 | 32.4998 | 30.6024 | 28.7718 | 26.7524 | 24.7943 | 22.8351 | 20.9759 | 18.9239 | 16.9076 | 15.4759 | 11.2035 | 8.8106 | 7.2422 | 26.8688 | 25.0122 | 23.2153 | 21.2378 | 19.2571 | 17.2592 | 15.2786 | 13.0255 | 10.6469 | 8.7112 | 2.7673 | -1.2133 | -3.0765
|  | UXBRIDGE | HE |  |  |  | 29.7635 | 28.5824 | 26.6773 | 24.7529 | 22.7345 | 20.6049 | 18.509 | 16.1467 | 13.6324 | 11.0631 | 4.6029 | 1.5784 | -0.43592 | 32.4661 | 31.3902 | 29.4871 | 27.6106 | 25.6759 | 23.6412 | 21.7422 | 19.6453 | 17.5116 | 15.4055 | 10.6433 | 6.9647 | 0.94429 | 26.8555 | 25.7408 | 23.9112 | 22.0959 | 20.2255 | 18.2102 | 16.2724 | 14.1337 | 11.7724 | 9.2837 | 3.1102 | 0.23571 | -1.7031
|  | UXBRIDGE | CF |  |  |  | 30.0073 | 28.96 | 27.9314 | 26.2222 | 24.3284 | 22.3896 | 20.508 | 18.6641 | 16.658 | 14.6131 | 9.3059 | 4.6304 | 1.012 | 32.5937 | 31.5739 | 30.5871 | 28.7473 | 26.7422 | 24.7024 | 22.7433 | 20.8953 | 18.8994 | 16.8749 | 12.5208 | 5.2453 | -6.6088 | 27.0412 | 26.0286 | 25.048 | 23.3204 | 21.4745 | 19.5531 | 17.6939 | 15.9224 | 14.0122 | 12.0796 | 7.5194 | 3.0724 | -0.34082
NURSLING GSP | VELMORE BSP | VELMORE | MINIMUM HEADROOM | SU 42935 19205 | YES | 4.697 | 5.2345 | 4.5753 | 3.8477 | 3.1783 | 2.2824 | 1.2671 | 0.0038408 | -1.5196 | -3.1155 | -4.5696 | -10.8094 | -14.3258 | -15.9717 | 8.6671 | 8.2477 | 7.7865 | 7.4987 | 6.9936 | 6.3467 | 5.4498 | 4.3589 | 3.2651 | 2.3242 | -2.09 | -6.4268 | -17.7798 | 6.0304 | 5.4079 | 4.7171 | 4.0824 | 3.2304 | 2.264 | 1.0722 | -0.36453 | -1.9278 | -3.2829 | -9.1727 | -12.4329 | -13.9523
|  | VELMORE | EE |  |  |  | 5.2345 | 4.5753 | 3.8477 | 3.1783 | 2.2824 | 1.2671 | 0.0038408 | -1.5196 | -3.1155 | -4.5696 | -9.9523 | -12.0839 | -13.4451 | 8.6671 | 8.2477 | 7.7865 | 7.4987 | 6.9936 | 6.3467 | 5.4498 | 4.3589 | 3.2651 | 2.3242 | -1.1829 | -5.0104 | -10.7421 | 6.0304 | 5.4079 | 4.7171 | 4.0824 | 3.2304 | 2.264 | 1.0722 | -0.36453 | -1.9278 | -3.2829 | -8.2727 | -10.1747 | -11.3666
|  | VELMORE | HT |  |  |  | 5.6722 | 5.1742 | 4.6314 | 4.0589 | 3.3375 | 2.4753 | 1.5202 | 0.24262 | -1.24 | -2.7911 | -9.5462 | -12.8543 | -14.5523 | 8.8967 | 8.5936 | 8.2814 | 8.0049 | 7.6202 | 7.1477 | 6.711 | 5.8824 | 4.96 | 3.9569 | -0.288 | -2.24 | -3.1931 | 6.4538 | 5.9875 | 5.4783 | 4.9345 | 4.2508 | 3.4406 | 2.5569 | 1.3008 | -0.084935 | -1.538 | -7.8655 | -10.9033 | -12.438
|  | VELMORE | HE |  |  |  | 5.6089 | 5.0722 | 4.4834 | 3.8498 | 3.0763 | 2.1538 | 1.164 | -0.21657 | -1.7298 | -3.338 | -10.8094 | -14.3258 | -15.9717 | 8.8345 | 8.4732 | 8.0885 | 7.7273 | 7.2702 | 6.7283 | 6.2589 | 5.3528 | 4.261 | 3.113 | -2.09 | -5.1125 | -10.6104 | 6.3906 | 5.8906 | 5.3334 | 4.7314 | 3.9947 | 3.1161 | 2.1926 | 0.88649 | -0.54208 | -2.1186 | -9.1727 | -12.4329 | -13.9523
|  | VELMORE | CF |  |  |  | 5.963 | 5.6426 | 5.3028 | 4.9559 | 4.5508 | 4.0875 | 3.5875 | 3.0365 | 2.2712 | 1.4242 | -4.5339 | -9.5533 | -13.2502 | 8.9559 | 8.6722 | 8.3753 | 8.1049 | 7.7804 | 7.3957 | 6.961 | 6.6304 | 6.0722 | 5.4569 | 0.42017 | -6.4268 | -17.7798 | 6.7283 | 6.4304 | 6.112 | 5.7814 | 5.3936 | 4.9528 | 4.4712 | 3.9477 | 3.2181 | 2.411 | -3.1921 | -8.0125 | -11.4543
FAWLEY GSP | COWES & WOOTTON COMMON BSP | VENTNOR | MINIMUM HEADROOM | SZ 56148 77857 | YES | 0.313 | 19.2776 | 18.9816 | 18.6694 | 18.2704 | 17.8255 | 17.7745 | 17.1806 | 16.5 | 15.8255 | 15.3449 | 12.8102 | 10.7357 | 9.5847 | 19.7265 | 19.4837 | 19.2296 | 18.9102 | 18.5439 | 18.4837 | 18.052 | 17.5418 | 17.0286 | 16.6643 | 14.6571 | 12.2602 | 6.249 | 18.8551 | 18.5551 | 18.251 | 17.8653 | 17.4357 | 17.3908 | 16.8327 | 16.1888 | 15.549 | 15.1031 | 12.8786 | 11.1112 | 10.1286
|  | VENTNOR | EE |  |  |  | 19.2776 | 18.9816 | 18.6694 | 18.2704 | 17.8255 | 17.7745 | 17.1806 | 16.5 | 15.8255 | 15.3449 | 12.8102 | 11.1714 | 9.9265 | 19.7265 | 19.4837 | 19.2296 | 18.9102 | 18.5439 | 18.4837 | 18.052 | 17.5418 | 17.0286 | 16.6643 | 14.6571 | 12.6439 | 9.5408 | 18.8551 | 18.5551 | 18.251 | 17.8653 | 17.4357 | 17.3908 | 16.8327 | 16.1888 | 15.549 | 15.1031 | 12.8786 | 11.4969 | 10.4122
|  | VENTNOR | HT |  |  |  | 19.4357 | 19.2082 | 18.9786 | 18.7051 | 18.4398 | 18.101 | 17.5469 | 16.9102 | 16.6612 | 16.0551 | 12.8786 | 10.7357 | 9.5847 | 19.8908 | 19.7367 | 19.5827 | 19.3898 | 19.2102 | 18.9663 | 18.6276 | 18.2337 | 18.1776 | 17.801 | 15.9847 | 14.9418 | 14.4582 | 19.0378 | 18.8163 | 18.5908 | 18.3163 | 18.0602 | 17.7235 | 17.201 | 16.6082 | 16.4327 | 15.8643 | 12.9694 | 11.1112 | 10.1286
|  | VENTNOR | HE |  |  |  | 19.4276 | 19.2133 | 18.9949 | 18.7337 | 18.4888 | 18.1806 | 17.7051 | 17.152 | 16.9898 | 16.4765 | 13.6827 | 12.0327 | 11.3245 | 19.8602 | 19.6878 | 19.5153 | 19.3 | 19.0878 | 18.8163 | 18.4612 | 18.0449 | 17.9653 | 17.5561 | 15.2337 | 13.149 | 10.2847 | 19.0286 | 18.8194 | 18.6051 | 18.348 | 18.1102 | 17.8051 | 17.352 | 16.8316 | 16.7337 | 16.248 | 13.7153 | 12.3031 | 11.7071
|  | VENTNOR | CF |  |  |  | 19.502 | 19.3745 | 19.202 | 19.048 | 18.8408 | 18.6551 | 18.4122 | 18.1235 | 17.8102 | 17.4806 | 16.1296 | 14.3112 | 12.652 | 19.898 | 19.7755 | 19.6092 | 19.4622 | 19.2469 | 19.0408 | 18.7612 | 18.4347 | 18.0837 | 17.7092 | 15.7388 | 12.2602 | 6.249 | 19.0918 | 18.9673 | 18.7918 | 18.6449 | 18.4378 | 18.2694 | 18.0337 | 17.751 | 17.448 | 17.1286 | 15.8684 | 14.2337 | 12.8194
MANNINGTON GSP | MANNINGTON BSP | VERWOOD | MINIMUM HEADROOM | SU 07716 10226 | YES | 1.123 | 3.4724 | 2.8714 | 2.3265 | 2.2265 | 1.7939 | 1.3367 | 0.62857 | -0.16122 | -0.95 | -1.4633 | -4.5582 | -7.2051 | -8.6194 | 5.8051 | 5.4133 | 5.0276 | 4.9755 | 4.6459 | 4.2918 | 3.8133 | 3.2622 | 2.7031 | 2.3571 | 0.39592 | -2.4245 | -8.85 | 4.0367 | 3.4969 | 2.9612 | 2.9296 | 2.5163 | 2.0786 | 1.4153 | 0.66224 | -0.087755 | -0.52449 | -3.1959 | -5.399 | -6.5806
|  | VERWOOD | EE |  |  |  | 3.4724 | 2.8714 | 2.3265 | 2.2265 | 1.7939 | 1.3367 | 0.62857 | -0.16122 | -0.95 | -1.4633 | -4.1622 | -6.6469 | -8.3806 | 5.8051 | 5.4133 | 5.0276 | 4.9755 | 4.6459 | 4.2918 | 3.8133 | 3.2622 | 2.7031 | 2.3571 | 0.39592 | -1.9786 | -5.4224 | 4.0367 | 3.4969 | 2.9612 | 2.9296 | 2.5163 | 2.0786 | 1.4153 | 0.66224 | -0.087755 | -0.52449 | -2.8837 | -4.9092 | -6.3786
|  | VERWOOD | HT |  |  |  | 3.6592 | 3.1122 | 2.6561 | 2.3082 | 1.8908 | 1.4418 | 1.1602 | 0.46531 | -0.25 | -0.98265 | -4.5582 | -7.2051 | -8.6194 | 5.9949 | 5.6898 | 5.4235 | 5.2194 | 4.9602 | 4.6755 | 4.6367 | 4.2653 | 3.8735 | 3.4643 | 1.6347 | 0.55408 | -0.0020408 | 4.2286 | 3.7582 | 3.3418 | 3.0204 | 2.6255 | 2.1908 | 1.9857 | 1.35 | 0.69286 | 0.016327 | -3.1959 | -5.399 | -6.5806
|  | VERWOOD | HE |  |  |  | 3.6776 | 3.1612 | 2.7347 | 2.4184 | 2.0347 | 1.6265 | 1.5061 | 0.96429 | 0.39796 | -0.17959 | -3.1755 | -5.6133 | -6.8071 | 5.9684 | 5.6439 | 5.352 | 5.1224 | 4.8316 | 4.5153 | 4.4745 | 4.0908 | 3.6786 | 3.2449 | 0.8449 | -1.5469 | -4.7878 | 4.2429 | 3.801 | 3.4122 | 3.1194 | 2.75 | 2.3429 | 2.2837 | 1.7796 | 1.252 | 0.71224 | -2.0306 | -4.0071 | -4.9959
|  | VERWOOD | CF |  |  |  | 3.7939 | 3.3847 | 3.0827 | 2.8857 | 2.6367 | 2.3755 | 2.1071 | 2.2184 | 1.9612 | 1.6888 | -0.36531 | -2.7429 | -4.7939 | 6.0224 | 5.7408 | 5.5 | 5.3214 | 5.0878 | 4.8224 | 4.5153 | 4.5051 | 4.1878 | 3.8469 | 1.3704 | -2.4245 | -8.85 | 4.348 | 4.0041 | 3.7286 | 3.5378 | 3.2827 | 3.0143 | 2.7316 | 2.9204 | 2.6612 | 2.3816 | 0.41633 | -1.6408 | -3.3827
NURSLING GSP |  | VICARAGE FARM ROAD | MINIMUM HEADROOM | TQ 12358 76435 | YES | 39.933 | 4.5962 | 3.1156 | -5.8553 | -10.6238 | -15.1156 | -19.4797 | -23.8063 | -28.4093 | -33.0124 | -37.0491 | -46.7373 | -51.2934 | -52.1516 | 14.6156 | 13.5738 | 5.0131 | 0.75884 | -3.131 | -6.7756 | -10.3848 | -14.2756 | -18.2073 | -21.7277 | -31.2822 | -38.3261 | -57.4148 | 7.3482 | 6.0115 | -2.7818 | -7.3789 | -11.6718 | -15.845 | -20.0063 | -24.4471 | -28.8818 | -32.8154 | -42.3271 | -47.1771 | -48.0271
|  | VICARAGE FARM ROAD | EE |  |  |  | 4.5962 | 3.1156 | -5.8553 | -10.6238 | -15.1156 | -19.4797 | -23.8063 | -28.4093 | -33.0124 | -37.0491 | -46.7373 | -51.2934 | -52.1516 | 14.6156 | 13.5738 | 5.0131 | 0.75884 | -3.131 | -6.7756 | -10.3848 | -14.2756 | -18.2073 | -21.7277 | -31.2822 | -38.3261 | -47.0863 | 7.3482 | 6.0115 | -2.7818 | -7.3789 | -11.6718 | -15.845 | -20.0063 | -24.4471 | -28.8818 | -32.8154 | -42.3271 | -47.1771 | -48.0271
|  | VICARAGE FARM ROAD | HT |  |  |  | 5.4085 | 3.9166 | -5.0481 | -9.6544 | -13.6677 | -17.5644 | -21.1032 | -24.9175 | -28.892 | -32.8624 | -43.725 | -49.2863 | -50.3832 | 15.3278 | 14.3972 | 6.008 | 2.0629 | -1.2636 | -4.3501 | -7.1971 | -10.3175 | -13.5777 | -16.8369 | -24.7067 | -28.2454 | -29.625 | 8.1401 | 6.8391 | -1.9441 | -6.3473 | -10.1218 | -13.8705 | -17.2899 | -20.9899 | -24.844 | -28.6899 | -39.0771 | -44.274 | -45.2056
|  | VICARAGE FARM ROAD | HE |  |  |  | 5.334 | 4.184 | -4.7736 | -9.1912 | -12.8463 | -16.6869 | -20.4175 | -24.3654 | -28.4593 | -32.5073 | -45.122 | -49.7495 | -50.3005 | 15.188 | 14.4054 | 5.8315 | 1.8527 | -1.3575 | -4.5807 | -7.7603 | -11.1736 | -14.7634 | -18.3818 | -29.0669 | -35.8587 | -44.4495 | 8.0676 | 7.0585 | -1.742 | -5.9973 | -9.4442 | -13.1675 | -16.7746 | -20.6052 | -24.5777 | -28.5093 | -41.4016 | -45.8046 | -46.3077
|  | VICARAGE FARM ROAD | CF |  |  |  | 5.8115 | 5.1697 | -2.9696 | -6.8126 | -9.9626 | -12.5603 | -14.6297 | -17.3848 | -20.3685 | -23.4348 | -34.5434 | -41.0893 | -46.3791 | 15.4717 | 14.9605 | 6.8651 | 3.1007 | -0.014624 | -2.6175 | -4.845 | -7.644 | -10.6042 | -13.695 | -25.475 | -37.924 | -57.4148 | 8.4901 | 7.9248 | -0.1665 | -3.9473 | -7.0422 | -9.5828 | -11.5756 | -14.2491 | -17.1185 | -20.0593 | -30.2883 | -37.1087 | -42.3852
COWLEY GSP | COWLEY LOCAL (2 X 90) | WALLINGFORD | MINIMUM HEADROOM | SU 59847 89486 | YES | 5.442 | -5.0111 | -5.5805 | -6.3091 | -7.7642 | -8.8713 | -12.0244 | -13.5611 | -15.4264 | -16.202 | -19.8713 | -28.2499 | -39.2866 | -48.902 | -0.40603 | -0.75399 | -1.3581 | -2.7234 | -3.5693 | -6.9132 | -8.4622 | -10.304 | -10.8152 | -15.0958 | -24.5989 | -36.9703 | -48.9622 | -4.5499 | -5.056 | -5.7193 | -7.2346 | -8.2887 | -11.8713 | -13.4662 | -15.5213 | -16.2254 | -20.6448 | -30.2836 | -42.4928 | -53.6917
|  | WALLINGFORD | EE |  |  |  | -5.0111 | -5.5805 | -6.3091 | -7.1387 | -7.7091 | -9.2866 | -10.903 | -11.9387 | -13.9917 | -15.1132 | -21.2438 | -35.2662 | -41.2509 | -0.40603 | -0.75399 | -1.1958 | -1.6856 | -1.9877 | -3.3346 | -4.7295 | -5.3775 | -7.356 | -8.4489 | -15.0683 | -32.1417 | -40.7897 | -4.5499 | -5.056 | -5.7193 | -6.4734 | -6.8458 | -8.4591 | -10.1152 | -11.0601 | -13.2917 | -14.4785 | -21.1713 | -37.6336 | -44.2295
|  | WALLINGFORD | HT |  |  |  | -4.8713 | -5.3887 | -6.252 | -7.3856 | -8.2081 | -10.8866 | -12.5377 | -14.5948 | -15.7305 | -17.8397 | -25.8642 | -39.2866 | -48.902 | -0.26522 | -0.54175 | -1.1458 | -2.0479 | -2.4713 | -5.152 | -6.6764 | -8.5897 | -9.3611 | -11.4989 | -19.2591 | -34.0111 | -44.6836 | -4.3458 | -4.7856 | -5.6091 | -6.7264 | -7.4203 | -10.404 | -12.0948 | -14.3346 | -15.4315 | -17.8509 | -26.8254 | -42.4928 | -53.6917
|  | WALLINGFORD | HE |  |  |  | -4.8642 | -5.3611 | -6.3071 | -7.7642 | -8.8713 | -12.0244 | -13.5611 | -15.4264 | -16.202 | -19.8713 | -28.2499 | -38.452 | -46.6407 | -0.29379 | -0.59481 | -1.3581 | -2.7234 | -3.5693 | -6.9132 | -8.4622 | -10.304 | -10.8152 | -15.0958 | -24.5989 | -36.9703 | -48.9622 | -4.3458 | -4.7693 | -5.7009 | -7.2346 | -8.2887 | -11.8713 | -13.4662 | -15.5213 | -16.2254 | -20.6448 | -30.2836 | -41.9948 | -51.7254
|  | WALLINGFORD | CF |  |  |  | -4.7224 | -5.1111 | -5.5703 | -6.1101 | -6.9081 | -7.8673 | -8.7897 | -9.6234 | -10.1346 | -10.8928 | -15.7815 | -22.1815 | -28.3499 | -0.23052 | -0.48767 | -0.78358 | -1.1295 | -1.7764 | -2.5785 | -3.4877 | -4.2826 | -4.8734 | -5.7662 | -11.8815 | -21.0815 | -32.7407 | -4.2295 | -4.5744 | -4.9642 | -5.4264 | -6.1764 | -7.103 | -8.0754 | -8.9438 | -9.3887 | -10.2581 | -15.8203 | -23.055 | -29.9703
COWLEY GSP | DRAYTON BSP | WANTAGE | MINIMUM HEADROOM | SU 41290 88304 | YES | 3.575 | 18.2417 | 17.6386 | 16.9192 | 16.207 | 15.4478 | 15.1141 | 14.3101 | 13.4284 | 12.5529 | 11.8795 | 8.2733 | 6.1101 | 4.8356 | 20.0672 | 19.6856 | 19.255 | 18.7927 | 18.2866 | 18.156 | 17.658 | 17.0999 | 16.5356 | 16.106 | 13.8509 | 11.9662 | 6.9172 | 18.7723 | 18.2478 | 17.6223 | 16.9825 | 16.2897 | 16.0254 | 15.2988 | 14.4948 | 13.6968 | 13.0978 | 10.1101 | 8.2897 | 7.2917
|  | WANTAGE | EE |  |  |  | 18.2417 | 17.6386 | 16.9192 | 16.207 | 15.4478 | 15.1141 | 14.3101 | 13.4284 | 12.5529 | 11.8795 | 8.4499 | 6.557 | 5.0978 | 20.0672 | 19.6856 | 19.255 | 18.7927 | 18.2866 | 18.156 | 17.658 | 17.0999 | 16.5356 | 16.106 | 13.8509 | 12.0244 | 9.3346 | 18.7723 | 18.2478 | 17.6223 | 16.9825 | 16.2897 | 16.0254 | 15.2988 | 14.4948 | 13.6968 | 13.0978 | 10.2162 | 8.707 | 7.5192
|  | WANTAGE | HT |  |  |  | 18.3988 | 17.858 | 17.205 | 16.5468 | 15.9795 | 15.307 | 14.5121 | 13.9805 | 13.1784 | 12.3295 | 8.2733 | 6.1101 | 4.8356 | 20.2111 | 19.9152 | 19.5723 | 19.1958 | 18.8948 | 18.5295 | 18.1009 | 17.9101 | 17.4744 | 16.9846 | 14.9009 | 13.9305 | 13.4101 | 18.9284 | 18.4652 | 17.9121 | 17.3274 | 16.8254 | 16.2254 | 15.5131 | 15.1397 | 14.4213 | 13.6376 | 10.1101 | 8.2897 | 7.2917
|  | WANTAGE | HE |  |  |  | 18.3999 | 17.8774 | 17.2468 | 16.6478 | 16.106 | 15.4233 | 14.7284 | 14.3182 | 13.6335 | 12.9203 | 9.3029 | 7.3968 | 6.458 | 20.1856 | 19.8703 | 19.505 | 19.1437 | 18.8182 | 18.3907 | 17.9621 | 17.7601 | 17.3141 | 16.8468 | 14.3244 | 12.4448 | 9.9692 | 18.9295 | 18.4846 | 17.9488 | 17.4203 | 16.9427 | 16.3305 | 15.708 | 15.4274 | 14.8019 | 14.1611 | 11.0019 | 9.4907 | 8.7448
|  | WANTAGE | CF |  |  |  | 18.507 | 18.0856 | 17.5805 | 17.1223 | 16.6437 | 16.2111 | 15.7978 | 15.3305 | 14.8427 | 14.7652 | 12.0917 | 10.1305 | 8.208 | 20.2407 | 19.9672 | 19.6539 | 19.356 | 19.0233 | 18.7284 | 18.4029 | 18.0244 | 17.6274 | 17.505 | 15.0284 | 11.9662 | 6.9172 | 19.0284 | 18.6774 | 18.2529 | 17.857 | 17.4295 | 17.055 | 16.6876 | 16.2682 | 15.8274 | 15.7978 | 13.3805 | 11.6488 | 10.0611
MANNINGTON GSP | WAREHAM | WAREHAM TOWN | MINIMUM HEADROOM | SY 92036 87463 | YES | 1.007 | 3.8658 | 3.3658 | 38.0092 | 37.6745 | 37.1776 | 37.0612 | 36.7122 | 36.2867 | 35.8592 | 35.499 | 32.7378 | 31.0082 | 29.9786 | 5.836 | 5.339 | 39.6143 | 39.3408 | 38.9888 | 38.9531 | 38.8327 | 38.6898 | 38.5102 | 38.3847 | 36.9827 | 36.0459 | 34.9796 | 4.6005 | 4.1301 | 38.5592 | 38.1337 | 37.4704 | 37.3786 | 36.9418 | 36.4622 | 35.9776 | 35.6224 | 33.1704 | 31.5816 | 30.6969
|  | WAREHAM TOWN | EE |  |  |  | 3.8658 | 3.3658 | 38.0092 | 37.6745 | 37.1776 | 37.0612 | 36.7122 | 36.2867 | 35.8592 | 35.499 | 32.9469 | 31.2959 | 30.1224 | 5.836 | 5.339 | 39.6143 | 39.3408 | 38.9888 | 38.9531 | 38.8327 | 38.6898 | 38.5102 | 38.3847 | 36.9827 | 36.0459 | 35.0306 | 4.6005 | 4.1301 | 38.5592 | 38.1337 | 37.4704 | 37.3786 | 36.9418 | 36.4622 | 35.9776 | 35.6224 | 33.3143 | 31.8857 | 30.8388
|  | WAREHAM TOWN | HT |  |  |  | 3.9393 | 3.4536 | 38.1296 | 37.8286 | 37.5633 | 37.2867 | 36.8561 | 36.4051 | 36.1316 | 35.5643 | 32.7378 | 31.0082 | 29.9786 | 5.889 | 5.4013 | 39.7 | 39.4531 | 39.3306 | 39.2347 | 39.1276 | 38.9939 | 38.9724 | 38.6367 | 37.1949 | 36.4622 | 36.0337 | 4.6597 | 4.2005 | 38.7163 | 38.3541 | 37.9541 | 37.6153 | 37.1673 | 36.6827 | 36.5122 | 35.9408 | 33.1704 | 31.5816 | 30.6969
|  | WAREHAM TOWN | HE |  |  |  | 3.9393 | 3.4577 | 38.1378 | 37.8408 | 37.3918 | 37.1888 | 36.8694 | 36.5133 | 36.3306 | 35.9888 | 33.5214 | 31.8786 | 31.0561 | 5.8839 | 5.3982 | 39.6959 | 39.4439 | 39.1327 | 39.0347 | 38.9347 | 38.7969 | 38.7827 | 38.6398 | 37.2602 | 36.3102 | 35.4357 | 4.6597 | 4.2056 | 38.7255 | 38.4163 | 37.8724 | 37.5582 | 37.2 | 36.8031 | 36.7204 | 36.3592 | 34.0235 | 32.6367 | 31.9796
|  | WAREHAM TOWN | CF |  |  |  | 4.1485 | 3.5709 | 38.2939 | 38.1224 | 37.6847 | 37.4061 | 37.3122 | 37.1898 | 37.0582 | 36.9194 | 36.0561 | 34.3112 | 32.7888 | 6.0615 | 5.4401 | 39.7469 | 39.5949 | 39.2327 | 38.9929 | 38.9367 | 38.8633 | 38.7847 | 38.6786 | 38.1735 | 36.8653 | 34.9796 | 4.8454 | 4.274 | 38.8153 | 38.6643 | 38.2531 | 37.9429 | 37.7929 | 37.6143 | 37.4214 | 37.2224 | 36.2582 | 34.6153 | 33.2633
BRAMLEY (FLEE) | BRACKNELL | WARFIELD | MINIMUM HEADROOM | SU 86960 71382 | YES | 5.447 | 6.0843 | 5.1884 | 4.1547 | 3.3792 | 2.2486 | 0.89041 | -0.53 | -2.2739 | -4.0178 | -5.0729 | -9.7616 | -13.7065 | -15.7392 | 9.5241 | 8.9445 | 8.2527 | 7.8537 | 7.1312 | 6.2771 | 5.3741 | 4.269 | 3.1547 | 2.4731 | -0.76163 | -4.5831 | -13.8565 | 4.6598 | 3.8761 | 2.9404 | 2.3373 | 1.3261 | 0.12612 | -1.1484 | -2.7116 | -4.2729 | -5.1953 | -9.3137 | -12.7504 | -14.4912
|  | WARFIELD | EE |  |  |  | 6.0843 | 5.1884 | 4.1547 | 3.3792 | 2.2486 | 0.89041 | -0.53 | -2.2739 | -4.0178 | -5.0729 | -9.6647 | -13.0371 | -15.481 | 9.5241 | 8.9445 | 8.2527 | 7.8537 | 7.1312 | 6.2771 | 5.3741 | 4.269 | 3.1547 | 2.4731 | -0.76163 | -4.029 | -8.8198 | 4.6598 | 3.8761 | 2.9404 | 2.3373 | 1.3261 | 0.12612 | -1.1484 | -2.7116 | -4.2729 | -5.1953 | -9.2882 | -12.1657 | -14.2831
|  | WARFIELD | HT |  |  |  | 6.3853 | 5.5822 | 4.7271 | 3.7312 | 2.6445 | 1.7435 | 0.47 | -1.082 | -2.6882 | -3.9535 | -9.7616 | -13.7065 | -15.7392 | 9.8312 | 9.3945 | 8.9292 | 8.3853 | 7.7782 | 7.422 | 6.7598 | 5.9455 | 5.0873 | 4.369 | 1.2414 | -0.53102 | -1.3443 | 4.9822 | 4.3037 | 3.569 | 2.7016 | 1.7506 | 1.0333 | -0.094286 | -1.4535 | -2.8657 | -4.0127 | -9.3137 | -12.7504 | -14.4912
|  | WARFIELD | HE |  |  |  | 6.4016 | 5.6741 | 4.8455 | 3.8455 | 2.7037 | 1.7914 | 0.64551 | -0.7902 | -2.2841 | -3.4382 | -8.7249 | -12.4718 | -14.0606 | 9.7843 | 9.3251 | 8.8067 | 8.1924 | 7.4955 | 7.0516 | 6.3414 | 5.4547 | 4.5129 | 3.6945 | -0.41367 | -4.0606 | -8.4984 | 4.9884 | 4.3639 | 3.6516 | 2.7812 | 1.7873 | 1.0588 | 0.043469 | -1.2188 | -2.5341 | -3.5922 | -8.4555 | -11.7218 | -13.0769
|  | WARFIELD | CF |  |  |  | 6.6231 | 6.0833 | 5.4424 | 4.7384 | 3.9027 | 2.9935 | 2.6496 | 1.7639 | 0.83735 | 0.22306 | -3.4198 | -7.4137 | -10.9647 | 9.8955 | 9.5241 | 9.071 | 8.6016 | 8.0445 | 7.419 | 7.1639 | 6.471 | 5.7404 | 5.122 | 1.1271 | -4.5831 | -13.8565 | 5.1904 | 4.7322 | 4.1731 | 3.5782 | 2.8567 | 2.068 | 1.8486 | 1.0812 | 0.27408 | -0.30143 | -3.732 | -7.2708 | -10.4239
MELKSHAM GSP | FROME BSP | WARMINSTER | MINIMUM HEADROOM | ST 84936 44551 | YES | 4.754 | 7.9876 | 7.6478 | 6.6169 | 6.0985 | 5.2801 | 4.5424 | 3.7424 | 3.1893 | 2.4393 | 1.8128 | 0.021971 | -1.3617 | -2.1556 | 8.5503 | 8.337 | 7.5021 | 7.1766 | 6.6398 | 6.2011 | 5.696 | 5.4796 | 5.0011 | 4.6684 | 3.3664 | 1.8225 | -1.9459 | 7.8731 | 7.5761 | 6.6024 | 6.1452 | 5.4238 | 4.7748 | 4.0585 | 3.683 | 3.0146 | 2.5401 | 0.95544 | -0.26905 | -0.95476
|  | WARMINSTER | EE |  |  |  | 7.9876 | 7.6478 | 6.6169 | 6.0985 | 5.2801 | 4.5424 | 3.7424 | 3.1893 | 2.4393 | 1.874 | 0.10973 | -1.1046 | -2.0117 | 8.5503 | 8.337 | 7.5021 | 7.1766 | 6.6398 | 6.2011 | 5.696 | 5.4796 | 5.0011 | 4.6684 | 3.3664 | 2.0153 | 0.022482 | 7.8731 | 7.5761 | 6.6024 | 6.1452 | 5.4238 | 4.7748 | 4.0585 | 3.683 | 3.0146 | 2.5473 | 1.0197 | -0.035376 | -0.83129
|  | WARMINSTER | HT |  |  |  | 8.0702 | 7.7549 | 6.7648 | 6.2852 | 5.5577 | 4.775 | 3.9965 | 3.1914 | 2.4832 | 1.8128 | 0.021971 | -1.3617 | -2.1556 | 8.635 | 8.4697 | 7.7072 | 7.4429 | 7.0378 | 6.6174 | 6.2072 | 5.7664 | 5.3664 | 4.998 | 4.1653 | 3.5215 | 3.1766 | 7.9496 | 7.6935 | 6.7983 | 6.3922 | 5.7707 | 5.1014 | 4.4422 | 3.7483 | 3.1238 | 2.5401 | 0.95544 | -0.26905 | -0.95476
|  | WARMINSTER | HE |  |  |  | 8.0733 | 7.7641 | 6.7883 | 6.3148 | 5.5597 | 4.8812 | 4.2322 | 3.4444 | 2.7618 | 2.1454 | 0.61177 | -0.60558 | -1.178 | 8.6207 | 8.4391 | 7.6613 | 7.3796 | 6.8888 | 6.5113 | 6.1317 | 5.6684 | 5.2419 | 4.8429 | 3.6296 | 2.2398 | 0.38779 | 7.9516 | 7.7027 | 6.8167 | 6.4197 | 5.7616 | 5.184 | 4.6361 | 3.9656 | 3.3758 | 2.8371 | 1.483 | 0.40442 | -0.09762
|  | WARMINSTER | CF |  |  |  | 8.1937 | 7.9029 | 7.0179 | 6.6169 | 6.0781 | 5.6261 | 5.2577 | 4.8648 | 4.3771 | 3.8832 | 2.4944 | 1.1863 | -0.071906 | 8.7034 | 8.5013 | 7.7592 | 7.4908 | 7.1102 | 6.8092 | 6.5276 | 6.2317 | 5.8755 | 5.5062 | 4.05 | 1.8225 | -1.9459 | 8.0639 | 7.8312 | 7.0238 | 6.6861 | 6.2228 | 5.8371 | 5.5248 | 5.1983 | 4.7799 | 4.3483 | 3.1371 | 1.983 | 0.87687
LOVEDEAN GSP | FORT WIDLEY | WATERLOOVILLE | MINIMUM HEADROOM | SU 67988 09282 | YES | 13.509 | 14.6316 | 13.0653 | 12.1571 | 10.8806 | 9.6704 | 8.3602 | 6.6438 | 4.7826 | 2.9551 | 1.5306 | -5.8705 | -11.1694 | -13.4256 | 18.9202 | 17.7365 | 17.1508 | 16.3059 | 15.4742 | 14.5181 | 13.3487 | 12.0334 | 10.7089 | 9.7375 | 4.3681 | -2.8451 | -18.9349 | 15.1969 | 13.7938 | 13.0438 | 11.9255 | 10.8489 | 9.6775 | 8.1357 | 6.45 | 4.7857 | 3.5204 | -2.8847 | -7.4878 | -9.3307
|  | WATERLOOVILLE | EE |  |  |  | 14.6316 | 13.0653 | 12.1571 | 10.8806 | 9.6704 | 8.3602 | 6.6438 | 4.7826 | 2.9551 | 1.5306 | -5.4715 | -10.2021 | -12.4429 | 18.9202 | 17.7365 | 17.1508 | 16.3059 | 15.4742 | 14.5181 | 13.3487 | 12.0334 | 10.7089 | 9.7375 | 4.3681 | -1.2217 | -9.1921 | 15.1969 | 13.7938 | 13.0438 | 11.9255 | 10.8489 | 9.6775 | 8.1357 | 6.45 | 4.7857 | 3.5204 | -2.6449 | -6.6745 | -8.5511
|  | WATERLOOVILLE | HT |  |  |  | 14.901 | 13.4091 | 12.2714 | 11.0683 | 10.2979 | 9.1449 | 7.5867 | 5.9398 | 4.252 | 2.5061 | -5.8705 | -11.1694 | -13.4256 | 19.2212 | 18.1967 | 17.5355 | 16.8446 | 16.5038 | 15.8834 | 15.1038 | 14.261 | 13.3498 | 12.3334 | 7.7671 | 5.2957 | 4.2518 | 15.501 | 14.1969 | 13.202 | 12.1438 | 11.5234 | 10.5071 | 9.1357 | 7.6693 | 6.1642 | 4.5979 | -2.8847 | -7.4878 | -9.3307
|  | WATERLOOVILLE | HE |  |  |  | 14.9224 | 13.5408 | 12.4479 | 11.2734 | 10.5551 | 9.4663 | 8.1255 | 6.6887 | 5.2306 | 3.7714 | -3.4215 | -8.2358 | -10.1317 | 19.1467 | 18.0926 | 17.3498 | 16.5681 | 16.1232 | 15.3946 | 14.5385 | 13.5906 | 12.5691 | 11.5028 | 5.3967 | -0.42576 | -8.2105 | 15.5122 | 14.2959 | 13.3387 | 12.3112 | 11.7357 | 10.7704 | 9.5846 | 8.303 | 6.9908 | 5.6724 | -0.7878 | -4.9133 | -6.4562
|  | WATERLOOVILLE | CF |  |  |  | 15.6755 | 14.1377 | 13.4326 | 12.6204 | 12.202 | 11.4775 | 10.8173 | 10.0653 | 9.2632 | 8.4724 | 3.5642 | -2.198 | -7.1256 | 19.6987 | 18.3508 | 17.7804 | 17.1406 | 16.7793 | 16.1518 | 15.4916 | 14.7161 | 13.8732 | 12.9895 | 6.9314 | -2.8451 | -18.9349 | 16.1928 | 14.8112 | 14.2061 | 13.5081 | 13.1826 | 12.5591 | 11.9898 | 11.3336 | 10.6224 | 9.9193 | 5.4816 | 0.36016 | -3.949
COWLEY GSP | HIGH WYCOMBE BSP | WATLINGTON | MINIMUM HEADROOM | SU 69106 94287 | YES | 1.424 | -10.2796 | -10.4551 | -10.6224 | -10.8531 | -11.1 | -11.8918 | -12.3582 | -12.9265 | -14.4582 | -15.5959 | -18.1173 | -20.8714 | -24.0357 | -11.2138 | -11.3383 | -11.4587 | -11.7903 | -12.0189 | -12.923 | -13.4046 | -13.9658 | -15.7403 | -17.023 | -19.7515 | -23.3291 | -28.1995 | -11.3347 | -11.4959 | -11.6449 | -11.9704 | -12.2235 | -13.1551 | -13.6847 | -14.301 | -16.1133 | -17.4316 | -20.2908 | -23.5204 | -27.3643
|  | WATLINGTON | EE |  |  |  | -10.2796 | -10.4551 | -10.6224 | -10.8449 | -11.0255 | -11.4449 | -11.9571 | -11.9469 | -12.5531 | -12.9061 | -14.9714 | -18.7622 | -20.2776 | -11.2138 | -11.3383 | -11.4587 | -11.627 | -11.7801 | -12.2056 | -12.6821 | -12.6199 | -13.2066 | -13.5383 | -15.6352 | -20.4852 | -23.1974 | -11.3347 | -11.4959 | -11.6449 | -11.8449 | -12.0173 | -12.4582 | -13.0082 | -13.0071 | -13.6571 | -14.0327 | -16.2755 | -20.7929 | -22.5378
|  | WATLINGTON | HT |  |  |  | -10.1776 | -10.2959 | -10.5 | -10.7449 | -10.9133 | -11.5755 | -12.0684 | -12.6847 | -13.0673 | -13.7755 | -16.0653 | -19.7745 | -22.4 | -11.1281 | -11.2026 | -11.3638 | -11.5852 | -11.6883 | -12.4046 | -12.875 | -13.4617 | -13.7526 | -14.4434 | -16.5117 | -20.576 | -23.4954 | -11.2469 | -11.3612 | -11.5633 | -11.8286 | -11.9847 | -12.752 | -13.3061 | -13.9724 | -14.3408 | -15.1122 | -17.6765 | -22.0469 | -25.148
|  | WATLINGTON | HE |  |  |  | -10.1786 | -10.2939 | -10.5224 | -10.8531 | -11.1 | -11.8918 | -12.3582 | -12.9265 | -14.4582 | -15.5959 | -18.1173 | -20.8714 | -24.0357 | -11.1434 | -11.2291 | -11.4372 | -11.7903 | -12.0189 | -12.923 | -13.4046 | -13.9658 | -15.7403 | -17.023 | -19.7515 | -23.3291 | -28.1995 | -11.2469 | -11.3602 | -11.5929 | -11.9704 | -12.2235 | -13.1551 | -13.6847 | -14.301 | -16.1133 | -17.4316 | -20.2908 | -23.5204 | -27.3643
|  | WATLINGTON | CF |  |  |  | -10.1418 | -10.248 | -10.3367 | -10.4551 | -10.6061 | -10.8133 | -11.0653 | -11.3092 | -11.5112 | -11.8071 | -13.2469 | -15.1837 | -17.001 | -11.1219 | -11.2056 | -11.2821 | -11.3791 | -11.5372 | -11.7536 | -12.026 | -12.2832 | -12.5179 | -12.8444 | -14.7321 | -17.725 | -21.7301 | -11.2112 | -11.3102 | -11.3898 | -11.4969 | -11.6582 | -11.8724 | -12.1367 | -12.3857 | -12.6031 | -12.9122 | -14.5276 | -16.7051 | -18.7582
AMERSHAM | LOUDWATER BSP | WELL END | MINIMUM HEADROOM | SU 88511 87957 | YES | 1.19 | 9.0751 | 8.4649 | 7.8057 | 7.0924 | 6.7159 | 6.0618 | 5.2588 | 4.3618 | 3.5169 | 2.9465 | 0.088367 | -2.1422 | -3.1249 | 13.6955 | 13.2843 | 12.8537 | 12.3659 | 12.1945 | 11.7384 | 11.1996 | 10.5822 | 9.968 | 9.571 | 7.4465 | 4.7067 | -1.7178 | 10.5669 | 10.021 | 9.4353 | 8.7782 | 8.5118 | 7.9078 | 7.168 | 6.3312 | 5.5384 | 5.0292 | 2.5853 | 0.54041 | -0.35755
|  | WELL END | EE |  |  |  | 9.0751 | 8.4649 | 7.8057 | 7.0924 | 6.7159 | 6.0618 | 5.2588 | 4.3618 | 3.5169 | 2.9465 | 0.088367 | -1.78 | -2.7627 | 13.6955 | 13.2843 | 12.8537 | 12.3659 | 12.1945 | 11.7384 | 11.1996 | 10.5822 | 9.968 | 9.571 | 7.4465 | 5.2578 | 2.1139 | 10.5669 | 10.021 | 9.4353 | 8.7782 | 8.5118 | 7.9078 | 7.168 | 6.3312 | 5.5384 | 5.0292 | 2.5853 | 0.85469 | -0.03102
|  | WELL END | HT |  |  |  | 9.2476 | 8.7384 | 8.1271 | 7.5547 | 6.9414 | 6.3292 | 5.5557 | 5.1118 | 4.3649 | 3.6598 | 0.1098 | -2.1422 | -3.1249 | 13.8792 | 13.6006 | 13.2567 | 12.9445 | 12.5945 | 12.2312 | 11.7853 | 11.6629 | 11.2302 | 10.8057 | 8.8353 | 7.7751 | 7.3424 | 10.7241 | 10.2986 | 9.7812 | 9.2894 | 8.7476 | 8.1873 | 7.4792 | 7.1333 | 6.469 | 5.8353 | 2.6169 | 0.54041 | -0.35755
|  | WELL END | HE |  |  |  | 9.2465 | 8.7476 | 8.1506 | 7.5914 | 6.9965 | 6.3965 | 5.6976 | 5.3312 | 4.6629 | 4.0312 | 0.8598 | -1.1035 | -1.8392 | 13.8435 | 13.5333 | 13.1527 | 12.8016 | 12.4149 | 12.0006 | 11.5292 | 11.368 | 10.8843 | 10.4006 | 7.7945 | 5.4639 | 2.4353 | 10.721 | 10.3067 | 9.8006 | 9.321 | 8.7924 | 8.2394 | 7.5986 | 7.3271 | 6.7312 | 6.1424 | 3.2659 | 1.4384 | 0.76694
|  | WELL END | CF |  |  |  | 9.4139 | 9.1088 | 8.7404 | 8.3618 | 7.919 | 7.3955 | 6.9486 | 6.5027 | 6.47 | 6.1659 | 4.0006 | 1.6282 | -0.53714 | 13.9312 | 13.6914 | 13.4241 | 13.1363 | 12.8261 | 12.4424 | 12.0506 | 11.6271 | 11.5527 | 11.1843 | 8.572 | 4.7067 | -1.7178 | 10.868 | 10.62 | 10.3129 | 9.971 | 9.5935 | 9.1333 | 8.7282 | 8.3057 | 8.3384 | 8.0394 | 5.972 | 3.8843 | 2.0098
WILLESDEN GSP | ACTON LANE | WESLEY AVENUE | MINIMUM HEADROOM | TQ 20927 83082 | YES | 18.729 | 56.8035 | 54.759 | 52.9751 | 51.4722 | 50.4464 | 49.4258 | 48.4501 | 47.4458 | 46.4017 | 45.4933 | 45.1831 | 45.1066 | 45.0453 | 54.9153 | 52.8299 | 51.0093 | 49.4717 | 48.4051 | 47.3447 | 46.3445 | 45.3106 | 44.2246 | 43.3112 | 43.0959 | 43.0714 | 43.0765 | 56.2091 | 54.1463 | 52.344 | 50.8227 | 49.7766 | 48.7365 | 47.7465 | 46.7259 | 45.6583 | 44.7448 | 44.4836 | 44.4438 | 44.4367
|  | WESLEY AVENUE | EE |  |  |  | 56.8035 | 54.8386 | 53.0476 | 51.5324 | 50.5322 | 49.5136 | 48.5348 | 47.5417 | 46.5221 | 45.5015 | 45.1831 | 45.1066 | 45.0872 | 54.9153 | 52.9371 | 51.1103 | 49.5604 | 48.5225 | 47.4712 | 46.4741 | 45.4524 | 44.4042 | 43.3499 | 43.0959 | 43.0714 | 43.0765 | 56.2091 | 54.2381 | 52.4277 | 50.8941 | 49.8755 | 48.8386 | 47.8496 | 46.8381 | 45.8022 | 44.7622 | 44.4836 | 44.4438 | 44.4367
|  | WESLEY AVENUE | HT |  |  |  | 56.8178 | 54.759 | 52.9751 | 51.4722 | 50.4464 | 49.4258 | 48.4501 | 47.4458 | 46.4017 | 45.4933 | 45.3341 | 45.1923 | 45.1229 | 54.9265 | 52.8299 | 51.0093 | 49.4717 | 48.4051 | 47.3447 | 46.3445 | 45.3106 | 44.2246 | 43.3112 | 43.2163 | 43.1683 | 43.1469 | 56.2234 | 54.1463 | 52.344 | 50.8227 | 49.7766 | 48.7365 | 47.7465 | 46.7259 | 45.6583 | 44.7448 | 44.601 | 44.5326 | 44.4999
|  | WESLEY AVENUE | HE |  |  |  | 56.8178 | 54.86 | 53.0741 | 51.5712 | 50.5781 | 49.5748 | 48.6083 | 47.6223 | 46.6109 | 45.5882 | 45.2372 | 45.1147 | 45.0453 | 54.9255 | 52.9544 | 51.1318 | 49.589 | 48.5612 | 47.5222 | 46.5333 | 45.5228 | 44.4818 | 43.4265 | 43.1571 | 43.1408 | 43.1295 | 56.2234 | 54.2585 | 52.4542 | 50.9309 | 49.9204 | 48.8978 | 47.919 | 46.9198 | 45.891 | 44.8489 | 44.5448 | 44.5061 | 44.4826
|  | WESLEY AVENUE | CF |  |  |  | 56.8301 | 54.8784 | 53.2037 | 51.7079 | 50.7271 | 49.7626 | 48.8317 | 47.8866 | 46.9231 | 45.9504 | 45.4678 | 45.3229 | 45.1535 | 54.9357 | 52.9697 | 51.2797 | 49.7431 | 48.7214 | 47.7253 | 46.769 | 45.7973 | 44.8042 | 43.802 | 43.2765 | 43.2071 | 43.1571 | 56.2347 | 54.2769 | 52.594 | 51.0798 | 50.0786 | 49.0978 | 48.1537 | 47.1953 | 46.2165 | 45.2285 | 44.7112 | 44.6081 | 44.5326
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | WEST END | MINIMUM HEADROOM | SU 57216 06147 | YES | 6.97 | 11.6653 | 11.3193 | 10.8887 | 10.4142 | 10.2877 | 9.8224 | 8.7663 | 7.5622 | 6.2663 | 5.351 | 1.1112 | -2.1031 | -3.9582 | 11.8398 | 11.5347 | 11.1255 | 10.6693 | 10.5704 | 10.1112 | 9.3908 | 8.5398 | 7.6285 | 7.0091 | 3.953 | -0.076571 | -9.7307 | 11.1622 | 10.7877 | 10.2959 | 9.7459 | 9.7469 | 9.2347 | 8.2765 | 7.1581 | 5.9724 | 5.2336 | 1.8969 | -0.84188 | -2.4102
|  | WEST END | EE |  |  |  | 11.6653 | 11.3193 | 10.8887 | 10.4142 | 10.2877 | 9.8224 | 8.7663 | 7.5622 | 6.2663 | 5.351 | 1.3438 | -1.4837 | -3.6909 | 11.8398 | 11.5347 | 11.1255 | 10.6693 | 10.5704 | 10.1112 | 9.3908 | 8.5398 | 7.6285 | 7.0091 | 3.953 | 0.72955 | -4.3041 | 11.1622 | 10.7877 | 10.2959 | 9.7459 | 9.7469 | 9.2347 | 8.2765 | 7.1581 | 5.9724 | 5.2336 | 1.9928 | -0.31841 | -2.2113
|  | WEST END | HT |  |  |  | 11.8561 | 11.5612 | 11.2132 | 10.8877 | 10.4959 | 10.0642 | 9.201 | 8.0102 | 6.9296 | 5.9173 | 1.1112 | -2.1031 | -3.9582 | 12.0857 | 11.8877 | 11.6255 | 11.4 | 11.0969 | 10.7571 | 10.5 | 9.8591 | 9.2551 | 8.6632 | 6.0591 | 4.6204 | 3.8765 | 11.4275 | 11.1428 | 10.7826 | 10.453 | 10.0377 | 9.5744 | 9.0714 | 8.0571 | 7.1102 | 6.1989 | 1.8969 | -0.84188 | -2.4102
|  | WEST END | HE |  |  |  | 11.8561 | 11.5877 | 11.2602 | 10.9602 | 10.5969 | 10.1989 | 9.6265 | 8.6438 | 7.5744 | 6.6683 | 2.6132 | -0.21127 | -1.5602 | 12.0459 | 11.8153 | 11.5163 | 11.2387 | 10.8898 | 10.4979 | 10.2296 | 9.5724 | 8.8428 | 8.1653 | 4.6928 | 1.3979 | -3.3256 | 11.4204 | 11.1571 | 10.8153 | 10.5091 | 10.1214 | 9.6877 | 9.404 | 8.5602 | 7.6398 | 6.8265 | 3.2234 | 0.88159 | -0.298
|  | WEST END | CF |  |  |  | 12.0071 | 11.8408 | 11.6806 | 11.5183 | 11.3132 | 11.0877 | 10.8296 | 10.7867 | 10.4132 | 9.9989 | 6.3877 | 3.6826 | 1.1367 | 12.1173 | 11.9153 | 11.7061 | 11.4857 | 11.204 | 10.8714 | 10.4816 | 10.3204 | 9.8428 | 9.3153 | 5.3061 | -0.076571 | -9.7307 | 11.5469 | 11.352 | 11.1683 | 10.9836 | 10.7367 | 10.4653 | 10.1612 | 10.2489 | 9.8693 | 9.452 | 6.2081 | 4.0387 | 1.9336
MELKSHAM GSP | WEST GRAFTON | WEST GRAFTON VILLAGE | MINIMUM HEADROOM | SU 24639 60279 | YES | 0.894 | 4.3255 | 4.148 | 3.9939 | 3.7888 | 3.6184 | 3.3908 | 3.1031 | 2.7571 | 2.4092 | 2.8316 | 1.9551 | 1.652 | 1.349 | 5.9066 | 5.7709 | 5.6587 | 5.5138 | 5.3964 | 5.2281 | 5.024 | 4.774 | 4.523 | 4.7689 | 4.0321 | 3.1434 | 1.0587 | 5.048 | 4.8694 | 4.7194 | 4.5184 | 4.3531 | 4.1265 | 3.8459 | 3.5061 | 3.1643 | 3.6827 | 2.9245 | 2.6673 | 2.4235
|  | WEST GRAFTON VILLAGE | EE |  |  |  | 4.3255 | 4.148 | 3.9939 | 3.7888 | 3.6184 | 3.3908 | 3.1031 | 2.7571 | 2.4092 | 2.8316 | 1.9551 | 1.652 | 1.4857 | 5.9066 | 5.7709 | 5.6587 | 5.5138 | 5.3964 | 5.2281 | 5.024 | 4.774 | 4.523 | 4.7689 | 4.1036 | 3.4862 | 2.5005 | 5.048 | 4.8694 | 4.7194 | 4.5184 | 4.3531 | 4.1265 | 3.8459 | 3.5061 | 3.1643 | 3.6827 | 2.9245 | 2.6673 | 2.5378
|  | WEST GRAFTON VILLAGE | HT |  |  |  | 4.4122 | 4.2704 | 4.1602 | 4.0224 | 3.9112 | 3.7633 | 3.5633 | 3.3786 | 3.1541 | 2.8786 | 2.1296 | 1.6684 | 1.349 | 5.9791 | 5.8811 | 5.8148 | 5.7179 | 5.6495 | 5.5403 | 5.4036 | 5.2985 | 5.1372 | 4.9597 | 4.6179 | 4.3689 | 4.2117 | 5.152 | 5.0265 | 4.9306 | 4.799 | 4.699 | 4.5449 | 4.351 | 4.1929 | 3.9602 | 3.7102 | 3.0857 | 2.6857 | 2.4235
|  | WEST GRAFTON VILLAGE | HE |  |  |  | 4.4173 | 4.2694 | 4.1612 | 4.0265 | 3.9204 | 3.7786 | 3.5857 | 3.4082 | 3.1929 | 2.9306 | 2.0837 | 1.7735 | 1.6276 | 5.975 | 5.8638 | 5.7852 | 5.6842 | 5.6066 | 5.4893 | 5.3485 | 5.2179 | 5.0434 | 4.8505 | 4.2117 | 3.575 | 2.6107 | 5.1622 | 5.0255 | 4.9316 | 4.799 | 4.7041 | 4.5531 | 4.3663 | 4.2051 | 3.9755 | 3.7286 | 3.052 | 2.7888 | 2.6765
|  | WEST GRAFTON VILLAGE | CF |  |  |  | 4.4306 | 4.3122 | 4.2224 | 4.1194 | 4.0041 | 3.9133 | 3.7837 | 3.6367 | 3.4704 | 3.3582 | 2.3939 | 2.2449 | 1.7592 | 5.9862 | 5.8944 | 5.8219 | 5.7413 | 5.6444 | 5.5648 | 5.4434 | 5.3066 | 5.1566 | 5.0393 | 4.0321 | 3.1434 | 1.0587 | 5.1816 | 5.0837 | 5.0031 | 4.9071 | 4.798 | 4.7163 | 4.598 | 4.4633 | 4.3061 | 4.1949 | 3.2704 | 3.1939 | 2.7765
AXMINSTER | YEOVIL BSP | WEST HENDFORD | MINIMUM HEADROOM | ST 55000 15442 | YES | 4.54 | 37.1747 | 36.8308 | 36.4033 | 35.94 | 35.3757 | 34.739 | 34.1482 | 33.3369 | 32.5502 | 31.8655 | 29.0635 | 27.4992 | 26.7206 | 36.7553 | 36.5451 | 36.2777 | 35.9982 | 35.6543 | 35.2696 | 34.8941 | 34.3288 | 33.7522 | 33.2492 | 31.1971 | 29.0788 | 23.2012 | 34.8941 | 34.6124 | 34.2604 | 33.8879 | 33.4288 | 32.9124 | 32.4145 | 31.6553 | 30.9175 | 30.2808 | 27.6226 | 26.1941 | 25.6226
|  | WEST HENDFORD | EE |  |  |  | 37.1747 | 36.8308 | 36.4033 | 35.94 | 35.3757 | 34.739 | 34.1482 | 33.3369 | 32.5502 | 31.8655 | 29.6614 | 28.1992 | 27.0747 | 36.7553 | 36.5451 | 36.2777 | 35.9982 | 35.6543 | 35.2696 | 34.8941 | 34.3288 | 33.7522 | 33.2492 | 31.643 | 29.6971 | 26.7012 | 34.8941 | 34.6124 | 34.2604 | 33.8879 | 33.4288 | 32.9124 | 32.4145 | 31.6553 | 30.9175 | 30.2808 | 28.3492 | 27.4216 | 26.4461
|  | WEST HENDFORD | HT |  |  |  | 37.4002 | 37.1369 | 36.8043 | 36.4563 | 36.0165 | 35.5084 | 34.9084 | 34.0941 | 33.2522 | 32.7186 | 29.7879 | 27.9094 | 26.8992 | 36.9155 | 36.7665 | 36.5716 | 36.3726 | 36.1206 | 35.841 | 35.5165 | 35.0737 | 34.5522 | 34.1369 | 32.0941 | 31.14 | 30.6696 | 35.091 | 34.8777 | 34.6053 | 34.3277 | 33.9777 | 33.5808 | 33.1216 | 32.541 | 31.8818 | 31.3359 | 28.7267 | 27.1808 | 26.3114
|  | WEST HENDFORD | HE |  |  |  | 37.3573 | 37.0696 | 36.7043 | 36.3206 | 35.8359 | 35.2726 | 34.6328 | 33.8686 | 33.0675 | 32.3573 | 29.0635 | 27.4992 | 26.7206 | 36.8839 | 36.7114 | 36.492 | 36.2645 | 35.9726 | 35.6482 | 35.2665 | 34.741 | 34.1584 | 33.6533 | 31.1971 | 29.7451 | 26.9237 | 35.0533 | 34.8196 | 34.5226 | 34.2145 | 33.8216 | 33.3798 | 32.8675 | 32.1635 | 31.4114 | 30.7533 | 27.6226 | 26.1941 | 25.6226
|  | WEST HENDFORD | CF |  |  |  | 37.5726 | 37.4482 | 37.2543 | 37.0584 | 36.7879 | 36.443 | 36.0522 | 35.5604 | 35.0277 | 34.4645 | 31.9971 | 29.7012 | 27.9665 | 37.0104 | 36.9328 | 36.8073 | 36.6788 | 36.5073 | 36.2941 | 36.0584 | 35.7288 | 35.2584 | 34.7584 | 32.5941 | 29.0788 | 23.2012 | 35.2267 | 35.1247 | 34.9614 | 34.7992 | 34.5747 | 34.291 | 33.9767 | 33.5696 | 33.1328 | 32.6696 | 30.3828 | 28.2043 | 26.5808
MANNINGTON GSP | SHAFTESBURY BSP | WEST STOUR | MINIMUM HEADROOM | ST 77699 22040 | YES | 0.118 | 4.8276 | 4.6286 | 4.4796 | 4.2847 | 3.9714 | 3.6704 | 3.4041 | 3.0939 | 3.1837 | 3.0265 | 2.1816 | 1.8143 | 1.5102 | 6.2597 | 6.1291 | 6.025 | 5.8832 | 5.6913 | 5.4923 | 5.2903 | 5.0485 | 5.173 | 5.0679 | 4.4668 | 3.8189 | 2.1913 | 5.2306 | 5.0418 | 4.8949 | 4.699 | 4.4092 | 4.1204 | 3.851 | 3.5337 | 3.7041 | 3.5439 | 2.8469 | 2.5316 | 2.2724
|  | WEST STOUR | EE |  |  |  | 4.8276 | 4.6286 | 4.4796 | 4.2847 | 3.9714 | 3.6704 | 3.4041 | 3.0939 | 3.1837 | 3.0265 | 2.1816 | 1.8143 | 1.6173 | 6.2597 | 6.1291 | 6.025 | 5.8832 | 5.6913 | 5.4923 | 5.2903 | 5.0485 | 5.173 | 5.0679 | 4.5066 | 4.0015 | 3.2301 | 5.2306 | 5.0418 | 4.8949 | 4.699 | 4.4092 | 4.1204 | 3.851 | 3.5337 | 3.7041 | 3.5653 | 2.8469 | 2.5316 | 2.3643
|  | WEST STOUR | HT |  |  |  | 4.9102 | 4.7571 | 4.6214 | 4.4735 | 4.1888 | 3.9224 | 3.7122 | 3.5184 | 3.2755 | 3.0276 | 2.3112 | 1.8306 | 1.5102 | 6.3301 | 6.2454 | 6.1587 | 6.0658 | 5.9168 | 5.7699 | 5.6393 | 5.526 | 5.3699 | 5.2036 | 4.8923 | 4.6648 | 4.5189 | 5.3204 | 5.1816 | 5.05 | 4.9031 | 4.6592 | 4.4204 | 4.2143 | 4.0347 | 3.7959 | 3.5439 | 2.9561 | 2.5429 | 2.2724
|  | WEST STOUR | HE |  |  |  | 4.9082 | 4.7582 | 4.6265 | 4.4796 | 4.201 | 3.9439 | 3.7459 | 3.5653 | 3.3378 | 3.1051 | 2.3071 | 1.9265 | 1.7694 | 6.3219 | 6.2291 | 6.1383 | 6.0332 | 5.8791 | 5.7219 | 5.5832 | 5.4587 | 5.2903 | 5.1107 | 4.5832 | 4.0668 | 3.3189 | 5.3173 | 5.1816 | 5.0551 | 4.9102 | 4.6724 | 4.4408 | 4.2449 | 4.0776 | 3.849 | 3.6102 | 2.9643 | 2.652 | 2.5235
|  | WEST STOUR | CF |  |  |  | 4.9286 | 4.7918 | 4.702 | 4.5918 | 4.3306 | 4.1469 | 4.0296 | 3.8878 | 3.7755 | 3.6265 | 2.7551 | 2.5153 | 1.9867 | 6.3332 | 6.2444 | 6.1811 | 6.0974 | 5.9342 | 5.824 | 5.7209 | 5.5883 | 5.4903 | 5.3536 | 4.4668 | 3.8189 | 2.1913 | 5.3378 | 5.2102 | 5.1224 | 5.0184 | 4.7827 | 4.6296 | 4.5082 | 4.3592 | 4.2531 | 4.0959 | 3.2 | 3.1337 | 2.6847
MANNINGTON GSP | BOURNEMOUTH | WESTBOURNE | MINIMUM HEADROOM | SZ 07642 91485 | YES | 1.73 | 12.915 | 12.3956 | 11.6721 | 10.917 | 10.0354 | 9.066 | 7.9742 | 6.6864 | 5.5221 | 4.5731 | 1.1129 | -1.6371 | -2.1575 | 16.7129 | 16.264 | 15.6701 | 15.0384 | 14.2925 | 13.464 | 12.5813 | 11.518 | 10.4864 | 9.6078 | 5.3089 | -1.2411 | -16.8728 | 13.3415 | 12.8578 | 12.1803 | 11.4578 | 10.6129 | 9.6895 | 8.665 | 7.4436 | 6.3231 | 5.418 | 2.1854 | -0.26053 | -0.6789
|  | WESTBOURNE | EE |  |  |  | 12.915 | 12.3956 | 11.6721 | 10.917 | 10.0354 | 9.066 | 7.9742 | 6.6864 | 5.5221 | 4.5731 | 1.1129 | -0.54931 | -1.235 | 16.7129 | 16.264 | 15.6701 | 15.0384 | 14.2925 | 13.464 | 12.5813 | 11.518 | 10.4864 | 9.6078 | 5.3089 | 0.7762 | -6.8942 | 13.3415 | 12.8578 | 12.1803 | 11.4578 | 10.6129 | 9.6895 | 8.665 | 7.4436 | 6.3231 | 5.418 | 2.1854 | 0.74967 | 0.082327
|  | WESTBOURNE | HT |  |  |  | 13.2262 | 12.7476 | 12.1527 | 11.5997 | 10.964 | 10.2364 | 9.3976 | 8.4119 | 7.4833 | 6.5517 | 1.5364 | -1.6371 | -2.1575 | 17.0272 | 16.7129 | 16.3384 | 15.965 | 15.5313 | 15.0313 | 14.5038 | 13.8476 | 13.1966 | 12.5456 | 9.1987 | 7.1884 | 6.8568 | 13.6425 | 13.2221 | 12.6966 | 12.1793 | 11.5782 | 10.8915 | 10.1221 | 9.1956 | 8.3017 | 7.4099 | 2.668 | -0.26053 | -0.6789
|  | WESTBOURNE | HE |  |  |  | 13.1997 | 12.8252 | 12.3048 | 11.7599 | 11.1752 | 10.5333 | 9.8262 | 9.0048 | 8.2731 | 7.5446 | 4.2854 | 2.6507 | 2.3609 | 16.9323 | 16.6048 | 16.1823 | 15.7282 | 15.2262 | 14.6578 | 14.064 | 13.3507 | 12.6354 | 11.9099 | 7.5701 | 2.8609 | -4.4279 | 13.615 | 13.2854 | 12.8221 | 12.3231 | 11.7833 | 11.1813 | 10.5384 | 9.7711 | 9.066 | 8.3721 | 5.266 | 3.8211 | 3.5946
|  | WESTBOURNE | CF |  |  |  | 13.3395 | 13.1691 | 12.8864 | 12.5721 | 12.1976 | 11.7721 | 11.367 | 10.8987 | 10.4466 | 9.9884 | 7.4089 | 4.7721 | 2.3731 | 17.0191 | 16.7823 | 16.4558 | 16.0997 | 15.6691 | 15.1487 | 14.5721 | 13.917 | 13.2344 | 12.5038 | 7.4762 | -1.2411 | -16.8728 | 13.7425 | 13.5823 | 13.3252 | 13.0425 | 12.6956 | 12.3099 | 11.9384 | 11.5058 | 11.0782 | 10.6405 | 8.1354 | 5.6507 | 3.4701
MELKSHAM GSP | FROME BSP | WESTBURY | MINIMUM HEADROOM | ST 87654 51530 | YES | 2.91 | 12.5918 | 12.0684 | 11.2673 | 10.6347 | 9.848 | 8.9143 | 7.6663 | 6.3102 | 5.0888 | 4.3306 | 0.25714 | -3.098 | -5.0561 | 15.7306 | 15.3592 | 14.7327 | 14.2602 | 13.7041 | 13.05 | 12.2235 | 11.3102 | 10.4439 | 9.9 | 7.0163 | 3.6592 | -4.8082 | 12.3694 | 11.8816 | 11.1245 | 10.5571 | 9.8337 | 8.9786 | 7.8357 | 6.5888 | 5.45 | 4.7459 | 1.2776 | -1.6143 | -3.2735
|  | WESTBURY | EE |  |  |  | 12.5918 | 12.0684 | 11.2673 | 10.6347 | 9.848 | 8.9143 | 7.6663 | 6.3102 | 5.0888 | 4.3306 | 0.31633 | -2.5235 | -4.6653 | 15.7306 | 15.3592 | 14.7327 | 14.2602 | 13.7041 | 13.05 | 12.2235 | 11.3102 | 10.4439 | 9.9 | 7.0163 | 4.0704 | -0.30204 | 12.3694 | 11.8816 | 11.1245 | 10.5571 | 9.8337 | 8.9786 | 7.8357 | 6.5888 | 5.45 | 4.7459 | 1.2806 | -1.1143 | -2.9551
|  | WESTBURY | HT |  |  |  | 12.8755 | 12.449 | 11.8102 | 10.7612 | 9.9684 | 9.399 | 8.2939 | 7.2653 | 6.3071 | 5.3235 | 0.25714 | -3.098 | -5.0561 | 16.002 | 15.751 | 15.3133 | 14.6031 | 14.1357 | 13.9092 | 13.3112 | 12.7122 | 12.1296 | 11.5398 | 8.7714 | 7.252 | 6.4571 | 12.6541 | 12.2633 | 11.6745 | 10.7194 | 10.0051 | 9.5796 | 8.6071 | 7.6612 | 6.7571 | 5.8439 | 1.2776 | -1.6143 | -3.2735
|  | WESTBURY | HE |  |  |  | 12.8673 | 12.4592 | 11.8673 | 10.9541 | 10.248 | 9.7735 | 8.7755 | 7.7224 | 6.7959 | 5.9357 | 1.3571 | -1.6388 | -3.0551 | 15.9561 | 15.6724 | 15.2153 | 14.5153 | 14.0296 | 13.7776 | 13.1388 | 12.4398 | 11.7694 | 11.1173 | 7.5469 | 4.4143 | 0.30612 | 12.6439 | 12.2694 | 11.7204 | 10.8724 | 10.2337 | 9.8745 | 8.9908 | 8.0378 | 7.1796 | 6.3673 | 2.2245 | -0.33878 | -1.5327
|  | WESTBURY | CF |  |  |  | 13.0367 | 12.7571 | 12.3102 | 11.7633 | 11.4459 | 11 | 10.9898 | 10.5214 | 9.9388 | 9.3337 | 5.601 | 2.4561 | -0.46224 | 16.048 | 15.8224 | 15.4184 | 14.9122 | 14.6082 | 14.1684 | 14.0541 | 13.5857 | 13.0429 | 12.4694 | 8.6806 | 3.6592 | -4.8082 | 12.802 | 12.5469 | 12.1235 | 11.602 | 11.299 | 10.8724 | 10.8837 | 10.451 | 9.9204 | 9.3653 | 5.9357 | 3.1265 | 0.67347
NURSLING GSP | SOUTHAMPTON (2 X 90) | WESTERN ESPLANADE | MINIMUM HEADROOM | SU 41618 12009 | YES | 7.441 | 27.1966 | 26.2578 | 24.9303 | 23.6772 | 22.3987 | 20.0466 | 18.4017 | 16.8109 | 15.0568 | 13.7905 | 10.166 | 7.5517 | 5.814 | 29.9548 | 29.4191 | 28.6864 | 27.9854 | 27.2538 | 25.6834 | 24.5232 | 23.0997 | 21.5232 | 20.2701 | 15.7078 | 11.0415 | 0.25274 | 26.8242 | 26.1527 | 25.0436 | 23.9548 | 22.817 | 20.7456 | 19.2823 | 17.8099 | 16.014 | 14.817 | 11.4517 | 9.2578 | 7.8487
|  | WESTERN ESPLANADE | EE |  |  |  | 27.1966 | 26.2578 | 24.9303 | 23.6772 | 22.3987 | 20.4936 | 19.0895 | 17.0262 | 15.0915 | 13.8405 | 10.166 | 8.1436 | 6.0364 | 29.9548 | 29.4191 | 28.6864 | 27.9854 | 27.2538 | 25.8354 | 24.664 | 23.0997 | 21.5232 | 20.2701 | 15.7078 | 12.317 | 6.5201 | 26.8242 | 26.1527 | 25.0436 | 23.9548 | 22.817 | 21.065 | 19.715 | 17.8099 | 16.014 | 14.817 | 11.4517 | 9.768 | 7.965
|  | WESTERN ESPLANADE | HT |  |  |  | 27.4068 | 26.5589 | 25.3405 | 24.2242 | 22.5119 | 20.0466 | 18.4017 | 16.8109 | 15.0568 | 13.7905 | 10.5476 | 7.5517 | 5.814 | 30.1425 | 29.7272 | 29.1385 | 28.6007 | 27.3456 | 25.6834 | 24.5232 | 23.3109 | 21.8885 | 20.8007 | 18.4772 | 16.9905 | 16.1864 | 26.967 | 26.4589 | 25.4609 | 24.517 | 22.9507 | 20.7456 | 19.2823 | 17.8609 | 16.2854 | 15.1313 | 11.9956 | 9.2578 | 7.8487
|  | WESTERN ESPLANADE | HE |  |  |  | 27.3803 | 26.5497 | 25.3507 | 24.264 | 23.2027 | 21.4752 | 20.3109 | 18.7109 | 17.1211 | 16.0242 | 11.7374 | 9.9283 | 8.9589 | 30.0772 | 29.6089 | 28.9548 | 28.3599 | 27.7589 | 26.4517 | 25.4272 | 24.116 | 22.7385 | 21.5609 | 16.5527 | 13.2783 | 8.164 | 26.9538 | 26.4456 | 25.4609 | 24.5395 | 23.6232 | 22.0497 | 20.9823 | 19.5385 | 18.115 | 17.0721 | 13.1578 | 11.6344 | 10.815
|  | WESTERN ESPLANADE | CF |  |  |  | 28.3099 | 28.1078 | 27.4313 | 26.6272 | 25.6803 | 24.5048 | 23.3905 | 22.2221 | 20.7507 | 19.4987 | 14.4425 | 12.3946 | 10.7129 | 30.5466 | 30.3578 | 29.916 | 29.4089 | 28.8221 | 28.0915 | 27.1507 | 26.0527 | 24.7527 | 23.5354 | 16.7762 | 11.0415 | 0.25274 | 27.4742 | 27.3721 | 27.017 | 26.4629 | 25.6783 | 24.7017 | 23.7497 | 22.7038 | 21.4099 | 20.3007 | 15.5936 | 13.6905 | 12.1589
BOTLEY WOOD GSP | NETLEY COMMON BSP | WESTON | MINIMUM HEADROOM | SU 45207 09912 | YES | 1.177 | 15.1286 | 14.701 | 14.1388 | 13.9133 | 13.3276 | 12.6694 | 11.6622 | 10.5449 | 9.4296 | 8.6276 | 4.152 | 0.35816 | -1.6714 | 16.8724 | 16.5571 | 16.1622 | 15.952 | 15.5133 | 14.9622 | 14.1765 | 13.2857 | 12.3765 | 11.6929 | 7.5929 | 0.41633 | -15.2276 | 15.3449 | 14.9194 | 14.3551 | 14.2173 | 13.649 | 13.0112 | 12.0806 | 11.0316 | 9.9786 | 9.2561 | 5.3561 | 1.9878 | 0.25102
|  | WESTON | EE |  |  |  | 15.1286 | 14.701 | 14.1388 | 13.9133 | 13.3276 | 12.6694 | 11.6622 | 10.5449 | 9.4296 | 8.6276 | 4.3541 | 1.1704 | -1.349 | 16.8724 | 16.5571 | 16.1622 | 15.952 | 15.5133 | 14.9622 | 14.1765 | 13.2857 | 12.3765 | 11.6929 | 7.5929 | 2.5714 | -5.7173 | 15.3449 | 14.9194 | 14.3551 | 14.2173 | 13.649 | 13.0112 | 12.0806 | 11.0316 | 9.9786 | 9.2561 | 5.4847 | 2.7112 | 0.52551
|  | WESTON | HT |  |  |  | 15.3592 | 15.0286 | 14.6245 | 14.2112 | 13.702 | 13.151 | 12.6398 | 11.7265 | 10.7724 | 9.7735 | 4.152 | 0.35816 | -1.6714 | 17.0878 | 16.9041 | 16.6745 | 16.448 | 16.1582 | 15.851 | 15.6367 | 15.1735 | 14.6653 | 14.0582 | 10.9806 | 9.1765 | 8.3122 | 15.6265 | 15.3143 | 14.9061 | 14.5194 | 14.0153 | 13.4745 | 13.1031 | 12.2592 | 11.3776 | 10.4531 | 5.3561 | 1.9878 | 0.25102
|  | WESTON | HE |  |  |  | 15.3582 | 15.0541 | 14.6796 | 14.3112 | 13.8724 | 13.3541 | 12.9745 | 12.2265 | 11.4418 | 10.6398 | 6.2418 | 3.1286 | 1.7296 | 17.0163 | 16.7684 | 16.4694 | 16.1663 | 15.7898 | 15.3643 | 15.0408 | 14.4724 | 13.8643 | 13.2092 | 8.7531 | 3.5969 | -4.1755 | 15.6224 | 15.3347 | 14.9582 | 14.6112 | 14.1704 | 13.6673 | 13.4184 | 12.7214 | 11.9969 | 11.2429 | 7.248 | 4.5173 | 3.3612
|  | WESTON | CF |  |  |  | 15.5276 | 15.3337 | 15.1449 | 14.9102 | 14.701 | 14.4163 | 14.0969 | 14.0837 | 13.7408 | 13.3755 | 10.55 | 7.5439 | 4.648 | 17.0867 | 16.8602 | 16.6276 | 16.3469 | 16.0561 | 15.6653 | 15.1857 | 14.85 | 14.3061 | 13.7184 | 8.9918 | 0.41633 | -15.2276 | 15.7816 | 15.5755 | 15.3745 | 15.1173 | 14.9071 | 14.6153 | 14.2878 | 14.3531 | 14.0133 | 13.6531 | 11.0122 | 8.3357 | 5.8276
CHICKERELL GSP | CHICKERELL BSP | WEYMOUTH | MINIMUM HEADROOM | SY 67443 79096 | YES | 5.158 | 12.1853 | 11.1526 | 9.8434 | 8.1261 | 6.2138 | 4.2577 | 2.0506 | -0.35964 | -2.6127 | -4.33 | -11.2637 | -15.5923 | -16.726 | 16.5863 | 15.7751 | 14.9424 | 13.7495 | 12.3955 | 10.97 | 9.42 | 7.6557 | 5.9444 | 4.671 | -1.2066 | -7.9494 | -25.5688 | 12.3342 | 11.3291 | 10.1893 | 8.6087 | 6.8322 | 4.9812 | 2.924 | 0.66485 | -1.4658 | -3.0709 | -9.4311 | -13.2382 | -14.1627
|  | WEYMOUTH | EE |  |  |  | 12.1853 | 11.1526 | 9.8434 | 8.1261 | 6.2138 | 4.2577 | 2.0506 | -0.35964 | -2.6127 | -4.33 | -11.2637 | -14.8749 | -15.6484 | 16.5863 | 15.7751 | 14.9424 | 13.7495 | 12.3955 | 10.97 | 9.42 | 7.6557 | 5.9444 | 4.671 | -1.2066 | -6.6535 | -14.4566 | 12.3342 | 11.3291 | 10.1893 | 8.6087 | 6.8322 | 4.9812 | 2.924 | 0.66485 | -1.4658 | -3.0709 | -9.4311 | -12.5933 | -13.2647
|  | WEYMOUTH | HT |  |  |  | 12.7302 | 11.9098 | 10.5495 | 9.0424 | 7.7189 | 6.0934 | 4.3291 | 2.5006 | 0.73016 | -1.0719 | -10.2158 | -15.5923 | -16.726 | 17.0975 | 16.5955 | 15.821 | 14.9353 | 14.2863 | 13.3251 | 12.3016 | 11.1628 | 10.0108 | 8.8118 | 3.2159 | 0.26996 | -0.3627 | 12.9353 | 12.172 | 10.9853 | 9.6465 | 8.5261 | 7.0475 | 5.4271 | 3.6965 | 1.9842 | 0.22404 | -8.3596 | -13.2382 | -14.1627
|  | WEYMOUTH | HE |  |  |  | 12.6577 | 11.8404 | 10.4771 | 8.9628 | 7.6251 | 5.9802 | 4.2995 | 2.5281 | 0.81689 | -0.928 | -8.9056 | -13.2311 | -14.28 | 16.9567 | 16.3649 | 15.4802 | 14.4955 | 13.6649 | 12.5638 | 11.42 | 10.1414 | 8.7975 | 7.3863 | 0.064853 | -6.1117 | -13.9576 | 12.8546 | 12.0934 | 10.9046 | 9.5618 | 8.4302 | 6.9393 | 5.3924 | 3.7108 | 2.0536 | 0.35261 | -7.2341 | -11.0923 | -11.9229
|  | WEYMOUTH | CF |  |  |  | 13.0322 | 12.5434 | 11.5669 | 10.4965 | 9.3087 | 8.4771 | 7.6842 | 6.8434 | 6.0587 | 5.2598 | -0.45249 | -6.776 | -12.2413 | 17.1638 | 16.7414 | 16.0383 | 15.271 | 14.4006 | 13.7363 | 12.92 | 11.9965 | 11.0587 | 10.0495 | 2.8261 | -7.9494 | -25.5688 | 13.2046 | 12.7618 | 11.9271 | 10.9955 | 9.9577 | 9.2679 | 8.5291 | 7.7036 | 6.9016 | 6.0751 | 0.52812 | -5.2954 | -10.1923
COWLEY GSP | HEADINGTON BSP | WHEATLEY | MINIMUM HEADROOM | SP 60777 05379 | YES | 17.968 | 5.6903 | 28.9347 | 14.5535 | 13.6433 | 12.628 | 10.2096 | 8.3024 | 6.2861 | 1.979 | -1.0588 | -9.7812 | -17.1812 | -24.669 | 6.7459 | 28.7296 | 14.4606 | 13.4371 | 12.5718 | 10.0331 | 8.3851 | 6.6667 | 2.0331 | -1.1557 | -9.5751 | -18.5016 | -31.2833 | 5.3184 | 27.9531 | 13.5892 | 12.5198 | 11.5086 | 8.7739 | 6.782 | 4.7555 | -0.19143 | -3.8159 | -13.2833 | -21.9067 | -31.1384
|  | WHEATLEY | EE |  |  |  | 5.6903 | 28.9347 | 14.5535 | 13.9055 | 13.0198 | 11.628 | 10.1392 | 8.7708 | 6.7882 | 5.4973 | 0.51367 | -8.5496 | -12.1894 | 6.7459 | 28.7296 | 14.4606 | 13.9943 | 13.3024 | 12.0024 | 10.8943 | 10.031 | 8.3178 | 7.2473 | 1.8565 | -10.3322 | -17.8241 | 5.3184 | 27.9531 | 13.5892 | 12.9739 | 12.1494 | 10.6555 | 9.1953 | 7.9831 | 5.9708 | 4.6208 | -0.93224 | -11.4404 | -15.6618
|  | WHEATLEY | HT |  |  |  | 6.073 | 29.4643 | 15.1167 | 14.382 | 13.6708 | 11.4616 | 9.4718 | 7.4616 | 6.0943 | 4.4524 | -1.8322 | -10.7741 | -17.068 | 6.9878 | 29.0857 | 14.7933 | 14.128 | 13.6229 | 11.6208 | 10.1065 | 8.4769 | 7.6127 | 6.1841 | -0.047551 | -10.1098 | -17.3343 | 5.6255 | 28.4163 | 14.0535 | 13.2402 | 12.4565 | 10.1167 | 8.1657 | 6.1402 | 4.8984 | 3.1627 | -3.6608 | -14.2435 | -21.7537
|  | WHEATLEY | HE |  |  |  | 5.9403 | 29.2541 | 14.7484 | 13.6433 | 12.628 | 10.2096 | 8.3024 | 6.2861 | 1.979 | -1.0588 | -9.7812 | -17.1812 | -24.669 | 6.9031 | 28.9388 | 14.5106 | 13.4371 | 12.5718 | 10.0331 | 8.3851 | 6.6667 | 2.0331 | -1.1557 | -9.5751 | -18.5016 | -31.2833 | 5.5643 | 28.2612 | 13.7208 | 12.5198 | 11.5086 | 8.7739 | 6.782 | 4.7555 | -0.19143 | -3.8159 | -13.2833 | -21.9067 | -31.1384
|  | WHEATLEY | CF |  |  |  | 6.1811 | 29.6327 | 15.4984 | 15.1341 | 14.43 | 13.4198 | 12.2045 | 11.1024 | 10.0045 | 8.9504 | 4.3422 | -1.5884 | -6.1935 | 6.999 | 29.0837 | 14.9545 | 14.6392 | 13.9453 | 13.1229 | 12.1545 | 11.2473 | 10.3086 | 9.2963 | 3.8647 | -4.5955 | -16.3557 | 5.7153 | 28.5714 | 14.4708 | 14.1208 | 13.2933 | 12.3208 | 11.2106 | 10.2045 | 9.1871 | 8.1576 | 2.9871 | -3.5241 | -8.7353
MELKSHAM GSP | ANDOVER BSP | WHITCHURCH | MINIMUM HEADROOM | SU 45924 48466 | YES | 1.028 | 0.71816 | 0.63245 | 0.52633 | 0.18143 | -0.0053061 | -0.86143 | -1.3757 | -1.9288 | -3.6869 | -4.9859 | -8.2339 | -11.3655 | -15.2624 | 2.0763 | 1.9661 | 1.8508 | 1.4304 | 1.2243 | 0.17224 | -0.42061 | -1.0227 | -3.1124 | -4.5961 | -8.0247 | -11.7818 | -17.339 | 1.4518 | 1.3467 | 1.2131 | 0.79061 | 0.58143 | -0.46857 | -1.1002 | -1.7512 | -3.8716 | -5.388 | -8.988 | -12.7665 | -17.5053
|  | WHITCHURCH | EE |  |  |  | 0.71816 | 0.63245 | 0.54571 | 0.43755 | 0.31306 | -0.055306 | -0.5951 | -0.96755 | -1.6859 | -2.0982 | -4.4216 | -8.8155 | -10.8063 | 2.0763 | 1.9661 | 1.861 | 1.7171 | 1.558 | 1.1661 | 0.66612 | 0.39163 | -0.32469 | -0.70939 | -3.0114 | -8.3063 | -11.2716 | 1.4518 | 1.3467 | 1.2457 | 1.111 | 0.96102 | 0.57122 | 0.027347 | -0.2849 | -1.0278 | -1.4727 | -4.0961 | -9.4461 | -11.7104
|  | WHITCHURCH | HT |  |  |  | 0.76714 | 0.6998 | 0.56 | 0.33551 | 0.24673 | -0.4849 | -1.0237 | -1.6584 | -2.0349 | -2.8053 | -5.5992 | -10.1573 | -13.3441 | 2.1253 | 2.0743 | 1.9222 | 1.6569 | 1.5886 | 0.72224 | 0.14469 | -0.47673 | -0.75939 | -1.5267 | -4.0339 | -8.9124 | -12.4114 | 1.4876 | 1.4141 | 1.2416 | 0.96102 | 0.86816 | -0.018571 | -0.67878 | -1.388 | -1.7543 | -2.5982 | -5.688 | -11.0553 | -14.8431
|  | WHITCHURCH | HE |  |  |  | 0.7651 | 0.69776 | 0.52633 | 0.18143 | -0.0053061 | -0.86143 | -1.3757 | -1.9288 | -3.6869 | -4.9859 | -8.2339 | -11.3655 | -15.2624 | 2.1243 | 2.0559 | 1.8508 | 1.4304 | 1.2243 | 0.17224 | -0.42061 | -1.0227 | -3.1124 | -4.5961 | -8.0247 | -11.7818 | -17.339 | 1.4876 | 1.4202 | 1.2131 | 0.79061 | 0.58143 | -0.46857 | -1.1002 | -1.7512 | -3.8716 | -5.388 | -8.988 | -12.7665 | -17.5053
|  | WHITCHURCH | CF |  |  |  | 0.81 | 0.77429 | 0.73653 | 0.69061 | 0.56204 | 0.41714 | 0.21408 | 0.015102 | -0.19918 | -0.45837 | -2.3716 | -4.3431 | -6.5257 | 2.1457 | 2.0998 | 2.0406 | 1.9631 | 1.7814 | 1.5906 | 1.31 | 1.0478 | 0.76102 | 0.46306 | -1.8573 | -4.6859 | -8.8614 | 1.5131 | 1.4855 | 1.4549 | 1.3967 | 1.2386 | 1.0712 | 0.82429 | 0.59878 | 0.35796 | 0.091633 | -1.9696 | -4.3145 | -6.8339
BOTLEY WOOD GSP | BOTLEY WOOD BSP | WHITELEY | MINIMUM HEADROOM | SU 52936 08794 | YES | 10.608 | 6.7607 | 13.0467 | 12.0324 | 11.0804 | 10.0345 | 8.9488 | 7.9528 | 6.6549 | 5.4437 | 4.4324 | -0.041029 | -2.5829 | -3.8676 | 9.6923 | 15.6702 | 14.9294 | 14.3212 | 13.6508 | 12.9722 | 12.4947 | 11.7743 | 10.9794 | 10.2151 | 6.9386 | 5.2702 | 1.1528 | 7.0637 | 11.9631 | 11.0314 | 10.1528 | 9.1845 | 8.1773 | 7.2477 | 5.9294 | 4.6651 | 3.608 | -0.90531 | -3.2788 | -4.4788
|  | WHITELEY | EE |  |  |  | 6.7607 | 13.0467 | 12.0324 | 11.0804 | 10.0345 | 8.9488 | 7.9528 | 6.6549 | 5.4437 | 4.4324 | 1.0406 | -0.15838 | -0.89409 | 9.6923 | 15.6702 | 14.9294 | 14.3212 | 13.6508 | 12.9722 | 12.4947 | 11.7743 | 10.9794 | 10.2151 | 7.9222 | 6.6049 | 4.0702 | 7.0637 | 11.9631 | 11.0314 | 10.1528 | 9.1845 | 8.1773 | 7.2477 | 5.9294 | 4.6651 | 3.608 | 0.17122 | -0.89715 | -1.5451
|  | WHITELEY | HT |  |  |  | 7.128 | 13.3682 | 12.6824 | 11.9131 | 10.81 | 9.5202 | 8.4947 | 7.5467 | 6.6375 | 6.0284 | 1.4641 | -0.77878 | -1.9278 | 9.8413 | 15.712 | 15.2386 | 14.7243 | 14.1559 | 13.4549 | 12.8406 | 12.26 | 11.7008 | 11.4212 | 8.3641 | 6.9733 | 6.2865 | 7.4188 | 12.2835 | 11.5773 | 10.7233 | 9.7763 | 8.6671 | 7.7773 | 6.9345 | 6.0824 | 5.1641 | 0.58856 | -1.4869 | -2.538
|  | WHITELEY | HE |  |  |  | 7.0637 | 13.4386 | 12.5426 | 11.7039 | 10.7773 | 9.6692 | 8.7641 | 7.5641 | 6.3243 | 5.2212 | -0.041029 | -2.5829 | -3.8676 | 9.8015 | 15.8192 | 15.1416 | 14.5692 | 13.96 | 13.3641 | 12.7743 | 12.108 | 11.4559 | 10.809 | 6.9386 | 5.2702 | 3.8069 | 7.3566 | 12.3437 | 11.5243 | 10.6977 | 9.7365 | 8.7753 | 7.9865 | 6.8763 | 5.5937 | 4.4712 | -0.90531 | -3.2788 | -4.4788
|  | WHITELEY | CF |  |  |  | 7.3678 | 13.8977 | 13.3814 | 12.6335 | 11.8233 | 10.9426 | 10.46 | 9.9294 | 9.3549 | 8.5906 | 4.4426 | 0.9753 | -1.6665 | 9.9076 | 15.9804 | 15.561 | 14.9212 | 14.4324 | 13.9335 | 13.5855 | 13.1406 | 12.6365 | 12.1416 | 9.6253 | 6.2753 | 1.1528 | 7.6433 | 12.759 | 12.2222 | 11.3967 | 10.6794 | 9.9569 | 9.5559 | 9.0835 | 8.5671 | 7.8549 | 3.8028 | 0.11305 | -2.4288
BRAMLEY (FLEE) | BURGHFIELD MAIN | WHITLEY WOOD | MINIMUM HEADROOM | SU 72812 69667 | YES | 0.681 | 23.3378 | 22.9071 | 22.3143 | 22.201 | 21.2265 | 20.4439 | 19.1796 | 17.7408 | 16.1878 | 14.7306 | 10.2122 | 7.7643 | 6.9633 | 25.4286 | 25.0908 | 24.6357 | 24.4837 | 24.0082 | 23.1347 | 22.1214 | 20.8969 | 19.5673 | 18.45 | 13.8418 | 9.2663 | -0.74898 | 23.2122 | 22.8643 | 22.401 | 22.2194 | 21.2112 | 20.2878 | 19.0235 | 17.5449 | 15.8204 | 14.2418 | 9.8327 | 7.7122 | 7.0439
|  | WHITLEY WOOD | EE |  |  |  | 23.3378 | 22.9071 | 22.3143 | 22.201 | 21.5837 | 20.549 | 19.252 | 17.7408 | 16.2041 | 15.0337 | 10.3837 | 8.1612 | 7.7551 | 25.4286 | 25.0908 | 24.6357 | 24.4837 | 24.0082 | 23.1347 | 22.1214 | 20.8969 | 19.5673 | 18.45 | 13.8418 | 10.6153 | 5.9592 | 23.2122 | 22.8643 | 22.401 | 22.2316 | 21.7235 | 20.7184 | 19.4531 | 17.9694 | 16.3327 | 14.9898 | 9.9337 | 8.0582 | 7.6918
|  | WHITLEY WOOD | HT |  |  |  | 23.5847 | 23.2245 | 22.7888 | 22.2265 | 21.2265 | 20.4439 | 19.1796 | 17.7684 | 16.1878 | 14.7306 | 10.2122 | 7.7643 | 6.9633 | 25.6704 | 25.4429 | 25.1673 | 24.8184 | 24.049 | 23.4173 | 22.5276 | 21.4316 | 20.1184 | 18.9163 | 15.9306 | 14.8184 | 14.3755 | 23.3908 | 23.0714 | 22.6918 | 22.2194 | 21.2112 | 20.2878 | 19.0235 | 17.5449 | 15.8204 | 14.2418 | 9.8327 | 7.7122 | 7.0439
|  | WHITLEY WOOD | HE |  |  |  | 23.5929 | 23.2867 | 22.9245 | 22.4571 | 21.9133 | 21.4378 | 20.3847 | 19.1704 | 17.8857 | 16.6173 | 11.6867 | 9.6316 | 8.9367 | 25.6204 | 25.3663 | 25.0612 | 24.6918 | 24.2796 | 23.7898 | 22.9459 | 21.9337 | 20.7755 | 19.5704 | 14.4571 | 11.2439 | 6.5541 | 23.4031 | 23.1378 | 22.8194 | 22.4327 | 21.9827 | 21.3551 | 20.2888 | 19.0571 | 17.6908 | 16.3071 | 11.1286 | 9.3765 | 8.7959
|  | WHITLEY WOOD | CF |  |  |  | 23.7388 | 23.5551 | 23.2949 | 23.0847 | 22.8061 | 22.4857 | 21.9694 | 21.8071 | 21.0184 | 20.1929 | 14.5878 | 12.3388 | 9.9408 | 25.6959 | 25.4908 | 25.2204 | 24.9714 | 24.6735 | 24.3163 | 23.7337 | 23.3133 | 22.448 | 21.5214 | 14.8224 | 9.2663 | -0.74898 | 23.5449 | 23.401 | 23.198 | 23.0418 | 22.8378 | 22.6031 | 22.1337 | 21.8041 | 21.001 | 20.149 | 13.95 | 11.748 | 9.5898
MINETY GSP | CIRENCESTER BSP | WHITEWAY | MINIMUM HEADROOM | SP 02076 03059 | YES | 5.715 | 14.0035 | 13.78 | 13.5167 | 13.2014 | 12.8535 | 12.78 | 12.2076 | 11.5453 | 10.8851 | 10.4035 | 7.5667 | 5.1902 | 3.7851 | 15.9392 | 15.7463 | 15.5065 | 15.2127 | 14.8841 | 14.8147 | 14.4086 | 13.9331 | 13.4596 | 13.1157 | 11.1606 | 9.0514 | 3.6229 | 14.1147 | 13.8749 | 13.5892 | 13.2371 | 12.8484 | 12.7892 | 12.2412 | 11.6188 | 11.0024 | 10.5616 | 8.1198 | 6.129 | 5.0392
|  | WHITEWAY | EE |  |  |  | 14.0035 | 13.78 | 13.5167 | 13.2014 | 12.8535 | 12.78 | 12.2076 | 11.5453 | 10.8851 | 10.4035 | 7.7759 | 5.7086 | 4.1494 | 15.9392 | 15.7463 | 15.5065 | 15.2127 | 14.8841 | 14.8147 | 14.4086 | 13.9331 | 13.4596 | 13.1157 | 11.1606 | 9.1249 | 6.178 | 14.1147 | 13.8749 | 13.5892 | 13.2371 | 12.8484 | 12.7892 | 12.2412 | 11.6188 | 11.0024 | 10.5616 | 8.231 | 6.6004 | 5.3351
|  | WHITEWAY | HT |  |  |  | 14.1382 | 13.9259 | 13.7065 | 13.4422 | 13.1922 | 12.8902 | 12.332 | 11.7269 | 11.4188 | 10.8433 | 7.5667 | 5.1902 | 3.7851 | 16.1096 | 15.9606 | 15.8147 | 15.6218 | 15.4443 | 15.2178 | 14.8922 | 14.5127 | 14.4259 | 14.0749 | 12.2749 | 11.1678 | 10.581 | 14.2912 | 14.0749 | 13.8545 | 13.5861 | 13.331 | 13.0137 | 12.4851 | 11.8984 | 11.6708 | 11.1137 | 8.1198 | 6.129 | 5.0392
|  | WHITEWAY | HE |  |  |  | 14.1402 | 13.9473 | 13.7484 | 13.5127 | 13.2892 | 13.0198 | 12.5616 | 12.0555 | 11.8524 | 11.3851 | 8.632 | 6.5984 | 5.5902 | 16.081 | 15.9208 | 15.7535 | 15.5463 | 15.3473 | 15.0994 | 14.7667 | 14.378 | 14.2769 | 13.9076 | 11.7239 | 9.6494 | 6.9351 | 14.2892 | 14.0933 | 13.8922 | 13.6494 | 13.4218 | 13.1382 | 12.6984 | 12.1994 | 12.0637 | 11.6065 | 9.1178 | 7.4912 | 6.7096
|  | WHITEWAY | CF |  |  |  | 14.2249 | 14.129 | 13.9922 | 13.878 | 13.73 | 13.6024 | 13.4229 | 13.2086 | 12.9729 | 12.7412 | 11.3076 | 9.3565 | 7.5147 | 16.1208 | 16.0137 | 15.8606 | 15.7259 | 15.5473 | 15.3698 | 15.129 | 14.8422 | 14.532 | 14.2076 | 12.3269 | 9.0514 | 3.6229 | 14.3647 | 14.2637 | 14.1127 | 13.9963 | 13.8351 | 13.6953 | 13.5014 | 13.2637 | 13.0045 | 12.7412 | 11.4218 | 9.6892 | 8.1535
BRAMLEY (FLEE) | BURGHFIELD MAIN | WILSON ROAD | MINIMUM HEADROOM | SU 69235 73304 | YES | 2.908 | 13.1882 | 12.6647 | 12.0892 | 11.3433 | 10.5484 | 9.8953 | 8.5963 | 7.4218 | 6.2586 | 5.3606 | 0.92286 | -2.8312 | -4.9669 | 15.8759 | 15.4269 | 14.9178 | 14.2484 | 13.5657 | 13.0953 | 12.1433 | 11.2096 | 10.2586 | 9.4994 | 5.4473 | 0.15959 | -13.3976 | 12.4147 | 11.9086 | 11.3422 | 10.5871 | 9.8188 | 9.282 | 8.0637 | 6.9453 | 5.8392 | 4.9984 | 1.0341 | -2.1271 | -3.97
|  | WILSON ROAD | EE |  |  |  | 13.1882 | 12.6647 | 12.0892 | 11.3433 | 10.5484 | 9.8953 | 8.5963 | 7.4218 | 6.2586 | 5.3606 | 0.92286 | -2.2353 | -4.7139 | 15.8759 | 15.4269 | 14.9178 | 14.2484 | 13.5657 | 13.0953 | 12.1433 | 11.2096 | 10.2586 | 9.4994 | 5.4473 | 1.1565 | -5.8088 | 12.4147 | 11.9086 | 11.3422 | 10.5871 | 9.8188 | 9.282 | 8.0637 | 6.9453 | 5.8392 | 4.9984 | 1.0341 | -1.5853 | -3.772
|  | WILSON ROAD | HT |  |  |  | 13.4759 | 13.0902 | 12.679 | 12.13 | 11.6024 | 10.7402 | 9.6218 | 8.6576 | 8.0565 | 7.081 | 1.4494 | -2.8312 | -4.9669 | 16.178 | 15.9045 | 15.5933 | 15.1616 | 14.8045 | 14.2627 | 13.5953 | 12.9739 | 12.6647 | 12.0269 | 8.7422 | 6.578 | 5.6943 | 12.728 | 12.3657 | 11.9637 | 11.4096 | 10.9188 | 10.1371 | 9.0943 | 8.1851 | 7.6667 | 6.7463 | 1.6014 | -2.1271 | -3.97
|  | WILSON ROAD | HE |  |  |  | 13.4341 | 13.0596 | 12.6637 | 12.1453 | 11.6545 | 10.8514 | 9.7963 | 8.9137 | 8.3718 | 7.4984 | 2.9178 | -0.22816 | -1.4455 | 16.0963 | 15.7759 | 15.4065 | 14.9239 | 14.5055 | 13.8912 | 13.1239 | 12.4065 | 11.9882 | 11.2412 | 6.88 | 2.431 | -4.1027 | 12.6912 | 12.3453 | 11.9586 | 11.4218 | 10.9657 | 10.2392 | 9.2657 | 8.431 | 7.9892 | 7.1729 | 3.0076 | 0.32286 | -0.71388
|  | WILSON ROAD | CF |  |  |  | 13.6106 | 13.3963 | 13.1208 | 12.8045 | 12.4606 | 11.9739 | 11.4045 | 10.9902 | 10.531 | 10.0484 | 7.4361 | 4.2341 | 1.2443 | 16.1851 | 15.9341 | 15.6065 | 15.2188 | 14.8382 | 14.3637 | 13.7402 | 13.1596 | 12.5259 | 11.8514 | 7.5984 | 0.15959 | -13.3976 | 12.8351 | 12.628 | 12.332 | 11.9943 | 11.6678 | 11.2351 | 10.7004 | 10.2912 | 9.8371 | 9.3657 | 6.979 | 4.0657 | 1.4892
MANNINGTON GSP | MANNINGTON BSP | WIMBORNE | MINIMUM HEADROOM | SZ 02014 99989 | YES | 3.43 | 2.2337 | -0.29398 | -1.0266 | -2.0583 | -3.1491 | 14.1264 | 12.8652 | 11.3428 | 9.804 | 8.6519 | 2.6938 | -1.7256 | -4.0736 | 7.152 | 4.9989 | 4.5917 | 3.904 | 3.1601 | 19.2693 | 18.3856 | 17.3121 | 16.2193 | 15.4591 | 11.4836 | 6.9468 | -3.9644 | 3.0908 | 0.65704 | 0.064188 | -0.87459 | -1.8817 | 13.2519 | 12.0632 | 10.6295 | 9.1846 | 8.1724 | 3.1958 | -0.68479 | -2.7419
|  | WIMBORNE | EE |  |  |  | 2.2337 | -0.29398 | -1.0266 | -2.0583 | -3.1491 | 14.1264 | 12.8652 | 11.3428 | 9.804 | 8.6519 | 2.8336 | -0.92969 | -3.7685 | 7.152 | 4.9989 | 4.5917 | 3.904 | 3.1601 | 19.2693 | 18.3856 | 17.3121 | 16.2193 | 15.4591 | 11.4836 | 7.703 | 2.0764 | 3.0908 | 0.65704 | 0.064188 | -0.87459 | -1.8817 | 13.2519 | 12.0632 | 10.6295 | 9.1846 | 8.1724 | 3.2591 | 0.0080653 | -2.4981
|  | WIMBORNE | HT |  |  |  | 2.5796 | 0.17235 | -0.72459 | -1.6756 | -2.3134 | 15.1438 | 14.0377 | 12.7285 | 11.3428 | 9.9193 | 2.6938 | -1.7256 | -4.0736 | 7.5082 | 5.5315 | 5.0387 | 4.4917 | 4.2509 | 20.6111 | 20.0081 | 19.2744 | 18.4836 | 17.6621 | 13.8162 | 11.805 | 10.8693 | 3.4643 | 1.1652 | 0.38051 | -0.47765 | -0.96642 | 14.3652 | 13.3621 | 12.1754 | 10.9172 | 9.6193 | 3.1958 | -0.68479 | -2.7419
|  | WIMBORNE | HE |  |  |  | 2.5592 | 0.17031 | -0.71234 | -1.6572 | -2.2889 | 15.1693 | 14.2285 | 13.0662 | 11.8264 | 10.5407 | 3.8264 | -0.34602 | -2.1603 | 7.4316 | 5.4019 | 4.8438 | 4.2285 | 3.904 | 20.1734 | 19.5101 | 18.7019 | 17.8193 | 16.8856 | 11.8356 | 7.6356 | 2.4142 | 3.4388 | 1.157 | 0.38153 | -0.46847 | -0.95622 | 14.3764 | 13.5081 | 12.4428 | 11.3019 | 10.1162 | 4.1183 | 0.45194 | -1.1256
|  | WIMBORNE | CF |  |  |  | 2.8051 | 0.65807 | 0.026433 | -0.62357 | -1.3042 | 16.7499 | 16.3621 | 15.7938 | 15.1642 | 14.504 | 9.856 | 5.3285 | 1.3999 | 7.5602 | 5.6397 | 5.1928 | 4.7142 | 4.1968 | 20.853 | 20.3938 | 19.7989 | 19.1438 | 18.4458 | 13.5805 | 6.9468 | -3.9644 | 3.6673 | 1.5979 | 1.0438 | 0.46113 | -0.1552 | 15.7887 | 15.4101 | 14.8713 | 14.2744 | 13.6448 | 9.3315 | 5.3621 | 2.0019
MANNINGTON GSP | MANNINGTON BSP | WIMBORNE ST GILES | MINIMUM HEADROOM | SU 03028 12678 | YES | 0.271 | 5.5367 | 5.5102 | 5.4704 | 5.4388 | 5.3908 | 5.3663 | 5.3082 | 5.25 | 5.1837 | 5.151 | 4.9969 | 4.9449 | 4.901 | 5.5082 | 5.4888 | 5.4592 | 5.4347 | 5.4 | 5.3806 | 5.3357 | 5.2929 | 5.2388 | 5.2153 | 5.101 | 4.9245 | 4.5235 | 5.601 | 5.5745 | 5.5367 | 5.5061 | 5.4622 | 5.4367 | 5.3806 | 5.3245 | 5.2582 | 5.2286 | 5.0918 | 5.0449 | 5.0061
|  | WIMBORNE ST GILES | EE |  |  |  | 5.5367 | 5.5102 | 5.4704 | 5.4388 | 5.3908 | 5.3663 | 5.3082 | 5.25 | 5.1837 | 5.151 | 4.9969 | 4.9449 | 4.9214 | 5.5082 | 5.4888 | 5.4592 | 5.4347 | 5.4 | 5.3806 | 5.3357 | 5.2929 | 5.2388 | 5.2153 | 5.101 | 4.9827 | 4.7918 | 5.601 | 5.5745 | 5.5367 | 5.5061 | 5.4622 | 5.4367 | 5.3806 | 5.3245 | 5.2582 | 5.2286 | 5.0918 | 5.0449 | 5.0245
|  | WIMBORNE ST GILES | HT |  |  |  | 5.5561 | 5.5296 | 5.5071 | 5.4857 | 5.4551 | 5.4265 | 5.3827 | 5.3327 | 5.301 | 5.249 | 5.0316 | 4.952 | 4.901 | 5.5255 | 5.5102 | 5.4949 | 5.4816 | 5.4622 | 5.4449 | 5.4173 | 5.3837 | 5.3684 | 5.3306 | 5.1888 | 5.149 | 5.1255 | 5.6184 | 5.5939 | 5.5724 | 5.5541 | 5.5235 | 5.498 | 5.4561 | 5.4082 | 5.3786 | 5.3286 | 5.1224 | 5.05 | 5.0061
|  | WIMBORNE ST GILES | HE |  |  |  | 5.5551 | 5.5316 | 5.5071 | 5.4867 | 5.4582 | 5.4316 | 5.3878 | 5.3367 | 5.3071 | 5.2571 | 5.0245 | 4.9673 | 4.948 | 5.5224 | 5.5061 | 5.4867 | 5.4735 | 5.4531 | 5.4337 | 5.4031 | 5.3663 | 5.349 | 5.3082 | 5.1245 | 4.998 | 4.8082 | 5.6173 | 5.5969 | 5.5735 | 5.5551 | 5.5255 | 5.502 | 5.4612 | 5.4133 | 5.3857 | 5.3388 | 5.1204 | 5.0684 | 5.05
|  | WIMBORNE ST GILES | CF |  |  |  | 5.5643 | 5.5449 | 5.5214 | 5.501 | 5.4786 | 5.4622 | 5.4367 | 5.4122 | 5.3816 | 5.348 | 5.1898 | 5.0745 | 4.9908 | 5.5296 | 5.5153 | 5.4969 | 5.4827 | 5.4622 | 5.451 | 5.4255 | 5.4031 | 5.3755 | 5.3449 | 5.1663 | 4.9245 | 4.5235 | 5.6276 | 5.6092 | 5.5867 | 5.5704 | 5.5459 | 5.5316 | 5.5071 | 5.4857 | 5.4541 | 5.4235 | 5.2714 | 5.1673 | 5.0908
MANNINGTON GSP | SHAFTESBURY BSP | WINCANTON | MINIMUM HEADROOM | ST 71286 27802 | YES | 2.867 | 4.6185 | 4.344 | 3.9868 | 3.6348 | 3.2838 | 2.9328 | 2.8164 | 2.3807 | 1.9419 | 1.6307 | -0.040714 | -1.2417 | -1.9866 | 2.969 | 2.8649 | 2.7169 | 2.5465 | 2.3088 | 2.0659 | 2.0159 | 1.7261 | 1.4261 | 1.2057 | -0.088163 | -1.6463 | -5.3586 | 3.0751 | 2.8802 | 2.6322 | 2.3822 | 2.1251 | 1.7935 | 1.7016 | 1.2894 | 0.87816 | 0.59245 | -0.90041 | -1.9576 | -2.5555
|  | WINCANTON | EE |  |  |  | 4.6185 | 4.344 | 3.9868 | 3.6348 | 3.2838 | 2.9328 | 2.8164 | 2.3807 | 1.9419 | 1.6307 | -0.040714 | -1.0356 | -1.7989 | 2.969 | 2.8649 | 2.7169 | 2.5465 | 2.3088 | 2.0659 | 2.0159 | 1.7261 | 1.4261 | 1.2057 | -0.088163 | -1.38 | -3.3035 | 3.0751 | 2.8802 | 2.6322 | 2.3822 | 2.1251 | 1.7935 | 1.7016 | 1.2894 | 0.87816 | 0.59245 | -0.90041 | -1.7708 | -2.3943
|  | WINCANTON | HT |  |  |  | 4.6879 | 4.4756 | 4.1766 | 3.8797 | 3.596 | 3.3511 | 2.9777 | 2.5593 | 2.1195 | 2.0123 | -0.028469 | -1.2417 | -1.9866 | 3.0261 | 2.9435 | 2.8343 | 2.7067 | 2.5833 | 2.4761 | 2.2996 | 2.0659 | 1.8159 | 1.8108 | 0.72918 | 0.1302 | -0.20653 | 3.1312 | 2.9486 | 2.7251 | 2.4996 | 2.2843 | 2.0976 | 1.8016 | 1.4761 | 1.0649 | 0.98531 | -0.88 | -1.9576 | -2.5555
|  | WINCANTON | HE |  |  |  | 4.6868 | 4.4879 | 4.1991 | 3.9174 | 3.647 | 3.4164 | 3.0991 | 2.7307 | 2.3501 | 2.2991 | 0.45418 | -0.58969 | -1.1111 | 3.0159 | 2.9302 | 2.8067 | 2.6731 | 2.5292 | 2.4037 | 2.1843 | 1.9333 | 1.6608 | 1.6302 | 0.17102 | -1.1514 | -2.9769 | 3.1363 | 2.9588 | 2.7414 | 2.5231 | 2.3149 | 2.1322 | 1.8812 | 1.5986 | 1.2731 | 1.1853 | -0.43918 | -1.3739 | -1.8371
|  | WINCANTON | CF |  |  |  | 4.7674 | 4.7256 | 4.5889 | 4.4052 | 4.1838 | 3.9032 | 3.6685 | 3.5032 | 3.3001 | 3.0868 | 2.1042 | 0.88888 | -0.22949 | 3.0639 | 3.0159 | 2.9435 | 2.8608 | 2.7496 | 2.5945 | 2.3965 | 2.2282 | 2.019 | 1.7945 | 0.55265 | -1.6463 | -5.3586 | 3.2251 | 3.1506 | 3.0353 | 2.9016 | 2.7373 | 2.5292 | 2.3598 | 2.2384 | 2.0945 | 1.9455 | 1.0424 | -0.058571 | -1.0412
COWLEY GSP | WITNEY BSP | WINDRUSH PARK | MINIMUM HEADROOM | SP 33366 09758 | YES | 10.171 | 14.0778 | 13.8339 | 13.6278 | 13.4257 | 13.1594 | 12.8471 | 12.4461 | 12.2982 | 11.9084 | 11.5104 | 9.8563 | 8.4961 | 7.6706 | 13.7492 | 13.6308 | 13.5145 | 13.388 | 13.2237 | 12.9686 | 12.6614 | 12.6084 | 12.3135 | 12.0961 | 10.8369 | 8.9737 | 4.6441 | 13.6716 | 13.4553 | 13.2512 | 13.0614 | 12.8022 | 12.5063 | 12.1257 | 12.0441 | 11.691 | 11.342 | 9.9196 | 8.7655 | 8.0961
|  | WINDRUSH PARK | EE |  |  |  | 14.0778 | 13.8339 | 13.6278 | 13.4257 | 13.1594 | 12.8471 | 12.4461 | 12.3165 | 11.9431 | 11.6512 | 10.0635 | 8.7839 | 7.8114 | 13.7492 | 13.6308 | 13.5145 | 13.388 | 13.2237 | 12.9686 | 12.6614 | 12.6084 | 12.3135 | 12.0961 | 10.8369 | 9.3522 | 7.0808 | 13.6716 | 13.4553 | 13.2512 | 13.0614 | 12.8022 | 12.5063 | 12.1257 | 12.0441 | 11.691 | 11.4318 | 10.0594 | 8.9941 | 8.191
|  | WINDRUSH PARK | HT |  |  |  | 14.1369 | 13.9012 | 13.7227 | 13.5431 | 13.2839 | 12.9961 | 12.6737 | 12.2982 | 11.9084 | 11.5104 | 9.8563 | 8.4961 | 7.6706 | 13.8155 | 13.7186 | 13.6359 | 13.5451 | 13.4186 | 13.2767 | 13.1329 | 12.9502 | 12.7471 | 12.5053 | 11.7594 | 11.1553 | 10.788 | 13.742 | 13.54 | 13.3716 | 13.2104 | 12.9727 | 12.7094 | 12.4257 | 12.0778 | 11.7145 | 11.342 | 9.9196 | 8.7655 | 8.0961
|  | WINDRUSH PARK | HE |  |  |  | 14.1482 | 13.9318 | 13.7716 | 13.6145 | 13.3971 | 13.139 | 12.8798 | 12.5757 | 12.2624 | 11.9451 | 10.6543 | 9.3992 | 8.7227 | 13.8114 | 13.7124 | 13.6278 | 13.5349 | 13.4104 | 13.2655 | 13.0798 | 12.8349 | 12.5727 | 12.2961 | 11.1563 | 9.6788 | 7.5084 | 13.7512 | 13.5665 | 13.4124 | 13.2686 | 13.0665 | 12.8288 | 12.5992 | 12.3135 | 12.0145 | 11.7104 | 10.5849 | 9.5686 | 9.0196
|  | WINDRUSH PARK | CF |  |  |  | 14.2788 | 14.0778 | 13.9829 | 13.8778 | 13.789 | 13.6757 | 13.5686 | 13.4686 | 13.3267 | 13.1747 | 12.2655 | 11.0227 | 9.8573 | 13.9196 | 13.7961 | 13.7461 | 13.6859 | 13.6247 | 13.4818 | 13.3124 | 13.1461 | 12.9369 | 12.7114 | 11.3859 | 8.9737 | 4.6441 | 13.8696 | 13.6951 | 13.6022 | 13.5012 | 13.4176 | 13.3063 | 13.2002 | 13.1053 | 12.9635 | 12.8145 | 12.0441 | 10.9022 | 9.9502
MANNINGTON GSP |  | WINFRITH HEATH | MINIMUM HEADROOM | SY 80748 86538 | YES | 5.671 | 9.5633 | 8.7051 | 7.6827 | 6.5388 | 5.3266 | 4.747 | 3.9439 | 3.2358 | 2.598 | 2.3256 | -0.53873 | -1.6796 | -2.1938 | 16.85 | 15.9756 | 15 | 13.9551 | 12.9153 | 12.597 | 12.3949 | 12.0796 | 11.7429 | 11.6429 | 9.7837 | 8.8215 | 6.6531 | 16.8766 | 16.0562 | 15.0898 | 14.0153 | 12.8694 | 12.4082 | 11.7643 | 11.1939 | 10.6735 | 10.4602 | 7.9919 | 7.0358 | 6.6051
|  | WINFRITH HEATH | EE |  |  |  | 9.5633 | 8.7051 | 7.6827 | 6.5388 | 5.3266 | 4.747 | 3.9439 | 3.2358 | 2.598 | 2.3256 | -0.50914 | -1.5469 | -2.0734 | 16.85 | 15.9756 | 15 | 13.9551 | 12.9153 | 12.7337 | 12.4031 | 12.0796 | 11.7429 | 11.6429 | 9.7837 | 8.8837 | 7.7878 | 16.8766 | 16.0562 | 15.0898 | 14.0153 | 12.8694 | 12.4082 | 11.7643 | 11.1939 | 10.6735 | 10.4602 | 8.0164 | 7.148 | 6.7062
|  | WINFRITH HEATH | HT |  |  |  | 9.6092 | 8.7684 | 7.7582 | 6.646 | 6.1909 | 5.6092 | 4.8307 | 4.1878 | 3.5807 | 2.6725 | -0.53873 | -1.6796 | -2.1938 | 16.8817 | 16.0225 | 15.0643 | 14.046 | 13.9102 | 13.7307 | 13.4072 | 13.1419 | 12.8623 | 12.2521 | 10.2215 | 9.7113 | 9.4827 | 16.9225 | 16.1021 | 15.1511 | 14.1 | 13.746 | 13.2786 | 12.6562 | 12.1419 | 11.649 | 10.8409 | 7.9919 | 7.0358 | 6.6051
|  | WINFRITH HEATH | HE |  |  |  | 9.6072 | 8.7745 | 7.7735 | 6.6633 | 5.5143 | 4.9419 | 4.198 | 3.5929 | 3.0235 | 2.447 | -0.25914 | -1.303 | -1.6387 | 16.8715 | 16.0051 | 15.0419 | 14.0113 | 12.997 | 12.8082 | 12.5225 | 12.248 | 11.9766 | 11.6909 | 9.8613 | 8.9358 | 7.9204 | 16.9062 | 16.099 | 15.1521 | 14.1082 | 13.0102 | 12.5613 | 11.9776 | 11.496 | 11.0307 | 10.5613 | 8.2072 | 7.3225 | 7.0429
|  | WINFRITH HEATH | CF |  |  |  | 10.1082 | 8.8633 | 7.9184 | 7.1643 | 5.798 | 5.096 | 4.5276 | 4.047 | 3.6164 | 3.2082 | 1.2184 | -0.049959 | -1.0132 | 17.3796 | 16.0398 | 15.096 | 14.4266 | 13.0878 | 12.597 | 12.3949 | 12.1939 | 11.9704 | 11.7602 | 10.3745 | 8.8215 | 6.6531 | 17.3725 | 16.1664 | 15.2613 | 14.5725 | 13.2572 | 12.6368 | 12.2143 | 11.846 | 11.5062 | 11.1878 | 9.5643 | 8.4358 | 7.5939
COWLEY GSP | DRAYTON BSP | WINSMORE LANE | MINIMUM HEADROOM | SU 49513 96982 | YES | 3.051 | 10.0265 | 9.549 | 9.0704 | 8.8694 | 8.3306 | 7.7765 | 6.8439 | 5.7949 | 4.751 | 3.9704 | -0.28163 | -3.8367 | -5.9388 | 13.7531 | 13.3184 | 12.8878 | 12.702 | 12.1918 | 11.7112 | 11.0571 | 10.3 | 9.5306 | 8.9571 | 5.7276 | 2.0265 | -7.6449 | 10.6827 | 10.1724 | 9.6755 | 9.4745 | 8.9 | 8.3653 | 7.4949 | 6.5133 | 5.5357 | 4.8143 | 1.0571 | -2.0051 | -3.702
|  | WINSMORE LANE | EE |  |  |  | 10.0265 | 9.549 | 9.0704 | 8.8694 | 8.3306 | 7.7765 | 6.8439 | 5.7949 | 4.751 | 3.9704 | -0.12959 | -3.1449 | -5.5929 | 13.7531 | 13.3184 | 12.8878 | 12.702 | 12.1918 | 11.7112 | 11.0571 | 10.3 | 9.5306 | 8.9571 | 5.7276 | 2.3796 | -2.7663 | 10.6827 | 10.1724 | 9.6755 | 9.4745 | 8.9 | 8.3653 | 7.4949 | 6.5133 | 5.5357 | 4.8143 | 1.1306 | -1.3878 | -3.4184
|  | WINSMORE LANE | HT |  |  |  | 10.2235 | 9.801 | 9.4133 | 8.9939 | 8.5724 | 8.1031 | 7.5857 | 6.7235 | 5.8286 | 4.8827 | -0.28163 | -3.8367 | -5.9388 | 13.9816 | 13.6653 | 13.3918 | 13.0765 | 12.7755 | 12.4306 | 12.2337 | 11.7378 | 11.2082 | 10.6255 | 7.8531 | 6.2031 | 5.3163 | 10.898 | 10.4724 | 10.0888 | 9.6571 | 9.2347 | 8.7602 | 8.3286 | 7.5184 | 6.6755 | 5.7776 | 1.0571 | -2.0051 | -3.702
|  | WINSMORE LANE | HE |  |  |  | 10.2224 | 9.8276 | 9.4694 | 9.149 | 8.7622 | 8.2714 | 7.8949 | 7.1724 | 6.4286 | 5.6643 | 1.4459 | -1.5347 | -3.0224 | 13.9316 | 13.5816 | 13.2643 | 12.9827 | 12.6316 | 12.1663 | 11.9398 | 11.4031 | 10.8276 | 10.2224 | 6.6959 | 3.3041 | -1.4878 | 10.898 | 10.4939 | 10.1378 | 9.8173 | 9.4316 | 8.9184 | 8.6102 | 7.9276 | 7.2194 | 6.4878 | 2.6449 | 0.16224 | -1.0327
|  | WINSMORE LANE | CF |  |  |  | 10.3898 | 10.1041 | 9.9204 | 9.7122 | 9.4612 | 9.2214 | 8.95 | 8.9286 | 8.6276 | 8.3143 | 5.5745 | 2.6898 | -0.12041 | 14.0153 | 13.6959 | 13.4755 | 13.2224 | 12.9 | 12.5735 | 12.1867 | 12.0041 | 11.5663 | 11.0888 | 7.5367 | 2.0265 | -7.6449 | 11.048 | 10.7418 | 10.5561 | 10.3378 | 10.0633 | 9.8133 | 9.5316 | 9.5214 | 9.2112 | 8.8816 | 6.3235 | 3.7061 | 1.2561
MANNINGTON GSP | LYTCHETT | WINTERBORNE KINGSTON | MINIMUM HEADROOM | SY 84631 98138 | YES | 2.171 | 3.8719 | 15.9836 | 15.6029 | 15.3662 | 15.0734 | 14.756 | 14.3407 | 14.3223 | 13.9325 | 13.6723 | 12.2693 | 11.405 | 10.8101 | 5.0653 | 16.3146 | 16.0615 | 15.8891 | 15.6625 | 15.4156 | 15.1085 | 15.2044 | 14.9238 | 14.7544 | 13.8013 | 12.8278 | 10.2034 | 4.1189 | 15.6458 | 15.2907 | 15.0642 | 14.7703 | 14.4529 | 14.0427 | 14.1182 | 13.7489 | 13.508 | 12.2734 | 11.508 | 11.0009
|  | WINTERBORNE KINGSTON | EE |  |  |  | 3.8719 | 15.9836 | 15.6029 | 15.3662 | 15.0734 | 14.756 | 14.3407 | 14.3223 | 13.9325 | 13.6723 | 12.2693 | 11.4754 | 10.9621 | 5.0653 | 16.3146 | 16.0615 | 15.8891 | 15.6625 | 15.4156 | 15.1085 | 15.2044 | 14.9238 | 14.7544 | 13.8013 | 12.9248 | 11.635 | 4.1189 | 15.6458 | 15.2907 | 15.0642 | 14.7703 | 14.4529 | 14.0427 | 14.1182 | 13.7489 | 13.508 | 12.2734 | 11.5785 | 11.1336
|  | WINTERBORNE KINGSTON | HT |  |  |  | 3.9842 | 16.1193 | 15.7948 | 15.6131 | 15.3836 | 15.1336 | 14.8448 | 14.4734 | 14.0825 | 13.6764 | 12.3734 | 11.405 | 10.8101 | 5.1735 | 16.4574 | 16.2727 | 16.1676 | 16.0187 | 15.8523 | 15.6972 | 15.4625 | 15.2115 | 14.9452 | 14.3727 | 13.9146 | 13.6513 | 4.2301 | 15.7897 | 15.504 | 15.3387 | 15.1172 | 14.8785 | 14.6213 | 14.2744 | 13.904 | 13.5162 | 12.3693 | 11.508 | 11.0009
|  | WINTERBORNE KINGSTON | HE |  |  |  | 3.9832 | 16.1285 | 15.8101 | 15.6376 | 15.4193 | 15.1856 | 14.9336 | 14.5989 | 14.2448 | 13.8795 | 12.6193 | 11.8519 | 11.508 | 5.1602 | 16.4401 | 16.2503 | 16.134 | 15.9768 | 15.8013 | 15.638 | 15.3962 | 15.134 | 14.8574 | 14.0085 | 13.1268 | 11.9289 | 4.2291 | 15.7968 | 15.5172 | 15.3601 | 15.1509 | 14.9244 | 14.7029 | 14.3856 | 14.0448 | 13.6897 | 12.6009 | 11.9264 | 11.6478
|  | WINTERBORNE KINGSTON | CF |  |  |  | 4.0352 | 16.2234 | 15.9672 | 15.8121 | 15.6876 | 15.5254 | 15.3591 | 15.2101 | 15.0111 | 14.7989 | 13.9744 | 12.9652 | 11.9805 | 5.1918 | 16.4911 | 16.3309 | 16.2095 | 16.1146 | 15.9758 | 15.8207 | 15.6799 | 15.487 | 15.2819 | 14.3738 | 12.8278 | 10.2034 | 4.277 | 15.8856 | 15.6591 | 15.507 | 15.3938 | 15.2346 | 15.0693 | 14.9325 | 14.7325 | 14.5182 | 13.7999 | 12.8856 | 12.0244
MANNINGTON GSP | REDHILL BSP | WINTON | MINIMUM HEADROOM | SZ 09349 93822 | YES | 1.431 | 4.8306 | 4.2163 | 3.9122 | 3.252 | 2.5235 | 8.5429 | 7.1929 | 5.6786 | 4.1694 | 3.0776 | -1.9316 | -5.4582 | -6.3959 | 9.5 | 8.9867 | 8.7347 | 8.151 | 7.4867 | 14.5714 | 13.5786 | 12.4296 | 11.2653 | 10.4612 | 6.2551 | -0.0020408 | -14.9888 | 4.7296 | 4.1082 | 3.8459 | 3.1878 | 2.452 | 8.4612 | 7.1796 | 5.7245 | 4.2704 | 3.2969 | -0.97755 | -3.9082 | -4.6776
|  | WINTON | EE |  |  |  | 4.8306 | 4.2163 | 3.9122 | 3.252 | 2.5235 | 8.5429 | 7.1929 | 5.6786 | 4.1694 | 3.0776 | -1.9316 | -5.1276 | -5.348 | 9.5 | 8.9867 | 8.7347 | 8.151 | 7.4867 | 14.5714 | 13.5786 | 12.4296 | 11.2653 | 10.4612 | 6.2551 | 1.6827 | -5.1 | 4.7296 | 4.1082 | 3.8459 | 3.1878 | 2.452 | 8.4612 | 7.1796 | 5.7245 | 4.2704 | 3.2969 | -0.97755 | -3.6122 | -3.8347
|  | WINTON | HT |  |  |  | 5.1878 | 4.702 | 4.2 | 3.6153 | 3.3827 | 9.5878 | 8.5031 | 7.3041 | 6.0418 | 4.7337 | -1.652 | -5.4582 | -6.3959 | 9.8214 | 9.5296 | 9.2306 | 8.8173 | 8.7357 | 16.1184 | 15.498 | 14.7888 | 14.0235 | 13.2235 | 9.5837 | 7.7194 | 7.1857 | 5.1255 | 4.6551 | 4.1673 | 3.5918 | 3.4235 | 9.6439 | 8.6541 | 7.5429 | 6.3714 | 5.152 | -0.65612 | -3.9082 | -4.6776
|  | WINTON | HE |  |  |  | 5.2031 | 4.7745 | 4.3286 | 3.8082 | 3.6327 | 9.9092 | 8.9449 | 7.8704 | 6.7439 | 5.5633 | 0.34592 | -2.7082 | -3.5276 | 9.7561 | 9.4102 | 9.048 | 8.5918 | 8.4255 | 15.7265 | 15.0235 | 14.2112 | 13.3357 | 12.3969 | 7.4439 | 2.7184 | -4.2755 | 5.1347 | 4.7102 | 4.2724 | 3.752 | 3.6378 | 9.9214 | 9.0347 | 8.0327 | 6.9755 | 5.8684 | 1.0755 | -1.5 | -2.1806
|  | WINTON | CF |  |  |  | 5.4184 | 5.2204 | 4.9908 | 4.7112 | 4.3959 | 11.2102 | 10.8235 | 10.3561 | 9.8673 | 9.3561 | 5.8102 | 1.5429 | -2.4837 | 9.8551 | 9.6112 | 9.3357 | 9.0051 | 8.5867 | 16.2265 | 15.6837 | 15.0398 | 14.3531 | 13.6204 | 8.4041 | -0.0020408 | -14.9888 | 5.3265 | 5.1194 | 4.8786 | 4.5816 | 4.249 | 11.1051 | 10.7276 | 10.2673 | 9.7745 | 9.2633 | 5.7969 | 2.0449 | -1.3398
COWLEY GSP | WITNEY BSP | WITNEY TOWN | MINIMUM HEADROOM | SP 35844 09625 | YES | 4.739 | -0.068814 | 15.4849 | 15.1726 | 14.5553 | 13.6982 | 12.4849 | 10.7686 | 9.0053 | 7.1288 | 5.5849 | -0.010008 | -4.2294 | -6.7029 | 6.5363 | 20.0533 | 19.8288 | 19.389 | 18.7461 | 17.9043 | 16.8186 | 15.6369 | 14.3798 | 13.4012 | 9.3757 | 5.0808 | -5.7212 | 1.4547 | 16.0533 | 15.7686 | 15.1696 | 14.342 | 13.2277 | 11.6839 | 10.0584 | 8.3492 | 7.0318 | 2.3849 | -1.2478 | -3.3059
|  | WITNEY TOWN | EE |  |  |  | -0.068814 | 15.4849 | 15.1726 | 14.5553 | 13.6982 | 12.4849 | 10.7686 | 9.0053 | 7.1288 | 5.5849 | 0.19203 | -3.3794 | -6.2784 | 6.5363 | 20.0533 | 19.8288 | 19.389 | 18.7461 | 17.9043 | 16.8186 | 15.6369 | 14.3798 | 13.4012 | 9.3757 | 5.6012 | -0.13042 | 1.4547 | 16.0533 | 15.7686 | 15.1696 | 14.342 | 13.2277 | 11.6839 | 10.0584 | 8.3492 | 7.0318 | 2.4308 | -0.51103 | -2.9763
|  | WITNEY TOWN | HT |  |  |  | 0.19343 | 15.8226 | 15.3655 | 14.7645 | 13.9002 | 12.991 | 11.2451 | 9.5482 | 7.8716 | 6.2277 | -0.010008 | -4.2294 | -6.7029 | 6.7751 | 20.4155 | 20.1563 | 19.8114 | 19.3298 | 18.9053 | 18.04 | 17.1686 | 16.242 | 15.2982 | 11.7237 | 9.6971 | 8.6461 | 1.7179 | 16.3951 | 15.9726 | 15.4257 | 14.6635 | 13.9277 | 12.439 | 10.9726 | 9.5186 | 8.0604 | 2.3849 | -1.2478 | -3.3059
|  | WITNEY TOWN | HE |  |  |  | 0.19343 | 15.8604 | 15.44 | 14.9084 | 14.1492 | 13.4012 | 11.9859 | 10.5369 | 8.9553 | 7.4155 | 1.7971 | -1.9202 | -3.7539 | 6.72 | 20.3186 | 20.0084 | 19.6288 | 19.1186 | 18.6798 | 17.8451 | 16.9614 | 15.9553 | 14.9033 | 10.2849 | 6.3053 | 0.97264 | 1.7138 | 16.4237 | 16.0298 | 15.541 | 14.8645 | 14.2614 | 13.041 | 11.7869 | 10.4094 | 9.0451 | 3.9696 | 0.84816 | -0.69572
|  | WITNEY TOWN | CF |  |  |  | 0.4118 | 16.2522 | 15.9747 | 15.7267 | 15.2961 | 14.7155 | 14.4002 | 13.7828 | 13.1135 | 12.3808 | 6.5175 | 2.838 | -0.67736 | 6.8302 | 20.4982 | 20.2431 | 19.992 | 19.6196 | 19.1339 | 18.8135 | 18.2431 | 17.6226 | 16.8971 | 11.4461 | 5.0808 | -5.7212 | 1.92 | 16.7818 | 16.5196 | 16.2869 | 15.8992 | 15.388 | 15.1614 | 14.6135 | 13.99 | 13.3145 | 8.1339 | 4.8084 | 1.7961
BRAMLEY (FLEE) | WOKINGHAM BSP | WOKINGHAM | MINIMUM HEADROOM | SU 79589 67665 | YES | 1.935 | 19.0133 | 18.6806 | 18.3408 | 17.9204 | 17.8143 | 17.3969 | 16.7184 | 15.9602 | 15.2143 | 14.6622 | 11.3847 | 9.1592 | 7.9633 | 21.4112 | 21.249 | 21.0633 | 20.7102 | 20.6704 | 20.3276 | 19.8714 | 19.3398 | 18.8061 | 18.4469 | 16.3439 | 13.6592 | 7.2061 | 18.7806 | 18.4663 | 18.1439 | 17.7245 | 17.6612 | 17.2694 | 16.6408 | 15.9378 | 15.2296 | 14.7408 | 11.851 | 9.8857 | 8.8
|  | WOKINGHAM | EE |  |  |  | 19.0133 | 18.6806 | 18.3408 | 17.9204 | 17.8143 | 17.3969 | 16.7184 | 15.9602 | 15.2143 | 14.6622 | 11.8173 | 9.7714 | 8.2418 | 21.4112 | 21.249 | 21.0633 | 20.7102 | 20.6704 | 20.3276 | 19.8714 | 19.3398 | 18.8061 | 18.4469 | 16.3439 | 14.0551 | 10.6806 | 18.7806 | 18.4663 | 18.1439 | 17.7245 | 17.6612 | 17.2694 | 16.6408 | 15.9378 | 15.2296 | 14.7408 | 12.1908 | 10.4031 | 9.0194
|  | WOKINGHAM | HT |  |  |  | 19.1408 | 18.85 | 18.5571 | 18.2378 | 17.8735 | 17.4612 | 16.7582 | 16.3888 | 15.6776 | 14.9551 | 11.3847 | 9.1592 | 7.9633 | 21.5184 | 21.3969 | 21.2561 | 21.0929 | 20.901 | 20.6776 | 20.3041 | 20.1673 | 19.8337 | 19.4622 | 17.5949 | 16.5847 | 16.0786 | 18.9102 | 18.6429 | 18.3714 | 18.0816 | 17.7429 | 17.3602 | 16.7184 | 16.4071 | 15.7561 | 15.0959 | 11.851 | 9.8857 | 8.8
|  | WOKINGHAM | HE |  |  |  | 19.1582 | 18.9347 | 18.65 | 18.3755 | 18.049 | 17.6776 | 17.1204 | 16.902 | 16.3439 | 15.7724 | 12.8214 | 10.8204 | 9.8031 | 21.5153 | 21.4 | 21.251 | 21.0908 | 20.851 | 20.5429 | 20.1459 | 20.0878 | 19.6796 | 19.2531 | 16.8439 | 14.549 | 11.3653 | 18.9245 | 18.7173 | 18.45 | 18.1949 | 17.8898 | 17.5429 | 17.0265 | 16.851 | 16.3337 | 15.8041 | 13.1102 | 11.35 | 10.4296
|  | WOKINGHAM | CF |  |  |  | 19.2857 | 19.1327 | 18.9827 | 18.7857 | 18.6122 | 18.3816 | 18.1316 | 17.8398 | 17.9061 | 17.652 | 15.6735 | 13.5051 | 11.5337 | 21.6041 | 21.5327 | 21.452 | 21.2663 | 21.0857 | 20.8286 | 20.5327 | 20.1806 | 20.1776 | 19.8459 | 17.4235 | 13.6592 | 7.2061 | 19.0418 | 18.8939 | 18.7551 | 18.5704 | 18.4122 | 18.1918 | 17.9214 | 17.6 | 17.7633 | 17.5163 | 15.6327 | 13.7092 | 11.9541
BRAMLEY (FLEE) | BURGHFIELD RESERVE | WOODCOTE | MINIMUM HEADROOM | SU 64425 81624 | YES | 0.257 | 5.7786 | 5.7327 | 5.6622 | 5.5837 | 5.4633 | 5.3378 | 5.1847 | 4.9663 | 4.749 | 4.6235 | 3.9306 | 3.448 | 3.1735 | 6.4821 | 6.426 | 6.3464 | 6.2832 | 6.1883 | 6.0852 | 5.9821 | 5.8219 | 5.6648 | 5.577 | 5.1128 | 4.4679 | 3.0811 | 6.0531 | 5.9837 | 5.8949 | 5.8245 | 5.7163 | 5.6051 | 5.4612 | 5.2653 | 5.0663 | 4.951 | 4.3031 | 3.8561 | 3.6041
|  | WOODCOTE | EE |  |  |  | 5.7786 | 5.7327 | 5.6622 | 5.5837 | 5.4633 | 5.3378 | 5.1847 | 4.9663 | 4.749 | 4.6235 | 4.0031 | 3.5602 | 3.2388 | 6.4821 | 6.426 | 6.3464 | 6.2832 | 6.1883 | 6.0852 | 5.9821 | 5.8219 | 5.6648 | 5.577 | 5.1128 | 4.6097 | 3.8699 | 6.0531 | 5.9837 | 5.8949 | 5.8245 | 5.7163 | 5.6051 | 5.4612 | 5.2653 | 5.0663 | 4.951 | 4.3694 | 3.9582 | 3.6633
|  | WOODCOTE | HT |  |  |  | 5.8143 | 5.7735 | 5.7316 | 5.6694 | 5.5827 | 5.4806 | 5.3449 | 5.1561 | 4.9622 | 4.8092 | 3.9306 | 3.448 | 3.1735 | 6.5352 | 6.4923 | 6.4485 | 6.3913 | 6.3342 | 6.2628 | 6.1964 | 6.0821 | 5.9648 | 5.8821 | 5.3913 | 5.1719 | 5.0474 | 6.102 | 6.0378 | 5.9776 | 5.8969 | 5.8204 | 5.7286 | 5.6031 | 5.4337 | 5.2571 | 5.1102 | 4.3031 | 3.8561 | 3.6041
|  | WOODCOTE | HE |  |  |  | 5.8122 | 5.7745 | 5.7337 | 5.6816 | 5.6061 | 5.5122 | 5.4071 | 5.251 | 5.0857 | 4.9633 | 4.1776 | 3.7316 | 3.5102 | 6.5281 | 6.4791 | 6.4311 | 6.3668 | 6.3015 | 6.223 | 6.1515 | 6.0352 | 5.9117 | 5.8189 | 5.1883 | 4.676 | 3.974 | 6.1031 | 6.0459 | 5.9888 | 5.9163 | 5.8429 | 5.7592 | 5.6633 | 5.5214 | 5.3704 | 5.2561 | 4.5398 | 4.1276 | 3.9235
|  | WOODCOTE | CF |  |  |  | 5.8367 | 5.8163 | 5.7878 | 5.7643 | 5.7316 | 5.6776 | 5.6041 | 5.5612 | 5.4735 | 5.3827 | 4.8316 | 4.3143 | 3.8867 | 6.5454 | 6.5066 | 6.4505 | 6.4148 | 6.3628 | 6.2974 | 6.2199 | 6.1607 | 6.0668 | 5.9658 | 5.3352 | 4.4679 | 3.0811 | 6.1286 | 6.0929 | 6.0439 | 6.0133 | 5.9663 | 5.9102 | 5.8459 | 5.8061 | 5.7306 | 5.648 | 5.1367 | 4.6714 | 4.2684
NURSLING GSP | SOUTHAMPTON (2 X 90) | WOODMILL LANE | MINIMUM HEADROOM | SU 43733 15470 | YES | 0.354 | 19.251 | 18.9531 | 18.601 | 18.1602 | 17.6684 | 17.1041 | 16.898 | 16.1582 | 15.4153 | 14.8653 | 11.8867 | 9.2643 | 7.7265 | 20.3255 | 20.0653 | 19.7541 | 19.3765 | 18.9469 | 18.4449 | 18.2 | 17.5929 | 16.9755 | 16.4908 | 13.6276 | 9.1949 | -1.501 | 18.8571 | 18.5724 | 18.2378 | 17.8143 | 17.3418 | 16.7969 | 16.6265 | 15.9255 | 15.2255 | 14.7204 | 12.1378 | 9.9367 | 8.6122
|  | WOODMILL LANE | EE |  |  |  | 19.251 | 18.9531 | 18.601 | 18.1602 | 17.6684 | 17.1041 | 16.898 | 16.1582 | 15.4153 | 14.8653 | 11.8867 | 9.6765 | 7.8908 | 20.3255 | 20.0653 | 19.7541 | 19.3765 | 18.9469 | 18.4449 | 18.2 | 17.5929 | 16.9755 | 16.4908 | 13.6276 | 10.2898 | 4.7531 | 18.8571 | 18.5724 | 18.2378 | 17.8143 | 17.3418 | 16.7969 | 16.6265 | 15.9255 | 15.2255 | 14.7204 | 12.1378 | 10.2694 | 8.7112
|  | WOODMILL LANE | HT |  |  |  | 19.4612 | 19.2357 | 18.9847 | 18.6571 | 18.2796 | 17.9469 | 17.3663 | 16.7112 | 16.3918 | 15.7337 | 11.9827 | 9.2643 | 7.7265 | 20.5265 | 20.3714 | 20.2 | 19.9765 | 19.7031 | 19.4633 | 19.1071 | 18.6959 | 18.5684 | 18.1694 | 16.0888 | 14.7898 | 14.1337 | 19.0663 | 18.8592 | 18.6265 | 18.3194 | 17.9653 | 17.652 | 17.1163 | 16.5061 | 16.249 | 15.6418 | 12.3061 | 9.9367 | 8.6122
|  | WOODMILL LANE | HE |  |  |  | 19.45 | 19.2408 | 19.0082 | 18.7112 | 18.3908 | 18.0663 | 17.5357 | 16.9612 | 16.3602 | 16.1541 | 13.1827 | 11.102 | 10.1327 | 20.4724 | 20.2776 | 20.0551 | 19.7847 | 19.4816 | 19.1561 | 18.7143 | 18.2306 | 17.7061 | 17.5153 | 14.4939 | 11.1643 | 5.9286 | 19.0551 | 18.8612 | 18.6429 | 18.3622 | 18.0622 | 17.7571 | 17.2684 | 16.7296 | 16.1633 | 16.0265 | 13.3827 | 11.6112 | 10.8051
|  | WOODMILL LANE | CF |  |  |  | 19.5776 | 19.4357 | 19.2704 | 19.1276 | 18.9378 | 18.7316 | 18.4959 | 18.2592 | 17.9602 | 17.652 | 16.252 | 14.2755 | 12.3327 | 20.5429 | 20.3745 | 20.1735 | 19.9796 | 19.7255 | 19.4255 | 19.0602 | 18.6755 | 18.2276 | 17.7531 | 14.7622 | 9.1949 | -1.501 | 19.1735 | 19.0429 | 18.8827 | 18.7469 | 18.5653 | 18.3663 | 18.1418 | 17.9194 | 17.6347 | 17.3378 | 16.0439 | 14.2918 | 12.6592
COWLEY GSP | YARNTON BSP | WOODSTOCK | MINIMUM HEADROOM | SP 44795 17462 | YES | 1.513 | 6.2028 | 5.862 | 5.5814 | 5.2324 | 4.8467 | 4.3763 | 3.8355 | 3.66 | 3.2794 | 3.0018 | 1.4518 | 0.071204 | -0.82165 | 7.8982 | 7.6758 | 7.4901 | 7.2513 | 7.0115 | 6.7013 | 6.3472 | 6.2829 | 5.9982 | 5.7972 | 4.687 | 3.3166 | -0.25686 | 5.9799 | 5.6809 | 5.4289 | 5.1013 | 4.7605 | 4.3248 | 3.8187 | 3.7717 | 3.4054 | 3.1493 | 1.7829 | 0.61049 | -0.1038
|  | WOODSTOCK | EE |  |  |  | 6.2028 | 5.862 | 5.5814 | 5.2324 | 4.8467 | 4.3763 | 3.8355 | 3.66 | 3.2794 | 3.0018 | 1.5018 | 0.31916 | -0.66145 | 7.8982 | 7.6758 | 7.4901 | 7.2513 | 7.0115 | 6.7013 | 6.3472 | 6.2829 | 5.9982 | 5.7972 | 4.687 | 3.4809 | 1.5472 | 5.9799 | 5.6809 | 5.4289 | 5.1013 | 4.7605 | 4.3248 | 3.8187 | 3.7717 | 3.4054 | 3.1615 | 1.8176 | 0.84008 | 0.033959
|  | WOODSTOCK | HT |  |  |  | 6.3018 | 6.0202 | 5.7569 | 5.4988 | 5.1324 | 4.7232 | 4.2814 | 3.81 | 3.4243 | 3.0253 | 1.4518 | 0.071204 | -0.82165 | 7.9799 | 7.8493 | 7.6982 | 7.5656 | 7.3646 | 7.137 | 6.9125 | 6.6401 | 6.4003 | 6.1493 | 5.4146 | 4.8064 | 4.4472 | 6.0829 | 5.8513 | 5.6187 | 5.3982 | 5.0799 | 4.7125 | 4.3421 | 3.9095 | 3.537 | 3.1493 | 1.7829 | 0.61049 | -0.1038
|  | WOODSTOCK | HE |  |  |  | 6.2998 | 6.0232 | 5.7743 | 5.5243 | 5.1681 | 4.7732 | 4.3865 | 3.9732 | 3.6437 | 3.3049 | 2.0243 | 0.83753 | 0.19059 | 7.9707 | 7.8156 | 7.6523 | 7.5013 | 7.2809 | 7.0289 | 6.7982 | 6.5156 | 6.2615 | 5.9891 | 4.9778 | 3.7462 | 1.9329 | 6.0789 | 5.8533 | 5.6299 | 5.4187 | 5.1105 | 4.7584 | 4.434 | 4.0493 | 3.7227 | 3.385 | 2.3013 | 1.338 | 0.80743
|  | WOODSTOCK | CF |  |  |  | 6.3692 | 6.1518 | 5.9671 | 5.7681 | 5.5273 | 5.2314 | 4.9743 | 4.762 | 4.5947 | 4.4141 | 3.6018 | 2.4549 | 1.3324 | 8.0095 | 7.8748 | 7.736 | 7.5901 | 7.4319 | 7.2278 | 7.0105 | 6.8187 | 6.6176 | 6.4074 | 5.3003 | 3.3166 | -0.25686 | 6.1421 | 5.9615 | 5.7972 | 5.6187 | 5.4187 | 5.1646 | 4.9309 | 4.7472 | 4.5687 | 4.385 | 3.7013 | 2.688 | 1.7136
BOTLEY WOOD GSP | NETLEY COMMON BSP | WOOLSTON | MINIMUM HEADROOM | SU 44145 11242 | YES | 3.447 | 21.8673 | 21.6878 | 21.5082 | 21.2633 | 21.0439 | 20.6673 | 20.1673 | 19.6337 | 19.5276 | 19.202 | 17.5857 | 16.1684 | 15.4102 | 21.501 | 21.3265 | 21.1469 | 20.9102 | 20.6878 | 20.3214 | 19.8929 | 19.4276 | 19.3143 | 18.9949 | 17.1143 | 13.252 | 5.5684 | 21.6949 | 21.5316 | 21.3673 | 21.1449 | 20.9296 | 20.5541 | 20.0776 | 19.5571 | 19.5092 | 19.1959 | 17.7245 | 16.4918 | 15.8398
|  | WOOLSTON | EE |  |  |  | 21.8673 | 21.6878 | 21.5082 | 21.2633 | 21.0439 | 20.6673 | 20.1673 | 19.6337 | 19.5276 | 19.202 | 17.5857 | 16.45 | 15.5418 | 21.501 | 21.3265 | 21.1469 | 20.9102 | 20.6878 | 20.3214 | 19.8929 | 19.4276 | 19.3143 | 18.9949 | 17.1143 | 14.7724 | 10.7827 | 21.6949 | 21.5316 | 21.3673 | 21.1449 | 20.9296 | 20.5541 | 20.0776 | 19.5571 | 19.5092 | 19.1959 | 17.7245 | 16.7388 | 15.9459
|  | WOOLSTON | HT |  |  |  | 21.9908 | 21.8673 | 21.7204 | 21.5408 | 21.2878 | 20.9714 | 20.5878 | 20.2235 | 19.801 | 19.3786 | 17.5969 | 16.1684 | 15.4102 | 21.6347 | 21.5459 | 21.4388 | 21.3071 | 21.1 | 20.849 | 20.5949 | 20.3622 | 20.0837 | 19.8031 | 18.8898 | 18.1857 | 17.8296 | 21.8041 | 21.6929 | 21.5571 | 21.398 | 21.1561 | 20.8622 | 20.5031 | 20.1592 | 19.7704 | 19.3816 | 17.7612 | 16.4918 | 15.8398
|  | WOOLSTON | HE |  |  |  | 21.9827 | 21.8673 | 21.7265 | 21.5592 | 21.4184 | 21.1347 | 20.7592 | 20.4235 | 20.0316 | 19.6469 | 18.1949 | 17.0408 | 16.5439 | 21.6 | 21.4786 | 21.3337 | 21.1622 | 21.0041 | 20.7143 | 20.3765 | 20.0633 | 19.6929 | 19.3173 | 17.4847 | 15.0571 | 11.2531 | 21.7949 | 21.6918 | 21.5612 | 21.4122 | 21.2857 | 21.0214 | 20.6735 | 20.352 | 19.9878 | 19.6276 | 18.2949 | 17.2816 | 16.8622
|  | WOOLSTON | CF |  |  |  | 22.0408 | 21.9602 | 21.8837 | 21.7908 | 21.6857 | 21.6031 | 21.4367 | 21.2112 | 21.0378 | 20.8224 | 19.4531 | 18.6776 | 17.5684 | 21.6245 | 21.5102 | 21.3918 | 21.251 | 21.0837 | 20.9133 | 20.6388 | 20.298 | 19.9806 | 19.6255 | 17.1316 | 13.252 | 5.5684 | 21.8531 | 21.7806 | 21.7133 | 21.6306 | 21.5337 | 21.4592 | 21.3041 | 21.0898 | 20.9143 | 20.698 | 19.3724 | 18.7133 | 17.7316
MINETY GSP | SWINDON BSP | WOOTTON BASSETT | MINIMUM HEADROOM | SU 07587 81123 | YES | 2.297 | 14.3535 | 14.029 | 13.6055 | 13.129 | 12.9412 | 12.0728 | 11.082 | 9.8922 | 8.6688 | 7.7341 | 4.1433 | 1.8382 | 0.37591 | 16.0702 | 15.811 | 15.461 | 15.0682 | 15.0375 | 14.5365 | 13.8916 | 13.1539 | 12.3865 | 11.8355 | 9.5141 | 7.0651 | 0.80489 | 13.0943 | 12.783 | 12.3688 | 11.8851 | 11.781 | 11.0586 | 10.1218 | 9.0524 | 7.9565 | 7.1412 | 3.9902 | 1.8473 | 0.62693
|  | WOOTTON BASSETT | EE |  |  |  | 14.3535 | 14.029 | 13.6055 | 13.129 | 12.9412 | 12.1555 | 11.082 | 9.8922 | 8.6688 | 7.7341 | 4.3698 | 2.3728 | 0.72591 | 16.0702 | 15.811 | 15.461 | 15.0682 | 15.0375 | 14.5365 | 13.8916 | 13.1539 | 12.3865 | 11.8355 | 9.5141 | 7.2804 | 3.9875 | 13.0943 | 12.783 | 12.3688 | 11.8851 | 11.781 | 11.079 | 10.1218 | 9.0524 | 7.9565 | 7.1412 | 4.18 | 2.3269 | 0.91774
|  | WOOTTON BASSETT | HT |  |  |  | 14.5453 | 14.2769 | 13.9484 | 13.6075 | 13.0024 | 12.0728 | 11.2463 | 10.1994 | 9.2147 | 8.2749 | 4.1433 | 1.8382 | 0.37591 | 16.2773 | 16.109 | 15.8875 | 15.6753 | 15.3182 | 14.811 | 14.5233 | 13.9753 | 13.4375 | 12.9182 | 10.7079 | 9.5875 | 8.961 | 13.2851 | 13.0382 | 12.7279 | 12.4137 | 11.8728 | 11.0586 | 10.3841 | 9.4596 | 8.5779 | 7.733 | 3.9902 | 1.8473 | 0.62693
|  | WOOTTON BASSETT | HE |  |  |  | 14.5494 | 14.3086 | 14.0024 | 13.7055 | 13.2157 | 12.4779 | 11.9239 | 10.9453 | 9.9443 | 8.9718 | 5.2555 | 3.1912 | 2.0871 | 16.2488 | 16.062 | 15.8182 | 15.5957 | 15.2488 | 14.7824 | 14.5457 | 13.96 | 13.3447 | 12.7253 | 9.9743 | 7.6518 | 4.5416 | 13.2902 | 13.0626 | 12.7739 | 12.4994 | 12.0535 | 11.3994 | 10.9545 | 10.0933 | 9.2096 | 8.3463 | 4.9943 | 3.0841 | 2.13
|  | WOOTTON BASSETT | CF |  |  |  | 14.6606 | 14.4861 | 14.3228 | 14.1188 | 13.9473 | 13.7055 | 13.4269 | 13.0004 | 12.9341 | 12.3504 | 8.3565 | 6.0004 | 3.8586 | 16.3028 | 16.1345 | 15.9722 | 15.7651 | 15.5835 | 15.3284 | 15.0263 | 14.6202 | 14.5702 | 14.0926 | 10.7835 | 7.0651 | 0.80489 | 13.3933 | 13.2259 | 13.0718 | 12.8739 | 12.7065 | 12.4616 | 12.1779 | 11.7626 | 11.7973 | 11.2841 | 7.7718 | 5.6453 | 3.7422
COWLEY GSP | OXFORD BSP | WOOTTON ROAD | MINIMUM HEADROOM | SU 49244 98269 | YES | 6.297 | -4.1678 | -4.8637 | -5.7331 | -6.1759 | -7.1188 | -8.1994 | -9.8402 | -11.7341 | -13.6219 | -15.181 | -23.3606 | -29.5698 | -31.6168 | -0.40818 | -0.88777 | -1.497 | -1.7296 | -2.3643 | -3.0796 | -4.0643 | -5.2194 | -6.3837 | -7.2643 | -11.9694 | -16.8633 | -26.25 | -3.2565 | -3.8851 | -4.6963 | -5.027 | -5.8821 | -6.8596 | -8.3025 | -9.9759 | -11.6453 | -12.9463 | -19.8137 | -25.0576 | -26.829
|  | WOOTTON ROAD | EE |  |  |  | -4.1678 | -4.8637 | -5.7331 | -6.1759 | -7.1188 | -8.1994 | -9.8402 | -11.7341 | -13.6219 | -15.181 | -23.0708 | -28.8535 | -31.3453 | -0.40818 | -0.88777 | -1.497 | -1.7296 | -2.3643 | -3.0796 | -4.0643 | -5.2194 | -6.3837 | -7.2643 | -11.9694 | -16.4898 | -21.3929 | -3.2565 | -3.8851 | -4.6963 | -5.027 | -5.8821 | -6.8596 | -8.3025 | -9.9759 | -11.6453 | -12.9463 | -19.5514 | -24.4361 | -26.6208
|  | WOOTTON ROAD | HT |  |  |  | -3.9014 | -4.5188 | -5.227 | -5.9494 | -6.8382 | -7.4759 | -8.9963 | -10.727 | -12.4943 | -14.3035 | -23.3606 | -29.5698 | -31.6168 | -0.12247 | -0.4694 | -0.86532 | -1.2949 | -1.8112 | -2.0337 | -2.7878 | -3.6694 | -4.5827 | -5.5296 | -10.048 | -12.8092 | -13.7153 | -2.9606 | -3.5004 | -4.1198 | -4.777 | -5.5759 | -6.0412 | -7.3361 | -8.8137 | -10.3341 | -11.9045 | -19.8137 | -25.0576 | -26.829
|  | WOOTTON ROAD | HE |  |  |  | -3.9076 | -4.4933 | -5.1739 | -5.8719 | -6.7402 | -7.3545 | -8.7157 | -10.2953 | -11.9157 | -13.5647 | -22.0208 | -28.0065 | -29.6219 | -0.17859 | -0.56532 | -1.0051 | -1.4868 | -2.0602 | -2.35 | -3.1398 | -4.0725 | -5.0531 | -6.0745 | -11.5653 | -16.3316 | -20.8878 | -2.9698 | -3.4831 | -4.0841 | -4.7229 | -5.4994 | -5.9474 | -7.1116 | -8.4688 | -9.8668 | -11.2974 | -18.6168 | -23.729 | -25.1147
|  | WOOTTON ROAD | CF |  |  |  | -3.6953 | -4.1065 | -4.6208 | -5.0555 | -5.6668 | -6.379 | -6.9004 | -7.9198 | -8.98 | -10.0668 | -16.7872 | -22.8872 | -26.4259 | -0.067363 | -0.37757 | -0.76838 | -1.1092 | -1.5623 | -2.1 | -2.4184 | -3.1551 | -3.9306 | -4.7459 | -10.0653 | -16.8633 | -26.25 | -2.777 | -3.1382 | -3.5984 | -3.9861 | -4.529 | -5.1647 | -5.5065 | -6.3729 | -7.277 | -8.2096 | -13.979 | -19.0688 | -22.3229
BRAMLEY (FLEE) | COXMOOR WOOD BSP | WRECCLESHAM | MINIMUM HEADROOM | SU 82093 44312 | YES | 1.206 | 19.1888 | 18.8847 | 18.4551 | 17.9959 | 17.9714 | 17.5071 | 16.8041 | 16.0194 | 15.2194 | 14.6776 | 11.3929 | 8.7265 | 7.15 | 21.398 | 21.1622 | 20.8429 | 20.498 | 20.4398 | 20.0663 | 19.5969 | 19.0602 | 18.5051 | 18.1204 | 15.852 | 13.001 | 6.2878 | 18.3398 | 18.0306 | 17.5908 | 17.1153 | 17.1837 | 16.7265 | 16.0684 | 15.3276 | 14.5694 | 14.1102 | 11.2969 | 9.0071 | 7.6163
|  | WRECCLESHAM | EE |  |  |  | 19.1888 | 18.8847 | 18.4551 | 17.9959 | 17.9714 | 17.5071 | 16.8041 | 16.0194 | 15.2194 | 14.6776 | 11.6867 | 9.2765 | 7.4398 | 21.398 | 21.1622 | 20.8429 | 20.498 | 20.4398 | 20.0663 | 19.5969 | 19.0602 | 18.5051 | 18.1204 | 15.852 | 13.3541 | 9.7418 | 18.3398 | 18.0306 | 17.5908 | 17.1153 | 17.1837 | 16.7265 | 16.0684 | 15.3276 | 14.5694 | 14.1102 | 11.5378 | 9.4908 | 7.8582
|  | WRECCLESHAM | HT |  |  |  | 19.3857 | 19.1347 | 18.7806 | 18.4908 | 18.1163 | 17.6745 | 17.3878 | 16.6878 | 15.9541 | 15.199 | 11.3929 | 8.7265 | 7.15 | 21.5694 | 21.4255 | 21.2102 | 21.0306 | 20.7878 | 20.4929 | 20.3959 | 20.0184 | 19.6122 | 19.1939 | 17.2163 | 16.049 | 15.3857 | 18.5602 | 18.3194 | 17.9745 | 17.6969 | 17.3235 | 16.8847 | 16.7276 | 16.0847 | 15.4112 | 14.7184 | 11.2969 | 9.0071 | 7.6163
|  | WRECCLESHAM | HE |  |  |  | 19.3908 | 19.1582 | 18.8378 | 18.5663 | 18.2112 | 17.7959 | 17.6449 | 17.0929 | 16.5031 | 15.8918 | 12.6592 | 10.3337 | 9.1531 | 21.5337 | 21.3571 | 21.1163 | 20.901 | 20.6153 | 20.2806 | 20.1796 | 19.7898 | 19.3622 | 18.9112 | 16.3122 | 13.8102 | 10.4541 | 18.5602 | 18.3357 | 18.0184 | 17.7561 | 17.399 | 16.9837 | 16.9582 | 16.4429 | 15.8929 | 15.3235 | 12.3878 | 10.4306 | 9.402
|  | WRECCLESHAM | CF |  |  |  | 19.4939 | 19.3582 | 19.1673 | 19.0194 | 18.8 | 18.5378 | 18.2714 | 18.3724 | 18.1071 | 17.8306 | 15.7327 | 13.4908 | 11.352 | 21.5878 | 21.45 | 21.2694 | 21.0969 | 20.8745 | 20.5857 | 20.2878 | 20.2255 | 19.898 | 19.5541 | 16.9918 | 13.001 | 6.2878 | 18.6541 | 18.5184 | 18.3204 | 18.1612 | 17.9337 | 17.6602 | 17.3847 | 17.5531 | 17.2867 | 17.0051 | 15.0092 | 13.0898 | 11.252
MINETY GSP | TOOTHILL BSP | WROUGHTON | MINIMUM HEADROOM | SU 14446 81504 | YES | 1.284 | 14.6416 | 13.8498 | 12.9743 | 12.21 | 11.3773 | 10.4233 | 9.4018 | 8.3753 | 7.5202 | 7.0324 | 4.0233 | 2.1324 | 0.98347 | 17.2845 | 16.7967 | 16.2518 | 15.8488 | 15.3998 | 14.8324 | 14.261 | 13.4192 | 12.7029 | 12.0467 | 9.8243 | 8.0886 | 5.6345 | 15.1294 | 14.459 | 13.6906 | 13.0549 | 12.3518 | 11.5131 | 10.5447 | 9.4978 | 8.6192 | 8.1284 | 5.1641 | 3.3202 | 2.1896
|  | WROUGHTON | EE |  |  |  | 14.6416 | 13.8498 | 12.9743 | 12.21 | 11.3773 | 10.4233 | 9.662 | 8.6896 | 7.8345 | 7.0845 | 4.4641 | 2.8835 | 1.6345 | 17.2845 | 16.7967 | 16.2518 | 15.8488 | 15.3998 | 14.8324 | 14.2865 | 13.4488 | 12.7029 | 12.0467 | 9.8243 | 8.0886 | 5.7294 | 15.1294 | 14.459 | 13.6906 | 13.0549 | 12.3518 | 11.5131 | 10.811 | 9.8131 | 8.9304 | 8.1692 | 5.6304 | 4.1488 | 2.9355
|  | WROUGHTON | HT |  |  |  | 14.7202 | 13.9498 | 13.1069 | 12.3733 | 11.4539 | 10.4998 | 9.4018 | 8.3753 | 7.5202 | 7.0324 | 4.0233 | 2.1324 | 0.98347 | 17.3784 | 16.9324 | 16.4447 | 16.1039 | 15.6018 | 15.0722 | 14.261 | 13.4192 | 12.7304 | 12.3376 | 10.2008 | 8.8947 | 8.0396 | 15.2222 | 14.5763 | 13.8488 | 13.262 | 12.461 | 11.6131 | 10.5447 | 9.4978 | 8.6192 | 8.1284 | 5.1641 | 3.3202 | 2.1896
|  | WROUGHTON | HE |  |  |  | 14.7284 | 13.9753 | 13.1447 | 12.4263 | 11.6529 | 10.8008 | 9.9212 | 9.0753 | 8.3876 | 8.0222 | 5.4253 | 3.8304 | 2.7998 | 17.3641 | 16.9069 | 16.4018 | 16.0478 | 15.6539 | 15.1763 | 14.5376 | 13.8233 | 13.2478 | 12.9049 | 10.6069 | 8.8376 | 6.5569 | 15.2273 | 14.5947 | 13.8773 | 13.3029 | 12.6651 | 11.9202 | 11.0876 | 10.2386 | 9.5508 | 9.1906 | 6.6529 | 5.1488 | 4.1253
|  | WROUGHTON | CF |  |  |  | 14.8029 | 14.1345 | 13.4294 | 12.8447 | 12.2253 | 11.6192 | 11.0702 | 10.5284 | 10.0141 | 9.5192 | 7.658 | 6.2345 | 4.9253 | 17.3998 | 16.9722 | 16.5202 | 16.2131 | 15.8763 | 15.5396 | 15.0988 | 14.5651 | 14.0386 | 13.5284 | 11.4814 | 9.2569 | 5.6345 | 15.2957 | 14.7355 | 14.1253 | 13.6671 | 13.1661 | 12.6702 | 12.1671 | 11.609 | 11.0722 | 10.558 | 8.7488 | 7.4794 | 6.3355
AMERSHAM | LOUDWATER BSP | WYCOMBE MARSH | MINIMUM HEADROOM | SU 88582 91845 | YES | 4.145 | 3.7353 | 3.2496 | 2.6802 | 2.1598 | 1.6383 | 1.4638 | 0.79649 | 0.040367 | -0.71984 | -1.2913 | -4.277 | -6.6668 | -7.8953 | 8.5455 | 8.2047 | 7.8128 | 7.4189 | 6.9985 | 6.8975 | 6.4189 | 5.8557 | 5.2781 | 4.8638 | 2.6475 | 0.084245 | -6.5168 | 5.9118 | 5.4567 | 4.9342 | 4.4251 | 3.8924 | 3.8138 | 3.1802 | 2.4567 | 1.7251 | 1.2087 | -1.3107 | -3.3678 | -4.4627
|  | WYCOMBE MARSH | EE |  |  |  | 3.7353 | 3.2496 | 2.6802 | 2.1598 | 1.6383 | 1.4638 | 0.79649 | 0.040367 | -0.71984 | -1.2913 | -4.1882 | -6.1607 | -7.7107 | 8.5455 | 8.2047 | 7.8128 | 7.4189 | 6.9985 | 6.8975 | 6.4189 | 5.8557 | 5.2781 | 4.8638 | 2.6475 | 0.33118 | -3.1331 | 5.9118 | 5.4567 | 4.9342 | 4.4251 | 3.8924 | 3.8138 | 3.1802 | 2.4567 | 1.7251 | 1.2087 | -1.2902 | -2.9198 | -4.3056
|  | WYCOMBE MARSH | HT |  |  |  | 3.8608 | 3.4608 | 2.9853 | 2.5781 | 2.2179 | 1.7924 | 1.1649 | 0.4669 | 0.12404 | -0.56473 | -4.277 | -6.6668 | -7.8953 | 8.7067 | 8.471 | 8.1985 | 7.9506 | 7.7291 | 7.4475 | 7.0761 | 6.6475 | 6.5536 | 6.1404 | 4.1047 | 2.9557 | 2.4363 | 6.1006 | 5.7302 | 5.3036 | 4.9128 | 4.5791 | 4.1669 | 3.5822 | 2.922 | 2.6771 | 2.0393 | -1.3107 | -3.3678 | -4.4627
|  | WYCOMBE MARSH | HE |  |  |  | 3.8638 | 3.4781 | 3.0189 | 2.6393 | 2.3067 | 1.9108 | 1.3873 | 0.79343 | 0.54955 | -0.02902 | -3.0994 | -5.1535 | -6.0413 | 8.6751 | 8.4138 | 8.1098 | 7.8353 | 7.5822 | 7.2761 | 6.8914 | 6.4353 | 6.2955 | 5.8516 | 3.2985 | 0.88016 | -2.2719 | 6.0944 | 5.7424 | 5.3353 | 4.9689 | 4.6587 | 4.2771 | 3.7842 | 3.2118 | 3.0567 | 2.5159 | -0.26371 | -2.0096 | -2.7525
|  | WYCOMBE MARSH | CF |  |  |  | 3.9751 | 3.7108 | 3.3557 | 3.1383 | 2.9087 | 2.6996 | 2.4883 | 2.2189 | 1.9179 | 1.5832 | -0.064735 | -2.2137 | -4.1943 | 8.7281 | 8.5271 | 8.2547 | 8.0618 | 7.8393 | 7.6169 | 7.3465 | 7.0087 | 6.6414 | 6.2444 | 4.0026 | 0.084245 | -6.5168 | 6.1985 | 5.9598 | 5.6271 | 5.42 | 5.1873 | 4.9914 | 4.7669 | 4.4812 | 4.1638 | 3.8271 | 2.3679 | 0.4618 | -1.2239
LOVEDEAN GSP | WYMERING BSP | WYMERING | MINIMUM HEADROOM | SU 64974 05375 | YES | 15.722 | 23.3669 | 22.4649 | 21.4588 | 19.9639 | 18.2782 | 16.37 | 14.1751 | 11.5802 | 9.0965 | 7.0282 | -4.4157 | -9.2331 | -10.0106 | 24.5098 | 23.8904 | 23.2302 | 22.1026 | 20.8108 | 19.3945 | 17.821 | 15.9414 | 14.1424 | 12.6669 | 3.7526 | 0.10264 | -6.9504 | 23.9128 | 23.1853 | 22.2404 | 20.8057 | 19.1863 | 17.3649 | 15.2792 | 12.8077 | 10.4455 | 8.4812 | -2.5178 | -7.1178 | -7.8474
|  | WYMERING | EE |  |  |  | 23.3669 | 22.4649 | 21.4588 | 19.9639 | 18.2782 | 16.37 | 14.1751 | 11.5802 | 9.0965 | 7.0282 | -0.44226 | -2.2076 | -2.3249 | 24.5098 | 23.8904 | 23.2302 | 22.1026 | 20.8108 | 19.3945 | 17.821 | 15.9414 | 14.1424 | 12.6669 | 6.9914 | 5.769 | 1.0863 | 23.9128 | 23.1853 | 22.2404 | 20.8057 | 19.1863 | 17.3649 | 15.2792 | 12.8077 | 10.4455 | 8.4812 | 1.4241 | -0.17491 | -0.2943
|  | WYMERING | HT |  |  |  | 23.9945 | 23.3904 | 22.7006 | 21.9006 | 20.8414 | 19.8822 | 18.3547 | 16.5312 | 14.6016 | 12.4986 | 3.1965 | -0.70144 | -1.4433 | 25.0139 | 24.6282 | 24.1955 | 23.6945 | 23.0843 | 22.2251 | 21.1782 | 19.8986 | 18.5404 | 16.9506 | 10.0384 | 7.3016 | 6.6598 | 24.5506 | 24.0608 | 23.4649 | 22.7792 | 21.9077 | 20.7802 | 19.3343 | 17.6037 | 15.7741 | 13.7659 | 4.921 | 1.2639 | 0.58223
|  | WYMERING | HE |  |  |  | 23.8751 | 23.2363 | 22.419 | 21.1057 | 19.5843 | 17.9424 | 15.9577 | 13.5282 | 10.9465 | 8.2567 | -4.4157 | -9.2331 | -10.0106 | 24.8526 | 24.3506 | 23.7496 | 22.9802 | 21.8118 | 20.5986 | 19.1669 | 17.3904 | 15.4986 | 13.52 | 3.7526 | 0.10264 | -0.79226 | 24.3394 | 23.7455 | 23.0394 | 21.9098 | 20.4486 | 18.8822 | 16.9904 | 14.669 | 12.1986 | 9.622 | -2.5178 | -7.1178 | -7.8474
|  | WYMERING | CF |  |  |  | 24.2863 | 23.8843 | 23.3771 | 22.9261 | 22.3363 | 21.4873 | 20.6353 | 19.371 | 17.969 | 16.4771 | 7.9455 | -0.50144 | -4.7382 | 25.1679 | 24.7822 | 24.3679 | 23.9679 | 23.4373 | 22.8526 | 22.3782 | 21.5526 | 20.4904 | 19.3639 | 12.9455 | 5.2904 | -6.9504 | 24.7853 | 24.3975 | 23.9547 | 23.5098 | 22.9363 | 22.269 | 21.4618 | 20.2496 | 18.9037 | 17.4761 | 9.2812 | 1.2333 | -2.7494
COWLEY GSP | YARNTON BSP | YARNTON | MINIMUM HEADROOM | SP 48277 12108 | YES | 38.45 | -10.9771 | -13.3649 | -15.4475 | -16.772 | -18.4067 | -21.2263 | -23.2314 | -25.6335 | -27.908 | -29.7682 | -40.5753 | -45.6978 | -46.8998 | -4.7312 | -6.7373 | -8.4914 | -9.473 | -10.6975 | -13.0569 | -14.5243 | -16.2947 | -17.9733 | -19.3263 | -27.3212 | -30.961 | -31.8957 | -10.6006 | -12.8465 | -14.8802 | -16.1475 | -17.721 | -20.4631 | -22.3804 | -24.6835 | -26.8651 | -28.6416 | -38.9947 | -43.8386 | -44.9304
|  | YARNTON | EE |  |  |  | -10.9771 | -13.3649 | -15.4475 | -16.772 | -18.4067 | -21.2263 | -23.2314 | -25.6335 | -27.908 | -29.7682 | -35.8712 | -37.5529 | -38.6702 | -4.7312 | -6.7373 | -8.4914 | -9.473 | -10.6975 | -13.0569 | -14.5243 | -16.2947 | -17.9733 | -19.3263 | -23.5233 | -24.461 | -26.5488 | -10.6006 | -12.8465 | -14.8802 | -16.1475 | -17.721 | -20.4631 | -22.3804 | -24.6835 | -26.8651 | -28.6416 | -34.4049 | -35.9131 | -36.8131
|  | YARNTON | HT |  |  |  | -9.9179 | -11.8955 | -13.4832 | -14.4057 | -15.4618 | -17.5702 | -18.962 | -20.6457 | -22.4171 | -24.2498 | -32.3886 | -36.2682 | -37.9916 | -3.9067 | -5.5863 | -6.9506 | -7.621 | -8.3934 | -10.1855 | -11.1651 | -12.3661 | -13.6386 | -14.9518 | -20.6671 | -23.1069 | -23.812 | -9.77 | -11.6985 | -13.1394 | -13.8842 | -14.87 | -16.9182 | -18.2416 | -19.8447 | -21.5376 | -23.2845 | -31.0202 | -34.5202 | -35.8988
|  | YARNTON | HE |  |  |  | -10.2802 | -12.4965 | -14.3822 | -15.6638 | -17.1516 | -19.7722 | -21.6508 | -23.9722 | -26.4396 | -29.01 | -40.5753 | -45.6978 | -46.8998 | -4.1924 | -6.0649 | -7.6659 | -8.6179 | -9.7291 | -11.9263 | -13.311 | -15.0355 | -16.8722 | -18.7916 | -27.3212 | -30.961 | -31.8957 | -9.9791 | -12.0291 | -13.8475 | -15.0761 | -16.5098 | -19.0529 | -20.8529 | -23.0814 | -25.4478 | -27.9171 | -38.9947 | -43.8386 | -44.9304
|  | YARNTON | CF |  |  |  | -9.6567 | -11.4373 | -12.8424 | -13.5271 | -14.3291 | -16.2682 | -17.0376 | -18.2212 | -19.5508 | -20.9529 | -29.2722 | -36.2825 | -40.0376 | -3.7057 | -5.2894 | -6.5424 | -7.0547 | -7.6618 | -9.362 | -9.9488 | -10.858 | -11.8763 | -12.9539 | -19.2467 | -24.458 | -31.8539 | -9.5577 | -11.2945 | -12.5812 | -13.0445 | -13.8006 | -15.6957 | -16.4345 | -17.5763 | -18.8569 | -20.2049 | -28.1988 | -34.8774 | -38.3876
BRAMLEY (ANDO-THAT) | THATCHAM BSP | YATTENDON | MINIMUM HEADROOM | SU 53699 74307 | YES | 1.18 | 5.6605 | 5.4666 | 5.2085 | 4.8411 | 4.4003 | 3.2432 | 2.4462 | 1.683 | -0.36806 | -1.4987 | -5.2742 | -8.8109 | -12.9874 | 8.2824 | 8.21 | 8.062 | 7.6131 | 7.2682 | 6.0243 | 5.2937 | 4.5396 | 2.1722 | 0.80388 | -3.0553 | -7.5512 | -13.5798 | 5.2712 | 5.0865 | 4.8416 | 4.3855 | 3.9498 | 2.6212 | 1.7753 | 0.93041 | -1.5227 | -2.8931 | -7.0471 | -11.2247 | -16.338
|  | YATTENDON | EE |  |  |  | 5.6605 | 5.4666 | 5.2085 | 4.9809 | 4.5758 | 3.9013 | 3.5217 | 3.1166 | 2.3442 | 1.8983 | -0.73235 | -5.6038 | -7.4089 | 8.2824 | 8.21 | 8.0702 | 7.9029 | 7.6376 | 7.0457 | 6.7161 | 6.4376 | 5.6733 | 5.2559 | 2.6937 | -3.4849 | -6.5267 | 5.2712 | 5.0865 | 4.8416 | 4.6243 | 4.2559 | 3.5569 | 3.162 | 2.7773 | 1.9304 | 1.4549 | -1.341 | -7.2053 | -9.3471
|  | YATTENDON | HT |  |  |  | 5.7432 | 5.5891 | 5.3319 | 5.0085 | 4.6758 | 3.7064 | 2.8983 | 2.0972 | 1.636 | 1.1126 | -2.1395 | -6.8915 | -10.3007 | 8.3457 | 8.2916 | 8.1324 | 7.8702 | 7.6947 | 6.7049 | 5.9937 | 5.2324 | 4.8876 | 4.3243 | 1.2549 | -4.1278 | -8.0216 | 5.3855 | 5.2365 | 4.9518 | 4.5957 | 4.2967 | 3.1998 | 2.3437 | 1.46 | 0.9998 | 0.39776 | -3.189 | -8.838 | -12.8971
|  | YATTENDON | HE |  |  |  | 5.7381 | 5.5881 | 5.2911 | 4.8411 | 4.4003 | 3.2432 | 2.4462 | 1.683 | -0.36806 | -1.4987 | -5.2742 | -8.8109 | -12.9874 | 8.3345 | 8.2773 | 8.062 | 7.6131 | 7.2682 | 6.0243 | 5.2937 | 4.5396 | 2.1722 | 0.80388 | -3.0553 | -7.5512 | -13.5798 | 5.3804 | 5.2345 | 4.9029 | 4.3855 | 3.9498 | 2.6212 | 1.7753 | 0.93041 | -1.5227 | -2.8931 | -7.0471 | -11.2247 | -16.338
|  | YATTENDON | CF |  |  |  | 5.7789 | 5.6523 | 5.5095 | 5.386 | 5.0401 | 4.6483 | 4.235 | 3.9054 | 3.5717 | 3.1687 | 1.2095 | -1.3334 | -3.7262 | 8.3671 | 8.3304 | 8.2845 | 8.2059 | 7.9253 | 7.5906 | 7.2253 | 6.9008 | 6.559 | 6.1437 | 3.8345 | 0.34163 | -3.9829 | 5.4243 | 5.3039 | 5.161 | 5.0437 | 4.7039 | 4.3069 | 3.8967 | 3.5467 | 3.1886 | 2.7569 | 0.59776 | -2.2471 | -4.9094
MELKSHAM GSP | CHIPPENHAM | YATTON KEYNELL | MINIMUM HEADROOM | ST 87300 75782 | YES | 0.539 | 0.72347 | -0.031633 | -0.92143 | -1.9714 | -3.2163 | -4.6408 | -6.2684 | -8.2918 | -10.2235 | -12.1082 | -22.249 | -25.8061 | -25.9541 | 2.1214 | 1.5908 | 0.91429 | 0.11429 | -0.83776 | -1.9255 | -3.1622 | -4.7 | -6.1704 | -7.6061 | -15.3163 | -18.0133 | -18.1367 | 0.80408 | 0.14082 | -0.71735 | -1.7316 | -2.9347 | -4.3112 | -5.8837 | -7.8347 | -9.701 | -11.5214 | -21.3061 | -24.7327 | -24.8684
|  | YATTON KEYNELL | EE |  |  |  | 0.72347 | -0.031633 | -0.92143 | -1.9714 | -3.2163 | -4.6408 | -6.2684 | -8.2918 | -10.2235 | -12.1082 | -19.5082 | -23.1398 | -24.1265 | 2.1214 | 1.5908 | 0.91429 | 0.11429 | -0.83776 | -1.9255 | -3.1622 | -4.7 | -6.1704 | -7.6061 | -13.1949 | -15.9398 | -16.6939 | 0.80408 | 0.14082 | -0.71735 | -1.7316 | -2.9347 | -4.3112 | -5.8837 | -7.8347 | -9.701 | -11.5214 | -18.652 | -22.149 | -23.0939
|  | YATTON KEYNELL | HT |  |  |  | 1.2939 | 0.99592 | 0.39796 | -0.34388 | -1.2429 | -2.3122 | -3.5684 | -5.1418 | -6.8276 | -8.6378 | -16.3929 | -20.5071 | -22.0031 | 2.6939 | 2.3327 | 1.9082 | 1.3694 | 0.68571 | -0.12857 | -1.0796 | -2.2694 | -3.548 | -4.9235 | -10.7908 | -13.8898 | -14.9959 | 1.501 | 1.048 | 0.51531 | -0.15612 | -1.0245 | -2.0551 | -3.2704 | -4.7867 | -6.4153 | -8.1633 | -15.6378 | -19.602 | -21.0367
|  | YATTON KEYNELL | HE |  |  |  | 1.2092 | 0.7102 | -0.079592 | -1.0378 | -2.1796 | -3.5714 | -5.2092 | -7.2918 | -9.5337 | -11.7327 | -22.249 | -25.8061 | -25.9541 | 2.5602 | 2.1194 | 1.5633 | 0.83163 | -0.037755 | -1.1 | -2.3459 | -3.9337 | -5.6418 | -7.3184 | -15.3163 | -18.0133 | -18.1367 | 1.3439 | 0.79184 | 0.096939 | -0.83061 | -1.9306 | -3.2765 | -4.8551 | -6.8673 | -9.0347 | -11.1551 | -21.3061 | -24.7327 | -24.8684
|  | YATTON KEYNELL | CF |  |  |  | 1.4867 | 1.3102 | 1.0806 | 0.78265 | 0.2398 | -0.40918 | -1.1265 | -2.1184 | -3.25 | -4.45 | -11.6255 | -17.9939 | -21.7714 | 2.9704 | 2.7694 | 2.4949 | 2.1704 | 1.7898 | 1.3092 | 0.76327 | 0.005102 | -0.85918 | -1.7786 | -7.2633 | -12.1235 | -15.0214 | 1.6816 | 1.5133 | 1.2541 | 0.84898 | 0.37449 | -0.22347 | -0.91531 | -1.8724 | -2.9653 | -4.1265 | -11.0551 | -17.2 | -20.8337
AXMINSTER | YEOVIL BSP | YEOVIL | MINIMUM HEADROOM | ST 57690 16833 | YES | 5.272 | 26.9786 | 23.3444 | 22.7485 | 22.6148 | 22.0669 | 21.4842 | 20.5873 | 19.5689 | 18.5464 | 17.876 | 14.0209 | 10.373 | 8.1424 | 26.5776 | 23.0771 | 22.6536 | 22.5883 | 22.1781 | 21.7281 | 21.1158 | 20.4067 | 19.6801 | 19.1842 | 16.1577 | 11.6209 | 0.9689 | 26.1204 | 22.5689 | 22.0975 | 21.9158 | 21.4618 | 20.9862 | 20.1883 | 19.3056 | 18.4087 | 17.7373 | 13.8975 | 10.6699 | 8.8199
|  | YEOVIL | EE |  |  |  | 26.9786 | 23.3444 | 22.7485 | 22.6148 | 22.0669 | 21.4842 | 20.5873 | 19.5689 | 18.5464 | 17.876 | 14.175 | 10.9383 | 8.3883 | 26.5776 | 23.0771 | 22.6536 | 22.5883 | 22.1781 | 21.7281 | 21.1158 | 20.4067 | 19.6801 | 19.1842 | 16.1577 | 12.3046 | 6.5311 | 26.1204 | 22.5689 | 22.0975 | 21.9158 | 21.4618 | 20.9862 | 20.1883 | 19.3056 | 18.4087 | 17.7373 | 13.9995 | 11.1832 | 9.024
|  | YEOVIL | HT |  |  |  | 27.2714 | 23.7342 | 23.2903 | 22.8791 | 22.3964 | 21.8771 | 21.6067 | 20.8067 | 19.9679 | 19.0944 | 14.0209 | 10.373 | 8.1424 | 26.7398 | 23.4169 | 23.1352 | 22.8791 | 22.5658 | 22.225 | 22.1811 | 21.7291 | 21.2495 | 20.7403 | 18.0924 | 16.5985 | 15.7924 | 26.3184 | 22.8291 | 22.4536 | 22.1005 | 21.6964 | 21.2658 | 20.8689 | 20.1271 | 19.3536 | 18.5567 | 13.8975 | 10.6699 | 8.8199
|  | YEOVIL | HE |  |  |  | 27.2622 | 23.7516 | 23.3322 | 22.9475 | 22.5026 | 22.026 | 21.8618 | 21.1801 | 20.4648 | 19.725 | 15.6699 | 12.5199 | 11.0505 | 26.7367 | 23.3781 | 23.0832 | 22.8169 | 22.4873 | 22.1077 | 21.9403 | 21.4648 | 20.9546 | 20.4148 | 16.9403 | 13.1067 | 7.7791 | 26.3133 | 22.8403 | 22.4873 | 22.1577 | 21.7801 | 21.3842 | 21.0964 | 20.4699 | 19.8199 | 19.1516 | 15.3862 | 12.6873 | 11.474
|  | YEOVIL | CF |  |  |  | 27.4378 | 24.0485 | 23.8424 | 23.5781 | 23.324 | 22.9954 | 22.6516 | 22.7516 | 22.4332 | 22.1005 | 19.4638 | 16.8924 | 14.2454 | 26.8194 | 23.5138 | 23.324 | 23.0954 | 22.8373 | 22.5097 | 22.1311 | 21.9383 | 21.5281 | 21.0944 | 17.6301 | 11.6209 | 0.9689 | 26.4806 | 23.1362 | 22.9699 | 22.7679 | 22.5597 | 22.2985 | 22.0322 | 22.0454 | 21.7934 | 21.5301 | 19.2322 | 16.6424 | 14.1485
AXMINSTER | YEOVIL BSP | YETMINSTER | MINIMUM HEADROOM | ST 60294 10206 | YES | 0.618 | 8.3122 | 8.1276 | 7.8602 | 7.6398 | 7.3408 | 7.0255 | 7.0918 | 6.7418 | 6.3929 | 6.1745 | 4.5878 | 3.5031 | 3.1878 | 10.0512 | 9.9176 | 9.7227 | 9.5584 | 9.3359 | 9.0961 | 9.1931 | 8.9369 | 8.6788 | 8.539 | 7.6278 | 6.391 | 4.1757 | 8.4708 | 8.3524 | 8.1157 | 7.9137 | 7.6433 | 7.3545 | 7.4065 | 7.081 | 6.7545 | 6.5667 | 5.281 | 4.4157 | 4.1484
|  | YETMINSTER | EE |  |  |  | 8.3122 | 8.1276 | 7.8602 | 7.6398 | 7.3408 | 7.0255 | 7.0918 | 6.7418 | 6.3929 | 6.1745 | 4.5878 | 3.5031 | 3.3418 | 10.0512 | 9.9176 | 9.7227 | 9.5584 | 9.3359 | 9.0961 | 9.1931 | 8.9369 | 8.6788 | 8.539 | 7.6278 | 6.6727 | 5.6176 | 8.4708 | 8.3524 | 8.1157 | 7.9137 | 7.6433 | 7.3545 | 7.4065 | 7.081 | 6.7545 | 6.5667 | 5.281 | 4.4157 | 4.2769
|  | YETMINSTER | HT |  |  |  | 8.3673 | 8.2316 | 8.0837 | 7.9255 | 7.7061 | 7.5296 | 7.2337 | 6.9 | 6.548 | 6.6163 | 4.849 | 3.5714 | 3.1878 | 10.1094 | 10.0431 | 9.94 | 9.842 | 9.6971 | 9.5839 | 9.3992 | 9.1818 | 8.9461 | 9.1022 | 8.1451 | 7.5441 | 7.3665 | 8.531 | 8.429 | 8.3065 | 8.178 | 7.98 | 7.8198 | 7.5514 | 7.2524 | 6.931 | 7.0249 | 5.4953 | 4.4545 | 4.1484
|  | YETMINSTER | HE |  |  |  | 8.3643 | 8.2296 | 8.0786 | 7.9327 | 7.7194 | 7.548 | 7.2633 | 6.9367 | 6.5918 | 6.6745 | 4.752 | 3.6796 | 3.5398 | 10.1063 | 10.042 | 9.9104 | 9.8022 | 9.6522 | 9.5267 | 9.3257 | 9.0931 | 8.841 | 8.9788 | 7.7584 | 6.792 | 5.7482 | 8.5259 | 8.4239 | 8.3004 | 8.1729 | 7.9943 | 7.8402 | 7.5831 | 7.2871 | 6.9769 | 7.081 | 5.4504 | 4.5912 | 4.4759
|  | YETMINSTER | CF |  |  |  | 8.3959 | 8.2786 | 8.152 | 8.0367 | 7.8796 | 7.7 | 7.501 | 7.3378 | 7.1051 | 6.8622 | 5.7551 | 4.3316 | 3.6959 | 10.1267 | 10.0716 | 9.9676 | 9.8788 | 9.7492 | 9.6104 | 9.4512 | 9.3073 | 9.1114 | 8.9002 | 7.9798 | 6.391 | 4.1757 | 8.5647 | 8.4851 | 8.3718 | 8.2688 | 8.1463 | 7.9902 | 7.8157 | 7.6698 | 7.4637 | 7.2463 | 6.28 | 5.1076 | 4.6004
AXMINSTER |  | YIEWSLEY | MINIMUM HEADROOM | TQ 05643 80961 | YES | 15.839 | 21.2424 | 20.3842 | 19.9301 | 18.924 | 17.7811 | 16.5342 | 14.472 | 12.1056 | 9.8434 | 8.1464 | 1.1056 | -4.0536 | -5.124 | 27.0771 | 26.3893 | 26.022 | 25.2169 | 24.2873 | 23.2638 | 21.6403 | 19.7352 | 17.9342 | 16.5495 | 10.5332 | 5.0556 | -9.1546 | 21.6832 | 20.8556 | 20.4403 | 19.4781 | 18.3852 | 17.1873 | 15.1444 | 12.7842 | 10.5505 | 8.8087 | 2.2699 | -2.4331 | -3.5107
|  | YIEWSLEY | EE |  |  |  | 21.2424 | 20.3842 | 19.9301 | 18.924 | 17.7811 | 16.5342 | 14.472 | 12.1056 | 9.8434 | 8.1464 | 1.1056 | -2.7515 | -2.9648 | 27.0771 | 26.3893 | 26.022 | 25.2169 | 24.2873 | 23.2638 | 21.6403 | 19.7352 | 17.9342 | 16.5495 | 10.5332 | 5.0556 | -2.2352 | 21.6832 | 20.8556 | 20.4403 | 19.4781 | 18.3852 | 17.1873 | 15.1444 | 12.7842 | 10.5505 | 8.8087 | 2.2699 | -1.0903 | -1.5352
|  | YIEWSLEY | HT |  |  |  | 21.772 | 21.1852 | 20.4158 | 19.5464 | 19.1556 | 18.2169 | 16.5536 | 14.6811 | 12.7587 | 10.7322 | 1.3056 | -4.0536 | -5.124 | 27.5669 | 27.175 | 26.6464 | 26.0475 | 25.8413 | 25.1893 | 24.0097 | 22.6393 | 21.3087 | 19.8893 | 13.7291 | 10.4964 | 9.3975 | 22.2138 | 21.6597 | 20.9393 | 20.122 | 19.7036 | 18.8097 | 17.1383 | 15.2485 | 13.3822 | 11.422 | 2.4842 | -2.4331 | -3.5107
|  | YIEWSLEY | HE |  |  |  | 21.7771 | 21.2077 | 20.5699 | 19.8016 | 19.5087 | 18.6934 | 17.3016 | 15.7097 | 14.173 | 12.5169 | 5.5434 | 2.0669 | 0.94339 | 27.5005 | 27.0393 | 26.5179 | 25.8944 | 25.6434 | 24.9618 | 23.8669 | 22.5771 | 21.3964 | 20.1128 | 13.6311 | 8.1689 | 0.75053 | 22.2138 | 21.6709 | 21.0709 | 20.3434 | 20.024 | 19.2424 | 17.8516 | 16.2505 | 14.7648 | 13.1954 | 6.5883 | 3.4842 | 2.3709
|  | YIEWSLEY | CF |  |  |  | 22.0434 | 21.7434 | 21.3597 | 20.8944 | 20.3577 | 20.2964 | 19.6362 | 18.8016 | 17.9424 | 17.075 | 12.126 | 7.0505 | 2.1679 | 27.6424 | 27.326 | 26.9311 | 26.4618 | 25.9199 | 25.7158 | 24.9373 | 23.9658 | 22.9709 | 21.9567 | 15.7526 | 6.3822 | -9.1546 | 22.4618 | 22.174 | 21.8056 | 21.3597 | 20.8464 | 20.8107 | 20.1536 | 19.3077 | 18.4444 | 17.5832 | 12.8403 | 8.0516 | 3.8291
LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | ZETLAND ROAD | MINIMUM HEADROOM | SU 60592 00043 | YES | 4.708 | 7.3334 | 6.7232 | 5.9262 | 5.4548 | 4.5773 | 3.616 | 2.2018 | 0.55277 | -1.0258 | -2.2003 | -8.2482 | -13.2646 | -16.3074 | 11.0783 | 10.5987 | 9.9711 | 9.5824 | 8.8885 | 8.1456 | 7.1538 | 5.9191 | 4.6844 | 3.7324 | -1.5972 | -9.0238 | -26.1819 | 8.516 | 7.8824 | 7.0446 | 6.6109 | 5.7058 | 4.762 | 3.4324 | 1.8671 | 0.35685 | -0.71458 | -6.0248 | -10.3901 | -12.8717
|  | ZETLAND ROAD | EE |  |  |  | 7.3334 | 6.7232 | 5.9262 | 5.4548 | 4.5773 | 3.616 | 2.2018 | 0.55277 | -1.0258 | -2.2003 | -8.2482 | -12.6156 | -16.0891 | 11.0783 | 10.5987 | 9.9711 | 9.5824 | 8.8885 | 8.1456 | 7.1538 | 5.9191 | 4.6844 | 3.7324 | -1.5972 | -7.4513 | -16.5666 | 8.516 | 7.8824 | 7.0446 | 6.6109 | 5.7058 | 4.762 | 3.4324 | 1.8671 | 0.35685 | -0.71458 | -6.0248 | -9.786 | -12.7074
|  | ZETLAND ROAD | HT |  |  |  | 7.6824 | 7.1915 | 6.5997 | 5.9334 | 5.2038 | 4.7854 | 3.6671 | 2.4232 | 1.1773 | -0.15539 | -7.7921 | -13.2646 | -16.3074 | 11.3956 | 11.0966 | 10.713 | 10.2966 | 9.863 | 9.6385 | 9.0507 | 8.3742 | 7.6681 | 6.8915 | 2.5926 | -0.12274 | -1.3574 | 8.9089 | 8.4558 | 7.8773 | 7.215 | 6.4844 | 6.1293 | 5.0895 | 3.9109 | 2.7171 | 1.4691 | -5.4972 | -10.3901 | -12.8717
|  | ZETLAND ROAD | HE |  |  |  | 7.6344 | 7.1507 | 6.5732 | 5.9487 | 5.2283 | 4.8303 | 3.8007 | 2.5885 | 1.416 | 0.24665 | -6.2003 | -10.7197 | -12.5431 | 11.2915 | 10.9109 | 10.4354 | 9.9354 | 9.3456 | 8.9834 | 8.2538 | 7.3864 | 6.4915 | 5.5293 | -0.32274 | -6.4564 | -14.8462 | 8.863 | 8.413 | 7.8558 | 7.2334 | 6.5201 | 6.1905 | 5.2405 | 4.1069 | 2.9824 | 1.8507 | -4.0544 | -7.8942 | -9.4003
|  | ZETLAND ROAD | CF |  |  |  | 8.0313 | 7.713 | 7.3405 | 7.0507 | 6.6752 | 6.3018 | 6.2007 | 5.7232 | 5.165 | 4.5773 | 0.20889 | -4.2421 | -8.1738 | 11.515 | 11.1701 | 10.7711 | 10.4222 | 9.964 | 9.463 | 9.1018 | 8.4446 | 7.7181 | 6.8997 | 0.8844 | -9.0238 | -26.1819 | 9.213 | 8.912 | 8.5415 | 8.2344 | 7.8334 | 7.4252 | 7.3711 | 6.8732 | 6.2997 | 5.7018 | 1.5956 | -2.3544 | -5.8023

## Primary Headroom Gen
Grid Supply Point | Bulk Supply Point | Primary Substation | Scenario | Grid Reference | Upstream Constraint (YES / NO) | Outstanding Contracted Generation (MVA) | Generation Headroom Winter (MVA) | [12 empty] | Generation Headroom Summer (MVA) | [12 empty] | Generation Headroom Spring/Autumn (MVA)
[7 empty] | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050
MANNINGTON GSP | BOURNEMOUTH | ALDERNEY | MINIMUM HEADROOM | SZ 04270 95141 | YES | 0.41789 | 23.2853 | 22.8863 | 22.4968 | 21.6747 | 21.2737 | 20.86 | 20.4221 | 20 | 19.5979 | 19.2147 | 17.5032 | 15.9674 | -10.9663 | 21.3547 | 20.9263 | 20.5095 | 19.5947 | 19.1674 | 18.7274 | 18.2547 | 17.7968 | 17.3579 | 16.94 | 15.06 | 13.3547 | 11.7989 | 21.5284 | 21.1 | 20.6821 | 19.7653 | 19.3379 | 18.8968 | 18.4263 | 17.9726 | 17.5368 | 17.1211 | 15.2547 | 13.5621 | 12.0211
|  | ALDERNEY | EE |  |  |  | 23.4484 | 23.1484 | 22.8421 | 22.3074 | 21.8326 | 21.4274 | 21.0537 | 20.7011 | 20.3242 | 20.0032 | 18.6526 | 17.4526 | 16.3916 | 21.5305 | 21.2105 | 20.8832 | 20.2947 | 19.7768 | 19.3411 | 18.9411 | 18.5611 | 18.1505 | 17.8 | 16.3221 | 14.9884 | 13.7937 | 21.7053 | 21.3842 | 21.0568 | 20.4674 | 19.9484 | 19.5105 | 19.1095 | 18.7305 | 18.3221 | 17.9747 | 16.5053 | 15.18 | 13.9968
|  | ALDERNEY | HT |  |  |  | 23.2853 | 22.8863 | 22.4968 | 21.6747 | 21.2737 | 20.86 | 20.4221 | 20 | 19.5979 | 19.2147 | 17.5032 | 15.9674 | 14.5779 | 21.3547 | 20.9263 | 20.5095 | 19.5947 | 19.1674 | 18.7274 | 18.2547 | 17.7968 | 17.3579 | 16.94 | 15.06 | 13.3547 | 11.7989 | 21.5284 | 21.1 | 20.6821 | 19.7653 | 19.3379 | 18.8968 | 18.4263 | 17.9726 | 17.5368 | 17.1211 | 15.2547 | 13.5621 | 12.0211
|  | ALDERNEY | HE |  |  |  | 23.6768 | 23.4853 | 23.2811 | 22.8347 | 22.46 | 22.1463 | 21.8621 | 21.6011 | 21.3032 | 21.0653 | 20.1232 | 19.3105 | -10.9663 | 21.7768 | 21.5737 | 21.3568 | 20.8632 | 20.4526 | 20.1158 | 19.8126 | 19.5337 | 19.2105 | 18.9526 | 17.9189 | 17.0053 | 16.2063 | 21.9516 | 21.7484 | 21.5316 | 21.0368 | 20.6253 | 20.2874 | 19.9832 | 19.7032 | 19.3789 | 19.1211 | 18.0937 | 17.1884 | 16.3968
|  | ALDERNEY | CF |  |  |  | 23.7958 | 23.6842 | 23.5705 | 23.4526 | 23.3337 | 23.2 | 23.0516 | 22.8779 | 22.6737 | 22.4684 | 21.5811 | 21.0126 | 20.5379 | 21.9042 | 21.7853 | 21.6632 | 21.5379 | 21.4116 | 21.2695 | 21.1095 | 20.9211 | 20.6958 | 20.4705 | 19.4958 | 18.8632 | 18.3211 | 22.0789 | 21.96 | 21.8389 | 21.7126 | 21.5863 | 21.4442 | 21.2832 | 21.0937 | 20.8684 | 20.6421 | 19.6642 | 19.0326 | 18.4968
BRAMLEY (FLEE) | ALDERSHOT BSP | ALDERSHOT | MINIMUM HEADROOM | SU 85976 48834 | YES | 0.084211 | 18.0632 | 17.7526 | 17.4411 | 17.1084 | 16.7653 | 16.4095 | 16.0526 | 15.5379 | 15.0116 | 14.5158 | 12.3053 | 10.2937 | -14.9716 | 15.0368 | 14.4326 | 13.8432 | 13.1589 | 12.3568 | 11.5274 | 10.9411 | 10.3611 | 9.7916 | 9.2568 | 6.8495 | 4.6326 | 2.6421 | 15.7653 | 15.4326 | 14.86 | 14.1758 | 13.3747 | 12.5432 | 11.9579 | 11.3758 | 10.8063 | 10.2695 | 7.8537 | 5.6253 | 3.6326
|  | ALDERSHOT | EE |  |  |  | 18.1853 | 17.9442 | 17.6884 | 17.4158 | 17.1347 | 16.8389 | 16.5516 | 16.28 | 16.0189 | 15.7021 | 13.9484 | 12.3895 | 11.0537 | 15.3074 | 14.8421 | 14.3747 | 13.8505 | 13.2368 | 12.5642 | 11.9853 | 11.4895 | 10.9989 | 10.5516 | 8.6526 | 6.9389 | 5.4411 | 15.8968 | 15.6421 | 15.3726 | 14.8674 | 14.2526 | 13.58 | 13 | 12.5021 | 12.0105 | 11.56 | 9.6474 | 7.9168 | 6.4147
|  | ALDERSHOT | HT |  |  |  | 18.0632 | 17.7526 | 17.4411 | 17.1084 | 16.7653 | 16.4095 | 16.0526 | 15.5379 | 15.0116 | 14.5158 | 12.3053 | 10.2937 | 8.5105 | 15.0368 | 14.4326 | 13.8432 | 13.1589 | 12.3568 | 11.5274 | 10.9411 | 10.3611 | 9.7916 | 9.2568 | 6.8495 | 4.6326 | 2.6421 | 15.7653 | 15.4326 | 14.86 | 14.1758 | 13.3747 | 12.5432 | 11.9579 | 11.3758 | 10.8063 | 10.2695 | 7.8537 | 5.6253 | 3.6326
|  | ALDERSHOT | HE |  |  |  | 18.3526 | 18.1916 | 18.0137 | 17.8168 | 17.6063 | 17.3779 | 17.1579 | 16.9537 | 16.7611 | 16.5926 | 16.0232 | 15.1516 | -14.9716 | 15.6726 | 15.3821 | 15.0832 | 14.7168 | 14.2505 | 13.7126 | 13.2811 | 12.9284 | 12.5747 | 12.2611 | 11.0189 | 9.9253 | 8.9758 | 16.0768 | 15.9074 | 15.7221 | 15.5147 | 15.2537 | 14.7284 | 14.2958 | 13.9432 | 13.5884 | 13.2737 | 12.0263 | 10.9295 | 9.9747
|  | ALDERSHOT | CF |  |  |  | 18.4495 | 18.3611 | 18.2695 | 18.1737 | 18.0747 | 17.9716 | 17.8653 | 17.7621 | 17.6589 | 17.5547 | 17.0937 | 16.8611 | 16.6716 | 15.8842 | 15.7095 | 15.5316 | 15.3495 | 15.1642 | 14.9737 | 14.7768 | 14.5674 | 14.3316 | 14.0937 | 13.0011 | 12.1958 | 11.5263 | 16.1811 | 16.0874 | 15.9905 | 15.8895 | 15.7842 | 15.6758 | 15.5642 | 15.4537 | 15.3305 | 15.1032 | 14.0137 | 13.2063 | 12.5347
MELKSHAM GSP | CHIPPENHAM | ALDERTON | MINIMUM HEADROOM | ST 84609 84059 | YES | 0 | 2.9611 | 2.8695 | 2.7768 | 2.68 | 2.5832 | 14.4747 | 14.2947 | 14.1421 | 14.0474 | 13.9505 | 13.4474 | 12.9505 | 9.8284 | 2.8695 | 2.7726 | 2.6758 | 2.5747 | 2.4505 | 14.3168 | 14.0326 | 13.7958 | 13.68 | 13.5579 | 12.8737 | 12.1663 | 11.5074 | 3.1253 | 3.0042 | 2.8842 | 2.7611 | 2.6389 | 14.5074 | 14.2337 | 14.0053 | 13.8884 | 13.7653 | 13.0811 | 12.3474 | 11.6747
|  | ALDERTON | EE |  |  |  | 3.0011 | 2.9295 | 2.8537 | 2.7768 | 2.6968 | 14.6053 | 15.6105 | 15.4158 | 15.1789 | 15.0747 | 14.5211 | 13.9253 | 13.4526 | 2.9116 | 2.8368 | 2.7579 | 2.6789 | 2.5947 | 14.4979 | 14.3853 | 14.1726 | 13.9147 | 13.8074 | 13.2516 | 12.6463 | 12.1274 | 3.1789 | 3.0874 | 2.9905 | 2.8926 | 2.7916 | 14.68 | 14.6337 | 14.4168 | 14.1537 | 14.0411 | 13.4484 | 12.7989 | 12.2674
|  | ALDERTON | HT |  |  |  | 2.9611 | 2.8695 | 2.7768 | 2.68 | 2.5832 | 14.4747 | 14.2947 | 14.1421 | 14.0474 | 13.9505 | 13.4474 | 12.9505 | 12.5453 | 2.8695 | 2.7726 | 2.6758 | 2.5747 | 2.4505 | 14.3168 | 14.0326 | 13.7958 | 13.68 | 13.5579 | 12.8737 | 12.1663 | 11.5074 | 3.1253 | 3.0042 | 2.8842 | 2.7611 | 2.6389 | 14.5074 | 14.2337 | 14.0053 | 13.8884 | 13.7653 | 13.0811 | 12.3474 | 11.6747
|  | ALDERTON | HE |  |  |  | 3.0526 | 3.0105 | 2.9611 | 2.9084 | 2.8526 | 14.7853 | 15.8768 | 15.7242 | 15.5126 | 15.4505 | 15.1084 | 14.7505 | 9.8284 | 2.9663 | 2.9221 | 2.8705 | 2.8158 | 2.7589 | 14.6926 | 14.6684 | 14.5021 | 14.2632 | 14.1989 | 13.8453 | 13.4568 | 13.0579 | 3.2505 | 3.1968 | 3.1347 | 3.0695 | 3 | 14.9189 | 14.9211 | 14.7505 | 14.5116 | 14.4453 | 14.0758 | 13.6747 | 13.2642
|  | ALDERTON | CF |  |  |  | 3.0737 | 3.0568 | 3.0305 | 3.0042 | 2.9747 | 14.94 | 14.9011 | 14.8684 | 14.8284 | 14.7821 | 14.5716 | 14.4253 | 14.2737 | 2.9979 | 2.9716 | 2.9432 | 2.9147 | 2.8842 | 14.8495 | 14.8105 | 14.7789 | 14.7379 | 14.6916 | 14.3916 | 14.1695 | 13.9147 | 3.2789 | 3.2558 | 3.2211 | 3.1853 | 3.1484 | 15.1032 | 15.0516 | 15.0095 | 14.9547 | 14.8874 | 14.5779 | 14.36 | 14.1116
BRAMLEY (FLEE) | ALTON | ALRESFORD | MINIMUM HEADROOM | SU 59684 32511 | YES | 0.073684 | 13.7758 | 13.5063 | 12.9179 | 32.2779 | 31.5874 | 30.8084 | 30.0768 | 29.4189 | 28.9789 | 28.4326 | 25.5116 | 22.6537 | 8.4442 | 10.1316 | 9.5568 | 8.8895 | 28.1674 | 27.3821 | 26.5147 | 25.7063 | 24.9842 | 24.5295 | 23.94 | 20.8895 | 17.9295 | 15.6411 | 10.9411 | 10.4021 | 9.7316 | 28.9937 | 28.1926 | 27.2968 | 26.4611 | 25.7137 | 25.2389 | 24.6242 | 21.4179 | 18.2811 | 15.9137
|  | ALRESFORD | EE |  |  |  | 13.8821 | 13.6737 | 13.3253 | 32.7811 | 32.1821 | 31.5 | 30.8505 | 30.3358 | 29.8779 | 29.3863 | 26.7937 | 24.2526 | 22.4632 | 10.3505 | 9.8884 | 9.3453 | 28.7274 | 28.0453 | 27.2832 | 26.5747 | 26.0295 | 25.5589 | 25.0442 | 22.3568 | 19.8084 | 17.9053 | 11.0537 | 10.7421 | 10.1895 | 29.5621 | 28.8653 | 28.0779 | 27.3389 | 26.7684 | 26.2716 | 25.7295 | 22.8516 | 20.0916 | 18.0937
|  | ALRESFORD | HT |  |  |  | 13.7758 | 13.5063 | 12.9179 | 32.2779 | 31.5874 | 30.8084 | 30.0768 | 29.4189 | 28.9789 | 28.4326 | 25.5116 | 22.6537 | 20.5274 | 10.1316 | 9.5568 | 8.8895 | 28.1674 | 27.3821 | 26.5147 | 25.7063 | 24.9842 | 24.5295 | 23.94 | 20.8895 | 17.9295 | 15.6411 | 10.9411 | 10.4021 | 9.7316 | 28.9937 | 28.1926 | 27.2968 | 26.4611 | 25.7137 | 25.2389 | 24.6242 | 21.4179 | 18.2811 | 15.9137
|  | ALRESFORD | HE |  |  |  | 14.0316 | 13.8937 | 13.74 | 33.4621 | 32.9863 | 32.4253 | 31.9253 | 31.5632 | 31.2642 | 30.9358 | 29.2811 | 27.8453 | 8.4442 | 10.6495 | 10.3305 | 9.9368 | 29.4832 | 28.9368 | 28.3063 | 27.7474 | 27.3589 | 27.0474 | 26.6947 | 24.8874 | 23.3168 | 21.9084 | 11.2147 | 11.0642 | 10.7905 | 30.3295 | 29.7747 | 29.1221 | 28.5463 | 28.1411 | 27.8179 | 27.4505 | 25.5484 | 23.8968 | 22.4126
|  | ALRESFORD | CF |  |  |  | 14.1168 | 14.0411 | 13.9632 | 33.8821 | 33.7968 | 33.6337 | 33.3779 | 33.1716 | 33.0074 | 32.8221 | 31.7737 | 30.8653 | 30.0621 | 10.8053 | 10.6253 | 10.4158 | 30.1895 | 29.9484 | 29.6726 | 29.3863 | 29.1589 | 28.9853 | 28.7821 | 27.6168 | 26.5905 | 25.6832 | 11.3053 | 11.2221 | 11.1347 | 31.0442 | 30.7989 | 30.5105 | 30.2242 | 29.9895 | 29.8084 | 29.5989 | 28.3916 | 27.3179 | 26.3589
BRAMLEY (FLEE) | ALTON | ALTON LOCAL | MINIMUM HEADROOM | SU 72434 39606 | YES | 0.62632 | 56.1632 | 55.7589 | 56.44 | 55.4326 | 54.3211 | 53.0958 | 51.9589 | 50.9432 | 49.8937 | 48.7905 | 43.1695 | 37.7442 | -2.4053 | 47.9284 | 46.6053 | 45.0221 | 43.9368 | 42.7337 | 41.4442 | 40.26 | 39.2105 | 38.1189 | 36.9632 | 31.1126 | 25.4526 | 20.6705 | 48.7263 | 47.2863 | 45.7021 | 44.6168 | 43.4126 | 42.0958 | 40.8832 | 39.8011 | 38.6737 | 37.48 | 31.3853 | 25.4337 | 20.54
|  | ALTON LOCAL | EE |  |  |  | 56.1632 | 55.7589 | 57.2484 | 56.4421 | 55.5537 | 54.5558 | 53.6305 | 52.7663 | 51.8316 | 50.8411 | 45.7768 | 40.86 | 37.3389 | 48.1168 | 46.9295 | 45.7853 | 45.0389 | 44.0821 | 43.0421 | 42.1042 | 41.2389 | 40.2968 | 39.2874 | 34.2 | 29.0537 | 25.2389 | 49.1758 | 47.9653 | 46.58 | 45.7147 | 44.7568 | 43.6884 | 42.7105 | 41.8021 | 40.8126 | 39.7484 | 34.3116 | 28.9642 | 25.0316
|  | ALTON LOCAL | HT |  |  |  | 59.1705 | 57.8674 | 56.44 | 55.4326 | 54.3211 | 53.0958 | 51.9589 | 50.9432 | 49.8937 | 48.7905 | 43.1695 | 37.7442 | 33.3589 | 47.9284 | 46.6053 | 45.0221 | 43.9368 | 42.7337 | 41.4442 | 40.26 | 39.2105 | 38.1189 | 36.9632 | 31.1126 | 25.4526 | 20.6705 | 48.7263 | 47.2863 | 45.7021 | 44.6168 | 43.4126 | 42.0958 | 40.8832 | 39.8011 | 38.6737 | 37.48 | 31.3853 | 25.4337 | 20.54
|  | ALTON LOCAL | HE |  |  |  | 60.1432 | 59.3179 | 58.3379 | 57.7863 | 57.1368 | 56.38 | 55.7421 | 55.1737 | 54.5505 | 53.8779 | 50.4821 | 47.5958 | -2.4053 | 48.9874 | 48.0653 | 47.0853 | 46.4968 | 45.7947 | 45.0105 | 44.3568 | 43.7832 | 43.1432 | 42.4411 | 38.8274 | 35.7189 | 32.9179 | 49.7853 | 48.8632 | 47.7653 | 47.1758 | 46.4758 | 45.6695 | 44.9958 | 44.4021 | 43.7411 | 43.0147 | 39.2516 | 36.0305 | 33.1274
|  | ALTON LOCAL | CF |  |  |  | 60.6821 | 60.3747 | 59.9705 | 59.4989 | 58.9989 | 58.42 | 57.9011 | 57.5032 | 57.1611 | 56.8263 | 54.8053 | 52.9042 | 51.2179 | 49.5916 | 49.2579 | 48.8116 | 48.4063 | 47.8484 | 47.2158 | 46.6537 | 46.2347 | 45.8789 | 45.5305 | 43.3716 | 41.3105 | 39.48 | 50.3895 | 50.0558 | 49.6095 | 49.0842 | 48.5274 | 47.8853 | 47.3137 | 46.8853 | 46.5189 | 46.1632 | 43.9579 | 41.8347 | 39.9368
MELKSHAM GSP | ANDOVER BSP | ANDOVER | MINIMUM HEADROOM | SU 35240 46643 | YES | 0.21053 | 26.0158 | 25.8211 | 25.6253 | 25.4168 | 25.1968 | 25.2347 | 24.8411 | 24.2105 | 23.3968 | 22.5758 | 20.8379 | 19.2495 | 5.3011 | 23.8253 | 23.4695 | 23.1221 | 22.6853 | 21.8758 | 21.8768 | 21.1895 | 20.4368 | 19.4505 | 18.4505 | 16.6758 | 14.8979 | 13.1811 | 24.2211 | 24.0158 | 23.7621 | 23.3105 | 22.4811 | 22.4842 | 21.7958 | 21.0442 | 20.06 | 19.0611 | 17.0874 | 15.3084 | 13.5916
|  | ANDOVER | EE |  |  |  | 26.0905 | 25.9379 | 25.7779 | 25.6063 | 25.4274 | 25.2347 | 24.8411 | 24.2105 | 23.3968 | 22.5758 | 21.84 | 20.6158 | 19.4558 | 23.9821 | 23.7095 | 23.4337 | 23.0958 | 22.54 | 21.8768 | 21.1895 | 20.4368 | 19.4505 | 18.4505 | 17.7642 | 16.3884 | 15.0726 | 24.3011 | 24.14 | 23.9726 | 23.7347 | 23.1547 | 22.4842 | 21.7958 | 21.0442 | 20.06 | 19.0611 | 18.1758 | 16.8 | 15.4842
|  | ANDOVER | HT |  |  |  | 26.0158 | 25.8211 | 25.6253 | 25.4168 | 25.1968 | 26.1442 | 25.3358 | 24.5579 | 23.8074 | 23.0537 | 20.8379 | 19.2495 | 17.7284 | 23.8253 | 23.4695 | 23.1221 | 22.6853 | 21.8758 | 22.8295 | 21.8674 | 20.9379 | 20.0368 | 19.1526 | 16.6758 | 14.8979 | 13.1811 | 24.2211 | 24.0158 | 23.7621 | 23.3105 | 22.4811 | 23.2389 | 22.2758 | 21.3453 | 20.4442 | 19.5611 | 17.0874 | 15.3084 | 13.5916
|  | ANDOVER | HE |  |  |  | 26.1916 | 26.0874 | 25.9726 | 25.8453 | 25.7084 | 25.5632 | 25.4074 | 24.9211 | 24.1695 | 23.4347 | 23.14 | 22.26 | 5.3011 | 24.1074 | 24 | 23.8389 | 23.5926 | 23.1147 | 22.5368 | 21.9453 | 21.2305 | 20.3116 | 19.4116 | 19.1621 | 18.1653 | 17.2126 | 24.4095 | 24.3011 | 24.1811 | 24.0463 | 23.7484 | 23.1442 | 22.5505 | 21.8368 | 20.92 | 20.0211 | 19.5653 | 18.5674 | 17.6147
|  | ANDOVER | CF |  |  |  | 26.2505 | 26.1916 | 26.1295 | 26.0653 | 26 | 25.9316 | 25.8621 | 25.7926 | 25.7253 | 25.6568 | 23.8526 | 24.7926 | 24.2758 | 24.1684 | 24.1074 | 24.0432 | 23.9558 | 23.82 | 23.6716 | 23.5295 | 23.3547 | 23.1579 | 22.9095 | 19.8621 | 21.0653 | 20.4347 | 24.4716 | 24.4095 | 24.3442 | 24.2758 | 24.2053 | 24.1316 | 24.0579 | 23.9811 | 23.7937 | 23.5337 | 20.4716 | 21.4737 | 20.8432
MELKSHAM GSP | ANDOVER BSP | ANDOVER EAST | MINIMUM HEADROOM | SU 37953 46433 | YES | 1.1579 | 35.0695 | 34.8053 | 34.5368 | 34.7989 | 34.6021 | 34.3884 | 35.2011 | 34.7947 | 34.3811 | 34.0063 | 32.42 | 29.2516 | -5.0042 | 30.3168 | 29.6021 | 28.7084 | 27.8179 | 27 | 27.0526 | 26.5063 | 26.0747 | 25.6358 | 25.2358 | 23.7242 | 20.1568 | 16.6158 | 31.3916 | 31.1021 | 30.5021 | 29.6105 | 28.7926 | 28.8432 | 28.2947 | 27.8611 | 27.4189 | 27.0147 | 25.3168 | 21.7326 | 18.1832
|  | ANDOVER EAST | EE |  |  |  | 35.16 | 34.9474 | 34.72 | 36.8853 | 36.2326 | 35.7074 | 35.2011 | 34.7947 | 34.3811 | 34.0063 | 33.8789 | 31.3295 | 28.8516 | 30.5137 | 29.9495 | 29.1558 | 28.3442 | 27.6221 | 27.0526 | 26.5063 | 26.0747 | 25.6358 | 25.2358 | 25.3474 | 22.4853 | 19.6558 | 31.4905 | 31.2558 | 30.9495 | 30.1358 | 29.4137 | 28.8432 | 28.2947 | 27.8611 | 27.4189 | 27.0147 | 26.9316 | 24.0453 | 21.2074
|  | ANDOVER EAST | HT |  |  |  | 35.0695 | 34.8053 | 34.5368 | 36.4042 | 35.6632 | 36.5221 | 35.9168 | 35.44 | 34.9926 | 34.5684 | 32.42 | 29.2516 | 26.1421 | 30.3168 | 29.6021 | 28.7084 | 27.8179 | 27 | 28.1453 | 27.4916 | 26.9811 | 26.5021 | 26.0474 | 23.7242 | 20.1568 | 16.6158 | 31.3916 | 31.1021 | 30.5021 | 29.6105 | 28.7926 | 29.7558 | 29.0989 | 28.5884 | 28.1074 | 27.6505 | 25.3168 | 21.7326 | 18.1832
|  | ANDOVER EAST | HE |  |  |  | 35.2979 | 35.1474 | 34.9821 | 34.7989 | 34.6021 | 34.3884 | 36.2242 | 35.9253 | 35.6316 | 35.3705 | 35.7495 | 33.7789 | -5.0042 | 30.6516 | 30.4095 | 29.7568 | 29.0874 | 28.4958 | 28.0463 | 27.6211 | 27.3053 | 26.9937 | 26.7158 | 27.3358 | 25.0863 | 22.7968 | 31.6295 | 31.4705 | 31.2768 | 30.88 | 30.2895 | 29.8389 | 29.4116 | 29.0937 | 28.7821 | 28.5032 | 28.9263 | 26.6695 | 24.3726
|  | ANDOVER EAST | CF |  |  |  | 35.3779 | 35.2895 | 35.1989 | 38.4337 | 38.1095 | 37.8074 | 37.5253 | 37.3411 | 37.1663 | 36.9863 | 36.0863 | 36.3632 | 35.1379 | 30.7326 | 30.6442 | 30.4211 | 30.0516 | 29.6884 | 29.3526 | 29.0411 | 28.8432 | 28.6547 | 28.4621 | 27.4884 | 27.94 | 26.5316 | 31.7095 | 31.6211 | 31.52 | 31.8453 | 31.4821 | 31.1442 | 30.8326 | 30.6337 | 30.4463 | 30.2526 | 29.2758 | 29.5432 | 28.1295
MELKSHAM GSP | ANDOVER BSP | ANDOVER TOWN | MINIMUM HEADROOM | SU 36207 45078 | YES | 0.063158 | 17.1926 | 16.9874 | 16.7832 | 16.5653 | 16.34 | 16.1084 | 15.8768 | 15.6684 | 15.4789 | 15.3053 | 13.9242 | 12.0305 | -0.93474 | 15.1653 | 14.8442 | 14.4821 | 14.0989 | 13.7232 | 13.3432 | 12.9674 | 12.62 | 12.2958 | 11.9895 | 10.4642 | 8.3642 | 6.2853 | 15.5253 | 15.3232 | 15.1084 | 14.7189 | 14.3379 | 13.9526 | 13.5716 | 13.2189 | 12.8884 | 12.5779 | 11.02 | 8.8853 | 6.8032
|  | ANDOVER TOWN | EE |  |  |  | 17.2716 | 17.1126 | 16.9453 | 16.7642 | 16.5789 | 16.3853 | 16.1968 | 16.0189 | 15.8442 | 15.6895 | 14.9716 | 13.4842 | 12.0442 | 15.2505 | 15.0832 | 14.8105 | 14.4863 | 14.1811 | 13.8737 | 13.5758 | 13.2884 | 13.0011 | 12.7379 | 11.6095 | 9.9611 | 8.3316 | 15.6032 | 15.4463 | 15.28 | 15.1011 | 14.8032 | 14.4916 | 14.1884 | 13.8968 | 13.6042 | 13.3368 | 12.1832 | 10.4874 | 8.8442
|  | ANDOVER TOWN | HT |  |  |  | 17.1926 | 16.9874 | 16.7832 | 16.5653 | 16.34 | 16.1084 | 15.8768 | 15.6684 | 15.4789 | 15.3053 | 13.9242 | 12.0305 | 10.1979 | 15.1653 | 14.8442 | 14.4821 | 14.0989 | 13.7232 | 13.3432 | 12.9674 | 12.62 | 12.2958 | 11.9895 | 10.4642 | 8.3642 | 6.2853 | 15.5253 | 15.3232 | 15.1084 | 14.7189 | 14.3379 | 13.9526 | 13.5716 | 13.2189 | 12.8884 | 12.5779 | 11.02 | 8.8853 | 6.8032
|  | ANDOVER TOWN | HE |  |  |  | 17.3768 | 17.2716 | 17.1526 | 17.02 | 16.8789 | 16.7274 | 16.5821 | 16.4463 | 16.3158 | 16.2042 | 15.8126 | 15.1863 | -0.93474 | 15.3663 | 15.2526 | 15.1295 | 14.9905 | 14.7926 | 14.5695 | 14.3558 | 14.1463 | 13.9411 | 13.7642 | 13.0347 | 11.78 | 10.5368 | 15.7105 | 15.6032 | 15.4842 | 15.3537 | 15.2126 | 15.0632 | 14.92 | 14.7716 | 14.5621 | 14.3832 | 13.6389 | 12.3495 | 11.0684
|  | ANDOVER TOWN | CF |  |  |  | 17.4337 | 17.3747 | 17.3126 | 17.2432 | 17.1705 | 17.0937 | 17.0158 | 16.9421 | 16.8684 | 16.7979 | 16.4674 | 16.2674 | 15.6905 | 15.4295 | 15.3642 | 15.2958 | 15.2211 | 15.1421 | 15.0011 | 14.8337 | 14.7021 | 14.5789 | 14.4558 | 13.8263 | 13.0442 | 12.2621 | 15.7705 | 15.7084 | 15.6442 | 15.5747 | 15.5032 | 15.4284 | 15.3516 | 15.2789 | 15.2032 | 15.0789 | 14.4389 | 13.6358 | 12.8295
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | ARBORFIELD | MINIMUM HEADROOM | SU 75949 65766 | YES | 0.42316 | 26.8716 | 26.7105 | 26.5474 | 26.3747 | 25.5789 | 24.7758 | 23.9558 | 22.8884 | 21.6011 | 20.3389 | 12.9758 | 5.7253 | -7.2684 | 21.9347 | 21.7747 | 21.6126 | 21.4389 | 20.5358 | 19.6221 | 18.6905 | 17.4632 | 15.9747 | 14.5137 | 5.9484 | -2.5116 | -9.7305 | 22.7684 | 22.6074 | 22.4442 | 22.2705 | 21.3768 | 20.4642 | 19.5347 | 18.3084 | 16.8221 | 15.3621 | 6.8095 | -1.6358 | -8.8453
|  | ARBORFIELD | EE |  |  |  | 26.9316 | 26.8063 | 26.6726 | 26.5295 | 26.38 | 25.8316 | 25.0611 | 24.2579 | 23.0179 | 21.7611 | 14.4547 | 7.2274 | 0.97474 | 21.9968 | 21.8716 | 21.7389 | 21.5968 | 21.4484 | 20.8326 | 19.9505 | 19.0326 | 17.5979 | 16.14 | 7.6263 | -0.82105 | -8.1358 | 22.8284 | 22.7021 | 22.5684 | 22.4337 | 22.2832 | 21.6674 | 20.7863 | 19.8674 | 18.4358 | 16.9789 | 8.4737 | 0.034737 | -7.2716
|  | ARBORFIELD | HT |  |  |  | 26.8716 | 26.7105 | 26.5474 | 26.3747 | 25.5789 | 24.7758 | 23.9558 | 22.8884 | 21.6011 | 20.3389 | 12.9758 | 5.7253 | -0.46 | 21.9347 | 21.7747 | 21.6126 | 21.4389 | 20.5358 | 19.6221 | 18.6905 | 17.4632 | 15.9747 | 14.5137 | 5.9484 | -2.5116 | -9.7305 | 22.7684 | 22.6074 | 22.4442 | 22.2705 | 21.3768 | 20.4642 | 19.5347 | 18.3084 | 16.8221 | 15.3621 | 6.8095 | -1.6358 | -8.8453
|  | ARBORFIELD | HE |  |  |  | 27.0242 | 26.94 | 26.8484 | 26.7463 | 26.6368 | 26.38 | 25.6705 | 24.8853 | 23.6811 | 22.4937 | 15.5147 | 8.5968 | -7.2684 | 22.0874 | 22.0032 | 21.9116 | 21.8095 | 21.7 | 21.4189 | 20.6042 | 19.6979 | 18.3 | 16.9168 | 8.7568 | 0.64526 | -6.2958 | 22.9211 | 22.8368 | 22.7453 | 22.6432 | 22.5337 | 22.2589 | 21.4474 | 20.5432 | 19.1474 | 17.7663 | 9.62 | 1.5242 | -5.4042
|  | ARBORFIELD | CF |  |  |  | 27.4137 | 27.3674 | 27.3189 | 26.9295 | 26.8789 | 26.8253 | 26.7716 | 26.7179 | 26.6653 | 26.6126 | 23.8937 | 17.9158 | 12.2832 | 24.3505 | 24.2274 | 24.1232 | 21.9926 | 21.9421 | 21.8884 | 21.8347 | 21.7811 | 21.7284 | 21.6758 | 18.52 | 11.5053 | 4.8895 | 24.9495 | 24.8989 | 24.8474 | 22.8263 | 22.7758 | 22.7221 | 22.6684 | 22.6147 | 22.5621 | 22.5095 | 19.3674 | 12.3653 | 5.7621
LOVEDEAN GSP | CHICHESTER & HUNSTON | ARGYLE ROAD | MINIMUM HEADROOM | SZ 93193 99152 | YES | 0.069474 | 35.2021 | 34.9337 | 34.6632 | 34.3747 | 34.0747 | 33.7621 | 33.4474 | 33.1674 | 32.9116 | 32.6747 | 30.5463 | 26.6621 | 0.70105 | 30.6179 | 30.3495 | 30.0705 | 29.52 | 28.9684 | 28.4053 | 27.8453 | 27.3411 | 26.8495 | 26.3684 | 22.84 | 18.4116 | 13.7368 | 31.0653 | 30.7811 | 30.4947 | 30.1905 | 29.8147 | 29.2432 | 28.6747 | 28.1642 | 27.6642 | 27.1832 | 23.6537 | 19.2253 | 14.5484
|  | ARGYLE ROAD | EE |  |  |  | 35.3137 | 35.1084 | 34.8916 | 34.66 | 34.4147 | 34.16 | 33.9126 | 33.6737 | 33.4432 | 33.2368 | 32.4653 | 29.6516 | 26.3653 | 30.7295 | 30.5242 | 30.3074 | 30.0695 | 29.6537 | 29.1916 | 28.7463 | 28.3253 | 27.9168 | 27.5421 | 25.1105 | 21.7495 | 17.9611 | 31.1842 | 30.9663 | 30.7368 | 30.4937 | 30.2358 | 29.9695 | 29.5905 | 29.1632 | 28.7495 | 28.3684 | 25.9253 | 22.5621 | 18.7737
|  | ARGYLE ROAD | HT |  |  |  | 35.2021 | 34.9337 | 34.6632 | 34.3747 | 34.0747 | 33.7621 | 33.4474 | 33.1674 | 32.9116 | 32.6747 | 30.5463 | 26.6621 | 22.5895 | 30.6179 | 30.3495 | 30.0705 | 29.52 | 28.9684 | 28.4053 | 27.8453 | 27.3411 | 26.8495 | 26.3684 | 22.84 | 18.4116 | 13.7368 | 31.0653 | 30.7811 | 30.4947 | 30.1905 | 29.8147 | 29.2432 | 28.6747 | 28.1642 | 27.6642 | 27.1832 | 23.6537 | 19.2253 | 14.5484
|  | ARGYLE ROAD | HE |  |  |  | 35.4326 | 35.2811 | 35.1126 | 34.9274 | 34.7284 | 34.5158 | 34.3126 | 34.1211 | 33.9421 | 33.7874 | 33.2558 | 31.8979 | 0.70105 | 30.8484 | 30.6968 | 30.5284 | 30.3432 | 30.1442 | 29.9305 | 29.7211 | 29.4189 | 29.1305 | 28.8705 | 27.0116 | 24.2105 | 20.9895 | 31.3126 | 31.1537 | 30.9768 | 30.7842 | 30.5779 | 30.3558 | 30.1442 | 29.9463 | 29.7611 | 29.6 | 27.8263 | 25.0253 | 21.8032
|  | ARGYLE ROAD | CF |  |  |  | 35.5042 | 35.4095 | 35.3126 | 35.2116 | 35.1074 | 34.9989 | 34.8895 | 34.7811 | 34.6737 | 34.5663 | 34.0884 | 33.8463 | 33.4211 | 30.92 | 30.8253 | 30.7284 | 30.6274 | 30.5232 | 30.4147 | 30.3053 | 30.1968 | 30.0895 | 29.9789 | 28.9989 | 27.7947 | 25.8642 | 31.3884 | 31.2884 | 31.1863 | 31.0811 | 30.9716 | 30.8579 | 30.7432 | 30.6295 | 30.5168 | 30.4042 | 29.8453 | 28.6105 | 26.6779
COWLEY GSP | HEADINGTON BSP | ARNCOTT | MINIMUM HEADROOM | SP 60730 18095 | YES | 0.50526 | 22.9905 | 22.8432 | 22.5895 | 21.3758 | 19.9947 | 18.4042 | 17.0474 | 15.8684 | 14.7032 | 13.5453 | 8.6389 | 6.2884 | -12.9232 | 22.5547 | 22.4 | 22.1211 | 20.7126 | 19.1084 | 17.2589 | 15.6853 | 14.3211 | 12.9705 | 11.6263 | 5.9474 | 3.2684 | 2.0989 | 22.7011 | 22.5463 | 22.2695 | 20.8821 | 19.3011 | 17.4779 | 15.9263 | 14.58 | 13.2989 | 11.9558 | 6.2695 | 3.5716 | 2.3947
|  | ARNCOTT | EE |  |  |  | 23.0389 | 22.9221 | 22.7516 | 21.5726 | 20.2263 | 18.6695 | 17.3453 | 16.1926 | 15.0432 | 13.9032 | 9.0979 | 6.8832 | 6.0495 | 22.6063 | 22.4821 | 22.2968 | 20.9284 | 19.36 | 17.5474 | 16.0105 | 14.6737 | 13.3421 | 12.02 | 6.4642 | 3.9495 | 3.0105 | 22.7516 | 22.6284 | 22.4453 | 21.0937 | 19.6832 | 17.8726 | 16.3358 | 15 | 13.6674 | 12.3442 | 6.7726 | 4.2274 | 3.2779
|  | ARNCOTT | HT |  |  |  | 22.9905 | 22.8432 | 22.5895 | 21.3758 | 19.9947 | 18.4042 | 17.0474 | 15.8684 | 14.7032 | 13.5453 | 8.6389 | 6.2884 | 5.2495 | 22.5547 | 22.4 | 22.1211 | 20.7126 | 19.1084 | 17.2589 | 15.6853 | 14.3211 | 12.9705 | 11.6263 | 5.9474 | 3.2684 | 2.0989 | 22.7011 | 22.5463 | 22.2695 | 20.8821 | 19.3011 | 17.4779 | 15.9263 | 14.58 | 13.2989 | 11.9558 | 6.2695 | 3.5716 | 2.3947
|  | ARNCOTT | HE |  |  |  | 23.0958 | 23.0211 | 22.9379 | 21.8442 | 20.5484 | 19.0337 | 17.7611 | 16.6589 | 15.5589 | 14.4716 | 9.9347 | 8.0011 | -12.9232 | 22.6632 | 22.5832 | 22.4968 | 21.2232 | 19.7084 | 17.9421 | 16.4589 | 15.1747 | 13.8937 | 12.6263 | 7.3379 | 5.0947 | 4.3442 | 22.8084 | 22.7295 | 22.6442 | 21.3874 | 19.8968 | 18.1568 | 16.6958 | 15.4295 | 14.1674 | 12.9189 | 7.6737 | 5.4263 | 4.6684
|  | ARNCOTT | CF |  |  |  | 23.1474 | 23.1074 | 23.0726 | 23.0337 | 22.9874 | 22.5916 | 21.9989 | 21.2863 | 20.5126 | 19.68 | 15.6968 | 14.2989 | 13.8853 | 22.7168 | 22.6758 | 22.64 | 22.6 | 22.5516 | 22.0926 | 21.4053 | 20.5737 | 19.6695 | 18.6958 | 14.0389 | 12.4147 | 11.9442 | 22.8632 | 22.8221 | 22.7863 | 22.7463 | 22.6968 | 22.2442 | 21.5642 | 20.7453 | 19.8558 | 18.8958 | 14.3105 | 12.7063 | 12.2368
BRAMLEY (FLEE) | BRACKNELL | ASCOT | MINIMUM HEADROOM | SU 91615 68855 | YES | 0.18 | 35.0453 | 34.8189 | 34.5905 | 34.3495 | 34.0989 | 34.4937 | 34.2779 | 34.0705 | 33.8674 | 33.6853 | 31.8421 | 29.6874 | 7.1674 | 30.8747 | 30.4316 | 29.9926 | 29.1611 | 28.3916 | 28.8579 | 28.2389 | 27.8884 | 27.5032 | 27.1463 | 25.1211 | 22.7211 | 20.5579 | 30.8926 | 30.6537 | 30.4126 | 29.6926 | 28.9253 | 29.3895 | 28.7674 | 28.4137 | 28.0242 | 27.6642 | 25.5274 | 23.1042 | 20.9326
|  | ASCOT | EE |  |  |  | 35.1316 | 34.9558 | 34.7674 | 34.5705 | 34.36 | 34.4937 | 34.2779 | 34.0705 | 33.8674 | 33.6853 | 33.0147 | 31.2653 | 29.7758 | 31.0126 | 30.7284 | 30.3768 | 29.8137 | 29.1263 | 28.8579 | 28.2389 | 27.8884 | 27.5032 | 27.1463 | 26.4179 | 24.4789 | 22.7916 | 30.9853 | 30.7989 | 30.6011 | 30.3284 | 29.66 | 29.3895 | 28.7674 | 28.4137 | 28.0242 | 27.6642 | 26.8126 | 24.8421 | 23.1453
|  | ASCOT | HT |  |  |  | 35.0453 | 34.8189 | 34.5905 | 34.3495 | 34.0989 | 34.8621 | 34.5958 | 34.3568 | 34.1421 | 33.8316 | 31.8421 | 29.6874 | 27.7737 | 30.8747 | 30.4316 | 29.9926 | 29.1611 | 28.3916 | 29.02 | 28.5747 | 28.16 | 27.7137 | 27.3 | 25.1211 | 22.7211 | 20.5579 | 30.8926 | 30.6537 | 30.4126 | 29.6926 | 28.9253 | 29.4547 | 29.0084 | 28.5905 | 28.1411 | 27.7242 | 25.5274 | 23.1042 | 20.9326
|  | ASCOT | HE |  |  |  | 35.2495 | 35.1284 | 34.9937 | 34.8453 | 34.6874 | 34.8674 | 34.7011 | 34.5421 | 34.3937 | 34.2642 | 34.4821 | 33.4095 | 7.1674 | 31.1305 | 31.0095 | 30.8705 | 30.4263 | 30.0663 | 29.9042 | 29.4053 | 28.9126 | 28.6211 | 28.3853 | 28.1937 | 26.7674 | 25.5095 | 31.1116 | 30.9842 | 30.8442 | 30.6779 | 30.5084 | 30.4263 | 29.9368 | 29.4421 | 29.1484 | 28.9116 | 28.6116 | 27.1779 | 25.9116
|  | ASCOT | CF |  |  |  | 35.3137 | 35.2453 | 35.1716 | 35.0958 | 35.0179 | 35.2895 | 35.2053 | 35.1211 | 35.0379 | 34.9547 | 34.5842 | 35.0611 | 34.8547 | 31.1947 | 31.1263 | 31.0526 | 30.9768 | 30.7295 | 30.7832 | 30.4811 | 30.2989 | 30.1411 | 29.9758 | 29.0989 | 29.1379 | 28.3295 | 31.1789 | 31.1063 | 31.0284 | 30.9474 | 30.8579 | 31.1168 | 30.9947 | 30.8158 | 30.6611 | 30.4968 | 29.6263 | 29.5632 | 28.7495
LOVEDEAN GSP | CHICHESTER & HUNSTON | ASHLING ROAD | MINIMUM HEADROOM | SU 84085 06737 | YES | 0.83368 | 27.9232 | 27.3821 | 31.9358 | 30.4842 | 28.7832 | 26.7695 | 24.4821 | 22.3368 | 20.7368 | 19.2337 | 12.5442 | 7.3 | -30.8642 | 19.3421 | 17.8811 | 21.3337 | 19.6358 | 17.7305 | 15.5116 | 12.9295 | 10.5 | 8.7053 | 7.0347 | -0.51263 | -6.4432 | -11.8905 | 20.7453 | 19.3253 | 22.8263 | 21.1779 | 19.2558 | 16.9989 | 14.42 | 11.9947 | 10.2021 | 8.5379 | 1.0011 | -4.9211 | -10.36
|  | ASHLING ROAD | EE |  |  |  | 28.1326 | 27.7116 | 32.3653 | 31.5347 | 30.1284 | 28.3863 | 26.3579 | 24.3579 | 22.9568 | 21.6147 | 16.0958 | 11.9421 | 8.1842 | 19.8032 | 18.58 | 22.2432 | 20.8126 | 19.1832 | 17.2611 | 14.9832 | 12.7126 | 11.1432 | 9.6347 | 3.4126 | -1.3042 | -5.6011 | 21.1958 | 20.0074 | 23.7147 | 22.3263 | 20.7347 | 18.7684 | 16.4705 | 14.2042 | 12.6368 | 11.1305 | 4.9221 | 0.21263 | -4.0768
|  | ASHLING ROAD | HT |  |  |  | 27.9232 | 27.3821 | 31.9358 | 30.4842 | 28.7832 | 26.7695 | 24.4821 | 22.3368 | 20.7368 | 19.2337 | 12.5442 | 7.3 | 2.5105 | 19.3421 | 17.8811 | 21.3337 | 19.6358 | 17.7305 | 15.5116 | 12.9295 | 10.5 | 8.7053 | 7.0347 | -0.51263 | -6.4432 | -11.8905 | 20.7453 | 19.3253 | 22.8263 | 21.1779 | 19.2558 | 16.9989 | 14.42 | 11.9947 | 10.2021 | 8.5379 | 1.0011 | -4.9211 | -10.36
|  | ASHLING ROAD | HE |  |  |  | 28.4221 | 28.1379 | 32.9232 | 32.5758 | 31.6853 | 30.2368 | 28.4284 | 26.6432 | 25.46 | 24.3305 | 19.7495 | 16.5305 | -30.8642 | 20.4284 | 19.5021 | 23.4495 | 22.2937 | 20.9242 | 19.2411 | 17.2347 | 15.2011 | 13.8674 | 12.5895 | 7.3526 | 3.6642 | 0.34526 | 21.6126 | 20.9084 | 24.8926 | 23.7726 | 22.4463 | 20.7811 | 18.7232 | 16.6895 | 15.3589 | 14.0821 | 8.8484 | 5.1663 | 1.8537
|  | ASHLING ROAD | CF |  |  |  | 28.5905 | 28.4316 | 33.3674 | 33.1958 | 33.0189 | 32.8358 | 32.52 | 31.6421 | 31.0358 | 30.3789 | 27.2853 | 25.1958 | 23.3842 | 20.7821 | 20.2558 | 24.7516 | 24.1895 | 23.5316 | 22.7768 | 21.8526 | 20.8063 | 20.0947 | 19.3621 | 15.9158 | 13.5274 | 11.4347 | 21.7811 | 21.6221 | 26.1568 | 25.6116 | 24.9747 | 24.2453 | 23.3537 | 22.3453 | 21.6463 | 20.8958 | 17.4042 | 15.02 | 12.9305
MELKSHAM GSP | NORRINGTON | ASHTON PARK | MINIMUM HEADROOM | ST 87141 57741 | YES | 0.38737 | 27.8253 | 26.6726 | 25.3147 | 24.0611 | 22.0453 | 19.2126 | 16.6 | 13.6158 | 10.9158 | 8.4211 | -0.91263 | -8.2947 | -30.4316 | 22.06 | 20.8137 | 19.4263 | 18.0442 | 15.7674 | 12.5295 | 9.5537 | 6.1242 | 3.0221 | 0.15579 | -10.5432 | -19.02 | -23.8779 | 23.6411 | 22.3726 | 20.8632 | 19.4811 | 17.2042 | 13.9653 | 10.9874 | 7.5568 | 4.4537 | 1.5874 | -9.1158 | -17.5968 | -22.4568
|  | ASHTON PARK | EE |  |  |  | 28.2263 | 27.3263 | 26.1789 | 25.0884 | 23.4663 | 21.1737 | 18.9779 | 16.2558 | 13.1316 | 10.5021 | 3.6042 | -2.7853 | -6.0947 | 22.4905 | 21.5189 | 20.3737 | 19.1684 | 17.3389 | 14.7211 | 12.2158 | 9.0853 | 5.4747 | 2.4411 | -4.8989 | -12.2684 | -16.0526 | 24.08 | 23.0895 | 21.8116 | 20.6053 | 18.7758 | 16.1568 | 13.6505 | 10.5179 | 6.9074 | 3.8726 | -3.1579 | -10.5316 | -14.3168
|  | ASHTON PARK | HT |  |  |  | 27.8253 | 26.6726 | 25.3147 | 24.0611 | 22.0453 | 19.2126 | 16.6 | 13.6158 | 10.9158 | 8.4211 | -0.91263 | -8.2947 | -12.5663 | 22.06 | 20.8137 | 19.4263 | 18.0442 | 15.7674 | 12.5295 | 9.5537 | 6.1242 | 3.0221 | 0.15579 | -10.5432 | -19.02 | -23.8779 | 23.6411 | 22.3726 | 20.8632 | 19.4811 | 17.2042 | 13.9653 | 10.9874 | 7.5568 | 4.4537 | 1.5874 | -9.1158 | -17.5968 | -22.4568
|  | ASHTON PARK | HE |  |  |  | 28.78 | 28.1421 | 27.2432 | 26.3937 | 24.9958 | 22.8853 | 20.8884 | 18.2895 | 15.4168 | 13.0568 | 5.5516 | 0.049474 | -30.4316 | 23.0842 | 22.3926 | 21.5347 | 20.5916 | 19.0053 | 16.5842 | 14.2937 | 11.2905 | 7.9579 | 5.2232 | -3.4653 | -9.86 | -12.7179 | 24.6832 | 23.9789 | 22.9716 | 22.0284 | 20.4421 | 18.02 | 15.7295 | 12.7232 | 9.3905 | 6.6547 | -2.0368 | -8.4337 | -11.2926
|  | ASHTON PARK | CF |  |  |  | 29.0884 | 28.7284 | 28.3042 | 27.9042 | 27.4558 | 26.8895 | 26.2789 | 25.4032 | 24.2389 | 22.86 | 15.3663 | 11.9853 | 10.4021 | 23.4137 | 23.0242 | 22.7095 | 22.2674 | 21.7674 | 21.1316 | 20.4421 | 19.4411 | 18.0979 | 16.5021 | 7.8 | 3.8779 | 2.0495 | 25.0179 | 24.6211 | 24.1474 | 23.7053 | 23.2053 | 22.5684 | 21.8789 | 20.8779 | 19.5347 | 17.9389 | 9.2316 | 5.3105 | 3.48
BRAMLEY (FLEE) | BRACKNELL | BAGSHOT | MINIMUM HEADROOM | SU 91122 63523 | YES | 0 | 27.9326 | 27.6 | 27.2663 | 26.9095 | 26.5421 | 26.1674 | 25.7895 | 25.4568 | 25.1558 | 24.8768 | 22.9095 | 20.9137 | -0.54737 | 24.3726 | 23.8084 | 23.2126 | 22.5642 | 21.9095 | 21.2589 | 20.62 | 20.0326 | 19.5158 | 19.0358 | 16.7453 | 14.5095 | 12.5211 | 24.9811 | 24.6505 | 24.1926 | 23.5453 | 22.8905 | 22.24 | 21.6011 | 21.0137 | 20.4958 | 20.0147 | 17.7211 | 15.4789 | 13.4905
|  | BAGSHOT | EE |  |  |  | 28.0663 | 27.8095 | 27.5368 | 27.2463 | 26.9463 | 26.6347 | 26.3337 | 26.0495 | 25.7716 | 25.5274 | 24.4589 | 22.9211 | 21.6105 | 24.5147 | 24.2189 | 23.7484 | 23.2432 | 22.7211 | 22.1916 | 21.6853 | 21.1863 | 20.6705 | 20.2653 | 18.4505 | 16.7253 | 15.2326 | 25.1137 | 24.8589 | 24.5874 | 24.2232 | 23.7021 | 23.1726 | 22.6642 | 22.1642 | 21.6484 | 21.2421 | 19.42 | 17.6853 | 16.1905
|  | BAGSHOT | HT |  |  |  | 27.9326 | 27.6 | 27.2663 | 26.9095 | 26.5421 | 26.1674 | 25.7895 | 25.4568 | 25.1558 | 24.8768 | 22.9095 | 20.9137 | 19.1589 | 24.3726 | 23.8084 | 23.2126 | 22.5642 | 21.9095 | 21.2589 | 20.62 | 20.0326 | 19.5158 | 19.0358 | 16.7453 | 14.5095 | 12.5211 | 24.9811 | 24.6505 | 24.1926 | 23.5453 | 22.8905 | 22.24 | 21.6011 | 21.0137 | 20.4958 | 20.0147 | 17.7211 | 15.4789 | 13.4905
|  | BAGSHOT | HE |  |  |  | 28.2495 | 28.0789 | 27.8926 | 27.6842 | 27.4621 | 27.2232 | 26.9937 | 26.7779 | 26.5716 | 26.4 | 25.7958 | 25.4126 | -0.54737 | 24.7095 | 24.5326 | 24.3379 | 24.1168 | 23.7505 | 23.3642 | 22.9968 | 22.6274 | 22.2589 | 21.9968 | 20.8389 | 19.7147 | 18.7705 | 25.2958 | 25.1274 | 24.9411 | 24.7337 | 24.5126 | 24.2747 | 23.9768 | 23.6053 | 23.2368 | 22.9758 | 21.8137 | 20.6884 | 19.7432
|  | BAGSHOT | CF |  |  |  | 28.3526 | 28.2558 | 28.1579 | 28.0537 | 27.9474 | 27.8379 | 27.7242 | 27.6126 | 27.5021 | 27.3905 | 26.8895 | 26.6179 | 26.4505 | 24.8179 | 24.7158 | 24.6126 | 24.5032 | 24.3926 | 24.2789 | 24.1011 | 23.9032 | 23.6905 | 23.4716 | 22.4558 | 21.6474 | 20.9758 | 25.3979 | 25.3021 | 25.2053 | 25.1011 | 24.9958 | 24.8874 | 24.7737 | 24.6632 | 24.5526 | 24.4432 | 23.4347 | 22.6253 | 21.9526
BRAMLEY (ANDO-THAT) | THATCHAM BSP | BALL HILL | MINIMUM HEADROOM | SU 42417 63142 | YES | 0 | 16.9389 | 16.7568 | 16.5758 | 16.3916 | 16.2084 | 16.0253 | 15.8379 | 15.6705 | 15.5137 | 15.3674 | 14.7484 | 14.1474 | 0.99789 | 14.9853 | 14.7863 | 14.5905 | 14.3916 | 14.1937 | 13.9968 | 13.7958 | 13.6137 | 13.4453 | 13.2853 | 12.6105 | 11.9368 | 11.2358 | 15.4379 | 15.2747 | 15.0789 | 14.88 | 14.6811 | 14.4853 | 14.2842 | 14.1021 | 13.9337 | 13.7737 | 13.0979 | 12.4253 | 11.7242
|  | BALL HILL | EE |  |  |  | 17.0211 | 16.8832 | 16.7389 | 16.5926 | 16.4453 | 16.2979 | 16.1558 | 16.0137 | 15.88 | 15.7558 | 15.2758 | 14.8695 | 14.4053 | 15.0758 | 14.9263 | 14.7695 | 14.6116 | 14.4526 | 14.2937 | 14.1421 | 13.9895 | 13.8453 | 13.7105 | 13.1853 | 12.7316 | 12.1989 | 15.4832 | 15.4 | 15.2579 | 15.1 | 14.9411 | 14.7821 | 14.6305 | 14.4779 | 14.3337 | 14.1989 | 13.6737 | 13.22 | 12.6863
|  | BALL HILL | HT |  |  |  | 16.9389 | 16.7568 | 16.5758 | 16.3916 | 16.2084 | 16.0253 | 15.8379 | 15.6705 | 15.5137 | 15.3674 | 14.7484 | 14.1474 | 13.5337 | 14.9853 | 14.7863 | 14.5905 | 14.3916 | 14.1937 | 13.9968 | 13.7958 | 13.6137 | 13.4453 | 13.2853 | 12.6105 | 11.9368 | 11.2358 | 15.4379 | 15.2747 | 15.0789 | 14.88 | 14.6811 | 14.4853 | 14.2842 | 14.1021 | 13.9337 | 13.7737 | 13.0979 | 12.4253 | 11.7242
|  | BALL HILL | HE |  |  |  | 17.0926 | 17.0421 | 16.9579 | 16.8579 | 16.7558 | 16.6516 | 16.5505 | 16.4558 | 16.3621 | 16.2832 | 15.9884 | 15.7737 | 0.99789 | 15.1979 | 15.1084 | 15.0095 | 14.9032 | 14.7937 | 14.6832 | 14.5758 | 14.4758 | 14.3747 | 14.2895 | 13.9716 | 13.7337 | 13.4253 | 15.5442 | 15.4916 | 15.4305 | 15.3632 | 15.2821 | 15.1716 | 15.0642 | 14.9642 | 14.8632 | 14.7779 | 14.46 | 14.2221 | 13.9137
|  | BALL HILL | CF |  |  |  | 17.1274 | 17.0989 | 17.0705 | 17.0368 | 16.9832 | 16.9274 | 16.8705 | 16.8126 | 16.7579 | 16.7021 | 16.4463 | 16.2642 | 16.1095 | 15.2632 | 15.2053 | 15.1505 | 15.0937 | 15.0347 | 14.9747 | 14.9126 | 14.8495 | 14.7905 | 14.7305 | 14.4495 | 14.2453 | 14.0663 | 15.5811 | 15.5505 | 15.52 | 15.4884 | 15.4558 | 15.4221 | 15.3874 | 15.3379 | 15.2779 | 15.2189 | 14.9379 | 14.7337 | 14.5547
MELKSHAM GSP | ANDOVER BSP | BARTON STACEY | MINIMUM HEADROOM | SU 42075 42720 | YES | 7.6842 | 16.6537 | 16.5642 | 9.0621 | 9.0063 | 8.9453 | 8.8537 | 8.5032 | 8.0884 | 8.1337 | 8.0558 | 6.4232 | 5.4684 | -7.3053 | 15.1895 | 15.0274 | 7.3874 | 7.2095 | 7.0368 | 6.8263 | 6.4337 | 5.96 | 5.8779 | 5.8011 | 3.9979 | 2.9158 | 2.2316 | 15.5253 | 15.3526 | 7.6074 | 7.4295 | 7.2568 | 7.0463 | 6.6516 | 6.1789 | 6.0947 | 6.0168 | 4.26 | 3.1674 | 2.4789
|  | BARTON STACEY | EE |  |  |  | 16.6884 | 17.2179 | 9.5158 | 9.3842 | 9.2526 | 9.12 | 8.9884 | 8.8653 | 8.7411 | 8.62 | 6.4232 | 5.4684 | 4.8663 | 15.2632 | 15.1937 | 7.4832 | 7.3421 | 7.2011 | 7.0611 | 6.9232 | 6.7916 | 6.66 | 6.5326 | 3.9979 | 2.9158 | 2.2316 | 15.6042 | 15.4726 | 7.7621 | 7.62 | 7.48 | 7.3379 | 7.1989 | 7.0674 | 6.9347 | 6.8053 | 4.26 | 3.1674 | 2.4789
|  | BARTON STACEY | HT |  |  |  | 16.6537 | 16.5642 | 9.3737 | 9.2084 | 9.0474 | 8.8537 | 8.5032 | 8.0884 | 8.1337 | 8.0558 | 7.2642 | 6.2695 | 5.9611 | 15.1895 | 15.0274 | 7.3874 | 7.2095 | 7.0368 | 6.8263 | 6.4337 | 5.96 | 5.8779 | 5.8011 | 4.9316 | 3.8158 | 3.4884 | 15.5253 | 15.3526 | 7.6074 | 7.4295 | 7.2568 | 7.0463 | 6.6516 | 6.1789 | 6.0947 | 6.0168 | 5.1411 | 4.0189 | 3.6874
|  | BARTON STACEY | HE |  |  |  | 16.7368 | 16.6916 | 9.0621 | 9.0063 | 8.9453 | 8.88 | 9.3389 | 9.2516 | 9.1653 | 9.0811 | 7.0042 | 6.4126 | -7.3053 | 15.3611 | 15.2863 | 7.6274 | 7.5368 | 7.4442 | 7.3505 | 7.3611 | 7.2705 | 7.1779 | 7.0884 | 4.6684 | 3.8484 | 3.3032 | 15.7011 | 15.6305 | 7.9674 | 7.8716 | 7.7747 | 7.6758 | 7.58 | 7.4884 | 7.3958 | 7.3053 | 4.8842 | 4.0632 | 3.5147
|  | BARTON STACEY | CF |  |  |  | 16.7653 | 16.7411 | 9.1358 | 9.1095 | 9.0811 | 9.0516 | 9.0211 | 8.9916 | 8.9621 | 8.9326 | 8.8021 | 8.7326 | 8.5716 | 15.4116 | 15.3663 | 7.7411 | 7.6884 | 7.6295 | 7.5663 | 7.5053 | 7.4516 | 7.4011 | 7.3432 | 7.0611 | 6.7505 | 6.4463 | 15.7389 | 15.7063 | 8.0863 | 8.0305 | 7.9674 | 7.8979 | 7.8316 | 7.7768 | 7.7211 | 7.6589 | 7.3537 | 7.0253 | 6.7179
BRAMLEY (BASI) | BASINGSTOKE T1A & T2A | BASINGSTOKE | MINIMUM HEADROOM | SU 65155 52705 | YES | 0.20947 | 31.6053 | 31.2558 | 30.9074 | 30.5537 | 30.1979 | 29.8463 | 28.7505 | 27.6853 | 26.6368 | 25.6116 | 24.0063 | 24.0305 | 6.8568 | 29.4547 | 29.0832 | 28.7126 | 28.3389 | 27.9632 | 27.5926 | 26.3474 | 25.1305 | 23.9316 | 22.7568 | 21.1095 | 19.9011 | 18.4663 | 29.7411 | 29.4326 | 29.06 | 28.6832 | 28.3053 | 27.9326 | 26.6874 | 25.4716 | 24.2758 | 23.1021 | 21.4789 | 21.5063 | 20.3789
|  | BASINGSTOKE | EE |  |  |  | 31.6884 | 31.4716 | 31.1895 | 30.9 | 30.6074 | 30.3137 | 30.0295 | 29.2558 | 28.2326 | 27.1895 | 24.7084 | 24.0305 | 23.0084 | 29.6063 | 29.3147 | 29.0158 | 28.7105 | 28.4032 | 28.0947 | 27.7958 | 26.9232 | 25.7505 | 24.5505 | 21.7421 | 21.1358 | 20.0074 | 29.8389 | 29.6274 | 29.3663 | 29.0589 | 28.7484 | 28.4389 | 28.1379 | 27.2621 | 26.0916 | 24.8937 | 22.0895 | 21.5063 | 20.3789
|  | BASINGSTOKE | HT |  |  |  | 31.6053 | 31.2558 | 30.9074 | 30.5537 | 30.1979 | 29.8463 | 28.7505 | 27.6853 | 26.6368 | 25.6116 | 24.0063 | 28.5095 | 27.8863 | 29.4547 | 29.0832 | 28.7126 | 28.3389 | 27.9632 | 27.5926 | 26.3474 | 25.1305 | 23.9316 | 22.7568 | 21.1095 | 19.9011 | 18.4663 | 29.7411 | 29.4326 | 29.06 | 28.6832 | 28.3053 | 27.9326 | 26.6874 | 25.4716 | 24.2758 | 23.1021 | 21.4789 | 24.8137 | 23.9558
|  | BASINGSTOKE | HE |  |  |  | 31.8137 | 31.6947 | 31.5653 | 31.4116 | 31.2126 | 31.0074 | 30.8105 | 30.1432 | 29.2958 | 28.4674 | 29.9032 | 29.64 | 6.8568 | 29.8032 | 29.64 | 29.4579 | 29.2579 | 29.0495 | 28.8347 | 28.6295 | 27.88 | 26.9053 | 25.9495 | 23.7863 | 23.3358 | 22.8168 | 29.9874 | 29.8537 | 29.7095 | 29.5568 | 29.3937 | 29.1853 | 28.9789 | 28.2179 | 27.2442 | 26.2905 | 26.7453 | 26.4221 | 26.1263
|  | BASINGSTOKE | CF |  |  |  | 31.8568 | 31.7663 | 31.6726 | 31.5758 | 31.4779 | 31.3695 | 31.2274 | 31.0884 | 30.8968 | 30.6716 | 28.0768 | 27.5274 | 27.0863 | 29.8768 | 29.7516 | 29.6284 | 29.5021 | 29.3611 | 29.2168 | 29.0674 | 28.9221 | 28.7137 | 28.4695 | 25.5011 | 24.9053 | 24.4295 | 30.0421 | 29.9379 | 29.8347 | 29.7284 | 29.62 | 29.5095 | 29.3958 | 29.2726 | 29.0632 | 28.8158 | 25.8421 | 25.2484 | 24.7726
NURSLING GSP | VELMORE BSP | BASSETT | MINIMUM HEADROOM | SU 42193 15958 | YES | 0 | 34.0495 | 33.7853 | 33.5179 | 33.2347 | 32.9411 | 32.6347 | 32.3274 | 32.0558 | 31.8074 | 31.5789 | 29.0884 | 26.9579 | 2.8526 | 30.6747 | 30.3137 | 29.8116 | 29.2326 | 28.6484 | 28.1211 | 27.6063 | 27.1358 | 26.6895 | 26.1947 | 23.3516 | 21 | 18.8653 | 31.3042 | 31.04 | 30.7726 | 30.4389 | 29.8705 | 29.3547 | 28.8516 | 28.3821 | 27.9326 | 27.4316 | 24.5505 | 22.1632 | 20.0032
|  | BASSETT | EE |  |  |  | 34.1537 | 33.9474 | 33.7295 | 33.4979 | 33.2537 | 33 | 32.7547 | 32.52 | 32.2926 | 32.0905 | 30.7 | 29.0389 | 27.5905 | 30.7853 | 30.5705 | 30.2611 | 29.8053 | 29.3474 | 28.8126 | 28.2737 | 27.8726 | 27.4874 | 27.1432 | 25.1116 | 23.2768 | 21.6611 | 31.4084 | 31.2021 | 30.9842 | 30.7526 | 30.4979 | 30.0284 | 29.5053 | 29.1126 | 28.7337 | 28.3874 | 26.3242 | 24.46 | 22.8179
|  | BASSETT | HT |  |  |  | 34.0495 | 33.7853 | 33.5179 | 33.2347 | 32.9411 | 32.6347 | 32.3274 | 32.0558 | 31.8074 | 31.5789 | 29.0884 | 26.9579 | 25.0411 | 30.6747 | 30.3137 | 29.8116 | 29.2326 | 28.6484 | 28.1211 | 27.6063 | 27.1358 | 26.6895 | 26.1947 | 23.3516 | 21 | 18.8653 | 31.3042 | 31.04 | 30.7726 | 30.4389 | 29.8705 | 29.3547 | 28.8516 | 28.3821 | 27.9326 | 27.4316 | 24.5505 | 22.1632 | 20.0032
|  | BASSETT | HE |  |  |  | 34.2863 | 34.1421 | 33.9832 | 33.8063 | 33.6168 | 33.4147 | 33.22 | 33.0358 | 32.8663 | 32.7168 | 32.2116 | 31.6168 | 2.8526 | 30.9179 | 30.7737 | 30.6126 | 30.4284 | 30.1758 | 29.7558 | 29.3295 | 29.0516 | 28.7905 | 28.5611 | 27.3074 | 26.0779 | 24.9695 | 31.5411 | 31.3968 | 31.2379 | 31.0611 | 30.8716 | 30.6695 | 30.4653 | 30.2558 | 29.9989 | 29.7726 | 28.5505 | 27.3042 | 26.1758
|  | BASSETT | CF |  |  |  | 34.3653 | 34.2821 | 34.1958 | 34.1053 | 34.0126 | 33.9158 | 33.8179 | 33.72 | 33.6253 | 33.5295 | 33.1 | 32.8842 | 32.7621 | 30.9968 | 30.9137 | 30.8274 | 30.7368 | 30.6411 | 30.5421 | 30.4389 | 30.3158 | 30.14 | 29.9621 | 29.0747 | 28.2568 | 27.4979 | 31.62 | 31.5368 | 31.4505 | 31.36 | 31.2674 | 31.1705 | 31.0726 | 30.9747 | 30.88 | 30.7842 | 30.28 | 29.4947 | 28.7358
NORTH HYDE GSP | NORTH HYDE 22kV | BATH ROAD EAST | MINIMUM HEADROOM | TQ 09097 76885 | NO | 0.14737 | 13.0716 | 13 | 12.9274 | 12.8516 | 12.7705 | 40.7863 | 40.7021 | 40.6263 | 40.5558 | 40.4916 | 40.0947 | 39.3158 | 23.5926 | 10.6116 | 10.3779 | 10.2116 | 10.0326 | 9.8379 | 37.7337 | 37.5526 | 37.3821 | 37.2168 | 37.06 | 36.3211 | 35.4526 | 34.6042 | 11.0347 | 10.8926 | 10.7242 | 10.5442 | 10.3463 | 38.2411 | 38.0579 | 37.8853 | 37.7189 | 37.56 | 36.8126 | 35.9316 | 35.0716
|  | BATH ROAD EAST | EE |  |  |  | 13.0979 | 13.0411 | 12.9811 | 12.9168 | 12.8495 | 40.8779 | 40.8095 | 40.7421 | 40.6779 | 40.62 | 40.4011 | 40.1211 | 39.5832 | 10.6768 | 10.4811 | 10.3632 | 10.2358 | 10.0989 | 38.0442 | 37.8989 | 37.7632 | 37.6253 | 37.5 | 36.9168 | 36.3484 | 35.7442 | 11.0611 | 10.9968 | 10.8779 | 10.7495 | 10.6105 | 38.5547 | 38.4084 | 38.2716 | 38.1326 | 38.0063 | 37.4168 | 36.84 | 36.2263
|  | BATH ROAD EAST | HT |  |  |  | 13.0716 | 13 | 12.9274 | 12.8516 | 12.7705 | 40.7863 | 40.7021 | 40.6263 | 40.5558 | 40.4916 | 40.0947 | 39.3158 | 38.5611 | 10.6116 | 10.3779 | 10.2116 | 10.0326 | 9.8379 | 37.7337 | 37.5526 | 37.3821 | 37.2168 | 37.06 | 36.3211 | 35.4526 | 34.6042 | 11.0347 | 10.8926 | 10.7242 | 10.5442 | 10.3463 | 38.2411 | 38.0579 | 37.8853 | 37.7189 | 37.56 | 36.8126 | 35.9316 | 35.0716
|  | BATH ROAD EAST | HE |  |  |  | 13.1284 | 13.0863 | 13.0379 | 12.9863 | 12.9295 | 40.9695 | 40.9116 | 40.8579 | 40.8063 | 40.7642 | 40.6126 | 40.5189 | 23.5926 | 10.7116 | 10.5947 | 10.5095 | 10.4147 | 10.3074 | 38.2842 | 38.1684 | 38.0568 | 37.9495 | 37.8579 | 37.4411 | 36.9568 | 36.5168 | 11.0916 | 11.0495 | 11.0011 | 10.9305 | 10.8221 | 38.7979 | 38.68 | 38.5684 | 38.4589 | 38.3674 | 37.9463 | 37.4547 | 37.0084
|  | BATH ROAD EAST | CF |  |  |  | 13.1484 | 13.12 | 13.0916 | 13.0632 | 13.0326 | 41.1011 | 41.0684 | 41.0379 | 41.0063 | 40.9758 | 40.8358 | 40.7663 | 40.7263 | 10.7347 | 10.7032 | 10.6684 | 10.6 | 10.5242 | 38.5432 | 38.4568 | 38.3916 | 38.3232 | 38.2568 | 37.9126 | 37.6063 | 37.3126 | 11.1116 | 11.0832 | 11.0547 | 11.0263 | 10.9958 | 39.0579 | 38.9716 | 38.9063 | 38.8368 | 38.7695 | 38.4211 | 38.1116 | 37.8137
IVER 132KV | LONGFORD | BATH ROAD WEST | MINIMUM HEADROOM | TQ 05814 76820 | YES | 2 | 23.5653 | 23.5189 | 23.4726 | 23.4232 | 23.3726 | 23.3189 | 23.2663 | 23.2189 | 23.1758 | 23.1358 | 22.9779 | 22.4126 | -9.7863 | 19.2916 | 19.2295 | 19.1589 | 18.3158 | 18.2726 | 18.2284 | 18.1853 | 18.1432 | 18.1032 | 18.0632 | 17.3263 | 16.6579 | 16.0326 | 19.8895 | 19.8432 | 19.7968 | 19.2 | 19.1568 | 19.1126 | 19.0695 | 19.0274 | 18.9874 | 18.9474 | 18.2147 | 17.5463 | 16.9221
|  | BATH ROAD WEST | EE |  |  |  | 23.5821 | 23.5453 | 23.5074 | 23.4663 | 23.4232 | 23.3789 | 23.3358 | 23.2937 | 23.2537 | 23.2179 | 23.0989 | 23.0084 | 22.6642 | 19.3168 | 19.2695 | 19.2137 | 18.3158 | 18.2726 | 18.2284 | 18.1853 | 18.1432 | 18.1032 | 18.0674 | 17.8874 | 17.4158 | 16.9411 | 19.9063 | 19.8695 | 19.8316 | 19.2 | 19.1568 | 19.1126 | 19.0695 | 19.0274 | 18.9874 | 18.9516 | 18.7737 | 18.3032 | 17.8295
|  | BATH ROAD WEST | HT |  |  |  | 23.5653 | 23.5189 | 23.4726 | 23.4232 | 23.3726 | 23.3189 | 23.2663 | 23.2189 | 23.1758 | 23.1358 | 22.9779 | 22.4126 | 21.8684 | 19.2916 | 19.2295 | 19.1589 | 19.0589 | 18.94 | 18.7747 | 18.5821 | 18.4021 | 18.2274 | 18.0632 | 17.3263 | 16.6579 | 16.0326 | 19.8895 | 19.8432 | 19.7968 | 19.7474 | 19.6968 | 19.6432 | 19.4653 | 19.2853 | 19.1116 | 18.9474 | 18.2147 | 17.5463 | 16.9221
|  | BATH ROAD WEST | HE |  |  |  | 23.6042 | 23.5789 | 23.5495 | 23.5179 | 23.4842 | 23.4474 | 23.4126 | 23.38 | 23.3495 | 23.3232 | 23.2337 | 23.1663 | -9.7863 | 19.3484 | 19.3168 | 19.2747 | 19.2242 | 19.1674 | 19.0842 | 19.0011 | 18.92 | 18.8211 | 18.7116 | 18.2295 | 17.7916 | 17.4116 | 19.9284 | 19.9032 | 19.8737 | 19.8421 | 19.8084 | 19.7716 | 19.7368 | 19.7042 | 19.6737 | 19.5958 | 19.1137 | 18.6737 | 18.2947
|  | BATH ROAD WEST | CF |  |  |  | 25.5126 | 25.4979 | 25.4821 | 25.4653 | 25.4484 | 25.4305 | 25.4126 | 25.3947 | 25.3779 | 25.36 | 25.2821 | 25.2432 | 25.2211 | 19.4168 | 19.3947 | 19.3674 | 19.3358 | 19.3 | 19.26 | 19.2189 | 19.1779 | 19.1358 | 19.0916 | 18.8853 | 18.7305 | 18.5916 | 20.6063 | 20.5895 | 20.5705 | 20.5495 | 20.5274 | 20.5032 | 20.4779 | 20.4537 | 20.4295 | 20.4042 | 20.1842 | 20.0705 | 19.9747
IVER 132KV | UPTON BSP | BEACONSFIELD | MINIMUM HEADROOM | SU 93668 91219 | YES | 0.19895 | 24.1126 | 23.8516 | 23.5874 | 23.3095 | 25.9221 | 25.6189 | 25.3137 | 25.0263 | 24.7158 | 24.4253 | 23.0674 | 21.4326 | -4.6768 | 20.5011 | 19.8884 | 19.2326 | 18.5337 | 20.6589 | 20.1726 | 19.6737 | 19.2116 | 18.7432 | 18.2958 | 16.2347 | 14.3747 | 12.7379 | 21.0768 | 20.7579 | 20.3905 | 19.7558 | 21.8842 | 21.3989 | 20.9 | 20.44 | 19.9726 | 19.52 | 17.4337 | 15.5526 | 13.9063
|  | BEACONSFIELD | EE |  |  |  | 24.2179 | 24.0168 | 23.8053 | 23.5789 | 26.2432 | 25.9926 | 25.7484 | 25.5158 | 25.2916 | 25.0895 | 24.0853 | 23.0979 | 22.0537 | 20.6863 | 20.2295 | 19.6821 | 19.0853 | 21.3074 | 20.9137 | 20.5284 | 20.1474 | 19.7505 | 19.3705 | 17.72 | 16.2842 | 15.0663 | 21.1821 | 20.9758 | 20.7032 | 20.3021 | 22.5274 | 22.1337 | 21.7474 | 21.3653 | 20.9684 | 20.5853 | 18.9095 | 17.44 | 16.2105
|  | BEACONSFIELD | HT |  |  |  | 24.1126 | 23.8516 | 23.5874 | 23.3095 | 25.9221 | 25.6189 | 25.3137 | 25.0263 | 24.7158 | 24.4253 | 23.0674 | 21.4326 | 20.0021 | 20.5011 | 19.8884 | 19.2326 | 18.5337 | 20.6589 | 20.1726 | 19.6737 | 19.2116 | 18.7432 | 18.2958 | 16.2347 | 14.3747 | 12.7379 | 21.0768 | 20.7579 | 20.3905 | 19.7558 | 21.8842 | 21.3989 | 20.9 | 20.44 | 19.9726 | 19.52 | 17.4337 | 15.5526 | 13.9063
|  | BEACONSFIELD | HE |  |  |  | 24.3579 | 24.2242 | 24.0768 | 23.9137 | 26.6379 | 26.4453 | 26.26 | 26.0863 | 25.9232 | 25.78 | 25.2842 | 24.9358 | -4.6768 | 20.8621 | 20.6653 | 20.26 | 19.7989 | 22.1505 | 21.8789 | 21.6095 | 21.3463 | 21.0674 | 20.8021 | 19.7211 | 18.8442 | 18.0884 | 21.3221 | 21.1884 | 21.0305 | 20.8526 | 23.3589 | 23.0916 | 22.8221 | 22.5568 | 22.2789 | 22.0137 | 20.9305 | 20.0526 | 19.2863
|  | BEACONSFIELD | CF |  |  |  | 24.4379 | 24.3642 | 24.2874 | 24.2074 | 27.0253 | 26.9379 | 26.8474 | 26.76 | 26.6726 | 26.5863 | 26.1937 | 25.9905 | 25.8337 | 20.9537 | 20.8653 | 20.7632 | 20.5389 | 23.1716 | 23.0189 | 22.8642 | 22.7063 | 22.5337 | 22.3547 | 21.4958 | 20.8411 | 20.2937 | 21.4021 | 21.3284 | 21.2516 | 21.1684 | 23.9768 | 23.8874 | 23.7947 | 23.7011 | 23.5821 | 23.4632 | 22.7126 | 22.0589 | 21.5126
BRAMLEY (ANDO-THAT) | THATCHAM BSP | BEENHAM | MINIMUM HEADROOM | SU 58204 69025 | YES | 1.2305 | 10.6105 | 10.5221 | 10.4337 | 10.3389 | 10.2421 | 10.1421 | 10.0411 | 9.9516 | 9.8716 | 9.7968 | 9.3632 | 8.6242 | -1.6705 | 8.9947 | 8.8358 | 8.6789 | 7.9411 | 7.8611 | 7.7779 | 7.6968 | 7.6221 | 7.5463 | 7.4726 | 6.7684 | 5.9011 | 5.4274 | 9.3116 | 9.2179 | 9.1242 | 8.4442 | 8.3642 | 8.28 | 8.2 | 8.1242 | 8.0474 | 7.9726 | 7.2674 | 6.3989 | 5.9211
|  | BEENHAM | EE |  |  |  | 10.6453 | 10.5779 | 10.5053 | 10.4295 | 10.3495 | 10.2663 | 10.1853 | 10.1105 | 10.0368 | 9.9726 | 9.4158 | 8.7147 | 8.26 | 9.0663 | 8.9463 | 8.82 | 7.9411 | 7.8611 | 7.7779 | 7.6968 | 7.6221 | 7.5495 | 7.4853 | 6.7716 | 5.9526 | 5.4274 | 9.3484 | 9.2779 | 9.2011 | 8.4442 | 8.3642 | 8.28 | 8.2 | 8.1242 | 8.0505 | 7.9853 | 7.2684 | 6.4463 | 5.9211
|  | BEENHAM | HT |  |  |  | 10.6105 | 10.5221 | 10.4337 | 10.3389 | 10.2421 | 10.1421 | 10.0411 | 9.9516 | 9.8716 | 9.7968 | 9.3632 | 8.6242 | 8.3611 | 8.9947 | 8.8358 | 8.6789 | 8.5168 | 8.3558 | 8.2011 | 7.9947 | 7.6274 | 7.5463 | 7.4726 | 6.7684 | 5.9011 | 5.62 | 9.3116 | 9.2179 | 9.1242 | 9.0011 | 8.8463 | 8.6874 | 8.4863 | 8.1284 | 8.0474 | 7.9726 | 7.2674 | 6.3989 | 6.1158
|  | BEENHAM | HE |  |  |  | 10.6937 | 10.6484 | 10.5989 | 10.5442 | 10.4853 | 10.4211 | 10.36 | 10.3021 | 10.2484 | 10.2021 | 10.0432 | 9.9516 | -1.6705 | 9.1379 | 9.0884 | 9.0074 | 8.9221 | 8.8326 | 8.7442 | 8.66 | 8.5747 | 8.5011 | 8.4358 | 8.1863 | 7.7653 | 7.3547 | 9.4011 | 9.3537 | 9.3011 | 9.2442 | 9.1832 | 9.1168 | 9.0547 | 8.9947 | 8.9389 | 8.8926 | 8.6768 | 8.2632 | 7.8537
|  | BEENHAM | CF |  |  |  | 10.7211 | 10.6968 | 10.6716 | 10.6453 | 10.6179 | 10.5884 | 10.56 | 10.5316 | 10.5032 | 10.4747 | 10.3463 | 10.2821 | 10.2463 | 9.1684 | 9.1411 | 9.1126 | 9.0726 | 9.0232 | 8.9737 | 8.9253 | 8.8779 | 8.8295 | 8.7821 | 8.5611 | 8.3853 | 8.1821 | 9.4295 | 9.4042 | 9.3768 | 9.3495 | 9.32 | 9.2895 | 9.2589 | 9.2295 | 9.2 | 9.1695 | 9.0326 | 8.8747 | 8.6726
MANNINGTON GSP | SALISBURY | BEMERTON | MINIMUM HEADROOM | SU 11583 31233 | YES | 0.40842 | 32.9589 | 32.7463 | 32.5189 | 32.2442 | 31.2853 | 30.9305 | 30.0642 | 29.3379 | 29.0305 | 28.7495 | 29.6053 | 27.4747 | 6.5642 | 30.1211 | 29.7389 | 29.3221 | 28.8411 | 27.8505 | 27.4421 | 26.4832 | 25.6842 | 25.3621 | 25.0684 | 26.5253 | 24.1463 | 21.76 | 30.72 | 30.4989 | 30.2705 | 29.8874 | 28.8611 | 28.4421 | 27.4568 | 26.6358 | 26.3063 | 26.0053 | 26.9937 | 24.5916 | 22.1958
|  | BEMERTON | EE |  |  |  | 33.0347 | 32.8684 | 32.6863 | 32.4821 | 31.7537 | 30.9305 | 30.0642 | 29.3379 | 29.0305 | 28.7495 | 30.8642 | 29.1516 | 27.4811 | 30.2853 | 29.9874 | 29.6474 | 29.2453 | 28.3368 | 27.4421 | 26.4832 | 25.6842 | 25.3621 | 25.0684 | 27.9179 | 26.04 | 24.1421 | 30.8011 | 30.6263 | 30.4379 | 30.2347 | 29.3505 | 28.4421 | 27.4568 | 26.6358 | 26.3063 | 26.0053 | 28.3926 | 26.4632 | 24.5526
|  | BEMERTON | HT |  |  |  | 32.9589 | 32.7463 | 32.5189 | 32.2442 | 31.2853 | 34.0484 | 33.1053 | 32.3284 | 31.9874 | 31.6221 | 29.6053 | 27.4747 | 25.3726 | 30.1211 | 29.7389 | 29.3221 | 28.8411 | 27.8505 | 31.3558 | 30.3137 | 29.4589 | 29.1 | 28.7116 | 26.5253 | 24.1463 | 21.76 | 30.72 | 30.4989 | 30.2705 | 29.8874 | 28.8611 | 31.9368 | 30.8684 | 29.9937 | 29.6274 | 29.2284 | 26.9937 | 24.5916 | 22.1958
|  | BEMERTON | HE |  |  |  | 33.1421 | 33.0263 | 32.8989 | 32.7579 | 32.3726 | 31.6358 | 30.86 | 30.2242 | 30.0168 | 29.8284 | 32.42 | 31.1884 | 6.5642 | 30.46 | 30.32 | 30.0832 | 29.7789 | 28.9632 | 28.1979 | 27.3368 | 26.6316 | 26.4147 | 26.2189 | 29.5653 | 28.2 | 26.7274 | 30.9147 | 30.7968 | 30.6611 | 30.5095 | 30 | 29.2095 | 28.3274 | 27.6032 | 27.3842 | 27.1842 | 30.0905 | 28.6832 | 27.1926
|  | BEMERTON | CF |  |  |  | 33.2053 | 33.1389 | 33.0705 | 32.9989 | 32.9147 | 32.8137 | 32.4832 | 32.1379 | 32.0053 | 31.8716 | 31.2453 | 34.2063 | 33.3895 | 30.5305 | 30.46 | 30.3653 | 30.2063 | 29.8379 | 29.4821 | 29.0737 | 28.72 | 28.5884 | 28.4526 | 27.7937 | 31.5211 | 30.6074 | 30.9779 | 30.9116 | 30.8411 | 30.7632 | 30.6674 | 30.5368 | 30.1063 | 29.7347 | 29.5979 | 29.4589 | 28.7989 | 32.0968 | 31.1526
COWLEY GSP | COWLEY LOCAL (2 X 45) | BERINSFIELD | MINIMUM HEADROOM | SU 58382 95467 | YES | 0.70526 | 23.2895 | 22.5811 | 21.7737 | 20.4758 | 18.8337 | 16.2716 | 16.1347 | 16.0053 | 14.2147 | 11.6221 | 0.29158 | -5.6105 | -53.3179 | 21.9442 | 21.1337 | 20.2032 | 18.6874 | 16.4432 | 13.6063 | 13.4695 | 13.34 | 11.1011 | 8.0011 | -5.7874 | -12.6305 | -13.0253 | 22.1032 | 21.2895 | 20.3568 | 18.8347 | 16.3663 | 13.7316 | 13.5947 | 13.4653 | 11.2147 | 8.1021 | -5.7442 | -12.6516 | -13.0463
|  | BERINSFIELD | EE |  |  |  | 23.4453 | 22.8147 | 22.08 | 20.8505 | 18.8337 | 18.6484 | 18.4695 | 18.3021 | 18.1411 | 17.9968 | 18.1789 | 15.32 | 14.4758 | 22.1147 | 21.3895 | 20.54 | 19.0989 | 16.7137 | 16.5284 | 16.3495 | 16.1821 | 16.0211 | 15.8768 | 15.5758 | 12.2716 | 11.3221 | 22.2747 | 21.5463 | 20.6937 | 19.2474 | 16.8537 | 16.6684 | 16.4895 | 16.3221 | 16.1611 | 16.0168 | 15.4989 | 12.2011 | 11.2526
|  | BERINSFIELD | HT |  |  |  | 23.2895 | 22.5811 | 21.7737 | 20.4758 | 19.0853 | 18.8632 | 18.6389 | 18.4432 | 18.2642 | 18.1021 | 17.4442 | 14.3284 | 13.1347 | 21.9442 | 21.1337 | 20.2032 | 18.6874 | 16.4432 | 16.2211 | 15.9968 | 15.8011 | 15.6221 | 15.46 | 14.8021 | 11.2221 | 9.8842 | 22.1032 | 21.2895 | 20.3568 | 18.8347 | 16.3663 | 16.1442 | 15.92 | 15.7242 | 15.5453 | 15.3832 | 14.7253 | 11.1516 | 9.8158
|  | BERINSFIELD | HE |  |  |  | 23.6579 | 23.1295 | 22.4895 | 21.3558 | 19.4263 | 16.2716 | 16.1347 | 16.0053 | 15.8853 | 15.7821 | 16.0621 | 13.4589 | -53.3179 | 22.3495 | 21.7347 | 20.9905 | 19.6537 | 17.3642 | 13.6063 | 13.4695 | 13.34 | 13.22 | 13.1168 | 12.9653 | 9.9368 | 9.3326 | 22.5095 | 21.8926 | 21.1453 | 19.8032 | 17.5053 | 13.7316 | 13.5947 | 13.4653 | 13.3453 | 13.2421 | 12.8947 | 9.8716 | 9.2684
|  | BERINSFIELD | CF |  |  |  | 23.8537 | 23.5653 | 23.2484 | 22.7316 | 21.9084 | 20.6242 | 18.8253 | 16.6179 | 14.2147 | 11.6221 | 0.29158 | -5.6105 | -5.9589 | 22.5716 | 22.2368 | 21.8684 | 21.2589 | 20.2842 | 18.7547 | 16.6084 | 13.9726 | 11.1011 | 8.0011 | -5.7874 | -12.6305 | -13.0253 | 22.7326 | 22.3968 | 22.0263 | 21.4147 | 20.4358 | 18.9011 | 16.7453 | 14.0979 | 11.2147 | 8.1021 | -5.7442 | -12.6516 | -13.0463
NURSLING GSP | SOUTHAMPTON (2 X 60) | BEVOIS VALLEY | MINIMUM HEADROOM | SU 42648 13187 | YES | 0.31579 | 35.1326 | 34.9895 | 34.8453 | 34.6916 | 34.2495 | 33.9716 | 33.6968 | 33.4463 | 33.2042 | 32.9389 | 31.4021 | 30.0779 | 5.8663 | 30.1737 | 29.6663 | 29.3926 | 29.0716 | 28.3 | 28.0011 | 27.7053 | 27.4347 | 27.1726 | 26.8811 | 25.1463 | 23.6453 | 22.2368 | 31.3168 | 30.8263 | 30.5621 | 30.2526 | 29.4926 | 29.1926 | 28.8968 | 28.6274 | 28.3642 | 28.0726 | 26.3379 | 24.8358 | 23.4274
|  | BEVOIS VALLEY | EE |  |  |  | 35.1937 | 35.0842 | 34.9684 | 34.8453 | 34.6105 | 34.3368 | 34.0558 | 33.8379 | 33.6305 | 33.4389 | 32.3368 | 31.3168 | 30.3874 | 30.3 | 29.8579 | 29.6453 | 29.3947 | 28.6979 | 28.3958 | 28.0863 | 27.8516 | 27.6263 | 27.4211 | 26.1863 | 25.0253 | 23.9579 | 31.44 | 31.0126 | 30.8053 | 30.5642 | 29.8895 | 29.5874 | 29.2779 | 29.0432 | 28.8189 | 28.6126 | 27.3779 | 26.2158 | 25.1484
|  | BEVOIS VALLEY | HT |  |  |  | 35.1326 | 34.9895 | 34.8453 | 34.6916 | 34.2495 | 33.9716 | 33.6968 | 33.4463 | 33.2042 | 32.9389 | 31.4021 | 30.0779 | 28.8453 | 30.1737 | 29.6663 | 29.3926 | 29.0716 | 28.3 | 28.0011 | 27.7053 | 27.4347 | 27.1726 | 26.8811 | 25.1463 | 23.6453 | 22.2368 | 31.3168 | 30.8263 | 30.5621 | 30.2526 | 29.4926 | 29.1926 | 28.8968 | 28.6274 | 28.3642 | 28.0726 | 26.3379 | 24.8358 | 23.4274
|  | BEVOIS VALLEY | HE |  |  |  | 35.2421 | 35.1526 | 35.0537 | 34.9453 | 34.8158 | 34.6779 | 34.4779 | 34.3168 | 34.1653 | 34.0337 | 33.3421 | 32.6684 | 5.8663 | 30.3853 | 30.0547 | 29.9011 | 29.7095 | 29.0684 | 28.8189 | 28.5642 | 28.3937 | 28.2316 | 28.0926 | 27.3253 | 26.5547 | 25.8505 | 31.5242 | 31.2042 | 31.0526 | 30.8642 | 30.26 | 30.0105 | 29.7558 | 29.5853 | 29.4242 | 29.2842 | 28.5168 | 27.7463 | 27.0411
|  | BEVOIS VALLEY | CF |  |  |  | 35.2726 | 35.2116 | 35.1484 | 35.0832 | 35.0158 | 34.9453 | 34.8737 | 34.8042 | 34.7347 | 34.6621 | 34.2926 | 33.8179 | 33.3863 | 30.4158 | 30.3547 | 30.2916 | 30.2263 | 30.0358 | 29.6905 | 29.4032 | 29.2316 | 29.1116 | 28.9905 | 28.3874 | 27.8474 | 27.3463 | 31.5547 | 31.4937 | 31.4305 | 31.3653 | 31.18 | 30.8463 | 30.5747 | 30.4095 | 30.2937 | 30.1768 | 29.5789 | 29.04 | 28.5379
EAST CLAYDON GSP | BICESTER NORTH BSP | BICESTER | MINIMUM HEADROOM | SP 58381 21988 | YES | 1.8411 | 42.4526 | 42.1105 | 41.7147 | 41.2684 | 40.7979 | 39.9095 | 38.0432 | 36.2295 | 34.7042 | 33.2095 | 26.0589 | 19.8621 | -11.4347 | 37.4726 | 36.8895 | 35.7116 | 34.1011 | 32.2916 | 30.2895 | 28.1316 | 26.0158 | 24.2389 | 22.4968 | 14.1179 | 6.8295 | 0.88105 | 38.3853 | 38.0284 | 36.9505 | 35.3189 | 33.4842 | 31.4526 | 29.2821 | 27.1653 | 25.3905 | 23.6463 | 15.2642 | 7.9716 | 2.02
|  | BICESTER | EE |  |  |  | 42.5726 | 42.3074 | 41.98 | 43.8589 | 42.3832 | 40.7379 | 38.9884 | 37.2589 | 35.7989 | 34.3747 | 28.1358 | 22.5232 | 18.3211 | 37.6011 | 37.2989 | 36.2611 | 34.8442 | 33.1305 | 31.2137 | 29.1705 | 27.1474 | 25.4463 | 23.7821 | 15.9116 | 9.4084 | 4.5337 | 38.5147 | 38.2295 | 37.5063 | 35.9979 | 34.2842 | 32.3663 | 30.3211 | 28.2979 | 26.5968 | 24.9316 | 17.0568 | 10.5484 | 5.6716
|  | BICESTER | HT |  |  |  | 42.4526 | 42.1105 | 41.7147 | 41.2684 | 40.7979 | 39.9095 | 38.0432 | 36.2295 | 34.7042 | 33.2095 | 26.0589 | 19.8621 | 14.8074 | 37.4726 | 36.8895 | 35.7116 | 34.1011 | 32.2916 | 30.2895 | 28.1316 | 26.0158 | 24.2389 | 22.4968 | 14.1179 | 6.8295 | 0.88105 | 38.3853 | 38.0284 | 36.9505 | 35.3189 | 33.4842 | 31.4526 | 29.2821 | 27.1653 | 25.3905 | 23.6463 | 15.2642 | 7.9716 | 2.02
|  | BICESTER | HE |  |  |  | 42.7474 | 42.5653 | 42.3453 | 42.0453 | 41.7137 | 41.3526 | 40.2474 | 38.6505 | 37.3263 | 36.0347 | 29.9905 | 25.0895 | -11.4347 | 37.7884 | 37.5926 | 37.0105 | 35.6947 | 34.1642 | 32.4232 | 30.5558 | 28.6832 | 27.1316 | 25.6147 | 18.4589 | 12.6284 | 8.3958 | 38.7021 | 38.5063 | 38.2621 | 36.9274 | 35.3747 | 33.6074 | 31.7116 | 29.8347 | 28.2821 | 26.7642 | 19.6063 | 13.7737 | 9.5389
|  | BICESTER | CF |  |  |  | 42.8474 | 42.7411 | 42.6316 | 42.5179 | 42.3937 | 42.2368 | 42.0558 | 41.8611 | 41.6674 | 41.4821 | 37.1811 | 33.6221 | 31.5126 | 37.8958 | 37.7842 | 37.6621 | 37.5347 | 37.2011 | 36.5874 | 35.6916 | 34.5432 | 33.4042 | 32.3579 | 26.8968 | 22.6611 | 20.1505 | 38.8074 | 38.6979 | 38.5758 | 38.4474 | 38.3105 | 37.8337 | 36.9242 | 35.7568 | 34.6011 | 33.5389 | 28.0463 | 23.8116 | 21.2989
EAST CLAYDON GSP | BICESTER NORTH BSP | BICESTER NORTH | MINIMUM HEADROOM | SP 59720 23735 | YES | 2.4263 | 32.2926 | 32.0558 | 31.8158 | 31.5621 | 31.2989 | 31.0263 | 30.7537 | 30.5126 | 30.2937 | 30.0905 | 29.2653 | 28.6411 | 3.5926 | 31.9463 | 31.6874 | 31.4242 | 31.1495 | 30.8453 | 30.3979 | 29.9537 | 29.5484 | 29.1695 | 28.8137 | 27.2126 | 25.8389 | 24.6242 | 28.0905 | 27.8537 | 27.6137 | 27.36 | 27.0968 | 26.8253 | 26.5516 | 26.3105 | 26.0916 | 25.8895 | 25.0642 | 24.4411 | 23.9526
|  | BICESTER NORTH | EE |  |  |  | 32.3758 | 32.1863 | 31.9863 | 33.8905 | 33.6526 | 33.3947 | 33.1453 | 32.8663 | 32.5537 | 32.2695 | 31.0895 | 30.1421 | 29.3463 | 32.0389 | 31.8337 | 31.6168 | 31.3863 | 31.1463 | 30.8863 | 30.6316 | 30.3421 | 30.0137 | 29.7137 | 28.4568 | 27.4358 | 26.5663 | 28.1737 | 27.9842 | 27.7842 | 32.0684 | 31.8274 | 31.5653 | 31.3116 | 31.02 | 30.6895 | 30.3884 | 29.12 | 28.0884 | 27.2116
|  | BICESTER NORTH | HT |  |  |  | 32.2926 | 32.0558 | 31.8158 | 31.5621 | 31.2989 | 31.0263 | 30.7537 | 30.5126 | 30.2937 | 30.0905 | 29.2653 | 28.6411 | 27.5558 | 31.9463 | 31.6874 | 31.4242 | 31.1495 | 30.8453 | 30.3979 | 29.9537 | 29.5484 | 29.1695 | 28.8137 | 27.2126 | 25.8389 | 24.6242 | 28.0905 | 27.8537 | 27.6137 | 27.36 | 27.0968 | 26.8253 | 26.5516 | 26.3105 | 26.0916 | 25.8895 | 25.0642 | 24.4411 | 23.9526
|  | BICESTER NORTH | HE |  |  |  | 32.5021 | 32.3726 | 32.2295 | 32.0705 | 31.9 | 31.7168 | 31.5421 | 31.3779 | 31.2221 | 31.0895 | 30.6379 | 30.3747 | 3.5926 | 32.1653 | 32.0358 | 31.8895 | 31.7211 | 31.54 | 31.3358 | 31.1379 | 30.9526 | 30.7789 | 30.6295 | 30.1432 | 29.7389 | 29.3211 | 28.3 | 28.1705 | 28.0274 | 27.8684 | 27.6979 | 27.5147 | 27.3411 | 27.1758 | 27.02 | 26.8884 | 26.4368 | 26.1737 | 26.0105
|  | BICESTER NORTH | CF |  |  |  | 32.5758 | 32.5011 | 32.4242 | 32.3442 | 32.2621 | 32.1747 | 32.0874 | 32.0011 | 31.9158 | 31.8305 | 31.4505 | 31.2589 | 31.1526 | 32.2389 | 32.1642 | 32.0874 | 32.0074 | 31.92 | 31.8263 | 31.7274 | 31.6305 | 31.5337 | 31.4368 | 31.0095 | 30.7863 | 30.4474 | 28.3737 | 28.2989 | 28.2221 | 28.1421 | 28.06 | 27.9726 | 27.8853 | 27.8 | 27.7147 | 27.6284 | 27.2484 | 27.0568 | 26.9505
LOVEDEAN GSP | CHICHESTER & HUNSTON | BILLINGSHURST | MINIMUM HEADROOM | TQ 08305 26315 | YES | 0 | 12.4063 | 12.1632 | 11.9021 | 11.6105 | 11.3 | 11 | 10.6811 | 10.3263 | 9.9895 | 9.6653 | 7.2368 | 4.9695 | -2.8147 | 10.6842 | 10.3074 | 9.8853 | 9.4032 | 8.8737 | 8.3747 | 7.8263 | 7.1463 | 6.4853 | 5.84 | 2.9421 | 0.34526 | -2.0811 | 11.5474 | 11.1853 | 10.7747 | 10.2863 | 9.7526 | 9.2547 | 8.7063 | 8.0274 | 7.3674 | 6.7232 | 3.8295 | 1.2368 | -1.1863
|  | BILLINGSHURST | EE |  |  |  | 12.5 | 12.3074 | 12.0905 | 11.8432 | 11.6063 | 11.3779 | 11.1316 | 10.8263 | 10.5347 | 10.2568 | 8.6432 | 6.7947 | 5.0937 | 10.8274 | 10.5284 | 10.1758 | 9.7611 | 9.3789 | 9.0274 | 8.6137 | 8.0305 | 7.4705 | 6.9242 | 4.5284 | 2.4 | 0.43579 | 11.6316 | 11.4011 | 11.0579 | 10.6516 | 10.2621 | 9.9063 | 9.4926 | 8.9105 | 8.3516 | 7.8053 | 5.4137 | 3.2884 | 1.3284
|  | BILLINGSHURST | HT |  |  |  | 12.4063 | 12.1632 | 11.9021 | 11.6105 | 11.3 | 11 | 10.6811 | 10.3263 | 9.9895 | 9.6653 | 7.2368 | 4.9695 | 2.8589 | 10.6842 | 10.3074 | 9.8853 | 9.4032 | 8.8737 | 8.3747 | 7.8263 | 7.1463 | 6.4853 | 5.84 | 2.9421 | 0.34526 | -2.0811 | 11.5474 | 11.1853 | 10.7747 | 10.2863 | 9.7526 | 9.2547 | 8.7063 | 8.0274 | 7.3674 | 6.7232 | 3.8295 | 1.2368 | -1.1863
|  | BILLINGSHURST | HE |  |  |  | 12.6242 | 12.4926 | 12.3295 | 12.1389 | 11.9526 | 11.7716 | 11.5716 | 11.3137 | 11.0684 | 10.8368 | 9.7516 | 8.1853 | -2.8147 | 11.0137 | 10.8053 | 10.5337 | 10.2053 | 9.9 | 9.6179 | 9.28 | 8.7705 | 8.2789 | 7.8011 | 5.7389 | 3.9189 | 2.2484 | 11.7168 | 11.6326 | 11.4074 | 11.0884 | 10.7916 | 10.5042 | 10.16 | 9.6495 | 9.1589 | 8.6821 | 6.6232 | 4.8063 | 3.1379
|  | BILLINGSHURST | CF |  |  |  | 12.6947 | 12.6189 | 12.5326 | 12.4316 | 12.34 | 12.2558 | 12.16 | 12.0326 | 11.9074 | 11.7779 | 11.1621 | 10.6758 | 10.1642 | 11.1179 | 10.9979 | 10.8516 | 10.6737 | 10.52 | 10.3884 | 10.2295 | 9.9895 | 9.7505 | 9.5011 | 8.2611 | 7.1579 | 6.1632 | 11.7663 | 11.7179 | 11.6684 | 11.5442 | 11.3958 | 11.2674 | 11.1126 | 10.88 | 10.6379 | 10.3811 | 9.1411 | 8.04 | 7.0463
LOVEDEAN GSP | CHICHESTER & HUNSTON | BILSHAM | MINIMUM HEADROOM | SU 97366 01594 | YES | 9.3063 | 19.6074 | 17.7453 | 15.7526 | 13.1737 | 10.3684 | 40.0021 | 39.6326 | 36.6253 | 34.3832 | 32.1674 | 27.7989 | 24.38 | 3.0516 | 18.1053 | 15.9779 | 13.5379 | 10.6758 | 7.4284 | 37.0642 | 36.6979 | 33.2032 | 30.6084 | 28.0421 | 23.0979 | 19.2263 | 15.2968 | 18.2747 | 16.2211 | 13.7484 | 10.8958 | 7.6484 | 37.2811 | 36.9116 | 33.42 | 30.8263 | 28.2632 | 23.3084 | 19.4232 | 15.4853
|  | BILSHAM | EE |  |  |  | 19.8463 | 17.7453 | 15.8232 | 13.3537 | 10.6495 | 40.3379 | 40.0326 | 37.3042 | 35.08 | 32.8547 | 28.8737 | 26.2326 | 23.4611 | 18.6347 | 15.9779 | 13.5379 | 10.6758 | 7.5368 | 37.2284 | 36.9295 | 33.76 | 31.1874 | 28.6063 | 24.1021 | 21.1368 | 17.9674 | 20.4537 | 18.3958 | 13.7484 | 10.9811 | 7.6979 | 37.3853 | 37.08 | 33.9105 | 31.3347 | 28.7526 | 24.2179 | 21.2189 | 18.0284
|  | BILSHAM | HT |  |  |  | 19.6074 | 17.7863 | 15.7526 | 13.1737 | 10.3684 | 40.0021 | 39.6326 | 36.6253 | 34.3832 | 32.1674 | 27.7989 | 24.38 | 20.9432 | 18.1053 | 16.0116 | 13.6674 | 10.6811 | 7.4284 | 37.0642 | 36.6979 | 33.2032 | 30.6084 | 28.0421 | 23.0979 | 19.2263 | 15.2968 | 18.2747 | 16.2211 | 13.8779 | 10.8958 | 7.6484 | 37.2811 | 36.9116 | 33.42 | 30.8263 | 28.2632 | 23.3084 | 19.4232 | 15.4853
|  | BILSHAM | HE |  |  |  | 20.2021 | 18.2716 | 16.5116 | 14.2 | 11.6453 | 41.4053 | 41.1768 | 38.5358 | 36.4253 | 34.3474 | 31.0232 | 29.0137 | 3.0516 | 18.9989 | 16.6589 | 14.2747 | 11.5779 | 8.5989 | 38.3589 | 38.1326 | 35.0484 | 32.5905 | 30.1663 | 26.3505 | 24.0442 | 21.4821 | 20.7137 | 18.7789 | 14.4874 | 11.8874 | 8.7863 | 38.5463 | 38.3179 | 35.24 | 32.7853 | 30.3642 | 26.5495 | 24.2411 | 21.68
|  | BILSHAM | CF |  |  |  | 20.6147 | 19.5063 | 18.5337 | 17.4768 | 16.3611 | 45.0842 | 43.6832 | 42.5905 | 41.7189 | 40.7589 | 37.2074 | 36.1379 | 34.78 | 19.4316 | 17.9632 | 16.9337 | 15.3874 | 14.0874 | 42.5989 | 40.9632 | 39.6916 | 38.6832 | 37.5674 | 33.4589 | 32.2442 | 30.6663 | 20.9379 | 19.3779 | 18.9274 | 15.5632 | 14.3095 | 42.8737 | 41.2968 | 40.0684 | 38.8684 | 37.7547 | 33.6516 | 32.4368 | 30.8589
FAWLEY GSP | COWES & WOOTTON COMMON BSP | BINSTEAD | MINIMUM HEADROOM | SZ 56409 91399 | YES | 0 | 16.4747 | 16.1621 | 15.8484 | 15.5337 | 15.2021 | 14.8137 | 14.4095 | 14.0168 | 13.6368 | 13.2537 | 10.9832 | 9.5453 | -0.28526 | 14.9442 | 14.6074 | 14.2716 | 13.9347 | 13.58 | 13.1695 | 12.7442 | 12.3274 | 11.9242 | 11.5158 | 9.0621 | 7.5758 | 5.9937 | 15.1021 | 14.7653 | 14.4274 | 14.0916 | 13.7358 | 13.3179 | 12.8842 | 12.46 | 12.0474 | 11.6295 | 9.1116 | 7.5505 | 5.9389
|  | BINSTEAD | EE |  |  |  | 16.5432 | 16.3053 | 16.0611 | 15.8589 | 15.5874 | 15.2842 | 14.9547 | 14.6284 | 14.3263 | 14.0168 | 12.4084 | 10.8137 | 9.6579 | 15.0547 | 14.8 | 14.54 | 14.2863 | 13.9968 | 13.6821 | 13.34 | 13.0011 | 12.6926 | 12.3737 | 10.72 | 9.0789 | 7.8137 | 15.2537 | 14.9947 | 14.7305 | 14.4432 | 14.1526 | 13.8305 | 13.4779 | 13.1284 | 12.8074 | 12.4758 | 10.7316 | 8.9863 | 7.6895
|  | BINSTEAD | HT |  |  |  | 16.4747 | 16.1621 | 15.8484 | 15.5337 | 15.2021 | 14.8137 | 14.4095 | 14.0168 | 13.6368 | 13.2537 | 10.9832 | 9.5453 | 8.1063 | 14.9442 | 14.6074 | 14.2716 | 13.9347 | 13.58 | 13.1695 | 12.7442 | 12.3274 | 11.9242 | 11.5158 | 9.0621 | 7.5758 | 5.9937 | 15.1021 | 14.7653 | 14.4274 | 14.0916 | 13.7358 | 13.3179 | 12.8842 | 12.46 | 12.0474 | 11.6295 | 9.1116 | 7.5505 | 5.9389
|  | BINSTEAD | HE |  |  |  | 16.6747 | 16.5842 | 16.4284 | 16.32 | 16.1305 | 15.9042 | 15.6726 | 15.4453 | 15.24 | 15.02 | 13.9526 | 12.9642 | -0.28526 | 15.2516 | 15.1021 | 14.9368 | 14.7863 | 14.5842 | 14.3495 | 14.1074 | 13.8695 | 13.6568 | 13.4253 | 12.2884 | 11.2084 | 10.2663 | 15.4074 | 15.3021 | 15.1347 | 14.9442 | 14.7421 | 14.5021 | 14.2547 | 14.0105 | 13.7937 | 13.5558 | 12.38 | 11.2716 | 10.3032
|  | BINSTEAD | CF |  |  |  | 16.7305 | 16.6821 | 16.6326 | 16.5453 | 16.4263 | 16.2853 | 16.1379 | 15.9979 | 15.9284 | 15.7989 | 15.2926 | 14.6684 | 14.1242 | 15.3105 | 15.26 | 15.1737 | 15.0568 | 14.9274 | 14.7758 | 14.6189 | 14.4663 | 14.3558 | 14.2179 | 13.6884 | 13.0042 | 12.4063 | 15.4663 | 15.4147 | 15.3632 | 15.2558 | 15.1232 | 14.9663 | 14.8032 | 14.6484 | 14.5042 | 14.3642 | 13.8211 | 13.1221 | 12.5063
LOVEDEAN GSP | CHICHESTER & HUNSTON | BIRDHAM | MINIMUM HEADROOM | SZ 81965 99422 | YES | 0 | 14.3032 | 14.0411 | 13.7768 | 13.1105 | 32.48 | 31.7432 | 31.0516 | 30.42 | 29.8653 | 29.3979 | 27.3095 | 25.08 | 9.0853 | 10.2905 | 9.7905 | 9.2063 | 8.4811 | 27.8011 | 26.9989 | 26.2358 | 25.5389 | 24.9263 | 24.4147 | 22.1063 | 19.5916 | 17.2916 | 10.7074 | 10.2189 | 9.6474 | 8.9421 | 28.2779 | 27.4621 | 26.6979 | 26.0011 | 25.3884 | 24.8758 | 22.5674 | 20.0526 | 17.7516
|  | BIRDHAM | EE |  |  |  | 14.4084 | 14.2074 | 13.9937 | 13.6453 | 33.1326 | 32.5137 | 31.9379 | 31.3811 | 30.9116 | 30.5337 | 28.9537 | 27.2084 | 25.6389 | 10.5168 | 10.1337 | 9.6526 | 9.0537 | 28.5011 | 27.8284 | 27.2042 | 26.5863 | 26.0705 | 25.6589 | 23.9158 | 21.9379 | 20.1453 | 10.9284 | 10.5537 | 10.0842 | 9.5011 | 28.9632 | 28.3032 | 27.6663 | 27.0484 | 26.5326 | 26.1211 | 24.3779 | 22.3989 | 20.6063
|  | BIRDHAM | HT |  |  |  | 14.3032 | 14.0411 | 13.7768 | 13.1105 | 32.48 | 31.7432 | 31.0516 | 30.42 | 29.8653 | 29.3979 | 27.3095 | 25.08 | 23.0537 | 10.2905 | 9.7905 | 9.2063 | 8.4811 | 27.8011 | 26.9989 | 26.2358 | 25.5389 | 24.9263 | 24.4147 | 22.1063 | 19.5916 | 17.2916 | 10.7074 | 10.2189 | 9.6474 | 8.9421 | 28.2779 | 27.4621 | 26.6979 | 26.0011 | 25.3884 | 24.8758 | 22.5674 | 20.0526 | 17.7516
|  | BIRDHAM | HE |  |  |  | 14.5516 | 14.4179 | 14.2695 | 14.1063 | 33.9232 | 33.4126 | 32.9432 | 32.4884 | 32.1232 | 31.8453 | 30.7421 | 29.4305 | 9.0853 | 10.8211 | 10.5832 | 10.2379 | 9.7726 | 29.3474 | 28.7905 | 28.28 | 27.7842 | 27.3884 | 27.0863 | 25.8663 | 24.3663 | 23.0232 | 11.1326 | 10.9926 | 10.6558 | 10.2042 | 29.7895 | 29.2495 | 28.7526 | 28.2537 | 27.8505 | 27.5484 | 26.3284 | 24.8274 | 23.4842
|  | BIRDHAM | CF |  |  |  | 14.6337 | 14.5611 | 14.4863 | 14.4074 | 34.3263 | 34.2421 | 34.1568 | 33.98 | 33.78 | 33.6158 | 32.8284 | 31.9611 | 31.2179 | 10.9747 | 10.8316 | 10.6442 | 10.4137 | 30.1958 | 29.9295 | 29.6653 | 29.3926 | 29.1758 | 29 | 28.1526 | 27.1758 | 26.3189 | 11.2189 | 11.1421 | 11.0537 | 10.8295 | 30.6189 | 30.36 | 30.1042 | 29.8389 | 29.6284 | 29.4568 | 28.6295 | 27.6389 | 26.78
BOTLEY WOOD GSP | NETLEY COMMON BSP | BISHOPS WALTHAM | MINIMUM HEADROOM | SU 56691 16683 | YES | 0.17789 | 24.42 | 39.7474 | 39.0295 | 38.1768 | 37.3789 | 36.7032 | 36.0389 | 35.4116 | 34.1989 | 33.8853 | 30.9811 | 26.8937 | 7.3358 | 22.8347 | 38.1558 | 37.4295 | 36.8568 | 35.9895 | 35.2705 | 34.5663 | 33.8947 | 32.5284 | 32.2158 | 29.0274 | 24.3916 | 21.2389 | 22.6926 | 37.9947 | 37.2463 | 37.0589 | 36.1937 | 35.4747 | 34.7684 | 34.0979 | 32.7326 | 32.4189 | 29.2316 | 24.5968 | 21.4442
|  | BISHOPS WALTHAM | EE |  |  |  | 24.7211 | 40.2053 | 39.6253 | 38.9074 | 38.2421 | 37.6926 | 37.1653 | 36.6705 | 36.1726 | 35.6368 | 33.1053 | 28.1158 | 24.3253 | 23.1411 | 38.6937 | 38.0716 | 37.6484 | 36.9263 | 36.3432 | 35.7842 | 35.2589 | 34.7295 | 34.1484 | 31.3558 | 25.6126 | 21.2389 | 23.0074 | 38.5684 | 37.9484 | 37.1747 | 36.4632 | 35.8853 | 35.3316 | 34.8116 | 34.2863 | 33.7137 | 30.9621 | 25.8105 | 21.4442
|  | BISHOPS WALTHAM | HT |  |  |  | 24.42 | 39.7474 | 39.0295 | 38.1768 | 37.3789 | 36.7032 | 36.0389 | 35.4116 | 34.1989 | 33.8853 | 30.9811 | 26.8937 | 25.6337 | 22.8347 | 38.1558 | 37.4295 | 36.8568 | 35.9895 | 35.2705 | 34.5663 | 33.8947 | 32.5284 | 32.2158 | 29.0274 | 24.3916 | 23.04 | 22.6926 | 37.9947 | 37.2463 | 37.0589 | 36.1937 | 35.4747 | 34.7684 | 34.0979 | 32.7326 | 32.4189 | 29.2316 | 24.5968 | 23.2442
|  | BISHOPS WALTHAM | HE |  |  |  | 25.1284 | 40.8074 | 40.4137 | 39.8768 | 39.3811 | 38.9874 | 38.6179 | 38.2716 | 37.9263 | 37.5389 | 35.7158 | 30.3705 | 7.3358 | 23.6821 | 39.3421 | 38.92 | 38.3368 | 37.8032 | 37.3916 | 37.0053 | 36.6442 | 36.2811 | 35.8663 | 33.8695 | 27.9621 | 23.9568 | 23.5526 | 39.2137 | 38.7937 | 38.2137 | 37.6821 | 37.2716 | 36.8853 | 36.5253 | 36.1621 | 35.7474 | 33.7579 | 27.7011 | 23.8021
|  | BISHOPS WALTHAM | CF |  |  |  | 25.3368 | 41.1432 | 40.92 | 40.6411 | 40.3853 | 40.1705 | 39.9558 | 39.7463 | 39.5389 | 39.2874 | 37.9463 | 36.8926 | 36.0042 | 23.7632 | 39.5674 | 39.3411 | 39.1526 | 38.8747 | 38.6463 | 38.4179 | 38.1947 | 37.9747 | 37.7021 | 36.2411 | 35.0684 | 34.0684 | 23.6495 | 39.4474 | 39.2137 | 39.0263 | 38.7495 | 38.5221 | 38.2937 | 38.0716 | 37.8516 | 37.5811 | 36.1263 | 34.9589 | 33.9663
NURSLING GSP | VELMORE BSP | BISHOPSTOKE | MINIMUM HEADROOM | SU 46463 18472 | YES | 7.7895 | 7.9116 | 7.8926 | 7.8758 | 7.8568 | 7.8368 | 7.8189 | 7.8105 | 7.8 | 7.7916 | 7.7842 | 7.7505 | 7.7084 | -1.4379 | 7.7232 | 7.7011 | 7.6811 | 7.6589 | 7.6358 | 7.6147 | 7.6042 | 7.5937 | 7.5832 | 7.5747 | 7.5368 | 7.4863 | 7.4389 | 7.5758 | 7.5537 | 7.5337 | 7.5116 | 7.4884 | 7.4674 | 7.4579 | 7.4463 | 7.4368 | 7.4274 | 7.3895 | 7.34 | 7.2916
|  | BISHOPSTOKE | EE |  |  |  | 7.9168 | 7.9011 | 7.8842 | 7.8674 | 7.8516 | 7.8358 | 7.8274 | 7.8211 | 7.8137 | 7.8074 | 7.7853 | 7.7526 | 7.7221 | 7.7284 | 7.7105 | 7.6916 | 7.6716 | 7.6526 | 7.6337 | 7.6253 | 7.6179 | 7.6095 | 7.6021 | 7.5758 | 7.5379 | 7.5021 | 7.5811 | 7.5632 | 7.5442 | 7.5242 | 7.5053 | 7.4874 | 7.4779 | 7.4705 | 7.4621 | 7.4547 | 7.4284 | 7.3916 | 7.3558
|  | BISHOPSTOKE | HT |  |  |  | 7.9116 | 7.8926 | 7.8758 | 7.8568 | 7.8368 | 7.8189 | 7.8105 | 7.8 | 7.7916 | 7.7842 | 7.7505 | 7.7084 | 7.6674 | 7.7232 | 7.7011 | 7.6811 | 7.6589 | 7.6358 | 7.6147 | 7.6042 | 7.5937 | 7.5832 | 7.5747 | 7.5368 | 7.4863 | 7.4389 | 7.5758 | 7.5537 | 7.5337 | 7.5116 | 7.4884 | 7.4674 | 7.4579 | 7.4463 | 7.4368 | 7.4274 | 7.3895 | 7.34 | 7.2916
|  | BISHOPSTOKE | HE |  |  |  | 7.9168 | 7.9074 | 7.8979 | 7.8832 | 7.8695 | 7.8568 | 7.8526 | 7.8474 | 7.8432 | 7.8421 | 7.8316 | 7.8126 | -1.4379 | 7.7284 | 7.7179 | 7.7074 | 7.6905 | 7.6737 | 7.6589 | 7.6547 | 7.6484 | 7.6432 | 7.6421 | 7.6305 | 7.6084 | 7.5895 | 7.5811 | 7.5705 | 7.56 | 7.5432 | 7.5263 | 7.5116 | 7.5074 | 7.5021 | 7.4958 | 7.4947 | 7.4832 | 7.4621 | 7.4421
|  | BISHOPSTOKE | CF |  |  |  | 7.9232 | 7.9211 | 7.9168 | 8.3179 | 8.3179 | 8.3168 | 8.3168 | 8.3158 | 8.3158 | 8.3147 | 8.3126 | 8.3116 | 8.3116 | 7.7358 | 7.7337 | 7.7295 | 7.7347 | 7.7326 | 7.7284 | 7.7253 | 7.7211 | 7.7179 | 7.7137 | 7.7011 | 7.6916 | 7.6842 | 7.5832 | 7.5832 | 7.5821 | 7.5884 | 7.5884 | 7.5863 | 7.5853 | 7.5832 | 7.5821 | 7.58 | 7.5747 | 7.5716 | 7.5516
BOTLEY WOOD GSP | NETLEY COMMON BSP | BITTERNE | MINIMUM HEADROOM | SU 45116 13082 | YES | 0 | 12.9179 | 12.6326 | 12.3442 | 12.0368 | 11.7211 | 11.3947 | 11.0663 | 10.7242 | 10.2863 | 9.8179 | 7.2884 | 5.2158 | -11.1379 | 10.4432 | 9.9 | 9.3642 | 8.7558 | 8.1453 | 7.5926 | 7.0432 | 6.5516 | 6.0842 | 5.5779 | 2.7863 | 0.48842 | -1.58 | 11.12 | 10.5874 | 10.0632 | 9.4579 | 8.8389 | 8.2789 | 7.7221 | 7.2242 | 6.7505 | 6.2358 | 3.3874 | 1.04 | -1.0758
|  | BITTERNE | EE |  |  |  | 13.0274 | 12.8021 | 12.5653 | 12.3126 | 12.0495 | 11.7768 | 11.5137 | 11.2642 | 11.0242 | 10.7695 | 8.9379 | 7.34 | 5.9368 | 10.6684 | 10.2653 | 9.8389 | 9.3611 | 8.8789 | 8.3337 | 7.7884 | 7.3674 | 6.9621 | 6.5989 | 4.5905 | 2.8116 | 1.2368 | 11.26 | 10.9442 | 10.5274 | 10.0579 | 9.5842 | 9.0316 | 8.4768 | 8.0505 | 7.64 | 7.2726 | 5.2242 | 3.4063 | 1.7947
|  | BITTERNE | HT |  |  |  | 12.9179 | 12.6326 | 12.3442 | 12.0368 | 11.7211 | 11.3947 | 11.0663 | 10.7242 | 10.2863 | 9.8179 | 7.2884 | 5.2158 | 3.3621 | 10.4432 | 9.9 | 9.3642 | 8.7558 | 8.1453 | 7.5926 | 7.0432 | 6.5516 | 6.0842 | 5.5779 | 2.7863 | 0.48842 | -1.58 | 11.12 | 10.5874 | 10.0632 | 9.4579 | 8.8389 | 8.2789 | 7.7221 | 7.2242 | 6.7505 | 6.2358 | 3.3874 | 1.04 | -1.0758
|  | BITTERNE | HE |  |  |  | 13.1768 | 13.0232 | 12.8547 | 12.6663 | 12.4653 | 12.2505 | 12.0432 | 11.8505 | 11.6684 | 11.5137 | 10.9863 | 9.9979 | -11.1379 | 10.8747 | 10.6863 | 10.4737 | 10.1368 | 9.7916 | 9.3726 | 8.9484 | 8.6568 | 8.38 | 8.14 | 6.8979 | 5.72 | 4.6705 | 11.4095 | 11.2558 | 11.0874 | 10.8158 | 10.4768 | 10.0674 | 9.6516 | 9.3621 | 9.0821 | 8.8389 | 7.5747 | 6.3695 | 5.2926
|  | BITTERNE | CF |  |  |  | 13.2653 | 13.18 | 13.0895 | 12.9968 | 12.9011 | 12.8011 | 12.6989 | 12.6 | 12.5 | 12.4021 | 11.9611 | 11.7421 | 11.4042 | 10.9905 | 10.8768 | 10.7621 | 10.6442 | 10.5021 | 10.3242 | 10.1421 | 9.9547 | 9.7737 | 9.5937 | 8.6989 | 7.9105 | 7.2042 | 11.4979 | 11.4126 | 11.3221 | 11.2295 | 11.1337 | 11.0011 | 10.8232 | 10.6389 | 10.4611 | 10.2853 | 9.4021 | 8.5958 | 7.8705
MINETY GSP | STRATTON (2 X 60) | BLACK BOURTON | MINIMUM HEADROOM | SP 28349 03818 | YES | 0 | 11.6621 | 11.5537 | 11.4316 | 11.2389 | 11.0547 | 10.6242 | 10.12 | 9.5105 | 9.4189 | 9.3347 | 8.26 | 6.8421 | -4.8632 | 10.1158 | 9.9316 | 9.7474 | 9.5411 | 9.3442 | 8.8579 | 8.2853 | 7.5853 | 7.4937 | 7.4095 | 6.2042 | 4.5811 | 4.1505 | 10.2558 | 10.0589 | 9.8642 | 9.6568 | 9.4611 | 8.9758 | 8.4032 | 7.7053 | 7.6137 | 7.5295 | 6.3253 | 4.7042 | 4.2747
|  | BLACK BOURTON | EE |  |  |  | 11.7053 | 11.62 | 11.5316 | 11.4368 | 11.2895 | 11.14 | 10.9968 | 10.8537 | 10.7179 | 10.5926 | 10.0789 | 8.7274 | 7.8495 | 10.1989 | 10.0558 | 9.9095 | 9.7568 | 9.5989 | 9.44 | 9.2874 | 9.1358 | 8.9895 | 8.8558 | 8.2979 | 6.7389 | 5.7295 | 10.3389 | 10.1926 | 10.0368 | 9.8747 | 9.7158 | 9.5568 | 9.4042 | 9.2526 | 9.1063 | 8.9726 | 8.4158 | 6.86 | 5.8516
|  | BLACK BOURTON | HT |  |  |  | 11.6621 | 11.5537 | 11.4316 | 11.2389 | 11.0547 | 10.6242 | 10.12 | 9.5105 | 9.4189 | 9.3347 | 8.26 | 6.8421 | 6.4474 | 10.1158 | 9.9316 | 9.7474 | 9.5411 | 9.3442 | 8.8579 | 8.2853 | 7.5853 | 7.4937 | 7.4095 | 6.2042 | 4.5811 | 4.1505 | 10.2558 | 10.0589 | 9.8642 | 9.6568 | 9.4611 | 8.9758 | 8.4032 | 7.7053 | 7.6137 | 7.5295 | 6.3253 | 4.7042 | 4.2747
|  | BLACK BOURTON | HE |  |  |  | 11.7653 | 11.7105 | 11.6495 | 11.5821 | 11.5095 | 11.4337 | 11.36 | 11.2905 | 11.1958 | 11.1095 | 10.7842 | 9.7611 | -4.8632 | 10.3126 | 10.2232 | 10.1284 | 10.0253 | 9.9211 | 9.8137 | 9.7105 | 9.6084 | 9.5095 | 9.4168 | 9.0653 | 7.88 | 7.0589 | 10.4442 | 10.36 | 10.2695 | 10.1632 | 10.0537 | 9.9421 | 9.8337 | 9.7274 | 9.6253 | 9.5337 | 9.1821 | 7.9989 | 7.1789
|  | BLACK BOURTON | CF |  |  |  | 11.8 | 11.7705 | 11.7389 | 11.7053 | 11.6705 | 11.6358 | 11.6 | 11.5653 | 11.5305 | 11.4958 | 11.2495 | 10.8516 | 10.3263 | 10.3705 | 10.3179 | 10.2632 | 10.2053 | 10.1432 | 10.0811 | 10.0147 | 9.9568 | 9.8989 | 9.8421 | 9.5516 | 9.0958 | 8.4853 | 10.4989 | 10.4495 | 10.3979 | 10.3442 | 10.2853 | 10.2189 | 10.1484 | 10.0874 | 10.0253 | 9.9642 | 9.6684 | 9.2126 | 8.6032
MANNINGTON GSP | LYTCHETT | BLANDFORD | MINIMUM HEADROOM | ST 88810 05536 | YES | 1.3211 | 43.5958 | 43.0495 | 42.2768 | 41.5295 | 40.6116 | 40.2695 | 39.3653 | 38.6537 | 37.9674 | 37.3095 | 34.42 | 31.8368 | 6.1137 | 37.2853 | 36.6958 | 35.8432 | 35.0211 | 34.0021 | 33.7116 | 32.7253 | 31.9579 | 31.2189 | 30.5095 | 27.4242 | 24.6758 | 21.9758 | 38.9968 | 38.4074 | 37.5537 | 36.7316 | 35.7116 | 35.3295 | 34.3358 | 33.56 | 32.8084 | 32.0884 | 28.9284 | 26.0926 | 23.3568
|  | BLANDFORD | EE |  |  |  | 43.8295 | 43.4053 | 42.7368 | 42.0926 | 41.2737 | 40.3568 | 39.5484 | 38.9021 | 38.2653 | 37.6537 | 35.7337 | 33.5926 | 31.7168 | 37.54 | 37.0832 | 36.3432 | 35.6358 | 34.7242 | 33.7137 | 32.8316 | 32.1411 | 31.4621 | 30.8116 | 28.9158 | 26.7063 | 24.64 | 39.2516 | 38.7947 | 38.0537 | 37.3453 | 36.4326 | 35.4126 | 34.52 | 33.8158 | 33.1232 | 32.4568 | 30.3747 | 28.0442 | 25.94
|  | BLANDFORD | HT |  |  |  | 43.5958 | 43.0495 | 42.2768 | 41.5295 | 40.6116 | 40.2695 | 39.3653 | 38.6537 | 37.9674 | 37.3095 | 34.42 | 31.8368 | 29.3958 | 37.2853 | 36.6958 | 35.8432 | 35.0211 | 34.0021 | 33.7116 | 32.7253 | 31.9579 | 31.2189 | 30.5095 | 27.4242 | 24.6758 | 21.9758 | 38.9968 | 38.4074 | 37.5537 | 36.7316 | 35.7116 | 35.3295 | 34.3358 | 33.56 | 32.8084 | 32.0884 | 28.9284 | 26.0926 | 23.3568
|  | BLANDFORD | HE |  |  |  | 44.1537 | 43.8821 | 43.3653 | 42.8632 | 42.18 | 41.3979 | 40.7358 | 40.2379 | 39.7568 | 39.3053 | 38.2263 | 36.9947 | 6.1137 | 37.8937 | 37.6032 | 37.0274 | 36.4726 | 35.7095 | 34.8411 | 34.1126 | 33.5747 | 33.0537 | 32.5642 | 31.5042 | 30.1758 | 28.7042 | 39.6053 | 39.3147 | 38.7389 | 38.1842 | 37.42 | 36.5442 | 35.8105 | 35.2663 | 34.7389 | 34.2421 | 33.0589 | 31.6947 | 30.1926
|  | BLANDFORD | CF |  |  |  | 44.3432 | 44.1758 | 43.8979 | 43.6368 | 43.3074 | 42.9411 | 42.6 | 42.3168 | 42.0305 | 41.7379 | 40.4516 | 40.2842 | 39.4253 | 38.1 | 37.92 | 37.6095 | 37.3211 | 36.9516 | 36.5463 | 36.1695 | 35.8621 | 35.5484 | 35.2274 | 33.8253 | 33.7368 | 32.7853 | 39.8105 | 39.6305 | 39.3211 | 39.0326 | 38.6632 | 38.2547 | 37.8747 | 37.5642 | 37.2474 | 36.9242 | 35.5074 | 35.32 | 34.3474
COWLEY GSP | WITNEY BSP | BLEDINGTON | MINIMUM HEADROOM | SP 25641 22580 | YES | 0 | 4.9337 | 4.84 | 4.7263 | 4.5758 | 4.4284 | 4.2811 | 4.1347 | 4.0032 | 3.88 | 3.7663 | 3.2295 | 2.6505 | -2.1379 | 5.5758 | 5.4158 | 5.2621 | 5.0989 | 4.9389 | 4.78 | 4.6232 | 4.4811 | 4.3474 | 4.2242 | 3.6316 | 2.9737 | 2.2958 | 4.9021 | 4.8158 | 4.7284 | 4.6347 | 4.5389 | 4.4411 | 4.3421 | 4.2558 | 4.1768 | 4.1063 | 3.6884 | 3.0347 | 2.3579
|  | BLEDINGTON | EE |  |  |  | 4.9716 | 4.8989 | 4.8221 | 4.7347 | 4.6179 | 4.4989 | 4.3832 | 4.2726 | 4.1663 | 4.0684 | 3.6684 | 3.2411 | 2.78 | 5.6463 | 5.5242 | 5.4011 | 5.2737 | 5.1484 | 5.0211 | 4.8958 | 4.7768 | 4.6632 | 4.5568 | 4.1179 | 3.6316 | 3.0947 | 4.9337 | 4.8705 | 4.7979 | 4.7221 | 4.6432 | 4.5621 | 4.4853 | 4.4105 | 4.3389 | 4.2758 | 4.0442 | 3.6895 | 3.1558
|  | BLEDINGTON | HT |  |  |  | 4.9337 | 4.84 | 4.7263 | 4.5758 | 4.4284 | 4.2811 | 4.1347 | 4.0032 | 3.88 | 3.7663 | 3.2295 | 2.6505 | 2.0621 | 5.5758 | 5.4158 | 5.2621 | 5.0989 | 4.9389 | 4.78 | 4.6232 | 4.4811 | 4.3474 | 4.2242 | 3.6316 | 2.9737 | 2.2958 | 4.9021 | 4.8158 | 4.7284 | 4.6347 | 4.5389 | 4.4411 | 4.3421 | 4.2558 | 4.1768 | 4.1063 | 3.6884 | 3.0347 | 2.3579
|  | BLEDINGTON | HE |  |  |  | 5.0253 | 4.9779 | 4.9253 | 4.8695 | 4.8084 | 4.7442 | 4.6832 | 4.62 | 4.5463 | 4.48 | 4.2337 | 3.9421 | -2.1379 | 5.7453 | 5.6695 | 5.5895 | 5.5063 | 5.4211 | 5.3295 | 5.2421 | 5.1589 | 5.0811 | 5.0105 | 4.7421 | 4.4063 | 4.0137 | 4.9789 | 4.9368 | 4.8895 | 4.8389 | 4.7811 | 4.72 | 4.6611 | 4.6042 | 4.5526 | 4.5074 | 4.3547 | 4.2516 | 4.0705
|  | BLEDINGTON | CF |  |  |  | 5.0558 | 5.0284 | 5.0021 | 4.9737 | 4.9432 | 4.9126 | 4.8821 | 4.8526 | 4.8221 | 4.7926 | 4.5947 | 4.4105 | 4.1937 | 5.7947 | 5.7495 | 5.7053 | 5.6558 | 5.6032 | 5.5495 | 5.4968 | 5.4495 | 5.4011 | 5.3505 | 5.12 | 4.9095 | 4.6537 | 5.0053 | 4.9821 | 4.9589 | 4.9337 | 4.9084 | 4.8811 | 4.8547 | 4.8263 | 4.7979 | 4.7695 | 4.6442 | 4.5737 | 4.5242
BRAMLEY (FLEE) | ALTON | BORDON | MINIMUM HEADROOM | SU 82256 35269 | YES | 0.49053 | 24.1021 | 23.6242 | 23.1011 | 22.5421 | 21.3547 | 19.8021 | 18.0179 | 16.2726 | 14.8284 | 13.6526 | 8.3242 | 4.1863 | -27.8642 | 18.8263 | 17.1368 | 15.8116 | 14.3463 | 12.9274 | 11.2063 | 9.2147 | 7.2463 | 5.5989 | 4.2768 | -1.6642 | -6.2674 | -10.4968 | 19.8916 | 18.1632 | 16.8105 | 15.3126 | 13.8663 | 12.1042 | 10.0653 | 8.0558 | 6.4074 | 5.0821 | -0.88316 | -5.5168 | -9.7558
|  | BORDON | EE |  |  |  | 24.2726 | 23.9137 | 23.4758 | 23.0084 | 22.4053 | 21.0726 | 19.5032 | 17.9221 | 16.62 | 15.5916 | 11.1 | 7.7516 | 4.8242 | 19.2105 | 17.7179 | 16.5653 | 15.2916 | 14.0884 | 12.5895 | 10.8358 | 9.0632 | 7.6063 | 6.4474 | 1.4316 | -2.2737 | -5.5853 | 20.2832 | 18.7547 | 17.5768 | 16.2758 | 15.0463 | 13.5137 | 11.7137 | 9.8947 | 8.4074 | 7.2442 | 2.1884 | -1.5642 | -4.8863
|  | BORDON | HT |  |  |  | 24.1021 | 23.6242 | 23.1011 | 22.5421 | 21.3547 | 19.8021 | 18.0179 | 16.2726 | 14.8284 | 13.6526 | 8.3242 | 4.1863 | 0.43263 | 18.8263 | 17.1368 | 15.8116 | 14.3463 | 12.9274 | 11.2063 | 9.2147 | 7.2463 | 5.5989 | 4.2768 | -1.6642 | -6.2674 | -10.4968 | 19.8916 | 18.1632 | 16.8105 | 15.3126 | 13.8663 | 12.1042 | 10.0653 | 8.0558 | 6.4074 | 5.0821 | -0.88316 | -5.5168 | -9.7558
|  | BORDON | HE |  |  |  | 24.5147 | 24.2695 | 23.9842 | 23.6316 | 23.2621 | 22.6105 | 21.2432 | 19.8547 | 18.7484 | 17.9126 | 14.4253 | 12.0295 | -27.8642 | 19.7389 | 18.4968 | 17.5863 | 16.5432 | 15.56 | 14.2653 | 12.7179 | 11.1505 | 9.9105 | 8.9811 | 5.0042 | 2.2958 | -0.15684 | 20.82 | 19.5463 | 18.6158 | 17.5484 | 16.5453 | 15.2189 | 13.6305 | 12.0221 | 10.7495 | 9.7968 | 5.7989 | 3.0789 | 0.61789
|  | BORDON | CF |  |  |  | 24.6547 | 24.5168 | 24.3716 | 24.2232 | 24.0684 | 23.9053 | 23.7337 | 23.4968 | 23.2716 | 22.7726 | 19.5242 | 17.9589 | 16.6011 | 20.6263 | 20.3295 | 19.8884 | 19.4747 | 19.0211 | 18.4021 | 17.4884 | 16.3126 | 15.2874 | 14.4158 | 10.7432 | 8.9842 | 7.4 | 21.6053 | 21.4284 | 20.9789 | 20.5568 | 20.0937 | 19.4589 | 18.5221 | 17.3126 | 16.2589 | 15.3653 | 11.5937 | 9.7863 | 8.1947
MELKSHAM GSP | AMESBURY | BOSCOMBE DOWN | MINIMUM HEADROOM | SU 17186 41044 | YES | 0.52632 | 32.4221 | 32.2895 | 32.1558 | 32.0137 | 31.6526 | 31.2789 | 30.9105 | 30.4947 | 30.3642 | 30.2421 | 29.3263 | 28.2811 | 4.9537 | 27.8747 | 27.8242 | 27.7379 | 27.5958 | 27.1968 | 26.7863 | 26.3821 | 25.9189 | 25.7905 | 25.6716 | 24.7011 | 23.5653 | 22.7063 | 28.1411 | 28.0084 | 27.8747 | 27.7326 | 27.3368 | 26.9274 | 26.5253 | 26.0642 | 25.9337 | 25.8116 | 24.8295 | 23.6821 | 22.8232
|  | BOSCOMBE DOWN | EE |  |  |  | 33.2695 | 32.3716 | 32.2621 | 32.1453 | 32.0242 | 31.8905 | 31.7589 | 31.6337 | 31.5095 | 31.3968 | 30.4747 | 29.4747 | 28.7337 | 28.96 | 27.8242 | 27.8442 | 27.7284 | 27.6063 | 27.4758 | 27.3474 | 27.2242 | 27.1032 | 26.9947 | 26.0137 | 24.9263 | 24.0979 | 29.2632 | 28.0905 | 27.9811 | 27.8642 | 27.7432 | 27.6095 | 27.4779 | 27.3526 | 27.2284 | 27.1158 | 26.1179 | 25.0126 | 24.1842
|  | BOSCOMBE DOWN | HT |  |  |  | 32.4221 | 32.2895 | 32.1558 | 32.0137 | 31.6526 | 31.2789 | 30.9105 | 30.4947 | 30.3642 | 30.2421 | 29.3263 | 28.2811 | 27.5011 | 27.8747 | 27.8716 | 27.7379 | 27.5958 | 27.1968 | 26.7863 | 26.3821 | 25.9189 | 25.7905 | 25.6716 | 24.7011 | 23.5653 | 22.7063 | 28.1411 | 28.0084 | 27.8747 | 27.7326 | 27.3368 | 26.9274 | 26.5253 | 26.0642 | 25.9337 | 25.8116 | 24.8295 | 23.6821 | 22.8232
|  | BOSCOMBE DOWN | HE |  |  |  | 33.3916 | 32.4789 | 32.4042 | 32.3211 | 32.2316 | 32.1295 | 32.0316 | 31.94 | 31.8526 | 31.7758 | 31.2368 | 30.5505 | 4.9537 | 29.1126 | 27.9316 | 27.9863 | 27.9032 | 27.8137 | 27.7137 | 27.6168 | 27.5263 | 27.4411 | 27.3653 | 26.7884 | 26.0189 | 25.5032 | 29.42 | 28.1979 | 28.1232 | 28.04 | 27.9505 | 27.8484 | 27.7505 | 27.6589 | 27.5716 | 27.4947 | 26.9126 | 26.1411 | 25.6242
|  | BOSCOMBE DOWN | CF |  |  |  | 33.48 | 33.42 | 32.5147 | 32.4758 | 32.4347 | 32.3895 | 32.3421 | 32.2979 | 32.2516 | 32.2084 | 31.9095 | 31.5147 | 31.18 | 29.2305 | 29.1558 | 27.9674 | 27.9284 | 27.8874 | 27.8432 | 27.7968 | 27.7526 | 27.7084 | 27.6653 | 27.48 | 27.04 | 26.6642 | 29.54 | 29.4642 | 28.2337 | 28.1947 | 28.1537 | 28.1084 | 28.0611 | 28.0168 | 27.9705 | 27.9274 | 27.6126 | 27.1716 | 26.7947
MANNINGTON GSP | CHRISTCHURCH BSP | BOSCOMBE EAST | MINIMUM HEADROOM | SZ 11636 92447 | YES | 1.0516 | 33.0747 | 32.8232 | 32.5705 | 32.3011 | 32.02 | 31.7295 | 31.4358 | 31.1758 | 30.9379 | 30.5884 | 28.2642 | 26.0884 | 6.4989 | 28.8442 | 28.5926 | 28.34 | 28.0705 | 27.7874 | 27.4821 | 26.9168 | 26.3547 | 25.7611 | 25.2863 | 22.6895 | 20.2442 | 17.9389 | 29.9937 | 29.7421 | 29.4895 | 29.22 | 28.9368 | 28.6326 | 28.0768 | 27.5263 | 26.9463 | 26.4958 | 23.9105 | 21.4684 | 19.1663
|  | BOSCOMBE EAST | EE |  |  |  | 33.1726 | 32.9768 | 32.7695 | 32.5495 | 32.3168 | 32.0747 | 31.84 | 31.6158 | 31.3979 | 31.2032 | 29.9232 | 28.2316 | 26.6684 | 28.9421 | 28.7463 | 28.5389 | 28.3189 | 28.0863 | 27.8442 | 27.6095 | 27.3442 | 26.9211 | 26.4558 | 24.5284 | 22.6211 | 20.8411 | 30.0916 | 29.8958 | 29.6884 | 29.4684 | 29.2358 | 28.9937 | 28.7589 | 28.4947 | 28.0789 | 27.6253 | 25.7463 | 23.8421 | 22.0642
|  | BOSCOMBE EAST | HT |  |  |  | 33.0747 | 32.8232 | 32.5705 | 32.3011 | 32.02 | 31.7295 | 31.4358 | 31.1758 | 30.9379 | 30.5884 | 28.2642 | 26.0884 | 24.0526 | 28.8442 | 28.5926 | 28.34 | 28.0705 | 27.7874 | 27.4821 | 26.9168 | 26.3547 | 25.7611 | 25.2863 | 22.6895 | 20.2442 | 17.9389 | 29.9937 | 29.7421 | 29.4895 | 29.22 | 28.9368 | 28.6326 | 28.0768 | 27.5263 | 26.9463 | 26.4958 | 23.9105 | 21.4684 | 19.1663
|  | BOSCOMBE EAST | HE |  |  |  | 33.2895 | 33.1474 | 32.9905 | 32.8168 | 32.6305 | 32.4316 | 32.2411 | 32.0611 | 31.8937 | 31.7495 | 31.2168 | 30.2863 | 6.4989 | 29.0589 | 28.9168 | 28.76 | 28.5863 | 28.4 | 28.2011 | 28.0105 | 27.8305 | 27.6632 | 27.5189 | 26.1926 | 24.82 | 23.5663 | 30.2084 | 30.0663 | 29.9095 | 29.7358 | 29.5495 | 29.3505 | 29.16 | 28.98 | 28.8126 | 28.6684 | 27.36 | 26.0274 | 24.7758
|  | BOSCOMBE EAST | CF |  |  |  | 33.36 | 33.2726 | 33.1842 | 33.0905 | 32.9947 | 32.8947 | 32.7937 | 32.6937 | 32.5947 | 32.4958 | 32.0558 | 31.8337 | 31.6505 | 29.1295 | 29.0421 | 28.9537 | 28.86 | 28.7642 | 28.6642 | 28.5632 | 28.4632 | 28.3642 | 28.2653 | 27.8242 | 27.1821 | 26.3442 | 30.2789 | 30.1916 | 30.1032 | 30.0095 | 29.9137 | 29.8137 | 29.7126 | 29.6126 | 29.5137 | 29.4147 | 28.9737 | 28.3474 | 27.5368
EALING GSP |  | BOSTON MANOR ROAD | MINIMUM HEADROOM | TQ 17043 78092 | YES | 0 | 50.8537 | 50.7474 | 50.6411 | 70.5274 | 70.4074 | 69.56 | 68.7389 | 68.5295 | 68.3368 | 68.1526 | 67.3084 | 66.4158 | 25.0579 | 43.3 | 42.7874 | 41.9453 | 61.0695 | 59.9368 | 58.6263 | 57.62 | 57.3853 | 57.1674 | 56.9589 | 55.9958 | 54.9453 | 53.9221 | 45.1916 | 45.0537 | 44.2674 | 63.3453 | 62.2516 | 60.9863 | 60.0137 | 59.7832 | 59.5705 | 59.3663 | 58.4137 | 57.3653 | 56.3432
|  | BOSTON MANOR ROAD | EE |  |  |  | 50.8926 | 50.8063 | 50.7168 | 70.6232 | 70.5221 | 70.4168 | 70.0116 | 69.1726 | 68.6937 | 68.5295 | 67.9032 | 67.2568 | 66.6316 | 43.3811 | 43.0495 | 42.5032 | 62.0137 | 61.2895 | 60.2579 | 59.1884 | 58.1537 | 57.5737 | 57.3874 | 56.6779 | 55.9211 | 55.1737 | 45.2337 | 45.1284 | 44.8895 | 64.3421 | 63.5758 | 62.56 | 61.5274 | 60.5295 | 59.9674 | 59.7853 | 59.0916 | 58.3389 | 57.5926
|  | BOSTON MANOR ROAD | HT |  |  |  | 50.8537 | 50.7474 | 50.6411 | 70.5274 | 70.4074 | 69.56 | 68.7389 | 68.5295 | 68.3368 | 68.1526 | 67.3084 | 66.4158 | 65.5568 | 43.3 | 42.7874 | 41.9453 | 61.0695 | 59.9368 | 58.6263 | 57.62 | 57.3853 | 57.1674 | 56.9589 | 55.9958 | 54.9453 | 53.9221 | 45.1916 | 45.0537 | 44.2674 | 63.3453 | 62.2516 | 60.9863 | 60.0137 | 59.7832 | 59.5705 | 59.3663 | 58.4137 | 57.3653 | 56.3432
|  | BOSTON MANOR ROAD | HE |  |  |  | 50.9411 | 50.8789 | 50.8105 | 70.7347 | 70.6537 | 70.5674 | 70.2989 | 69.5011 | 69.1547 | 69.0389 | 68.6295 | 68.1895 | 25.0579 | 43.4811 | 43.1947 | 42.6842 | 62.24 | 61.5442 | 60.5495 | 59.5074 | 58.5189 | 58.1 | 57.9716 | 57.5105 | 56.9884 | 56.4716 | 45.2863 | 45.2063 | 45.0832 | 64.5747 | 63.8389 | 62.8463 | 61.8411 | 60.8874 | 60.4821 | 60.3558 | 59.9042 | 59.3968 | 58.8895
|  | BOSTON MANOR ROAD | CF |  |  |  | 50.9684 | 50.9295 | 50.8895 | 70.8474 | 70.8042 | 70.7589 | 70.7126 | 70.6674 | 70.6232 | 70.5789 | 70.3463 | 70.02 | 69.7347 | 43.5589 | 43.4274 | 43.2737 | 63.1947 | 63.1095 | 63.0221 | 62.9295 | 62.7474 | 62.3684 | 61.8947 | 59.5958 | 59.2084 | 58.8632 | 45.3168 | 45.2716 | 45.2221 | 65.1768 | 65.1305 | 65.0821 | 65.0326 | 64.9768 | 64.7421 | 64.2179 | 61.9221 | 61.5463 | 61.2116
MANNINGTON GSP | BOURNEMOUTH | BOURNE VALLEY | MINIMUM HEADROOM | SZ 06207 92415 | YES | 0.25263 | 35.9874 | 35.4737 | 34.9547 | 34.4032 | 33.8316 | 33.2421 | 32.6484 | 32 | 30.9221 | 29.8811 | 25.2284 | 20.9463 | -14.9032 | 30.4263 | 29.4432 | 28.4684 | 27.4726 | 26.4758 | 25.4653 | 24.3368 | 23.2211 | 22.0568 | 20.9284 | 15.8221 | 11.0053 | 6.5337 | 31.3916 | 30.7095 | 29.72 | 28.7095 | 27.7 | 26.6758 | 25.5316 | 24.3968 | 23.2105 | 22.0611 | 16.8947 | 12.0842 | 7.6189
|  | BOURNE VALLEY | EE |  |  |  | 36.1842 | 35.7821 | 35.3558 | 34.9032 | 34.4274 | 33.9347 | 33.46 | 33.0063 | 32.5695 | 32.18 | 28.5653 | 25.24 | 22.2074 | 30.7474 | 30.1063 | 29.3295 | 28.5358 | 27.7274 | 26.9242 | 26.0411 | 25.1821 | 24.3547 | 23.4379 | 19.4895 | 15.7684 | 12.3147 | 31.6021 | 31.1789 | 30.5958 | 29.7905 | 28.9726 | 28.1589 | 27.2632 | 26.3905 | 25.5516 | 24.6179 | 20.5905 | 16.8421 | 13.3926
|  | BOURNE VALLEY | HT |  |  |  | 35.9874 | 35.4737 | 34.9547 | 34.4032 | 33.8316 | 33.2421 | 32.6484 | 32 | 30.9221 | 29.8811 | 25.2284 | 20.9463 | 16.9968 | 30.4263 | 29.4432 | 28.4684 | 27.4726 | 26.4758 | 25.4653 | 24.3368 | 23.2211 | 22.0568 | 20.9284 | 15.8221 | 11.0053 | 6.5337 | 31.3916 | 30.7095 | 29.72 | 28.7095 | 27.7 | 26.6758 | 25.5316 | 24.3968 | 23.2105 | 22.0611 | 16.8947 | 12.0842 | 7.6189
|  | BOURNE VALLEY | HE |  |  |  | 36.4432 | 36.1621 | 35.8516 | 35.5074 | 35.1368 | 34.7432 | 34.3663 | 34.0105 | 33.6789 | 33.3926 | 32.0568 | 29.6747 | -14.9032 | 31.0495 | 30.7411 | 30.4042 | 29.9011 | 29.3316 | 28.7505 | 28.0863 | 27.4621 | 26.8358 | 26.1263 | 23.2432 | 20.6 | 18.1842 | 31.8811 | 31.5874 | 31.2653 | 30.9084 | 30.5263 | 30.0179 | 29.3442 | 28.7116 | 28.0758 | 27.3526 | 24.4095 | 21.7021 | 19.2558
|  | BOURNE VALLEY | CF |  |  |  | 36.5968 | 36.4337 | 36.2642 | 36.0884 | 35.9063 | 35.7179 | 35.5253 | 35.3368 | 35.1495 | 34.9632 | 34.1295 | 33.7126 | 32.3611 | 31.2211 | 31.0389 | 30.8516 | 30.6568 | 30.4558 | 30.1042 | 29.6716 | 29.2232 | 28.8189 | 28.4379 | 26.82 | 25.0221 | 23.4389 | 32.0421 | 31.8705 | 31.6926 | 31.5084 | 31.3179 | 31.1189 | 30.9116 | 30.4874 | 30.0758 | 29.6874 | 28.0453 | 26.2042 | 24.5779
MANNINGTON GSP | SHAFTESBURY BSP | BOURTON | MINIMUM HEADROOM | ST 77363 30262 | YES | 0.52 | 11.0368 | 10.5421 | 10.0895 | 9.6295 | 9.1684 | 9.0758 | 8.6253 | 8.2137 | 7.8295 | 7.4653 | 5.7516 | 3.9432 | -11.4937 | 8.6021 | 8.0716 | 7.5863 | 7.0947 | 6.6032 | 6.5726 | 6.0958 | 5.6579 | 5.2484 | 4.8579 | 3 | 0.98 | -1.0758 | 9.0021 | 8.5053 | 8.0337 | 7.5558 | 7.0768 | 7.0179 | 6.5516 | 6.1253 | 5.72 | 5.3274 | 3.4579 | 1.4368 | -0.61368
|  | BOURTON | EE |  |  |  | 11.2379 | 10.8474 | 10.4874 | 10.1179 | 9.7453 | 9.3684 | 9.0126 | 8.6737 | 8.3463 | 8.0484 | 7.1074 | 5.7674 | 4.4042 | 8.8126 | 8.4021 | 8.0168 | 7.6232 | 7.2263 | 6.8274 | 6.4505 | 6.0905 | 5.7442 | 5.4274 | 4.4705 | 2.9821 | 1.4284 | 9.1916 | 8.8211 | 8.4495 | 8.0674 | 7.6811 | 7.2916 | 6.9242 | 6.5726 | 6.2347 | 5.9263 | 4.9379 | 3.4368 | 1.8863
|  | BOURTON | HT |  |  |  | 11.0368 | 10.5421 | 10.0895 | 9.6295 | 9.1684 | 9.0758 | 8.6253 | 8.2137 | 7.8295 | 7.4653 | 5.7516 | 3.9432 | 2.1305 | 8.6021 | 8.0716 | 7.5863 | 7.0947 | 6.6032 | 6.5726 | 6.0958 | 5.6579 | 5.2484 | 4.8579 | 3 | 0.98 | -1.0758 | 9.0021 | 8.5053 | 8.0337 | 7.5558 | 7.0768 | 7.0179 | 6.5516 | 6.1253 | 5.72 | 5.3274 | 3.4579 | 1.4368 | -0.61368
|  | BOURTON | HE |  |  |  | 11.5147 | 11.2568 | 11.0221 | 10.7726 | 10.5137 | 10.2453 | 9.9926 | 9.7526 | 9.5295 | 9.3284 | 8.8632 | 7.9516 | -11.4937 | 9.1032 | 8.8326 | 8.5895 | 8.3316 | 8.0579 | 7.7758 | 7.5105 | 7.2589 | 7.0242 | 6.8126 | 6.3737 | 5.3537 | 4.2611 | 9.4558 | 9.2095 | 8.9832 | 8.7432 | 8.4853 | 8.2084 | 7.9495 | 7.7021 | 7.4726 | 7.2653 | 6.8126 | 5.8242 | 4.72
|  | BOURTON | CF |  |  |  | 11.6516 | 11.5284 | 11.3947 | 11.2558 | 11.1137 | 10.9642 | 10.8126 | 10.6674 | 10.5253 | 10.3842 | 9.7316 | 9.4968 | 8.8663 | 9.2453 | 9.1168 | 8.9779 | 8.8337 | 8.6842 | 8.5284 | 8.3705 | 8.2158 | 8.0632 | 7.9116 | 7.2116 | 6.9979 | 6.2789 | 9.5863 | 9.4684 | 9.3411 | 9.2084 | 9.0716 | 8.9284 | 8.7842 | 8.6411 | 8.4926 | 8.3453 | 7.6663 | 7.4411 | 6.7505
MANNINGTON GSP | WAREHAM | BOVINGTON | MINIMUM HEADROOM | SY 83933 87831 | YES | 0 | 8.1821 | 8.0274 | 7.7832 | 7.6263 | 7.2316 | 6.6547 | 6.1716 | 5.4432 | 4.8053 | 3.7789 | 2.5726 | 1.1463 | -2.0653 | 7.8368 | 7.6726 | 7.4063 | 7.2411 | 6.8042 | 6.1158 | 5.5379 | 4.68 | 3.9474 | 2.7579 | 1.4084 | -0.20947 | -0.64632 | 7.7558 | 7.6032 | 7.3484 | 7.1863 | 6.7684 | 6.0821 | 5.5011 | 4.64 | 3.9063 | 2.7147 | 1.3568 | -0.27053 | -0.71158
|  | BOVINGTON | EE |  |  |  | 8.2484 | 8.1284 | 7.9126 | 7.7874 | 7.42 | 6.8705 | 6.4168 | 5.7179 | 5.0947 | 4.48 | 2.9779 | 2.4421 | 1.94 | 7.9074 | 7.78 | 7.5453 | 7.4126 | 7.0074 | 6.3558 | 5.8126 | 4.9779 | 4.2632 | 3.5579 | 1.86 | 1.2895 | 0.72737 | 7.8211 | 7.7021 | 7.4832 | 7.3537 | 6.9642 | 6.3253 | 5.7737 | 4.9368 | 4.22 | 3.5126 | 1.8 | 1.2116 | 0.64526
|  | BOVINGTON | HT |  |  |  | 8.1821 | 8.0274 | 7.7832 | 7.6263 | 7.2316 | 6.6547 | 6.1716 | 5.4432 | 4.8053 | 3.7789 | 2.5726 | 1.1463 | 0.74 | 7.8368 | 7.6726 | 7.4063 | 7.2411 | 6.8042 | 6.1158 | 5.5379 | 4.68 | 3.9474 | 2.7579 | 1.4084 | -0.20947 | -0.64632 | 7.7558 | 7.6032 | 7.3484 | 7.1863 | 6.7684 | 6.0821 | 5.5011 | 4.64 | 3.9063 | 2.7147 | 1.3568 | -0.27053 | -0.71158
|  | BOVINGTON | HE |  |  |  | 8.3411 | 8.2642 | 8.0937 | 8.0074 | 7.6811 | 7.1674 | 6.7516 | 6.1042 | 5.5221 | 4.9495 | 3.6526 | 3.3242 | -2.0653 | 8.0063 | 7.9263 | 7.7379 | 7.6484 | 7.2842 | 6.6863 | 6.1874 | 5.3947 | 4.7232 | 4.06 | 2.5758 | 2.2147 | 1.82 | 7.9116 | 7.8358 | 7.6695 | 7.5832 | 7.2347 | 6.6589 | 6.1516 | 5.3579 | 4.6832 | 4.02 | 2.5295 | 2.1642 | 1.7653
|  | BOVINGTON | CF |  |  |  | 8.3905 | 8.3442 | 8.2568 | 8.2095 | 8.0621 | 7.8453 | 7.6495 | 7.3263 | 7.0284 | 6.7095 | 5.8684 | 5.6442 | 5.4116 | 8.0589 | 8.0095 | 7.9137 | 7.8632 | 7.7 | 7.4579 | 7.24 | 6.8568 | 6.4947 | 6.1053 | 5.1137 | 4.8663 | 4.6053 | 7.96 | 7.9147 | 7.8295 | 7.7821 | 7.6358 | 7.4042 | 7.1937 | 6.8316 | 6.4621 | 6.0674 | 5.0737 | 4.8242 | 4.56
AMERSHAM | LOUDWATER BSP | BOWERDEAN | MINIMUM HEADROOM | SU 87718 93880 | YES | 0.65053 | 24.5926 | 23.8958 | 22.2421 | 20.5874 | 18.9274 | 17.3758 | 15.8526 | 14.5926 | 13.6316 | 12.7116 | 8.5442 | 4.8863 | -24.1537 | 19.2474 | 17.4358 | 15.2884 | 13.3884 | 11.5221 | 9.7905 | 8.0926 | 6.6979 | 5.6621 | 4.6684 | 0.12632 | -3.9053 | -7.5274 | 20.8084 | 18.9979 | 16.8347 | 14.9337 | 13.0674 | 11.3337 | 9.6368 | 8.24 | 7.2042 | 6.2095 | 1.6611 | -2.3768 | -6.0032
|  | BOWERDEAN | EE |  |  |  | 24.8305 | 24.3726 | 23.1442 | 21.7295 | 20.2768 | 18.9211 | 17.6337 | 16.5495 | 15.7379 | 14.9768 | 11.7074 | 8.9505 | 6.5474 | 19.7568 | 18.2063 | 16.3074 | 14.6411 | 13 | 11.48 | 10.0379 | 8.8368 | 7.9579 | 7.1284 | 3.5632 | 0.51579 | -2.1716 | 21.0632 | 19.7811 | 17.8537 | 16.1874 | 14.5453 | 13.0242 | 11.5821 | 10.3789 | 9.4989 | 8.6684 | 5.0958 | 2.04 | -0.65053
|  | BOWERDEAN | HT |  |  |  | 24.5926 | 23.8958 | 22.2421 | 20.5874 | 18.9274 | 17.3758 | 15.8526 | 14.5926 | 13.6316 | 12.7116 | 8.5442 | 4.8863 | 1.6295 | 19.2474 | 17.4358 | 15.2884 | 13.3884 | 11.5221 | 9.7905 | 8.0926 | 6.6979 | 5.6621 | 4.6684 | 0.12632 | -3.9053 | -7.5274 | 20.8084 | 18.9979 | 16.8347 | 14.9337 | 13.0674 | 11.3337 | 9.6368 | 8.24 | 7.2042 | 6.2095 | 1.6611 | -2.3768 | -6.0032
|  | BOWERDEAN | HE |  |  |  | 25.1505 | 24.8474 | 24.3253 | 23.1821 | 22.0316 | 20.9189 | 19.8705 | 19.0168 | 18.4389 | 17.9032 | 15.7547 | 14.02 | -24.1537 | 20.3526 | 19.2126 | 17.6411 | 16.2853 | 14.9305 | 13.6779 | 12.4968 | 11.5474 | 10.9263 | 10.3432 | 7.9716 | 6.0253 | 4.36 | 21.4042 | 20.8053 | 19.1937 | 17.8316 | 16.4768 | 15.2221 | 14.0421 | 13.0916 | 12.4684 | 11.8863 | 9.5105 | 7.5621 | 5.8947
|  | BOWERDEAN | CF |  |  |  | 25.3358 | 25.1716 | 25.0011 | 24.8232 | 24.5453 | 24.2253 | 23.7074 | 23.2547 | 22.9147 | 22.5642 | 20.8853 | 19.6242 | 18.5947 | 20.5526 | 20.2095 | 19.4126 | 18.7558 | 18.1211 | 17.5326 | 16.9305 | 16.4042 | 16.02 | 15.6232 | 13.7379 | 12.3053 | 11.1137 | 21.6053 | 21.4105 | 21.0063 | 20.3347 | 19.6853 | 19.0842 | 18.4758 | 17.9495 | 17.5653 | 17.1695 | 15.2811 | 13.8474 | 12.6547
BRAMLEY (FLEE) | BRACKNELL | BRACKNELL | MINIMUM HEADROOM | SU 86075 69397 | YES | 0.70947 | 93.7389 | 93.8947 | 93.7621 | 93.6242 | 93.4821 | 93.2432 | 102.6158 | 102.2337 | 100.5947 | 98.0874 | 90.3558 | 87.1811 | 11.4116 | 82.6832 | 82.8411 | 82.7063 | 82.5674 | 82.3421 | 81.6337 | 91.8558 | 89.0853 | 85.94 | 83.04 | 74.1611 | 70.6021 | 67.3589 | 84.6789 | 84.8358 | 84.7021 | 84.5632 | 84.4126 | 84.1411 | 93.1505 | 90.3621 | 87.2158 | 84.3147 | 75.4316 | 71.8695 | 68.6242
|  | BRACKNELL | EE |  |  |  | 93.7389 | 104.98 | 104.6695 | 104.3389 | 103.9916 | 103.5379 | 103.1863 | 102.8505 | 101.8611 | 99.4358 | 92.3779 | 89.9032 | 87.6905 | 82.6832 | 97.3726 | 97.0621 | 96.7316 | 96.3589 | 94.5905 | 93.02 | 90.3768 | 87.3179 | 84.5095 | 76.3789 | 73.5968 | 71.0884 | 84.6789 | 97.9484 | 97.6379 | 97.3074 | 96.96 | 95.9432 | 94.3337 | 91.6547 | 88.5937 | 85.7832 | 77.6484 | 74.8621 | 72.3526
|  | BRACKNELL | HT |  |  |  | 105.1347 | 104.7632 | 104.3874 | 103.9874 | 103.5716 | 103.0505 | 102.6158 | 102.2337 | 100.5947 | 98.0874 | 90.3558 | 87.1811 | 84.3074 | 97.5274 | 97.1558 | 96.78 | 96.38 | 95.4632 | 93.5663 | 91.8558 | 89.0853 | 85.94 | 83.04 | 74.1611 | 70.6021 | 67.3589 | 98.1032 | 97.7316 | 97.3558 | 96.9558 | 96.54 | 94.9021 | 93.1505 | 90.3621 | 87.2158 | 84.3147 | 75.4316 | 71.8695 | 68.6242
|  | BRACKNELL | HE |  |  |  | 93.9189 | 105.2442 | 105.0116 | 104.7547 | 104.4779 | 104.0926 | 103.8095 | 103.5442 | 103.2947 | 101.2411 | 94.9347 | 93.1811 | 11.4116 | 82.8632 | 97.6368 | 97.4042 | 97.1474 | 96.8705 | 95.8874 | 94.4779 | 92.0221 | 89.1274 | 86.4842 | 79.1789 | 77.1895 | 75.4505 | 84.8589 | 98.2126 | 97.98 | 97.7232 | 97.4463 | 97.0611 | 95.8179 | 93.2989 | 90.4032 | 87.7611 | 80.4516 | 78.4621 | 76.72
|  | BRACKNELL | CF |  |  |  | 94.0221 | 93.8947 | 93.7621 | 93.6242 | 93.4821 | 93.2432 | 104.6263 | 104.4789 | 104.3326 | 104.1853 | 103.3021 | 102.0653 | 101.0337 | 82.9695 | 82.8411 | 82.7063 | 82.5674 | 82.3421 | 81.6337 | 97.02 | 96.8337 | 95.2716 | 93.7158 | 88.8358 | 87.4368 | 86.2537 | 84.9632 | 84.8358 | 84.7021 | 84.5632 | 84.4126 | 84.1411 | 97.5947 | 97.4474 | 96.6211 | 95.02 | 90.1126 | 88.7126 | 87.5284
MELKSHAM GSP | NORRINGTON | BRADFORD-ON-AVON | MINIMUM HEADROOM | ST 81260 60564 | YES | 1.4705 | 24.1716 | 23.8579 | 23.5389 | 23.1989 | 22.8495 | 22.3653 | 20.5 | 18.9032 | 18.5611 | 18.24 | 15.8274 | 13.0547 | -2.9558 | 19.5579 | 19.1358 | 18.7116 | 18.2684 | 17.8211 | 17.3316 | 15.2232 | 13.4221 | 13.0979 | 12.7937 | 10.3179 | 7.3968 | 6.1874 | 20.4053 | 19.98 | 19.5516 | 19.1053 | 18.6526 | 18.1505 | 16.0305 | 14.2168 | 13.8747 | 13.5537 | 10.9726 | 7.9358 | 6.6758
|  | BRADFORD-ON-AVON | EE |  |  |  | 24.2884 | 24.0432 | 23.7768 | 23.4958 | 23.2021 | 22.8632 | 22.5042 | 22.0947 | 21.6874 | 21.3032 | 18.9084 | 16.3526 | 14.2621 | 19.7179 | 19.4021 | 19.0547 | 18.6947 | 18.3242 | 17.9126 | 17.5 | 17.0968 | 16.6958 | 16.3189 | 13.9074 | 11.2874 | 8.9958 | 20.5663 | 20.2484 | 19.8958 | 19.5337 | 19.1579 | 18.7347 | 18.3042 | 17.8832 | 17.4642 | 17.0653 | 14.5 | 11.7105 | 9.3653
|  | BRADFORD-ON-AVON | HT |  |  |  | 24.1716 | 23.8579 | 23.5389 | 23.1989 | 22.8495 | 22.3653 | 20.5 | 18.9032 | 18.5611 | 18.24 | 15.8274 | 13.0547 | 11.8632 | 19.5579 | 19.1358 | 18.7116 | 18.2684 | 17.8211 | 17.3316 | 15.2232 | 13.4221 | 13.0979 | 12.7937 | 10.3179 | 7.3968 | 6.1874 | 20.4053 | 19.98 | 19.5516 | 19.1053 | 18.6526 | 18.1505 | 16.0305 | 14.2168 | 13.8747 | 13.5537 | 10.9726 | 7.9358 | 6.6758
|  | BRADFORD-ON-AVON | HE |  |  |  | 24.4526 | 24.2905 | 24.1095 | 23.9053 | 23.6874 | 23.4242 | 23.1747 | 22.9347 | 22.7084 | 22.5063 | 21.5916 | 19.8379 | -2.9558 | 19.8821 | 19.72 | 19.5242 | 19.2747 | 19.0116 | 18.7063 | 18.4147 | 18.1347 | 17.8695 | 17.6284 | 16.6337 | 14.7326 | 13.3063 | 20.7316 | 20.5684 | 20.3726 | 20.1232 | 19.8579 | 19.5421 | 19.2421 | 18.9547 | 18.68 | 18.4295 | 17.3779 | 15.4084 | 13.94
|  | BRADFORD-ON-AVON | CF |  |  |  | 24.5453 | 24.4526 | 24.3579 | 24.2589 | 24.1537 | 24.0295 | 23.9042 | 23.78 | 23.6579 | 23.5411 | 22.9853 | 22.5221 | 21.5116 | 19.9747 | 19.8821 | 19.7874 | 19.6884 | 19.5642 | 19.4053 | 19.2495 | 19.0937 | 18.9389 | 18.7884 | 18.0789 | 17.5284 | 16.4263 | 20.8242 | 20.7316 | 20.6368 | 20.5379 | 20.4126 | 20.2505 | 20.0884 | 19.9284 | 19.7705 | 19.6158 | 18.8842 | 18.3063 | 17.1621
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | BRAMLEY GREEN | MINIMUM HEADROOM | SU 67431 58511 | YES | 0 | 16.2863 | 16.2432 | 16.2695 | 15.9811 | 15.7758 | 15.5495 | 14.9253 | 14.1642 | 14.0632 | 13.9705 | 12.66 | 10.8926 | 6.1274 | 15.1126 | 14.7979 | 14.4221 | 14 | 13.78 | 13.5768 | 12.8653 | 11.9895 | 11.8884 | 11.7958 | 10.3189 | 8.2874 | 7.7726 | 15.3326 | 15.0179 | 14.6421 | 14.22 | 14 | 13.7558 | 13.0463 | 12.1716 | 12.0705 | 11.9779 | 10.5032 | 8.4747 | 7.96
|  | BRAMLEY GREEN | EE |  |  |  | 16.3295 | 16.2432 | 16.5326 | 16.1989 | 16.0316 | 15.8632 | 15.7011 | 15.5421 | 15.3832 | 15.2358 | 14.6632 | 13.2421 | 12.1442 | 15.2084 | 14.9442 | 14.6116 | 14.2368 | 14.0589 | 13.92 | 13.7463 | 13.5358 | 13.4053 | 13.2474 | 12.6242 | 10.9863 | 9.7189 | 15.4284 | 15.1642 | 14.8316 | 14.4568 | 14.2779 | 14.0979 | 13.9253 | 13.7558 | 13.5853 | 13.4263 | 12.8042 | 11.1695 | 9.9042
|  | BRAMLEY GREEN | HT |  |  |  | 16.2863 | 16.6947 | 16.3579 | 15.9811 | 15.7758 | 15.5495 | 14.9253 | 14.1642 | 14.0632 | 13.9705 | 12.66 | 10.8926 | 10.4221 | 15.1126 | 14.7979 | 14.4221 | 14 | 13.78 | 13.5768 | 12.8653 | 11.9895 | 11.8884 | 11.7958 | 10.3189 | 8.2874 | 7.7726 | 15.3326 | 15.0179 | 14.6421 | 14.22 | 14 | 13.7558 | 13.0463 | 12.1716 | 12.0705 | 11.9779 | 10.5032 | 8.4747 | 7.96
|  | BRAMLEY GREEN | HE |  |  |  | 16.3905 | 16.3326 | 16.2695 | 16.4874 | 16.3705 | 16.2495 | 16.1326 | 16.0179 | 15.9095 | 15.8105 | 15.4432 | 14.4832 | 6.1274 | 15.3211 | 15.1411 | 14.8684 | 14.5505 | 14.4263 | 14.2979 | 14.2158 | 14.0526 | 13.9379 | 13.8716 | 13.4747 | 12.3642 | 11.3263 | 15.5611 | 15.3611 | 15.0884 | 14.7705 | 14.6463 | 14.5179 | 14.3947 | 14.2716 | 14.1568 | 14.0505 | 13.6537 | 12.5453 | 11.5084
|  | BRAMLEY GREEN | CF |  |  |  | 16.4242 | 16.3937 | 16.36 | 16.9968 | 16.8789 | 16.7495 | 16.6337 | 16.5526 | 16.4853 | 16.4189 | 16.1053 | 15.7958 | 15.1326 | 15.36 | 15.3232 | 15.2505 | 15.1274 | 14.9937 | 14.8484 | 14.7189 | 14.6305 | 14.5579 | 14.4863 | 14.1453 | 13.8368 | 13.0642 | 15.6147 | 15.5611 | 15.4705 | 15.3474 | 15.2137 | 15.0684 | 14.9389 | 14.8495 | 14.7779 | 14.7063 | 14.3653 | 14.0158 | 13.2442
LOVEDEAN GSP | PORTSMOUTH BSP | BRANDON ROAD | MINIMUM HEADROOM | SZ 64712 98665 | YES | 0.12105 | 35.3368 | 35.0211 | 34.7021 | 34.3642 | 34.0042 | 33.6284 | 33.2442 | 32.9 | 32.58 | 32.2842 | 29.3053 | 26.1737 | 0.80526 | 30.6137 | 30.1842 | 29.6411 | 28.9084 | 28.1737 | 27.5316 | 26.8884 | 26.2916 | 25.72 | 25.0411 | 21.5737 | 18.0737 | 14.7989 | 31.2558 | 30.9189 | 30.5768 | 30.0389 | 29.2926 | 28.64 | 27.9905 | 27.3832 | 26.8063 | 26.1284 | 22.6611 | 19.1611 | 15.8895
|  | BRANDON ROAD | EE |  |  |  | 35.4674 | 35.2263 | 34.9705 | 34.6979 | 34.4042 | 34.0947 | 33.7916 | 33.4937 | 33.2032 | 32.94 | 31.4768 | 29.0242 | 26.8042 | 30.7726 | 30.46 | 30.1 | 29.5874 | 28.9884 | 28.4642 | 27.9568 | 27.4568 | 26.9674 | 26.5116 | 23.9716 | 21.2274 | 18.7158 | 31.3947 | 31.1368 | 30.8621 | 30.5695 | 30.12 | 29.5874 | 29.0747 | 28.5674 | 28.0716 | 27.6074 | 25.0526 | 22.3053 | 19.7958
|  | BRANDON ROAD | HT |  |  |  | 35.3368 | 35.0211 | 34.7021 | 34.3642 | 34.0042 | 33.6284 | 33.2442 | 32.9 | 32.58 | 32.2842 | 29.3053 | 26.1737 | 23.2632 | 30.6137 | 30.1842 | 29.6411 | 28.9084 | 28.1737 | 27.5316 | 26.8884 | 26.2916 | 25.72 | 25.0411 | 21.5737 | 18.0737 | 14.7989 | 31.2558 | 30.9189 | 30.5768 | 30.0389 | 29.2926 | 28.64 | 27.9905 | 27.3832 | 26.8063 | 26.1284 | 22.6611 | 19.1611 | 15.8895
|  | BRANDON ROAD | HE |  |  |  | 35.5768 | 35.38 | 35.1632 | 34.9242 | 34.6663 | 34.3905 | 34.1263 | 33.8779 | 33.6453 | 33.4453 | 32.7347 | 32.2821 | 0.80526 | 30.9074 | 30.6853 | 30.4137 | 30.0958 | 29.7674 | 29.3937 | 29.0105 | 28.6463 | 28.3074 | 28.0042 | 26.7442 | 25.0537 | 23.3421 | 31.5158 | 31.3074 | 31.0768 | 30.8242 | 30.5526 | 30.2695 | 29.9979 | 29.7421 | 29.4411 | 29.1337 | 27.8537 | 26.1358 | 24.4253
|  | BRANDON ROAD | CF |  |  |  | 35.6389 | 35.5032 | 35.3621 | 35.2147 | 35.0642 | 34.9063 | 34.7463 | 34.5884 | 34.4316 | 34.2758 | 33.58 | 33.2221 | 33.02 | 30.9779 | 30.8242 | 30.66 | 30.4716 | 30.2747 | 30.0853 | 29.8926 | 29.7011 | 29.4958 | 29.2358 | 28.0263 | 26.9063 | 25.74 | 31.5821 | 31.4379 | 31.2863 | 31.1295 | 30.9705 | 30.8074 | 30.6411 | 30.4768 | 30.3137 | 30.1516 | 29.1526 | 28.0084 | 26.8253
BRAMLEY (FLEE) | MAIDENHEAD BSP | BRAYWICK ROAD | MINIMUM HEADROOM | SU 88887 80726 | YES | -0.74 | 37.7737 | 37.5337 | 37.2916 | 36.3747 | 33.5379 | 31.5579 | 29.8095 | 28.1232 | 27.6189 | 27.1442 | 24.9726 | 23.0295 | -11.5389 | 30.2589 | 29.6958 | 28.3568 | 25.7074 | 22.4242 | 19.9347 | 17.9221 | 15.9758 | 15.4221 | 14.8968 | 12.4842 | 10.3021 | 8.2758 | 32.0053 | 31.46 | 30.1021 | 27.4105 | 24.1105 | 21.6211 | 19.6074 | 17.66 | 17.1063 | 16.5811 | 14.1674 | 11.9853 | 9.9589
|  | BRAYWICK ROAD | EE |  |  |  | 37.8705 | 37.6842 | 37.4874 | 37.1168 | 34.3642 | 32.4695 | 30.1642 | 28.5453 | 28.1126 | 27.7116 | 25.9747 | 24.4705 | 23.1032 | 30.3937 | 29.9168 | 29.08 | 26.5295 | 23.3463 | 20.9495 | 18.2684 | 16.3958 | 15.9221 | 15.4811 | 13.5474 | 11.8526 | 10.2968 | 32.1253 | 31.6768 | 30.8337 | 28.2421 | 25.0337 | 22.6358 | 19.9537 | 18.08 | 17.6063 | 17.1653 | 15.2316 | 13.5358 | 11.9789
|  | BRAYWICK ROAD | HT |  |  |  | 37.7737 | 37.5337 | 37.2916 | 36.3747 | 33.5379 | 31.5579 | 29.8095 | 28.1232 | 27.6189 | 27.1442 | 24.9726 | 23.0295 | 21.2379 | 30.2589 | 29.6958 | 28.3568 | 25.7074 | 22.4242 | 19.9347 | 17.9221 | 15.9758 | 15.4221 | 14.8968 | 12.4842 | 10.3021 | 8.2758 | 32.0053 | 31.46 | 30.1021 | 27.4105 | 24.1105 | 21.6211 | 19.6074 | 17.66 | 17.1063 | 16.5811 | 14.1674 | 11.9853 | 9.9589
|  | BRAYWICK ROAD | HE |  |  |  | 37.9947 | 37.8663 | 37.7253 | 37.5695 | 35.7126 | 34.2168 | 32.3126 | 30.4463 | 29.8189 | 29.2168 | 27.4779 | 26.3958 | -11.5389 | 30.5179 | 30.1611 | 29.7126 | 27.6253 | 24.8747 | 22.94 | 20.7242 | 18.5516 | 17.84 | 17.1516 | 15.1789 | 13.9495 | 12.8389 | 32.2495 | 31.9179 | 31.4726 | 29.3526 | 26.5621 | 24.6263 | 22.4105 | 20.2368 | 19.5242 | 18.8368 | 16.8632 | 15.6337 | 14.5221
|  | BRAYWICK ROAD | CF |  |  |  | 38.0632 | 37.9895 | 37.9126 | 37.8326 | 37.7505 | 38.7895 | 38.5558 | 36.8463 | 36.3758 | 36 | 34.5653 | 33.8179 | 33.1768 | 30.6674 | 30.5316 | 30.3737 | 30.2189 | 29.9526 | 29.8147 | 27.9716 | 25.9947 | 25.4547 | 25.0263 | 23.4021 | 22.5537 | 21.8158 | 32.3221 | 32.2453 | 32.1211 | 31.9705 | 31.7137 | 31.5589 | 29.6842 | 27.6821 | 27.1421 | 26.7137 | 25.0895 | 24.24 | 23.5021
EALING GSP | EALING 22kV | BRENTFORD | MINIMUM HEADROOM | TQ 17659 78277 | YES | 0 | 37.3811 | 37.0558 | 36.6621 | 35.4547 | 33.8779 | 32.1937 | 30.6147 | 29.5989 | 28.6189 | 27.6684 | 23.3789 | 20.1495 | -15.1074 | 30.2253 | 28.3621 | 26.8684 | 25.1811 | 23.3863 | 21.4695 | 19.6768 | 18.5411 | 17.4432 | 16.3747 | 11.5326 | 7.8947 | 4.5842 | 31.8147 | 29.9684 | 28.4621 | 26.7737 | 24.9789 | 23.0611 | 21.2684 | 20.1316 | 19.0337 | 17.9653 | 13.1295 | 9.4968 | 6.1905
|  | BRENTFORD | EE |  |  |  | 37.5053 | 37.2516 | 36.9811 | 36.6474 | 35.9674 | 34.6432 | 33.3895 | 32.0842 | 30.8558 | 29.8379 | 25.9579 | 23.6042 | 21.5137 | 30.5295 | 29.0716 | 28.1232 | 27.0968 | 25.7842 | 24.28 | 22.8579 | 21.3726 | 19.9758 | 18.8232 | 14.4242 | 11.7737 | 9.4032 | 32.1158 | 30.6811 | 29.7263 | 28.6905 | 27.3768 | 25.8726 | 24.4495 | 22.9642 | 21.5663 | 20.4137 | 16.0179 | 13.3705 | 11.0042
|  | BRENTFORD | HT |  |  |  | 37.3811 | 37.0558 | 36.6621 | 35.4547 | 33.8779 | 32.1937 | 30.6147 | 29.5989 | 28.6189 | 27.6684 | 23.3789 | 20.1495 | 17.2253 | 30.2253 | 28.3621 | 26.8684 | 25.1811 | 23.3863 | 21.4695 | 19.6768 | 18.5411 | 17.4432 | 16.3747 | 11.5326 | 7.8947 | 4.5842 | 31.8147 | 29.9684 | 28.4621 | 26.7737 | 24.9789 | 23.0611 | 21.2684 | 20.1316 | 19.0337 | 17.9653 | 13.1295 | 9.4968 | 6.1905
|  | BRENTFORD | HE |  |  |  | 37.6358 | 37.4368 | 37.2168 | 36.9579 | 36.6326 | 35.5063 | 34.3653 | 33.1611 | 32.12 | 31.2789 | 28.1347 | 26.4758 | -15.1074 | 30.8779 | 29.5884 | 28.7137 | 27.8042 | 26.6242 | 25.2316 | 23.9337 | 22.5589 | 21.3726 | 20.4158 | 16.8337 | 14.9526 | 13.3674 | 32.46 | 31.1916 | 30.3242 | 29.4032 | 28.2168 | 26.8242 | 25.5263 | 24.1505 | 22.9642 | 22.0074 | 18.4242 | 16.5453 | 14.9632
|  | BRENTFORD | CF |  |  |  | 37.7063 | 37.5726 | 37.4337 | 37.2884 | 37.1389 | 36.9853 | 36.8274 | 36.6726 | 36.5189 | 36.3526 | 32.3589 | 30.9337 | 29.9832 | 31.3832 | 30.6947 | 30.3705 | 30.0695 | 29.7558 | 29.4274 | 29.0895 | 28.6568 | 27.9968 | 27.2474 | 21.6537 | 20.0337 | 18.9484 | 32.7295 | 32.2779 | 31.9579 | 31.66 | 31.3495 | 31.0253 | 30.6905 | 30.2632 | 29.6063 | 28.8463 | 23.2453 | 21.6253 | 20.54
EALING GSP |  | BRIDGE ROAD | MINIMUM HEADROOM | TQ 14778 75741 | NO | 0.71158 | 87.0789 | 86.4726 | 85.8589 | 85.0326 | 160.5253 | 159.8179 | 156.3989 | 153.0916 | 149.8537 | 146.6705 | 137.9968 | 131.5011 | 84.3326 | 77.0074 | 75.3305 | 72.5179 | 69.1411 | 65.3284 | 141.4211 | 137.5253 | 133.7453 | 130.0379 | 126.3884 | 116.58 | 109.2421 | 102.2968 | 78.6411 | 78.0347 | 75.46 | 72.0884 | 68.2821 | 144.3747 | 140.4842 | 136.7105 | 133.0095 | 129.3653 | 119.5705 | 112.2442 | 105.3095
|  | BRIDGE ROAD | EE |  |  |  | 87.3053 | 86.8263 | 86.32 | 85.7811 | 161.9053 | 161.1189 | 159.12 | 156.2726 | 155.7337 | 155.2505 | 146.0347 | 141.1368 | 136.7137 | 77.3326 | 76.58 | 75.0474 | 72.9695 | 70.1789 | 143.6537 | 140.5621 | 137.3105 | 136.7716 | 136.2884 | 125.7642 | 120.2253 | 115.1895 | 78.8674 | 78.3884 | 77.8821 | 75.9105 | 73.1253 | 146.6042 | 143.5168 | 140.2716 | 139.7326 | 139.2495 | 128.7411 | 123.2095 | 118.1821
|  | BRIDGE ROAD | HT |  |  |  | 87.0789 | 86.4726 | 85.8589 | 85.0326 | 160.5253 | 159.8179 | 156.3989 | 153.0916 | 149.8537 | 146.6705 | 137.9968 | 131.5011 | 125.3884 | 77.0074 | 75.3305 | 72.5179 | 69.1411 | 65.3284 | 141.4211 | 137.5253 | 133.7453 | 130.0379 | 126.3884 | 116.58 | 109.2421 | 102.2968 | 78.6411 | 78.0347 | 75.46 | 72.0884 | 68.2821 | 144.3747 | 140.4842 | 136.7105 | 133.0095 | 129.3653 | 119.5705 | 112.2442 | 105.3095
|  | BRIDGE ROAD | HE |  |  |  | 87.5789 | 87.2232 | 86.8305 | 86.3968 | 162.6926 | 162.0116 | 161.0505 | 158.3158 | 154.8863 | 151.5789 | 143.8789 | 140.2653 | 84.3326 | 77.6758 | 77.1526 | 76.1937 | 74.4305 | 71.8632 | 145.5284 | 142.6716 | 139.5326 | 135.5716 | 131.7442 | 122.9032 | 118.7853 | 115.0926 | 79.1411 | 78.7853 | 78.3926 | 77.3705 | 74.8063 | 148.4768 | 145.6253 | 142.4916 | 138.5368 | 134.7158 | 125.8884 | 121.7768 | 118.0905
|  | BRIDGE ROAD | CF |  |  |  | 87.7368 | 87.5137 | 87.28 | 87.0389 | 163.5905 | 163.3316 | 163.0684 | 162.8095 | 162.5537 | 162.2968 | 153.6432 | 150.2705 | 148.1632 | 77.8484 | 77.6126 | 77.3653 | 77.0168 | 76.6495 | 153.06 | 152.5084 | 151.7242 | 150.5916 | 149.0968 | 134.0621 | 130.1947 | 127.7716 | 79.2989 | 79.0758 | 78.8421 | 78.6011 | 78.3526 | 154.8937 | 154.6305 | 154.3716 | 153.5316 | 152.0389 | 137.0295 | 133.1695 | 130.7505
LOVEDEAN GSP | HAVANT | BROCKHAMPTON | MINIMUM HEADROOM | SU 70868 05828 | YES | 0.74737 | 33.7284 | 33.7832 | 33.7537 | 33.7221 | 33.6895 | 33.6558 | 44.0095 | 43.9105 | 43.82 | 43.7358 | 43.3968 | 43.1421 | 3.5758 | 30.7263 | 30.7811 | 30.7516 | 30.68 | 30.6116 | 30.5411 | 44.6768 | 44.5779 | 44.4874 | 44.4042 | 44.0674 | 43.8158 | 43.6189 | 31.4221 | 31.4768 | 31.4474 | 31.4158 | 31.3832 | 31.3495 | 43.9411 | 43.8411 | 43.7505 | 43.6663 | 43.3274 | 43.0737 | 42.8747
|  | BROCKHAMPTON | EE |  |  |  | 33.7284 | 44.6105 | 44.5284 | 44.4421 | 44.3516 | 44.2568 | 44.1653 | 44.08 | 43.9958 | 43.9221 | 43.6495 | 43.4632 | 43.3295 | 30.7263 | 45.2768 | 45.1947 | 45.1084 | 45.0179 | 44.9242 | 44.8326 | 44.7474 | 44.6642 | 44.5916 | 44.3221 | 44.14 | 44.0095 | 31.4221 | 44.5411 | 44.4589 | 44.3726 | 44.2821 | 44.1874 | 44.0968 | 44.0105 | 43.9263 | 43.8537 | 43.5811 | 43.3947 | 43.2621
|  | BROCKHAMPTON | HT |  |  |  | 44.6495 | 44.5516 | 44.4516 | 44.3453 | 44.2368 | 44.1232 | 44.0095 | 43.9105 | 43.82 | 43.7358 | 43.3968 | 43.1421 | 42.9432 | 45.3158 | 45.2179 | 45.1179 | 45.0116 | 44.9032 | 44.7905 | 44.6768 | 44.5779 | 44.4874 | 44.4042 | 44.0674 | 43.8158 | 43.6189 | 44.58 | 44.4821 | 44.3821 | 44.2758 | 44.1674 | 44.0537 | 43.9411 | 43.8411 | 43.7505 | 43.6663 | 43.3274 | 43.0737 | 42.8747
|  | BROCKHAMPTON | HE |  |  |  | 33.7821 | 44.6884 | 44.6305 | 44.5674 | 44.4989 | 44.4242 | 44.3547 | 44.2884 | 44.2263 | 44.1737 | 43.9926 | 43.8863 | 3.5758 | 30.78 | 45.3547 | 45.2968 | 45.2337 | 45.1653 | 45.0916 | 45.0221 | 44.9558 | 44.8937 | 44.8411 | 44.6611 | 44.5568 | 44.4926 | 31.4758 | 44.6189 | 44.5611 | 44.4979 | 44.4295 | 44.3547 | 44.2853 | 44.22 | 44.1579 | 44.1042 | 43.9232 | 43.8168 | 43.7516
|  | BROCKHAMPTON | CF |  |  |  | 33.8126 | 33.7832 | 33.7537 | 33.7221 | 33.6895 | 33.6558 | 44.58 | 44.5463 | 44.5126 | 44.4789 | 44.3295 | 44.2537 | 44.2126 | 30.8105 | 30.7811 | 30.7516 | 30.68 | 30.6116 | 30.5411 | 45.2474 | 45.2137 | 45.18 | 45.1463 | 44.9968 | 44.9221 | 44.8811 | 31.5063 | 31.4768 | 31.4474 | 31.4158 | 31.3832 | 31.3495 | 44.5105 | 44.4768 | 44.4432 | 44.4095 | 44.26 | 44.1842 | 44.1432
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | BROCKHURST | MINIMUM HEADROOM | SU 59381 02061 | YES | 0.48947 | 34.6663 | 34.3937 | 34.1179 | 33.8242 | 33.5189 | 33.2 | 62.7547 | 61.5916 | 60.7032 | 59.8663 | 56.4874 | 54.4368 | 26.34 | 31.2989 | 30.6421 | 29.8158 | 29.0021 | 27.9905 | 26.7884 | 55.8874 | 54.5726 | 53.5758 | 52.6368 | 48.8547 | 46.5905 | 44.4789 | 32.2895 | 31.66 | 30.8747 | 30.0989 | 29.0989 | 27.8958 | 56.9937 | 55.6768 | 54.6789 | 53.7389 | 49.9474 | 47.6726 | 45.5579
|  | BROCKHURST | EE |  |  |  | 34.7663 | 34.5495 | 34.32 | 34.0747 | 33.8168 | 33.5474 | 63.2832 | 63.0316 | 61.9526 | 60.6863 | 57.66 | 56.0621 | 54.6379 | 31.5347 | 31.0853 | 30.4989 | 29.9053 | 29.1358 | 28.1821 | 57.4179 | 56.28 | 54.9653 | 53.5189 | 50.1211 | 48.3621 | 46.7684 | 32.4326 | 32.0832 | 31.5221 | 30.9537 | 30.2221 | 29.2895 | 58.5242 | 57.3842 | 56.0663 | 54.6189 | 51.2084 | 49.4368 | 47.8379
|  | BROCKHURST | HT |  |  |  | 34.6663 | 34.3937 | 34.1179 | 33.8242 | 33.5189 | 33.2 | 62.7547 | 61.5916 | 60.7032 | 59.8663 | 56.4874 | 54.4368 | 52.5442 | 31.2989 | 30.6421 | 29.8158 | 29.0021 | 27.9905 | 26.7884 | 55.8874 | 54.5726 | 53.5758 | 52.6368 | 48.8547 | 46.5905 | 44.4789 | 32.2895 | 31.66 | 30.8747 | 30.0989 | 29.0989 | 27.8958 | 56.9937 | 55.6768 | 54.6789 | 53.7389 | 49.9474 | 47.6726 | 45.5579
|  | BROCKHURST | HE |  |  |  | 34.9 | 34.7463 | 34.5747 | 34.3863 | 34.1832 | 33.9642 | 63.7547 | 63.5568 | 63.1084 | 62.0337 | 59.5989 | 58.5663 | 26.34 | 31.7495 | 31.5432 | 31.0874 | 30.62 | 29.9716 | 29.1168 | 58.4695 | 57.3905 | 56.2158 | 54.9842 | 52.2263 | 51.0768 | 50.0474 | 32.5663 | 32.4126 | 32.0863 | 31.64 | 31.0232 | 30.2158 | 59.5768 | 58.4968 | 57.3221 | 56.0895 | 53.3253 | 52.1716 | 51.1379
|  | BROCKHURST | CF |  |  |  | 34.9789 | 34.8863 | 34.7905 | 34.6905 | 34.5863 | 34.4779 | 64.3684 | 64.2589 | 64.1516 | 64.0453 | 62.6305 | 61.7842 | 61.1568 | 31.8284 | 31.7358 | 31.64 | 31.5074 | 31.3179 | 31.1095 | 60.92 | 60.6421 | 60.2821 | 59.6474 | 55.6242 | 54.6737 | 53.9642 | 32.6453 | 32.5526 | 32.4568 | 32.3568 | 32.2526 | 32.1 | 61.9158 | 61.6495 | 61.3084 | 60.7105 | 56.7284 | 55.7768 | 55.0642
MELKSHAM GSP | NORRINGTON | BROMHAM | MINIMUM HEADROOM | ST 98670 65994 | YES | 1.2063 | 4.8063 | 4.7421 | 4.6758 | 4.6053 | 4.5337 | 4.3221 | 4.0063 | 3.6284 | 3.5463 | 3.4674 | 2.6642 | 1.6411 | -1.6979 | 3.7537 | 3.6674 | 3.58 | 3.4874 | 3.3947 | 3.1211 | 2.7632 | 2.3295 | 2.2537 | 2.1811 | 1.3358 | 0.22421 | -0.093684 | 4.02 | 3.9368 | 3.8526 | 3.7632 | 3.6726 | 3.4021 | 3.0474 | 2.6095 | 2.5284 | 2.4495 | 1.5611 | 0.40105 | 0.064211
|  | BROMHAM | EE |  |  |  | 4.8316 | 4.7811 | 4.7274 | 4.6684 | 4.6084 | 4.5326 | 4.4526 | 4.3168 | 4.1737 | 4.0611 | 3.4558 | 2.5758 | 1.9779 | 3.7884 | 3.7232 | 3.6526 | 3.5779 | 3.5021 | 3.4126 | 3.3211 | 3.1463 | 2.9989 | 2.8905 | 2.3053 | 1.3937 | 0.72842 | 4.0526 | 3.9905 | 3.9211 | 3.8495 | 3.7747 | 3.6853 | 3.5884 | 3.4126 | 3.26 | 3.1463 | 2.5021 | 1.5221 | 0.83684
|  | BROMHAM | HT |  |  |  | 4.8063 | 4.7421 | 4.6758 | 4.6053 | 4.5337 | 4.3221 | 4.0063 | 3.6284 | 3.5463 | 3.4674 | 2.6642 | 1.6411 | 1.3253 | 3.7537 | 3.6674 | 3.58 | 3.4874 | 3.3947 | 3.1211 | 2.7632 | 2.3295 | 2.2537 | 2.1811 | 1.3358 | 0.22421 | -0.093684 | 4.02 | 3.9368 | 3.8526 | 3.7632 | 3.6726 | 3.4021 | 3.0474 | 2.6095 | 2.5284 | 2.4495 | 1.5611 | 0.40105 | 0.064211
|  | BROMHAM | HE |  |  |  | 4.8663 | 4.8337 | 4.7979 | 4.7568 | 4.7126 | 4.6547 | 4.6 | 4.5474 | 4.4958 | 4.4495 | 4.1158 | 3.5989 | -1.6979 | 3.8232 | 3.7905 | 3.7516 | 3.7011 | 3.6474 | 3.5821 | 3.52 | 3.4589 | 3.3653 | 3.3053 | 2.9537 | 2.3789 | 1.8411 | 4.0874 | 4.0547 | 4.0168 | 3.9674 | 3.9158 | 3.8484 | 3.7853 | 3.7242 | 3.6326 | 3.5695 | 3.2053 | 2.6126 | 2.0558
|  | BROMHAM | CF |  |  |  | 4.8874 | 4.8695 | 4.8516 | 4.8326 | 4.8126 | 4.7853 | 4.76 | 4.7337 | 4.7074 | 4.6832 | 4.5653 | 4.3863 | 4.0368 | 3.8442 | 3.8263 | 3.8084 | 3.7895 | 3.7653 | 3.7316 | 3.7 | 3.6674 | 3.6368 | 3.6042 | 3.4526 | 3.2147 | 2.8189 | 4.1084 | 4.0905 | 4.0726 | 4.0537 | 4.0305 | 3.9979 | 3.9653 | 3.9337 | 3.9011 | 3.8705 | 3.7179 | 3.4768 | 3.0758
BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | BROOK STREET | MINIMUM HEADROOM | SU 63480 52228 | YES | 0.52105 | 33.2547 | 33.1558 | 33.0568 | 32.9516 | 32.8421 | 32.7274 | 32.6105 | 32.5063 | 32.4095 | 32.32 | 31.9653 | 31.6526 | 10.2684 | 30.4579 | 30.3379 | 30.2179 | 30.0916 | 29.9621 | 29.8284 | 29.6768 | 29.5326 | 29.3968 | 29.2684 | 28.7695 | 28.1116 | 27.2253 | 30.9895 | 30.8916 | 30.7926 | 30.6874 | 30.5789 | 30.4642 | 30.3484 | 30.2442 | 30.1484 | 30.0589 | 29.7284 | 29.4 | 28.5274
|  | BROOK STREET | EE |  |  |  | 33.2958 | 33.22 | 33.1389 | 33.0547 | 32.9653 | 32.8716 | 32.78 | 32.6895 | 32.6011 | 32.5232 | 32.2463 | 32.0221 | 31.8316 | 30.5095 | 30.4168 | 30.3211 | 30.22 | 30.1147 | 30.0063 | 29.9 | 29.7926 | 29.6789 | 29.5695 | 29.1937 | 28.7989 | 28.2179 | 31.0305 | 30.9547 | 30.8747 | 30.7905 | 30.7011 | 30.6074 | 30.5158 | 30.4263 | 30.3389 | 30.2611 | 30.0074 | 29.7863 | 29.5084
|  | BROOK STREET | HT |  |  |  | 33.2547 | 33.1558 | 33.0568 | 32.9516 | 32.8421 | 32.7274 | 32.6105 | 32.5063 | 32.4095 | 32.32 | 31.9653 | 31.6526 | 31.3495 | 30.4579 | 30.3379 | 30.2179 | 30.0916 | 29.9621 | 29.8284 | 29.6768 | 29.5326 | 29.3968 | 29.2684 | 28.7695 | 28.1116 | 27.2253 | 30.9895 | 30.8916 | 30.7926 | 30.6874 | 30.5789 | 30.4642 | 30.3484 | 30.2442 | 30.1484 | 30.0589 | 29.7284 | 29.4 | 28.5274
|  | BROOK STREET | HE |  |  |  | 33.3358 | 33.2779 | 33.2147 | 33.1442 | 33.0695 | 32.9884 | 32.9126 | 32.8389 | 32.7705 | 32.7116 | 32.4768 | 32.3432 | 10.2684 | 30.5632 | 30.4968 | 30.4242 | 30.3432 | 30.2589 | 30.1695 | 30.0842 | 30.0011 | 29.9211 | 29.8537 | 29.5337 | 29.3253 | 29.0821 | 31.0695 | 31.0126 | 30.9495 | 30.8789 | 30.8042 | 30.7242 | 30.6474 | 30.5747 | 30.5063 | 30.4484 | 30.18 | 30.0474 | 29.9495
|  | BROOK STREET | CF |  |  |  | 33.3589 | 33.32 | 33.28 | 33.2389 | 33.1958 | 33.1526 | 33.1074 | 33.0632 | 33.0179 | 32.9747 | 32.7768 | 32.6716 | 32.6074 | 30.5916 | 30.5453 | 30.4979 | 30.4495 | 30.3989 | 30.3484 | 30.2947 | 30.2421 | 30.1895 | 30.1389 | 29.8989 | 29.7495 | 29.6042 | 31.0937 | 31.0547 | 31.0147 | 30.9737 | 30.9305 | 30.8874 | 30.8421 | 30.7979 | 30.7537 | 30.7105 | 30.5137 | 30.4095 | 30.3453
MELKSHAM GSP | FROME BSP | BRUTON | MINIMUM HEADROOM | ST 69094 35148 | YES | 0.81579 | 8.0758 | 7.94 | 7.8021 | 7.6611 | 7.5211 | 7.2158 | 6.8158 | 6.3421 | 6.2011 | 6.0589 | 4.8063 | 3.2526 | -0.69684 | 7.0411 | 6.8937 | 6.7474 | 6.5979 | 6.4484 | 6.1284 | 5.6989 | 5.1832 | 5.0579 | 4.9337 | 3.7189 | 2.1726 | 1.6863 | 7.4263 | 7.2789 | 7.1316 | 6.98 | 6.8305 | 6.4958 | 6.0516 | 5.52 | 5.3789 | 5.2358 | 3.8979 | 2.2084 | 1.6663
|  | BRUTON | EE |  |  |  | 8.1326 | 8.0274 | 7.9147 | 7.7968 | 7.68 | 7.5063 | 7.3211 | 7.1326 | 6.9368 | 6.74 | 5.6053 | 3.9379 | 3.0863 | 7.1032 | 6.9905 | 6.8695 | 6.7453 | 6.6232 | 6.4568 | 6.2842 | 6.1095 | 5.9337 | 5.7558 | 4.7558 | 3.1621 | 2.2874 | 7.4874 | 7.3747 | 7.2537 | 7.1284 | 7.0042 | 6.8232 | 6.6316 | 6.4347 | 6.2337 | 6.0316 | 4.8579 | 3.0653 | 2.1274
|  | BRUTON | HT |  |  |  | 8.0758 | 7.94 | 7.8021 | 7.6611 | 7.5211 | 7.2158 | 6.8158 | 6.3421 | 6.2011 | 6.0589 | 4.8063 | 3.2526 | 2.7347 | 7.0411 | 6.8937 | 6.7474 | 6.5979 | 6.4484 | 6.1284 | 5.6989 | 5.1832 | 5.0579 | 4.9337 | 3.7189 | 2.1726 | 1.6863 | 7.4263 | 7.2789 | 7.1316 | 6.98 | 6.8305 | 6.4958 | 6.0516 | 5.52 | 5.3789 | 5.2358 | 3.8979 | 2.2084 | 1.6663
|  | BRUTON | HE |  |  |  | 8.2147 | 8.1484 | 8.0768 | 8.0021 | 7.9221 | 7.7958 | 7.6821 | 7.5716 | 7.46 | 7.3558 | 6.7958 | 5.9189 | -0.69684 | 7.1916 | 7.1211 | 7.0453 | 6.9653 | 6.8821 | 6.76 | 6.6526 | 6.5484 | 6.4442 | 6.3484 | 5.8368 | 4.9168 | 4.2105 | 7.5768 | 7.5063 | 7.4305 | 7.3505 | 7.2663 | 7.1337 | 7.0179 | 6.9032 | 6.7884 | 6.6811 | 6.0979 | 5.1232 | 4.3642
|  | BRUTON | CF |  |  |  | 8.2579 | 8.2179 | 8.1779 | 8.1368 | 8.0926 | 8.0274 | 7.9621 | 7.8958 | 7.8316 | 7.7747 | 7.4589 | 7.0905 | 6.6 | 7.2379 | 7.1958 | 7.1526 | 7.1084 | 7.06 | 6.9979 | 6.9326 | 6.8684 | 6.8063 | 6.7484 | 6.4389 | 6.0705 | 5.5579 | 7.6232 | 7.5811 | 7.5379 | 7.4937 | 7.4453 | 7.3768 | 7.3084 | 7.2389 | 7.1716 | 7.1105 | 6.7768 | 6.3768 | 5.8305
COWLEY GSP | WITNEY BSP | BURFORD | MINIMUM HEADROOM | SP 25671 12529 | YES | 0 | 7.7716 | 7.7242 | 7.6758 | 7.6253 | 7.5705 | 7.5137 | 7.4558 | 7.4053 | 7.3589 | 7.3158 | 7.1126 | 6.7695 | -0.032632 | 6.5926 | 6.5337 | 6.4547 | 6.3642 | 6.2758 | 6.18 | 6.0853 | 5.9979 | 5.9158 | 5.8379 | 5.4842 | 5.1011 | 4.7137 | 6.7632 | 6.7158 | 6.6674 | 6.6095 | 6.5179 | 6.4221 | 6.3274 | 6.2411 | 6.1589 | 6.0811 | 5.7274 | 5.3453 | 4.9579
|  | BURFORD | EE |  |  |  | 7.7895 | 7.7516 | 7.7105 | 7.6684 | 7.6242 | 7.5779 | 7.5326 | 7.4884 | 7.4453 | 7.4074 | 7.2663 | 7.1084 | 6.8274 | 6.6137 | 6.5716 | 6.52 | 6.4558 | 6.3853 | 6.3137 | 6.2453 | 6.1716 | 6.1 | 6.0347 | 5.7611 | 5.4747 | 5.1558 | 6.7811 | 6.7432 | 6.7021 | 6.66 | 6.6158 | 6.5589 | 6.4884 | 6.4147 | 6.3421 | 6.2768 | 6.0042 | 5.7179 | 5.3989
|  | BURFORD | HT |  |  |  | 7.7716 | 7.7242 | 7.6758 | 7.6253 | 7.5705 | 7.5137 | 7.4558 | 7.4053 | 7.3589 | 7.3158 | 7.1126 | 6.7695 | 6.4253 | 6.5926 | 6.5337 | 6.4547 | 6.3642 | 6.2758 | 6.18 | 6.0853 | 5.9979 | 5.9158 | 5.8379 | 5.4842 | 5.1011 | 4.7137 | 6.7632 | 6.7158 | 6.6674 | 6.6095 | 6.5179 | 6.4221 | 6.3274 | 6.2411 | 6.1589 | 6.0811 | 5.7274 | 5.3453 | 4.9579
|  | BURFORD | HE |  |  |  | 7.8147 | 7.7884 | 7.76 | 7.7284 | 7.6947 | 7.6589 | 7.6242 | 7.5916 | 7.5611 | 7.5347 | 7.4432 | 7.3821 | -0.032632 | 6.6432 | 6.6147 | 6.5842 | 6.5495 | 6.5116 | 6.4705 | 6.4295 | 6.3789 | 6.3316 | 6.2874 | 6.1274 | 5.9337 | 5.7042 | 6.8063 | 6.78 | 6.7516 | 6.72 | 6.6863 | 6.6505 | 6.6158 | 6.5832 | 6.5526 | 6.5263 | 6.3695 | 6.1758 | 5.9484
|  | BURFORD | CF |  |  |  | 7.8295 | 7.8147 | 7.7989 | 7.7832 | 7.7674 | 7.7495 | 7.7326 | 7.7158 | 7.6989 | 7.6821 | 7.6063 | 7.5642 | 7.5347 | 6.66 | 6.6432 | 6.6253 | 6.6084 | 6.5905 | 6.5705 | 6.5495 | 6.5284 | 6.5074 | 6.4853 | 6.3442 | 6.2263 | 6.0821 | 6.8211 | 6.8063 | 6.7905 | 6.7747 | 6.7589 | 6.7411 | 6.7242 | 6.7074 | 6.6905 | 6.6737 | 6.5905 | 6.4695 | 6.3253
MANNINGTON GSP | WAREHAM | BUSHEY | MINIMUM HEADROOM | SY 97671 83532 | YES | 0 | 5.1358 | 5.0916 | 5.0495 | 4.9295 | 4.8863 | 4.8432 | 4.8011 | 4.7621 | 4.7253 | 4.6916 | 4.5411 | 4.4147 | 2.4021 | 5.1337 | 5.1053 | 5.0747 | 4.9505 | 4.9063 | 4.8611 | 4.8158 | 4.7747 | 4.7358 | 4.7 | 4.5379 | 4.4011 | 4.2789 | 4.9179 | 4.8705 | 4.8242 | 4.6853 | 4.6379 | 4.5926 | 4.5474 | 4.5053 | 4.4653 | 4.4295 | 4.2653 | 4.1253 | 4.0011
|  | BUSHEY | EE |  |  |  | 5.1537 | 5.12 | 5.0863 | 4.9758 | 4.94 | 4.9032 | 4.8695 | 4.8368 | 4.8042 | 4.7768 | 4.6589 | 4.5653 | 4.4863 | 5.1442 | 5.1211 | 5.0989 | 4.9979 | 4.9611 | 4.9242 | 4.8895 | 4.8547 | 4.8221 | 4.7926 | 4.6653 | 4.5642 | 4.4779 | 4.9379 | 4.9011 | 4.8642 | 4.7358 | 4.6968 | 4.6589 | 4.6232 | 4.5874 | 4.5526 | 4.5232 | 4.3947 | 4.2916 | 4.2032
|  | BUSHEY | HT |  |  |  | 5.1358 | 5.0916 | 5.0495 | 4.9295 | 4.8863 | 4.8432 | 4.8011 | 4.7621 | 4.7253 | 4.6916 | 4.5411 | 4.4147 | 4.3032 | 5.1337 | 5.1053 | 5.0747 | 4.9505 | 4.9063 | 4.8611 | 4.8158 | 4.7747 | 4.7358 | 4.7 | 4.5379 | 4.4011 | 4.2789 | 4.9179 | 4.8705 | 4.8242 | 4.6853 | 4.6379 | 4.5926 | 4.5474 | 4.5053 | 4.4653 | 4.4295 | 4.2653 | 4.1253 | 4.0011
|  | BUSHEY | HE |  |  |  | 5.18 | 5.1589 | 5.1368 | 5.0368 | 5.0137 | 4.9874 | 4.9632 | 4.94 | 4.9189 | 4.8989 | 4.8295 | 4.7789 | 2.4021 | 5.1589 | 5.1442 | 5.1284 | 5.0611 | 5.0368 | 5.0105 | 4.9853 | 4.9621 | 4.9411 | 4.9211 | 4.8495 | 4.7968 | 4.7558 | 4.9674 | 4.9442 | 4.9211 | 4.8042 | 4.7789 | 4.7516 | 4.7253 | 4.7011 | 4.6789 | 4.6579 | 4.5832 | 4.5284 | 4.4863
|  | BUSHEY | CF |  |  |  | 5.1947 | 5.1811 | 5.1674 | 5.1221 | 5.1084 | 5.0947 | 5.08 | 5.0653 | 5.0516 | 5.0379 | 4.9747 | 4.9326 | 4.9011 | 5.1674 | 5.16 | 5.1505 | 5.1368 | 5.1274 | 5.1189 | 5.1053 | 5.0905 | 5.0758 | 5.0621 | 4.9979 | 4.9547 | 4.9221 | 4.9832 | 4.9684 | 4.9537 | 4.9011 | 4.8853 | 4.8705 | 4.8547 | 4.8389 | 4.8242 | 4.8095 | 4.7411 | 4.6937 | 4.6579
FAWLEY GSP | LANGLEY BSP | BUTTS ASH | MINIMUM HEADROOM | SU 41923 05772 | YES | 0 | 25.0211 | 24.5874 | 24.1505 | 23.6895 | 23.2168 | 22.7295 | 22.24 | 21.7147 | 21.0926 | 20.5126 | 17.6589 | 14.6926 | -9.1505 | 20.9495 | 20.1947 | 19.4421 | 18.6674 | 17.8947 | 17.1242 | 16.3411 | 15.6284 | 14.9632 | 14.3411 | 11.2337 | 7.9316 | 4.7526 | 21.6158 | 20.8389 | 20.0842 | 19.3242 | 18.5653 | 17.8084 | 17.0453 | 16.3547 | 15.7084 | 15.1 | 11.9853 | 8.6737 | 5.4905
|  | BUTTS ASH | EE |  |  |  | 25.1895 | 24.8505 | 24.4937 | 24.1147 | 23.7232 | 23.3168 | 22.9232 | 22.5484 | 22.1895 | 21.8674 | 19.7947 | 17.5105 | 15.3684 | 21.28 | 20.6989 | 20.1211 | 19.5221 | 18.8968 | 18.2663 | 17.6505 | 17.0621 | 16.4947 | 15.9674 | 13.5737 | 11.0284 | 8.6032 | 21.84 | 21.36 | 20.7674 | 20.1579 | 19.5453 | 18.9242 | 18.3179 | 17.7379 | 17.1811 | 16.6674 | 14.32 | 11.7642 | 9.3347
|  | BUTTS ASH | HT |  |  |  | 25.0211 | 24.5874 | 24.1505 | 23.6895 | 23.2168 | 22.7295 | 22.24 | 21.7147 | 21.0926 | 20.5126 | 17.6589 | 14.6926 | 11.8695 | 20.9495 | 20.1947 | 19.4421 | 18.6674 | 17.8947 | 17.1242 | 16.3411 | 15.6284 | 14.9632 | 14.3411 | 11.2337 | 7.9316 | 4.7526 | 21.6158 | 20.8389 | 20.0842 | 19.3242 | 18.5653 | 17.8084 | 17.0453 | 16.3547 | 15.7084 | 15.1 | 11.9853 | 8.6737 | 5.4905
|  | BUTTS ASH | HE |  |  |  | 25.4253 | 25.1979 | 24.9495 | 24.6747 | 24.3811 | 24.0674 | 23.7653 | 23.4811 | 23.2147 | 22.9842 | 22.1779 | 21.0895 | -9.1505 | 21.7263 | 21.3568 | 20.9832 | 20.5842 | 20.1705 | 19.7347 | 19.3126 | 18.9105 | 18.52 | 18.1726 | 16.6516 | 14.9189 | 13.24 | 22.0737 | 21.8474 | 21.6 | 21.2495 | 20.8263 | 20.3821 | 19.9526 | 19.5453 | 19.16 | 18.8179 | 17.3263 | 15.6726 | 13.9895
|  | BUTTS ASH | CF |  |  |  | 25.5526 | 25.4316 | 25.3 | 25.1632 | 25.02 | 24.8737 | 24.7221 | 24.5747 | 24.4274 | 24.2811 | 23.6242 | 23.2568 | 22.6411 | 21.8863 | 21.7316 | 21.5105 | 21.2821 | 21.0484 | 20.8105 | 20.5653 | 20.3274 | 20.0884 | 19.8495 | 18.7284 | 17.6284 | 16.5021 | 22.2074 | 22.08 | 21.9495 | 21.8126 | 21.6716 | 21.4768 | 21.2253 | 20.9821 | 20.7358 | 20.4905 | 19.3779 | 18.3116 | 17.2505
MELKSHAM GSP | CHIPPENHAM | CALNE | MINIMUM HEADROOM | SU 00521 72497 | YES | 1.1389 | 14.0832 | 13.6105 | 12.9779 | 12.3705 | 11.3316 | 10.0789 | 8.9221 | 8.0726 | 7.2379 | 6.3968 | 3.5032 | 1.3274 | -15.0074 | 12.9326 | 12.4547 | 11.8137 | 11.1979 | 10.0168 | 8.5547 | 7.1811 | 6.1905 | 5.2095 | 4.2147 | 0.85684 | -2.4147 | -6.1926 | 13.6474 | 13.2316 | 12.7053 | 12.0526 | 10.8884 | 9.4726 | 8.1 | 7.1095 | 6.1284 | 5.1326 | 1.7663 | -1.7632 | -5.2926
|  | CALNE | EE |  |  |  | 14.2453 | 13.9158 | 13.5063 | 12.9674 | 13.7368 | 12.7389 | 11.82 | 11.0063 | 10.0032 | 10.4695 | 8.1779 | 8.6137 | 6.1558 | 13.0947 | 12.7632 | 12.3495 | 11.8042 | 11.0747 | 9.96 | 8.9379 | 8.0379 | 6.9116 | 8.22 | 5.8137 | 7.4842 | 4.6874 | 13.7937 | 13.4895 | 13.1326 | 12.6958 | 11.9905 | 10.8758 | 9.8537 | 8.9526 | 7.8253 | 9.3916 | 6.8747 | 9.2042 | 6.4032
|  | CALNE | HT |  |  |  | 14.0832 | 13.6105 | 12.9779 | 12.3705 | 11.3316 | 10.0789 | 8.9221 | 8.0726 | 7.2379 | 6.3968 | 3.5032 | 1.3274 | -1.7726 | 12.9326 | 12.4547 | 11.8137 | 11.1979 | 10.0168 | 8.5547 | 7.1811 | 6.1905 | 5.2095 | 4.2147 | 0.85684 | -2.4147 | -6.1926 | 13.6474 | 13.2316 | 12.7053 | 12.0526 | 10.8884 | 9.4726 | 8.1 | 7.1095 | 6.1284 | 5.1326 | 1.7663 | -1.7632 | -5.2926
|  | CALNE | HE |  |  |  | 14.4274 | 14.2421 | 14.0263 | 13.7632 | 13.1874 | 12.3579 | 11.6189 | 10.9611 | 10.1558 | 9.2368 | 7.7263 | 11.1821 | -15.0074 | 13.2768 | 13.0916 | 12.8758 | 12.6116 | 12.0253 | 11.1432 | 10.2853 | 9.5263 | 8.5674 | 7.4432 | 5.6958 | 3.8337 | 1.72 | 13.9758 | 13.7905 | 13.58 | 13.3326 | 12.9011 | 11.9926 | 11.1611 | 10.4232 | 9.4832 | 8.36 | 6.6063 | 8.8968 | 6.8221
|  | CALNE | CF |  |  |  | 14.5337 | 14.4284 | 14.3211 | 14.2084 | 14.0758 | 13.9253 | 13.7737 | 13.5221 | 13.2389 | 12.7632 | 10.6937 | 9.7084 | 8.6063 | 13.3832 | 13.2779 | 13.1705 | 13.0579 | 12.9242 | 12.7747 | 12.6211 | 12.3663 | 12.08 | 11.5926 | 9.1611 | 7.9779 | 6.6095 | 14.0821 | 13.9768 | 13.8695 | 13.7568 | 13.6305 | 13.4926 | 13.3526 | 13.1579 | 12.9442 | 12.4411 | 10.0768 | 8.8905 | 7.5211
BRAMLEY (FLEE) | CAMBERLEY MAIN | CAMBERLEY | MINIMUM HEADROOM | SU 86584 59452 | YES | 1.5674 | 89.0305 | 88.6916 | 88.3505 | 87.9874 | 87.6116 | 87.2253 | 86.8358 | 86.4947 | 86.1853 | 85.8989 | 83.9874 | 81.4295 | 37.7926 | 81.1579 | 80.4484 | 79.7284 | 79.0674 | 78.4042 | 77.7474 | 77.1011 | 76.5105 | 75.9611 | 75.4411 | 72.8042 | 69.9305 | 67.3389 | 82.7547 | 82.4158 | 81.8453 | 81.1958 | 80.5421 | 79.8853 | 79.2389 | 78.6484 | 78.0979 | 77.5779 | 74.94 | 72.0653 | 69.4726
|  | CAMBERLEY | EE |  |  |  | 89.1642 | 88.9 | 88.6221 | 88.3253 | 88.0168 | 87.6958 | 87.3863 | 87.0926 | 86.8116 | 86.56 | 85.6474 | 83.8316 | 82.1074 | 81.4032 | 80.8937 | 80.3095 | 79.78 | 79.2463 | 78.7095 | 78.1958 | 77.7063 | 77.2295 | 76.7958 | 74.7705 | 72.5579 | 70.6042 | 82.8884 | 82.6242 | 82.3463 | 81.8947 | 81.3695 | 80.84 | 80.3337 | 79.8453 | 79.3674 | 78.9337 | 76.9074 | 74.6926 | 72.7389
|  | CAMBERLEY | HT |  |  |  | 89.0305 | 88.6916 | 88.3505 | 87.9874 | 87.6116 | 87.2253 | 86.8358 | 86.4947 | 86.1853 | 85.8989 | 83.9874 | 81.4295 | 79.1211 | 81.1579 | 80.4484 | 79.7284 | 79.0674 | 78.4042 | 77.7474 | 77.1011 | 76.5105 | 75.9611 | 75.4411 | 72.8042 | 69.9305 | 67.3389 | 82.7547 | 82.4158 | 81.8453 | 81.1958 | 80.5421 | 79.8853 | 79.2389 | 78.6484 | 78.0979 | 77.5779 | 74.94 | 72.0653 | 69.4726
|  | CAMBERLEY | HE |  |  |  | 89.3411 | 89.1611 | 88.9632 | 88.7442 | 88.5084 | 88.2579 | 88.0158 | 87.7884 | 87.5768 | 87.3937 | 86.7789 | 86.4189 | 37.7926 | 81.5895 | 81.4011 | 81.0684 | 80.7126 | 80.3389 | 79.9558 | 79.5916 | 79.2463 | 78.9168 | 78.6274 | 77.3053 | 75.7463 | 74.4158 | 83.0653 | 82.8853 | 82.6874 | 82.4684 | 82.2326 | 81.9821 | 81.7011 | 81.36 | 81.0347 | 80.7495 | 79.4421 | 77.8842 | 76.5516
|  | CAMBERLEY | CF |  |  |  | 89.1021 | 89 | 88.8937 | 88.7832 | 88.6695 | 88.5516 | 88.4305 | 88.3126 | 88.1937 | 88.0758 | 87.8937 | 87.6326 | 87.4895 | 81.2495 | 81.1421 | 81.0305 | 80.8958 | 80.6832 | 80.4642 | 80.2305 | 80.0158 | 79.7968 | 79.58 | 79.0337 | 77.9495 | 77.0232 | 82.7895 | 82.6874 | 82.5811 | 82.4705 | 82.3568 | 82.2389 | 82.1179 | 82 | 81.8811 | 81.7232 | 81.1589 | 80.0863 | 79.16
WILLESDEN GSP |  | CANAL BANK 11kV | MINIMUM HEADROOM | TQ 20927 83082 | NO | 0.32737 | 70.8768 | 70.8547 | 70.0526 | 68.3642 | 66.3947 | 63.7726 | 61.2642 | 58.9853 | 58.9621 | 58.9421 | 56.4663 | 52.0937 | -10.2853 | 63.1337 | 62.52 | 61.0632 | 59.2653 | 57.1674 | 54.3747 | 51.5905 | 48.9 | 48.8768 | 48.8568 | 45.8937 | 40.7863 | 36.2863 | 65.0474 | 64.9632 | 64.2642 | 62.5716 | 60.4989 | 57.52 | 54.6137 | 51.9284 | 51.9053 | 51.8853 | 48.9284 | 43.8211 | 39.3484
|  | CANAL BANK 11kV | EE |  |  |  | 70.8874 | 70.8705 | 70.82 | 69.5295 | 67.76 | 65.5084 | 63.5053 | 61.4 | 61.38 | 61.3621 | 56.5105 | 52.3632 | 48.8768 | 63.1516 | 62.8684 | 61.8789 | 60.5053 | 58.62 | 56.2232 | 54.0895 | 51.7463 | 51.7263 | 51.7084 | 45.9537 | 41.1337 | 37.0379 | 65.0589 | 65.0042 | 64.9168 | 63.74 | 61.9653 | 59.4895 | 57.2147 | 54.7705 | 54.7505 | 54.7326 | 48.9884 | 44.1874 | 40.0989
|  | CANAL BANK 11kV | HT |  |  |  | 70.8768 | 70.8547 | 70.0526 | 68.3642 | 66.3947 | 63.7726 | 61.2642 | 58.9853 | 58.9621 | 58.9421 | 56.8168 | 52.0937 | 48.2211 | 63.1337 | 62.52 | 61.0632 | 59.2653 | 57.1674 | 54.3747 | 51.5905 | 48.9 | 48.8768 | 48.8568 | 46.3768 | 40.8326 | 36.2863 | 65.0474 | 64.9632 | 64.2642 | 62.5716 | 60.4989 | 57.52 | 54.6137 | 51.9284 | 51.9053 | 51.8853 | 49.42 | 43.8863 | 39.3484
|  | CANAL BANK 11kV | HE |  |  |  | 70.8937 | 70.88 | 70.8232 | 69.5189 | 67.7558 | 65.4821 | 63.4674 | 61.2789 | 61.2632 | 61.2495 | 56.4663 | 52.1642 | -10.2853 | 63.1621 | 62.8884 | 61.8811 | 60.4926 | 58.6147 | 56.1937 | 54.0484 | 51.6 | 51.5842 | 51.5705 | 45.8937 | 40.7863 | 36.7484 | 65.0663 | 65.0147 | 64.9274 | 63.7284 | 61.9611 | 59.4579 | 57.1695 | 54.6242 | 54.6084 | 54.5947 | 48.9284 | 43.8211 | 39.7905
|  | CANAL BANK 11kV | CF |  |  |  | 70.8979 | 70.8884 | 70.8789 | 70.8684 | 70.8579 | 70.8463 | 70.8347 | 70.6432 | 69.3558 | 67.7474 | 57.4147 | 54.0737 | 51.5242 | 63.3284 | 63.3158 | 63.2716 | 63.2042 | 63.1116 | 62.9326 | 62.4895 | 61.6916 | 60.3221 | 58.6084 | 47.0337 | 43.0726 | 40.0758 | 65.1063 | 65.0937 | 65.0747 | 65.0537 | 65.0284 | 64.9874 | 64.9421 | 64.8558 | 63.5663 | 61.9537 | 50.0663 | 46.1126 | 43.1211
COWLEY GSP | WITNEY BSP | CARTERTON | MINIMUM HEADROOM | SP 28261 07823 | YES | 0.14737 | 35.7989 | 35.9537 | 35.1989 | 34.4789 | 33.7411 | 33.0811 | 32.54 | 32.0442 | 31.5842 | 31.1505 | 29.0663 | 26.6032 | 0.82 | 33.8968 | 32.5653 | 31.5347 | 30.7453 | 29.9832 | 29.2663 | 28.6874 | 28.1558 | 27.6621 | 27.1958 | 24.9537 | 22.1874 | 19.2389 | 34.4095 | 33.0653 | 32.0263 | 31.2316 | 30.4179 | 29.6989 | 29.12 | 28.5874 | 28.0937 | 27.6253 | 25.3474 | 22.5779 | 19.6326
|  | CARTERTON | EE |  |  |  | 35.7989 | 36.4642 | 35.64 | 35.0232 | 34.3874 | 33.8242 | 33.3926 | 32.9747 | 32.5674 | 32.1842 | 30.6095 | 28.7516 | 26.7179 | 34.1389 | 32.9337 | 32.0126 | 31.3358 | 30.6884 | 30.0768 | 29.6168 | 29.1716 | 28.7358 | 28.3263 | 26.6242 | 24.5474 | 22.2242 | 34.6484 | 33.4368 | 32.5084 | 31.8253 | 31.1232 | 30.5095 | 30.0484 | 29.6011 | 29.1642 | 28.7526 | 27.0421 | 24.9526 | 22.6242
|  | CARTERTON | HT |  |  |  | 37.3063 | 36.1242 | 35.1989 | 34.4789 | 33.7411 | 33.0811 | 32.54 | 32.0442 | 31.5842 | 31.1505 | 29.0663 | 26.6032 | 24.0168 | 33.8968 | 32.5653 | 31.5347 | 30.7453 | 29.9832 | 29.2663 | 28.6874 | 28.1558 | 27.6621 | 27.1958 | 24.9537 | 22.1874 | 19.2389 | 34.4095 | 33.0653 | 32.0263 | 31.2316 | 30.4179 | 29.6989 | 29.12 | 28.5874 | 28.0937 | 27.6253 | 25.3474 | 22.5779 | 19.6326
|  | CARTERTON | HE |  |  |  | 35.9526 | 36.9232 | 36.2411 | 35.7632 | 35.2558 | 34.8126 | 34.5021 | 34.2011 | 33.9137 | 33.6484 | 32.6495 | 31.3232 | 0.82 | 34.4789 | 33.4316 | 32.6642 | 32.1389 | 31.5811 | 31.1011 | 30.8253 | 30.5074 | 30.2011 | 29.9189 | 28.8411 | 27.3379 | 25.5526 | 34.9863 | 33.9379 | 33.1632 | 32.6347 | 32.0726 | 31.5884 | 31.2589 | 30.94 | 30.6337 | 30.3495 | 29.2684 | 27.7611 | 25.9716
|  | CARTERTON | CF |  |  |  | 36.0411 | 35.9537 | 37.2653 | 37.0168 | 36.7432 | 36.5063 | 36.3084 | 36.1368 | 35.9642 | 35.7905 | 34.9442 | 34.1695 | 33.1842 | 34.7337 | 34.2147 | 33.82 | 33.5453 | 33.2421 | 32.9842 | 32.7705 | 32.5863 | 32.4042 | 32.2179 | 31.3074 | 30.4421 | 29.3579 | 35.18 | 34.7232 | 34.3305 | 34.0537 | 33.7484 | 33.4874 | 33.2716 | 33.0884 | 32.9032 | 32.7168 | 31.7989 | 30.9242 | 29.7853
AXMINSTER | YEOVIL BSP | CASTLE CARY | MINIMUM HEADROOM | ST 64534 31039 | YES | 0.15789 | 15.3432 | 15.2411 | 15.1295 | 14.8558 | 14.5105 | 14.1368 | 13.9432 | 13.7853 | 13.6368 | 13.5042 | 12.8221 | 12.2253 | 4.8432 | 14.4895 | 14.3032 | 13.9863 | 13.6337 | 13.2463 | 12.8263 | 12.6179 | 12.4495 | 12.2916 | 12.1505 | 11.4074 | 10.7516 | 10.0968 | 14.5526 | 14.3726 | 14.0705 | 13.7179 | 13.3305 | 12.9105 | 12.7032 | 12.5337 | 12.3758 | 12.2337 | 11.4895 | 10.8326 | 10.1768
|  | CASTLE CARY | EE |  |  |  | 15.3821 | 15.3011 | 15.2074 | 15.0368 | 14.7232 | 14.38 | 14.22 | 14.0853 | 13.9579 | 13.8463 | 13.3168 | 12.8758 | 12.4379 | 14.5705 | 14.4253 | 14.1463 | 13.8305 | 13.4789 | 13.0926 | 12.9189 | 12.7768 | 12.6432 | 12.5242 | 11.9495 | 11.4663 | 10.9779 | 14.6305 | 14.4916 | 14.2274 | 13.9147 | 13.5621 | 13.1747 | 13.0021 | 12.86 | 12.7232 | 12.6042 | 12.0295 | 11.5421 | 11.0526
|  | CASTLE CARY | HT |  |  |  | 15.3432 | 15.2411 | 15.1295 | 14.8558 | 14.5105 | 14.1368 | 13.9432 | 13.7853 | 13.6368 | 13.5042 | 12.8221 | 12.2253 | 11.6379 | 14.4895 | 14.3032 | 13.9863 | 13.6337 | 13.2463 | 12.8263 | 12.6179 | 12.4495 | 12.2916 | 12.1505 | 11.4074 | 10.7516 | 10.0968 | 14.5526 | 14.3726 | 14.0705 | 13.7179 | 13.3305 | 12.9105 | 12.7032 | 12.5337 | 12.3758 | 12.2337 | 11.4895 | 10.8326 | 10.1768
|  | CASTLE CARY | HE |  |  |  | 15.4347 | 15.3832 | 15.3158 | 15.2379 | 15.0147 | 14.7126 | 14.5926 | 14.4979 | 14.4095 | 14.3347 | 13.9937 | 13.7284 | 4.8432 | 14.6295 | 14.5779 | 14.3663 | 14.0989 | 13.7947 | 13.4526 | 13.3232 | 13.2242 | 13.1295 | 13.0516 | 12.6832 | 12.3884 | 12.08 | 14.6895 | 14.6379 | 14.4389 | 14.1842 | 13.8789 | 13.5368 | 13.4084 | 13.3084 | 13.2147 | 13.1368 | 12.7663 | 12.4737 | 12.1632
|  | CASTLE CARY | CF |  |  |  | 15.4642 | 15.4347 | 15.4032 | 15.3642 | 15.3253 | 15.2832 | 15.2463 | 15.2 | 15.1421 | 15.0842 | 14.8105 | 14.6032 | 14.4 | 14.6589 | 14.6295 | 14.5695 | 14.4389 | 14.2968 | 14.1421 | 14.0663 | 14.0042 | 13.9421 | 13.88 | 13.5842 | 13.3547 | 13.1242 | 14.7189 | 14.6895 | 14.6316 | 14.5084 | 14.3758 | 14.2274 | 14.1516 | 14.0895 | 14.0263 | 13.9653 | 13.6684 | 13.4379 | 13.2074
LALEHAM | STAINES | CAUSEWAY | MINIMUM HEADROOM | TQ 02763 71680 | YES | 0.13684 | 58.8284 | 58.5874 | 58.3453 | 58.0874 | 57.8211 | 57.3305 | 56.3063 | 55.3274 | 54.3653 | 52.6895 | 50.6705 | 48.88 | 22.8916 | 55.2105 | 54.7663 | 53.6958 | 53.0463 | 51.9547 | 50.8937 | 49.7389 | 48.6326 | 47.5411 | 45.6095 | 43.3821 | 41.3874 | 39.5589 | 56.1779 | 55.9368 | 55.2453 | 54.6095 | 53.5789 | 52.5747 | 51.4853 | 50.4411 | 49.3884 | 47.4558 | 45.2284 | 43.2326 | 41.4042
|  | CAUSEWAY | EE |  |  |  | 58.9221 | 58.7337 | 58.5337 | 58.3232 | 58.1021 | 57.8726 | 57.0505 | 56.1484 | 55.2484 | 53.6389 | 52.0147 | 50.6179 | 49.3621 | 55.4053 | 55.06 | 53.6958 | 53.4853 | 52.5484 | 51.5874 | 50.5474 | 49.5232 | 48.5032 | 46.6432 | 44.8505 | 43.2874 | 41.8705 | 56.2716 | 56.0832 | 55.2453 | 55.0347 | 54.1495 | 53.2421 | 52.2611 | 51.2968 | 50.3358 | 48.4905 | 46.6979 | 45.1337 | 43.7158
|  | CAUSEWAY | HT |  |  |  | 58.8284 | 58.5874 | 58.3453 | 58.0874 | 57.8211 | 57.3305 | 56.3063 | 55.3274 | 54.3653 | 52.6895 | 50.6705 | 48.88 | 47.2505 | 55.2105 | 54.7663 | 54.0411 | 53.0463 | 51.9547 | 50.8937 | 49.7389 | 48.6326 | 47.5411 | 45.6095 | 43.3821 | 41.3874 | 39.5589 | 56.1779 | 55.9368 | 55.5516 | 54.6095 | 53.5789 | 52.5747 | 51.4853 | 50.4411 | 49.3884 | 47.4558 | 45.2284 | 43.2326 | 41.4042
|  | CAUSEWAY | HE |  |  |  | 59.0463 | 58.9179 | 58.7758 | 58.6179 | 58.4484 | 58.2684 | 57.9589 | 57.1495 | 56.3547 | 54.8432 | 53.6884 | 52.72 | 22.8916 | 55.6642 | 55.4432 | 54.9253 | 54.2095 | 53.3253 | 52.4716 | 51.5358 | 50.6137 | 49.7074 | 47.9558 | 46.6768 | 45.5842 | 44.6147 | 56.3958 | 56.2674 | 56.1253 | 55.7274 | 54.8947 | 54.0905 | 53.2095 | 52.3432 | 51.4926 | 49.8032 | 48.5242 | 47.4305 | 46.4611
|  | CAUSEWAY | CF |  |  |  | 59.1179 | 59.0442 | 58.9674 | 58.8874 | 58.8053 | 58.7211 | 58.6337 | 58.5484 | 58.4632 | 58.1126 | 57.24 | 56.5737 | 56.0232 | 55.8116 | 55.6747 | 55.5084 | 55.2789 | 54.9611 | 54.5063 | 53.9337 | 53.3621 | 52.8084 | 51.6663 | 50.7074 | 49.9589 | 49.3295 | 56.4674 | 56.3937 | 56.3168 | 56.2368 | 56.1547 | 56.0211 | 55.4726 | 54.9368 | 54.4168 | 53.3526 | 52.4358 | 51.7274 | 51.1368
BRAMLEY (FLEE) | READING TOWN BSP | CAVERSHAM | MINIMUM HEADROOM | SU 71512 75747 | YES | 0 | 33.0516 | 32.6653 | 32.2747 | 31.6126 | 30.9042 | 30.1789 | 29.4516 | 28.7895 | 28.1726 | 27.5947 | 25.0663 | 22.5 | 4.4558 | 29.66 | 28.9074 | 28.1758 | 27.42 | 26.6632 | 25.8884 | 25.1105 | 24.4032 | 23.74 | 23.1179 | 20.3789 | 17.5358 | 14.8874 | 30.4063 | 29.6811 | 28.9747 | 28.2337 | 27.4768 | 26.7021 | 25.9242 | 25.2158 | 24.5516 | 23.9295 | 21.1895 | 18.3453 | 15.6958
|  | CAVERSHAM | EE |  |  |  | 33.2042 | 32.9032 | 32.5853 | 32.2474 | 31.7905 | 31.1989 | 30.6242 | 30.0726 | 29.5274 | 29.0337 | 27.1053 | 25.1779 | 23.3905 | 29.9968 | 29.4168 | 28.8389 | 28.2358 | 27.6232 | 26.9916 | 26.3779 | 25.7905 | 25.2053 | 24.6747 | 22.5926 | 20.4516 | 18.4432 | 30.7305 | 30.1705 | 29.6116 | 29.0274 | 28.4337 | 27.8063 | 27.1926 | 26.6032 | 26.0189 | 25.4884 | 23.4042 | 21.2621 | 19.2516
|  | CAVERSHAM | HT |  |  |  | 33.0516 | 32.6653 | 32.2747 | 31.6126 | 30.9042 | 30.1789 | 29.4516 | 28.7895 | 28.1726 | 27.5947 | 25.0663 | 22.5 | 20.1295 | 29.66 | 28.9074 | 28.1758 | 27.42 | 26.6632 | 25.8884 | 25.1105 | 24.4032 | 23.74 | 23.1179 | 20.3789 | 17.5358 | 14.8874 | 30.4063 | 29.6811 | 28.9747 | 28.2337 | 27.4768 | 26.7021 | 25.9242 | 25.2158 | 24.5516 | 23.9295 | 21.1895 | 18.3453 | 15.6958
|  | CAVERSHAM | HE |  |  |  | 33.4095 | 33.2063 | 32.9821 | 32.7347 | 32.4674 | 32.1832 | 31.9095 | 31.6537 | 31.3105 | 30.9674 | 29.7684 | 28.5074 | 4.4558 | 30.4495 | 30.0853 | 29.7137 | 29.3063 | 28.8811 | 28.4263 | 27.98 | 27.5537 | 27.1432 | 26.7779 | 25.4895 | 24.08 | 22.7695 | 30.9705 | 30.7579 | 30.4505 | 30.0558 | 29.6421 | 29.1989 | 28.7663 | 28.3516 | 27.9537 | 27.5905 | 26.3042 | 24.8926 | 23.5811
|  | CAVERSHAM | CF |  |  |  | 33.5263 | 33.4116 | 33.2926 | 33.1684 | 33.0411 | 32.9084 | 32.7737 | 32.64 | 32.5084 | 32.3768 | 31.5063 | 30.6379 | 29.8379 | 30.6653 | 30.4442 | 30.2179 | 29.9789 | 29.7347 | 29.4842 | 29.2326 | 28.98 | 28.7253 | 28.4726 | 27.3084 | 26.34 | 25.4263 | 31.0937 | 30.9726 | 30.8474 | 30.7105 | 30.4747 | 30.2337 | 29.9895 | 29.7463 | 29.5 | 29.2558 | 28.1221 | 27.1526 | 26.24
MANNINGTON GSP | BOURNEMOUTH | CENTRAL | MINIMUM HEADROOM | SZ 10293 91931 | YES | 0.12211 | 37.9716 | 37.6126 | 37.2505 | 36.8663 | 36.4568 | 36.0284 | 35.5937 | 35.2011 | 34.5232 | 33.6474 | 29.5863 | 25.6474 | -10.1168 | 31.1916 | 30.8179 | 29.9589 | 29.2484 | 28.52 | 27.7642 | 26.8747 | 25.9642 | 24.9705 | 23.9989 | 19.4768 | 15.0474 | 10.7568 | 32.1589 | 31.7811 | 31.3811 | 30.9179 | 30.2379 | 29.5316 | 28.6432 | 27.7316 | 26.7389 | 25.7695 | 21.2526 | 16.8284 | 12.5421
|  | CENTRAL | EE |  |  |  | 38.1316 | 37.8632 | 37.5789 | 37.2768 | 36.9505 | 36.6053 | 36.2684 | 35.9379 | 35.6137 | 35.32 | 32.3874 | 29.2947 | 26.3821 | 31.3589 | 31.0789 | 30.6063 | 30.0537 | 29.4768 | 28.8937 | 28.2116 | 27.5326 | 26.8653 | 26.08 | 22.5726 | 19.0842 | 15.7716 | 32.3284 | 32.0463 | 31.7284 | 31.4116 | 31.0705 | 30.5779 | 29.9474 | 29.2989 | 28.6326 | 27.8484 | 24.3442 | 20.8589 | 17.5495
|  | CENTRAL | HT |  |  |  | 37.9716 | 37.6126 | 37.2505 | 36.8663 | 36.4568 | 36.0284 | 35.5937 | 35.2011 | 34.5232 | 33.6474 | 29.5863 | 25.6474 | 21.8568 | 31.1916 | 30.8179 | 29.9589 | 29.2484 | 28.52 | 27.7642 | 26.8747 | 25.9642 | 24.9705 | 23.9989 | 19.4768 | 15.0474 | 10.7568 | 32.1589 | 31.7811 | 31.3811 | 30.9179 | 30.2379 | 29.5316 | 28.6432 | 27.7316 | 26.7389 | 25.7695 | 21.2526 | 16.8284 | 12.5421
|  | CENTRAL | HE |  |  |  | 38.2474 | 38.0263 | 37.7821 | 37.5116 | 37.2211 | 36.9116 | 36.6147 | 36.3358 | 36.0747 | 35.8505 | 34.6147 | 32.3284 | -10.1168 | 31.4842 | 31.2568 | 30.9916 | 30.7147 | 30.3789 | 29.9242 | 29.3747 | 28.8579 | 28.3284 | 27.7011 | 25.04 | 22.44 | 20.0347 | 32.4568 | 32.2284 | 31.9558 | 31.6768 | 31.3779 | 31.06 | 30.7484 | 30.4558 | 30.0168 | 29.4505 | 26.8095 | 24.2126 | 21.8116
|  | CENTRAL | CF |  |  |  | 38.3189 | 38.1663 | 38.0084 | 37.8432 | 37.6737 | 37.4979 | 37.3179 | 37.1411 | 36.9663 | 36.7916 | 36.0126 | 35.6074 | 34.22 | 31.5589 | 31.4011 | 31.2316 | 31.0611 | 30.8874 | 30.7042 | 30.4874 | 30.0726 | 29.7011 | 29.3526 | 27.8684 | 26.1095 | 24.5158 | 32.5326 | 32.3737 | 32.2 | 32.0284 | 31.8526 | 31.6674 | 31.4747 | 31.2842 | 31.0979 | 30.9137 | 29.6168 | 27.8779 | 26.2874
NURSLING GSP | SOUTHAMPTON (2 X 60) | CENTRAL BRIDGE | MINIMUM HEADROOM | SU 42591 11255 | YES | 0.078947 | 45.9011 | 45.8095 | 45.7168 | 45.6116 | 45.4684 | 43.04 | 40.7 | 39.1716 | 38.1653 | 37.0663 | 35.8421 | 34.7926 | -12.3589 | 40.8684 | 40.6432 | 40.3305 | 39.9389 | 39.4758 | 36.6326 | 33.9368 | 32.18 | 31.0284 | 29.7674 | 28.4105 | 27.2442 | 26.1295 | 42.3495 | 42.1105 | 41.8295 | 41.4547 | 40.9789 | 38.0884 | 35.3474 | 33.5621 | 32.3916 | 31.1105 | 29.7358 | 28.5547 | 27.4253
|  | CENTRAL BRIDGE | EE |  |  |  | 45.9484 | 45.8842 | 45.8147 | 45.7421 | 45.6305 | 45.3305 | 44.8811 | 42.4568 | 40.1611 | 38.6305 | 36.5811 | 35.76 | 34.9947 | 40.9368 | 40.7547 | 40.4979 | 40.1579 | 39.76 | 39.2611 | 38.7526 | 35.9421 | 33.2432 | 31.5421 | 29.2116 | 28.2947 | 27.4358 | 42.4211 | 42.2211 | 41.9926 | 41.6684 | 41.2663 | 40.76 | 40.2442 | 37.3989 | 34.7053 | 32.9116 | 30.5453 | 29.6168 | 28.7453
|  | CENTRAL BRIDGE | HT |  |  |  | 45.9011 | 45.8095 | 45.7168 | 45.6116 | 45.4684 | 43.04 | 40.7 | 39.1716 | 38.1653 | 37.0663 | 35.8421 | 34.7926 | 33.7968 | 40.8684 | 40.6432 | 40.3305 | 39.9389 | 39.4758 | 36.6326 | 33.9368 | 32.18 | 31.0284 | 29.7674 | 28.4105 | 27.2442 | 26.1295 | 42.3495 | 42.1105 | 41.8295 | 41.4547 | 40.9789 | 38.0884 | 35.3474 | 33.5621 | 32.3916 | 31.1105 | 29.7358 | 28.5547 | 27.4253
|  | CENTRAL BRIDGE | HE |  |  |  | 45.9695 | 45.9126 | 45.8495 | 45.7789 | 45.6874 | 45.5263 | 47.1042 | 46.7937 | 41.8274 | 40.4874 | 37.56 | 36.6358 | -12.3589 | 40.9863 | 40.8253 | 40.6263 | 40.3116 | 39.9516 | 39.4811 | 39.0653 | 37.1147 | 35.2263 | 33.68 | 30.32 | 29.2695 | 28.6537 | 42.4747 | 42.2979 | 42.1116 | 41.8158 | 41.4611 | 40.9832 | 42.5158 | 38.7358 | 36.6568 | 35.0853 | 31.6695 | 30.6032 | 29.9779
|  | CENTRAL BRIDGE | CF |  |  |  | 45.9821 | 45.94 | 45.8958 | 45.8495 | 45.8021 | 45.7537 | 45.7032 | 45.6474 | 44.9674 | 43.7253 | 41.4337 | 42.6716 | 42.3116 | 41.2242 | 41.1611 | 41.0495 | 40.9284 | 40.7895 | 40.6168 | 40.3242 | 39.9832 | 38.8347 | 37.4021 | 34.7453 | 36.9453 | 36.5326 | 42.7074 | 42.6632 | 42.5579 | 42.4263 | 42.2737 | 42.0832 | 41.8221 | 41.4989 | 40.3263 | 38.8695 | 36.2042 | 38.7926 | 38.3811
CHICKERELL GSP | CHICKERELL BSP | CERNE ABBAS | MINIMUM HEADROOM | ST 66140 01039 | YES | 0 | 4.4432 | 4.4084 | 4.3747 | 4.34 | 4.3063 | 4.2716 | 4.2379 | 4.2074 | 4.1789 | 4.1516 | 4.0305 | 3.9295 | 1.8084 | 3.9632 | 3.9295 | 3.8968 | 3.8632 | 3.8305 | 3.7958 | 3.7632 | 3.7326 | 3.7053 | 3.6789 | 3.5653 | 3.4705 | 3.3884 | 3.9789 | 3.9568 | 3.9347 | 3.9116 | 3.8884 | 3.8632 | 3.8389 | 3.8168 | 3.7979 | 3.7789 | 3.7042 | 3.5958 | 3.5
|  | CERNE ABBAS | EE |  |  |  | 4.4579 | 4.4305 | 4.4032 | 4.3758 | 4.3474 | 4.32 | 4.2926 | 4.2674 | 4.2421 | 4.22 | 4.1274 | 4.0526 | 3.9905 | 3.9779 | 3.9516 | 3.9253 | 3.8979 | 3.8705 | 3.8432 | 3.8158 | 3.7916 | 3.7663 | 3.7442 | 3.6558 | 3.5853 | 3.5284 | 3.9874 | 3.9705 | 3.9516 | 3.9316 | 3.9126 | 3.8926 | 3.8716 | 3.8537 | 3.8358 | 3.8189 | 3.7589 | 3.7179 | 3.6621
|  | CERNE ABBAS | HT |  |  |  | 4.4432 | 4.4084 | 4.3747 | 4.34 | 4.3063 | 4.2716 | 4.2379 | 4.2074 | 4.1789 | 4.1516 | 4.0305 | 3.9295 | 3.8411 | 3.9632 | 3.9295 | 3.8968 | 3.8632 | 3.8305 | 3.7958 | 3.7632 | 3.7326 | 3.7053 | 3.6789 | 3.5653 | 3.4705 | 3.3884 | 3.9789 | 3.9568 | 3.9347 | 3.9116 | 3.8884 | 3.8632 | 3.8389 | 3.8168 | 3.7979 | 3.7789 | 3.7042 | 3.5958 | 3.5
|  | CERNE ABBAS | HE |  |  |  | 4.4789 | 4.4611 | 4.4442 | 4.4263 | 4.4063 | 4.3853 | 4.3674 | 4.3484 | 4.3326 | 4.3168 | 4.2621 | 4.2242 | 1.8084 | 3.9979 | 3.9821 | 3.9642 | 3.9463 | 3.9274 | 3.9063 | 3.8895 | 3.8705 | 3.8547 | 3.8389 | 3.7863 | 3.7484 | 3.7211 | 4 | 3.9884 | 3.9758 | 3.9621 | 3.9463 | 3.9305 | 3.9168 | 3.9021 | 3.8895 | 3.8779 | 3.8389 | 3.8147 | 3.8
|  | CERNE ABBAS | CF |  |  |  | 4.4895 | 4.4789 | 4.4684 | 4.4568 | 4.4463 | 4.4347 | 4.4232 | 4.4116 | 4.4011 | 4.3905 | 4.34 | 4.3074 | 4.2832 | 4.0084 | 3.9979 | 3.9874 | 3.9768 | 3.9663 | 3.9547 | 3.9442 | 3.9326 | 3.9232 | 3.9116 | 3.8621 | 3.8316 | 3.8074 | 4.0074 | 4 | 3.9926 | 3.9863 | 3.9789 | 3.9705 | 3.9632 | 3.9558 | 3.9484 | 3.9411 | 3.9063 | 3.8895 | 3.8779
LOVEDEAN GSP | CHICHESTER & HUNSTON | CHALCRAFT LANE | MINIMUM HEADROOM | TBC | YES | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 40 | 40 | 40 | 40 | 40 | 40
|  | CHALCRAFT LANE | EE |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 40 | 40 | 40 | 40 | 40 | 40
|  | CHALCRAFT LANE | HT |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 40 | 40 | 40 | 40 | 40 | 40
|  | CHALCRAFT LANE | HE |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 40 | 40 | 40 | 40 | 40 | 40
|  | CHALCRAFT LANE | CF |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 40 | 40 | 40 | 40 | 40 | 40
IVER 132KV | CHALVEY BSP | CHALVEY | MINIMUM HEADROOM | SU 96669 79364 | YES | 0.14737 | 91.9137 | 91.2253 | 90.4789 | 89.7116 | 88.9021 | 87.7337 | 85.5705 | 83.9811 | 82.4747 | 81.0579 | 74.9768 | 69.6789 | 6.3674 | 81.7842 | 79.5232 | 77.1084 | 74.8968 | 72.4768 | 69.58 | 67.1579 | 65.3979 | 63.7253 | 62.1516 | 55.38 | 49.44 | 43.9168 | 83.8989 | 82.6916 | 80.2684 | 78.0568 | 75.6358 | 72.7389 | 70.3158 | 68.5547 | 66.8821 | 65.3084 | 58.5358 | 52.5937 | 47.0695
|  | CHALVEY | EE |  |  |  | 92.1421 | 91.6137 | 90.9821 | 90.3358 | 89.6442 | 88.8958 | 87.3726 | 86.0011 | 84.6811 | 83.4621 | 78.5537 | 74.4221 | 70.6747 | 82.1737 | 80.3158 | 78.1474 | 76.1779 | 73.9842 | 71.3011 | 69.1168 | 67.5989 | 66.1389 | 64.7874 | 59.3221 | 54.6737 | 50.4221 | 84.1463 | 83.4758 | 81.3074 | 79.3379 | 77.1442 | 74.46 | 72.2747 | 70.7568 | 69.2958 | 67.9442 | 62.4789 | 57.8284 | 53.5758
|  | CHALVEY | HT |  |  |  | 91.9137 | 91.2253 | 90.4789 | 89.7116 | 88.9021 | 87.7337 | 85.5705 | 83.9811 | 82.4747 | 81.0579 | 74.9768 | 69.6789 | 64.7863 | 81.7842 | 79.5232 | 77.1084 | 74.8968 | 72.4768 | 69.58 | 67.1579 | 65.3979 | 63.7253 | 62.1516 | 55.38 | 49.44 | 43.9168 | 83.8989 | 82.6916 | 80.2684 | 78.0568 | 75.6358 | 72.7389 | 70.3158 | 68.5547 | 66.8821 | 65.3084 | 58.5358 | 52.5937 | 47.0695
|  | CHALVEY | HE |  |  |  | 92.4284 | 92.0747 | 91.5779 | 91.0568 | 90.4905 | 89.8579 | 89.28 | 88.4453 | 87.4116 | 86.4726 | 82.8705 | 79.9537 | 6.3674 | 82.6747 | 81.3168 | 79.4663 | 77.7853 | 75.8811 | 73.46 | 71.5358 | 70.2853 | 69.1421 | 68.0989 | 64.0716 | 60.7642 | 57.8337 | 84.4579 | 84.0158 | 82.6263 | 80.9463 | 79.0411 | 76.6189 | 74.6947 | 73.4442 | 72.3 | 71.2579 | 67.2284 | 63.9211 | 60.9895
|  | CHALVEY | CF |  |  |  | 92.6 | 92.3832 | 92.1579 | 91.9242 | 91.6821 | 91.3768 | 91.0221 | 90.6189 | 90.3379 | 90.0526 | 88.8126 | 87.2411 | 85.5116 | 83.1074 | 82.8632 | 82.4853 | 81.9589 | 81.2021 | 79.8874 | 78.2137 | 75.7937 | 75.0779 | 74.2895 | 71.2874 | 68.9726 | 66.9884 | 84.6853 | 84.4547 | 84.1968 | 83.9284 | 83.6421 | 83.0516 | 81.3737 | 78.9537 | 78.2379 | 77.4495 | 74.4463 | 72.1305 | 70.1453
NURSLING GSP | VELMORE BSP | CHANDLERS FORD | MINIMUM HEADROOM | SU 43494 21552 | YES | 0.25474 | 33.5326 | 33.1168 | 32.6989 | 32.2168 | 31.4305 | 30.5042 | 29.3442 | 28.2326 | 27.2926 | 26.2863 | 22.3579 | 18.8432 | -15.2053 | 29.4747 | 28.72 | 27.84 | 26.7842 | 25.8958 | 24.8937 | 23.6084 | 22.3758 | 21.3379 | 20.2158 | 15.8611 | 11.9137 | 8.3137 | 30.2779 | 29.5032 | 28.6432 | 27.5779 | 26.6768 | 25.6568 | 24.3611 | 23.1274 | 22.0895 | 20.9674 | 16.62 | 12.6716 | 9.0705
|  | CHANDLERS FORD | EE |  |  |  | 33.6968 | 33.3768 | 33.0358 | 32.6684 | 32.2674 | 31.6411 | 30.6821 | 29.76 | 28.9621 | 28.0916 | 24.9674 | 22.2253 | 19.7716 | 29.8105 | 29.2326 | 28.54 | 27.6505 | 26.9211 | 26.1232 | 25.0653 | 24.04 | 23.1621 | 22.1916 | 18.7295 | 15.6358 | 12.8474 | 30.6242 | 30.0316 | 29.3274 | 28.4589 | 27.7179 | 26.9074 | 25.8274 | 24.7926 | 23.9147 | 22.9442 | 19.4895 | 16.3937 | 13.6053
|  | CHANDLERS FORD | HT |  |  |  | 33.5326 | 33.1168 | 32.6989 | 32.2168 | 31.4305 | 30.5042 | 29.3442 | 28.2326 | 27.2926 | 26.2863 | 22.3579 | 18.8432 | 15.6579 | 29.4747 | 28.72 | 27.84 | 26.7842 | 25.8958 | 24.8937 | 23.6084 | 22.3758 | 21.3379 | 20.2158 | 15.8611 | 11.9137 | 8.3137 | 30.2779 | 29.5032 | 28.6432 | 27.5779 | 26.6768 | 25.6568 | 24.3611 | 23.1274 | 22.0895 | 20.9674 | 16.62 | 12.6716 | 9.0705
|  | CHANDLERS FORD | HE |  |  |  | 33.92 | 33.7074 | 33.4705 | 33.2084 | 32.9263 | 32.6242 | 32.2516 | 31.4937 | 30.8663 | 30.1716 | 27.7179 | 25.6758 | -15.2053 | 30.2632 | 29.9032 | 29.4295 | 28.7874 | 28.2568 | 27.6432 | 26.7642 | 25.9253 | 25.2337 | 24.4516 | 21.6821 | 19.3568 | 17.2968 | 30.8979 | 30.6758 | 30.2347 | 29.5716 | 29.0526 | 28.4516 | 27.5547 | 26.6979 | 25.9937 | 25.2032 | 22.4253 | 20.1 | 18.0389
|  | CHANDLERS FORD | CF |  |  |  | 34.0484 | 33.9295 | 33.8063 | 33.6789 | 33.5474 | 33.4095 | 33.2695 | 33.1316 | 32.9821 | 32.8274 | 31.1979 | 29.8389 | 28.6663 | 30.5221 | 30.3021 | 30.0337 | 29.6989 | 29.4242 | 29.1116 | 28.6632 | 28.2158 | 27.8589 | 27.46 | 25.5474 | 23.9989 | 22.6516 | 31.0347 | 30.9095 | 30.7768 | 30.5084 | 30.2232 | 29.9011 | 29.4558 | 29.0211 | 28.6632 | 28.2568 | 26.3032 | 24.7516 | 23.4032
NURSLING GSP | SOUTHAMPTON (2 X 60) | CHAPEL | MINIMUM HEADROOM | SU 42849 11983 | YES | 0.27053 | 27.2211 | 27.1558 | 27.0895 | 27.0189 | 26.9432 | 26.1884 | 25.0968 | 24.6411 | 24.2221 | 24.1126 | 22.9832 | 22.0474 | 3.9032 | 24.4379 | 24.3547 | 24.2284 | 24.0453 | 23.8558 | 22.2705 | 20.9979 | 20.4737 | 19.9905 | 19.8926 | 18.6084 | 17.5432 | 16.5442 | 24.9 | 24.8347 | 24.7684 | 24.6979 | 24.6221 | 23.0832 | 21.8095 | 21.2853 | 20.8021 | 20.7147 | 19.4305 | 18.3642 | 17.3653
|  | CHAPEL | EE |  |  |  | 27.2516 | 27.2032 | 27.1516 | 27.0968 | 27.0368 | 26.9737 | 26.9126 | 26.0516 | 24.9916 | 24.5705 | 23.5663 | 22.8147 | 22.1137 | 24.4684 | 24.42 | 24.3484 | 24.2095 | 24.0695 | 23.8737 | 23.6684 | 22.1126 | 20.8726 | 20.3863 | 19.2568 | 18.3979 | 17.5937 | 24.9305 | 24.8821 | 24.8305 | 24.7758 | 24.7158 | 24.6526 | 24.4811 | 22.9242 | 21.6842 | 21.1968 | 20.0789 | 19.22 | 18.4147
|  | CHAPEL | HT |  |  |  | 27.2211 | 27.1558 | 27.0895 | 27.0189 | 26.9432 | 26.1884 | 25.0968 | 24.6411 | 24.2221 | 24.1126 | 22.9832 | 22.0474 | 21.1737 | 24.4379 | 24.3547 | 24.2284 | 24.0453 | 23.8558 | 22.2705 | 20.9979 | 20.4737 | 19.9905 | 19.8926 | 18.6084 | 17.5432 | 16.5442 | 24.9 | 24.8347 | 24.7684 | 24.6979 | 24.6221 | 23.0832 | 21.8095 | 21.2853 | 20.8021 | 20.7147 | 19.4305 | 18.3642 | 17.3653
|  | CHAPEL | HE |  |  |  | 27.2705 | 27.2295 | 27.1842 | 27.1347 | 27.08 | 27.0232 | 26.9674 | 26.6368 | 25.7074 | 25.1347 | 23.9989 | 23.4358 | 3.9032 | 24.4874 | 24.4463 | 24.4011 | 24.3453 | 24.2263 | 24.0537 | 23.8716 | 22.7916 | 21.7032 | 21.0347 | 19.7032 | 19.0558 | 18.4221 | 24.9495 | 24.9084 | 24.8632 | 24.8137 | 24.7589 | 24.7021 | 24.6463 | 23.6032 | 22.5147 | 21.8463 | 20.5032 | 19.8568 | 19.2221
|  | CHAPEL | CF |  |  |  | 27.2842 | 27.2547 | 27.2253 | 27.1947 | 27.1632 | 27.1295 | 27.0968 | 27.0632 | 27.0305 | 26.8189 | 25.8284 | 25.4863 | 25.1432 | 24.5011 | 24.4716 | 24.4421 | 24.4116 | 24.38 | 24.3463 | 24.3032 | 24.2389 | 23.6442 | 22.9979 | 21.8495 | 21.4579 | 21.0621 | 24.9632 | 24.9337 | 24.9042 | 24.8737 | 24.8421 | 24.8084 | 24.7758 | 24.7421 | 24.4568 | 23.8105 | 22.6611 | 22.2705 | 21.8737
COWLEY GSP | YARNTON BSP | CHARLBURY | MINIMUM HEADROOM | SP 36034 18376 | YES | 0 | 16.7421 | 16.5874 | 16.3558 | 16.0674 | 15.7905 | 15.3874 | 15.0989 | 14.8358 | 14.5905 | 14.3589 | 13.26 | 12.0074 | 4.0874 | 15.58 | 15.2768 | 14.9821 | 14.6684 | 14.3684 | 13.92 | 13.6137 | 13.3326 | 13.0695 | 12.8211 | 11.6337 | 10.2411 | 8.7842 | 15.9674 | 15.6758 | 15.3874 | 15.0768 | 14.7789 | 14.3347 | 14.0284 | 13.7484 | 13.4853 | 13.2358 | 12.0389 | 10.6389 | 9.18
|  | CHARLBURY | EE |  |  |  | 16.8011 | 16.6789 | 16.5495 | 16.3589 | 16.1337 | 15.78 | 15.5526 | 15.3305 | 15.1147 | 14.9084 | 14.0684 | 13.1158 | 12.1284 | 15.7137 | 15.4789 | 15.2421 | 14.9895 | 14.7474 | 14.3526 | 14.1105 | 13.8726 | 13.6432 | 13.4232 | 12.5284 | 11.4779 | 10.3537 | 16.0958 | 15.8684 | 15.6411 | 15.3947 | 15.1537 | 14.7611 | 14.52 | 14.2821 | 14.0526 | 13.8326 | 12.9263 | 11.8621 | 10.7347
|  | CHARLBURY | HT |  |  |  | 16.7421 | 16.5874 | 16.3558 | 16.0674 | 15.7905 | 15.3874 | 15.0989 | 14.8358 | 14.5905 | 14.3589 | 13.26 | 12.0074 | 10.7242 | 15.58 | 15.2768 | 14.9821 | 14.6684 | 14.3684 | 13.92 | 13.6137 | 13.3326 | 13.0695 | 12.8211 | 11.6337 | 10.2411 | 8.7842 | 15.9674 | 15.6758 | 15.3874 | 15.0768 | 14.7789 | 14.3347 | 14.0284 | 13.7484 | 13.4853 | 13.2358 | 12.0389 | 10.6389 | 9.18
|  | CHARLBURY | HE |  |  |  | 16.8853 | 16.8042 | 16.7147 | 16.6158 | 16.5095 | 16.3168 | 16.1547 | 15.9979 | 15.8495 | 15.7147 | 15.1958 | 14.5516 | 4.0874 | 15.8979 | 15.7516 | 15.6 | 15.4326 | 15.2684 | 14.9432 | 14.7726 | 14.6053 | 14.4463 | 14.3042 | 13.7442 | 13.0158 | 12.1684 | 16.2716 | 16.1305 | 15.9842 | 15.8221 | 15.6611 | 15.3484 | 15.1779 | 15.0116 | 14.8516 | 14.7095 | 14.1495 | 13.4221 | 12.5737
|  | CHARLBURY | CF |  |  |  | 16.9337 | 16.8895 | 16.8432 | 16.7947 | 16.7453 | 16.6916 | 16.6389 | 16.5853 | 16.5095 | 16.4168 | 15.9884 | 15.6053 | 15.1274 | 15.9905 | 15.9032 | 15.8126 | 15.7147 | 15.6116 | 15.4505 | 15.3389 | 15.2421 | 15.1484 | 15.0474 | 14.58 | 14.1453 | 13.5947 | 16.3516 | 16.2768 | 16.1905 | 16.0958 | 15.9968 | 15.8432 | 15.7368 | 15.6432 | 15.5505 | 15.4505 | 14.9863 | 14.5537 | 14.0074
CHICKERELL GSP | CHICKERELL BSP | CHARMINSTER | MINIMUM HEADROOM | SY 67309 93186 | YES | 0 | 18.0916 | 17.8558 | 17.1737 | 16.6874 | 16.1926 | 15.8463 | 15.5032 | 14.6874 | 13.1726 | 11.6705 | 5.3737 | -1.1326 | -11.8295 | 14.7937 | 14.2063 | 13.4432 | 12.9105 | 12.3663 | 12.0042 | 11.6432 | 10.7253 | 8.9789 | 7.2484 | 0.010526 | -7.4895 | -14.9789 | 15.1032 | 14.9242 | 14.2158 | 13.6789 | 13.1326 | 12.7642 | 12.4 | 11.4779 | 9.7305 | 7.9979 | 0.73789 | -6.7905 | -14.2779
|  | CHARMINSTER | EE |  |  |  | 18.1579 | 18.0168 | 17.4495 | 17.0263 | 16.5916 | 16.3032 | 16.0158 | 15.2432 | 13.7537 | 12.2811 | 6.1705 | -0.052632 | -6.1589 | 14.9453 | 14.4347 | 13.7432 | 13.2758 | 12.7989 | 12.4989 | 12.2021 | 11.3316 | 9.6189 | 7.9242 | 0.91263 | -6.2432 | -13.3589 | 15.1695 | 15.0284 | 14.5168 | 14.0474 | 13.5653 | 13.26 | 12.9568 | 12.08 | 10.3632 | 8.6642 | 1.6126 | -5.5916 | -12.7084
|  | CHARMINSTER | HT |  |  |  | 18.0916 | 17.8558 | 17.1737 | 16.6874 | 16.1926 | 15.8463 | 15.5032 | 14.6874 | 13.1726 | 11.6705 | 5.3737 | -1.1326 | -7.5737 | 14.7937 | 14.2063 | 13.4432 | 12.9105 | 12.3663 | 12.0042 | 11.6432 | 10.7253 | 8.9789 | 7.2484 | 0.010526 | -7.4895 | -14.9789 | 15.1032 | 14.9242 | 14.2158 | 13.6789 | 13.1326 | 12.7642 | 12.4 | 11.4779 | 9.7305 | 7.9979 | 0.73789 | -6.7905 | -14.2779
|  | CHARMINSTER | HE |  |  |  | 18.2526 | 18.1558 | 17.8221 | 17.4842 | 17.1295 | 16.9189 | 16.7189 | 16.0316 | 14.6347 | 13.2547 | 7.6232 | 1.9168 | -11.8295 | 15.1547 | 14.7432 | 14.1442 | 13.7705 | 13.38 | 13.1642 | 12.9568 | 12.18 | 10.5611 | 8.9589 | 2.4263 | -4.2295 | -10.9947 | 15.2642 | 15.1674 | 14.9221 | 14.5453 | 14.1516 | 13.9305 | 13.72 | 12.9358 | 11.3179 | 9.7168 | 3.1768 | -3.4779 | -10.2411
|  | CHARMINSTER | CF |  |  |  | 18.3053 | 18.2505 | 18.1926 | 18.1326 | 18.0305 | 17.9126 | 17.7937 | 17.4337 | 16.6674 | 15.8495 | 12.2053 | 8.5968 | 4.9621 | 15.3063 | 15.0747 | 14.7705 | 14.5768 | 14.3821 | 14.2589 | 14.1347 | 13.7295 | 12.8526 | 11.9021 | 7.6737 | 3.4663 | -0.78211 | 15.3168 | 15.2621 | 15.2042 | 15.1442 | 15.0821 | 15.0126 | 14.9105 | 14.4989 | 13.6116 | 12.6621 | 8.4379 | 4.2316 | -0.015789
LOVEDEAN GSP | CHICHESTER & HUNSTON | CHICHESTER | MINIMUM HEADROOM | SU 92198 07420 | YES | 6.7547 | 20.2684 | 19.9053 | 19.24 | 33.2853 | 32.2147 | 30.9389 | 29.6937 | 28.4337 | 27.1558 | 26.0126 | 21.1042 | 16.6579 | -7.5611 | 18.7368 | 18.3737 | 17.6547 | 31.5821 | 30.3926 | 28.9663 | 27.5747 | 26.1579 | 24.7158 | 23.4263 | 18.1916 | 13.1463 | 1.7674 | 19.2158 | 18.8526 | 18.1347 | 32.0653 | 30.8779 | 29.4526 | 28.0632 | 26.6474 | 25.2063 | 23.9179 | 18.4926 | 13.4389 | 2.0621
|  | CHICHESTER | EE |  |  |  | 20.4042 | 20.1189 | 19.8074 | 34.0021 | 33.0695 | 31.9305 | 30.8295 | 29.6621 | 28.4916 | 27.4653 | 23.3821 | 20.12 | 10.2305 | 18.8726 | 18.5874 | 18.2737 | 32.3653 | 31.3263 | 30.0484 | 28.8147 | 27.4989 | 26.1789 | 25.0221 | 20.4147 | 17.0347 | 6.6084 | 19.3516 | 19.0663 | 18.7537 | 32.8463 | 31.8095 | 30.5326 | 29.2989 | 27.9853 | 26.6653 | 25.5084 | 20.8947 | 17.3084 | 6.8832
|  | CHICHESTER | HT |  |  |  | 20.2684 | 19.9053 | 19.24 | 33.2853 | 32.2147 | 30.9389 | 29.6937 | 28.4337 | 27.1558 | 26.0126 | 21.1042 | 16.6579 | 5.9232 | 18.7368 | 18.3737 | 17.6547 | 31.5821 | 30.3926 | 28.9663 | 27.5747 | 26.1579 | 24.7158 | 23.4263 | 18.1916 | 13.1463 | 1.7674 | 19.2158 | 18.8526 | 18.1347 | 32.0653 | 30.8779 | 29.4526 | 28.0632 | 26.6474 | 25.2063 | 23.9179 | 18.4926 | 13.4389 | 2.0621
|  | CHICHESTER | HE |  |  |  | 22.7779 | 20.4084 | 20.1958 | 34.9421 | 34.1747 | 33.1905 | 32.2421 | 31.2242 | 30.2126 | 29.3358 | 34.2105 | 23.1695 | -7.5611 | 21.6337 | 18.8768 | 18.6642 | 33.3884 | 32.5305 | 31.42 | 30.3516 | 29.1958 | 28.0463 | 27.0516 | 23.5589 | 20.4253 | 10.72 | 22.1053 | 19.3558 | 19.1432 | 33.8684 | 33.0116 | 31.9032 | 30.8347 | 29.6821 | 28.5347 | 27.5389 | 24.0737 | 20.4874 | 10.7211
|  | CHICHESTER | CF |  |  |  | 23.0474 | 20.6084 | 20.4979 | 35.4832 | 35.3642 | 35.24 | 35.1126 | 34.9758 | 34.3526 | 33.7253 | 31.54 | 30.1768 | 22.0726 | 21.9316 | 19.0768 | 18.9663 | 33.9516 | 33.8326 | 33.7095 | 33.5821 | 33.4442 | 32.7316 | 32.0158 | 29.5421 | 27.9895 | 19.6011 | 22.3979 | 19.5558 | 19.4453 | 34.4305 | 34.3116 | 34.1874 | 34.06 | 33.9211 | 33.2105 | 32.4958 | 30.0263 | 28.4737 | 20.0863
CHICKERELL GSP | CHICKERELL BSP | CHICKERELL | MINIMUM HEADROOM | SY 65479 80511 | YES | 0.87789 | 28.48 | 28.16 | 27.7095 | 27.2505 | 26.6442 | 25.8589 | 25.0726 | 24.3095 | 23.6568 | 22.9147 | 20.4779 | 19.3453 | 12.9211 | 28.1874 | 27.84 | 27.3337 | 26.8179 | 26.1284 | 25.2368 | 24.3453 | 23.4779 | 22.74 | 21.8968 | 19.1811 | 17.9979 | 16.9042 | 28.2242 | 27.8863 | 27.4021 | 26.8958 | 26.2221 | 25.3453 | 24.4526 | 23.58 | 22.8358 | 21.9853 | 19.2242 | 17.9821 | 16.8663
|  | CHICKERELL | EE |  |  |  | 28.5853 | 28.32 | 27.9158 | 27.5053 | 26.9432 | 26.2011 | 25.4579 | 24.7189 | 24.0832 | 23.3621 | 21.0326 | 20.06 | 19.28 | 28.2958 | 28.0147 | 27.56 | 27.0968 | 26.4568 | 25.6116 | 24.7684 | 23.9326 | 23.2168 | 22.3989 | 19.8274 | 18.8516 | 18.0053 | 28.3337 | 28.0547 | 27.6232 | 27.1695 | 26.5432 | 25.7116 | 24.8705 | 24.0263 | 23.3032 | 22.4747 | 19.8347 | 18.7789 | 17.9063
|  | CHICKERELL | HT |  |  |  | 28.48 | 28.16 | 27.7095 | 27.2505 | 26.6442 | 25.8589 | 25.0726 | 24.3095 | 23.6568 | 22.9147 | 20.4779 | 19.3453 | 18.3463 | 28.1874 | 27.84 | 27.3337 | 26.8179 | 26.1284 | 25.2368 | 24.3453 | 23.4779 | 22.74 | 21.8968 | 19.1811 | 17.9979 | 16.9042 | 28.2242 | 27.8863 | 27.4021 | 26.8958 | 26.2221 | 25.3453 | 24.4526 | 23.58 | 22.8358 | 21.9853 | 19.2242 | 17.9821 | 16.8663
|  | CHICKERELL | HE |  |  |  | 28.7347 | 28.5411 | 28.2074 | 27.8632 | 27.3632 | 26.6832 | 26.0105 | 25.3453 | 24.7853 | 24.14 | 22.2284 | 21.7147 | 12.9211 | 28.4463 | 28.2484 | 27.8758 | 27.4842 | 26.9116 | 26.1337 | 25.3621 | 24.5989 | 23.96 | 23.2179 | 21.0484 | 20.5042 | 19.9242 | 28.4905 | 28.2853 | 27.9284 | 27.5537 | 26.9937 | 26.2295 | 25.4726 | 24.7063 | 24.0642 | 23.3189 | 21.1242 | 20.5579 | 19.9568
|  | CHICKERELL | CF |  |  |  | 28.7937 | 28.7 | 28.5295 | 28.3611 | 28.1358 | 27.8411 | 27.5232 | 27.18 | 26.8695 | 26.4842 | 25.22 | 24.86 | 24.5105 | 28.5053 | 28.4105 | 28.2358 | 28.0453 | 27.7863 | 27.4505 | 27.0863 | 26.6926 | 26.3368 | 25.8937 | 24.4505 | 24.0642 | 23.6821 | 28.5505 | 28.4526 | 28.2695 | 28.0895 | 27.8474 | 27.5211 | 27.1621 | 26.7768 | 26.4274 | 25.9926 | 24.5505 | 24.1537 | 23.7589
AXMINSTER | YEOVIL BSP | CHILTON CANTELO | MINIMUM HEADROOM | ST 57910 21616 | YES | 7.5789 | 15.8116 | 15.3147 | 14.7126 | 13.9979 | 13.0737 | 11.9579 | 10.9663 | 10.2621 | 9.5684 | 8.8968 | 7.8147 | 6.9074 | -11.7537 | 14.5958 | 14.0379 | 13.3516 | 12.5347 | 11.4726 | 10.1979 | 9.0684 | 8.2726 | 7.4895 | 6.7274 | 5.5958 | 4.6663 | -3.7779 | 14.6821 | 14.1832 | 13.5474 | 12.7274 | 11.6611 | 10.3758 | 9.2358 | 8.4295 | 7.6368 | 6.8674 | 5.6884 | 4.7074 | -3.7589
|  | CHILTON CANTELO | EE |  |  |  | 15.8905 | 15.4368 | 14.8705 | 14.1905 | 13.2979 | 12.2147 | 11.2516 | 10.5674 | 9.8832 | 9.2232 | 8.2442 | 7.4295 | -0.77053 | 14.6821 | 14.1695 | 13.5642 | 12.7811 | 11.7495 | 10.5011 | 9.3979 | 8.6232 | 7.8495 | 7.1032 | 6.12 | 5.3074 | -2.9368 | 14.7611 | 14.3053 | 13.7189 | 12.9368 | 11.9063 | 10.6537 | 9.5453 | 8.7621 | 7.98 | 7.2253 | 6.1705 | 5.2989 | -2.9695
|  | CHILTON CANTELO | HT |  |  |  | 15.8116 | 15.3147 | 14.7126 | 13.9979 | 13.0737 | 11.9579 | 10.9663 | 10.2621 | 9.5684 | 8.8968 | 7.8147 | 6.9074 | -1.4705 | 14.5958 | 14.0379 | 13.3516 | 12.5347 | 11.4726 | 10.1979 | 9.0684 | 8.2726 | 7.4895 | 6.7274 | 5.5958 | 4.6663 | -3.7779 | 14.6821 | 14.1832 | 13.5474 | 12.7274 | 11.6611 | 10.3758 | 9.2358 | 8.4295 | 7.6368 | 6.8674 | 5.6884 | 4.7074 | -3.7589
|  | CHILTON CANTELO | HE |  |  |  | 16.0011 | 15.6021 | 15.0874 | 14.4579 | 13.6137 | 12.5789 | 11.6726 | 11.0484 | 10.4232 | 9.8284 | 9.2032 | 8.7937 | -11.7537 | 14.8011 | 14.3484 | 13.7579 | 13.0326 | 12.0579 | 10.8684 | 9.8274 | 9.1158 | 8.4053 | 7.7253 | 7.0695 | 6.6442 | -1.3989 | 14.8726 | 14.4705 | 13.9537 | 13.2274 | 12.2484 | 11.0505 | 10.0011 | 9.2821 | 8.5632 | 7.8768 | 7.1937 | 6.7474 | -1.3147
|  | CHILTON CANTELO | CF |  |  |  | 16.2158 | 16.0737 | 15.8726 | 15.6474 | 15.3053 | 14.8484 | 14.3537 | 13.9242 | 13.4821 | 13.0211 | 12.3905 | 12.1137 | 4.2442 | 15.0432 | 14.8842 | 14.6568 | 14.4011 | 14.0095 | 13.4853 | 12.9147 | 12.4221 | 11.9158 | 11.3842 | 10.6884 | 10.4021 | 2.5137 | 15.0874 | 14.9453 | 14.7432 | 14.5158 | 14.1726 | 13.68 | 13.1053 | 12.6084 | 12.0979 | 11.5621 | 10.8537 | 10.5526 | 2.6474
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | CHINEHAM | MINIMUM HEADROOM | SU 65105 55805 | YES | 0.25158 | 33.5474 | 33.3526 | 33.1558 | 32.9474 | 32.6674 | 31.66 | 29.5547 | 27.4811 | 25.4326 | 23.9042 | 21.5832 | 20.3 | 0.45368 | 30.3095 | 30.0189 | 29.3758 | 28.5979 | 27.4768 | 26.3316 | 23.8937 | 21.4884 | 19.1084 | 17.34 | 14.7274 | 13.3042 | 11.6968 | 30.8737 | 30.6653 | 30.1189 | 29.3189 | 28.1842 | 27.04 | 24.6063 | 22.2053 | 19.8305 | 18.0642 | 15.4547 | 14.0347 | 12.4284
|  | CHINEHAM | EE |  |  |  | 33.6168 | 33.4611 | 33.2979 | 33.1232 | 32.9411 | 32.1495 | 31.3642 | 29.7463 | 27.7011 | 26.1211 | 22.5421 | 21.6768 | 20.5874 | 30.4095 | 30.1937 | 29.6768 | 28.9884 | 27.9442 | 26.8632 | 25.9716 | 24.0989 | 21.7221 | 19.8884 | 15.7716 | 14.8179 | 13.5832 | 30.9484 | 30.7811 | 30.4432 | 29.7158 | 28.6505 | 27.5716 | 26.6811 | 24.8116 | 22.4389 | 20.6084 | 16.4989 | 15.5463 | 14.3126
|  | CHINEHAM | HT |  |  |  | 33.5474 | 33.3526 | 33.1558 | 32.9474 | 32.6674 | 31.66 | 29.5547 | 27.4811 | 25.4326 | 23.9042 | 21.5832 | 20.3 | 18.8737 | 30.3095 | 30.0189 | 29.3758 | 28.5979 | 27.4768 | 26.3316 | 23.8937 | 21.4884 | 19.1084 | 17.34 | 14.7274 | 13.3042 | 11.6968 | 30.8737 | 30.6653 | 30.1189 | 29.3189 | 28.1842 | 27.04 | 24.6063 | 22.2053 | 19.8305 | 18.0642 | 15.4547 | 14.0347 | 12.4284
|  | CHINEHAM | HE |  |  |  | 33.72 | 33.6147 | 33.4968 | 33.3674 | 33.2284 | 32.82 | 32.1147 | 30.9379 | 29.5937 | 28.7663 | 25.7789 | 23.6621 | 0.45368 | 30.5516 | 30.4063 | 30.0905 | 29.5253 | 28.5811 | 27.5958 | 26.7895 | 25.4295 | 23.8695 | 22.9158 | 19.4642 | 17.0105 | 16.1284 | 31.0589 | 30.9463 | 30.8042 | 30.2621 | 29.2926 | 28.3032 | 27.4989 | 26.1411 | 24.5832 | 23.6305 | 20.1853 | 17.7368 | 16.8558
|  | CHINEHAM | CF |  |  |  | 33.7779 | 33.7168 | 33.6526 | 33.5863 | 33.5189 | 33.4474 | 33.3758 | 33.3042 | 33.1947 | 32.8789 | 30.8221 | 28.9358 | 27.9905 | 30.6263 | 30.5442 | 30.4505 | 30.3474 | 30.2053 | 29.6958 | 29.1221 | 28.5853 | 28.0084 | 27.6505 | 25.2842 | 23.0937 | 21.9958 | 31.12 | 31.0547 | 30.9853 | 30.9126 | 30.8326 | 30.4432 | 29.8453 | 29.2937 | 28.7158 | 28.3579 | 25.9958 | 23.8084 | 22.7137
COWLEY GSP | YARNTON BSP | CHIPPING NORTON | MINIMUM HEADROOM | SP 31382 26792 | YES | 0.41789 | 19.2274 | 19.0747 | 18.92 | 18.7558 | 18.5368 | 17.9442 | 17.1242 | 16.0105 | 14.9074 | 13.7621 | 11.5074 | 10.2832 | -5.7716 | 15.5463 | 15.1958 | 14.7863 | 14.3295 | 13.8832 | 13.1716 | 12.1674 | 10.7779 | 9.4695 | 8.1126 | 5.4989 | 4.1021 | 2.6189 | 16.1832 | 15.9632 | 15.5537 | 15.0979 | 14.6516 | 13.9411 | 12.9379 | 11.5526 | 10.2484 | 8.8937 | 6.2842 | 4.8895 | 3.4084
|  | CHIPPING NORTON | EE |  |  |  | 19.2821 | 19.1611 | 19.0326 | 18.8947 | 18.7516 | 18.4663 | 17.8968 | 17.0505 | 15.8958 | 14.6432 | 12.3084 | 11.4021 | 10.3947 | 15.62 | 15.3916 | 15.0421 | 14.6421 | 14.3084 | 13.7863 | 13.0958 | 12.0463 | 10.5989 | 9.1042 | 6.3895 | 5.3547 | 4.1811 | 16.2421 | 16.1116 | 15.8095 | 15.4095 | 15.0768 | 14.5558 | 13.8663 | 12.8179 | 11.3737 | 9.8811 | 7.1747 | 6.14 | 4.9684
|  | CHIPPING NORTON | HT |  |  |  | 19.2274 | 19.0747 | 18.92 | 18.7558 | 18.5368 | 17.9442 | 17.1242 | 16.0105 | 14.9074 | 13.7621 | 11.5074 | 10.2832 | 9.0021 | 15.5463 | 15.1958 | 14.7863 | 14.3295 | 13.8832 | 13.1716 | 12.1674 | 10.7779 | 9.4695 | 8.1126 | 5.4989 | 4.1021 | 2.6189 | 16.1832 | 15.9632 | 15.5537 | 15.0979 | 14.6516 | 13.9411 | 12.9379 | 11.5526 | 10.2484 | 8.8937 | 6.2842 | 4.8895 | 3.4084
|  | CHIPPING NORTON | HE |  |  |  | 19.3642 | 19.28 | 19.1884 | 19.0863 | 18.9768 | 18.86 | 18.4495 | 17.6095 | 16.5 | 15.3632 | 13.2947 | 12.6516 | -5.7716 | 15.7147 | 15.6158 | 15.3905 | 15.0758 | 14.8116 | 14.3516 | 13.7242 | 12.6737 | 11.2758 | 9.8947 | 7.4379 | 6.6958 | 5.8147 | 16.3305 | 16.2389 | 16.1379 | 15.8432 | 15.5789 | 15.12 | 14.4937 | 13.4453 | 12.0495 | 10.6705 | 8.2147 | 7.4737 | 6.5947
|  | CHIPPING NORTON | CF |  |  |  | 19.4105 | 19.3632 | 19.3147 | 19.2621 | 19.2095 | 19.1547 | 19.0989 | 19.0442 | 18.9905 | 18.9358 | 16.1189 | 15.6737 | 15.2011 | 15.7642 | 15.7105 | 15.6495 | 15.5179 | 15.4105 | 15.3032 | 15.1905 | 15.0221 | 14.7874 | 14.4611 | 10.7589 | 10.2463 | 9.6895 | 16.3789 | 16.3274 | 16.2737 | 16.2147 | 16.1589 | 16.0705 | 15.9579 | 15.7895 | 15.5547 | 15.2295 | 11.5337 | 11.0211 | 10.4663
COWLEY GSP | HIGH WYCOMBE BSP | CHISBRIDGE | MINIMUM HEADROOM | SU 80226 89155 | YES | 0.091579 | 7.1179 | 7.0274 | 6.94 | 6.8505 | 6.7611 | 6.6726 | 6.5842 | 6.5 | 6.4179 | 6.3379 | 5.9853 | 5.6821 | -0.58105 | 7.5147 | 7.4232 | 7.3347 | 7.2442 | 7.1547 | 7.0653 | 6.9768 | 6.8926 | 6.8074 | 6.7284 | 6.3726 | 6.0663 | 5.7989 | 7.8926 | 7.7968 | 7.7032 | 7.6084 | 7.5147 | 7.4211 | 7.3284 | 7.24 | 7.1526 | 7.0674 | 6.6895 | 6.3621 | 6.0737
|  | CHISBRIDGE | EE |  |  |  | 7.1589 | 7.0905 | 7.0221 | 6.9505 | 6.8789 | 6.8074 | 6.7368 | 6.6726 | 6.6042 | 6.5421 | 6.2547 | 6.0168 | 5.8168 | 7.5568 | 7.4874 | 7.4179 | 7.3453 | 7.2737 | 7.2011 | 7.1316 | 7.0663 | 6.9979 | 6.9347 | 6.6463 | 6.4074 | 6.2053 | 7.9368 | 7.8642 | 7.7905 | 7.7158 | 7.6411 | 7.5653 | 7.4926 | 7.4242 | 7.3516 | 7.2863 | 6.9779 | 6.72 | 6.5
|  | CHISBRIDGE | HT |  |  |  | 7.1179 | 7.0274 | 6.94 | 6.8505 | 6.7611 | 6.6726 | 6.5842 | 6.5 | 6.4179 | 6.3379 | 5.9853 | 5.6821 | 5.4179 | 7.5147 | 7.4232 | 7.3347 | 7.2442 | 7.1547 | 7.0653 | 6.9768 | 6.8926 | 6.8074 | 6.7284 | 6.3726 | 6.0663 | 5.7989 | 7.8926 | 7.7968 | 7.7032 | 7.6084 | 7.5147 | 7.4211 | 7.3284 | 7.24 | 7.1526 | 7.0674 | 6.6895 | 6.3621 | 6.0737
|  | CHISBRIDGE | HE |  |  |  | 7.2147 | 7.1716 | 7.1284 | 7.0821 | 7.0337 | 6.9832 | 6.9358 | 6.8895 | 6.8442 | 6.8 | 6.6105 | 6.4642 | -0.58105 | 7.6126 | 7.5695 | 7.5253 | 7.4789 | 7.4305 | 7.38 | 7.3316 | 7.2863 | 7.24 | 7.1958 | 7.0042 | 6.8558 | 6.7316 | 7.9958 | 7.9505 | 7.9053 | 7.8568 | 7.8063 | 7.7537 | 7.7042 | 7.6568 | 7.6084 | 7.5621 | 7.3579 | 7.1979 | 7.0632
|  | CHISBRIDGE | CF |  |  |  | 7.2432 | 7.2179 | 7.1916 | 7.1653 | 7.1389 | 7.1116 | 7.0842 | 7.0568 | 7.0274 | 6.9979 | 6.8611 | 6.7526 | 6.6611 | 7.6411 | 7.6168 | 7.5895 | 7.5632 | 7.5358 | 7.5084 | 7.48 | 7.4537 | 7.4232 | 7.3937 | 7.2558 | 7.1453 | 7.0526 | 8.0263 | 8 | 7.9716 | 7.9432 | 7.9158 | 7.8863 | 7.8568 | 7.8284 | 7.7968 | 7.7663 | 7.6189 | 7.5011 | 7.3989
MINETY GSP | TOOTHILL BSP | CHISLEDON | MINIMUM HEADROOM | SU 18894 79934 | YES | 0 | 16.0505 | 15.8063 | 14.6905 | 12.7937 | 10.4295 | 7.6189 | 4.5063 | 1.6432 | -1.2305 | -3.7379 | -9.3937 | -10.1989 | -13.0695 | 15.12 | 14.4874 | 13.2126 | 11.0663 | 8.3126 | 5.0242 | 1.38 | -1.9726 | -5.34 | -8.2758 | -14.8768 | -15.7853 | -16.6474 | 15.4242 | 14.8232 | 13.6432 | 11.4547 | 8.6968 | 5.4137 | 1.7768 | -1.5705 | -4.9305 | -7.8611 | -14.4505 | -15.3579 | -16.2189
|  | CHISLEDON | EE |  |  |  | 16.0874 | 15.9179 | 14.8379 | 12.9747 | 10.6442 | 7.8642 | 4.7853 | 1.9463 | -0.90632 | -3.3916 | -8.8821 | -9.5105 | -10.1032 | 15.1989 | 14.6042 | 13.3705 | 11.26 | 8.5463 | 5.2895 | 1.6811 | -1.6453 | -4.9895 | -7.9021 | -14.32 | -15.0316 | -15.7095 | 15.5 | 14.9368 | 13.7968 | 11.6516 | 8.9295 | 5.6789 | 2.0779 | -1.2432 | -4.5811 | -7.4874 | -13.8947 | -14.6053 | -15.2821
|  | CHISLEDON | HT |  |  |  | 16.0505 | 15.8063 | 14.6905 | 12.7937 | 10.4295 | 7.6189 | 4.5063 | 1.6432 | -1.2305 | -3.7379 | -9.3937 | -10.1989 | -10.9579 | 15.12 | 14.4874 | 13.2126 | 11.0663 | 8.3126 | 5.0242 | 1.38 | -1.9726 | -5.34 | -8.2758 | -14.8768 | -15.7853 | -16.6474 | 15.4242 | 14.8232 | 13.6432 | 11.4547 | 8.6968 | 5.4137 | 1.7768 | -1.5705 | -4.9305 | -7.8611 | -14.4505 | -15.3579 | -16.2189
|  | CHISLEDON | HE |  |  |  | 16.1379 | 16.0663 | 15.0326 | 13.2147 | 10.9263 | 8.1853 | 5.1442 | 2.3421 | -0.47474 | -2.9242 | -8.2526 | -8.7274 | -13.0695 | 15.2947 | 14.7589 | 13.5789 | 11.5168 | 8.8516 | 5.6379 | 2.0716 | -1.2147 | -4.52 | -7.3947 | -13.6347 | -14.1779 | -14.7 | 15.6 | 15.0863 | 14.0011 | 11.9116 | 9.2347 | 6.0274 | 2.4663 | -0.81263 | -4.1116 | -6.9811 | -13.2105 | -13.7526 | -14.2737
|  | CHISLEDON | CF |  |  |  | 16.1674 | 16.1421 | 15.9032 | 15.1242 | 14.1674 | 13.0653 | 11.7095 | 10.3337 | 8.8242 | 7.3968 | 4.0347 | 3.7589 | 3.4811 | 15.3768 | 15.1074 | 14.5789 | 13.6758 | 12.5905 | 11.34 | 9.7589 | 8.1453 | 6.3747 | 4.7 | 0.76737 | 0.45368 | 0.13263 | 15.6895 | 15.4168 | 14.9179 | 14.0958 | 13.0179 | 11.7284 | 10.14 | 8.5295 | 6.7621 | 5.0916 | 1.1653 | 0.85263 | 0.53158
BRAMLEY (FLEE) | BRACKNELL | CHOBHAM | MINIMUM HEADROOM | SU 97173 63223 | YES | 0 | 26.1842 | 25.9653 | 25.7463 | 25.5137 | 24.8853 | 24.1695 | 23.7 | 23.2642 | 22.9316 | 22.6179 | 21.1463 | 19.7326 | 4.5084 | 24.1305 | 23.42 | 22.6463 | 21.8453 | 20.9611 | 20.1621 | 19.6537 | 19.1779 | 18.8211 | 18.4842 | 16.8811 | 15.3116 | 13.9084 | 24.9221 | 24.1958 | 23.4042 | 22.5958 | 21.7116 | 20.9116 | 20.4032 | 19.9274 | 19.5705 | 19.2326 | 17.6274 | 16.0537 | 14.6495
|  | CHOBHAM | EE |  |  |  | 26.2726 | 26.1053 | 25.9274 | 25.7379 | 25.4537 | 24.6 | 24.2284 | 23.8074 | 23.4579 | 23.1916 | 22.0316 | 20.9495 | 20.0158 | 24.3189 | 23.7074 | 23.0168 | 22.3484 | 21.5832 | 20.6147 | 20.2095 | 19.7463 | 19.3684 | 19.0811 | 17.82 | 16.6158 | 15.5642 | 25.1126 | 24.4874 | 23.7811 | 23.1 | 22.3337 | 21.3642 | 20.96 | 20.4958 | 20.1168 | 19.8295 | 18.5632 | 17.3547 | 16.3021
|  | CHOBHAM | HT |  |  |  | 26.1842 | 25.9653 | 25.7463 | 25.5137 | 24.8853 | 24.1695 | 23.7 | 23.2642 | 22.9316 | 22.6179 | 21.1463 | 19.7326 | 18.4779 | 24.1305 | 23.42 | 22.6463 | 21.8453 | 20.9611 | 20.1621 | 19.6537 | 19.1779 | 18.8211 | 18.4842 | 16.8811 | 15.3116 | 13.9084 | 24.9221 | 24.1958 | 23.4042 | 22.5958 | 21.7116 | 20.9116 | 20.4032 | 19.9274 | 19.5705 | 19.2326 | 17.6274 | 16.0537 | 14.6495
|  | CHOBHAM | HE |  |  |  | 26.3926 | 26.2821 | 26.1611 | 26.0263 | 25.8032 | 25.0368 | 24.7526 | 24.4126 | 24.1695 | 23.9947 | 23.2474 | 22.5316 | 4.5084 | 24.5716 | 24.0821 | 23.5084 | 22.8632 | 21.9347 | 21.0579 | 20.7516 | 20.3747 | 20.1105 | 19.9263 | 19.1126 | 18.3084 | 17.6242 | 25.2558 | 24.8684 | 24.2811 | 23.62 | 22.6863 | 21.8084 | 21.5011 | 21.1242 | 20.8611 | 20.6747 | 19.8611 | 19.0547 | 18.3684
|  | CHOBHAM | CF |  |  |  | 26.4611 | 26.4011 | 26.34 | 26.2747 | 26.2095 | 26.1389 | 26.0705 | 26 | 25.9326 | 25.8642 | 25.5579 | 25.3221 | 24.9137 | 24.7716 | 24.5 | 24.2105 | 23.9589 | 23.6832 | 23.4432 | 23.3042 | 23.1642 | 22.9989 | 22.8221 | 22.0158 | 21.4558 | 20.9895 | 25.3316 | 25.2589 | 24.9989 | 24.7411 | 24.46 | 24.2137 | 24.0726 | 23.9295 | 23.7611 | 23.58 | 22.7663 | 22.2042 | 21.7379
COWLEY GSP | DRAYTON BSP | CHOLSEY | MINIMUM HEADROOM | SU 58223 84685 | YES | 0.23158 | 16.4505 | 16.2979 | 16.0789 | 15.8326 | 15.58 | 15.3316 | 15.08 | 14.8516 | 14.6337 | 14.4274 | 13.5347 | 12.7316 | -10.1105 | 14.8147 | 14.4768 | 14.2116 | 13.9411 | 13.6653 | 13.3937 | 13.12 | 12.8684 | 12.6337 | 12.4126 | 11.4411 | 10.5432 | 9.5653 | 14.9389 | 14.5937 | 14.3253 | 14.0505 | 13.7705 | 13.4958 | 13.2179 | 12.9642 | 12.7253 | 12.5011 | 11.52 | 10.6221 | 9.6463
|  | CHOLSEY | EE |  |  |  | 16.5095 | 16.3895 | 16.2684 | 16.0895 | 15.8853 | 15.68 | 15.4779 | 15.2853 | 15.0989 | 14.9284 | 14.2274 | 13.6558 | 13.0537 | 14.9337 | 14.6537 | 14.4463 | 14.2263 | 14.0042 | 13.7811 | 13.56 | 13.3484 | 13.1453 | 12.9579 | 12.1947 | 11.5611 | 10.8705 | 15.06 | 14.7747 | 14.5632 | 14.3411 | 14.1158 | 13.8895 | 13.6653 | 13.4516 | 13.2442 | 13.0547 | 12.2789 | 11.64 | 10.9495
|  | CHOLSEY | HT |  |  |  | 16.4505 | 16.2979 | 16.0789 | 15.8326 | 15.58 | 15.3316 | 15.08 | 14.8516 | 14.6337 | 14.4274 | 13.5347 | 12.7316 | 11.8768 | 14.8147 | 14.4768 | 14.2116 | 13.9411 | 13.6653 | 13.3937 | 13.12 | 12.8684 | 12.6337 | 12.4126 | 11.4411 | 10.5432 | 9.5653 | 14.9389 | 14.5937 | 14.3253 | 14.0505 | 13.7705 | 13.4958 | 13.2179 | 12.9642 | 12.7253 | 12.5011 | 11.52 | 10.6221 | 9.6463
|  | CHOLSEY | HE |  |  |  | 16.5905 | 16.5105 | 16.4263 | 16.3347 | 16.2358 | 16.1316 | 15.9947 | 15.8537 | 15.72 | 15.6011 | 15.1611 | 14.8316 | -10.1105 | 15.0674 | 14.8937 | 14.7579 | 14.6105 | 14.4547 | 14.2947 | 14.1358 | 13.9821 | 13.8379 | 13.7084 | 13.2189 | 12.8442 | 12.4074 | 15.2232 | 15.0189 | 14.8811 | 14.7305 | 14.5737 | 14.4116 | 14.2505 | 14.0958 | 13.9495 | 13.8168 | 13.3211 | 12.9389 | 12.4905
|  | CHOLSEY | CF |  |  |  | 16.6389 | 16.5926 | 16.5505 | 16.5042 | 16.4568 | 16.4084 | 16.3579 | 16.3084 | 16.2589 | 16.2105 | 15.8442 | 15.5947 | 15.3484 | 15.1137 | 15.0695 | 14.9979 | 14.92 | 14.8337 | 14.7453 | 14.6516 | 14.5589 | 14.4663 | 14.3737 | 13.9558 | 13.6705 | 13.3768 | 15.3305 | 15.2126 | 15.1316 | 15.0453 | 14.9579 | 14.8684 | 14.7726 | 14.6789 | 14.5842 | 14.4905 | 14.0663 | 13.7747 | 13.4737
MANNINGTON GSP | CHRISTCHURCH BSP | CHRISTCHURCH | MINIMUM HEADROOM | SZ 15698 93141 | YES | 0.54316 | 36.1842 | 35.6947 | 35.2 | 34.6747 | 34.1316 | 34.2063 | 33.6453 | 32.6916 | 31.72 | 30.7842 | 26.5811 | 22.7526 | -13.3347 | 30.5947 | 29.6126 | 28.6874 | 27.7474 | 26.8074 | 26.8832 | 25.8326 | 24.8042 | 23.8011 | 22.7811 | 18.1874 | 13.9705 | 10.1653 | 31.2832 | 30.6368 | 29.6979 | 28.7442 | 27.7947 | 27.7579 | 26.7011 | 25.6684 | 24.6074 | 23.5811 | 18.9474 | 14.6853 | 10.8642
|  | CHRISTCHURCH | EE |  |  |  | 36.3695 | 35.9853 | 35.5768 | 35.1442 | 34.6905 | 34.2063 | 33.7347 | 33.2832 | 32.78 | 32.8316 | 29.4579 | 26.3853 | 23.7811 | 30.9547 | 30.2411 | 29.5063 | 28.7526 | 27.9926 | 27.2232 | 26.3926 | 25.5832 | 24.7979 | 24.9937 | 21.3442 | 17.9863 | 15.0653 | 31.4821 | 31.0747 | 30.5295 | 29.7663 | 28.9968 | 28.2137 | 27.3674 | 26.5505 | 25.7568 | 25.8379 | 22.1316 | 18.7074 | 15.7663
|  | CHRISTCHURCH | HT |  |  |  | 36.1842 | 35.6947 | 35.2 | 34.6747 | 34.1316 | 34.2642 | 33.6453 | 32.6916 | 31.72 | 30.7842 | 26.5811 | 22.7526 | 19.3547 | 30.5947 | 29.6126 | 28.6874 | 27.7474 | 26.8074 | 26.8832 | 25.8326 | 24.8042 | 23.8011 | 22.7811 | 18.1874 | 13.9705 | 10.1653 | 31.2832 | 30.6368 | 29.6979 | 28.7442 | 27.7947 | 27.7579 | 26.7011 | 25.6684 | 24.6074 | 23.5811 | 18.9474 | 14.6853 | 10.8642
|  | CHRISTCHURCH | HE |  |  |  | 36.6263 | 36.3653 | 36.0758 | 35.7558 | 35.4095 | 35.0305 | 34.6684 | 34.3253 | 34.0032 | 34.4305 | 33.0305 | 31.0147 | -13.3347 | 31.2295 | 30.9537 | 30.5958 | 30.0884 | 29.5621 | 29.0116 | 28.4116 | 27.8432 | 27.2811 | 27.6968 | 25.2368 | 22.9811 | 20.9821 | 31.7568 | 31.4821 | 31.1811 | 30.8495 | 30.4926 | 30.0347 | 29.4242 | 28.8474 | 28.2747 | 28.5811 | 26.0179 | 23.7453 | 21.7305
|  | CHRISTCHURCH | CF |  |  |  | 36.7779 | 36.6305 | 36.4768 | 36.3168 | 36.1526 | 35.9747 | 35.7947 | 35.6179 | 35.4442 | 35.2684 | 35.1916 | 34.7368 | 33.5484 | 31.3916 | 31.2358 | 31.0747 | 30.9063 | 30.7347 | 30.4021 | 30.0179 | 29.6232 | 29.2642 | 28.92 | 28.4716 | 26.9379 | 25.5926 | 31.92 | 31.7642 | 31.6021 | 31.4347 | 31.2621 | 31.0747 | 30.8832 | 30.6463 | 30.28 | 29.9295 | 29.3589 | 27.7916 | 26.4347
LALEHAM | EAST BEDFONT A | CHURCH ROAD | MINIMUM HEADROOM | TQ 06820 71722 | YES | 0 | 15.4621 | 15.1379 | 14.8116 | 14.4642 | 14.1063 | 13.7358 | 13.3653 | 12.4726 | 11.6737 | 11.2095 | 8.6505 | 6.3758 | -13.3853 | 12.5526 | 11.6779 | 11.0547 | 10.4221 | 9.7926 | 9.1684 | 8.5611 | 7.4158 | 6.5126 | 6.0084 | 3.1463 | 0.56947 | -1.8189 | 13.2611 | 12.4295 | 11.8284 | 11.2168 | 10.6084 | 9.9926 | 9.3863 | 8.2421 | 7.34 | 6.8358 | 3.9779 | 1.4042 | -0.98105
|  | CHURCH ROAD | EE |  |  |  | 15.5874 | 15.3326 | 15.0653 | 14.7811 | 14.4842 | 14.1758 | 13.88 | 13.5347 | 12.7989 | 12.4074 | 10.3863 | 8.6579 | 7.1021 | 12.8347 | 12.1063 | 11.6158 | 11.1168 | 10.6158 | 10.1116 | 9.6316 | 8.5821 | 7.7495 | 7.3263 | 5.0674 | 3.1011 | 1.3116 | 13.3863 | 12.84 | 12.3663 | 11.8832 | 11.3979 | 10.9084 | 10.4421 | 9.4074 | 8.5758 | 8.1537 | 5.8968 | 3.9337 | 2.1463
|  | CHURCH ROAD | HT |  |  |  | 15.4621 | 15.1379 | 14.8116 | 14.4642 | 14.1063 | 13.7358 | 13.3653 | 12.4726 | 11.6737 | 11.2095 | 8.6505 | 6.3758 | 4.2632 | 12.5526 | 11.6779 | 11.0547 | 10.4221 | 9.7926 | 9.1684 | 8.5611 | 7.4158 | 6.5126 | 6.0084 | 3.1463 | 0.56947 | -1.8189 | 13.2611 | 12.4295 | 11.8284 | 11.2168 | 10.6084 | 9.9926 | 9.3863 | 8.2421 | 7.34 | 6.8358 | 3.9779 | 1.4042 | -0.98105
|  | CHURCH ROAD | HE |  |  |  | 15.7579 | 15.5853 | 15.3947 | 15.1853 | 14.9579 | 14.7179 | 14.4863 | 14.2695 | 14.0653 | 13.8916 | 12.5895 | 11.4211 | -13.3853 | 13.0916 | 12.6663 | 12.3484 | 12.0137 | 11.6684 | 11.3105 | 10.9726 | 10.0642 | 9.3716 | 9.0895 | 7.5021 | 6.1621 | 4.9705 | 13.5568 | 13.3768 | 13.0684 | 12.7432 | 12.4063 | 12.0579 | 11.7284 | 10.8716 | 10.1968 | 9.9147 | 8.3284 | 6.9905 | 5.8011
|  | CHURCH ROAD | CF |  |  |  | 15.8547 | 15.7558 | 15.6547 | 15.5484 | 15.4389 | 15.3253 | 15.2095 | 15.0958 | 14.9842 | 14.8716 | 14.3705 | 13.6347 | 12.92 | 13.2021 | 13.0979 | 12.9884 | 12.8253 | 12.5368 | 12.2305 | 11.9474 | 11.4316 | 11.0242 | 10.8126 | 9.5589 | 8.5947 | 7.76 | 13.6537 | 13.5547 | 13.4537 | 13.3474 | 13.2379 | 12.9537 | 12.6842 | 12.1989 | 11.8126 | 11.6084 | 10.3842 | 9.4211 | 8.5874
MINETY GSP | CIRENCESTER BSP | CIRENCESTER TOWN | MINIMUM HEADROOM | SP 02761 00827 | YES | 1.4463 | 35.4705 | 35.1621 | 34.8537 | 34.5126 | 34.0232 | 33.5011 | 32.9758 | 32.4726 | 31.9905 | 31.5958 | 29.0347 | 26.2105 | -21.0221 | 29.1411 | 28.8137 | 28.4884 | 28.1253 | 27.5916 | 27.0232 | 26.4516 | 25.8989 | 25.3695 | 24.9411 | 22.0842 | 18.8895 | 15.9368 | 30.5326 | 30.2053 | 29.88 | 29.5168 | 28.9821 | 28.4116 | 27.8368 | 27.2832 | 26.7516 | 26.32 | 23.4484 | 20.2379 | 17.2768
|  | CIRENCESTER TOWN | EE |  |  |  | 35.5853 | 35.3537 | 35.1032 | 34.8432 | 34.5768 | 34.2053 | 33.8105 | 33.4179 | 33.0274 | 32.7284 | 30.6779 | 28.3474 | 26.2642 | 29.2632 | 29.02 | 28.7558 | 28.4842 | 28.2032 | 27.8042 | 27.3779 | 26.9526 | 26.5305 | 26.2116 | 23.9411 | 21.3137 | 18.9326 | 30.6537 | 30.4105 | 30.1463 | 29.8726 | 29.5926 | 29.1926 | 28.7653 | 28.3368 | 27.9095 | 27.5895 | 25.2968 | 22.6442 | 20.2558
|  | CIRENCESTER TOWN | HT |  |  |  | 35.4705 | 35.1621 | 34.8537 | 34.5126 | 34.0232 | 33.5011 | 32.9758 | 32.4726 | 31.9905 | 31.5958 | 29.0347 | 26.2105 | 23.62 | 29.1411 | 28.8137 | 28.4884 | 28.1253 | 27.5916 | 27.0232 | 26.4516 | 25.8989 | 25.3695 | 24.9411 | 22.0842 | 18.8895 | 15.9368 | 30.5326 | 30.2053 | 29.88 | 29.5168 | 28.9821 | 28.4116 | 27.8368 | 27.2832 | 26.7516 | 26.32 | 23.4484 | 20.2379 | 17.2768
|  | CIRENCESTER TOWN | HE |  |  |  | 35.6895 | 35.5758 | 35.4368 | 35.2526 | 35.06 | 34.8537 | 34.5874 | 34.28 | 33.98 | 33.7726 | 32.1779 | 30.3021 | -21.0221 | 29.3663 | 29.2526 | 29.1116 | 28.92 | 28.72 | 28.5074 | 28.2221 | 27.8895 | 27.5632 | 27.3411 | 25.5516 | 23.4021 | 21.4316 | 30.7579 | 30.6442 | 30.5032 | 30.3116 | 30.1105 | 29.8979 | 29.6116 | 29.2768 | 28.9495 | 28.7263 | 26.9284 | 24.7705 | 22.7937
|  | CIRENCESTER TOWN | CF |  |  |  | 35.7505 | 35.6842 | 35.6147 | 35.5432 | 35.4495 | 35.3379 | 35.2253 | 35.1137 | 35.0053 | 34.8937 | 33.9642 | 32.7958 | 31.7474 | 29.4274 | 29.3611 | 29.2916 | 29.22 | 29.1232 | 29.0074 | 28.8884 | 28.7737 | 28.6589 | 28.5421 | 27.5158 | 26.18 | 24.9716 | 30.8189 | 30.7526 | 30.6832 | 30.6116 | 30.5147 | 30.3979 | 30.2789 | 30.1632 | 30.0484 | 29.9316 | 28.9011 | 27.5611 | 26.3495
IVER 132KV | CIPPENHAM | CLARENCE ROAD | MINIMUM HEADROOM | SU 95654 76652 | YES | 1.0516 | 46.9126 | 46.3832 | 45.8484 | 45.2789 | 44.6895 | 44.0789 | 43.4621 | 42.9189 | 42.2611 | 41.1874 | 36.2526 | 31.7916 | -16.5295 | 38.9105 | 38.3316 | 36.8663 | 35.0379 | 33.1221 | 31.6832 | 30.6558 | 29.4368 | 28.1863 | 27.0042 | 21.5221 | 16.5211 | 11.8474 | 40.1779 | 39.6032 | 39.0126 | 37.5305 | 35.6147 | 34.1737 | 33.1474 | 31.9263 | 30.6768 | 29.4926 | 24.0063 | 19.0011 | 14.3242
|  | CLARENCE ROAD | EE |  |  |  | 47.1116 | 46.6947 | 46.2526 | 45.7832 | 45.2884 | 44.7758 | 44.28 | 43.8042 | 43.3463 | 42.9389 | 39.1516 | 35.6737 | 32.5116 | 39.1242 | 38.6705 | 37.7674 | 36.3347 | 34.6126 | 33.36 | 32.2611 | 31.1926 | 30.1168 | 29.1189 | 24.7021 | 20.7926 | 17.2 | 40.3926 | 39.9368 | 39.4463 | 38.8274 | 37.1053 | 35.8505 | 34.7537 | 33.6832 | 32.6063 | 31.6074 | 27.1853 | 23.2705 | 19.6758
|  | CLARENCE ROAD | HT |  |  |  | 46.9126 | 46.3832 | 45.8484 | 45.2789 | 44.6895 | 44.0789 | 43.4621 | 42.9189 | 42.2611 | 41.1874 | 36.2526 | 31.7916 | 27.6568 | 38.9105 | 38.3316 | 36.8663 | 35.0379 | 33.1221 | 31.6832 | 30.6558 | 29.4368 | 28.1863 | 27.0042 | 21.5221 | 16.5211 | 11.8474 | 40.1779 | 39.6032 | 39.0126 | 37.5305 | 35.6147 | 34.1737 | 33.1474 | 31.9263 | 30.6768 | 29.4926 | 24.0063 | 19.0011 | 14.3242
|  | CLARENCE ROAD | HE |  |  |  | 47.3768 | 47.0821 | 46.7558 | 46.3968 | 46.0095 | 45.5968 | 45.2011 | 44.8274 | 44.4789 | 44.18 | 43.0726 | 40.6021 | -16.5295 | 39.4105 | 39.0863 | 38.7211 | 37.7611 | 36.5242 | 35.5211 | 34.6768 | 33.5821 | 32.8084 | 32.1347 | 29.0147 | 26.2105 | 23.6789 | 40.6789 | 40.3537 | 39.9874 | 39.5811 | 39.0168 | 38.0137 | 37.1684 | 36.0737 | 35.2989 | 34.6253 | 31.5032 | 28.6968 | 26.1632
|  | CLARENCE ROAD | CF |  |  |  | 47.5242 | 47.3474 | 47.1642 | 46.9726 | 46.7758 | 46.5705 | 46.3621 | 46.1579 | 45.9547 | 45.7516 | 44.8453 | 44.3916 | 44.1389 | 39.5726 | 39.3811 | 39.1811 | 38.9695 | 38.7411 | 38.2105 | 37.5579 | 36.9716 | 36.5895 | 36.1284 | 33.8021 | 31.8389 | 30.1274 | 40.8411 | 40.6495 | 40.4484 | 40.2368 | 40.0074 | 39.7716 | 39.5368 | 39.3105 | 39.0811 | 38.62 | 36.2926 | 34.3284 | 32.6158
MELKSHAM GSP | CHIPPENHAM | COCKLEBURY | MINIMUM HEADROOM | ST 92447 73890 | YES | 0.18947 | 41.2884 | 41.0642 | 41.3611 | 40.4768 | 39.4032 | 38.0979 | 36.6916 | 35.5316 | 34.5779 | 33.6042 | 30.4842 | 27.8947 | 4.8 | 34.9505 | 34.7253 | 34.4389 | 33.4516 | 32.24 | 30.7621 | 29.1653 | 27.8526 | 26.7821 | 25.6821 | 21.8768 | 19.0263 | 16.2274 | 36.44 | 36.2158 | 35.9284 | 34.9411 | 33.7316 | 32.2526 | 30.6537 | 29.34 | 28.2663 | 27.1621 | 23.3253 | 20.4379 | 17.6274
|  | COCKLEBURY | EE |  |  |  | 41.2884 | 41.0642 | 41.4368 | 40.9768 | 40.0063 | 39.1316 | 37.8253 | 36.7358 | 35.8274 | 34.9547 | 32.0916 | 30.0095 | 28.0484 | 34.9505 | 34.7253 | 34.4874 | 33.9895 | 32.8905 | 31.5211 | 30.04 | 28.8105 | 27.7968 | 26.82 | 23.6695 | 21.4053 | 19.1947 | 36.44 | 36.2158 | 35.9768 | 35.48 | 34.3821 | 33.0095 | 31.5253 | 30.2926 | 29.2726 | 28.2895 | 25.0937 | 22.7747 | 20.5495
|  | COCKLEBURY | HT |  |  |  | 42.9284 | 42.2674 | 41.3611 | 40.4768 | 39.4032 | 38.0979 | 36.6916 | 35.5316 | 34.5779 | 33.6042 | 30.4842 | 27.8947 | 25.4063 | 36.1853 | 35.4558 | 34.4389 | 33.4516 | 32.24 | 30.7621 | 29.1653 | 27.8526 | 26.7821 | 25.6821 | 21.8768 | 19.0263 | 16.2274 | 37.6737 | 36.9453 | 35.9284 | 34.9411 | 33.7316 | 32.2526 | 30.6537 | 29.34 | 28.2663 | 27.1621 | 23.3253 | 20.4379 | 17.6274
|  | COCKLEBURY | HE |  |  |  | 41.44 | 41.2874 | 41.7305 | 41.5432 | 40.8337 | 39.7484 | 38.5747 | 37.6126 | 36.84 | 36.0989 | 33.9 | 32.4779 | 4.8 | 35.1011 | 34.9484 | 34.78 | 34.5926 | 33.7905 | 32.5516 | 31.2042 | 30.1063 | 29.2305 | 28.3884 | 25.9158 | 24.3158 | 22.6474 | 36.5916 | 36.4389 | 36.2705 | 36.0832 | 35.2821 | 34.0421 | 32.6947 | 31.5958 | 30.7179 | 29.8737 | 27.3853 | 25.7716 | 24.0905
|  | COCKLEBURY | CF |  |  |  | 41.5284 | 41.4421 | 41.9642 | 41.8716 | 41.7758 | 41.6705 | 41.2126 | 40.7021 | 40.2653 | 39.8032 | 38.44 | 37.6095 | 36.6789 | 35.1895 | 35.1032 | 35.0137 | 34.9211 | 34.8253 | 34.7211 | 34.2 | 33.6168 | 33.12 | 32.5947 | 31.0726 | 30.1453 | 29.0832 | 36.68 | 36.5937 | 36.5042 | 36.4116 | 36.3158 | 36.2105 | 35.6895 | 35.1053 | 34.6074 | 34.0821 | 32.5558 | 31.62 | 30.5505
MELKSHAM GSP | FROME BSP | CODFORD | MINIMUM HEADROOM | ST 97372 39559 | YES | 0.042105 | 4.9421 | 4.9053 | 4.8674 | 4.8274 | 4.7842 | 4.7937 | 4.7589 | 4.72 | 2.8189 | 2.7884 | 0.071579 | -1.4547 | -1.5284 | 5.0032 | 4.9505 | 4.8874 | 4.8242 | 4.7611 | 4.7884 | 4.74 | 4.6916 | 2.5495 | 2.5189 | -0.64947 | -2.4263 | -2.5 | 4.9084 | 4.8589 | 4.8095 | 4.7579 | 4.7063 | 4.7242 | 4.6832 | 4.6432 | 2.4674 | 2.4368 | -0.73263 | -2.5095 | -2.5832
|  | CODFORD | EE |  |  |  | 4.9568 | 4.9274 | 4.8968 | 4.8632 | 4.8295 | 4.7937 | 4.7589 | 4.72 | 4.6726 | 4.6295 | 4.0853 | 2.7232 | -0.058947 | 5.0232 | 4.9863 | 4.9432 | 4.8916 | 4.8411 | 4.7884 | 4.74 | 4.6916 | 4.6421 | 4.5968 | 4.0463 | 2.4579 | -0.8 | 4.9295 | 4.8905 | 4.8505 | 4.8095 | 4.7674 | 4.7242 | 4.6832 | 4.6432 | 4.6063 | 4.5726 | 3.9642 | 2.3758 | -0.88316
|  | CODFORD | HT |  |  |  | 4.9421 | 4.9053 | 4.8674 | 4.8274 | 4.7842 | 5.3632 | 5.32 | 5.2684 | 2.8189 | 2.7884 | 0.071579 | -1.4547 | -1.5284 | 5.0032 | 4.9505 | 4.8874 | 4.8242 | 4.7611 | 5.5442 | 5.4768 | 5.4147 | 2.5495 | 2.5189 | -0.64947 | -2.4263 | -2.5 | 4.9084 | 4.8589 | 4.8095 | 4.7579 | 4.7063 | 5.4547 | 5.3905 | 5.3316 | 2.4674 | 2.4368 | -0.73263 | -2.5095 | -2.5832
|  | CODFORD | HE |  |  |  | 4.9768 | 4.9579 | 4.9358 | 4.9126 | 4.8874 | 4.86 | 4.8337 | 4.8084 | 4.7863 | 4.7663 | 4.2147 | 2.8811 | 0.59895 | 5.0484 | 5.0263 | 5 | 4.9737 | 4.9453 | 4.9126 | 4.8768 | 4.8442 | 4.8147 | 4.7863 | 4.1758 | 2.6158 | -0.61684 | 4.9579 | 4.9337 | 4.9063 | 4.8789 | 4.8484 | 4.8168 | 4.7863 | 4.7579 | 4.7316 | 4.7084 | 4.0937 | 2.5337 | -0.7
|  | CODFORD | CF |  |  |  | 4.9895 | 4.9789 | 4.9684 | 4.9568 | 4.9453 | 4.9326 | 4.92 | 4.9084 | 4.8958 | 4.8842 | 4.8305 | 5.4232 | 5.3663 | 5.0642 | 5.0516 | 5.0379 | 5.0242 | 5.0095 | 4.9937 | 4.9789 | 4.9642 | 4.9453 | 4.9253 | 4.8389 | 5.6116 | 5.5095 | 4.9737 | 4.96 | 4.9463 | 4.9305 | 4.9158 | 4.8989 | 4.8821 | 4.8674 | 4.8516 | 4.8358 | 4.7674 | 5.5179 | 5.4305
IVER 132KV | DENHAM | COKES LANE | MINIMUM HEADROOM | SU 99240 97483 | YES | 0.12842 | 14.26 | 14.1537 | 14.0474 | 13.7937 | 13.6137 | 13.4337 | 13.2526 | 13.0832 | 12.9221 | 12.7663 | 12.0768 | 11.4853 | 0.58211 | 12.8095 | 12.5126 | 12.1632 | 11.7916 | 11.5937 | 11.3979 | 11.1989 | 11.0116 | 10.8337 | 10.6589 | 9.8737 | 9.1884 | 8.5916 | 13.3316 | 13.0221 | 12.6768 | 12.3221 | 12.1295 | 11.9389 | 11.7463 | 11.5653 | 11.3916 | 11.2232 | 10.4695 | 9.8147 | 9.2421
|  | COKES LANE | EE |  |  |  | 14.3063 | 14.2253 | 14.1389 | 13.9979 | 13.8558 | 13.7126 | 13.5758 | 13.44 | 13.3 | 13.1726 | 12.64 | 12.1926 | 11.8126 | 12.8989 | 12.6474 | 12.3463 | 12.0211 | 11.8653 | 11.7095 | 11.56 | 11.4126 | 11.2579 | 11.1158 | 10.5084 | 9.9874 | 9.5368 | 13.4242 | 13.1611 | 12.8568 | 12.5432 | 12.3916 | 12.24 | 12.0947 | 11.9505 | 11.8011 | 11.6632 | 11.08 | 10.5832 | 10.1547
|  | COKES LANE | HT |  |  |  | 14.26 | 14.1537 | 14.0474 | 13.7937 | 13.6137 | 13.4337 | 13.2526 | 13.0832 | 12.9221 | 12.7663 | 12.0768 | 11.4853 | 10.9547 | 12.8095 | 12.5126 | 12.1632 | 11.7916 | 11.5937 | 11.3979 | 11.1989 | 11.0116 | 10.8337 | 10.6589 | 9.8737 | 9.1884 | 8.5916 | 13.3316 | 13.0221 | 12.6768 | 12.3221 | 12.1295 | 11.9389 | 11.7463 | 11.5653 | 11.3916 | 11.2232 | 10.4695 | 9.8147 | 9.2421
|  | COKES LANE | HE |  |  |  | 14.3642 | 14.3105 | 14.2526 | 14.1874 | 14.1179 | 14.0442 | 13.9663 | 13.8705 | 13.7726 | 13.6842 | 13.3337 | 13.0537 | 0.58211 | 13.0147 | 12.8189 | 12.5811 | 12.3158 | 12.2116 | 12.1063 | 12.0021 | 11.8989 | 11.7916 | 11.6926 | 11.2947 | 10.9653 | 10.6874 | 13.5432 | 13.3379 | 13.0895 | 12.8284 | 12.7263 | 12.6221 | 12.52 | 12.4189 | 12.3147 | 12.22 | 11.8358 | 11.5232 | 11.2611
|  | COKES LANE | CF |  |  |  | 14.3968 | 14.3684 | 14.3379 | 14.3063 | 14.2737 | 14.2411 | 14.2074 | 14.1737 | 14.1389 | 14.1063 | 13.9589 | 13.8074 | 13.6474 | 13.0979 | 12.9895 | 12.8663 | 12.7442 | 12.6874 | 12.6305 | 12.5726 | 12.5126 | 12.4495 | 12.3821 | 12.0621 | 11.8232 | 11.6305 | 13.6295 | 13.5158 | 13.3874 | 13.2589 | 13.2011 | 13.1421 | 13.0832 | 13.0211 | 12.9558 | 12.8884 | 12.5768 | 12.3474 | 12.1653
LOVEDEAN GSP | WYMERING BSP | COLLEGE PARK | MINIMUM HEADROOM | SU 65893 02686 | YES | 0.21684 | 17.2274 | 17.02 | 16.8116 | 16.5895 | 16.3579 | 16.1168 | 15.8737 | 15.6568 | 15.4589 | 15.2758 | 13.9832 | 12.0589 | -2.4474 | 15.1074 | 14.8042 | 14.4 | 13.9874 | 13.56 | 13.1337 | 12.7137 | 12.3253 | 11.9589 | 11.5242 | 9.3337 | 7.1505 | 5.1484 | 15.4421 | 15.2232 | 15.0032 | 14.6716 | 14.26 | 13.8474 | 13.44 | 13.0642 | 12.7116 | 12.2958 | 10.1147 | 7.9347 | 5.9347
|  | COLLEGE PARK | EE |  |  |  | 17.2979 | 17.1305 | 16.9537 | 16.7663 | 16.5674 | 16.36 | 16.1589 | 15.9663 | 15.7789 | 15.6116 | 14.9853 | 13.7674 | 12.3968 | 15.1884 | 15.0042 | 14.7442 | 14.4095 | 14.0663 | 13.7084 | 13.3663 | 13.0368 | 12.7168 | 12.4189 | 10.7937 | 9.0663 | 7.4968 | 15.5189 | 15.3421 | 15.1568 | 14.9611 | 14.7432 | 14.3968 | 14.0653 | 13.7463 | 13.4358 | 13.1474 | 11.5737 | 9.8474 | 8.28
|  | COLLEGE PARK | HT |  |  |  | 17.2274 | 17.02 | 16.8116 | 16.5895 | 16.3579 | 16.1168 | 15.8737 | 15.6568 | 15.4589 | 15.2758 | 13.9832 | 12.0589 | 10.2842 | 15.1074 | 14.8042 | 14.4 | 13.9874 | 13.56 | 13.1337 | 12.7137 | 12.3253 | 11.9589 | 11.5242 | 9.3337 | 7.1505 | 5.1484 | 15.4421 | 15.2232 | 15.0032 | 14.6716 | 14.26 | 13.8474 | 13.44 | 13.0642 | 12.7116 | 12.2958 | 10.1147 | 7.9347 | 5.9347
|  | COLLEGE PARK | HE |  |  |  | 17.3947 | 17.2716 | 17.1358 | 16.9853 | 16.8232 | 16.6516 | 16.4863 | 16.3305 | 16.1863 | 16.0611 | 15.6305 | 15.3705 | -2.4474 | 15.2937 | 15.1653 | 15.0242 | 14.8632 | 14.6895 | 14.4432 | 14.1968 | 13.9621 | 13.7432 | 13.5463 | 12.7463 | 11.6505 | 10.5453 | 15.6232 | 15.4958 | 15.3547 | 15.1989 | 15.0316 | 14.8547 | 14.6853 | 14.5253 | 14.3758 | 14.2242 | 13.4516 | 12.42 | 11.3253
|  | COLLEGE PARK | CF |  |  |  | 17.4484 | 17.3705 | 17.2905 | 17.2063 | 17.12 | 17.0305 | 16.9389 | 16.8495 | 16.76 | 16.6716 | 16.2747 | 16.0758 | 15.9642 | 15.3495 | 15.2684 | 15.1832 | 15.0947 | 15 | 14.9021 | 14.7895 | 14.6305 | 14.4716 | 14.3137 | 13.5811 | 12.8821 | 12.1389 | 15.68 | 15.5979 | 15.5137 | 15.4253 | 15.3347 | 15.2411 | 15.1463 | 15.0526 | 14.9589 | 14.8663 | 14.2726 | 13.6116 | 12.9158
EALING GSP |  | COPLEY DENE | MINIMUM HEADROOM | TQ 17445 80798 | NO | 0 | 47.0747 | 46.6189 | 46.1589 | 45.6705 | 45.1568 | 83.3221 | 82.7811 | 82.0326 | 81.2421 | 80.4905 | 76.9832 | 73.3768 | 25.0495 | 39.2916 | 38.5042 | 37.4379 | 36.0316 | 34.5189 | 71.7284 | 70.7168 | 69.7895 | 68.9379 | 68.1263 | 64.3042 | 60.3011 | 56.4442 | 40.4863 | 39.9989 | 39.5032 | 38.5642 | 37.0621 | 74.2705 | 73.26 | 72.3337 | 71.4832 | 70.6716 | 66.8537 | 62.8547 | 59.0032
|  | COPLEY DENE | EE |  |  |  | 47.2495 | 46.8926 | 46.5158 | 46.1137 | 45.6863 | 83.9389 | 83.5042 | 83.0832 | 82.6737 | 82.3053 | 80.0484 | 77.5263 | 75.1832 | 39.5516 | 39.0358 | 38.3895 | 37.2989 | 36.1074 | 73.5284 | 72.7137 | 71.9495 | 71.2211 | 70.5505 | 67.6979 | 64.9063 | 62.28 | 40.6747 | 40.2958 | 39.8947 | 39.4516 | 38.6316 | 76.0747 | 75.2547 | 74.4905 | 73.7621 | 73.0937 | 70.2432 | 67.4547 | 64.8326
|  | COPLEY DENE | HT |  |  |  | 47.0747 | 46.6189 | 46.1589 | 45.6705 | 45.1568 | 83.3221 | 82.7811 | 82.0326 | 81.2421 | 80.4905 | 76.9832 | 73.3768 | 69.9347 | 39.2916 | 38.5042 | 37.4379 | 36.0316 | 34.5189 | 71.7284 | 70.7168 | 69.7895 | 68.9379 | 68.1263 | 64.3042 | 60.3011 | 56.4442 | 40.4863 | 39.9989 | 39.5032 | 38.5642 | 37.0621 | 74.2705 | 73.26 | 72.3337 | 71.4832 | 70.6716 | 66.8537 | 62.8547 | 59.0032
|  | COPLEY DENE | HE |  |  |  | 47.4389 | 47.1663 | 46.8653 | 46.5316 | 46.1737 | 84.4916 | 84.1263 | 83.7821 | 83.4611 | 83.1832 | 82.2211 | 81.5284 | 25.0495 | 39.7579 | 39.4716 | 39.0842 | 38.3926 | 37.3937 | 75.0084 | 74.38 | 73.8084 | 73.2937 | 72.8337 | 71.0484 | 69.3147 | 67.7453 | 40.8811 | 40.5947 | 40.2768 | 39.9095 | 39.5137 | 77.5189 | 76.9263 | 76.3621 | 75.8442 | 75.3811 | 73.5895 | 71.8579 | 70.2916
|  | COPLEY DENE | CF |  |  |  | 47.5421 | 47.3611 | 47.1726 | 46.9779 | 46.7758 | 85.2674 | 85.0547 | 84.8453 | 84.6379 | 84.4305 | 83.5074 | 83.0411 | 82.78 | 39.8684 | 39.6779 | 39.48 | 39.2211 | 38.8621 | 77.1463 | 76.7684 | 76.3705 | 75.9432 | 75.5095 | 73.4695 | 72.2011 | 71.1 | 40.9916 | 40.8011 | 40.6032 | 40.3926 | 40.1726 | 78.6463 | 78.4242 | 78.2042 | 77.9832 | 77.7621 | 76.0221 | 74.7421 | 73.6421
BRAMLEY (FLEE) | MAIDENHEAD BSP | CORDWALLIS | MINIMUM HEADROOM | SU 88285 81857 | YES | 0.26211 | 36.9516 | 36.6316 | 36.3084 | 35.9653 | 35.6095 | 35.0337 | 34.4747 | 33.9632 | 33.3316 | 32.7358 | 29.9695 | 27.4495 | 1.4589 | 31.2011 | 30.3737 | 29.4789 | 28.4895 | 27.3958 | 26.5684 | 25.96 | 25.4 | 24.68 | 24.0011 | 20.8674 | 18.0368 | 15.3832 | 32.3832 | 31.7779 | 30.9158 | 29.9632 | 28.9116 | 28.0989 | 27.5053 | 26.9411 | 26.2137 | 25.5274 | 22.3589 | 19.4937 | 16.8326
|  | CORDWALLIS | EE |  |  |  | 37.0726 | 36.8221 | 36.5558 | 36.2737 | 35.9768 | 35.4716 | 35.1758 | 34.8937 | 34.3979 | 33.8905 | 31.7168 | 29.7726 | 28.0116 | 31.4768 | 30.7884 | 30.0179 | 29.1516 | 28.1758 | 27.46 | 26.9653 | 26.4958 | 25.8779 | 25.3 | 22.7905 | 20.5937 | 18.5884 | 32.5126 | 32.1811 | 31.4379 | 30.6053 | 29.6684 | 28.9642 | 28.4811 | 28.0232 | 27.4221 | 26.8389 | 24.3011 | 22.0768 | 20.0442
|  | CORDWALLIS | HT |  |  |  | 36.9516 | 36.6316 | 36.3084 | 35.9653 | 35.6095 | 35.0337 | 34.4747 | 33.9632 | 33.3316 | 32.7358 | 29.9695 | 27.4495 | 25.1042 | 31.2011 | 30.3737 | 29.4789 | 28.4895 | 27.3958 | 26.5684 | 25.96 | 25.4 | 24.68 | 24.0011 | 20.8674 | 18.0368 | 15.3832 | 32.3832 | 31.7779 | 30.9158 | 29.9632 | 28.9116 | 28.0989 | 27.5053 | 26.9411 | 26.2137 | 25.5274 | 22.3589 | 19.4937 | 16.8326
|  | CORDWALLIS | HE |  |  |  | 37.2368 | 37.0621 | 36.8695 | 36.6568 | 36.4274 | 35.9842 | 35.7505 | 35.5305 | 35.3242 | 35.1474 | 33.7905 | 32.4789 | 1.4589 | 31.7063 | 31.4095 | 30.8695 | 30.2463 | 29.5442 | 28.5853 | 28.0232 | 27.6853 | 27.2695 | 26.8874 | 25.1305 | 23.5695 | 22.1737 | 32.6853 | 32.4989 | 32.2589 | 31.6589 | 30.9853 | 30.0547 | 29.5116 | 29.18 | 28.7768 | 28.4053 | 26.6632 | 25.0811 | 23.6653
|  | CORDWALLIS | CF |  |  |  | 37.3305 | 37.2284 | 37.1232 | 37.0137 | 36.9 | 36.5842 | 36.4642 | 36.3463 | 36.2305 | 36.1137 | 35.5937 | 35.3158 | 34.5337 | 31.8074 | 31.6947 | 31.5168 | 31.1947 | 30.8453 | 30.2726 | 29.9526 | 29.7326 | 29.5147 | 29.2537 | 27.9442 | 26.8474 | 25.8989 | 32.7789 | 32.6768 | 32.5632 | 32.4411 | 32.2379 | 31.68 | 31.3716 | 31.1568 | 30.9453 | 30.6926 | 29.4284 | 28.3789 | 27.4347
MANNINGTON GSP | LYTCHETT | CORFE MULLEN | MINIMUM HEADROOM | SY 98583 96071 | YES | 0 | 32.2632 | 31.9295 | 31.8674 | 31.4337 | 30.5716 | 29.4442 | 28.2137 | 27.1758 | 26.6074 | 26.0674 | 22.1937 | 19.2389 | 4.4295 | 30.2253 | 29.4684 | 28.5547 | 27.7442 | 26.7979 | 25.5526 | 24.1884 | 23.0432 | 22.4442 | 21.8768 | 17.7768 | 14.4474 | 11.8947 | 30.5442 | 29.8053 | 28.9116 | 28.1032 | 27.1547 | 25.9021 | 24.5295 | 23.3747 | 22.7653 | 22.1874 | 17.88 | 14.6095 | 12.0242
|  | CORFE MULLEN | EE |  |  |  | 32.3989 | 32.1421 | 31.8674 | 32.2621 | 31.5337 | 30.5253 | 29.4095 | 28.3126 | 27.62 | 27.1368 | 23.6305 | 21.1316 | 19.3516 | 30.5137 | 29.9716 | 29.2842 | 28.6589 | 27.8568 | 26.7411 | 25.5011 | 24.2832 | 23.5389 | 23.0379 | 19.2358 | 16.5916 | 14.6347 | 30.7937 | 30.2958 | 29.6263 | 29.0158 | 28.2137 | 27.0895 | 25.8389 | 24.6074 | 23.8505 | 23.3347 | 19.4368 | 16.6821 | 14.6884
|  | CORFE MULLEN | HT |  |  |  | 32.2632 | 31.9295 | 32.1758 | 31.4337 | 30.5716 | 29.4442 | 28.2137 | 27.1758 | 26.6074 | 26.0674 | 22.1937 | 19.2389 | 16.9242 | 30.2253 | 29.4684 | 28.5547 | 27.7442 | 26.7979 | 25.5526 | 24.1884 | 23.0432 | 22.4442 | 21.8768 | 17.7768 | 14.4474 | 11.8947 | 30.5442 | 29.8053 | 28.9116 | 28.1032 | 27.1547 | 25.9021 | 24.5295 | 23.3747 | 22.7653 | 22.1874 | 17.88 | 14.6095 | 12.0242
|  | CORFE MULLEN | HE |  |  |  | 32.5811 | 32.4116 | 32.2242 | 32.0158 | 31.7916 | 31.5116 | 30.6747 | 29.7189 | 29.2305 | 28.9189 | 26.2737 | 24.6716 | 4.4295 | 30.7874 | 30.5421 | 30.0274 | 29.5621 | 28.9379 | 27.9853 | 26.9095 | 25.8316 | 25.3011 | 24.9737 | 22.0221 | 20.2432 | 18.8747 | 30.9884 | 30.8074 | 30.3537 | 29.8989 | 29.2926 | 28.3379 | 27.2568 | 26.1716 | 25.6358 | 25.3021 | 22.3095 | 20.4989 | 19.1021
|  | CORFE MULLEN | CF |  |  |  | 32.6863 | 32.5947 | 32.5 | 32.4011 | 32.2979 | 32.1811 | 32.0632 | 31.9463 | 31.8316 | 31.7137 | 29.6021 | 28.5232 | 27.7305 | 30.9042 | 30.7989 | 30.6895 | 30.5116 | 30.2779 | 29.9295 | 29.5116 | 29.1537 | 28.7895 | 28.4063 | 25.6737 | 24.4726 | 23.5895 | 31.1 | 31.0021 | 30.9 | 30.7947 | 30.5958 | 30.2558 | 29.8484 | 29.4979 | 29.1432 | 28.7505 | 26.0053 | 24.7863 | 23.8842
MELKSHAM GSP | NORRINGTON | CORSHAM | MINIMUM HEADROOM | ST 86766 69583 | YES | 0.50316 | 11.7726 | 11.5663 | 11.3579 | 11.1368 | 10.8989 | 10.4474 | 10.0495 | 9.6874 | 9.3442 | 8.9853 | 7.0884 | 5.1463 | -11.6495 | 9.1421 | 8.7589 | 8.2684 | 7.7105 | 7.2126 | 6.7316 | 6.3168 | 5.9379 | 5.5779 | 5.1958 | 3.1505 | 1.0263 | -0.98526 | 9.7242 | 9.5179 | 9.0547 | 8.5158 | 8.0337 | 7.5589 | 7.1442 | 6.7589 | 6.3916 | 6.0011 | 3.9032 | 1.7232 | -0.31158
|  | CORSHAM | EE |  |  |  | 11.8484 | 11.6863 | 11.5126 | 11.3284 | 11.1347 | 10.9179 | 10.6421 | 10.3232 | 10.0074 | 9.7147 | 8.1547 | 6.5116 | 5.0947 | 9.2832 | 9.0137 | 8.6053 | 8.1316 | 7.7074 | 7.3021 | 6.9674 | 6.6411 | 6.3179 | 6.0189 | 4.3874 | 2.6368 | 1.0337 | 9.8 | 9.6379 | 9.3884 | 8.9242 | 8.5116 | 8.1105 | 7.7716 | 7.4411 | 7.1126 | 6.8084 | 5.1116 | 3.2832 | 1.6547
|  | CORSHAM | HT |  |  |  | 11.7726 | 11.5663 | 11.3579 | 11.1368 | 10.8989 | 10.4474 | 10.0495 | 9.6874 | 9.3442 | 8.9853 | 7.0884 | 5.1463 | 3.3695 | 9.1421 | 8.7589 | 8.2684 | 7.7105 | 7.2126 | 6.7316 | 6.3168 | 5.9379 | 5.5779 | 5.1958 | 3.1505 | 1.0263 | -0.98526 | 9.7242 | 9.5179 | 9.0547 | 8.5158 | 8.0337 | 7.5589 | 7.1442 | 6.7589 | 6.3916 | 6.0011 | 3.9032 | 1.7232 | -0.31158
|  | CORSHAM | HE |  |  |  | 11.9579 | 11.8474 | 11.7253 | 11.5895 | 11.4442 | 11.2726 | 11.1116 | 10.9579 | 10.8116 | 10.6821 | 9.8463 | 8.8074 | -11.6495 | 9.3937 | 9.2832 | 9.0505 | 8.6937 | 8.3789 | 8.0695 | 7.8358 | 7.6137 | 7.4011 | 7.2105 | 6.1611 | 4.9989 | 3.7937 | 9.9095 | 9.7989 | 9.6768 | 9.4789 | 9.1653 | 8.8579 | 8.6242 | 8.4 | 8.1863 | 7.9916 | 6.9421 | 5.7642 | 4.5379
|  | CORSHAM | CF |  |  |  | 12.0221 | 11.96 | 11.8958 | 11.8284 | 11.7589 | 11.68 | 11.5989 | 11.52 | 11.4411 | 11.3653 | 11.0137 | 10.6779 | 10.0084 | 9.4579 | 9.3958 | 9.3316 | 9.1926 | 9.0337 | 8.8663 | 8.7137 | 8.5768 | 8.4442 | 8.3084 | 7.6737 | 7.0116 | 6.2537 | 9.9737 | 9.9116 | 9.8474 | 9.78 | 9.7105 | 9.6316 | 9.4926 | 9.3516 | 9.2158 | 9.0832 | 8.4516 | 7.7989 | 7.0463
EAST CLAYDON GSP | BICESTER NORTH BSP | COTTISFORD | MINIMUM HEADROOM | SP 59021 31128 | YES | 0.12105 | 2.4826 | 2.3858 | 2.2879 | 2.1837 | 1.9395 | 1.4247 | 0.92158 | 0.29737 | -1.8563 | -1.9795 | -3.4026 | -5.2868 | -5.8268 | 1.7563 | 1.6532 | 1.5468 | 1.4374 | 1.1605 | 0.58895 | 0.031053 | -0.66789 | -3.1742 | -3.2784 | -4.7079 | -6.6563 | -7.1742 | 1.7837 | 1.6816 | 1.5763 | 1.4647 | 1.1921 | 0.61316 | 0.046842 | -0.65947 | -3.1458 | -3.2689 | -4.8132 | -6.8858 | -7.4584
|  | COTTISFORD | EE |  |  |  | 2.5258 | 2.4521 | 2.3721 | 2.2837 | 2.1984 | 2.0563 | 1.8974 | 1.7321 | 1.5605 | 1.3847 | -1.0111 | -3.1153 | -4.1837 | 1.8037 | 1.7247 | 1.6395 | 1.5479 | 1.4574 | 1.3237 | 1.1805 | 1.0321 | 0.87737 | 0.71632 | -1.7732 | -3.8858 | -5.0247 | 1.8268 | 1.7532 | 1.6668 | 1.5742 | 1.4837 | 1.3363 | 1.1721 | 1.0026 | 0.82684 | 0.64579 | -2.0016 | -4.2974 | -5.4858
|  | COTTISFORD | HT |  |  |  | 2.4826 | 2.3858 | 2.2879 | 2.1837 | 1.9395 | 1.4247 | 0.92158 | 0.29737 | -1.8563 | -1.9795 | -3.4026 | -5.2868 | -5.8268 | 1.7563 | 1.6532 | 1.5468 | 1.4374 | 1.1605 | 0.58895 | 0.031053 | -0.66789 | -3.1742 | -3.2784 | -4.7079 | -6.6563 | -7.1742 | 1.7837 | 1.6816 | 1.5763 | 1.4647 | 1.1921 | 0.61316 | 0.046842 | -0.65947 | -3.1458 | -3.2689 | -4.8132 | -6.8858 | -7.4584
|  | COTTISFORD | HE |  |  |  | 2.5858 | 2.5384 | 2.4911 | 2.4374 | 2.3784 | 2.2753 | 2.1795 | 2.0837 | 1.9879 | 1.8953 | 0.20789 | -1.0279 | -5.3826 | 1.8689 | 1.8195 | 1.7679 | 1.7111 | 1.6489 | 1.5532 | 1.4637 | 1.3753 | 1.2858 | 1.2016 | -0.64684 | -1.9974 | -2.9447 | 1.8868 | 1.8405 | 1.7921 | 1.7384 | 1.6763 | 1.57 | 1.4721 | 1.3732 | 1.2732 | 1.1795 | -0.72053 | -2.1121 | -3.0995
|  | COTTISFORD | CF |  |  |  | 2.6163 | 2.5847 | 2.5521 | 2.5247 | 2.4953 | 2.4437 | 2.3911 | 2.3374 | 2.2868 | 2.2384 | 1.9953 | 1.3184 | 0.67632 | 1.9016 | 1.8679 | 1.8332 | 1.8037 | 1.7711 | 1.7216 | 1.6711 | 1.6216 | 1.5732 | 1.5237 | 1.2953 | 0.55526 | -0.13842 | 1.9174 | 1.8868 | 1.8542 | 1.8268 | 1.7963 | 1.7437 | 1.6889 | 1.6342 | 1.5816 | 1.53 | 1.2763 | 0.51526 | -0.20474
BRAMLEY (FLEE) | BURGHFIELD MAIN | COURAGES | MINIMUM HEADROOM | SU 70990 69570 | YES | 2.2295 | 31.8174 | 31.7689 | 31.7184 | 31.6668 | 31.5353 | 29.2058 | 28.6205 | 28.0416 | 27.4384 | 27.2247 | 26.7784 | 26.2658 | -20.3837 | 27.9026 | 27.8511 | 27.7974 | 27.4321 | 26.8289 | 24.7805 | 24.0553 | 23.3363 | 22.6321 | 22.3889 | 21.8953 | 21.3174 | 20.7384 | 28.6795 | 28.6279 | 28.5742 | 28.4942 | 27.9321 | 25.4921 | 24.7932 | 24.0774 | 23.3742 | 23.1311 | 22.6384 | 22.0605 | 21.4826
|  | COURAGES | EE |  |  |  | 31.8363 | 31.7974 | 31.7563 | 31.7132 | 31.6574 | 29.3595 | 28.7911 | 28.2289 | 27.6521 | 27.4626 | 27.1532 | 26.7847 | 26.4237 | 27.9226 | 27.8816 | 27.8384 | 27.5479 | 26.9668 | 24.9521 | 24.25 | 23.5511 | 22.8689 | 22.6521 | 22.3142 | 21.8974 | 21.4868 | 28.6995 | 28.6584 | 28.6153 | 28.5447 | 28.0689 | 25.6637 | 24.9826 | 24.2921 | 23.61 | 23.3942 | 23.0563 | 22.6405 | 22.2311
|  | COURAGES | HT |  |  |  | 31.8174 | 31.7689 | 31.7184 | 31.6668 | 31.5353 | 29.2058 | 28.6205 | 28.0416 | 27.4384 | 27.2247 | 26.7784 | 26.2658 | 25.7574 | 27.9026 | 27.8511 | 27.7974 | 27.4321 | 26.8289 | 24.7805 | 24.0553 | 23.3363 | 22.6321 | 22.3889 | 21.8953 | 21.3174 | 20.7384 | 28.6795 | 28.6279 | 28.5742 | 28.4942 | 27.9321 | 25.4921 | 24.7932 | 24.0774 | 23.3742 | 23.1311 | 22.6384 | 22.0605 | 21.4826
|  | COURAGES | HE |  |  |  | 31.8584 | 31.83 | 31.7974 | 31.7637 | 31.7247 | 30.3689 | 29.8184 | 29.2784 | 28.7511 | 28.5911 | 28.3868 | 28.11 | -20.3837 | 27.9468 | 27.9163 | 27.8826 | 27.6711 | 27.1111 | 25.7921 | 25.1058 | 24.4321 | 23.7742 | 23.5795 | 23.3479 | 23.0342 | 22.7026 | 28.7237 | 28.6932 | 28.6595 | 28.5995 | 28.2121 | 26.6889 | 26.0279 | 25.3774 | 24.7447 | 24.5553 | 24.3268 | 24.0132 | 23.6826
|  | COURAGES | CF |  |  |  | 31.8711 | 31.8532 | 31.8342 | 31.8142 | 31.7953 | 31.7742 | 31.7532 | 31.5332 | 31.2468 | 31.15 | 30.9774 | 30.8458 | 30.7111 | 27.9595 | 27.9405 | 27.9205 | 27.8889 | 27.7363 | 27.4479 | 27.1321 | 26.7974 | 26.4458 | 26.3311 | 26.1395 | 25.9879 | 25.8258 | 28.7363 | 28.7174 | 28.6974 | 28.6658 | 28.6332 | 28.5426 | 28.2321 | 27.9047 | 27.5595 | 27.4468 | 27.2563 | 27.1068 | 26.9479
BRAMLEY (FLEE) | CAMBERLEY RESERVE | COVE | MINIMUM HEADROOM | SU 85415 55937 | YES | 0 | 26.3863 | 26.1526 | 25.9168 | 25.2053 | 24.3389 | 23.32 | 22.5063 | 21.6842 | 20.9705 | 20.28 | 17.1053 | 22.8968 | 0.10211 | 24.1232 | 23.5284 | 22.5011 | 21.6979 | 20.7253 | 19.5758 | 18.6684 | 17.7442 | 16.9442 | 16.1663 | 12.5789 | 11.0305 | 9.4895 | 24.6358 | 24.0674 | 23.0968 | 22.2947 | 21.3221 | 20.1726 | 19.2642 | 18.3389 | 17.5389 | 16.7621 | 13.1716 | 18.3632 | 17.5221
|  | COVE | EE |  |  |  | 26.4758 | 26.2916 | 26.0979 | 25.6568 | 24.8695 | 23.9316 | 23.2105 | 22.4484 | 21.7884 | 21.1526 | 27.9474 | 26.7589 | 25.7179 | 24.32 | 23.8337 | 22.8968 | 22.1884 | 21.3021 | 20.24 | 19.4316 | 18.5726 | 17.8305 | 17.1147 | 27.4232 | 26.9979 | 26.4316 | 24.7442 | 24.3611 | 23.4779 | 22.7853 | 21.8989 | 20.8358 | 20.0263 | 19.1674 | 18.4274 | 17.7105 | 29.5221 | 29.0926 | 28.7821
|  | COVE | HT |  |  |  | 26.3863 | 26.1526 | 25.9168 | 25.2053 | 24.3389 | 23.32 | 22.5063 | 21.6842 | 20.9705 | 20.28 | 17.1053 | 24.6232 | 24.0684 | 24.1232 | 23.5284 | 22.5011 | 21.6979 | 20.7253 | 19.5758 | 18.6684 | 17.7442 | 16.9442 | 16.1663 | 12.5789 | 11.0305 | 9.4895 | 24.6358 | 24.0674 | 23.0968 | 22.2947 | 21.3221 | 20.1726 | 19.2642 | 18.3389 | 17.5389 | 16.7621 | 13.1716 | 18.3632 | 17.5221
|  | COVE | HE |  |  |  | 26.6011 | 26.4779 | 26.34 | 26.1884 | 25.5779 | 24.7368 | 24.1126 | 23.4442 | 22.8789 | 22.3379 | 27.4505 | 27.2032 | 0.10211 | 24.4926 | 24.2432 | 23.4305 | 22.8432 | 22.0726 | 21.1158 | 20.4116 | 19.6558 | 19.0168 | 18.4042 | 17.4642 | 16.7558 | 16.1642 | 24.8895 | 24.7358 | 23.9905 | 23.4347 | 22.6695 | 21.7126 | 21.0084 | 20.2505 | 19.6126 | 18.9989 | 21.3179 | 20.8589 | 20.5053
|  | COVE | CF |  |  |  | 26.6737 | 26.6042 | 26.5326 | 26.4579 | 26.3811 | 26.3011 | 26.1611 | 25.8084 | 25.4842 | 25.1421 | 23.4695 | 22.8968 | 22.4274 | 24.5926 | 24.48 | 24.1442 | 23.8568 | 23.4989 | 23.0758 | 22.7232 | 22.3242 | 21.9558 | 21.5695 | 19.6684 | 19.0253 | 18.4916 | 24.9737 | 24.8853 | 24.6663 | 24.3937 | 24.0568 | 23.6589 | 23.3211 | 22.9211 | 22.5537 | 22.1663 | 20.2642 | 19.6221 | 19.0874
FAWLEY GSP | COWES & WOOTTON COMMON BSP | COWES | MINIMUM HEADROOM | SP 56113 03074 | YES | 0.47368 | 35.9811 | 35.3758 | 34.2453 | 33.08 | 31.7411 | 31.84 | 30.6158 | 29.5368 | 28.4116 | 27.2674 | 26.6568 | 29.4674 | -15.5789 | 28.8758 | 27.5326 | 26.2663 | 24.9632 | 23.4568 | 23.5716 | 22.2137 | 21.0274 | 19.7863 | 18.5126 | 17.7558 | 20.8221 | 19.1642 | 29.9874 | 28.6284 | 27.3621 | 26.06 | 24.5558 | 24.6621 | 23.3 | 22.1063 | 20.8558 | 19.5737 | 18.8105 | 21.8937 | 20.2242
|  | COWES | EE |  |  |  | 36.1547 | 35.7884 | 35.1484 | 34.2189 | 33.1 | 31.84 | 30.6158 | 29.5368 | 28.4116 | 27.2674 | 103.5968 | 102.4547 | 101.7347 | 29.2684 | 28.2653 | 27.2842 | 26.2474 | 24.9874 | 23.5716 | 22.2137 | 21.0274 | 19.7863 | 18.5126 | 121.4063 | 120.4042 | 119.7274 | 30.3863 | 29.3621 | 28.3789 | 27.3432 | 26.0832 | 24.6621 | 23.3 | 22.1063 | 20.8558 | 19.5737 | 113.2853 | 112.1547 | 111.0421
|  | COWES | HT |  |  |  | 35.9811 | 35.3758 | 34.2453 | 33.08 | 31.7411 | 106.22 | 105.6653 | 105.1737 | 104.72 | 104.3 | 102.5284 | 101.1284 | 100.1011 | 28.8758 | 27.5326 | 26.2663 | 24.9632 | 23.4568 | 123.8432 | 123.2979 | 122.8179 | 122.3768 | 121.9695 | 120.2842 | 118.9853 | 115.9158 | 29.9874 | 28.6284 | 27.3621 | 26.06 | 24.5558 | 115.8916 | 115.3379 | 114.8463 | 114.3947 | 113.9758 | 112.2116 | 110.3705 | 105.9547
|  | COWES | HE |  |  |  | 36.4 | 36.1484 | 35.8705 | 35.3811 | 34.4684 | 33.3958 | 32.4042 | 31.5337 | 30.6347 | 29.7021 | 26.6568 | 104.7979 | -15.5789 | 29.8063 | 29.0526 | 28.3305 | 27.5295 | 26.4958 | 25.2821 | 24.1611 | 23.1958 | 22.1937 | 21.1453 | 17.7558 | 122.5358 | 122.1905 | 30.9337 | 30.1632 | 29.4274 | 28.6242 | 27.5926 | 26.3758 | 25.2526 | 24.2842 | 23.2779 | 22.2263 | 18.8105 | 114.48 | 114.1011
|  | COWES | CF |  |  |  | 36.5432 | 36.4 | 36.2516 | 36.0979 | 35.9389 | 35.7663 | 35.5558 | 35.1105 | 34.6379 | 34.1147 | 31.1621 | 29.4674 | 28.0137 | 30.3147 | 29.9084 | 29.5695 | 29.2 | 28.7621 | 28.2674 | 27.7411 | 27.2411 | 26.7074 | 26.1126 | 22.7389 | 20.8221 | 19.1642 | 31.4189 | 31.0389 | 30.6937 | 30.3168 | 29.8705 | 29.3642 | 28.8316 | 28.3305 | 27.7958 | 27.2 | 23.8211 | 21.8937 | 20.2242
COWLEY GSP | COWLEY LOCAL (2 X 90) | COWLEY LOCAL | MINIMUM HEADROOM | SP 56113 03074 | YES | 0.53158 | 37.5484 | 87.1537 | 86.7516 | 86.3274 | 85.8842 | 85.7421 | 83.4074 | 81.4779 | 79.8979 | 78.6158 | 74.1432 | 70.5063 | 19.8221 | 31.0084 | 79.1295 | 78.3663 | 77.58 | 76.4179 | 75.2326 | 72.3768 | 70.1368 | 68.3168 | 66.8505 | 61.8895 | 57.8642 | 55.5442 | 32.0537 | 80.9589 | 80.1968 | 79.4084 | 78.2474 | 77.0084 | 74.1937 | 71.9463 | 70.12 | 68.6463 | 63.6063 | 59.5368 | 57.0168
|  | COWLEY LOCAL | EE |  |  |  | 37.6895 | 87.3747 | 87.04 | 86.6821 | 86.3063 | 85.9032 | 83.4074 | 81.4779 | 79.8979 | 78.6158 | 75.2611 | 72.1989 | 70.5453 | 31.1884 | 80.0674 | 79.1432 | 78.3421 | 77.2126 | 75.6274 | 72.3768 | 70.1368 | 68.3168 | 66.8505 | 64.08 | 60.6674 | 58.8432 | 32.2063 | 81.8347 | 80.9716 | 80.1716 | 79.0411 | 77.4505 | 74.1937 | 71.9463 | 70.12 | 68.6463 | 66.3095 | 62.8358 | 60.9937
|  | COWLEY LOCAL | HT |  |  |  | 37.5484 | 87.1537 | 86.7516 | 86.3274 | 85.8842 | 85.7421 | 85.2821 | 83.78 | 82.3579 | 80.9968 | 74.1432 | 70.5063 | 68.2295 | 31.0084 | 79.1295 | 78.3663 | 77.58 | 76.4179 | 75.2326 | 74.7589 | 73.0421 | 71.4147 | 69.8558 | 61.8895 | 57.8642 | 55.5442 | 32.0537 | 80.9589 | 80.1968 | 79.4084 | 78.2474 | 77.0084 | 76.5305 | 74.8084 | 73.1747 | 71.6095 | 63.6063 | 59.5368 | 57.0168
|  | COWLEY LOCAL | HE |  |  |  | 37.8842 | 87.6589 | 87.4095 | 87.1347 | 86.8358 | 86.5084 | 84.8358 | 83.0589 | 81.7189 | 80.6147 | 75.5558 | 73.4021 | 19.8221 | 31.4168 | 80.7242 | 79.9979 | 79.4 | 78.4705 | 77.0716 | 73.9505 | 71.8737 | 70.32 | 69.0421 | 63.2968 | 60.8642 | 59.8726 | 32.4158 | 82.14 | 81.8284 | 81.2295 | 80.3011 | 78.8979 | 75.7726 | 73.6926 | 72.1347 | 70.8537 | 64.8568 | 62.4105 | 61.4021
|  | COWLEY LOCAL | CF |  |  |  | 38.0021 | 87.8684 | 87.7305 | 87.5863 | 87.4379 | 87.2789 | 87.1168 | 86.9558 | 86.7979 | 86.64 | 81.7284 | 80.5895 | 79.9189 | 31.5389 | 81.3663 | 81.2137 | 81.0137 | 80.5916 | 79.9705 | 79.2926 | 78.4558 | 77.3653 | 76.1905 | 70.2695 | 68.9937 | 68.2432 | 32.5358 | 82.3842 | 82.24 | 82.0884 | 81.9242 | 81.7389 | 81.1189 | 80.2811 | 79.1884 | 78.0126 | 72.0832 | 70.7484 | 69.9884
BRAMLEY (FLEE) | COXMOOR WOOD BSP | COXMOOR WOOD | MINIMUM HEADROOM | SU 78275 50779 | YES | 0.34211 | 15.2789 | 15.1379 | 14.9958 | 14.8442 | 14.6895 | 14.5158 | 14.2316 | 13.7653 | 13.6189 | 13.3295 | 11.9484 | 10.3674 | 0.057895 | 13.4737 | 13.0295 | 12.6653 | 12.3611 | 12.0305 | 11.6874 | 11.3158 | 10.7989 | 10.6568 | 10.3432 | 8.8526 | 7.1147 | 5.6516 | 14.3032 | 13.9042 | 13.5411 | 13.2358 | 12.9053 | 12.5579 | 12.1821 | 11.6611 | 11.5137 | 11.1958 | 9.6716 | 7.8958 | 6.4168
|  | COXMOOR WOOD | EE |  |  |  | 15.3337 | 15.2242 | 15.1063 | 14.9821 | 14.8526 | 14.7063 | 14.5589 | 14.4179 | 14.1895 | 13.9421 | 12.7684 | 11.4453 | 10.3537 | 13.5958 | 13.2137 | 12.9053 | 12.6705 | 12.4126 | 12.1411 | 11.8442 | 11.5747 | 11.2905 | 11.0295 | 9.7895 | 8.3611 | 7.1326 | 14.3579 | 14.0895 | 13.78 | 13.5453 | 13.2874 | 13.0116 | 12.7105 | 12.4337 | 12.1442 | 11.8747 | 10.5884 | 9.1063 | 7.8611
|  | COXMOOR WOOD | HT |  |  |  | 15.2789 | 15.1379 | 14.9958 | 14.8442 | 14.6895 | 14.5158 | 14.2316 | 13.7653 | 13.6189 | 13.3295 | 11.9484 | 10.3674 | 9.0632 | 13.4737 | 13.0295 | 12.6653 | 12.3611 | 12.0305 | 11.6874 | 11.3158 | 10.7989 | 10.6568 | 10.3432 | 8.8526 | 7.1147 | 5.6516 | 14.3032 | 13.9042 | 13.5411 | 13.2358 | 12.9053 | 12.5579 | 12.1821 | 11.6611 | 11.5137 | 11.1958 | 9.6716 | 7.8958 | 6.4168
|  | COXMOOR WOOD | HE |  |  |  | 15.4095 | 15.3358 | 15.2558 | 15.1663 | 15.0684 | 14.9558 | 14.8484 | 14.7453 | 14.6484 | 14.5632 | 13.9137 | 12.9884 | 0.057895 | 13.7611 | 13.4579 | 13.2274 | 13.0663 | 12.8758 | 12.6737 | 12.4484 | 12.2474 | 12.0368 | 11.8474 | 10.9832 | 9.9432 | 8.9726 | 14.4337 | 14.3337 | 14.1032 | 13.9421 | 13.7516 | 13.5453 | 13.3189 | 13.1147 | 12.9011 | 12.7074 | 11.8253 | 10.7695 | 9.7853
|  | COXMOOR WOOD | CF |  |  |  | 15.4526 | 15.4116 | 15.3695 | 15.3253 | 15.28 | 15.2284 | 15.1747 | 15.1242 | 15.0716 | 15.0211 | 14.7884 | 14.5053 | 13.9695 | 13.8842 | 13.7137 | 13.5874 | 13.5021 | 13.4063 | 13.3053 | 13.1895 | 13.0811 | 12.9621 | 12.8421 | 12.2558 | 11.5947 | 10.9863 | 14.4768 | 14.4358 | 14.3937 | 14.3495 | 14.2821 | 14.18 | 14.0621 | 13.9537 | 13.8316 | 13.7116 | 13.1189 | 12.4495 | 11.8326
MANNINGTON GSP | LYTCHETT | CREEKMOOR | MINIMUM HEADROOM | SZ 00552 94121 | YES | 0.11579 | 34.2558 | 33.9295 | 33.6011 | 33.2516 | 32.8926 | 32.3832 | 31.7611 | 31.1653 | 30.5495 | 29.9421 | 27.26 | 24.8558 | -0.57368 | 29.9611 | 29.2516 | 28.6158 | 27.7084 | 27.0568 | 26.3926 | 25.6758 | 24.9768 | 24.3011 | 23.6484 | 20.7495 | 18.0705 | 15.6168 | 31.0168 | 30.3242 | 29.7021 | 28.8189 | 28.1811 | 27.5295 | 26.8274 | 26.1442 | 25.4853 | 24.8411 | 21.8842 | 19.2042 | 16.7537
|  | CREEKMOOR | EE |  |  |  | 34.3842 | 34.1305 | 33.8621 | 33.5768 | 33.28 | 32.9716 | 32.6758 | 32.2042 | 31.7274 | 31.2768 | 29.2158 | 27.3526 | 25.6958 | 30.2411 | 29.6905 | 29.1937 | 28.5484 | 27.9305 | 27.3474 | 26.7674 | 26.1916 | 25.6379 | 25.1063 | 22.8558 | 20.8168 | 18.9421 | 31.2558 | 30.7537 | 30.2663 | 29.6368 | 29.0326 | 28.4621 | 27.8937 | 27.3316 | 26.7895 | 26.2705 | 24.0295 | 21.9453 | 20.0726
|  | CREEKMOOR | HT |  |  |  | 34.2558 | 33.9295 | 33.6011 | 33.2516 | 32.8926 | 32.3832 | 31.7611 | 31.1653 | 30.5495 | 29.9421 | 27.26 | 24.8558 | 22.6737 | 29.9611 | 29.2516 | 28.6158 | 27.7084 | 27.0568 | 26.3926 | 25.6758 | 24.9768 | 24.3011 | 23.6484 | 20.7495 | 18.0705 | 15.6168 | 31.0168 | 30.3242 | 29.7021 | 28.8189 | 28.1811 | 27.5295 | 26.8274 | 26.1442 | 25.4853 | 24.8411 | 21.8842 | 19.2042 | 16.7537
|  | CREEKMOOR | HE |  |  |  | 34.5589 | 34.3884 | 34.2011 | 33.9926 | 33.7695 | 33.5295 | 33.3021 | 33.0874 | 32.8863 | 32.7116 | 31.4611 | 30.1811 | -0.57368 | 30.6179 | 30.2453 | 29.9179 | 29.4326 | 28.9747 | 28.5421 | 28.0989 | 27.6558 | 27.2663 | 26.8695 | 25.2705 | 23.8463 | 22.5884 | 31.4421 | 31.26 | 30.9737 | 30.5 | 30.0526 | 29.6295 | 29.1947 | 28.7611 | 28.38 | 27.9926 | 26.4368 | 25.0274 | 23.7358
|  | CREEKMOOR | CF |  |  |  | 34.6632 | 34.5695 | 34.4716 | 34.3716 | 34.2674 | 34.1589 | 34.0474 | 33.94 | 33.8337 | 33.7253 | 33.2474 | 32.7011 | 32.0295 | 30.7274 | 30.6337 | 30.4589 | 30.2726 | 30.0853 | 29.8705 | 29.6242 | 29.3579 | 29.0737 | 28.7979 | 27.6242 | 26.6463 | 25.8 | 31.5463 | 31.4526 | 31.3505 | 31.2453 | 31.1358 | 30.9263 | 30.6853 | 30.4263 | 30.1505 | 29.8811 | 28.7368 | 27.7916 | 26.9768
MINETY GSP | CIRENCESTER BSP | CRICKLADE | MINIMUM HEADROOM | SU 09400 93270 | YES | 0.30421 | 17.4316 | 17.5263 | 17.7558 | 17.4737 | 17.1947 | 16.9147 | 16.5158 | 15.8789 | 15.3253 | 15.1895 | 13.9421 | 12.42 | -1.8042 | 14.8968 | 14.5821 | 14.2874 | 13.9863 | 13.6884 | 13.3916 | 12.9558 | 12.2379 | 11.6147 | 11.48 | 10.1926 | 8.4884 | 7.4842 | 15.7 | 15.3789 | 15.0842 | 14.7832 | 14.4853 | 14.1874 | 13.7505 | 13.0305 | 12.4053 | 12.2695 | 10.9021 | 9.1884 | 8.24
|  | CRICKLADE | EE |  |  |  | 17.4316 | 18.2158 | 17.9958 | 17.7747 | 17.5474 | 17.3179 | 17.0958 | 16.8811 | 16.6747 | 16.4853 | 15.5463 | 12.5695 | 11.6505 | 14.8968 | 14.7853 | 14.5495 | 14.3126 | 14.0716 | 13.8284 | 13.5937 | 13.3684 | 13.1526 | 12.9526 | 11.9432 | 8.5211 | 7.4842 | 15.7053 | 15.5821 | 15.3453 | 15.1084 | 14.8674 | 14.6242 | 14.3884 | 14.1611 | 13.9421 | 13.74 | 12.7189 | 9.2811 | 8.24
|  | CRICKLADE | HT |  |  |  | 18.3263 | 18.0295 | 17.7558 | 17.4737 | 17.1947 | 16.9147 | 16.5158 | 15.8789 | 15.3253 | 15.1895 | 13.9421 | 12.42 | 11.9126 | 14.9032 | 14.5821 | 14.2874 | 13.9863 | 13.6884 | 13.3916 | 12.9558 | 12.2379 | 11.6147 | 11.48 | 10.1926 | 8.4884 | 7.9526 | 15.7 | 15.3789 | 15.0842 | 14.7832 | 14.4853 | 14.1874 | 13.7505 | 13.0305 | 12.4053 | 12.2695 | 10.9021 | 9.1884 | 8.6484
|  | CRICKLADE | HE |  |  |  | 17.5221 | 18.4653 | 18.3253 | 18.1747 | 18.0189 | 17.8547 | 17.6979 | 17.5495 | 17.4084 | 17.2842 | 16.6705 | 13.96 | -1.8042 | 15.0674 | 15.0558 | 14.9063 | 14.7474 | 14.5821 | 14.4105 | 14.2474 | 14.0916 | 13.9453 | 13.8137 | 13.1505 | 10.0042 | 9.1863 | 15.8011 | 15.8526 | 15.7032 | 15.5442 | 15.3789 | 15.2074 | 15.0421 | 14.8863 | 14.7379 | 14.6074 | 13.9379 | 10.7863 | 9.9632
|  | CRICKLADE | CF |  |  |  | 17.5747 | 17.5263 | 18.5411 | 18.4547 | 18.3684 | 18.2716 | 18.1705 | 18.0789 | 17.9884 | 17.9 | 17.4926 | 17.1074 | 16.7053 | 15.1632 | 15.0716 | 15.1379 | 15.0453 | 14.9526 | 14.8495 | 14.7379 | 14.6411 | 14.5453 | 14.4505 | 14.0147 | 13.5874 | 13.1295 | 15.8579 | 15.8053 | 15.9347 | 15.8421 | 15.7495 | 15.6453 | 15.5347 | 15.4368 | 15.34 | 15.2453 | 14.8074 | 14.3768 | 13.9179
MELKSHAM GSP | FROME BSP | CROCKERTON | MINIMUM HEADROOM | ST 87736 43371 | YES | 0.55789 | 16.7484 | 16.5 | 16.2495 | 15.9821 | 15.7074 | 15.42 | 15.1305 | 14.8758 | 14.6432 | 14.28 | 12.2263 | 10.1 | -8.6684 | 13.6442 | 13.1684 | 12.5884 | 11.9716 | 11.4232 | 10.9411 | 10.4663 | 10.0284 | 9.6253 | 9.1958 | 6.8958 | 4.54 | 2.2053 | 14.2063 | 13.9442 | 13.5884 | 12.9663 | 12.4095 | 11.92 | 11.4379 | 10.9937 | 10.5842 | 10.1453 | 7.7937 | 5.3726 | 2.9768
|  | CROCKERTON | EE |  |  |  | 16.8432 | 16.6484 | 16.4421 | 16.2221 | 15.9926 | 15.7516 | 15.5179 | 15.2958 | 15.0811 | 14.8863 | 13.5989 | 11.9537 | 10.3211 | 13.8547 | 13.4905 | 13.0558 | 12.5895 | 12.0674 | 11.6105 | 11.2053 | 10.8326 | 10.4726 | 10.1505 | 8.4316 | 6.5884 | 4.7474 | 14.3011 | 14.1021 | 13.8821 | 13.5853 | 13.0653 | 12.6011 | 12.1874 | 11.8074 | 11.4421 | 11.1137 | 9.3495 | 7.4495 | 5.5558
|  | CROCKERTON | HT |  |  |  | 16.7484 | 16.5 | 16.2495 | 15.9821 | 15.7074 | 15.42 | 15.1305 | 14.8758 | 14.6432 | 14.28 | 12.2263 | 10.1 | 8.0232 | 13.6442 | 13.1684 | 12.5884 | 11.9716 | 11.4232 | 10.9411 | 10.4663 | 10.0284 | 9.6253 | 9.1958 | 6.8958 | 4.54 | 2.2053 | 14.2063 | 13.9442 | 13.5884 | 12.9663 | 12.4095 | 11.92 | 11.4379 | 10.9937 | 10.5842 | 10.1453 | 7.7937 | 5.3726 | 2.9768
|  | CROCKERTON | HE |  |  |  | 16.9747 | 16.8421 | 16.6968 | 16.5347 | 16.3611 | 16.1716 | 15.9916 | 15.8211 | 15.6621 | 15.5253 | 15.0495 | 14.1768 | -8.6684 | 14.0232 | 13.8905 | 13.6074 | 13.2621 | 12.8642 | 12.5179 | 12.2295 | 11.9653 | 11.7158 | 11.5042 | 10.3232 | 8.9916 | 7.6021 | 14.4337 | 14.3011 | 14.1558 | 13.9832 | 13.7958 | 13.5158 | 13.2305 | 12.9632 | 12.7105 | 12.4958 | 11.2863 | 9.9179 | 8.4863
|  | CROCKERTON | CF |  |  |  | 17.0526 | 16.9789 | 16.9021 | 16.8221 | 16.74 | 16.6537 | 16.5642 | 16.4779 | 16.3916 | 16.3063 | 15.9211 | 15.7232 | 15.3305 | 14.1011 | 14.0274 | 13.9505 | 13.8558 | 13.7063 | 13.5326 | 13.3463 | 13.1695 | 12.9758 | 12.78 | 11.8768 | 11.1032 | 10.2158 | 14.5116 | 14.4379 | 14.3611 | 14.2811 | 14.1989 | 14.1105 | 14.0158 | 13.9242 | 13.8316 | 13.7389 | 12.8674 | 12.0737 | 11.16
BRAMLEY (FLEE) | PYESTOCK BSP | CROOKHAM | MINIMUM HEADROOM | SU 81702 53403 | YES | 0.077895 | 32.5895 | 32.2474 | 31.9032 | 31.3684 | 30.6853 | 30.0042 | 29.2884 | 28.6547 | 28.0326 | 27.4495 | 24.7937 | 22.0674 | 6.6526 | 29.4211 | 28.7758 | 28.14 | 27.4474 | 26.72 | 25.9968 | 25.2347 | 24.5589 | 23.8926 | 23.2684 | 20.3989 | 17.4084 | 14.6568 | 30.2495 | 29.6084 | 28.9695 | 28.2663 | 27.5284 | 26.7937 | 26.02 | 25.3326 | 24.6547 | 24.0179 | 21.0905 | 18.0263 | 15.2063
|  | CROOKHAM | EE |  |  |  | 32.7326 | 32.4716 | 32.1958 | 31.9011 | 31.5347 | 30.9989 | 30.4421 | 29.9284 | 29.4063 | 28.9326 | 26.8779 | 24.7505 | 22.8389 | 29.72 | 29.2295 | 28.7284 | 28.1968 | 27.6284 | 27.0621 | 26.4695 | 25.9242 | 25.3674 | 24.8611 | 22.6463 | 20.3084 | 18.1853 | 30.5147 | 30.06 | 29.56 | 29.0284 | 28.4516 | 27.8768 | 27.2747 | 26.72 | 26.1537 | 25.6379 | 23.3747 | 20.9737 | 18.7947
|  | CROOKHAM | HT |  |  |  | 32.5895 | 32.2474 | 31.9032 | 31.3684 | 30.6853 | 30.0042 | 29.2884 | 28.6547 | 28.0326 | 27.4495 | 24.7937 | 22.0674 | 19.5779 | 29.4211 | 28.7758 | 28.14 | 27.4474 | 26.72 | 25.9968 | 25.2347 | 24.5589 | 23.8926 | 23.2684 | 20.3989 | 17.4084 | 14.6568 | 30.2495 | 29.6084 | 28.9695 | 28.2663 | 27.5284 | 26.7937 | 26.02 | 25.3326 | 24.6547 | 24.0179 | 21.0905 | 18.0263 | 15.2063
|  | CROOKHAM | HE |  |  |  | 32.92 | 32.7484 | 32.5589 | 32.3495 | 32.1242 | 31.8821 | 31.6505 | 31.3758 | 30.9895 | 30.6495 | 29.2232 | 27.6779 | 6.6526 | 30.1158 | 29.8137 | 29.4926 | 29.1347 | 28.7316 | 28.3168 | 27.8737 | 27.4716 | 27.06 | 26.6947 | 25.1526 | 23.4358 | 21.8737 | 30.8158 | 30.5916 | 30.3 | 29.9653 | 29.5632 | 29.1484 | 28.7032 | 28.2937 | 27.8758 | 27.5053 | 25.9295 | 24.1663 | 22.5589
|  | CROOKHAM | CF |  |  |  | 33.0242 | 32.9305 | 32.8337 | 32.7326 | 32.6284 | 32.5189 | 32.4095 | 32.3 | 32.1916 | 32.0832 | 31.1758 | 30.1263 | 29.2137 | 30.3084 | 30.1253 | 29.9358 | 29.74 | 29.5284 | 29.3126 | 29.0758 | 28.8505 | 28.6095 | 28.3705 | 27.2179 | 26.0537 | 25.0305 | 30.9263 | 30.8263 | 30.7063 | 30.5305 | 30.3421 | 30.1432 | 29.9063 | 29.6832 | 29.4432 | 29.2 | 28.0263 | 26.8316 | 25.7789
BRAMLEY (FLEE) | CAMBERLEY MAIN | CROWTHORNE | MINIMUM HEADROOM | SU 84470 64352 | YES | 0.43053 | 36.3958 | 35.2389 | 33.78 | 32.0968 | 30.2642 | 28.5126 | 27.1063 | 25.9726 | 25.0979 | 24.2958 | 20.6684 | 17.1095 | -16.7368 | 29.0442 | 26.7032 | 25.1179 | 23.2316 | 21.1726 | 19.2126 | 17.66 | 16.4147 | 15.4684 | 14.6011 | 10.6495 | 6.7053 | 3.0874 | 30.6032 | 28.2621 | 26.6358 | 24.7516 | 22.6958 | 20.7368 | 19.1842 | 17.9389 | 16.9905 | 16.1211 | 12.1579 | 8.2 | 4.58
|  | CROWTHORNE | EE |  |  |  | 36.3958 | 35.9726 | 34.66 | 33.1937 | 31.5642 | 29.9305 | 28.6842 | 27.7032 | 27 | 26.3684 | 23.7316 | 21.0916 | 18.7484 | 29.4832 | 27.5084 | 26.0379 | 24.4305 | 22.5916 | 20.7526 | 19.3674 | 18.2905 | 17.5379 | 16.8632 | 14.0221 | 11.1063 | 8.4695 | 31.0421 | 29.0674 | 27.5958 | 25.9495 | 24.1126 | 22.2747 | 20.8884 | 19.8105 | 19.0547 | 18.3779 | 15.5158 | 12.5789 | 9.9368
|  | CROWTHORNE | HT |  |  |  | 37.3053 | 35.2389 | 33.78 | 32.0968 | 30.2642 | 28.5126 | 27.1063 | 25.9726 | 25.0979 | 24.2958 | 20.6684 | 17.1095 | 13.8832 | 29.0442 | 26.7032 | 25.1179 | 23.2316 | 21.1726 | 19.2126 | 17.66 | 16.4147 | 15.4684 | 14.6011 | 10.6495 | 6.7053 | 3.0874 | 30.6032 | 28.2621 | 26.6358 | 24.7516 | 22.6958 | 20.7368 | 19.1842 | 17.9389 | 16.9905 | 16.1211 | 12.1579 | 8.2 | 4.58
|  | CROWTHORNE | HE |  |  |  | 36.6642 | 36.4158 | 35.6905 | 34.46 | 33.0505 | 31.6337 | 30.5916 | 29.8189 | 29.3274 | 28.8884 | 27.1811 | 25.4158 | -16.7368 | 30.0632 | 28.3611 | 27.1568 | 25.8053 | 24.2042 | 22.6021 | 21.4358 | 20.5853 | 20.0621 | 19.5926 | 17.7484 | 15.7695 | 13.9558 | 31.6326 | 29.92 | 28.7158 | 27.3232 | 25.7242 | 24.1221 | 22.9579 | 22.1063 | 21.5811 | 21.1116 | 19.26 | 17.2758 | 15.46
|  | CROWTHORNE | CF |  |  |  | 36.8168 | 36.6811 | 36.5389 | 36.3905 | 36.1253 | 35.5063 | 34.9568 | 34.4705 | 34.0284 | 33.5905 | 31.8916 | 30.7989 | 29.9253 | 30.7947 | 29.9242 | 29.3337 | 28.6895 | 27.9821 | 27.2705 | 26.6411 | 26.0895 | 25.5895 | 25.0937 | 22.9842 | 21.7674 | 20.7779 | 32.1695 | 31.4895 | 30.8926 | 30.2484 | 29.5411 | 28.8284 | 28.1989 | 27.6463 | 27.1453 | 26.6495 | 24.4989 | 23.2789 | 22.2884
COWLEY GSP |  | CULHAM | MINIMUM HEADROOM | SU 50731 95053 | YES | 0 | 31.1074 | 31.0389 | 30.9832 | 30.9284 | 30.8716 | 30.8716 | 30.8705 | 30.8695 | 30.8684 | 30.8684 | 30.8632 | 30.8589 | 24.8884 | 30.0947 | 30.0137 | 29.9484 | 29.8842 | 29.8179 | 29.8168 | 29.8158 | 29.8147 | 29.8137 | 29.8126 | 29.8074 | 29.8032 | 29.7979 | 30.4284 | 30.3474 | 30.2821 | 30.2179 | 30.1516 | 30.1505 | 30.1495 | 30.1484 | 30.1474 | 30.1463 | 30.1411 | 30.1368 | 30.1316
|  | CULHAM | EE |  |  |  | 31.1084 | 31.04 | 30.9853 | 30.9305 | 30.8747 | 30.8747 | 30.8747 | 30.8747 | 30.8747 | 30.8747 | 30.8737 | 30.8674 | 30.8621 | 30.0958 | 30.0147 | 29.9505 | 29.8863 | 29.8211 | 29.8211 | 29.8211 | 29.8211 | 29.8211 | 29.8211 | 29.82 | 29.8126 | 29.8063 | 30.4284 | 30.3484 | 30.2842 | 30.2189 | 30.1547 | 30.1547 | 30.1547 | 30.1547 | 30.1547 | 30.1547 | 30.1537 | 30.1463 | 30.14
|  | CULHAM | HT |  |  |  | 31.1074 | 31.0389 | 30.9832 | 30.9284 | 30.8716 | 30.8716 | 30.8705 | 30.8695 | 30.8684 | 30.8684 | 30.8632 | 30.8589 | 30.8558 | 30.0947 | 30.0137 | 29.9484 | 29.8842 | 29.8179 | 29.8168 | 29.8158 | 29.8147 | 29.8137 | 29.8126 | 29.8074 | 29.8032 | 29.7979 | 30.4284 | 30.3474 | 30.2821 | 30.2179 | 30.1516 | 30.1505 | 30.1495 | 30.1484 | 30.1474 | 30.1463 | 30.1411 | 30.1368 | 30.1316
|  | CULHAM | HE |  |  |  | 31.1084 | 31.0411 | 30.9874 | 30.9337 | 30.8779 | 30.8779 | 30.8779 | 30.8779 | 30.8779 | 30.8779 | 30.8779 | 30.8779 | 24.8884 | 30.0958 | 30.0158 | 29.9537 | 29.8895 | 29.8253 | 29.8253 | 29.8253 | 29.8253 | 29.8253 | 29.8253 | 29.8253 | 29.8253 | 29.8253 | 30.4284 | 30.3495 | 30.2863 | 30.2232 | 30.1579 | 30.1579 | 30.1579 | 30.1579 | 30.1579 | 30.1579 | 30.1579 | 30.1579 | 30.1579
|  | CULHAM | CF |  |  |  | 31.1379 | 31.1189 | 31.1042 | 31.0895 | 31.0758 | 31.06 | 31.0453 | 31.0305 | 31.0147 | 30.9989 | 30.9821 | 30.98 | 30.9779 | 30.1295 | 30.1084 | 30.0905 | 30.0737 | 30.0568 | 30.0389 | 30.0211 | 30.0032 | 29.9853 | 29.9674 | 29.9474 | 29.9442 | 29.9411 | 30.4632 | 30.4421 | 30.4242 | 30.4074 | 30.3905 | 30.3726 | 30.3547 | 30.3368 | 30.3189 | 30.3 | 30.28 | 30.2779 | 30.2747
EALING GSP | EALING 22kV | DEAN GARDENS | MINIMUM HEADROOM | TQ 16546 80368 | YES | 0.10526 | 11.7663 | 11.68 | 11.5832 | 11.5105 | 11.4326 | 11.3526 | 11.2737 | 11.2021 | 11.1368 | 11.0758 | 10.8095 | 10.5442 | 4.3011 | 11.3284 | 11.0432 | 10.5695 | 10.4158 | 10.2558 | 10.0926 | 9.96 | 9.8368 | 9.7189 | 9.6074 | 9.08 | 8.5358 | 8.0074 | 11.6453 | 11.3789 | 10.8989 | 10.7432 | 10.5821 | 10.4168 | 10.2832 | 10.1589 | 10.04 | 9.9274 | 9.3947 | 8.8505 | 8.3221
|  | DEAN GARDENS | EE |  |  |  | 11.7926 | 11.7221 | 11.64 | 11.5821 | 11.5189 | 11.4537 | 11.3905 | 11.3295 | 11.2684 | 11.2147 | 11.0021 | 10.8411 | 10.7147 | 11.3726 | 11.1411 | 10.7221 | 10.62 | 10.5116 | 10.4021 | 10.3 | 10.2011 | 10.1032 | 10.0137 | 9.6158 | 9.2442 | 8.9 | 11.6684 | 11.4779 | 11.0526 | 10.9495 | 10.8411 | 10.7305 | 10.6274 | 10.5284 | 10.4295 | 10.3389 | 9.9379 | 9.5621 | 9.2147
|  | DEAN GARDENS | HT |  |  |  | 11.7663 | 11.68 | 11.5832 | 11.5105 | 11.4326 | 11.3526 | 11.2737 | 11.2021 | 11.1368 | 11.0758 | 10.8095 | 10.5442 | 10.0716 | 11.3284 | 11.0432 | 10.5695 | 10.4158 | 10.2558 | 10.0926 | 9.96 | 9.8368 | 9.7189 | 9.6074 | 9.08 | 8.5358 | 8.0074 | 11.6453 | 11.3789 | 10.8989 | 10.7432 | 10.5821 | 10.4168 | 10.2832 | 10.1589 | 10.04 | 9.9274 | 9.3947 | 8.8505 | 8.3221
|  | DEAN GARDENS | HE |  |  |  | 11.8189 | 11.7589 | 11.6884 | 11.6379 | 11.5853 | 11.5284 | 11.4747 | 11.4242 | 11.3768 | 11.3358 | 11.1905 | 11.0937 | 4.3011 | 11.42 | 11.22 | 10.84 | 10.7621 | 10.68 | 10.5937 | 10.5158 | 10.4421 | 10.3716 | 10.3095 | 10.0611 | 9.8379 | 9.6453 | 11.6916 | 11.5684 | 11.1726 | 11.0937 | 11.0105 | 10.9242 | 10.8453 | 10.7716 | 10.7 | 10.6379 | 10.3874 | 10.1621 | 9.9674
|  | DEAN GARDENS | CF |  |  |  | 11.8379 | 11.8 | 11.7589 | 11.7284 | 11.6968 | 11.6642 | 11.6326 | 11.6 | 11.5674 | 11.5358 | 11.3916 | 11.3158 | 11.2684 | 11.4768 | 11.3621 | 11.2284 | 11.1863 | 11.1442 | 11.0916 | 11.04 | 10.9863 | 10.9326 | 10.8811 | 10.6326 | 10.4611 | 10.32 | 11.7053 | 11.6789 | 11.5853 | 11.5337 | 11.4821 | 11.4284 | 11.3768 | 11.3232 | 11.2695 | 11.2168 | 10.9663 | 10.7937 | 10.6495
COWLEY GSP | YARNTON BSP | DEDDINGTON | MINIMUM HEADROOM | SP 46729 30325 | YES | 0.047368 | 5.8747 | 5.7326 | 5.5947 | 5.4505 | 5.3042 | 5.1589 | 5.0137 | 4.8811 | 4.7589 | 4.6432 | 2.9621 | 2.7474 | -3.0968 | 4.5368 | 4.3842 | 4.2358 | 4.0811 | 3.9242 | 3.7684 | 3.6137 | 3.4726 | 3.3411 | 3.2168 | 1.2874 | 1.0684 | 0.91263 | 4.4789 | 4.3263 | 4.1779 | 4.0232 | 3.8663 | 3.7105 | 3.5558 | 3.4137 | 3.2821 | 3.1579 | 1.2284 | 1.0095 | 0.85368
|  | DEDDINGTON | EE |  |  |  | 5.9368 | 5.8284 | 5.7158 | 5.6 | 5.4811 | 5.36 | 5.2453 | 5.1337 | 5.0263 | 4.9284 | 4.5442 | 4.0495 | 3.5263 | 4.6053 | 4.4884 | 4.3674 | 4.2432 | 4.1158 | 3.9874 | 3.8642 | 3.7442 | 3.6305 | 3.5253 | 3.1095 | 2.5516 | 1.9547 | 4.5474 | 4.4305 | 4.3095 | 4.1853 | 4.0579 | 3.9284 | 3.8053 | 3.6863 | 3.5726 | 3.4674 | 3.0516 | 2.4937 | 1.8958
|  | DEDDINGTON | HT |  |  |  | 5.8747 | 5.7326 | 5.5947 | 5.4505 | 5.3042 | 5.1589 | 5.0137 | 4.8811 | 4.7589 | 4.6432 | 2.9621 | 2.7474 | 2.5926 | 4.5368 | 4.3842 | 4.2358 | 4.0811 | 3.9242 | 3.7684 | 3.6137 | 3.4726 | 3.3411 | 3.2168 | 1.2874 | 1.0684 | 0.91263 | 4.4789 | 4.3263 | 4.1779 | 4.0232 | 3.8663 | 3.7105 | 3.5558 | 3.4137 | 3.2821 | 3.1579 | 1.2284 | 1.0095 | 0.85368
|  | DEDDINGTON | HE |  |  |  | 5.9874 | 5.9463 | 5.8811 | 5.8021 | 5.7168 | 5.6284 | 5.5453 | 5.4653 | 5.3905 | 5.3211 | 5.0821 | 4.3853 | -3.0968 | 4.6579 | 4.6168 | 4.5474 | 4.4621 | 4.3726 | 4.2779 | 4.1905 | 4.1053 | 4.0253 | 3.9505 | 3.6937 | 2.8895 | 2.8189 | 4.5989 | 4.5579 | 4.4895 | 4.4042 | 4.3147 | 4.22 | 4.1326 | 4.0474 | 3.9663 | 3.8926 | 3.6358 | 2.8305 | 2.7611
|  | DEDDINGTON | CF |  |  |  | 6.0116 | 5.9895 | 5.9663 | 5.9305 | 5.8842 | 5.8389 | 5.7926 | 5.7442 | 5.6968 | 5.6495 | 5.4368 | 5.2337 | 4.9389 | 4.6821 | 4.66 | 4.6368 | 4.5989 | 4.5484 | 4.5 | 4.4484 | 4.3968 | 4.3453 | 4.2947 | 4.0642 | 3.8358 | 3.4947 | 4.6232 | 4.6011 | 4.5779 | 4.5411 | 4.4905 | 4.4421 | 4.3905 | 4.3389 | 4.2874 | 4.2368 | 4.0063 | 3.7779 | 3.4368
IVER 132KV | DENHAM | DENHAM AVENUE | MINIMUM HEADROOM | TQ 03761 86587 | YES | 31.7979 | -18.0716 | -18.2053 | -18.34 | -18.4832 | -18.6316 | 11.2147 | 11.0611 | 10.9253 | 10.8032 | 10.6895 | 9.7474 | 8.8084 | -7.4411 | -20.7895 | -20.9842 | -21.2358 | -21.5 | -21.7684 | 7.9632 | 7.6926 | 7.3663 | 7.1621 | 6.9074 | 5.7074 | 4.6495 | 3.6926 | -20.2305 | -20.3642 | -20.4989 | -20.6421 | -20.8989 | 8.8284 | 8.5547 | 8.2389 | 8.0421 | 7.7958 | 6.5989 | 5.5379 | 4.58
|  | DENHAM AVENUE | EE |  |  |  | -18.0189 | -18.1232 | -18.2326 | -17.2811 | -17.4863 | 12.3032 | 12.0968 | 11.8947 | 11.6842 | 11.4905 | 10.6463 | 9.9179 | 9.28 | -20.7284 | -20.8453 | -21.0137 | -21.1674 | -21.3874 | 8.3874 | 8.2074 | 7.9895 | 7.7632 | 7.5526 | 6.6253 | 5.8126 | 5.0947 | -20.1779 | -20.2821 | -20.3916 | -20.2758 | -20.4958 | 9.2789 | 9.0579 | 8.8411 | 8.6137 | 8.4032 | 7.4758 | 6.6642 | 5.9463
|  | DENHAM AVENUE | HT |  |  |  | -18.0716 | -18.2053 | -18.34 | -18.4832 | -18.6316 | 11.2147 | 11.0611 | 10.9253 | 10.8032 | 10.6895 | 9.7474 | 8.8084 | 7.9674 | -20.7895 | -20.9842 | -21.2358 | -21.5 | -21.7684 | 7.9632 | 7.6926 | 7.3663 | 7.1621 | 6.9074 | 5.7074 | 4.6495 | 3.6926 | -20.2305 | -20.3642 | -20.4989 | -20.6421 | -20.8989 | 8.8284 | 8.5547 | 8.2389 | 8.0421 | 7.7958 | 6.5989 | 5.5379 | 4.58
|  | DENHAM AVENUE | HE |  |  |  | -17.9495 | -18.0211 | -18.1 | -18.1874 | -18.2821 | 11.6179 | 12.5989 | 12.4505 | 12.2947 | 12.1516 | 11.5653 | 11.0779 | -7.4411 | -20.6484 | -20.7263 | -20.8137 | -20.9084 | -21.0284 | 8.8105 | 8.7547 | 8.5958 | 8.4274 | 8.2726 | 7.6274 | 7.0779 | 6.6147 | -20.1084 | -20.18 | -20.2589 | -20.3463 | -20.4411 | 9.4589 | 9.6042 | 9.4463 | 9.2779 | 9.1232 | 8.4779 | 7.9305 | 7.4663
|  | DENHAM AVENUE | CF |  |  |  | -17.9084 | -17.9505 | -17.9916 | -18.0358 | -18.0821 | 11.8716 | 11.8232 | 11.7758 | 11.7284 | 11.6811 | 11.4726 | 11.3695 | 11.3116 | -20.6021 | -20.6495 | -20.6958 | -20.7453 | -20.7968 | 9.1516 | 9.0968 | 9.0116 | 8.9147 | 8.8147 | 8.3442 | 7.9884 | 7.6674 | -20.0674 | -20.1095 | -20.1505 | -20.1947 | -20.2411 | 9.7126 | 9.6642 | 9.6168 | 9.5695 | 9.5221 | 9.2126 | 8.8495 | 8.5453
MELKSHAM GSP | NORRINGTON | DEVIZES | MINIMUM HEADROOM | SU 00106 60986 | YES | 0.33474 | 28.2021 | 46.8947 | 46.5674 | 45.7347 | 44.6737 | 43.5737 | 42.6063 | 41.8295 | 41.2221 | 40.5863 | 37.5979 | 34.2842 | 0.30211 | 21.1411 | 39.2895 | 38.0621 | 36.78 | 35.4074 | 34.1905 | 33.1316 | 32.2884 | 31.64 | 30.9516 | 27.7516 | 24.0621 | 20.4189 | 24.4211 | 42.5705 | 41.3442 | 40.0632 | 38.6916 | 37.4758 | 36.4158 | 35.5705 | 34.92 | 34.2316 | 31.0432 | 27.34 | 23.6937
|  | DEVIZES | EE |  |  |  | 28.2021 | 46.8947 | 46.5674 | 46.22 | 45.3505 | 44.4653 | 43.7105 | 43.0716 | 42.4147 | 42.0505 | 39.5547 | 37.2684 | 34.7453 | 21.3316 | 39.6674 | 38.6147 | 37.5095 | 36.3568 | 35.3505 | 34.5042 | 33.8 | 33.0811 | 32.5568 | 29.8389 | 27.3779 | 24.5168 | 24.7526 | 43.08 | 42.0053 | 40.8758 | 39.6979 | 38.6705 | 37.8074 | 37.0884 | 36.3579 | 35.8316 | 33.0937 | 30.6337 | 27.7695
|  | DEVIZES | HT |  |  |  | 29.7263 | 47.9537 | 46.8695 | 45.7347 | 44.6737 | 43.5737 | 42.6063 | 41.8295 | 41.2221 | 40.5863 | 37.5979 | 34.2842 | 31.0558 | 21.1411 | 39.2895 | 38.0621 | 36.78 | 35.4074 | 34.1905 | 33.1316 | 32.2884 | 31.64 | 30.9516 | 27.7516 | 24.0621 | 20.4189 | 24.4211 | 42.5705 | 41.3442 | 40.0632 | 38.6916 | 37.4758 | 36.4158 | 35.5705 | 34.92 | 34.2316 | 31.0432 | 27.34 | 23.6937
|  | DEVIZES | HE |  |  |  | 28.4053 | 47.1937 | 46.9589 | 46.6989 | 46.42 | 45.7284 | 45.1295 | 44.6337 | 44.1642 | 43.8484 | 42.3442 | 40.5442 | 0.30211 | 21.6495 | 40.3284 | 39.48 | 38.5695 | 37.6032 | 36.7642 | 36.0905 | 35.5411 | 35.02 | 34.6821 | 32.8642 | 30.8263 | 28.7189 | 25.0589 | 43.7505 | 42.8863 | 41.9558 | 40.9663 | 40.1095 | 39.4242 | 38.8632 | 38.3337 | 37.9905 | 36.1379 | 34.0968 | 31.9842
|  | DEVIZES | CF |  |  |  | 28.5253 | 47.4042 | 47.2789 | 47.1484 | 47.0137 | 46.8716 | 46.7274 | 46.5853 | 46.4442 | 46.3032 | 45.4305 | 44.5158 | 43.3326 | 21.7695 | 40.6484 | 40.2884 | 39.8326 | 39.4011 | 39.0116 | 38.6579 | 38.3768 | 38.0779 | 37.7768 | 36.4547 | 35.2389 | 33.8768 | 25.1789 | 44.0579 | 43.7105 | 43.2432 | 42.8032 | 42.4042 | 42.0442 | 41.7589 | 41.4558 | 41.1474 | 39.7326 | 38.5158 | 37.1516
MINETY GSP | TOOTHILL BSP | DORCAN SOUTH | MINIMUM HEADROOM | SU 19288 83540 | YES | 0 | 26.1758 | 26.1158 | 26.0558 | 25.9916 | 25.9253 | 25.8579 | 25.7884 | 25.7284 | 25.6653 | 25.6011 | 25.4979 | 24.8495 | 12.4516 | 23.2811 | 23.1821 | 23.0747 | 22.9642 | 22.8537 | 22.7411 | 22.6232 | 22.5147 | 22.4179 | 22.3284 | 22.1716 | 21.1695 | 20.5147 | 25.1042 | 25.0295 | 24.9547 | 24.8758 | 24.7968 | 24.7158 | 24.6326 | 24.5579 | 24.4895 | 24.4095 | 24.2516 | 23.2389 | 22.5821
|  | DORCAN SOUTH | EE |  |  |  | 26.1968 | 26.1484 | 26.0979 | 26.0453 | 25.9884 | 25.9305 | 25.8737 | 25.8211 | 25.7684 | 25.7211 | 25.4979 | 25.5611 | 25.1211 | 23.3179 | 23.2442 | 23.1642 | 23.0768 | 22.9832 | 22.8916 | 22.8011 | 22.7137 | 22.6232 | 22.5453 | 22.1716 | 22.1389 | 21.6274 | 25.1337 | 25.0737 | 25.0116 | 24.9474 | 24.88 | 24.8116 | 24.7453 | 24.6811 | 24.6179 | 24.5621 | 24.2516 | 24.2242 | 23.7105
|  | DORCAN SOUTH | HT |  |  |  | 26.1758 | 26.1158 | 26.0558 | 25.9916 | 25.9253 | 25.8579 | 25.7884 | 25.7284 | 25.6653 | 25.6011 | 25.6232 | 24.8495 | 24.2726 | 23.2811 | 23.1821 | 23.0747 | 22.9642 | 22.8537 | 22.7411 | 22.6232 | 22.5147 | 22.4179 | 22.3284 | 22.3358 | 21.1695 | 20.5147 | 25.1042 | 25.0295 | 24.9547 | 24.8758 | 24.7968 | 24.7158 | 24.6326 | 24.5579 | 24.4895 | 24.4095 | 24.4221 | 23.2389 | 22.5821
|  | DORCAN SOUTH | HE |  |  |  | 26.2284 | 26.1947 | 26.1579 | 26.1179 | 26.0737 | 26.0274 | 25.9821 | 25.94 | 25.8989 | 25.8663 | 25.7474 | 25.5768 | 12.4516 | 23.3663 | 23.3211 | 23.2737 | 23.2158 | 23.1558 | 23.0905 | 23.0263 | 22.9589 | 22.8663 | 22.8242 | 22.5926 | 22.1832 | 21.7926 | 25.1747 | 25.1347 | 25.0916 | 25.0432 | 24.9926 | 24.94 | 24.8884 | 24.8389 | 24.7821 | 24.7463 | 24.5937 | 24.2621 | 23.8642
|  | DORCAN SOUTH | CF |  |  |  | 26.2463 | 26.2263 | 26.2042 | 26.1832 | 26.1611 | 26.1379 | 26.1137 | 26.0905 | 26.0684 | 26.0442 | 25.9421 | 25.8789 | 25.7716 | 23.3916 | 23.3621 | 23.3337 | 23.3032 | 23.2716 | 23.2358 | 23.2 | 23.1632 | 23.1253 | 23.0853 | 22.9011 | 22.6621 | 22.4105 | 25.1968 | 25.1716 | 25.1453 | 25.1189 | 25.0916 | 25.0632 | 25.0347 | 25.0063 | 24.9789 | 24.9505 | 24.8221 | 24.7074 | 24.4905
CHICKERELL GSP | CHICKERELL BSP | DORCHESTER | MINIMUM HEADROOM | SY 69113 90401 | YES | 0.66421 | 34.8958 | 34.7768 | 46.5516 | 46.1642 | 45.7632 | 45.3263 | 44.8832 | 44.4874 | 44.1211 | 43.7789 | 42.3126 | 40.24 | -14.6253 | 30.3516 | 30.2253 | 45.8653 | 45.4779 | 45.0779 | 44.6526 | 44.1695 | 43.5074 | 42.8821 | 42.2926 | 39.0232 | 35.8484 | 32.6547 | 29.6263 | 29.5074 | 44.6979 | 44.3095 | 43.9095 | 43.4747 | 43.0347 | 42.6421 | 42.28 | 41.8495 | 38.4789 | 35.1853 | 31.9421
|  | DORCHESTER | EE |  |  |  | 47.4084 | 47.1232 | 46.82 | 46.4958 | 46.1568 | 45.7832 | 45.4105 | 45.0516 | 44.6989 | 44.3758 | 43.0684 | 42.0189 | 40.2895 | 46.7211 | 46.4358 | 46.1337 | 45.8116 | 45.4737 | 45.1126 | 44.7568 | 44.4179 | 44.0863 | 43.6453 | 40.8526 | 38.3526 | 35.9347 | 45.5537 | 45.2684 | 44.9653 | 44.6421 | 44.3032 | 43.9316 | 43.5632 | 43.2095 | 42.8611 | 42.5432 | 40.3126 | 37.6874 | 35.1874
|  | DORCHESTER | HT |  |  |  | 47.2768 | 46.9168 | 46.5516 | 46.1642 | 45.7632 | 45.3263 | 44.8832 | 44.4874 | 44.1211 | 43.7789 | 42.3126 | 40.24 | 37.3611 | 46.5895 | 46.2295 | 45.8653 | 45.4779 | 45.0779 | 44.6526 | 44.1695 | 43.5074 | 42.8821 | 42.2926 | 39.0232 | 35.8484 | 32.6547 | 45.4221 | 45.0621 | 44.6979 | 44.3095 | 43.9095 | 43.4747 | 43.0347 | 42.6421 | 42.28 | 41.8495 | 38.4789 | 35.1853 | 31.9421
|  | DORCHESTER | HE |  |  |  | 47.5905 | 47.3905 | 47.1695 | 46.9232 | 46.66 | 46.3611 | 46.0758 | 45.8053 | 45.5495 | 45.3263 | 44.5095 | 43.9832 | -14.6253 | 46.9032 | 46.7032 | 46.4821 | 46.2368 | 45.9737 | 45.6842 | 45.4074 | 45.1453 | 44.9 | 44.6874 | 43.7411 | 42.1568 | 40.4611 | 45.7358 | 45.5358 | 45.3147 | 45.0684 | 44.8053 | 44.5084 | 44.2253 | 43.9568 | 43.7032 | 43.4821 | 42.6789 | 41.6589 | 39.9
|  | DORCHESTER | CF |  |  |  | 34.8958 | 34.7768 | 47.4516 | 47.3232 | 47.1905 | 47.0442 | 46.8958 | 46.7495 | 46.6053 | 46.4621 | 45.8126 | 45.4558 | 45.2274 | 30.3516 | 30.2253 | 46.7642 | 46.6358 | 46.5032 | 46.3611 | 46.2168 | 46.0758 | 45.9347 | 45.7958 | 45.1684 | 44.8389 | 43.9537 | 29.6263 | 29.5074 | 45.5968 | 45.4684 | 45.3358 | 45.1905 | 45.0432 | 44.8979 | 44.7537 | 44.6126 | 43.9684 | 43.6168 | 43.3958
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | DOWN GRANGE | MINIMUM HEADROOM | SU 61604 50238 | YES | 0.57895 | 33.6105 | 33.0232 | 32.4295 | 31.0442 | 29.2011 | 27.2263 | 25.1179 | 23.4568 | 21.88 | 20.6884 | 16.3168 | 12.5116 | -17.0537 | 29.0526 | 27.62 | 26.0895 | 24.4337 | 22.3768 | 20.1705 | 17.8053 | 15.9558 | 14.1958 | 12.8832 | 8.1095 | 3.9158 | -0.67579 | 29.5274 | 28.1558 | 26.6947 | 25.1137 | 23.1537 | 20.9453 | 18.5779 | 16.7253 | 14.9653 | 13.6484 | 8.8611 | 4.6505 | 0.051579
|  | DOWN GRANGE | EE |  |  |  | 33.8316 | 33.3695 | 32.8789 | 32.1611 | 30.5179 | 28.7337 | 27.2242 | 25.84 | 24.3421 | 22.8558 | 19.2347 | 16.6147 | 13.4895 | 29.5579 | 28.3832 | 27.0811 | 25.6526 | 23.8116 | 21.8095 | 20.1295 | 18.5926 | 16.9189 | 15.2495 | 11.2968 | 8.4358 | 4.9032 | 30.0126 | 28.8895 | 27.6463 | 26.2842 | 24.5358 | 22.5842 | 20.9021 | 19.3621 | 17.6853 | 16.0137 | 12.0411 | 9.1579 | 5.6168
|  | DOWN GRANGE | HT |  |  |  | 33.6105 | 33.0232 | 32.4295 | 31.0442 | 29.2011 | 27.2263 | 25.1179 | 23.4568 | 21.88 | 20.6884 | 16.3168 | 12.5116 | 8.4284 | 29.0526 | 27.62 | 26.0895 | 24.4337 | 22.3768 | 20.1705 | 17.8053 | 15.9558 | 14.1958 | 12.8832 | 8.1095 | 3.9158 | -0.67579 | 29.5274 | 28.1558 | 26.6947 | 25.1137 | 23.1537 | 20.9453 | 18.5779 | 16.7253 | 14.9653 | 13.6484 | 8.8611 | 4.6505 | 0.051579
|  | DOWN GRANGE | HE |  |  |  | 34.1421 | 33.8263 | 33.4768 | 33.0905 | 32.2768 | 30.7358 | 29.4695 | 28.4137 | 27.3221 | 26.2947 | 23.4337 | 22.1116 | -17.0537 | 30.2147 | 29.4021 | 28.4147 | 27.2863 | 25.7295 | 23.9937 | 22.5779 | 21.4053 | 20.1863 | 19.0347 | 15.8663 | 14.4316 | 12.4747 | 30.6758 | 29.8663 | 28.9263 | 27.8516 | 26.3789 | 24.7358 | 23.3526 | 22.1789 | 20.9589 | 19.8053 | 16.6284 | 15.1863 | 13.2242
|  | DOWN GRANGE | CF |  |  |  | 34.3221 | 34.1432 | 33.9568 | 33.7632 | 33.5632 | 33.3547 | 33.1305 | 32.3326 | 31.7705 | 31.1821 | 28.5284 | 27.3905 | 26.3968 | 30.5316 | 30.3421 | 30.0095 | 29.5905 | 29.0168 | 28.2021 | 26.6611 | 25.7526 | 25.1242 | 24.4695 | 21.5074 | 20.2526 | 19.1326 | 30.8874 | 30.7084 | 30.4695 | 30.0379 | 29.4905 | 28.7189 | 27.2758 | 26.4168 | 25.8189 | 25.1968 | 22.2789 | 21.0211 | 19.8958
MINETY GSP | STRATTON (2 X 90) | DRAKES WAY | MINIMUM HEADROOM | SU 16899 85647 | YES | 0.29368 | 16.3326 | 16.2821 | 16.2326 | 16.1789 | 16.1232 | 16.0653 | 16.0074 | 15.9568 | 15.9095 | 15.8663 | 15.6211 | 15.3295 | 3.8168 | 14.9947 | 14.9421 | 14.8905 | 14.8347 | 14.6979 | 14.3821 | 14.1568 | 13.9484 | 13.7695 | 13.7221 | 13.4558 | 13.1368 | 12.6558 | 15.1937 | 15.1368 | 15.0811 | 15.0211 | 14.9484 | 14.7442 | 14.5189 | 14.3116 | 14.1326 | 14.0853 | 13.82 | 13.5011 | 13.02
|  | DRAKES WAY | EE |  |  |  | 16.3505 | 16.3105 | 16.2684 | 16.2232 | 16.1758 | 16.1274 | 16.08 | 16.0347 | 15.9905 | 15.9516 | 15.8074 | 15.6484 | 15.4211 | 15.0137 | 14.9716 | 14.9284 | 14.8811 | 14.8326 | 14.72 | 14.5295 | 14.3137 | 14.1095 | 14.0337 | 13.7232 | 13.4853 | 13.2305 | 15.2147 | 15.1695 | 15.1232 | 15.0726 | 15.02 | 14.9547 | 14.8884 | 14.6758 | 14.4726 | 14.3968 | 14.0863 | 13.8484 | 13.5937
|  | DRAKES WAY | HT |  |  |  | 16.3326 | 16.2821 | 16.2326 | 16.1789 | 16.1232 | 16.0653 | 16.0074 | 15.9568 | 15.9095 | 15.8663 | 15.6211 | 15.3295 | 14.9042 | 14.9947 | 14.9421 | 14.8905 | 14.8347 | 14.6979 | 14.3821 | 14.1568 | 13.9484 | 13.7695 | 13.7221 | 13.4558 | 13.1368 | 12.6558 | 15.1937 | 15.1368 | 15.0811 | 15.0211 | 14.9484 | 14.7442 | 14.5189 | 14.3116 | 14.1326 | 14.0853 | 13.82 | 13.5011 | 13.02
|  | DRAKES WAY | HE |  |  |  | 16.3747 | 16.3463 | 16.3147 | 16.2811 | 16.2432 | 16.2032 | 16.1653 | 16.1295 | 16.0958 | 16.0674 | 15.9695 | 15.9105 | 3.8168 | 15.0389 | 15.0095 | 14.9768 | 14.9421 | 14.9032 | 14.8579 | 14.7253 | 14.5326 | 14.3495 | 14.2958 | 14.0895 | 13.9526 | 13.8137 | 15.2432 | 15.2116 | 15.1768 | 15.1411 | 15.1 | 15.0442 | 14.9884 | 14.8947 | 14.7126 | 14.6589 | 14.4526 | 14.3158 | 14.1768
|  | DRAKES WAY | CF |  |  |  | 16.3895 | 16.3726 | 16.3558 | 16.3379 | 16.3189 | 16.3 | 16.28 | 16.2611 | 16.2421 | 16.2221 | 16.1368 | 16.0947 | 16.0705 | 15.0547 | 15.0368 | 15.02 | 15.0011 | 14.9811 | 14.9621 | 14.9411 | 14.9211 | 14.9 | 14.8768 | 14.5589 | 14.4558 | 14.3726 | 15.26 | 15.2411 | 15.2221 | 15.2021 | 15.1811 | 15.16 | 15.1379 | 15.1168 | 15.0905 | 15.06 | 14.9211 | 14.8179 | 14.7347
NURSLING GSP | WINCHESTER | DUNBRIDGE | MINIMUM HEADROOM | SU 31520 26244 | YES | 0.12632 | 10.3316 | 10.1726 | 9.9221 | 9.7842 | 9.22 | 8.0368 | 7.0705 | 5.6295 | 5.4558 | 5.2905 | 2.7105 | -0.85158 | -32.08 | 7.8284 | 7.5453 | 7.2663 | 6.9916 | 6.3568 | 5.1063 | 3.7874 | 2.1337 | 1.9705 | 1.8168 | -1.0137 | -5.1063 | -6.06 | 8.2474 | 7.9926 | 7.7295 | 7.4368 | 6.8021 | 5.4411 | 4.1158 | 2.4558 | 2.2821 | 2.1168 | -0.78105 | -4.8484 | -5.8337
|  | DUNBRIDGE | EE |  |  |  | 10.3979 | 10.2768 | 10.1453 | 9.9389 | 9.7284 | 9.4926 | 9.2516 | 9.0158 | 8.7758 | 8.5484 | 6.6358 | 3.0411 | 0.88526 | 7.9568 | 7.7453 | 7.5232 | 7.2895 | 7.0611 | 6.8158 | 6.5674 | 6.3253 | 6.0789 | 5.8484 | 3.7211 | -0.32421 | -2.7811 | 8.3621 | 8.1705 | 7.9684 | 7.7526 | 7.5211 | 7.2663 | 7.0074 | 6.7537 | 6.4947 | 6.2505 | 4.0168 | -0.13474 | -2.6242
|  | DUNBRIDGE | HT |  |  |  | 10.3316 | 10.1726 | 9.9221 | 9.7842 | 9.22 | 8.0368 | 7.0705 | 5.6295 | 5.4558 | 5.2905 | 2.7105 | -0.85158 | -1.7516 | 7.8284 | 7.5453 | 7.2663 | 6.9916 | 6.3568 | 5.1063 | 3.7874 | 2.1337 | 1.9705 | 1.8168 | -1.0137 | -5.1063 | -6.06 | 8.2474 | 7.9926 | 7.7295 | 7.4368 | 6.8021 | 5.4411 | 4.1158 | 2.4558 | 2.2821 | 2.1168 | -0.78105 | -4.8484 | -5.8337
|  | DUNBRIDGE | HE |  |  |  | 10.4811 | 10.4063 | 10.3221 | 10.2253 | 10.1232 | 9.9947 | 9.8453 | 9.6905 | 9.5389 | 9.3979 | 8.3568 | 5.8179 | -32.08 | 8.0505 | 7.9758 | 7.8632 | 7.7084 | 7.5568 | 7.3832 | 7.2158 | 7.0568 | 6.9 | 6.7537 | 5.5926 | 2.5758 | 0.53474 | 8.4526 | 8.3779 | 8.2716 | 8.1295 | 7.9905 | 7.82 | 7.66 | 7.5053 | 7.3453 | 7.1926 | 5.9758 | 2.9263 | 0.85579
|  | DUNBRIDGE | CF |  |  |  | 10.5295 | 10.4905 | 10.4484 | 10.4063 | 10.3579 | 10.2979 | 10.2379 | 10.18 | 10.0979 | 10.0137 | 9.5989 | 8.3063 | 7.02 | 8.0989 | 8.06 | 8.0179 | 7.9684 | 7.8789 | 7.7653 | 7.6558 | 7.5611 | 7.4684 | 7.3779 | 6.9358 | 5.36 | 3.8453 | 8.5011 | 8.4621 | 8.42 | 8.3726 | 8.2926 | 8.1884 | 8.0874 | 7.9989 | 7.9126 | 7.8284 | 7.3747 | 5.7642 | 4.2316
EALING GSP |  | EALING 11kV | MINIMUM HEADROOM | SZ 06789 95116 | YES | 0.21789 | 50.5558 | 50.1484 | 49.7389 | 49.3032 | 48.8463 | 47.6958 | 46.0611 | 44.9537 | 43.9053 | 43.2316 | 40.0768 | 36.7937 | -15.8716 | 41.6147 | 40.2305 | 38.6053 | 36.7063 | 34.5632 | 32.8737 | 31.0347 | 29.8074 | 28.6442 | 27.9158 | 24.4726 | 20.82 | 17.3095 | 43.6326 | 42.7389 | 41.1158 | 39.22 | 37.08 | 35.3411 | 33.5053 | 32.2789 | 31.1168 | 30.3895 | 26.9495 | 23.3021 | 19.7958
|  | EALING 11kV | EE |  |  |  | 50.7011 | 50.3779 | 50.0347 | 49.6716 | 49.2842 | 48.8789 | 48.4874 | 47.1158 | 45.7937 | 44.8179 | 42.7253 | 40.4179 | 38.2621 | 41.9832 | 41.0305 | 39.96 | 38.7221 | 37.1737 | 35.3579 | 33.7958 | 32.2032 | 30.7126 | 29.6232 | 27.4137 | 24.8547 | 22.4347 | 43.7916 | 43.4316 | 42.4695 | 41.2326 | 39.6863 | 37.8737 | 36.3137 | 34.7242 | 33.2347 | 32.1463 | 29.8874 | 27.3316 | 24.9147
|  | EALING 11kV | HT |  |  |  | 50.5558 | 50.1484 | 49.7389 | 49.3032 | 48.8463 | 47.6958 | 46.0611 | 44.9537 | 43.9053 | 43.2316 | 40.0768 | 36.7937 | 33.6653 | 41.6147 | 40.2305 | 38.6053 | 36.7063 | 34.5632 | 32.8737 | 31.0347 | 29.8074 | 28.6442 | 27.9158 | 24.4726 | 20.82 | 17.3095 | 43.6326 | 42.7389 | 41.1158 | 39.22 | 37.08 | 35.3411 | 33.5053 | 32.2789 | 31.1168 | 30.3895 | 26.9495 | 23.3021 | 19.7958
|  | EALING 11kV | HE |  |  |  | 50.8789 | 50.6347 | 50.3653 | 50.0674 | 49.7453 | 49.4042 | 49.0768 | 48.6053 | 47.5063 | 46.7505 | 45.5221 | 44.0705 | -15.8716 | 42.4042 | 41.6768 | 40.7863 | 39.7158 | 38.3368 | 36.68 | 35.2884 | 33.84 | 32.5979 | 31.7516 | 30.4916 | 28.8758 | 27.3916 | 43.9758 | 43.7116 | 43.2947 | 42.2253 | 40.8484 | 39.1947 | 37.8053 | 36.3579 | 35.1179 | 34.2726 | 32.9621 | 31.3484 | 29.8663
|  | EALING 11kV | CF |  |  |  | 50.9758 | 50.8168 | 50.6516 | 50.48 | 50.3021 | 50.1179 | 49.9305 | 49.7463 | 49.5632 | 49.3811 | 48.5674 | 47.8705 | 46.9653 | 42.5516 | 42.3789 | 42.1747 | 41.8579 | 41.5147 | 41.1642 | 40.8126 | 40.2916 | 39.5074 | 38.48 | 33.9926 | 33.1168 | 32.0926 | 44.0726 | 43.9137 | 43.7484 | 43.5758 | 43.3884 | 43.1947 | 42.9979 | 42.7937 | 42.0168 | 40.9916 | 36.5105 | 35.5832 | 34.56
LALEHAM |  | EAST BEDFONT 11kV | MINIMUM HEADROOM | TQ 08394 73826 | YES | 3.0589 | 43.9674 | 83.6926 | 83.4137 | 83.1189 | 82.8116 | 82.4947 | 82.1758 | 81.8937 | 81.6358 | 81.3989 | 79.4284 | 77.0042 | 30.0042 | 37.9095 | 77.5263 | 77.1516 | 76.7589 | 76.1463 | 75.5326 | 74.9547 | 74.4347 | 73.9442 | 73.4811 | 71.0937 | 68.3758 | 65.7368 | 39.2579 | 78.9832 | 78.6232 | 78.2326 | 77.62 | 77.0063 | 76.4284 | 75.9084 | 75.4168 | 74.9537 | 72.5684 | 69.8495 | 67.2105
|  | EAST BEDFONT 11kV | EE |  |  |  | 44.0716 | 83.8537 | 83.6232 | 83.3789 | 83.1221 | 82.8558 | 82.5979 | 82.3516 | 82.1137 | 81.9021 | 81.1221 | 79.5421 | 77.8789 | 38.04 | 77.7368 | 77.4232 | 77.1 | 76.7674 | 76.3505 | 75.9905 | 75.6242 | 75.2221 | 74.8347 | 73.1411 | 71.1979 | 69.3147 | 39.3621 | 79.1442 | 78.8905 | 78.5726 | 78.2411 | 77.8232 | 77.4632 | 77.0968 | 76.6947 | 76.3074 | 74.6137 | 72.6726 | 70.7884
|  | EAST BEDFONT 11kV | HT |  |  |  | 43.9674 | 83.6926 | 83.4137 | 83.1189 | 82.8116 | 82.4947 | 82.1758 | 81.8937 | 81.6358 | 81.3989 | 79.4284 | 77.0042 | 74.6695 | 37.9095 | 77.5263 | 77.1516 | 76.7589 | 76.1463 | 75.5326 | 74.9547 | 74.4347 | 73.9442 | 73.4811 | 71.0937 | 68.3758 | 65.7368 | 39.2579 | 78.9832 | 78.6232 | 78.2326 | 77.62 | 77.0063 | 76.4284 | 75.9084 | 75.4168 | 74.9537 | 72.5684 | 69.8495 | 67.2105
|  | EAST BEDFONT 11kV | HE |  |  |  | 44.2084 | 84.0547 | 83.8853 | 83.6979 | 83.4958 | 83.28 | 83.0747 | 82.8811 | 82.6989 | 82.5442 | 82.0126 | 81.6958 | 30.0042 | 38.1768 | 77.9821 | 77.7716 | 77.5253 | 77.2653 | 76.9189 | 76.6326 | 76.3368 | 76.0316 | 75.7389 | 74.8589 | 73.8253 | 72.4926 | 39.4989 | 79.3453 | 79.1758 | 78.9884 | 78.7347 | 78.3926 | 78.1063 | 77.8105 | 77.5042 | 77.2126 | 76.3316 | 75.2958 | 73.9632
|  | EAST BEDFONT 11kV | CF |  |  |  | 44.2905 | 84.2011 | 84.1074 | 84.0105 | 83.9105 | 83.8074 | 83.7011 | 83.5968 | 83.4937 | 83.3905 | 82.9316 | 82.7021 | 82.5737 | 38.2716 | 78.1716 | 78.0695 | 77.9642 | 77.8432 | 77.7105 | 77.5642 | 77.4126 | 77.2495 | 77.0811 | 76.1916 | 75.3853 | 74.4947 | 39.5811 | 79.4916 | 79.3979 | 79.3011 | 79.2011 | 79.0979 | 78.9916 | 78.8789 | 78.72 | 78.5537 | 77.6653 | 76.8579 | 75.9674
MANNINGTON GSP | REDHILL BSP | EAST HOWE | MINIMUM HEADROOM | SZ 06789 95116 | YES | 1.7516 | 26.6368 | 26.0295 | 24.8589 | 23.6137 | 22.3063 | 20.9158 | 19.5611 | 18.5137 | 17.4421 | 16.4158 | 11.8526 | 7.7379 | -18.5221 | 21.7768 | 20.5368 | 19.2379 | 17.8558 | 16.4105 | 14.8853 | 13.4053 | 12.2716 | 11.1011 | 9.9758 | 4.9495 | 0.36947 | -3.8211 | 22.5611 | 21.3716 | 20.1274 | 18.7716 | 17.3274 | 15.8021 | 14.32 | 13.1853 | 12.0116 | 10.8863 | 5.8516 | 1.2632 | -2.9316
|  | EAST HOWE | EE |  |  |  | 26.8495 | 26.4274 | 25.7053 | 24.6832 | 23.5526 | 22.3642 | 21.2442 | 20.4263 | 19.6368 | 18.7958 | 15.2295 | 12.0295 | 9.1789 | 22.2442 | 21.2495 | 20.1684 | 19.0021 | 17.7611 | 16.4568 | 15.2295 | 14.3516 | 13.5053 | 12.5905 | 8.6705 | 5.1 | 1.8832 | 23.0137 | 22.0568 | 21.0221 | 19.92 | 18.6779 | 17.3726 | 16.1432 | 15.2642 | 14.4168 | 13.5 | 9.5695 | 5.9863 | 2.7653
|  | EAST HOWE | HT |  |  |  | 26.6368 | 26.0295 | 24.8589 | 23.6137 | 22.3063 | 20.9158 | 19.5611 | 18.5137 | 17.4421 | 16.4158 | 11.8526 | 7.7379 | 4.0063 | 21.7768 | 20.5368 | 19.2379 | 17.8558 | 16.4105 | 14.8853 | 13.4053 | 12.2716 | 11.1011 | 9.9758 | 4.9495 | 0.36947 | -3.8211 | 22.5611 | 21.3716 | 20.1274 | 18.7716 | 17.3274 | 15.8021 | 14.32 | 13.1853 | 12.0116 | 10.8863 | 5.8516 | 1.2632 | -2.9316
|  | EAST HOWE | HE |  |  |  | 27.1389 | 26.8547 | 26.5411 | 26.0242 | 25.1495 | 24.2021 | 23.3168 | 22.7358 | 22.1516 | 21.5168 | 18.9789 | 16.7463 | -18.5221 | 22.8632 | 22.1874 | 21.3979 | 20.5095 | 19.5326 | 18.4726 | 17.4853 | 16.8632 | 16.2358 | 15.5421 | 12.7379 | 10.2211 | 7.98 | 23.6253 | 22.9589 | 22.2021 | 21.3537 | 20.42 | 19.3884 | 18.4011 | 17.7779 | 17.1495 | 16.4547 | 13.6463 | 11.1253 | 8.8811
|  | EAST HOWE | CF |  |  |  | 27.3147 | 27.16 | 27 | 26.8337 | 26.6621 | 26.4558 | 25.9611 | 25.5768 | 25.2232 | 24.8874 | 23.4505 | 21.9537 | 20.6621 | 23.2221 | 22.8568 | 22.4432 | 21.9968 | 21.5158 | 20.9705 | 20.4116 | 19.9853 | 19.5968 | 19.2284 | 17.66 | 15.9642 | 14.4895 | 23.9958 | 23.6168 | 23.2105 | 22.7789 | 22.32 | 21.8021 | 21.2695 | 20.8621 | 20.4874 | 20.1337 | 18.5747 | 16.8758 | 15.3989
MELKSHAM GSP | NORRINGTON | EASTERTON | MINIMUM HEADROOM | SU 01568 54730 | YES | 0.21053 | 17.3232 | 17.0389 | 16.7547 | 16.4653 | 16.1295 | 15.5705 | 14.8147 | 13.8611 | 13.6516 | 13.4484 | 9.3621 | 6.7558 | 2.2347 | 14.7695 | 14.4558 | 14.1442 | 13.8295 | 13.4579 | 12.8274 | 11.9568 | 10.9032 | 10.7042 | 10.5147 | 6.0263 | 3.2505 | 2.4484 | 15.2253 | 14.9074 | 14.5905 | 14.2705 | 13.8937 | 13.24 | 12.34 | 11.2463 | 11.0368 | 10.8337 | 6.2011 | 3.2968 | 2.4432
|  | EASTERTON | EE |  |  |  | 17.4495 | 17.2316 | 17.0042 | 16.7705 | 16.5074 | 16.1579 | 15.8147 | 15.4189 | 14.98 | 14.7011 | 13.2084 | 10.1411 | 8.6274 | 14.9116 | 14.6705 | 14.4242 | 14.1705 | 13.8832 | 13.5053 | 13.1442 | 12.72 | 12.2442 | 11.9653 | 10.4832 | 7.2589 | 5.6347 | 15.3695 | 15.1253 | 14.8737 | 14.6158 | 14.3232 | 13.9305 | 13.5516 | 13.1053 | 12.6032 | 12.3053 | 10.6874 | 7.2505 | 5.5453
|  | EASTERTON | HT |  |  |  | 17.3232 | 17.0389 | 16.7547 | 16.4653 | 16.1295 | 15.5705 | 14.8147 | 13.8611 | 13.6516 | 13.4484 | 9.3621 | 6.7558 | 5.9547 | 14.7695 | 14.4558 | 14.1442 | 13.8295 | 13.4579 | 12.8274 | 11.9568 | 10.9032 | 10.7042 | 10.5147 | 6.0263 | 3.2505 | 2.4484 | 15.2253 | 14.9074 | 14.5905 | 14.2705 | 13.8937 | 13.24 | 12.34 | 11.2463 | 11.0368 | 10.8337 | 6.2011 | 3.2968 | 2.4432
|  | EASTERTON | HE |  |  |  | 17.54 | 17.4568 | 17.3432 | 17.1926 | 17.0063 | 16.7337 | 16.4884 | 16.1916 | 15.8653 | 15.7032 | 14.8589 | 12.7653 | 2.2347 | 15.0021 | 14.9189 | 14.8 | 14.6368 | 14.4337 | 14.1389 | 13.8768 | 13.5484 | 13.1832 | 13.0211 | 12.1526 | 9.8042 | 8.4926 | 15.46 | 15.3768 | 15.2568 | 15.0926 | 14.8853 | 14.5789 | 14.3063 | 13.9663 | 13.5853 | 13.4137 | 12.4832 | 10.0337 | 8.6537
|  | EASTERTON | CF |  |  |  | 17.5937 | 17.5484 | 17.5021 | 17.4537 | 17.3842 | 17.2726 | 17.1579 | 17.0442 | 16.9158 | 16.7747 | 16.1179 | 15.64 | 14.9 | 15.0558 | 15.0105 | 14.9642 | 14.9158 | 14.8411 | 14.7221 | 14.6011 | 14.48 | 14.34 | 14.1832 | 13.4579 | 12.94 | 12.0863 | 15.5137 | 15.4684 | 15.4221 | 15.3737 | 15.2979 | 15.1747 | 15.0474 | 14.9211 | 14.7768 | 14.6137 | 13.8589 | 13.3095 | 12.4126
BRAMLEY (FLEE) | BRACKNELL | EASTHAMPSTEAD | MINIMUM HEADROOM | SU 86148 67194 | YES | 0.20421 | 35.0621 | 34.6632 | 34.2611 | 33.8326 | 33.3863 | 32.9821 | 32.1821 | 31.1705 | 30.4989 | 29.8789 | 26.4189 | 22.2874 | -10.6947 | 30.4084 | 29.5063 | 28.7158 | 27.9116 | 27.0011 | 25.8137 | 24.5811 | 23.4789 | 22.7653 | 22.1042 | 18.3421 | 13.6979 | 9.4316 | 31.4811 | 30.6747 | 29.8779 | 29.0663 | 28.1474 | 26.9463 | 25.6989 | 24.5832 | 23.8611 | 23.1947 | 19.3863 | 14.7337 | 10.4621
|  | EASTHAMPSTEAD | EE |  |  |  | 35.1905 | 34.8642 | 34.5189 | 34.1516 | 33.7653 | 33.4189 | 33.0263 | 32.36 | 31.7611 | 31.22 | 28.5347 | 25.2189 | 22.2558 | 30.7326 | 29.9968 | 29.3495 | 28.6884 | 27.9147 | 26.8547 | 25.7653 | 24.7674 | 24.1347 | 23.5621 | 20.6653 | 16.9579 | 13.5916 | 31.6211 | 31.1674 | 30.5179 | 29.8516 | 29.0716 | 27.9968 | 26.8937 | 25.8832 | 25.2442 | 24.6663 | 21.7274 | 17.9863 | 14.6147
|  | EASTHAMPSTEAD | HT |  |  |  | 35.0621 | 34.6632 | 34.2611 | 33.8326 | 33.3863 | 32.9821 | 32.1821 | 31.1705 | 30.4989 | 29.8789 | 26.4189 | 22.2874 | 18.5179 | 30.4084 | 29.5063 | 28.7158 | 27.9116 | 27.0011 | 25.8137 | 24.5811 | 23.4789 | 22.7653 | 22.1042 | 18.3421 | 13.6979 | 9.4316 | 31.4811 | 30.6747 | 29.8779 | 29.0663 | 28.1474 | 26.9463 | 25.6989 | 24.5832 | 23.8611 | 23.1947 | 19.3863 | 14.7337 | 10.4621
|  | EASTHAMPSTEAD | HE |  |  |  | 35.3884 | 35.1537 | 34.8947 | 34.6084 | 34.3 | 34.0284 | 33.7126 | 33.4137 | 33.1358 | 32.8947 | 31.3547 | 28.8747 | -10.6947 | 31.0021 | 30.7474 | 30.2274 | 29.7137 | 29.1242 | 28.2411 | 27.3295 | 26.5116 | 26.0632 | 25.6747 | 23.7011 | 20.9211 | 18.4316 | 31.8368 | 31.5874 | 31.3126 | 30.8863 | 30.2926 | 29.3968 | 28.4758 | 27.6474 | 27.1958 | 26.8032 | 24.8053 | 21.98 | 19.4747
|  | EASTHAMPSTEAD | CF |  |  |  | 35.5011 | 35.3568 | 35.2084 | 35.0537 | 34.8937 | 34.7853 | 34.6158 | 34.4484 | 34.2832 | 34.1179 | 33.3789 | 32.3758 | 30.9547 | 31.1211 | 30.9684 | 30.8042 | 30.52 | 30.1842 | 29.7674 | 29.2737 | 28.7968 | 28.4863 | 28.1842 | 26.6 | 24.7316 | 23.1274 | 31.9558 | 31.8021 | 31.6432 | 31.48 | 31.3095 | 30.9379 | 30.4379 | 29.9558 | 29.6432 | 29.3379 | 27.7368 | 25.84 | 24.2084
NURSLING GSP | VELMORE BSP | EASTLEIGH NORTH | MINIMUM HEADROOM | SU 45426 18958 | YES | 0.66842 | 47.6032 | 47.0168 | 46.4242 | 45.7947 | 44.6179 | 42.6242 | 41.04 | 39.6968 | 38.3547 | 36.9958 | 30.66 | 25.1179 | -22.5179 | 40.1137 | 38.3126 | 35.7368 | 32.8716 | 30.9737 | 28.7568 | 27.0189 | 25.5495 | 24.08 | 22.5811 | 15.5053 | 9.2632 | 3.5389 | 41.7137 | 40.5463 | 38.0568 | 35.2789 | 33.3411 | 31.0758 | 29.3042 | 27.8074 | 26.3084 | 24.8 | 17.7295 | 11.4863 | 5.76
|  | EASTLEIGH NORTH | EE |  |  |  | 47.8284 | 47.3684 | 46.8821 | 46.3642 | 45.8232 | 44.2821 | 43.0463 | 41.8684 | 40.7526 | 39.6074 | 34.4432 | 30.0947 | 26.1642 | 40.6116 | 39.0663 | 36.7179 | 34.0811 | 32.3979 | 30.5611 | 29.2074 | 27.9179 | 26.7211 | 25.4537 | 19.6716 | 14.7663 | 10.3326 | 41.9547 | 41.2821 | 39.0147 | 36.4716 | 34.7895 | 32.9116 | 31.5326 | 30.2189 | 28.9421 | 27.6737 | 21.8895 | 16.9905 | 12.5147
|  | EASTLEIGH NORTH | HT |  |  |  | 47.6032 | 47.0168 | 46.4242 | 45.7947 | 44.6179 | 42.6242 | 41.04 | 39.6968 | 38.3547 | 36.9958 | 30.66 | 25.1179 | 20.0632 | 40.1137 | 38.3126 | 35.7368 | 32.8716 | 30.9737 | 28.7568 | 27.0189 | 25.5495 | 24.08 | 22.5811 | 15.5053 | 9.2632 | 3.5389 | 41.7137 | 40.5463 | 38.0568 | 35.2789 | 33.3411 | 31.0758 | 29.3042 | 27.8074 | 26.3084 | 24.8 | 17.7295 | 11.4863 | 5.76
|  | EASTLEIGH NORTH | HE |  |  |  | 48.1326 | 47.8147 | 47.4642 | 47.0768 | 46.66 | 46.2158 | 45.2137 | 44.2716 | 43.3632 | 42.5147 | 38.4811 | 35.1337 | -22.5179 | 41.1368 | 40.0537 | 38.0074 | 35.6611 | 34.2547 | 32.6674 | 31.5611 | 30.5274 | 29.5284 | 28.62 | 24.0737 | 20.2432 | 16.9253 | 42.2811 | 41.9095 | 40.2737 | 38.0137 | 36.6505 | 35.0547 | 33.9263 | 32.8737 | 31.8547 | 30.84 | 26.2937 | 22.4558 | 19.0947
|  | EASTLEIGH NORTH | CF |  |  |  | 48.3074 | 48.1263 | 47.9368 | 47.74 | 47.5368 | 47.3274 | 47.1116 | 46.9011 | 46.6926 | 46.4842 | 45.5537 | 43.52 | 41.6779 | 41.3274 | 41.0326 | 39.9979 | 38.8853 | 38.1989 | 37.5084 | 36.9895 | 36.4463 | 35.8495 | 35.2084 | 32.14 | 29.6989 | 27.5895 | 42.4726 | 42.26 | 42.02 | 41.1242 | 40.46 | 39.7916 | 39.2853 | 38.7558 | 38.1758 | 37.5547 | 34.5326 | 32.0284 | 29.86
LOVEDEAN GSP | PORTSMOUTH BSP | EASTNEY | MINIMUM HEADROOM | SZ 66357 99040 | YES | 0 | 22.0316 | 21.8905 | 21.7474 | 21.5926 | 21.4232 | 21.2474 | 21.0705 | 20.9105 | 20.7632 | 20.5916 | 19.0916 | 17.5611 | 6.6579 | 20.3263 | 20.1432 | 19.8821 | 19.6 | 19.3063 | 19.0116 | 18.7232 | 18.4526 | 18.1989 | 17.8747 | 16.2011 | 14.4789 | 12.8674 | 20.66 | 20.4442 | 20.2263 | 20.0021 | 19.7389 | 19.4726 | 19.2105 | 18.9663 | 18.7211 | 18.4074 | 16.7168 | 14.9716 | 13.3379
|  | EASTNEY | EE |  |  |  | 22.0811 | 21.9684 | 21.8484 | 21.7211 | 21.5853 | 21.4358 | 21.2905 | 21.1484 | 21.0105 | 20.8842 | 20.0484 | 18.8347 | 17.7411 | 20.3979 | 20.2526 | 20.1011 | 19.8884 | 19.6516 | 19.4042 | 19.1705 | 18.9411 | 18.7179 | 18.5095 | 17.2737 | 15.8979 | 14.6579 | 20.7295 | 20.5779 | 20.4021 | 20.2179 | 20.0263 | 19.8158 | 19.6042 | 19.3937 | 19.1916 | 19.0021 | 17.8021 | 16.4063 | 15.1474
|  | EASTNEY | HT |  |  |  | 22.0316 | 21.8905 | 21.7474 | 21.5926 | 21.4232 | 21.2474 | 21.0705 | 20.9105 | 20.7632 | 20.5916 | 19.0916 | 17.5611 | 16.1221 | 20.3263 | 20.1432 | 19.8821 | 19.6 | 19.3063 | 19.0116 | 18.7232 | 18.4526 | 18.1989 | 17.8747 | 16.2011 | 14.4789 | 12.8674 | 20.66 | 20.4442 | 20.2263 | 20.0021 | 19.7389 | 19.4726 | 19.2105 | 18.9663 | 18.7211 | 18.4074 | 16.7168 | 14.9716 | 13.3379
|  | EASTNEY | HE |  |  |  | 22.1389 | 22.0516 | 21.9547 | 21.8474 | 21.7316 | 21.6084 | 21.4905 | 21.3789 | 21.2758 | 21.1863 | 20.8537 | 20.4895 | 6.6579 | 20.4842 | 20.3789 | 20.2621 | 20.1358 | 20.0011 | 19.8579 | 19.6926 | 19.5242 | 19.3663 | 19.2232 | 18.6389 | 17.7526 | 16.8537 | 20.7937 | 20.7021 | 20.6011 | 20.4653 | 20.3147 | 20.1579 | 20.0074 | 19.8642 | 19.7295 | 19.6095 | 19.0937 | 18.2884 | 17.3737
|  | EASTNEY | CF |  |  |  | 22.1716 | 22.1126 | 22.0516 | 21.9884 | 21.9232 | 21.8558 | 21.7863 | 21.7168 | 21.6505 | 21.5832 | 21.2716 | 21.0905 | 20.7632 | 20.5253 | 20.4526 | 20.3705 | 20.2916 | 20.2116 | 20.1284 | 20.0432 | 19.9495 | 19.8316 | 19.7137 | 19.1674 | 18.6168 | 18.0105 | 20.8274 | 20.7663 | 20.7011 | 20.6326 | 20.54 | 20.4453 | 20.3474 | 20.2505 | 20.1558 | 20.06 | 19.5958 | 19.1326 | 18.5442
LALEHAM | STAINES | EGHAM | MINIMUM HEADROOM | TQ 01030 71404 | YES | 0.024211 | 39.5716 | 39.2505 | 38.9274 | 38.5832 | 38.0611 | 67.4295 | 66.6316 | 65.8905 | 65.1947 | 64.5474 | 61.5747 | 58.8716 | 2.1484 | 31.2968 | 30.0326 | 28.6779 | 27.1653 | 26.5442 | 55.8663 | 54.9968 | 54.1842 | 53.4221 | 52.7147 | 49.4432 | 46.4453 | 43.7105 | 33.2968 | 32.0768 | 30.7211 | 29.2095 | 28.5874 | 57.9084 | 57.0347 | 56.22 | 55.4537 | 54.7421 | 51.4474 | 48.4242 | 45.6779
|  | EGHAM | EE |  |  |  | 39.6874 | 39.4326 | 39.1632 | 38.8779 | 38.5779 | 68.2589 | 67.6 | 66.9653 | 66.3579 | 65.8032 | 63.3526 | 61.1768 | 59.2884 | 31.5695 | 30.4442 | 29.2095 | 27.82 | 27.3147 | 56.7853 | 56.0695 | 55.38 | 54.7221 | 54.1221 | 51.4516 | 49.0632 | 46.9453 | 33.4337 | 32.4811 | 31.2442 | 29.8537 | 29.3453 | 58.8116 | 58.0895 | 57.3947 | 56.7295 | 56.1232 | 53.4074 | 50.9726 | 48.8305
|  | EGHAM | HT |  |  |  | 39.5716 | 39.2505 | 38.9274 | 38.5832 | 38.0611 | 67.4295 | 66.6316 | 65.8905 | 65.1947 | 64.5474 | 61.5747 | 58.8716 | 56.4379 | 31.2968 | 30.0326 | 28.6779 | 27.1653 | 26.5442 | 55.8663 | 54.9968 | 54.1842 | 53.4221 | 52.7147 | 49.4432 | 46.4453 | 43.7105 | 33.2968 | 32.0768 | 30.7211 | 29.2095 | 28.5874 | 57.9084 | 57.0347 | 56.22 | 55.4537 | 54.7421 | 51.4474 | 48.4242 | 45.6779
|  | EGHAM | HE |  |  |  | 39.8558 | 39.68 | 39.4863 | 39.2716 | 39.0411 | 68.7884 | 68.5484 | 68.3211 | 67.8674 | 67.4547 | 65.7074 | 64.2295 | 2.1484 | 31.9432 | 30.9937 | 29.9284 | 28.6989 | 28.3474 | 57.96 | 57.3937 | 56.8495 | 56.3411 | 55.8916 | 53.9621 | 52.3 | 50.8189 | 33.6189 | 33.0379 | 31.9737 | 30.7453 | 30.3937 | 60.0032 | 59.4326 | 58.8874 | 58.3779 | 57.9263 | 55.9811 | 54.3063 | 52.8126
|  | EGHAM | CF |  |  |  | 39.9495 | 39.8463 | 39.74 | 39.6305 | 39.5168 | 69.3958 | 69.2726 | 69.1495 | 69.0305 | 68.9105 | 68.3747 | 67.9547 | 67.0905 | 32.2705 | 31.7958 | 31.2495 | 30.6621 | 30.4537 | 60.2411 | 59.9411 | 59.6347 | 59.3316 | 59.0316 | 57.5989 | 56.4484 | 55.4632 | 33.7295 | 33.6011 | 33.2832 | 32.7074 | 32.5 | 62.2863 | 61.9853 | 61.68 | 61.3758 | 61.0747 | 59.64 | 58.4842 | 57.4947
MANNINGTON GSP | BOURNEMOUTH | ELECTRIC HOUSE | MINIMUM HEADROOM | SZ 08757 91379 | YES | 0.063158 | 26.1747 | 26.0905 | 26.0053 | 25.9158 | 25.6074 | 24.5589 | 23.8821 | 23.7 | 23.5105 | 23.3263 | 22.4516 | 21.6 | -2.8368 | 25.1832 | 25.0989 | 25.0137 | 24.9242 | 24.8263 | 24.7253 | 24.5947 | 24.4 | 24.1947 | 23.9958 | 23.0484 | 22.1168 | 21.1989 | 25.1663 | 25.0821 | 24.9968 | 24.9074 | 24.8095 | 24.6484 | 24.5063 | 24.4063 | 24.3105 | 24.1695 | 23.2516 | 22.3042 | 21.3726
|  | ELECTRIC HOUSE | EE |  |  |  | 26.2189 | 26.16 | 26.0968 | 26.0305 | 25.8347 | 24.8211 | 24.1895 | 24.0526 | 23.9158 | 23.7674 | 23.0968 | 22.4453 | 21.8137 | 25.2274 | 25.1684 | 25.1053 | 25.0389 | 24.9653 | 24.8874 | 24.8105 | 24.7347 | 24.6274 | 24.4674 | 23.7411 | 23.0242 | 22.3232 | 25.2105 | 25.1516 | 25.0884 | 25.0221 | 24.9484 | 24.8179 | 24.7042 | 24.6242 | 24.5432 | 24.4695 | 23.9242 | 23.2253 | 22.5105
|  | ELECTRIC HOUSE | HT |  |  |  | 26.1747 | 26.0905 | 26.0053 | 25.9158 | 25.6074 | 24.5589 | 23.8821 | 23.7 | 23.5105 | 23.3263 | 22.4516 | 21.6 | 20.7747 | 25.1832 | 25.0989 | 25.0137 | 24.9242 | 24.8263 | 24.7253 | 24.5947 | 24.4 | 24.1947 | 23.9958 | 23.0484 | 22.1168 | 21.1989 | 25.1663 | 25.0821 | 24.9968 | 24.9074 | 24.8095 | 24.6484 | 24.5063 | 24.4063 | 24.3105 | 24.1695 | 23.2516 | 22.3042 | 21.3726
|  | ELECTRIC HOUSE | HE |  |  |  | 26.2379 | 26.1853 | 26.1274 | 26.0632 | 25.9916 | 24.9989 | 24.3916 | 24.2884 | 24.1842 | 24.0695 | 23.5832 | 23.1284 | -2.8368 | 25.2463 | 25.1937 | 25.1358 | 25.0716 | 25.0021 | 24.9274 | 24.8568 | 24.7905 | 24.7284 | 24.6747 | 24.2726 | 23.7705 | 23.2937 | 25.2295 | 25.1768 | 25.1189 | 25.0547 | 24.9853 | 24.8663 | 24.76 | 24.6916 | 24.6263 | 24.5695 | 24.3547 | 23.9547 | 23.4968
|  | ELECTRIC HOUSE | CF |  |  |  | 26.2495 | 26.2105 | 26.1695 | 26.1274 | 26.0832 | 26.0379 | 25.9916 | 25.9463 | 25.9011 | 25.8568 | 25.5232 | 25.1895 | 24.8905 | 25.2579 | 25.2189 | 25.1779 | 25.1358 | 25.0916 | 25.0463 | 25 | 24.9547 | 24.9095 | 24.8653 | 24.6642 | 24.5611 | 24.5021 | 25.2411 | 25.2021 | 25.1611 | 25.1189 | 25.0747 | 25.0295 | 24.9832 | 24.9379 | 24.8926 | 24.8484 | 24.6474 | 24.5368 | 24.4621
BRAMLEY (FLEE) | WOKINGHAM BSP | ELMS ROAD | MINIMUM HEADROOM | SU 81057 68532 | YES | 0.55579 | 29.7684 | 29.4189 | 29.0653 | 28.5632 | 27.4821 | 26.3032 | 24.9621 | 23.6821 | 22.38 | 21.1411 | 16.6316 | 14.0537 | -11.3768 | 24.1221 | 23.2747 | 22.22 | 20.9421 | 19.74 | 18.4253 | 16.9211 | 15.4789 | 14.0063 | 12.6032 | 7.5158 | 4.6453 | 1.8505 | 25.6284 | 24.7979 | 23.7695 | 22.5242 | 21.3516 | 20.0705 | 18.6053 | 17.2011 | 15.7274 | 14.3242 | 9.2358 | 6.3642 | 3.5684
|  | ELMS ROAD | EE |  |  |  | 29.9063 | 29.6326 | 29.3442 | 29.0379 | 28.4589 | 27.5221 | 26.5074 | 25.4979 | 24.3242 | 23.1663 | 19.1453 | 17.3347 | 15.6253 | 24.4274 | 23.7821 | 22.9137 | 21.8021 | 20.8147 | 19.7716 | 18.6368 | 17.5042 | 16.1768 | 14.8632 | 10.3053 | 8.2895 | 6.3642 | 25.9274 | 25.2958 | 24.4484 | 23.3663 | 22.4021 | 21.3853 | 20.28 | 19.1768 | 17.8874 | 16.5842 | 12.0263 | 10.0095 | 8.0832
|  | ELMS ROAD | HT |  |  |  | 29.7684 | 29.4189 | 29.0653 | 28.5632 | 27.4821 | 26.3032 | 24.9621 | 23.6821 | 22.38 | 21.1411 | 16.6316 | 14.0537 | 11.5695 | 24.1221 | 23.2747 | 22.22 | 20.9421 | 19.74 | 18.4253 | 16.9211 | 15.4789 | 14.0063 | 12.6032 | 7.5158 | 4.6453 | 1.8505 | 25.6284 | 24.7979 | 23.7695 | 22.5242 | 21.3516 | 20.0705 | 18.6053 | 17.2011 | 15.7274 | 14.3242 | 9.2358 | 6.3642 | 3.5684
|  | ELMS ROAD | HE |  |  |  | 30.0905 | 29.9053 | 29.7 | 29.4737 | 29.2295 | 28.6968 | 27.82 | 26.9168 | 25.8758 | 24.8632 | 21.5589 | 20.3579 | -11.3768 | 24.8358 | 24.3832 | 23.7 | 22.7663 | 21.9432 | 21.0505 | 20.0642 | 19.0442 | 17.86 | 16.7053 | 12.9358 | 11.5895 | 10.2705 | 26.1495 | 25.8853 | 25.2189 | 24.3105 | 23.5084 | 22.6389 | 21.6789 | 20.6884 | 19.5389 | 18.4179 | 14.6568 | 13.3095 | 11.9905
|  | ELMS ROAD | CF |  |  |  | 30.1926 | 30.0863 | 29.9758 | 29.86 | 29.7411 | 29.6179 | 29.4926 | 29.3695 | 29.2474 | 29.1242 | 25.5453 | 24.7895 | 24.2684 | 25.3295 | 25.1137 | 24.7263 | 24.2411 | 23.8326 | 23.4347 | 23.0263 | 22.5968 | 22.1484 | 21.6684 | 17.4179 | 16.5779 | 15.9916 | 26.2768 | 26.1621 | 26.0347 | 25.7463 | 25.3474 | 24.96 | 24.5621 | 24.1432 | 23.7074 | 23.24 | 19.1242 | 18.2989 | 17.7126
LOVEDEAN GSP | HAVANT | EMSWORTH | MINIMUM HEADROOM | SU 74861 05807 | YES | 1.2032 | 11.7021 | 11.4358 | 11.1674 | 10.7011 | 30.0832 | 29.2611 | 28.1916 | 26.9505 | 25.4853 | 24.0937 | 17.7453 | 12.9137 | -2.9305 | 7.9316 | 7.6653 | 7.3968 | 6.8926 | 26.2074 | 25.2947 | 24.0905 | 22.6768 | 20.9947 | 19.3979 | 12.0874 | 6.5211 | 3.7726 | 8.4347 | 8.1684 | 7.9 | 7.4126 | 26.7568 | 25.8895 | 24.7526 | 23.3905 | 21.7116 | 20.1158 | 12.8179 | 7.2621 | 4.5168
|  | EMSWORTH | EE |  |  |  | 11.8032 | 11.5947 | 11.3737 | 11.1389 | 30.7274 | 30.0516 | 29.1916 | 28.1895 | 26.84 | 25.5326 | 19.6453 | 15.2632 | 13.3726 | 8.0326 | 7.8242 | 7.6032 | 7.3684 | 26.9221 | 26.1611 | 25.1926 | 24.0547 | 22.5053 | 21.0021 | 14.2011 | 9.1295 | 6.9674 | 8.5358 | 8.3274 | 8.1063 | 7.8716 | 27.44 | 26.7179 | 25.8032 | 24.7337 | 23.22 | 21.7189 | 14.9295 | 9.8674 | 7.7084
|  | EMSWORTH | HT |  |  |  | 11.7021 | 11.4358 | 11.1674 | 10.7011 | 30.0832 | 29.2611 | 28.1916 | 26.9505 | 25.4853 | 24.0937 | 17.7453 | 12.9137 | 10.4979 | 7.9316 | 7.6653 | 7.3968 | 6.8926 | 26.2074 | 25.2947 | 24.0905 | 22.6768 | 20.9947 | 19.3979 | 12.0874 | 6.5211 | 3.7726 | 8.4347 | 8.1684 | 7.9 | 7.4126 | 26.7568 | 25.8895 | 24.7526 | 23.3905 | 21.7116 | 20.1158 | 12.8179 | 7.2621 | 4.5168
|  | EMSWORTH | HE |  |  |  | 11.9453 | 11.8042 | 11.6474 | 11.4758 | 31.2895 | 30.9547 | 30.2084 | 29.2874 | 28.0253 | 26.8347 | 21.52 | 17.5747 | -2.9305 | 8.1747 | 8.0337 | 7.8768 | 7.7053 | 27.5189 | 27.1568 | 26.3 | 25.2484 | 23.7926 | 22.4168 | 16.2484 | 11.6558 | 9.9811 | 8.6779 | 8.5368 | 8.38 | 8.2084 | 28.0221 | 27.6716 | 26.8653 | 25.8789 | 24.5053 | 23.1316 | 16.9747 | 12.3895 | 10.7179
|  | EMSWORTH | CF |  |  |  | 12.0263 | 11.9463 | 11.8642 | 11.7779 | 31.6884 | 31.5968 | 31.5021 | 31.2379 | 30.8579 | 30.4684 | 27.7358 | 23.5126 | 22.5968 | 8.2558 | 8.1758 | 8.0937 | 8.0074 | 27.9179 | 27.8263 | 27.7316 | 27.4316 | 26.9916 | 26.5495 | 23.4063 | 18.4716 | 17.4137 | 8.7589 | 8.6789 | 8.5968 | 8.5105 | 28.4211 | 28.3295 | 28.2347 | 27.9505 | 27.5358 | 27.12 | 24.12 | 19.1947 | 18.1389
MELKSHAM GSP | AMESBURY | ENFORD | MINIMUM HEADROOM | SU 13728 51712 | YES | 0 | 8.6789 | 8.5726 | 8.4695 | 8.3642 | 8.2579 | 8.1463 | 7.9284 | 7.6684 | 7.6042 | 7.5421 | 6.9863 | 6.3074 | 2.4926 | 8.0589 | 7.9432 | 7.8316 | 7.7168 | 7.6042 | 7.4853 | 7.2421 | 6.9453 | 6.8842 | 6.8253 | 6.2337 | 5.4895 | 5.2547 | 8.2916 | 8.1758 | 8.0642 | 7.9495 | 7.8358 | 7.7168 | 7.4705 | 7.1726 | 7.1074 | 7.0453 | 6.4347 | 5.6674 | 5.4242
|  | ENFORD | EE |  |  |  | 8.7242 | 8.6421 | 8.5589 | 8.4737 | 8.3874 | 8.2947 | 8.2 | 8.1084 | 8.0189 | 7.9326 | 7.5032 | 6.9884 | 6.5884 | 8.1095 | 8.02 | 7.9305 | 7.8389 | 7.7474 | 7.6495 | 7.5537 | 7.46 | 7.3684 | 7.2821 | 6.8474 | 6.3084 | 5.8632 | 8.3421 | 8.2526 | 8.1632 | 8.0716 | 7.9789 | 7.88 | 7.7811 | 7.6832 | 7.5884 | 7.4979 | 7.0368 | 6.4663 | 6.0116
|  | ENFORD | HT |  |  |  | 8.6789 | 8.5726 | 8.4695 | 8.3642 | 8.2579 | 8.1463 | 7.9284 | 7.6684 | 7.6042 | 7.5421 | 6.9863 | 6.3074 | 6.08 | 8.0589 | 7.9432 | 7.8316 | 7.7168 | 7.6042 | 7.4853 | 7.2421 | 6.9453 | 6.8842 | 6.8253 | 6.2337 | 5.4895 | 5.2547 | 8.2916 | 8.1758 | 8.0642 | 7.9495 | 7.8358 | 7.7168 | 7.4705 | 7.1726 | 7.1074 | 7.0453 | 6.4347 | 5.6674 | 5.4242
|  | ENFORD | HE |  |  |  | 8.7874 | 8.7368 | 8.6832 | 8.6284 | 8.5695 | 8.5021 | 8.4379 | 8.3789 | 8.32 | 8.2674 | 8.0147 | 7.6611 | 2.4926 | 8.1789 | 8.1253 | 8.0674 | 8.0084 | 7.9463 | 7.8779 | 7.8116 | 7.7495 | 7.6905 | 7.6379 | 7.3768 | 6.9789 | 6.6263 | 8.3768 | 8.3453 | 8.3 | 8.2411 | 8.1789 | 8.1084 | 8.0411 | 7.9779 | 7.9168 | 7.8621 | 7.5905 | 7.1842 | 6.8232
|  | ENFORD | CF |  |  |  | 8.8211 | 8.7916 | 8.76 | 8.7284 | 8.6958 | 8.6579 | 8.62 | 8.58 | 8.5474 | 8.5116 | 8.3484 | 8.2042 | 7.9895 | 8.2105 | 8.1832 | 8.1495 | 8.1147 | 8.08 | 8.0379 | 7.9979 | 7.9579 | 7.9221 | 7.8842 | 7.7137 | 7.5579 | 7.3147 | 8.3958 | 8.3789 | 8.3611 | 8.3421 | 8.3126 | 8.2716 | 8.2295 | 8.1884 | 8.1516 | 8.1137 | 7.9389 | 7.7779 | 7.5295
COWLEY GSP | YARNTON BSP | EYNSHAM | MINIMUM HEADROOM | SP 42236 10266 | YES | 1.62 | 27.9895 | 27.6032 | 27.1189 | 25.5821 | 25.4179 | 24.4347 | 22.5579 | 20.4116 | 18.7305 | 17.1011 | 10.7284 | 7.2474 | -5.6042 | 23.4421 | 23.0189 | 22.4821 | 20.7242 | 20.56 | 19.4789 | 17.3084 | 14.82 | 12.8747 | 10.9884 | 3.6274 | -0.35474 | -2.1379 | 24.4916 | 24.0684 | 23.5316 | 21.7295 | 21.5653 | 20.4832 | 18.3158 | 15.8284 | 13.8842 | 11.9979 | 4.6305 | 0.63263 | -1.1568
|  | EYNSHAM | EE |  |  |  | 28.1305 | 27.8168 | 27.3968 | 25.5821 | 25.4179 | 25.2432 | 24.1737 | 22.5284 | 20.5884 | 18.3168 | 11.9095 | 8.4842 | 7.2295 | 23.5958 | 23.2516 | 22.7842 | 20.7242 | 20.56 | 20.3863 | 19.1621 | 17.26 | 15.0095 | 12.3663 | 4.9558 | 1.0305 | -0.38947 | 24.6453 | 24.3011 | 23.8326 | 21.7295 | 21.5653 | 21.3905 | 20.1642 | 18.2621 | 16.0126 | 13.3705 | 5.9453 | 1.9968 | 0.56842
|  | EYNSHAM | HT |  |  |  | 27.9895 | 27.6032 | 27.1189 | 26.4632 | 25.7137 | 24.4347 | 22.5579 | 20.4116 | 18.7305 | 17.1011 | 10.7284 | 7.2474 | 5.6674 | 23.4421 | 23.0189 | 22.4821 | 21.7905 | 20.9442 | 19.4789 | 17.3084 | 14.82 | 12.8747 | 10.9884 | 3.6274 | -0.35474 | -2.1379 | 24.4916 | 24.0684 | 23.5316 | 22.7947 | 21.9484 | 20.4832 | 18.3158 | 15.8284 | 13.8842 | 11.9979 | 4.6305 | 0.63263 | -1.1568
|  | EYNSHAM | HE |  |  |  | 28.3263 | 28.1063 | 27.7758 | 27.3253 | 26.88 | 26.0179 | 24.8074 | 23.1116 | 21.2368 | 19.1495 | 13.18 | 10.1905 | -5.6042 | 23.8084 | 23.5663 | 23.1968 | 22.6874 | 22.1853 | 21.2432 | 19.8421 | 17.8705 | 15.6874 | 13.2495 | 6.3 | 2.8305 | 1.7316 | 24.8579 | 24.6158 | 24.2463 | 23.7368 | 23.2347 | 22.2463 | 20.8463 | 18.8768 | 16.6958 | 14.2621 | 7.3126 | 3.84 | 2.7358
|  | EYNSHAM | CF |  |  |  | 28.4253 | 28.2989 | 28.1253 | 27.9295 | 27.8179 | 27.7021 | 27.5811 | 27.3379 | 27.0147 | 26.3663 | 21.5705 | 17.2 | 16.6042 | 23.9158 | 23.7758 | 23.5811 | 23.36 | 23.24 | 23.1158 | 22.9842 | 22.7105 | 22.3421 | 21.5926 | 16.0474 | 10.9358 | 10.2558 | 24.9653 | 24.8253 | 24.6305 | 24.4095 | 24.2884 | 24.1642 | 24.0326 | 23.7579 | 23.3895 | 22.6379 | 17.0547 | 11.9474 | 11.2632
MINETY GSP | CIRENCESTER BSP | FAIRFORD | MINIMUM HEADROOM | SP 14418 00559 | YES | 0 | 18.5505 | 18.3853 | 18.2179 | 18.04 | 17.7674 | 17.3832 | 16.9968 | 16.6337 | 16.2821 | 15.9811 | 14.2126 | 12.3579 | 0.36 | 15.3663 | 15.0589 | 14.74 | 14.3768 | 13.9958 | 13.5863 | 13.1737 | 12.7832 | 12.4063 | 12.0874 | 10.1758 | 8.1484 | 6.3758 | 15.9116 | 15.6684 | 15.3337 | 14.9642 | 14.5905 | 14.1842 | 13.7737 | 13.3863 | 13.0126 | 12.6937 | 10.7653 | 8.6832 | 6.8895
|  | FAIRFORD | EE |  |  |  | 18.6158 | 18.9853 | 18.7411 | 18.5516 | 18.28 | 17.98 | 17.6768 | 17.3758 | 17.08 | 16.8337 | 15.3295 | 13.7158 | 12.4295 | 15.5011 | 15.3211 | 15.0589 | 14.7695 | 14.4789 | 14.1621 | 13.8432 | 13.5284 | 13.2211 | 12.9695 | 11.3905 | 9.6747 | 8.24 | 15.9821 | 15.9884 | 15.7242 | 15.4368 | 15.1442 | 14.8232 | 14.4968 | 14.1737 | 13.8558 | 13.5947 | 11.9474 | 10.1547 | 8.6968
|  | FAIRFORD | HT |  |  |  | 18.5505 | 18.3853 | 18.2179 | 18.04 | 17.7674 | 17.3832 | 16.9968 | 16.6337 | 16.2821 | 15.9811 | 14.2126 | 12.3579 | 10.7789 | 15.3663 | 15.0589 | 14.74 | 14.3768 | 13.9958 | 13.5863 | 13.1737 | 12.7832 | 12.4063 | 12.0874 | 10.1758 | 8.1484 | 6.3758 | 15.9116 | 15.6684 | 15.3337 | 14.9642 | 14.5905 | 14.1842 | 13.7737 | 13.3863 | 13.0126 | 12.6937 | 10.7653 | 8.6832 | 6.8895
|  | FAIRFORD | HE |  |  |  | 18.7053 | 18.6211 | 18.5263 | 18.9053 | 18.7105 | 18.4863 | 18.2663 | 18.0484 | 17.84 | 17.68 | 16.6411 | 15.5295 | 0.36 | 15.6789 | 15.5389 | 15.3768 | 15.2389 | 15.0295 | 14.7926 | 14.5589 | 14.3284 | 14.1074 | 13.9411 | 12.8105 | 11.5632 | 10.4263 | 16.0779 | 15.9895 | 15.8905 | 15.9063 | 15.6968 | 15.4568 | 15.2189 | 14.9832 | 14.7579 | 14.5884 | 13.4295 | 12.1621 | 11.0074
|  | FAIRFORD | CF |  |  |  | 18.7579 | 18.7126 | 18.6642 | 18.6147 | 18.5632 | 18.5032 | 18.4421 | 18.3811 | 18.3221 | 18.2642 | 17.9179 | 17.2126 | 16.5958 | 15.7368 | 15.6863 | 15.6042 | 15.5095 | 15.4126 | 15.3084 | 15.1989 | 15.0863 | 14.9726 | 14.8768 | 14.1663 | 13.3737 | 12.6779 | 16.1326 | 16.0853 | 16.0337 | 15.9811 | 15.9263 | 15.8653 | 15.8011 | 15.6958 | 15.5747 | 15.4747 | 14.7463 | 13.9674 | 13.2832
MINETY GSP | STRATTON (2 X 60) | FARINGDON | MINIMUM HEADROOM | SU 28819 94924 | YES | 0.063158 | 15.4974 | 43.8516 | 43.5295 | 42.9421 | 42.5368 | 42.2579 | 41.1611 | 40.4021 | 40.16 | 39.9305 | 38.1558 | 36.0916 | 19.4747 | 11.6605 | 39.5863 | 38.8716 | 38.2116 | 37.7737 | 37.3926 | 36.1621 | 35.3242 | 35.0937 | 34.8768 | 33.0547 | 30.8821 | 29.8263 | 12.3847 | 40.3979 | 39.7021 | 39.0421 | 38.6032 | 38.1326 | 36.8947 | 36.0484 | 35.8053 | 35.5758 | 33.6726 | 31.4063 | 30.3137
|  | FARINGDON | EE |  |  |  | 15.5774 | 43.9779 | 43.7937 | 43.3432 | 43.0084 | 42.6379 | 42.4242 | 42.0516 | 41.6916 | 41.3505 | 39.78 | 38.3105 | 36.7905 | 11.8458 | 39.8653 | 39.2316 | 38.6547 | 38.2937 | 37.9063 | 37.5147 | 37.1337 | 36.7653 | 36.4221 | 34.8589 | 33.4074 | 31.7379 | 12.4711 | 40.6663 | 40.0621 | 39.4842 | 39.1221 | 38.7263 | 38.3242 | 37.9284 | 37.5474 | 37.1874 | 35.5189 | 33.9484 | 32.2411
|  | FARINGDON | HT |  |  |  | 15.4974 | 43.8516 | 43.5295 | 42.9421 | 42.5368 | 42.2579 | 41.1611 | 40.4021 | 40.16 | 39.9305 | 38.1558 | 36.0916 | 35.0747 | 11.6605 | 39.5863 | 38.8716 | 38.2116 | 37.7737 | 37.3926 | 36.1621 | 35.3242 | 35.0937 | 34.8768 | 33.0547 | 30.8821 | 29.8263 | 12.3847 | 40.3979 | 39.7021 | 39.0421 | 38.6032 | 38.1326 | 36.8947 | 36.0484 | 35.8053 | 35.5758 | 33.6726 | 31.4063 | 30.3137
|  | FARINGDON | HE |  |  |  | 15.6932 | 44.1474 | 44.02 | 43.8779 | 43.6611 | 43.3884 | 43.1242 | 42.8695 | 42.6305 | 42.4158 | 41.5221 | 40.7074 | 19.4747 | 12.1005 | 40.2421 | 39.7284 | 39.2632 | 39.0105 | 38.7274 | 38.4516 | 38.1874 | 37.9389 | 37.7179 | 36.8063 | 35.9358 | 34.8116 | 12.5953 | 41.0284 | 40.5421 | 40.0947 | 39.8421 | 39.5516 | 39.2705 | 38.9989 | 38.7453 | 38.5179 | 37.5621 | 36.6579 | 35.5011
|  | FARINGDON | CF |  |  |  | 15.7605 | 44.2653 | 44.1979 | 44.1274 | 44.0547 | 43.9684 | 43.8811 | 43.7947 | 43.7095 | 43.6274 | 43.0863 | 42.6021 | 41.9358 | 12.2068 | 40.5968 | 40.3284 | 40.0926 | 39.9516 | 39.7958 | 39.6347 | 39.4747 | 39.3179 | 39.1653 | 38.4505 | 37.9368 | 37.1926 | 12.6679 | 41.1621 | 41.0832 | 40.8884 | 40.7516 | 40.5979 | 40.4389 | 40.28 | 40.1263 | 39.9768 | 39.2537 | 38.72 | 37.9558
LOVEDEAN GSP | WYMERING BSP | FARLINGTON | MINIMUM HEADROOM | SU 67400 04843 | YES | 0.73474 | 21.3674 | 21.2768 | 21.1863 | 21.0895 | 20.9895 | 20.8874 | 20.7842 | 20.6926 | 20.6105 | 20.5347 | 19.8568 | 19.0716 | 6.6789 | 19.6474 | 19.4789 | 19.3126 | 19.1432 | 18.9684 | 18.7947 | 18.6274 | 18.4737 | 18.3316 | 18.1611 | 17.3095 | 16.4368 | 15.6263 | 19.1589 | 19.0684 | 18.9779 | 18.8811 | 18.7811 | 18.6789 | 18.5758 | 18.4842 | 18.4021 | 18.3263 | 17.6821 | 16.7968 | 15.9874
|  | FARLINGTON | EE |  |  |  | 21.4 | 21.3284 | 21.2526 | 21.1726 | 21.0874 | 21.0011 | 20.9168 | 20.8368 | 20.76 | 20.6926 | 20.4263 | 19.8116 | 19.2674 | 19.72 | 19.5916 | 19.46 | 19.3242 | 19.1832 | 19.04 | 18.9032 | 18.7747 | 18.6505 | 18.5368 | 17.9189 | 17.2505 | 16.64 | 19.1916 | 19.12 | 19.0442 | 18.9642 | 18.8789 | 18.7926 | 18.7084 | 18.6284 | 18.5516 | 18.4842 | 18.2358 | 17.6189 | 17
|  | FARLINGTON | HT |  |  |  | 21.3674 | 21.2768 | 21.1863 | 21.0895 | 20.9895 | 20.8874 | 20.7842 | 20.6926 | 20.6105 | 20.5347 | 19.8568 | 19.0716 | 18.3568 | 19.6474 | 19.4789 | 19.3126 | 19.1432 | 18.9684 | 18.7947 | 18.6274 | 18.4737 | 18.3316 | 18.1611 | 17.3095 | 16.4368 | 15.6263 | 19.1589 | 19.0684 | 18.9779 | 18.8811 | 18.7811 | 18.6789 | 18.5758 | 18.4842 | 18.4021 | 18.3263 | 17.6821 | 16.7968 | 15.9874
|  | FARLINGTON | HE |  |  |  | 21.4474 | 21.3979 | 21.3442 | 21.2842 | 21.22 | 21.1516 | 21.0863 | 21.0242 | 20.9653 | 20.9158 | 20.7484 | 20.6516 | 6.6789 | 19.8211 | 19.7379 | 19.6505 | 19.5568 | 19.4611 | 19.3589 | 19.2632 | 19.1716 | 19.0842 | 19.0074 | 18.7074 | 18.2947 | 17.88 | 19.2389 | 19.1895 | 19.1358 | 19.0758 | 19.0116 | 18.9432 | 18.8779 | 18.8158 | 18.7568 | 18.7074 | 18.54 | 18.4432 | 18.2589
|  | FARLINGTON | CF |  |  |  | 21.4747 | 21.4463 | 21.4168 | 21.3863 | 21.3558 | 21.3232 | 21.2895 | 21.2568 | 21.2242 | 21.1926 | 21.0484 | 20.9768 | 20.9379 | 19.8695 | 19.8168 | 19.7568 | 19.7021 | 19.6463 | 19.5884 | 19.5295 | 19.4726 | 19.4137 | 19.3568 | 19.0958 | 18.84 | 18.5674 | 19.2663 | 19.2379 | 19.2084 | 19.1779 | 19.1474 | 19.1147 | 19.0811 | 19.0484 | 19.0158 | 18.9842 | 18.84 | 18.7684 | 18.7295
BRAMLEY (FLEE) | CAMBERLEY RESERVE | FARNBOROUGH | MINIMUM HEADROOM | SU 88404 53930 | YES | 0.86 | 33.5905 | 33.2453 | 32.8958 | 32.5253 | 32.1411 | 31.4432 | 30.0505 | 28.9632 | 27.9126 | 26.8968 | 22.0379 | 19.68 | -8.5611 | 29.4463 | 28.6021 | 27.8232 | 27 | 26.1832 | 24.5779 | 23.0105 | 21.7947 | 20.6158 | 19.4758 | 13.9842 | 11.3811 | 9.0147 | 30.3 | 29.6389 | 28.8768 | 28.0716 | 27.2716 | 25.7105 | 24.1884 | 23.0053 | 21.8568 | 20.7295 | 15.2368 | 12.6295 | 10.2611
|  | FARNBOROUGH | EE |  |  |  | 33.7221 | 33.4495 | 33.1632 | 32.8558 | 32.5358 | 32.2021 | 31.0674 | 30.0653 | 29.0789 | 28.1453 | 23.7663 | 21.9474 | 20.3663 | 29.7453 | 29.0516 | 28.4105 | 27.7189 | 27.0305 | 25.5463 | 24.1126 | 22.9895 | 21.8832 | 20.8326 | 15.8674 | 13.8632 | 12.0947 | 30.4421 | 30.08 | 29.4516 | 28.7747 | 28.1011 | 26.66 | 25.2674 | 24.1747 | 23.0989 | 22.0779 | 17.1137 | 15.0989 | 13.3284
|  | FARNBOROUGH | HT |  |  |  | 33.5905 | 33.2453 | 32.8958 | 32.5253 | 32.1411 | 31.4432 | 30.0505 | 28.9632 | 27.9126 | 26.8968 | 22.0379 | 19.68 | 17.5579 | 29.4463 | 28.6021 | 27.8232 | 27 | 26.1832 | 24.5779 | 23.0105 | 21.7947 | 20.6158 | 19.4758 | 13.9842 | 11.3811 | 9.0147 | 30.3 | 29.6389 | 28.8768 | 28.0716 | 27.2716 | 25.7105 | 24.1884 | 23.0053 | 21.8568 | 20.7295 | 15.2368 | 12.6295 | 10.2611
|  | FARNBOROUGH | HE |  |  |  | 33.9011 | 33.7137 | 33.5074 | 33.28 | 33.0337 | 32.7695 | 32.3779 | 31.5168 | 30.6737 | 29.8811 | 26.1937 | 25.0337 | -8.5611 | 30.0684 | 29.6453 | 29.1884 | 28.6726 | 28.1505 | 26.82 | 25.5411 | 24.5705 | 23.6179 | 22.7211 | 18.5032 | 17.2126 | 16.1011 | 30.6347 | 30.4274 | 30.2053 | 29.7084 | 29.1968 | 27.9074 | 26.6663 | 25.7242 | 24.7989 | 23.9284 | 19.7579 | 18.4642 | 17.3526
|  | FARNBOROUGH | CF |  |  |  | 34.0032 | 33.8947 | 33.7832 | 33.6663 | 33.5453 | 33.42 | 33.2916 | 33.1653 | 33.0411 | 32.9168 | 30.5568 | 29.7011 | 28.9958 | 30.2105 | 30.0432 | 29.8168 | 29.5347 | 29.2547 | 28.6558 | 28.0179 | 27.4926 | 26.9389 | 26.3663 | 23.4284 | 22.4726 | 21.6737 | 30.7453 | 30.6253 | 30.5032 | 30.3758 | 30.2453 | 29.6968 | 29.0789 | 28.5684 | 28.0316 | 27.4758 | 24.6284 | 23.6968 | 22.92
BRAMLEY (FLEE) | PYESTOCK BSP | FARNBORO AIRFIELD | MINIMUM HEADROOM | SU 85838 54449 | YES | 0.23158 | 21.6011 | 21.5779 | 21.5547 | 21.5295 | 21.5032 | 21.4768 | 21.4495 | 21.4253 | 21.4042 | 21.3832 | 21.3011 | 21.2379 | 7.3179 | 18.5074 | 18.4663 | 18.4189 | 18.3642 | 18.3084 | 18.1916 | 18.0853 | 18.0042 | 17.9253 | 17.8305 | 17.6663 | 17.4347 | 17.2168 | 19.6253 | 19.5989 | 19.5716 | 19.5411 | 19.5095 | 19.4768 | 19.4316 | 19.3442 | 19.26 | 19.1653 | 19.0011 | 18.7705 | 18.5516
|  | FARNBORO AIRFIELD | EE |  |  |  | 21.6095 | 21.5905 | 21.5705 | 21.5484 | 21.5263 | 21.5032 | 21.4811 | 21.4589 | 21.4389 | 21.42 | 21.3526 | 21.3053 | 21.2705 | 18.5189 | 18.4842 | 18.4421 | 18.3916 | 18.3411 | 18.2495 | 18.1526 | 18.0758 | 18.0032 | 17.9179 | 17.7884 | 17.6179 | 17.4653 | 19.6347 | 19.6126 | 19.5884 | 19.5611 | 19.5337 | 19.5053 | 19.4779 | 19.4211 | 19.3421 | 19.2516 | 19.1232 | 18.9526 | 18.8
|  | FARNBORO AIRFIELD | HT |  |  |  | 21.6011 | 21.5779 | 21.5547 | 21.5295 | 21.5032 | 21.4768 | 21.4495 | 21.4253 | 21.4042 | 21.3832 | 21.3011 | 21.2379 | 21.1874 | 18.5074 | 18.4663 | 18.4189 | 18.3642 | 18.3084 | 18.1916 | 18.0853 | 18.0042 | 17.9253 | 17.8305 | 17.6663 | 17.4347 | 17.2168 | 19.6253 | 19.5989 | 19.5716 | 19.5411 | 19.5095 | 19.4768 | 19.4316 | 19.3442 | 19.26 | 19.1653 | 19.0011 | 18.7705 | 18.5516
|  | FARNBORO AIRFIELD | HE |  |  |  | 21.6211 | 21.6074 | 21.5926 | 21.5758 | 21.5589 | 21.54 | 21.5221 | 21.5053 | 21.4895 | 21.4758 | 21.4295 | 21.4021 | 7.3179 | 18.5358 | 18.5084 | 18.4737 | 18.4305 | 18.3874 | 18.3316 | 18.2432 | 18.1779 | 18.1137 | 18.0411 | 17.9674 | 17.8474 | 17.7453 | 19.6474 | 19.6305 | 19.6126 | 19.5905 | 19.5695 | 19.5442 | 19.5221 | 19.5021 | 19.4589 | 19.38 | 19.3032 | 19.1821 | 19.08
|  | FARNBORO AIRFIELD | CF |  |  |  | 21.6274 | 21.62 | 21.6116 | 21.6021 | 21.5937 | 21.5842 | 21.5747 | 21.5653 | 21.5568 | 21.5474 | 21.5063 | 21.4853 | 21.4747 | 18.5611 | 18.5453 | 18.5274 | 18.5053 | 18.4853 | 18.4621 | 18.4411 | 18.4221 | 18.4042 | 18.3821 | 18.3305 | 18.2895 | 18.2232 | 19.6568 | 19.6484 | 19.6379 | 19.6263 | 19.6158 | 19.6032 | 19.5916 | 19.5811 | 19.5705 | 19.5589 | 19.5158 | 19.4905 | 19.4768
BRAMLEY (FLEE) | ALDERSHOT BSP | FARNHAM | MINIMUM HEADROOM | SU 84517 47217 | YES | 0.59474 | 24.2589 | 23.9747 | 23.6568 | 23.3042 | 22.9274 | 22.2495 | 21.4295 | 20.9284 | 20.4358 | 19.9779 | 17.9179 | 16.0579 | -22.9979 | 20.1695 | 19.4274 | 18.6274 | 17.5505 | 16.2642 | 14.8579 | 13.9505 | 13.4126 | 12.8789 | 12.3842 | 10.1347 | 8.0811 | 6.1926 | 21.4232 | 20.6821 | 19.8821 | 18.8053 | 17.5179 | 16.1105 | 15.2032 | 14.6653 | 14.1305 | 13.6347 | 11.3832 | 9.3253 | 7.4347
|  | FARNHAM | EE |  |  |  | 24.3684 | 24.1516 | 23.8968 | 23.6084 | 23.2926 | 22.9589 | 22.3558 | 21.8884 | 21.44 | 21.0568 | 19.4284 | 18.0147 | 16.7684 | 20.4126 | 19.7926 | 19.1032 | 18.2147 | 17.1 | 15.8316 | 14.96 | 14.4547 | 13.9705 | 13.5558 | 11.7842 | 10.2179 | 8.8221 | 21.6663 | 21.0474 | 20.3568 | 19.4684 | 18.3537 | 17.0842 | 16.2137 | 15.7074 | 15.2211 | 14.8074 | 13.0295 | 11.4589 | 10.0611
|  | FARNHAM | HT |  |  |  | 24.2589 | 23.9747 | 23.6568 | 23.3042 | 22.9274 | 22.2495 | 21.4295 | 20.9284 | 20.4358 | 19.9779 | 17.9179 | 16.0579 | 14.3642 | 20.1695 | 19.4274 | 18.6274 | 17.5505 | 16.2642 | 14.8579 | 13.9505 | 13.4126 | 12.8789 | 12.3842 | 10.1347 | 8.0811 | 6.1926 | 21.4232 | 20.6821 | 19.8821 | 18.8053 | 17.5179 | 16.1105 | 15.2032 | 14.6653 | 14.1305 | 13.6347 | 11.3832 | 9.3253 | 7.4347
|  | FARNHAM | HE |  |  |  | 24.5158 | 24.3674 | 24.2021 | 23.9821 | 23.7337 | 23.4589 | 23.2232 | 23.02 | 22.7158 | 22.4432 | 21.3547 | 20.4411 | -22.9979 | 20.6821 | 20.2716 | 19.7284 | 18.9779 | 17.9968 | 16.8463 | 16.1011 | 15.7084 | 15.3568 | 15.0621 | 13.8747 | 12.8579 | 11.9758 | 21.8684 | 21.5263 | 20.9821 | 20.2326 | 19.2505 | 18.0989 | 17.3537 | 16.9611 | 16.6095 | 16.3147 | 15.1263 | 14.1063 | 13.2221
|  | FARNHAM | CF |  |  |  | 24.5979 | 24.5126 | 24.4253 | 24.3347 | 24.2337 | 24.1116 | 23.9989 | 23.8937 | 23.7863 | 23.6779 | 23.1937 | 22.9368 | 22.78 | 20.8105 | 20.6674 | 20.4032 | 20.0726 | 19.6726 | 19.2389 | 18.9611 | 18.7547 | 18.5084 | 18.2568 | 17.1011 | 16.3337 | 15.6905 | 21.9695 | 21.86 | 21.6579 | 21.3274 | 20.9263 | 20.4937 | 20.2158 | 20.0084 | 19.7611 | 19.5095 | 18.3537 | 17.5853 | 16.9421
IVER 132KV | SLOUGH | FARNHAM ROYAL | MINIMUM HEADROOM | SU 95597 82844 | YES | 0.30211 | 40.7137 | 40.0905 | 39.4611 | 38.7916 | 38.1011 | 37.3842 | 36.6642 | 36.0526 | 35.2958 | 34.2011 | 28.9653 | 24.4505 | -22.0126 | 37.1158 | 35.8305 | 34.3905 | 33.0832 | 31.8484 | 30.6179 | 29.4053 | 28.1379 | 26.8495 | 25.6211 | 19.8537 | 14.84 | 10.2663 | 38.1789 | 37.3632 | 35.9821 | 34.6747 | 33.44 | 32.2095 | 30.9968 | 29.7358 | 28.4474 | 27.2189 | 21.4495 | 16.4347 | 11.86
|  | FARNHAM ROYAL | EE |  |  |  | 40.9463 | 40.4537 | 39.9326 | 39.3779 | 38.7979 | 38.1958 | 37.6137 | 37.06 | 36.5274 | 36.0747 | 32.4011 | 28.9326 | 25.8589 | 37.5747 | 36.6137 | 35.4389 | 34.3726 | 33.3642 | 32.3526 | 31.3916 | 30.2937 | 29.1895 | 28.2158 | 23.6147 | 19.7516 | 16.2958 | 38.4116 | 37.9189 | 36.9895 | 35.96 | 34.9558 | 33.9442 | 32.9821 | 31.8853 | 30.78 | 29.8126 | 25.2116 | 21.3463 | 17.8884
|  | FARNHAM ROYAL | HT |  |  |  | 40.7137 | 40.0905 | 39.4611 | 38.7916 | 38.1011 | 37.3842 | 36.6642 | 36.0526 | 35.2958 | 34.2011 | 28.9653 | 24.4505 | 20.3621 | 37.1158 | 35.8305 | 34.3905 | 33.0832 | 31.8484 | 30.6179 | 29.4053 | 28.1379 | 26.8495 | 25.6211 | 19.8537 | 14.84 | 10.2663 | 38.1789 | 37.3632 | 35.9821 | 34.6747 | 33.44 | 32.2095 | 30.9968 | 29.7358 | 28.4474 | 27.2189 | 21.4495 | 16.4347 | 11.86
|  | FARNHAM ROYAL | HE |  |  |  | 41.2642 | 40.9211 | 40.5411 | 40.1232 | 39.6716 | 39.1916 | 38.7316 | 38.2968 | 37.8916 | 37.5432 | 36.3379 | 34.3232 | -22.0126 | 37.9642 | 37.5284 | 36.78 | 36.0768 | 35.3663 | 34.6305 | 33.9442 | 33.1158 | 32.2874 | 31.5242 | 28.2032 | 25.6063 | 23.3695 | 38.7295 | 38.3863 | 38.0063 | 37.5884 | 36.9021 | 36.1863 | 35.5158 | 34.7074 | 33.8789 | 33.1158 | 29.7853 | 27.1874 | 24.9516
|  | FARNHAM ROYAL | CF |  |  |  | 41.4558 | 41.26 | 41.0568 | 40.8453 | 40.6274 | 40.4 | 40.1695 | 39.9421 | 39.7179 | 39.4926 | 38.4905 | 37.9895 | 37.3232 | 38.1905 | 37.9695 | 37.7368 | 37.4653 | 37.0432 | 36.5926 | 36.1189 | 35.6705 | 35.1895 | 34.7095 | 32.2147 | 30.3558 | 28.8074 | 38.9211 | 38.7253 | 38.5221 | 38.3105 | 38.0926 | 37.8653 | 37.6347 | 37.2053 | 36.7421 | 36.2811 | 33.8063 | 31.9463 | 30.3968
LALEHAM | EAST BEDFONT A | FELTHAM | MINIMUM HEADROOM | TQ 10628 72811 | YES | 0.070526 | 27.0074 | 26.86 | 26.7116 | 26.5337 | 25.9832 | 24.9495 | 23.9358 | 22.9263 | 21.7042 | 20.4895 | 16.2168 | 14.5463 | 0.70737 | 23.6947 | 23.2821 | 22.5653 | 21.6516 | 20.5516 | 19.2895 | 18.0947 | 16.9295 | 15.5105 | 14.0979 | 9.1579 | 7.2642 | 5.7326 | 24.4463 | 24.2674 | 23.5242 | 22.6126 | 21.5484 | 20.3284 | 19.1726 | 18.0168 | 16.6011 | 15.1905 | 10.2589 | 8.3684 | 6.8379
|  | FELTHAM | EE |  |  |  | 27.06 | 26.9421 | 26.8179 | 26.6863 | 26.5463 | 26.3537 | 25.7158 | 24.9053 | 23.5558 | 22.1358 | 17.5411 | 16.2863 | 15.3253 | 23.7884 | 23.5589 | 23.2379 | 22.7211 | 22.0305 | 21.1242 | 20.2484 | 19.2579 | 17.6558 | 15.9979 | 10.6537 | 9.2305 | 8.14 | 24.5032 | 24.3726 | 24.2242 | 23.6926 | 22.9768 | 22.0989 | 21.2516 | 20.2947 | 18.7421 | 17.0874 | 11.7516 | 10.3316 | 9.2421
|  | FELTHAM | HT |  |  |  | 27.0074 | 26.86 | 26.7116 | 26.5337 | 25.9832 | 24.9495 | 23.9358 | 22.9263 | 21.7042 | 20.4895 | 16.2168 | 14.5463 | 13.1937 | 23.6947 | 23.2821 | 22.5653 | 21.6516 | 20.5516 | 19.2895 | 18.0947 | 16.9295 | 15.5105 | 14.0979 | 9.1579 | 7.2642 | 5.7326 | 24.4463 | 24.2674 | 23.5242 | 22.6126 | 21.5484 | 20.3284 | 19.1726 | 18.0168 | 16.6011 | 15.1905 | 10.2589 | 8.3684 | 6.8379
|  | FELTHAM | HE |  |  |  | 27.1284 | 27.0421 | 26.9474 | 26.8421 | 26.7295 | 26.5789 | 26.1589 | 25.3568 | 24.0568 | 22.7337 | 18.5653 | 17.6021 | 0.70737 | 23.8989 | 23.7305 | 23.4558 | 23.0495 | 22.4253 | 21.5684 | 20.7453 | 19.76 | 18.1958 | 16.6463 | 11.7768 | 10.6747 | 9.9063 | 24.5779 | 24.4811 | 24.3642 | 24.0316 | 23.3726 | 22.5347 | 21.7389 | 20.7874 | 19.2779 | 17.7358 | 12.8737 | 11.7747 | 11.0063
|  | FELTHAM | CF |  |  |  | 27.1695 | 27.1168 | 27.0621 | 27.0042 | 26.9463 | 26.8853 | 26.8232 | 26.7611 | 26.7011 | 26.64 | 22.5463 | 21.54 | 21.0947 | 23.9421 | 23.8874 | 23.8074 | 23.7105 | 23.6084 | 23.5 | 23.3863 | 23.24 | 23.0074 | 22.6221 | 16.3926 | 15.2274 | 14.7158 | 24.6221 | 24.5663 | 24.5074 | 24.4453 | 24.3821 | 24.3147 | 24.2474 | 24.1747 | 23.9968 | 23.5884 | 17.4821 | 16.3189 | 15.8074
MANNINGTON GSP | MANNINGTON BSP | FERNDOWN | MINIMUM HEADROOM | SU 06593 00685 | YES | 6 | 43.2526 | 42.7547 | 42.2516 | 41.7179 | 41.1695 | 40.5916 | 39.8053 | 39.0832 | 38.2484 | 37.3684 | 31.8326 | 26.9989 | -33.7168 | 40.1179 | 39.1558 | 38.1495 | 37.1021 | 35.9884 | 35.0453 | 33.8642 | 32.7253 | 31.6305 | 30.6189 | 24.0484 | 18.5611 | 14.7053 | 41.4421 | 40.5 | 39.5158 | 38.4916 | 37.4021 | 36.4747 | 35.3211 | 34.22 | 33.1695 | 32.1842 | 25.6063 | 20.0379 | 16.1863
|  | FERNDOWN | EE |  |  |  | 43.4526 | 43.0684 | 42.6621 | 42.2295 | 41.7779 | 41.3116 | 40.8611 | 40.2842 | 39.6811 | 39.1368 | 34.3421 | 30.4368 | 27.9305 | 40.5474 | 39.8063 | 38.9958 | 38.1442 | 37.2147 | 36.4505 | 35.4642 | 34.4821 | 33.5263 | 32.6379 | 26.8368 | 22.28 | 19.4716 | 41.7253 | 41.1358 | 40.3442 | 39.5105 | 38.6021 | 37.8495 | 36.8863 | 35.9284 | 34.9968 | 34.1453 | 28.3947 | 23.8305 | 20.9421
|  | FERNDOWN | HT |  |  |  | 43.2526 | 42.7547 | 42.2516 | 41.7179 | 41.1695 | 40.5916 | 39.8053 | 39.0832 | 38.2484 | 37.3684 | 31.8326 | 26.9989 | 23.6358 | 40.1179 | 39.1558 | 38.1495 | 37.1021 | 35.9884 | 35.0453 | 33.8642 | 32.7253 | 31.6305 | 30.6189 | 24.0484 | 18.5611 | 14.7053 | 41.4421 | 40.5 | 39.5158 | 38.4916 | 37.4021 | 36.4747 | 35.3211 | 34.22 | 33.1695 | 32.1842 | 25.6063 | 20.0379 | 16.1863
|  | FERNDOWN | HE |  |  |  | 43.7189 | 43.4611 | 43.1758 | 42.8611 | 42.5221 | 42.1589 | 41.8126 | 41.4853 | 41.18 | 40.8884 | 37.6189 | 34.6663 | -33.7168 | 41.0305 | 40.6505 | 40.1011 | 39.5 | 38.8074 | 38.2632 | 37.4916 | 36.72 | 35.9779 | 35.3116 | 30.5558 | 27.0274 | 25.0189 | 42.0095 | 41.7389 | 41.4232 | 40.8337 | 40.1568 | 39.6189 | 38.8663 | 38.1147 | 37.3916 | 36.7432 | 32.1189 | 28.5021 | 26.4958
|  | FERNDOWN | CF |  |  |  | 43.8726 | 43.7305 | 43.5821 | 43.4284 | 43.2695 | 43.1042 | 42.9358 | 42.7705 | 42.6074 | 42.4442 | 41.2032 | 39.2979 | 38.2347 | 41.2021 | 41.0411 | 40.8116 | 40.48 | 40.1158 | 39.8116 | 39.3958 | 38.9568 | 38.5063 | 38.06 | 34.7337 | 32.3337 | 31.0305 | 42.1716 | 42.0211 | 41.8632 | 41.6989 | 41.4411 | 41.1432 | 40.7368 | 40.3095 | 39.8716 | 39.4379 | 36.24 | 33.8989 | 32.5926
BRAMLEY (FLEE) | FERNHURST | FIVE OAKS | MINIMUM HEADROOM | TQ 10647 29057 | YES | 1.3674 | 14.5811 | 14.2863 | 13.92 | 13.4484 | 12.9011 | 10.8663 | 10.0674 | 9.0926 | 8.9379 | 8.7926 | 4.94 | 2.5221 | -0.77474 | 13.2716 | 12.9495 | 12.5442 | 12.0147 | 11.3968 | 9.0337 | 8.1284 | 7.0126 | 6.8642 | 6.7253 | 2.3368 | -0.26211 | -0.96842 | 13.2211 | 12.9253 | 12.5558 | 12.0537 | 11.4358 | 9.0674 | 8.1558 | 7.0337 | 6.8789 | 6.7337 | 2.2989 | -0.45895 | -1.1874
|  | FIVE OAKS | EE |  |  |  | 14.7011 | 14.4716 | 14.1811 | 14.8989 | 14.7695 | 14.5347 | 13.9495 | 13.5284 | 13.1168 | 12.72 | 10.9053 | 7.5853 | 6.1179 | 13.4032 | 13.1516 | 12.8305 | 14.3442 | 14.2158 | 13.9579 | 13.3032 | 12.8432 | 12.3937 | 11.9621 | 10.0032 | 6.2684 | 4.6137 | 13.3421 | 13.1116 | 12.8189 | 14.7526 | 14.6232 | 14.36 | 13.7 | 13.2316 | 12.7726 | 12.3316 | 10.3084 | 6.5021 | 4.8253
|  | FIVE OAKS | HT |  |  |  | 14.5811 | 14.2863 | 13.92 | 13.4484 | 12.9011 | 10.8663 | 10.0674 | 9.0926 | 8.9379 | 8.7926 | 4.94 | 2.5221 | 1.8526 | 13.2716 | 12.9495 | 12.5442 | 12.0147 | 11.3968 | 9.0337 | 8.1284 | 7.0126 | 6.8642 | 6.7253 | 2.3368 | -0.26211 | -0.96842 | 13.2211 | 12.9253 | 12.5558 | 12.0537 | 11.4358 | 9.0674 | 8.1558 | 7.0337 | 6.8789 | 6.7337 | 2.2989 | -0.45895 | -1.1874
|  | FIVE OAKS | HE |  |  |  | 14.8547 | 14.6989 | 14.4811 | 14.1758 | 13.7379 | 13.1495 | 12.6379 | 12.2895 | 11.9547 | 11.6379 | 10.2421 | 9.0905 | -0.77474 | 13.5705 | 13.3989 | 13.1568 | 12.8116 | 12.3126 | 11.6421 | 11.0621 | 10.6737 | 10.3 | 9.9453 | 8.3863 | 7.1979 | 6.02 | 13.4968 | 13.3389 | 13.1211 | 12.8126 | 12.3526 | 11.6779 | 11.0937 | 10.7011 | 10.3242 | 9.9653 | 8.38 | 7.0568 | 5.8589
|  | FIVE OAKS | CF |  |  |  | 14.94 | 14.8547 | 14.7495 | 14.6284 | 14.4495 | 14.2084 | 13.9779 | 13.8 | 13.6137 | 13.4189 | 12.5 | 13.66 | 13.0126 | 13.6632 | 13.5684 | 13.4516 | 13.3158 | 13.1126 | 12.84 | 12.5789 | 12.38 | 12.1716 | 11.9526 | 10.9158 | 12.9642 | 12.2316 | 13.5821 | 13.4958 | 13.3905 | 13.2684 | 13.0874 | 12.8453 | 12.6116 | 12.4147 | 12.2042 | 11.9842 | 10.9379 | 13.3442 | 12.5979
AMERSHAM | LOUDWATER BSP | FLACKWELL HEATH | MINIMUM HEADROOM | SU 90667 89318 | YES | 0.46316 | 30.4389 | 30.1653 | 29.8874 | 29.5937 | 29.2905 | 28.9779 | 28.6632 | 28.3768 | 28.0663 | 27.7747 | 26.0779 | 24.3421 | 7.8642 | 28.9937 | 28.4663 | 27.9432 | 27.4189 | 26.8968 | 26.38 | 25.8568 | 25.3663 | 24.88 | 24.4126 | 22.2684 | 20.3558 | 18.6484 | 29.4126 | 29.1389 | 28.6284 | 28.1126 | 27.5979 | 27.0874 | 26.5726 | 26.0884 | 25.6084 | 25.1411 | 22.9916 | 21.0758 | 19.3663
|  | FLACKWELL HEATH | EE |  |  |  | 30.5495 | 30.3368 | 30.1126 | 31.3989 | 31.0042 | 30.6095 | 30.2295 | 29.8547 | 29.4716 | 29.1063 | 27.5547 | 26.2347 | 25.0811 | 29.2347 | 28.8295 | 28.4168 | 28.0021 | 27.5821 | 27.1642 | 26.7611 | 26.3642 | 25.9526 | 25.5611 | 23.8726 | 22.4179 | 21.1284 | 29.5232 | 29.3105 | 29.0863 | 28.7326 | 28.3126 | 27.8947 | 27.4916 | 27.0937 | 26.6821 | 26.2884 | 24.5947 | 23.1337 | 21.8421
|  | FLACKWELL HEATH | HT |  |  |  | 30.4389 | 30.1653 | 29.8874 | 29.5937 | 29.2905 | 28.9779 | 28.6632 | 28.3768 | 28.0663 | 27.7747 | 26.0779 | 24.3421 | 22.8053 | 28.9937 | 28.4663 | 27.9432 | 27.4189 | 26.8968 | 26.38 | 25.8568 | 25.3663 | 24.88 | 24.4126 | 22.2684 | 20.3558 | 18.6484 | 29.4126 | 29.1389 | 28.6284 | 28.1126 | 27.5979 | 27.0874 | 26.5726 | 26.0884 | 25.6084 | 25.1411 | 22.9916 | 21.0758 | 19.3663
|  | FLACKWELL HEATH | HE |  |  |  | 30.6958 | 30.5526 | 30.3947 | 30.2211 | 30.0326 | 29.8326 | 29.64 | 29.4589 | 29.2895 | 29.1432 | 28.6484 | 28.2653 | 7.8642 | 29.5484 | 29.3021 | 29.0358 | 28.7611 | 28.4737 | 28.18 | 27.8968 | 27.62 | 27.3284 | 27.0526 | 25.9305 | 25.0053 | 24.2032 | 29.6695 | 29.5263 | 29.3684 | 29.1947 | 29.0063 | 28.8063 | 28.5747 | 28.3 | 28.0126 | 27.7411 | 26.64 | 25.7295 | 24.9263
|  | FLACKWELL HEATH | CF |  |  |  | 30.78 | 30.7 | 30.6179 | 30.5326 | 30.4442 | 30.3516 | 30.2579 | 30.1663 | 30.0747 | 29.9832 | 29.5747 | 29.3716 | 29.2 | 29.6368 | 29.5526 | 29.4011 | 29.2411 | 29.0779 | 28.9105 | 28.7442 | 28.5747 | 28.3916 | 28.2021 | 27.3011 | 26.6137 | 26.0484 | 29.7537 | 29.6737 | 29.5916 | 29.5063 | 29.4179 | 29.3253 | 29.2316 | 29.14 | 29.0484 | 28.8811 | 27.9968 | 27.3253 | 26.7758
NURSLING GSP | ROWNHAMS | FLETCHWOOD | MINIMUM HEADROOM | SU 33800 12142 | YES | 1.2537 | 33.9053 | 33.4811 | 33.0516 | 32.5958 | 32.1274 | 31.6453 | 30.6863 | 29.5232 | 28.2653 | 27.0968 | 23.0274 | 19.7126 | -5.9337 | 29.2947 | 28.4642 | 27.4737 | 26.3442 | 25.3432 | 24.2011 | 22.8347 | 21.5263 | 20.0895 | 18.7537 | 14.4621 | 10.7989 | 7.4863 | 30.1379 | 29.5684 | 28.6032 | 27.4842 | 26.4663 | 25.3032 | 23.9095 | 22.5937 | 21.1568 | 19.8211 | 15.2474 | 11.5379 | 8.1821
|  | FLETCHWOOD | EE |  |  |  | 34.0705 | 33.74 | 33.3895 | 34.8874 | 34.0979 | 33.18 | 32.0832 | 31.0137 | 29.8189 | 28.7189 | 25.3074 | 22.7368 | 20.4737 | 29.5632 | 29.0263 | 28.2116 | 27.3347 | 26.4747 | 25.4674 | 24.2463 | 23.0547 | 21.7116 | 20.4747 | 16.6642 | 14.0695 | 11.5411 | 30.3158 | 29.9663 | 29.3232 | 28.4032 | 27.5432 | 26.5358 | 25.3147 | 24.1221 | 22.7789 | 21.5421 | 17.7305 | 14.8411 | 12.2768
|  | FLETCHWOOD | HT |  |  |  | 33.9053 | 33.4811 | 33.0516 | 32.5958 | 32.1274 | 31.6453 | 30.6863 | 29.5232 | 28.2653 | 27.0968 | 23.0274 | 19.7126 | 16.7326 | 29.2947 | 28.4642 | 27.4737 | 26.3442 | 25.3432 | 24.2011 | 22.8347 | 21.5263 | 20.0895 | 18.7537 | 14.4621 | 10.7989 | 7.4863 | 30.1379 | 29.5684 | 28.6032 | 27.4842 | 26.4663 | 25.3032 | 23.9095 | 22.5937 | 21.1568 | 19.8211 | 15.2474 | 11.5379 | 8.1821
|  | FLETCHWOOD | HE |  |  |  | 34.3042 | 34.0821 | 33.8389 | 33.5695 | 33.28 | 32.9705 | 32.6747 | 32.3958 | 31.7042 | 30.7905 | 28.2495 | 26.3937 | -5.9337 | 29.8126 | 29.5789 | 29.1716 | 28.4253 | 27.7874 | 26.9884 | 25.9789 | 24.9916 | 23.8611 | 22.8126 | 19.8642 | 18.0168 | 16.2274 | 30.5653 | 30.3326 | 30.0684 | 29.5358 | 28.9126 | 28.1358 | 27.1042 | 26.0947 | 24.9368 | 23.88 | 20.9305 | 18.8263 | 17.0095
|  | FLETCHWOOD | CF |  |  |  | 34.4389 | 34.3179 | 34.1926 | 34.0621 | 33.9284 | 33.7895 | 33.6474 | 33.5084 | 33.3705 | 33.2316 | 32.2811 | 31.1295 | 30.0937 | 29.9537 | 29.8263 | 29.6895 | 29.4747 | 29.1474 | 28.7579 | 28.2505 | 27.72 | 27.0789 | 26.4326 | 24.4537 | 23.1389 | 21.9263 | 30.7074 | 30.5789 | 30.4421 | 30.2968 | 30.1516 | 29.8632 | 29.3716 | 28.8589 | 28.2179 | 27.5558 | 25.5326 | 24.2063 | 22.9937
MANNINGTON GSP | MANNINGTON BSP | FORDINGBRIDGE | MINIMUM HEADROOM | SU 14069 15523 | YES | 0.21053 | 17.1021 | 16.7505 | 16.2863 | 15.7642 | 15.0705 | 14.1442 | 13.2558 | 12.6158 | 11.9926 | 11.3842 | 9.3926 | 8.3305 | -0.46316 | 14.8105 | 14.3716 | 13.82 | 13.1968 | 12.3537 | 11.28 | 10.2684 | 9.5432 | 8.8347 | 8.1421 | 5.8926 | 4.7116 | 3.5821 | 15.2537 | 14.8358 | 14.3126 | 13.7232 | 12.9021 | 11.8284 | 10.8168 | 10.0905 | 9.3832 | 8.6895 | 6.44 | 5.2589 | 4.1284
|  | FORDINGBRIDGE | EE |  |  |  | 17.1632 | 16.9326 | 16.5242 | 16.0568 | 15.4137 | 14.5526 | 13.7253 | 13.1274 | 12.5379 | 11.9642 | 10.2168 | 9.4126 | 8.6537 | 14.9463 | 14.5789 | 14.0905 | 13.5274 | 12.7421 | 11.7232 | 10.7758 | 10.0958 | 9.4242 | 8.7705 | 6.7884 | 5.8916 | 5.0326 | 15.3832 | 15.0347 | 14.5726 | 14.0421 | 13.2905 | 12.2716 | 11.3242 | 10.6442 | 9.9726 | 9.3179 | 7.3358 | 6.4379 | 5.58
|  | FORDINGBRIDGE | HT |  |  |  | 17.1021 | 16.7505 | 16.2863 | 15.7642 | 15.0705 | 14.1442 | 13.2558 | 12.6158 | 11.9926 | 11.3842 | 9.3926 | 8.3305 | 7.3253 | 14.8105 | 14.3716 | 13.82 | 13.1968 | 12.3537 | 11.28 | 10.2684 | 9.5432 | 8.8347 | 8.1421 | 5.8926 | 4.7116 | 3.5821 | 15.2537 | 14.8358 | 14.3126 | 13.7232 | 12.9021 | 11.8284 | 10.8168 | 10.0905 | 9.3832 | 8.6895 | 6.44 | 5.2589 | 4.1284
|  | FORDINGBRIDGE | HE |  |  |  | 17.2442 | 17.1642 | 16.8274 | 16.4295 | 15.8516 | 15.0705 | 14.3063 | 13.7674 | 13.2389 | 12.7232 | 11.2558 | 10.7095 | -0.46316 | 15.1232 | 14.8421 | 14.4337 | 13.9505 | 13.2379 | 12.2863 | 11.4074 | 10.7916 | 10.1863 | 9.5947 | 7.9189 | 7.3042 | 6.7116 | 15.4863 | 15.2874 | 14.9032 | 14.4474 | 13.78 | 12.8347 | 11.9547 | 11.34 | 10.7347 | 10.1421 | 8.4663 | 7.8516 | 7.2589
|  | FORDINGBRIDGE | CF |  |  |  | 17.2926 | 17.2495 | 17.2042 | 17.0189 | 16.7611 | 16.4337 | 16.1011 | 15.8411 | 15.5653 | 15.2674 | 14.2811 | 13.9253 | 13.5705 | 15.2179 | 15.0958 | 14.8884 | 14.6579 | 14.3411 | 13.9347 | 13.5221 | 13.2032 | 12.8632 | 12.5011 | 11.3821 | 10.9832 | 10.5768 | 15.5347 | 15.4916 | 15.3337 | 15.1158 | 14.8189 | 14.4389 | 14.0526 | 13.7516 | 13.4116 | 13.0495 | 11.9295 | 11.5305 | 11.1253
LOVEDEAN GSP | PORTSMOUTH BSP | FRATTON PARK | MINIMUM HEADROOM | SU 66139 00180 | YES | 0.36316 | 26.8474 | 26.4305 | 26.0095 | 25.5632 | 25.0926 | 24.6021 | 24.1063 | 23.6621 | 23.2537 | 22.8758 | 19.2979 | 15.1168 | -22.92 | 20.8263 | 19.8179 | 18.9453 | 18.0116 | 16.9632 | 15.9547 | 15.0979 | 14.3011 | 13.5474 | 12.6305 | 8 | 3.3116 | -1.0358 | 21.6747 | 21.2168 | 20.5989 | 19.6863 | 18.6642 | 17.6716 | 16.8137 | 16.0158 | 15.2621 | 14.3463 | 9.7116 | 5.02 | 0.67053
|  | FRATTON PARK | EE |  |  |  | 26.9884 | 26.6516 | 26.2958 | 25.9179 | 25.5137 | 25.0916 | 24.68 | 24.2821 | 23.8947 | 23.5463 | 22.0221 | 18.7168 | 15.7379 | 20.9789 | 20.34 | 19.6305 | 18.8505 | 17.9684 | 17.1032 | 16.4126 | 15.7411 | 15.0789 | 14.4632 | 11.0337 | 7.3211 | 3.9484 | 21.8274 | 21.4558 | 21.0789 | 20.5042 | 19.6432 | 18.7968 | 18.1179 | 17.4579 | 16.7937 | 16.1768 | 12.7453 | 9.0284 | 5.6537
|  | FRATTON PARK | HT |  |  |  | 26.8474 | 26.4305 | 26.0095 | 25.5632 | 25.0926 | 24.6021 | 24.1063 | 23.6621 | 23.2537 | 22.8758 | 19.2979 | 15.1168 | 11.2621 | 20.8263 | 19.8179 | 18.9453 | 18.0116 | 16.9632 | 15.9547 | 15.0979 | 14.3011 | 13.5474 | 12.6305 | 8 | 3.3116 | -1.0358 | 21.6747 | 21.2168 | 20.5989 | 19.6863 | 18.6642 | 17.6716 | 16.8137 | 16.0158 | 15.2621 | 14.3463 | 9.7116 | 5.02 | 0.67053
|  | FRATTON PARK | HE |  |  |  | 27.1674 | 26.9105 | 26.6263 | 26.3126 | 25.9747 | 25.6137 | 25.2695 | 24.9453 | 24.6411 | 24.3789 | 23.4695 | 22.9084 | -22.92 | 21.1737 | 20.8905 | 20.4747 | 19.88 | 19.18 | 18.4947 | 17.9895 | 17.5053 | 17.0516 | 16.6463 | 14.9916 | 12.6442 | 10.2684 | 22.0221 | 21.7379 | 21.44 | 21.1095 | 20.7495 | 20.1505 | 19.6516 | 19.1737 | 18.7274 | 18.3295 | 16.7053 | 14.3589 | 11.9789
|  | FRATTON PARK | CF |  |  |  | 27.2674 | 27.0989 | 26.9232 | 26.7411 | 26.5526 | 26.3579 | 26.1579 | 25.9632 | 25.7695 | 25.5758 | 24.7126 | 24.2747 | 24.0284 | 21.2821 | 21.0968 | 20.9095 | 20.7168 | 20.3484 | 19.9568 | 19.6179 | 19.2842 | 18.9495 | 18.6147 | 17.0684 | 15.5874 | 13.98 | 22.1284 | 21.9453 | 21.7579 | 21.5642 | 21.3632 | 21.1568 | 20.9484 | 20.7453 | 20.5432 | 20.2632 | 18.7463 | 17.3021 | 15.6937
COWLEY GSP | OXFORD BSP | FRENCHAY ROAD | MINIMUM HEADROOM | SP 50426 08256 | YES | 0.24 | 17.9189 | 17.7768 | 17.6337 | 17.4821 | 17.3232 | 17.16 | 16.66 | 16.4095 | 16.1737 | 15.96 | 14.9895 | 14.1768 | 0.65895 | 15.4116 | 14.9979 | 14.7284 | 14.4495 | 14.1695 | 13.8916 | 12.7747 | 12.4789 | 12.2221 | 11.9905 | 10.9242 | 10.0232 | 9.1895 | 15.9747 | 15.7716 | 15.5063 | 15.2326 | 14.9579 | 14.6842 | 13.6042 | 13.3137 | 13.0611 | 12.8337 | 11.7884 | 10.9074 | 10.0937
|  | FRENCHAY ROAD | EE |  |  |  | 17.9705 | 17.8589 | 17.74 | 17.6137 | 17.48 | 17.3421 | 17.1158 | 16.8474 | 16.6421 | 16.4905 | 15.7316 | 15.1316 | 14.5937 | 15.5326 | 15.2716 | 14.9905 | 14.7337 | 14.4853 | 14.2516 | 13.5105 | 13.0811 | 12.7811 | 12.5832 | 11.7463 | 11.0811 | 10.4758 | 16.0305 | 15.9095 | 15.7632 | 15.5116 | 15.2674 | 15.0368 | 14.32 | 13.9021 | 13.6084 | 13.4137 | 12.5937 | 11.9421 | 11.3526
|  | FRENCHAY ROAD | HT |  |  |  | 17.9189 | 17.7768 | 17.6337 | 17.4821 | 17.3232 | 17.16 | 16.66 | 16.4095 | 16.1737 | 15.96 | 14.9895 | 14.1768 | 13.4326 | 15.4116 | 14.9979 | 14.7284 | 14.4495 | 14.1695 | 13.8916 | 12.7747 | 12.4789 | 12.2221 | 11.9905 | 10.9242 | 10.0232 | 9.1895 | 15.9747 | 15.7716 | 15.5063 | 15.2326 | 14.9579 | 14.6842 | 13.6042 | 13.3137 | 13.0611 | 12.8337 | 11.7884 | 10.9074 | 10.0937
|  | FRENCHAY ROAD | HE |  |  |  | 18.0389 | 17.9579 | 17.8684 | 17.7695 | 17.6632 | 17.5505 | 17.4421 | 17.2674 | 17.1147 | 17.0095 | 16.6168 | 16.3589 | 0.65895 | 15.64 | 15.5053 | 15.2926 | 15.1074 | 14.9253 | 14.7589 | 14.0674 | 13.6874 | 13.4684 | 13.3347 | 12.8126 | 12.4516 | 12.1442 | 16.1053 | 16.0168 | 15.92 | 15.8158 | 15.6979 | 15.5337 | 14.8642 | 14.4947 | 14.28 | 14.1484 | 13.6358 | 13.2821 | 12.9821
|  | FRENCHAY ROAD | CF |  |  |  | 18.0758 | 18.0253 | 17.9726 | 17.9179 | 17.8611 | 17.8032 | 17.7432 | 17.6853 | 17.6263 | 17.5684 | 17.2653 | 17.0463 | 16.8937 | 15.6779 | 15.6253 | 15.5611 | 15.4632 | 15.36 | 15.2589 | 15.1505 | 15.0147 | 14.82 | 14.6147 | 13.7158 | 13.3916 | 13.1474 | 16.1442 | 16.0905 | 16.0347 | 15.9768 | 15.9168 | 15.8568 | 15.7937 | 15.7305 | 15.5947 | 15.3947 | 14.5211 | 14.2042 | 13.9663
FAWLEY GSP | COWES & WOOTTON COMMON BSP | FRESHWATER | MINIMUM HEADROOM | SZ 34325 86965 | YES | 0 | 17.2884 | 16.8726 | 16.5126 | 16.1484 | 15.7684 | 15.3579 | 14.9305 | 14.5211 | 14.1295 | 13.7421 | 11.8853 | 10.2063 | 1.2158 | 14.9158 | 14.4611 | 14.0726 | 13.6811 | 13.2726 | 12.8295 | 12.3663 | 11.92 | 11.4905 | 11.0642 | 8.9937 | 7.1011 | 5.4011 | 15.1305 | 14.6758 | 14.2884 | 13.8968 | 13.4895 | 13.0463 | 12.5832 | 12.1368 | 11.7084 | 11.2821 | 9.2137 | 7.3242 | 5.6274
|  | FRESHWATER | EE |  |  |  | 17.4484 | 17.1179 | 16.8326 | 16.5274 | 16.2105 | 15.8916 | 15.5632 | 15.2368 | 14.9421 | 14.6495 | 13.2495 | 11.9389 | 10.78 | 15.0916 | 14.7295 | 14.4221 | 14.0937 | 13.7537 | 13.4116 | 13.0568 | 12.7032 | 12.3853 | 12.0663 | 10.5105 | 9.0274 | 7.7053 | 15.3063 | 14.9442 | 14.6368 | 14.3095 | 13.9695 | 13.6274 | 13.2726 | 12.92 | 12.6021 | 12.2842 | 10.7295 | 9.2484 | 7.9284
|  | FRESHWATER | HT |  |  |  | 17.2884 | 16.8726 | 16.5126 | 16.1484 | 15.7684 | 15.3579 | 14.9305 | 14.5211 | 14.1295 | 13.7421 | 11.8853 | 10.2063 | 8.7063 | 14.9158 | 14.4611 | 14.0726 | 13.6811 | 13.2726 | 12.8295 | 12.3663 | 11.92 | 11.4905 | 11.0642 | 8.9937 | 7.1011 | 5.4011 | 15.1305 | 14.6758 | 14.2884 | 13.8968 | 13.4895 | 13.0463 | 12.5832 | 12.1368 | 11.7084 | 11.2821 | 9.2137 | 7.3242 | 5.6274
|  | FRESHWATER | HE |  |  |  | 17.6674 | 17.44 | 17.2537 | 17.0474 | 16.8263 | 16.5842 | 16.3442 | 16.1032 | 15.8895 | 15.6716 | 14.5663 | 13.6853 | 1.2158 | 15.3305 | 15.0811 | 14.8821 | 14.6621 | 14.4263 | 14.1684 | 13.9105 | 13.6505 | 13.4211 | 13.1832 | 11.9421 | 10.9389 | 9.9874 | 15.5442 | 15.2947 | 15.0968 | 14.8768 | 14.6411 | 14.3832 | 14.1253 | 13.8663 | 13.6368 | 13.3989 | 12.16 | 11.1579 | 10.2084
|  | FRESHWATER | CF |  |  |  | 17.7947 | 17.6621 | 17.5516 | 17.4242 | 17.2853 | 17.1316 | 16.9737 | 16.8211 | 16.6779 | 16.5347 | 15.9884 | 15.3632 | 14.8316 | 15.4695 | 15.3242 | 15.2042 | 15.0642 | 14.9126 | 14.7432 | 14.5695 | 14.4021 | 14.2442 | 14.0884 | 13.4979 | 12.7853 | 12.1716 | 15.6832 | 15.5379 | 15.4189 | 15.2789 | 15.1263 | 14.9579 | 14.7842 | 14.6168 | 14.46 | 14.3042 | 13.7137 | 13.0021 | 12.3895
BRAMLEY (FLEE) | CAMBERLEY RESERVE | FRIMLEY | MINIMUM HEADROOM | SU 87745 57942 | YES | 0.46316 | 35.8242 | 35.4074 | 34.9842 | 34.5358 | 33.2421 | 31.9589 | 31.1495 | 30.4042 | 29.7116 | 29.0568 | 26.0158 | 22.7589 | -11.9642 | 29.8516 | 28.4495 | 26.8326 | 25.4516 | 23.9568 | 22.5368 | 21.6737 | 20.8758 | 20.1347 | 19.4316 | 16.1442 | 12.3863 | 9.6537 | 31.4074 | 30.0274 | 28.3937 | 27.0116 | 25.5158 | 24.0937 | 23.2274 | 22.4274 | 21.6821 | 20.9768 | 17.6663 | 13.7979 | 11.0537
|  | FRIMLEY | EE |  |  |  | 35.9895 | 35.6653 | 35.3211 | 34.9537 | 34.1916 | 33.0347 | 32.3726 | 32.1463 | 31.5316 | 30.9653 | 28.4926 | 26.2611 | 24.4105 | 30.2095 | 29.0242 | 27.5905 | 26.3442 | 24.9832 | 23.7 | 22.9926 | 22.9558 | 22.3011 | 21.6979 | 19.04 | 16.6105 | 14.5516 | 31.7284 | 30.6095 | 29.1516 | 27.9042 | 26.5442 | 25.2568 | 24.5453 | 24.5884 | 23.9295 | 23.3221 | 20.6326 | 18.1653 | 16.0937
|  | FRIMLEY | HT |  |  |  | 35.8242 | 35.4074 | 34.9842 | 34.5358 | 33.2421 | 31.9589 | 31.1495 | 30.4042 | 29.7116 | 29.0568 | 26.0158 | 22.7589 | 20.2958 | 29.8516 | 28.4495 | 26.8326 | 25.4516 | 23.9568 | 22.5368 | 21.6737 | 20.8758 | 20.1347 | 19.4316 | 16.1442 | 12.3863 | 9.6537 | 31.4074 | 30.0274 | 28.3937 | 27.0116 | 25.5158 | 24.0937 | 23.2274 | 22.4274 | 21.6821 | 20.9768 | 17.6663 | 13.7979 | 11.0537
|  | FRIMLEY | HE |  |  |  | 36.2147 | 35.9979 | 35.7579 | 35.4926 | 35.2063 | 34.4779 | 33.9926 | 33.5274 | 33.0905 | 32.6979 | 30.6684 | 29.2579 | -11.9642 | 30.6937 | 29.7389 | 28.5316 | 27.5105 | 26.3589 | 25.2663 | 24.7495 | 24.2547 | 23.7895 | 23.3716 | 20.9789 | 19.4158 | 18.0989 | 32.0242 | 31.3074 | 30.1011 | 29.0716 | 27.92 | 26.8242 | 26.3063 | 25.8095 | 25.3432 | 24.9221 | 22.4337 | 20.86 | 19.5347
|  | FRIMLEY | CF |  |  |  | 36.3442 | 36.2232 | 36.0979 | 35.9684 | 35.8337 | 35.6905 | 35.5453 | 35.4021 | 35.2611 | 35.12 | 34.4874 | 33.8453 | 33.0263 | 31.1 | 30.5779 | 29.9926 | 29.5105 | 28.9874 | 28.4926 | 28.1789 | 27.88 | 27.5905 | 27.2916 | 25.7832 | 24.6632 | 23.7411 | 32.1589 | 32.0253 | 31.5547 | 31.0884 | 30.5695 | 30.0632 | 29.7421 | 29.4389 | 29.1474 | 28.8484 | 27.3358 | 26.2095 | 25.2811
MELKSHAM GSP | FROME BSP | FROME | MINIMUM HEADROOM | ST 78850 48051 | YES | 1.8674 | 52.46 | 51.9411 | 51.3884 | 50.0316 | 48.7684 | 47.1842 | 45.8484 | 43.9937 | 42.2958 | 40.88 | 34.0842 | 26.8789 | -12.5179 | 43.5989 | 42.1516 | 40.1558 | 38.2663 | 36.5453 | 34.7589 | 33.3295 | 31.2811 | 29.3916 | 27.8284 | 20.6653 | 12.2632 | 7.5232 | 43.2747 | 42.2937 | 41.0347 | 39.7947 | 38.0516 | 36.2326 | 34.7747 | 32.6968 | 30.7958 | 29.22 | 22.0389 | 13.4611 | 8.68
|  | FROME | EE |  |  |  | 52.6484 | 52.2337 | 51.7937 | 51.3642 | 49.9674 | 48.4863 | 47.32 | 45.5832 | 43.9695 | 42.6505 | 35.9389 | 30.9758 | 27.6316 | 44.0358 | 42.8105 | 41.0105 | 39.4095 | 37.8547 | 36.2211 | 34.9611 | 33.0284 | 31.2421 | 29.7947 | 22.3874 | 17.3432 | 13.6253 | 43.5853 | 42.7653 | 41.6463 | 40.8463 | 39.2905 | 37.6463 | 36.3716 | 34.4232 | 32.6179 | 31.1505 | 23.6095 | 18.4789 | 14.7074
|  | FROME | HT |  |  |  | 52.46 | 51.9411 | 51.3884 | 50.0316 | 48.7684 | 47.1842 | 45.8484 | 43.9937 | 42.2958 | 40.88 | 34.0842 | 26.8789 | 22.6232 | 43.5989 | 42.1516 | 40.1558 | 38.2663 | 36.5453 | 34.7589 | 33.3295 | 31.2811 | 29.3916 | 27.8284 | 20.6653 | 12.2632 | 7.5232 | 43.2747 | 42.2937 | 41.0347 | 39.7947 | 38.0516 | 36.2326 | 34.7747 | 32.6968 | 30.7958 | 29.22 | 22.0389 | 13.4611 | 8.68
|  | FROME | HE |  |  |  | 52.9221 | 52.6368 | 52.3221 | 51.9716 | 51.0516 | 50.0526 | 49.2863 | 47.8716 | 46.5126 | 45.4484 | 40.0737 | 35.4179 | -12.5179 | 44.6421 | 43.7042 | 42.1789 | 40.7505 | 39.4663 | 38.0968 | 37.1011 | 35.4484 | 33.9463 | 32.7695 | 26.7116 | 21.2295 | 18.5505 | 44.0274 | 43.4179 | 42.5011 | 41.6158 | 40.7884 | 39.6084 | 38.5958 | 36.9116 | 35.38 | 34.1863 | 28.0811 | 22.5284 | 19.8137
|  | FROME | CF |  |  |  | 53.0779 | 52.9137 | 52.7432 | 52.5653 | 52.3821 | 52.1779 | 51.9726 | 51.5053 | 50.8979 | 50.3653 | 47.0547 | 44.2432 | 42.6726 | 45.0242 | 44.6326 | 43.8905 | 43.2316 | 42.5021 | 41.6979 | 41.0484 | 40.1284 | 39.2537 | 38.5021 | 34.5084 | 31.3242 | 29.5621 | 44.3347 | 44.0189 | 43.5642 | 43.1474 | 42.6926 | 42.1874 | 41.7611 | 41.1989 | 40.6621 | 40.0074 | 35.9379 | 32.7242 | 30.9389
COWLEY GSP | HIGH WYCOMBE BSP | FRYERS LANE | MINIMUM HEADROOM | SU 84935 93873 | YES | 0.69474 | 23.0684 | 22.7158 | 22.3589 | 21.98 | 21.5884 | 21.1832 | 20.7747 | 20.4158 | 20.0884 | 19.7874 | 17.3326 | 14.8832 | -10.4821 | 19.6568 | 19.0074 | 18.3326 | 17.6516 | 16.9747 | 16.3053 | 15.6232 | 14.9747 | 14.3147 | 13.6779 | 10.7095 | 8.0168 | 5.5179 | 20.1853 | 19.8116 | 19.1916 | 18.5274 | 17.8516 | 17.1779 | 16.4905 | 15.8368 | 15.1705 | 14.5274 | 11.5284 | 8.8032 | 6.3074
|  | FRYERS LANE | EE |  |  |  | 23.2011 | 22.9232 | 22.6295 | 22.3158 | 21.9884 | 21.6474 | 21.32 | 21.0074 | 20.7063 | 20.4368 | 19.2305 | 17.3568 | 15.6916 | 19.8116 | 19.4526 | 18.9232 | 18.3768 | 17.8295 | 17.2811 | 16.7484 | 16.2179 | 15.6558 | 15.1189 | 12.7684 | 10.7032 | 8.8516 | 20.3284 | 20.0347 | 19.7253 | 19.2305 | 18.6958 | 18.16 | 17.6263 | 17.0905 | 16.5242 | 15.9832 | 13.6063 | 11.5168 | 9.64
|  | FRYERS LANE | HT |  |  |  | 23.0684 | 22.7158 | 22.3589 | 21.98 | 21.5884 | 21.1832 | 20.7747 | 20.4158 | 20.0884 | 19.7874 | 17.3326 | 14.8832 | 12.6547 | 19.6568 | 19.0074 | 18.3326 | 17.6516 | 16.9747 | 16.3053 | 15.6232 | 14.9747 | 14.3147 | 13.6779 | 10.7095 | 8.0168 | 5.5179 | 20.1853 | 19.8116 | 19.1916 | 18.5274 | 17.8516 | 17.1779 | 16.4905 | 15.8368 | 15.1705 | 14.5274 | 11.5284 | 8.8032 | 6.3074
|  | FRYERS LANE | HE |  |  |  | 23.3821 | 23.1884 | 22.9747 | 22.7379 | 22.4842 | 22.2126 | 21.9526 | 21.7084 | 21.48 | 21.2832 | 20.6168 | 20.2221 | -10.4821 | 20.0221 | 19.8095 | 19.5779 | 19.3105 | 18.9505 | 18.5589 | 18.1779 | 17.8 | 17.3916 | 17.0095 | 15.4063 | 14.0505 | 12.8768 | 20.5242 | 20.3211 | 20.0989 | 19.8526 | 19.5905 | 19.3116 | 19.0221 | 18.6526 | 18.2537 | 17.8821 | 16.2716 | 14.8989 | 13.7084
|  | FRYERS LANE | CF |  |  |  | 23.4874 | 23.3758 | 23.26 | 23.1389 | 23.0147 | 22.8853 | 22.7537 | 22.6242 | 22.4947 | 22.3674 | 21.7958 | 21.5105 | 21.3516 | 20.14 | 20.0147 | 19.8863 | 19.7516 | 19.6147 | 19.4716 | 19.2663 | 19.0368 | 18.7758 | 18.5105 | 17.2242 | 16.2263 | 15.3874 | 20.6358 | 20.5179 | 20.3958 | 20.2674 | 20.1368 | 20.0011 | 19.8632 | 19.7274 | 19.5895 | 19.3589 | 18.1021 | 17.0905 | 16.24
COWLEY GSP | DRAYTON BSP | FULSCOT | MINIMUM HEADROOM | SU 54413 89511 | YES | 7.9579 | 16.3637 | 16.1437 | 15.7784 | 14.6795 | 13.4584 | 12.6226 | 11.7763 | 10.8405 | 9.8037 | 8.8016 | 4.6437 | 2.31 | -29.6921 | 12.2132 | 11.5479 | 9.8553 | 8.6205 | 7.2426 | 6.3216 | 5.3868 | 4.3395 | 3.1689 | 2.0353 | -2.6742 | -5.2837 | -7.6247 | 12.7268 | 12.1479 | 10.4553 | 9.2205 | 7.8447 | 6.9247 | 5.9911 | 4.9458 | 3.7763 | 2.6447 | -2.0584 | -4.6637 | -7.0016
|  | FULSCOT | EE |  |  |  | 16.4805 | 16.3247 | 16.0342 | 15.2626 | 14.1447 | 13.4089 | 12.6732 | 11.8184 | 10.8458 | 9.9111 | 6.1742 | 4.3584 | 2.8826 | 12.4468 | 11.9447 | 10.3711 | 9.2542 | 7.9889 | 7.1742 | 6.3584 | 5.3995 | 4.2995 | 3.2405 | -1.0111 | -3.0511 | -4.7142 | 12.8532 | 12.5458 | 10.9711 | 9.8542 | 8.5911 | 7.7763 | 6.9616 | 6.0047 | 4.9058 | 3.8479 | -0.39632 | -2.4332 | -4.0953
|  | FULSCOT | HT |  |  |  | 16.3637 | 16.1437 | 15.7784 | 14.6795 | 13.4584 | 12.6226 | 11.7763 | 10.8405 | 9.8037 | 8.8016 | 4.6437 | 2.31 | 0.22895 | 12.2132 | 11.5479 | 9.8553 | 8.6205 | 7.2426 | 6.3216 | 5.3868 | 4.3395 | 3.1689 | 2.0353 | -2.6742 | -5.2837 | -7.6247 | 12.7268 | 12.1479 | 10.4553 | 9.2205 | 7.8447 | 6.9247 | 5.9911 | 4.9458 | 3.7763 | 2.6447 | -2.0584 | -4.6637 | -7.0016
|  | FULSCOT | HE |  |  |  | 16.6416 | 16.5616 | 16.3732 | 16.0426 | 15.0605 | 14.4489 | 13.8384 | 13.1047 | 12.2553 | 11.4395 | 8.2826 | 7.0047 | -29.6921 | 12.6174 | 12.4711 | 11.0637 | 10.1037 | 8.9868 | 8.3079 | 7.6279 | 6.8005 | 5.8353 | 4.9047 | 1.2879 | -0.15737 | -1.2616 | 13.0247 | 12.9489 | 11.6637 | 10.7037 | 9.5868 | 8.9089 | 8.23 | 7.4037 | 6.4395 | 5.5111 | 1.9005 | 0.45632 | -0.64474
|  | FULSCOT | CF |  |  |  | 16.7342 | 16.6426 | 16.5468 | 16.4479 | 16.3363 | 16.2132 | 16.1774 | 16.0111 | 15.5247 | 15.0142 | 12.7953 | 11.8953 | 11.2837 | 12.7142 | 12.6142 | 12.0658 | 11.5995 | 11.0847 | 10.7563 | 10.5268 | 10.0805 | 9.5268 | 8.9458 | 6.4184 | 5.3995 | 4.7026 | 13.1247 | 13.0216 | 12.6805 | 12.2153 | 11.7016 | 11.3721 | 11.1279 | 10.6805 | 10.1268 | 9.5458 | 7.0226 | 6.0058 | 5.31
COWLEY GSP | WITNEY BSP | FYFIELD | MINIMUM HEADROOM | SU 42256 99551 | YES | 0.14737 | 18.0726 | 17.8926 | 17.7116 | 17.5179 | 17.0853 | 16.1747 | 15.2579 | 14.3726 | 13.5084 | 13.2253 | 11.9232 | 9.1 | -1.5274 | 15.2495 | 14.9021 | 14.5611 | 14.0937 | 13.2053 | 12.1779 | 11.1453 | 10.1442 | 9.1674 | 8.8726 | 7.5211 | 4.3663 | 3.4547 | 15.8547 | 15.5032 | 15.1568 | 14.68 | 13.7611 | 12.7295 | 11.6926 | 10.6863 | 9.7042 | 9.4032 | 8.0053 | 4.8011 | 3.8695
|  | FYFIELD | EE |  |  |  | 18.1442 | 18.0063 | 17.8589 | 17.7 | 17.3484 | 16.5126 | 15.6758 | 14.8463 | 14.0274 | 13.7779 | 12.6547 | 11.6537 | 10.0558 | 15.4032 | 15.1368 | 14.8663 | 14.4663 | 13.6358 | 12.6884 | 11.7242 | 10.7695 | 9.8263 | 9.5695 | 8.4316 | 7.4263 | 5.5863 | 15.9895 | 15.7411 | 15.4653 | 15.0589 | 14.2074 | 13.2379 | 12.2674 | 11.3053 | 10.3568 | 10.0895 | 8.8874 | 7.8063 | 5.9463
|  | FYFIELD | HT |  |  |  | 18.0726 | 17.8926 | 17.7116 | 17.5179 | 17.0853 | 16.1747 | 15.2579 | 14.3726 | 13.5084 | 13.2253 | 11.9232 | 9.1 | 8.2442 | 15.2495 | 14.9021 | 14.5611 | 14.0937 | 13.2053 | 12.1779 | 11.1453 | 10.1442 | 9.1674 | 8.8726 | 7.5211 | 4.3663 | 3.4547 | 15.8547 | 15.5032 | 15.1568 | 14.68 | 13.7611 | 12.7295 | 11.6926 | 10.6863 | 9.7042 | 9.4032 | 8.0053 | 4.8011 | 3.8695
|  | FYFIELD | HE |  |  |  | 18.2432 | 18.1526 | 18.0526 | 17.9411 | 17.8211 | 17.1368 | 16.3874 | 15.6432 | 14.9158 | 14.7537 | 14.1032 | 13.6021 | -1.5274 | 15.5411 | 15.4432 | 15.2726 | 14.9674 | 14.2242 | 13.3684 | 12.4979 | 11.6305 | 10.78 | 10.6126 | 9.94 | 9.4126 | 8.5874 | 16.0884 | 15.9979 | 15.88 | 15.5684 | 14.8053 | 13.9242 | 13.0474 | 12.1779 | 11.3253 | 11.1537 | 10.4537 | 9.9042 | 9.0621
|  | FYFIELD | CF |  |  |  | 18.3 | 18.2505 | 18.2 | 18.1474 | 18.0926 | 18.0284 | 17.9368 | 17.5547 | 17.1526 | 17.0442 | 16.5442 | 16.1895 | 15.6189 | 15.5989 | 15.5495 | 15.4979 | 15.3621 | 15.0284 | 14.6579 | 14.2537 | 13.82 | 13.3611 | 13.2442 | 12.7084 | 12.3284 | 11.6768 | 16.1453 | 16.0958 | 16.0453 | 15.9705 | 15.6274 | 15.2442 | 14.8284 | 14.3821 | 13.9095 | 13.7916 | 13.2484 | 12.8568 | 12.1926
LOVEDEAN GSP | HAVANT | GABLE HEAD | MINIMUM HEADROOM | SZ 72204 99904 | YES | 0 | 33.7221 | 33.2116 | 32.6105 | 31.9432 | 30.9347 | 29.8274 | 28.8368 | 27.9495 | 27.1221 | 26.2695 | 23.3463 | 21 | 4.9179 | 29.7505 | 29.0011 | 28.3621 | 27.6442 | 26.5211 | 25.2832 | 24.1853 | 23.2 | 22.28 | 21.3253 | 18.0947 | 15.4926 | 12.2926 | 30.2379 | 29.5053 | 28.88 | 28.1684 | 27.0463 | 25.8095 | 24.7116 | 23.7274 | 22.8074 | 21.8516 | 18.6158 | 16.0084 | 12.8095
|  | GABLE HEAD | EE |  |  |  | 33.8589 | 33.5958 | 33.1537 | 32.6253 | 31.7832 | 30.8495 | 30.0053 | 29.2253 | 28.5316 | 27.8263 | 25.6579 | 23.94 | 21.7453 | 30.0442 | 29.4484 | 28.9432 | 28.3811 | 27.4484 | 26.4032 | 25.4632 | 24.5979 | 23.8305 | 23.0453 | 20.6653 | 18.7674 | 16.2611 | 30.5242 | 29.9421 | 29.4474 | 28.8968 | 27.9726 | 26.9295 | 25.9884 | 25.1221 | 24.3537 | 23.5684 | 21.1789 | 19.2684 | 16.7621
|  | GABLE HEAD | HT |  |  |  | 33.7221 | 33.2116 | 32.6105 | 31.9432 | 30.9347 | 29.8274 | 28.8368 | 27.9495 | 27.1221 | 26.2695 | 23.3463 | 21 | 18.1832 | 29.7505 | 29.0011 | 28.3621 | 27.6442 | 26.5211 | 25.2832 | 24.1853 | 23.2 | 22.28 | 21.3253 | 18.0947 | 15.4926 | 12.2926 | 30.2379 | 29.5053 | 28.88 | 28.1684 | 27.0463 | 25.8095 | 24.7116 | 23.7274 | 22.8074 | 21.8516 | 18.6158 | 16.0084 | 12.8095
|  | GABLE HEAD | HE |  |  |  | 34.0379 | 33.86 | 33.6621 | 33.4453 | 32.7916 | 31.9905 | 31.2863 | 30.6526 | 30.0979 | 29.5189 | 27.9916 | 26.9074 | 4.9179 | 30.4326 | 30.0221 | 29.6926 | 29.3021 | 28.5442 | 27.6495 | 26.86 | 26.1537 | 25.5379 | 24.8874 | 23.2 | 21.9895 | 20.1011 | 30.8589 | 30.5032 | 30.1789 | 29.7958 | 29.0611 | 28.1737 | 27.3853 | 26.6789 | 26.0632 | 25.4116 | 23.7221 | 22.5084 | 20.62
|  | GABLE HEAD | CF |  |  |  | 34.1421 | 34.0421 | 33.9389 | 33.8316 | 33.72 | 33.4168 | 33.04 | 32.6642 | 32.3011 | 31.9063 | 30.8611 | 30.1211 | 29.0684 | 30.6547 | 30.4126 | 30.2189 | 29.9916 | 29.6158 | 29.2042 | 28.7905 | 28.3705 | 27.9621 | 27.5168 | 26.3768 | 25.5516 | 24.3358 | 30.9695 | 30.8611 | 30.6937 | 30.4726 | 30.1084 | 29.7095 | 29.3074 | 28.8947 | 28.4863 | 28.0411 | 26.9 | 26.0737 | 24.8579
MINETY GSP |  | GALILEO | MINIMUM HEADROOM | SU 10596 83733 | YES | 0.31368 | 50.8821 | 50.7568 | 50.6305 | 50.4958 | 50.3568 | 50.2137 | 50.0695 | 49.9442 | 49.8284 | 49.7211 | 49.3263 | 48.6211 | 26.0611 | 46.6021 | 46.4611 | 46.2895 | 46.0411 | 45.7905 | 45.5442 | 45.2916 | 45.0621 | 44.8505 | 44.6505 | 43.7389 | 42.4611 | 41.2453 | 47.8168 | 47.6916 | 47.5653 | 47.4242 | 47.1832 | 46.9358 | 46.6842 | 46.4537 | 46.2421 | 46.0432 | 45.1358 | 43.8579 | 42.6442
|  | GALILEO | EE |  |  |  | 50.9284 | 50.8295 | 50.7242 | 50.6126 | 50.4968 | 50.3758 | 50.26 | 50.1495 | 50.0421 | 49.9474 | 49.6368 | 49.4011 | 48.7095 | 46.6537 | 46.5442 | 46.4274 | 46.3053 | 46.1011 | 45.8968 | 45.7 | 45.5095 | 45.32 | 45.1526 | 44.4779 | 43.4758 | 42.5263 | 47.8632 | 47.7642 | 47.6589 | 47.5474 | 47.4284 | 47.2884 | 47.0916 | 46.9011 | 46.7126 | 46.5442 | 45.8737 | 44.8705 | 43.9221
|  | GALILEO | HT |  |  |  | 50.8821 | 50.7568 | 50.6305 | 50.4958 | 50.3568 | 50.2137 | 50.0695 | 49.9442 | 49.8284 | 49.7211 | 49.3263 | 48.6211 | 47.5526 | 46.6021 | 46.4611 | 46.2895 | 46.0411 | 45.7905 | 45.5442 | 45.2916 | 45.0621 | 44.8505 | 44.6505 | 43.7389 | 42.4611 | 41.2453 | 47.8168 | 47.6916 | 47.5653 | 47.4242 | 47.1832 | 46.9358 | 46.6842 | 46.4537 | 46.2421 | 46.0432 | 45.1358 | 43.8579 | 42.6442
|  | GALILEO | HE |  |  |  | 50.9947 | 50.9274 | 50.8526 | 50.7705 | 50.6821 | 50.5874 | 50.4968 | 50.4116 | 50.3316 | 50.2632 | 49.9926 | 49.8568 | 26.0611 | 46.72 | 46.6526 | 46.5758 | 46.4863 | 46.3916 | 46.1663 | 46 | 45.8305 | 45.6705 | 45.5926 | 45.2232 | 44.4842 | 43.7726 | 47.9295 | 47.8621 | 47.7874 | 47.7053 | 47.6168 | 47.5179 | 47.3916 | 47.2221 | 47.0632 | 46.9832 | 46.6084 | 45.8705 | 45.1589
|  | GALILEO | CF |  |  |  | 51.0337 | 50.9958 | 50.9568 | 50.9158 | 50.8737 | 50.8305 | 50.7853 | 50.7411 | 50.6968 | 50.6537 | 50.4611 | 50.3621 | 50.3084 | 46.7589 | 46.7211 | 46.6821 | 46.6411 | 46.5947 | 46.5484 | 46.4789 | 46.4032 | 46.3179 | 46.2347 | 45.9105 | 45.5705 | 45.1158 | 47.9684 | 47.9305 | 47.8916 | 47.8505 | 47.8084 | 47.7653 | 47.72 | 47.6758 | 47.6295 | 47.5842 | 47.3011 | 46.9632 | 46.5074
LOVEDEAN GSP | WYMERING BSP | GAMBLE ROAD | MINIMUM HEADROOM | SU 64771 01769 | YES | 0.38947 | 35.5842 | 35.2032 | 34.8084 | 34.3811 | 33.2232 | 30.9011 | 28.5789 | 26.3021 | 24.0568 | 22.4695 | 16.3674 | 13.1632 | -9.5695 | 30.6842 | 29.8421 | 28.5989 | 27.1811 | 24.8421 | 22.2211 | 19.6011 | 16.9968 | 14.4126 | 12.5968 | 5.6432 | 2.0526 | -1.3074 | 31.5968 | 30.8811 | 29.6221 | 28.1853 | 25.8116 | 23.1516 | 20.4926 | 17.88 | 15.3 | 13.4874 | 6.5442 | 2.9589 | -0.39579
|  | GAMBLE ROAD | EE |  |  |  | 35.7137 | 35.4389 | 35.1021 | 34.7389 | 34.3411 | 32.7811 | 30.5811 | 28.3926 | 26.2158 | 24.0716 | 17.8337 | 15.32 | 13.0263 | 30.8516 | 30.5211 | 29.5989 | 28.3074 | 26.8368 | 24.3284 | 21.8379 | 19.36 | 16.8568 | 14.3811 | 7.2263 | 4.4021 | 1.8053 | 31.7232 | 31.4526 | 30.6347 | 29.3253 | 27.8347 | 25.2884 | 22.76 | 20.2442 | 17.74 | 15.2695 | 8.1253 | 5.3053 | 2.7126
|  | GAMBLE ROAD | HT |  |  |  | 35.5842 | 35.2032 | 34.8084 | 34.3811 | 33.2232 | 30.9011 | 28.5789 | 26.3021 | 24.0568 | 22.4695 | 16.3674 | 13.1632 | 10.1832 | 30.6842 | 29.8421 | 28.5989 | 27.1811 | 24.8421 | 22.2211 | 19.6011 | 16.9968 | 14.4126 | 12.5968 | 5.6432 | 2.0526 | -1.3074 | 31.5968 | 30.8811 | 29.6221 | 28.1853 | 25.8116 | 23.1516 | 20.4926 | 17.88 | 15.3 | 13.4874 | 6.5442 | 2.9589 | -0.39579
|  | GAMBLE ROAD | HE |  |  |  | 35.8526 | 35.6389 | 35.3653 | 35.0568 | 34.72 | 34.3274 | 33.1 | 31.6095 | 30.1389 | 28.7042 | 21.8295 | 18.7726 | -9.5695 | 31.0421 | 30.7968 | 30.3253 | 29.2926 | 28.1095 | 26.3863 | 24.6842 | 23.0042 | 21.3442 | 19.7211 | 11.7705 | 8.2537 | 6.4758 | 31.86 | 31.6484 | 31.3705 | 30.3242 | 29.1242 | 27.3758 | 25.6495 | 23.9442 | 22.2589 | 20.6105 | 12.6642 | 9.1526 | 7.3768
|  | GAMBLE ROAD | CF |  |  |  | 35.9326 | 35.7884 | 35.6368 | 35.46 | 35.2747 | 35.0821 | 34.8705 | 34.6568 | 34.44 | 34.0011 | 29.3116 | 26.6347 | 25.5674 | 31.1389 | 30.9695 | 30.7853 | 30.5147 | 30.0484 | 29.42 | 28.5758 | 27.6726 | 26.7126 | 25.6916 | 20.3863 | 17.32 | 16.1 | 31.9389 | 31.7958 | 31.6463 | 31.4747 | 31.0895 | 30.4526 | 29.5968 | 28.6811 | 27.7063 | 26.6705 | 21.2853 | 18.2032 | 16.9853
IVER 132KV | DENHAM | GERRARDS CROSS | MINIMUM HEADROOM | SU 99973 87964 | YES | 0 | 17.1842 | 16.9674 | 16.7495 | 16.5168 | 16.2789 | 16.0316 | 15.7842 | 15.5674 | 15.3705 | 15.1895 | 14.0853 | 12.7179 | -8.2547 | 13.4832 | 13.1516 | 12.7453 | 12.3347 | 11.9274 | 11.5295 | 11.1253 | 10.7463 | 10.3632 | 9.9947 | 8.32 | 6.82 | 5.4632 | 14.3842 | 14.1411 | 13.8989 | 13.6368 | 13.2389 | 12.8495 | 12.4474 | 12.0642 | 11.6768 | 11.3053 | 9.6084 | 8.0926 | 6.7337
|  | GERRARDS CROSS | EE |  |  |  | 17.2737 | 17.1074 | 16.9316 | 18.3716 | 18.0632 | 17.7589 | 17.4611 | 17.1684 | 16.8653 | 16.5811 | 15.3547 | 14.3137 | 13.4179 | 13.6032 | 13.3916 | 13.1179 | 12.8453 | 12.5168 | 12.1958 | 11.88 | 11.5695 | 11.2442 | 10.94 | 9.6074 | 8.46 | 7.46 | 14.4863 | 14.3011 | 14.1063 | 14.1305 | 13.8011 | 13.48 | 13.1642 | 12.8526 | 12.5274 | 12.22 | 10.8821 | 9.7284 | 8.7253
|  | GERRARDS CROSS | HT |  |  |  | 17.1842 | 16.9674 | 16.7495 | 16.5168 | 16.2789 | 16.0316 | 15.7842 | 15.5674 | 15.3705 | 15.1895 | 14.0853 | 12.7179 | 11.5011 | 13.4832 | 13.1516 | 12.7453 | 12.3347 | 11.9274 | 11.5295 | 11.1253 | 10.7463 | 10.3632 | 9.9947 | 8.32 | 6.82 | 5.4632 | 14.3842 | 14.1411 | 13.8989 | 13.6368 | 13.2389 | 12.8495 | 12.4474 | 12.0642 | 11.6768 | 11.3053 | 9.6084 | 8.0926 | 6.7337
|  | GERRARDS CROSS | HE |  |  |  | 17.3905 | 17.2811 | 17.16 | 17.0253 | 16.8811 | 16.7253 | 16.5779 | 16.4379 | 16.3074 | 16.1947 | 15.8126 | 15.5905 | -8.2547 | 13.7379 | 13.6168 | 13.48 | 13.32 | 13.1516 | 12.9484 | 12.7316 | 12.5147 | 12.2863 | 12.0747 | 11.1916 | 10.46 | 9.8368 | 14.6211 | 14.5011 | 14.3684 | 14.2232 | 14.0695 | 13.9053 | 13.7474 | 13.5979 | 13.4537 | 13.3284 | 12.5095 | 11.7674 | 11.1326
|  | GERRARDS CROSS | CF |  |  |  | 17.4558 | 17.3947 | 17.3316 | 17.2663 | 17.1979 | 17.1263 | 17.0537 | 16.9832 | 16.9137 | 16.8421 | 16.5274 | 16.3695 | 16.2821 | 13.8095 | 13.7411 | 13.6705 | 13.5968 | 13.5126 | 13.4242 | 13.3326 | 13.2368 | 13.0926 | 12.9442 | 12.2316 | 11.6874 | 11.2379 | 14.6937 | 14.6253 | 14.5537 | 14.4811 | 14.4042 | 14.3253 | 14.2463 | 14.1674 | 14.0874 | 14.0053 | 13.5379 | 13.0074 | 12.5505
MANNINGTON GSP | SHAFTESBURY BSP | GILLINGHAM | MINIMUM HEADROOM | ST 80185 25765 | YES | 0.54737 | 30.5653 | 30.1379 | 29.6463 | 29.0653 | 28.3589 | 27.4695 | 26.5789 | 25.7032 | 25.0832 | 24.4695 | 21.5832 | 21.0168 | 11.4242 | 28.9884 | 28.4242 | 27.8589 | 27.1979 | 26.3926 | 25.3632 | 24.3263 | 23.3063 | 22.5863 | 21.8737 | 18.5242 | 17.8958 | 17.2368 | 29.4274 | 28.8537 | 28.28 | 27.6095 | 26.7916 | 25.7589 | 24.7253 | 23.7063 | 22.9874 | 22.2758 | 18.9316 | 18.3032 | 17.6453
|  | GILLINGHAM | EE |  |  |  | 30.62 | 30.2263 | 29.7695 | 29.2232 | 28.5389 | 27.6747 | 26.8158 | 25.9611 | 25.3547 | 24.7611 | 21.9884 | 21.5684 | 21.1432 | 29.0547 | 28.5274 | 27.9916 | 27.3695 | 26.5874 | 25.5874 | 24.5863 | 23.5874 | 22.8853 | 22.1937 | 18.9663 | 18.5 | 18.0211 | 29.4937 | 28.96 | 28.4137 | 27.7821 | 26.9884 | 25.9821 | 24.9821 | 23.9853 | 23.2842 | 22.5937 | 19.3705 | 18.9042 | 18.4253
|  | GILLINGHAM | HT |  |  |  | 30.5653 | 30.1379 | 29.6463 | 29.0653 | 28.3589 | 27.4695 | 26.5789 | 25.7032 | 25.0832 | 24.4695 | 21.5832 | 21.0168 | 20.4326 | 28.9884 | 28.4242 | 27.8589 | 27.1979 | 26.3926 | 25.3632 | 24.3263 | 23.3063 | 22.5863 | 21.8737 | 18.5242 | 17.8958 | 17.2368 | 29.4274 | 28.8537 | 28.28 | 27.6095 | 26.7916 | 25.7589 | 24.7253 | 23.7063 | 22.9874 | 22.2758 | 18.9316 | 18.3032 | 17.6453
|  | GILLINGHAM | HE |  |  |  | 30.7021 | 30.3432 | 29.9379 | 29.4274 | 28.78 | 27.9495 | 27.1221 | 26.2989 | 25.7295 | 25.1663 | 22.5547 | 22.2853 | 11.4242 | 29.1505 | 28.6663 | 28.1726 | 27.5884 | 26.8474 | 25.8863 | 24.9189 | 23.9568 | 23.2916 | 22.6347 | 19.5821 | 19.28 | 18.9579 | 29.5916 | 29.1 | 28.5979 | 28.0053 | 27.2516 | 26.2821 | 25.3168 | 24.3558 | 23.6926 | 23.0368 | 19.9895 | 19.6874 | 19.3663
|  | GILLINGHAM | CF |  |  |  | 30.8095 | 30.6168 | 30.4358 | 30.2389 | 29.9653 | 29.62 | 29.2411 | 28.8274 | 28.5137 | 28.1768 | 26.4821 | 26.2895 | 26.1021 | 29.2916 | 29.0316 | 28.7905 | 28.5242 | 28.2021 | 27.8063 | 27.3726 | 26.8968 | 26.5389 | 26.1484 | 24.1695 | 23.9526 | 23.7389 | 29.7337 | 29.4705 | 29.2253 | 28.9558 | 28.6284 | 28.2263 | 27.7853 | 27.3021 | 26.9368 | 26.5442 | 24.5684 | 24.3526 | 24.1379
BRAMLEY (FLEE) | ALDERSHOT BSP | GODALMING | MINIMUM HEADROOM | SU 96743 44375 | YES | 0.52632 | 34.9684 | 34.5758 | 34.1789 | 33.7568 | 33.3221 | 32.8716 | 32.4189 | 32.0211 | 31.4084 | 30.7495 | 27.7747 | 25.0453 | -15.6989 | 29.9937 | 29.0874 | 28.3389 | 27.5747 | 26.8095 | 26.0474 | 25.3042 | 24.5274 | 23.7537 | 23.0295 | 19.7284 | 16.6789 | 13.8705 | 30.8811 | 30.3926 | 29.6695 | 28.9316 | 28.1895 | 27.4484 | 26.7084 | 25.9305 | 25.1568 | 24.4316 | 21.1242 | 18.0684 | 15.2568
|  | GODALMING | EE |  |  |  | 35.1189 | 34.8126 | 34.4863 | 34.14 | 33.7768 | 33.4032 | 33.04 | 32.6947 | 32.3632 | 32.0674 | 29.9358 | 27.8389 | 25.9716 | 30.32 | 29.5989 | 29.0084 | 28.3979 | 27.7747 | 27.16 | 26.5684 | 25.9926 | 25.3611 | 24.7505 | 22.1295 | 19.7642 | 17.6421 | 31.0421 | 30.7105 | 30.3137 | 29.7221 | 29.1179 | 28.5189 | 27.9453 | 27.3842 | 26.7632 | 26.1516 | 23.5232 | 21.1505 | 19.0232
|  | GODALMING | HT |  |  |  | 34.9684 | 34.5758 | 34.1789 | 33.7568 | 33.3221 | 32.8716 | 32.4189 | 32.0211 | 31.4084 | 30.7495 | 27.7747 | 25.0453 | 22.5326 | 29.9937 | 29.0874 | 28.3389 | 27.5747 | 26.8095 | 26.0474 | 25.3042 | 24.5274 | 23.7537 | 23.0295 | 19.7284 | 16.6789 | 13.8705 | 30.8811 | 30.3926 | 29.6695 | 28.9316 | 28.1895 | 27.4484 | 26.7084 | 25.9305 | 25.1568 | 24.4316 | 21.1242 | 18.0684 | 15.2568
|  | GODALMING | HE |  |  |  | 35.3274 | 35.1189 | 34.8874 | 34.6316 | 34.3568 | 34.0632 | 33.7811 | 33.5158 | 33.2674 | 33.0526 | 32.3263 | 31.2432 | -15.6989 | 30.6 | 30.2674 | 29.8863 | 29.4811 | 29.0547 | 28.6179 | 28.2011 | 27.7968 | 27.3284 | 26.8874 | 25.0947 | 23.5116 | 22.1105 | 31.2653 | 31.0389 | 30.7979 | 30.5337 | 30.2495 | 29.9189 | 29.5137 | 29.1179 | 28.6642 | 28.24 | 26.4947 | 24.9095 | 23.5053
|  | GODALMING | CF |  |  |  | 35.4453 | 35.3263 | 35.2032 | 35.0747 | 34.9421 | 34.8042 | 34.6642 | 34.5242 | 34.3874 | 34.2505 | 33.64 | 33.3337 | 33.0779 | 30.7242 | 30.5947 | 30.4653 | 30.2442 | 30 | 29.7516 | 29.4947 | 29.2389 | 28.9937 | 28.7495 | 27.5789 | 26.4358 | 25.46 | 31.3905 | 31.26 | 31.1305 | 30.9958 | 30.8568 | 30.7116 | 30.5653 | 30.4179 | 30.2747 | 30.0558 | 28.9242 | 27.8379 | 26.8611
WILLESDEN GSP | ACTON LANE | GOLDSMITHS | MINIMUM HEADROOM | TQ 21089 80758 | NO | 0.069474 | 13.9611 | 13.4705 | 12.6916 | 11.3968 | 9.5558 | 7.3926 | 5.3116 | 3.3358 | 1.8958 | 0.81684 | -2.84 | -3.9379 | -13.9674 | 11.9579 | 11.4947 | 10.6011 | 9.0989 | 6.9558 | 4.4326 | 2.0074 | -0.29789 | -1.9726 | -3.2263 | -7.4537 | -8.6758 | -10.9537 | 12.4095 | 12.2484 | 11.4495 | 9.9621 | 7.8179 | 5.2947 | 2.8684 | 0.56316 | -1.1116 | -2.3632 | -6.5842 | -7.8042 | -10.1453
|  | GOLDSMITHS | EE |  |  |  | 14.0737 | 13.8105 | 13.3368 | 12.6116 | 11.4516 | 9.9589 | 8.48 | 6.6063 | 4.3326 | 2.8242 | -0.68632 | -1.4505 | -2.1726 | 12.0221 | 11.8811 | 11.3411 | 10.5084 | 9.1621 | 7.4253 | 5.7042 | 3.5168 | 0.85684 | -0.90316 | -4.7358 | -5.5832 | -6.3947 | 12.4642 | 12.3505 | 12.1442 | 11.3632 | 10.0253 | 8.2874 | 6.5663 | 4.3779 | 1.7168 | -0.043158 | -3.7442 | -4.5905 | -5.4021
|  | GOLDSMITHS | HT |  |  |  | 13.9611 | 13.4705 | 12.6916 | 11.3968 | 9.5558 | 7.3926 | 5.3116 | 3.3358 | 1.8958 | 0.81684 | -2.84 | -3.9379 | -5.6632 | 11.9579 | 11.4947 | 10.6011 | 9.0989 | 6.9558 | 4.4326 | 2.0074 | -0.29789 | -1.9726 | -3.2263 | -7.4537 | -8.6758 | -10.9537 | 12.4095 | 12.2484 | 11.4495 | 9.9621 | 7.8179 | 5.2947 | 2.8684 | 0.56316 | -1.1116 | -2.3632 | -6.5842 | -7.8042 | -10.1453
|  | GOLDSMITHS | HE |  |  |  | 14.2032 | 13.9937 | 13.5589 | 12.86 | 11.7179 | 10.2263 | 8.7726 | 6.8179 | 4.6389 | 3.3263 | -0.42842 | -1.9179 | -13.9674 | 12.0874 | 11.9853 | 11.5863 | 10.78 | 9.4516 | 7.7137 | 6.0179 | 3.7305 | 1.1779 | -0.35579 | -4.74 | -6.9189 | -7.4063 | 12.5189 | 12.4358 | 12.3211 | 11.6232 | 10.3147 | 8.5768 | 6.88 | 4.5926 | 2.0389 | 0.50421 | -3.8737 | -6.1495 | -6.6358
|  | GOLDSMITHS | CF |  |  |  | 14.2611 | 14.1663 | 14.0684 | 13.9653 | 13.8621 | 13.7558 | 13.6516 | 13.3274 | 12.7179 | 11.9021 | 4.8684 | 4.3179 | 4.0305 | 12.1232 | 12.0632 | 12 | 11.9337 | 11.8674 | 11.7979 | 11.7221 | 11.3516 | 10.6442 | 9.6926 | 1.4453 | 0.82 | 0.49579 | 12.5505 | 12.4958 | 12.4389 | 12.38 | 12.3189 | 12.2526 | 12.1863 | 12.1053 | 11.4842 | 10.5558 | 2.3053 | 1.6811 | 1.3558
NURSLING GSP | WINCHESTER | GORDON ROAD | MINIMUM HEADROOM | SU 48217 29991 | YES | 1.0368 | 36.0316 | 34.8558 | 34.6242 | 34.3789 | 34.1232 | 33.8568 | 33.5884 | 33.3495 | 33.1316 | 32.9295 | 30.74 | 28.5842 | -9.5768 | 31.1863 | 30.0011 | 29.7042 | 29.0558 | 28.2147 | 27.1958 | 26.1558 | 25.5916 | 25.1453 | 24.6453 | 22.0337 | 19.6021 | 17.3179 | 31.9442 | 30.7684 | 30.5368 | 30.2758 | 29.9463 | 28.9168 | 27.8768 | 27.3126 | 26.8674 | 26.3674 | 23.76 | 21.3326 | 19.0505
|  | GORDON ROAD | EE |  |  |  | 36.1158 | 34.9863 | 34.7947 | 34.5895 | 34.3737 | 34.1484 | 33.9305 | 33.72 | 33.5168 | 33.3347 | 32.1011 | 30.3968 | 28.8295 | 31.2737 | 30.1389 | 29.9326 | 29.5179 | 28.76 | 27.82 | 26.88 | 26.4116 | 26.0526 | 25.6389 | 23.5411 | 21.6137 | 19.8253 | 32.0274 | 30.8979 | 30.7063 | 30.5021 | 30.2547 | 29.5537 | 28.6 | 28.1316 | 27.7737 | 27.36 | 25.2642 | 23.3389 | 21.5537
|  | GORDON ROAD | HT |  |  |  | 36.0316 | 34.8558 | 34.6242 | 34.3789 | 34.1232 | 33.8568 | 33.5884 | 33.3495 | 33.1316 | 32.9295 | 30.74 | 28.5842 | 26.5705 | 31.1863 | 30.0011 | 29.7042 | 29.0558 | 28.2147 | 27.1958 | 26.1558 | 25.5916 | 25.1453 | 24.6453 | 22.0337 | 19.6021 | 17.3179 | 31.9442 | 30.7684 | 30.5368 | 30.2758 | 29.9463 | 28.9168 | 27.8768 | 27.3126 | 26.8674 | 26.3674 | 23.76 | 21.3326 | 19.0505
|  | GORDON ROAD | HE |  |  |  | 36.2211 | 35.1411 | 34.9937 | 34.8305 | 34.6547 | 34.4684 | 34.2895 | 34.1211 | 33.9642 | 33.8284 | 33.3632 | 32.4221 | -9.5768 | 31.3789 | 30.2989 | 30.1453 | 29.9684 | 29.4474 | 28.6032 | 27.7684 | 27.4063 | 27.1516 | 26.84 | 25.2621 | 23.8421 | 22.5547 | 32.1337 | 31.0537 | 30.9063 | 30.7432 | 30.56 | 30.3337 | 29.4958 | 29.1274 | 28.8726 | 28.5611 | 26.9853 | 25.5674 | 24.2821
|  | GORDON ROAD | CF |  |  |  | 36.2811 | 35.2505 | 35.1632 | 35.0726 | 34.98 | 34.8832 | 34.7853 | 34.6884 | 34.5926 | 34.4968 | 34.0695 | 33.8547 | 33.7358 | 31.4389 | 30.4084 | 30.3211 | 30.2274 | 30.1242 | 30.0021 | 29.58 | 29.3558 | 29.1916 | 28.9811 | 27.8211 | 26.8632 | 26.0189 | 32.1937 | 31.1632 | 31.0758 | 30.9853 | 30.8926 | 30.7958 | 30.6905 | 30.5863 | 30.4863 | 30.3832 | 29.5568 | 28.5842 | 27.7411
BRAMLEY (FLEE) | BURGHFIELD RESERVE | GORING | MINIMUM HEADROOM | SU 60305 82895 | YES | 7.4947 | 9.4484 | 9.2853 | 9.1242 | 8.96 | 8.7947 | 8.6316 | 8.4653 | 8.3137 | 8.1716 | 8.0411 | 7.4726 | 6.9474 | -1.3263 | 7.9116 | 7.7579 | 7.6053 | 7.4442 | 7.2684 | 7.0947 | 6.9179 | 6.7547 | 6.6021 | 6.4611 | 5.8463 | 5.2684 | 4.6989 | 8.1895 | 8.0789 | 7.9674 | 7.8505 | 7.7326 | 7.6126 | 7.4863 | 7.3263 | 7.1768 | 7.0379 | 6.4263 | 5.8484 | 5.28
|  | GORING | EE |  |  |  | 9.5063 | 9.3979 | 9.2695 | 9.14 | 9.0084 | 8.8737 | 8.7421 | 8.6158 | 8.4947 | 8.3821 | 7.9421 | 7.5589 | 7.1926 | 7.9811 | 7.8632 | 7.7421 | 7.6179 | 7.4926 | 7.3568 | 7.2158 | 7.08 | 6.9505 | 6.8305 | 6.3537 | 5.9316 | 5.5189 | 8.2368 | 8.1516 | 8.0632 | 7.9695 | 7.8747 | 7.7758 | 7.68 | 7.5895 | 7.5032 | 7.4011 | 6.9326 | 6.5116 | 6.1
|  | GORING | HT |  |  |  | 9.4484 | 9.2853 | 9.1242 | 8.96 | 8.7947 | 8.6316 | 8.4653 | 8.3137 | 8.1716 | 8.0411 | 7.4726 | 6.9474 | 6.4379 | 7.9116 | 7.7579 | 7.6053 | 7.4442 | 7.2684 | 7.0947 | 6.9179 | 6.7547 | 6.6021 | 6.4611 | 5.8463 | 5.2684 | 4.6989 | 8.1895 | 8.0789 | 7.9674 | 7.8505 | 7.7326 | 7.6126 | 7.4863 | 7.3263 | 7.1768 | 7.0379 | 6.4263 | 5.8484 | 5.28
|  | GORING | HE |  |  |  | 9.5568 | 9.5105 | 9.4589 | 9.3737 | 9.2821 | 9.1884 | 9.0926 | 9.0021 | 8.9168 | 8.84 | 8.5632 | 8.3316 | -1.3263 | 8.0737 | 8 | 7.9211 | 7.8379 | 7.7505 | 7.66 | 7.5684 | 7.4821 | 7.4 | 7.3274 | 7.0295 | 6.7737 | 6.5158 | 8.3011 | 8.2463 | 8.1853 | 8.1211 | 8.0516 | 7.9789 | 7.9074 | 7.8389 | 7.7758 | 7.72 | 7.5295 | 7.3453 | 7.0958
|  | GORING | CF |  |  |  | 9.5842 | 9.5589 | 9.5326 | 9.5042 | 9.4737 | 9.42 | 9.3663 | 9.3105 | 9.2579 | 9.2032 | 8.9621 | 8.7853 | 8.6284 | 8.12 | 8.0758 | 8.0305 | 7.9821 | 7.9347 | 7.8842 | 7.8337 | 7.7811 | 7.7316 | 7.6789 | 7.4463 | 7.2484 | 7.0716 | 8.3347 | 8.3032 | 8.2705 | 8.2358 | 8.2021 | 8.1653 | 8.1295 | 8.0916 | 8.0568 | 8.02 | 7.8589 | 7.7632 | 7.6432
IVER 132KV | DENHAM | GRASSINGHAM ROAD | MINIMUM HEADROOM | TQ 00165 90988 | YES | 0.24632 | 18.9295 | 18.7074 | 18.4811 | 18.2442 | 17.9968 | 17.7316 | 17.4653 | 17.2295 | 17.0116 | 16.8095 | 15.1653 | 13.6147 | -8.7137 | 13.7547 | 13.4653 | 13.1747 | 12.8758 | 12.5705 | 12.2579 | 11.9179 | 11.5011 | 11.0863 | 10.6853 | 8.7968 | 7.0789 | 5.5589 | 15.9632 | 15.5432 | 15.1242 | 14.7053 | 14.2832 | 13.8611 | 13.4305 | 13.0253 | 12.6158 | 12.2095 | 10.2989 | 8.5516 | 7.0221
|  | GRASSINGHAM ROAD | EE |  |  |  | 19.0053 | 18.8263 | 18.6358 | 18.4337 | 18.2221 | 17.9947 | 17.7705 | 17.5547 | 17.3453 | 17.1547 | 16.1716 | 14.9347 | 13.9095 | 13.8642 | 13.6347 | 13.3947 | 13.1463 | 12.8905 | 12.6263 | 12.3663 | 12.1147 | 11.8632 | 11.5326 | 9.9821 | 8.6074 | 7.4421 | 16.14 | 15.8116 | 15.4726 | 15.1295 | 14.7853 | 14.4347 | 14.0853 | 13.7368 | 13.3768 | 13.0347 | 11.4642 | 10.0484 | 8.8716
|  | GRASSINGHAM ROAD | HT |  |  |  | 18.9295 | 18.7074 | 18.4811 | 18.2442 | 17.9968 | 17.7316 | 17.4653 | 17.2295 | 17.0116 | 16.8095 | 15.1653 | 13.6147 | 12.26 | 13.7547 | 13.4653 | 13.1747 | 12.8758 | 12.5705 | 12.2579 | 11.9179 | 11.5011 | 11.0863 | 10.6853 | 8.7968 | 7.0789 | 5.5589 | 15.9632 | 15.5432 | 15.1242 | 14.7053 | 14.2832 | 13.8611 | 13.4305 | 13.0253 | 12.6158 | 12.2095 | 10.2989 | 8.5516 | 7.0221
|  | GRASSINGHAM ROAD | HE |  |  |  | 19.1232 | 19 | 18.8642 | 18.7137 | 18.5516 | 18.3705 | 18.1989 | 18.0368 | 17.8821 | 17.7495 | 17.2747 | 16.9842 | -8.7137 | 14.0137 | 13.8768 | 13.7116 | 13.5347 | 13.3453 | 13.1453 | 12.9526 | 12.7674 | 12.5832 | 12.42 | 11.8011 | 10.9716 | 10.2474 | 16.3495 | 16.1863 | 15.9653 | 15.7347 | 15.4937 | 15.24 | 14.9979 | 14.7547 | 14.5011 | 14.2663 | 13.2874 | 12.4747 | 11.7421
|  | GRASSINGHAM ROAD | CF |  |  |  | 19.1895 | 19.1168 | 19.0421 | 18.9653 | 18.8853 | 18.7989 | 18.7116 | 18.6232 | 18.5379 | 18.4537 | 18.0695 | 17.8632 | 17.7358 | 14.08 | 14.0074 | 13.9232 | 13.8253 | 13.7253 | 13.62 | 13.5137 | 13.4053 | 13.2958 | 13.1863 | 12.6747 | 12.2947 | 11.78 | 16.4158 | 16.3432 | 16.2421 | 16.1032 | 15.9621 | 15.8158 | 15.6663 | 15.5137 | 15.3516 | 15.1884 | 14.4 | 13.7979 | 13.2979
BRAMLEY (FLEE) | BURGHFIELD MAIN | GREEN PARK | MINIMUM HEADROOM | SU 70508 70222 | YES | 0 | 40.9337 | 40.8389 | 40.8379 | 40.6821 | 40.5274 | 40.3726 | 40.3726 | 40.3705 | 40.3705 | 40.3705 | 40.3684 | 40.3684 | 29.2 | 38.7516 | 38.6389 | 38.6379 | 38.4558 | 38.2726 | 38.0905 | 38.0905 | 38.0884 | 38.0884 | 38.0884 | 38.0863 | 38.0863 | 38.0853 | 39.3189 | 39.2232 | 39.2221 | 39.0632 | 38.8874 | 38.7126 | 38.7126 | 38.7105 | 38.7105 | 38.7105 | 38.7084 | 38.7084 | 38.7074
|  | GREEN PARK | EE |  |  |  | 40.9337 | 40.84 | 40.8379 | 40.6821 | 40.5274 | 40.3726 | 40.3726 | 40.3726 | 40.3716 | 40.3716 | 40.3705 | 40.3705 | 40.3684 | 38.7516 | 38.64 | 38.6379 | 38.4558 | 38.2726 | 38.0905 | 38.0905 | 38.0905 | 38.0895 | 38.0895 | 38.0884 | 38.0884 | 38.0863 | 39.3189 | 39.2242 | 39.2221 | 39.0632 | 38.8874 | 38.7126 | 38.7126 | 38.7126 | 38.7116 | 38.7116 | 38.7105 | 38.7105 | 38.7084
|  | GREEN PARK | HT |  |  |  | 40.9337 | 40.8389 | 40.8379 | 40.6821 | 40.5274 | 40.3726 | 40.3726 | 40.3705 | 40.3705 | 40.3705 | 40.3684 | 40.3684 | 40.3684 | 38.7516 | 38.6389 | 38.6379 | 38.4558 | 38.2726 | 38.0905 | 38.0905 | 38.0884 | 38.0884 | 38.0884 | 38.0863 | 38.0863 | 38.0853 | 39.3189 | 39.2232 | 39.2221 | 39.0632 | 38.8874 | 38.7126 | 38.7126 | 38.7105 | 38.7105 | 38.7105 | 38.7084 | 38.7084 | 38.7074
|  | GREEN PARK | HE |  |  |  | 40.9337 | 40.84 | 40.84 | 40.6842 | 40.5284 | 40.3726 | 40.3726 | 40.3726 | 40.3726 | 40.3726 | 40.3716 | 40.3716 | 29.2 | 38.7516 | 38.64 | 38.64 | 38.4579 | 38.2737 | 38.0905 | 38.0905 | 38.0905 | 38.0905 | 38.0905 | 38.0895 | 38.0895 | 38.0895 | 39.3189 | 39.2242 | 39.2242 | 39.0653 | 38.8884 | 38.7126 | 38.7126 | 38.7126 | 38.7126 | 38.7126 | 38.7116 | 38.7116 | 38.7116
|  | GREEN PARK | CF |  |  |  | 41.0737 | 41.0253 | 41.0253 | 41.0253 | 41.0253 | 41.0253 | 41.0253 | 40.9453 | 40.9453 | 40.8684 | 40.7905 | 40.7905 | 40.7905 | 38.9158 | 38.8579 | 38.8579 | 38.8579 | 38.8579 | 38.8579 | 38.8579 | 38.7653 | 38.7653 | 38.6737 | 38.5821 | 38.5821 | 38.5821 | 39.4579 | 39.4095 | 39.4095 | 39.4095 | 39.4095 | 39.4095 | 39.4095 | 39.3305 | 39.3305 | 39.2526 | 39.1758 | 39.1758 | 39.1758
WILLESDEN GSP |  | GREENFORD | MINIMUM HEADROOM | TQ 14695 83785 | NO | 1.0653 | 73.0695 | 72.5926 | 72.1105 | 71.5979 | 71.0642 | 71.0716 | 69.6547 | 68.62 | 67.9116 | 67.2589 | 63.6916 | 60.0147 | 2.0463 | 61.7263 | 60.0105 | 58.18 | 55.2621 | 53.0484 | 52.9642 | 51.3653 | 50.2232 | 49.4653 | 48.7684 | 45.1737 | 41.0768 | 37.1663 | 64.7389 | 63.0221 | 61.1916 | 58.2726 | 56.0589 | 55.9747 | 54.3747 | 53.2326 | 52.4747 | 51.7368 | 47.84 | 43.7432 | 39.8316
|  | GREENFORD | EE |  |  |  | 73.2305 | 72.8474 | 72.44 | 72.0063 | 71.5484 | 71.0716 | 69.6547 | 68.62 | 67.9116 | 67.2621 | 67.34 | 64.7621 | 62.3811 | 62.1537 | 60.6989 | 59.1842 | 56.6842 | 54.9032 | 52.9642 | 51.3653 | 50.2232 | 49.4653 | 48.7684 | 49.2821 | 46.42 | 43.7442 | 65.1653 | 63.7105 | 62.1947 | 59.6947 | 57.9126 | 55.9747 | 54.3747 | 53.2326 | 52.4747 | 51.7768 | 51.9495 | 49.0863 | 46.4105
|  | GREENFORD | HT |  |  |  | 73.0695 | 72.5926 | 72.1105 | 71.5979 | 71.0642 | 71.7853 | 70.0842 | 68.8621 | 68.0389 | 67.2589 | 63.6916 | 60.0147 | 56.5347 | 61.7263 | 60.0105 | 58.18 | 55.2621 | 53.0484 | 54.0621 | 52.1558 | 50.8042 | 49.9147 | 49.0705 | 45.1737 | 41.0768 | 37.1663 | 64.7389 | 63.0221 | 61.1916 | 58.2726 | 56.0589 | 56.7305 | 54.8232 | 53.4716 | 52.5811 | 51.7368 | 47.84 | 43.7432 | 39.8316
|  | GREENFORD | HE |  |  |  | 73.4589 | 73.1789 | 72.8684 | 72.5253 | 72.1568 | 71.7632 | 71.3874 | 70.5453 | 70.0368 | 69.5842 | 70.6579 | 69.0442 | 2.0463 | 62.6989 | 61.4979 | 60.2253 | 57.9558 | 56.3979 | 54.6674 | 53.2758 | 52.3389 | 51.7989 | 51.3168 | 52.9253 | 51.1274 | 49.4968 | 65.4358 | 64.5095 | 63.2368 | 60.9663 | 59.4084 | 57.6768 | 56.2853 | 55.3484 | 54.8084 | 54.3263 | 55.5937 | 53.7958 | 52.1642
|  | GREENFORD | CF |  |  |  | 73.5937 | 73.4211 | 73.2432 | 73.0579 | 72.8653 | 72.6663 | 72.4642 | 72.2653 | 72.0684 | 71.8716 | 70.9926 | 72.7232 | 72.4768 | 63.1042 | 62.4442 | 61.7684 | 60.7726 | 60.1021 | 59.3453 | 58.6084 | 57.9737 | 57.4421 | 57.0768 | 55.3263 | 57.5179 | 56.4284 | 65.5884 | 65.3853 | 64.7811 | 63.7842 | 63.1137 | 62.3568 | 61.62 | 60.9842 | 60.4526 | 60.0884 | 58.3368 | 60.1874 | 59.0979
LOVEDEAN GSP | PORTSMOUTH BSP | GREETHAM STREET | MINIMUM HEADROOM | SU 64445 00178 | YES | 0.072632 | 34.4621 | 34.3768 | 34.2905 | 34.1989 | 33.5432 | 31.9 | 31.1979 | 30.5063 | 29.8042 | 29.6147 | 28.6168 | 27.5853 | 11.7347 | 30.9947 | 30.9 | 30.8032 | 30.1158 | 28.4642 | 26.5495 | 25.7421 | 24.9453 | 24.1337 | 23.9253 | 22.8137 | 21.6495 | 20.5589 | 31.6979 | 31.6084 | 31.5179 | 31.2305 | 29.6095 | 27.6979 | 26.8916 | 26.0968 | 25.2863 | 25.0779 | 23.9674 | 22.8053 | 21.7168
|  | GREETHAM STREET | EE |  |  |  | 34.5011 | 34.4368 | 34.3684 | 34.2968 | 34.2137 | 32.6032 | 31.9379 | 31.2737 | 30.6126 | 29.9389 | 29.2242 | 28.4137 | 27.6642 | 31.0389 | 30.9674 | 30.8916 | 30.3095 | 29.2326 | 27.3526 | 26.5832 | 25.8168 | 25.0526 | 24.2726 | 23.48 | 22.5632 | 21.7095 | 31.7389 | 31.6716 | 31.6 | 31.4095 | 30.3768 | 28.5 | 27.7326 | 26.9663 | 26.2032 | 25.4253 | 24.6337 | 23.7179 | 22.8653
|  | GREETHAM STREET | HT |  |  |  | 34.4621 | 34.3768 | 34.2905 | 34.1989 | 33.5432 | 31.9 | 31.1979 | 30.5063 | 29.8042 | 29.6147 | 28.6168 | 27.5853 | 26.6232 | 30.9947 | 30.9 | 30.8032 | 30.1158 | 28.4642 | 26.5495 | 25.7421 | 24.9453 | 24.1337 | 23.9253 | 22.8137 | 21.6495 | 20.5589 | 31.6979 | 31.6084 | 31.5179 | 31.2305 | 29.6095 | 27.6979 | 26.8916 | 26.0968 | 25.2863 | 25.0779 | 23.9674 | 22.8053 | 21.7168
|  | GREETHAM STREET | HE |  |  |  | 34.5263 | 34.4726 | 34.4126 | 34.3463 | 34.2758 | 33.0137 | 32.5789 | 32.1505 | 31.7263 | 31.3126 | 29.9526 | 29.4253 | 11.7347 | 31.0705 | 31.0137 | 30.9484 | 30.4853 | 29.4421 | 27.8242 | 27.3253 | 26.8337 | 26.3453 | 25.8674 | 24.3032 | 23.7042 | 23.0737 | 31.7674 | 31.7116 | 31.6505 | 31.5368 | 30.5863 | 28.9705 | 28.4726 | 27.9821 | 27.4937 | 27.0179 | 25.4558 | 24.8568 | 24.2284
|  | GREETHAM STREET | CF |  |  |  | 34.5453 | 34.5084 | 34.4705 | 34.4305 | 34.3895 | 34.3474 | 34.3042 | 34.2611 | 34.2189 | 34.0084 | 32.8579 | 32.5442 | 32.1937 | 31.0895 | 31.0526 | 31.0095 | 30.8642 | 30.5905 | 30.0811 | 29.8379 | 29.5758 | 29.2968 | 28.9989 | 27.6779 | 27.3263 | 26.9232 | 31.7863 | 31.7495 | 31.7095 | 31.6484 | 31.5832 | 31.2232 | 30.98 | 30.72 | 30.4411 | 30.1432 | 28.8242 | 28.4726 | 28.0716
COWLEY GSP | DRAYTON BSP | GROVE | MINIMUM HEADROOM | SU 39515 89611 | YES | 0.37895 | 16.5695 | 15.9337 | 15.64 | 15.3126 | 14.0947 | 12.4053 | 10.7189 | 9.2474 | 7.9463 | 6.9211 | 1.9989 | -2.9168 | -21.7242 | 12.7011 | 11.5116 | 10.5905 | 9.4137 | 7.8021 | 5.8642 | 3.9295 | 2.2411 | 0.74947 | -0.42211 | -6.0684 | -11.7442 | -17.8558 | 13.6895 | 12.5432 | 11.6726 | 10.5642 | 8.9747 | 7.0389 | 5.1084 | 3.4221 | 1.9326 | 0.76421 | -4.8737 | -10.54 | -16.6411
|  | GROVE | EE |  |  |  | 16.6632 | 16.0916 | 15.8474 | 15.5716 | 14.5305 | 12.9863 | 11.3958 | 9.9968 | 8.7505 | 7.7832 | 3.2263 | -1.16 | -5.9105 | 12.9126 | 11.8305 | 11.0063 | 9.9242 | 8.4042 | 6.5505 | 4.7105 | 3.0937 | 1.6579 | 0.54737 | -4.7358 | -9.8211 | -15.3547 | 13.8495 | 12.8495 | 12.0716 | 11.0547 | 9.5758 | 7.7253 | 5.8884 | 4.2747 | 2.8411 | 1.7316 | -3.5421 | -8.6189 | -14.1421
|  | GROVE | HT |  |  |  | 16.5695 | 15.9337 | 15.64 | 15.3126 | 14.0947 | 12.4053 | 10.7189 | 9.2474 | 7.9463 | 6.9211 | 1.9989 | -2.9168 | -8.1821 | 12.7011 | 11.5116 | 10.5905 | 9.4137 | 7.8021 | 5.8642 | 3.9295 | 2.2411 | 0.74947 | -0.42211 | -6.0684 | -11.7442 | -17.8558 | 13.6895 | 12.5432 | 11.6726 | 10.5642 | 8.9747 | 7.0389 | 5.1084 | 3.4221 | 1.9326 | 0.76421 | -4.8737 | -10.54 | -16.6411
|  | GROVE | HE |  |  |  | 16.7947 | 16.2874 | 16.1232 | 15.9105 | 15.2379 | 13.8253 | 12.3358 | 11.0305 | 9.8842 | 9.0126 | 4.9158 | 0.95053 | -21.7242 | 13.2011 | 12.2568 | 11.5653 | 10.6084 | 9.2084 | 7.4663 | 5.7358 | 4.2232 | 2.8947 | 1.8884 | -2.8958 | -7.5168 | -12.6137 | 13.9811 | 13.2579 | 12.6074 | 11.7105 | 10.3789 | 8.64 | 6.9126 | 5.4021 | 4.0768 | 3.0716 | -1.7042 | -6.3168 | -11.4042
|  | GROVE | CF |  |  |  | 16.8705 | 16.42 | 16.3453 | 16.2589 | 16.1421 | 16.0137 | 15.6853 | 15.0663 | 14.4737 | 13.9579 | 11.1968 | 8.6705 | 5.9758 | 13.3926 | 12.6979 | 12.3432 | 11.8916 | 11.2716 | 10.5326 | 9.7263 | 8.9537 | 8.2147 | 7.5989 | 4.4 | 1.4463 | -1.7221 | 14.0568 | 13.6063 | 13.3421 | 12.9189 | 12.34 | 11.6495 | 10.8958 | 10.1253 | 9.3874 | 8.7726 | 5.58 | 2.6305 | -0.53158
MANNINGTON GSP | SHAFTESBURY BSP | GUSSAGE ST MICHAEL | MINIMUM HEADROOM | ST 98638 11417 | YES | 0 | 6.7505 | 6.7253 | 6.7 | 6.6737 | 6.6463 | 6.62 | 6.5926 | 6.5674 | 6.5453 | 6.5242 | 6.4316 | 6.32 | 4.6853 | 6.5505 | 6.5274 | 6.5042 | 6.48 | 6.4558 | 6.4316 | 6.4063 | 6.3789 | 6.3547 | 6.3316 | 6.2305 | 6.1042 | 5.9726 | 6.5537 | 6.5305 | 6.5084 | 6.4853 | 6.4611 | 6.4379 | 6.4147 | 6.3926 | 6.3737 | 6.3558 | 6.28 | 6.1979 | 6.0947
|  | GUSSAGE ST MICHAEL | EE |  |  |  | 6.7621 | 6.7432 | 6.7221 | 6.7021 | 6.68 | 6.6589 | 6.6389 | 6.6189 | 6.6 | 6.5821 | 6.5105 | 6.4253 | 6.3305 | 6.5611 | 6.5432 | 6.5242 | 6.5053 | 6.4853 | 6.4663 | 6.4474 | 6.4295 | 6.4126 | 6.3947 | 6.3179 | 6.2211 | 6.1105 | 6.5632 | 6.5463 | 6.5274 | 6.5095 | 6.4895 | 6.4705 | 6.4526 | 6.4347 | 6.4189 | 6.4032 | 6.3442 | 6.2832 | 6.2189
|  | GUSSAGE ST MICHAEL | HT |  |  |  | 6.7505 | 6.7253 | 6.7 | 6.6737 | 6.6463 | 6.62 | 6.5926 | 6.5674 | 6.5453 | 6.5242 | 6.4316 | 6.32 | 6.2053 | 6.5505 | 6.5274 | 6.5042 | 6.48 | 6.4558 | 6.4316 | 6.4063 | 6.3789 | 6.3547 | 6.3316 | 6.2305 | 6.1042 | 5.9726 | 6.5537 | 6.5305 | 6.5084 | 6.4853 | 6.4611 | 6.4379 | 6.4147 | 6.3926 | 6.3737 | 6.3558 | 6.28 | 6.1979 | 6.0947
|  | GUSSAGE ST MICHAEL | HE |  |  |  | 6.7789 | 6.7663 | 6.7526 | 6.7389 | 6.7253 | 6.7105 | 6.6958 | 6.6821 | 6.6705 | 6.6589 | 6.6179 | 6.56 | 4.6853 | 6.5758 | 6.5642 | 6.5516 | 6.5389 | 6.5253 | 6.5116 | 6.4979 | 6.4853 | 6.4737 | 6.4632 | 6.4253 | 6.3695 | 6.2863 | 6.5779 | 6.5663 | 6.5537 | 6.5421 | 6.5284 | 6.5147 | 6.5011 | 6.4884 | 6.4779 | 6.4674 | 6.4305 | 6.3895 | 6.3442
|  | GUSSAGE ST MICHAEL | CF |  |  |  | 6.7884 | 6.7789 | 6.7726 | 6.7663 | 6.7579 | 6.7505 | 6.7421 | 6.7347 | 6.7263 | 6.72 | 6.6853 | 6.6537 | 6.6211 | 6.5842 | 6.5758 | 6.5705 | 6.5642 | 6.5558 | 6.5505 | 6.5421 | 6.5347 | 6.5284 | 6.5221 | 6.4895 | 6.4632 | 6.4316 | 6.5853 | 6.5779 | 6.5716 | 6.5663 | 6.5589 | 6.5526 | 6.5453 | 6.5379 | 6.5305 | 6.5253 | 6.4937 | 6.4695 | 6.4474
BOTLEY WOOD GSP | NETLEY COMMON BSP | HAMBLE | MINIMUM HEADROOM | SU 47370 08794 | YES | 2.1242 | 33.8232 | 33.64 | 33.4547 | 33.2579 | 33.0558 | 32.8442 | 32.6316 | 32.4421 | 32.0158 | 31.5768 | 29.52 | 27.7189 | 3.7179 | 29.7295 | 29.3916 | 29.0526 | 28.7063 | 28.3663 | 27.9874 | 27.5053 | 27.0632 | 26.5926 | 26.1158 | 23.8705 | 21.8558 | 20.0084 | 30.8158 | 30.4684 | 30.12 | 29.7516 | 29.3916 | 28.9968 | 28.5053 | 28.0547 | 27.5726 | 27.0853 | 24.7842 | 22.7568 | 20.9084
|  | HAMBLE | EE |  |  |  | 33.8895 | 33.7442 | 33.5916 | 33.4274 | 33.2568 | 33.0768 | 32.9042 | 32.7379 | 32.5779 | 32.3779 | 30.6853 | 29.2347 | 27.9484 | 29.8495 | 29.6105 | 29.3379 | 29.0558 | 28.7768 | 28.4958 | 28.1316 | 27.7684 | 27.3874 | 26.9853 | 25.1411 | 23.5495 | 22.0884 | 30.94 | 30.6937 | 30.4137 | 30.1253 | 29.8326 | 29.5358 | 29.1421 | 28.7716 | 28.3821 | 27.9705 | 26.0779 | 24.44 | 22.9758
|  | HAMBLE | HT |  |  |  | 33.8232 | 33.64 | 33.4547 | 33.2579 | 33.0558 | 32.8442 | 32.6316 | 32.4421 | 32.0158 | 31.5768 | 29.52 | 27.7189 | 26.0884 | 29.7295 | 29.3916 | 29.0526 | 28.7063 | 28.3663 | 27.9874 | 27.5053 | 27.0632 | 26.5926 | 26.1158 | 23.8705 | 21.8558 | 20.0084 | 30.8158 | 30.4684 | 30.12 | 29.7516 | 29.3916 | 28.9968 | 28.5053 | 28.0547 | 27.5726 | 27.0853 | 24.7842 | 22.7568 | 20.9084
|  | HAMBLE | HE |  |  |  | 33.9863 | 33.8874 | 33.7779 | 33.6568 | 33.5263 | 33.3863 | 33.2505 | 33.1232 | 33.0042 | 32.9021 | 32 | 30.9137 | 3.7179 | 29.9463 | 29.8474 | 29.7253 | 29.5305 | 29.3358 | 29.1326 | 28.8442 | 28.5832 | 28.2968 | 27.9853 | 26.54 | 25.3347 | 24.2463 | 31.0368 | 30.9379 | 30.8137 | 30.6147 | 30.4158 | 30.2084 | 29.9105 | 29.6295 | 29.3179 | 28.9905 | 27.5074 | 26.2684 | 25.1526
|  | HAMBLE | CF |  |  |  | 34.0432 | 33.9874 | 33.9284 | 33.8684 | 33.8053 | 33.74 | 33.6726 | 33.6063 | 33.5411 | 33.4768 | 33.1832 | 32.7326 | 32.1253 | 30.0032 | 29.9474 | 29.8884 | 29.8284 | 29.7453 | 29.6295 | 29.4737 | 29.3137 | 29.1505 | 28.9747 | 28.0874 | 27.3032 | 26.6263 | 31.0937 | 31.0379 | 30.9789 | 30.9189 | 30.8337 | 30.7147 | 30.5526 | 30.3884 | 30.2168 | 30.0263 | 29.0874 | 28.2821 | 27.5842
MANNINGTON GSP | POOLE PS (HAMWORTHY) | HAMWORTHY | MINIMUM HEADROOM | SZ 00104 90800 | YES | 0.48105 | 26.8547 | 26.5084 | 26.0916 | 25.0368 | 23.8863 | 23.8937 | 22.6126 | 21.1011 | 19.8242 | 18.5768 | 13.8726 | 11.0968 | -21.6295 | 22.5937 | 21.6916 | 20.8316 | 19.6611 | 18.3832 | 18.5189 | 17.0926 | 15.3895 | 13.9411 | 12.5116 | 7.2316 | 4.1695 | 1.2305 | 23.5705 | 22.7274 | 21.8516 | 20.6558 | 19.3484 | 19.3137 | 17.8526 | 16.1053 | 14.6358 | 13.2021 | 7.9011 | 4.8147 | 1.8663
|  | HAMWORTHY | EE |  |  |  | 26.9821 | 26.7074 | 26.4168 | 25.8905 | 25.0442 | 24.0874 | 23.1316 | 21.8937 | 20.6337 | 20.5884 | 15.7032 | 13.5211 | 11.5189 | 22.8842 | 22.1305 | 21.4021 | 20.6074 | 19.6726 | 18.6137 | 17.5558 | 16.1663 | 14.7495 | 14.8053 | 9.2526 | 6.86 | 4.6105 | 23.8263 | 23.1737 | 22.4316 | 21.62 | 20.6663 | 19.5842 | 18.5 | 17.0737 | 15.62 | 15.4958 | 9.9105 | 7.4842 | 5.2242
|  | HAMWORTHY | HT |  |  |  | 26.8547 | 26.5084 | 26.0916 | 25.0368 | 23.8863 | 23.8937 | 22.6126 | 21.1011 | 19.8242 | 18.5768 | 13.8726 | 11.0968 | 8.4747 | 22.5937 | 21.6916 | 20.8316 | 19.6611 | 18.3832 | 18.5189 | 17.0926 | 15.3895 | 13.9411 | 12.5116 | 7.2316 | 4.1695 | 1.2305 | 23.5705 | 22.7274 | 21.8516 | 20.6558 | 19.3484 | 19.3137 | 17.8526 | 16.1053 | 14.6358 | 13.2021 | 7.9011 | 4.8147 | 1.8663
|  | HAMWORTHY | HE |  |  |  | 27.1632 | 26.9737 | 26.7632 | 26.5326 | 26.0453 | 25.2137 | 24.3937 | 23.2568 | 22.1305 | 22.2537 | 18.2211 | 16.7705 | -21.6295 | 23.2842 | 22.72 | 22.1716 | 21.5337 | 20.7558 | 19.8337 | 18.9189 | 17.6337 | 16.3589 | 16.5947 | 11.9632 | 10.3421 | 8.7674 | 24.18 | 23.6958 | 23.2158 | 22.5642 | 21.7695 | 20.8242 | 19.8884 | 18.5695 | 17.2589 | 17.3221 | 12.6463 | 11.0168 | 9.4337
|  | HAMWORTHY | CF |  |  |  | 27.2695 | 27.1611 | 27.0495 | 26.9316 | 26.8116 | 26.6842 | 26.5537 | 26.4253 | 26.3 | 25.8884 | 22.8747 | 21.7747 | 20.8705 | 23.5 | 23.1737 | 22.8747 | 22.6611 | 22.4432 | 22.2021 | 21.94 | 21.5116 | 21.08 | 20.5968 | 17.2305 | 15.9989 | 14.9558 | 24.3189 | 24.0926 | 23.8326 | 23.64 | 23.4432 | 23.2242 | 22.9811 | 22.5432 | 22.1 | 21.6053 | 17.9611 | 16.6958 | 15.6432
IVER 132KV | DENHAM | HAREFIELD | MINIMUM HEADROOM | TQ 04001 91227 | YES | 0 | 16.0111 | 15.9216 | 15.8311 | 15.7363 | 15.6374 | 15.5332 | 15.4237 | 15.1953 | 14.9679 | 14.7542 | 13.7711 | 12.9121 | 4.9268 | 14.6216 | 14.4511 | 14.2405 | 14.0026 | 13.7321 | 13.4363 | 13.1584 | 12.8932 | 12.6395 | 12.3995 | 11.3058 | 10.3468 | 9.4637 | 14.8458 | 14.7511 | 14.6532 | 14.4268 | 14.1595 | 13.8616 | 13.5847 | 13.3184 | 13.0637 | 12.8237 | 11.7247 | 10.7605 | 9.8753
|  | HAREFIELD | EE |  |  |  | 16.0405 | 15.9679 | 15.8932 | 15.8111 | 15.7268 | 15.6374 | 15.5511 | 15.4679 | 15.3868 | 15.2447 | 14.4942 | 13.8458 | 13.2837 | 14.6542 | 14.57 | 14.4111 | 14.2289 | 14.0237 | 13.7995 | 13.5816 | 13.3668 | 13.1584 | 12.9637 | 12.1258 | 11.4058 | 10.7732 | 14.8774 | 14.8016 | 14.7216 | 14.6342 | 14.4458 | 14.2258 | 14.0079 | 13.7921 | 13.5826 | 13.3879 | 12.5416 | 11.8153 | 11.1795
|  | HAREFIELD | HT |  |  |  | 16.0111 | 15.9216 | 15.8311 | 15.7363 | 15.6374 | 15.5332 | 15.4237 | 15.1953 | 14.9679 | 14.7542 | 13.7711 | 12.9121 | 12.1289 | 14.6216 | 14.4511 | 14.2405 | 14.0026 | 13.7321 | 13.4363 | 13.1584 | 12.8932 | 12.6395 | 12.3995 | 11.3058 | 10.3468 | 9.4637 | 14.8458 | 14.7511 | 14.6532 | 14.4268 | 14.1595 | 13.8616 | 13.5847 | 13.3184 | 13.0637 | 12.8237 | 11.7247 | 10.7605 | 9.8753
|  | HAREFIELD | HE |  |  |  | 16.0879 | 16.0384 | 15.9847 | 15.9237 | 15.8584 | 15.7879 | 15.7216 | 15.6563 | 15.5974 | 15.5458 | 15.1468 | 14.6889 | 4.9268 | 14.7047 | 14.6532 | 14.5963 | 14.4816 | 14.3195 | 14.1374 | 13.9595 | 13.7868 | 13.6195 | 13.4689 | 12.8321 | 12.3121 | 11.8542 | 14.9289 | 14.8774 | 14.8195 | 14.7542 | 14.6837 | 14.5563 | 14.3847 | 14.2132 | 14.0458 | 13.8942 | 13.2542 | 12.7321 | 12.2732
|  | HAREFIELD | CF |  |  |  | 16.1163 | 16.0868 | 16.0584 | 16.0279 | 15.9963 | 15.9637 | 15.93 | 15.8963 | 15.8637 | 15.8311 | 15.6837 | 15.6068 | 15.3584 | 14.7342 | 14.7037 | 14.6732 | 14.6405 | 14.6005 | 14.5153 | 14.4258 | 14.3342 | 14.2405 | 14.1458 | 13.6953 | 13.35 | 13.0468 | 14.9584 | 14.9279 | 14.8974 | 14.8647 | 14.83 | 14.7942 | 14.7574 | 14.7205 | 14.6595 | 14.5679 | 14.1205 | 13.7742 | 13.47
NURSLING GSP | WINCHESTER | HARESTOCK | MINIMUM HEADROOM | SU 45908 31300 | YES | 0.49158 | 29.1832 | 29.5295 | 29.4242 | 29.3137 | 29.2011 | 28.6411 | 27.3653 | 26.1053 | 24.8505 | 24.0853 | 20.0958 | 16.3453 | -24.6463 | 24.2905 | 24.9863 | 24.7621 | 24.3716 | 23.9263 | 22.7158 | 21.3421 | 19.9779 | 18.6211 | 17.82 | 13.6284 | 9.6579 | 6.2621 | 25.4747 | 25.8968 | 25.7916 | 25.5579 | 25.0968 | 23.7432 | 22.3526 | 20.9463 | 19.5411 | 18.7105 | 14.3274 | 10.1863 | 6.7284
|  | HARESTOCK | EE |  |  |  | 29.3242 | 31.5495 | 31.2495 | 30.9326 | 30.7316 | 29.5695 | 28.4042 | 27.26 | 26.0989 | 25.4211 | 21.8905 | 18.5537 | 16.0726 | 24.5842 | 27.7105 | 27.0968 | 26.0811 | 25.1663 | 23.8842 | 22.6095 | 21.3579 | 20.0895 | 19.3863 | 15.7253 | 12.2832 | 9.5663 | 25.6905 | 28.3042 | 28.0042 | 27.0263 | 26.0684 | 24.7726 | 23.4747 | 22.2 | 20.9063 | 20.1747 | 16.3263 | 12.6695 | 9.8832
|  | HARESTOCK | HT |  |  |  | 29.1832 | 31.3295 | 30.9642 | 30.5779 | 29.9211 | 28.6411 | 27.3653 | 26.1053 | 24.8505 | 24.0853 | 20.0958 | 16.3453 | 13.2611 | 24.2905 | 27.2484 | 26.4968 | 25.3442 | 24.0958 | 22.7158 | 21.3421 | 19.9779 | 18.6211 | 17.82 | 13.6284 | 9.6579 | 6.2621 | 25.4747 | 28.0842 | 27.4274 | 26.3074 | 25.0968 | 23.7432 | 22.3526 | 20.9463 | 19.5411 | 18.7105 | 14.3274 | 10.1863 | 6.7284
|  | HARESTOCK | HE |  |  |  | 29.5189 | 31.8379 | 31.6337 | 31.4084 | 31.8379 | 30.8368 | 29.8632 | 28.9095 | 27.9516 | 27.48 | 25.0747 | 22.9916 | -24.6463 | 24.9779 | 28.2137 | 27.9074 | 27.0779 | 26.3611 | 25.2495 | 24.1674 | 23.1074 | 22.04 | 21.54 | 18.9558 | 16.6768 | 14.6211 | 25.8863 | 28.5926 | 28.3884 | 28.0042 | 27.2684 | 26.1463 | 25.0537 | 23.9832 | 22.9021 | 22.3916 | 19.7305 | 17.3895 | 15.2768
|  | HARESTOCK | CF |  |  |  | 29.6305 | 29.5295 | 29.4242 | 29.3137 | 29.2011 | 29.0642 | 31.4274 | 31.2916 | 31.1579 | 30.9042 | 29.3189 | 27.9716 | 26.7779 | 25.1768 | 24.9863 | 24.7621 | 24.3716 | 23.9263 | 23.4284 | 26.5442 | 25.9926 | 25.4179 | 25.1168 | 23.42 | 21.9674 | 20.68 | 25.9979 | 25.8968 | 25.7916 | 25.5579 | 25.1274 | 24.64 | 27.4853 | 26.9474 | 26.3874 | 26.0916 | 24.4189 | 22.9316 | 21.5811
EALING GSP | EALING 22kV | HARVARD LANE | MINIMUM HEADROOM | TQ 20021 78030 | YES | 0 | 33.5913 | 33.3208 | 33.0471 | 83.7566 | 83.4503 | 83.1324 | 82.6734 | 81.9018 | 81.4303 | 80.9818 | 78.665 | 75.5766 | 34.3818 | 26.3524 | 25.685 | 24.7818 | 74.7482 | 73.5829 | 72.525 | 71.5429 | 70.6829 | 70.1734 | 69.6882 | 67.1366 | 63.4155 | 60.5418 | 27.8534 | 27.5829 | 26.9513 | 76.9155 | 75.7513 | 74.6955 | 73.7145 | 72.8555 | 72.3471 | 71.8618 | 69.3134 | 65.5482 | 62.6787
|  | HARVARD LANE | EE |  |  |  | 33.6924 | 33.4787 | 33.2524 | 84.0113 | 83.7545 | 83.4861 | 83.225 | 82.9713 | 82.6134 | 82.2261 | 81.0639 | 79.1934 | 77.3734 | 26.5197 | 26.1292 | 25.5313 | 75.8534 | 75.0176 | 74.0587 | 73.2334 | 72.3839 | 71.4871 | 71.0692 | 70.065 | 67.9639 | 65.8934 | 27.9545 | 27.7408 | 27.5145 | 78.0208 | 77.1839 | 76.2261 | 75.4018 | 74.5534 | 73.6587 | 73.2408 | 72.2861 | 70.1871 | 68.1208
|  | HARVARD LANE | HT |  |  |  | 33.5913 | 33.3208 | 33.0471 | 83.7566 | 83.4503 | 83.1324 | 82.6734 | 81.9018 | 81.4303 | 80.9818 | 78.665 | 75.5766 | 73.0439 | 26.3524 | 25.685 | 24.7818 | 74.7482 | 73.5829 | 72.525 | 71.5429 | 70.6829 | 70.1734 | 69.6882 | 67.1366 | 63.4155 | 60.5418 | 27.8534 | 27.5829 | 26.9513 | 76.9155 | 75.7513 | 74.6955 | 73.7145 | 72.8555 | 72.3471 | 71.8618 | 69.3134 | 65.5482 | 62.6787
|  | HARVARD LANE | HE |  |  |  | 33.8039 | 33.6397 | 33.4587 | 84.2576 | 84.0418 | 83.8113 | 83.5913 | 83.3839 | 83.1903 | 83.0229 | 82.3966 | 80.3587 | 34.3818 | 26.6397 | 26.4671 | 26.0555 | 76.4945 | 75.7818 | 74.9218 | 74.2082 | 73.4587 | 72.7261 | 72.4492 | 71.2818 | 68.6071 | 67.1808 | 28.0661 | 27.9018 | 27.7208 | 78.5197 | 77.9503 | 77.0892 | 76.3766 | 75.6271 | 74.8955 | 74.6187 | 73.4534 | 70.7124 | 69.285
|  | HARVARD LANE | CF |  |  |  | 33.8629 | 33.7513 | 33.6366 | 84.5176 | 84.3945 | 84.2661 | 84.1355 | 84.0082 | 83.8808 | 83.7545 | 83.1882 | 82.9029 | 82.0808 | 26.7039 | 26.5871 | 26.4671 | 77.3418 | 77.0724 | 76.7787 | 76.4766 | 76.1755 | 75.7018 | 75.1945 | 72.8703 | 71.8313 | 70.8534 | 28.125 | 28.0134 | 27.8987 | 78.7797 | 78.6566 | 78.5282 | 78.3976 | 78.2703 | 77.8703 | 77.3608 | 75.0397 | 74.0029 | 73.0261
COWLEY GSP |  | HARWELL | MINIMUM HEADROOM | SU 47395 86969 | YES | 0.92632 | 40.1168 | 40.6379 | 40.6232 | 40.1211 | 40.1158 | 40.1116 | 40.58 | 40.5674 | 40.5547 | 40.5442 | 40.6042 | 41.7726 | 31.9389 | 37.1968 | 37.8389 | 37.8242 | 37.2011 | 37.1958 | 37.1916 | 37.7811 | 37.7684 | 37.7558 | 37.7453 | 37.8053 | 39.2853 | 39.2558 | 37.74 | 38.3168 | 38.3021 | 37.7442 | 37.7389 | 37.7347 | 38.2589 | 38.2463 | 38.2337 | 38.2232 | 38.2832 | 39.6 | 39.5705
|  | HARWELL | EE |  |  |  | 42.1316 | 40.6463 | 40.6347 | 40.6211 | 40.6074 | 40.5937 | 40.58 | 40.5674 | 40.5547 | 40.5442 | 41.8442 | 41.8179 | 41.7989 | 39.9653 | 37.8474 | 37.8358 | 37.8221 | 37.8084 | 37.7947 | 37.7811 | 37.7684 | 37.7558 | 37.7453 | 39.3568 | 39.3305 | 39.3116 | 40.5242 | 38.3253 | 38.3137 | 38.3 | 38.2863 | 38.2726 | 38.2589 | 38.2463 | 38.2337 | 38.2232 | 39.6716 | 39.6453 | 39.6263
|  | HARWELL | HT |  |  |  | 40.1168 | 40.6379 | 40.6232 | 40.6074 | 40.5916 | 41.9147 | 41.8979 | 41.8842 | 41.8705 | 41.8579 | 41.8084 | 41.7726 | 41.7432 | 37.1968 | 37.8389 | 37.8242 | 37.8084 | 37.7926 | 39.4274 | 39.4105 | 39.3968 | 39.3832 | 39.3705 | 39.3211 | 39.2853 | 39.2558 | 37.74 | 38.3168 | 38.3021 | 38.2863 | 38.2705 | 39.7421 | 39.7253 | 39.7116 | 39.6979 | 39.6853 | 39.6358 | 39.6 | 39.5705
|  | HARWELL | HE |  |  |  | 42.14 | 40.6579 | 40.6495 | 40.64 | 40.6305 | 40.6189 | 40.6084 | 40.5989 | 40.5895 | 40.5821 | 41.8947 | 41.88 | 31.9389 | 39.9737 | 37.8589 | 37.8505 | 37.8411 | 37.8316 | 37.82 | 37.8095 | 37.8 | 37.7905 | 37.7832 | 39.4074 | 39.3926 | 39.3832 | 40.5326 | 38.3368 | 38.3284 | 38.3189 | 38.3095 | 38.2979 | 38.2874 | 38.2779 | 38.2684 | 38.2611 | 39.7221 | 39.7074 | 39.6979
|  | HARWELL | CF |  |  |  | 42.1579 | 42.1484 | 42.1389 | 40.1211 | 40.1158 | 40.1116 | 40.6421 | 40.6368 | 40.6316 | 40.6263 | 40.6042 | 41.9326 | 41.9263 | 39.9968 | 39.9874 | 39.9747 | 37.2011 | 37.1958 | 37.1916 | 37.8432 | 37.8379 | 37.8326 | 37.8274 | 37.8053 | 39.4453 | 39.4389 | 40.5663 | 40.5516 | 40.5358 | 37.7442 | 37.7389 | 37.7347 | 38.3211 | 38.3158 | 38.3105 | 38.3053 | 38.2832 | 39.76 | 39.7537
BRAMLEY (FLEE) | FERNHURST | HASLEMERE | MINIMUM HEADROOM | SU 89300 31710 | YES | 0.62316 | 24.8684 | 24.5126 | 24.1558 | 23.7747 | 23.3832 | 22.9726 | 22.5611 | 22.1968 | 21.7063 | 21.0653 | 18.0737 | 15.1453 | -11.5358 | 20.4379 | 19.5 | 18.8232 | 18.0958 | 17.3505 | 16.5368 | 15.6 | 14.9326 | 14.2305 | 13.5337 | 10.26 | 7.0105 | 4.0695 | 21.2695 | 20.4305 | 19.7547 | 19.0263 | 18.28 | 17.4653 | 16.5263 | 15.8558 | 15.1516 | 14.4526 | 11.16 | 7.8905 | 4.9389
|  | HASLEMERE | EE |  |  |  | 25.0074 | 24.7316 | 24.4379 | 24.1274 | 23.8053 | 23.4642 | 23.1305 | 22.8158 | 22.5095 | 22.2358 | 20.1705 | 17.8442 | 15.8305 | 20.5863 | 20.0095 | 19.44 | 18.8537 | 18.2558 | 17.6179 | 16.9116 | 16.3305 | 15.7305 | 15.1495 | 12.5758 | 10.0021 | 7.7337 | 21.4179 | 20.94 | 20.3705 | 19.7832 | 19.1863 | 18.5463 | 17.8368 | 17.2526 | 16.6495 | 16.0642 | 13.4653 | 10.8632 | 8.5863
|  | HASLEMERE | HT |  |  |  | 24.8684 | 24.5126 | 24.1558 | 23.7747 | 23.3832 | 22.9726 | 22.5611 | 22.1968 | 21.7063 | 21.0653 | 18.0737 | 15.1453 | 12.5242 | 20.4379 | 19.5 | 18.8232 | 18.0958 | 17.3505 | 16.5368 | 15.6 | 14.9326 | 14.2305 | 13.5337 | 10.26 | 7.0105 | 4.0695 | 21.2695 | 20.4305 | 19.7547 | 19.0263 | 18.28 | 17.4653 | 16.5263 | 15.8558 | 15.1516 | 14.4526 | 11.16 | 7.8905 | 4.9389
|  | HASLEMERE | HE |  |  |  | 25.1958 | 25.0105 | 24.8063 | 24.5789 | 24.3347 | 24.0695 | 23.8158 | 23.5747 | 23.3495 | 23.1547 | 22.4832 | 21.0684 | -11.5358 | 20.7874 | 20.5789 | 20.24 | 19.8358 | 19.4105 | 18.9326 | 18.3895 | 17.9589 | 17.5274 | 17.1 | 15.3 | 13.46 | 11.8368 | 21.62 | 21.4095 | 21.1747 | 20.7674 | 20.3411 | 19.8611 | 19.3189 | 18.8853 | 18.4516 | 18.0232 | 16.2126 | 14.3653 | 12.7337
|  | HASLEMERE | CF |  |  |  | 25.3053 | 25.2011 | 25.0937 | 24.9821 | 24.8663 | 24.7453 | 24.62 | 24.4968 | 24.3768 | 24.2558 | 23.7137 | 23.4337 | 23.0442 | 20.9063 | 20.7884 | 20.6758 | 20.5579 | 20.4358 | 20.2526 | 20.0358 | 19.7958 | 19.5347 | 19.2589 | 17.8789 | 16.64 | 15.5642 | 21.7379 | 21.62 | 21.5063 | 21.3895 | 21.2674 | 21.14 | 20.9674 | 20.7253 | 20.4632 | 20.1863 | 18.8032 | 17.5589 | 16.4779
BRAMLEY (FLEE) | FERNHURST | HASLINGBOURNE | MINIMUM HEADROOM | SU 98188 20276 | YES | 0 | 12.1611 | 12.0326 | 11.9011 | 11.7632 | 11.6211 | 11.4747 | 11.2337 | 11.0253 | 10.7926 | 10.5453 | 9.4368 | 8.2084 | -0.91474 | 10.1989 | 9.9632 | 9.7158 | 9.4211 | 9.1368 | 8.8453 | 8.5842 | 8.3621 | 8.1095 | 7.8389 | 6.6137 | 5.2284 | 3.9621 | 10.6 | 10.4168 | 10.18 | 9.8968 | 9.6168 | 9.3242 | 9.0632 | 8.8421 | 8.5884 | 8.3168 | 7.0916 | 5.7042 | 4.4379
|  | HASLINGBOURNE | EE |  |  |  | 12.2095 | 12.1084 | 12.0021 | 11.8884 | 11.7705 | 11.6495 | 11.5305 | 11.4189 | 11.3126 | 11.12 | 10.2716 | 9.2905 | 8.4137 | 10.3021 | 10.1211 | 9.9358 | 9.7074 | 9.4905 | 9.2674 | 9.0726 | 8.8884 | 8.6884 | 8.4726 | 7.5389 | 6.4305 | 5.4326 | 10.6526 | 10.5474 | 10.3884 | 10.1684 | 9.9579 | 9.7432 | 9.5495 | 9.3653 | 9.1642 | 8.9484 | 8.0116 | 6.9 | 5.9
|  | HASLINGBOURNE | HT |  |  |  | 12.1611 | 12.0326 | 11.9011 | 11.7632 | 11.6211 | 11.4747 | 11.2337 | 11.0253 | 10.7926 | 10.5453 | 9.4368 | 8.2084 | 7.0926 | 10.1989 | 9.9632 | 9.7158 | 9.4211 | 9.1368 | 8.8453 | 8.5842 | 8.3621 | 8.1095 | 7.8389 | 6.6137 | 5.2284 | 3.9621 | 10.6 | 10.4168 | 10.18 | 9.8968 | 9.6168 | 9.3242 | 9.0632 | 8.8421 | 8.5884 | 8.3168 | 7.0916 | 5.7042 | 4.4379
|  | HASLINGBOURNE | HE |  |  |  | 12.28 | 12.2126 | 12.1379 | 12.0558 | 11.9674 | 11.8726 | 11.7821 | 11.6968 | 11.6179 | 11.5495 | 11.1705 | 10.4158 | -0.91474 | 10.4442 | 10.3305 | 10.2116 | 10.06 | 9.9147 | 9.7495 | 9.6126 | 9.4853 | 9.3411 | 9.1811 | 8.5105 | 7.6474 | 6.8842 | 10.7284 | 10.6579 | 10.5811 | 10.4937 | 10.3695 | 10.2084 | 10.0758 | 9.9505 | 9.8116 | 9.6579 | 8.9916 | 8.1284 | 7.3642
|  | HASLINGBOURNE | CF |  |  |  | 12.3211 | 12.2842 | 12.2453 | 12.2053 | 12.1642 | 12.1211 | 12.0779 | 12.0347 | 11.9926 | 11.9495 | 11.76 | 11.4674 | 11.0453 | 10.4968 | 10.4495 | 10.38 | 10.3011 | 10.2211 | 10.1358 | 10.0611 | 9.9863 | 9.9084 | 9.8126 | 9.3558 | 8.7989 | 8.3116 | 10.7716 | 10.7326 | 10.6916 | 10.6495 | 10.6053 | 10.56 | 10.5147 | 10.44 | 10.3653 | 10.2726 | 9.8358 | 9.28 | 8.7926
MELKSHAM GSP | FROME BSP | HAWKERIDGE | MINIMUM HEADROOM | ST 86422 53026 | YES | 8.0842 | 18.1347 | 10.5505 | 10.4789 | 10.4074 | 10.3379 | 10.2684 | 10.2 | 10.1358 | 10.0726 | 10.0105 | 9.7095 | 7.7663 | -7.5611 | 16.4779 | 8.42 | 8.3379 | 8.2558 | 8.1768 | 8.0979 | 8.02 | 7.9463 | 7.8747 | 7.8032 | 7.4568 | 5.1726 | 5.0463 | 16.6558 | 8.8021 | 8.72 | 8.6379 | 8.5589 | 8.48 | 8.4021 | 8.3284 | 8.2558 | 8.1842 | 7.8389 | 5.5537 | 5.4274
|  | HAWKERIDGE | EE |  |  |  | 18.6379 | 10.6032 | 10.5474 | 10.4916 | 10.4379 | 10.3842 | 10.3316 | 10.28 | 10.2305 | 10.1811 | 9.9516 | 7.7663 | 7.6558 | 16.52 | 8.48 | 8.4168 | 8.3537 | 8.2916 | 8.2305 | 8.1705 | 8.1116 | 8.0547 | 7.9989 | 7.7358 | 5.1726 | 5.0463 | 16.9021 | 8.8621 | 8.7989 | 8.7358 | 8.6737 | 8.6126 | 8.5526 | 8.4937 | 8.4368 | 8.3811 | 8.1168 | 5.5537 | 5.4274
|  | HAWKERIDGE | HT |  |  |  | 18.6242 | 10.5505 | 10.4789 | 10.4074 | 10.3379 | 10.2684 | 10.2 | 10.1358 | 10.0726 | 10.0105 | 9.7095 | 9.4232 | 9.1453 | 16.5042 | 8.42 | 8.3379 | 8.2558 | 8.1768 | 8.0979 | 8.02 | 7.9463 | 7.8747 | 7.8032 | 7.4568 | 7.1253 | 6.8032 | 16.8863 | 8.8021 | 8.72 | 8.6379 | 8.5589 | 8.48 | 8.4021 | 8.3284 | 8.2558 | 8.1842 | 7.8389 | 7.5074 | 7.1853
|  | HAWKERIDGE | HE |  |  |  | 18.6516 | 10.6411 | 10.6305 | 10.6053 | 10.5716 | 10.5389 | 10.5063 | 10.4737 | 10.4432 | 10.4147 | 10.2821 | 7.8947 | -7.5611 | 16.5337 | 8.5232 | 8.5116 | 8.4842 | 8.4453 | 8.4084 | 8.3716 | 8.3347 | 8.3 | 8.2674 | 8.1158 | 5.3147 | 5.2105 | 16.9158 | 8.9053 | 8.8937 | 8.8663 | 8.8274 | 8.7905 | 8.7537 | 8.7168 | 8.6821 | 8.6495 | 8.4968 | 5.6958 | 5.5916
|  | HAWKERIDGE | CF |  |  |  | 18.1347 | 10.6526 | 10.8758 | 10.8726 | 10.8695 | 10.8621 | 10.8547 | 10.8484 | 10.8411 | 10.8347 | 10.8032 | 10.7811 | 10.7621 | 16.4779 | 8.5347 | 8.5821 | 8.5768 | 8.5705 | 8.5495 | 8.5232 | 8.4989 | 8.4737 | 8.4495 | 8.3284 | 8.2211 | 8.12 | 16.6558 | 8.9168 | 8.9105 | 8.9053 | 8.8989 | 8.8779 | 8.8526 | 8.8284 | 8.8032 | 8.78 | 8.6621 | 8.5558 | 8.4568
BRAMLEY (FLEE) | COXMOOR WOOD BSP | HAWLEY | MINIMUM HEADROOM | SU 85973 57691 | YES | 0.30211 | 32.3526 | 32.0642 | 31.7758 | 31.4684 | 31.1495 | 30.8211 | 30.4905 | 30.0811 | 29.64 | 29.2295 | 27.3926 | 25.4853 | 5.9811 | 29.82 | 29.2516 | 28.6895 | 28.1084 | 27.5368 | 26.9716 | 26.4095 | 25.8989 | 25.4221 | 24.9768 | 22.9684 | 20.8232 | 18.8589 | 30.4084 | 30.0126 | 29.4547 | 28.8747 | 28.3032 | 27.7368 | 27.1747 | 26.6653 | 26.1874 | 25.7432 | 23.7326 | 21.5884 | 19.6232
|  | HAWLEY | EE |  |  |  | 32.4589 | 32.2305 | 31.9916 | 31.7358 | 31.4684 | 31.1916 | 30.9242 | 30.6705 | 30.4242 | 30.2063 | 28.8074 | 27.3505 | 26.0568 | 30.0653 | 29.6232 | 29.1695 | 28.6989 | 28.2337 | 27.7663 | 27.3147 | 26.8874 | 26.4737 | 26.1 | 24.5263 | 22.8821 | 21.4053 | 30.5221 | 30.2811 | 29.9316 | 29.4653 | 28.9989 | 28.5316 | 28.0811 | 27.6526 | 27.2389 | 26.8653 | 25.2916 | 23.6474 | 22.1695
|  | HAWLEY | HT |  |  |  | 32.3526 | 32.0642 | 31.7758 | 31.4684 | 31.1495 | 30.8211 | 30.4905 | 30.0811 | 29.64 | 29.2295 | 27.3926 | 25.4853 | 23.7547 | 29.82 | 29.2516 | 28.6895 | 28.1084 | 27.5368 | 26.9716 | 26.4095 | 25.8989 | 25.4221 | 24.9768 | 22.9684 | 20.8232 | 18.8589 | 30.4084 | 30.0126 | 29.4547 | 28.8747 | 28.3032 | 27.7368 | 27.1747 | 26.6653 | 26.1874 | 25.7432 | 23.7326 | 21.5884 | 19.6232
|  | HAWLEY | HE |  |  |  | 32.6063 | 32.4495 | 32.2747 | 32.0832 | 31.8768 | 31.6568 | 31.4453 | 31.2463 | 31.0621 | 30.9021 | 30.3611 | 29.8347 | 5.9811 | 30.2558 | 30.0832 | 29.8137 | 29.4884 | 29.1621 | 28.8221 | 28.4968 | 28.1937 | 27.9084 | 27.6611 | 26.6989 | 25.6337 | 24.7137 | 30.68 | 30.5168 | 30.3337 | 30.1347 | 29.9158 | 29.5853 | 29.2632 | 28.9589 | 28.6747 | 28.4263 | 27.4642 | 26.3989 | 25.4789
|  | HAWLEY | CF |  |  |  | 32.6937 | 32.6032 | 32.5095 | 32.4126 | 32.3126 | 32.2074 | 32.1011 | 31.9979 | 31.8947 | 31.7905 | 31.3305 | 31.1 | 30.78 | 30.3537 | 30.2526 | 30.1474 | 30.0221 | 29.8358 | 29.6411 | 29.4474 | 29.2568 | 29.0684 | 28.8811 | 28.0211 | 27.2368 | 26.5832 | 30.7726 | 30.6768 | 30.5779 | 30.4758 | 30.3716 | 30.2611 | 30.1495 | 30.0126 | 29.8305 | 29.6474 | 28.7863 | 28.0021 | 27.3484
NORTH HYDE GSP |  | HAYES | MINIMUM HEADROOM | TQ 09519 79541 | NO | 1.6326 | 72.2337 | 71.7747 | 71.3105 | 70.8168 | 130.3032 | 129.7716 | 128.7537 | 127.2326 | 125.7611 | 124.3747 | 117.9768 | 112.3789 | 50.6958 | 61.0589 | 59.9516 | 58.5253 | 56.7305 | 115.0147 | 113.0821 | 111.28 | 109.5758 | 107.9242 | 106.3663 | 99.1432 | 92.7905 | 86.8295 | 63.6126 | 62.9137 | 61.4747 | 59.68 | 117.9642 | 116.0305 | 114.2284 | 112.5242 | 110.8726 | 109.3137 | 102.0895 | 95.7347 | 89.7726
|  | HAYES | EE |  |  |  | 72.4042 | 72.0411 | 71.6568 | 71.2484 | 130.8179 | 130.3695 | 129.9358 | 129.5211 | 128.7979 | 127.6937 | 122.7958 | 118.6305 | 114.7853 | 61.4158 | 60.6042 | 59.4979 | 58.1095 | 116.8411 | 115.4221 | 114.0242 | 112.6779 | 111.3516 | 110.1179 | 104.5989 | 99.8695 | 95.4747 | 63.7832 | 63.42 | 62.4537 | 61.0589 | 119.7905 | 118.3716 | 116.9737 | 115.6274 | 114.3 | 113.0663 | 107.5453 | 102.8147 | 98.4189
|  | HAYES | HT |  |  |  | 72.2337 | 71.7747 | 71.3105 | 70.8168 | 130.3032 | 129.7716 | 128.7537 | 127.2326 | 125.7611 | 124.3747 | 117.9768 | 112.3789 | 107.1516 | 61.0589 | 59.9516 | 58.5253 | 56.7305 | 115.0147 | 113.0821 | 111.28 | 109.5758 | 107.9242 | 106.3663 | 99.1432 | 92.7905 | 86.8295 | 63.6126 | 62.9137 | 61.4747 | 59.68 | 117.9642 | 116.0305 | 114.2284 | 112.5242 | 110.8726 | 109.3137 | 102.0895 | 95.7347 | 89.7726
|  | HAYES | HE |  |  |  | 72.6253 | 72.3632 | 72.0747 | 71.7547 | 131.4105 | 131.0442 | 130.6937 | 130.3632 | 130.0547 | 129.7884 | 125.9505 | 122.68 | 50.6958 | 61.86 | 61.3053 | 60.4832 | 59.3232 | 118.2695 | 117.0484 | 115.8495 | 114.7 | 113.5821 | 112.5516 | 108.0505 | 104.3053 | 100.8716 | 64.0042 | 63.7421 | 63.4495 | 62.2747 | 121.2189 | 119.9979 | 118.7989 | 117.6495 | 116.5305 | 115.5 | 110.9979 | 107.2516 | 103.8168
|  | HAYES | CF |  |  |  | 72.7611 | 72.6053 | 72.4453 | 72.2768 | 132.1042 | 131.9253 | 131.7432 | 131.5632 | 131.3863 | 131.2084 | 130.4168 | 129.7958 | 127.9421 | 62.3621 | 62.0579 | 61.6684 | 61.1989 | 120.7558 | 120.2105 | 119.6368 | 119.0474 | 118.4284 | 117.8021 | 114.7674 | 112.3663 | 110.2295 | 64.14 | 63.9842 | 63.8242 | 63.6558 | 123.4832 | 123.1747 | 122.5937 | 121.9979 | 121.3779 | 120.7526 | 117.7158 | 115.3147 | 113.1779
COWLEY GSP | HEADINGTON BSP | HEADINGTON | MINIMUM HEADROOM | SP 54440 08085 | YES | 0 | 44.2768 | 43.9737 | 43.6674 | 43.3432 | 43.0042 | 42.6411 | 40.3411 | 39.7653 | 39.2516 | 38.7737 | 36.6 | 34.7389 | 10.5305 | 40.9211 | 38.5389 | 37.9611 | 37.3716 | 36.7811 | 36.1874 | 32.7495 | 32.1347 | 31.5895 | 31.0832 | 28.7779 | 26.8074 | 25.2189 | 41.7 | 39.9611 | 39.3832 | 38.7926 | 38.2032 | 37.6042 | 34.16 | 33.54 | 32.9874 | 32.4758 | 30.1274 | 28.1074 | 26.3926
|  | HEADINGTON | EE |  |  |  | 44.3874 | 44.1484 | 43.8926 | 44.9526 | 44.4958 | 43.9716 | 41.1337 | 40.6379 | 40.1821 | 39.7705 | 39.8358 | 38.3211 | 37.1674 | 41.0463 | 39.4053 | 38.5989 | 37.9368 | 37.3337 | 36.7789 | 33.5074 | 32.9842 | 32.5084 | 32.0821 | 33.1358 | 31.5758 | 30.3305 | 41.8189 | 40.8263 | 40.02 | 39.3589 | 38.7547 | 38.1947 | 34.9147 | 34.3842 | 33.9021 | 33.4663 | 34.8411 | 33.2116 | 31.9463
|  | HEADINGTON | HT |  |  |  | 44.2768 | 43.9737 | 43.6674 | 43.3432 | 43.0042 | 42.6411 | 40.3411 | 39.7653 | 39.2516 | 38.7737 | 36.6 | 34.7389 | 33.1789 | 40.9211 | 38.5389 | 37.9611 | 37.3716 | 36.7811 | 36.1874 | 32.7495 | 32.1347 | 31.5895 | 31.0832 | 28.7779 | 26.8074 | 25.2189 | 41.7 | 39.9611 | 39.3832 | 38.7926 | 38.2032 | 37.6042 | 34.16 | 33.54 | 32.9874 | 32.4758 | 30.1274 | 28.1074 | 26.3926
|  | HEADINGTON | HE |  |  |  | 44.5421 | 44.3747 | 44.1905 | 43.9863 | 43.7663 | 44.9063 | 42.2095 | 41.8589 | 41.5568 | 41.2811 | 39.5842 | 38.8411 | 10.5305 | 41.2095 | 39.9095 | 39.2526 | 38.7568 | 38.3095 | 37.9042 | 34.7695 | 34.3989 | 34.0832 | 33.7947 | 31.7653 | 30.9842 | 30.3495 | 41.9789 | 41.3105 | 40.6758 | 40.1789 | 39.7316 | 39.3232 | 36.1842 | 35.8095 | 35.4895 | 35.1979 | 32.9821 | 32.18 | 31.5263
|  | HEADINGTON | CF |  |  |  | 44.6337 | 44.5379 | 44.4368 | 44.3316 | 44.2242 | 44.1053 | 43.9853 | 43.8674 | 43.7516 | 43.6347 | 43.1105 | 42.7874 | 42.3063 | 41.3053 | 40.9463 | 40.76 | 40.5674 | 40.3726 | 40.1705 | 38.7926 | 38.5368 | 38.1895 | 37.8263 | 36.2147 | 35.5526 | 35.0295 | 42.0705 | 41.9474 | 41.8421 | 41.7316 | 41.6189 | 41.4958 | 40.2126 | 39.9526 | 39.6042 | 39.24 | 37.62 | 36.9484 | 36.4116
NURSLING GSP | VELMORE BSP | HEDGE END | MINIMUM HEADROOM | SU 49035 15685 | YES | 0.38842 | 32.0116 | 31.4853 | 30.7926 | 29.8695 | 29.1358 | 28.1421 | 27.3453 | 26.4905 | 25.8242 | 25.4547 | 23.7726 | 22.2758 | 13.2126 | 29.4484 | 28.8579 | 28.0726 | 27.02 | 26.1895 | 25.0568 | 24.1526 | 23.1737 | 22.4147 | 22 | 20.1295 | 18.4347 | 16.8874 | 29.9905 | 29.3863 | 28.58 | 27.4989 | 26.6474 | 25.4821 | 24.5547 | 23.5642 | 22.8042 | 22.3916 | 20.5232 | 18.8274 | 17.28
|  | HEDGE END | EE |  |  |  | 32.1232 | 31.6558 | 31.0147 | 30.1432 | 29.4568 | 28.5547 | 27.8389 | 27.12 | 26.4421 | 26.1295 | 24.7547 | 23.5495 | 22.4716 | 29.5705 | 29.0432 | 28.3137 | 27.3158 | 26.5358 | 25.5053 | 24.6905 | 23.8716 | 23.0947 | 22.7453 | 21.2211 | 19.8547 | 18.62 | 30.1147 | 29.5737 | 28.8242 | 27.8 | 26.9989 | 25.9389 | 25.1042 | 24.2621 | 23.4842 | 23.1358 | 21.6116 | 20.2411 | 19.0063
|  | HEDGE END | HT |  |  |  | 32.0116 | 31.4853 | 30.7926 | 29.8695 | 29.1358 | 28.1421 | 27.3453 | 26.4905 | 25.8242 | 25.4547 | 23.7726 | 22.2758 | 20.9158 | 29.4484 | 28.8579 | 28.0726 | 27.02 | 26.1895 | 25.0568 | 24.1526 | 23.1737 | 22.4147 | 22 | 20.1295 | 18.4347 | 16.8874 | 29.9905 | 29.3863 | 28.58 | 27.4989 | 26.6474 | 25.4821 | 24.5547 | 23.5642 | 22.8042 | 22.3916 | 20.5232 | 18.8274 | 17.28
|  | HEDGE END | HE |  |  |  | 32.2789 | 31.8853 | 31.3137 | 30.5105 | 29.8905 | 29.0474 | 28.3874 | 27.7042 | 27.1063 | 26.8547 | 25.6779 | 24.7253 | 13.2126 | 29.7389 | 29.2905 | 28.6368 | 27.7137 | 27.0042 | 26.0368 | 25.2842 | 24.5011 | 23.8137 | 23.5316 | 22.1758 | 21.0821 | 20.0947 | 30.2853 | 29.8253 | 29.1537 | 28.2042 | 27.4758 | 26.4811 | 25.7063 | 24.9011 | 24.2042 | 23.9221 | 22.5632 | 21.4705 | 20.4832
|  | HEDGE END | CF |  |  |  | 32.4 | 32.2589 | 31.9768 | 31.6116 | 31.3347 | 30.9895 | 30.6989 | 30.4368 | 30.1663 | 29.9789 | 29.1189 | 28.5263 | 28.0074 | 29.9579 | 29.7147 | 29.3926 | 28.9726 | 28.6568 | 28.2611 | 27.9295 | 27.6316 | 27.3232 | 27.1126 | 26.1432 | 25.4695 | 24.8726 | 30.5095 | 30.26 | 29.9295 | 29.4979 | 29.1737 | 28.7674 | 28.4263 | 28.1189 | 27.8021 | 27.5863 | 26.5937 | 25.9 | 25.2874
BRAMLEY (FLEE) | READING BSP | HENLEY | MINIMUM HEADROOM | SU 76070 82422 | YES | 0.34421 | 29.1316 | 28.84 | 28.5453 | 28.2347 | 27.9116 | 27.5695 | 27.2274 | 26.9221 | 26.6432 | 26.3863 | 24.5779 | 22.7758 | -5.5505 | 24.4274 | 23.9516 | 23.3968 | 22.6126 | 21.7737 | 21.1747 | 20.58 | 20.0179 | 19.4874 | 18.9926 | 16.78 | 14.7358 | 12.7042 | 25.0295 | 24.7221 | 24.4116 | 23.7505 | 22.8937 | 22.2853 | 21.6811 | 21.1137 | 20.5811 | 20.0821 | 17.8474 | 15.7779 | 13.7358
|  | HENLEY | EE |  |  |  | 29.2411 | 29.0126 | 28.7716 | 28.5137 | 28.2442 | 27.9568 | 27.6758 | 27.4095 | 27.1484 | 26.9126 | 25.9263 | 24.5168 | 23.2695 | 24.5453 | 24.3053 | 23.8842 | 23.2116 | 22.4737 | 21.9779 | 21.4874 | 21.0116 | 20.5516 | 20.1284 | 18.3263 | 16.7505 | 15.2874 | 25.1463 | 24.9053 | 24.6526 | 24.3453 | 23.6063 | 23.1021 | 22.6011 | 22.1168 | 21.6463 | 21.2137 | 19.3811 | 17.7684 | 16.2937
|  | HENLEY | HT |  |  |  | 29.1316 | 28.84 | 28.5453 | 28.2347 | 27.9116 | 27.5695 | 27.2274 | 26.9221 | 26.6432 | 26.3863 | 24.5779 | 22.7758 | 20.9916 | 24.4274 | 23.9516 | 23.3968 | 22.6126 | 21.7737 | 21.1747 | 20.58 | 20.0179 | 19.4874 | 18.9926 | 16.78 | 14.7358 | 12.7042 | 25.0295 | 24.7221 | 24.4116 | 23.7505 | 22.8937 | 22.2853 | 21.6811 | 21.1137 | 20.5811 | 20.0821 | 17.8474 | 15.7779 | 13.7358
|  | HENLEY | HE |  |  |  | 29.3937 | 29.2368 | 29.0663 | 28.8737 | 28.6684 | 28.4421 | 28.2263 | 28.0232 | 27.8305 | 27.6642 | 27.0832 | 26.7326 | -5.5505 | 24.7084 | 24.5453 | 24.3674 | 23.9968 | 23.4 | 23.0305 | 22.6758 | 22.3326 | 22.0042 | 21.7126 | 20.5937 | 19.6832 | 18.7716 | 25.3116 | 25.1474 | 24.9695 | 24.7568 | 24.5284 | 24.1695 | 23.8126 | 23.4642 | 23.1295 | 22.8326 | 21.6853 | 20.7568 | 19.8358
|  | HENLEY | CF |  |  |  | 29.4789 | 29.3884 | 29.2947 | 29.1968 | 29.0968 | 28.9884 | 28.8779 | 28.7716 | 28.6632 | 28.5568 | 28.0779 | 27.8284 | 27.68 | 24.7979 | 24.7021 | 24.6042 | 24.4958 | 24.3158 | 24.1074 | 23.8947 | 23.6842 | 23.4663 | 23.2558 | 22.2947 | 21.6011 | 20.9968 | 25.4 | 25.3053 | 25.2063 | 25.0979 | 24.9853 | 24.8716 | 24.7547 | 24.6432 | 24.5284 | 24.3884 | 23.42 | 22.7084 | 22.0842
AXMINSTER | YEOVIL BSP | HENSTRIDGE | MINIMUM HEADROOM | ST 72676 19263 | YES | 0.31684 | 23.1589 | 22.6958 | 22.2705 | 21.8189 | 21.1853 | 20.4716 | 19.9842 | 19.5168 | 19.2653 | 19.0253 | 17.8537 | 16.6768 | 7.9211 | 22.6568 | 22.1379 | 21.6653 | 21.1632 | 20.4463 | 19.6453 | 19.1105 | 18.5958 | 18.3347 | 18.0863 | 16.8695 | 15.6347 | 14.4589 | 22.8537 | 22.34 | 21.8726 | 21.3758 | 20.6674 | 19.8705 | 19.3358 | 18.8221 | 18.5579 | 18.3032 | 17.0547 | 15.7853 | 14.6032
|  | HENSTRIDGE | EE |  |  |  | 23.2779 | 22.8768 | 22.5021 | 22.1063 | 21.5221 | 20.8568 | 20.4168 | 19.9832 | 19.7547 | 19.5379 | 18.5358 | 17.5421 | 16.7274 | 22.7863 | 22.3347 | 21.9179 | 21.4747 | 20.8116 | 20.0642 | 19.5811 | 19.1074 | 18.8737 | 18.6537 | 17.6474 | 16.6453 | 15.7589 | 22.9821 | 22.5358 | 22.1221 | 21.6853 | 21.0295 | 20.2853 | 19.8021 | 19.3253 | 19.0853 | 18.8568 | 17.8021 | 16.7411 | 15.8432
|  | HENSTRIDGE | HT |  |  |  | 23.1589 | 22.6958 | 22.2705 | 21.8189 | 21.1853 | 20.4716 | 19.9842 | 19.5168 | 19.2653 | 19.0253 | 17.8537 | 16.6768 | 15.6042 | 22.6568 | 22.1379 | 21.6653 | 21.1632 | 20.4463 | 19.6453 | 19.1105 | 18.5958 | 18.3347 | 18.0863 | 16.8695 | 15.6347 | 14.4589 | 22.8537 | 22.34 | 21.8726 | 21.3758 | 20.6674 | 19.8705 | 19.3358 | 18.8221 | 18.5579 | 18.3032 | 17.0547 | 15.7853 | 14.6032
|  | HENSTRIDGE | HE |  |  |  | 23.4516 | 23.1337 | 22.8105 | 22.4863 | 21.9716 | 21.3737 | 21.0095 | 20.6526 | 20.4989 | 20.3632 | 19.7779 | 19.2379 | 7.9211 | 22.9768 | 22.6158 | 22.2516 | 21.8863 | 21.2989 | 20.6211 | 20.2168 | 19.8189 | 19.6621 | 19.5232 | 18.9253 | 18.3495 | 17.7358 | 23.1705 | 22.8147 | 22.4537 | 22.0937 | 21.5126 | 20.8411 | 20.4379 | 20.0411 | 19.8811 | 19.74 | 19.1211 | 18.5326 | 17.9095
|  | HENSTRIDGE | CF |  |  |  | 23.5916 | 23.4211 | 23.2547 | 23.0989 | 22.8653 | 22.6053 | 22.4232 | 22.2347 | 22.1411 | 22.0516 | 21.6284 | 21.2642 | 20.8989 | 23.1326 | 22.9389 | 22.7516 | 22.5758 | 22.3095 | 22.0147 | 21.8126 | 21.6021 | 21.5042 | 21.4095 | 20.9642 | 20.5716 | 20.1726 | 23.3253 | 23.1337 | 22.9484 | 22.7747 | 22.5116 | 22.2189 | 22.0179 | 21.8084 | 21.7095 | 21.6137 | 21.1642 | 20.7653 | 20.3589
BRAMLEY (FLEE) | ALTON | HERRIARD | MINIMUM HEADROOM | SU 66770 44972 | YES | 0 | 7.4495 | 7.4032 | 7.3568 | 7.3084 | 7.2568 | 7.0558 | 6.8537 | 4.6779 | 4.5863 | 4.4895 | 3.6989 | 2.7242 | 1.9158 | 7.4632 | 7.4147 | 7.3653 | 7.3158 | 7.2621 | 7.0558 | 6.8495 | 4.3768 | 4.3021 | 4.2242 | 3.5084 | 2.5947 | 2.2968 | 7.4495 | 7.4074 | 7.3621 | 7.3105 | 7.2568 | 7.0379 | 6.8189 | 4.2937 | 4.2011 | 4.1042 | 3.2758 | 2.2379 | 1.8937
|  | HERRIARD | EE |  |  |  | 7.4684 | 7.4347 | 7.3958 | 7.3547 | 7.3137 | 7.2221 | 7.1095 | 6.9947 | 6.8642 | 6.7284 | 4.8989 | 3.7158 | 3.2147 | 7.4779 | 7.4484 | 7.4084 | 7.3663 | 7.3895 | 7.3116 | 7.2147 | 7.1189 | 7.0095 | 6.8968 | 5.0484 | 4 | 3.5221 | 7.4663 | 7.4368 | 7.4011 | 7.3611 | 7.3421 | 7.2484 | 7.1326 | 7.0158 | 6.8832 | 6.7432 | 4.7232 | 3.4737 | 2.9337
|  | HERRIARD | HT |  |  |  | 7.4495 | 7.4032 | 7.3568 | 7.3084 | 7.2568 | 7.0558 | 6.8537 | 4.6779 | 4.5863 | 4.4895 | 3.6989 | 2.7242 | 2.3926 | 7.4632 | 7.4147 | 7.3653 | 7.3158 | 7.2621 | 7.0558 | 6.8495 | 4.3768 | 4.3021 | 4.2242 | 3.5084 | 2.5947 | 2.2968 | 7.4495 | 7.4074 | 7.3621 | 7.3105 | 7.2568 | 7.0379 | 6.8189 | 4.2937 | 4.2011 | 4.1042 | 3.2758 | 2.2379 | 1.8937
|  | HERRIARD | HE |  |  |  | 7.4958 | 7.4758 | 7.4537 | 7.4295 | 7.4042 | 7.3368 | 7.2758 | 7.2116 | 7.1495 | 7.0842 | 5.7242 | 5.1926 | 1.9158 | 7.4937 | 7.48 | 7.4653 | 7.4432 | 7.4179 | 7.3579 | 7.3032 | 7.3179 | 7.2653 | 7.2095 | 5.7368 | 5.2105 | 4.8211 | 7.4916 | 7.4726 | 7.4526 | 7.4295 | 7.4074 | 7.3411 | 7.28 | 7.2432 | 7.1789 | 7.1126 | 5.5695 | 4.9895 | 4.5474
|  | HERRIARD | CF |  |  |  | 7.5084 | 7.4968 | 7.4842 | 7.4705 | 7.4568 | 7.4221 | 7.3916 | 7.3579 | 7.3263 | 7.2979 | 7.1442 | 6.8737 | 6.5832 | 7.5021 | 7.4947 | 7.4874 | 7.4779 | 7.4695 | 7.4411 | 7.4126 | 7.3821 | 7.3547 | 7.3274 | 7.1884 | 6.9232 | 6.6389 | 7.5042 | 7.4926 | 7.4811 | 7.4684 | 7.4558 | 7.4242 | 7.3937 | 7.3611 | 7.3295 | 7.3011 | 7.1474 | 6.8632 | 6.5505
COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE | MINIMUM HEADROOM | SU 84733 92200 | YES | 1.8211 | 35.1737 | 34.9758 | 34.7747 | 34.5621 | 34.3432 | 34.1147 | 33.8842 | 33.6832 | 33.4979 | 33.3284 | 32.4389 | 31.0779 | -5.7421 | 29.7337 | 29.4505 | 29.1242 | 28.7895 | 28.4505 | 28.1063 | 27.7842 | 27.4463 | 27.0811 | 26.7284 | 25.1274 | 23.6284 | 22.2684 | 30.9642 | 30.7589 | 30.5505 | 30.2726 | 29.9411 | 29.6032 | 29.2853 | 28.9547 | 28.5979 | 28.2568 | 26.7011 | 25.2295 | 23.8663
|  | HIGH WYCOMBE | EE |  |  |  | 35.2495 | 35.0937 | 34.9295 | 34.7547 | 34.5705 | 34.3811 | 34.1958 | 34.02 | 33.8505 | 33.6989 | 33.1505 | 32.4305 | 31.5053 | 29.8326 | 29.6263 | 29.38 | 29.1053 | 28.8232 | 28.5389 | 28.2832 | 28.0389 | 27.8 | 27.5295 | 26.26 | 25.1095 | 24.0747 | 31.0432 | 30.8811 | 30.7116 | 30.5305 | 30.3063 | 30.0263 | 29.7747 | 29.5316 | 29.2958 | 29.0305 | 27.7947 | 26.6789 | 25.6684
|  | HIGH WYCOMBE | HT |  |  |  | 35.1737 | 34.9758 | 34.7747 | 34.5621 | 34.3432 | 34.1147 | 33.8842 | 33.6832 | 33.4979 | 33.3284 | 32.4389 | 31.0779 | 29.86 | 29.7337 | 29.4505 | 29.1242 | 28.7895 | 28.4505 | 28.1063 | 27.7842 | 27.4463 | 27.0811 | 26.7284 | 25.1274 | 23.6284 | 22.2684 | 30.9642 | 30.7589 | 30.5505 | 30.2726 | 29.9411 | 29.6032 | 29.2853 | 28.9547 | 28.5979 | 28.2568 | 26.7011 | 25.2295 | 23.8663
|  | HIGH WYCOMBE | HE |  |  |  | 35.3537 | 35.2474 | 35.1295 | 34.9989 | 34.86 | 34.7084 | 34.5653 | 34.4295 | 34.3032 | 34.1937 | 33.8063 | 33.5863 | -5.7421 | 29.9368 | 29.8179 | 29.68 | 29.5137 | 29.3105 | 29.0947 | 28.9084 | 28.7316 | 28.5663 | 28.4179 | 27.6779 | 26.9253 | 26.2674 | 31.1474 | 31.0389 | 30.9189 | 30.7853 | 30.6421 | 30.4874 | 30.3411 | 30.2032 | 30.0474 | 29.8989 | 29.1758 | 28.4537 | 27.8232
|  | HIGH WYCOMBE | CF |  |  |  | 35.4158 | 35.3558 | 35.2947 | 35.2305 | 35.1642 | 35.0937 | 35.0232 | 34.9537 | 34.8863 | 34.8168 | 34.5105 | 34.3547 | 34.2674 | 30.0074 | 29.9442 | 29.88 | 29.8116 | 29.7326 | 29.6411 | 29.5495 | 29.4558 | 29.3484 | 29.2432 | 28.7768 | 28.2453 | 27.7989 | 31.2095 | 31.1495 | 31.0884 | 31.0232 | 30.9558 | 30.8832 | 30.8116 | 30.74 | 30.6695 | 30.5968 | 30.2558 | 29.7442 | 29.3168
COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE TOWN | MINIMUM HEADROOM | SU 86304 92972 | YES | 0.90316 | 65.7179 | 65.5621 | 65.3989 | 65.2242 | 65.04 | 64.8484 | 64.6632 | 64.6979 | 64.5084 | 64.3347 | 63.6158 | 62.6453 | 29.9147 | 60.0074 | 59.8337 | 59.6347 | 59.4179 | 59.1874 | 58.9305 | 58.6821 | 58.7453 | 58.4011 | 58.0716 | 56.2674 | 54.5632 | 52.9758 | 61.0284 | 60.8726 | 60.7011 | 60.5189 | 60.3274 | 60.1284 | 59.9368 | 60.0884 | 59.8874 | 59.7011 | 58.1147 | 56.4095 | 54.8232
|  | HIGH WYCOMBE TOWN | EE |  |  |  | 65.7179 | 65.5621 | 65.3989 | 65.2242 | 65.04 | 64.8484 | 64.6632 | 65.0558 | 64.8842 | 64.7305 | 64.1611 | 63.7663 | 63.0726 | 60.0074 | 59.8337 | 59.6347 | 59.4179 | 59.1874 | 58.9305 | 58.6821 | 59.3505 | 59.0895 | 58.8147 | 57.5084 | 56.2011 | 54.9958 | 61.0284 | 60.8726 | 60.7011 | 60.5189 | 60.3274 | 60.1284 | 59.9368 | 60.4684 | 60.2874 | 60.1242 | 59.3558 | 58.0484 | 56.8421
|  | HIGH WYCOMBE TOWN | HT |  |  |  | 66.2084 | 66.0084 | 65.8063 | 65.5916 | 65.3684 | 65.1379 | 64.9042 | 64.6979 | 64.5084 | 64.3347 | 63.6158 | 62.6453 | 61.2968 | 60.7316 | 60.5074 | 60.2821 | 60.0368 | 59.7242 | 59.4105 | 59.0842 | 58.7453 | 58.4011 | 58.0716 | 56.2674 | 54.5632 | 52.9758 | 61.6326 | 61.4326 | 61.2305 | 61.0158 | 60.7884 | 60.5484 | 60.3053 | 60.0884 | 59.8874 | 59.7011 | 58.1147 | 56.4095 | 54.8232
|  | HIGH WYCOMBE TOWN | HE |  |  |  | 65.8116 | 65.7 | 65.5758 | 65.4389 | 65.2916 | 65.1347 | 64.9853 | 65.4137 | 65.2821 | 65.1684 | 64.7789 | 64.5442 | 29.9147 | 60.1179 | 59.9958 | 59.8611 | 59.7137 | 59.5568 | 59.3779 | 59.2063 | 59.8958 | 59.7495 | 59.6074 | 58.8474 | 58.0958 | 57.3021 | 61.1221 | 61.0105 | 60.8863 | 60.7495 | 60.6 | 60.4389 | 60.2853 | 60.8379 | 60.7063 | 60.5926 | 60.1716 | 59.8989 | 59.1495
|  | HIGH WYCOMBE TOWN | CF |  |  |  | 65.8663 | 65.7979 | 65.7274 | 65.6537 | 65.5779 | 65.5 | 65.42 | 65.3411 | 65.2632 | 65.1853 | 64.8379 | 65.2337 | 65.1368 | 60.1789 | 60.1032 | 60.0242 | 59.9432 | 59.86 | 59.7747 | 59.6874 | 59.5905 | 59.4863 | 59.38 | 58.8063 | 59.2421 | 58.8074 | 61.1768 | 61.1084 | 61.0379 | 60.9642 | 60.8884 | 60.8105 | 60.7284 | 60.6463 | 60.5632 | 60.48 | 60.1053 | 60.6211 | 60.4989
IVER 66KV |  | HILLINGDON | MINIMUM HEADROOM | TQ 07470 82827 | YES | 0.10421 | 48.0411 | 47.3821 | 46.7168 | 46.0105 | 45.28 | 45.3863 | 44.4863 | 43 | 41.2663 | 39.6179 | 32.0737 | 25.5484 | -27.8547 | 39.0937 | 36.9368 | 35.3442 | 33.5053 | 31.4074 | 32.0526 | 30.3842 | 28.7737 | 27.0526 | 25.2158 | 16.7568 | 9.3958 | 2.5737 | 41.1421 | 39.4811 | 37.8726 | 36.0326 | 33.9347 | 34.58 | 32.9116 | 31.1253 | 29.1716 | 27.3337 | 18.8737 | 11.5105 | 4.6874
|  | HILLINGDON | EE |  |  |  | 48.2863 | 47.7674 | 47.2179 | 46.6326 | 46.0211 | 45.3863 | 44.4863 | 43.0505 | 41.6474 | 40.3495 | 37.9968 | 33.1947 | 28.8358 | 39.6716 | 37.8526 | 36.6747 | 35.3253 | 33.7632 | 32.0526 | 30.3842 | 28.7737 | 27.1979 | 25.7368 | 23.4211 | 17.9989 | 13.0411 | 41.4074 | 40.3937 | 39.2168 | 37.8537 | 36.2905 | 34.58 | 32.9116 | 31.3011 | 29.7242 | 28.2632 | 25.5389 | 20.1158 | 15.1568
|  | HILLINGDON | HT |  |  |  | 48.0411 | 47.3821 | 46.7168 | 46.0105 | 45.28 | 46.7179 | 44.7968 | 43 | 41.2663 | 39.6179 | 32.0737 | 25.5484 | 19.5358 | 39.0937 | 36.9368 | 35.3442 | 33.5053 | 31.4074 | 33.1947 | 31.0337 | 29.0053 | 27.0526 | 25.2158 | 16.7568 | 9.3958 | 2.5737 | 41.1421 | 39.4811 | 37.8726 | 36.0326 | 33.9347 | 35.3147 | 33.1537 | 31.1253 | 29.1716 | 27.3337 | 18.8737 | 11.5105 | 4.6874
|  | HILLINGDON | HE |  |  |  | 48.6263 | 48.2653 | 47.8674 | 47.4274 | 46.9537 | 46.4484 | 45.9653 | 45.5105 | 44.6179 | 43.5821 | 42.5568 | 38.9611 | -27.8547 | 40.3589 | 38.9621 | 38.1253 | 37.1116 | 35.8853 | 34.4674 | 33.0874 | 31.7642 | 30.48 | 29.3074 | 28.3947 | 24.3 | 20.6168 | 41.7726 | 41.3453 | 40.6589 | 39.66 | 38.4137 | 36.9947 | 35.6147 | 34.2916 | 33.0074 | 31.8337 | 30.5147 | 26.4179 | 22.7337
|  | HILLINGDON | CF |  |  |  | 48.8232 | 48.6147 | 48.3989 | 48.1737 | 47.9411 | 47.7011 | 47.4558 | 47.2147 | 46.9758 | 46.7368 | 45.6 | 46.5979 | 44.5821 | 40.6253 | 40.1484 | 39.6853 | 39.1568 | 38.5547 | 37.9021 | 37.2189 | 36.5253 | 35.8021 | 35.0653 | 31.5432 | 32.9221 | 30.5526 | 41.9905 | 41.7453 | 41.5147 | 41.2705 | 41.0158 | 40.4379 | 39.7705 | 39.0621 | 38.3305 | 37.5937 | 34.0695 | 35.0421 | 32.6726
LOVEDEAN GSP | WYMERING BSP | HILSEA | MINIMUM HEADROOM | SU 66394 03806 | YES | 1.2263 | 24.3095 | 24.2916 | 24.2747 | 24.2568 | 24.2368 | 24.2958 | 24.2884 | 24.2821 | 24.2747 | 24.2684 | 40.6442 | 40.4211 | 5.7074 | 22.5337 | 22.4779 | 22.4053 | 22.3326 | 22.2589 | 22.52 | 22.5042 | 22.4811 | 22.4568 | 22.4326 | 38.5295 | 38.2758 | 38.0347 | 22.9474 | 22.9263 | 22.8789 | 22.8105 | 22.7411 | 22.9337 | 22.9253 | 22.9179 | 22.9095 | 22.9021 | 39.0158 | 38.7632 | 38.5221
|  | HILSEA | EE |  |  |  | 24.3147 | 24.3 | 24.2853 | 24.2695 | 24.2526 | 41.0779 | 41.0611 | 41.0442 | 41.0284 | 41 | 40.8211 | 40.6516 | 40.4937 | 22.5389 | 22.5211 | 22.4621 | 22.4032 | 22.3432 | 39.1263 | 39.0758 | 39.0253 | 38.9779 | 38.9326 | 38.7316 | 38.5368 | 38.3568 | 22.9537 | 22.9368 | 22.92 | 22.8768 | 22.8211 | 39.6063 | 39.5579 | 39.5116 | 39.4653 | 39.4189 | 39.2179 | 39.0253 | 38.8442
|  | HILSEA | HT |  |  |  | 24.3095 | 24.2916 | 24.2747 | 24.2568 | 24.2368 | 41.06 | 41.0337 | 40.9789 | 40.9263 | 40.8758 | 40.6442 | 40.4211 | 40.2105 | 22.5337 | 22.4779 | 22.4053 | 22.3326 | 22.2589 | 39.0295 | 38.9663 | 38.9063 | 38.8474 | 38.7905 | 38.5295 | 38.2758 | 38.0347 | 22.9474 | 22.9263 | 22.8789 | 22.8105 | 22.7411 | 39.5158 | 39.4537 | 39.3926 | 39.3347 | 39.2779 | 39.0158 | 38.7632 | 38.5221
|  | HILSEA | HE |  |  |  | 24.3232 | 24.3137 | 24.3021 | 24.2895 | 24.2768 | 41.1053 | 41.0916 | 41.0789 | 41.0674 | 41.0568 | 41.0211 | 40.9811 | 5.7074 | 22.5474 | 22.5379 | 22.5263 | 22.5011 | 22.46 | 39.26 | 39.2263 | 39.1947 | 39.1642 | 39.1347 | 39.02 | 38.9126 | 38.8147 | 22.9621 | 22.9526 | 22.94 | 22.9263 | 22.9116 | 39.7326 | 39.7 | 39.6695 | 39.6411 | 39.6137 | 39.5042 | 39.3989 | 39.3011
|  | HILSEA | CF |  |  |  | 24.3284 | 24.3221 | 24.3158 | 24.3095 | 24.3032 | 24.2958 | 24.2884 | 24.2821 | 24.2747 | 24.2684 | 41.08 | 41.0632 | 41.0547 | 22.5526 | 22.5463 | 22.54 | 22.5337 | 22.5274 | 22.52 | 22.5042 | 22.4811 | 22.4568 | 22.4326 | 39.1705 | 39.0842 | 39.0084 | 22.9684 | 22.9611 | 22.9547 | 22.9484 | 22.9421 | 22.9337 | 22.9253 | 22.9179 | 22.9095 | 22.9021 | 39.6474 | 39.5663 | 39.4958
MANNINGTON GSP | ARNEWOOD | HINCHESLEA | MINIMUM HEADROOM | SU 27805 00447 | YES | 0 | 15.4874 | 15.2716 | 15.0611 | 14.8463 | 14.6305 | 14.4147 | 14.2021 | 14.0105 | 13.8316 | 13.6674 | 12.8968 | 12.1558 | 3.9358 | 15.5305 | 15.3347 | 15.0789 | 14.82 | 14.5621 | 14.3074 | 14.0568 | 13.8284 | 13.6158 | 13.4168 | 12.4432 | 11.4432 | 10.5105 | 15.8379 | 15.64 | 15.4032 | 15.1442 | 14.8863 | 14.6316 | 14.3811 | 14.1526 | 13.9389 | 13.7411 | 12.7674 | 11.7663 | 10.8337
|  | HINCHESLEA | EE |  |  |  | 15.5821 | 15.4179 | 15.2537 | 15.0832 | 14.9095 | 14.7347 | 14.5674 | 14.4084 | 14.2568 | 14.1179 | 13.5326 | 12.98 | 12.4726 | 15.5863 | 15.4821 | 15.32 | 15.1158 | 14.9095 | 14.7032 | 14.5063 | 14.3189 | 14.14 | 13.9747 | 13.2379 | 12.4811 | 11.76 | 15.8937 | 15.7895 | 15.6232 | 15.44 | 15.2326 | 15.0274 | 14.8305 | 14.6432 | 14.4632 | 14.2979 | 13.5621 | 12.8053 | 12.0832
|  | HINCHESLEA | HT |  |  |  | 15.4874 | 15.2716 | 15.0611 | 14.8463 | 14.6305 | 14.4147 | 14.2021 | 14.0105 | 13.8316 | 13.6674 | 12.8968 | 12.1558 | 11.4832 | 15.5305 | 15.3347 | 15.0789 | 14.82 | 14.5621 | 14.3074 | 14.0568 | 13.8284 | 13.6158 | 13.4168 | 12.4432 | 11.4432 | 10.5105 | 15.8379 | 15.64 | 15.4032 | 15.1442 | 14.8863 | 14.6316 | 14.3811 | 14.1526 | 13.9389 | 13.7411 | 12.7674 | 11.7663 | 10.8337
|  | HINCHESLEA | HE |  |  |  | 15.7074 | 15.6053 | 15.5011 | 15.3853 | 15.2653 | 15.14 | 15.0211 | 14.9063 | 14.8011 | 14.7084 | 14.3284 | 13.9611 | 3.9358 | 15.66 | 15.5926 | 15.5179 | 15.4347 | 15.3453 | 15.2116 | 15.0747 | 14.9432 | 14.8211 | 14.7137 | 14.2411 | 13.7253 | 13.2305 | 15.9674 | 15.9 | 15.8253 | 15.7421 | 15.6442 | 15.5116 | 15.3853 | 15.2642 | 15.1453 | 15.0379 | 14.5653 | 14.0495 | 13.5537
|  | HINCHESLEA | CF |  |  |  | 15.7768 | 15.7179 | 15.6579 | 15.5968 | 15.5337 | 15.4684 | 15.4032 | 15.3379 | 15.2747 | 15.2105 | 14.9189 | 14.6789 | 14.4537 | 15.7042 | 15.6674 | 15.6295 | 15.5905 | 15.5505 | 15.5084 | 15.4653 | 15.4232 | 15.3474 | 15.2695 | 14.9116 | 14.58 | 14.2442 | 16.0116 | 15.9747 | 15.9368 | 15.8979 | 15.8579 | 15.8158 | 15.7726 | 15.7158 | 15.6463 | 15.5768 | 15.2358 | 14.9042 | 14.5684
BRAMLEY (FLEE) | ALDERSHOT BSP | HINDHEAD | MINIMUM HEADROOM | SU 88631 36479 | YES | 0 | 25.1316 | 24.8684 | 24.6032 | 24.3116 | 24.0105 | 23.6263 | 23.2042 | 22.7926 | 22.3863 | 21.9674 | 20.0116 | 18.2389 | 0.30737 | 21.3726 | 20.8884 | 20.4516 | 19.8547 | 19.1905 | 18.4189 | 17.9421 | 17.4663 | 16.9884 | 16.5295 | 14.4032 | 12.4589 | 10.7105 | 22.1137 | 21.5874 | 21.1242 | 20.5305 | 19.8737 | 19.1189 | 18.6463 | 18.1779 | 17.7063 | 17.2547 | 15.1621 | 13.2063 | 11.4526
|  | HINDHEAD | EE |  |  |  | 25.2305 | 25.0358 | 24.82 | 24.5884 | 24.3421 | 24.0737 | 23.8232 | 23.5653 | 23.2021 | 22.8695 | 21.3305 | 19.9337 | 18.7547 | 21.5347 | 21.1432 | 20.8484 | 20.4474 | 19.9284 | 19.2979 | 18.7947 | 18.3842 | 17.9611 | 17.5726 | 15.8526 | 14.3305 | 13.0137 | 22.22 | 21.9232 | 21.5537 | 21.12 | 20.6032 | 19.9779 | 19.4832 | 19.0758 | 18.6589 | 18.2747 | 16.5737 | 15.06 | 13.7358
|  | HINDHEAD | HT |  |  |  | 25.1316 | 24.8684 | 24.6032 | 24.3116 | 24.0105 | 23.6263 | 23.2042 | 22.7926 | 22.3863 | 21.9674 | 20.0116 | 18.2389 | 16.6705 | 21.3726 | 20.8884 | 20.4516 | 19.8547 | 19.1905 | 18.4189 | 17.9421 | 17.4663 | 16.9884 | 16.5295 | 14.4032 | 12.4589 | 10.7105 | 22.1137 | 21.5874 | 21.1242 | 20.5305 | 19.8737 | 19.1189 | 18.6463 | 18.1779 | 17.7063 | 17.2547 | 15.1621 | 13.2063 | 11.4526
|  | HINDHEAD | HE |  |  |  | 25.3642 | 25.2379 | 25.0958 | 24.9347 | 24.7495 | 24.54 | 24.3505 | 24.1747 | 24.0074 | 23.8621 | 23.0558 | 22.2084 | 0.30737 | 21.7537 | 21.4684 | 21.2705 | 21.0284 | 20.72 | 20.1937 | 19.8221 | 19.5242 | 19.2211 | 18.9421 | 17.7621 | 16.7579 | 15.8758 | 22.3642 | 22.2189 | 22.0705 | 21.7947 | 21.3926 | 20.8674 | 20.4958 | 20.1979 | 19.8989 | 19.6242 | 18.4621 | 17.48 | 16.6179
|  | HINDHEAD | CF |  |  |  | 25.4421 | 25.3716 | 25.3 | 25.2232 | 25.1463 | 25.0621 | 24.9768 | 24.8916 | 24.8 | 24.7095 | 24.2884 | 24.06 | 23.6242 | 21.8758 | 21.7158 | 21.6074 | 21.4947 | 21.3811 | 21.2611 | 21.1379 | 21.0042 | 20.8537 | 20.7 | 19.6705 | 18.9484 | 18.3284 | 22.4474 | 22.3663 | 22.2905 | 22.2084 | 22.1274 | 22.0389 | 21.9495 | 21.7832 | 21.5768 | 21.3705 | 20.3432 | 19.6358 | 19.0295
MANNINGTON GSP | MANNINGTON BSP | HINTON MARTELL | MINIMUM HEADROOM | SU 00702 06030 | YES | 0.16842 | 6.5232 | 6.4558 | 6.3884 | 6.3253 | 6.2284 | 5.9768 | 5.7316 | 5.4284 | 5.3811 | 5.3368 | 4.7958 | 4.0095 | 3.1663 | 6.0537 | 5.9842 | 5.9126 | 5.8453 | 5.7421 | 5.4632 | 5.1863 | 4.8432 | 4.8 | 4.7589 | 4.2074 | 3.3463 | 3.1263 | 6.0105 | 5.9432 | 5.8768 | 5.8126 | 5.7168 | 5.4663 | 5.2105 | 4.8632 | 4.8158 | 4.7716 | 4.2 | 3.3116 | 3.0811
|  | HINTON MARTELL | EE |  |  |  | 6.5526 | 6.5011 | 6.4474 | 6.3947 | 6.3389 | 6.2768 | 6.2126 | 6.1495 | 6.0853 | 6.0242 | 5.5705 | 4.8 | 4.3316 | 6.0832 | 6.0305 | 5.9747 | 5.9211 | 5.8611 | 5.7989 | 5.7347 | 5.6737 | 5.6105 | 5.5516 | 5.0947 | 4.2958 | 3.7747 | 6.04 | 5.9884 | 5.9347 | 5.8832 | 5.8263 | 5.7653 | 5.7032 | 5.64 | 5.5768 | 5.5179 | 5.0758 | 4.2368 | 3.7021
|  | HINTON MARTELL | HT |  |  |  | 6.5232 | 6.4558 | 6.3884 | 6.3253 | 6.2284 | 5.9768 | 5.7316 | 5.4284 | 5.3811 | 5.3368 | 4.7958 | 4.0095 | 3.7958 | 6.0537 | 5.9842 | 5.9126 | 5.8453 | 5.7421 | 5.4632 | 5.1863 | 4.8432 | 4.8 | 4.7589 | 4.2074 | 3.3463 | 3.1263 | 6.0105 | 5.9432 | 5.8768 | 5.8126 | 5.7168 | 5.4663 | 5.2105 | 4.8632 | 4.8158 | 4.7716 | 4.2 | 3.3116 | 3.0811
|  | HINTON MARTELL | HE |  |  |  | 6.5916 | 6.56 | 6.5263 | 6.4937 | 6.4547 | 6.4095 | 6.3674 | 6.3284 | 6.2884 | 6.2547 | 6.0126 | 5.4547 | 3.1663 | 6.1232 | 6.0905 | 6.0568 | 6.0232 | 5.9832 | 5.9389 | 5.8968 | 5.8589 | 5.82 | 5.7853 | 5.5389 | 4.92 | 4.4895 | 6.0789 | 6.0474 | 6.0137 | 5.9811 | 5.9421 | 5.8979 | 5.8558 | 5.8179 | 5.7789 | 5.7453 | 5.5084 | 4.9105 | 4.4695
|  | HINTON MARTELL | CF |  |  |  | 6.6126 | 6.5937 | 6.5758 | 6.5568 | 6.5368 | 6.5137 | 6.4916 | 6.4674 | 6.4463 | 6.4242 | 6.32 | 6.0284 | 5.7463 | 6.1442 | 6.1253 | 6.1063 | 6.0874 | 6.0674 | 6.0453 | 6.0232 | 5.9989 | 5.9779 | 5.9547 | 5.8505 | 5.5295 | 5.2147 | 6.1 | 6.0811 | 6.0632 | 6.0442 | 6.0242 | 6.0011 | 5.98 | 5.9558 | 5.9347 | 5.9126 | 5.8116 | 5.5221 | 5.2211
BRAMLEY (FLEE) | COXMOOR WOOD BSP | HITCHES LANE | MINIMUM HEADROOM | SU 79461 54769 | YES | 0.2 | 27.3863 | 26.9737 | 26.5568 | 25.8916 | 25.0695 | 24.3505 | 23.4863 | 22.7189 | 21.9674 | 21.26 | 16.08 | 12.8284 | -27.2042 | 20.0905 | 19.0558 | 18.1074 | 17.0811 | 16.1926 | 15.4379 | 14.5053 | 13.6768 | 12.8589 | 12.0916 | 6.2484 | 2.6211 | 1.3432 | 21.5926 | 20.5653 | 19.6211 | 18.5968 | 17.7242 | 16.9726 | 16.0558 | 15.2411 | 14.4389 | 13.6842 | 7.9926 | 4.4484 | 3.1821
|  | HITCHES LANE | EE |  |  |  | 27.5484 | 27.2274 | 26.8853 | 26.5232 | 26.0589 | 25.4 | 24.7179 | 24.0853 | 23.4474 | 22.8589 | 20.4211 | 17.8295 | 15.5316 | 20.4253 | 19.5905 | 18.8021 | 17.9611 | 17.2684 | 16.5674 | 15.8326 | 15.1516 | 14.4653 | 13.8284 | 11.1811 | 8.2853 | 5.6821 | 21.9053 | 21.0989 | 20.3126 | 19.4747 | 18.7821 | 18.0874 | 17.3653 | 16.6947 | 16.0179 | 15.3916 | 12.7821 | 9.9495 | 7.4158
|  | HITCHES LANE | HT |  |  |  | 27.3863 | 26.9737 | 26.5568 | 25.8916 | 25.0695 | 24.3505 | 23.4863 | 22.7189 | 21.9674 | 21.26 | 16.08 | 12.8284 | 11.6126 | 20.0905 | 19.0558 | 18.1074 | 17.0811 | 16.1926 | 15.4379 | 14.5053 | 13.6768 | 12.8589 | 12.0916 | 6.2484 | 2.6211 | 1.3432 | 21.5926 | 20.5653 | 19.6211 | 18.5968 | 17.7242 | 16.9726 | 16.0558 | 15.2411 | 14.4389 | 13.6842 | 7.9926 | 4.4484 | 3.1821
|  | HITCHES LANE | HE |  |  |  | 27.7663 | 27.5474 | 27.3063 | 27.0389 | 26.7516 | 26.4421 | 26.1453 | 25.8189 | 25.3526 | 24.9295 | 23.3053 | 21.4842 | -27.2042 | 20.8737 | 20.28 | 19.7179 | 19.0821 | 18.5853 | 18.0716 | 17.5263 | 17.0347 | 16.5379 | 16.0821 | 14.3158 | 12.2537 | 10.4084 | 22.3253 | 21.7779 | 21.2253 | 20.5926 | 20.0958 | 19.5842 | 19.0389 | 18.5484 | 18.0526 | 17.6042 | 15.8653 | 13.8568 | 12.0653
|  | HITCHES LANE | CF |  |  |  | 27.8884 | 27.7632 | 27.6326 | 27.4979 | 27.3579 | 27.2126 | 27.0632 | 26.9168 | 26.7716 | 26.6263 | 25.7632 | 24.6116 | 23.5253 | 21.1232 | 20.7747 | 20.4684 | 20.1537 | 19.8832 | 19.6084 | 19.3053 | 19.0168 | 18.7126 | 18.4095 | 16.9558 | 15.6653 | 14.42 | 22.5589 | 22.2389 | 21.9537 | 21.6611 | 21.3905 | 21.1147 | 20.8137 | 20.5253 | 20.2221 | 19.92 | 18.4695 | 17.2053 | 15.9958
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | HOEFORD | MINIMUM HEADROOM | SU 57855 04433 | YES | 0.41158 | 19.5347 | 19.2737 | 18.9779 | 18.5011 | 18.0168 | 41.5379 | 41.0621 | 40.6232 | 40.2147 | 39.8326 | 37.7653 | 35.8189 | 11.5442 | 15.5221 | 15.0442 | 14.5516 | 14.0463 | 13.5358 | 37.0316 | 36.5337 | 36.0716 | 35.6684 | 35.26 | 32.9295 | 30.7747 | 28.7947 | 16.2358 | 15.96 | 15.6074 | 15.1126 | 14.6105 | 38.1158 | 37.6253 | 37.1716 | 36.86 | 36.4516 | 34.1011 | 31.9411 | 29.9611
|  | HOEFORD | EE |  |  |  | 20.4642 | 20.2579 | 20.0379 | 19.8032 | 19.5589 | 43.3032 | 42.9368 | 42.6874 | 41.0926 | 40.7663 | 39.2958 | 37.6368 | 36.3011 | 15.8053 | 15.4979 | 15.1789 | 14.8495 | 14.5116 | 38.0389 | 37.6789 | 37.3295 | 36.6253 | 36.2779 | 34.6947 | 32.7811 | 31.2779 | 17.3389 | 17.0684 | 16.7863 | 16.4905 | 16.1874 | 39.8747 | 39.5726 | 39.28 | 37.8158 | 37.4674 | 35.8737 | 33.9358 | 32.4316
|  | HOEFORD | HT |  |  |  | 19.5347 | 19.2737 | 18.9779 | 18.5011 | 18.0168 | 41.5379 | 41.0621 | 40.6232 | 40.2147 | 39.8326 | 37.7653 | 35.8189 | 34.0516 | 15.5221 | 15.0442 | 14.5516 | 14.0463 | 13.5358 | 37.0316 | 36.5337 | 36.0716 | 35.6684 | 35.26 | 32.9295 | 30.7747 | 28.7947 | 16.2358 | 15.96 | 15.6074 | 15.1126 | 14.6105 | 38.1158 | 37.6253 | 37.1716 | 36.86 | 36.4516 | 34.1011 | 31.9411 | 29.9611
|  | HOEFORD | HE |  |  |  | 20.6011 | 20.4589 | 20.3 | 20.1263 | 19.9379 | 43.7358 | 43.5421 | 43.3589 | 42.3126 | 42.0937 | 41.1484 | 39.9284 | 11.5442 | 16.0337 | 15.8347 | 15.6179 | 15.3884 | 15.1453 | 38.8905 | 38.6474 | 38.4126 | 37.9516 | 37.7211 | 36.7032 | 35.22 | 34.2221 | 17.5347 | 17.3558 | 17.1611 | 16.9516 | 16.7284 | 40.4916 | 40.2663 | 40.0495 | 39.1432 | 38.9116 | 37.8895 | 36.3842 | 35.3842
|  | HOEFORD | CF |  |  |  | 20.6821 | 20.6021 | 20.5179 | 20.4295 | 20.3389 | 44.2442 | 44.1474 | 44.0516 | 43.9579 | 43.8642 | 43.4442 | 43.0853 | 42.9168 | 16.1526 | 16.0347 | 15.9084 | 15.7758 | 15.6442 | 39.5032 | 39.3674 | 39.2305 | 39.0968 | 38.9621 | 38.2274 | 37.6147 | 36.5968 | 17.64 | 17.5358 | 17.4242 | 17.3084 | 17.1916 | 41.0674 | 40.9453 | 40.8232 | 40.7032 | 40.5842 | 40.0368 | 39.6316 | 39.3147
MANNINGTON GSP | LYTCHETT | HOLES BAY | MINIMUM HEADROOM | SZ 00725 91955 | YES | 0.79158 | 23.6968 | 23.6095 | 23.5211 | 23.3884 | 23.1905 | 22.9926 | 22.8042 | 22.6284 | 22.4632 | 22.3053 | 21.5937 | 20.9537 | -0.78947 | 23.2337 | 23.0663 | 22.8547 | 22.6347 | 22.4189 | 22.2042 | 21.9989 | 21.8074 | 21.6274 | 21.4558 | 20.6695 | 19.9547 | 19.2916 | 23.3653 | 23.2579 | 23.1505 | 23.0379 | 22.9232 | 22.8063 | 22.6895 | 22.5863 | 22.4916 | 22.4042 | 21.9042 | 21.4674 | 20.9242
|  | HOLES BAY | EE |  |  |  | 23.7316 | 23.6642 | 23.5926 | 23.5168 | 23.4347 | 23.2758 | 23.1284 | 22.9863 | 22.8495 | 22.72 | 22.1747 | 21.7011 | 21.2726 | 23.2726 | 23.1979 | 23.0389 | 22.8642 | 22.6874 | 22.5158 | 22.3558 | 22.2021 | 22.0526 | 21.9116 | 21.3116 | 20.7811 | 20.2968 | 23.4063 | 23.3263 | 23.24 | 23.1484 | 23.0547 | 22.9589 | 22.8684 | 22.7811 | 22.6979 | 22.6221 | 22.3211 | 22.0021 | 21.7253
|  | HOLES BAY | HT |  |  |  | 23.6968 | 23.6095 | 23.5211 | 23.3884 | 23.1905 | 22.9926 | 22.8042 | 22.6284 | 22.4632 | 22.3053 | 21.5937 | 20.9537 | 20.3642 | 23.2337 | 23.0663 | 22.8547 | 22.6347 | 22.4189 | 22.2042 | 21.9989 | 21.8074 | 21.6274 | 21.4558 | 20.6695 | 19.9547 | 19.2916 | 23.3653 | 23.2579 | 23.1505 | 23.0379 | 22.9232 | 22.8063 | 22.6895 | 22.5863 | 22.4916 | 22.4042 | 21.9042 | 21.4674 | 20.9242
|  | HOLES BAY | HE |  |  |  | 23.7779 | 23.7326 | 23.6832 | 23.6274 | 23.5684 | 23.5042 | 23.4442 | 23.3874 | 23.3337 | 23.2684 | 22.94 | 22.6716 | -0.78947 | 23.3189 | 23.2737 | 23.2221 | 23.16 | 23.04 | 22.9179 | 22.8105 | 22.7074 | 22.6095 | 22.5179 | 22.16 | 21.8589 | 21.5737 | 23.4537 | 23.4074 | 23.3537 | 23.2884 | 23.22 | 23.1463 | 23.0789 | 23.0147 | 22.9547 | 22.9011 | 22.7147 | 22.5926 | 22.5032
|  | HOLES BAY | CF |  |  |  | 23.8053 | 23.7811 | 23.7547 | 23.7284 | 23.7 | 23.6716 | 23.6421 | 23.6137 | 23.5853 | 23.5558 | 23.4084 | 23.2032 | 23.0326 | 23.3474 | 23.3221 | 23.2958 | 23.2695 | 23.2389 | 23.2063 | 23.1611 | 23.0947 | 23.0274 | 22.9611 | 22.6579 | 22.4284 | 22.2326 | 23.4811 | 23.4568 | 23.4295 | 23.4032 | 23.3705 | 23.3358 | 23.3011 | 23.2663 | 23.2316 | 23.1968 | 23.0432 | 22.9537 | 22.8947
MELKSHAM GSP | FROME BSP | HOLWELL | MINIMUM HEADROOM | ST 72191 44633 | YES | 3.12 | 14.4937 | 13.4926 | 13.4695 | 11.7053 | 11.6411 | 11.4789 | 10.8211 | 9.6463 | 9.5116 | 9.3726 | 5.0232 | 1.7632 | -0.17789 | 13.0653 | 11.9947 | 11.9032 | 10.5716 | 10.5032 | 9.9274 | 8.8758 | 7.5316 | 7.42 | 7.3063 | 2.4716 | -1.0505 | -1.8758 | 13.0389 | 12.0137 | 12 | 10.2168 | 10.1484 | 9.9811 | 8.9579 | 7.5926 | 7.4558 | 7.3147 | 2.3116 | -1.4116 | -2.9916
|  | HOLWELL | EE |  |  |  | 14.4937 | 13.6095 | 13.5368 | 11.7053 | 11.6411 | 11.4789 | 11.3137 | 11.1411 | 11.0095 | 10.8158 | 6.6032 | 1.9589 | 0.017895 | 13.0653 | 12.0526 | 11.9779 | 10.5716 | 10.5032 | 10.3611 | 10.2168 | 10.0684 | 9.9116 | 9.7516 | 5.2274 | 0.25053 | -1.8758 | 13.0389 | 12.1726 | 12.0958 | 10.2168 | 10.1484 | 9.9811 | 9.8095 | 9.6295 | 9.44 | 9.2421 | 4.4747 | -0.78 | -2.9916
|  | HOLWELL | HT |  |  |  | 14.6884 | 13.5558 | 13.4695 | 13.3832 | 12.6916 | 11.7463 | 10.8211 | 9.6463 | 9.5116 | 9.3726 | 5.0232 | 1.7632 | 0.95579 | 13.1337 | 11.9947 | 11.9032 | 11.8105 | 11.0053 | 9.9274 | 8.8758 | 7.5316 | 7.42 | 7.3063 | 2.4716 | -1.0505 | -1.8526 | 13.2537 | 12.1147 | 12.0221 | 11.9284 | 11.1242 | 10.0274 | 8.9579 | 7.5926 | 7.4558 | 7.3147 | 2.3116 | -1.4116 | -2.2937
|  | HOLWELL | HE |  |  |  | 14.5411 | 13.6821 | 13.6379 | 13.5916 | 13.5453 | 13.4442 | 13.3484 | 13.2537 | 13.1579 | 13.0632 | 10.1958 | 6.8453 | -0.17789 | 13.1053 | 12.1326 | 12.0853 | 12.0368 | 11.9884 | 11.8979 | 11.8126 | 11.7284 | 11.6453 | 11.5642 | 8.2684 | 4.4663 | 2.6695 | 13.0632 | 12.2526 | 12.2053 | 12.1558 | 12.1074 | 12.0011 | 11.9042 | 11.8042 | 11.7063 | 11.6084 | 8.2158 | 4.34 | 2.4726
|  | HOLWELL | CF |  |  |  | 14.5653 | 13.4926 | 13.4695 | 13.4453 | 13.4189 | 13.3642 | 13.3158 | 13.2621 | 13.2126 | 13.1695 | 12.6737 | 11.4832 | 10.3632 | 13.1274 | 12.0568 | 12.0368 | 12.0168 | 11.9937 | 11.9558 | 11.9211 | 11.8842 | 11.8495 | 11.8189 | 11.3211 | 9.8916 | 8.5611 | 13.0779 | 12.0137 | 12 | 11.9853 | 11.9705 | 11.9316 | 11.8958 | 11.8568 | 11.8211 | 11.7895 | 11.3726 | 9.9032 | 8.5253
MANNINGTON GSP | SALISBURY | HOMINGTON | MINIMUM HEADROOM | SU 11742 26037 | YES | 0 | 17.0905 | 17.02 | 16.9484 | 16.8726 | 16.7947 | 16.7147 | 16.6337 | 16.5632 | 16.4989 | 16.44 | 15.9463 | 15.38 | 5.4095 | 15.3789 | 15.2432 | 15.1095 | 14.9726 | 14.8358 | 14.7011 | 14.5653 | 14.3295 | 14.2653 | 14.2063 | 13.5958 | 12.9737 | 12.3684 | 15.6516 | 15.5768 | 15.5011 | 15.4 | 15.2621 | 15.1253 | 14.9884 | 14.7463 | 14.6821 | 14.6232 | 14 | 13.3642 | 12.7442
|  | HOMINGTON | EE |  |  |  | 17.1189 | 17.0642 | 17.0053 | 17.3768 | 17.2716 | 17.1674 | 17.0663 | 16.9695 | 16.8758 | 16.7895 | 16.3653 | 15.9284 | 15.4937 | 15.44 | 15.3379 | 15.2305 | 15.2716 | 15.1589 | 15.0474 | 14.94 | 14.8368 | 14.7368 | 14.6442 | 14.1789 | 13.6863 | 13.1905 | 15.6821 | 15.6242 | 15.5621 | 15.5516 | 15.4389 | 15.3284 | 15.22 | 15.1179 | 15.0179 | 14.9253 | 14.4589 | 13.9684 | 13.4726
|  | HOMINGTON | HT |  |  |  | 17.0905 | 17.02 | 16.9484 | 16.8726 | 16.7947 | 16.7147 | 16.6337 | 16.5632 | 16.4989 | 16.44 | 15.9463 | 15.38 | 14.8316 | 15.3789 | 15.2432 | 15.1095 | 14.9726 | 14.8358 | 14.7011 | 14.5653 | 14.3295 | 14.2653 | 14.2063 | 13.5958 | 12.9737 | 12.3684 | 15.6516 | 15.5768 | 15.5011 | 15.4 | 15.2621 | 15.1253 | 14.9884 | 14.7463 | 14.6821 | 14.6232 | 14 | 13.3642 | 12.7442
|  | HOMINGTON | HE |  |  |  | 17.1579 | 17.1211 | 17.0811 | 17.5621 | 17.4895 | 17.4137 | 17.3411 | 17.2747 | 17.2095 | 17.1516 | 16.8579 | 16.5379 | 5.4095 | 15.5232 | 15.46 | 15.3905 | 15.4716 | 15.3947 | 15.3147 | 15.2389 | 15.1674 | 15.0989 | 15.0368 | 14.7137 | 14.3516 | 13.9758 | 15.7242 | 15.6853 | 15.6432 | 15.7516 | 15.6758 | 15.5958 | 15.5189 | 15.4484 | 15.3789 | 15.3179 | 14.9937 | 14.6316 | 14.2568
|  | HOMINGTON | CF |  |  |  | 17.1811 | 17.1611 | 17.1411 | 17.1211 | 17.0989 | 17.0768 | 17.0537 | 17.0316 | 17.0095 | 16.9874 | 16.8874 | 16.8379 | 16.8116 | 15.5663 | 15.5295 | 15.4916 | 15.4516 | 15.4126 | 15.3653 | 15.3179 | 15.2747 | 15.2337 | 15.1916 | 14.9947 | 14.7926 | 14.5611 | 15.7484 | 15.7274 | 15.7063 | 15.6842 | 15.6611 | 15.6379 | 15.6126 | 15.5895 | 15.5663 | 15.5421 | 15.4232 | 15.2158 | 14.9779
BRAMLEY (FLEE) | COXMOOR WOOD BSP | HOOK | MINIMUM HEADROOM | SU 72602 53780 | YES | 0.53158 | 33.9842 | 33.7189 | 33.4516 | 33.1663 | 32.8747 | 32.5547 | 31.9084 | 30.4979 | 30.2305 | 29.9789 | 27.2863 | 23.8221 | 0.74211 | 29.7421 | 29.3432 | 28.9726 | 28.5368 | 28.0105 | 27.1168 | 25.7895 | 24.1832 | 23.9221 | 23.6779 | 20.7453 | 16.8716 | 15.7695 | 30.7884 | 30.5126 | 30.1695 | 29.7253 | 29.1905 | 28.3284 | 26.9958 | 25.3832 | 25.1158 | 24.8632 | 21.8832 | 17.9505 | 16.8253
|  | HOOK | EE |  |  |  | 34.0884 | 33.8832 | 33.6632 | 33.4284 | 33.1874 | 32.9189 | 32.6516 | 32.3947 | 32.1432 | 32.3968 | 30.6084 | 27.9011 | 25.8126 | 29.8768 | 29.5632 | 29.2579 | 28.9379 | 28.6116 | 28.2179 | 27.7632 | 27.32 | 26.8695 | 26.4537 | 24.5853 | 21.6105 | 19.2474 | 30.8947 | 30.6811 | 30.4547 | 30.1326 | 29.8021 | 29.3947 | 28.9305 | 28.4916 | 28.0463 | 27.6305 | 25.6905 | 22.6379 | 20.2505
|  | HOOK | HT |  |  |  | 33.9842 | 33.7189 | 33.4516 | 33.1663 | 32.8747 | 32.5547 | 31.9084 | 30.4979 | 30.2305 | 29.9789 | 27.2863 | 23.8221 | 22.7789 | 29.7421 | 29.3432 | 28.9726 | 28.5368 | 28.0105 | 27.1168 | 25.7895 | 24.1832 | 23.9221 | 23.6779 | 20.7453 | 16.8716 | 15.7695 | 30.7884 | 30.5126 | 30.1695 | 29.7253 | 29.1905 | 28.3284 | 26.9958 | 25.3832 | 25.1158 | 24.8632 | 21.8832 | 17.9505 | 16.8253
|  | HOOK | HE |  |  |  | 34.2316 | 34.0958 | 33.9442 | 33.7768 | 33.5958 | 33.3895 | 33.1937 | 33.0063 | 32.8305 | 32.6747 | 32.1053 | 30.8116 | 0.74211 | 30.02 | 29.8263 | 29.6368 | 29.4074 | 29.1653 | 28.9 | 28.6737 | 28.4568 | 28.2316 | 27.9611 | 26.7747 | 24.6379 | 22.7347 | 31.0379 | 30.8979 | 30.7432 | 30.5716 | 30.3663 | 30.0926 | 29.8611 | 29.6379 | 29.4063 | 29.1253 | 27.9379 | 25.7811 | 23.8558
|  | HOOK | CF |  |  |  | 34.3147 | 34.24 | 34.1611 | 34.0811 | 33.9979 | 33.9042 | 33.8074 | 33.7126 | 33.6189 | 33.5295 | 33.1116 | 32.8768 | 32.3032 | 30.1032 | 30.0126 | 29.9253 | 29.8379 | 29.7326 | 29.6063 | 29.4811 | 29.3558 | 29.2316 | 29.1105 | 28.3726 | 27.5432 | 26.2011 | 31.1211 | 31.0453 | 30.9653 | 30.8842 | 30.8 | 30.7042 | 30.6063 | 30.5084 | 30.4137 | 30.3042 | 29.5358 | 28.7263 | 27.3747
LALEHAM | EAST BEDFONT A | HOPE AND ANCHOR | MINIMUM HEADROOM | TQ 12710 72057 | YES | 0.14316 | 7.2284 | 7.0989 | 7.0042 | 6.9042 | 6.8 | 6.6926 | 6.5916 | 6.5032 | 6.42 | 6.34 | 5.9063 | 5.3842 | 1.0579 | 6.9232 | 6.7705 | 6.6632 | 6.5495 | 6.4305 | 6.3095 | 6.1968 | 6.0979 | 6.0042 | 5.9137 | 5.4095 | 4.78 | 4.1632 | 7.0737 | 6.9916 | 6.8863 | 6.7747 | 6.6589 | 6.54 | 6.4284 | 6.3316 | 6.24 | 6.1516 | 5.6589 | 5.0358 | 4.42
|  | HOPE AND ANCHOR | EE |  |  |  | 7.2653 | 7.1863 | 7.0947 | 7.0116 | 6.9242 | 6.8389 | 6.76 | 6.6811 | 6.6053 | 6.5358 | 6.2253 | 5.84 | 5.4674 | 6.9653 | 6.8747 | 6.7695 | 6.6758 | 6.5758 | 6.48 | 6.3916 | 6.3042 | 6.22 | 6.1421 | 5.7853 | 5.3211 | 4.8653 | 7.0905 | 7.0495 | 6.9895 | 6.8979 | 6.8 | 6.7063 | 6.6189 | 6.5337 | 6.4505 | 6.3737 | 6.0253 | 5.5747 | 5.1211
|  | HOPE AND ANCHOR | HT |  |  |  | 7.2284 | 7.0989 | 7.0042 | 6.9042 | 6.8 | 6.6926 | 6.5916 | 6.5032 | 6.42 | 6.34 | 5.9063 | 5.3842 | 4.8789 | 6.9232 | 6.7705 | 6.6632 | 6.5495 | 6.4305 | 6.3095 | 6.1968 | 6.0979 | 6.0042 | 5.9137 | 5.4095 | 4.78 | 4.1632 | 7.0737 | 6.9916 | 6.8863 | 6.7747 | 6.6589 | 6.54 | 6.4284 | 6.3316 | 6.24 | 6.1516 | 5.6589 | 5.0358 | 4.42
|  | HOPE AND ANCHOR | HE |  |  |  | 7.3126 | 7.2537 | 7.1832 | 7.1189 | 7.0505 | 6.9811 | 6.92 | 6.8621 | 6.8053 | 6.7547 | 6.5463 | 6.26 | 1.0579 | 6.9968 | 6.9526 | 6.8716 | 6.8 | 6.7232 | 6.6453 | 6.5779 | 6.5137 | 6.4516 | 6.3947 | 6.1568 | 5.8074 | 5.4642 | 7.1116 | 7.0821 | 7.0474 | 7.0084 | 6.9442 | 6.8674 | 6.8011 | 6.7379 | 6.6768 | 6.6211 | 6.3874 | 6.0495 | 5.7179
|  | HOPE AND ANCHOR | CF |  |  |  | 7.3611 | 7.3295 | 7.2926 | 7.2474 | 7.2011 | 7.1495 | 7.0958 | 7.0568 | 7.0063 | 6.9526 | 6.6905 | 6.5116 | 6.3337 | 7.0126 | 6.9926 | 6.9726 | 6.9484 | 6.8947 | 6.8358 | 6.7726 | 6.7284 | 6.6705 | 6.6074 | 6.2979 | 6.0821 | 5.8611 | 7.1253 | 7.1063 | 7.0874 | 7.0663 | 7.0453 | 7.0221 | 6.9926 | 6.9495 | 6.8916 | 6.8305 | 6.5295 | 6.32 | 6.1063
LOVEDEAN GSP | HAVANT | HORNDEAN | MINIMUM HEADROOM | SU 70271 12802 | YES | 0.52105 | 34.2168 | 32.9642 | 31.3547 | 29.6421 | 27.7347 | 25.8232 | 54.0768 | 52.4905 | 50.9284 | 49.5095 | 43.9684 | 39.1495 | 13.6474 | 28.0905 | 26.6547 | 24.8147 | 22.8832 | 20.7568 | 18.6337 | 46.7063 | 44.9537 | 43.2179 | 41.6453 | 35.5242 | 30.1642 | 24.5705 | 29.1232 | 27.7474 | 25.9979 | 24.1095 | 21.9821 | 19.8568 | 47.9274 | 46.1705 | 44.4337 | 42.8558 | 36.7158 | 31.3326 | 25.7284
|  | HORNDEAN | EE |  |  |  | 34.68 | 33.6705 | 32.2989 | 30.8253 | 29.2179 | 27.5979 | 56.1221 | 54.7526 | 53.4137 | 52.2221 | 47.9095 | 44.2105 | 40.3621 | 28.6168 | 27.4526 | 25.8516 | 24.1842 | 22.3716 | 20.5695 | 48.9368 | 47.4242 | 45.9432 | 44.6284 | 39.8874 | 35.7789 | 31.4126 | 29.6042 | 28.5147 | 26.9947 | 25.4095 | 23.5968 | 21.7937 | 50.1579 | 48.6411 | 47.1558 | 45.8358 | 41.0663 | 36.9284 | 32.5505
|  | HORNDEAN | HT |  |  |  | 34.2168 | 32.9642 | 31.3547 | 29.6421 | 27.7347 | 25.8232 | 54.0768 | 52.4905 | 50.9284 | 49.5095 | 43.9684 | 39.1495 | 34.1979 | 28.0905 | 26.6547 | 24.8147 | 22.8832 | 20.7568 | 18.6337 | 46.7063 | 44.9537 | 43.2179 | 41.6453 | 35.5242 | 30.1642 | 24.5705 | 29.1232 | 27.7474 | 25.9979 | 24.1095 | 21.9821 | 19.8568 | 47.9274 | 46.1705 | 44.4337 | 42.8558 | 36.7158 | 31.3326 | 25.7284
|  | HORNDEAN | HE |  |  |  | 35.3 | 34.5853 | 33.5126 | 32.3484 | 31.0147 | 29.6611 | 58.4337 | 57.3147 | 56.2242 | 55.2705 | 52.1284 | 49.5505 | 13.6474 | 29.3211 | 28.4926 | 27.2126 | 25.8611 | 24.3379 | 22.8126 | 51.4463 | 50.2032 | 48.9895 | 47.9284 | 44.4442 | 41.5379 | 38.2389 | 30.2189 | 29.5116 | 28.3021 | 27.0211 | 25.5653 | 24.0368 | 52.6695 | 51.4253 | 50.2084 | 49.1453 | 45.6495 | 42.7347 | 39.4263
|  | HORNDEAN | CF |  |  |  | 35.6442 | 35.3368 | 34.9284 | 34.4895 | 33.9842 | 33.4284 | 62.74 | 61.9 | 61.04 | 59.9895 | 57.9358 | 56.2126 | 54.3674 | 29.7611 | 29.3632 | 28.8905 | 28.38 | 27.7853 | 27.1295 | 56.3158 | 55.3484 | 54.3526 | 53.1411 | 50.8884 | 48.9484 | 46.8326 | 30.5989 | 30.2547 | 29.8505 | 29.4063 | 28.8421 | 28.2189 | 57.4484 | 56.5347 | 55.5758 | 54.3632 | 52.1063 | 50.1621 | 48.04
NURSLING GSP | WINCHESTER | HOUGHTON | MINIMUM HEADROOM | SU 33784 31741 | YES | 0.16842 | 16.4589 | 16.2895 | 16.1221 | 15.9453 | 15.0642 | 13.7411 | 12.4463 | 10.8126 | 10.6389 | 10.4663 | 7.9989 | 3.6947 | -15.9211 | 15.0747 | 14.8926 | 14.7147 | 14.5263 | 13.5126 | 12.0042 | 10.5326 | 8.6632 | 8.5095 | 8.3589 | 5.8316 | 1.0453 | -0.029474 | 14.7421 | 14.6484 | 14.62 | 14.6642 | 13.9674 | 12.4432 | 10.9526 | 9.0642 | 8.8905 | 8.7168 | 5.9779 | 1.0863 | -0.054737
|  | HOUGHTON | EE |  |  |  | 16.5326 | 16.4042 | 16.2653 | 16.1168 | 15.9716 | 15.7674 | 15.5379 | 15.3021 | 15.06 | 14.8179 | 11.7916 | 7.8684 | 5.2842 | 15.1495 | 15.0179 | 14.8726 | 14.7147 | 14.5642 | 14.3663 | 14.1495 | 13.9305 | 13.7074 | 13.4884 | 10.3316 | 6.1579 | 3.2737 | 14.7779 | 14.7042 | 14.62 | 15.1695 | 15.0158 | 14.8032 | 14.5632 | 14.3189 | 14.0684 | 13.8179 | 10.4547 | 6.0453 | 3.0863
|  | HOUGHTON | HT |  |  |  | 16.4589 | 16.2895 | 16.1221 | 15.9453 | 15.0642 | 13.7411 | 12.4463 | 10.8126 | 10.6389 | 10.4663 | 7.9989 | 3.6947 | 2.6537 | 15.0747 | 14.8926 | 14.7147 | 14.5263 | 13.5126 | 12.0042 | 10.5326 | 8.6632 | 8.5095 | 8.3589 | 5.8316 | 1.0453 | -0.029474 | 14.7421 | 14.6484 | 15.1716 | 14.9821 | 13.9674 | 12.4432 | 10.9526 | 9.0642 | 8.8905 | 8.7168 | 5.9779 | 1.0863 | -0.054737
|  | HOUGHTON | HE |  |  |  | 16.6368 | 16.5558 | 16.4705 | 16.3747 | 16.2811 | 16.1284 | 15.9853 | 15.8442 | 15.7053 | 15.5737 | 13.9811 | 11.5137 | -15.9211 | 15.2537 | 15.1726 | 15.0863 | 14.9905 | 14.8926 | 14.7463 | 14.6095 | 14.4758 | 14.3442 | 14.2211 | 12.5253 | 9.7589 | 7.3305 | 14.8295 | 14.78 | 14.7253 | 14.6642 | 15.3495 | 15.1916 | 15.0432 | 14.8968 | 14.7526 | 14.6168 | 12.8358 | 10.0032 | 7.5126
|  | HOUGHTON | CF |  |  |  | 16.6884 | 16.64 | 16.5905 | 16.5337 | 16.4758 | 16.3874 | 16.3042 | 16.2232 | 16.1495 | 16.08 | 15.4737 | 13.7442 | 12.1442 | 15.3063 | 15.2579 | 15.2074 | 15.1505 | 15.0958 | 15.0074 | 14.9253 | 14.8463 | 14.7737 | 14.7053 | 14.0663 | 12.1105 | 10.3084 | 14.8589 | 14.8326 | 14.8042 | 14.7737 | 15.5537 | 15.4589 | 15.3716 | 15.2863 | 15.2084 | 15.1347 | 14.4684 | 12.4758 | 10.6326
BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | HOUNDMILLS | MINIMUM HEADROOM | SU 62187 52886 | YES | 2.2747 | 44.0537 | 43.9063 | 43.7579 | 43.5979 | 42.9063 | 41.2305 | 39.4663 | 37.6811 | 35.9095 | 34.1537 | 26.86 | 25.5863 | 0.75895 | 39.4579 | 39.28 | 38.3979 | 36.6337 | 34.8737 | 32.8484 | 30.7842 | 28.7253 | 26.68 | 24.6526 | 16.2726 | 14.9716 | 13.6516 | 40.5137 | 40.3526 | 39.8705 | 38.1221 | 36.3337 | 34.2663 | 32.1811 | 30.1168 | 28.0663 | 26.0316 | 17.5979 | 16.22 | 14.8695
|  | HOUNDMILLS | EE |  |  |  | 44.1063 | 43.9884 | 43.8632 | 44.8789 | 43.3789 | 41.6347 | 39.8853 | 38.1337 | 36.3779 | 34.6347 | 27.4284 | 26.3474 | 25.3726 | 39.52 | 39.3758 | 38.6389 | 37.0168 | 35.2779 | 33.2632 | 31.2484 | 29.2284 | 27.2063 | 25.1979 | 16.9474 | 15.9053 | 14.8537 | 40.5705 | 40.4411 | 40.1032 | 38.4179 | 36.6811 | 34.6621 | 32.6389 | 30.6116 | 28.5811 | 26.5621 | 18.2305 | 17.0811 | 15.9937
|  | HOUNDMILLS | HT |  |  |  | 44.0537 | 43.9063 | 43.7579 | 43.5979 | 42.9063 | 41.2305 | 39.4663 | 37.6811 | 35.9095 | 34.1537 | 26.86 | 25.5863 | 24.3747 | 39.4579 | 39.28 | 38.3979 | 36.6337 | 34.8737 | 32.8484 | 30.7842 | 28.7253 | 26.68 | 24.6526 | 16.2726 | 14.9716 | 13.6516 | 40.5137 | 40.3526 | 39.8705 | 38.1221 | 36.3337 | 34.2663 | 32.1811 | 30.1168 | 28.0663 | 26.0316 | 17.5979 | 16.22 | 14.8695
|  | HOUNDMILLS | HE |  |  |  | 44.1832 | 44.1021 | 44.0126 | 45.26 | 43.8295 | 42.1526 | 40.4853 | 38.82 | 37.1579 | 35.5084 | 28.8074 | 28.3558 | 0.75895 | 39.6074 | 39.5084 | 38.9716 | 37.4305 | 35.7653 | 33.8211 | 31.8874 | 29.9558 | 28.0263 | 26.1105 | 18.34 | 17.8884 | 17.2768 | 40.6516 | 40.5621 | 40.4274 | 38.8326 | 37.1705 | 35.2253 | 33.2895 | 31.3558 | 29.4232 | 27.5053 | 19.7084 | 19.2263 | 18.5895
|  | HOUNDMILLS | CF |  |  |  | 44.2284 | 44.1811 | 44.1337 | 44.0832 | 44.0316 | 43.9684 | 43.9053 | 43.8421 | 43.2853 | 42.1832 | 36.5821 | 36.2221 | 35.8916 | 39.6526 | 39.6053 | 39.5432 | 39.4621 | 39.2168 | 38.6032 | 37.7032 | 36.5274 | 35.2705 | 33.9189 | 27.3305 | 26.9558 | 26.6095 | 40.6968 | 40.6495 | 40.5958 | 40.5316 | 40.46 | 40.0737 | 39.2 | 38 | 36.7189 | 35.3442 | 28.7253 | 28.3337 | 27.9695
BRAMLEY (ANDO-THAT) | THATCHAM BSP | HUNGERFORD | MINIMUM HEADROOM | SU 34066 68957 | YES | 0.48526 | 16.8032 | 16.6832 | 16.5632 | 16.4358 | 16.3042 | 16.1674 | 16.0305 | 15.9105 | 15.8 | 15.7 | 15.2021 | 14.4421 | 1.8063 | 14.86 | 14.6263 | 14.3968 | 14.1642 | 13.9316 | 13.6989 | 13.4705 | 13.2611 | 13.0642 | 12.8811 | 12.0653 | 11.2274 | 10.44 | 15.2084 | 15.0884 | 14.9684 | 14.7705 | 14.5621 | 14.3389 | 14.1095 | 13.9 | 13.7042 | 13.5211 | 12.7042 | 11.8663 | 11.0789
|  | HUNGERFORD | EE |  |  |  | 16.8463 | 16.7516 | 16.6516 | 16.5453 | 16.4347 | 16.3179 | 16.2074 | 16.1021 | 16.0011 | 15.9105 | 15.5811 | 15.2316 | 14.6874 | 14.9211 | 14.78 | 14.5958 | 14.4084 | 14.2189 | 14.0274 | 13.8432 | 13.6674 | 13.4989 | 13.3421 | 12.7179 | 12.0884 | 11.4779 | 15.2516 | 15.1568 | 15.0568 | 14.9505 | 14.8126 | 14.6389 | 14.4716 | 14.3074 | 14.1389 | 13.9821 | 13.3579 | 12.7274 | 12.1168
|  | HUNGERFORD | HT |  |  |  | 16.8032 | 16.6832 | 16.5632 | 16.4358 | 16.3042 | 16.1674 | 16.0305 | 15.9105 | 15.8 | 15.7 | 15.2021 | 14.4421 | 13.7358 | 14.86 | 14.6263 | 14.3968 | 14.1642 | 13.9316 | 13.6989 | 13.4705 | 13.2611 | 13.0642 | 12.8811 | 12.0653 | 11.2274 | 10.44 | 15.2084 | 15.0884 | 14.9684 | 14.7705 | 14.5621 | 14.3389 | 14.1095 | 13.9 | 13.7042 | 13.5211 | 12.7042 | 11.8663 | 11.0789
|  | HUNGERFORD | HE |  |  |  | 16.9095 | 16.8442 | 16.7726 | 16.6926 | 16.6074 | 16.5168 | 16.4305 | 16.3484 | 16.2716 | 16.2053 | 15.9832 | 15.8537 | 1.8063 | 14.9863 | 14.9211 | 14.8474 | 14.74 | 14.6074 | 14.4705 | 14.3411 | 14.2168 | 14.1011 | 13.9958 | 13.6253 | 13.2337 | 12.8484 | 15.3147 | 15.2495 | 15.1779 | 15.0979 | 15.0126 | 14.9221 | 14.8358 | 14.7537 | 14.6768 | 14.5884 | 14.2526 | 13.8737 | 13.4884
|  | HUNGERFORD | CF |  |  |  | 16.9463 | 16.9084 | 16.8705 | 16.8305 | 16.7884 | 16.7474 | 16.7032 | 16.66 | 16.6179 | 16.5747 | 16.3863 | 16.2926 | 16.24 | 15.0232 | 14.9853 | 14.9474 | 14.9063 | 14.8621 | 14.8 | 14.72 | 14.6453 | 14.5705 | 14.4958 | 14.1495 | 13.8589 | 13.5884 | 15.3516 | 15.3137 | 15.2758 | 15.2358 | 15.1937 | 15.1526 | 15.1084 | 15.0653 | 15.0232 | 14.98 | 14.7484 | 14.4989 | 14.2284
LOVEDEAN GSP | CHICHESTER & HUNSTON | HUNSTON | MINIMUM HEADROOM | SU 86949 02632 | YES | 2.4516 | 31.8263 | 31.6737 | 31.52 | 31.3568 | 31.1884 | 31.4063 | 30.9895 | 29.3411 | 29.2011 | 29.0716 | 25.6368 | 25.14 | 3.2937 | 27.4947 | 27.3421 | 27.1884 | 27.0253 | 26.8168 | 26.3211 | 25.8611 | 23.94 | 23.8 | 23.6705 | 19.7053 | 19.1895 | 18.2516 | 28.3579 | 28.2053 | 28.0516 | 27.8884 | 27.6832 | 27.4368 | 26.9768 | 25.0589 | 24.9189 | 24.7895 | 20.8305 | 20.3158 | 19.3789
|  | HUNSTON | EE |  |  |  | 31.8821 | 31.7611 | 33.1021 | 32.9663 | 32.8242 | 32.6768 | 32.5347 | 32.4 | 32.2695 | 32.1537 | 31.7305 | 27.2705 | 26.0168 | 27.5505 | 27.4295 | 27.3411 | 27.2053 | 27.1737 | 26.8674 | 26.4916 | 26.1274 | 25.7347 | 25.3137 | 23.2853 | 21.7358 | 20.3158 | 28.4137 | 28.2926 | 29.5411 | 29.4053 | 29.2632 | 29.0989 | 28.8747 | 28.66 | 28.4389 | 28.2168 | 24.3137 | 22.7432 | 21.3021
|  | HUNSTON | HT |  |  |  | 31.8263 | 31.6737 | 31.52 | 31.3568 | 31.1884 | 31.4063 | 30.9895 | 29.3411 | 29.2011 | 29.0716 | 25.6368 | 25.14 | 24.2979 | 27.4947 | 27.3421 | 27.1884 | 27.0253 | 26.8168 | 26.3211 | 25.8611 | 23.94 | 23.8 | 23.6705 | 19.7053 | 19.1895 | 18.2516 | 28.3579 | 28.2053 | 28.0516 | 27.8884 | 27.6832 | 27.4368 | 26.9768 | 25.0589 | 24.9189 | 24.7895 | 20.8305 | 20.3158 | 19.3789
|  | HUNSTON | HE |  |  |  | 31.9611 | 31.8779 | 33.2537 | 33.1516 | 33.0421 | 32.1547 | 32.0432 | 31.8242 | 31.5316 | 31.2137 | 29.7021 | 28.6063 | 3.2937 | 27.6295 | 27.5463 | 27.4926 | 27.3905 | 27.2811 | 27.1253 | 27.0137 | 26.7747 | 26.4453 | 26.0863 | 24.3516 | 23.0853 | 21.9379 | 28.4926 | 28.4095 | 29.6926 | 29.5905 | 29.4811 | 28.24 | 28.1284 | 27.8895 | 27.5611 | 27.2021 | 25.4695 | 24.2063 | 23.06
|  | HUNSTON | CF |  |  |  | 32.0074 | 31.96 | 33.3789 | 33.3263 | 33.2737 | 33.2179 | 33.1621 | 33.1063 | 33.0516 | 32.9968 | 32.7526 | 32.6305 | 32.5632 | 27.6758 | 27.6284 | 27.6179 | 27.5653 | 27.5126 | 27.4568 | 27.4011 | 27.3453 | 27.2905 | 27.2358 | 26.5432 | 25.7558 | 25.0632 | 28.5389 | 28.4916 | 29.8179 | 29.7653 | 29.7126 | 29.6568 | 29.6011 | 29.5453 | 29.4905 | 29.4358 | 29.0347 | 28.6821 | 25.9863
MELKSHAM GSP | ANDOVER BSP | HURSTBOURNE TARRANT | MINIMUM HEADROOM | SU 39384 52476 | YES | 0.63158 | 5.6232 | 5.5484 | 5.4737 | 3.7895 | 3.6842 | 3.5768 | 3.4737 | 3.3695 | 3.2642 | 3.1674 | 2.7737 | 2.3747 | -1.8905 | 4.5747 | 4.4621 | 4.3232 | 2.9484 | 2.8368 | 2.7232 | 2.6147 | 2.5053 | 2.3947 | 2.2895 | 1.8726 | 1.4168 | 0.96526 | 4.5842 | 4.4411 | 4.3032 | 2.5011 | 2.3895 | 2.2758 | 2.1663 | 2.0547 | 1.9432 | 1.8379 | 1.4137 | 0.94842 | 0.49368
|  | HURSTBOURNE TARRANT | EE |  |  |  | 5.6526 | 5.5947 | 5.5347 | 3.7895 | 3.6842 | 3.5768 | 3.4737 | 3.3695 | 3.2642 | 3.1674 | 2.7737 | 2.3747 | 1.9726 | 4.6158 | 4.5421 | 4.4505 | 2.9484 | 2.8368 | 2.7232 | 2.6147 | 2.5053 | 2.3947 | 2.2895 | 1.8726 | 1.4168 | 0.96526 | 4.6484 | 4.54 | 4.4295 | 2.5011 | 2.3895 | 2.2758 | 2.1663 | 2.0547 | 1.9432 | 1.8379 | 1.4137 | 0.94842 | 0.49368
|  | HURSTBOURNE TARRANT | HT |  |  |  | 5.6232 | 5.5484 | 5.4737 | 5.3947 | 5.2768 | 5.1421 | 5.0021 | 4.8747 | 4.7558 | 4.6442 | 4.1589 | 3.6274 | 3.1274 | 4.5747 | 4.4621 | 4.3232 | 4.1789 | 4.0379 | 3.8947 | 3.7442 | 3.6084 | 3.48 | 3.3589 | 2.8358 | 2.2516 | 1.6916 | 4.5842 | 4.4411 | 4.3032 | 4.1579 | 4.0179 | 3.8737 | 3.7232 | 3.5853 | 3.4568 | 3.3347 | 2.8053 | 2.2147 | 1.6526
|  | HURSTBOURNE TARRANT | HE |  |  |  | 5.6937 | 5.6547 | 5.6137 | 5.5674 | 5.5179 | 5.4632 | 5.4105 | 5.3621 | 5.3147 | 5.2758 | 5.0895 | 4.8358 | -1.8905 | 4.6695 | 4.6232 | 4.5737 | 4.5179 | 4.46 | 4.3916 | 4.3168 | 4.2411 | 4.1632 | 4.0979 | 3.8558 | 3.5684 | 3.2653 | 4.7295 | 4.6695 | 4.6 | 4.5242 | 4.4495 | 4.3695 | 4.2958 | 4.2189 | 4.14 | 4.0758 | 3.8305 | 3.54 | 3.2358
|  | HURSTBOURNE TARRANT | CF |  |  |  | 5.7168 | 5.6968 | 5.6768 | 5.6547 | 5.6316 | 5.6074 | 5.5832 | 5.5589 | 5.5347 | 5.5105 | 5.4042 | 5.2389 | 5.0789 | 4.6926 | 4.6726 | 4.6495 | 4.62 | 4.5895 | 4.5568 | 4.5232 | 4.48 | 4.4368 | 4.3947 | 4.1853 | 3.9905 | 3.8053 | 4.7526 | 4.7326 | 4.7032 | 4.66 | 4.6105 | 4.5579 | 4.5032 | 4.4579 | 4.4158 | 4.3737 | 4.1621 | 3.9653 | 3.78
EALING GSP |  | IRONBRIDGE | MINIMUM HEADROOM | TQ 14226 80171 | NO | 0.061053 | 29.8832 | 29.5295 | 29.1737 | 28.7958 | 28.3979 | 28.4432 | 27.5474 | 26.5021 | 25.2895 | 24.1063 | 20.4863 | 17.5368 | -28.4221 | 22.4516 | 21.7674 | 20.3589 | 17.9821 | 15.7211 | 16.0684 | 14.4358 | 13.2642 | 11.8916 | 10.5495 | 6.8189 | 3.5347 | 0.34737 | 23.6726 | 23.2853 | 22.5179 | 20.1463 | 17.8884 | 18.2347 | 16.6042 | 15.4337 | 14.0642 | 12.7242 | 8.6263 | 5.3421 | 2.1537
|  | IRONBRIDGE | EE |  |  |  | 30.0137 | 29.7337 | 29.4389 | 29.1242 | 28.7916 | 28.4432 | 27.5474 | 26.5021 | 25.2895 | 24.1063 | 23.16 | 21.0905 | 19.1305 | 22.5926 | 22.2937 | 21.4663 | 19.7011 | 18.0147 | 16.0684 | 14.4358 | 13.2642 | 11.8916 | 10.5495 | 9.8021 | 7.5042 | 5.3032 | 23.8137 | 23.5137 | 23.1821 | 21.8611 | 20.1779 | 18.2347 | 16.6042 | 15.4337 | 14.0642 | 12.7242 | 11.6105 | 9.3116 | 7.1095
|  | IRONBRIDGE | HT |  |  |  | 29.8832 | 29.5295 | 29.1737 | 28.7958 | 28.3979 | 29.6611 | 27.9389 | 26.7011 | 25.52 | 24.3705 | 20.4863 | 17.5368 | 14.6989 | 22.4516 | 21.7674 | 20.3589 | 17.9821 | 15.7211 | 17.1084 | 15.1589 | 13.7716 | 12.4432 | 11.1495 | 6.8189 | 3.5347 | 0.34737 | 23.6726 | 23.2853 | 22.5179 | 20.1463 | 17.8884 | 18.9189 | 16.9684 | 15.58 | 14.2526 | 12.9579 | 8.6263 | 5.3421 | 2.1537
|  | IRONBRIDGE | HE |  |  |  | 30.1684 | 29.9589 | 29.7263 | 29.4695 | 29.1937 | 28.9011 | 28.62 | 27.7747 | 26.7063 | 25.7021 | 25.5926 | 24.2537 | -28.4221 | 22.7611 | 22.5379 | 22.18 | 20.5589 | 19.0095 | 17.1989 | 15.7126 | 14.6589 | 13.4453 | 12.3011 | 12.4758 | 10.9832 | 9.5832 | 23.9821 | 23.7589 | 23.4947 | 22.7189 | 21.1716 | 19.3642 | 17.88 | 16.8284 | 15.6158 | 14.4737 | 14.2842 | 12.7916 | 11.3905
|  | IRONBRIDGE | CF |  |  |  | 30.2589 | 30.1263 | 29.9884 | 29.8453 | 29.6968 | 29.5432 | 29.3874 | 29.2337 | 29.0811 | 28.9284 | 27.3189 | 29.14 | 28.3463 | 22.8653 | 22.7263 | 22.5811 | 22.4126 | 22.1989 | 21.74 | 21.2516 | 20.8253 | 20.2621 | 19.62 | 14.1411 | 16.5105 | 15.6116 | 24.0874 | 23.9474 | 23.8021 | 23.6326 | 23.4684 | 23.2968 | 23.1211 | 22.9516 | 22.4221 | 21.78 | 16.3105 | 18.3211 | 17.4211
BRAMLEY (BASI) | BASINGSTOKE T1A & T2A | JAYS CLOSE | MINIMUM HEADROOM | SU 63055 50105 | YES | 0.66526 | 46.1379 | 45.8768 | 45.6126 | 45.3305 | 45.04 | 44.7158 | 44.3895 | 44.0958 | 43.8221 | 43.4726 | 41.6179 | 39.7853 | 6.94 | 41.0905 | 40.8295 | 40.5653 | 40.1516 | 39.6379 | 39.1021 | 38.5474 | 38.0337 | 37.5442 | 37.0905 | 35.0368 | 32.9568 | 30.7895 | 42.8063 | 42.5305 | 42.2516 | 41.9558 | 41.5095 | 40.9611 | 40.3937 | 39.8653 | 39.3621 | 38.8926 | 36.7484 | 34.56 | 32.3326
|  | JAYS CLOSE | EE |  |  |  | 46.2337 | 46.0274 | 45.8063 | 45.5716 | 45.3242 | 45.0463 | 44.7684 | 44.4989 | 44.2337 | 43.9884 | 42.6611 | 41.1958 | 39.8116 | 41.1863 | 40.98 | 40.76 | 40.5253 | 40.2611 | 39.8147 | 39.3811 | 38.9442 | 38.5053 | 38.0916 | 36.3505 | 34.7884 | 33.0895 | 42.9053 | 42.6916 | 42.46 | 42.2147 | 41.9579 | 41.6716 | 41.2316 | 40.7779 | 40.3221 | 39.8895 | 38.0295 | 36.3337 | 34.5758
|  | JAYS CLOSE | HT |  |  |  | 46.1379 | 45.8768 | 45.6126 | 45.3305 | 45.04 | 44.7158 | 44.3895 | 44.0958 | 43.8221 | 43.4726 | 41.6179 | 39.7853 | 38.0221 | 41.0905 | 40.8295 | 40.5653 | 40.1516 | 39.6379 | 39.1021 | 38.5474 | 38.0337 | 37.5442 | 37.0905 | 35.0368 | 32.9568 | 30.7895 | 42.8063 | 42.5305 | 42.2516 | 41.9558 | 41.5095 | 40.9611 | 40.3937 | 39.8653 | 39.3621 | 38.8926 | 36.7484 | 34.56 | 32.3326
|  | JAYS CLOSE | HE |  |  |  | 46.3674 | 46.2232 | 46.0632 | 45.8863 | 45.6968 | 45.4758 | 45.2663 | 45.0663 | 44.8768 | 44.7105 | 44.0884 | 43.6958 | 6.94 | 41.32 | 41.1758 | 41.0158 | 40.84 | 40.6505 | 40.4358 | 40.2326 | 40.0389 | 39.8568 | 39.6021 | 38.5621 | 37.8274 | 36.8674 | 43.0389 | 42.8947 | 42.7347 | 42.5526 | 42.3568 | 42.1316 | 41.9158 | 41.7105 | 41.5168 | 41.3463 | 40.3568 | 39.5811 | 38.5779
|  | JAYS CLOSE | CF |  |  |  | 46.4453 | 46.3611 | 46.2737 | 46.1832 | 46.0895 | 45.9832 | 45.8758 | 45.7705 | 45.6663 | 45.5632 | 45.0926 | 44.8253 | 44.6463 | 41.3979 | 41.3137 | 41.2263 | 41.1358 | 41.0421 | 40.9389 | 40.8347 | 40.7326 | 40.6326 | 40.5316 | 39.88 | 39.2758 | 38.7158 | 43.1168 | 43.0326 | 42.9453 | 42.8547 | 42.76 | 42.6505 | 42.5379 | 42.4295 | 42.3211 | 42.2137 | 41.7221 | 41.0979 | 40.5116
MINETY GSP | CIRENCESTER BSP | KEMBLE RAF | MINIMUM HEADROOM | ST 96064 96012 | YES | 0.36421 | 9.7463 | 9.7274 | 9.7084 | 9.6895 | 9.6705 | 9.6505 | 9.6316 | 9.6116 | 9.5895 | 9.5684 | 9.46 | 9.3453 | 7.0716 | 9.3526 | 9.3347 | 9.3137 | 9.2916 | 9.2695 | 9.2474 | 9.2263 | 9.2042 | 9.1811 | 9.1589 | 9.0442 | 8.9263 | 8.8263 | 9.3453 | 9.3463 | 9.3832 | 9.3611 | 9.3389 | 9.3158 | 9.2937 | 9.2716 | 9.2463 | 9.2232 | 9.1011 | 8.9726 | 8.8695
|  | KEMBLE RAF | EE |  |  |  | 9.7526 | 9.74 | 9.7253 | 9.7105 | 9.6968 | 9.68 | 9.6632 | 9.6453 | 9.6263 | 9.6074 | 9.5032 | 9.3958 | 9.3232 | 9.3526 | 9.3505 | 9.3326 | 9.3158 | 9.3 | 9.2821 | 9.2653 | 9.2463 | 9.2263 | 9.2074 | 9.1042 | 8.9979 | 8.9211 | 9.3453 | 9.4189 | 9.4021 | 9.3853 | 9.3695 | 9.3495 | 9.3305 | 9.3105 | 9.2895 | 9.2695 | 9.1558 | 9.0368 | 8.9558
|  | KEMBLE RAF | HT |  |  |  | 9.7463 | 9.7274 | 9.7084 | 9.6895 | 9.6705 | 9.6505 | 9.6316 | 9.6116 | 9.5895 | 9.5684 | 9.46 | 9.3453 | 9.2558 | 9.3568 | 9.3347 | 9.3137 | 9.2916 | 9.2695 | 9.2474 | 9.2263 | 9.2042 | 9.1811 | 9.1589 | 9.0442 | 8.9263 | 8.8263 | 9.4263 | 9.4042 | 9.3832 | 9.3611 | 9.3389 | 9.3158 | 9.2937 | 9.2716 | 9.2463 | 9.2232 | 9.1011 | 8.9726 | 8.8695
|  | KEMBLE RAF | HE |  |  |  | 9.7537 | 9.7526 | 9.7495 | 9.7421 | 9.7337 | 9.7221 | 9.7126 | 9.7021 | 9.6926 | 9.6821 | 9.6305 | 9.5832 | 7.0716 | 9.3537 | 9.3653 | 9.3611 | 9.3516 | 9.3432 | 9.3305 | 9.32 | 9.3095 | 9.2989 | 9.2884 | 9.2347 | 9.1863 | 9.1411 | 9.3463 | 9.4337 | 9.4305 | 9.4211 | 9.4116 | 9.3989 | 9.3884 | 9.3768 | 9.3653 | 9.3537 | 9.2968 | 9.2442 | 9.1958
|  | KEMBLE RAF | CF |  |  |  | 9.7537 | 9.7537 | 9.7526 | 9.7526 | 9.7495 | 9.7421 | 9.7358 | 9.7295 | 9.72 | 9.7137 | 9.6811 | 9.6474 | 9.6137 | 9.3537 | 9.3537 | 9.3653 | 9.3653 | 9.3611 | 9.3526 | 9.3463 | 9.3379 | 9.3284 | 9.3232 | 9.2863 | 9.2505 | 9.2147 | 9.3463 | 9.3463 | 9.4337 | 9.4337 | 9.4305 | 9.4221 | 9.4147 | 9.4074 | 9.3968 | 9.3905 | 9.3526 | 9.3147 | 9.2768
COWLEY GSP | COWLEY LOCAL (2 X 45) | KENNINGTON | MINIMUM HEADROOM | SP 52881 01094 | YES | 1.1368 | 5.4232 | 5.2947 | 5.1642 | 5.0253 | 4.7432 | 4.4516 | 4.1632 | 3.8495 | 3.7253 | 3.6105 | 2.8716 | 2.0853 | -4.7368 | 3.7074 | 3.5789 | 3.4484 | 3.3095 | 2.9979 | 2.6789 | 2.3632 | 2.0147 | 1.8937 | 1.7811 | 1.0032 | 0.14947 | -0.84947 | 4.04 | 3.9116 | 3.7811 | 3.6421 | 3.3316 | 3.0105 | 2.6937 | 2.3442 | 2.22 | 2.1063 | 1.3137 | 0.44421 | -0.56105
|  | KENNINGTON | EE |  |  |  | 5.4758 | 5.3758 | 5.2695 | 5.1579 | 5.04 | 4.9147 | 4.7895 | 4.6726 | 4.5568 | 4.4137 | 3.7105 | 3.0126 | 2.3621 | 3.76 | 3.66 | 3.5537 | 3.4421 | 3.3253 | 3.2011 | 3.0789 | 2.9642 | 2.8516 | 2.7021 | 1.96 | 1.2042 | 0.46526 | 4.0926 | 3.9926 | 3.8863 | 3.7747 | 3.6568 | 3.5316 | 3.4074 | 3.2895 | 3.1747 | 3.0221 | 2.26 | 1.4832 | 0.73789
|  | KENNINGTON | HT |  |  |  | 5.4232 | 5.2947 | 5.1642 | 5.0253 | 4.7432 | 4.4516 | 4.1632 | 3.8495 | 3.7253 | 3.6105 | 2.8716 | 2.0853 | 1.2053 | 3.7074 | 3.5789 | 3.4484 | 3.3095 | 2.9979 | 2.6789 | 2.3632 | 2.0147 | 1.8937 | 1.7811 | 1.0032 | 0.14947 | -0.84947 | 4.04 | 3.9116 | 3.7811 | 3.6421 | 3.3316 | 3.0105 | 2.6937 | 2.3442 | 2.22 | 2.1063 | 1.3137 | 0.44421 | -0.56105
|  | KENNINGTON | HE |  |  |  | 5.5463 | 5.4811 | 5.4084 | 5.3284 | 5.2432 | 5.1463 | 5.0547 | 4.9674 | 4.8853 | 4.8137 | 4.3884 | 3.9011 | -4.7368 | 3.8305 | 3.7653 | 3.6926 | 3.6126 | 3.5274 | 3.4316 | 3.3421 | 3.2547 | 3.1747 | 3.1042 | 2.6526 | 2.1011 | 1.7337 | 4.1632 | 4.0979 | 4.0253 | 3.9453 | 3.86 | 3.7632 | 3.6716 | 3.5842 | 3.5021 | 3.4316 | 2.9705 | 2.4137 | 2.0411
|  | KENNINGTON | CF |  |  |  | 6.0653 | 5.5516 | 5.5158 | 5.4768 | 5.4379 | 5.3937 | 5.3516 | 5.3074 | 5.2653 | 5.2232 | 4.9568 | 4.6716 | 4.4368 | 4.9074 | 3.8358 | 3.8 | 3.7611 | 3.7221 | 3.6789 | 3.6368 | 3.5937 | 3.5526 | 3.5095 | 3.2316 | 2.9105 | 2.6453 | 5.2295 | 4.1684 | 4.1326 | 4.0937 | 4.0547 | 4.0105 | 3.9684 | 3.9242 | 3.8821 | 3.84 | 3.5579 | 3.2347 | 2.9663
BRAMLEY (FLEE) | BURGHFIELD MAIN | KENTWOOD HILL | MINIMUM HEADROOM | SU 67102 74048 | YES | 0.070526 | 32.3242 | 31.7105 | 31.0905 | 30.4326 | 29.7537 | 28.6874 | 27.32 | 26.3137 | 25.3789 | 24.4958 | 20.6116 | 16.6611 | -13.7505 | 27.7832 | 26.6116 | 25.4579 | 24.28 | 23.0979 | 21.6126 | 20.1316 | 19.06 | 18.0611 | 17.1242 | 12.9295 | 8.5505 | 4.42 | 28.8863 | 27.7579 | 26.5874 | 25.3937 | 24.1958 | 22.6853 | 21.18 | 20.0937 | 19.0811 | 18.1305 | 13.9295 | 9.5568 | 5.4316
|  | KENTWOOD HILL | EE |  |  |  | 32.5621 | 32.0832 | 31.5768 | 31.0379 | 30.4768 | 29.8958 | 29.1389 | 28.2989 | 27.4811 | 26.7379 | 23.7842 | 20.8126 | 18.0442 | 28.3063 | 27.4032 | 26.4884 | 25.5474 | 24.5916 | 23.3232 | 22.0916 | 21.2 | 20.3305 | 19.5368 | 16.3768 | 13.0726 | 9.9547 | 29.1432 | 28.5505 | 27.6358 | 26.6811 | 25.7126 | 24.4232 | 23.1705 | 22.2674 | 21.3863 | 20.5821 | 17.3726 | 14.0726 | 10.96
|  | KENTWOOD HILL | HT |  |  |  | 32.3242 | 31.7105 | 31.0905 | 30.4326 | 29.7537 | 28.6874 | 27.32 | 26.3137 | 25.3789 | 24.4958 | 20.6116 | 16.6611 | 12.9695 | 27.7832 | 26.6116 | 25.4579 | 24.28 | 23.0979 | 21.6126 | 20.1316 | 19.06 | 18.0611 | 17.1242 | 12.9295 | 8.5505 | 4.42 | 28.8863 | 27.7579 | 26.5874 | 25.3937 | 24.1958 | 22.6853 | 21.18 | 20.0937 | 19.0811 | 18.1305 | 13.9295 | 9.5568 | 5.4316
|  | KENTWOOD HILL | HE |  |  |  | 32.8947 | 32.5726 | 32.2179 | 31.8263 | 31.4032 | 30.9547 | 30.5242 | 30.1189 | 29.7389 | 29.4126 | 28 | 26.1116 | -13.7505 | 28.8253 | 28.4558 | 27.8663 | 27.2379 | 26.5758 | 25.5842 | 24.62 | 23.9895 | 23.3884 | 22.8568 | 20.9326 | 18.8347 | 16.8453 | 29.5011 | 29.1632 | 28.7926 | 28.3811 | 27.7295 | 26.7221 | 25.7411 | 25.1042 | 24.4958 | 23.9579 | 22.0074 | 19.8621 | 17.8432
|  | KENTWOOD HILL | CF |  |  |  | 33.0863 | 32.9095 | 32.7263 | 32.5347 | 32.3368 | 32.1326 | 31.9232 | 31.7179 | 31.5147 | 31.3126 | 30.4084 | 29.7095 | 28.4958 | 29.04 | 28.8411 | 28.6358 | 28.3326 | 27.9621 | 27.4642 | 26.9474 | 26.5726 | 26.1979 | 25.8242 | 24.1 | 22.6547 | 21.2779 | 29.7042 | 29.5158 | 29.3221 | 29.1189 | 28.9095 | 28.6116 | 28.0979 | 27.7179 | 27.3379 | 26.9589 | 25.2084 | 23.7326 | 22.3189
COWLEY GSP | YARNTON BSP | KIDDINGTON | MINIMUM HEADROOM | SP 43362 24301 | YES | 0.12105 | 26.1274 | 26.1 | 26.0726 | 26.0432 | 26.0126 | 25.9811 | 25.9337 | 25.8379 | 25.7505 | 25.6432 | 25.0242 | 24.3474 | 11.4253 | 23.6642 | 23.6221 | 23.5789 | 23.5347 | 23.4789 | 23.3042 | 23.1168 | 22.9463 | 22.7926 | 22.6495 | 21.9811 | 21.2305 | 20.3895 | 24.3179 | 24.2863 | 24.2547 | 24.2221 | 24.1874 | 24.0558 | 23.8716 | 23.7053 | 23.5547 | 23.4137 | 22.7568 | 21.9895 | 21.1284
|  | KIDDINGTON | EE |  |  |  | 26.5947 | 26.5189 | 26.4389 | 26.7979 | 26.6589 | 26.5105 | 26.3705 | 26.2368 | 26.1126 | 25.9979 | 25.5337 | 25.0358 | 24.4821 | 24.3221 | 24.18 | 24.0379 | 24.0116 | 23.8621 | 23.7021 | 23.5516 | 23.4063 | 23.2737 | 23.1505 | 22.6432 | 22.0768 | 21.4347 | 24.9621 | 24.8863 | 24.7747 | 24.6884 | 24.5379 | 24.3789 | 24.2284 | 24.0832 | 23.9505 | 23.8274 | 23.3189 | 22.7526 | 22.1105
|  | KIDDINGTON | HT |  |  |  | 26.5568 | 26.4611 | 26.3632 | 26.26 | 26.1526 | 26.0432 | 25.9337 | 25.8379 | 25.7505 | 25.6432 | 25.0242 | 24.3474 | 23.6011 | 24.24 | 24.0558 | 23.8758 | 23.6832 | 23.4905 | 23.3042 | 23.1168 | 22.9463 | 22.7926 | 22.6495 | 21.9811 | 21.2305 | 20.3895 | 24.9242 | 24.7926 | 24.6168 | 24.4274 | 24.2389 | 24.0558 | 23.8716 | 23.7053 | 23.5547 | 23.4137 | 22.7568 | 21.9895 | 21.1284
|  | KIDDINGTON | HE |  |  |  | 26.6484 | 26.5979 | 26.5421 | 26.4811 | 26.4158 | 26.3463 | 26.2779 | 26.2158 | 26.1568 | 26.1063 | 25.9358 | 25.8389 | 11.4253 | 24.4368 | 24.3474 | 24.2568 | 24.1537 | 24.0516 | 23.9411 | 23.8316 | 23.7316 | 23.6411 | 23.5611 | 23.2516 | 22.8684 | 22.4063 | 25.0158 | 24.9653 | 24.9095 | 24.8484 | 24.7832 | 24.6779 | 24.5705 | 24.4726 | 24.3832 | 24.3042 | 24.0011 | 23.6305 | 23.1821
|  | KIDDINGTON | CF |  |  |  | 26.1274 | 26.1 | 26.0726 | 26.0432 | 26.0126 | 25.9811 | 25.9495 | 25.9179 | 25.8863 | 25.8547 | 25.7168 | 26.1989 | 26.1242 | 23.6642 | 23.6221 | 23.5789 | 23.5347 | 23.4789 | 23.4189 | 23.3558 | 23.2968 | 23.2379 | 23.1768 | 22.9042 | 23.4484 | 23.1295 | 24.3179 | 24.2863 | 24.2547 | 24.2221 | 24.1874 | 24.1526 | 24.1168 | 24.0811 | 24.0368 | 23.9768 | 23.7095 | 24.2011 | 23.8947
BRAMLEY (FLEE) | READING BSP | KIDMORE END | MINIMUM HEADROOM | SU 69953 78205 | YES | 0.073684 | 26.1032 | 25.8979 | 25.6895 | 25.4326 | 25.0716 | 24.7021 | 24.3242 | 23.9779 | 23.6558 | 23.3568 | 22.0505 | 20.8695 | 9.3674 | 23.8926 | 23.5053 | 23.12 | 22.4874 | 22.0937 | 21.6937 | 21.2853 | 20.9084 | 20.5579 | 20.2326 | 18.8095 | 17.4947 | 16.2284 | 24.4011 | 24.0084 | 23.6179 | 22.9716 | 22.5716 | 22.1653 | 21.7495 | 21.3663 | 21.0084 | 20.6758 | 19.2137 | 17.8642 | 16.5905
|  | KIDMORE END | EE |  |  |  | 26.1884 | 26.0316 | 25.8642 | 25.6874 | 25.5032 | 25.2337 | 24.9284 | 24.6368 | 24.3505 | 24.0937 | 23.0284 | 22.1021 | 21.3495 | 24.0716 | 23.7768 | 23.4737 | 22.9211 | 22.6053 | 22.2821 | 21.9526 | 21.6368 | 21.3295 | 21.0526 | 19.9053 | 18.8958 | 18.0379 | 24.5832 | 24.2842 | 23.9758 | 23.4116 | 23.0916 | 22.7632 | 22.4263 | 22.1032 | 21.7884 | 21.5042 | 20.3168 | 19.2642 | 18.38
|  | KIDMORE END | HT |  |  |  | 26.1032 | 25.8979 | 25.6895 | 25.4326 | 25.0716 | 24.7021 | 24.3242 | 23.9779 | 23.6558 | 23.3568 | 22.0505 | 20.8695 | 19.7663 | 23.8926 | 23.5053 | 23.12 | 22.4874 | 22.0937 | 21.6937 | 21.2853 | 20.9084 | 20.5579 | 20.2326 | 18.8095 | 17.4947 | 16.2284 | 24.4011 | 24.0084 | 23.6179 | 22.9716 | 22.5716 | 22.1653 | 21.7495 | 21.3663 | 21.0084 | 20.6758 | 19.2137 | 17.8642 | 16.5905
|  | KIDMORE END | HE |  |  |  | 26.3021 | 26.2011 | 26.0884 | 25.9621 | 25.8284 | 25.6789 | 25.5358 | 25.4021 | 25.2758 | 25.1284 | 24.4821 | 23.9663 | 9.3674 | 24.3095 | 24.1305 | 23.9389 | 23.4947 | 23.28 | 23.0516 | 22.8158 | 22.5916 | 22.3811 | 22.1916 | 21.4937 | 20.9158 | 20.3937 | 24.7347 | 24.6284 | 24.4505 | 23.9958 | 23.7779 | 23.5463 | 23.3053 | 23.0779 | 22.8621 | 22.6695 | 21.9516 | 21.3568 | 20.8147
|  | KIDMORE END | CF |  |  |  | 26.3674 | 26.3126 | 26.2558 | 26.1979 | 26.1368 | 26.0705 | 26.0032 | 25.9379 | 25.8726 | 25.8084 | 25.5147 | 25.2295 | 24.9179 | 24.4295 | 24.3653 | 24.2537 | 24.0368 | 23.9179 | 23.7926 | 23.6621 | 23.5316 | 23.4042 | 23.2768 | 22.7 | 22.2737 | 21.9147 | 24.8063 | 24.7484 | 24.6874 | 24.5463 | 24.4263 | 24.2989 | 24.1653 | 24.0337 | 23.9011 | 23.7726 | 23.1832 | 22.7442 | 22.3726
BRAMLEY (FLEE) | CAMBERLEY MAIN | KINGS RIDE | MINIMUM HEADROOM | SU 87551 61530 | YES | 0.12632 | 28.3189 | 28.0958 | 27.8705 | 27.6295 | 27.3821 | 27.1221 | 26.8611 | 26.5926 | 25.7274 | 24.8821 | 21.7905 | 20.2642 | 0.47263 | 25.0884 | 24.8347 | 24.4421 | 23.6011 | 22.6789 | 21.6726 | 20.6747 | 19.7 | 18.7221 | 17.7642 | 14.2926 | 12.6232 | 11.1442 | 25.5611 | 25.3263 | 25.0895 | 24.6516 | 23.7789 | 22.8274 | 21.8726 | 20.8989 | 19.92 | 18.9621 | 15.4853 | 13.8032 | 12.32
|  | KINGS RIDE | EE |  |  |  | 28.4084 | 28.2358 | 28.0516 | 27.8579 | 27.6547 | 27.4389 | 27.2295 | 27.0284 | 26.4916 | 25.6421 | 22.8274 | 21.6537 | 20.6495 | 25.1779 | 25.0053 | 24.7916 | 24.28 | 23.6053 | 22.8032 | 21.9989 | 20.8968 | 19.5495 | 18.5832 | 15.4084 | 14.1442 | 13.0253 | 25.6568 | 25.4747 | 25.2821 | 25.0674 | 24.6558 | 23.8968 | 23.1347 | 22.0926 | 20.7453 | 19.7779 | 16.5895 | 15.3084 | 14.1853
|  | KINGS RIDE | HT |  |  |  | 28.3189 | 28.0958 | 27.8705 | 27.6295 | 27.3821 | 27.1221 | 26.8611 | 26.5926 | 25.7274 | 24.8821 | 21.7905 | 20.2642 | 18.9295 | 25.0884 | 24.8347 | 24.4421 | 23.6011 | 22.6789 | 21.6726 | 20.6747 | 19.7 | 18.7221 | 17.7642 | 14.2926 | 12.6232 | 11.1442 | 25.5611 | 25.3263 | 25.0895 | 24.6516 | 23.7789 | 22.8274 | 21.8726 | 20.8989 | 19.92 | 18.9621 | 15.4853 | 13.8032 | 12.32
|  | KINGS RIDE | HE |  |  |  | 28.5221 | 28.4032 | 28.2705 | 28.1253 | 27.9684 | 27.7968 | 27.6337 | 27.48 | 27.3368 | 26.7463 | 24.4116 | 23.6516 | 0.47263 | 25.2916 | 25.1726 | 25.04 | 24.8558 | 24.2937 | 23.5821 | 22.8768 | 21.8221 | 20.5842 | 19.78 | 17.1179 | 16.2653 | 15.5695 | 25.7789 | 25.6547 | 25.5168 | 25.3537 | 25.1726 | 24.6453 | 23.9789 | 22.9916 | 21.7821 | 20.9779 | 18.3126 | 17.4537 | 16.7537
|  | KINGS RIDE | CF |  |  |  | 28.5884 | 28.5189 | 28.4484 | 28.3737 | 28.2979 | 28.2179 | 28.1347 | 28.0537 | 27.9737 | 27.8926 | 27.3316 | 26.74 | 26.2916 | 25.3579 | 25.2884 | 25.2179 | 25.1432 | 25.0674 | 24.9874 | 24.9063 | 24.7895 | 24.3811 | 23.8895 | 20.4095 | 19.7495 | 19.2463 | 25.8484 | 25.7758 | 25.7011 | 25.6232 | 25.5432 | 25.46 | 25.3726 | 25.2832 | 25.1832 | 24.9347 | 21.6084 | 20.9463 | 20.44
BRAMLEY (ANDO-THAT) | THATCHAM BSP | KINGSCLERE | MINIMUM HEADROOM | SU 51982 59358 | YES | 0 | 9.5189 | 9.4074 | 9.2168 | 9.0242 | 8.8274 | 8.4789 | 8.0021 | 7.4295 | 7.3295 | 7.2358 | 6.1821 | 4.8274 | -2.0368 | 7.2811 | 7.0737 | 6.8684 | 6.6621 | 6.4516 | 6.0621 | 5.5253 | 4.8705 | 4.7726 | 4.68 | 3.5137 | 1.9789 | 1.5463 | 7.8642 | 7.6568 | 7.4526 | 7.2453 | 7.0358 | 6.6474 | 6.1095 | 5.4558 | 5.3558 | 5.2621 | 4.0926 | 2.5526 | 2.1179
|  | KINGSCLERE | EE |  |  |  | 9.56 | 9.4768 | 9.3853 | 9.2284 | 9.0716 | 8.9105 | 8.7537 | 8.6042 | 8.4621 | 8.3263 | 7.7695 | 6.5537 | 5.7242 | 7.3737 | 7.2147 | 7.0516 | 6.8842 | 6.7168 | 6.5453 | 6.3811 | 6.2232 | 6.0726 | 5.9305 | 5.3421 | 3.9621 | 3.0147 | 7.9558 | 7.7979 | 7.6347 | 7.4674 | 7.3 | 7.1295 | 6.9621 | 6.8042 | 6.6526 | 6.5084 | 5.9116 | 4.5232 | 3.5758
|  | KINGSCLERE | HT |  |  |  | 9.5189 | 9.4074 | 9.2168 | 9.0242 | 8.8274 | 8.4789 | 8.0021 | 7.4295 | 7.3295 | 7.2358 | 6.1821 | 4.8274 | 4.4232 | 7.2811 | 7.0737 | 6.8684 | 6.6621 | 6.4516 | 6.0621 | 5.5253 | 4.8705 | 4.7726 | 4.68 | 3.5137 | 1.9789 | 1.5463 | 7.8642 | 7.6568 | 7.4526 | 7.2453 | 7.0358 | 6.6474 | 6.1095 | 5.4558 | 5.3558 | 5.2621 | 4.0926 | 2.5526 | 2.1179
|  | KINGSCLERE | HE |  |  |  | 9.6168 | 9.5611 | 9.5 | 9.4316 | 9.3947 | 9.28 | 9.1705 | 9.0653 | 8.9684 | 8.88 | 8.5432 | 7.6158 | -2.0368 | 7.4989 | 7.4021 | 7.2968 | 7.1863 | 7.0684 | 6.9484 | 6.8337 | 6.7232 | 6.6221 | 6.5284 | 6.1726 | 5.1053 | 4.3411 | 8.0811 | 7.9842 | 7.8789 | 7.7695 | 7.6516 | 7.5305 | 7.4158 | 7.3042 | 7.2021 | 7.1084 | 6.7495 | 5.6821 | 4.9168
|  | KINGSCLERE | CF |  |  |  | 9.6505 | 9.62 | 9.5884 | 9.5547 | 9.52 | 9.4842 | 9.4474 | 9.4095 | 9.3737 | 9.3126 | 9.0263 | 8.6768 | 8.1863 | 7.5621 | 7.5011 | 7.4411 | 7.3779 | 7.3147 | 7.2484 | 7.18 | 7.1105 | 7.0453 | 6.9768 | 6.6695 | 6.2747 | 5.7084 | 8.1442 | 8.0832 | 8.0232 | 7.9611 | 7.8979 | 7.8305 | 7.7621 | 7.6937 | 7.6274 | 7.5589 | 7.2505 | 6.8547 | 6.2874
BRAMLEY (ANDO-THAT) | THATCHAM BSP | KINTBURY | MINIMUM HEADROOM | SU 37657 67143 | YES | 0.075789 | 8.4716 | 8.3326 | 8.1958 | 8.0568 | 7.9158 | 7.7747 | 7.6379 | 7.5137 | 7.3958 | 7.2916 | 6.8263 | 6.3674 | 0.047368 | 7.5916 | 7.4305 | 7.2737 | 7.1137 | 6.9526 | 6.7926 | 6.6379 | 6.4968 | 6.3621 | 6.2432 | 5.7021 | 5.14 | 4.6074 | 7.8389 | 7.6779 | 7.52 | 7.3611 | 7.1989 | 7.04 | 6.8853 | 6.7432 | 6.6095 | 6.4905 | 5.9495 | 5.3874 | 4.8547
|  | KINTBURY | EE |  |  |  | 8.5126 | 8.4253 | 8.3147 | 8.2032 | 8.0895 | 7.9737 | 7.8632 | 7.7589 | 7.6589 | 7.5705 | 7.2189 | 6.8716 | 6.5442 | 7.6358 | 7.54 | 7.4126 | 7.2863 | 7.1568 | 7.0263 | 6.9011 | 6.7832 | 6.6695 | 6.5705 | 6.1642 | 5.7358 | 5.3189 | 7.8842 | 7.7874 | 7.66 | 7.5337 | 7.4042 | 7.2726 | 7.1484 | 7.0305 | 6.9168 | 6.8179 | 6.4116 | 5.9832 | 5.5663
|  | KINTBURY | HT |  |  |  | 8.4716 | 8.3326 | 8.1958 | 8.0568 | 7.9158 | 7.7747 | 7.6379 | 7.5137 | 7.3958 | 7.2916 | 6.8263 | 6.3674 | 5.9411 | 7.5916 | 7.4305 | 7.2737 | 7.1137 | 6.9526 | 6.7926 | 6.6379 | 6.4968 | 6.3621 | 6.2432 | 5.7021 | 5.14 | 4.6074 | 7.8389 | 7.6779 | 7.52 | 7.3611 | 7.1989 | 7.04 | 6.8853 | 6.7432 | 6.6095 | 6.4905 | 5.9495 | 5.3874 | 4.8547
|  | KINTBURY | HE |  |  |  | 8.5579 | 8.5147 | 8.4642 | 8.4011 | 8.32 | 8.2389 | 8.1611 | 8.0853 | 8.0137 | 7.9558 | 7.7442 | 7.5221 | 0.047368 | 7.6811 | 7.6379 | 7.5863 | 7.5179 | 7.4284 | 7.3379 | 7.2516 | 7.1674 | 7.0874 | 7.0232 | 6.7853 | 6.5074 | 6.2337 | 7.9295 | 7.8853 | 7.8337 | 7.7653 | 7.6758 | 7.5853 | 7.4979 | 7.4147 | 7.3347 | 7.2705 | 7.0316 | 6.7547 | 6.48
|  | KINTBURY | CF |  |  |  | 8.5853 | 8.5632 | 8.5389 | 8.5137 | 8.4853 | 8.4526 | 8.4105 | 8.3695 | 8.3263 | 8.2874 | 8.0958 | 7.94 | 7.7989 | 7.7095 | 7.6874 | 7.6621 | 7.6368 | 7.6084 | 7.5737 | 7.5253 | 7.4779 | 7.4295 | 7.3842 | 7.1632 | 6.9684 | 6.7842 | 7.9579 | 7.9358 | 7.9105 | 7.8853 | 7.8558 | 7.8211 | 7.7726 | 7.7253 | 7.6768 | 7.6316 | 7.4105 | 7.2158 | 7.0316
BRAMLEY (FLEE) | MAIDENHEAD BSP | KNOWL HILL | MINIMUM HEADROOM | SU 82849 79105 | YES | 0.62105 | 6.6884 | 6.6347 | 6.5779 | 6.5189 | 6.4589 | 6.4484 | 6.2379 | 5.8958 | 5.8326 | 5.7726 | 5.0842 | 4.1926 | -0.098947 | 5.7695 | 5.6653 | 5.5589 | 5.4526 | 5.3474 | 5.1305 | 4.8158 | 4.4284 | 4.3684 | 4.3105 | 3.5842 | 2.6084 | 2.34 | 5.8632 | 5.8063 | 5.7474 | 5.6737 | 5.5653 | 5.3389 | 5.0158 | 4.6158 | 4.5526 | 4.4926 | 3.7326 | 2.7274 | 2.4495
|  | KNOWL HILL | EE |  |  |  | 6.7116 | 6.6695 | 7.0179 | 6.9358 | 6.8526 | 6.8232 | 6.7284 | 6.6411 | 6.5295 | 6.4221 | 5.9095 | 5.1284 | 4.5979 | 5.8179 | 5.7368 | 5.6884 | 5.6021 | 5.5116 | 5.4811 | 5.3853 | 5.2979 | 5.1821 | 5.0737 | 4.5568 | 3.7253 | 3.1358 | 5.8884 | 5.8432 | 5.8768 | 5.7895 | 5.7011 | 5.6663 | 5.5663 | 5.4737 | 5.3537 | 5.24 | 4.6853 | 3.8126 | 3.2095
|  | KNOWL HILL | HT |  |  |  | 6.6884 | 6.6347 | 6.5779 | 6.5189 | 6.4589 | 6.4484 | 6.2379 | 5.8958 | 5.8326 | 5.7726 | 5.0842 | 4.1926 | 3.9326 | 5.7695 | 5.6653 | 5.5589 | 5.4526 | 5.3474 | 5.1305 | 4.8158 | 4.4284 | 4.3684 | 4.3105 | 3.5842 | 2.6084 | 2.34 | 5.8632 | 5.8063 | 5.7474 | 5.6737 | 5.5653 | 5.3389 | 5.0158 | 4.6158 | 4.5526 | 4.4926 | 3.7326 | 2.7274 | 2.4495
|  | KNOWL HILL | HE |  |  |  | 6.7432 | 6.7147 | 6.6832 | 6.6516 | 6.6147 | 6.6305 | 6.5874 | 6.5453 | 6.5042 | 6.4684 | 6.3242 | 5.9411 | -0.098947 | 5.8558 | 5.8242 | 5.7779 | 5.7221 | 5.6632 | 5.6568 | 5.5926 | 5.5295 | 5.4589 | 5.3926 | 5.0653 | 4.5137 | 4.0421 | 5.9221 | 5.8916 | 5.8589 | 5.8263 | 5.7874 | 5.8021 | 5.7589 | 5.7158 | 5.6726 | 5.6042 | 5.26 | 4.6832 | 4.1926
|  | KNOWL HILL | CF |  |  |  | 6.76 | 6.7453 | 6.7295 | 6.7137 | 6.6968 | 6.7379 | 6.7179 | 6.6979 | 6.6768 | 6.6579 | 6.5653 | 6.5063 | 6.2926 | 5.8737 | 5.8579 | 5.84 | 5.8221 | 5.7916 | 5.8179 | 5.7821 | 5.7432 | 5.7084 | 5.6663 | 5.4516 | 5.2284 | 4.88 | 5.9389 | 5.9242 | 5.9074 | 5.8905 | 5.8726 | 5.9137 | 5.8926 | 5.8705 | 5.8495 | 5.8295 | 5.6632 | 5.4295 | 5.0653
BRAMLEY (FLEE) | ALDERSHOT BSP | LABURNUM ROAD | MINIMUM HEADROOM | SU 86017 50475 | YES | 0 | 43.7832 | 43.48 | 43.1747 | 42.4579 | 40.6084 | 39.2568 | 38.0537 | 37.1032 | 36.18 | 35.2968 | 32.4379 | 30.2053 | -4.6537 | 37.7947 | 36.7347 | 34.7074 | 32.2979 | 30.1389 | 28.5832 | 27.2063 | 26.1263 | 25.0768 | 24.0874 | 20.9253 | 18.4537 | 16.16 | 38.8432 | 38.4305 | 36.5063 | 34.0968 | 31.9368 | 30.38 | 29.0021 | 27.9211 | 26.8737 | 25.8821 | 22.7179 | 20.2442 | 17.9474
|  | LABURNUM ROAD | EE |  |  |  | 43.8968 | 43.6579 | 43.4063 | 43.0295 | 41.2821 | 40.0305 | 38.9368 | 38.0663 | 37.2105 | 36.4021 | 33.9863 | 32.2779 | 30.7505 | 38.0211 | 37.1284 | 35.2189 | 32.9284 | 30.8811 | 29.4326 | 28.1747 | 27.1811 | 26.2053 | 25.2884 | 22.6105 | 20.7147 | 19.0021 | 38.9568 | 38.7179 | 37.0116 | 34.7263 | 32.6789 | 31.2305 | 29.9705 | 28.9779 | 28 | 27.0842 | 24.4021 | 22.5042 | 20.7905
|  | LABURNUM ROAD | HT |  |  |  | 43.7832 | 43.48 | 43.1747 | 42.4579 | 40.6084 | 39.2568 | 38.0537 | 37.1032 | 36.18 | 35.2968 | 32.4379 | 30.2053 | 28.1495 | 37.7947 | 36.7347 | 34.7074 | 32.2979 | 30.1389 | 28.5832 | 27.2063 | 26.1263 | 25.0768 | 24.0874 | 20.9253 | 18.4537 | 16.16 | 38.8432 | 38.4305 | 36.5063 | 34.0968 | 31.9368 | 30.38 | 29.0021 | 27.9211 | 26.8737 | 25.8821 | 22.7179 | 20.2442 | 17.9474
|  | LABURNUM ROAD | HE |  |  |  | 44.0389 | 43.8653 | 43.6737 | 43.4621 | 42.1168 | 40.9811 | 40.0053 | 39.2516 | 38.5189 | 37.8421 | 36.0589 | 34.9547 | -4.6537 | 38.1726 | 37.6253 | 35.8653 | 33.7179 | 31.8095 | 30.4895 | 29.3611 | 28.5 | 27.6589 | 26.8789 | 24.8768 | 23.6442 | 22.5726 | 39.0989 | 38.9253 | 37.6379 | 35.5158 | 33.6074 | 32.2874 | 31.1589 | 30.2958 | 29.4547 | 28.6747 | 26.6705 | 25.4379 | 24.3653
|  | LABURNUM ROAD | CF |  |  |  | 44.1221 | 44.0158 | 43.9053 | 43.7905 | 43.6726 | 43.5505 | 43.4242 | 43.3021 | 43.18 | 42.9537 | 41.5526 | 40.7368 | 40.0705 | 38.2632 | 38.1421 | 37.3484 | 36.3558 | 35.5011 | 34.9042 | 34.3379 | 33.8621 | 33.3611 | 32.8537 | 31.2779 | 30.3505 | 29.5789 | 39.1821 | 39.0758 | 38.9653 | 38.1011 | 37.2926 | 36.7032 | 36.1368 | 35.66 | 35.1589 | 34.6526 | 33.0747 | 32.1474 | 31.3747
BRAMLEY (ANDO-THAT) | THATCHAM BSP | LAMBOURN | MINIMUM HEADROOM | SU 33280 78217 | YES | 0.052632 | 9.7011 | 26.0958 | 25.9895 | 25.8768 | 25.7611 | 25.64 | 25.52 | 25.4147 | 25.32 | 25.2316 | 24.8768 | 24.3105 | -32.9663 | 7.9221 | 24.2526 | 24.0621 | 23.8695 | 23.6747 | 23.4768 | 23.2758 | 23.0916 | 22.9242 | 22.7684 | 22.0684 | 21.3432 | 20.66 | 8.0337 | 24.4221 | 24.3105 | 24.1926 | 24.0716 | 23.8768 | 23.6758 | 23.4926 | 23.3253 | 23.1695 | 22.4695 | 21.7432 | 21.06
|  | LAMBOURN | EE |  |  |  | 9.7411 | 26.1589 | 26.0716 | 25.9768 | 25.8821 | 25.7811 | 25.6853 | 25.5937 | 25.5063 | 25.4284 | 25.1484 | 24.96 | 24.5589 | 7.9653 | 24.3789 | 24.2284 | 24.0716 | 23.9158 | 23.7579 | 23.6074 | 23.4579 | 23.3126 | 23.1779 | 22.6474 | 22.1053 | 21.5989 | 8.0758 | 24.4895 | 24.3979 | 24.2989 | 24.2 | 24.0958 | 23.9958 | 23.8589 | 23.7137 | 23.5779 | 23.0474 | 22.5063 | 21.9989
|  | LAMBOURN | HT |  |  |  | 9.7011 | 26.0958 | 25.9895 | 25.8768 | 25.7611 | 25.64 | 25.52 | 25.4147 | 25.32 | 25.2316 | 24.8768 | 24.3105 | 23.6979 | 7.9221 | 24.2526 | 24.0621 | 23.8695 | 23.6747 | 23.4768 | 23.2758 | 23.0916 | 22.9242 | 22.7684 | 22.0684 | 21.3432 | 20.66 | 8.0337 | 24.4221 | 24.3105 | 24.1926 | 24.0716 | 23.8768 | 23.6758 | 23.4926 | 23.3253 | 23.1695 | 22.4695 | 21.7432 | 21.06
|  | LAMBOURN | HE |  |  |  | 9.7989 | 26.2432 | 26.1811 | 26.1147 | 26.0421 | 25.9642 | 25.8895 | 25.8189 | 25.7558 | 25.6979 | 25.5105 | 25.4021 | -32.9663 | 8.0263 | 24.4684 | 24.4042 | 24.3347 | 24.2411 | 24.1284 | 24.02 | 23.9179 | 23.8232 | 23.7411 | 23.4442 | 23.1095 | 22.7884 | 8.1379 | 24.58 | 24.5147 | 24.4463 | 24.3716 | 24.2916 | 24.2137 | 24.1411 | 24.0758 | 24.0168 | 23.8221 | 23.5105 | 23.1895
|  | LAMBOURN | CF |  |  |  | 9.8326 | 26.3021 | 26.2705 | 26.2368 | 26.2042 | 26.1684 | 26.1326 | 26.0979 | 26.0621 | 26.0263 | 25.8716 | 25.7937 | 25.7516 | 8.0621 | 24.5295 | 24.4968 | 24.4611 | 24.4274 | 24.3895 | 24.3526 | 24.2947 | 24.2347 | 24.1758 | 23.9042 | 23.6737 | 23.4379 | 8.1737 | 24.6411 | 24.6084 | 24.5726 | 24.5379 | 24.5011 | 24.4632 | 24.4274 | 24.3895 | 24.3526 | 24.1895 | 24.0747 | 23.8389
FAWLEY GSP | LANGLEY BSP | LANGLEY | MINIMUM HEADROOM | SU 45158 01418 | YES | 0 | 13.7747 | 13.4263 | 13.0789 | 13.1074 | 12.8105 | 12.6747 | 12.0253 | 11.2411 | 10.7347 | 9.8379 | 8.9432 | 7.4116 | -12.0463 | 13.4379 | 13.0232 | 12.6063 | 12.6547 | 12.3189 | 12.24 | 11.4379 | 10.5074 | 9.9537 | 8.9389 | 8.0221 | 6.3221 | 4.6947 | 13.5263 | 13.1989 | 12.7895 | 12.8368 | 12.5011 | 12.3168 | 11.5084 | 10.5695 | 10.0105 | 8.9884 | 8.0674 | 6.3653 | 4.7389
|  | LANGLEY | EE |  |  |  | 13.9253 | 13.6568 | 13.3874 | 13.1074 | 12.8105 | 13.2084 | 12.9168 | 12.4453 | 11.8779 | 11.2337 | 10.0863 | 8.9116 | 7.8189 | 13.5968 | 13.3147 | 12.9874 | 12.6547 | 12.3189 | 12.8642 | 12.5368 | 11.96 | 11.2442 | 10.4958 | 9.2653 | 7.9663 | 6.7316 | 13.6589 | 13.4179 | 13.1621 | 12.8368 | 12.5011 | 12.9442 | 12.6158 | 12.0337 | 11.3116 | 10.5547 | 9.3105 | 8.0032 | 6.7674
|  | LANGLEY | HT |  |  |  | 13.7747 | 13.4263 | 13.0789 | 13.4095 | 13.0442 | 12.6747 | 12.0253 | 11.2411 | 10.7347 | 9.8379 | 8.9432 | 7.4116 | 5.9632 | 13.4379 | 13.0232 | 12.6063 | 13.0684 | 12.6547 | 12.24 | 11.4379 | 10.5074 | 9.9537 | 8.9389 | 8.0221 | 6.3221 | 4.6947 | 13.5263 | 13.1989 | 12.7895 | 13.1495 | 12.7337 | 12.3168 | 11.5084 | 10.5695 | 10.0105 | 8.9884 | 8.0674 | 6.3653 | 4.7389
|  | LANGLEY | HE |  |  |  | 14.1284 | 13.9589 | 13.7811 | 13.5926 | 13.3958 | 13.8863 | 13.6853 | 13.3684 | 13.0074 | 12.6684 | 11.6063 | 10.8158 | -12.0463 | 13.8042 | 13.6316 | 13.4505 | 13.2537 | 13.0368 | 13.6747 | 13.4442 | 13.0537 | 12.6074 | 12.1821 | 10.9021 | 10.0211 | 9.18 | 13.8379 | 13.6842 | 13.5211 | 13.3474 | 13.1642 | 13.7611 | 13.5284 | 13.1358 | 12.6853 | 12.2568 | 10.9632 | 10.0737 | 9.2232
|  | LANGLEY | CF |  |  |  | 14.9358 | 14.1411 | 14.0411 | 13.94 | 13.8358 | 13.7274 | 13.62 | 13.5137 | 13.3937 | 13.9642 | 12.9968 | 12.5274 | 12.0589 | 14.8389 | 13.8158 | 13.7147 | 13.6116 | 13.5063 | 13.3916 | 13.2789 | 13.1537 | 13.0032 | 13.7147 | 12.4947 | 11.9074 | 11.3442 | 14.8747 | 13.8484 | 13.7589 | 13.6684 | 13.5747 | 13.4768 | 13.3789 | 13.2821 | 13.1737 | 13.7989 | 12.5684 | 11.9747 | 11.4042
BRAMLEY (FLEE) | FERNHURST | LANGLEY COURT | MINIMUM HEADROOM | SU 80847 29056 | YES | 0.43895 | 26.2221 | 26.0474 | 25.8737 | 25.6874 | 25.4979 | 25.3 | 24.9726 | 24.68 | 24.3695 | 24.0347 | 22.3874 | 20.7926 | 7.1768 | 23.5779 | 23.2442 | 22.9189 | 22.5663 | 22.1632 | 21.7495 | 21.3863 | 21.0747 | 20.7379 | 20.3716 | 18.56 | 16.8042 | 15.1484 | 24.1158 | 23.8168 | 23.5232 | 23.2053 | 22.8274 | 22.4063 | 22.0379 | 21.7211 | 21.3779 | 21.0042 | 19.1537 | 17.3558 | 15.6716
|  | LANGLEY COURT | EE |  |  |  | 26.2895 | 26.1558 | 26.0137 | 25.8632 | 25.7063 | 25.5432 | 25.3884 | 25.2411 | 25.0884 | 24.8126 | 23.5211 | 22.2621 | 21.0979 | 23.7242 | 23.4695 | 23.2105 | 22.9389 | 22.6189 | 22.3 | 22.0316 | 21.7926 | 21.5232 | 21.2221 | 19.7916 | 18.3958 | 17.1021 | 24.2463 | 24.0168 | 23.7832 | 23.5368 | 23.2516 | 22.9653 | 22.6947 | 22.4516 | 22.1779 | 21.8726 | 20.4095 | 18.9779 | 17.6495
|  | LANGLEY COURT | HT |  |  |  | 26.2221 | 26.0474 | 25.8737 | 25.6874 | 25.4979 | 25.3 | 24.9726 | 24.68 | 24.3695 | 24.0347 | 22.3874 | 20.7926 | 19.3095 | 23.5779 | 23.2442 | 22.9189 | 22.5663 | 22.1632 | 21.7495 | 21.3863 | 21.0747 | 20.7379 | 20.3716 | 18.56 | 16.8042 | 15.1484 | 24.1158 | 23.8168 | 23.5232 | 23.2053 | 22.8274 | 22.4063 | 22.0379 | 21.7211 | 21.3779 | 21.0042 | 19.1537 | 17.3558 | 15.6716
|  | LANGLEY COURT | HE |  |  |  | 26.3853 | 26.2968 | 26.1979 | 26.0905 | 25.9737 | 25.8484 | 25.7295 | 25.6168 | 25.5126 | 25.4221 | 24.7053 | 23.7526 | 7.1768 | 23.9274 | 23.7684 | 23.6021 | 23.4189 | 23.1811 | 22.9411 | 22.7484 | 22.5821 | 22.3863 | 22.1579 | 21.0726 | 19.9895 | 18.9895 | 24.4263 | 24.2832 | 24.1305 | 23.9632 | 23.7516 | 23.5347 | 23.3589 | 23.2032 | 23.0253 | 22.8221 | 21.7126 | 20.6011 | 19.5716
|  | LANGLEY COURT | CF |  |  |  | 26.44 | 26.3916 | 26.3421 | 26.2905 | 26.2379 | 26.1821 | 26.1253 | 26.0695 | 26.0137 | 25.9589 | 25.7137 | 25.3284 | 24.7947 | 24.0747 | 24.0189 | 23.9074 | 23.7884 | 23.6642 | 23.5326 | 23.4095 | 23.2989 | 23.1947 | 23.0853 | 22.4158 | 21.72 | 21.1074 | 24.5126 | 24.4611 | 24.4021 | 24.2968 | 24.1874 | 24.0716 | 23.9632 | 23.8653 | 23.7705 | 23.6726 | 23.0789 | 22.3663 | 21.7368
AXMINSTER | YEOVIL BSP | LARKHILL | MINIMUM HEADROOM | ST 53677 16914 | YES | 0.72316 | 32.1547 | 31.8758 | 31.5947 | 31.2884 | 30.7811 | 30.2737 | 29.7747 | 29.3168 | 28.8863 | 28.4884 | 26.3253 | 24.3768 | 6.8747 | 29.2221 | 28.6768 | 28.1368 | 27.5863 | 27.0379 | 26.4947 | 25.96 | 25.4663 | 25.0032 | 24.5747 | 22.1779 | 19.9905 | 17.6716 | 29.92 | 29.3947 | 28.8726 | 28.3411 | 27.8105 | 27.2821 | 26.7621 | 26.2832 | 25.8337 | 25.4168 | 23.1 | 20.9053 | 18.5811
|  | LARKHILL | EE |  |  |  | 32.2579 | 32.0389 | 31.8063 | 31.5579 | 31.2989 | 30.9768 | 30.5758 | 30.1874 | 29.8126 | 29.4737 | 27.7979 | 26.3232 | 24.7611 | 29.4611 | 29.0389 | 28.6053 | 28.1611 | 27.7147 | 27.2674 | 26.8389 | 26.4242 | 26.0232 | 25.6589 | 23.8168 | 22.1684 | 20.3695 | 30.1463 | 29.7421 | 29.3232 | 28.8926 | 28.4611 | 28.0242 | 27.6074 | 27.2032 | 26.8126 | 26.4589 | 24.6811 | 23.0747 | 21.2705
|  | LARKHILL | HT |  |  |  | 32.1547 | 31.8758 | 31.5947 | 31.2884 | 30.7811 | 30.2737 | 29.7747 | 29.3168 | 28.8863 | 28.4884 | 26.3253 | 24.3768 | 22.3505 | 29.2221 | 28.6768 | 28.1368 | 27.5863 | 27.0379 | 26.4947 | 25.96 | 25.4663 | 25.0032 | 24.5747 | 22.1779 | 19.9905 | 17.6716 | 29.92 | 29.3947 | 28.8726 | 28.3411 | 27.8105 | 27.2821 | 26.7621 | 26.2832 | 25.8337 | 25.4168 | 23.1 | 20.9053 | 18.5811
|  | LARKHILL | HE |  |  |  | 32.4063 | 32.2558 | 32.0905 | 31.9074 | 31.7095 | 31.4979 | 31.2947 | 31.1021 | 30.9232 | 30.7684 | 29.7495 | 28.8053 | 6.8747 | 29.7916 | 29.5242 | 29.24 | 28.9389 | 28.6295 | 28.3084 | 28.0063 | 27.7137 | 27.4379 | 27.1968 | 25.9589 | 24.8863 | 23.6105 | 30.3063 | 30.1484 | 29.9326 | 29.64 | 29.3379 | 29.0242 | 28.7284 | 28.4421 | 28.1737 | 27.9389 | 26.7474 | 25.7263 | 24.5274
|  | LARKHILL | CF |  |  |  | 32.4937 | 32.4095 | 32.3232 | 32.2326 | 32.1389 | 32.0411 | 31.9411 | 31.8432 | 31.7463 | 31.6495 | 31.16 | 30.4968 | 29.7705 | 29.9611 | 29.8 | 29.6326 | 29.4621 | 29.2853 | 29.1032 | 28.9221 | 28.7389 | 28.56 | 28.3811 | 27.4505 | 26.6989 | 25.8526 | 30.3989 | 30.3095 | 30.2179 | 30.1221 | 29.9779 | 29.8011 | 29.6253 | 29.4495 | 29.2758 | 29.1032 | 28.2074 | 27.4926 | 26.6958
COWLEY GSP | WITNEY BSP | LEAFIELD | MINIMUM HEADROOM | SP 30282 15270 | YES | 0 | 6.2253 | 6.1295 | 6.0337 | 5.8811 | 5.7095 | 5.5389 | 5.3716 | 5.2179 | 5.0768 | 4.9432 | 4.3274 | 3.6768 | -2.2474 | 5.1189 | 4.9453 | 4.7684 | 4.5821 | 4.3989 | 4.2179 | 4.04 | 3.8779 | 3.7263 | 3.5842 | 2.9179 | 2.1968 | 1.4726 | 5.2568 | 5.0716 | 4.8926 | 4.7032 | 4.5179 | 4.3347 | 4.1547 | 3.9895 | 3.8368 | 3.6926 | 3.0147 | 2.2789 | 1.5368
|  | LEAFIELD | EE |  |  |  | 6.2621 | 6.1874 | 6.1095 | 6.0253 | 5.9284 | 5.7884 | 5.6547 | 5.5274 | 5.4053 | 5.2884 | 4.8242 | 4.3495 | 3.8484 | 5.1621 | 5.0684 | 4.9284 | 4.7779 | 4.6358 | 4.4874 | 4.3453 | 4.2105 | 4.0811 | 3.9568 | 3.4558 | 2.9295 | 2.3632 | 5.34 | 5.1968 | 5.0547 | 4.9021 | 4.7589 | 4.6084 | 4.4642 | 4.3274 | 4.1968 | 4.0705 | 3.5621 | 3.0242 | 2.4442
|  | LEAFIELD | HT |  |  |  | 6.2253 | 6.1295 | 6.0337 | 5.8811 | 5.7095 | 5.5389 | 5.3716 | 5.2179 | 5.0768 | 4.9432 | 4.3274 | 3.6768 | 3.0305 | 5.1189 | 4.9453 | 4.7684 | 4.5821 | 4.3989 | 4.2179 | 4.04 | 3.8779 | 3.7263 | 3.5842 | 2.9179 | 2.1968 | 1.4726 | 5.2568 | 5.0716 | 4.8926 | 4.7032 | 4.5179 | 4.3347 | 4.1547 | 3.9895 | 3.8368 | 3.6926 | 3.0147 | 2.2789 | 1.5368
|  | LEAFIELD | HE |  |  |  | 6.3147 | 6.2653 | 6.2105 | 6.1505 | 6.0853 | 6.0168 | 5.9505 | 5.8884 | 5.8305 | 5.7747 | 5.4842 | 5.1684 | -2.2474 | 5.2221 | 5.1674 | 5.1084 | 5.0432 | 4.9505 | 4.8463 | 4.7463 | 4.6505 | 4.5621 | 4.4821 | 4.1726 | 3.8189 | 3.4158 | 5.4116 | 5.36 | 5.2747 | 5.1758 | 5.0779 | 4.9737 | 4.8716 | 4.7758 | 4.6863 | 4.6053 | 4.2905 | 3.9295 | 3.5158
|  | LEAFIELD | CF |  |  |  | 6.3453 | 6.3179 | 6.2905 | 6.2611 | 6.2316 | 6.2 | 6.1684 | 6.1379 | 6.1074 | 6.0768 | 5.9011 | 5.6958 | 5.4621 | 5.2568 | 5.2253 | 5.1947 | 5.1621 | 5.1284 | 5.0926 | 5.0347 | 4.9811 | 4.9263 | 4.8695 | 4.6042 | 4.3758 | 4.1095 | 5.4442 | 5.4147 | 5.3863 | 5.3474 | 5.2863 | 5.2253 | 5.1632 | 5.1084 | 5.0526 | 4.9947 | 4.7263 | 4.4916 | 4.2179
WILLESDEN GSP | ACTON LANE | LEAMINGTON PARK | MINIMUM HEADROOM | TQ 20539 81536 | NO | 0 | 50.6295 | 49.6674 | 47.9737 | 45.7189 | 44.1474 | 41.8084 | 40.7842 | 39.7684 | 38.7611 | 37.6095 | 34.6147 | 33.7916 | 20.8442 | 52.1726 | 50.9568 | 48.8474 | 46.1937 | 44.3495 | 41.5979 | 40.4011 | 39.2137 | 38.0358 | 36.6853 | 33.1947 | 32.2663 | 31.5547 | 49.6884 | 48.4916 | 46.4116 | 43.7653 | 41.9263 | 39.1832 | 37.9895 | 36.8053 | 35.6305 | 34.2853 | 30.8042 | 29.8768 | 29.1674
|  | LEAMINGTON PARK | EE |  |  |  | 50.7053 | 49.8126 | 48.2747 | 46.2537 | 44.9379 | 43.1063 | 42.3663 | 41.5642 | 40.5768 | 39.4137 | 36.5853 | 35.9747 | 35.5432 | 52.2674 | 51.1295 | 49.1926 | 46.8126 | 45.2674 | 43.1126 | 42.2495 | 41.3126 | 40.1558 | 38.7905 | 35.4853 | 34.7937 | 34.3053 | 49.7821 | 48.6621 | 46.7558 | 44.3821 | 42.8421 | 40.6937 | 39.8326 | 38.8989 | 37.7453 | 36.3842 | 33.0884 | 32.3979 | 31.9105
|  | LEAMINGTON PARK | HT |  |  |  | 50.6295 | 49.6674 | 47.9737 | 45.7189 | 44.1474 | 41.8084 | 40.7842 | 39.7684 | 38.7611 | 37.6095 | 34.6147 | 33.7916 | 33.1589 | 52.1726 | 50.9568 | 48.8474 | 46.1937 | 44.3495 | 41.5979 | 40.4011 | 39.2137 | 38.0358 | 36.6853 | 33.1947 | 32.2663 | 31.5547 | 49.6884 | 48.4916 | 46.4116 | 43.7653 | 41.9263 | 39.1832 | 37.9895 | 36.8053 | 35.6305 | 34.2853 | 30.8042 | 29.8768 | 29.1674
|  | LEAMINGTON PARK | HE |  |  |  | 50.7432 | 49.9095 | 48.4042 | 46.4116 | 45.1232 | 43.3032 | 42.5789 | 41.7758 | 40.8137 | 39.7105 | 37.0726 | 36.6232 | 20.8442 | 52.3474 | 51.2421 | 49.3368 | 46.9874 | 45.4726 | 43.3305 | 42.4853 | 41.5453 | 40.4158 | 39.1189 | 36.0253 | 35.5116 | 35.2042 | 49.8611 | 48.7737 | 46.8989 | 44.5568 | 43.0474 | 40.9116 | 40.0684 | 39.1305 | 38.0042 | 36.7116 | 33.6274 | 33.1147 | 32.8074
|  | LEAMINGTON PARK | CF |  |  |  | 50.7611 | 50.5526 | 49.8474 | 49.0368 | 48.5274 | 47.9137 | 47.7158 | 47.4632 | 47.1568 | 46.5316 | 43.3937 | 43.0526 | 42.8821 | 52.6453 | 52.0611 | 51.1621 | 50.1274 | 49.4842 | 48.7642 | 48.5358 | 48.2432 | 47.8863 | 47.1526 | 43.4674 | 43.0779 | 42.8842 | 50.1421 | 49.58 | 48.6947 | 47.6779 | 47.0442 | 46.3295 | 46.1011 | 45.8084 | 45.4537 | 44.7221 | 41.0474 | 40.6589 | 40.4653
MINETY GSP | STRATTON (2 X 60) | LECHLADE | MINIMUM HEADROOM | SP 22074 00496 | YES | 0.21158 | 9.88 | 9.7789 | 9.6768 | 9.5684 | 8.9895 | 7.9126 | 6.8621 | 5.5432 | 5.4011 | 5.2684 | 2.8905 | -0.45263 | -1.2663 | 7.8821 | 7.7474 | 7.6158 | 7.46 | 6.7832 | 5.5863 | 4.4095 | 2.8968 | 2.7663 | 2.6453 | 0.050526 | -3.6705 | -4.5274 | 8.1126 | 7.9768 | 7.8432 | 7.6853 | 6.9916 | 5.7537 | 4.5453 | 3.0221 | 2.8811 | 2.7474 | 0.070526 | -3.7453 | -4.64
|  | LECHLADE | EE |  |  |  | 9.9179 | 9.8379 | 9.7526 | 9.66 | 9.5653 | 9.4358 | 9.2316 | 9.0158 | 8.7989 | 8.5968 | 7.0989 | 3.6147 | 1.5832 | 7.9326 | 7.8326 | 7.7211 | 7.6063 | 7.4895 | 7.3105 | 7.1021 | 6.8884 | 6.6747 | 6.4768 | 5.0326 | 1.1958 | -1.0968 | 8.1632 | 8.0621 | 7.9505 | 7.8326 | 7.7147 | 7.5274 | 7.3053 | 7.0768 | 6.8484 | 6.6347 | 5.0042 | 1.0368 | -1.2979
|  | LECHLADE | HT |  |  |  | 9.88 | 9.7789 | 9.6768 | 9.5684 | 8.9895 | 7.9126 | 6.8621 | 5.5432 | 5.4011 | 5.2684 | 2.8905 | -0.45263 | -1.2663 | 7.8821 | 7.7474 | 7.6158 | 7.46 | 6.7832 | 5.5863 | 4.4095 | 2.8968 | 2.7663 | 2.6453 | 0.050526 | -3.6705 | -4.5274 | 8.1126 | 7.9768 | 7.8432 | 7.6853 | 6.9916 | 5.7537 | 4.5453 | 3.0221 | 2.8811 | 2.7474 | 0.070526 | -3.7453 | -4.64
|  | LECHLADE | HE |  |  |  | 9.9716 | 9.9189 | 9.8611 | 9.7958 | 9.7274 | 9.6284 | 9.5347 | 9.4421 | 9.3537 | 9.26 | 8.4916 | 6.0147 | -1.1726 | 7.9863 | 7.9337 | 7.8726 | 7.7926 | 7.7116 | 7.6 | 7.4958 | 7.3926 | 7.2653 | 7.1463 | 6.4305 | 3.6042 | 1.6842 | 8.2168 | 8.1642 | 8.1032 | 8.0232 | 7.9411 | 7.8242 | 7.7126 | 7.6042 | 7.4705 | 7.3442 | 6.5053 | 3.6411 | 1.6874
|  | LECHLADE | CF |  |  |  | 10.0032 | 9.9747 | 9.9453 | 9.9147 | 9.8811 | 9.8347 | 9.7895 | 9.7453 | 9.6989 | 9.6579 | 9.4011 | 8.0284 | 6.7737 | 8.0179 | 7.9895 | 7.96 | 7.9295 | 7.8895 | 7.8347 | 7.7811 | 7.7284 | 7.6716 | 7.6211 | 7.2779 | 5.7547 | 4.3611 | 8.2484 | 8.22 | 8.1905 | 8.16 | 8.12 | 8.0621 | 8.0042 | 7.9495 | 7.8905 | 7.8379 | 7.4779 | 5.8926 | 4.4432
BRAMLEY (ANDO-THAT) | THATCHAM BSP | LECKHAMPSTEAD | MINIMUM HEADROOM | SU 43962 77635 | YES | 0 | 8.1916 | 8.0989 | 8.0074 | 7.9095 | 7.8126 | 7.7137 | 7.6168 | 7.5295 | 7.4505 | 7.3768 | 7.0705 | 6.8242 | -0.86526 | 6.8042 | 6.6695 | 6.5358 | 6.3937 | 6.2547 | 6.1179 | 5.9821 | 5.8579 | 5.7432 | 5.6347 | 5.1579 | 4.7158 | 4.3147 | 7.1726 | 7.0295 | 6.8895 | 6.7453 | 6.6053 | 6.4663 | 6.3305 | 6.2063 | 6.0916 | 5.9832 | 5.5063 | 5.0653 | 4.6653
|  | LECKHAMPSTEAD | EE |  |  |  | 8.2305 | 8.16 | 8.0863 | 8.0095 | 7.9284 | 7.8484 | 7.7726 | 7.6989 | 7.6284 | 7.5663 | 7.3305 | 7.1579 | 7.02 | 6.8653 | 6.7632 | 6.6589 | 6.5526 | 6.4389 | 6.3305 | 6.2253 | 6.1242 | 6.0274 | 5.9379 | 5.5747 | 5.2642 | 4.9926 | 7.2389 | 7.1305 | 7.02 | 6.9074 | 6.7926 | 6.6821 | 6.5758 | 6.4737 | 6.3758 | 6.2863 | 5.9232 | 5.6126 | 5.3421
|  | LECKHAMPSTEAD | HT |  |  |  | 8.1916 | 8.0989 | 8.0074 | 7.9095 | 7.8126 | 7.7137 | 7.6168 | 7.5295 | 7.4505 | 7.3768 | 7.0705 | 6.8242 | 6.6179 | 6.8042 | 6.6695 | 6.5358 | 6.3937 | 6.2547 | 6.1179 | 5.9821 | 5.8579 | 5.7432 | 5.6347 | 5.1579 | 4.7158 | 4.3147 | 7.1726 | 7.0295 | 6.8895 | 6.7453 | 6.6053 | 6.4663 | 6.3305 | 6.2063 | 6.0916 | 5.9832 | 5.5063 | 5.0653 | 4.6653
|  | LECKHAMPSTEAD | HE |  |  |  | 8.2842 | 8.2389 | 8.1895 | 8.1368 | 8.0811 | 8.0221 | 7.9642 | 7.9105 | 7.8611 | 7.8168 | 7.6663 | 7.5684 | -0.86526 | 6.9484 | 6.8853 | 6.8189 | 6.7495 | 6.6779 | 6.6053 | 6.5326 | 6.4663 | 6.4032 | 6.3463 | 6.1337 | 5.9621 | 5.8189 | 7.3284 | 7.2611 | 7.1916 | 7.1189 | 7.0442 | 6.9674 | 6.8926 | 6.8232 | 6.7579 | 6.7 | 6.4853 | 6.3105 | 6.1674
|  | LECKHAMPSTEAD | CF |  |  |  | 8.3137 | 8.2884 | 8.2621 | 8.2368 | 8.2084 | 8.1811 | 8.1526 | 8.1253 | 8.0968 | 8.0695 | 7.9432 | 7.8695 | 7.8211 | 6.9916 | 6.9547 | 6.9168 | 6.8789 | 6.8389 | 6.7989 | 6.7589 | 6.72 | 6.68 | 6.6411 | 6.4579 | 6.3221 | 6.2105 | 7.3695 | 7.3347 | 7.2937 | 7.2537 | 7.2116 | 7.1695 | 7.1274 | 7.0853 | 7.0432 | 7.0021 | 6.8116 | 6.6726 | 6.5579
LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | LEE-ON-SOLENT | MINIMUM HEADROOM | SU 56858 00293 | YES | 0 | 27.1547 | 26.8305 | 26.4916 | 25.8232 | 24.9526 | 24.1284 | 23.0568 | 22.2695 | 21.5526 | 21.0863 | 18.6926 | 16.2537 | -1.1158 | 23.9253 | 23.0779 | 22.3705 | 21.6158 | 20.6558 | 19.7547 | 18.5611 | 17.6947 | 16.9063 | 16.4084 | 13.8074 | 11.1063 | 8.6537 | 24.4484 | 23.6242 | 22.9337 | 22.2095 | 21.2947 | 20.4305 | 19.2663 | 18.3989 | 17.6105 | 17.1095 | 14.4989 | 11.7863 | 9.3316
|  | LEE-ON-SOLENT | EE |  |  |  | 27.2821 | 27.0295 | 26.7632 | 26.4368 | 25.7105 | 24.9947 | 24.04 | 23.34 | 22.6842 | 22.2874 | 20.4484 | 18.5484 | 16.8832 | 24.2042 | 23.5032 | 22.9232 | 22.3084 | 21.4811 | 20.6947 | 19.6274 | 18.8547 | 18.1358 | 17.7137 | 15.7326 | 13.6347 | 11.7611 | 24.7211 | 24.04 | 23.4737 | 22.8737 | 22.0853 | 21.3337 | 20.3221 | 19.5568 | 18.8358 | 18.4126 | 16.4147 | 14.2979 | 12.4211
|  | LEE-ON-SOLENT | HT |  |  |  | 27.1547 | 26.8305 | 26.4916 | 25.8232 | 24.9526 | 24.1284 | 23.0568 | 22.2695 | 21.5526 | 21.0863 | 18.6926 | 16.2537 | 14.0653 | 23.9253 | 23.0779 | 22.3705 | 21.6158 | 20.6558 | 19.7547 | 18.5611 | 17.6947 | 16.9063 | 16.4084 | 13.8074 | 11.1063 | 8.6537 | 24.4484 | 23.6242 | 22.9337 | 22.2095 | 21.2947 | 20.4305 | 19.2663 | 18.3989 | 17.6105 | 17.1095 | 14.4989 | 11.7863 | 9.3316
|  | LEE-ON-SOLENT | HE |  |  |  | 27.4537 | 27.2842 | 27.0958 | 26.8874 | 26.6579 | 26.1032 | 25.2842 | 24.7168 | 24.1947 | 23.9316 | 22.7358 | 21.4526 | -1.1158 | 24.5768 | 24.0558 | 23.6442 | 23.1947 | 22.5389 | 21.9011 | 20.9789 | 20.3505 | 19.7747 | 19.4968 | 18.2053 | 16.7653 | 15.4821 | 25.0842 | 24.5789 | 24.1779 | 23.7389 | 23.1021 | 22.4916 | 21.6211 | 21.0221 | 20.4716 | 20.1989 | 18.9011 | 17.4568 | 16.1705
|  | LEE-ON-SOLENT | CF |  |  |  | 27.5516 | 27.4558 | 27.3558 | 27.2516 | 27.1442 | 27.0316 | 26.9158 | 26.7011 | 26.4095 | 26.2189 | 25.3284 | 24.4484 | 23.6832 | 24.7968 | 24.4958 | 24.2568 | 24.0042 | 23.6747 | 23.3537 | 22.9021 | 22.5579 | 22.2147 | 22.0105 | 21.0526 | 20.0663 | 19.1958 | 25.3 | 25.0074 | 24.7747 | 24.5284 | 24.2084 | 23.8958 | 23.46 | 23.1274 | 22.8021 | 22.6032 | 21.6779 | 20.7421 | 19.8916
LOVEDEAN GSP | HAVANT | LEIGH PARK | MINIMUM HEADROOM | SU 72144 07875 | YES | 0.81053 | 33.8737 | 33.6105 | 33.3442 | 33.0621 | 32.7663 | 32.4337 | 31.7779 | 31.22 | 30.7032 | 30.1421 | 27.2821 | 24.9021 | 0.42947 | 28.1074 | 27.8442 | 27.5547 | 26.78 | 25.9379 | 25.0874 | 24.3895 | 23.7979 | 23.2484 | 22.6463 | 19.5547 | 16.9747 | 13.6147 | 32.9789 | 32.7158 | 32.4242 | 31.6126 | 30.7316 | 29.84 | 29.1137 | 28.4979 | 27.9263 | 27.2979 | 24.0495 | 21.3347 | 17.7716
|  | LEIGH PARK | EE |  |  |  | 33.9621 | 33.7505 | 33.5253 | 33.2863 | 33.0326 | 32.7705 | 32.5137 | 32.1642 | 31.7747 | 31.3495 | 29.2084 | 27.4453 | 25.0274 | 28.9253 | 27.9842 | 27.7589 | 27.4579 | 26.6779 | 25.9084 | 25.3105 | 24.8095 | 24.4011 | 23.9505 | 21.6442 | 19.7326 | 17.0695 | 33.8505 | 32.8558 | 32.6305 | 32.3242 | 31.5053 | 30.6989 | 30.0758 | 29.5558 | 29.1347 | 28.6663 | 26.2484 | 24.2379 | 21.4084
|  | LEIGH PARK | HT |  |  |  | 33.8737 | 33.6105 | 33.3442 | 33.0621 | 32.7663 | 32.4337 | 31.7779 | 31.22 | 30.7032 | 30.1421 | 27.2821 | 24.9021 | 21.8432 | 28.1074 | 27.8442 | 27.5547 | 26.78 | 25.9379 | 25.0874 | 24.3895 | 23.7979 | 23.2484 | 22.6463 | 19.5547 | 16.9747 | 13.6147 | 32.9789 | 32.7158 | 32.4242 | 31.6126 | 30.7316 | 29.84 | 29.1137 | 28.4979 | 27.9263 | 27.2979 | 24.0495 | 21.3347 | 17.7716
|  | LEIGH PARK | HE |  |  |  | 34.0853 | 33.9295 | 33.7568 | 33.5642 | 33.36 | 33.1411 | 32.9305 | 32.7326 | 32.5484 | 32.3895 | 31.0158 | 29.7968 | 0.42947 | 29.2105 | 28.1632 | 27.9905 | 27.7979 | 27.4558 | 26.7937 | 26.3116 | 25.9253 | 25.6337 | 25.2905 | 23.5726 | 22.2432 | 20.1411 | 33.9737 | 33.0347 | 32.8621 | 32.6695 | 32.3168 | 31.6211 | 31.1189 | 30.7189 | 30.42 | 30.0632 | 28.2589 | 26.8558 | 24.6137
|  | LEIGH PARK | CF |  |  |  | 34.1621 | 34.0674 | 33.9684 | 33.8653 | 33.7589 | 33.6505 | 33.5368 | 33.4274 | 33.3179 | 33.2084 | 32.7232 | 32.2516 | 31.0737 | 29.3568 | 29.1863 | 28.2021 | 28.0989 | 27.9926 | 27.8842 | 27.7705 | 27.6611 | 27.4116 | 27.0979 | 25.7421 | 24.8821 | 23.5758 | 34.0505 | 33.9558 | 33.0737 | 32.9705 | 32.8642 | 32.7558 | 32.6421 | 32.5326 | 32.2726 | 31.9442 | 30.5232 | 29.6179 | 28.2263
BRAMLEY (FLEE) | READING BSP | LITTLE HUNGERFORD | MINIMUM HEADROOM | SU 75372 72019 | YES | 1.0305 | 45.0147 | 44.3758 | 43.7305 | 43.0453 | 42.3411 | 40.8474 | 39.3663 | 37.9958 | 36.7547 | 35.6232 | 30.8168 | 26.3737 | -9.9895 | 37.9295 | 36.5621 | 35.1968 | 33.6684 | 32.1432 | 30.3558 | 28.7389 | 27.2368 | 25.8758 | 24.6379 | 19.3558 | 14.4011 | 9.6832 | 39.8053 | 38.4642 | 37.1253 | 35.6274 | 34.1316 | 32.3811 | 30.7979 | 29.3253 | 27.9937 | 26.78 | 21.5326 | 16.5737 | 11.8547
|  | LITTLE HUNGERFORD | EE |  |  |  | 45.2663 | 44.7695 | 44.2432 | 43.6832 | 43.1011 | 42.4989 | 41.5589 | 40.4284 | 39.4789 | 38.62 | 35.2611 | 32.1411 | 29.2316 | 38.4874 | 37.4937 | 36.4495 | 35.2126 | 33.9621 | 32.4779 | 31.1389 | 29.9042 | 28.88 | 27.9505 | 24.2958 | 20.8189 | 17.5347 | 40.3516 | 39.3768 | 38.3505 | 37.1389 | 35.9116 | 34.4579 | 33.1484 | 31.9379 | 30.9305 | 30.0179 | 26.4316 | 22.9916 | 19.7053
|  | LITTLE HUNGERFORD | HT |  |  |  | 45.0147 | 44.3758 | 43.7305 | 43.0453 | 42.3411 | 40.8474 | 39.3663 | 37.9958 | 36.7547 | 35.6232 | 30.8168 | 26.3737 | 22.1842 | 37.9295 | 36.5621 | 35.1968 | 33.6684 | 32.1432 | 30.3558 | 28.7389 | 27.2368 | 25.8758 | 24.6379 | 19.3558 | 14.4011 | 9.6832 | 39.8053 | 38.4642 | 37.1253 | 35.6274 | 34.1316 | 32.3811 | 30.7979 | 29.3253 | 27.9937 | 26.78 | 21.5326 | 16.5737 | 11.8547
|  | LITTLE HUNGERFORD | HE |  |  |  | 45.6158 | 45.2853 | 44.92 | 44.5158 | 44.0821 | 43.6179 | 43.1737 | 42.7558 | 42.3653 | 41.88 | 39.6832 | 37.6432 | -9.9895 | 39.2211 | 38.6116 | 37.9168 | 37.0116 | 36.0811 | 34.8916 | 33.8453 | 32.8916 | 32.1684 | 31.4989 | 29.1105 | 26.8232 | 24.6389 | 40.8705 | 40.4726 | 39.7895 | 38.9032 | 37.9895 | 36.8274 | 35.8011 | 34.8674 | 34.1568 | 33.4979 | 31.1547 | 28.9253 | 26.8053
|  | LITTLE HUNGERFORD | CF |  |  |  | 45.8147 | 45.6316 | 45.4432 | 45.2463 | 45.0432 | 44.8316 | 44.6168 | 44.4053 | 44.1958 | 43.9874 | 43.0547 | 41.9558 | 41.0737 | 39.42 | 39.2368 | 39.0053 | 38.4884 | 37.9316 | 37.26 | 36.5705 | 35.9474 | 35.4011 | 34.8905 | 32.7421 | 31.4884 | 30.4937 | 41.0695 | 40.8863 | 40.6947 | 40.3516 | 39.8084 | 39.1537 | 38.4811 | 37.8716 | 37.3368 | 36.8379 | 34.7337 | 33.5074 | 32.5389
COWLEY GSP | HIGH WYCOMBE BSP | LITTLE MARLOW | MINIMUM HEADROOM | SU 86037 87794 | YES | 0.75158 | 35.0568 | 34.7442 | 34.4284 | 34.0926 | 33.7463 | 33.3895 | 33.0305 | 32.7168 | 32.4305 | 32.1674 | 30.7368 | 28.7063 | -2.4484 | 33.98 | 33.6516 | 33.3147 | 32.9589 | 32.5905 | 32.2126 | 31.6705 | 31.1105 | 30.5453 | 30.0042 | 27.5105 | 25.2737 | 23.2442 | 34.5726 | 34.26 | 33.9442 | 33.6084 | 33.2621 | 32.9053 | 32.3411 | 31.7842 | 31.2232 | 30.6853 | 28.2137 | 25.9979 | 23.9895
|  | LITTLE MARLOW | EE |  |  |  | 35.1779 | 34.9337 | 34.6747 | 34.3989 | 34.1116 | 33.8147 | 33.5295 | 33.2579 | 32.9968 | 32.7653 | 31.9232 | 30.8716 | 29.5053 | 34.1095 | 33.8537 | 33.5779 | 33.2842 | 32.9789 | 32.6632 | 32.3684 | 32.0863 | 31.7411 | 31.2884 | 29.3221 | 27.6253 | 26.1011 | 34.6937 | 34.4495 | 34.1905 | 33.9147 | 33.6274 | 33.3305 | 33.0453 | 32.7737 | 32.4095 | 31.96 | 30.0105 | 28.3305 | 26.8221
|  | LITTLE MARLOW | HT |  |  |  | 35.0568 | 34.7442 | 34.4284 | 34.0926 | 33.7463 | 33.3895 | 33.0305 | 32.7168 | 32.4305 | 32.1674 | 30.7368 | 28.7063 | 26.8758 | 33.98 | 33.6516 | 33.3147 | 32.9589 | 32.5905 | 32.2126 | 31.6705 | 31.1105 | 30.5453 | 30.0042 | 27.5105 | 25.2737 | 23.2442 | 34.5726 | 34.26 | 33.9442 | 33.6084 | 33.2621 | 32.9053 | 32.3411 | 31.7842 | 31.2232 | 30.6853 | 28.2137 | 25.9979 | 23.9895
|  | LITTLE MARLOW | HE |  |  |  | 35.3442 | 35.1779 | 34.9947 | 34.7916 | 34.5737 | 34.3411 | 34.1179 | 33.9084 | 33.7126 | 33.5442 | 32.9768 | 32.6463 | -2.4484 | 34.2874 | 34.1137 | 33.9189 | 33.7042 | 33.4726 | 33.2253 | 32.9968 | 32.7811 | 32.5768 | 32.3989 | 31.66 | 30.56 | 29.6042 | 34.86 | 34.6937 | 34.5105 | 34.3074 | 34.0895 | 33.8568 | 33.6337 | 33.4242 | 33.2284 | 33.06 | 32.3284 | 31.2411 | 30.2968
|  | LITTLE MARLOW | CF |  |  |  | 35.4379 | 35.3432 | 35.2453 | 35.1432 | 35.0379 | 34.9284 | 34.8179 | 34.7084 | 34.6 | 34.4916 | 34.0095 | 33.7695 | 33.6379 | 34.3863 | 34.2863 | 34.1811 | 34.0716 | 33.9579 | 33.84 | 33.7253 | 33.6105 | 33.4958 | 33.3811 | 32.8653 | 32.5916 | 31.9442 | 34.9537 | 34.8589 | 34.7611 | 34.6589 | 34.5537 | 34.4442 | 34.3337 | 34.2242 | 34.1158 | 34.0074 | 33.5253 | 33.2853 | 32.6189
NURSLING GSP | ROWNHAMS | LORDSHILL | MINIMUM HEADROOM | SU 38746 16055 | YES | 0.31263 | 32.8116 | 32.6368 | 32.46 | 32.4305 | 32.4989 | 32.4537 | 32.1242 | 31.8263 | 31.5432 | 31.2495 | 29.6253 | 27.9958 | 10.4653 | 30.2189 | 29.8747 | 29.5347 | 29.2895 | 28.9063 | 28.5537 | 28.2032 | 27.8853 | 27.5789 | 27.2611 | 25.4642 | 23.6347 | 21.9 | 30.7811 | 30.6063 | 30.3105 | 29.9832 | 29.6011 | 29.2484 | 28.8968 | 28.5789 | 28.2747 | 27.9558 | 26.1589 | 24.3295 | 22.5968
|  | LORDSHILL | EE |  |  |  | 32.8737 | 32.7347 | 32.5874 | 32.4305 | 33.1905 | 32.8758 | 32.5589 | 32.3032 | 32.0463 | 31.8168 | 30.6263 | 29.3484 | 28.1663 | 30.3368 | 30.1011 | 29.8274 | 29.5189 | 29.2137 | 29.0116 | 28.6695 | 28.3947 | 28.1221 | 27.8779 | 26.5695 | 25.1326 | 23.7895 | 30.8432 | 30.7042 | 30.5568 | 30.2937 | 30.0463 | 29.7063 | 29.3632 | 29.0905 | 28.8158 | 28.5705 | 27.2621 | 25.8242 | 24.4821
|  | LORDSHILL | HT |  |  |  | 32.8116 | 32.6368 | 32.46 | 33.1379 | 32.7842 | 32.4537 | 32.1242 | 31.8263 | 31.5432 | 31.2495 | 29.6253 | 27.9958 | 26.4642 | 30.2189 | 29.8747 | 29.5347 | 29.2895 | 28.9063 | 28.5537 | 28.2032 | 27.8853 | 27.5789 | 27.2611 | 25.4642 | 23.6347 | 21.9 | 30.7811 | 30.6063 | 30.3105 | 29.9832 | 29.6011 | 29.2484 | 28.8968 | 28.5789 | 28.2747 | 27.9558 | 26.1589 | 24.3295 | 22.5968
|  | LORDSHILL | HE |  |  |  | 32.96 | 32.86 | 32.7505 | 32.6295 | 32.4989 | 33.4505 | 33.2053 | 33.0232 | 32.8463 | 32.6895 | 31.9411 | 31.0358 | 10.4653 | 30.4284 | 30.3253 | 30.2126 | 29.9895 | 29.7663 | 29.6411 | 29.3758 | 29.1853 | 28.9979 | 28.8305 | 28.0126 | 26.9853 | 26.0032 | 30.9295 | 30.8295 | 30.72 | 30.5989 | 30.4684 | 30.3347 | 30.0705 | 29.8779 | 29.6905 | 29.5242 | 28.7063 | 27.68 | 26.6979
|  | LORDSHILL | CF |  |  |  | 33.0095 | 32.9495 | 32.8874 | 32.8242 | 32.7568 | 32.6884 | 33.8168 | 33.6947 | 33.5768 | 33.4568 | 32.8705 | 32.2758 | 31.7053 | 30.48 | 30.4168 | 30.3526 | 30.2863 | 30.1737 | 30.0295 | 30.0263 | 29.8947 | 29.7684 | 29.6411 | 29.0042 | 28.3326 | 27.6768 | 30.9789 | 30.9189 | 30.8568 | 30.7937 | 30.7263 | 30.6579 | 30.72 | 30.5884 | 30.4621 | 30.3337 | 29.6979 | 29.0263 | 28.3705
BRAMLEY (ANDO-THAT) | THATCHAM BSP | LOVE LANE | MINIMUM HEADROOM | SU 47334 68495 | YES | 0 | 47.1421 | 46.86 | 46.5758 | 46.2737 | 45.9611 | 45.6379 | 45.3126 | 45.0274 | 44.7663 | 44.5242 | 42.7358 | 40.7884 | -30.1074 | 41.2705 | 40.5126 | 39.7863 | 38.7779 | 37.7326 | 37.1884 | 36.6411 | 36.1411 | 35.6768 | 35.24 | 33.2716 | 31.1095 | 28.9958 | 42.2842 | 41.9747 | 41.3442 | 40.3463 | 39.3032 | 38.7579 | 38.2116 | 37.7126 | 37.2484 | 36.8126 | 34.8453 | 32.6863 | 30.5758
|  | LOVE LANE | EE |  |  |  | 47.2474 | 47.0253 | 46.7905 | 48.3611 | 47.5221 | 47.1021 | 46.6958 | 46.3011 | 45.9263 | 45.5832 | 44.1768 | 42.6989 | 41.2779 | 41.4305 | 40.8789 | 40.2621 | 39.3611 | 38.42 | 37.9747 | 37.5421 | 37.1221 | 36.7232 | 36.3568 | 34.8411 | 33.1958 | 31.5926 | 42.3979 | 42.1516 | 41.8011 | 40.9295 | 39.9895 | 39.5442 | 39.1126 | 38.6926 | 38.2937 | 37.9274 | 36.4126 | 34.7705 | 33.1684
|  | LOVE LANE | HT |  |  |  | 47.1421 | 46.86 | 46.5758 | 46.2737 | 45.9611 | 45.6379 | 45.3126 | 45.0274 | 44.7663 | 44.5242 | 42.7358 | 40.7884 | 38.9042 | 41.2705 | 40.5126 | 39.7863 | 38.7779 | 37.7326 | 37.1884 | 36.6411 | 36.1411 | 35.6768 | 35.24 | 33.2716 | 31.1095 | 28.9958 | 42.2842 | 41.9747 | 41.3442 | 40.3463 | 39.3032 | 38.7579 | 38.2116 | 37.7126 | 37.2484 | 36.8126 | 34.8453 | 32.6863 | 30.5758
|  | LOVE LANE | HE |  |  |  | 47.3926 | 47.2389 | 47.0684 | 46.88 | 46.6779 | 46.4621 | 46.2558 | 46.0611 | 45.88 | 45.7232 | 45.1937 | 44.8821 | -30.1074 | 41.5989 | 41.3621 | 40.8947 | 40.1358 | 39.3305 | 39.0084 | 38.7021 | 38.4042 | 38.1305 | 37.8853 | 36.9716 | 35.9 | 34.8421 | 42.5537 | 42.3811 | 42.1926 | 41.6905 | 40.8989 | 40.5768 | 40.2705 | 39.9726 | 39.7 | 39.4547 | 38.5421 | 37.4716 | 36.4158
|  | LOVE LANE | CF |  |  |  | 47.4768 | 47.3874 | 47.2958 | 47.1989 | 47.1 | 46.9968 | 46.8926 | 46.7895 | 46.6874 | 46.5853 | 46.1305 | 45.9032 | 45.7779 | 41.7095 | 41.5958 | 41.4832 | 41.2158 | 40.8305 | 40.6442 | 40.4568 | 40.2705 | 40.0884 | 39.9074 | 39.0621 | 38.3168 | 37.5758 | 42.6495 | 42.5495 | 42.4474 | 42.3347 | 42.2189 | 42.1116 | 41.9884 | 41.8084 | 41.6316 | 41.4568 | 40.6295 | 39.8853 | 39.1463
COWLEY GSP | YARNTON BSP | LOVELACE ROAD | MINIMUM HEADROOM | SP 50395 10376 | YES | 0 | 13.2842 | 13.1453 | 30.9084 | 30.66 | 30.4158 | 30.1716 | 28.8579 | 28.6189 | 28.4042 | 28.2074 | 27.3211 | 26.5853 | 17.6189 | 11.9842 | 11.4063 | 29.1474 | 28.88 | 28.62 | 28.36 | 26.8389 | 26.5811 | 26.3516 | 26.14 | 25.1811 | 24.3811 | 23.6653 | 11.6316 | 11.0537 | 28.7947 | 28.5274 | 28.2663 | 28.0063 | 26.4853 | 26.2274 | 25.9979 | 25.7863 | 24.8274 | 24.0263 | 23.3116
|  | LOVELACE ROAD | EE |  |  |  | 13.3368 | 13.2305 | 31.1168 | 30.9242 | 30.7263 | 30.5284 | 29.6811 | 29.2116 | 28.9074 | 28.7368 | 28.0547 | 27.5179 | 27.0558 | 12.1032 | 11.5905 | 29.3821 | 29.1695 | 28.9579 | 28.7484 | 27.7705 | 27.2389 | 26.9011 | 26.7179 | 25.9811 | 25.3947 | 24.8853 | 11.7505 | 11.2379 | 29.0295 | 28.8158 | 28.6053 | 28.3958 | 27.4168 | 26.8853 | 26.5474 | 26.3642 | 25.6274 | 25.0411 | 24.5316
|  | LOVELACE ROAD | HT |  |  |  | 13.2842 | 13.1453 | 30.9084 | 30.66 | 30.4158 | 30.1716 | 28.8579 | 28.6189 | 28.4042 | 28.2074 | 27.3211 | 26.5853 | 25.9347 | 11.9842 | 11.4063 | 29.1474 | 28.88 | 28.62 | 28.36 | 26.8389 | 26.5811 | 26.3516 | 26.14 | 25.1811 | 24.3811 | 23.6653 | 11.6316 | 11.0537 | 28.7947 | 28.5274 | 28.2663 | 28.0063 | 26.4853 | 26.2274 | 25.9979 | 25.7863 | 24.8274 | 24.0263 | 23.3116
|  | LOVELACE ROAD | HE |  |  |  | 13.4063 | 13.3326 | 31.2495 | 31.1589 | 31.0611 | 30.9568 | 30.1705 | 29.7453 | 29.5253 | 29.4126 | 28.9968 | 28.7084 | 17.6189 | 12.26 | 11.8232 | 29.6853 | 29.5411 | 29.3947 | 29.2453 | 28.3042 | 27.82 | 27.5758 | 27.4568 | 27.0116 | 26.6989 | 26.4547 | 11.9084 | 11.4695 | 29.3326 | 29.1874 | 29.0421 | 28.8926 | 27.9516 | 27.4663 | 27.2221 | 27.1042 | 26.6589 | 26.3463 | 26.1011
|  | LOVELACE ROAD | CF |  |  |  | 13.4463 | 13.4032 | 31.3579 | 31.3105 | 31.2621 | 31.2116 | 31.1611 | 31.1105 | 31.06 | 30.8968 | 30.1084 | 29.8526 | 29.6663 | 12.3295 | 12.0937 | 30.0105 | 29.9242 | 29.8379 | 29.7484 | 29.6579 | 29.5295 | 29.3347 | 29.1337 | 28.2432 | 27.9621 | 27.7526 | 11.9821 | 11.7411 | 29.6568 | 29.5716 | 29.4853 | 29.3958 | 29.3042 | 29.1768 | 28.9821 | 28.7811 | 27.8895 | 27.6095 | 27.4
MANNINGTON GSP | ARNEWOOD | LYMINGTON | MINIMUM HEADROOM | SZ 31720 96856 | YES | 0.38526 | 35.2 | 34.6168 | 33.8389 | 32.9168 | 31.8505 | 30.8221 | 29.7442 | 29.0768 | 28.4558 | 27.8768 | 25.0389 | 22.1116 | -4.0337 | 29.4421 | 28.6516 | 27.8211 | 26.8284 | 25.6726 | 24.5642 | 23.4 | 22.6968 | 22.0421 | 21.4305 | 18.3968 | 15.1579 | 12.0474 | 30.1579 | 29.4495 | 28.7074 | 27.8095 | 26.6316 | 25.5021 | 24.3147 | 23.6011 | 22.9358 | 22.3137 | 19.22 | 15.9579 | 12.8411
|  | LYMINGTON | EE |  |  |  | 35.3589 | 35.0421 | 34.5211 | 33.8368 | 32.9863 | 32.0653 | 31.0526 | 30.3947 | 29.8063 | 29.3105 | 27.1095 | 24.8516 | 22.7621 | 29.7958 | 29.1895 | 28.5537 | 27.8232 | 27.0537 | 26.0379 | 24.9105 | 24.2021 | 23.5716 | 23.0453 | 20.6684 | 18.1632 | 15.8042 | 30.4705 | 29.9253 | 29.3537 | 28.7021 | 27.8853 | 26.8695 | 25.74 | 25.0284 | 24.3958 | 23.8663 | 21.4747 | 18.9516 | 16.5874
|  | LYMINGTON | HT |  |  |  | 35.2 | 34.6168 | 33.8389 | 32.9168 | 31.8505 | 30.8221 | 29.7442 | 29.0768 | 28.4558 | 27.8768 | 25.0389 | 22.1116 | 19.3442 | 29.4421 | 28.6516 | 27.8211 | 26.8284 | 25.6726 | 24.5642 | 23.4 | 22.6968 | 22.0421 | 21.4305 | 18.3968 | 15.1579 | 12.0474 | 30.1579 | 29.4495 | 28.7074 | 27.8095 | 26.6316 | 25.5021 | 24.3147 | 23.6011 | 22.9358 | 22.3137 | 19.22 | 15.9579 | 12.8411
|  | LYMINGTON | HE |  |  |  | 35.5747 | 35.3611 | 35.1253 | 34.8642 | 34.1968 | 33.4453 | 32.5926 | 32.1011 | 31.6968 | 31.3695 | 29.9611 | 28.4526 | -4.0337 | 30.2642 | 29.8811 | 29.46 | 28.9253 | 28.3716 | 27.5411 | 26.5884 | 26.0568 | 25.6274 | 25.2811 | 23.7632 | 22.0674 | 20.4474 | 30.8853 | 30.5379 | 30.1558 | 29.68 | 29.2042 | 28.3726 | 27.4189 | 26.8884 | 26.4558 | 26.1095 | 24.5842 | 22.8832 | 21.2579
|  | LYMINGTON | CF |  |  |  | 35.7011 | 35.5811 | 35.4579 | 35.3284 | 35.1958 | 35.0568 | 34.7832 | 34.5211 | 34.2084 | 33.8905 | 32.4716 | 31.4768 | 30.5232 | 30.5011 | 30.2684 | 30.0389 | 29.8 | 29.5168 | 29.1789 | 28.8232 | 28.5453 | 28.2074 | 27.8642 | 26.3316 | 25.2411 | 24.1779 | 31.0989 | 30.8905 | 30.6832 | 30.4674 | 30.2158 | 29.9189 | 29.6095 | 29.36 | 29.0642 | 28.7632 | 27.2958 | 26.1779 | 25.0842
MELKSHAM GSP | CHIPPENHAM | LYNEHAM | MINIMUM HEADROOM | ST 99348 80481 | YES | 0 | 13.6526 | 13.7411 | 32.9968 | 32.4979 | 32.2211 | 31.3611 | 30.1326 | 28.6116 | 28.3937 | 28.18 | 25.2221 | 21.1958 | 15.5537 | 10.8389 | 10.2684 | 29.2179 | 28.6611 | 28.3642 | 27.4116 | 26.0263 | 24.2947 | 24.0979 | 23.9074 | 20.7695 | 16.3926 | 15.3053 | 11.3589 | 10.8526 | 29.8021 | 29.2442 | 28.9474 | 27.9789 | 26.5779 | 24.8284 | 24.6105 | 24.3958 | 21.1084 | 16.5589 | 15.4032
|  | LYNEHAM | EE |  |  |  | 13.6526 | 14.3116 | 33.3684 | 32.9074 | 32.4053 | 32.1211 | 31.8137 | 31.5074 | 31.2 | 30.8979 | 29.1547 | 25.0137 | 22.6179 | 10.8968 | 10.6305 | 29.6347 | 29.1189 | 28.5547 | 28.2726 | 27.9768 | 27.6832 | 27.3905 | 27.1074 | 25.4832 | 21.0684 | 18.4116 | 11.3589 | 11.2147 | 30.2179 | 29.7 | 29.1347 | 28.8358 | 28.5158 | 28.1958 | 27.8747 | 27.5589 | 25.72 | 21.0621 | 18.3316
|  | LYNEHAM | HT |  |  |  | 14.4968 | 13.9895 | 32.9968 | 32.4979 | 32.2211 | 31.3611 | 30.1326 | 28.6116 | 28.3937 | 28.18 | 25.2221 | 21.1958 | 20.1295 | 10.8389 | 10.2684 | 29.2179 | 28.6611 | 28.3642 | 27.4116 | 26.0263 | 24.2947 | 24.0979 | 23.9074 | 20.7695 | 16.3926 | 15.3053 | 11.4232 | 10.8526 | 29.8021 | 29.2442 | 28.9474 | 27.9789 | 26.5779 | 24.8284 | 24.6105 | 24.3958 | 21.1084 | 16.5589 | 15.4032
|  | LYNEHAM | HE |  |  |  | 13.7347 | 14.5526 | 33.7705 | 33.4853 | 33.1611 | 32.7537 | 32.3589 | 32.1653 | 31.9779 | 31.8095 | 30.8284 | 28.6137 | 15.5537 | 11.0726 | 10.8937 | 30.0768 | 29.7589 | 29.3958 | 28.9568 | 28.5295 | 28.3411 | 28.1579 | 27.9958 | 27.0368 | 24.5737 | 22.3684 | 11.4463 | 11.4768 | 30.6611 | 30.3421 | 29.9789 | 29.5284 | 29.0895 | 28.8895 | 28.6926 | 28.5168 | 27.4684 | 24.94 | 22.6747
|  | LYNEHAM | CF |  |  |  | 13.7832 | 13.7411 | 34.1558 | 34.0137 | 33.8621 | 33.6653 | 33.4558 | 33.2453 | 33.1421 | 33.0421 | 32.5432 | 31.4705 | 30.0158 | 11.1495 | 11.0347 | 30.5074 | 30.3484 | 30.1779 | 29.9663 | 29.7368 | 29.5105 | 29.4063 | 29.3042 | 28.8032 | 27.6242 | 25.9926 | 11.4989 | 11.4505 | 31.0905 | 30.9326 | 30.7621 | 30.5442 | 30.3095 | 30.0758 | 29.9663 | 29.86 | 29.3305 | 28.1137 | 26.4432
BRAMLEY (FLEE) | BRACKNELL | M V E E | MINIMUM HEADROOM | SU 98120 65945 | YES | 0.21053 | 29.78 | 29.6947 | 29.6116 | 29.5189 | 29.4316 | 29.3411 | 29.2411 | 29.1337 | 29.0642 | 28.0484 | 27.7242 | 27.3474 | 23.8284 | 29.7168 | 29.6179 | 29.5221 | 29.4211 | 29.3274 | 29.2295 | 29.1211 | 29.0021 | 28.9274 | 27.7147 | 27.3611 | 26.94 | 26.7947 | 29.6947 | 29.5968 | 29.5032 | 29.4042 | 29.3116 | 29.2137 | 29.1053 | 28.9853 | 28.9116 | 27.7011 | 27.3474 | 26.9274 | 26.7821
|  | M V E E | EE |  |  |  | 29.8179 | 29.7537 | 29.6874 | 29.6474 | 29.5789 | 29.5095 | 29.4326 | 29.36 | 29.2895 | 29.2253 | 28.7274 | 28.3842 | 28.1611 | 29.7611 | 29.6874 | 29.6105 | 29.5316 | 29.4589 | 29.3853 | 29.3021 | 29.2253 | 29.1484 | 29.0789 | 28.5158 | 28.1263 | 27.8747 | 29.7379 | 29.6653 | 29.5905 | 29.5158 | 29.4421 | 29.3684 | 29.2863 | 29.2084 | 29.1326 | 29.0632 | 28.5 | 28.1116 | 27.86
|  | M V E E | HT |  |  |  | 29.78 | 29.6947 | 29.6116 | 29.5189 | 29.4316 | 29.3411 | 29.2411 | 29.1337 | 29.0642 | 28.0484 | 27.7242 | 27.3474 | 27.2105 | 29.7168 | 29.6179 | 29.5221 | 29.4211 | 29.3274 | 29.2295 | 29.1211 | 29.0021 | 28.9274 | 27.7147 | 27.3611 | 26.94 | 26.7947 | 29.6947 | 29.5968 | 29.5032 | 29.4042 | 29.3116 | 29.2137 | 29.1053 | 28.9853 | 28.9116 | 27.7011 | 27.3474 | 26.9274 | 26.7821
|  | M V E E | HE |  |  |  | 29.8663 | 29.8295 | 29.7863 | 29.7411 | 29.6958 | 29.6495 | 29.5968 | 29.5474 | 29.4979 | 29.4526 | 28.9674 | 28.7158 | 23.8284 | 29.8211 | 29.7758 | 29.7274 | 29.6747 | 29.6263 | 29.5747 | 29.5147 | 29.4579 | 29.4042 | 29.3547 | 28.7863 | 28.4916 | 28.2968 | 29.7979 | 29.7526 | 29.7042 | 29.6526 | 29.6042 | 29.5537 | 29.4947 | 29.4389 | 29.3863 | 29.3379 | 28.7705 | 28.4768 | 28.2821
|  | M V E E | CF |  |  |  | 29.8895 | 29.8684 | 29.8463 | 29.8221 | 29.7979 | 29.7726 | 29.7442 | 29.7158 | 29.6863 | 29.6579 | 29.5137 | 29.4084 | 29.3232 | 29.8516 | 29.8232 | 29.7947 | 29.7663 | 29.7379 | 29.7095 | 29.6758 | 29.6421 | 29.6074 | 29.5737 | 29.4105 | 29.2905 | 29.1916 | 29.8274 | 29.8 | 29.7705 | 29.7432 | 29.7158 | 29.6874 | 29.6537 | 29.6211 | 29.5874 | 29.5547 | 29.3947 | 29.2747 | 29.1747
CHICKERELL GSP | CHICKERELL BSP | MAIDEN NEWTON | MINIMUM HEADROOM | SY 59138 97747 | YES | 0.13158 | 11.5432 | 11.3684 | 11.1947 | 11.0189 | 10.8463 | 10.6747 | 10.5042 | 10.3495 | 10.2063 | 10.0726 | 9.4789 | 5.9558 | 1.3895 | 9.9453 | 9.7568 | 9.5695 | 9.3811 | 9.1968 | 9.0137 | 8.8337 | 8.6684 | 8.5147 | 8.3716 | 7.7326 | 3.5621 | 3.4347 | 10.2621 | 10.0737 | 9.8863 | 9.6979 | 9.5137 | 9.3305 | 9.1505 | 8.9842 | 8.8316 | 8.6884 | 8.0474 | 3.8768 | 3.7484
|  | MAIDEN NEWTON | EE |  |  |  | 11.6189 | 11.4842 | 11.3432 | 11.2032 | 11.0611 | 10.9211 | 10.7853 | 10.6568 | 10.5316 | 10.4189 | 9.9579 | 5.9558 | 5.8274 | 10.0284 | 9.8832 | 9.7326 | 9.5832 | 9.4326 | 9.2832 | 9.14 | 9.0032 | 8.8705 | 8.7505 | 8.2526 | 3.5621 | 3.4347 | 10.2779 | 10.2 | 10.0495 | 9.8989 | 9.7484 | 9.5989 | 9.4558 | 9.3189 | 9.1863 | 9.0663 | 8.5695 | 3.8768 | 3.7484
|  | MAIDEN NEWTON | HT |  |  |  | 11.5432 | 11.3684 | 11.1947 | 11.0189 | 10.8463 | 10.6747 | 10.5042 | 10.3495 | 10.2063 | 10.0726 | 9.4789 | 8.9137 | 8.3821 | 9.9453 | 9.7568 | 9.5695 | 9.3811 | 9.1968 | 9.0137 | 8.8337 | 8.6684 | 8.5147 | 8.3716 | 7.7326 | 7.1095 | 6.5168 | 10.2621 | 10.0737 | 9.8863 | 9.6979 | 9.5137 | 9.3305 | 9.1505 | 8.9842 | 8.8316 | 8.6884 | 8.0474 | 7.4242 | 6.8316
|  | MAIDEN NEWTON | HE |  |  |  | 11.7253 | 11.6411 | 11.5505 | 11.4568 | 11.36 | 11.26 | 11.1642 | 11.0758 | 10.9916 | 10.9168 | 10.6411 | 6.3663 | 1.3895 | 10.1453 | 10.0547 | 9.9579 | 9.8589 | 9.7568 | 9.6526 | 9.5516 | 9.4579 | 9.3695 | 9.2916 | 8.9979 | 3.9726 | 3.9116 | 10.3895 | 10.3716 | 10.2747 | 10.1758 | 10.0737 | 9.9695 | 9.8684 | 9.7747 | 9.6863 | 9.6084 | 9.3147 | 4.2874 | 4.2263
|  | MAIDEN NEWTON | CF |  |  |  | 11.78 | 11.7295 | 11.6747 | 11.6221 | 11.5684 | 11.5137 | 11.4579 | 11.4021 | 11.3474 | 11.2947 | 11.0463 | 10.8558 | 10.6884 | 10.2042 | 10.1495 | 10.0905 | 10.0337 | 9.9758 | 9.9168 | 9.8568 | 9.7968 | 9.7389 | 9.6821 | 9.4158 | 9.2032 | 9.0137 | 10.4463 | 10.4663 | 10.4074 | 10.3505 | 10.2926 | 10.2337 | 10.1737 | 10.1137 | 10.0558 | 9.9989 | 9.7326 | 9.52 | 9.3295
BRAMLEY (FLEE) | MAIDENHEAD BSP | MAIDENHEAD | MINIMUM HEADROOM | SU 86485 79800 | YES | 1.2737 | 43.0042 | 42.5284 | 42.0495 | 41.5411 | 39.8621 | 38.5432 | 37.3168 | 36.1579 | 35.1716 | 34.2432 | 30.0589 | 26.3095 | -0.56632 | 37.3126 | 36.2611 | 35.1474 | 33.7032 | 31.5968 | 30.1326 | 28.7674 | 27.4768 | 26.3937 | 25.3737 | 20.76 | 16.5695 | 12.6968 | 38.7884 | 37.8474 | 36.78 | 35.4032 | 33.4126 | 32.0011 | 30.6347 | 29.3442 | 28.2621 | 27.2411 | 22.6305 | 18.4379 | 14.5632
|  | MAIDENHEAD | EE |  |  |  | 43.1895 | 42.8189 | 42.4263 | 42.0095 | 40.9389 | 39.7768 | 38.7116 | 37.6874 | 36.8495 | 36.0684 | 32.68 | 29.7989 | 27.1568 | 37.7295 | 36.8926 | 35.9642 | 34.7084 | 32.7811 | 31.4863 | 30.2916 | 29.1411 | 28.2147 | 27.3589 | 23.6063 | 20.3905 | 17.4 | 38.9863 | 38.4537 | 37.5642 | 36.3695 | 34.5505 | 33.3126 | 32.16 | 31.0095 | 30.0821 | 29.2253 | 25.4695 | 22.2579 | 19.2642
|  | MAIDENHEAD | HT |  |  |  | 43.0042 | 42.5284 | 42.0495 | 41.5411 | 39.8621 | 38.5432 | 37.3168 | 36.1579 | 35.1716 | 34.2432 | 30.0589 | 26.3095 | 22.8695 | 37.3126 | 36.2611 | 35.1474 | 33.7032 | 31.5968 | 30.1326 | 28.7674 | 27.4768 | 26.3937 | 25.3737 | 20.76 | 16.5695 | 12.6968 | 38.7884 | 37.8474 | 36.78 | 35.4032 | 33.4126 | 32.0011 | 30.6347 | 29.3442 | 28.2621 | 27.2411 | 22.6305 | 18.4379 | 14.5632
|  | MAIDENHEAD | HE |  |  |  | 43.4421 | 43.1916 | 42.9158 | 42.6095 | 42.28 | 41.3863 | 40.5189 | 39.6716 | 39.1063 | 38.5884 | 36.2274 | 34.1053 | -0.56632 | 38.1705 | 37.72 | 37.0495 | 36.0368 | 34.3432 | 33.2611 | 32.2842 | 31.3284 | 30.7084 | 30.1358 | 27.4884 | 25.0684 | 22.9379 | 39.2568 | 38.9884 | 38.6063 | 37.6442 | 36.0505 | 35.0168 | 34.0874 | 33.1768 | 32.5758 | 32.0042 | 29.3547 | 26.9263 | 24.7937
|  | MAIDENHEAD | CF |  |  |  | 43.5874 | 43.4474 | 43.3011 | 43.1495 | 42.9937 | 42.7684 | 42.6011 | 42.4389 | 42.2779 | 42.0895 | 40.3916 | 38.9874 | 37.7863 | 38.3232 | 38.1758 | 37.9811 | 37.54 | 36.8937 | 36.2453 | 35.5905 | 34.9116 | 34.4368 | 34.0579 | 32.1579 | 30.54 | 29.1379 | 39.4105 | 39.2621 | 39.1063 | 38.9379 | 38.4663 | 37.8495 | 37.2295 | 36.5895 | 36.1368 | 35.7726 | 33.9589 | 32.4074 | 31.0032
MELKSHAM GSP | CHIPPENHAM | MALMESBURY | MINIMUM HEADROOM | ST 92288 87493 | YES | 0.19158 | 14.42 | 14.2389 | 13.7589 | 13.3937 | 13.0632 | 12.7253 | 11.3084 | 10.5126 | 10.3305 | 10.2716 | 8.6516 | 3.9926 | -9.1695 | 10.1305 | 9.3653 | 8.6989 | 8.3063 | 7.9537 | 7.5968 | 5.9453 | 5.0305 | 4.8516 | 4.6863 | 2.9379 | -2.3979 | -3.0832 | 11.0705 | 10.2874 | 9.6053 | 9.2042 | 8.8474 | 8.4863 | 6.8347 | 5.9168 | 5.7337 | 5.5642 | 3.7874 | -1.5811 | -2.28
|  | MALMESBURY | EE |  |  |  | 14.4905 | 14.3474 | 14.0389 | 13.7368 | 13.4684 | 13.1863 | 12.9116 | 12.6432 | 12.4021 | 12.1611 | 9.3874 | 7.4674 | 4.9926 | 10.2853 | 9.5989 | 9.0032 | 8.6779 | 8.3916 | 8.0979 | 7.8095 | 7.5305 | 7.2916 | 7.0389 | 3.8716 | 1.7105 | -1.1968 | 11.2284 | 10.5242 | 9.9126 | 9.5821 | 9.2926 | 8.9926 | 8.6979 | 8.4126 | 8.1695 | 7.9116 | 4.7042 | 2.4979 | -0.42316
|  | MALMESBURY | HT |  |  |  | 14.42 | 14.2389 | 13.7589 | 13.3937 | 13.0632 | 12.7253 | 11.3084 | 10.5126 | 10.3305 | 10.2716 | 8.6516 | 3.9926 | 3.3358 | 10.1305 | 9.3653 | 8.6989 | 8.3063 | 7.9537 | 7.5968 | 5.9453 | 5.0305 | 4.8516 | 4.6863 | 2.9379 | -2.3979 | -3.0832 | 11.0705 | 10.2874 | 9.6053 | 9.2042 | 8.8474 | 8.4863 | 6.8347 | 5.9168 | 5.7337 | 5.5642 | 3.7874 | -1.5811 | -2.28
|  | MALMESBURY | HE |  |  |  | 14.5874 | 14.4905 | 14.3842 | 14.2011 | 14.0126 | 13.8105 | 13.6147 | 13.4316 | 13.2547 | 13.0979 | 10.5758 | 9.18 | -9.1695 | 10.4968 | 9.9084 | 9.4126 | 9.18 | 8.9811 | 8.7716 | 8.5684 | 8.3779 | 8.1937 | 8.0316 | 5.1021 | 3.4758 | 0.84947 | 11.4421 | 10.8389 | 10.3316 | 10.0947 | 9.8937 | 9.6789 | 9.4726 | 9.2779 | 9.0895 | 8.9242 | 5.9663 | 4.3232 | 1.6853
|  | MALMESBURY | CF |  |  |  | 14.6432 | 14.5895 | 14.5337 | 14.4758 | 14.4158 | 14.3505 | 14.2821 | 14.2158 | 14.1516 | 14.0863 | 13.7105 | 13.1905 | 12.6126 | 10.6716 | 10.3516 | 10.0979 | 9.9695 | 9.86 | 9.7305 | 9.5937 | 9.4705 | 9.3558 | 9.24 | 8.6968 | 8.1232 | 7.4674 | 11.6211 | 11.2926 | 11.0326 | 10.9032 | 10.7905 | 10.6589 | 10.5189 | 10.3926 | 10.2768 | 10.1568 | 9.6032 | 9.0095 | 8.3358
MINETY GSP | SWINDON BSP | MANCHESTER ROAD | MINIMUM HEADROOM | SU 15254 85130 | YES | 0.32842 | 68.1516 | 67.8684 | 67.5821 | 67.2768 | 66.9568 | 66.1084 | 63.2389 | 60.0958 | 57.3684 | 54.6095 | 46.9105 | 42.5811 | 7.6074 | 61.5979 | 61.2979 | 60.7516 | 59.9611 | 58.6821 | 55.1547 | 51.6347 | 47.9968 | 44.8432 | 41.6495 | 32.7989 | 27.8632 | 24.1537 | 62.7895 | 62.4832 | 62.1621 | 61.8179 | 60.7463 | 57.2716 | 53.7505 | 50.1116 | 46.9568 | 43.7621 | 34.9095 | 29.9726 | 26.2611
|  | MANCHESTER ROAD | EE |  |  |  | 68.26 | 68.0368 | 67.8011 | 67.5505 | 67.2832 | 67.0042 | 65.9232 | 63.3589 | 63.1021 | 59.9147 | 51.8895 | 48.2095 | 45.64 | 61.7126 | 61.4789 | 61.2263 | 60.7474 | 59.9832 | 57.4274 | 54.8537 | 51.7442 | 51.4874 | 47.7853 | 38.5147 | 34.3042 | 31.3684 | 62.9063 | 62.6684 | 62.4105 | 62.1337 | 61.8253 | 59.5389 | 56.9705 | 53.86 | 53.6032 | 49.9 | 40.6263 | 36.4147 | 33.4779
|  | MANCHESTER ROAD | HT |  |  |  | 68.1516 | 67.8684 | 67.5821 | 67.2768 | 66.9568 | 66.1084 | 63.2389 | 60.0958 | 57.3684 | 54.6095 | 46.9105 | 42.5811 | 39.3179 | 61.5979 | 61.2979 | 60.7516 | 59.9611 | 58.6821 | 55.1547 | 51.6347 | 47.9968 | 44.8432 | 41.6495 | 32.7989 | 27.8632 | 24.1537 | 62.7895 | 62.4832 | 62.1621 | 61.8179 | 60.7463 | 57.2716 | 53.7505 | 50.1116 | 46.9568 | 43.7621 | 34.9095 | 29.9726 | 26.2611
|  | MANCHESTER ROAD | HE |  |  |  | 68.3758 | 68.2053 | 68.0158 | 67.8063 | 67.5811 | 67.3411 | 66.6853 | 64.1063 | 63.9042 | 60.9537 | 53.7 | 50.6495 | 7.6074 | 61.8368 | 61.6589 | 61.4558 | 61.2284 | 60.6432 | 58.2653 | 55.7674 | 52.5474 | 52.3453 | 48.9116 | 40.5 | 36.9842 | 34.7137 | 63.0326 | 62.8526 | 62.6453 | 62.4137 | 62.1516 | 60.3589 | 57.8842 | 54.6632 | 54.4611 | 51.0263 | 42.6126 | 39.0947 | 36.8242
|  | MANCHESTER ROAD | CF |  |  |  | 68.4442 | 68.3326 | 68.2158 | 68.0947 | 67.9705 | 67.8411 | 67.7095 | 67.58 | 67.4516 | 67.3232 | 59.6263 | 56.9053 | 55.6547 | 61.9084 | 61.7926 | 61.6716 | 61.5463 | 61.4179 | 61.2842 | 61.1484 | 60.9642 | 60.2842 | 59.0126 | 47.3116 | 44.1674 | 42.7274 | 63.1053 | 62.9874 | 62.8653 | 62.7389 | 62.6095 | 62.4737 | 62.3368 | 62.1842 | 62.0042 | 61.0789 | 49.4263 | 46.2811 | 44.8411
MANNINGTON GSP | MANNINGTON BSP | MANNINGTON | MINIMUM HEADROOM | SU 07592 05256 | YES | 0 | 16.6232 | 16.4779 | 16.3326 | 16.1779 | 16.0189 | 15.7884 | 15.2895 | 14.7095 | 14.5758 | 14.6526 | 12.9821 | 11.8789 | 2.6232 | 15.0263 | 14.7526 | 14.4832 | 14.2105 | 13.9389 | 13.6653 | 13.0811 | 12.3884 | 12.2558 | 12.1432 | 10.2926 | 8.9716 | 7.9695 | 15.4063 | 15.1389 | 14.8768 | 14.6116 | 14.3463 | 14.0779 | 13.5158 | 12.8505 | 12.7158 | 12.5947 | 10.7337 | 9.4011 | 8.3958
|  | MANNINGTON | EE |  |  |  | 16.6842 | 16.5747 | 16.4589 | 16.3337 | 16.2063 | 16.0726 | 15.9421 | 15.7905 | 15.6147 | 15.4516 | 12.9821 | 11.8789 | 10.9958 | 15.1537 | 14.9453 | 14.7358 | 14.5189 | 14.3042 | 14.0895 | 13.88 | 13.6811 | 13.4905 | 13.3147 | 10.2926 | 8.9716 | 7.9695 | 15.5295 | 15.3274 | 15.1232 | 14.9116 | 14.7011 | 14.4895 | 14.2832 | 14.0874 | 13.9 | 13.7263 | 10.7337 | 9.4011 | 8.3958
|  | MANNINGTON | HT |  |  |  | 16.6232 | 16.4779 | 16.3326 | 16.1779 | 16.0189 | 15.7884 | 15.2895 | 14.7095 | 14.5758 | 14.6526 | 13.4684 | 12.0032 | 11.5389 | 15.0263 | 14.7526 | 14.4832 | 14.2105 | 13.9389 | 13.6653 | 13.0811 | 12.3884 | 12.2558 | 12.1432 | 10.8453 | 9.1979 | 8.7042 | 15.4063 | 15.1389 | 14.8768 | 14.6116 | 14.3463 | 14.0779 | 13.5158 | 12.8505 | 12.7158 | 12.5947 | 11.2916 | 9.6358 | 9.1379
|  | MANNINGTON | HE |  |  |  | 16.7642 | 16.6937 | 16.6147 | 16.5274 | 16.4347 | 16.3326 | 16.2358 | 16.1442 | 16.0589 | 15.9842 | 13.8358 | 13.0042 | 2.6232 | 15.3221 | 15.1958 | 15.0632 | 14.9221 | 14.7147 | 14.5316 | 14.4105 | 14.2947 | 14.1853 | 14.1011 | 11.2274 | 10.1621 | 9.3653 | 15.6926 | 15.5705 | 15.44 | 15.3021 | 15.1011 | 14.9221 | 14.8021 | 14.6874 | 14.5779 | 14.4937 | 11.6768 | 10.6084 | 9.8084
|  | MANNINGTON | CF |  |  |  | 16.8105 | 16.7737 | 16.7358 | 16.6947 | 16.6537 | 16.6095 | 16.5663 | 16.5211 | 16.4779 | 16.4347 | 16.24 | 16.1263 | 15.6537 | 15.4105 | 15.3368 | 15.2621 | 15.1842 | 15.1053 | 15.0232 | 14.9432 | 14.8611 | 14.7811 | 14.6989 | 14.3326 | 14.0211 | 13.4421 | 15.7432 | 15.7032 | 15.6347 | 15.5589 | 15.4821 | 15.4021 | 15.3232 | 15.2432 | 15.1653 | 15.0853 | 14.7274 | 14.4242 | 13.8737
LOVEDEAN GSP | CHICHESTER & HUNSTON | MARKET | MINIMUM HEADROOM | SU 86479 04732 | YES | 0 | 32.2137 | 32.0063 | 31.7979 | 31.5758 | 31.3284 | 31.0705 | 30.8126 | 30.4958 | 29.9958 | 29.5884 | 27.2737 | 24.9221 | 3.4305 | 28.6505 | 28.4053 | 28.0242 | 27.4326 | 26.9484 | 26.4495 | 26.0032 | 25.3726 | 24.7516 | 24.2547 | 21.3189 | 18.6053 | 16.06 | 29.2547 | 29.0284 | 28.7989 | 28.5537 | 28.1116 | 27.6316 | 27.1863 | 26.5558 | 25.9358 | 25.4389 | 22.5074 | 19.7979 | 17.2558
|  | MARKET | EE |  |  |  | 32.2895 | 32.1253 | 31.9516 | 31.7674 | 31.5716 | 31.3642 | 31.1579 | 30.9411 | 30.7337 | 30.4484 | 28.5642 | 26.8453 | 25.0768 | 28.74 | 28.5442 | 28.3116 | 27.8895 | 27.5168 | 27.1358 | 26.8063 | 26.2358 | 25.7095 | 25.3105 | 22.9179 | 20.7495 | 18.7263 | 29.3368 | 29.1568 | 28.9653 | 28.7621 | 28.5547 | 28.2747 | 27.9642 | 27.4179 | 26.8926 | 26.4937 | 24.1042 | 21.9389 | 19.9189
|  | MARKET | HT |  |  |  | 32.2137 | 32.0063 | 31.7979 | 31.5758 | 31.3284 | 31.0705 | 30.8126 | 30.4958 | 29.9958 | 29.5884 | 27.2737 | 24.9221 | 22.6874 | 28.6505 | 28.4053 | 28.0242 | 27.4326 | 26.9484 | 26.4495 | 26.0032 | 25.3726 | 24.7516 | 24.2547 | 21.3189 | 18.6053 | 16.06 | 29.2547 | 29.0284 | 28.7989 | 28.5537 | 28.1116 | 27.6316 | 27.1863 | 26.5558 | 25.9358 | 25.4389 | 22.5074 | 19.7979 | 17.2558
|  | MARKET | HE |  |  |  | 32.3842 | 32.2632 | 32.1295 | 31.9811 | 31.8221 | 31.6526 | 31.4905 | 31.3358 | 31.1726 | 31.0368 | 29.8526 | 28.5621 | 3.4305 | 28.8516 | 28.7074 | 28.5453 | 28.3537 | 28.1316 | 27.8526 | 27.6116 | 27.1305 | 26.6968 | 26.3926 | 24.4705 | 22.7653 | 21.1968 | 29.44 | 29.3074 | 29.16 | 28.9968 | 28.8295 | 28.6526 | 28.4853 | 28.2653 | 27.8758 | 27.5737 | 25.6547 | 23.9526 | 22.3874
|  | MARKET | CF |  |  |  | 32.4389 | 32.3632 | 32.2842 | 32.2032 | 32.1179 | 32.0305 | 31.9421 | 31.8547 | 31.7674 | 31.6811 | 31.2495 | 30.6179 | 29.8811 | 28.9158 | 28.8253 | 28.7305 | 28.6337 | 28.5379 | 28.4389 | 28.3421 | 28.1863 | 27.98 | 27.7958 | 26.4832 | 25.3621 | 24.3726 | 29.5 | 29.4168 | 29.3295 | 29.2411 | 29.1505 | 29.0568 | 28.9642 | 28.8653 | 28.7674 | 28.6758 | 27.6653 | 26.5453 | 25.5579
MELKSHAM GSP | WEST GRAFTON | MARLBOROUGH SOUTH | MINIMUM HEADROOM | SU 19293 68264 | YES | 0.094737 | 20.2832 | 20.0642 | 19.8442 | 19.6011 | 18.9716 | 18.5821 | 18.1947 | 17.8463 | 17.5232 | 17.1874 | 15.4 | 13.6032 | -5.6558 | 15.4474 | 15.0821 | 14.7189 | 14.1663 | 13.4442 | 13.02 | 12.6011 | 12.22 | 11.8674 | 11.4926 | 9.5126 | 7.4905 | 5.4653 | 16.4558 | 16.0874 | 15.7211 | 15.1632 | 14.4337 | 14.0063 | 13.5832 | 13.2 | 12.8453 | 12.4695 | 10.4916 | 8.4726 | 6.4505
|  | MARLBOROUGH SOUTH | EE |  |  |  | 20.3663 | 20.1947 | 20.0126 | 19.82 | 19.5579 | 19.14 | 18.8032 | 18.4979 | 18.2032 | 17.9453 | 16.6347 | 15.2611 | 13.8937 | 15.5884 | 15.32 | 15.0274 | 14.7042 | 14.1105 | 13.6432 | 13.2726 | 12.94 | 12.6179 | 12.3379 | 10.8716 | 9.32 | 7.7558 | 16.5832 | 16.3274 | 16.0326 | 15.7074 | 15.1074 | 14.6347 | 14.2611 | 13.9263 | 13.6021 | 13.3189 | 11.8484 | 10.3 | 8.7379
|  | MARLBOROUGH SOUTH | HT |  |  |  | 20.2832 | 20.0642 | 19.8442 | 19.6011 | 18.9716 | 18.5821 | 18.1947 | 17.8463 | 17.5232 | 17.1874 | 15.4 | 13.6032 | 11.8232 | 15.4474 | 15.0821 | 14.7189 | 14.1663 | 13.4442 | 13.02 | 12.6011 | 12.22 | 11.8674 | 11.4926 | 9.5126 | 7.4905 | 5.4653 | 16.4558 | 16.0874 | 15.7211 | 15.1632 | 14.4337 | 14.0063 | 13.5832 | 13.2 | 12.8453 | 12.4695 | 10.4916 | 8.4726 | 6.4505
|  | MARLBOROUGH SOUTH | HE |  |  |  | 20.4821 | 20.3653 | 20.2368 | 20.0947 | 19.9411 | 19.7779 | 19.6063 | 19.3853 | 19.1811 | 19.0074 | 18.1295 | 17.1674 | -5.6558 | 15.7042 | 15.5874 | 15.4411 | 15.2358 | 14.8063 | 14.4463 | 14.1705 | 13.9316 | 13.7116 | 13.5253 | 12.5316 | 11.4095 | 10.2516 | 16.6989 | 16.5821 | 16.4495 | 16.2432 | 15.8095 | 15.4453 | 15.1674 | 14.9274 | 14.7063 | 14.5179 | 13.5137 | 12.3874 | 11.2316
|  | MARLBOROUGH SOUTH | CF |  |  |  | 20.5495 | 20.4842 | 20.4158 | 20.3453 | 20.2726 | 20.1968 | 20.12 | 20.0442 | 19.9684 | 19.8926 | 19.3947 | 18.8316 | 18.2179 | 15.7716 | 15.7063 | 15.6379 | 15.5674 | 15.4674 | 15.3463 | 15.2242 | 15.1042 | 14.9842 | 14.8642 | 13.9232 | 13.2642 | 12.5221 | 16.7663 | 16.7011 | 16.6326 | 16.5621 | 16.4758 | 16.3547 | 16.2316 | 16.1105 | 15.9895 | 15.8695 | 14.9168 | 14.2495 | 13.4989
NURSLING GSP | ROWNHAMS | MAYBUSH | MINIMUM HEADROOM | SU 38426 14930 | YES | 0.43895 | 27.3695 | 27.06 | 26.7463 | 26.4137 | 25.9558 | 26.1 | 24.9084 | 24.0526 | 23.4316 | 22.6484 | 19.9905 | 17.5295 | -9.8368 | 21.0032 | 20.4011 | 19.8011 | 19.1253 | 18.4411 | 18.6253 | 17.2158 | 16.2632 | 15.5842 | 14.4432 | 11.8032 | 9.0642 | 6.5442 | 22.3105 | 21.7084 | 21.1105 | 20.4347 | 19.7505 | 19.9347 | 18.2242 | 17.2716 | 16.5926 | 15.7074 | 12.8747 | 10.0389 | 7.5105
|  | MAYBUSH | EE |  |  |  | 27.4821 | 27.2358 | 26.9747 | 26.6979 | 26.4053 | 26.1 | 25.5484 | 24.7632 | 23.9937 | 22.6484 | 21.7874 | 19.8832 | 18.1779 | 21.2484 | 20.7979 | 20.32 | 19.7842 | 19.2389 | 18.6253 | 18.0074 | 17.1316 | 16.2705 | 14.4432 | 13.8811 | 11.6558 | 9.7368 | 22.5747 | 22.1053 | 21.6284 | 21.0926 | 20.5474 | 19.9347 | 19.3168 | 18.4421 | 17.5832 | 15.7074 | 14.9389 | 12.7295 | 10.7116
|  | MAYBUSH | HT |  |  |  | 27.3695 | 27.06 | 26.7463 | 26.4137 | 25.9558 | 26.4379 | 24.9084 | 24.0526 | 23.4316 | 22.9011 | 19.9905 | 17.5295 | 15.2789 | 21.0032 | 20.4011 | 19.8011 | 19.1253 | 18.4411 | 19.1663 | 17.2158 | 16.2632 | 15.5842 | 15.1137 | 11.8032 | 9.0642 | 6.5442 | 22.3105 | 21.7084 | 21.1105 | 20.4347 | 19.7505 | 20.2958 | 18.2242 | 17.2716 | 16.5926 | 18.6253 | 12.8747 | 10.0389 | 7.5105
|  | MAYBUSH | HE |  |  |  | 27.6242 | 27.4442 | 27.2442 | 27.0232 | 26.7853 | 26.5326 | 26.2895 | 26.0621 | 24.9558 | 24.4642 | 28.3411 | 27.8768 | -9.8368 | 21.5537 | 21.2705 | 20.9716 | 20.5916 | 20.1874 | 19.7053 | 19.22 | 18.6147 | 16.9979 | 16.4558 | 16.4653 | 15.0263 | 13.7926 | 22.92 | 22.6126 | 22.2895 | 21.9 | 21.4947 | 21.0137 | 20.5295 | 19.9242 | 18.2737 | 17.7295 | 19.4516 | 18.7263 | 18.1389
|  | MAYBUSH | CF |  |  |  | 27.7126 | 27.6021 | 27.4895 | 27.3705 | 27.2474 | 27.1211 | 26.9916 | 26.8642 | 26.7379 | 26.6116 | 25.5274 | 26.06 | 25.3032 | 21.7116 | 21.5189 | 21.3347 | 21.1432 | 20.9463 | 20.7295 | 20.5084 | 20.2758 | 19.9126 | 19.5368 | 17.9379 | 18.7105 | 17.8453 | 23.0937 | 22.8821 | 22.68 | 22.4716 | 22.2558 | 22.0368 | 21.8158 | 21.5842 | 21.2211 | 20.8463 | 19.2484 | 19.84 | 18.9747
MELKSHAM GSP | NORRINGTON | MELKSHAM TOWN | MINIMUM HEADROOM | ST 90170 64096 | YES | 0.38842 | 22.2242 | 22.6579 | 22.3105 | 21.9337 | 22.2705 | 21.8874 | 22.3726 | 21.2253 | 20.2811 | 19.3968 | 15.4442 | 11.3768 | -22.2421 | 18.42 | 19.3 | 18.8758 | 18.4105 | 18.0063 | 17.5611 | 16.8295 | 15.5642 | 14.5326 | 13.5642 | 9.2263 | 4.6705 | 0.094737 | 20.2842 | 20.7695 | 20.3589 | 19.9105 | 20.0768 | 19.6305 | 17.7632 | 16.4979 | 15.4642 | 14.4958 | 10.1589 | 5.5937 | 1.0126
|  | MELKSHAM TOWN | EE |  |  |  | 22.2242 | 29.6316 | 30.7316 | 29.38 | 27.8663 | 26.1032 | 24.5863 | 23.1863 | 21.9968 | 21.0926 | 18.0726 | 14.9568 | 11.8042 | 18.8032 | 27.2726 | 26.2105 | 24.6958 | 22.9937 | 21.0032 | 19.2989 | 17.7263 | 16.4 | 15.4021 | 12.0905 | 8.6147 | 5.0253 | 20.2842 | 28.2105 | 27.1495 | 25.6337 | 23.9316 | 21.9389 | 20.2337 | 18.66 | 17.3316 | 16.3316 | 13.0105 | 9.5305 | 5.9379
|  | MELKSHAM TOWN | HT |  |  |  | 22.5947 | 29.0884 | 29.9916 | 28.1937 | 26.2284 | 24.0747 | 22.3726 | 21.2253 | 20.2811 | 19.3968 | 15.4442 | 11.3768 | 7.3368 | 18.42 | 26.6558 | 25.4053 | 23.3832 | 21.1663 | 18.7305 | 16.8295 | 15.5642 | 14.5326 | 13.5642 | 9.2263 | 4.6705 | 0.094737 | 20.4926 | 27.5947 | 26.3432 | 24.3211 | 22.1032 | 19.6674 | 17.7632 | 16.4979 | 15.4642 | 14.4958 | 10.1589 | 5.5937 | 1.0126
|  | MELKSHAM TOWN | HE |  |  |  | 22.6895 | 29.6926 | 29.6589 | 28.5884 | 29.2526 | 27.6653 | 26.3411 | 25.0842 | 24.1368 | 23.4347 | 21.3821 | 19.0758 | -22.2421 | 19.3484 | 27.7516 | 27.28 | 25.9916 | 24.4989 | 22.6979 | 21.2 | 19.78 | 18.7189 | 17.94 | 15.6842 | 13.0663 | 10.3284 | 20.8147 | 28.8284 | 28.2189 | 26.9295 | 25.4368 | 23.6337 | 22.1358 | 20.7147 | 19.6537 | 18.8737 | 16.6126 | 13.9926 | 11.2484
|  | MELKSHAM TOWN | CF |  |  |  | 22.9463 | 22.6579 | 22.3105 | 21.9337 | 22.2705 | 21.8874 | 28.9432 | 28.5674 | 28.0505 | 27.4168 | 26.3674 | 25.0179 | 23.5063 | 19.6463 | 19.3 | 18.8758 | 18.4105 | 18.0063 | 17.5611 | 26.4295 | 25.9905 | 25.3726 | 24.6053 | 21.2495 | 19.7295 | 17.9926 | 21.1053 | 20.7695 | 20.3589 | 19.9105 | 20.0768 | 19.6305 | 27.3663 | 26.9284 | 26.3095 | 25.5421 | 22.1842 | 20.6621 | 18.9221
NURSLING GSP |  | MARCHWOOD | MINIMUM HEADROOM | SU 39234 11008 | YES | 1.0484 | 16.7316 | 16.6663 | 16.5989 | 16.5284 | 16.4547 | 16.2758 | 15.9632 | 15.6589 | 14.5411 | 14.4853 | 14.2147 | 13.9737 | 8.0084 | 15.8779 | 15.8095 | 15.74 | 15.6663 | 15.5905 | 15.5021 | 15.2789 | 14.9263 | 13.5916 | 13.5358 | 13.2568 | 13.0021 | 12.7084 | 16.54 | 16.4474 | 16.3263 | 16.2042 | 16.0811 | 15.7579 | 15.4116 | 15.0589 | 13.7232 | 13.6674 | 13.3884 | 13.1337 | 12.84
|  | MARCHWOOD | EE |  |  |  | 16.7568 | 16.7042 | 16.6495 | 16.5905 | 16.5295 | 16.4505 | 16.16 | 15.8737 | 15.6389 | 15.5568 | 15.1695 | 14.74 | 14.3042 | 15.9053 | 15.8505 | 15.7937 | 15.7326 | 15.6695 | 15.5926 | 15.4895 | 15.1632 | 14.8905 | 14.8021 | 14.3737 | 13.8811 | 13.3747 | 16.5653 | 16.5126 | 16.4358 | 16.3368 | 16.2358 | 15.9347 | 15.6284 | 15.2947 | 15.0232 | 14.9347 | 14.5053 | 14.0137 | 13.5063
|  | MARCHWOOD | HT |  |  |  | 16.7316 | 16.6663 | 16.5989 | 16.5284 | 16.4547 | 16.2758 | 15.9632 | 15.6589 | 14.5411 | 14.4853 | 14.2147 | 13.9737 | 13.7074 | 15.8779 | 15.8095 | 15.74 | 15.6663 | 15.5905 | 15.5021 | 15.2789 | 14.9263 | 13.5916 | 13.5358 | 13.2568 | 13.0021 | 12.7084 | 16.54 | 16.4474 | 16.3263 | 16.2042 | 16.0811 | 15.7579 | 15.4116 | 15.0589 | 13.7232 | 13.6674 | 13.3884 | 13.1337 | 12.84
|  | MARCHWOOD | HE |  |  |  | 16.7905 | 16.7547 | 16.7147 | 16.6716 | 16.6242 | 16.5737 | 16.4074 | 16.1463 | 15.9379 | 15.8811 | 15.6221 | 15.3105 | 8.0084 | 15.9411 | 15.9032 | 15.8621 | 15.8179 | 15.7695 | 15.7074 | 15.6474 | 15.4642 | 15.2211 | 15.1611 | 14.8737 | 14.5137 | 14.1337 | 16.5989 | 16.5632 | 16.5232 | 16.48 | 16.4326 | 16.1589 | 15.8884 | 15.5958 | 15.3537 | 15.2926 | 15.0063 | 14.6453 | 14.2663
|  | MARCHWOOD | CF |  |  |  | 16.8105 | 16.7895 | 16.7684 | 16.7453 | 16.7221 | 16.6989 | 16.6737 | 16.6495 | 16.5811 | 16.5389 | 16.3474 | 16.1579 | 15.9484 | 15.9611 | 15.9389 | 15.9179 | 15.8937 | 15.8695 | 15.8411 | 15.8105 | 15.78 | 15.7526 | 15.7274 | 15.6158 | 15.4821 | 15.2389 | 16.6189 | 16.5979 | 16.5768 | 16.5537 | 16.5305 | 16.4579 | 16.3253 | 16.1863 | 16.0642 | 16.0221 | 15.8284 | 15.6179 | 15.3716
LOVEDEAN GSP | HAVANT | MEYRICK ROAD | MINIMUM HEADROOM | SU 70849 06469 | YES | 0.21053 | 28.7684 | 28.2789 | 27.7758 | 27.26 | 26.6484 | 25.4642 | 24.2568 | 23.1747 | 22.1716 | 21.2653 | 17.2937 | 11.98 | -10.7242 | 23.8674 | 22.6253 | 21.2021 | 19.9905 | 18.8632 | 17.5611 | 16.2295 | 15.0358 | 13.9295 | 12.9284 | 8.5305 | 2.4926 | -1.9832 | 24.8389 | 23.6558 | 22.3053 | 21.1474 | 20.0684 | 18.8232 | 17.54 | 16.3463 | 15.2379 | 14.2368 | 9.8347 | 3.7905 | -0.68842
|  | MEYRICK ROAD | EE |  |  |  | 28.9453 | 28.5568 | 28.1347 | 27.7095 | 27.2737 | 26.7379 | 25.7074 | 24.7663 | 23.9368 | 23.2379 | 20.2968 | 15.8484 | 12.7832 | 24.2368 | 23.1916 | 21.9421 | 20.9232 | 20.0232 | 18.9568 | 17.8168 | 16.78 | 15.8684 | 15.1074 | 11.8684 | 6.7958 | 3.3032 | 25.1221 | 24.1989 | 23.0147 | 22.0421 | 21.1789 | 20.1589 | 19.0737 | 18.0832 | 17.1779 | 16.4158 | 13.1705 | 8.0905 | 4.5947
|  | MEYRICK ROAD | HT |  |  |  | 28.7684 | 28.2789 | 27.7758 | 27.26 | 26.6484 | 25.4642 | 24.2568 | 23.1747 | 22.1716 | 21.2653 | 17.2937 | 11.98 | 8.0337 | 23.8674 | 22.6253 | 21.2021 | 19.9905 | 18.8632 | 17.5611 | 16.2295 | 15.0358 | 13.9295 | 12.9284 | 8.5305 | 2.4926 | -1.9832 | 24.8389 | 23.6558 | 22.3053 | 21.1474 | 20.0684 | 18.8232 | 17.54 | 16.3463 | 15.2379 | 14.2368 | 9.8347 | 3.7905 | -0.68842
|  | MEYRICK ROAD | HE |  |  |  | 29.1842 | 28.9168 | 28.6074 | 28.2863 | 27.9537 | 27.5874 | 27.2305 | 26.5811 | 25.9295 | 25.3937 | 23.3874 | 19.7979 | -10.7242 | 24.6905 | 23.9358 | 22.9116 | 22.1126 | 21.4211 | 20.5442 | 19.5937 | 18.7547 | 18.0368 | 17.4505 | 15.2368 | 11.1074 | 8.4295 | 25.3653 | 24.9137 | 23.9453 | 23.1832 | 22.52 | 21.6832 | 20.7789 | 19.9789 | 19.2937 | 18.7316 | 16.5453 | 12.4126 | 9.7316
|  | MEYRICK ROAD | CF |  |  |  | 29.3158 | 29.1789 | 29.0137 | 28.8505 | 28.6874 | 28.5158 | 28.3337 | 28.1558 | 27.9789 | 27.8074 | 27.0695 | 24.8084 | 23.3179 | 24.8442 | 24.5821 | 24.0421 | 23.6137 | 23.2421 | 22.8095 | 22.2905 | 21.78 | 21.2884 | 20.8537 | 19.3411 | 16.7084 | 14.9937 | 25.5063 | 25.3547 | 25.0189 | 24.6116 | 24.2568 | 23.8442 | 23.3505 | 22.8653 | 22.3989 | 21.9853 | 20.5337 | 18.0179 | 16.3011
MELKSHAM GSP | ANDOVER BSP | MIDDLE WALLOP | MINIMUM HEADROOM | SU 30984 40155 | YES | 0.23895 | 6.6307 | 6.5107 | 6.3928 | 6.2686 | 6.0717 | 5.5917 | 5.1201 | 4.5401 | 4.457 | 4.3738 | 3.2686 | 1.7728 | -0.63776 | 6.2624 | 6.1487 | 6.0371 | 5.9192 | 5.7161 | 5.1697 | 4.6361 | 3.9718 | 3.8939 | 3.8182 | 2.6266 | 0.97605 | 0.56342 | 6.5621 | 6.4379 | 6.3147 | 6.1863 | 5.9779 | 5.4547 | 4.9147 | 4.2463 | 4.1611 | 4.0789 | 2.8411 | 1.1368 | 0.70316
|  | MIDDLE WALLOP | EE |  |  |  | 6.6833 | 6.5938 | 6.4991 | 6.398 | 6.297 | 6.1812 | 6.0601 | 5.9391 | 5.8191 | 5.7033 | 5.0801 | 3.5307 | 2.638 | 6.3118 | 6.2266 | 6.1382 | 6.0424 | 5.9476 | 5.8424 | 5.7276 | 5.6118 | 5.495 | 5.3813 | 4.7824 | 3.0929 | 2.0897 | 6.6137 | 6.5242 | 6.4263 | 6.3211 | 6.2168 | 6.0968 | 5.9716 | 5.8463 | 5.7221 | 5.6011 | 4.9632 | 3.2 | 2.1737
|  | MIDDLE WALLOP | HT |  |  |  | 6.6307 | 6.5107 | 6.3928 | 6.2686 | 6.0717 | 5.5917 | 5.1201 | 4.5401 | 4.457 | 4.3738 | 3.2686 | 1.7728 | 1.3759 | 6.2624 | 6.1487 | 6.0371 | 5.9192 | 5.7161 | 5.1697 | 4.6361 | 3.9718 | 3.8939 | 3.8182 | 2.6266 | 0.97605 | 0.56342 | 6.5621 | 6.4379 | 6.3147 | 6.1863 | 5.9779 | 5.4547 | 4.9147 | 4.2463 | 4.1611 | 4.0789 | 2.8411 | 1.1368 | 0.70316
|  | MIDDLE WALLOP | HE |  |  |  | 6.7559 | 6.7001 | 6.6433 | 6.5738 | 6.5064 | 6.4222 | 6.3391 | 6.2633 | 6.1886 | 6.118 | 5.7917 | 4.7201 | -0.63776 | 6.3803 | 6.3276 | 6.2729 | 6.2066 | 6.1424 | 6.0666 | 5.9918 | 5.9234 | 5.8561 | 5.7908 | 5.4855 | 4.2645 | 3.4329 | 6.6737 | 6.6253 | 6.5747 | 6.5053 | 6.4358 | 6.3474 | 6.2632 | 6.1832 | 6.1063 | 6.0347 | 5.7263 | 4.4853 | 3.6358
|  | MIDDLE WALLOP | CF |  |  |  | 6.7928 | 6.7612 | 6.7286 | 6.6896 | 6.6464 | 6.5907 | 6.5433 | 6.497 | 6.4538 | 6.4117 | 6.2043 | 5.6833 | 5.1433 | 6.4161 | 6.3855 | 6.355 | 6.3182 | 6.2782 | 6.2287 | 6.1855 | 6.1445 | 6.1055 | 6.0676 | 5.875 | 5.295 | 4.6803 | 6.7053 | 6.6779 | 6.6505 | 6.6189 | 6.5789 | 6.5211 | 6.4705 | 6.4221 | 6.3779 | 6.3337 | 6.1179 | 5.5547 | 4.9284
BRAMLEY (FLEE) | FERNHURST | MIDHURST | MINIMUM HEADROOM | SU 88127 19555 | YES | 2.1053 | 34.0137 | 31.4674 | 31.2663 | 31.0526 | 30.8295 | 30.5368 | 30.0884 | 29.6979 | 29.28 | 28.8474 | 26.9084 | 24.8558 | 7.7684 | 30.3832 | 27.1495 | 26.8316 | 26.4716 | 26.0832 | 25.68 | 25.3158 | 24.9116 | 24.46 | 23.9884 | 22.0095 | 19.6579 | 17.5179 | 31.2242 | 27.5368 | 27.28 | 26.9958 | 26.7116 | 26.42 | 26.0916 | 25.7505 | 25.38 | 24.9053 | 22.8811 | 20.3895 | 18.2516
|  | MIDHURST | EE |  |  |  | 34.1053 | 31.4674 | 31.2663 | 31.0526 | 30.8295 | 30.5989 | 30.3063 | 29.98 | 29.6358 | 29.2842 | 27.8074 | 28.5705 | 24.7579 | 30.5884 | 27.1495 | 26.8316 | 26.4716 | 26.0832 | 25.68 | 25.3158 | 24.9695 | 24.6021 | 24.2221 | 22.6063 | 20.9989 | 19.1821 | 31.3632 | 27.5368 | 27.28 | 26.9958 | 26.7116 | 26.42 | 26.0916 | 25.7505 | 25.3905 | 25.0189 | 23.3779 | 21.6274 | 19.8579
|  | MIDHURST | HT |  |  |  | 34.0137 | 31.6663 | 31.4221 | 31.1621 | 30.8947 | 30.5368 | 30.0884 | 29.6979 | 29.28 | 28.8474 | 26.9084 | 24.8558 | 23 | 30.3832 | 27.8168 | 27.3632 | 26.8379 | 26.3263 | 25.8042 | 25.3263 | 24.9116 | 24.46 | 23.9884 | 22.0095 | 19.6579 | 17.5179 | 31.2242 | 28.6674 | 28.2232 | 27.7095 | 27.2084 | 26.6968 | 26.2284 | 25.8211 | 25.38 | 24.9053 | 22.8811 | 20.3895 | 18.2516
|  | MIDHURST | HE |  |  |  | 34.2337 | 31.6568 | 31.5137 | 31.3568 | 31.1874 | 31.0063 | 30.8337 | 30.6716 | 30.5189 | 30.3884 | 29.4621 | 28.8947 | 7.7684 | 30.7716 | 27.5042 | 27.2937 | 27.0389 | 26.7884 | 26.5211 | 26.2863 | 26.0611 | 25.8011 | 25.5232 | 24.4 | 23.0337 | 21.5579 | 31.5021 | 27.8053 | 27.6305 | 27.4263 | 27.2179 | 26.9958 | 26.7937 | 26.6032 | 26.4116 | 26.2284 | 25.1979 | 24.0242 | 23.5032
|  | MIDHURST | CF |  |  |  | 34.3084 | 31.7884 | 31.7126 | 31.6347 | 31.5547 | 31.4705 | 31.3853 | 31.3021 | 31.2189 | 31.1358 | 30.7663 | 30.0084 | 29.3253 | 30.8547 | 27.7053 | 27.5811 | 27.4463 | 27.3095 | 27.1653 | 27.0295 | 26.8968 | 26.7632 | 26.6158 | 25.8305 | 24.9316 | 24.1505 | 31.5811 | 27.9705 | 27.8716 | 27.7663 | 27.6589 | 27.5463 | 27.4368 | 27.3295 | 27.2232 | 27.1084 | 26.5821 | 25.7326 | 24.9295
AXMINSTER | YEOVIL BSP | MILBORNE PORT | MINIMUM HEADROOM | ST 67929 19741 | YES | 0 | 4.7632 | 4.6263 | 4.4895 | 4.3495 | 4.2074 | 4.0463 | 3.8926 | 3.7421 | 3.6 | 3.4684 | 1.9947 | 1.5958 | -0.87158 | 4.7253 | 4.5747 | 4.4263 | 4.2726 | 4.1221 | 3.9579 | 3.8011 | 3.6484 | 3.5042 | 3.3705 | 1.7842 | 1.4221 | 1.2053 | 4.7663 | 4.6168 | 4.4684 | 4.3126 | 4.16 | 3.9895 | 3.8274 | 3.6695 | 3.5179 | 3.3779 | 1.7221 | 1.32 | 1.0884
|  | MILBORNE PORT | EE |  |  |  | 4.8221 | 4.7158 | 4.6042 | 4.4979 | 4.3789 | 4.2442 | 4.1095 | 3.9737 | 3.8379 | 3.7126 | 3.0537 | 2.4263 | 1.9768 | 4.7905 | 4.6747 | 4.5537 | 4.4958 | 4.3705 | 4.2337 | 4.1 | 3.9632 | 3.8295 | 3.7074 | 3.0716 | 2.4747 | 2.0021 | 4.8316 | 4.7158 | 4.5947 | 4.4737 | 4.3474 | 4.2053 | 4.0642 | 3.92 | 3.7779 | 3.6463 | 2.9484 | 2.2821 | 1.7874
|  | MILBORNE PORT | HT |  |  |  | 4.7632 | 4.6263 | 4.4895 | 4.3495 | 4.2074 | 4.0463 | 3.8926 | 3.7421 | 3.6 | 3.4684 | 1.9947 | 1.5958 | 1.3653 | 4.7253 | 4.5747 | 4.4263 | 4.2726 | 4.1221 | 3.9579 | 3.8011 | 3.6484 | 3.5042 | 3.3705 | 1.7842 | 1.4221 | 1.2053 | 4.7663 | 4.6168 | 4.4684 | 4.3126 | 4.16 | 3.9895 | 3.8274 | 3.6695 | 3.5179 | 3.3779 | 1.7221 | 1.32 | 1.0884
|  | MILBORNE PORT | HE |  |  |  | 4.9042 | 4.8368 | 4.7674 | 4.6905 | 4.6116 | 4.5137 | 4.4295 | 4.3411 | 4.2579 | 4.1842 | 3.8105 | 3.24 | -0.87158 | 4.8821 | 4.8095 | 4.7337 | 4.6516 | 4.5663 | 4.4653 | 4.3789 | 4.2874 | 4.2011 | 4.1274 | 3.7505 | 3.1379 | 3.0263 | 4.9095 | 4.8474 | 4.7747 | 4.6926 | 4.6084 | 4.5042 | 4.4168 | 4.3221 | 4.2326 | 4.1537 | 3.7547 | 3.1116 | 2.9863
|  | MILBORNE PORT | CF |  |  |  | 4.9495 | 4.9095 | 4.8695 | 4.8284 | 4.7853 | 4.7337 | 4.6842 | 4.6326 | 4.5821 | 4.5347 | 4.2937 | 4.0916 | 3.8874 | 4.9316 | 4.8884 | 4.8442 | 4.7989 | 4.7526 | 4.6979 | 4.6453 | 4.5905 | 4.5368 | 4.4863 | 4.2295 | 4.0211 | 3.8084 | 4.9516 | 4.9147 | 4.8768 | 4.8389 | 4.7926 | 4.7379 | 4.6842 | 4.6284 | 4.5737 | 4.5232 | 4.2579 | 4.0368 | 3.8116
BRAMLEY (FLEE) | ALDERSHOT BSP | MILFORD | MINIMUM HEADROOM | SU 94719 43018 | YES | 0.12632 | 27.3579 | 27.0926 | 26.8263 | 26.5411 | 25.6484 | 24.8863 | 24.2211 | 23.5526 | 23.0979 | 22.6726 | 20.7674 | 19.0495 | 0.91579 | 23.6168 | 23.3516 | 22.8842 | 21.9379 | 20.8442 | 20.0011 | 19.2737 | 18.5358 | 18.0453 | 17.5863 | 15.5158 | 13.6263 | 11.9232 | 23.7884 | 23.5232 | 23.0705 | 22.1737 | 21.14 | 20.3095 | 19.5821 | 18.8442 | 18.3516 | 17.8926 | 15.8147 | 13.9168 | 12.2116
|  | MILFORD | EE |  |  |  | 27.4621 | 27.2568 | 27.0379 | 26.8063 | 26.26 | 25.5842 | 25.0158 | 24.4568 | 24.0832 | 23.7263 | 22.2084 | 20.8842 | 19.74 | 23.7211 | 23.5158 | 23.2968 | 22.5021 | 21.5095 | 20.7579 | 20.1337 | 19.5179 | 19.1189 | 18.7368 | 17.0958 | 15.6432 | 14.3642 | 23.8926 | 23.6874 | 23.4684 | 22.7158 | 21.7789 | 21.0642 | 20.4411 | 19.8242 | 19.4242 | 19.04 | 17.3874 | 15.9211 | 14.64
|  | MILFORD | HT |  |  |  | 27.3579 | 27.0926 | 26.8263 | 26.5411 | 25.6484 | 24.8863 | 24.2211 | 23.5526 | 23.0979 | 22.6726 | 20.7674 | 19.0495 | 17.5189 | 23.6168 | 23.3516 | 22.8842 | 21.9379 | 20.8442 | 20.0011 | 19.2737 | 18.5358 | 18.0453 | 17.5863 | 15.5158 | 13.6263 | 11.9232 | 23.7884 | 23.5232 | 23.0705 | 22.1737 | 21.14 | 20.3095 | 19.5821 | 18.8442 | 18.3516 | 17.8926 | 15.8147 | 13.9168 | 12.2116
|  | MILFORD | HE |  |  |  | 27.6063 | 27.4695 | 27.3179 | 27.1505 | 26.9716 | 26.4989 | 26.0421 | 25.5926 | 25.3221 | 25.0716 | 24.0737 | 23.2347 | 0.91579 | 23.8653 | 23.7284 | 23.5768 | 23.2463 | 22.3832 | 21.7537 | 21.2474 | 20.7505 | 20.4621 | 20.1947 | 19.1105 | 18.1779 | 17.3663 | 24.0368 | 23.9 | 23.7484 | 23.4305 | 22.6179 | 22.0211 | 21.5379 | 21.0579 | 20.7684 | 20.5 | 19.4116 | 18.4758 | 17.6621
|  | MILFORD | CF |  |  |  | 27.6895 | 27.6137 | 27.5358 | 27.4547 | 27.3716 | 27.2832 | 27.1947 | 27.1053 | 27.02 | 26.9326 | 26.5421 | 25.9642 | 25.4495 | 24.9842 | 23.8726 | 23.7947 | 23.7137 | 23.6305 | 23.4895 | 23.2221 | 22.9421 | 22.7842 | 22.6305 | 21.8937 | 21.2053 | 20.6211 | 25.1042 | 24.0442 | 23.9663 | 23.8853 | 23.8021 | 23.6642 | 23.4105 | 23.1442 | 22.9926 | 22.8421 | 22.1295 | 21.4758 | 20.9211
MANNINGTON GSP | ARNEWOOD | MILFORD-ON-SEA | MINIMUM HEADROOM | SZ 28252 93347 | YES | 0 | 12.62 | 26.3411 | 26.02 | 25.2358 | 24.4063 | 23.5442 | 22.6137 | 21.7253 | 20.8653 | 20.2295 | 17.9968 | 15.6389 | 2.6095 | 9.9516 | 23.3611 | 22.6116 | 21.7579 | 20.8537 | 19.9242 | 18.9084 | 17.9253 | 16.9737 | 16.2842 | 13.9411 | 11.4305 | 9.1621 | 9.6463 | 23.3674 | 23.0421 | 22.2137 | 21.3347 | 20.4158 | 19.3821 | 18.3895 | 17.4263 | 16.7263 | 14.3095 | 11.7126 | 9.4095
|  | MILFORD-ON-SEA | EE |  |  |  | 12.7305 | 26.5147 | 26.2821 | 25.8021 | 25.0642 | 24.3232 | 23.5558 | 22.7779 | 21.9221 | 21.2105 | 19.3116 | 17.2958 | 15.6811 | 10.1937 | 23.7326 | 23.1116 | 22.3653 | 21.56 | 20.7611 | 19.9326 | 19.0905 | 18.1442 | 17.3663 | 15.4295 | 13.3432 | 11.5747 | 9.7568 | 23.5411 | 23.3084 | 22.8074 | 22.0242 | 21.24 | 20.4126 | 19.5474 | 18.5874 | 17.7926 | 15.7537 | 13.5474 | 11.7421
|  | MILFORD-ON-SEA | HT |  |  |  | 12.62 | 26.3411 | 26.02 | 25.2358 | 24.4063 | 23.5442 | 22.6137 | 21.7253 | 20.8653 | 20.2295 | 17.9968 | 15.6389 | 13.5758 | 9.9516 | 23.3611 | 22.6116 | 21.7579 | 20.8537 | 19.9242 | 18.9084 | 17.9253 | 16.9737 | 16.2842 | 13.9411 | 11.4305 | 9.1621 | 9.6463 | 23.3674 | 23.0421 | 22.2137 | 21.3347 | 20.4158 | 19.3821 | 18.3895 | 17.4263 | 16.7263 | 14.3095 | 11.7126 | 9.4095
|  | MILFORD-ON-SEA | HE |  |  |  | 12.8811 | 26.7358 | 26.5747 | 26.3968 | 25.9084 | 25.2895 | 24.6589 | 24.0063 | 23.2884 | 22.7505 | 21.6232 | 20.4389 | 2.6095 | 10.4642 | 24.2095 | 23.7347 | 23.1316 | 22.4621 | 21.7926 | 21.1063 | 20.3937 | 19.6 | 19.0032 | 17.8316 | 16.5421 | 15.2916 | 9.9074 | 23.7621 | 23.6011 | 23.4232 | 22.9074 | 22.2516 | 21.5811 | 20.8789 | 20.0663 | 19.4642 | 18.2505 | 16.9263 | 15.6453
|  | MILFORD-ON-SEA | CF |  |  |  | 12.9663 | 26.8853 | 26.8021 | 26.7147 | 26.6242 | 26.52 | 26.4137 | 26.1684 | 25.86 | 25.5242 | 24.3958 | 23.6326 | 22.8789 | 10.5526 | 24.4674 | 24.2495 | 23.9484 | 23.6295 | 23.3432 | 23.0611 | 22.7505 | 22.4147 | 22.0463 | 20.8347 | 20.0158 | 19.1916 | 9.9926 | 23.9116 | 23.8284 | 23.7411 | 23.6505 | 23.5463 | 23.4411 | 23.18 | 22.8516 | 22.4937 | 21.3021 | 20.4726 | 19.6168
MANNINGTON GSP | MANNINGTON BSP | MILL LANE | MINIMUM HEADROOM | SU 14691 05633 | YES | 0.4 | 35.0895 | 34.9495 | 45.9347 | 45.1947 | 44.3474 | 43.1758 | 41.8053 | 40.4937 | 39.3705 | 38.2895 | 34.1179 | 31.3905 | -4.6716 | 30.0316 | 29.3926 | 38.6758 | 37.8758 | 36.9547 | 35.6558 | 34.1253 | 32.6537 | 31.3989 | 30.1884 | 25.5421 | 22.5421 | 19.6305 | 31.2453 | 30.6684 | 39.9516 | 39.1516 | 38.2295 | 36.9284 | 35.3937 | 33.92 | 32.6632 | 31.4495 | 26.7821 | 23.7579 | 20.8368
|  | MILL LANE | EE |  |  |  | 35.24 | 34.9495 | 46.5421 | 45.9726 | 45.3263 | 44.3726 | 43.3116 | 42.2095 | 40.9747 | 39.8947 | 36.0368 | 33.9253 | 31.9547 | 30.3589 | 29.8042 | 39.3347 | 38.7242 | 38.0242 | 36.9705 | 35.7874 | 34.5547 | 33.1642 | 31.9505 | 27.64 | 25.3274 | 23.1137 | 31.4063 | 31.1 | 40.6105 | 39.9979 | 39.2989 | 38.2421 | 37.0558 | 35.8189 | 34.4263 | 33.2063 | 28.8674 | 26.5232 | 24.2989
|  | MILL LANE | HT |  |  |  | 35.0895 | 36.6021 | 45.9347 | 45.1947 | 44.3474 | 43.1758 | 41.8053 | 40.4937 | 39.3705 | 38.2895 | 34.1179 | 31.3905 | 28.7905 | 30.0316 | 29.3926 | 38.6758 | 37.8758 | 36.9547 | 35.6558 | 34.1253 | 32.6537 | 31.3989 | 30.1884 | 25.5421 | 22.5421 | 19.6305 | 31.2453 | 30.6684 | 39.9516 | 39.1516 | 38.2295 | 36.9284 | 35.3937 | 33.92 | 32.6632 | 31.4495 | 26.7821 | 23.7579 | 20.8368
|  | MILL LANE | HE |  |  |  | 35.44 | 37.6621 | 47.3253 | 46.9316 | 46.4495 | 45.6411 | 44.7316 | 43.7463 | 42.6811 | 41.78 | 38.7137 | 37.3305 | -4.6716 | 30.7895 | 30.5442 | 40.1863 | 39.7642 | 39.2442 | 38.3453 | 37.3232 | 36.2126 | 35.0053 | 33.9832 | 30.5179 | 28.9747 | 27.4189 | 31.62 | 31.82 | 41.4611 | 41.04 | 40.5189 | 39.6179 | 38.5958 | 37.4821 | 36.2716 | 35.2484 | 31.7716 | 30.2189 | 28.6537
|  | MILL LANE | CF |  |  |  | 35.5589 | 35.4526 | 47.8095 | 47.6095 | 47.4053 | 47.1105 | 46.8042 | 46.4537 | 46.0463 | 45.6032 | 42.5305 | 41.5895 | 40.6979 | 30.96 | 30.8042 | 40.7011 | 40.4863 | 40.2663 | 39.9432 | 39.6074 | 39.2168 | 38.7621 | 38.2642 | 34.7568 | 33.7074 | 32.6937 | 31.7453 | 31.6326 | 41.9768 | 41.7621 | 41.5421 | 41.2179 | 40.88 | 40.4905 | 40.0347 | 39.5347 | 36.0232 | 34.9684 | 33.9505
COWLEY GSP | DRAYTON BSP | MILTON | MINIMUM HEADROOM | SU 49992 92060 | YES | 1.3347 | 69.3432 | 68.78 | 67.2253 | 65.0768 | 62.6832 | 61.3168 | 60.1905 | 57.9947 | 57.4863 | 55.7558 | 61.0253 | 58.9537 | -10.5779 | 60.7874 | 59.6705 | 57.6032 | 55.2695 | 52.5484 | 50.9547 | 49.9095 | 47.4084 | 46.7853 | 44.8137 | 50.6032 | 48.2621 | 45.6126 | 62.6663 | 61.5063 | 59.4379 | 57.0042 | 54.2726 | 52.6568 | 51.3653 | 48.8611 | 48.2042 | 46.2274 | 52.1526 | 49.7305 | 47.08
|  | MILTON | EE |  |  |  | 70.3621 | 69.0389 | 67.2253 | 65.1811 | 62.9232 | 61.3168 | 61.3737 | 59.2842 | 57.4863 | 55.7558 | 76.6779 | 71.7558 | 67.4263 | 61.1421 | 59.6705 | 57.6032 | 55.2695 | 52.6853 | 50.9547 | 51.2158 | 48.8316 | 46.7853 | 44.8137 | 80.6168 | 74.9947 | 70.0347 | 63.0137 | 61.5063 | 59.4379 | 57.1042 | 54.5179 | 52.6568 | 52.6453 | 50.2547 | 48.2042 | 46.2274 | 87.7779 | 82.1274 | 77.1421
|  | MILTON | HT |  |  |  | 70.0421 | 69.2232 | 67.2642 | 65.0768 | 62.6832 | 62.4821 | 60.1905 | 57.9947 | 84.7526 | 82.9379 | 74.6768 | 69.0147 | 63.8968 | 60.7874 | 60.0032 | 57.7758 | 55.2832 | 52.5484 | 52.5147 | 49.9095 | 47.4084 | 77.06 | 87.36 | 78.3958 | 71.9389 | 66.0821 | 62.6663 | 61.7211 | 59.4947 | 57.0042 | 54.2726 | 53.9737 | 51.3653 | 48.8611 | 83.4389 | 95.0642 | 85.6095 | 79.1411 | 73.2747
|  | MILTON | HE |  |  |  | 69.3432 | 69.2611 | 68.2095 | 66.4116 | 64.1611 | 62.7379 | 62.9737 | 61.0579 | 59.4347 | 57.8768 | 79.6147 | 75.4484 | -10.5779 | 61.5874 | 60.4337 | 58.6653 | 56.5989 | 54.0042 | 52.4695 | 52.9179 | 50.7189 | 48.8589 | 47.0726 | 83.4284 | 78.9421 | 74.7505 | 63.4337 | 62.3137 | 60.5158 | 58.4516 | 55.86 | 54.1968 | 54.3789 | 52.1789 | 50.3168 | 48.5284 | 90.9705 | 86.1526 | 81.9526
|  | MILTON | CF |  |  |  | 69.4726 | 68.78 | 68.6526 | 68.2968 | 67.3053 | 66.4011 | 66.3042 | 65.3179 | 64.4074 | 63.4568 | 61.0253 | 58.9537 | 56.6716 | 62.0084 | 60.4084 | 59.5832 | 58.6232 | 57.48 | 56.4432 | 56.4589 | 55.3232 | 54.2779 | 53.1842 | 50.6032 | 48.2621 | 45.6126 | 63.5821 | 62.4874 | 61.5968 | 60.6379 | 59.4968 | 58.4611 | 58.3158 | 57.1821 | 56.1379 | 55.0463 | 52.1526 | 49.7305 | 47.08
MANNINGTON GSP | SHAFTESBURY BSP | MINCHINGTON | MINIMUM HEADROOM | ST 96164 14520 | YES | 0 | 5.6 | 5.5189 | 5.4389 | 5.3589 | 5.2779 | 5.1989 | 5.12 | 5.0495 | 4.9842 | 4.9221 | 4.6505 | 4.3737 | 1.28 | 5.0295 | 4.9421 | 4.8568 | 4.7716 | 4.6863 | 4.6021 | 4.5189 | 4.4432 | 4.3747 | 4.3084 | 4.0168 | 3.7116 | 3.4137 | 5.2316 | 5.1495 | 5.0695 | 4.9884 | 4.9074 | 4.8274 | 4.7474 | 4.6758 | 4.6105 | 4.5474 | 4.2737 | 3.9926 | 3.7211
|  | MINCHINGTON | EE |  |  |  | 5.6379 | 5.5737 | 5.5105 | 5.4463 | 5.3821 | 5.3168 | 5.2547 | 5.1958 | 5.1389 | 5.0884 | 4.8779 | 4.6863 | 4.5011 | 5.0705 | 5.0021 | 4.9347 | 4.8663 | 4.7979 | 4.7295 | 4.6642 | 4.6011 | 4.5411 | 4.4874 | 4.2621 | 4.0516 | 3.8453 | 5.2695 | 5.2053 | 5.1421 | 5.0768 | 5.0116 | 4.9463 | 4.8842 | 4.8242 | 4.7674 | 4.7158 | 4.5032 | 4.3084 | 4.1211
|  | MINCHINGTON | HT |  |  |  | 5.6 | 5.5189 | 5.4389 | 5.3589 | 5.2779 | 5.1989 | 5.12 | 5.0495 | 4.9842 | 4.9221 | 4.6505 | 4.3737 | 4.1063 | 5.0295 | 4.9421 | 4.8568 | 4.7716 | 4.6863 | 4.6021 | 4.5189 | 4.4432 | 4.3747 | 4.3084 | 4.0168 | 3.7116 | 3.4137 | 5.2316 | 5.1495 | 5.0695 | 4.9884 | 4.9074 | 4.8274 | 4.7474 | 4.6758 | 4.6105 | 4.5474 | 4.2737 | 3.9926 | 3.7211
|  | MINCHINGTON | HE |  |  |  | 5.6863 | 5.6474 | 5.6074 | 5.5642 | 5.52 | 5.4747 | 5.4316 | 5.3905 | 5.3516 | 5.3168 | 5.1926 | 5.0758 | 1.28 | 5.1232 | 5.0821 | 5.0389 | 4.9937 | 4.9484 | 4.9 | 4.8558 | 4.8126 | 4.7716 | 4.7347 | 4.6032 | 4.4747 | 4.3484 | 5.3189 | 5.28 | 5.2389 | 5.1958 | 5.1516 | 5.1063 | 5.0632 | 5.0221 | 4.9821 | 4.9474 | 4.8211 | 4.7032 | 4.5895
|  | MINCHINGTON | CF |  |  |  | 5.7116 | 5.6895 | 5.6663 | 5.6432 | 5.6189 | 5.5947 | 5.5695 | 5.5453 | 5.5211 | 5.4968 | 5.3884 | 5.2979 | 5.2158 | 5.1505 | 5.1263 | 5.1021 | 5.0768 | 5.0516 | 5.0253 | 4.9989 | 4.9726 | 4.9463 | 4.9211 | 4.8053 | 4.7053 | 4.6116 | 5.3453 | 5.3232 | 5.2989 | 5.2758 | 5.2516 | 5.2263 | 5.2021 | 5.1768 | 5.1516 | 5.1284 | 5.0189 | 4.9263 | 4.8421
MINETY GSP | CIRENCESTER BSP | MINETY VILLAGE | MINIMUM HEADROOM | SU 01647 91932 | YES | 3.1579 | 16.4168 | 14.3368 | 14.2589 | 11.0147 | 10.3337 | 8.9747 | 7.6916 | 6.4653 | 5.3442 | 4.0021 | 0.53895 | -0.62632 | -2.4568 | 15.0368 | 12.6347 | 12.5579 | 9.3158 | 8.5495 | 6.9905 | 5.5221 | 4.1221 | 2.8474 | 1.3126 | -2.5021 | -3.5926 | -4.3989 | 15.1621 | 12.7242 | 12.6463 | 9.4021 | 8.6368 | 7.0674 | 5.5863 | 4.1726 | 2.8832 | 1.3316 | -2.6032 | -3.8389 | -4.7021
|  | MINETY VILLAGE | EE |  |  |  | 16.4905 | 14.3368 | 14.2589 | 11.0147 | 10.5358 | 9.2042 | 7.9368 | 6.7168 | 5.5863 | 4.2484 | 0.75263 | -0.46947 | -1.1474 | 15.1147 | 12.6347 | 12.5579 | 9.3158 | 8.7695 | 7.2411 | 5.7968 | 4.4105 | 3.1316 | 1.6137 | -2.1674 | -3.2442 | -3.9158 | 15.2411 | 12.7242 | 12.6463 | 9.4021 | 8.8558 | 7.3158 | 5.8526 | 4.4484 | 3.1474 | 1.6053 | -2.3453 | -3.6253 | -4.3589
|  | MINETY VILLAGE | HT |  |  |  | 16.4168 | 16.0305 | 15.4211 | 11.4305 | 10.3337 | 8.9747 | 7.6916 | 6.4653 | 5.3442 | 4.0021 | 0.53895 | -0.62632 | -1.4179 | 15.0368 | 14.6032 | 13.9158 | 9.82 | 8.5495 | 6.9905 | 5.5221 | 4.1221 | 2.8474 | 1.3126 | -2.5021 | -3.5926 | -4.3989 | 15.1621 | 14.7232 | 14.0242 | 9.9063 | 8.6368 | 7.0674 | 5.5863 | 4.1726 | 2.8832 | 1.3316 | -2.6032 | -3.8389 | -4.7021
|  | MINETY VILLAGE | HE |  |  |  | 16.5916 | 14.4116 | 14.3611 | 11.1463 | 10.8305 | 9.5484 | 8.3558 | 7.2137 | 6.1684 | 4.9232 | 1.9811 | 1.4568 | -2.4568 | 15.2232 | 12.7095 | 12.6589 | 9.4442 | 9.0853 | 7.6053 | 6.2274 | 4.9126 | 3.7095 | 2.2705 | -1.0432 | -1.5484 | -2.0379 | 15.3516 | 12.7989 | 12.7484 | 9.5337 | 9.1737 | 7.6874 | 6.3021 | 4.9779 | 3.7674 | 2.3189 | -1.0632 | -1.6253 | -2.1653
|  | MINETY VILLAGE | CF |  |  |  | 16.6674 | 16.5053 | 16.2505 | 12.7589 | 12.3274 | 11.7989 | 11.2526 | 10.6863 | 10.1274 | 9.4074 | 7.6337 | 7.3211 | 6.9916 | 15.3074 | 15.1242 | 14.8337 | 11.2947 | 10.8011 | 10.2053 | 9.5842 | 8.9316 | 8.2863 | 7.4505 | 5.4242 | 5.1189 | 4.7947 | 15.4358 | 15.2495 | 14.9547 | 11.4095 | 10.9074 | 10.2958 | 9.6621 | 9.0053 | 8.3568 | 7.5189 | 5.4726 | 5.1368 | 4.7779
BRAMLEY (FLEE) | BURGHFIELD RESERVE | MORTIMER | MINIMUM HEADROOM | SU 62236 64103 | YES | 0 | 17.4274 | 17.2274 | 17.0242 | 16.8084 | 16.5853 | 16.1484 | 15.2853 | 14.2474 | 14.0495 | 13.8632 | 11.8695 | 9.3211 | -0.44 | 14.9368 | 14.5358 | 14.1737 | 13.7884 | 13.4032 | 12.8179 | 11.8316 | 10.6347 | 10.4411 | 10.2589 | 8.0758 | 5.2168 | 4.4032 | 15.4905 | 15.1463 | 14.7716 | 14.3916 | 14.0126 | 13.4368 | 12.4737 | 11.2779 | 11.0789 | 10.8926 | 8.6789 | 5.7853 | 4.9558
|  | MORTIMER | EE |  |  |  | 17.5074 | 17.3516 | 17.1853 | 17.0095 | 16.8263 | 16.6253 | 16.4263 | 16.2358 | 15.9621 | 15.6968 | 14.5737 | 12.4042 | 10.8642 | 15.1 | 14.7821 | 14.4989 | 14.2084 | 13.9021 | 13.5863 | 13.2747 | 12.9716 | 12.6716 | 12.3937 | 11.2295 | 8.7821 | 7.0358 | 15.5758 | 15.4053 | 15.1095 | 14.8063 | 14.5021 | 14.1874 | 13.8768 | 13.5726 | 13.2726 | 12.9947 | 11.8147 | 9.3189 | 7.5558
|  | MORTIMER | HT |  |  |  | 17.4274 | 17.2274 | 17.0242 | 16.8084 | 16.5853 | 16.1484 | 15.2853 | 14.2474 | 14.0495 | 13.8632 | 11.8695 | 9.3211 | 8.5537 | 14.9368 | 14.5358 | 14.1737 | 13.7884 | 13.4032 | 12.8179 | 11.8316 | 10.6347 | 10.4411 | 10.2589 | 8.0758 | 5.2168 | 4.4032 | 15.4905 | 15.1463 | 14.7716 | 14.3916 | 14.0126 | 13.4368 | 12.4737 | 11.2779 | 11.0789 | 10.8926 | 8.6789 | 5.7853 | 4.9558
|  | MORTIMER | HE |  |  |  | 17.6189 | 17.5147 | 17.4021 | 17.2758 | 17.14 | 16.9863 | 16.8389 | 16.7 | 16.5684 | 16.4537 | 16.04 | 14.5326 | -0.44 | 15.3242 | 15.1116 | 14.9316 | 14.7389 | 14.5379 | 14.3253 | 14.1189 | 13.92 | 13.7305 | 13.5526 | 12.8716 | 11.0316 | 9.6232 | 15.6947 | 15.5832 | 15.4663 | 15.3358 | 15.1579 | 14.9358 | 14.7232 | 14.5147 | 14.32 | 14.1421 | 13.4579 | 11.6411 | 10.2211
|  | MORTIMER | CF |  |  |  | 17.6821 | 17.6253 | 17.5674 | 17.5074 | 17.4442 | 17.3737 | 17.3032 | 17.2337 | 17.1653 | 17.0979 | 16.7905 | 16.5137 | 15.6242 | 15.4442 | 15.3179 | 15.2126 | 15.1042 | 14.9926 | 14.8737 | 14.7537 | 14.6358 | 14.5211 | 14.4063 | 13.8579 | 13.2189 | 12.1789 | 15.7621 | 15.7 | 15.6389 | 15.5758 | 15.5095 | 15.4358 | 15.3632 | 15.2526 | 15.1326 | 15.0126 | 14.4505 | 13.8221 | 12.8053
MANNINGTON GSP | SALISBURY | NETHERHAMPTON | MINIMUM HEADROOM | SU 12478 29102 | YES | 9.4737 | 11.1274 | 1.4389 | 1.1389 | 0.95789 | 0.28947 | -0.63579 | -1.6337 | -2.5579 | -3.3263 | -3.7263 | -4.7295 | -5.38 | -13.06 | 9.76 | -0.16632 | -0.50316 | -0.69579 | -1.4663 | -2.54 | -3.6968 | -4.7716 | -5.6632 | -6.1211 | -7.2463 | -7.9642 | -8.6358 | 10.12 | 0.19474 | -0.14211 | -0.33474 | -1.1042 | -2.1758 | -3.3316 | -4.4042 | -5.2947 | -5.7516 | -6.8768 | -7.5958 | -8.2684
|  | NETHERHAMPTON | EE |  |  |  | 11.1663 | 1.5979 | 1.3063 | 1.1474 | 0.56737 | -0.23895 | -0.99789 | -1.8442 | -2.8305 | -3.2453 | -4.2147 | -4.7021 | -5.1463 | 9.8432 | 0.0094737 | -0.31895 | -0.49053 | -1.1589 | -2.0958 | -2.9737 | -3.9589 | -5.1105 | -5.5863 | -6.6789 | -7.2189 | -7.7179 | 10.2074 | 0.37053 | 0.042105 | -0.12947 | -0.79684 | -1.7316 | -2.6095 | -3.5926 | -4.7421 | -5.2179 | -6.3105 | -6.8526 | -7.3526
|  | NETHERHAMPTON | HT |  |  |  | 11.1274 | 1.4389 | 1.1389 | 0.95789 | 0.28947 | -0.63579 | -1.6337 | -2.5579 | -3.3263 | -3.7263 | -4.7295 | -5.38 | -5.9832 | 9.76 | -0.16632 | -0.50316 | -0.69579 | -1.4663 | -2.54 | -3.6968 | -4.7716 | -5.6632 | -6.1211 | -7.2463 | -7.9642 | -8.6358 | 10.12 | 0.19474 | -0.14211 | -0.33474 | -1.1042 | -2.1758 | -3.3316 | -4.4042 | -5.2947 | -5.7516 | -6.8768 | -7.5958 | -8.2684
|  | NETHERHAMPTON | HE |  |  |  | 11.2211 | 1.6937 | 1.5179 | 1.4084 | 0.86947 | 0.092632 | -0.64211 | -1.4474 | -2.3347 | -2.7632 | -3.5053 | -3.8116 | -13.06 | 9.9558 | 0.18632 | -0.087368 | -0.20632 | -0.83053 | -1.7337 | -2.5905 | -3.5284 | -4.5663 | -5.0621 | -5.9063 | -6.2484 | -6.5653 | 10.3274 | 0.54737 | 0.27263 | 0.15474 | -0.46842 | -1.3705 | -2.2253 | -3.1632 | -4.1989 | -4.6947 | -5.5368 | -5.88 | -6.1958
|  | NETHERHAMPTON | CF |  |  |  | 11.2526 | 1.7495 | 1.7189 | 1.6874 | 1.6537 | 1.5221 | 1.2842 | 0.98316 | 0.59684 | 0.37158 | -1.1095 | -1.3484 | -1.5537 | 10.1632 | 0.55684 | 0.44421 | 0.38842 | 0.17053 | -0.08 | -0.35579 | -0.70526 | -1.1547 | -1.4147 | -3.1379 | -3.4074 | -3.6411 | 10.5705 | 0.94 | 0.81474 | 0.75579 | 0.53053 | 0.28 | 0.0052632 | -0.34316 | -0.79263 | -1.0516 | -2.7737 | -3.0411 | -3.2758
BOTLEY WOOD GSP | NETLEY COMMON BSP | NETLEY COMMON | MINIMUM HEADROOM | SU 47615 12025 | YES | 2.0432 | 36.5737 | 35.9105 | 35.2411 | 34.0779 | 31.6516 | 30.3758 | 28.9453 | 27.6432 | 26.3189 | 24.9505 | 18.1326 | 12.2547 | -29.7326 | 28.7263 | 27.0779 | 24.5116 | 21.06 | 18.4011 | 17.0547 | 15.5337 | 14.1274 | 12.6832 | 11.1779 | 3.6074 | -2.9558 | -8.9253 | 30.0505 | 28.9126 | 26.3621 | 22.8242 | 20.1042 | 18.7389 | 17.1937 | 15.7832 | 14.3368 | 12.8284 | 5.2379 | -1.3495 | -7.3295
|  | NETLEY COMMON | EE |  |  |  | 36.8253 | 36.3084 | 38.2695 | 35.6768 | 33.3579 | 32.0905 | 30.7947 | 29.6842 | 28.5674 | 27.4642 | 22.1021 | 17.4547 | 13.3842 | 29.2853 | 27.9295 | 25.6621 | 22.7926 | 20.3084 | 18.9337 | 17.5253 | 16.3274 | 15.1211 | 13.92 | 7.9863 | 2.7979 | -1.8053 | 31.2379 | 29.8547 | 27.5337 | 24.5905 | 21.9737 | 20.5968 | 19.1842 | 17.9832 | 16.7726 | 15.5663 | 9.6053 | 4.3853 | -0.22842
|  | NETLEY COMMON | HT |  |  |  | 36.5737 | 35.9105 | 35.2411 | 34.0779 | 31.6516 | 30.3758 | 28.9453 | 27.6432 | 26.3189 | 24.9505 | 18.1326 | 12.2547 | 6.9537 | 28.7263 | 27.0779 | 24.5116 | 21.06 | 18.4011 | 17.0547 | 15.5337 | 14.1274 | 12.6832 | 11.1779 | 3.6074 | -2.9558 | -8.9253 | 30.0505 | 28.9126 | 26.3621 | 22.8242 | 20.1042 | 18.7389 | 17.1937 | 15.7832 | 14.3368 | 12.8284 | 5.2379 | -1.3495 | -7.3295
|  | NETLEY COMMON | HE |  |  |  | 37.1642 | 36.8053 | 39.6211 | 37.3179 | 35.2884 | 34.2905 | 33.2758 | 32.4526 | 31.6147 | 30.7779 | 26.92 | 23.6189 | -29.7326 | 30.0389 | 29.0358 | 27.1105 | 24.5495 | 22.4126 | 21.3316 | 20.2263 | 19.3421 | 18.4347 | 17.52 | 13.2242 | 9.4884 | 6.1621 | 32.0042 | 30.9811 | 29.0074 | 26.38 | 24.0779 | 22.9947 | 21.8884 | 21.0021 | 20.0937 | 19.1758 | 14.8684 | 11.1232 | 7.7874
|  | NETLEY COMMON | CF |  |  |  | 37.3653 | 37.1579 | 36.9453 | 36.7232 | 36.4937 | 36.2537 | 36.0074 | 35.7663 | 35.5274 | 35.2895 | 33.7958 | 31.5821 | 29.6474 | 29.8568 | 29.6358 | 28.8758 | 27.8305 | 26.9716 | 26.5379 | 26.0253 | 25.46 | 24.8116 | 24.1168 | 20.7874 | 18.3463 | 16.1779 | 30.8632 | 30.6558 | 30.4084 | 29.6684 | 28.8368 | 28.4116 | 27.8989 | 27.3242 | 26.66 | 25.9505 | 22.5474 | 20.0421 | 17.8253
MANNINGTON GSP | ARNEWOOD | NEW MILTON | MINIMUM HEADROOM | SZ 23049 94942 | YES | 0.37579 | 35.4474 | 34.9863 | 34.3768 | 33.5495 | 32.7189 | 31.7789 | 30.7305 | 29.76 | 28.1411 | 27.7326 | 23.8168 | 21.2379 | -8.3021 | 30.0021 | 29.0979 | 28.2147 | 27.3305 | 26.4432 | 25.4368 | 24.3032 | 23.2516 | 21.4274 | 21.0253 | 16.7547 | 13.9937 | 10.5537 | 30.6284 | 29.7242 | 28.8432 | 27.9579 | 27.0726 | 26.0621 | 24.9263 | 23.8705 | 22.0442 | 21.6358 | 17.3337 | 14.5358 | 11.0832
|  | NEW MILTON | EE |  |  |  | 35.6284 | 35.2716 | 34.8905 | 34.4621 | 33.7916 | 33.0074 | 32.1347 | 31.2884 | 30.4589 | 29.6821 | 27.0284 | 24.3674 | 22.0168 | 30.3821 | 29.7147 | 29.0253 | 28.3211 | 27.6095 | 26.7684 | 25.8263 | 24.9105 | 24.0126 | 23.1705 | 20.3505 | 17.46 | 14.8305 | 30.9926 | 30.3411 | 29.6505 | 28.9484 | 28.2358 | 27.3926 | 26.4442 | 25.5242 | 24.6211 | 23.7716 | 20.9042 | 17.96 | 15.3158
|  | NEW MILTON | HT |  |  |  | 35.4474 | 34.9863 | 34.3768 | 33.5495 | 32.7189 | 31.7789 | 30.7305 | 29.76 | 28.1411 | 27.7326 | 23.8168 | 21.2379 | 18.1526 | 30.0021 | 29.0979 | 28.2147 | 27.3305 | 26.4432 | 25.4368 | 24.3032 | 23.2516 | 21.4274 | 21.0253 | 16.7547 | 13.9937 | 10.5537 | 30.6284 | 29.7242 | 28.8432 | 27.9579 | 27.0726 | 26.0621 | 24.9263 | 23.8705 | 22.0442 | 21.6358 | 17.3337 | 14.5358 | 11.0832
|  | NEW MILTON | HE |  |  |  | 35.8705 | 35.6284 | 35.3589 | 35.6284 | 35.1632 | 34.5695 | 33.8958 | 33.2432 | 32.6084 | 32.0274 | 30.3547 | 28.6537 | -8.3021 | 30.88 | 30.4695 | 30.0463 | 29.5926 | 29.1021 | 28.4695 | 27.7368 | 27.0284 | 26.3379 | 25.7032 | 23.9158 | 22.0263 | 20.2463 | 31.3295 | 31.0695 | 30.6653 | 30.2179 | 29.7284 | 29.0926 | 28.3579 | 27.6484 | 26.9558 | 26.3179 | 24.5116 | 22.6084 | 20.8158
|  | NEW MILTON | CF |  |  |  | 36.0137 | 35.8768 | 35.7358 | 35.5895 | 35.4368 | 35.2758 | 35.1105 | 34.9474 | 34.7084 | 34.3305 | 33.0958 | 31.9705 | 30.8811 | 31.1368 | 30.8884 | 30.6379 | 30.3821 | 30.1189 | 29.7958 | 29.3958 | 28.9853 | 28.5653 | 28.1484 | 26.8305 | 25.5821 | 24.3516 | 31.4726 | 31.3358 | 31.1947 | 30.9874 | 30.7379 | 30.42 | 30.02 | 29.6084 | 29.1863 | 28.7705 | 27.4463 | 26.1895 | 24.9516
FAWLEY GSP | COWES & WOOTTON COMMON BSP | NEWPORT | MINIMUM HEADROOM | SZ 50076 89544 | YES | 0.029474 | 64.9884 | 64.6495 | 64.2874 | 63.9032 | 64.7484 | 62.4884 | 60.4705 | 58.7621 | 57.2063 | 55.8147 | 49.9168 | 45.0505 | 8.3368 | 58.2211 | 57.0526 | 55.3779 | 53.5168 | 53.4274 | 50.8747 | 48.6063 | 46.6937 | 44.9558 | 43.4063 | 36.8747 | 31.5116 | 26.7853 | 59.8916 | 59.1011 | 57.4284 | 55.5705 | 55.2874 | 52.7263 | 50.4484 | 48.5242 | 46.7758 | 45.2137 | 38.6032 | 33.1484 | 28.3853
|  | NEWPORT | EE |  |  |  | 64.9884 | 64.6495 | 64.2874 | 63.9032 | 64.9758 | 64.3684 | 62.5337 | 60.8632 | 59.2253 | 57.8747 | 52.5979 | 48.4958 | 45.1347 | 58.5558 | 57.6895 | 56.4474 | 55.0337 | 55.3674 | 53.0368 | 50.9232 | 49.0537 | 47.2189 | 45.7189 | 39.92 | 35.46 | 31.6863 | 59.8916 | 59.2726 | 58.2368 | 57.0653 | 57.2274 | 54.8884 | 52.7611 | 50.8768 | 49.0263 | 47.5105 | 41.6011 | 37.0137 | 33.2011
|  | NEWPORT | HT |  |  |  | 69.1558 | 68.0989 | 66.6095 | 64.9589 | 64.7484 | 62.4884 | 60.4705 | 58.7621 | 57.2063 | 55.8147 | 49.9168 | 45.0505 | 40.84 | 58.2211 | 57.0526 | 55.3779 | 53.5168 | 53.4274 | 50.8747 | 48.6063 | 46.6937 | 44.9558 | 43.4063 | 36.8747 | 31.5116 | 26.7853 | 60.2684 | 59.1011 | 57.4284 | 55.5705 | 55.2874 | 52.7263 | 50.4484 | 48.5242 | 46.7758 | 45.2137 | 38.6032 | 33.1484 | 28.3853
|  | NEWPORT | HE |  |  |  | 65.2095 | 64.9737 | 64.7137 | 64.4253 | 65.5926 | 65.2379 | 64.1853 | 62.6916 | 61.2589 | 60.1811 | 55.9968 | 53.0653 | 8.3368 | 58.9589 | 58.4232 | 57.3968 | 56.1832 | 56.7116 | 54.6611 | 52.7095 | 51.0189 | 49.3968 | 48.1853 | 43.4905 | 40.1926 | 37.2768 | 60.1284 | 59.8695 | 59.0642 | 58.0684 | 58.5747 | 56.5168 | 54.5579 | 52.8611 | 51.2316 | 50.0116 | 45.2726 | 41.9379 | 38.9895
|  | NEWPORT | CF |  |  |  | 65.3411 | 65.2063 | 65.0663 | 64.9211 | 64.7705 | 64.6021 | 64.4326 | 64.2653 | 64.0989 | 63.9368 | 60.8821 | 60.7453 | 59.1105 | 59.1642 | 58.9642 | 58.6895 | 58.2474 | 57.7126 | 57.0989 | 56.4453 | 55.7389 | 54.9221 | 54.0568 | 48.7937 | 48.8221 | 46.9737 | 60.2737 | 60.1274 | 59.9726 | 59.7632 | 59.3189 | 58.8074 | 58.2642 | 57.6811 | 56.9874 | 56.12 | 50.84 | 50.6337 | 48.7621
BRAMLEY (FLEE) | ALDERSHOT BSP | NORMANDY | MINIMUM HEADROOM | SU 93221 52894 | YES | 0 | 6.2974 | 6.1837 | 6.0595 | 5.9216 | 5.7721 | 5.6153 | 5.4521 | 5.2921 | 5.1342 | 5.0637 | 4.7689 | 4.3342 | 1.8447 | 6.2521 | 6.1195 | 5.9742 | 5.8111 | 5.6342 | 5.4489 | 5.2637 | 5.0858 | 4.9079 | 4.8332 | 4.5216 | 4.0405 | 3.8584 | 6.3721 | 6.2468 | 6.1079 | 5.9521 | 5.7763 | 5.59 | 5.4047 | 5.2258 | 5.0479 | 4.9721 | 4.6553 | 4.1689 | 3.9847
|  | NORMANDY | EE |  |  |  | 6.3332 | 6.2384 | 6.1311 | 6.01 | 5.8774 | 5.7353 | 5.5932 | 5.4468 | 5.2974 | 5.2416 | 5.0068 | 4.7468 | 4.5289 | 6.2921 | 6.1816 | 6.0542 | 5.91 | 5.7521 | 5.5837 | 5.4153 | 5.2521 | 5.0847 | 5.0268 | 4.7847 | 4.5037 | 4.2626 | 6.4026 | 6.3058 | 6.1847 | 6.0479 | 5.8942 | 5.7247 | 5.5563 | 5.3921 | 5.2237 | 5.1647 | 4.9142 | 4.6268 | 4.3837
|  | NORMANDY | HT |  |  |  | 6.2974 | 6.1837 | 6.0595 | 5.9216 | 5.7721 | 5.6153 | 5.4521 | 5.2921 | 5.1342 | 5.0637 | 4.7689 | 4.3342 | 4.1637 | 6.2521 | 6.1195 | 5.9742 | 5.8111 | 5.6342 | 5.4489 | 5.2637 | 5.0858 | 4.9079 | 4.8332 | 4.5216 | 4.0405 | 3.8584 | 6.3721 | 6.2468 | 6.1079 | 5.9521 | 5.7763 | 5.59 | 5.4047 | 5.2258 | 5.0479 | 4.9721 | 4.6553 | 4.1689 | 3.9847
|  | NORMANDY | HE |  |  |  | 6.3647 | 6.3111 | 6.2268 | 6.1279 | 6.0153 | 5.8921 | 5.7711 | 5.6511 | 5.5226 | 5.4858 | 5.3511 | 5.1879 | 1.8447 | 6.3247 | 6.2637 | 6.1616 | 6.0437 | 5.9079 | 5.7605 | 5.6142 | 5.4721 | 5.3268 | 5.2889 | 5.15 | 4.97 | 4.8079 | 6.4289 | 6.3847 | 6.2889 | 6.1763 | 6.0479 | 5.9016 | 5.7563 | 5.6121 | 5.4668 | 5.4279 | 5.2858 | 5.1037 | 4.9395
|  | NORMANDY | CF |  |  |  | 6.3795 | 6.3668 | 6.3342 | 6.2868 | 6.2353 | 6.1784 | 6.1205 | 6.0584 | 5.9921 | 5.97 | 5.8605 | 5.7532 | 5.6711 | 6.3395 | 6.3268 | 6.2889 | 6.2321 | 6.17 | 6.1026 | 6.0332 | 5.9574 | 5.8753 | 5.85 | 5.7311 | 5.6058 | 5.5068 | 6.4437 | 6.4311 | 6.4089 | 6.3553 | 6.2974 | 6.2332 | 6.1668 | 6.0953 | 6.0174 | 5.9921 | 5.8711 | 5.7447 | 5.6447
NURSLING GSP | ROWNHAMS | NORTH BADDESLEY | MINIMUM HEADROOM | SU 38080 20568 | YES | 0.21789 | 35.3032 | 35.4705 | 35.2663 | 34.4189 | 33.4389 | 32.4695 | 31.7021 | 31.1779 | 30.6853 | 30.2211 | 27.9379 | 25.08 | -46.6126 | 30.4968 | 29.6653 | 28.6263 | 27.6863 | 26.5895 | 25.5168 | 24.68 | 24.1253 | 23.6042 | 23.1105 | 20.6695 | 17.5137 | 14.5411 | 30.5116 | 30.7 | 29.8526 | 28.9116 | 27.8147 | 26.7347 | 25.8947 | 25.3337 | 24.8063 | 24.3063 | 21.8242 | 18.6189 | 15.6263
|  | NORTH BADDESLEY | EE |  |  |  | 35.3032 | 36.5632 | 35.7958 | 35.1726 | 34.4326 | 33.6095 | 32.7379 | 32.1126 | 31.5926 | 31.1726 | 29.3779 | 27.0389 | 24.9558 | 30.7621 | 30.0695 | 29.2105 | 28.5232 | 27.7021 | 26.7895 | 25.8211 | 25.1432 | 24.5863 | 24.1463 | 22.2716 | 19.7168 | 17.3674 | 30.5116 | 31.2947 | 30.4358 | 29.7484 | 28.9253 | 28.0084 | 27.0326 | 26.3474 | 25.7832 | 25.3347 | 23.4 | 20.7789 | 18.4074
|  | NORTH BADDESLEY | HT |  |  |  | 36.9442 | 36.1926 | 35.2663 | 34.4189 | 33.4389 | 32.4695 | 31.7021 | 31.1779 | 30.6853 | 30.2211 | 27.9379 | 25.08 | 22.4442 | 30.4968 | 29.6653 | 28.6263 | 27.6863 | 26.5895 | 25.5168 | 24.68 | 24.1253 | 23.6042 | 23.1105 | 20.6695 | 17.5137 | 14.5411 | 31.7232 | 30.8905 | 29.8526 | 28.9116 | 27.8147 | 26.7347 | 25.8947 | 25.3337 | 24.8063 | 24.3063 | 21.8242 | 18.6189 | 15.6263
|  | NORTH BADDESLEY | HE |  |  |  | 35.4653 | 37.0474 | 36.4295 | 35.9453 | 35.3379 | 34.6379 | 33.9095 | 33.4179 | 33.0579 | 32.7874 | 31.6884 | 30.0716 | -46.6126 | 31.1189 | 30.5979 | 29.8989 | 29.3642 | 28.6853 | 27.9042 | 27.0916 | 26.5516 | 26.1653 | 25.8821 | 24.7232 | 22.9021 | 21.1074 | 30.7 | 31.8242 | 31.1253 | 30.5895 | 29.9105 | 29.1263 | 28.3084 | 27.7663 | 27.3768 | 27.0905 | 25.9053 | 24.0663 | 22.2526
|  | NORTH BADDESLEY | CF |  |  |  | 35.56 | 35.4705 | 35.3779 | 35.2832 | 35.1832 | 35.0747 | 34.9632 | 34.8558 | 34.7484 | 34.64 | 33.8621 | 32.8179 | 31.8147 | 31.3895 | 31.0905 | 30.7589 | 30.5432 | 30.3074 | 30.0379 | 29.7832 | 29.5221 | 29.16 | 28.7821 | 27.0621 | 25.8874 | 24.7463 | 30.8168 | 30.7 | 30.5768 | 30.4663 | 30.3484 | 30.2189 | 30.0884 | 29.9611 | 29.8211 | 29.6768 | 28.2705 | 27.0863 | 25.9326
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | NORTH FAREHAM | MINIMUM HEADROOM | SU 56427 07430 | YES | 0.12947 | 16.9179 | 16.5958 | 16.2705 | 15.9232 | 15.4737 | 14.9 | 14.3221 | 13.7926 | 13.2937 | 12.8253 | 10.2653 | 7.6716 | -13.6168 | 12.9768 | 12.3032 | 11.6905 | 11.0684 | 10.4463 | 9.8221 | 9.1958 | 8.6168 | 8.0705 | 7.5547 | 4.7189 | 1.8758 | -0.68842 | 14.2589 | 13.6074 | 13.0126 | 12.4063 | 11.8011 | 11.1895 | 10.5758 | 10.0095 | 9.4758 | 8.9716 | 6.1411 | 3.26 | 0.68421
|  | NORTH FAREHAM | EE |  |  |  | 17.0442 | 16.7937 | 16.5274 | 16.2453 | 15.9505 | 15.6347 | 15.2474 | 14.8042 | 14.3705 | 13.9589 | 11.9432 | 9.8537 | 8.0705 | 13.2537 | 12.7263 | 12.24 | 11.7442 | 11.2432 | 10.7326 | 10.2326 | 9.7579 | 9.2905 | 8.8453 | 6.5958 | 4.3042 | 2.3095 | 14.5263 | 14.0158 | 13.5432 | 13.0611 | 12.5716 | 12.0705 | 11.5789 | 11.1084 | 10.6463 | 10.2063 | 7.9989 | 5.6558 | 3.6453
|  | NORTH FAREHAM | HT |  |  |  | 16.9179 | 16.5958 | 16.2705 | 15.9232 | 15.4737 | 14.9 | 14.3221 | 13.7926 | 13.2937 | 12.8253 | 10.2653 | 7.6716 | 5.3758 | 12.9768 | 12.3032 | 11.6905 | 11.0684 | 10.4463 | 9.8221 | 9.1958 | 8.6168 | 8.0705 | 7.5547 | 4.7189 | 1.8758 | -0.68842 | 14.2589 | 13.6074 | 13.0126 | 12.4063 | 11.8011 | 11.1895 | 10.5758 | 10.0095 | 9.4758 | 8.9716 | 6.1411 | 3.26 | 0.68421
|  | NORTH FAREHAM | HE |  |  |  | 17.2168 | 17.0484 | 16.8632 | 16.6579 | 16.4368 | 16.1905 | 15.9568 | 15.7358 | 15.5274 | 15.3463 | 14.2105 | 12.8905 | -13.6168 | 13.6316 | 13.2821 | 12.9674 | 12.6368 | 12.2916 | 11.9274 | 11.5789 | 11.2432 | 10.9253 | 10.6284 | 9.1084 | 7.5411 | 6.1295 | 14.7874 | 14.5526 | 14.2474 | 13.9232 | 13.5863 | 13.2263 | 12.8832 | 12.5526 | 12.2379 | 11.9463 | 10.4642 | 8.9663 | 7.5453
|  | NORTH FAREHAM | CF |  |  |  | 17.3168 | 17.2232 | 17.1253 | 17.0242 | 16.92 | 16.8074 | 16.6926 | 16.58 | 16.4695 | 16.3579 | 15.8579 | 15.1232 | 14.3547 | 13.7589 | 13.6211 | 13.4337 | 13.2432 | 13.0484 | 12.8463 | 12.6421 | 12.4421 | 12.24 | 12.0337 | 11.0495 | 10.0158 | 9.0853 | 14.8937 | 14.7926 | 14.6895 | 14.5147 | 14.3263 | 14.1284 | 13.9295 | 13.7316 | 13.5347 | 13.3337 | 12.3737 | 11.3811 | 10.4968
LALEHAM | EAST BEDFONT A | NORTH FELTHAM | MINIMUM HEADROOM | TQ 10987 74875 | YES | 2.5337 | 27.0347 | 26.6537 | 26.2095 | 25.7116 | 25.2411 | 24.4589 | 23.7305 | 23.0232 | 22.3326 | 21.7158 | 19.3453 | 17.6821 | -13.9968 | 22.76 | 22.3421 | 21.8368 | 21.2684 | 20.7347 | 19.8263 | 18.9821 | 18.16 | 17.3558 | 16.6474 | 13.9547 | 12.0716 | 10.4937 | 24.0621 | 23.9137 | 23.5095 | 22.9421 | 22.4095 | 21.5021 | 20.6589 | 19.8389 | 19.0358 | 18.3274 | 15.6389 | 13.7589 | 12.1842
|  | NORTH FELTHAM | EE |  |  |  | 27.1589 | 26.8895 | 26.5958 | 26.2484 | 25.8179 | 25.2474 | 24.7326 | 24.1916 | 23.4758 | 22.8084 | 20.7116 | 19.4674 | 18.4705 | 22.8158 | 22.6105 | 22.2821 | 21.8905 | 21.3989 | 20.7421 | 20.1484 | 19.5232 | 18.6874 | 17.9053 | 15.5011 | 14.0916 | 12.9589 | 24.1126 | 23.9937 | 23.8684 | 23.5632 | 23.0726 | 22.4158 | 21.8242 | 21.2 | 20.3642 | 19.5842 | 17.1832 | 15.7768 | 14.6453
|  | NORTH FELTHAM | HT |  |  |  | 27.0347 | 26.6537 | 26.2095 | 25.7116 | 25.2411 | 24.4589 | 23.7305 | 23.0232 | 22.3326 | 21.7158 | 19.3453 | 17.6821 | 16.2905 | 22.76 | 22.3421 | 21.8368 | 21.2684 | 20.7347 | 19.8263 | 18.9821 | 18.16 | 17.3558 | 16.6474 | 13.9547 | 12.0716 | 10.4937 | 24.0621 | 23.9137 | 23.5095 | 22.9421 | 22.4095 | 21.5021 | 20.6589 | 19.8389 | 19.0358 | 18.3274 | 15.6389 | 13.7589 | 12.1842
|  | NORTH FELTHAM | HE |  |  |  | 27.2726 | 27.1095 | 26.8758 | 26.5853 | 26.2232 | 25.7095 | 25.2432 | 24.7158 | 24.0526 | 23.4547 | 21.7484 | 20.8 | -13.9968 | 22.8884 | 22.7958 | 22.5926 | 22.2642 | 21.8505 | 21.2558 | 20.7168 | 20.1032 | 19.3232 | 18.62 | 16.6389 | 15.5558 | 14.7516 | 24.1821 | 24.0947 | 23.9989 | 23.8916 | 23.5242 | 22.9295 | 22.3916 | 21.7789 | 21.0011 | 20.2979 | 18.3211 | 17.2379 | 16.4358
|  | NORTH FELTHAM | CF |  |  |  | 27.3137 | 27.26 | 27.2042 | 27.12 | 26.9905 | 26.8526 | 26.7105 | 26.5526 | 26.3137 | 26.0326 | 23.7937 | 22.9811 | 22.5242 | 22.9295 | 22.8758 | 22.82 | 22.76 | 22.6968 | 22.5779 | 22.4189 | 22.2421 | 21.9663 | 21.6389 | 18.9916 | 18.04 | 17.5042 | 24.2232 | 24.1695 | 24.1137 | 24.0558 | 23.9968 | 23.9347 | 23.8716 | 23.8095 | 23.6389 | 23.3126 | 20.6695 | 19.7189 | 19.1842
COWLEY GSP | OXFORD BSP | NORTH HINKSEY | MINIMUM HEADROOM | SP 48645 04403 | YES | 0 | 7.0316 | 6.8568 | 6.8179 | 6.6537 | 6.1716 | 5.6558 | 5.1495 | 4.5758 | 4.3821 | 4.1989 | 2.8421 | 1.2895 | -4.6253 | 4.6063 | 4.4316 | 4.2526 | 4.0621 | 3.5316 | 2.9716 | 2.4232 | 1.7926 | 1.6074 | 1.4337 | 0.041053 | -1.5937 | -2.1853 | 4.7189 | 4.5442 | 4.3642 | 4.1747 | 3.6421 | 3.0768 | 2.52 | 1.8832 | 1.6905 | 1.5074 | 0.055789 | -1.6463 | -2.2642
|  | NORTH HINKSEY | EE |  |  |  | 7.1021 | 6.9653 | 6.8179 | 6.6632 | 6.6674 | 6.4758 | 6.2789 | 6.0884 | 5.8979 | 5.72 | 4.2968 | 2.7421 | 1.8579 | 4.6768 | 4.54 | 4.3937 | 4.2389 | 4.0779 | 3.8926 | 3.7042 | 3.5232 | 3.3442 | 3.1779 | 1.7263 | 0.11368 | -0.83579 | 4.7895 | 4.6526 | 4.5053 | 4.3505 | 4.1884 | 3.9968 | 3.8 | 3.6084 | 3.4179 | 3.24 | 1.7074 | 0.0010526 | -0.97895
|  | NORTH HINKSEY | HT |  |  |  | 7.0316 | 6.8568 | 6.8432 | 6.6537 | 6.1716 | 5.6558 | 5.1495 | 4.5758 | 4.3821 | 4.1989 | 2.8421 | 1.2895 | 0.69684 | 4.6063 | 4.4316 | 4.2526 | 4.0621 | 3.5316 | 2.9716 | 2.4232 | 1.7926 | 1.6074 | 1.4337 | 0.041053 | -1.5937 | -2.1853 | 4.7189 | 4.5442 | 4.3642 | 4.1747 | 3.6421 | 3.0768 | 2.52 | 1.8832 | 1.6905 | 1.5074 | 0.055789 | -1.6463 | -2.2642
|  | NORTH HINKSEY | HE |  |  |  | 7.1989 | 7.1084 | 7.0095 | 6.8989 | 6.9463 | 6.8 | 6.66 | 6.5274 | 6.3989 | 6.2863 | 5.4863 | 4.5095 | -4.6253 | 4.7737 | 4.6832 | 4.5842 | 4.4737 | 4.3547 | 4.2137 | 4.0779 | 3.9495 | 3.8263 | 3.7189 | 2.8916 | 1.82 | 1.0895 | 4.8863 | 4.7958 | 4.6968 | 4.5863 | 4.4674 | 4.32 | 4.18 | 4.0474 | 3.92 | 3.8063 | 2.9453 | 1.8474 | 1.0926
|  | NORTH HINKSEY | CF |  |  |  | 7.2537 | 7.2053 | 7.1547 | 7.1011 | 7.0474 | 6.98 | 6.9137 | 6.8463 | 6.7811 | 6.7168 | 6.2684 | 5.7147 | 5.2389 | 4.8284 | 4.78 | 4.7295 | 4.6758 | 4.6221 | 4.5568 | 4.4926 | 4.4284 | 4.3653 | 4.3032 | 3.8358 | 3.2221 | 2.6926 | 4.9411 | 4.8926 | 4.8421 | 4.7884 | 4.7347 | 4.6674 | 4.6011 | 4.5347 | 4.4684 | 4.4042 | 3.9263 | 3.2979 | 2.7526
NORTH HYDE GSP |  | NORTH HYDE 11kV | MINIMUM HEADROOM | TQ 10367 79001 | NO | 1.0947 | 106.4768 | 106.06 | 145.6368 | 144.5516 | 141.7168 | 139.7337 | 137.9558 | 136.2537 | 134.6032 | 133.0011 | 125.1253 | 120.4537 | 22.3716 | 85.14 | 82.8642 | 120.5958 | 117.8389 | 114.5789 | 112.3274 | 110.3168 | 108.3884 | 106.5126 | 104.6884 | 95.6937 | 90.4147 | 85.6263 | 89.7358 | 87.46 | 125.1905 | 122.4326 | 119.1716 | 116.92 | 114.9095 | 112.9789 | 111.1032 | 109.2789 | 100.2811 | 95.0021 | 90.2116
|  | NORTH HYDE 11kV | EE |  |  |  | 106.6295 | 106.2979 | 145.9463 | 145.5726 | 143.4947 | 141.9916 | 140.5095 | 139.06 | 137.6221 | 136.24 | 129.8263 | 126.3821 | 123.3505 | 85.5326 | 83.5158 | 121.6042 | 119.2979 | 116.5947 | 114.8958 | 113.2189 | 111.5768 | 109.9484 | 108.3779 | 101.0347 | 97.1411 | 93.6958 | 90.1284 | 88.1116 | 126.1989 | 123.8916 | 121.1884 | 119.4884 | 117.8116 | 116.1695 | 114.54 | 112.9695 | 105.6242 | 101.7295 | 98.2832
|  | NORTH HYDE 11kV | HT |  |  |  | 106.4768 | 106.06 | 145.6368 | 144.5516 | 141.7168 | 139.7337 | 137.9558 | 136.2537 | 134.6032 | 133.0011 | 125.1253 | 120.4537 | 116.2326 | 85.14 | 82.8642 | 120.5958 | 117.8389 | 114.5789 | 112.3274 | 110.3168 | 108.3884 | 106.5126 | 104.6884 | 95.6937 | 90.4147 | 85.6263 | 89.7358 | 87.46 | 125.1905 | 122.4326 | 119.1716 | 116.92 | 114.9095 | 112.9789 | 111.1032 | 109.2789 | 100.2811 | 95.0021 | 90.2116
|  | NORTH HYDE 11kV | HE |  |  |  | 106.8211 | 106.5758 | 146.3063 | 146.0074 | 144.6526 | 143.3032 | 141.9842 | 140.6947 | 139.4316 | 138.2221 | 132.6726 | 130.0768 | 22.3716 | 85.9958 | 84.1979 | 122.4916 | 120.3821 | 117.8684 | 116.3389 | 114.8421 | 113.3758 | 111.9368 | 110.5547 | 104.1621 | 101.1937 | 98.6684 | 90.5926 | 88.7926 | 127.0874 | 124.9758 | 122.4621 | 120.9326 | 119.4347 | 117.9684 | 116.5295 | 115.1474 | 108.7526 | 105.7832 | 103.2568
|  | NORTH HYDE 11kV | CF |  |  |  | 106.9411 | 106.7916 | 146.6358 | 146.4747 | 146.3095 | 146.1368 | 145.9621 | 145.7884 | 145.6179 | 145.3263 | 141.7484 | 139.7937 | 138.3937 | 86.7021 | 85.7705 | 124.8905 | 123.8611 | 122.6968 | 121.9484 | 121.1474 | 120.3779 | 119.5642 | 118.7063 | 114.6221 | 112.3863 | 110.7726 | 90.9789 | 90.3663 | 129.4863 | 128.4568 | 127.2926 | 126.5432 | 125.7421 | 124.9726 | 124.1589 | 123.3 | 119.2158 | 116.9779 | 115.3642
MINETY GSP | CIRENCESTER BSP | NORTHLEACH | MINIMUM HEADROOM | SP 10557 14251 | YES | 0.10526 | 12.2389 | 12.0547 | 11.8632 | 11.6547 | 11.4389 | 11.2074 | 10.9758 | 10.7537 | 10.5337 | 10.3505 | 9.2558 | 8.1147 | 0.80737 | 10.1495 | 9.9421 | 9.7263 | 9.4895 | 9.2474 | 8.9874 | 8.7295 | 8.4842 | 8.2484 | 8.0516 | 6.8589 | 5.6 | 4.4947 | 10.6063 | 10.3989 | 10.1842 | 9.9474 | 9.7042 | 9.4432 | 9.1821 | 8.9347 | 8.6947 | 8.4947 | 7.2811 | 5.9968 | 4.8821
|  | NORTHLEACH | EE |  |  |  | 12.3189 | 12.1779 | 12.0284 | 11.8642 | 11.7011 | 11.5189 | 11.34 | 11.1611 | 10.9863 | 10.8379 | 9.9347 | 8.9632 | 8.1611 | 10.2411 | 10.0832 | 9.9158 | 9.7316 | 9.5484 | 9.3484 | 9.1526 | 8.9568 | 8.7663 | 8.6074 | 7.6326 | 6.5758 | 5.6695 | 10.6768 | 10.54 | 10.3737 | 10.1884 | 10.0063 | 9.8032 | 9.6042 | 9.4053 | 9.2084 | 9.0453 | 8.0411 | 6.9505 | 6.0337
|  | NORTHLEACH | HT |  |  |  | 12.2389 | 12.0547 | 11.8632 | 11.6547 | 11.4389 | 11.2074 | 10.9758 | 10.7537 | 10.5337 | 10.3505 | 9.2558 | 8.1147 | 7.1358 | 10.1495 | 9.9421 | 9.7263 | 9.4895 | 9.2474 | 8.9874 | 8.7295 | 8.4842 | 8.2484 | 8.0516 | 6.8589 | 5.6 | 4.4947 | 10.6063 | 10.3989 | 10.1842 | 9.9474 | 9.7042 | 9.4432 | 9.1821 | 8.9347 | 8.6947 | 8.4947 | 7.2811 | 5.9968 | 4.8821
|  | NORTHLEACH | HE |  |  |  | 12.4295 | 12.3411 | 12.2421 | 12.1274 | 12.0095 | 11.8726 | 11.74 | 11.6095 | 11.4842 | 11.3863 | 10.7695 | 10.0747 | 0.80737 | 10.3663 | 10.2674 | 10.1579 | 10.0295 | 9.8979 | 9.7474 | 9.6021 | 9.4579 | 9.3189 | 9.2137 | 8.5084 | 7.7221 | 7.0042 | 10.7347 | 10.6811 | 10.6158 | 10.4874 | 10.3558 | 10.2032 | 10.0558 | 9.9095 | 9.7705 | 9.6611 | 8.9442 | 8.1484 | 7.4211
|  | NORTHLEACH | CF |  |  |  | 12.4842 | 12.4358 | 12.3832 | 12.3253 | 12.2695 | 12.2063 | 12.14 | 12.0737 | 12.0053 | 11.9463 | 11.5453 | 11.1347 | 10.7537 | 10.4189 | 10.3737 | 10.3137 | 10.2495 | 10.1863 | 10.1158 | 10.0432 | 9.9684 | 9.8937 | 9.8284 | 9.3653 | 8.8737 | 8.44 | 10.7684 | 10.7389 | 10.7084 | 10.6768 | 10.6432 | 10.5726 | 10.4979 | 10.4242 | 10.3474 | 10.2821 | 9.8137 | 9.3179 | 8.8789
IVER 66KV |  | NORTHOLT | MINIMUM HEADROOM | TQ 11550 83230 | YES | 0.63263 | 47.0558 | 46.4537 | 45.8453 | 45.1979 | 44.52 | 43.8147 | 43.1011 | 42.4568 | 41.7747 | 40.6884 | 35.6316 | 30.6179 | -16.6747 | 38.68 | 37.5747 | 36.2284 | 34.7621 | 33.2337 | 31.6568 | 30.2021 | 28.8621 | 27.6221 | 26.44 | 20.8884 | 15.3011 | 9.9547 | 39.9516 | 39.3116 | 38.6611 | 37.2453 | 35.7189 | 34.1432 | 32.6905 | 31.3516 | 30.1126 | 28.9316 | 23.3874 | 17.8063 | 12.4674
|  | NORTHOLT | EE |  |  |  | 47.2842 | 46.8105 | 46.3084 | 45.7747 | 45.2074 | 44.6158 | 44.0389 | 43.4821 | 42.9432 | 42.4579 | 39.8989 | 36.3526 | 33.0621 | 38.9947 | 38.3874 | 37.4105 | 36.3126 | 35.1716 | 34.0063 | 32.8821 | 31.7989 | 30.7537 | 29.7842 | 25.6347 | 21.6905 | 17.9905 | 40.1979 | 39.6979 | 39.1653 | 38.5989 | 37.6547 | 36.4895 | 35.3663 | 34.2853 | 33.24 | 32.2716 | 28.1263 | 24.1874 | 20.4926
|  | NORTHOLT | HT |  |  |  | 47.0558 | 46.4537 | 45.8453 | 45.1979 | 44.52 | 43.8147 | 43.1011 | 42.4568 | 41.7747 | 40.6884 | 35.6316 | 30.6179 | 25.8589 | 38.68 | 37.5747 | 36.2284 | 34.7621 | 33.2337 | 31.6568 | 30.2021 | 28.8621 | 27.6221 | 26.44 | 20.8884 | 15.3011 | 9.9547 | 39.9516 | 39.3116 | 38.6611 | 37.2453 | 35.7189 | 34.1432 | 32.6905 | 31.3516 | 30.1126 | 28.9316 | 23.3874 | 17.8063 | 12.4674
|  | NORTHOLT | HE |  |  |  | 47.5442 | 47.1863 | 46.7905 | 46.3537 | 45.8832 | 45.3811 | 44.9011 | 44.4495 | 44.0284 | 43.6642 | 42.4053 | 41.5905 | -16.6747 | 39.3053 | 38.9116 | 38.4442 | 37.8242 | 36.9474 | 36.0211 | 35.1495 | 34.3253 | 33.5516 | 32.8558 | 30.1 | 27.5326 | 25.2074 | 40.4811 | 40.1063 | 39.6916 | 39.2326 | 38.7379 | 38.2116 | 37.6316 | 36.8084 | 36.0358 | 35.34 | 32.5863 | 30.0232 | 27.7011
|  | NORTHOLT | CF |  |  |  | 47.7042 | 47.4789 | 47.2453 | 47.0021 | 46.7516 | 46.4916 | 46.2263 | 45.9653 | 45.7074 | 45.4495 | 44.3011 | 43.7179 | 43.3926 | 39.4863 | 39.2358 | 38.9747 | 38.6968 | 38.3716 | 37.9926 | 37.4842 | 36.9758 | 36.4716 | 35.9632 | 33.5168 | 31.7232 | 30.1505 | 40.6505 | 40.4137 | 40.1674 | 39.9105 | 39.6463 | 39.3716 | 39.0926 | 38.8168 | 38.5453 | 38.2726 | 36.0011 | 34.2095 | 32.64
BRAMLEY (FLEE) | READING BSP | NORTHUMBERLAND AVENUE | MINIMUM HEADROOM | SU 72207 71092 | YES | 0.57895 | 24.4884 | 24.3074 | 24.1274 | 23.9389 | 23.74 | 23.3589 | 22.7884 | 21.3968 | 20.4884 | 19.5968 | 14.8168 | 12.3474 | -3.1295 | 20.4789 | 20.2632 | 19.9547 | 19.6347 | 19.3053 | 18.4347 | 17.5589 | 15.92 | 14.8758 | 13.8474 | 8.3032 | 5.3063 | 3.8611 | 21.1716 | 20.9937 | 20.8168 | 20.6295 | 20.4326 | 19.8611 | 18.9705 | 17.3642 | 16.3211 | 15.2937 | 9.7589 | 6.7326 | 5.2895
|  | NORTHUMBERLAND AVENUE | EE |  |  |  | 24.5505 | 24.4074 | 24.2568 | 24.0979 | 23.9284 | 23.7274 | 23.3632 | 22.3916 | 21.2589 | 20.3674 | 16.0968 | 14.2358 | 13.2463 | 20.5463 | 20.3958 | 20.2147 | 19.9526 | 19.6789 | 19.0516 | 18.4105 | 17.0505 | 15.7379 | 14.7074 | 9.8905 | 7.7547 | 6.6305 | 21.2337 | 21.0916 | 20.9432 | 20.7863 | 20.6189 | 20.4242 | 19.8411 | 18.4758 | 17.1811 | 16.1526 | 11.3937 | 9.2568 | 8.1337
|  | NORTHUMBERLAND AVENUE | HT |  |  |  | 24.4884 | 24.3074 | 24.1274 | 23.9389 | 23.74 | 23.3589 | 22.7884 | 21.3968 | 20.4884 | 19.5968 | 14.8168 | 12.3474 | 11.0705 | 20.4789 | 20.2632 | 19.9547 | 19.6347 | 19.3053 | 18.4347 | 17.5589 | 15.92 | 14.8758 | 13.8474 | 8.3032 | 5.3063 | 3.8611 | 21.1716 | 20.9937 | 20.8168 | 20.6295 | 20.4326 | 19.8611 | 18.9705 | 17.3642 | 16.3211 | 15.2937 | 9.7589 | 6.7326 | 5.2895
|  | NORTHUMBERLAND AVENUE | HE |  |  |  | 24.6442 | 24.5442 | 24.4337 | 24.3126 | 24.1821 | 24.0147 | 23.8421 | 22.9832 | 21.9442 | 21.1379 | 16.5126 | 15.0011 | -3.1295 | 20.6379 | 20.5389 | 20.4284 | 20.3021 | 20.1684 | 19.6158 | 19.0389 | 17.6895 | 16.4821 | 15.5453 | 9.9779 | 8.2253 | 7.4411 | 21.3253 | 21.2263 | 21.1168 | 20.9968 | 20.8684 | 20.7074 | 20.4495 | 19.1032 | 17.9253 | 16.9905 | 11.3979 | 9.6484 | 8.8653
|  | NORTHUMBERLAND AVENUE | CF |  |  |  | 24.7 | 24.6411 | 24.5821 | 24.5179 | 24.4526 | 24.3874 | 24.3179 | 24.2453 | 24.1632 | 24.0758 | 21.7368 | 19.4326 | 18.98 | 20.6937 | 20.6347 | 20.5768 | 20.5137 | 20.4463 | 20.3779 | 20.3053 | 20.1737 | 19.86 | 19.5032 | 16.2084 | 13.5095 | 12.9884 | 21.3811 | 21.3221 | 21.2632 | 21.2011 | 21.1368 | 21.0716 | 21.0032 | 20.9316 | 20.8537 | 20.7716 | 17.6526 | 14.9589 | 14.4379
COWLEY GSP | HIGH WYCOMBE BSP | NUFFIELD | MINIMUM HEADROOM | SU 68329 86784 | YES | 0 | 8.3389 | 8.2716 | 8.2053 | 8.1347 | 8.0611 | 7.9863 | 7.9105 | 7.8453 | 7.7863 | 7.7316 | 7.3453 | 6.9811 | -13.28 | 7.2526 | 7.1442 | 7.0168 | 6.8895 | 6.7589 | 6.6316 | 6.4989 | 6.3779 | 6.2653 | 6.1579 | 5.7116 | 5.3116 | 4.9232 | 7.4263 | 7.3295 | 7.2063 | 7.0821 | 6.9568 | 6.8326 | 6.7042 | 6.5874 | 6.4779 | 6.3758 | 5.9453 | 5.5632 | 5.1937
|  | NUFFIELD | EE |  |  |  | 8.3663 | 8.3147 | 8.26 | 8.2032 | 8.1432 | 8.0821 | 8.0232 | 7.9684 | 7.9137 | 7.8663 | 7.6853 | 7.4179 | 7.1779 | 7.2821 | 7.2263 | 7.1316 | 7.0295 | 6.9253 | 6.8221 | 6.7168 | 6.6168 | 6.5179 | 6.4274 | 6.08 | 5.7853 | 5.5168 | 7.4558 | 7.4011 | 7.3168 | 7.2179 | 7.1158 | 7.0158 | 6.9147 | 6.8168 | 6.7221 | 6.6347 | 6.3 | 6.0189 | 5.7642
|  | NUFFIELD | HT |  |  |  | 8.3389 | 8.2716 | 8.2053 | 8.1347 | 8.0611 | 7.9863 | 7.9105 | 7.8453 | 7.7863 | 7.7316 | 7.3453 | 6.9811 | 6.6326 | 7.2526 | 7.1442 | 7.0168 | 6.8895 | 6.7589 | 6.6316 | 6.4989 | 6.3779 | 6.2653 | 6.1579 | 5.7116 | 5.3116 | 4.9232 | 7.4263 | 7.3295 | 7.2063 | 7.0821 | 6.9568 | 6.8326 | 6.7042 | 6.5874 | 6.4779 | 6.3758 | 5.9453 | 5.5632 | 5.1937
|  | NUFFIELD | HE |  |  |  | 8.4032 | 8.3695 | 8.3326 | 8.2905 | 8.2474 | 8.2 | 8.1558 | 8.1137 | 8.0747 | 8.04 | 7.9263 | 7.8621 | -13.28 | 7.3211 | 7.2863 | 7.2474 | 7.2032 | 7.1463 | 7.0716 | 6.9958 | 6.9232 | 6.8547 | 6.7916 | 6.5737 | 6.4 | 6.24 | 7.4926 | 7.4589 | 7.4211 | 7.3779 | 7.3284 | 7.2558 | 7.1832 | 7.1116 | 7.0463 | 6.9853 | 6.7747 | 6.6084 | 6.4579
|  | NUFFIELD | CF |  |  |  | 8.4242 | 8.4063 | 8.3874 | 8.3684 | 8.3484 | 8.3284 | 8.3074 | 8.2863 | 8.2653 | 8.2453 | 8.1547 | 8.1095 | 8.0853 | 7.3432 | 7.3242 | 7.3042 | 7.2842 | 7.2632 | 7.2421 | 7.2179 | 7.1758 | 7.1316 | 7.0895 | 6.9053 | 6.7663 | 6.6463 | 7.5137 | 7.4958 | 7.4768 | 7.4579 | 7.4368 | 7.4158 | 7.3937 | 7.3589 | 7.3168 | 7.2758 | 7.0979 | 6.9674 | 6.8537
BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | OAKRIDGE | MINIMUM HEADROOM | SU 63496 53664 | YES | 0.25368 | 32.5789 | 32.3411 | 32.1011 | 32.0516 | 31.6674 | 31.1653 | 30.0042 | 28.8821 | 27.8053 | 27.3147 | 25.5653 | 23.7284 | 4.7179 | 30.1232 | 29.5421 | 28.9211 | 28.4284 | 27.9432 | 27.4042 | 26.0884 | 24.8158 | 23.5916 | 23.0537 | 21.1705 | 19.1516 | 16.7895 | 30.5358 | 30.1937 | 29.56 | 29.0442 | 28.5589 | 28.0179 | 26.7042 | 25.4305 | 24.2063 | 23.6674 | 21.7737 | 19.74 | 17.3747
|  | OAKRIDGE | EE |  |  |  | 32.66 | 32.4695 | 32.2663 | 32.0516 | 31.8242 | 31.5821 | 31.3474 | 30.54 | 29.4568 | 28.3284 | 26.7147 | 25.4411 | 23.82 | 30.2474 | 29.8379 | 29.3032 | 28.8832 | 28.4884 | 28.0326 | 27.6389 | 26.7042 | 25.4705 | 24.1832 | 22.4389 | 21.0642 | 19.2326 | 30.6242 | 30.4158 | 29.9495 | 29.5221 | 29.1221 | 28.66 | 28.2621 | 27.3147 | 26.0811 | 24.7926 | 23.0305 | 21.6347 | 19.7989
|  | OAKRIDGE | HT |  |  |  | 32.5789 | 32.3411 | 32.1011 | 32.12 | 31.6674 | 31.1653 | 30.0042 | 28.8821 | 27.8053 | 27.3147 | 25.5653 | 23.7284 | 21.6305 | 30.1232 | 29.5421 | 28.9211 | 28.4284 | 27.9432 | 27.4042 | 26.0884 | 24.8158 | 23.5916 | 23.0537 | 21.1705 | 19.1516 | 16.7895 | 30.5358 | 30.1937 | 29.56 | 29.0442 | 28.5589 | 28.0179 | 26.7042 | 25.4305 | 24.2063 | 23.6674 | 21.7737 | 19.74 | 17.3747
|  | OAKRIDGE | HE |  |  |  | 32.7747 | 32.6358 | 32.4832 | 32.3137 | 32.1316 | 31.9337 | 31.7442 | 31.5663 | 30.9611 | 30.2853 | 28.4747 | 27.8474 | 4.7179 | 30.3821 | 30.2105 | 29.8158 | 29.5074 | 29.2221 | 28.8726 | 28.5832 | 27.9347 | 27.1484 | 26.38 | 24.3495 | 23.6726 | 22.6326 | 30.7474 | 30.5958 | 30.4274 | 30.1579 | 29.8705 | 29.5147 | 29.2211 | 28.56 | 27.7611 | 26.9926 | 24.9568 | 24.2737 | 23.2305
|  | OAKRIDGE | CF |  |  |  | 32.8411 | 32.7558 | 32.6674 | 32.5758 | 32.4811 | 32.3811 | 32.2789 | 32.18 | 32.08 | 31.9821 | 30.4705 | 29.8832 | 29.3768 | 30.4621 | 30.3663 | 30.2642 | 30.1611 | 30.0158 | 29.7179 | 29.4421 | 29.2326 | 29.0084 | 28.7642 | 26.5474 | 25.9011 | 25.3316 | 30.82 | 30.7295 | 30.6347 | 30.5379 | 30.4379 | 30.3253 | 30.0905 | 29.8779 | 29.6495 | 29.4011 | 27.16 | 26.5116 | 25.9389
COWLEY GSP | HEADINGTON BSP | OLD ROAD | MINIMUM HEADROOM | SP 55274 06426 | YES | 0.063158 | 40.3074 | 40.1189 | 39.9295 | 39.7284 | 39.52 | 39.2989 | 38.1737 | 37.8242 | 37.5147 | 37.2295 | 35.7537 | 34.6337 | 5.6926 | 32.96 | 31.8263 | 31.4716 | 31.1032 | 30.7368 | 30.3705 | 28.6484 | 28.2589 | 27.9147 | 27.6042 | 26.0042 | 24.8011 | 23.7253 | 34.4526 | 33.5432 | 33.1947 | 32.8316 | 32.4705 | 32.1074 | 30.4379 | 30.0547 | 29.7147 | 29.4063 | 27.8284 | 26.6337 | 25.5758
|  | OLD ROAD | EE |  |  |  | 40.3758 | 40.2274 | 40.0684 | 39.9021 | 39.7253 | 39.5379 | 38.8684 | 38.3211 | 37.9411 | 37.6979 | 36.4821 | 35.6063 | 34.8842 | 33.1189 | 32.6011 | 31.9295 | 31.4263 | 30.9853 | 30.6126 | 29.4674 | 28.8179 | 28.3842 | 28.1179 | 26.8042 | 25.8747 | 25.0884 | 34.5242 | 34.2768 | 33.6368 | 33.1463 | 32.7116 | 32.3453 | 31.2316 | 30.5958 | 30.1684 | 29.9042 | 28.5968 | 27.6632 | 26.8853
|  | OLD ROAD | HT |  |  |  | 40.3074 | 40.1189 | 39.9295 | 39.7284 | 39.52 | 39.2989 | 38.1737 | 37.8242 | 37.5147 | 37.2295 | 35.7537 | 34.6337 | 33.6505 | 32.96 | 31.8263 | 31.4716 | 31.1032 | 30.7368 | 30.3705 | 28.6484 | 28.2589 | 27.9147 | 27.6042 | 26.0042 | 24.8011 | 23.7253 | 34.4526 | 33.5432 | 33.1947 | 32.8316 | 32.4705 | 32.1074 | 30.4379 | 30.0547 | 29.7147 | 29.4063 | 27.8284 | 26.6337 | 25.5758
|  | OLD ROAD | HE |  |  |  | 40.4695 | 40.3642 | 40.2484 | 40.1211 | 39.9832 | 39.8316 | 39.5358 | 39.0589 | 38.7842 | 38.6189 | 37.8505 | 37.4158 | 5.6926 | 33.2242 | 32.9021 | 32.3189 | 31.9168 | 31.5789 | 31.3011 | 30.2189 | 29.6463 | 29.3316 | 29.1516 | 28.2853 | 27.8021 | 27.4 | 34.6284 | 34.5021 | 34.0242 | 33.6316 | 33.3011 | 33.0274 | 31.9779 | 31.4211 | 31.1116 | 30.9337 | 30.0789 | 29.5989 | 29.2021
|  | OLD ROAD | CF |  |  |  | 40.5242 | 40.4611 | 40.3968 | 40.3295 | 40.2611 | 40.1874 | 40.1116 | 40.0379 | 39.9642 | 39.8937 | 39.1674 | 38.7884 | 38.5053 | 33.2811 | 33.2147 | 33.1474 | 33.0747 | 32.9516 | 32.8274 | 32.6937 | 32.4747 | 32.0884 | 31.6758 | 29.7842 | 29.3495 | 29.0211 | 34.6863 | 34.6189 | 34.5516 | 34.48 | 34.4084 | 34.3326 | 34.2537 | 34.1442 | 33.7905 | 33.3895 | 31.5526 | 31.1253 | 30.8011
COWLEY GSP | OXFORD BSP | OXFORD | MINIMUM HEADROOM | SP 50148 05901 | YES | 0.46947 | 35.3147 | 35.2137 | 35.1084 | 34.9947 | 34.8747 | 34.7516 | 34.6305 | 34.5137 | 34.4021 | 33.56 | 32.4263 | 31.5316 | -24.2895 | 28.2084 | 28.1074 | 28.0021 | 27.8884 | 27.7684 | 27.6453 | 27.5242 | 27.4074 | 27.2958 | 26.38 | 25.1274 | 24.1358 | 23.22 | 29.8811 | 29.78 | 29.6747 | 29.5611 | 29.4411 | 29.3179 | 29.1968 | 29.08 | 28.9684 | 28.0095 | 26.7558 | 25.7642 | 24.8484
|  | OXFORD | EE |  |  |  | 35.3147 | 35.2137 | 35.1084 | 34.9947 | 34.8747 | 34.7516 | 34.6305 | 34.5137 | 34.4021 | 34.3011 | 33.1674 | 32.4958 | 31.8958 | 28.2084 | 28.1074 | 28.0021 | 27.8884 | 27.7684 | 27.6453 | 27.5242 | 27.4074 | 27.2958 | 27.1947 | 25.9453 | 25.2011 | 24.5284 | 29.8811 | 29.78 | 29.6747 | 29.5611 | 29.4411 | 29.3179 | 29.1968 | 29.08 | 28.9684 | 28.8674 | 27.5747 | 26.8295 | 26.1568
|  | OXFORD | HT |  |  |  | 36.5758 | 36.4495 | 36.3232 | 36.9863 | 36.7526 | 36.7253 | 35.8863 | 35.3874 | 34.4221 | 33.56 | 32.4263 | 31.5316 | 30.7126 | 31.0326 | 30.6421 | 30.4284 | 30.2589 | 30.0084 | 30.0232 | 29.0589 | 28.4947 | 27.3779 | 26.38 | 25.1274 | 24.1358 | 23.22 | 32.0442 | 31.9179 | 31.7916 | 31.9316 | 31.6811 | 31.6526 | 30.6895 | 30.1253 | 29.0074 | 28.0095 | 26.7558 | 25.7642 | 24.8484
|  | OXFORD | HE |  |  |  | 35.3726 | 35.2989 | 35.2179 | 35.1274 | 35.0295 | 34.9263 | 34.8274 | 34.7347 | 34.6463 | 34.5705 | 34.1547 | 33.7716 | -24.2895 | 28.2663 | 28.1926 | 28.1116 | 28.0211 | 27.9232 | 27.9158 | 27.8168 | 27.7242 | 27.6358 | 27.5611 | 27.0432 | 26.6179 | 26.2579 | 29.9389 | 29.8653 | 29.7842 | 29.6937 | 29.5958 | 29.4926 | 29.3937 | 29.3011 | 29.2126 | 29.1368 | 28.6705 | 28.2463 | 27.8863
|  | OXFORD | CF |  |  |  | 36.7105 | 36.6642 | 36.6147 | 36.5642 | 36.5126 | 36.4579 | 36.4021 | 36.3474 | 36.2937 | 36.2389 | 35.5074 | 35.5568 | 35.3158 | 31.1674 | 31.1211 | 31.0716 | 31.0211 | 30.9695 | 30.9147 | 30.8589 | 30.8042 | 30.6547 | 30.4453 | 28.5474 | 28.6484 | 28.3758 | 32.1789 | 32.1326 | 32.0832 | 32.0326 | 31.9811 | 31.9263 | 31.8705 | 31.8158 | 31.7621 | 31.7074 | 30.22 | 30.2779 | 30.0053
COWLEY GSP | COWLEY LOCAL (2 X 90) | OXFORD SCIENCE PARK | MINIMUM HEADROOM | TBC | YES | 0 | 0 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 0 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 0 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  | OXFORD SCIENCE PARK | EE |  |  |  | 0 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 0 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 0 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  | OXFORD SCIENCE PARK | HT |  |  |  | 0 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 0 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 0 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  | OXFORD SCIENCE PARK | HE |  |  |  | 0 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 0 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 0 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  | OXFORD SCIENCE PARK | CF |  |  |  | 0 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 0 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 0 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | OVERTON | MINIMUM HEADROOM | SU 52061 50913 | YES | 1.2516 | 28.8968 | 28.6684 | 28.46 | 28.2484 | 27.9505 | 27.4842 | 24.8863 | 22.4084 | 20.0895 | 17.7811 | 7.8874 | 4.1337 | 3.4011 | 28.3968 | 28.1568 | 27.9326 | 27.7053 | 27.3789 | 26.8568 | 23.8253 | 20.9305 | 18.2242 | 15.5284 | 3.98 | -0.34632 | -1.1516 | 28.4905 | 28.2453 | 28.0253 | 27.8 | 27.4789 | 26.9653 | 23.9411 | 21.0526 | 18.3505 | 15.6589 | 4.1232 | -0.21895 | -1.0305
|  | OVERTON | EE |  |  |  | 28.9905 | 28.8074 | 28.6411 | 28.4705 | 28.2116 | 27.7821 | 27.3547 | 25.5842 | 23.2958 | 20.9179 | 10.1989 | 4.8284 | 4.2695 | 28.4926 | 28.3042 | 28.1295 | 27.9484 | 27.6621 | 27.18 | 26.7021 | 24.64 | 21.9684 | 19.1905 | 6.6726 | 0.44421 | -0.16947 | 28.5916 | 28.3947 | 28.2189 | 28.0389 | 27.7579 | 27.2842 | 26.8095 | 24.7495 | 22.0821 | 19.3074 | 6.7937 | 0.54737 | -0.074737
|  | OVERTON | HT |  |  |  | 28.8968 | 28.6684 | 28.46 | 28.2484 | 27.9505 | 27.4842 | 24.8863 | 22.4084 | 20.0895 | 17.7811 | 7.8874 | 4.1337 | 3.4011 | 28.3968 | 28.1568 | 27.9326 | 27.7053 | 27.3789 | 26.8568 | 23.8253 | 20.9305 | 18.2242 | 15.5284 | 3.98 | -0.34632 | -1.1516 | 28.4905 | 28.2453 | 28.0253 | 27.8 | 27.4789 | 26.9653 | 23.9411 | 21.0526 | 18.3505 | 15.6589 | 4.1232 | -0.21895 | -1.0305
|  | OVERTON | HE |  |  |  | 29.1179 | 28.9947 | 28.8853 | 28.7716 | 28.5674 | 28.1884 | 27.8158 | 26.2705 | 24.4074 | 22.5537 | 14.4326 | 7.6947 | 10.0126 | 28.6242 | 28.4968 | 28.3853 | 28.2695 | 28.0484 | 27.6211 | 27.2 | 25.3968 | 23.2168 | 21.0484 | 11.5411 | 3.6432 | 1.4105 | 28.7274 | 28.5958 | 28.48 | 28.3611 | 28.1389 | 27.7189 | 27.3063 | 25.5095 | 23.3347 | 21.1695 | 11.6789 | 3.7937 | 1.5579
|  | OVERTON | CF |  |  |  | 29.2726 | 29.2095 | 29.1263 | 29.0389 | 28.9326 | 28.7737 | 28.5705 | 28.3316 | 28.1116 | 27.8263 | 23.9253 | 17.6053 | 14.6211 | 28.7821 | 28.7179 | 28.6347 | 28.5442 | 28.4337 | 28.2684 | 28.0389 | 27.7653 | 27.5147 | 27.1863 | 22.6316 | 15.2105 | 11.7137 | 28.8958 | 28.8316 | 28.7432 | 28.6474 | 28.5316 | 28.3558 | 28.1295 | 27.8632 | 27.6179 | 27.2968 | 22.7484 | 15.3463 | 11.8516
BRAMLEY (FLEE) | BURGHFIELD RESERVE | PADWORTH | MINIMUM HEADROOM | SU 62243 66052 | YES | 1.2105 | 6.7043 | 6.6749 | 6.6443 | 6.6117 | 6.5243 | 6.2517 | 5.9896 | 5.6538 | 5.6138 | 5.5728 | 5.0075 | 4.0949 | 1.4401 | 5.7024 | 5.6708 | 5.6382 | 5.6045 | 5.515 | 5.1813 | 4.8603 | 4.4518 | 4.415 | 4.3782 | 3.775 | 2.7676 | 2.5318 | 5.9074 | 5.8779 | 5.8474 | 5.8158 | 5.6632 | 5.3263 | 5.0032 | 4.5916 | 4.5505 | 4.5105 | 3.8811 | 2.8432 | 2.5947
|  | PADWORTH | EE |  |  |  | 6.7159 | 6.6928 | 6.6675 | 6.6412 | 6.6138 | 6.5749 | 6.5349 | 6.4938 | 6.4517 | 6.4107 | 5.8559 | 5.1338 | 4.5812 | 5.715 | 5.6908 | 5.6634 | 5.635 | 5.6076 | 5.5697 | 5.5329 | 5.4961 | 5.4582 | 5.4234 | 4.8297 | 4.0203 | 3.3929 | 5.9189 | 5.8958 | 5.8705 | 5.8442 | 5.8168 | 5.7789 | 5.7389 | 5.6916 | 5.6316 | 5.5737 | 4.9221 | 4.0642 | 3.4316
|  | PADWORTH | HT |  |  |  | 6.7043 | 6.6749 | 6.6443 | 6.6117 | 6.5243 | 6.2517 | 5.9896 | 5.6538 | 5.6138 | 5.5728 | 5.0075 | 4.0949 | 3.8686 | 5.7024 | 5.6708 | 5.6382 | 5.6045 | 5.515 | 5.1813 | 4.8603 | 4.4518 | 4.415 | 4.3782 | 3.775 | 2.7676 | 2.5318 | 5.9074 | 5.8779 | 5.8474 | 5.8158 | 5.6632 | 5.3263 | 5.0032 | 4.5916 | 4.5505 | 4.5105 | 3.8811 | 2.8432 | 2.5947
|  | PADWORTH | HE |  |  |  | 6.7317 | 6.717 | 6.7001 | 6.6812 | 6.6612 | 6.6307 | 6.6043 | 6.577 | 6.5517 | 6.5275 | 6.3033 | 5.8401 | 1.4401 | 5.7329 | 5.7171 | 5.6992 | 5.6792 | 5.6582 | 5.6297 | 5.6045 | 5.5792 | 5.555 | 5.5339 | 5.3045 | 4.7213 | 4.2045 | 5.9347 | 5.92 | 5.9032 | 5.8842 | 5.8642 | 5.8347 | 5.8074 | 5.7811 | 5.7558 | 5.7326 | 5.4274 | 4.8316 | 4.3032
|  | PADWORTH | CF |  |  |  | 6.7412 | 6.7328 | 6.7233 | 6.7149 | 6.7054 | 6.6896 | 6.678 | 6.6643 | 6.6507 | 6.638 | 6.577 | 6.278 | 5.9654 | 5.7434 | 5.7339 | 5.7234 | 5.715 | 5.7045 | 5.6897 | 5.6782 | 5.6645 | 5.6508 | 5.6403 | 5.5782 | 5.2297 | 4.8476 | 5.9442 | 5.9358 | 5.9263 | 5.9179 | 5.9084 | 5.8937 | 5.8821 | 5.8674 | 5.8537 | 5.8421 | 5.7821 | 5.3621 | 4.9726
BRAMLEY (FLEE) | BURGHFIELD RESERVE | PANGBOURNE | MINIMUM HEADROOM | SU 62960 76144 | YES | 0.094737 | 32.5789 | 32.4358 | 32.2926 | 32.1116 | 31.8589 | 31.6095 | 31.36 | 31.1347 | 30.9253 | 30.7305 | 29.8768 | 29.0411 | 15.8368 | 30.3053 | 30.0916 | 29.88 | 29.6358 | 29.3558 | 29.0811 | 28.8074 | 28.5589 | 28.3263 | 28.1095 | 27.1474 | 26.1726 | 25.2126 | 30.7979 | 30.6474 | 30.4874 | 30.2126 | 29.9337 | 29.6589 | 29.3853 | 29.1368 | 28.9042 | 28.6884 | 27.7263 | 26.7537 | 25.7947
|  | PANGBOURNE | EE |  |  |  | 32.6368 | 32.5263 | 32.4095 | 32.2853 | 32.1558 | 31.9726 | 31.7758 | 31.5884 | 31.4074 | 31.2442 | 30.5937 | 29.98 | 29.4168 | 30.4 | 30.2358 | 30.0663 | 29.8916 | 29.7116 | 29.4905 | 29.2737 | 29.0674 | 28.8684 | 28.6874 | 27.9568 | 27.2379 | 26.5653 | 30.86 | 30.7432 | 30.6211 | 30.4905 | 30.2916 | 30.0674 | 29.8505 | 29.6453 | 29.4463 | 29.2653 | 28.5358 | 27.8179 | 27.1453
|  | PANGBOURNE | HT |  |  |  | 32.5789 | 32.4358 | 32.2926 | 32.1116 | 31.8589 | 31.6095 | 31.36 | 31.1347 | 30.9253 | 30.7305 | 29.8768 | 29.0411 | 28.2337 | 30.3053 | 30.0916 | 29.88 | 29.6358 | 29.3558 | 29.0811 | 28.8074 | 28.5589 | 28.3263 | 28.1095 | 27.1474 | 26.1726 | 25.2126 | 30.7979 | 30.6474 | 30.4874 | 30.2126 | 29.9337 | 29.6589 | 29.3853 | 29.1368 | 28.9042 | 28.6884 | 27.7263 | 26.7537 | 25.7947
|  | PANGBOURNE | HE |  |  |  | 32.7147 | 32.6421 | 32.56 | 32.4716 | 32.3747 | 32.2737 | 32.1747 | 32.0821 | 31.9968 | 31.9232 | 31.5316 | 31.1442 | 15.8368 | 30.5263 | 30.4232 | 30.3116 | 30.1926 | 30.0653 | 29.9326 | 29.8042 | 29.6832 | 29.5716 | 29.4695 | 29.0232 | 28.5663 | 28.1389 | 30.9432 | 30.8663 | 30.7811 | 30.6895 | 30.5895 | 30.4853 | 30.3832 | 30.2874 | 30.1684 | 30.0463 | 29.6011 | 29.1442 | 28.7179
|  | PANGBOURNE | CF |  |  |  | 32.7579 | 32.7179 | 32.6758 | 32.6326 | 32.5874 | 32.5411 | 32.4947 | 32.4463 | 32.4011 | 32.3547 | 32.1295 | 31.8453 | 31.5842 | 30.5905 | 30.5295 | 30.4663 | 30.4011 | 30.3326 | 30.2632 | 30.1937 | 30.1221 | 30.0558 | 29.9874 | 29.6558 | 29.3189 | 29 | 30.9884 | 30.9463 | 30.9011 | 30.8558 | 30.8084 | 30.7589 | 30.7105 | 30.66 | 30.6116 | 30.5632 | 30.2326 | 29.8968 | 29.5779
BOTLEY WOOD GSP | BOTLEY WOOD BSP | PARK GATE | MINIMUM HEADROOM | SU 51369 08259 | YES | 0.22105 | 33.3958 | 33.5968 | 33.4884 | 33.3811 | 33.2705 | 42.9621 | 42.5937 | 42.2705 | 41.9779 | 41.7074 | 40.5968 | 38.0789 | 5.1 | 29.8958 | 30.3295 | 30.0863 | 29.8979 | 29.7137 | 43.0716 | 42.7032 | 42.2126 | 41.6937 | 41.2074 | 38.5105 | 35.76 | 33.1832 | 30.6726 | 30.8979 | 30.7916 | 30.6747 | 30.4863 | 42.2853 | 41.9158 | 41.4032 | 40.8779 | 40.3832 | 37.6337 | 34.8179 | 32.2263
|  | PARK GATE | EE |  |  |  | 33.3958 | 44.5547 | 44.2895 | 44.0084 | 43.7147 | 43.4105 | 43.1179 | 42.8421 | 42.5747 | 42.3368 | 41.4737 | 40.3547 | 38.5916 | 29.8958 | 44.6632 | 44.3979 | 44.1168 | 43.8242 | 43.52 | 43.2284 | 42.9526 | 42.6874 | 42.4221 | 40.3484 | 38.2032 | 36.2568 | 30.6726 | 43.8768 | 43.6116 | 43.3305 | 43.0368 | 42.7337 | 42.44 | 42.1642 | 41.8979 | 41.6168 | 39.5 | 37.3021 | 35.3053
|  | PARK GATE | HT |  |  |  | 44.6779 | 44.3558 | 44.0305 | 43.6853 | 43.3295 | 42.9621 | 42.5937 | 42.2705 | 41.9779 | 41.7074 | 40.5968 | 38.0789 | 35.7768 | 44.7863 | 44.4642 | 44.1389 | 43.7937 | 43.4379 | 43.0716 | 42.7032 | 42.2126 | 41.6937 | 41.2074 | 38.5105 | 35.76 | 33.1832 | 44 | 43.6779 | 43.3526 | 43.0074 | 42.6516 | 42.2853 | 41.9158 | 41.4032 | 40.8779 | 40.3832 | 37.6337 | 34.8179 | 32.2263
|  | PARK GATE | HE |  |  |  | 33.5842 | 44.8116 | 44.6274 | 44.4232 | 44.2032 | 43.9684 | 43.7432 | 43.5316 | 43.3337 | 43.1621 | 42.5863 | 42.2526 | 5.1 | 30.2495 | 44.92 | 44.7358 | 44.5316 | 44.3116 | 44.0779 | 43.8526 | 43.6411 | 43.4442 | 43.2726 | 42.7011 | 41.1789 | 39.7905 | 30.8874 | 44.1337 | 43.9495 | 43.7453 | 43.5253 | 43.2905 | 43.0653 | 42.8537 | 42.6558 | 42.4842 | 41.9095 | 40.3337 | 38.9074
|  | PARK GATE | CF |  |  |  | 33.7 | 33.5968 | 33.4884 | 33.3811 | 33.2705 | 44.5758 | 44.4663 | 44.3579 | 44.2516 | 44.1453 | 43.6674 | 43.4295 | 43.2979 | 30.5579 | 30.3295 | 30.0863 | 29.8979 | 29.7137 | 44.6853 | 44.5758 | 44.4674 | 44.3611 | 44.2547 | 43.7789 | 43.5421 | 42.6853 | 31 | 30.8979 | 30.7916 | 30.6747 | 30.4863 | 43.8979 | 43.7884 | 43.6811 | 43.5747 | 43.4674 | 42.9905 | 42.7526 | 41.8568
MELKSHAM GSP | AMESBURY | PARK HOUSE | MINIMUM HEADROOM | SU 23138 43780 | YES | 0 | 4.5737 | 4.5053 | 4.4368 | 4.3632 | 3.9779 | 3.3979 | 2.8263 | 2.1095 | 2.0211 | 1.9305 | 0.51158 | -1.4726 | -1.9684 | 3.9347 | 3.8611 | 3.7884 | 3.7105 | 3.2653 | 2.6074 | 1.9611 | 1.1432 | 1.0684 | 0.99263 | -0.49368 | -2.6253 | -3.1211 | 4.0779 | 4.0042 | 3.9305 | 3.8526 | 3.4074 | 2.7411 | 2.0853 | 1.2568 | 1.1684 | 1.0779 | -0.50105 | -2.7411 | -3.28
|  | PARK HOUSE | EE |  |  |  | 4.6053 | 4.5526 | 4.4947 | 4.4326 | 4.3726 | 4.2768 | 4.1653 | 4.0505 | 3.9295 | 3.8063 | 2.3211 | 0.16211 | -1.0095 | 3.9695 | 3.9126 | 3.8526 | 3.7884 | 3.7253 | 3.6368 | 3.5368 | 3.4347 | 3.3305 | 3.2242 | 1.7211 | -0.54737 | -1.8368 | 4.1126 | 4.0558 | 3.9947 | 3.9284 | 3.8642 | 3.7663 | 3.6516 | 3.5326 | 3.4084 | 3.2832 | 1.6463 | -0.77368 | -2.1074
|  | PARK HOUSE | HT |  |  |  | 4.5737 | 4.5053 | 4.4368 | 4.3632 | 3.9779 | 3.3979 | 2.8263 | 2.1095 | 2.0211 | 1.9305 | 0.51158 | -1.4726 | -1.9684 | 3.9347 | 3.8611 | 3.7884 | 3.7105 | 3.2653 | 2.6074 | 1.9611 | 1.1432 | 1.0684 | 0.99263 | -0.49368 | -2.6253 | -3.1211 | 4.0779 | 4.0042 | 3.9305 | 3.8526 | 3.4074 | 2.7411 | 2.0853 | 1.2568 | 1.1684 | 1.0779 | -0.50105 | -2.7411 | -3.28
|  | PARK HOUSE | HE |  |  |  | 4.6463 | 4.6126 | 4.5789 | 4.54 | 4.5011 | 4.4305 | 4.3642 | 4.2979 | 4.2326 | 4.1695 | 3.4032 | 2 | 0.91579 | 4.0137 | 3.9789 | 3.9432 | 3.9 | 3.8611 | 3.7968 | 3.7358 | 3.6758 | 3.6179 | 3.56 | 2.7642 | 1.1926 | 0.10842 | 4.1579 | 4.1221 | 4.0863 | 4.0442 | 4.0032 | 3.9305 | 3.8632 | 3.7958 | 3.7284 | 3.6632 | 2.8116 | 1.2011 | 0.077895
|  | PARK HOUSE | CF |  |  |  | 4.6674 | 4.6484 | 4.6284 | 4.6053 | 4.5811 | 4.5368 | 4.4958 | 4.4611 | 4.4253 | 4.3926 | 4.1084 | 3.3347 | 2.6137 | 4.0368 | 4.0158 | 3.9947 | 3.9695 | 3.9432 | 3.9 | 3.8621 | 3.8284 | 3.7937 | 3.7653 | 3.4705 | 2.6053 | 1.8021 | 4.18 | 4.1589 | 4.1379 | 4.1126 | 4.0863 | 4.0411 | 3.9968 | 3.96 | 3.9221 | 3.8895 | 3.5779 | 2.6895 | 1.8621
MINETY GSP | STRATTON (2 X 90) | PARK NORTH | MINIMUM HEADROOM | SU 18052 84542 | YES | 0.053684 | 34.6063 | 34.3042 | 33.9758 | 33.5663 | 33.0705 | 32.3474 | 31.1168 | 29.9484 | 28.8253 | 27.7421 | 22.2105 | 17.7253 | -8.5684 | 30.4 | 29.6832 | 28.9863 | 28.2947 | 27.5242 | 26.7411 | 25.3716 | 24.0653 | 22.8053 | 21.5884 | 15.3158 | 10.2168 | 5.6968 | 31.54 | 30.8537 | 30.1853 | 29.5674 | 28.8242 | 28.0663 | 26.7663 | 25.5053 | 24.2484 | 23.0326 | 16.7695 | 11.6779 | 7.1642
|  | PARK NORTH | EE |  |  |  | 34.6063 | 34.3042 | 33.9853 | 33.6453 | 33.2895 | 32.8895 | 32.0105 | 31.0853 | 30.0105 | 28.9663 | 23.9674 | 20.2758 | 17.58 | 30.4 | 29.6832 | 28.9863 | 28.3726 | 27.7432 | 27.0979 | 26.1095 | 25.08 | 23.8737 | 22.6968 | 17.0042 | 12.7895 | 9.9253 | 31.54 | 30.8537 | 30.1853 | 29.5926 | 28.9832 | 28.3589 | 27.4179 | 26.44 | 25.2716 | 24.0968 | 18.4137 | 14.2042 | 11.3884
|  | PARK NORTH | HT |  |  |  | 34.7432 | 34.3611 | 33.9758 | 33.5663 | 33.0705 | 32.3474 | 31.1168 | 29.9484 | 28.8253 | 27.7421 | 22.2105 | 17.7253 | 13.7621 | 30.7905 | 29.9074 | 29.0589 | 28.2947 | 27.5242 | 26.7411 | 25.3716 | 24.0653 | 22.8053 | 21.5884 | 15.3158 | 10.2168 | 5.6968 | 31.9653 | 31.1189 | 30.3053 | 29.5674 | 28.8242 | 28.0663 | 26.7663 | 25.5053 | 24.2484 | 23.0326 | 16.7695 | 11.6779 | 7.1642
|  | PARK NORTH | HE |  |  |  | 34.8 | 34.5895 | 34.3558 | 34.0968 | 33.82 | 33.5232 | 33.24 | 32.6263 | 31.6926 | 30.8084 | 26.5821 | 23.62 | -8.5684 | 30.7947 | 30.3347 | 29.8379 | 29.4137 | 28.9674 | 28.4895 | 27.6579 | 26.7611 | 25.7063 | 24.7042 | 19.86 | 16.4505 | 13.6179 | 31.8221 | 31.4789 | 31.0011 | 30.5895 | 30.1558 | 29.6916 | 28.9011 | 28.0516 | 27.0568 | 26.1021 | 21.2653 | 17.8611 | 15.0337
|  | PARK NORTH | CF |  |  |  | 34.9158 | 34.7926 | 34.6653 | 34.5326 | 34.3968 | 34.2547 | 34.1105 | 33.9684 | 33.8284 | 33.6874 | 31.4695 | 28.7653 | 27.2421 | 30.9853 | 30.7642 | 30.5053 | 30.2558 | 30.0021 | 29.74 | 29.4758 | 29.1747 | 28.8442 | 28.4821 | 25.3842 | 22.2568 | 20.4968 | 31.9474 | 31.8126 | 31.6411 | 31.4011 | 31.1558 | 30.9032 | 30.6474 | 30.3589 | 30.0421 | 29.6968 | 26.7821 | 23.66 | 21.9021
WILLESDEN GSP | ACTON LANE | PARK ROYAL | MINIMUM HEADROOM | TQ 20137 82215 | NO | 0.5 | 13.1579 | 13.12 | 12.7453 | 12.2632 | 11.6726 | 10.9674 | 10.3032 | 9.6389 | 8.9811 | 8.3232 | 7.6453 | 7.5316 | -7.1579 | 11.5516 | 11.2337 | 10.7947 | 10.2284 | 9.5347 | 8.7063 | 7.9242 | 7.1432 | 6.3695 | 5.5958 | 4.8253 | 4.6979 | 4.5642 | 12.0189 | 11.8063 | 11.3821 | 10.8358 | 10.1663 | 9.3674 | 8.6126 | 7.84 | 7.0663 | 6.2926 | 5.5326 | 5.4063 | 5.2716
|  | PARK ROYAL | EE |  |  |  | 13.1621 | 13.1484 | 12.8042 | 12.3737 | 11.8547 | 11.2526 | 10.6516 | 10.0484 | 9.4526 | 8.8579 | 8.2074 | 8.18 | 8.0968 | 11.5642 | 11.2663 | 10.8632 | 10.3568 | 9.7474 | 9.0389 | 8.3316 | 7.6232 | 6.9221 | 6.2221 | 5.4621 | 5.4558 | 5.3611 | 12.0232 | 11.8368 | 11.4484 | 10.9589 | 10.3716 | 9.6884 | 9.0063 | 8.3211 | 7.62 | 6.92 | 6.1589 | 6.1642 | 6.0695
|  | PARK ROYAL | HT |  |  |  | 13.1579 | 13.12 | 12.7453 | 12.2632 | 11.6726 | 10.9674 | 10.3032 | 9.6389 | 8.9811 | 8.3232 | 7.6453 | 7.5316 | 7.4137 | 11.5516 | 11.2337 | 10.7947 | 10.2284 | 9.5347 | 8.7063 | 7.9242 | 7.1432 | 6.3695 | 5.5958 | 4.8253 | 4.6979 | 4.5642 | 12.0189 | 11.8063 | 11.3821 | 10.8358 | 10.1663 | 9.3674 | 8.6126 | 7.84 | 7.0663 | 6.2926 | 5.5326 | 5.4063 | 5.2716
|  | PARK ROYAL | HE |  |  |  | 13.1674 | 13.1589 | 12.8284 | 12.4021 | 11.8895 | 11.2905 | 10.6937 | 10.0979 | 9.5063 | 8.9168 | 8.2947 | 8.2368 | -7.1579 | 11.5758 | 11.2863 | 10.8895 | 10.3884 | 9.7853 | 9.0811 | 8.3789 | 7.6779 | 6.9821 | 6.2874 | 5.5589 | 5.4937 | 5.4295 | 12.0284 | 11.8568 | 11.4737 | 10.9905 | 10.4095 | 9.7295 | 9.0526 | 8.3758 | 7.6789 | 6.9853 | 6.2558 | 6.1905 | 6.1263
|  | PARK ROYAL | CF |  |  |  | 13.1705 | 13.1653 | 13.16 | 13.1537 | 13.1484 | 13.1421 | 12.8337 | 12.3611 | 11.8474 | 11.2916 | 10.1705 | 10.1337 | 10.1032 | 11.6537 | 11.6484 | 11.6316 | 11.6158 | 11.5211 | 11.2874 | 10.8979 | 10.3421 | 9.7368 | 9.0821 | 7.7642 | 7.7242 | 7.6884 | 12.0316 | 12.0263 | 12.0211 | 12.0147 | 12.0095 | 11.8579 | 11.4821 | 10.9453 | 10.3632 | 9.7305 | 8.46 | 8.4211 | 8.3863
MANNINGTON GSP | BOURNEMOUTH | PARKSTONE NORTH | MINIMUM HEADROOM | SZ 03222 92233 | YES | 0.14 | 25.7726 | 25.2158 | 24.6547 | 24.0568 | 23.4411 | 22.5379 | 21.4821 | 20.4663 | 19.4242 | 18.4021 | 13.8211 | 9.7011 | -28.6589 | 20.2316 | 19.1137 | 17.7326 | 15.9389 | 14.6326 | 13.1642 | 12.0063 | 10.88 | 9.7274 | 8.6211 | 3.6063 | -0.98947 | -5.2242 | 21.4032 | 20.6095 | 19.2642 | 17.5084 | 16.18 | 14.6853 | 13.5105 | 12.3663 | 11.1937 | 10.0663 | 5.0211 | 0.43158 | -3.7968
|  | PARKSTONE NORTH | EE |  |  |  | 25.9895 | 25.5547 | 25.0958 | 24.6074 | 24.0968 | 23.5674 | 23.0579 | 22.2589 | 21.4789 | 20.6737 | 17.1589 | 13.9832 | 11.12 | 20.7074 | 19.8347 | 18.7137 | 17.3484 | 16.0547 | 14.7084 | 13.7705 | 12.8737 | 12.0168 | 11.1158 | 7.2674 | 3.7179 | 0.48211 | 21.6358 | 21.1747 | 20.2211 | 18.8947 | 17.6253 | 16.2537 | 15.3021 | 14.3926 | 13.5232 | 12.6063 | 8.6832 | 5.1337 | 1.9021
|  | PARKSTONE NORTH | HT |  |  |  | 25.7726 | 25.2158 | 24.6547 | 24.0568 | 23.4411 | 22.5379 | 21.4821 | 20.4663 | 19.4242 | 18.4021 | 13.8211 | 9.7011 | 5.9305 | 20.2316 | 19.1137 | 17.7326 | 15.9389 | 14.6326 | 13.1642 | 12.0063 | 10.88 | 9.7274 | 8.6211 | 3.6063 | -0.98947 | -5.2242 | 21.4032 | 20.6095 | 19.2642 | 17.5084 | 16.18 | 14.6853 | 13.5105 | 12.3663 | 11.1937 | 10.0663 | 5.0211 | 0.43158 | -3.7968
|  | PARKSTONE NORTH | HE |  |  |  | 26.2779 | 25.9789 | 25.6495 | 25.2853 | 24.8937 | 24.4758 | 24.0758 | 23.6989 | 23.3474 | 23.0432 | 20.9274 | 18.7884 | -28.6589 | 21.1453 | 20.7695 | 19.9337 | 18.8305 | 17.8032 | 16.7053 | 16.0126 | 15.3684 | 14.7411 | 14.0621 | 11.3516 | 8.9505 | 6.78 | 21.9442 | 21.6295 | 21.2695 | 20.3411 | 19.3411 | 18.2737 | 17.5832 | 16.9305 | 16.2947 | 15.6032 | 12.84 | 10.3811 | 8.1926
|  | PARKSTONE NORTH | CF |  |  |  | 26.4474 | 26.2768 | 26.1021 | 25.9189 | 25.7295 | 25.5347 | 25.3347 | 25.1389 | 24.9442 | 24.7505 | 23.8842 | 23.3147 | 22.1021 | 21.3242 | 21.1432 | 20.8789 | 20.4421 | 20.0042 | 19.4674 | 19.0379 | 18.5747 | 18.0989 | 17.6379 | 15.6558 | 13.9716 | 12.5211 | 22.1232 | 21.9421 | 21.7516 | 21.5537 | 21.3484 | 20.9611 | 20.5411 | 20.0895 | 19.6263 | 19.1768 | 17.2211 | 15.4968 | 14.0084
MANNINGTON GSP | BOURNEMOUTH | PARKSTONE SOUTH | MINIMUM HEADROOM | SZ 04762 89848 | YES | 0 | 33.2863 | 32.9863 | 32.6705 | 32.3305 | 31.8168 | 31.2989 | 30.7463 | 30.2158 | 29.6811 | 29.1737 | 26.8832 | 24.8137 | 7.9411 | 30.2484 | 29.7653 | 29.0316 | 28.4842 | 27.9358 | 27.3842 | 26.7905 | 26.2179 | 25.6358 | 25.0811 | 22.5621 | 20.2611 | 18.1358 | 30.8526 | 30.3116 | 29.5747 | 29.0284 | 28.48 | 27.9284 | 27.3358 | 26.7632 | 26.1811 | 25.6274 | 23.1105 | 20.8105 | 18.6884
|  | PARKSTONE SOUTH | EE |  |  |  | 33.3979 | 33.1674 | 32.9147 | 32.6484 | 32.3737 | 32.0126 | 31.5737 | 31.1495 | 30.7421 | 30.3211 | 28.5347 | 26.9474 | 25.5242 | 30.3968 | 30.1147 | 29.6011 | 29.1042 | 28.6221 | 28.1568 | 27.6863 | 27.2326 | 26.7958 | 26.3368 | 24.3779 | 22.6084 | 21.0053 | 31.0179 | 30.6758 | 30.1442 | 29.6474 | 29.1653 | 28.7011 | 28.2305 | 27.7758 | 27.34 | 26.8832 | 24.9232 | 23.1547 | 21.5526
|  | PARKSTONE SOUTH | HT |  |  |  | 33.2863 | 32.9863 | 32.6705 | 32.3305 | 31.8168 | 31.2989 | 30.7463 | 30.2158 | 29.6811 | 29.1737 | 26.8832 | 24.8137 | 22.9168 | 30.2484 | 29.7653 | 29.0316 | 28.4842 | 27.9358 | 27.3842 | 26.7905 | 26.2179 | 25.6358 | 25.0811 | 22.5621 | 20.2611 | 18.1358 | 30.8526 | 30.3116 | 29.5747 | 29.0284 | 28.48 | 27.9284 | 27.3358 | 26.7632 | 26.1811 | 25.6274 | 23.1105 | 20.8105 | 18.6884
|  | PARKSTONE SOUTH | HE |  |  |  | 33.5368 | 33.3832 | 33.2042 | 33.0032 | 32.7905 | 32.5642 | 32.3453 | 32.14 | 31.9474 | 31.6937 | 30.4589 | 29.3979 | 7.9411 | 30.5926 | 30.4042 | 30.1621 | 29.8474 | 29.5063 | 29.1716 | 28.8211 | 28.4926 | 28.1768 | 27.8379 | 26.48 | 25.2884 | 24.2411 | 31.16 | 31.0063 | 30.7537 | 30.3958 | 30.0495 | 29.7147 | 29.3642 | 29.0368 | 28.7189 | 28.3811 | 27.0242 | 25.8337 | 24.7884
|  | PARKSTONE SOUTH | CF |  |  |  | 33.6158 | 33.5221 | 33.4253 | 33.3253 | 33.22 | 33.1042 | 32.9874 | 32.8684 | 32.7516 | 32.6347 | 31.9547 | 31.1737 | 30.5232 | 30.6926 | 30.5726 | 30.4505 | 30.3242 | 30.1947 | 30.0558 | 29.8505 | 29.6095 | 29.3653 | 29.1211 | 28.0821 | 27.2063 | 26.4632 | 31.2389 | 31.1453 | 31.0484 | 30.9453 | 30.8347 | 30.6274 | 30.3989 | 30.1537 | 29.9074 | 29.6642 | 28.6263 | 27.7505 | 27.0095
BRAMLEY (FLEE) | WOKINGHAM BSP | PEACOCK FARM | MINIMUM HEADROOM | SU 84770 68709 | YES | 0.34316 | 16.2684 | 16.1789 | 16.0884 | 15.9579 | 15.78 | 15.5789 | 15.3937 | 15.2211 | 15.0632 | 14.9211 | 14.2621 | 13.5126 | 2.4011 | 14.4853 | 14.2821 | 13.9884 | 13.7853 | 13.58 | 13.3474 | 13.1337 | 12.9337 | 12.7516 | 12.5874 | 11.8105 | 10.9874 | 10.2179 | 15.1526 | 14.9463 | 14.6453 | 14.4368 | 14.2284 | 13.9905 | 13.7737 | 13.5695 | 13.3842 | 13.2158 | 12.4221 | 11.5779 | 10.7863
|  | PEACOCK FARM | EE |  |  |  | 16.3011 | 16.2295 | 16.1547 | 16.0747 | 15.9789 | 15.8137 | 15.6621 | 15.5189 | 15.3926 | 15.2768 | 14.7958 | 14.2937 | 13.7853 | 14.5232 | 14.3958 | 14.1474 | 13.9842 | 13.8126 | 13.6232 | 13.4474 | 13.2832 | 13.1411 | 13.0095 | 12.4495 | 11.8358 | 11.2747 | 15.1916 | 15.0611 | 14.8063 | 14.64 | 14.4663 | 14.2726 | 14.0937 | 13.9274 | 13.7821 | 13.6484 | 13.0768 | 12.4474 | 11.8695
|  | PEACOCK FARM | HT |  |  |  | 16.2684 | 16.1789 | 16.0884 | 15.9579 | 15.78 | 15.5789 | 15.3937 | 15.2211 | 15.0632 | 14.9211 | 14.2621 | 13.5126 | 12.8074 | 14.4853 | 14.2821 | 13.9884 | 13.7853 | 13.58 | 13.3474 | 13.1337 | 12.9337 | 12.7516 | 12.5874 | 11.8105 | 10.9874 | 10.2179 | 15.1526 | 14.9463 | 14.6453 | 14.4368 | 14.2284 | 13.9905 | 13.7737 | 13.5695 | 13.3842 | 13.2158 | 12.4221 | 11.5779 | 10.7863
|  | PEACOCK FARM | HE |  |  |  | 16.3495 | 16.3011 | 16.2474 | 16.1884 | 16.1253 | 16.0579 | 15.9853 | 15.8747 | 15.7842 | 15.7011 | 15.3726 | 15.0147 | 2.4011 | 14.5716 | 14.5232 | 14.3495 | 14.2305 | 14.1095 | 13.9579 | 13.8211 | 13.6947 | 13.5926 | 13.4989 | 13.1168 | 12.6716 | 12.2747 | 15.24 | 15.1916 | 15.0126 | 14.8916 | 14.7684 | 14.6147 | 14.4747 | 14.3463 | 14.2421 | 14.1463 | 13.7568 | 13.3 | 12.8895
|  | PEACOCK FARM | CF |  |  |  | 16.3758 | 16.3484 | 16.3189 | 16.2884 | 16.2579 | 16.2253 | 16.1926 | 16.1611 | 16.1284 | 16.0958 | 15.9495 | 15.7358 | 15.5589 | 14.5979 | 14.5705 | 14.5411 | 14.5105 | 14.4695 | 14.3821 | 14.2926 | 14.2137 | 14.1442 | 14.08 | 13.7863 | 13.5253 | 13.3021 | 15.2663 | 15.2389 | 15.2095 | 15.1789 | 15.1368 | 15.0484 | 14.9558 | 14.8747 | 14.8042 | 14.7389 | 14.44 | 14.1726 | 13.9432
WILLESDEN GSP |  | PERIVALE | MINIMUM HEADROOM | TQ 17544 82947 | NO | 0.72632 | 82.2242 | 82.0211 | 81.8158 | 81.5979 | 81.3705 | 81.1337 | 80.8958 | 80.6832 | 80.4884 | 80.3084 | 79.56 | 78.4526 | 24.0779 | 77.5168 | 77.1379 | 76.7137 | 76.26 | 75.7968 | 75.3274 | 74.8821 | 74.4705 | 74.0947 | 73.7368 | 72.0705 | 70.3263 | 68.6632 | 78.6589 | 78.4432 | 78.2242 | 77.9905 | 77.5389 | 77.0537 | 76.6137 | 76.2032 | 75.8274 | 75.4695 | 73.8053 | 72.0632 | 70.4021
|  | PERIVALE | EE |  |  |  | 82.2926 | 82.1295 | 81.9558 | 81.7716 | 81.5768 | 81.3737 | 81.1758 | 80.9863 | 80.8032 | 80.6379 | 80.0242 | 79.5937 | 79.1495 | 77.5926 | 77.3926 | 77.0716 | 76.7232 | 76.3684 | 76.0168 | 75.6779 | 75.3568 | 75.0495 | 74.7589 | 73.4968 | 72.2726 | 71.1295 | 78.7337 | 78.5611 | 78.3779 | 78.1832 | 77.9779 | 77.7653 | 77.4253 | 77.0958 | 76.78 | 76.4853 | 75.2295 | 74.0074 | 72.8653
|  | PERIVALE | HT |  |  |  | 82.2242 | 82.0211 | 81.8158 | 81.5979 | 81.3705 | 81.1337 | 80.8958 | 80.6832 | 80.4884 | 80.3084 | 79.56 | 78.4526 | 77.04 | 77.5168 | 77.1379 | 76.7137 | 76.26 | 75.7968 | 75.3274 | 74.8821 | 74.4705 | 74.0947 | 73.7368 | 72.0705 | 70.3263 | 68.6632 | 78.6589 | 78.4432 | 78.2242 | 77.9905 | 77.5389 | 77.0537 | 76.6137 | 76.2032 | 75.8274 | 75.4695 | 73.8053 | 72.0632 | 70.4021
|  | PERIVALE | HE |  |  |  | 82.3874 | 82.2674 | 82.1337 | 81.9863 | 81.8274 | 81.6579 | 81.4968 | 81.3442 | 81.2021 | 81.0789 | 80.6579 | 80.4021 | 24.0779 | 77.6926 | 77.5684 | 77.4305 | 77.2274 | 76.9611 | 76.6853 | 76.4316 | 76.1937 | 75.9747 | 75.7768 | 75.0221 | 74.28 | 73.5895 | 78.8368 | 78.7105 | 78.5705 | 78.4168 | 78.2505 | 78.0747 | 77.9074 | 77.7495 | 77.6021 | 77.4747 | 76.76 | 76.0116 | 75.3221
|  | PERIVALE | CF |  |  |  | 82.4421 | 82.3663 | 82.2874 | 82.2053 | 82.1211 | 82.0337 | 81.9442 | 81.8568 | 81.7705 | 81.6832 | 81.2968 | 81.1021 | 80.9937 | 77.7495 | 77.6716 | 77.5884 | 77.5032 | 77.4126 | 77.2821 | 77.1253 | 76.9726 | 76.8221 | 76.6705 | 75.9474 | 75.44 | 74.9958 | 78.8947 | 78.8147 | 78.7316 | 78.6453 | 78.5558 | 78.4642 | 78.3705 | 78.2789 | 78.1884 | 78.0968 | 77.6895 | 77.1758 | 76.7263
BRAMLEY (FLEE) | FERNHURST | PETERSFIELD | MINIMUM HEADROOM | SU 74173 23420 | YES | 0.50526 | 36.5 | 36.1189 | 35.7347 | 35.3274 | 34.9074 | 34.3821 | 33.6295 | 32.9737 | 32.2905 | 31.5758 | 28.0389 | 24.7516 | -6.6232 | 30.4179 | 29.72 | 29.0326 | 28.2989 | 27.4105 | 26.5095 | 25.6989 | 24.9937 | 24.2484 | 23.4621 | 19.5168 | 15.8074 | 12.3832 | 31.4895 | 30.9379 | 30.2063 | 29.4442 | 28.5568 | 27.6568 | 26.8463 | 26.1432 | 25.3979 | 24.6126 | 20.6726 | 16.9684 | 13.5484
|  | PETERSFIELD | EE |  |  |  | 36.6442 | 36.3474 | 36.0326 | 35.6968 | 35.3484 | 34.9863 | 34.6389 | 34.3074 | 33.8368 | 33.2463 | 30.4495 | 27.8568 | 25.4979 | 30.7221 | 30.1821 | 29.6347 | 29.0716 | 28.4116 | 27.7095 | 27.1 | 26.5537 | 25.9526 | 25.3063 | 22.1874 | 19.2474 | 16.5516 | 31.6337 | 31.3358 | 30.8537 | 30.2568 | 29.5568 | 28.8547 | 28.2463 | 27.7011 | 27.1 | 26.4547 | 23.34 | 20.4042 | 17.7126
|  | PETERSFIELD | HT |  |  |  | 36.5 | 36.1189 | 35.7347 | 35.3274 | 34.9074 | 34.3821 | 33.6295 | 32.9737 | 32.2905 | 31.5758 | 28.0389 | 24.7516 | 21.7368 | 30.4179 | 29.72 | 29.0326 | 28.2989 | 27.4105 | 26.5095 | 25.6989 | 24.9937 | 24.2484 | 23.4621 | 19.5168 | 15.8074 | 12.3832 | 31.4895 | 30.9379 | 30.2063 | 29.4442 | 28.5568 | 27.6568 | 26.8463 | 26.1432 | 25.3979 | 24.6126 | 20.6726 | 16.9684 | 13.5484
|  | PETERSFIELD | HE |  |  |  | 36.8453 | 36.6421 | 36.4189 | 36.1705 | 35.9032 | 35.62 | 35.3474 | 35.0916 | 35.5811 | 35.1432 | 33.0653 | 31.1453 | -6.6232 | 30.9937 | 30.7811 | 30.4337 | 30.0516 | 29.5642 | 29.0653 | 28.6442 | 28.28 | 27.8579 | 27.3779 | 25.0484 | 22.8505 | 20.8568 | 31.8347 | 31.6316 | 31.4084 | 31.16 | 30.7916 | 30.2611 | 29.8179 | 29.4379 | 29.0042 | 28.5232 | 26.1968 | 24.0032 | 22.0126
|  | PETERSFIELD | CF |  |  |  | 36.96 | 36.8442 | 36.7253 | 36.6 | 36.4716 | 36.3389 | 36.2032 | 36.0695 | 35.9368 | 35.8042 | 35.2158 | 34.3242 | 33.2126 | 31.1147 | 30.9916 | 30.8663 | 30.6779 | 30.4526 | 30.2189 | 29.9821 | 29.7505 | 29.5211 | 29.2863 | 27.8232 | 26.3589 | 25.0737 | 31.9495 | 31.8337 | 31.7147 | 31.5895 | 31.4611 | 31.3284 | 31.1874 | 30.98 | 30.7368 | 30.4874 | 28.9695 | 27.5074 | 26.2242
IVER 132KV | CHALVEY BSP | PETERSFIELD AVENUE | MINIMUM HEADROOM | SU 98108 80286 | YES | 0.36 | 58.1758 | 57.9232 | 57.6095 | 55.4347 | 52.9147 | 50.9221 | 49.6337 | 49.0747 | 48.5379 | 48.0274 | 45.6095 | 43.5263 | 13.3589 | 51.3084 | 49.7253 | 47.7432 | 45.2211 | 42.2937 | 39.9905 | 38.5221 | 37.9084 | 37.3179 | 36.7558 | 34.0653 | 31.7326 | 29.5726 | 52.9684 | 51.3105 | 49.3032 | 46.7853 | 43.8621 | 41.5632 | 40.0968 | 39.4842 | 38.8947 | 38.3326 | 35.6453 | 33.3158 | 31.1589
|  | PETERSFIELD AVENUE | EE |  |  |  | 58.2674 | 58.0653 | 57.8526 | 55.9095 | 53.4737 | 51.5632 | 50.3663 | 49.8979 | 49.4326 | 48.9989 | 47.0411 | 45.4168 | 43.9568 | 51.5116 | 50.0463 | 48.1674 | 45.74 | 42.9042 | 40.6916 | 39.32 | 38.8084 | 38.2989 | 37.8232 | 35.6453 | 33.82 | 32.1663 | 53.1 | 51.6337 | 49.7263 | 47.3032 | 44.4726 | 42.2632 | 40.8947 | 40.3832 | 39.8747 | 39.3989 | 37.2242 | 35.4011 | 33.7495
|  | PETERSFIELD AVENUE | HT |  |  |  | 58.1758 | 57.9232 | 57.6095 | 55.4347 | 52.9147 | 50.9221 | 49.6337 | 49.0747 | 48.5379 | 48.0274 | 45.6095 | 43.5263 | 41.6105 | 51.3084 | 49.7253 | 47.7432 | 45.2211 | 42.2937 | 39.9905 | 38.5221 | 37.9084 | 37.3179 | 36.7558 | 34.0653 | 31.7326 | 29.5726 | 52.9684 | 51.3105 | 49.3032 | 46.7853 | 43.8621 | 41.5632 | 40.0968 | 39.4842 | 38.8947 | 38.3326 | 35.6453 | 33.3158 | 31.1589
|  | PETERSFIELD AVENUE | HE |  |  |  | 58.3853 | 58.2379 | 58.0747 | 56.5105 | 54.1821 | 52.3695 | 51.2716 | 50.9042 | 50.5421 | 50.2137 | 48.78 | 47.6621 | 13.3589 | 51.7789 | 50.46 | 48.7042 | 46.4032 | 43.6842 | 41.5789 | 40.3168 | 39.9168 | 39.52 | 39.1589 | 37.5568 | 36.2926 | 35.1895 | 53.2284 | 52.0516 | 50.2695 | 47.9653 | 45.2516 | 43.1505 | 41.8905 | 41.4905 | 41.0937 | 40.7337 | 39.1337 | 37.8716 | 36.7695
|  | PETERSFIELD AVENUE | CF |  |  |  | 58.4558 | 58.3663 | 58.2726 | 58.1747 | 58.0737 | 57.9705 | 56.0926 | 55.3274 | 55.1189 | 54.9147 | 53.8105 | 53.0116 | 52.3442 | 52.2884 | 52.1705 | 51.9337 | 51.3663 | 50.3737 | 48.4474 | 45.9137 | 45.0284 | 44.8 | 44.5768 | 43.3558 | 42.4537 | 41.6874 | 53.3568 | 53.2621 | 53.1389 | 53.0042 | 51.9674 | 50.0095 | 47.4768 | 46.5926 | 46.3653 | 46.1432 | 44.9232 | 44.0221 | 43.2568
MANNINGTON GSP | SALISBURY | PETERSFINGER | MINIMUM HEADROOM | SU 15608 29334 | YES | 0 | 26.5526 | 26.2874 | 26.0158 | 25.7284 | 25.2726 | 24.54 | 23.8084 | 23.12 | 22.5547 | 22.0568 | 19.3284 | 16.5726 | 0.61895 | 23.0274 | 22.4495 | 21.9358 | 21.2495 | 20.5242 | 19.7368 | 18.9526 | 18.2126 | 17.6168 | 17.1 | 14.2558 | 11.3305 | 8.5684 | 24.1084 | 23.8232 | 23.3653 | 22.7179 | 21.9937 | 21.1937 | 20.3968 | 19.6432 | 19.0316 | 18.4979 | 15.5305 | 12.4895 | 9.6779
|  | PETERSFINGER | EE |  |  |  | 26.6568 | 26.4495 | 26.2263 | 25.9884 | 25.9937 | 25.3979 | 24.7979 | 24.1674 | 23.3768 | 22.9516 | 20.6789 | 18.2116 | 16.1905 | 23.2579 | 22.8421 | 22.4011 | 21.8821 | 21.3211 | 20.6842 | 20.0495 | 19.3811 | 18.5263 | 18.1 | 15.8158 | 13.3011 | 11.08 | 24.22 | 24.0011 | 23.7663 | 23.3168 | 22.7863 | 22.1389 | 21.4863 | 20.7989 | 19.9242 | 19.4737 | 17.0305 | 14.3347 | 12.06
|  | PETERSFINGER | HT |  |  |  | 26.5526 | 26.2874 | 26.0158 | 25.7284 | 25.2726 | 24.54 | 23.8084 | 23.12 | 22.5547 | 22.0568 | 19.3284 | 16.5726 | 14.0726 | 23.0274 | 22.4495 | 21.9358 | 21.2495 | 20.5242 | 19.7368 | 18.9526 | 18.2126 | 17.6168 | 17.1 | 14.2558 | 11.3305 | 8.5684 | 24.1084 | 23.8232 | 23.3653 | 22.7179 | 21.9937 | 21.1937 | 20.3968 | 19.6432 | 19.0316 | 18.4979 | 15.5305 | 12.4895 | 9.6779
|  | PETERSFINGER | HE |  |  |  | 26.7979 | 26.6579 | 26.5032 | 26.3326 | 26.8 | 26.3189 | 25.8537 | 25.3526 | 24.7347 | 24.48 | 23.0642 | 21.5547 | 0.61895 | 23.5579 | 23.3021 | 23.0084 | 22.6274 | 22.1926 | 21.6779 | 21.1789 | 20.6347 | 19.9547 | 19.6947 | 18.2232 | 16.5821 | 14.8705 | 24.3705 | 24.2232 | 24.0611 | 23.8779 | 23.6611 | 23.1368 | 22.6305 | 22.0779 | 21.3884 | 21.1189 | 19.5821 | 17.8916 | 16.1358
|  | PETERSFINGER | CF |  |  |  | 26.8789 | 26.8011 | 26.72 | 26.6358 | 26.5474 | 26.4421 | 26.3358 | 26.2284 | 26.1253 | 26.0232 | 25.0916 | 24.2179 | 23.2379 | 23.6484 | 23.5663 | 23.4811 | 23.3537 | 23.1895 | 22.9895 | 22.7779 | 22.5442 | 22.2168 | 21.8726 | 20.3326 | 19.3884 | 18.3053 | 24.4621 | 24.38 | 24.2947 | 24.2063 | 24.1126 | 24.0042 | 23.8916 | 23.7789 | 23.5895 | 23.3 | 21.7621 | 20.7884 | 19.6768
MELKSHAM GSP | AMESBURY | PEWSEY | MINIMUM HEADROOM | SU 14710 59252 | YES | 0.065263 | 15.7337 | 15.4579 | 15.1853 | 14.9074 | 14.6253 | 14.2842 | 13.8968 | 13.5368 | 13.2926 | 13.0316 | 11.6674 | 10.2789 | 1.5684 | 13.9505 | 13.6537 | 13.36 | 13.0642 | 12.8347 | 12.4705 | 12.0505 | 11.6589 | 11.4042 | 11.1263 | 9.6579 | 8.1463 | 6.7021 | 14.3526 | 14.0547 | 13.7621 | 13.4642 | 13.1632 | 12.7947 | 12.3726 | 11.9789 | 11.72 | 11.4368 | 9.9432 | 8.4 | 6.9442
|  | PEWSEY | EE |  |  |  | 15.8547 | 15.6432 | 15.4242 | 15.2011 | 14.9716 | 14.6968 | 14.3958 | 14.0674 | 13.7979 | 13.5968 | 12.5116 | 11.3684 | 10.3453 | 14.0821 | 13.8547 | 13.62 | 13.3821 | 13.1389 | 12.8442 | 12.5221 | 12.1674 | 11.8821 | 11.6747 | 10.5326 | 9.3074 | 8.1632 | 14.4821 | 14.2558 | 14.0221 | 13.7832 | 13.5389 | 13.2432 | 12.9168 | 12.5579 | 12.2674 | 12.0547 | 10.8758 | 9.6095 | 8.4505
|  | PEWSEY | HT |  |  |  | 15.7337 | 15.4579 | 15.1853 | 14.9074 | 14.6253 | 14.2842 | 13.8968 | 13.5368 | 13.2926 | 13.0316 | 11.6674 | 10.2789 | 8.9874 | 13.9505 | 13.6537 | 13.36 | 13.0642 | 12.8347 | 12.4705 | 12.0505 | 11.6589 | 11.4042 | 11.1263 | 9.6579 | 8.1463 | 6.7021 | 14.3526 | 14.0547 | 13.7621 | 13.4642 | 13.1632 | 12.7947 | 12.3726 | 11.9789 | 11.72 | 11.4368 | 9.9432 | 8.4 | 6.9442
|  | PEWSEY | HE |  |  |  | 16.0232 | 15.8895 | 15.7495 | 15.6011 | 15.4421 | 15.2337 | 15.0032 | 14.7347 | 14.5516 | 14.4211 | 13.7116 | 12.9505 | 1.5684 | 14.2611 | 14.1211 | 13.9737 | 13.8168 | 13.6484 | 13.4263 | 13.1779 | 12.8853 | 12.6895 | 12.5537 | 11.7937 | 10.9484 | 10.0832 | 14.6579 | 14.52 | 14.3747 | 14.2189 | 14.0505 | 13.8263 | 13.5758 | 13.28 | 13.0821 | 12.9453 | 12.1705 | 11.3116 | 10.4358
|  | PEWSEY | CF |  |  |  | 16.1105 | 16.0305 | 15.9495 | 15.8653 | 15.7811 | 15.68 | 15.5716 | 15.4674 | 15.3579 | 15.2442 | 14.7337 | 14.2926 | 13.7968 | 14.3432 | 14.2695 | 14.1832 | 14.0947 | 14.0053 | 13.8968 | 13.78 | 13.6695 | 13.5495 | 13.4274 | 12.8747 | 12.3884 | 11.8274 | 14.7358 | 14.6653 | 14.5811 | 14.4937 | 14.4063 | 14.2979 | 14.18 | 14.0674 | 13.9474 | 13.8242 | 13.2663 | 12.7737 | 12.2063
CHICKERELL GSP | CHICKERELL BSP | PIDDLETRENTHIDE | MINIMUM HEADROOM | SY 70169 99809 | YES | 0.13158 | 6.4832 | 6.4042 | 6.3232 | 3.6168 | 3.5537 | 3.4863 | 3.42 | 3.3547 | 3.2937 | 3.2347 | 1.9379 | 1.1779 | 1.1011 | 6.2158 | 6.1326 | 6.0474 | 3.8526 | 3.7874 | 3.7179 | 3.6505 | 3.5853 | 3.5221 | 3.4621 | 1.0011 | 0.85579 | 0.75684 | 6.2516 | 6.1684 | 6.0821 | 3.3295 | 3.2663 | 3.1979 | 3.1305 | 3.0642 | 3.0011 | 2.94 | 1.0284 | 0.60421 | 0.52737
|  | PIDDLETRENTHIDE | EE |  |  |  | 6.5189 | 6.4579 | 6.3937 | 3.6168 | 3.5537 | 3.4863 | 3.42 | 3.3547 | 3.2937 | 3.2347 | 2.8516 | 1.1779 | 1.1011 | 6.2547 | 6.1905 | 6.1221 | 3.8526 | 3.7874 | 3.7179 | 3.6505 | 3.5853 | 3.5221 | 3.4621 | 3.0663 | 1.1937 | 1.12 | 6.2895 | 6.2253 | 6.1568 | 3.3295 | 3.2663 | 3.1979 | 3.1305 | 3.0642 | 3.0011 | 2.94 | 2.5242 | 0.60421 | 0.52737
|  | PIDDLETRENTHIDE | HT |  |  |  | 6.4832 | 6.4042 | 6.3232 | 6.2442 | 6.1642 | 6.0821 | 6.0011 | 5.2779 | 5.2316 | 5.1884 | 1.9379 | 1.78 | 1.6758 | 6.2158 | 6.1326 | 6.0474 | 5.9632 | 5.8789 | 5.7947 | 5.7105 | 4.8716 | 4.8263 | 4.7853 | 1.0011 | 0.85579 | 0.75684 | 6.2516 | 6.1684 | 6.0821 | 5.9979 | 5.9137 | 5.8284 | 5.7432 | 4.9032 | 4.8558 | 4.8126 | 1.0284 | 0.87053 | 0.76632
|  | PIDDLETRENTHIDE | HE |  |  |  | 6.5674 | 6.5305 | 6.4884 | 6.4484 | 6.4053 | 6.3579 | 6.3116 | 6.2695 | 6.2284 | 6.1916 | 5.7674 | 4.1726 | 1.9516 | 6.3063 | 6.2674 | 6.2232 | 6.1811 | 6.1358 | 6.0874 | 6.04 | 5.9968 | 5.9568 | 5.9189 | 5.4495 | 3.5895 | 3.5495 | 6.3379 | 6.3011 | 6.2579 | 6.2158 | 6.1716 | 6.1221 | 6.0747 | 6.0305 | 5.9884 | 5.9505 | 5.4737 | 3.6126 | 3.5674
|  | PIDDLETRENTHIDE | CF |  |  |  | 6.5926 | 6.5716 | 6.5484 | 6.5242 | 6.5011 | 6.4747 | 6.4495 | 6.4242 | 6.3989 | 6.3747 | 6.2621 | 6.1547 | 6.0453 | 6.3326 | 6.3105 | 6.2853 | 6.26 | 6.2358 | 6.2095 | 6.1821 | 6.1558 | 6.1295 | 6.1053 | 5.9874 | 5.8737 | 5.7547 | 6.3632 | 6.3421 | 6.3179 | 6.2947 | 6.2695 | 6.2432 | 6.2168 | 6.1895 | 6.1632 | 6.1379 | 6.0179 | 5.9032 | 5.7811
BRAMLEY (FLEE) | FERNHURST | PLAISTOW | MINIMUM HEADROOM | TQ 02071 29626 | YES | 0.50316 | 16.2084 | 16.0358 | 15.8653 | 15.6653 | 15.4684 | 15.0968 | 14.6232 | 14.0526 | 13.9642 | 13.8832 | 12.8747 | 11.5495 | 5.7884 | 14.5105 | 14.3253 | 14.1421 | 13.9263 | 13.7147 | 13.2968 | 12.7484 | 12.08 | 11.9916 | 11.9105 | 10.7589 | 9.2084 | 8.7979 | 14.6842 | 14.5021 | 14.3232 | 14.1126 | 13.9053 | 13.5021 | 12.9821 | 12.3147 | 12.2263 | 12.1453 | 10.9958 | 9.4474 | 9.0379
|  | PLAISTOW | EE |  |  |  | 16.2874 | 16.1558 | 16.0189 | 15.8621 | 15.7137 | 15.5642 | 15.5032 | 15.3747 | 15.2337 | 15.0916 | 13.5484 | 12.8695 | 12.2621 | 14.5968 | 14.4558 | 14.3095 | 14.14 | 13.9811 | 13.8221 | 13.6853 | 13.5495 | 13.3968 | 13.2421 | 11.4705 | 10.7 | 10.0074 | 14.7674 | 14.6295 | 14.4863 | 14.3211 | 14.1642 | 14.0084 | 13.9179 | 13.7821 | 13.6295 | 13.4747 | 11.7063 | 10.9379 | 10.2453
|  | PLAISTOW | HT |  |  |  | 16.2084 | 16.0358 | 15.8653 | 15.6653 | 15.4684 | 15.0968 | 14.6232 | 14.0526 | 13.9642 | 13.8832 | 12.8747 | 11.5495 | 11.1726 | 14.5105 | 14.3253 | 14.1421 | 13.9263 | 13.7147 | 13.2968 | 12.7484 | 12.08 | 11.9916 | 11.9105 | 10.7589 | 9.2084 | 8.7979 | 14.6842 | 14.5021 | 14.3232 | 14.1126 | 13.9053 | 13.5021 | 12.9821 | 12.3147 | 12.2263 | 12.1453 | 10.9958 | 9.4474 | 9.0379
|  | PLAISTOW | HE |  |  |  | 16.3895 | 16.3105 | 16.2242 | 16.1158 | 16.0105 | 15.9 | 15.8853 | 15.7947 | 15.6937 | 15.5874 | 14.2221 | 13.7021 | 5.7884 | 14.7105 | 14.6242 | 14.5316 | 14.4137 | 14.3021 | 14.1842 | 14.1011 | 14.0053 | 13.8968 | 13.78 | 12.2032 | 11.6084 | 11.08 | 14.8789 | 14.7947 | 14.7032 | 14.5884 | 14.4789 | 14.3632 | 14.3326 | 14.2368 | 14.1295 | 14.0126 | 12.4379 | 11.8453 | 11.3168
|  | PLAISTOW | CF |  |  |  | 16.4432 | 16.3968 | 16.3484 | 16.2937 | 16.2389 | 16.18 | 16.1263 | 16.0737 | 16.0189 | 15.9579 | 15.1 | 14.7579 | 14.4663 | 14.7695 | 14.7179 | 14.6642 | 14.6042 | 14.5432 | 14.4811 | 14.4221 | 14.3653 | 14.3074 | 14.2411 | 13.2495 | 12.8516 | 12.5063 | 14.9368 | 14.8863 | 14.8337 | 14.7747 | 14.7158 | 14.6547 | 14.5979 | 14.5421 | 14.4853 | 14.42 | 13.4779 | 13.0853 | 12.7411
MINETY GSP | STRATTON (2 X 90) | PLESSEY | MINIMUM HEADROOM | SU 16381 86720 | YES | 0.78947 | 17.8358 | 17.6421 | 17.4484 | 17.2442 | 17.0305 | 16.8074 | 16.5779 | 16.3758 | 16.1916 | 16.0326 | 14.7168 | 12.4389 | -8.4253 | 14.8505 | 14.5389 | 14.2021 | 13.4747 | 13.3053 | 13.0284 | 12.5442 | 12.0979 | 11.7074 | 11.5053 | 9.9937 | 7.3874 | 4.8337 | 15.6726 | 15.3611 | 15.0168 | 14.3411 | 14.1716 | 13.8863 | 13.4232 | 12.9968 | 12.6221 | 12.4242 | 10.9779 | 8.5316 | 6.0863
|  | PLESSEY | EE |  |  |  | 17.9053 | 17.7516 | 17.5884 | 17.3621 | 17.1926 | 17.0158 | 16.8453 | 16.6832 | 16.5126 | 16.3568 | 15.72 | 13.8989 | 12.1053 | 14.9821 | 14.7379 | 14.4853 | 13.4747 | 13.3053 | 13.1284 | 12.9579 | 12.7958 | 12.4537 | 12.1168 | 11.1063 | 9.0147 | 6.9411 | 15.7463 | 15.5842 | 15.3074 | 14.3411 | 14.1716 | 13.9947 | 13.8242 | 13.6621 | 13.3347 | 13.0126 | 12.0389 | 10.0779 | 8.14
|  | PLESSEY | HT |  |  |  | 17.8358 | 17.6421 | 17.4484 | 17.2442 | 17.0305 | 16.8074 | 16.5779 | 16.3758 | 16.1916 | 16.0326 | 14.7168 | 12.4389 | 10.22 | 14.8505 | 14.5389 | 14.2021 | 13.8389 | 13.4653 | 13.0284 | 12.5442 | 12.0979 | 11.7074 | 11.5053 | 9.9937 | 7.3874 | 4.8337 | 15.6726 | 15.3611 | 15.0168 | 14.6663 | 14.3063 | 13.8863 | 13.4232 | 12.9968 | 12.6221 | 12.4242 | 10.9779 | 8.5316 | 6.0863
|  | PLESSEY | HE |  |  |  | 18 | 17.8979 | 17.7811 | 17.6505 | 17.5116 | 17.3589 | 17.2084 | 17.0632 | 16.9263 | 16.8116 | 16.4537 | 15.5 | -8.4253 | 15.1063 | 15.0011 | 14.8316 | 14.6442 | 14.4495 | 14.2074 | 13.8747 | 13.5116 | 13.1674 | 12.8958 | 12.4211 | 10.7726 | 9.0632 | 15.8442 | 15.7421 | 15.62 | 15.4853 | 15.2821 | 15.0168 | 14.6968 | 14.3516 | 14.0242 | 13.7653 | 13.3 | 11.76 | 10.1684
|  | PLESSEY | CF |  |  |  | 18.0568 | 17.9979 | 17.9379 | 17.8726 | 17.8032 | 17.7316 | 17.6589 | 17.5874 | 17.5158 | 17.4411 | 17.1137 | 16.9168 | 16.3968 | 15.1632 | 15.1042 | 15.0442 | 14.9568 | 14.8495 | 14.7389 | 14.6263 | 14.5126 | 14.3989 | 14.24 | 13.5253 | 12.7537 | 11.7232 | 15.9011 | 15.8421 | 15.7821 | 15.7158 | 15.6432 | 15.5674 | 15.4674 | 15.3421 | 15.2168 | 15.0516 | 14.3684 | 13.6432 | 12.6842
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | PLESSEY TITCHFIELD | MINIMUM HEADROOM | SU 53390 06922 | YES | 0.45579 | 35.4474 | 35.0621 | 34.6842 | 34.3 | 33.9147 | 33.5316 | 33.2063 | 32.8568 | 32.5337 | 32.2347 | 30.6379 | 29.0705 | 1.4232 | 31.5663 | 31.1621 | 30.7653 | 30.3632 | 29.9611 | 29.5621 | 29.2579 | 28.8758 | 28.5232 | 28.1968 | 26.3821 | 24.5537 | 22.8695 | 32.8716 | 32.4558 | 32.0474 | 31.6358 | 31.2232 | 30.8158 | 30.5095 | 30.1358 | 29.7884 | 29.4684 | 27.7084 | 25.9484 | 24.2642
|  | PLESSEY TITCHFIELD | EE |  |  |  | 35.6179 | 35.3232 | 35.0221 | 34.7158 | 34.4063 | 34.0937 | 33.7926 | 33.5042 | 33.2832 | 33.0274 | 31.8021 | 30.5937 | 29.5305 | 31.7463 | 31.4379 | 31.1211 | 30.8021 | 30.4789 | 30.1537 | 29.8411 | 29.54 | 29.3516 | 29.0747 | 27.6979 | 26.2811 | 25.0137 | 33.0568 | 32.74 | 32.4147 | 32.0874 | 31.7568 | 31.4242 | 31.1042 | 30.7958 | 30.6011 | 30.3263 | 28.9811 | 27.6189 | 26.4063
|  | PLESSEY TITCHFIELD | HT |  |  |  | 35.4474 | 35.0621 | 34.6842 | 34.3 | 33.9147 | 33.5316 | 33.2063 | 32.8568 | 32.5337 | 32.2347 | 30.6379 | 29.0705 | 27.6453 | 31.5663 | 31.1621 | 30.7653 | 30.3632 | 29.9611 | 29.5621 | 29.2579 | 28.8758 | 28.5232 | 28.1968 | 26.3821 | 24.5537 | 22.8695 | 32.8716 | 32.4558 | 32.0474 | 31.6358 | 31.2232 | 30.8158 | 30.5095 | 30.1358 | 29.7884 | 29.4684 | 27.7084 | 25.9484 | 24.2642
|  | PLESSEY TITCHFIELD | HE |  |  |  | 35.8137 | 35.6621 | 35.4663 | 35.2611 | 35.0453 | 34.8221 | 34.6095 | 34.4021 | 34.1484 | 33.9758 | 33.1316 | 32.2832 | 1.4232 | 31.9516 | 31.7958 | 31.5916 | 31.3779 | 31.1547 | 30.9242 | 30.7032 | 30.4895 | 30.1863 | 30.0053 | 29.1074 | 28.0968 | 27.2063 | 33.2674 | 33.1095 | 32.9 | 32.6811 | 32.4537 | 32.2189 | 31.9937 | 31.7747 | 31.4653 | 31.2811 | 30.3505 | 29.3842 | 28.5358
|  | PLESSEY TITCHFIELD | CF |  |  |  | 35.8832 | 35.8211 | 35.7432 | 35.6295 | 35.5137 | 35.3947 | 35.2737 | 35.1537 | 35.0347 | 34.9147 | 34.3547 | 33.7874 | 33.2937 | 32.0211 | 31.9589 | 31.8789 | 31.7611 | 31.6389 | 31.5137 | 31.3874 | 31.2611 | 31.1368 | 31.0116 | 30.4232 | 29.8063 | 29.2126 | 33.3368 | 33.2747 | 33.1947 | 33.0726 | 32.9474 | 32.8189 | 32.6895 | 32.56 | 32.4316 | 32.3032 | 31.6979 | 31.0516 | 30.4821
MANNINGTON GSP | POOLE PS (HAMWORTHY) | POOLE | MINIMUM HEADROOM | SZ 01091 90595 | YES | 1.0632 | 23.0484 | 22.9368 | 22.4358 | 21.3926 | 20.3863 | 19.2379 | 18.0674 | 16.9168 | 16.4347 | 16.2021 | 15.1389 | 14.1316 | -1.7221 | 19.8242 | 19.2326 | 18.18 | 17.0105 | 15.8621 | 14.5347 | 13.1811 | 11.8495 | 11.3011 | 11.0463 | 9.8726 | 8.7484 | 7.6747 | 20.3116 | 20.1674 | 19.4611 | 18.2579 | 17.0979 | 15.7716 | 14.4211 | 13.0916 | 12.5432 | 12.2884 | 11.1168 | 9.9937 | 8.9221
|  | POOLE | EE |  |  |  | 23.0947 | 23.0095 | 22.9189 | 22.1558 | 21.3632 | 20.3642 | 19.3389 | 17.9295 | 16.5284 | 16.2905 | 15.4632 | 14.6884 | 13.9526 | 19.8737 | 19.4947 | 18.7211 | 17.8621 | 16.9747 | 15.8305 | 14.6432 | 13.0032 | 11.3726 | 11.1084 | 10.1968 | 9.3295 | 8.4979 | 20.3611 | 20.2526 | 20.0158 | 19.1326 | 18.2211 | 17.0653 | 15.88 | 14.2432 | 12.6147 | 12.3516 | 11.4411 | 10.5747 | 9.7442
|  | POOLE | HT |  |  |  | 23.0484 | 22.9368 | 22.4358 | 21.3926 | 20.3863 | 19.2379 | 18.0674 | 16.9168 | 16.4347 | 16.2021 | 15.1389 | 14.1316 | 13.1758 | 19.8242 | 19.2326 | 18.18 | 17.0105 | 15.8621 | 14.5347 | 13.1811 | 11.8495 | 11.3011 | 11.0463 | 9.8726 | 8.7484 | 7.6747 | 20.3116 | 20.1674 | 19.4611 | 18.2579 | 17.0979 | 15.7716 | 14.4211 | 13.0916 | 12.5432 | 12.2884 | 11.1168 | 9.9937 | 8.9221
|  | POOLE | HE |  |  |  | 23.1358 | 23.0674 | 22.9916 | 22.3589 | 21.5905 | 20.6042 | 19.6074 | 18.1747 | 16.9284 | 16.7863 | 16.1958 | 15.6642 | -1.7221 | 19.9179 | 19.6421 | 18.9084 | 18.0821 | 17.22 | 16.0926 | 14.9358 | 13.2663 | 11.8137 | 11.6589 | 11.0074 | 10.4084 | 9.8516 | 20.4063 | 20.3168 | 20.1989 | 19.3568 | 18.4695 | 17.3274 | 16.1726 | 14.5063 | 13.0558 | 12.9011 | 12.2505 | 11.6526 | 11.0958
|  | POOLE | CF |  |  |  | 23.16 | 23.1137 | 23.0653 | 23.0158 | 22.9642 | 22.9105 | 22.8568 | 22.8032 | 22.4811 | 21.8695 | 19.2905 | 18.8653 | 18.5389 | 19.9484 | 19.8926 | 19.7379 | 19.5263 | 19.3874 | 19.2316 | 19.0579 | 18.7326 | 18.2421 | 17.5537 | 14.5937 | 14.1147 | 13.7421 | 20.4368 | 20.3811 | 20.3211 | 20.2611 | 20.2032 | 20.1432 | 20.0821 | 20.0116 | 19.5274 | 18.8189 | 15.8305 | 15.3526 | 14.9811
LOVEDEAN GSP | WYMERING BSP | PORTCHESTER | MINIMUM HEADROOM | SU 62043 05575 | YES | 0.96632 | 33.6937 | 33.3063 | 32.8221 | 31.7684 | 30.6326 | 29.4232 | 28.2137 | 27.0663 | 25.9589 | 25.3726 | 22.2747 | 19.2368 | -3.1274 | 29.2789 | 28.2284 | 27.1579 | 26.0642 | 24.8284 | 23.4863 | 22.1463 | 20.8695 | 19.6337 | 19.0084 | 15.6305 | 12.2726 | 9.2242 | 30.5737 | 29.5053 | 28.4168 | 27.3053 | 26.1084 | 24.8137 | 23.4758 | 22.1968 | 20.96 | 20.3316 | 16.9368 | 13.5558 | 10.5032
|  | PORTCHESTER | EE |  |  |  | 33.8411 | 33.5368 | 33.2137 | 32.5989 | 31.7589 | 30.8074 | 29.88 | 28.8853 | 27.6589 | 26.7295 | 24.3042 | 21.8947 | 19.7874 | 29.5947 | 28.7084 | 27.7874 | 26.9242 | 26.0547 | 25.0242 | 24.0021 | 22.8979 | 21.52 | 20.4842 | 17.8674 | 15.2147 | 12.8453 | 30.8926 | 29.9916 | 29.0547 | 28.1768 | 27.2947 | 26.2926 | 25.3116 | 24.2211 | 22.8411 | 21.8011 | 19.1579 | 16.4716 | 14.0947
|  | PORTCHESTER | HT |  |  |  | 33.6937 | 33.3063 | 32.8221 | 31.7684 | 30.6326 | 29.4232 | 28.2137 | 27.0663 | 25.9589 | 25.3726 | 22.2747 | 19.2368 | 16.5147 | 29.2789 | 28.2284 | 27.1579 | 26.0642 | 24.8284 | 23.4863 | 22.1463 | 20.8695 | 19.6337 | 19.0084 | 15.6305 | 12.2726 | 9.2242 | 30.5737 | 29.5053 | 28.4168 | 27.3053 | 26.1084 | 24.8137 | 23.4758 | 22.1968 | 20.96 | 20.3316 | 16.9368 | 13.5558 | 10.5032
|  | PORTCHESTER | HE |  |  |  | 34.0463 | 33.8389 | 33.6116 | 33.3568 | 32.9126 | 32.1147 | 31.3505 | 30.4884 | 29.4347 | 28.7316 | 27.1789 | 25.5811 | -3.1274 | 30.0263 | 29.3442 | 28.6211 | 27.9411 | 27.2432 | 26.4168 | 25.5989 | 24.6326 | 23.4389 | 22.6537 | 20.9726 | 19.1811 | 17.5326 | 31.3316 | 30.6358 | 29.9 | 29.2095 | 28.5 | 27.6579 | 26.8505 | 25.9358 | 24.7653 | 23.9789 | 22.2874 | 20.4884 | 18.8326
|  | PORTCHESTER | CF |  |  |  | 34.1663 | 34.0495 | 33.9295 | 33.8032 | 33.6737 | 33.5368 | 33.3947 | 33.2579 | 33.1211 | 32.9863 | 30.7547 | 29.6547 | 28.6832 | 30.3253 | 29.9379 | 29.5495 | 29.2442 | 29.0147 | 28.7811 | 28.5389 | 28.2453 | 27.8958 | 27.3589 | 24.9263 | 23.6937 | 22.5884 | 31.6347 | 31.24 | 30.8442 | 30.5347 | 30.3032 | 30.0642 | 29.8189 | 29.5189 | 29.1642 | 28.6147 | 26.2137 | 25.0116 | 23.9032
CHICKERELL GSP | CHICKERELL BSP | PORTLAND | MINIMUM HEADROOM | SY 68307 73941 | YES | 0.57579 | 20.8674 | 20.6526 | 20.4358 | 20.2053 | 19.9653 | 19.6284 | 19.2274 | 18.8579 | 18.5063 | 18.18 | 15.2242 | 13.1326 | -6.4789 | 17.5547 | 17.0632 | 16.6021 | 16.0705 | 15.5347 | 14.8832 | 14.4558 | 14.0632 | 13.6853 | 13.3337 | 10.0021 | 7.6526 | 5.5905 | 18.32 | 17.8989 | 17.4558 | 16.9453 | 16.4305 | 15.8095 | 15.3947 | 15.0126 | 14.6484 | 14.3095 | 11.0032 | 8.6526 | 6.5895
|  | PORTLAND | EE |  |  |  | 20.9368 | 20.7611 | 20.5758 | 20.3789 | 20.1705 | 19.9537 | 19.7442 | 19.5021 | 19.1968 | 18.9137 | 16.2642 | 14.6168 | 13.2295 | 17.7316 | 17.3305 | 16.9484 | 16.4947 | 16.0316 | 15.4505 | 15.1021 | 14.7663 | 14.4411 | 14.1389 | 11.1432 | 9.2895 | 7.72 | 18.3958 | 18.1537 | 17.7863 | 17.3516 | 16.9074 | 16.3526 | 16.0126 | 15.6874 | 15.3716 | 15.0789 | 12.1453 | 10.2884 | 8.7168
|  | PORTLAND | HT |  |  |  | 20.8674 | 20.6526 | 20.4358 | 20.2053 | 19.9653 | 19.6284 | 19.2274 | 18.8579 | 18.5063 | 18.18 | 15.2242 | 13.1326 | 11.3053 | 17.5547 | 17.0632 | 16.6021 | 16.0705 | 15.5347 | 14.8832 | 14.4558 | 14.0632 | 13.6853 | 13.3337 | 10.0021 | 7.6526 | 5.5905 | 18.32 | 17.8989 | 17.4558 | 16.9453 | 16.4305 | 15.8095 | 15.3947 | 15.0126 | 14.6484 | 14.3095 | 11.0032 | 8.6526 | 6.5895
|  | PORTLAND | HE |  |  |  | 21.0432 | 20.9168 | 20.7768 | 20.6232 | 20.4568 | 20.2789 | 20.1095 | 19.9505 | 19.8011 | 19.6726 | 17.7937 | 16.5842 | -6.4789 | 17.9832 | 17.6989 | 17.4284 | 17.0811 | 16.7221 | 16.2347 | 15.9832 | 15.7442 | 15.5168 | 15.3147 | 12.8147 | 11.4421 | 10.3358 | 18.5116 | 18.3758 | 18.2274 | 17.9126 | 17.5674 | 17.1032 | 16.8568 | 16.6242 | 16.4021 | 16.2053 | 13.8179 | 12.4432 | 11.3368
|  | PORTLAND | CF |  |  |  | 21.1042 | 21.0274 | 20.9474 | 20.8653 | 20.7789 | 20.6905 | 20.6 | 20.5105 | 20.4221 | 20.3337 | 19.5189 | 18.6895 | 18.0611 | 18.1284 | 17.9516 | 17.7863 | 17.5905 | 17.3926 | 17.1474 | 16.9884 | 16.8295 | 16.6716 | 16.5137 | 14.7168 | 13.7758 | 13.0589 | 18.5779 | 18.4947 | 18.4095 | 18.32 | 18.2126 | 17.9789 | 17.8242 | 17.6716 | 17.5189 | 17.3663 | 15.6695 | 14.78 | 14.0611
LOVEDEAN GSP | PORTSMOUTH BSP | PORTSMOUTH | MINIMUM HEADROOM | SZ 63405 99685 | YES | 0.68421 | 42.6547 | 42.5453 | 42.4358 | 42.32 | 42.1947 | 42.0632 | 41.9295 | 41.8084 | 41.6958 | 41.5905 | 41.1326 | 40.7632 | 21.2137 | 38.5305 | 38.38 | 38.2305 | 38.0758 | 37.9126 | 37.7442 | 37.5747 | 37.4074 | 37.2305 | 37.0621 | 36.0905 | 34.8137 | 33.6063 | 39.1442 | 39.0095 | 38.8747 | 38.7337 | 38.5842 | 38.4295 | 38.2726 | 38.1295 | 37.9937 | 37.8663 | 37.18 | 35.9063 | 34.6821
|  | PORTSMOUTH | EE |  |  |  | 42.7084 | 42.6305 | 42.5474 | 42.46 | 42.3632 | 42.2611 | 42.1611 | 42.0611 | 41.9632 | 41.8747 | 41.5242 | 41.2611 | 41.0558 | 38.6 | 38.4947 | 38.3811 | 38.2642 | 38.1379 | 38.0074 | 37.88 | 37.7516 | 37.6274 | 37.5116 | 36.9316 | 36.0011 | 35.0821 | 39.2084 | 39.1137 | 39.0105 | 38.9042 | 38.7895 | 38.6695 | 38.5516 | 38.4337 | 38.3189 | 38.2126 | 37.7779 | 37.0947 | 36.1726
|  | PORTSMOUTH | HT |  |  |  | 42.6547 | 42.5453 | 42.4358 | 42.32 | 42.1947 | 42.0632 | 41.9295 | 41.8084 | 41.6958 | 41.5905 | 41.1326 | 40.7632 | 39.7674 | 38.5305 | 38.38 | 38.2305 | 38.0758 | 37.9126 | 37.7442 | 37.5747 | 37.4074 | 37.2305 | 37.0621 | 36.0905 | 34.8137 | 33.6063 | 39.1442 | 39.0095 | 38.8747 | 38.7337 | 38.5842 | 38.4295 | 38.2726 | 38.1295 | 37.9937 | 37.8663 | 37.18 | 35.9063 | 34.6821
|  | PORTSMOUTH | HE |  |  |  | 42.7358 | 42.6674 | 42.5916 | 42.5084 | 42.4179 | 42.3221 | 42.2305 | 42.1442 | 42.0642 | 41.9947 | 41.7453 | 43.9558 | 21.2137 | 38.6274 | 38.5589 | 38.4779 | 38.3779 | 38.2695 | 38.1579 | 38.0495 | 37.9463 | 37.8505 | 37.7663 | 37.4421 | 38.9211 | 38.1432 | 39.2358 | 39.1674 | 39.0884 | 38.9947 | 38.8926 | 38.7863 | 38.6842 | 38.5874 | 38.4979 | 38.4189 | 38.1221 | 40.5589 | 40.2842
|  | PORTSMOUTH | CF |  |  |  | 42.7537 | 42.7053 | 42.6537 | 42.6011 | 42.5463 | 42.4905 | 42.4326 | 42.3758 | 42.32 | 42.2632 | 42.0137 | 41.8842 | 41.8116 | 38.6453 | 38.5968 | 38.5453 | 38.4926 | 38.4305 | 38.3621 | 38.2916 | 38.2221 | 38.1547 | 38.0853 | 37.7758 | 37.5874 | 37.3926 | 39.2537 | 39.2053 | 39.1537 | 39.1011 | 39.0421 | 38.9779 | 38.9116 | 38.8474 | 38.7842 | 38.7189 | 38.4316 | 38.2653 | 38.1253
MELKSHAM GSP | ANDOVER BSP | PORTWAY | MINIMUM HEADROOM | SU 34402 46001 | YES | 5.4821 | 26.0421 | 25.88 | 25.7158 | 25.5421 | 25.3653 | 25.1853 | 25.0042 | 24.8442 | 20.5326 | 19.4316 | 18.68 | 17.9011 | -12.0337 | 24.1368 | 23.8916 | 23.6495 | 23.2758 | 23.0042 | 22.7347 | 22.4674 | 22.2232 | 19.4779 | 18.2042 | 17.4074 | 16.5547 | 16.1832 | 24.5 | 24.3095 | 24.12 | 23.92 | 23.7179 | 23.5137 | 23.3105 | 23.1284 | 19.5905 | 18.3189 | 17.5221 | 16.6705 | 16.2989
|  | PORTWAY | EE |  |  |  | 26.1074 | 25.98 | 25.8463 | 25.7042 | 25.5579 | 25.4084 | 25.2632 | 25.1263 | 24.9916 | 24.8737 | 21.3832 | 20.6989 | 20.2421 | 24.2453 | 24.0558 | 23.8621 | 23.6526 | 23.3432 | 23.1211 | 22.9074 | 22.7032 | 22.5 | 22.3189 | 20.6884 | 19.8758 | 19.3779 | 24.5789 | 24.4316 | 24.2779 | 24.1137 | 23.9484 | 23.78 | 23.6168 | 23.4621 | 23.3095 | 23.1747 | 20.6316 | 19.8737 | 19.3705
|  | PORTWAY | HT |  |  |  | 26.0421 | 25.88 | 25.7158 | 25.5421 | 25.3653 | 25.1853 | 25.0042 | 24.8442 | 20.5326 | 19.4316 | 18.68 | 17.9011 | 17.5421 | 24.1368 | 23.8916 | 23.6495 | 23.2758 | 23.0042 | 22.7347 | 22.4674 | 22.2232 | 19.4779 | 18.2042 | 17.4074 | 16.5547 | 16.1832 | 24.5 | 24.3095 | 24.12 | 23.92 | 23.7179 | 23.5137 | 23.3105 | 23.1284 | 19.5905 | 18.3189 | 17.5221 | 16.6705 | 16.2989
|  | PORTWAY | HE |  |  |  | 26.1968 | 26.1116 | 26.0189 | 25.9147 | 25.8053 | 25.6895 | 25.58 | 25.4747 | 25.3768 | 25.2916 | 22 | 21.5074 | -12.0337 | 24.3916 | 24.2705 | 24.1432 | 23.9947 | 23.8526 | 23.7011 | 23.5568 | 23.42 | 23.2853 | 23.0611 | 21.3137 | 20.7168 | 20.36 | 24.6874 | 24.5905 | 24.4863 | 24.3674 | 24.2474 | 24.12 | 23.9989 | 23.8832 | 23.7726 | 23.6779 | 21.2716 | 20.7189 | 20.3579
|  | PORTWAY | CF |  |  |  | 26.2474 | 26.1968 | 26.1474 | 26.0916 | 26.0358 | 25.9747 | 25.9147 | 25.8589 | 25.8032 | 25.7474 | 25.4937 | 25.3274 | 25.2042 | 24.4653 | 24.3916 | 24.3168 | 24.2274 | 24.1347 | 24.0305 | 23.9316 | 23.8484 | 23.7684 | 23.6884 | 23.1663 | 22.6937 | 22.2368 | 24.7453 | 24.6874 | 24.6295 | 24.5632 | 24.4947 | 24.42 | 24.3474 | 24.2811 | 24.2179 | 24.1547 | 23.8547 | 23.6084 | 23.3979
IVER 132KV | LONGFORD | POYLE | MINIMUM HEADROOM | TQ 03425 75555 | YES | 0.98421 | 35.2158 | 35.0684 | 34.9179 | 34.7579 | 34.5926 | 34.4263 | 34.2526 | 34.1011 | 33.9632 | 33.8347 | 33.3126 | 34.5516 | -9.8758 | 30.8242 | 30.6211 | 30.3632 | 30.0979 | 29.7105 | 29.4347 | 29.1537 | 28.8811 | 28.6116 | 27.7684 | 26.4274 | 29.0853 | 28.7274 | 31.5526 | 31.4053 | 31.2547 | 31.0947 | 30.8526 | 30.5779 | 30.2958 | 30.0242 | 29.7547 | 28.9105 | 27.5695 | 30.2274 | 29.8695
|  | POYLE | EE |  |  |  | 35.2758 | 35.1589 | 35.0368 | 34.9063 | 34.7695 | 34.6274 | 34.4905 | 34.3611 | 34.2326 | 34.1211 | 33.7105 | 67.1116 | 66.7958 | 30.8863 | 30.7663 | 30.5874 | 30.3768 | 30.0821 | 29.8547 | 29.6347 | 29.4084 | 29.1716 | 28.3674 | 27.2937 | 60.0516 | 59.2242 | 31.6126 | 31.4958 | 31.3737 | 31.2432 | 31.1063 | 30.9642 | 30.7779 | 30.5505 | 30.3147 | 29.5105 | 28.4358 | 61.1937 | 60.3663
|  | POYLE | HT |  |  |  | 35.2158 | 35.0684 | 34.9179 | 34.7579 | 34.5926 | 34.4263 | 34.2526 | 34.1011 | 33.9632 | 33.8347 | 33.3126 | 66.4884 | 65.5095 | 30.8242 | 30.6211 | 30.3632 | 30.0979 | 29.7105 | 29.4347 | 29.1537 | 28.8811 | 28.6116 | 27.7684 | 26.4274 | 58.9158 | 57.7979 | 31.5526 | 31.4053 | 31.2547 | 31.0947 | 30.8526 | 30.5779 | 30.2958 | 30.0242 | 29.7547 | 28.9105 | 27.5695 | 60.0579 | 58.94
|  | POYLE | HE |  |  |  | 35.3484 | 35.2663 | 35.1768 | 35.0779 | 34.9695 | 34.8558 | 34.7474 | 34.6442 | 34.5484 | 34.4653 | 34.1874 | 67.7042 | -9.8758 | 30.9589 | 30.8768 | 30.7874 | 30.6863 | 30.5484 | 30.3853 | 30.2305 | 30.0642 | 29.9032 | 29.1684 | 28.4232 | 61.4821 | 60.9484 | 31.6853 | 31.6032 | 31.5137 | 31.4147 | 31.3063 | 31.1926 | 31.0842 | 30.9811 | 30.8853 | 30.3105 | 29.5653 | 62.6242 | 62.0905
|  | POYLE | CF |  |  |  | 35.3926 | 35.3442 | 35.2947 | 35.2432 | 35.1905 | 35.1347 | 35.0779 | 35.0232 | 34.9684 | 34.9137 | 34.6695 | 34.5516 | 34.4832 | 31.0032 | 30.9547 | 30.9053 | 30.8537 | 30.8 | 30.7432 | 30.6853 | 30.6063 | 30.5189 | 30.0832 | 29.5074 | 29.0853 | 28.7274 | 31.7295 | 31.6811 | 31.6316 | 31.58 | 31.5274 | 31.4716 | 31.4147 | 31.36 | 31.3053 | 31.2263 | 30.6495 | 30.2274 | 29.8695
MINETY GSP | STRATTON (2 X 90) | PRESSED STEEL SWINDON | MINIMUM HEADROOM | SU 16963 86368 | YES | 0.24842 | 44.9253 | 44.7158 | 93.5042 | 93.2789 | 93.0474 | 92.7926 | 92.1716 | 91.3253 | 90.5095 | 89.7126 | 86.7663 | 85.0621 | 62.8589 | 41.8642 | 41.4589 | 90.0579 | 89.6516 | 89.2453 | 88.5463 | 87.8463 | 86.8884 | 85.9611 | 85.0547 | 81.7116 | 79.7979 | 77.9789 | 42.4968 | 42.1063 | 90.72 | 90.3263 | 89.9337 | 89.2695 | 88.6032 | 87.7011 | 86.8295 | 85.9305 | 82.5937 | 80.6821 | 78.8653
|  | PRESSED STEEL SWINDON | EE |  |  |  | 45.0105 | 44.8484 | 93.6768 | 93.4947 | 93.3042 | 93.1084 | 92.8137 | 92.0305 | 91.2547 | 90.5053 | 87.9158 | 86.5979 | 85.3632 | 42.0442 | 41.7389 | 90.4232 | 90.1011 | 89.7737 | 89.1505 | 88.54 | 87.6505 | 86.7674 | 85.9126 | 82.9621 | 81.4768 | 80.0705 | 42.6758 | 42.3758 | 91.0705 | 90.7579 | 90.4411 | 89.8505 | 89.2705 | 88.4358 | 87.6053 | 86.7884 | 83.8421 | 82.3589 | 80.9558
|  | PRESSED STEEL SWINDON | HT |  |  |  | 44.9253 | 44.7158 | 93.5042 | 93.2789 | 93.0474 | 92.7926 | 92.1716 | 91.3253 | 90.5095 | 89.7126 | 86.7663 | 85.0621 | 83.4537 | 41.8642 | 41.4589 | 90.0579 | 89.6516 | 89.2453 | 88.5463 | 87.8463 | 86.8884 | 85.9611 | 85.0547 | 81.7116 | 79.7979 | 77.9789 | 42.4968 | 42.1063 | 90.72 | 90.3263 | 89.9337 | 89.2695 | 88.6032 | 87.7011 | 86.8295 | 85.9305 | 82.5937 | 80.6821 | 78.8653
|  | PRESSED STEEL SWINDON | HE |  |  |  | 45.1232 | 45.0147 | 93.8947 | 93.7621 | 93.62 | 93.4684 | 93.3232 | 92.9095 | 92.2179 | 91.5495 | 89.3432 | 88.38 | 62.8589 | 42.2726 | 42.0895 | 90.8968 | 90.6832 | 90.46 | 89.9316 | 89.4116 | 88.6063 | 87.8137 | 87.0474 | 84.5158 | 83.4211 | 82.3821 | 42.9116 | 42.7242 | 91.5263 | 91.3168 | 91.1 | 90.5989 | 90.1084 | 89.3526 | 88.6105 | 87.8926 | 85.3947 | 84.3011 | 83.2642
|  | PRESSED STEEL SWINDON | CF |  |  |  | 45.1884 | 45.1284 | 94.0663 | 94.0011 | 93.9347 | 93.8653 | 93.7947 | 93.7263 | 93.6547 | 93.3863 | 91.9 | 91.3168 | 90.7347 | 42.3884 | 42.2789 | 91.1653 | 91.0484 | 90.9295 | 90.6853 | 90.4242 | 90.0105 | 89.5663 | 89.0958 | 87.4 | 86.7411 | 86.0716 | 43.0316 | 42.9179 | 91.8011 | 91.6811 | 91.5589 | 91.3263 | 91.08 | 90.6916 | 90.2768 | 89.8358 | 88.2442 | 87.6168 | 86.9484
BRAMLEY (FLEE) | FERNHURST | PRESTON CANDOVER | MINIMUM HEADROOM | SU 60879 41131 | YES | 0.12211 | 16.5463 | 16.4305 | 16.1463 | 15.7632 | 15.6105 | 15.4326 | 15.2463 | 15.0674 | 14.8926 | 14.7221 | 13.8558 | 12.9842 | 2.6958 | 14.4063 | 14.2832 | 13.9579 | 13.5189 | 13.3579 | 13.1779 | 12.9905 | 12.8105 | 12.6358 | 12.4653 | 11.6116 | 10.76 | 10.0453 | 14.5305 | 14.4084 | 14.0821 | 13.6453 | 13.4821 | 13.2947 | 13.0979 | 12.9084 | 12.7221 | 12.5411 | 11.62 | 10.6884 | 9.9432
|  | PRESTON CANDOVER | EE |  |  |  | 16.5895 | 16.5095 | 16.2779 | 15.9211 | 15.7979 | 15.6432 | 15.4811 | 15.32 | 15.1558 | 14.9821 | 14.1032 | 13.2653 | 12.7011 | 14.4516 | 14.3674 | 14.0968 | 13.6926 | 13.5611 | 13.4074 | 13.2495 | 13.0947 | 12.9368 | 12.7705 | 11.9495 | 11.1905 | 10.6084 | 14.5768 | 14.4926 | 14.2221 | 13.8168 | 13.6853 | 13.5232 | 13.3537 | 13.1842 | 13.0126 | 12.8295 | 11.9032 | 11.0221 | 10.4021
|  | PRESTON CANDOVER | HT |  |  |  | 16.5463 | 16.4305 | 16.1463 | 15.7632 | 15.6105 | 15.4326 | 15.2463 | 15.0674 | 14.8926 | 14.7221 | 13.8558 | 12.9842 | 12.3063 | 14.4063 | 14.2832 | 13.9579 | 13.5189 | 13.3579 | 13.1779 | 12.9905 | 12.8105 | 12.6358 | 12.4653 | 11.6116 | 10.76 | 10.0453 | 14.5305 | 14.4084 | 14.0821 | 13.6453 | 13.4821 | 13.2947 | 13.0979 | 12.9084 | 12.7221 | 12.5411 | 11.62 | 10.6884 | 9.9432
|  | PRESTON CANDOVER | HE |  |  |  | 16.6347 | 16.5926 | 16.4547 | 16.14 | 16.0568 | 15.9442 | 15.84 | 15.74 | 15.64 | 15.54 | 14.8884 | 14.6253 | 2.6958 | 14.4968 | 14.4547 | 14.2895 | 13.9284 | 13.8411 | 13.7305 | 13.6253 | 13.5284 | 13.4305 | 13.3305 | 12.6642 | 12.4253 | 12.1316 | 14.6221 | 14.58 | 14.4147 | 14.0537 | 13.9663 | 13.8495 | 13.7389 | 13.6347 | 13.5305 | 13.4242 | 12.7137 | 12.4411 | 12.1168
|  | PRESTON CANDOVER | CF |  |  |  | 16.6611 | 16.6379 | 16.6147 | 16.5874 | 16.5558 | 16.5084 | 16.3558 | 16.2653 | 16.2084 | 16.1484 | 15.8453 | 15.5021 | 15.3526 | 14.5232 | 14.5 | 14.4768 | 14.4484 | 14.4158 | 14.3695 | 14.1979 | 14.0979 | 14.04 | 13.9768 | 13.6621 | 13.2968 | 13.1579 | 14.6484 | 14.6253 | 14.6021 | 14.5726 | 14.54 | 14.4916 | 14.3168 | 14.2137 | 14.1526 | 14.0874 | 13.7579 | 13.3768 | 13.2189
CHICKERELL GSP | CHICKERELL BSP | PUDDLETOWN | MINIMUM HEADROOM | SY 74226 95039 | YES | 0 | 6.8874 | 6.8379 | 6.7695 | 6.6758 | 6.3916 | 5.8453 | 5.3074 | 4.6389 | 4.5168 | 4.3884 | 2.8779 | 0.85474 | 0.28842 | 6.1968 | 6.1105 | 6.0126 | 5.9158 | 5.6095 | 5.0137 | 4.4158 | 3.6663 | 3.5632 | 3.4568 | 1.9421 | -0.14316 | -0.68526 | 6.3474 | 6.2979 | 6.2021 | 6.1053 | 5.7884 | 5.1632 | 4.5505 | 3.7842 | 3.6611 | 3.5337 | 1.8811 | -0.36421 | -0.96947
|  | PUDDLETOWN | EE |  |  |  | 6.9074 | 6.8674 | 6.8211 | 6.7684 | 6.6863 | 6.5463 | 6.3947 | 6.2347 | 6.0674 | 5.8958 | 4.3579 | 2.0968 | 0.94632 | 6.2337 | 6.1674 | 6.0947 | 6.0147 | 5.9305 | 5.7979 | 5.6579 | 5.5116 | 5.3589 | 5.2053 | 3.7505 | 1.5274 | 0.30316 | 6.3674 | 6.3274 | 6.2821 | 6.2021 | 6.1179 | 5.9726 | 5.8147 | 5.6484 | 5.4758 | 5.2979 | 3.6537 | 1.1653 | -0.12632
|  | PUDDLETOWN | HT |  |  |  | 6.8874 | 6.8379 | 6.7695 | 6.6758 | 6.3916 | 5.8453 | 5.3074 | 4.6389 | 4.5168 | 4.3884 | 2.8779 | 0.85474 | 0.28842 | 6.1968 | 6.1105 | 6.0126 | 5.9158 | 5.6095 | 5.0137 | 4.4158 | 3.6663 | 3.5632 | 3.4568 | 1.9421 | -0.14316 | -0.68526 | 6.3474 | 6.2979 | 6.2021 | 6.1053 | 5.7884 | 5.1632 | 4.5505 | 3.7842 | 3.6611 | 3.5337 | 1.8811 | -0.36421 | -0.96947
|  | PUDDLETOWN | HE |  |  |  | 6.9347 | 6.9084 | 6.8789 | 6.8463 | 6.8116 | 6.7326 | 6.6611 | 6.5726 | 6.4842 | 6.3958 | 5.6421 | 4.3074 | 2.0547 | 6.2853 | 6.2421 | 6.1968 | 6.1516 | 6.1021 | 6.0084 | 5.9242 | 5.8389 | 5.7568 | 5.6768 | 4.9432 | 3.5316 | 2.5116 | 6.3947 | 6.3684 | 6.3389 | 6.3063 | 6.2726 | 6.1874 | 6.0958 | 6.0011 | 5.9095 | 5.8189 | 5.0116 | 3.4958 | 2.4211
|  | PUDDLETOWN | CF |  |  |  | 6.9505 | 6.9358 | 6.9211 | 6.9053 | 6.8884 | 6.8516 | 6.8158 | 6.78 | 6.7453 | 6.7147 | 6.4474 | 5.7147 | 5.02 | 6.3063 | 6.2853 | 6.26 | 6.2347 | 6.2063 | 6.16 | 6.1179 | 6.0737 | 6.0274 | 5.9863 | 5.7179 | 4.9537 | 4.2105 | 6.4105 | 6.3958 | 6.3811 | 6.3653 | 6.3484 | 6.3137 | 6.28 | 6.2453 | 6.2 | 6.1558 | 5.8663 | 5.0389 | 4.2526
AXMINSTER | YEOVIL BSP | PULHAM | MINIMUM HEADROOM | ST 71579 09451 | YES | 0.094737 | 8.8863 | 8.7368 | 8.5874 | 8.4358 | 7.4842 | 6.1726 | 4.88 | 3.2316 | 3.1253 | 3.0232 | 0.31158 | -3.6642 | -4.5232 | 7.7905 | 7.6284 | 7.4674 | 7.3042 | 6.1758 | 4.6347 | 3.1358 | 1.2189 | 1.1189 | 1.0232 | -2.0421 | -6.5968 | -7.5432 | 8.0253 | 7.8674 | 7.7116 | 7.5537 | 6.4642 | 4.9158 | 3.4116 | 1.4874 | 1.3789 | 1.2758 | -1.84 | -6.4558 | -7.4263
|  | PULHAM | EE |  |  |  | 8.9547 | 8.8389 | 8.7211 | 8.6 | 8.4779 | 8.3347 | 8.1853 | 8.0411 | 7.8958 | 7.7558 | 5.1453 | 1.0705 | -1.4 | 7.8663 | 7.7411 | 7.6137 | 7.4842 | 7.3547 | 7.2095 | 7.06 | 6.9179 | 6.7758 | 6.64 | 3.6779 | -0.97474 | -3.8295 | 8.0979 | 7.9768 | 7.8526 | 7.7263 | 7.5989 | 7.4516 | 7.2979 | 7.1484 | 6.9989 | 6.8558 | 3.8505 | -0.88526 | -3.7663
|  | PULHAM | HT |  |  |  | 8.8863 | 8.7368 | 8.5874 | 8.4358 | 7.4842 | 6.1726 | 4.88 | 3.2316 | 3.1253 | 3.0232 | 0.31158 | -3.6642 | -4.5232 | 7.7905 | 7.6284 | 7.4674 | 7.3042 | 6.1758 | 4.6347 | 3.1358 | 1.2189 | 1.1189 | 1.0232 | -2.0421 | -6.5968 | -7.5432 | 8.0253 | 7.8674 | 7.7116 | 7.5537 | 6.4642 | 4.9158 | 3.4116 | 1.4874 | 1.3789 | 1.2758 | -1.84 | -6.4558 | -7.4263
|  | PULHAM | HE |  |  |  | 9.0463 | 8.9768 | 8.9 | 8.8221 | 8.7411 | 8.6379 | 8.5421 | 8.4505 | 8.36 | 8.28 | 6.8305 | 3.7758 | 1.1442 | 7.9674 | 7.8916 | 7.8095 | 7.7263 | 7.64 | 7.5368 | 7.4421 | 7.3484 | 7.2611 | 7.1821 | 5.5221 | 1.9474 | -0.46632 | 8.1947 | 8.1211 | 8.0421 | 7.96 | 7.8768 | 7.7716 | 7.6726 | 7.5779 | 7.4853 | 7.4042 | 5.76 | 2.1611 | -0.27368
|  | PULHAM | CF |  |  |  | 9.0958 | 9.0547 | 9.0116 | 8.9684 | 8.9253 | 8.8705 | 8.8179 | 8.7653 | 8.7126 | 8.6632 | 8.0716 | 6.4084 | 4.8589 | 8.02 | 7.9768 | 7.9284 | 7.8821 | 7.8358 | 7.7789 | 7.7242 | 7.6705 | 7.6158 | 7.5642 | 6.8947 | 4.9274 | 3.1263 | 8.2463 | 8.2032 | 8.1568 | 8.1126 | 8.0674 | 8.0105 | 7.9547 | 7.9011 | 7.8463 | 7.7947 | 7.1516 | 5.1842 | 3.3684
LOVEDEAN GSP | FORT WIDLEY | PURBROOK | MINIMUM HEADROOM | SU 67047 07819 | YES | 0 | 16.8189 | 16.6347 | 16.4484 | 16.0579 | 15.3968 | 14.6411 | 13.9568 | 13.3337 | 12.7316 | 12.0989 | 9.5074 | 7.8695 | 1.0147 | 14.9705 | 14.4884 | 13.9674 | 13.3568 | 12.6021 | 11.7495 | 10.9874 | 10.2884 | 9.6147 | 8.9011 | 5.9926 | 4.1863 | 1.9842 | 15.4042 | 14.9442 | 14.4474 | 13.86 | 13.1053 | 12.2516 | 11.4853 | 10.7832 | 10.1063 | 9.3895 | 6.4579 | 4.6253 | 2.4137
|  | PURBROOK | EE |  |  |  | 16.8905 | 16.7474 | 16.5937 | 16.4337 | 16.1179 | 15.5221 | 14.9737 | 14.4358 | 13.8295 | 13.1684 | 10.6347 | 9.3495 | 7.8032 | 15.1305 | 14.8179 | 14.44 | 14.0063 | 13.4295 | 12.7463 | 12.1347 | 11.5347 | 10.8537 | 10.1063 | 7.2558 | 5.8568 | 4.0958 | 15.4937 | 15.2579 | 14.8958 | 14.4811 | 13.9326 | 13.2463 | 12.6305 | 12.0274 | 11.3421 | 10.5905 | 7.7095 | 6.2747 | 4.5011
|  | PURBROOK | HT |  |  |  | 16.8189 | 16.6347 | 16.4484 | 16.0579 | 15.3968 | 14.6411 | 13.9568 | 13.3337 | 12.7316 | 12.0989 | 9.5074 | 7.8695 | 5.9337 | 14.9705 | 14.4884 | 13.9674 | 13.3568 | 12.6021 | 11.7495 | 10.9874 | 10.2884 | 9.6147 | 8.9011 | 5.9926 | 4.1863 | 1.9842 | 15.4042 | 14.9442 | 14.4474 | 13.86 | 13.1053 | 12.2516 | 11.4853 | 10.7832 | 10.1063 | 9.3895 | 6.4579 | 4.6253 | 2.4137
|  | PURBROOK | HE |  |  |  | 16.9874 | 16.8895 | 16.7821 | 16.6621 | 16.5347 | 16.1305 | 15.6737 | 15.2095 | 14.7011 | 14.1547 | 12.0116 | 11.1589 | 1.0147 | 15.3368 | 15.1316 | 14.8474 | 14.4958 | 14.0116 | 13.4116 | 12.8926 | 12.3716 | 11.7968 | 11.1716 | 8.7242 | 7.7695 | 6.3516 | 15.5968 | 15.4926 | 15.2874 | 14.9526 | 14.4947 | 13.9137 | 13.3926 | 12.8695 | 12.2926 | 11.6653 | 9.2053 | 8.24 | 6.8137
|  | PURBROOK | CF |  |  |  | 17.0442 | 16.9895 | 16.9326 | 16.8726 | 16.8116 | 16.7442 | 16.6779 | 16.6095 | 16.5442 | 16.4789 | 14.2221 | 13.6442 | 12.8884 | 15.4011 | 15.3432 | 15.2832 | 15.1832 | 15.0168 | 14.8347 | 14.66 | 14.4547 | 14.2474 | 13.9842 | 11.1989 | 10.5505 | 9.6832 | 15.6611 | 15.6042 | 15.5442 | 15.48 | 15.4126 | 15.2726 | 15.1042 | 14.9095 | 14.7116 | 14.4611 | 11.6937 | 11.04 | 10.1653
BRAMLEY (FLEE) | PYESTOCK BSP | PYESTOCK | MINIMUM HEADROOM | SU 82940 54553 | YES | 0 | 25.5274 | 25.5211 | 25.5168 | 25.5137 | 25.5105 | 25.4937 | 25.4758 | 25.4547 | 25.4547 | 25.4547 | 25.4232 | 25.3737 | 21.1821 | 24.4989 | 24.4958 | 24.4926 | 24.4916 | 24.4895 | 24.4789 | 24.4695 | 24.4568 | 24.4568 | 24.4568 | 24.4389 | 24.4105 | 24.4053 | 24.7063 | 24.6989 | 24.6947 | 24.6905 | 24.6863 | 24.6663 | 24.6463 | 24.6221 | 24.6221 | 24.6221 | 24.5842 | 24.5263 | 24.5158
|  | PYESTOCK | EE |  |  |  | 25.5274 | 25.5221 | 25.5189 | 25.5147 | 25.5116 | 25.5105 | 25.5095 | 25.5084 | 25.5084 | 25.5074 | 25.4905 | 25.44 | 25.4074 | 24.4989 | 24.4958 | 24.4937 | 24.4916 | 24.4895 | 24.4895 | 24.4884 | 24.4884 | 24.4874 | 24.4874 | 24.4779 | 24.4484 | 24.4295 | 24.7063 | 24.7 | 24.6958 | 24.6916 | 24.6884 | 24.6863 | 24.6853 | 24.6842 | 24.6832 | 24.6832 | 24.6621 | 24.6032 | 24.5653
|  | PYESTOCK | HT |  |  |  | 25.5274 | 25.5211 | 25.5168 | 25.5137 | 25.5105 | 25.4937 | 25.4758 | 25.4547 | 25.4547 | 25.4547 | 25.4232 | 25.3737 | 25.3653 | 24.4989 | 24.4958 | 24.4926 | 24.4916 | 24.4895 | 24.4789 | 24.4695 | 24.4568 | 24.4568 | 24.4568 | 24.4389 | 24.4105 | 24.4053 | 24.7063 | 24.6989 | 24.6947 | 24.6905 | 24.6863 | 24.6663 | 24.6463 | 24.6221 | 24.6221 | 24.6221 | 24.5842 | 24.5263 | 24.5158
|  | PYESTOCK | HE |  |  |  | 25.5274 | 25.5232 | 25.52 | 25.5168 | 25.5147 | 25.5126 | 25.5126 | 25.5116 | 25.5116 | 25.5116 | 25.5063 | 25.4653 | 21.1821 | 24.4989 | 24.4958 | 24.4947 | 24.4926 | 24.4916 | 24.4905 | 24.4905 | 24.4895 | 24.4895 | 24.4895 | 24.4863 | 24.4632 | 24.4474 | 24.7063 | 24.7011 | 24.6979 | 24.6947 | 24.6916 | 24.6895 | 24.6895 | 24.6884 | 24.6884 | 24.6884 | 24.6821 | 24.6337 | 24.6011
|  | PYESTOCK | CF |  |  |  | 25.5274 | 25.5263 | 25.5263 | 25.5253 | 25.5242 | 25.5232 | 25.5221 | 25.5221 | 25.52 | 25.52 | 25.5168 | 25.4958 | 25.4758 | 24.4989 | 24.4979 | 24.4979 | 24.4979 | 24.4968 | 24.4958 | 24.4958 | 24.4958 | 24.4947 | 24.4947 | 24.4926 | 24.4811 | 24.4684 | 24.7063 | 24.7042 | 24.7042 | 24.7032 | 24.7032 | 24.7011 | 24.7 | 24.7 | 24.6979 | 24.6968 | 24.6937 | 24.6695 | 24.6453
MINETY GSP | TOOTHILL BSP | QUARRY ROAD | MINIMUM HEADROOM | SU 15334 83380 | YES | 0 | 24.4432 | 24.2011 | 23.9579 | 23.6989 | 23.4095 | 23.0463 | 22.1347 | 21.4895 | 20.8716 | 20.5053 | 18.5642 | 15.6758 | -4.0211 | 19.2316 | 18.8158 | 18.3337 | 17.7526 | 17.1326 | 16.2484 | 15.3611 | 14.7326 | 14.1305 | 13.7705 | 11.8874 | 8.8168 | 5.5989 | 21.2158 | 20.9589 | 20.6947 | 20.0368 | 19.3232 | 18.2337 | 17.1421 | 16.3842 | 15.6547 | 15.2442 | 13.0126 | 9.7211 | 6.5021
|  | QUARRY ROAD | EE |  |  |  | 24.5347 | 24.3453 | 24.1453 | 23.9316 | 23.7074 | 23.4484 | 23.1768 | 22.4821 | 21.76 | 21.2916 | 19.8284 | 17.58 | 15.3411 | 19.4147 | 19.0916 | 18.7232 | 18.2937 | 17.8084 | 17.1137 | 16.42 | 15.7021 | 15.0011 | 14.5442 | 13.1137 | 10.9 | 8.34 | 21.3147 | 21.1137 | 20.9 | 20.6526 | 20.1042 | 19.2821 | 18.4305 | 17.5421 | 16.6747 | 16.1263 | 14.4421 | 11.8242 | 9.2442
|  | QUARRY ROAD | HT |  |  |  | 24.4432 | 24.2011 | 23.9579 | 23.6989 | 23.4095 | 23.0463 | 22.1347 | 21.4895 | 20.8716 | 20.5053 | 18.5642 | 15.6758 | 12.8663 | 19.2316 | 18.8158 | 18.3337 | 17.7526 | 17.1326 | 16.2484 | 15.3611 | 14.7326 | 14.1305 | 13.7705 | 11.8874 | 8.8168 | 5.5989 | 21.2158 | 20.9589 | 20.6947 | 20.0368 | 19.3232 | 18.2337 | 17.1421 | 16.3842 | 15.6547 | 15.2442 | 13.0126 | 9.7211 | 6.5021
|  | QUARRY ROAD | HE |  |  |  | 24.6526 | 24.5179 | 24.3684 | 24.2042 | 24.0263 | 23.8379 | 23.6221 | 23.3663 | 22.7484 | 22.4137 | 21.3989 | 19.6758 | -4.0211 | 19.6484 | 19.4368 | 19.1695 | 18.8379 | 18.4474 | 17.8326 | 17.22 | 16.5684 | 15.9684 | 15.6421 | 14.6495 | 12.9979 | 11.1211 | 21.4432 | 21.3011 | 21.1421 | 20.9632 | 20.7674 | 20.1032 | 19.3621 | 18.5484 | 17.8 | 17.4095 | 16.24 | 14.1242 | 12.0347
|  | QUARRY ROAD | CF |  |  |  | 24.7189 | 24.6368 | 24.5526 | 24.4642 | 24.3726 | 24.2789 | 24.1821 | 24.0874 | 23.9937 | 23.9 | 23.3516 | 22.3821 | 21.3537 | 19.76 | 19.6211 | 19.48 | 19.3337 | 19.1842 | 19.0284 | 18.8705 | 18.6642 | 18.3495 | 18.0179 | 16.5537 | 15.6158 | 14.6242 | 21.5126 | 21.4263 | 21.3368 | 21.2432 | 21.1474 | 21.0484 | 20.9463 | 20.8421 | 20.7063 | 20.3179 | 18.5305 | 17.3453 | 16.0579
BRAMLEY (FLEE) | CAMBERLEY RESERVE | QUEENSMEAD | MINIMUM HEADROOM | SU 87062 55683 | YES | 0 | 12.1242 | 11.9874 | 11.8495 | 11.7032 | 11.5526 | 11.3968 | 11.24 | 11.1021 | 10.9768 | 10.8621 | 9.4116 | 8.5379 | -15.0621 | 10.4337 | 10.0811 | 9.8137 | 9.1326 | 8.8653 | 8.5695 | 8.3053 | 8.0684 | 7.8474 | 7.64 | 5.9768 | 4.9937 | 4.1042 | 10.6726 | 10.5358 | 10.3958 | 9.7547 | 9.4947 | 9.2105 | 8.9537 | 8.7242 | 8.5105 | 8.3105 | 6.7368 | 5.8011 | 4.9579
|  | QUEENSMEAD | EE |  |  |  | 12.18 | 12.0747 | 11.9632 | 11.8442 | 11.7211 | 11.5926 | 11.4695 | 11.3516 | 11.2389 | 11.1389 | 10.1126 | 9.4537 | 8.8768 | 10.5095 | 10.2632 | 10.0516 | 9.4242 | 9.2084 | 8.9621 | 8.7526 | 8.5568 | 8.3695 | 8.1979 | 6.7442 | 6 | 5.3411 | 10.7284 | 10.6232 | 10.5116 | 10.0347 | 9.8253 | 9.5884 | 9.3853 | 9.1958 | 9.0137 | 8.8463 | 7.4758 | 6.7674 | 6.1453
|  | QUEENSMEAD | HT |  |  |  | 12.1242 | 11.9874 | 11.8495 | 11.7032 | 11.5526 | 11.3968 | 11.24 | 11.1021 | 10.9768 | 10.8621 | 9.4116 | 8.5379 | 7.7537 | 10.4337 | 10.0811 | 9.8137 | 9.1326 | 8.8653 | 8.5695 | 8.3053 | 8.0684 | 7.8474 | 7.64 | 5.9768 | 4.9937 | 4.1042 | 10.6726 | 10.5358 | 10.3958 | 9.7547 | 9.4947 | 9.2105 | 8.9537 | 8.7242 | 8.5105 | 8.3105 | 6.7368 | 5.8011 | 4.9579
|  | QUEENSMEAD | HE |  |  |  | 12.2495 | 12.1779 | 12.0979 | 12.0105 | 11.9158 | 11.8147 | 11.7179 | 11.6263 | 11.5421 | 11.4684 | 11.0263 | 10.6032 | -15.0621 | 10.6063 | 10.4705 | 10.3537 | 9.7958 | 9.6442 | 9.4579 | 9.3074 | 9.1705 | 9.0421 | 8.9263 | 7.7547 | 7.2747 | 6.8663 | 10.7979 | 10.7263 | 10.6463 | 10.3905 | 10.2432 | 10.0642 | 9.9168 | 9.7832 | 9.6589 | 9.5463 | 8.4432 | 7.9884 | 7.6042
|  | QUEENSMEAD | CF |  |  |  | 12.2895 | 12.2484 | 12.2053 | 12.16 | 12.1137 | 12.0653 | 12.0168 | 11.9684 | 11.9211 | 11.8737 | 11.6611 | 11.5558 | 11.4968 | 10.6684 | 10.5989 | 10.5421 | 10.3863 | 10.2979 | 10.1958 | 10.1042 | 10.0158 | 9.9295 | 9.8432 | 8.9842 | 8.6211 | 8.3284 | 10.8379 | 10.7968 | 10.7537 | 10.7084 | 10.6621 | 10.6137 | 10.5653 | 10.5168 | 10.4695 | 10.4221 | 9.6137 | 9.2695 | 8.9947
MELKSHAM GSP | WEST GRAFTON | RAMSBURY | MINIMUM HEADROOM | SU 27380 72108 | YES | 0.04 | 9.0305 | 8.8716 | 8.6705 | 8.5021 | 8.3537 | 8.2074 | 8.0611 | 7.9284 | 7.8053 | 7.6768 | 6.3284 | 6.1853 | 1.0095 | 7.9411 | 7.7705 | 7.5537 | 7.3726 | 7.2158 | 7.0611 | 6.9053 | 6.7632 | 6.6316 | 6.4916 | 4.9116 | 4.7684 | 4.2147 | 8.1368 | 7.9674 | 7.7505 | 7.5705 | 7.4126 | 7.2568 | 7.1011 | 6.9589 | 6.8274 | 6.6874 | 5.1063 | 4.9632 | 4.4095
|  | RAMSBURY | EE |  |  |  | 9.0947 | 8.9768 | 8.8305 | 8.6768 | 8.5358 | 8.3989 | 8.2789 | 8.1695 | 8.0611 | 7.9642 | 6.3284 | 6.1853 | 6.0821 | 8.0105 | 7.8853 | 7.7274 | 7.5611 | 7.4105 | 7.2663 | 7.1389 | 7.0221 | 6.9074 | 6.8032 | 4.9116 | 4.7684 | 4.6653 | 8.1768 | 8.0811 | 7.9242 | 7.7579 | 7.6084 | 7.4632 | 7.3358 | 7.2179 | 7.1032 | 6.9989 | 5.1063 | 4.9632 | 4.86
|  | RAMSBURY | HT |  |  |  | 9.0305 | 8.8716 | 8.6705 | 8.5021 | 8.3537 | 8.2074 | 8.0611 | 7.9284 | 7.8053 | 7.6768 | 7.0021 | 6.3232 | 5.6516 | 7.9411 | 7.7705 | 7.5537 | 7.3726 | 7.2158 | 7.0611 | 6.9053 | 6.7632 | 6.6316 | 6.4916 | 5.7442 | 4.9789 | 4.2147 | 8.1368 | 7.9674 | 7.7505 | 7.5705 | 7.4126 | 7.2568 | 7.1011 | 6.9589 | 6.8274 | 6.6874 | 5.94 | 5.1747 | 4.4095
|  | RAMSBURY | HE |  |  |  | 9.1832 | 9.1084 | 9 | 8.8853 | 8.7789 | 8.6842 | 8.5968 | 8.5189 | 8.4453 | 8.3789 | 6.6084 | 6.5263 | 1.0095 | 8.1053 | 8.0263 | 7.9084 | 7.7842 | 7.6716 | 7.5716 | 7.4789 | 7.3979 | 7.3211 | 7.2505 | 5.1916 | 5.1095 | 5.0589 | 8.2211 | 8.1789 | 8.1042 | 7.9811 | 7.8684 | 7.7684 | 7.6768 | 7.5947 | 7.5179 | 7.4484 | 5.3863 | 5.3042 | 5.2537
|  | RAMSBURY | CF |  |  |  | 9.2316 | 9.1884 | 9.1463 | 9.1021 | 9.0568 | 9.0053 | 8.9505 | 8.8968 | 8.8389 | 8.7768 | 8.5011 | 8.2768 | 8.0242 | 8.1568 | 8.1105 | 8.0653 | 8.0189 | 7.9716 | 7.9158 | 7.8568 | 7.8 | 7.7368 | 7.6695 | 7.3716 | 7.12 | 6.8284 | 8.2474 | 8.2232 | 8.2 | 8.1758 | 8.1505 | 8.1116 | 8.0537 | 7.9958 | 7.9337 | 7.8663 | 7.5684 | 7.3158 | 7.0232
MELKSHAM GSP | AMESBURY | RATFYN | MINIMUM HEADROOM | SU 16215 42533 | YES | 0 | 27.4526 | 27.2042 | 26.9516 | 26.6842 | 26.3611 | 25.9074 | 25.4505 | 25.0263 | 24.6358 | 24.2116 | 21.9211 | 19.5295 | 5.4821 | 24.2411 | 23.7853 | 23.2495 | 22.6558 | 22.1621 | 21.6653 | 21.1737 | 20.7221 | 20.3053 | 19.8463 | 17.3253 | 14.6484 | 11.9726 | 24.8442 | 24.5674 | 24.0189 | 23.4253 | 22.9295 | 22.4316 | 21.9389 | 21.4832 | 21.0653 | 20.6042 | 18.0642 | 15.3674 | 12.6832
|  | RATFYN | EE |  |  |  | 27.5453 | 27.3484 | 27.14 | 26.9179 | 26.6863 | 26.44 | 26.1379 | 25.7842 | 25.4411 | 25.1211 | 23.3821 | 21.4758 | 19.5916 | 24.4389 | 24.0863 | 23.6916 | 23.2347 | 22.78 | 22.34 | 21.9411 | 21.5537 | 21.1821 | 20.8453 | 18.9547 | 16.8316 | 14.6832 | 24.9442 | 24.7368 | 24.4695 | 24.0032 | 23.5484 | 23.1074 | 22.7042 | 22.3137 | 21.9411 | 21.5989 | 19.6842 | 17.5326 | 15.3737
|  | RATFYN | HT |  |  |  | 27.4526 | 27.2042 | 26.9516 | 26.6842 | 26.3611 | 25.9074 | 25.4505 | 25.0263 | 24.6358 | 24.2116 | 21.9211 | 19.5295 | 17.1747 | 24.2411 | 23.7853 | 23.2495 | 22.6558 | 22.1621 | 21.6653 | 21.1737 | 20.7221 | 20.3053 | 19.8463 | 17.3253 | 14.6484 | 11.9726 | 24.8442 | 24.5674 | 24.0189 | 23.4253 | 22.9295 | 22.4316 | 21.9389 | 21.4832 | 21.0653 | 20.6042 | 18.0642 | 15.3674 | 12.6832
|  | RATFYN | HE |  |  |  | 27.6811 | 27.5484 | 27.4021 | 27.24 | 27.0663 | 26.8758 | 26.6926 | 26.52 | 26.3589 | 26.2179 | 25.2126 | 23.8221 | 5.4821 | 24.5947 | 24.4495 | 24.2263 | 23.9084 | 23.5989 | 23.2853 | 22.9968 | 22.7232 | 22.4684 | 22.2453 | 20.9232 | 19.3432 | 17.6537 | 25.0905 | 24.9516 | 24.7968 | 24.6232 | 24.3747 | 24.0537 | 23.7632 | 23.4874 | 23.2326 | 23.0063 | 21.6737 | 20.0853 | 18.3895
|  | RATFYN | CF |  |  |  | 27.7611 | 27.6874 | 27.6126 | 27.5337 | 27.4526 | 27.3653 | 27.2768 | 27.1905 | 27.1042 | 27.0189 | 26.6347 | 26.0021 | 25.0853 | 24.6842 | 24.6021 | 24.5179 | 24.4305 | 24.3063 | 24.1347 | 23.9526 | 23.7853 | 23.6168 | 23.4368 | 22.5937 | 21.7221 | 20.6653 | 25.1758 | 25.0979 | 25.0179 | 24.9347 | 24.8495 | 24.7558 | 24.66 | 24.5684 | 24.3874 | 24.2032 | 23.3547 | 22.4811 | 21.4189
BRAMLEY (FLEE) | READING BSP | READING | MINIMUM HEADROOM | SU 74591 73788 | YES | 1.1926 | 49.9989 | 49.4126 | 48.8095 | 48.1526 | 47.5032 | 46.8232 | 45.8084 | 44.6937 | 43.6716 | 42.7316 | 38.7147 | 34.8253 | -4.2116 | 42.1537 | 41.1011 | 39.8547 | 38.2832 | 37.0389 | 35.64 | 34.3326 | 33.1211 | 32.0095 | 30.9863 | 26.6095 | 22.2905 | 18.1558 | 43.9347 | 43.0137 | 41.7284 | 40.1558 | 38.9116 | 37.5105 | 36.2053 | 34.9916 | 33.8789 | 32.8558 | 28.4789 | 24.1558 | 20.0189
|  | READING | EE |  |  |  | 50.2179 | 49.7747 | 49.2874 | 48.7484 | 48.2105 | 47.6495 | 47.1084 | 46.5979 | 45.9021 | 45.1589 | 42.2632 | 39.4474 | 36.8 | 42.4284 | 41.7842 | 40.8442 | 39.5516 | 38.5463 | 37.3947 | 36.3295 | 35.3305 | 34.4537 | 33.6526 | 30.5274 | 27.4011 | 24.4221 | 44.1579 | 43.7011 | 42.7411 | 41.4242 | 40.4189 | 39.2663 | 38.2011 | 37.2 | 36.3232 | 35.5211 | 32.3958 | 29.2632 | 26.2811
|  | READING | HT |  |  |  | 49.9989 | 49.4126 | 48.8095 | 48.1526 | 47.5032 | 46.8232 | 45.8084 | 44.6937 | 43.6716 | 42.7316 | 38.7147 | 34.8253 | 31.14 | 42.1537 | 41.1011 | 39.8547 | 38.2832 | 37.0389 | 35.64 | 34.3326 | 33.1211 | 32.0095 | 30.9863 | 26.6095 | 22.2905 | 18.1558 | 43.9347 | 43.0137 | 41.7284 | 40.1558 | 38.9116 | 37.5105 | 36.2053 | 34.9916 | 33.8789 | 32.8558 | 28.4789 | 24.1558 | 20.0189
|  | READING | HE |  |  |  | 50.5053 | 50.2158 | 49.8884 | 49.4863 | 49.08 | 48.6379 | 48.2179 | 47.8232 | 47.4611 | 47.1474 | 45.9674 | 44.1126 | -4.2116 | 42.7158 | 42.4263 | 42.0074 | 41.0347 | 40.3168 | 39.4084 | 38.5842 | 37.8179 | 37.1926 | 36.6211 | 34.5347 | 32.4632 | 30.4674 | 44.4453 | 44.1547 | 43.8221 | 42.9305 | 42.1905 | 41.2789 | 40.4537 | 39.6884 | 39.06 | 38.4895 | 36.3926 | 34.3158 | 32.3179
|  | READING | CF |  |  |  | 50.6705 | 50.5063 | 50.3379 | 50.1558 | 49.9547 | 49.7411 | 49.5242 | 49.3147 | 49.1126 | 48.9105 | 48.0168 | 47.54 | 47.1453 | 42.8811 | 42.7168 | 42.5484 | 42.2947 | 41.8768 | 41.3937 | 40.8989 | 40.4316 | 40.0274 | 39.6495 | 37.9968 | 36.7758 | 35.7179 | 44.6105 | 44.4463 | 44.2779 | 44.0916 | 43.8168 | 43.3021 | 42.7758 | 42.3032 | 41.8989 | 41.5211 | 39.8674 | 38.6463 | 37.5863
BRAMLEY (FLEE) | READING TOWN BSP | READING TOWN | MINIMUM HEADROOM | SU 71540 74122 | YES | 0.59474 | 99.3526 | 99.1137 | 98.8705 | 98.5916 | 96.7705 | 94.2611 | 91.8379 | 91.6126 | 91.3968 | 91.2 | 86.4863 | 85.7463 | 40.0853 | 90.1484 | 88.3211 | 87.6842 | 86.5779 | 84.4684 | 81.5547 | 78.6947 | 78.4737 | 78.2611 | 78.0684 | 72.3253 | 71.4937 | 70.8232 | 92.4653 | 90.6968 | 90.0726 | 88.9979 | 86.9568 | 84.0642 | 81.1821 | 80.9558 | 80.7389 | 80.5421 | 74.8632 | 74.0337 | 73.3642
|  | READING TOWN | EE |  |  |  | 99.4442 | 99.2558 | 99.0589 | 98.84 | 97.3 | 95.0421 | 91.8379 | 91.6126 | 91.3968 | 91.2 | 88.3421 | 86.9295 | 85.5821 | 90.3547 | 88.6316 | 88.0905 | 87.0789 | 85.0611 | 82.4379 | 78.6947 | 78.4737 | 78.2611 | 78.0684 | 74.8453 | 73.2947 | 71.7989 | 92.66 | 90.9895 | 90.4568 | 89.4716 | 87.5179 | 84.9232 | 81.1821 | 80.9558 | 80.7389 | 80.5421 | 77.3 | 75.7263 | 74.2084
|  | READING TOWN | HT |  |  |  | 99.3526 | 99.1137 | 98.8705 | 98.5916 | 96.7705 | 94.2611 | 93.9758 | 93.7211 | 93.4874 | 93.2695 | 90.1326 | 88.2947 | 86.5337 | 90.1484 | 88.3211 | 87.6842 | 86.5779 | 84.4684 | 81.5547 | 81.2705 | 81.0179 | 80.7853 | 80.5684 | 77.0326 | 74.9968 | 73.0284 | 92.4653 | 90.6968 | 90.0726 | 88.9979 | 86.9568 | 84.0642 | 83.7779 | 83.5232 | 83.2884 | 83.0705 | 79.5337 | 77.4916 | 75.5168
|  | READING TOWN | HE |  |  |  | 99.5505 | 99.4105 | 99.2547 | 99.0842 | 97.9463 | 95.76 | 92.6274 | 92.4505 | 92.2853 | 92.1421 | 89.7674 | 88.8821 | 40.0853 | 90.6084 | 89.0011 | 88.5705 | 87.6642 | 85.7505 | 83.2032 | 79.5316 | 79.3558 | 79.1905 | 79.0474 | 76.3316 | 75.3432 | 74.4126 | 92.9168 | 91.3653 | 90.9453 | 90.0663 | 88.2189 | 85.7189 | 82.0547 | 81.8789 | 81.7126 | 81.5705 | 78.8568 | 77.8674 | 76.9358
|  | READING TOWN | CF |  |  |  | 99.6042 | 99.5116 | 99.4158 | 99.3168 | 99.2137 | 99.1074 | 98.44 | 97.2095 | 95.2568 | 93.4295 | 86.4863 | 85.7463 | 85.1589 | 91.04 | 90.2263 | 89.9537 | 89.4547 | 88.5505 | 87.5768 | 86.3147 | 84.88 | 82.5905 | 80.4484 | 72.3253 | 71.4937 | 70.8232 | 93.1295 | 92.5474 | 92.2821 | 91.7979 | 90.9253 | 89.9842 | 88.7674 | 87.3821 | 85.1105 | 82.9726 | 74.8632 | 74.0337 | 73.3642
MANNINGTON GSP | REDHILL BSP | REDHILL | MINIMUM HEADROOM | SZ 08512 96149 | YES | 0.29053 | 44.3189 | 44.5832 | 43.5695 | 42.5368 | 41.6379 | 40.8042 | 39.9116 | 39.0516 | 38.1789 | 37.3411 | 33.6368 | 30.2716 | 1.9284 | 38.3695 | 37.1642 | 36.4168 | 35.2905 | 34.3221 | 33.4358 | 32.4779 | 31.5484 | 30.5958 | 29.6811 | 25.6042 | 21.8558 | 18.4063 | 39.9179 | 38.6989 | 37.4547 | 36.3284 | 35.36 | 34.4726 | 33.5147 | 32.5842 | 31.6316 | 30.7158 | 26.6358 | 22.8832 | 19.4305
|  | REDHILL | EE |  |  |  | 44.3189 | 45.2516 | 44.2916 | 43.4305 | 42.6863 | 42.0263 | 41.3253 | 40.6484 | 39.9989 | 39.3126 | 36.4326 | 33.84 | 31.5337 | 38.7516 | 37.7611 | 36.7095 | 36.2589 | 35.4589 | 34.76 | 34.0084 | 33.2832 | 32.5884 | 31.84 | 28.6758 | 25.7811 | 23.1779 | 40.18 | 39.3011 | 38.2389 | 37.2979 | 36.4968 | 35.7968 | 35.0453 | 34.3189 | 33.6232 | 32.8747 | 29.7053 | 26.8053 | 24.2011
|  | REDHILL | HT |  |  |  | 45.8032 | 44.6968 | 43.5695 | 42.5368 | 41.6379 | 40.8042 | 39.9116 | 39.0516 | 38.1789 | 37.3411 | 33.6368 | 30.2716 | 27.1979 | 38.3695 | 37.1642 | 36.4168 | 35.2905 | 34.3221 | 33.4358 | 32.4779 | 31.5484 | 30.5958 | 29.6811 | 25.6042 | 21.8558 | 18.4063 | 39.9179 | 38.6989 | 37.4547 | 36.3284 | 35.36 | 34.4726 | 33.5147 | 32.5842 | 31.6316 | 30.7158 | 26.6358 | 22.8832 | 19.4305
|  | REDHILL | HE |  |  |  | 44.5663 | 45.9842 | 45.2495 | 44.6053 | 44.0705 | 43.6 | 43.0853 | 42.6011 | 42.1221 | 41.6105 | 39.5842 | 37.7863 | 1.9284 | 38.9989 | 38.5505 | 37.7432 | 37.5368 | 36.9632 | 36.4684 | 35.9211 | 35.4042 | 34.8926 | 34.3337 | 32.0989 | 30.0726 | 28.2811 | 40.4274 | 40.0979 | 39.2811 | 38.5747 | 38.0011 | 37.5074 | 36.9579 | 36.4421 | 35.9295 | 35.3705 | 33.1337 | 31.1053 | 29.3126
|  | REDHILL | CF |  |  |  | 44.7126 | 44.5832 | 46.2137 | 44.9726 | 44.6926 | 44.4147 | 44.1011 | 43.7779 | 43.4853 | 43.2011 | 41.9905 | 40.7663 | 39.7137 | 39.1695 | 39.0211 | 38.7968 | 36.8284 | 37.2211 | 36.92 | 36.5779 | 36.2263 | 35.9084 | 35.6021 | 34.2947 | 32.9168 | 31.7126 | 40.5968 | 40.4495 | 40.3463 | 38.3811 | 38.0758 | 37.7758 | 37.4337 | 37.0811 | 36.7632 | 36.4558 | 35.1484 | 33.7684 | 32.5642
CHICKERELL GSP | CHICKERELL BSP | REDLANDS | MINIMUM HEADROOM | SY 67131 82321 | YES | 1.1295 | 15.6495 | 14.8779 | 14.0705 | 13.1789 | 12.2095 | 11.3495 | 10.4979 | 9.7895 | 9.2021 | 8.6474 | 6.7063 | 4.68 | -9.0589 | 13.1621 | 12.2716 | 11.3579 | 10.3474 | 9.2432 | 8.2758 | 7.32 | 6.5284 | 5.8779 | 5.2621 | 3.1547 | 0.92211 | -1.3411 | 13.7189 | 12.8274 | 11.9147 | 10.9032 | 9.7989 | 8.8305 | 7.8726 | 7.08 | 6.4274 | 5.8095 | 3.6905 | 1.4463 | -0.82316
|  | REDLANDS | EE |  |  |  | 15.8642 | 15.2147 | 14.5084 | 13.7189 | 12.8453 | 12.0768 | 11.3263 | 10.6905 | 10.1642 | 9.6684 | 8.1179 | 6.6074 | 5.0895 | 13.4084 | 12.6432 | 11.8411 | 10.9411 | 9.9442 | 9.0758 | 8.2284 | 7.5168 | 6.9368 | 6.3863 | 4.7084 | 3.0421 | 1.3379 | 13.9116 | 13.1989 | 12.3979 | 11.4968 | 10.4989 | 9.6295 | 8.78 | 8.0674 | 7.4842 | 6.9326 | 5.2379 | 3.5547 | 1.8432
|  | REDLANDS | HT |  |  |  | 15.6495 | 14.8779 | 14.0705 | 13.1789 | 12.2095 | 11.3495 | 10.4979 | 9.7895 | 9.2021 | 8.6474 | 6.7063 | 4.68 | 2.6579 | 13.1621 | 12.2716 | 11.3579 | 10.3474 | 9.2432 | 8.2758 | 7.32 | 6.5284 | 5.8779 | 5.2621 | 3.1547 | 0.92211 | -1.3411 | 13.7189 | 12.8274 | 11.9147 | 10.9032 | 9.7989 | 8.8305 | 7.8726 | 7.08 | 6.4274 | 5.8095 | 3.6905 | 1.4463 | -0.82316
|  | REDLANDS | HE |  |  |  | 16.1611 | 15.6558 | 15.1 | 14.4432 | 13.6958 | 13.0474 | 12.4147 | 11.8958 | 11.4895 | 11.1116 | 10.1389 | 9.1937 | -9.0589 | 13.7453 | 13.14 | 12.4926 | 11.74 | 10.8811 | 10.1442 | 9.4263 | 8.8421 | 8.3916 | 7.9695 | 6.9179 | 5.8516 | 4.68 | 14.0642 | 13.6968 | 13.0495 | 12.2958 | 11.4368 | 10.6989 | 9.98 | 9.3947 | 8.9432 | 8.52 | 7.4621 | 6.3895 | 5.2126
|  | REDLANDS | CF |  |  |  | 16.3768 | 16.0926 | 15.8084 | 15.4989 | 15.1495 | 14.8432 | 14.5221 | 14.2347 | 13.9884 | 13.7358 | 12.9147 | 12.2484 | 11.5853 | 13.9968 | 13.6568 | 13.3179 | 12.9463 | 12.5432 | 12.1958 | 11.8284 | 11.5053 | 11.2295 | 10.9463 | 10.0495 | 9.2979 | 8.5295 | 14.1526 | 14.0663 | 13.8747 | 13.5032 | 13.0989 | 12.7516 | 12.3853 | 12.06 | 11.7842 | 11.5 | 10.6011 | 9.8474 | 9.0747
MANNINGTON GSP | SALISBURY | REDLYNCH | MINIMUM HEADROOM | SU 19073 20576 | YES | 0.97368 | 16.2821 | 15.9453 | 15.6116 | 15.2758 | 14.9337 | 14.5568 | 14.1337 | 13.4053 | 10.5 | 10.2874 | 8.5789 | 6.5505 | -0.43368 | 13.3947 | 13.0347 | 12.6789 | 12.3189 | 11.9558 | 11.5674 | 11.1263 | 10.3189 | 6.9368 | 6.7379 | 4.9874 | 2.8537 | 2.1379 | 14.4947 | 14.1368 | 13.7863 | 13.4295 | 13.0705 | 12.6768 | 12.2326 | 11.4379 | 8.0495 | 7.8347 | 5.9905 | 3.7463 | 2.9853
|  | REDLYNCH | EE |  |  |  | 16.4337 | 16.1768 | 15.9126 | 15.6411 | 15.3632 | 15.0474 | 14.7274 | 14.4126 | 14.1 | 13.8021 | 11.7253 | 9.6421 | 8.4947 | 13.5579 | 13.2842 | 13.0032 | 12.7158 | 12.4221 | 12.1011 | 11.7779 | 11.4632 | 11.1537 | 10.8589 | 8.7147 | 6.5558 | 5.3179 | 14.6558 | 14.3842 | 14.1053 | 13.8189 | 13.5284 | 13.2 | 12.8684 | 12.5432 | 12.2211 | 11.9126 | 9.6474 | 7.3411 | 6.0568
|  | REDLYNCH | HT |  |  |  | 16.2821 | 15.9453 | 15.6116 | 15.2758 | 14.9337 | 14.5568 | 14.1337 | 13.4053 | 10.5 | 10.2874 | 8.5789 | 6.5505 | 5.8284 | 13.3947 | 13.0347 | 12.6789 | 12.3189 | 11.9558 | 11.5674 | 11.1263 | 10.3189 | 6.9368 | 6.7379 | 4.9874 | 2.8537 | 2.1379 | 14.4947 | 14.1368 | 13.7863 | 13.4295 | 13.0705 | 12.6768 | 12.2326 | 11.4379 | 8.0495 | 7.8347 | 5.9905 | 3.7463 | 2.9853
|  | REDLYNCH | HE |  |  |  | 16.5389 | 16.4442 | 16.3126 | 16.1347 | 15.9463 | 15.7211 | 15.5053 | 15.3 | 15.1 | 14.9253 | 13.2189 | 11.9316 | -0.43368 | 13.7758 | 13.6105 | 13.4337 | 13.2463 | 13.0484 | 12.8221 | 12.6053 | 12.3979 | 12.1979 | 12.0242 | 10.1611 | 8.7442 | 7.7716 | 14.8747 | 14.7074 | 14.5316 | 14.3463 | 14.1495 | 13.9168 | 13.6937 | 13.4811 | 13.2758 | 13.0947 | 11.2168 | 9.7579 | 8.7474
|  | REDLYNCH | CF |  |  |  | 16.6 | 16.5474 | 16.4958 | 16.44 | 16.3589 | 16.2316 | 16.0979 | 15.9758 | 15.86 | 15.7495 | 15.2116 | 14.64 | 14.0126 | 13.8863 | 13.7905 | 13.6916 | 13.5874 | 13.48 | 13.3495 | 13.2105 | 13.0853 | 12.9663 | 12.8516 | 12.2968 | 11.6863 | 11 | 14.9905 | 14.8895 | 14.7895 | 14.6853 | 14.5789 | 14.4442 | 14.3042 | 14.1758 | 14.0547 | 13.9379 | 13.3737 | 12.7579 | 12.0663
NURSLING GSP | SOUTHAMPTON (2 X 90) | REGENTS PARK | MINIMUM HEADROOM | SU 39267 13050 | YES | 0.42105 | 34.6263 | 34.4895 | 34.3505 | 34.2042 | 34.0505 | 33.8916 | 33.7316 | 33.5895 | 33.46 | 33.34 | 32.2884 | 31.1137 | -23.8221 | 30.7674 | 30.6011 | 30.3821 | 30.1158 | 29.8137 | 29.5337 | 29.2632 | 29.0126 | 28.7779 | 28.5137 | 26.9453 | 25.6274 | 24.4126 | 31.4021 | 31.2653 | 31.1263 | 30.9074 | 30.6053 | 30.3358 | 30.0726 | 29.8295 | 29.6021 | 29.3484 | 27.8589 | 26.5653 | 25.3505
|  | REGENTS PARK | EE |  |  |  | 34.6821 | 34.5768 | 34.4653 | 34.3463 | 34.22 | 34.0895 | 33.9632 | 33.8421 | 33.7242 | 33.6189 | 33.1516 | 32.2411 | 31.42 | 30.8305 | 30.7137 | 30.5779 | 30.38 | 30.1653 | 29.9 | 29.6095 | 29.3958 | 29.1937 | 29.0126 | 27.8937 | 26.8684 | 25.9368 | 31.4579 | 31.3526 | 31.2411 | 31.1221 | 30.9642 | 30.6895 | 30.4105 | 30.2042 | 30.0074 | 29.8326 | 28.7663 | 27.7958 | 26.8747
|  | REGENTS PARK | HT |  |  |  | 34.6263 | 34.4895 | 34.3505 | 34.2042 | 34.0505 | 33.8916 | 33.7316 | 33.5895 | 33.46 | 33.34 | 32.2884 | 31.1137 | 30.0379 | 30.7674 | 30.6011 | 30.3821 | 30.1158 | 29.8137 | 29.5337 | 29.2632 | 29.0126 | 28.7779 | 28.5137 | 26.9453 | 25.6274 | 24.4126 | 31.4021 | 31.2653 | 31.1263 | 30.9074 | 30.6053 | 30.3358 | 30.0726 | 29.8295 | 29.6021 | 29.3484 | 27.8589 | 26.5653 | 25.3505
|  | REGENTS PARK | HE |  |  |  | 34.7453 | 34.6684 | 34.5832 | 34.4895 | 34.3884 | 34.2811 | 34.1779 | 34.0811 | 33.9905 | 33.9116 | 33.6442 | 33.4821 | -23.8221 | 30.9053 | 30.8211 | 30.7295 | 30.6253 | 30.5021 | 30.3168 | 30.1158 | 29.9789 | 29.8432 | 29.7211 | 29.0242 | 28.3221 | 27.6747 | 31.5211 | 31.4442 | 31.3589 | 31.2653 | 31.1642 | 31.0568 | 30.9137 | 30.7674 | 30.6295 | 30.5095 | 29.8453 | 29.1821 | 28.5747
|  | REGENTS PARK | CF |  |  |  | 34.7842 | 34.7379 | 34.6905 | 34.64 | 34.5895 | 34.5358 | 34.4821 | 34.4284 | 34.3758 | 34.3232 | 34.0884 | 33.9695 | 33.9032 | 30.9495 | 30.8968 | 30.8453 | 30.7895 | 30.7337 | 30.6747 | 30.6158 | 30.5495 | 30.4832 | 30.4032 | 29.9789 | 29.5221 | 29.0979 | 31.56 | 31.5137 | 31.4663 | 31.4158 | 31.3653 | 31.3116 | 31.2579 | 31.2042 | 31.1516 | 31.0989 | 30.7663 | 30.3295 | 29.9316
COWLEY GSP | WITNEY BSP | RISSINGTON | MINIMUM HEADROOM | SP 19225 19563 | YES | 0.4 | 11.7421 | 11.6105 | 11.4768 | 11.3358 | 11.1916 | 11.0105 | 10.6916 | 10.3853 | 10.0926 | 9.8389 | 8.3074 | 6.6684 | -1.3326 | 9.9389 | 9.7358 | 9.5263 | 9.2926 | 9.0389 | 8.7611 | 8.4874 | 8.2284 | 7.9821 | 7.7684 | 6.5347 | 5.1737 | 3.7389 | 9.66 | 9.5179 | 9.3295 | 9.0495 | 8.7537 | 8.4189 | 8.0884 | 7.7632 | 7.4526 | 7.1853 | 5.5221 | 3.6989 | 2.1274
|  | RISSINGTON | EE |  |  |  | 11.7895 | 11.6853 | 11.5758 | 11.4558 | 11.3337 | 11.1905 | 11.0453 | 10.9042 | 10.6684 | 10.4589 | 9.1474 | 7.7147 | 6.5863 | 10.0221 | 9.8653 | 9.7 | 9.5189 | 9.3347 | 9.1211 | 8.9042 | 8.6884 | 8.4789 | 8.3032 | 7.2716 | 6.1832 | 5.1958 | 9.7126 | 9.6011 | 9.4832 | 9.3284 | 9.1063 | 8.8589 | 8.5968 | 8.3347 | 8.0768 | 7.8611 | 6.4642 | 4.8874 | 3.6105
|  | RISSINGTON | HT |  |  |  | 11.7421 | 11.6105 | 11.4768 | 11.3358 | 11.1916 | 11.0105 | 10.6916 | 10.3853 | 10.0926 | 9.8389 | 8.3074 | 6.6684 | 5.28 | 9.9389 | 9.7358 | 9.5263 | 9.2926 | 9.0389 | 8.7611 | 8.4874 | 8.2284 | 7.9821 | 7.7684 | 6.5347 | 5.1737 | 3.7389 | 9.66 | 9.5179 | 9.3295 | 9.0495 | 8.7537 | 8.4189 | 8.0884 | 7.7632 | 7.4526 | 7.1853 | 5.5221 | 3.6989 | 2.1274
|  | RISSINGTON | HE |  |  |  | 11.8611 | 11.7916 | 11.7147 | 11.6284 | 11.5358 | 11.4263 | 11.32 | 11.22 | 11.1242 | 11.0389 | 10.2958 | 9.3053 | -1.3326 | 10.1211 | 10.0389 | 9.9274 | 9.7968 | 9.6621 | 9.5084 | 9.3568 | 9.2053 | 9.0526 | 8.9358 | 8.2074 | 7.4379 | 6.7547 | 9.7884 | 9.7179 | 9.6358 | 9.5421 | 9.4432 | 9.3232 | 9.1368 | 8.9516 | 8.7726 | 8.6337 | 7.6684 | 6.5705 | 5.5632
|  | RISSINGTON | CF |  |  |  | 11.9021 | 11.8632 | 11.8232 | 11.7811 | 11.7379 | 11.6853 | 11.6337 | 11.5821 | 11.5316 | 11.4832 | 11.2547 | 10.7442 | 10.1863 | 10.1621 | 10.1232 | 10.08 | 10.0137 | 9.9484 | 9.8747 | 9.7968 | 9.72 | 9.6442 | 9.5768 | 9.1084 | 8.6189 | 8.1916 | 9.8295 | 9.7905 | 9.7505 | 9.7053 | 9.6579 | 9.6032 | 9.5463 | 9.4905 | 9.4358 | 9.3853 | 8.7926 | 8.1189 | 7.5032
BRAMLEY (ANDO-THAT) | THATCHAM BSP | RIVERSIDE | MINIMUM HEADROOM | SU 47846 67187 | YES | 0.070526 | 23.0989 | 23.0053 | 22.9105 | 22.8095 | 22.4137 | 22.04 | 21.6168 | 21.2179 | 21.0653 | 20.9263 | 20.3358 | 19.6768 | 2.0737 | 20.1368 | 19.8758 | 19.5379 | 19.1884 | 18.7653 | 18.3642 | 17.8842 | 17.4305 | 17.2674 | 17.1179 | 16.5084 | 15.7779 | 15.0674 | 20.7074 | 20.6011 | 20.2937 | 19.9168 | 19.4589 | 19.0379 | 18.5589 | 18.1053 | 17.9421 | 17.7937 | 17.1895 | 16.46 | 15.7505
|  | RIVERSIDE | EE |  |  |  | 23.1347 | 23.06 | 22.9811 | 22.8979 | 22.6242 | 22.2811 | 21.8926 | 21.5189 | 21.3874 | 21.2695 | 20.8284 | 20.3284 | 19.84 | 20.2137 | 19.9905 | 19.6874 | 19.3737 | 18.9832 | 18.6232 | 18.1842 | 17.7589 | 17.6179 | 17.4926 | 17.0474 | 16.4926 | 15.9421 | 20.7453 | 20.66 | 20.4516 | 20.1126 | 19.6895 | 19.3011 | 18.8589 | 18.4337 | 18.2926 | 18.1674 | 17.7284 | 17.1737 | 16.6242
|  | RIVERSIDE | HT |  |  |  | 23.0989 | 23.0053 | 22.9105 | 22.8095 | 22.4137 | 22.04 | 21.6168 | 21.2179 | 21.0653 | 20.9263 | 20.3358 | 19.6768 | 19.0421 | 20.1368 | 19.8758 | 19.5379 | 19.1884 | 18.7653 | 18.3642 | 17.8842 | 17.4305 | 17.2674 | 17.1179 | 16.5084 | 15.7779 | 15.0674 | 20.7074 | 20.6011 | 20.2937 | 19.9168 | 19.4589 | 19.0379 | 18.5589 | 18.1053 | 17.9421 | 17.7937 | 17.1895 | 16.46 | 15.7505
|  | RIVERSIDE | HE |  |  |  | 23.1768 | 23.1211 | 23.0611 | 22.9926 | 22.8821 | 22.5747 | 22.2232 | 21.8863 | 21.7916 | 21.7137 | 21.3537 | 21.0463 | 2.0737 | 20.3105 | 20.1337 | 19.8747 | 19.6 | 19.2505 | 18.9274 | 18.5484 | 18.1632 | 18.0632 | 17.9811 | 17.5653 | 17.2232 | 16.88 | 20.7916 | 20.7274 | 20.6495 | 20.3526 | 19.9737 | 19.6242 | 19.2221 | 18.8379 | 18.7379 | 18.6558 | 18.2347 | 17.8926 | 17.5505
|  | RIVERSIDE | CF |  |  |  | 23.2 | 23.1653 | 23.1284 | 23.0905 | 23.0505 | 23.0105 | 22.9684 | 22.9105 | 22.8463 | 22.7821 | 22.4789 | 22.2389 | 22.0242 | 20.36 | 20.2537 | 20.1137 | 19.9737 | 19.8053 | 19.6558 | 19.4705 | 19.28 | 19.2137 | 19.1484 | 18.8368 | 18.5874 | 18.3579 | 20.8168 | 20.7768 | 20.7326 | 20.6874 | 20.5737 | 20.4126 | 20.2116 | 20.0063 | 19.9368 | 19.8684 | 19.5432 | 19.2768 | 19.0316
MANNINGTON GSP | MANNINGTON BSP | ROCKBOURNE | MINIMUM HEADROOM | SU 11617 17810 | YES | 0.41579 | 3.7326 | 3.6758 | 3.6211 | 3.5653 | 3.5105 | 3.4558 | 3.4021 | 3.3537 | 3.3084 | 3.2674 | 3.0589 | 2.8474 | 0.52105 | 3.5526 | 3.4926 | 3.4368 | 3.3789 | 3.3221 | 3.2653 | 3.2105 | 3.16 | 3.1137 | 3.0716 | 2.8547 | 2.6347 | 2.4147 | 3.5368 | 3.4768 | 3.42 | 3.3621 | 3.3042 | 3.2474 | 3.1926 | 3.1421 | 3.0947 | 3.0526 | 2.8337 | 2.6105 | 2.3947
|  | ROCKBOURNE | EE |  |  |  | 3.7495 | 3.7158 | 3.6737 | 3.6295 | 3.5863 | 3.5421 | 3.4989 | 3.46 | 3.4211 | 3.3874 | 3.2326 | 3.08 | 2.9389 | 3.5705 | 3.5347 | 3.4905 | 3.4453 | 3.4011 | 3.3558 | 3.3116 | 3.2716 | 3.2305 | 3.1968 | 3.0347 | 2.8747 | 2.7274 | 3.5547 | 3.5189 | 3.4747 | 3.4295 | 3.3842 | 3.3389 | 3.2937 | 3.2537 | 3.2126 | 3.1789 | 3.0158 | 2.8537 | 2.7042
|  | ROCKBOURNE | HT |  |  |  | 3.7326 | 3.6758 | 3.6211 | 3.5653 | 3.5105 | 3.4558 | 3.4021 | 3.3537 | 3.3084 | 3.2674 | 3.0589 | 2.8474 | 2.6432 | 3.5526 | 3.4926 | 3.4368 | 3.3789 | 3.3221 | 3.2653 | 3.2105 | 3.16 | 3.1137 | 3.0716 | 2.8547 | 2.6347 | 2.4147 | 3.5368 | 3.4768 | 3.42 | 3.3621 | 3.3042 | 3.2474 | 3.1926 | 3.1421 | 3.0947 | 3.0526 | 2.8337 | 2.6105 | 2.3947
|  | ROCKBOURNE | HE |  |  |  | 3.7674 | 3.7505 | 3.7337 | 3.7084 | 3.68 | 3.6505 | 3.6211 | 3.5926 | 3.5674 | 3.5432 | 3.4474 | 3.3463 | 0.52105 | 3.5884 | 3.5716 | 3.5537 | 3.5284 | 3.4989 | 3.4684 | 3.4379 | 3.4095 | 3.3832 | 3.3589 | 3.2589 | 3.1516 | 3.0526 | 3.5726 | 3.5558 | 3.5379 | 3.5126 | 3.4832 | 3.4526 | 3.4221 | 3.3937 | 3.3674 | 3.3421 | 3.2411 | 3.1326 | 3.0326
|  | ROCKBOURNE | CF |  |  |  | 3.7779 | 3.7695 | 3.7611 | 3.7516 | 3.74 | 3.7284 | 3.7147 | 3.7 | 3.6842 | 3.6684 | 3.5958 | 3.5295 | 3.4632 | 3.5989 | 3.5905 | 3.5821 | 3.5726 | 3.56 | 3.5484 | 3.5347 | 3.5189 | 3.5021 | 3.4863 | 3.4116 | 3.34 | 3.2695 | 3.5832 | 3.5747 | 3.5663 | 3.5568 | 3.5442 | 3.5326 | 3.5189 | 3.5032 | 3.4863 | 3.4705 | 3.3947 | 3.3221 | 3.2505
NURSLING GSP | ROWNHAMS | ROMSEY | MINIMUM HEADROOM | SU 36092 21110 | YES | 0 | 14.5568 | 44.2863 | 44.0042 | 44.0253 | 43.2232 | 42.3358 | 41.1495 | 40.0042 | 38.8895 | 37.7979 | 33.68 | 31.2421 | 11.9905 | 10.3747 | 39.88 | 39.2316 | 38.4716 | 37.5747 | 36.5821 | 35.2379 | 33.9337 | 32.6642 | 31.4168 | 26.7337 | 23.9958 | 21.4411 | 10.8558 | 40.4179 | 39.8621 | 39.2674 | 38.3716 | 37.3768 | 36.0305 | 34.7263 | 33.4537 | 32.2042 | 27.5084 | 24.7579 | 22.1979
|  | ROMSEY | EE |  |  |  | 14.6621 | 44.4516 | 44.2211 | 44.6368 | 43.8221 | 42.9674 | 41.8579 | 40.7768 | 39.7032 | 38.66 | 34.98 | 33.0074 | 31.2189 | 10.5958 | 40.2189 | 39.7453 | 39.1484 | 38.2305 | 37.2674 | 36.0011 | 34.7705 | 33.5463 | 32.3526 | 28.1611 | 25.9474 | 23.9084 | 11.0105 | 40.7126 | 40.3 | 39.9453 | 39.0263 | 38.0621 | 36.7937 | 35.5611 | 34.3337 | 33.1379 | 28.9295 | 26.6979 | 24.6526
|  | ROMSEY | HT |  |  |  | 14.5568 | 44.2863 | 44.0042 | 44.0253 | 43.2232 | 42.3358 | 41.1495 | 40.0042 | 38.8895 | 37.7979 | 33.68 | 31.2421 | 28.9905 | 10.3747 | 39.88 | 39.2316 | 38.4716 | 37.5747 | 36.5821 | 35.2379 | 33.9337 | 32.6642 | 31.4168 | 26.7337 | 23.9958 | 21.4411 | 10.8558 | 40.4179 | 39.8621 | 39.2674 | 38.3716 | 37.3768 | 36.0305 | 34.7263 | 33.4537 | 32.2042 | 27.5084 | 24.7579 | 22.1979
|  | ROMSEY | HE |  |  |  | 14.8063 | 44.6611 | 44.4979 | 44.3084 | 44.0863 | 43.8168 | 42.8158 | 41.8411 | 40.8811 | 39.9432 | 36.7768 | 35.3095 | 11.9905 | 10.8021 | 40.6516 | 40.3126 | 39.8389 | 39.0432 | 38.1937 | 37.0474 | 35.9295 | 34.8263 | 33.7463 | 30.1074 | 28.4337 | 26.8768 | 11.1526 | 41.0084 | 40.7947 | 40.3926 | 39.7421 | 38.9884 | 37.8411 | 36.7232 | 35.6179 | 34.5368 | 30.8895 | 29.2105 | 27.6484
|  | ROMSEY | CF |  |  |  | 14.8853 | 44.8011 | 44.7147 | 45.9126 | 45.5926 | 45.2253 | 44.7179 | 44.1895 | 43.6063 | 42.9884 | 40.5895 | 39.6326 | 38.7568 | 10.8863 | 40.7979 | 40.7063 | 40.5474 | 40.1853 | 39.7695 | 39.1863 | 38.5811 | 37.9105 | 37.1968 | 34.4442 | 33.3558 | 32.3474 | 11.2316 | 41.1484 | 41.0621 | 41.3442 | 40.9811 | 40.5642 | 39.9821 | 39.3758 | 38.7042 | 37.9905 | 35.2347 | 34.1432 | 33.1326
LOVEDEAN GSP | CHICHESTER & HUNSTON | ROSE GREEN | MINIMUM HEADROOM | SZ 89974 99335 | YES | 0.23053 | 21.7695 | 21.4558 | 21.0684 | 19.4011 | 17.8053 | 16.0032 | 14.4316 | 13.0695 | 11.7316 | 10.4221 | 3.3674 | -1.7358 | -8.3053 | 17.4316 | 16.5821 | 15.3211 | 13.4074 | 11.5884 | 9.5316 | 7.7453 | 6.1968 | 4.6747 | 3.1811 | -4.9295 | -10.7853 | -14.4084 | 17.9832 | 17.1558 | 15.9316 | 14.0758 | 12.2811 | 10.2516 | 8.4884 | 6.9589 | 5.4558 | 3.9811 | -4.0189 | -9.8011 | -13.3789
|  | ROSE GREEN | EE |  |  |  | 21.8937 | 21.6505 | 21.3947 | 20.9421 | 19.6968 | 18.0242 | 16.6053 | 15.1368 | 13.6053 | 12.2253 | 5.2147 | 0.25789 | -2.2663 | 17.5558 | 17.3126 | 16.4158 | 15.1737 | 13.7516 | 11.8326 | 10.2137 | 8.5347 | 6.7789 | 5.1979 | -2.8937 | -8.6126 | -11.5074 | 18.1074 | 17.8642 | 16.9937 | 15.7895 | 14.4126 | 12.5221 | 10.9232 | 9.2663 | 7.5337 | 5.9737 | -2.0095 | -7.6558 | -10.5137
|  | ROSE GREEN | HT |  |  |  | 21.7695 | 21.4558 | 21.0684 | 19.4011 | 17.8053 | 16.0032 | 14.4316 | 13.0695 | 11.7316 | 10.4221 | 3.3674 | -1.7358 | -4.9095 | 17.4316 | 16.5821 | 15.3211 | 13.4074 | 11.5884 | 9.5316 | 7.7453 | 6.1968 | 4.6747 | 3.1811 | -4.9295 | -10.7853 | -14.4084 | 17.9832 | 17.1558 | 15.9316 | 14.0758 | 12.2811 | 10.2516 | 8.4884 | 6.9589 | 5.4558 | 3.9811 | -4.0189 | -9.8011 | -13.3789
|  | ROSE GREEN | HE |  |  |  | 22.0632 | 21.9032 | 21.7242 | 21.5284 | 20.5663 | 18.98 | 17.5284 | 16.2726 | 14.9295 | 13.7011 | 7.3705 | 3.02 | -8.3053 | 17.7253 | 17.5653 | 17.1021 | 15.9863 | 14.6937 | 12.8611 | 11.1916 | 9.7505 | 8.2032 | 6.7863 | -0.56632 | -5.6263 | -7.9768 | 18.2768 | 18.1168 | 17.6653 | 16.5853 | 15.3358 | 13.5421 | 11.8958 | 10.4747 | 8.9484 | 7.5537 | 0.30842 | -4.6768 | -6.9937
|  | ROSE GREEN | CF |  |  |  | 22.1632 | 22.0758 | 21.9853 | 21.8905 | 21.7926 | 21.6905 | 21.5863 | 21.4821 | 21.3811 | 21.28 | 16.7579 | 11.2811 | 10.0421 | 19.1284 | 17.7379 | 17.6474 | 17.5526 | 17.4547 | 17.3526 | 17.2484 | 17.1453 | 16.6526 | 15.9453 | 10.2926 | 3.8842 | 2.4516 | 19.6295 | 18.2895 | 18.1989 | 18.1042 | 18.0063 | 17.9032 | 17.8 | 17.6958 | 17.2179 | 16.5347 | 11.0095 | 4.7021 | 3.2895
COWLEY GSP | COWLEY LOCAL (2 X 90) | ROSE HILL | MINIMUM HEADROOM | SP 53637 03027 | YES | 1.6295 | 23.1463 | 22.9084 | 22.6684 | 22.6179 | 22.3916 | 40.2558 | 38.4768 | 36.7389 | 35.3811 | 34.34 | 29.3263 | 24.6747 | 4.5211 | 19.1589 | 18.2421 | 17.7853 | 17.3158 | 16.8421 | 34.4716 | 31.74 | 29.6916 | 28.0979 | 26.8821 | 20.9821 | 15.4758 | 10.0811 | 19.76 | 19.4705 | 19.1484 | 18.6789 | 18.2053 | 35.8347 | 33.1032 | 31.0537 | 29.46 | 28.2432 | 22.3411 | 16.8337 | 11.4368
|  | ROSE HILL | EE |  |  |  | 23.2274 | 23.0358 | 22.8337 | 22.6179 | 22.3916 | 40.2558 | 38.4768 | 36.7389 | 35.3811 | 34.34 | 29.3263 | 24.6747 | 20.1379 | 19.2453 | 18.9895 | 18.2979 | 17.7379 | 17.2347 | 34.8821 | 31.74 | 29.6916 | 28.0979 | 26.8821 | 20.9821 | 15.4758 | 10.0811 | 19.8474 | 19.6337 | 19.4032 | 19.1021 | 18.5989 | 36.2453 | 33.1032 | 31.0537 | 29.46 | 28.2432 | 22.3411 | 16.8337 | 11.4368
|  | ROSE HILL | HT |  |  |  | 23.1463 | 22.9084 | 22.6684 | 23.5084 | 23.0705 | 40.7326 | 40.4558 | 39.2842 | 38.1621 | 37.0747 | 31.7211 | 27.6358 | 22.6642 | 19.1589 | 18.2421 | 17.7853 | 17.3158 | 16.8421 | 34.4716 | 34.1947 | 32.8316 | 31.5263 | 30.2579 | 23.9811 | 18.2032 | 12.42 | 19.76 | 19.4705 | 19.1484 | 18.6789 | 18.2053 | 35.8347 | 35.5579 | 34.1947 | 32.8884 | 31.62 | 25.3411 | 19.4547 | 13.6821
|  | ROSE HILL | HE |  |  |  | 23.3453 | 23.2084 | 23.0568 | 22.8895 | 22.7095 | 40.6189 | 39.3116 | 37.6421 | 36.4547 | 35.5147 | 30.9811 | 26.7905 | 4.5211 | 19.3705 | 19.22 | 18.8095 | 18.3716 | 17.9905 | 35.76 | 32.6642 | 30.6874 | 29.2895 | 28.1853 | 22.8189 | 17.8263 | 12.9316 | 19.9747 | 19.82 | 19.6432 | 19.46 | 19.2684 | 37.1242 | 34.0263 | 32.0495 | 30.6516 | 29.5463 | 24.1789 | 19.1842 | 14.2884
|  | ROSE HILL | CF |  |  |  | 23.4168 | 23.3358 | 23.2505 | 23.1642 | 23.0737 | 41.08 | 40.9842 | 40.8905 | 40.7979 | 40.3947 | 35.9221 | 33.1547 | 30.5137 | 19.4421 | 19.3611 | 19.2726 | 19.1832 | 19.0895 | 37.0926 | 36.7442 | 36.0105 | 35.0053 | 33.9137 | 28.6084 | 25.3158 | 22.1558 | 20.0463 | 19.9653 | 19.8758 | 19.7863 | 19.6916 | 37.6937 | 37.5705 | 37.3747 | 36.3695 | 35.2768 | 29.9705 | 26.6768 | 23.5158
MELKSHAM GSP | CHIPPENHAM | ROWDEN | MINIMUM HEADROOM | ST 90805 72608 | YES | 0.26 | 25.8853 | 25.5537 | 25.2179 | 24.8632 | 23.8295 | 31.6716 | 30.3495 | 29.0905 | 27.2705 | 25.4926 | 16.1305 | 10.0084 | -13.3095 | 21.1537 | 20.1747 | 19.2095 | 17.9905 | 16.5589 | 24.2726 | 22.7947 | 21.38 | 19.2811 | 17.2474 | 6.4863 | -0.51368 | -3.7853 | 22.2916 | 21.6095 | 20.6726 | 19.4916 | 18.0389 | 16.7232 | 15.2084 | 13.7642 | 11.6621 | 9.6242 | -1.1568 | -8.1811 | -11.4642
|  | ROWDEN | EE |  |  |  | 26.0074 | 25.7463 | 25.4684 | 25.1737 | 24.5611 | 32.5105 | 31.3979 | 30.3705 | 28.6495 | 26.9684 | 18.1463 | 12.5547 | 10.2716 | 21.4305 | 20.5979 | 19.76 | 18.6653 | 17.3505 | 25.1789 | 23.9358 | 22.7905 | 20.8042 | 18.8842 | 8.7316 | 2.3253 | -0.25789 | 22.4221 | 22.0211 | 21.2084 | 20.1484 | 18.8453 | 17.6453 | 16.3705 | 15.1958 | 13.1821 | 11.2568 | 1.0747 | -5.3642 | -7.9589
|  | ROWDEN | HT |  |  |  | 25.8853 | 25.5537 | 25.2179 | 24.8632 | 23.8295 | 31.6716 | 30.3495 | 29.0905 | 27.2705 | 25.4926 | 16.1305 | 10.0084 | 7.1074 | 21.1537 | 20.1747 | 19.2095 | 17.9905 | 16.5589 | 24.2726 | 22.7947 | 21.38 | 19.2811 | 17.2474 | 6.4863 | -0.51368 | -3.7853 | 22.2916 | 21.6095 | 20.6726 | 19.4916 | 18.0389 | 16.7232 | 15.2084 | 13.7642 | 11.6621 | 9.6242 | -1.1568 | -8.1811 | -11.4642
|  | ROWDEN | HE |  |  |  | 26.1811 | 26.0011 | 25.8032 | 25.5832 | 25.3463 | 33.6242 | 32.6474 | 31.7284 | 30.1095 | 28.5989 | 20.5453 | 15.6642 | -13.3095 | 21.8126 | 21.16 | 20.4979 | 19.5684 | 18.4126 | 26.3874 | 25.2884 | 24.2547 | 22.3958 | 20.6389 | 11.3095 | 5.6568 | 3.7095 | 22.5989 | 22.4011 | 21.9295 | 21.0316 | 19.9168 | 18.8758 | 17.7484 | 16.6874 | 14.7821 | 13.0232 | 3.68 | -1.9842 | -3.94
|  | ROWDEN | CF |  |  |  | 26.2832 | 26.18 | 26.0747 | 25.9632 | 25.8495 | 34.7284 | 34.6053 | 34.4842 | 34.3642 | 34.2316 | 30.3916 | 24.8958 | 23.8126 | 22.0147 | 21.7126 | 21.3621 | 20.9053 | 20.3747 | 28.88 | 28.3821 | 28.0063 | 27.5411 | 27.0716 | 22.6726 | 16.2558 | 15.0179 | 22.7011 | 22.5979 | 22.4821 | 22.3263 | 21.8137 | 21.3358 | 20.8526 | 20.4874 | 20.0379 | 19.5747 | 15.0579 | 8.6347 | 7.3905
LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | ROWNER PARK | MINIMUM HEADROOM | SU 58018 00782 | YES | 1.3253 | 22.6189 | 22.4379 | 22.2558 | 22.0642 | 21.8642 | 21.6579 | 21.4168 | 21.1347 | 20.8684 | 20.6168 | 19.3947 | 18.1589 | 1.7389 | 19.9947 | 19.6632 | 19.3358 | 19.0042 | 18.6695 | 18.3368 | 18.0053 | 17.7 | 17.4137 | 17.1411 | 15.8 | 14.4105 | 13.1168 | 20.4379 | 20.1189 | 19.8032 | 19.4832 | 19.16 | 18.8358 | 18.5137 | 18.2189 | 17.94 | 17.6779 | 16.3832 | 14.9916 | 13.6979
|  | ROWNER PARK | EE |  |  |  | 22.6863 | 22.5421 | 22.3916 | 22.2316 | 22.0621 | 21.8863 | 21.7158 | 21.5526 | 21.3937 | 21.2126 | 20.2779 | 19.3168 | 18.4495 | 20.1389 | 19.8821 | 19.6211 | 19.3526 | 19.0789 | 18.8042 | 18.5368 | 18.28 | 18.0316 | 17.8 | 16.7842 | 15.7053 | 14.7137 | 20.5758 | 20.3284 | 20.0758 | 19.8168 | 19.5516 | 19.2832 | 19.0253 | 18.7747 | 18.5326 | 18.3084 | 17.3242 | 16.2821 | 15.2905
|  | ROWNER PARK | HT |  |  |  | 22.6189 | 22.4379 | 22.2558 | 22.0642 | 21.8642 | 21.6579 | 21.4168 | 21.1347 | 20.8684 | 20.6168 | 19.3947 | 18.1589 | 17.0211 | 19.9947 | 19.6632 | 19.3358 | 19.0042 | 18.6695 | 18.3368 | 18.0053 | 17.7 | 17.4137 | 17.1411 | 15.8 | 14.4105 | 13.1168 | 20.4379 | 20.1189 | 19.8032 | 19.4832 | 19.16 | 18.8358 | 18.5137 | 18.2189 | 17.94 | 17.6779 | 16.3832 | 14.9916 | 13.6979
|  | ROWNER PARK | HE |  |  |  | 22.7758 | 22.6737 | 22.56 | 22.4368 | 22.3042 | 22.1621 | 22.0274 | 21.8989 | 21.7779 | 21.6747 | 21.3084 | 20.8274 | 1.7389 | 20.3126 | 20.1663 | 19.9895 | 19.8032 | 19.6105 | 19.4084 | 19.2168 | 19.0337 | 18.8621 | 18.7084 | 18.0726 | 17.3737 | 16.7411 | 20.6989 | 20.5926 | 20.4295 | 20.2474 | 20.0589 | 19.8621 | 19.6747 | 19.4947 | 19.3284 | 19.1779 | 18.5621 | 17.8979 | 17.3021
|  | ROWNER PARK | CF |  |  |  | 22.8274 | 22.7642 | 22.7 | 22.6316 | 22.5621 | 22.4884 | 22.4147 | 22.3442 | 22.2726 | 22.2 | 21.8789 | 21.6958 | 21.3063 | 20.3632 | 20.3021 | 20.2011 | 20.0811 | 19.9621 | 19.8295 | 19.7105 | 19.5905 | 19.4726 | 19.3516 | 18.7979 | 18.2916 | 17.8389 | 20.7526 | 20.6874 | 20.62 | 20.5189 | 20.4042 | 20.2758 | 20.16 | 20.0432 | 19.9284 | 19.8126 | 19.2768 | 18.7968 | 18.3705
FAWLEY GSP | COWES & WOOTTON COMMON BSP | RYDE | MINIMUM HEADROOM | SZ 59554 91973 | YES | 0 | 35.4474 | 34.9695 | 34.4853 | 33.9726 | 32.7905 | 31.4126 | 29.9411 | 28.4979 | 27.0926 | 25.7821 | 19.5211 | 14.8968 | -12.4726 | 30.1074 | 28.8537 | 27.4074 | 25.9305 | 24.3789 | 22.8558 | 21.2232 | 19.6126 | 18.0389 | 16.5726 | 9.5084 | 4.3432 | -0.32211 | 31.1116 | 29.9063 | 28.5295 | 27.1221 | 25.5747 | 24.0495 | 22.4147 | 20.8 | 19.2232 | 17.7526 | 10.6632 | 5.4716 | 0.79474
|  | RYDE | EE |  |  |  | 35.6316 | 35.2568 | 34.86 | 34.4379 | 33.9884 | 33.0126 | 31.8758 | 30.7053 | 29.5032 | 28.3705 | 22.7884 | 19.0905 | 15.8684 | 30.5147 | 29.5516 | 28.3526 | 27.0947 | 25.8 | 24.6263 | 23.3716 | 22.0737 | 20.7358 | 19.4716 | 13.1768 | 9.0379 | 5.3821 | 31.3737 | 30.5737 | 29.4337 | 28.2358 | 26.9979 | 25.8211 | 24.5621 | 23.2589 | 21.9168 | 20.6474 | 14.3189 | 10.1421 | 6.4737
|  | RYDE | HT |  |  |  | 35.4474 | 34.9695 | 34.4853 | 33.9726 | 32.7905 | 31.4126 | 29.9411 | 28.4979 | 27.0926 | 25.7821 | 19.5211 | 14.8968 | 10.76 | 30.1074 | 28.8537 | 27.4074 | 25.9305 | 24.3789 | 22.8558 | 21.2232 | 19.6126 | 18.0389 | 16.5726 | 9.5084 | 4.3432 | -0.32211 | 31.1116 | 29.9063 | 28.5295 | 27.1221 | 25.5747 | 24.0495 | 22.4147 | 20.8 | 19.2232 | 17.7526 | 10.6632 | 5.4716 | 0.79474
|  | RYDE | HE |  |  |  | 35.8737 | 35.6137 | 35.3253 | 35.0074 | 34.6653 | 34.2926 | 33.6337 | 32.6516 | 31.6432 | 30.6905 | 26.1768 | 23.4611 | -12.4726 | 31.0495 | 30.3463 | 29.4042 | 28.3842 | 27.3189 | 26.3274 | 25.2863 | 24.1905 | 23.0589 | 21.9874 | 16.8453 | 13.7537 | 11.0295 | 31.6337 | 31.3474 | 30.4421 | 29.4737 | 28.46 | 27.5126 | 26.48 | 25.3821 | 24.2484 | 23.1737 | 18.0168 | 14.9137 | 12.18
|  | RYDE | CF |  |  |  | 36.0189 | 35.8684 | 35.7137 | 35.5516 | 35.3853 | 35.2084 | 35.0295 | 34.8526 | 34.6779 | 34.5042 | 31.6705 | 29.7674 | 28.2484 | 31.2368 | 31.0537 | 30.6495 | 30.1389 | 29.6211 | 29.1305 | 28.6147 | 28.0705 | 27.54 | 27.0442 | 23.0137 | 20.8463 | 19.1021 | 31.7979 | 31.6326 | 31.4589 | 31.1453 | 30.6474 | 30.1789 | 29.6863 | 29.1695 | 28.6621 | 28.1895 | 24.2021 | 22.0274 | 20.2779
MANNINGTON GSP | SALISBURY | SALISBURY CENTRAL | MINIMUM HEADROOM | SU 14215 30481 | YES | 0.10526 | 45.3137 | 44.8842 | 44.4495 | 43.9884 | 43.5095 | 43.2084 | 42.7095 | 42.0211 | 40.8116 | 39.8758 | 35.1463 | 31.3295 | -1.8095 | 39.2263 | 38.5737 | 37.7558 | 36.66 | 35.2884 | 34.4747 | 33.0011 | 31.5937 | 30.2389 | 29.2032 | 23.9021 | 19.6126 | 15.2916 | 40.1179 | 39.6884 | 39.2537 | 38.7347 | 37.3684 | 36.54 | 35.0716 | 33.6747 | 32.3211 | 31.2842 | 25.9768 | 21.6811 | 17.3568
|  | SALISBURY CENTRAL | EE |  |  |  | 45.4747 | 45.1358 | 44.7768 | 44.3947 | 43.9937 | 43.5779 | 43.1737 | 42.7895 | 42.4168 | 41.3937 | 37.6579 | 34.6947 | 31.7158 | 39.3968 | 39.0442 | 38.4705 | 37.6653 | 36.5705 | 35.5442 | 34.6558 | 33.5358 | 32.1968 | 30.8389 | 26.6737 | 23.3389 | 19.9379 | 40.2789 | 39.94 | 39.5811 | 39.1989 | 38.6453 | 37.6232 | 36.7368 | 35.6211 | 34.2884 | 32.9484 | 28.7463 | 25.4032 | 22
|  | SALISBURY CENTRAL | HT |  |  |  | 45.3137 | 44.8842 | 44.4495 | 43.9884 | 43.5095 | 43.2084 | 42.7095 | 42.0211 | 40.8116 | 39.8758 | 35.1463 | 31.3295 | 27.5211 | 39.2263 | 38.5737 | 37.7558 | 36.66 | 35.2884 | 34.4747 | 33.0011 | 31.5937 | 30.2389 | 29.2032 | 23.9021 | 19.6126 | 15.2916 | 40.1179 | 39.6884 | 39.2537 | 38.7347 | 37.3684 | 36.54 | 35.0716 | 33.6747 | 32.3211 | 31.2842 | 25.9768 | 21.6811 | 17.3568
|  | SALISBURY CENTRAL | HE |  |  |  | 45.6905 | 45.4526 | 45.1895 | 44.8989 | 44.5863 | 44.2516 | 43.9305 | 43.6284 | 43.3474 | 43.1032 | 40.6589 | 38.5168 | -1.8095 | 39.6253 | 39.3789 | 39.1084 | 38.8021 | 37.8989 | 37.0579 | 36.3558 | 35.4979 | 34.5189 | 33.6021 | 29.9516 | 27.5168 | 24.9716 | 40.4947 | 40.2568 | 39.9937 | 39.7032 | 39.3905 | 39.0347 | 38.4316 | 37.5768 | 36.6021 | 35.6895 | 32.0316 | 29.5926 | 27.0453
|  | SALISBURY CENTRAL | CF |  |  |  | 45.8147 | 45.6737 | 45.5284 | 45.3768 | 45.22 | 45.0568 | 44.8905 | 44.7274 | 44.5663 | 44.4042 | 43.6821 | 43.0547 | 41.6432 | 39.7547 | 39.6074 | 39.4568 | 39.3 | 39.1368 | 38.9674 | 38.7316 | 38.3768 | 37.9589 | 37.5021 | 33.7853 | 32.5895 | 30.9621 | 40.6189 | 40.4779 | 40.3326 | 40.1811 | 40.0242 | 39.8611 | 39.6947 | 39.5316 | 39.3705 | 39.2042 | 35.8737 | 34.6716 | 33.0411
BRAMLEY (FLEE) | CAMBERLEY MAIN | SANDHURST | MINIMUM HEADROOM | SU 83597 60930 | YES | 0.44737 | 35.2989 | 34.7747 | 34.2453 | 33.6821 | 33.1042 | 32.4895 | 31.74 | 30.7874 | 29.8695 | 29.0105 | 24.9811 | 20.8042 | -12.9105 | 29.6779 | 28.6726 | 27.6821 | 26.6305 | 25.5389 | 24.4474 | 23.3137 | 22.2863 | 21.2905 | 20.3568 | 15.9305 | 11.2495 | 6.9368 | 30.6495 | 29.6663 | 28.6947 | 27.6653 | 26.5653 | 25.4579 | 24.3211 | 23.2947 | 22.2989 | 21.3663 | 16.9432 | 12.2663 | 7.9579
|  | SANDHURST | EE |  |  |  | 35.5011 | 35.0905 | 34.6558 | 34.1947 | 33.7137 | 33.2168 | 32.7379 | 32.2716 | 31.8084 | 31.1295 | 28.0116 | 24.7505 | 21.8074 | 30.1232 | 29.3484 | 28.5579 | 27.7337 | 26.8611 | 25.9916 | 25.1053 | 24.2768 | 23.4432 | 22.6758 | 19.2579 | 15.5916 | 12.2495 | 30.9263 | 30.3253 | 29.5505 | 28.7421 | 27.8874 | 27.0284 | 26.1284 | 25.2895 | 24.4495 | 23.6811 | 20.2653 | 16.6 | 13.2621
|  | SANDHURST | HT |  |  |  | 35.2989 | 34.7747 | 34.2453 | 33.6821 | 33.1042 | 32.4895 | 31.74 | 30.7874 | 29.8695 | 29.0105 | 24.9811 | 20.8042 | 16.9821 | 29.6779 | 28.6726 | 27.6821 | 26.6305 | 25.5389 | 24.4474 | 23.3137 | 22.2863 | 21.2905 | 20.3568 | 15.9305 | 11.2495 | 6.9368 | 30.6495 | 29.6663 | 28.6947 | 27.6653 | 26.5653 | 25.4579 | 24.3211 | 23.2947 | 22.2989 | 21.3663 | 16.9432 | 12.2663 | 7.9579
|  | SANDHURST | HE |  |  |  | 35.7853 | 35.5116 | 35.2074 | 34.8716 | 34.5116 | 34.1253 | 33.7568 | 33.4095 | 33.0842 | 32.8042 | 31.6516 | 29.3032 | -12.9105 | 30.7147 | 30.2516 | 29.7411 | 29.1789 | 28.5621 | 27.9253 | 27.2695 | 26.6663 | 26.0642 | 25.5274 | 23.22 | 20.5526 | 18.1474 | 31.2295 | 30.9432 | 30.6263 | 30.1537 | 29.5484 | 28.9221 | 28.2779 | 27.6863 | 27.0968 | 26.5632 | 24.2253 | 21.5611 | 19.1589
|  | SANDHURST | CF |  |  |  | 35.9474 | 35.7937 | 35.6337 | 35.4695 | 35.2979 | 35.12 | 34.9389 | 34.7611 | 34.5853 | 34.4095 | 33.6242 | 32.8832 | 31.5116 | 30.8958 | 30.7221 | 30.4295 | 30.1158 | 29.7811 | 29.4411 | 29.0768 | 28.7253 | 28.3537 | 27.9895 | 26.2137 | 24.4242 | 22.8505 | 31.4 | 31.2379 | 31.0684 | 30.8958 | 30.7147 | 30.4158 | 30.0589 | 29.7147 | 29.3526 | 28.9958 | 27.2453 | 25.4316 | 23.8589
FAWLEY GSP | COWES & WOOTTON COMMON BSP | SANDOWN | MINIMUM HEADROOM | SZ 59877 85052 | YES | 0.26421 | 18.0295 | 17.7537 | 17.4758 | 17.18 | 16.8747 | 16.5611 | 16.2432 | 15.9653 | 15.5032 | 14.9305 | 12.1221 | 9.5516 | -8.9842 | 15.2368 | 14.6547 | 14.0611 | 13.4442 | 12.8821 | 12.2579 | 11.6011 | 10.9642 | 10.3463 | 9.7263 | 6.6042 | 3.7116 | 1.0905 | 15.8568 | 15.4337 | 14.8305 | 14.2032 | 13.6326 | 12.9979 | 12.3316 | 11.6832 | 11.0526 | 10.4211 | 7.2884 | 4.3937 | 1.7716
|  | SANDOWN | EE |  |  |  | 18.1326 | 17.9168 | 17.6874 | 17.4432 | 17.1884 | 16.9253 | 16.6705 | 16.4295 | 16.1968 | 15.9895 | 14.1263 | 12.0947 | 10.3 | 15.3853 | 15.0095 | 14.5242 | 13.9926 | 13.5253 | 13.0516 | 12.5474 | 12.0495 | 11.6063 | 11.1474 | 8.8368 | 6.54 | 4.4989 | 15.9653 | 15.7379 | 15.3021 | 14.76 | 14.2863 | 13.8063 | 13.2937 | 12.7874 | 12.3368 | 11.8705 | 9.5189 | 7.2221 | 5.18
|  | SANDOWN | HT |  |  |  | 18.0295 | 17.7537 | 17.4758 | 17.18 | 16.8747 | 16.5611 | 16.2432 | 15.9653 | 15.5032 | 14.9305 | 12.1221 | 9.5516 | 7.2368 | 15.2368 | 14.6547 | 14.0611 | 13.4442 | 12.8821 | 12.2579 | 11.6011 | 10.9642 | 10.3463 | 9.7263 | 6.6042 | 3.7116 | 1.0905 | 15.8568 | 15.4337 | 14.8305 | 14.2032 | 13.6326 | 12.9979 | 12.3316 | 11.6832 | 11.0526 | 10.4211 | 7.2884 | 4.3937 | 1.7716
|  | SANDOWN | HE |  |  |  | 18.2779 | 18.1295 | 17.9663 | 17.7853 | 17.5895 | 17.3821 | 17.1821 | 16.9958 | 16.8211 | 16.6695 | 16.0126 | 14.4768 | -8.9842 | 15.5305 | 15.3821 | 15.1368 | 14.7421 | 14.4105 | 14.0474 | 13.6684 | 13.2947 | 12.9705 | 12.6126 | 10.8642 | 9.1368 | 7.6126 | 16.1105 | 15.9621 | 15.7916 | 15.5179 | 15.1874 | 14.8189 | 14.4337 | 14.0547 | 13.7253 | 13.3611 | 11.5726 | 9.8211 | 8.2958
|  | SANDOWN | CF |  |  |  | 18.3632 | 18.28 | 18.1937 | 18.1032 | 18.0105 | 17.9147 | 17.8158 | 17.72 | 17.6232 | 17.5274 | 17.1021 | 16.8895 | 16.2253 | 15.6158 | 15.5326 | 15.4463 | 15.3305 | 15.1105 | 14.8642 | 14.6063 | 14.36 | 14.1295 | 13.9032 | 13.0705 | 11.98 | 11.0221 | 16.1958 | 16.1126 | 16.0263 | 15.9316 | 15.8316 | 15.6421 | 15.3821 | 15.1305 | 14.8958 | 14.6653 | 13.82 | 12.7011 | 11.7158
LOVEDEAN GSP | CHICHESTER & HUNSTON | SELSEY | MINIMUM HEADROOM | SZ 85667 94289 | YES | 11.1042 | 6.9884 | 6.7547 | 6.52 | 6.2642 | 5.9884 | 5.6537 | 5.22 | 4.8442 | 4.4337 | 4.0053 | 2.0958 | 0.026316 | -13.3726 | 3.8168 | 3.3884 | 2.9674 | 2.4768 | 1.9937 | 2.2011 | 1.7379 | 1.3368 | 0.89158 | 0.42211 | -1.6874 | -4.02 | -6.1611 | 4.9063 | 4.5221 | 4.0968 | 3.5989 | 3.1105 | 2.6168 | 2.1547 | 1.7537 | 1.3084 | 0.84 | -1.2674 | -3.5968 | -5.7347
|  | SELSEY | EE |  |  |  | 7.08 | 6.8989 | 6.7074 | 6.5032 | 6.2905 | 6.3368 | 6.0084 | 5.6958 | 5.3642 | 5.0211 | 3.5705 | 1.9495 | 0.48737 | 4.0095 | 3.6811 | 3.3463 | 2.9611 | 2.5895 | 2.9495 | 2.6 | 2.2663 | 1.9105 | 1.5358 | -0.062105 | -1.8968 | -3.5642 | 5.0042 | 4.8126 | 4.4811 | 4.0895 | 3.7147 | 3.3642 | 3.0147 | 2.6821 | 2.3263 | 1.9516 | 0.35579 | -1.4758 | -3.14
|  | SELSEY | HT |  |  |  | 6.9884 | 6.7547 | 6.52 | 6.2642 | 5.9884 | 5.6537 | 5.22 | 4.8442 | 4.4337 | 4.0053 | 2.0958 | 0.026316 | -1.8621 | 3.8168 | 3.3884 | 2.9674 | 2.4768 | 1.9937 | 2.2011 | 1.7379 | 1.3368 | 0.89158 | 0.42211 | -1.6874 | -4.02 | -6.1611 | 4.9063 | 4.5221 | 4.0968 | 3.5989 | 3.1105 | 2.6168 | 2.1547 | 1.7537 | 1.3084 | 0.84 | -1.2674 | -3.5968 | -5.7347
|  | SELSEY | HE |  |  |  | 7.2053 | 7.0842 | 6.9505 | 6.8021 | 6.6421 | 6.4726 | 6.3105 | 6.1568 | 6.0137 | 5.8821 | 5.1747 | 3.9516 | -13.3726 | 4.2695 | 4.0642 | 3.8495 | 3.5768 | 3.3137 | 3.04 | 2.8021 | 2.5768 | 2.3337 | 2.0716 | 1.6863 | 0.28842 | -0.96421 | 5.1389 | 5.0126 | 4.8726 | 4.7147 | 4.4484 | 4.1716 | 3.9316 | 3.7042 | 3.4589 | 3.1937 | 2.1021 | 0.70737 | -0.54421
|  | SELSEY | CF |  |  |  | 7.28 | 7.2137 | 7.1453 | 7.0737 | 7 | 6.9242 | 6.8463 | 6.7695 | 6.6937 | 6.6179 | 6.2695 | 5.7463 | 5.0589 | 4.4053 | 4.2832 | 4.1589 | 4.0179 | 3.8768 | 3.7263 | 3.5895 | 3.4537 | 3.32 | 3.1674 | 2.4253 | 2.2453 | 1.4537 | 5.2189 | 5.1484 | 5.0758 | 4.9989 | 4.9211 | 4.84 | 4.7263 | 4.5895 | 4.4537 | 4.2979 | 3.5463 | 2.6621 | 1.8716
MANNINGTON GSP | SHAFTESBURY BSP | SHAFTESBURY | MINIMUM HEADROOM | ST 85605 23325 | YES | 0.62 | 15.3568 | 15.1021 | 14.5158 | 14.0137 | 13.1926 | 12.3853 | 11.8242 | 11.4242 | 11.0453 | 10.6779 | 8.5979 | 6.9316 | -9.7579 | 11.4368 | 10.8337 | 10.1695 | 9.6232 | 8.7053 | 7.8253 | 7.2305 | 6.8126 | 6.4189 | 6.0368 | 3.8358 | 2.0884 | 0.083158 | 12.4084 | 11.8853 | 11.2232 | 10.6674 | 9.7295 | 8.8253 | 8.2168 | 7.7895 | 7.3853 | 6.9926 | 4.7158 | 2.8947 | 0.85158
|  | SHAFTESBURY | EE |  |  |  | 15.4484 | 15.2453 | 14.8653 | 14.4389 | 13.6926 | 12.9642 | 12.48 | 12.1305 | 11.7884 | 11.4684 | 9.9979 | 8.4053 | 6.9558 | 11.6284 | 11.1253 | 10.5484 | 10.0842 | 9.2484 | 8.5505 | 8.0295 | 7.6674 | 7.3137 | 6.9832 | 5.4674 | 3.7874 | 2.1768 | 12.5758 | 12.1432 | 11.6084 | 11.1368 | 10.2811 | 9.4547 | 8.9274 | 8.5568 | 8.1958 | 7.8568 | 6.2789 | 4.5305 | 2.8979
|  | SHAFTESBURY | HT |  |  |  | 15.3568 | 15.1021 | 14.5158 | 14.0137 | 13.1926 | 12.3853 | 11.8242 | 11.4242 | 11.0453 | 10.6779 | 8.5979 | 6.9316 | 5.1116 | 11.4368 | 10.8337 | 10.1695 | 9.6232 | 8.7053 | 7.8253 | 7.2305 | 6.8126 | 6.4189 | 6.0368 | 3.8358 | 2.0884 | 0.083158 | 12.4084 | 11.8853 | 11.2232 | 10.6674 | 9.7295 | 8.8253 | 8.2168 | 7.7895 | 7.3853 | 6.9926 | 4.7158 | 2.8947 | 0.85158
|  | SHAFTESBURY | HE |  |  |  | 15.5811 | 15.44 | 15.2832 | 15.0105 | 14.3674 | 13.7389 | 13.3674 | 13.1263 | 12.8979 | 12.6905 | 11.8053 | 10.8263 | -9.7579 | 11.8958 | 11.5242 | 11.0811 | 10.7021 | 9.9779 | 9.2789 | 8.8768 | 8.6274 | 8.3905 | 8.1779 | 7.2621 | 6.2084 | 5.0621 | 12.7053 | 12.4947 | 12.1168 | 11.7653 | 11.0232 | 10.3053 | 9.8937 | 9.6368 | 9.3958 | 9.1779 | 8.2284 | 7.1347 | 5.9442
|  | SHAFTESBURY | CF |  |  |  | 15.6589 | 15.58 | 15.4968 | 15.4137 | 15.3189 | 15.0768 | 14.8726 | 14.7274 | 14.5853 | 14.4432 | 13.7916 | 13.1705 | 12.5074 | 12.0726 | 11.8589 | 11.6242 | 11.4253 | 11.0905 | 10.7653 | 10.5421 | 10.3895 | 10.2389 | 10.0874 | 9.3989 | 8.72 | 7.9863 | 12.7821 | 12.7053 | 12.5842 | 12.4116 | 12.1326 | 11.8253 | 11.5968 | 11.44 | 11.2863 | 11.1316 | 10.4274 | 9.7253 | 8.9621
FAWLEY GSP | COWES & WOOTTON COMMON BSP | SHALFLEET | MINIMUM HEADROOM | SZ 40828 88643 | YES | 0.11579 | 16.4432 | 16.1926 | 15.9411 | 15.6863 | 15.4232 | 15.1063 | 12.3095 | 9.3189 | 9.1368 | 8.9611 | 7.7021 | 6.2632 | 5.0337 | 14.7179 | 14.4474 | 14.1789 | 13.9074 | 13.6263 | 13.2989 | 9.8074 | 6.34 | 6.1716 | 6.0095 | 4.7684 | 3.3221 | 2.7884 | 14.9968 | 14.8305 | 14.5611 | 14.2884 | 14.0074 | 13.6705 | 10.0326 | 6.5526 | 6.3705 | 6.1947 | 4.8621 | 3.3084 | 2.7326
|  | SHALFLEET | EE |  |  |  | 16.5579 | 16.3653 | 16.1642 | 15.9516 | 15.7368 | 15.48 | 15.2011 | 14.9253 | 14.6579 | 13.7211 | 10.9989 | 7.7368 | 6.9547 | 14.8421 | 14.6347 | 14.4211 | 14.1947 | 13.9663 | 13.7063 | 13.4242 | 13.1484 | 12.8853 | 11.58 | 8.6684 | 5.1358 | 4.3274 | 14.9968 | 15.0179 | 14.8032 | 14.5758 | 14.3453 | 14.0747 | 13.7789 | 13.4863 | 13.2063 | 11.7484 | 8.7074 | 5.0242 | 4.1695
|  | SHALFLEET | HT |  |  |  | 16.4432 | 16.1926 | 15.9411 | 15.6863 | 15.4232 | 15.1063 | 12.3095 | 9.3189 | 9.1368 | 8.9611 | 7.7021 | 6.2632 | 5.7074 | 14.7179 | 14.4474 | 14.1789 | 13.9074 | 13.6263 | 13.2989 | 9.8074 | 6.34 | 6.1716 | 6.0095 | 4.7684 | 3.3221 | 2.7884 | 15.1011 | 14.8305 | 14.5611 | 14.2884 | 14.0074 | 13.6705 | 10.0326 | 6.5526 | 6.3705 | 6.1947 | 4.8621 | 3.3084 | 2.7326
|  | SHALFLEET | HE |  |  |  | 16.7116 | 16.5916 | 16.4663 | 16.3295 | 16.1811 | 15.9916 | 15.8042 | 15.6189 | 14.7853 | 14.6137 | 12.1895 | 9.6105 | 5.0337 | 15.0095 | 14.8811 | 14.7474 | 14.6021 | 14.4453 | 14.2516 | 14.0621 | 13.8737 | 12.6674 | 12.4916 | 9.7811 | 6.8484 | 6.2242 | 15.1579 | 15.2642 | 15.1305 | 14.9853 | 14.8274 | 14.6263 | 14.4295 | 14.2337 | 12.8853 | 12.7021 | 9.9368 | 6.9611 | 6.2989
|  | SHALFLEET | CF |  |  |  | 16.7926 | 16.7253 | 16.6526 | 16.5716 | 16.4811 | 16.3705 | 16.2568 | 16.1474 | 16.04 | 15.9411 | 15.5168 | 15.0421 | 14.6179 | 15.0968 | 15.0232 | 14.9453 | 14.8568 | 14.7589 | 14.6421 | 14.5242 | 14.4074 | 14.2968 | 14.1916 | 13.7579 | 13.2558 | 12.8116 | 15.2421 | 15.1716 | 15.3284 | 15.24 | 15.1421 | 15.0221 | 14.8989 | 14.7789 | 14.6653 | 14.5568 | 14.1053 | 13.5811 | 13.1116
FAWLEY GSP | COWES & WOOTTON COMMON BSP | SHANKLIN | MINIMUM HEADROOM | SZ 57809 81912 | YES | 0.36737 | 30.4295 | 29.88 | 29.3347 | 28.7832 | 28.2 | 27.5442 | 26.8621 | 26.2 | 25.5611 | 24.9263 | 21.7895 | 18.8842 | 6.1463 | 27.2105 | 26.6189 | 26.0337 | 25.4432 | 24.8168 | 24.1179 | 23.3874 | 22.6747 | 21.9853 | 21.2968 | 18.1032 | 14.9789 | 12.2411 | 27.7347 | 27.1432 | 26.5568 | 25.9653 | 25.34 | 24.6347 | 23.8989 | 23.18 | 22.4832 | 21.7874 | 18.32 | 15.0863 | 12.2842
|  | SHANKLIN | EE |  |  |  | 30.6726 | 30.2505 | 29.8168 | 29.3547 | 28.8758 | 28.3705 | 27.8337 | 27.2958 | 26.8032 | 26.3063 | 30.7242 | 29.8558 | 28.7632 | 27.4158 | 26.9684 | 26.5116 | 26.0221 | 25.5158 | 24.9884 | 24.4263 | 23.8621 | 23.3505 | 22.8305 | 20.88 | 17.8011 | 15.6442 | 27.8032 | 27.3747 | 26.9253 | 26.4463 | 25.9495 | 25.4263 | 24.8684 | 24.3095 | 23.7979 | 23.28 | 24.2221 | 22.7242 | 21.6305
|  | SHANKLIN | HT |  |  |  | 30.4295 | 29.88 | 29.3347 | 28.7832 | 28.2 | 27.5442 | 26.8621 | 26.2 | 25.5611 | 24.9263 | 21.7895 | 18.8842 | 16.3926 | 27.2105 | 26.6189 | 26.0337 | 25.4432 | 24.8168 | 24.1179 | 23.3874 | 22.6747 | 21.9853 | 21.2968 | 18.1032 | 14.9789 | 12.2411 | 27.7347 | 27.1432 | 26.5568 | 25.9653 | 25.34 | 24.6347 | 23.8989 | 23.18 | 22.4832 | 21.7874 | 18.32 | 15.0863 | 12.2842
|  | SHANKLIN | HE |  |  |  | 30.9968 | 30.7284 | 30.4463 | 30.1295 | 29.7863 | 29.4011 | 29.0074 | 28.6179 | 28.2716 | 27.9053 | 31.9811 | 31.5663 | 6.1463 | 27.7632 | 27.48 | 27.1832 | 26.8505 | 26.4905 | 26.0895 | 25.6768 | 25.2663 | 24.9053 | 24.5168 | 23.8884 | 21.5147 | 20.0432 | 28.1105 | 27.8526 | 27.5811 | 27.2547 | 26.9011 | 26.5032 | 26.0947 | 25.6905 | 25.3316 | 24.9474 | 25.92 | 25.0095 | 24.2663
|  | SHANKLIN | CF |  |  |  | 31.1811 | 31.0189 | 30.8463 | 30.6474 | 30.4295 | 30.18 | 29.9221 | 29.6737 | 29.44 | 29.2126 | 28.3263 | 27.2674 | 26.3347 | 27.9611 | 27.7874 | 27.6042 | 27.5642 | 27.3274 | 27.0611 | 26.7832 | 26.5168 | 26.2674 | 26.0232 | 25.0895 | 23.9253 | 22.8947 | 28.2863 | 28.1305 | 27.9663 | 28.1537 | 27.9758 | 27.7758 | 27.5684 | 27.3684 | 27.1779 | 26.9916 | 26.2411 | 24.26 | 23.1979
AXMINSTER | YEOVIL BSP | SHERBORNE | MINIMUM HEADROOM | ST 63978 18163 | YES | 0 | 14.6505 | 14.38 | 14.1074 | 13.8326 | 13.3768 | 13.0653 | 12.5032 | 11.9621 | 11.1147 | 10.1411 | 7.4611 | 5.9179 | -3.1074 | 15.2337 | 14.9484 | 14.6642 | 14.3758 | 13.8768 | 13.5463 | 12.8947 | 12.2653 | 11.2432 | 10.0568 | 6.9379 | 5.2674 | 3.6558 | 14.8305 | 14.6568 | 14.4821 | 14.2211 | 13.6979 | 13.3653 | 12.7232 | 12.1021 | 11.1021 | 9.9442 | 6.8516 | 5.1474 | 3.5505
|  | SHERBORNE | EE |  |  |  | 14.7632 | 14.5516 | 14.3305 | 14.1053 | 13.6968 | 13.4316 | 12.9095 | 12.3937 | 11.5579 | 10.5979 | 7.9979 | 6.6126 | 5.5084 | 15.3537 | 15.1316 | 14.8989 | 14.6642 | 14.2263 | 13.9589 | 13.3611 | 12.7663 | 11.7642 | 10.6011 | 7.6232 | 6.2 | 4.9305 | 14.8947 | 14.7589 | 14.6116 | 14.4568 | 14.0558 | 13.7737 | 13.1779 | 12.5874 | 11.6042 | 10.4632 | 7.4832 | 5.9905 | 4.7242
|  | SHERBORNE | HT |  |  |  | 14.6505 | 14.38 | 14.1074 | 13.8326 | 13.3768 | 13.0653 | 12.5032 | 11.9621 | 11.1147 | 10.1411 | 7.4611 | 5.9179 | 4.5305 | 15.2337 | 14.9484 | 14.6642 | 14.3758 | 13.8768 | 13.5463 | 12.8947 | 12.2653 | 11.2432 | 10.0568 | 6.9379 | 5.2674 | 3.6558 | 14.8305 | 14.6568 | 14.4821 | 14.2211 | 13.6979 | 13.3653 | 12.7232 | 12.1021 | 11.1021 | 9.9442 | 6.8516 | 5.1474 | 3.5505
|  | SHERBORNE | HE |  |  |  | 14.9189 | 14.78 | 14.6316 | 14.4758 | 14.1347 | 13.9379 | 13.5011 | 13.0705 | 12.3305 | 11.4684 | 9.4242 | 8.6842 | -3.1074 | 15.5189 | 15.3726 | 15.2179 | 15.0568 | 14.6884 | 14.4916 | 14.0211 | 13.5126 | 12.6063 | 11.54 | 9.0979 | 8.2747 | 7.3347 | 14.9863 | 14.8905 | 14.7874 | 14.6737 | 14.5221 | 14.3379 | 13.8326 | 13.3326 | 12.4495 | 11.4126 | 9.0084 | 8.1768 | 7.24
|  | SHERBORNE | CF |  |  |  | 14.9979 | 14.9105 | 14.8221 | 14.7305 | 14.5642 | 14.4547 | 14.2347 | 14.0042 | 13.5937 | 13.0811 | 11.7253 | 11.2389 | 10.7179 | 15.6011 | 15.5095 | 15.4168 | 15.32 | 15.1411 | 15.0305 | 14.7947 | 14.5474 | 14.0726 | 13.4358 | 11.8021 | 11.2558 | 10.6537 | 15.0368 | 14.98 | 14.9221 | 14.8611 | 14.7874 | 14.7116 | 14.6158 | 14.3811 | 13.8905 | 13.2726 | 11.6768 | 11.1274 | 10.5263
MINETY GSP | CIRENCESTER BSP | SHIPTON OLIFFE | MINIMUM HEADROOM | SP 03884 19102 | YES | 0 | 4.9253 | 4.8526 | 4.7695 | 4.68 | 4.5884 | 4.4926 | 4.3968 | 4.3074 | 4.2253 | 4.1537 | 3.7653 | 3.3726 | -0.94 | 4.0168 | 3.9284 | 3.8368 | 3.7379 | 3.6379 | 3.5316 | 3.4253 | 3.3274 | 3.2347 | 3.1579 | 2.7158 | 2.2558 | 1.8432 | 4.1832 | 4.0937 | 4.0011 | 3.9 | 3.7989 | 3.6905 | 3.5832 | 3.4832 | 3.3895 | 3.3105 | 2.8589 | 2.3926 | 1.9737
|  | SHIPTON OLIFFE | EE |  |  |  | 4.9432 | 4.9053 | 4.8411 | 4.7705 | 4.6989 | 4.6263 | 4.5558 | 4.4884 | 4.4242 | 4.3684 | 4.0621 | 3.7516 | 3.4811 | 4.0558 | 3.9863 | 3.9158 | 3.8389 | 3.7611 | 3.6821 | 3.6042 | 3.5305 | 3.4611 | 3.4 | 3.0516 | 2.6895 | 2.3684 | 4.2232 | 4.1526 | 4.0811 | 4.0032 | 3.9242 | 3.8432 | 3.7653 | 3.6905 | 3.6189 | 3.5579 | 3.2021 | 2.8305 | 2.5053
|  | SHIPTON OLIFFE | HT |  |  |  | 4.9253 | 4.8526 | 4.7695 | 4.68 | 4.5884 | 4.4926 | 4.3968 | 4.3074 | 4.2253 | 4.1537 | 3.7653 | 3.3726 | 3.0221 | 4.0168 | 3.9284 | 3.8368 | 3.7379 | 3.6379 | 3.5316 | 3.4253 | 3.3274 | 3.2347 | 3.1579 | 2.7158 | 2.2558 | 1.8432 | 4.1832 | 4.0937 | 4.0011 | 3.9 | 3.7989 | 3.6905 | 3.5832 | 3.4832 | 3.3895 | 3.3105 | 2.8589 | 2.3926 | 1.9737
|  | SHIPTON OLIFFE | HE |  |  |  | 4.9684 | 4.9442 | 4.9189 | 4.8863 | 4.8337 | 4.78 | 4.7284 | 4.6779 | 4.6316 | 4.5937 | 4.3695 | 4.1316 | -0.94 | 4.1095 | 4.0653 | 4.02 | 3.9674 | 3.9105 | 3.8516 | 3.7958 | 3.74 | 3.6905 | 3.6495 | 3.3926 | 3.1116 | 2.8705 | 4.2779 | 4.2326 | 4.1874 | 4.1337 | 4.0758 | 4.0168 | 3.96 | 3.9032 | 3.8526 | 3.8105 | 3.5484 | 3.26 | 3.0137
|  | SHIPTON OLIFFE | CF |  |  |  | 4.9832 | 4.9705 | 4.9568 | 4.9432 | 4.9284 | 4.9137 | 4.8937 | 4.8674 | 4.8379 | 4.8147 | 4.6579 | 4.5053 | 4.3821 | 4.1358 | 4.1126 | 4.0874 | 4.06 | 4.0316 | 4.0032 | 3.9747 | 3.9453 | 3.9126 | 3.8874 | 3.7105 | 3.5305 | 3.3832 | 4.3053 | 4.2811 | 4.2558 | 4.2274 | 4.1979 | 4.1695 | 4.14 | 4.1116 | 4.0779 | 4.0526 | 3.8716 | 3.6874 | 3.5358
NURSLING GSP | SOUTHAMPTON (2 X 90) | SHIRLEY | MINIMUM HEADROOM | SU 39988 13808 | YES | 0.19789 | 34.9358 | 34.5979 | 34.2337 | 33.8284 | 33.4084 | 32.9853 | 32.4779 | 31.9958 | 31.5389 | 31.0189 | 27.3789 | 24.3558 | -1.3274 | 30.3421 | 29.8053 | 29.2053 | 28.4442 | 27.6695 | 26.9905 | 26.3211 | 25.7137 | 25.1274 | 24.4642 | 20.3968 | 17.0053 | 13.8916 | 31.0537 | 30.6979 | 30.2916 | 29.5179 | 28.7316 | 28.0432 | 27.3653 | 26.7495 | 26.1547 | 25.48 | 21.4168 | 18.0295 | 14.92
|  | SHIRLEY | EE |  |  |  | 35.0674 | 34.8032 | 34.5242 | 34.2042 | 33.8589 | 33.4916 | 33.1305 | 32.7337 | 32.3337 | 31.9758 | 29.54 | 27.1895 | 25.0821 | 30.5621 | 30.1663 | 29.7326 | 29.1768 | 28.5716 | 27.8495 | 27.1158 | 26.5916 | 26.0895 | 25.6411 | 22.7811 | 20.1347 | 17.7442 | 31.1947 | 30.9168 | 30.6242 | 30.2632 | 29.6495 | 28.9147 | 28.1674 | 27.6358 | 27.1274 | 26.6737 | 23.7979 | 21.1547 | 18.7684
|  | SHIRLEY | HT |  |  |  | 34.9358 | 34.5979 | 34.2337 | 33.8284 | 33.4084 | 32.9853 | 32.4779 | 31.9958 | 31.5389 | 31.0189 | 27.3789 | 24.3558 | 21.5968 | 30.3421 | 29.8053 | 29.2053 | 28.4442 | 27.6695 | 26.9905 | 26.3211 | 25.7137 | 25.1274 | 24.4642 | 20.3968 | 17.0053 | 13.8916 | 31.0537 | 30.6979 | 30.2916 | 29.5179 | 28.7316 | 28.0432 | 27.3653 | 26.7495 | 26.1547 | 25.48 | 21.4168 | 18.0295 | 14.92
|  | SHIRLEY | HE |  |  |  | 35.2263 | 35.0358 | 34.8242 | 34.5905 | 34.3389 | 34.0474 | 33.7558 | 33.5 | 33.2621 | 33.0568 | 32.0053 | 30.5211 | -1.3274 | 30.7642 | 30.5558 | 30.2863 | 29.9379 | 29.5453 | 29.0074 | 28.4137 | 28.0432 | 27.6937 | 27.3926 | 25.6274 | 23.8221 | 22.1379 | 31.3663 | 31.1684 | 30.9484 | 30.7021 | 30.4389 | 30.0926 | 29.4895 | 29.1147 | 28.7611 | 28.4568 | 26.6568 | 24.8379 | 23.1568
|  | SHIRLEY | CF |  |  |  | 35.3211 | 35.2042 | 35.0842 | 34.9589 | 34.8295 | 34.6958 | 34.5589 | 34.4253 | 34.2916 | 34.1484 | 33.4884 | 32.9926 | 32.28 | 30.8705 | 30.7389 | 30.6053 | 30.4474 | 30.2632 | 30.0726 | 29.8811 | 29.66 | 29.4421 | 29.2242 | 27.9874 | 26.8116 | 25.7116 | 31.4663 | 31.3432 | 31.2168 | 31.0863 | 30.9505 | 30.8105 | 30.6684 | 30.5274 | 30.3863 | 30.2474 | 29.0579 | 27.8537 | 26.7263
MINETY GSP | STRATTON (2 X 60) | SHRIVENHAM | MINIMUM HEADROOM | SU 23782 87902 | YES | 0.18105 | 16.5326 | 16.4358 | 16.3389 | 16.2347 | 16.1295 | 16.02 | 15.9105 | 15.8137 | 13.2316 | 13.1432 | 12.7042 | 11.6242 | 3.0358 | 14.8695 | 14.5042 | 14.3 | 14.1116 | 13.9211 | 13.7295 | 13.5411 | 13.3674 | 11.2305 | 11.1095 | 10.6074 | 9.3758 | 9.1979 | 15.4389 | 15.0863 | 14.8821 | 14.6937 | 14.5032 | 14.3116 | 14.1232 | 13.9495 | 11.1979 | 11.0789 | 10.5747 | 9.3063 | 9.1263
|  | SHRIVENHAM | EE |  |  |  | 16.5705 | 16.4958 | 16.4147 | 16.3305 | 16.2432 | 16.1516 | 16.0642 | 15.9821 | 13.2316 | 13.1432 | 12.7042 | 11.6242 | 11.4537 | 14.9537 | 14.6326 | 14.4642 | 14.3158 | 14.16 | 14.0011 | 13.8505 | 13.7063 | 11.2305 | 11.1095 | 10.6105 | 9.3758 | 9.1979 | 15.52 | 15.2147 | 15.0463 | 14.8968 | 14.7411 | 14.5832 | 14.4326 | 14.2884 | 11.1979 | 11.0789 | 10.5747 | 9.3063 | 9.1263
|  | SHRIVENHAM | HT |  |  |  | 16.5326 | 16.4358 | 16.3389 | 16.2347 | 16.1295 | 16.02 | 15.9105 | 15.8137 | 13.5484 | 13.4137 | 12.8442 | 12.2684 | 11.6074 | 14.8695 | 14.5042 | 14.3 | 14.1116 | 13.9211 | 13.7295 | 13.5411 | 13.3674 | 11.3495 | 11.2053 | 10.6074 | 9.9726 | 9.2284 | 15.4389 | 15.0863 | 14.8821 | 14.6937 | 14.5032 | 14.3116 | 14.1232 | 13.9495 | 11.4326 | 11.2874 | 10.6368 | 10.0021 | 9.2579
|  | SHRIVENHAM | HE |  |  |  | 16.6242 | 16.5737 | 16.5189 | 16.4579 | 16.3926 | 16.3232 | 16.2558 | 16.1926 | 14.8621 | 14.8126 | 14.6432 | 13.5484 | 3.0358 | 15.0695 | 14.8011 | 14.6874 | 14.5884 | 14.4789 | 14.3684 | 14.2589 | 14.1568 | 12.9 | 12.82 | 12.5126 | 10.9937 | 10.8853 | 15.6316 | 15.3789 | 15.2695 | 15.1705 | 15.0611 | 14.9495 | 14.8411 | 14.7379 | 13.1653 | 13.0863 | 12.7768 | 11.2295 | 11.1211
|  | SHRIVENHAM | CF |  |  |  | 16.6547 | 16.6274 | 16.6 | 16.5705 | 16.54 | 16.5095 | 16.4779 | 16.4463 | 15.1442 | 15.1126 | 14.9747 | 14.9063 | 14.8695 | 15.1832 | 15.0379 | 14.9737 | 14.9168 | 14.8558 | 14.7968 | 14.7337 | 14.6726 | 13.4432 | 13.3842 | 13.1189 | 12.9337 | 12.7021 | 15.6937 | 15.6011 | 15.54 | 15.4853 | 15.4274 | 15.3695 | 15.3095 | 15.2495 | 13.6968 | 13.6389 | 13.38 | 13.1989 | 12.9642
MANNINGTON GSP | SHAFTESBURY BSP | SHROTON | MINIMUM HEADROOM | ST 85356 13659 | YES | 0.16316 | 25.6453 | 25.0758 | 24.4863 | 23.8653 | 22.9663 | 22.0568 | 21.64 | 21.26 | 18.9979 | 18.7874 | 16.7463 | 14.2105 | -0.56211 | 22.9884 | 22.3695 | 21.7305 | 21.0589 | 20.0705 | 19.0758 | 18.6432 | 18.2474 | 15.6705 | 15.4663 | 13.28 | 10.4947 | 9.6484 | 23.0768 | 22.5084 | 21.92 | 21.2484 | 20.2368 | 19.2158 | 18.7737 | 18.3684 | 15.7516 | 15.5411 | 13.3032 | 10.4516 | 9.5821
|  | SHROTON | EE |  |  |  | 25.8221 | 25.3442 | 24.8337 | 24.2947 | 23.4747 | 22.6358 | 22.2947 | 21.9663 | 21.6463 | 21.3474 | 20.0347 | 18.5116 | 16.9895 | 23.1779 | 22.6589 | 22.1063 | 21.5189 | 20.6137 | 19.6947 | 19.3432 | 19.0063 | 18.6768 | 18.3726 | 17.0368 | 15.4379 | 13.7516 | 23.2537 | 22.7768 | 22.2674 | 21.7158 | 20.7863 | 19.8411 | 19.4811 | 19.1326 | 18.7937 | 18.4779 | 17.0768 | 15.3989 | 13.6758
|  | SHROTON | HT |  |  |  | 25.6453 | 25.0758 | 24.4863 | 23.8653 | 22.9663 | 22.0568 | 21.64 | 21.26 | 18.9979 | 18.7874 | 16.7463 | 14.2105 | 13.3958 | 22.9884 | 22.3695 | 21.7305 | 21.0589 | 20.0705 | 19.0758 | 18.6432 | 18.2474 | 15.6705 | 15.4663 | 13.28 | 10.4947 | 9.6484 | 23.0768 | 22.5084 | 21.92 | 21.2484 | 20.2368 | 19.2158 | 18.7737 | 18.3684 | 15.7516 | 15.5411 | 13.3032 | 10.4516 | 9.5821
|  | SHROTON | HE |  |  |  | 26.0705 | 25.7063 | 25.3116 | 24.8821 | 24.1632 | 23.4242 | 23.1884 | 22.9642 | 22.7516 | 22.5611 | 21.7989 | 20.7863 | -0.56211 | 23.4421 | 23.0442 | 22.6137 | 22.1432 | 21.3453 | 20.5316 | 20.2884 | 20.0579 | 19.8389 | 19.6432 | 18.8611 | 17.7632 | 16.4274 | 23.5011 | 23.1389 | 22.7453 | 22.3147 | 21.5347 | 20.6968 | 20.4495 | 20.2147 | 19.9895 | 19.7905 | 18.9789 | 17.8411 | 16.4726
|  | SHROTON | CF |  |  |  | 26.2389 | 26.0379 | 25.8305 | 25.6179 | 25.2905 | 24.9632 | 24.8284 | 24.6968 | 24.5653 | 24.4337 | 23.8295 | 23.2653 | 22.6737 | 23.6253 | 23.4042 | 23.1779 | 22.9442 | 22.5821 | 22.2211 | 22.0811 | 21.9432 | 21.8042 | 21.6663 | 21.0326 | 20.4263 | 19.7789 | 23.6705 | 23.4695 | 23.2621 | 23.0495 | 22.7242 | 22.3979 | 22.2632 | 22.1326 | 22.0011 | 21.8611 | 21.2116 | 20.5853 | 19.9116
LALEHAM | STAINES | SIDNEY ROAD | MINIMUM HEADROOM | TQ 04100 71760 | YES | 0.042105 | 34.2516 | 34.0189 | 33.7842 | 33.5347 | 33.2758 | 33.0095 | 32.7411 | 32.5053 | 32.2905 | 32.0789 | 30.42 | 28.7074 | 6.3979 | 30.7137 | 30.2358 | 29.5358 | 28.9853 | 28.5379 | 28.0968 | 27.6589 | 27.2537 | 26.8737 | 26.5042 | 24.28 | 22.2747 | 20.3916 | 31.4274 | 31.1716 | 30.8537 | 30.3084 | 29.8653 | 29.4274 | 28.9937 | 28.5905 | 28.2147 | 27.8484 | 25.6074 | 23.6053 | 21.7242
|  | SIDNEY ROAD | EE |  |  |  | 34.3421 | 34.16 | 33.9684 | 33.7632 | 33.5495 | 33.3274 | 33.1137 | 32.9095 | 32.7137 | 32.5389 | 31.6432 | 30.3232 | 29.1358 | 30.8105 | 30.5389 | 29.9295 | 29.4684 | 29.1084 | 28.7495 | 28.4032 | 28.0653 | 27.74 | 27.4274 | 25.6547 | 24.1095 | 22.6937 | 31.5253 | 31.3221 | 31.1053 | 30.7874 | 30.4305 | 30.0737 | 29.7305 | 29.3947 | 29.0716 | 28.7621 | 26.9905 | 25.4379 | 24.0242
|  | SIDNEY ROAD | HT |  |  |  | 34.2516 | 34.0189 | 33.7842 | 33.5347 | 33.2758 | 33.0095 | 32.7411 | 32.5053 | 32.2905 | 32.0789 | 30.42 | 28.7074 | 27.1168 | 30.7137 | 30.2358 | 29.5358 | 28.9853 | 28.5379 | 28.0968 | 27.6589 | 27.2537 | 26.8737 | 26.5042 | 24.28 | 22.2747 | 20.3916 | 31.4274 | 31.1716 | 30.8537 | 30.3084 | 29.8653 | 29.4274 | 28.9937 | 28.5905 | 28.2147 | 27.8484 | 25.6074 | 23.6053 | 21.7242
|  | SIDNEY ROAD | HE |  |  |  | 34.46 | 34.3337 | 34.1947 | 34.04 | 33.8747 | 33.6979 | 33.5284 | 33.3695 | 33.2211 | 33.0926 | 32.6589 | 32.2632 | 6.3979 | 30.9368 | 30.7937 | 30.44 | 30.0926 | 29.8432 | 29.5853 | 29.3389 | 29.1 | 28.8758 | 28.6632 | 27.3758 | 26.3021 | 25.3453 | 31.6516 | 31.5084 | 31.3484 | 31.1832 | 31.0126 | 30.8305 | 30.6547 | 30.4179 | 30.1947 | 29.9842 | 28.7137 | 27.64 | 26.6726
|  | SIDNEY ROAD | CF |  |  |  | 34.5274 | 34.4526 | 34.3758 | 34.2968 | 34.2137 | 34.1284 | 34.0421 | 33.9558 | 33.8716 | 33.7863 | 33.4095 | 33.2211 | 33.0968 | 31.0105 | 30.9284 | 30.8421 | 30.7579 | 30.6684 | 30.4979 | 30.3 | 30.1305 | 29.9768 | 29.8168 | 28.8368 | 28.08 | 27.4242 | 31.7263 | 31.6442 | 31.5568 | 31.4726 | 31.3832 | 31.2895 | 31.1968 | 31.1053 | 31.0168 | 30.9274 | 30.16 | 29.4147 | 28.7695
NURSLING GSP | ROWNHAMS | SILKSTEAD | MINIMUM HEADROOM | SU 44578 24565 | YES | 0 | 10.5589 | 10.3979 | 10.2337 | 10.0611 | 9.4105 | 8.7221 | 8.0442 | 7.2421 | 7.0537 | 6.8747 | 3.1021 | 0.93368 | -25.5084 | 8.1737 | 8.0126 | 7.8495 | 7.6768 | 6.9432 | 6.18 | 5.4295 | 4.5316 | 4.3537 | 4.1842 | -0.028421 | -2.3589 | -3.1137 | 8.7242 | 8.5632 | 8.3989 | 8.2263 | 7.4926 | 6.7221 | 5.9621 | 5.0547 | 4.8674 | 4.6874 | 0.40421 | -2.0074 | -2.7937
|  | SILKSTEAD | EE |  |  |  | 11.76 | 10.4895 | 10.3526 | 10.2074 | 10.0579 | 9.8747 | 9.6832 | 9.4937 | 9.3053 | 9.1242 | 7.2347 | 3.9937 | 2.6842 | 10.3832 | 8.1042 | 7.9674 | 7.8242 | 7.6747 | 7.4989 | 7.3189 | 7.1411 | 6.9653 | 6.7989 | 4.8253 | 1.2705 | -0.16 | 10.8011 | 8.6547 | 8.5179 | 8.3726 | 8.2232 | 8.04 | 7.8484 | 7.6589 | 7.4695 | 7.2884 | 5.2179 | 1.5495 | 0.084211
|  | SILKSTEAD | HT |  |  |  | 10.5589 | 10.3979 | 10.2337 | 10.0611 | 9.4105 | 8.7221 | 8.0442 | 7.2421 | 7.0537 | 6.8747 | 3.1021 | 0.93368 | 0.18947 | 8.1737 | 8.0126 | 7.8495 | 7.6768 | 6.9432 | 6.18 | 5.4295 | 4.5316 | 4.3537 | 4.1842 | -0.028421 | -2.3589 | -3.1137 | 8.7242 | 8.5632 | 8.3989 | 8.2263 | 7.4926 | 6.7221 | 5.9621 | 5.0547 | 4.8674 | 4.6874 | 0.40421 | -2.0074 | -2.7937
|  | SILKSTEAD | HE |  |  |  | 11.8463 | 10.6211 | 10.5305 | 10.4305 | 10.3263 | 10.1884 | 10.0579 | 9.9316 | 9.8105 | 9.7011 | 8.6642 | 6.1937 | -25.5084 | 10.5505 | 8.2358 | 8.1453 | 8.0453 | 7.9411 | 7.8095 | 7.6832 | 7.5632 | 7.4474 | 7.3453 | 6.2463 | 3.4305 | 2.3274 | 10.8874 | 8.7863 | 8.6958 | 8.5958 | 8.4916 | 8.3537 | 8.2232 | 8.0958 | 7.9747 | 7.8653 | 6.7274 | 3.8789 | 2.7463
|  | SILKSTEAD | CF |  |  |  | 11.8842 | 11.8274 | 10.6263 | 10.5674 | 10.5063 | 10.4305 | 10.3558 | 10.2821 | 10.2074 | 10.1379 | 9.54 | 8.6642 | 7.8747 | 10.6032 | 10.5305 | 8.2411 | 8.1821 | 8.1211 | 8.0484 | 7.9758 | 7.9053 | 7.8337 | 7.7653 | 7.1368 | 6.1684 | 5.2979 | 10.9253 | 10.8684 | 8.7916 | 8.7326 | 8.6716 | 8.5958 | 8.5211 | 8.4474 | 8.3726 | 8.3032 | 7.66 | 6.6747 | 5.7842
BRAMLEY (FLEE) | READING BSP | SILVER STREET | MINIMUM HEADROOM | SU 71957 72821 | YES | 0.15895 | 31.4253 | 31.2053 | 30.9832 | 30.7474 | 30.4979 | 30.1547 | 28.5758 | 27.0105 | 26.2421 | 25.4905 | 23.3789 | 21.42 | -0.56 | 27.4189 | 27.04 | 26.4305 | 25.4211 | 24.2316 | 23.1863 | 21.3453 | 19.5453 | 18.68 | 17.8316 | 15.5011 | 13.3168 | 11.1495 | 27.8716 | 27.6316 | 27.3832 | 26.5842 | 25.3958 | 24.3526 | 22.5137 | 20.7179 | 19.8526 | 19.0053 | 16.6779 | 14.4968 | 12.3326
|  | SILVER STREET | EE |  |  |  | 31.5158 | 31.3474 | 31.1695 | 30.98 | 30.7758 | 30.5611 | 29.8389 | 28.4579 | 27.2632 | 26.4832 | 24.6526 | 23.1568 | 21.6916 | 27.5168 | 27.2642 | 26.8126 | 25.8937 | 24.7947 | 24.0326 | 22.7821 | 21.1758 | 19.8053 | 18.9189 | 16.8863 | 15.2158 | 13.5589 | 27.9674 | 27.7821 | 27.5811 | 27.06 | 25.9589 | 25.1979 | 23.9484 | 22.3453 | 20.9768 | 20.0916 | 18.0621 | 16.3937 | 14.74
|  | SILVER STREET | HT |  |  |  | 31.4253 | 31.2053 | 30.9832 | 30.7474 | 30.4979 | 30.1547 | 28.5758 | 27.0105 | 26.2421 | 25.4905 | 23.3789 | 21.42 | 19.4926 | 27.4189 | 27.04 | 26.4305 | 25.4211 | 24.2316 | 23.1863 | 21.3453 | 19.5453 | 18.68 | 17.8316 | 15.5011 | 13.3168 | 11.1495 | 27.8716 | 27.6316 | 27.3832 | 26.5842 | 25.3958 | 24.3526 | 22.5137 | 20.7179 | 19.8526 | 19.0053 | 16.6779 | 14.4968 | 12.3326
|  | SILVER STREET | HE |  |  |  | 31.5947 | 31.4589 | 31.3095 | 31.1442 | 30.9663 | 30.7768 | 30.4758 | 29.0989 | 28.0568 | 27.3926 | 26.0632 | 25.0474 | -0.56 | 27.6021 | 27.4547 | 27.1484 | 26.3842 | 25.3811 | 24.6884 | 23.5 | 21.88 | 20.6832 | 19.9253 | 18.4463 | 17.3053 | 16.1947 | 28.0547 | 27.9063 | 27.7368 | 27.5316 | 26.5442 | 25.8526 | 24.6663 | 23.0484 | 21.8537 | 21.0979 | 19.6211 | 18.4811 | 17.3726
|  | SILVER STREET | CF |  |  |  | 31.64 | 31.5474 | 31.4505 | 31.3505 | 31.2474 | 31.1411 | 31.0316 | 30.9242 | 30.8189 | 30.7126 | 29.3137 | 28.5884 | 27.9168 | 27.6495 | 27.5505 | 27.4379 | 27.1674 | 26.7389 | 26.5537 | 26.3674 | 26.0895 | 25.6495 | 25.1389 | 22.1695 | 21.3547 | 20.5884 | 28.1032 | 28.0021 | 27.8937 | 27.7747 | 27.6495 | 27.5389 | 27.4242 | 27.2611 | 26.8158 | 26.3021 | 23.3379 | 22.5242 | 21.7589
MANNINGTON GSP | CHRISTCHURCH BSP | SOMERFORD | MINIMUM HEADROOM | SZ 18262 93590 | YES | 0.18526 | 25.1958 | 24.6768 | 24.1537 | 23.5958 | 22.3547 | 21.4032 | 20.3905 | 19.4263 | 18.4642 | 17.5463 | 13.3663 | 9.4968 | -21.3379 | 19.6263 | 18.3221 | 16.8579 | 15.1674 | 13.34 | 12.34 | 11.2737 | 10.2505 | 9.2263 | 8.24 | 3.6716 | -0.60632 | -4.5221 | 21.2663 | 20.0011 | 18.5274 | 16.7989 | 14.9316 | 13.9189 | 12.8347 | 11.7947 | 10.7505 | 9.7505 | 5.1642 | 0.86421 | -3.0558
|  | SOMERFORD | EE |  |  |  | 25.3958 | 24.9905 | 24.5611 | 24.1042 | 23.5432 | 22.7758 | 21.9747 | 21.2011 | 20.4547 | 19.6863 | 16.3853 | 13.3495 | 10.6853 | 20.0695 | 18.9916 | 17.7305 | 16.2453 | 14.6074 | 13.8042 | 12.9632 | 12.1495 | 11.3653 | 10.5495 | 7.0063 | 3.6621 | 0.66737 | 21.4811 | 20.6547 | 19.4137 | 17.8947 | 16.2221 | 15.4074 | 14.5516 | 13.7253 | 12.9253 | 12.0937 | 8.4811 | 5.1032 | 2.1021
|  | SOMERFORD | HT |  |  |  | 25.1958 | 24.6768 | 24.1537 | 23.5958 | 22.3547 | 21.4032 | 20.3905 | 19.4263 | 18.4642 | 17.5463 | 13.3663 | 9.4968 | 5.9968 | 19.6263 | 18.3221 | 16.8579 | 15.1674 | 13.34 | 12.34 | 11.2737 | 10.2505 | 9.2263 | 8.24 | 3.6716 | -0.60632 | -4.5221 | 21.2663 | 20.0011 | 18.5274 | 16.7989 | 14.9316 | 13.9189 | 12.8347 | 11.7947 | 10.7505 | 9.7505 | 5.1642 | 0.86421 | -3.0558
|  | SOMERFORD | HE |  |  |  | 25.6716 | 25.3968 | 25.0926 | 24.7568 | 24.3958 | 24.0032 | 23.6295 | 23.2758 | 22.8768 | 22.3179 | 20.0663 | 18.0411 | -21.3379 | 20.6684 | 19.8758 | 18.8874 | 17.6621 | 16.2726 | 15.7 | 15.0905 | 14.5158 | 13.9484 | 13.3547 | 10.9379 | 8.7116 | 6.6726 | 21.7758 | 21.4705 | 20.5589 | 19.3368 | 17.9158 | 17.3347 | 16.7168 | 16.1337 | 15.5579 | 14.9526 | 12.4811 | 10.2053 | 8.1579
|  | SOMERFORD | CF |  |  |  | 25.8305 | 25.6768 | 25.5158 | 25.3484 | 25.1758 | 24.9947 | 24.8095 | 24.6274 | 24.4474 | 24.2684 | 23.4621 | 22.8516 | 21.6347 | 20.9726 | 20.5863 | 20.0589 | 19.4526 | 18.7947 | 18.4474 | 18.0621 | 17.6726 | 17.3095 | 16.96 | 15.4316 | 13.9116 | 12.5632 | 21.9474 | 21.7758 | 21.5926 | 21.1105 | 20.4747 | 20.1347 | 19.7474 | 19.3505 | 18.98 | 18.6253 | 17.0705 | 15.5105 | 14.1232
LOVEDEAN GSP | CHICHESTER & HUNSTON | SOUTH BERSTED | MINIMUM HEADROOM | SU 94025 00705 | YES | 0 | 24.2747 | 23.8695 | 23.46 | 33.0253 | 32.5758 | 32.1063 | 31.6337 | 31.2168 | 30.8347 | 30.4821 | 26.78 | 21.9463 | -4.3579 | 20.2537 | 19.4295 | 18.6242 | 27.8011 | 26.9779 | 26.1484 | 25.3242 | 24.5832 | 23.8621 | 23.1821 | 18.6053 | 13.14 | 7.54 | 18.4947 | 17.6768 | 16.8779 | 26.06 | 25.2421 | 24.4168 | 23.5958 | 22.8568 | 22.14 | 21.4611 | 16.9147 | 11.4979 | 5.9632
|  | SOUTH BERSTED | EE |  |  |  | 24.4326 | 24.1168 | 23.7811 | 33.4253 | 33.0516 | 32.66 | 32.2789 | 31.9158 | 31.5653 | 31.2505 | 29.4705 | 25.7611 | 21.8274 | 20.6074 | 19.9674 | 19.3253 | 28.6642 | 27.9979 | 27.3116 | 26.6442 | 26.02 | 25.4221 | 24.8684 | 21.6021 | 17.4211 | 12.9074 | 18.8453 | 18.2105 | 17.5726 | 26.9158 | 26.2537 | 25.5705 | 24.9053 | 24.2811 | 23.6853 | 23.1305 | 19.8716 | 15.7126 | 11.2495
|  | SOUTH BERSTED | HT |  |  |  | 24.2747 | 23.8695 | 23.46 | 33.0253 | 32.5758 | 32.1063 | 31.6337 | 31.2168 | 30.8347 | 30.4821 | 26.78 | 21.9463 | 17.0516 | 20.2537 | 19.4295 | 18.6242 | 27.8011 | 26.9779 | 26.1484 | 25.3242 | 24.5832 | 23.8621 | 23.1821 | 18.6053 | 13.14 | 7.54 | 18.4947 | 17.6768 | 16.8779 | 26.06 | 25.2421 | 24.4168 | 23.5958 | 22.8568 | 22.14 | 21.4611 | 16.9147 | 11.4979 | 5.9632
|  | SOUTH BERSTED | HE |  |  |  | 24.6442 | 24.4284 | 24.1895 | 33.9253 | 33.6411 | 33.3316 | 33.0379 | 32.76 | 32.5 | 32.2737 | 31.4947 | 29.4 | -4.3579 | 20.9389 | 20.6642 | 20.2368 | 29.7811 | 29.3116 | 28.8063 | 28.3221 | 27.8779 | 27.4632 | 27.0895 | 24.6684 | 21.3295 | 17.5758 | 19.3126 | 18.9011 | 18.4768 | 28.0242 | 27.5579 | 27.0526 | 26.5705 | 26.1274 | 25.7137 | 25.3411 | 22.9358 | 19.6326 | 15.9253
|  | SOUTH BERSTED | CF |  |  |  | 24.7695 | 24.6474 | 24.52 | 34.3884 | 34.2526 | 34.1084 | 33.9632 | 33.82 | 33.6768 | 33.5347 | 32.9 | 32.5726 | 31.6547 | 21.0716 | 20.9421 | 20.8074 | 30.5653 | 30.3063 | 30.0368 | 29.7653 | 29.4979 | 29.2179 | 28.9547 | 27.5347 | 26.0147 | 23.7326 | 19.5558 | 19.3105 | 19.0568 | 28.8032 | 28.5463 | 28.2779 | 28.0074 | 27.7421 | 27.4632 | 27.2011 | 25.7884 | 24.2832 | 22.0295
MANNINGTON GSP | CHRISTCHURCH BSP | SOUTHBOURNE | MINIMUM HEADROOM | SZ 13563 92074 | YES | 0 | 17.9537 | 17.5926 | 17.2295 | 16.8432 | 16.4063 | 16.5032 | 16.1095 | 15.5589 | 15.0126 | 14.3284 | 11.1579 | 8.2453 | -8.5621 | 14.9779 | 14.2926 | 13.5989 | 12.8895 | 12.1789 | 12.4958 | 11.8768 | 11.2737 | 10.6874 | 10.0537 | 6.6379 | 3.3937 | 0.35789 | 15.5368 | 14.9 | 14.2063 | 13.4979 | 12.7874 | 13.1032 | 12.4853 | 11.8821 | 11.2958 | 10.5589 | 7.06 | 3.8105 | 0.77368
|  | SOUTHBOURNE | EE |  |  |  | 18.0895 | 17.8063 | 17.5074 | 17.1884 | 16.8526 | 16.5032 | 16.1095 | 15.5589 | 15.0126 | 14.4316 | 13.4189 | 11.1568 | 9.1011 | 15.2716 | 14.7558 | 14.2095 | 13.6442 | 13.0684 | 12.4958 | 11.8768 | 11.2737 | 10.6874 | 10.0537 | 9.1347 | 6.6084 | 4.2874 | 15.6842 | 15.3695 | 14.8168 | 14.2516 | 13.6768 | 13.1032 | 12.4853 | 11.8821 | 11.2958 | 10.6611 | 9.5547 | 7.0242 | 4.7021
|  | SOUTHBOURNE | HT |  |  |  | 17.9537 | 17.5926 | 17.2295 | 16.8432 | 16.4063 | 17.2147 | 16.4821 | 15.7705 | 15.0358 | 14.3284 | 11.1579 | 8.2453 | 5.5421 | 14.9779 | 14.2926 | 13.5989 | 12.8895 | 12.1789 | 13.2726 | 12.4853 | 11.7126 | 10.9095 | 10.1347 | 6.6379 | 3.3937 | 0.35789 | 15.5368 | 14.9 | 14.2063 | 13.4979 | 12.7874 | 13.7 | 12.9105 | 12.1389 | 11.3347 | 10.5589 | 7.06 | 3.8105 | 0.77368
|  | SOUTHBOURNE | HE |  |  |  | 18.2653 | 18.0642 | 17.8411 | 17.5947 | 17.3295 | 17.0463 | 16.7758 | 16.52 | 16.2811 | 16.0747 | 15.8916 | 14.3253 | -8.5621 | 15.48 | 15.2705 | 14.9695 | 14.5926 | 14.1968 | 13.7811 | 13.3189 | 12.8832 | 12.4453 | 11.9663 | 11.8316 | 10.0674 | 8.4779 | 15.8747 | 15.6642 | 15.4316 | 15.1758 | 14.8042 | 14.3884 | 13.9253 | 13.4895 | 13.0537 | 12.5737 | 12.2568 | 10.4895 | 8.8989
|  | SOUTHBOURNE | CF |  |  |  | 18.3684 | 18.2474 | 18.1221 | 17.9916 | 17.8568 | 17.7179 | 17.5747 | 17.4347 | 17.2968 | 17.1589 | 16.54 | 16.9284 | 15.9842 | 15.5884 | 15.4611 | 15.3305 | 15.1821 | 14.9516 | 14.6947 | 14.3937 | 14.0789 | 13.7905 | 13.5158 | 12.3263 | 12.9 | 11.8221 | 15.9832 | 15.8558 | 15.7242 | 15.5863 | 15.4453 | 15.2979 | 15.0011 | 14.6863 | 14.3968 | 14.1221 | 12.9347 | 13.3253 | 12.2463
BRAMLEY (FLEE) | BURGHFIELD RESERVE | SOUTHCOTE | MINIMUM HEADROOM | SU 68199 71325 | YES | 0 | 17.4011 | 17.1979 | 16.9916 | 16.7726 | 16.4663 | 15.84 | 15.2684 | 14.9179 | 14.5895 | 14.2811 | 12.9221 | 11.4926 | -1.6863 | 15.1621 | 14.7842 | 14.3916 | 13.9895 | 13.3326 | 12.6368 | 12.0074 | 11.6326 | 11.28 | 10.9474 | 9.4747 | 7.8905 | 6.3737 | 15.6926 | 15.3011 | 14.9084 | 14.5063 | 13.8484 | 13.1537 | 12.5232 | 12.1484 | 11.7958 | 11.4632 | 9.9905 | 8.4053 | 6.8884
|  | SOUTHCOTE | EE |  |  |  | 17.4737 | 17.3116 | 17.14 | 16.9558 | 16.7653 | 16.5021 | 15.9832 | 15.5905 | 15.2589 | 14.9937 | 13.9505 | 12.8663 | 11.8442 | 15.3221 | 15.0295 | 14.7305 | 14.4042 | 13.9211 | 13.3705 | 12.7947 | 12.3663 | 12.0074 | 11.7232 | 10.5979 | 9.3926 | 8.2432 | 15.8421 | 15.56 | 15.2463 | 14.92 | 14.4379 | 13.8874 | 13.3105 | 12.8821 | 12.5232 | 12.2389 | 11.1137 | 9.9084 | 8.7579
|  | SOUTHCOTE | HT |  |  |  | 17.4011 | 17.1979 | 16.9916 | 16.7726 | 16.4663 | 15.84 | 15.2684 | 14.9179 | 14.5895 | 14.2811 | 12.9221 | 11.4926 | 10.1379 | 15.1621 | 14.7842 | 14.3916 | 13.9895 | 13.3326 | 12.6368 | 12.0074 | 11.6326 | 11.28 | 10.9474 | 9.4747 | 7.8905 | 6.3737 | 15.6926 | 15.3011 | 14.9084 | 14.5063 | 13.8484 | 13.1537 | 12.5232 | 12.1484 | 11.7958 | 11.4632 | 9.9905 | 8.4053 | 6.8884
|  | SOUTHCOTE | HE |  |  |  | 17.5789 | 17.4674 | 17.3421 | 17.2032 | 17.0547 | 16.8968 | 16.7442 | 16.4368 | 16.2 | 16.0168 | 15.3768 | 14.6716 | -1.6863 | 15.4979 | 15.3579 | 15.1611 | 14.9495 | 14.5779 | 14.1126 | 13.6263 | 13.2884 | 13.0326 | 12.8379 | 12.1537 | 11.3653 | 10.6158 | 15.9632 | 15.8463 | 15.6853 | 15.4832 | 15.0937 | 14.6295 | 14.1432 | 13.8042 | 13.5484 | 13.3537 | 12.6705 | 11.8811 | 11.1316
|  | SOUTHCOTE | CF |  |  |  | 17.6411 | 17.5758 | 17.5074 | 17.4368 | 17.3632 | 17.2884 | 17.2105 | 17.1347 | 17.06 | 16.9853 | 16.5316 | 16.04 | 15.5863 | 15.5779 | 15.4937 | 15.4074 | 15.2937 | 15.1653 | 15.0368 | 14.9042 | 14.7526 | 14.5463 | 14.3326 | 13.3916 | 12.8421 | 12.3263 | 16.0295 | 15.96 | 15.8884 | 15.8126 | 15.6916 | 15.5695 | 15.4316 | 15.2684 | 15.0632 | 14.8484 | 13.9074 | 13.3589 | 12.8421
EALING GSP |  | SOUTHFIELD ROAD | MINIMUM HEADROOM | TQ 20533 79746 | YES | 0.057895 | 69.7032 | 69.2726 | 68.8368 | 67.4811 | 64.2253 | 62.8368 | 60.5832 | 58.3558 | 57.6916 | 57.0611 | 53.4611 | 49.4758 | 0.24 | 61.8663 | 60.3284 | 57.4926 | 54.0221 | 50.2853 | 48.6411 | 46.0684 | 43.5232 | 42.8126 | 42.1484 | 38.3411 | 33.8916 | 29.5189 | 62.9389 | 62.4505 | 60.1105 | 56.6389 | 52.9011 | 51.2568 | 48.6832 | 46.1368 | 45.4263 | 44.7621 | 40.9547 | 36.5042 | 32.1305
|  | SOUTHFIELD ROAD | EE |  |  |  | 69.8684 | 69.5316 | 69.1747 | 68.7368 | 65.9684 | 62.8368 | 60.5832 | 58.3558 | 57.6916 | 57.0737 | 54.4168 | 51.6074 | 48.9042 | 62.0421 | 60.9537 | 58.4432 | 55.4221 | 52.2432 | 48.6411 | 46.0684 | 43.5232 | 42.8126 | 42.1484 | 39.2642 | 36.1347 | 33.0895 | 63.1042 | 62.7316 | 61.0621 | 58.04 | 54.86 | 51.2568 | 48.6832 | 46.1368 | 45.4263 | 44.7621 | 41.8779 | 38.7484 | 35.7021
|  | SOUTHFIELD ROAD | HT |  |  |  | 69.7032 | 69.2726 | 68.8368 | 67.4811 | 64.2253 | 63.7158 | 61.1032 | 58.5726 | 57.7979 | 57.0611 | 53.4611 | 49.4758 | 45.5905 | 61.8663 | 60.3284 | 57.4926 | 54.0221 | 50.2853 | 49.7758 | 46.7979 | 43.9074 | 43.0726 | 42.2758 | 38.3411 | 33.8916 | 29.5189 | 62.9389 | 62.4505 | 60.1105 | 56.6389 | 52.9011 | 52.3916 | 49.4126 | 46.5221 | 45.6874 | 44.8905 | 40.9547 | 36.5042 | 32.1305
|  | SOUTHFIELD ROAD | HE |  |  |  | 70.0368 | 69.7716 | 69.4779 | 69.1547 | 67.0558 | 64.0747 | 61.9789 | 59.9126 | 59.4263 | 58.9947 | 57.2695 | 55.4011 | 0.24 | 62.2221 | 61.6021 | 59.2853 | 56.4453 | 53.4474 | 50.0126 | 47.6137 | 45.2453 | 44.7284 | 44.2695 | 42.4074 | 40.3168 | 38.3179 | 63.2726 | 62.9947 | 61.9042 | 59.0632 | 56.0642 | 52.6284 | 50.2284 | 47.86 | 47.3432 | 46.8842 | 45.0221 | 42.9305 | 40.9305
|  | SOUTHFIELD ROAD | CF |  |  |  | 70.1263 | 69.9453 | 69.7579 | 69.5632 | 69.3621 | 69.1537 | 68.9411 | 67.8621 | 67.5116 | 67.1579 | 65.4379 | 64.1337 | 62.9558 | 62.32 | 62.1137 | 61.1947 | 59.82 | 58.4274 | 56.8937 | 55.6695 | 54.4074 | 54.0316 | 53.6526 | 51.7937 | 50.3442 | 49.0063 | 63.3621 | 63.1811 | 62.9579 | 62.4389 | 61.0463 | 59.5116 | 58.2863 | 57.0242 | 56.6495 | 56.2705 | 54.4105 | 52.9611 | 51.6232
AXMINSTER | YEOVIL BSP | SPARKFORD | MINIMUM HEADROOM | ST 60767 25496 | YES | 0.16316 | 5.9853 | 5.8768 | 5.7695 | 5.66 | 5.5505 | 5.4411 | 5.3305 | 5.2326 | 5.14 | 5.0526 | 3.0611 | 2.9063 | -0.98105 | 4.9442 | 4.8284 | 4.7126 | 4.5947 | 4.4779 | 4.3611 | 4.2453 | 4.14 | 4.04 | 3.9474 | 1.6463 | 1.4937 | 1.3768 | 5.3137 | 5.1979 | 5.0821 | 4.9642 | 4.8474 | 4.7305 | 4.6137 | 4.5074 | 4.4084 | 4.3147 | 2.0116 | 1.8568 | 1.7389
|  | SPARKFORD | EE |  |  |  | 6.0347 | 5.9495 | 5.8653 | 5.7768 | 5.6863 | 5.5968 | 5.5084 | 5.4263 | 5.3463 | 5.2716 | 4.9179 | 4.2305 | 4.1526 | 4.9979 | 4.9074 | 4.8158 | 4.7211 | 4.6253 | 4.5295 | 4.4368 | 4.3484 | 4.2632 | 4.1842 | 3.8011 | 3.0179 | 2.9411 | 5.3674 | 5.2768 | 5.1853 | 5.0905 | 4.9947 | 4.8989 | 4.8053 | 4.7179 | 4.6316 | 4.5516 | 4.1663 | 3.38 | 3.3021
|  | SPARKFORD | HT |  |  |  | 5.9853 | 5.8768 | 5.7695 | 5.66 | 5.5505 | 5.4411 | 5.3305 | 5.2326 | 5.14 | 5.0526 | 3.0611 | 2.9063 | 2.7884 | 4.9442 | 4.8284 | 4.7126 | 4.5947 | 4.4779 | 4.3611 | 4.2453 | 4.14 | 4.04 | 3.9474 | 1.6463 | 1.4937 | 1.3768 | 5.3137 | 5.1979 | 5.0821 | 4.9642 | 4.8474 | 4.7305 | 4.6137 | 4.5074 | 4.4084 | 4.3147 | 2.0116 | 1.8568 | 1.7389
|  | SPARKFORD | HE |  |  |  | 6.0989 | 6.0463 | 5.9916 | 5.9326 | 5.8705 | 5.8042 | 5.7421 | 5.6853 | 5.6274 | 5.5789 | 5.3411 | 4.5021 | -0.98105 | 5.0684 | 5.0116 | 4.9537 | 4.8905 | 4.8253 | 4.7547 | 4.6905 | 4.6295 | 4.5695 | 4.5168 | 4.2579 | 3.2842 | 3.2463 | 5.4379 | 5.3811 | 5.3232 | 5.26 | 5.1937 | 5.1242 | 5.0589 | 4.9979 | 4.9368 | 4.8863 | 4.6253 | 3.6516 | 3.6116
|  | SPARKFORD | CF |  |  |  | 6.1337 | 6.1053 | 6.0726 | 6.0411 | 6.0074 | 5.9726 | 5.9368 | 5.9021 | 5.8684 | 5.8337 | 5.6547 | 5.5116 | 5.3463 | 5.1063 | 5.0747 | 5.04 | 5.0053 | 4.9695 | 4.9316 | 4.8937 | 4.8568 | 4.82 | 4.7832 | 4.5863 | 4.4284 | 4.2389 | 5.4758 | 5.4442 | 5.4095 | 5.3747 | 5.3389 | 5.3011 | 5.2632 | 5.2263 | 5.1895 | 5.1516 | 4.9558 | 4.7968 | 4.6063
MELKSHAM GSP | NORRINGTON | SPRING QUARRY WEST | MINIMUM HEADROOM | ST 84368 68717 | YES | 1.0516 | 31.5632 | 31.3347 | 31.1084 | 30.8758 | 30.5316 | 30.0905 | 29.6495 | 29.2274 | 28.9232 | 28.7011 | 25.9389 | 24.9147 | 11.8168 | 28.3884 | 28.1442 | 27.9011 | 27.6558 | 27.2779 | 26.7947 | 26.3105 | 25.8474 | 25.5158 | 25.28 | 22.1337 | 21.0326 | 20.6284 | 28.6579 | 28.4895 | 28.3189 | 28.1042 | 27.7221 | 27.2295 | 26.7368 | 26.2642 | 25.9274 | 25.6895 | 22.5211 | 21.3895 | 20.9716
|  | SPRING QUARRY WEST | EE |  |  |  | 31.6632 | 31.4863 | 31.3042 | 31.1189 | 30.8168 | 30.4147 | 30.0221 | 29.6295 | 29.34 | 29.1663 | 28.2211 | 27.2137 | 26.3168 | 28.4968 | 28.3074 | 28.1137 | 27.9453 | 27.6095 | 27.1611 | 26.7242 | 26.2884 | 25.9747 | 25.7958 | 24.8011 | 23.7211 | 22.7137 | 28.7284 | 28.5958 | 28.4589 | 28.3684 | 28.0337 | 27.5821 | 27.1421 | 26.7021 | 26.3832 | 26.1979 | 25.1674 | 24.0442 | 23.0242
|  | SPRING QUARRY WEST | HT |  |  |  | 31.5632 | 31.3347 | 31.1084 | 30.8758 | 30.5316 | 30.0905 | 29.6495 | 29.2274 | 28.9232 | 28.7011 | 25.9389 | 24.9147 | 24.5158 | 28.3884 | 28.1442 | 27.9011 | 27.6558 | 27.2779 | 26.7947 | 26.3105 | 25.8474 | 25.5158 | 25.28 | 22.1337 | 21.0326 | 20.6284 | 28.6579 | 28.4895 | 28.3189 | 28.1042 | 27.7221 | 27.2295 | 26.7368 | 26.2642 | 25.9274 | 25.6895 | 22.5211 | 21.3895 | 20.9716
|  | SPRING QUARRY WEST | HE |  |  |  | 31.8011 | 31.6895 | 31.5726 | 31.4484 | 31.2042 | 30.8579 | 30.52 | 30.1863 | 29.9589 | 29.8495 | 29.2368 | 28.5021 | 11.8168 | 28.6453 | 28.5274 | 28.4032 | 28.2716 | 28.0326 | 27.6432 | 27.2632 | 26.8884 | 26.6379 | 26.5242 | 25.8674 | 25.0432 | 24.3505 | 28.8253 | 28.74 | 28.6484 | 28.5484 | 28.4558 | 28.0653 | 27.6842 | 27.3063 | 27.0547 | 26.9379 | 26.2674 | 25.4316 | 24.7274
|  | SPRING QUARRY WEST | CF |  |  |  | 31.8684 | 31.8053 | 31.7347 | 31.6642 | 31.5463 | 31.3821 | 31.2021 | 31.0221 | 30.8916 | 30.8158 | 30.4558 | 30.0737 | 29.64 | 28.7179 | 28.6495 | 28.5747 | 28.4989 | 28.3695 | 28.1874 | 27.9884 | 27.7884 | 27.6453 | 27.5653 | 27.1863 | 26.7695 | 26.2863 | 28.8779 | 28.8295 | 28.7779 | 28.7242 | 28.6505 | 28.5547 | 28.4358 | 28.2316 | 28.0863 | 28.0042 | 27.6168 | 27.1874 | 26.6884
NORTH HYDE GSP | NORTH HYDE 22kV | SPRINGFIELD ROAD | MINIMUM HEADROOM | TQ 11409 80620 | YES | 0.086316 | 27.1379 | 26.9242 | 26.6979 | 26.4526 | 48.8937 | 48.6211 | 48.3484 | 48.1032 | 47.8758 | 47.6653 | 45.9674 | 43.6684 | 18.88 | 23.7642 | 23.5211 | 23.1221 | 22.5674 | 44.6453 | 43.9295 | 43.24 | 42.5884 | 41.9653 | 41.3737 | 38.6168 | 36.0105 | 33.5242 | 24.2189 | 24.0032 | 23.78 | 23.5253 | 45.56 | 44.8221 | 44.1284 | 43.4768 | 42.8526 | 42.2621 | 39.5042 | 36.8979 | 34.4105
|  | SPRINGFIELD ROAD | EE |  |  |  | 27.2095 | 27.0484 | 26.8611 | 26.6589 | 49.1421 | 48.9158 | 48.6937 | 48.48 | 48.2737 | 48.0874 | 47.3632 | 46.1147 | 44.5537 | 23.8421 | 23.6716 | 23.4442 | 23.0674 | 45.2874 | 44.7674 | 44.2558 | 43.7432 | 43.2442 | 42.7747 | 40.6758 | 38.7811 | 36.9989 | 24.2958 | 24.1263 | 23.9411 | 23.7421 | 46.2295 | 45.6937 | 45.1537 | 44.6358 | 44.1337 | 43.6642 | 41.5632 | 39.6684 | 37.8863
|  | SPRINGFIELD ROAD | HT |  |  |  | 27.1379 | 26.9242 | 26.6979 | 26.4526 | 48.8937 | 48.6211 | 48.3484 | 48.1032 | 47.8758 | 47.6653 | 45.9674 | 43.6684 | 41.4874 | 23.7642 | 23.5211 | 23.1221 | 22.5674 | 44.6453 | 43.9295 | 43.24 | 42.5884 | 41.9653 | 41.3737 | 38.6168 | 36.0105 | 33.5242 | 24.2189 | 24.0032 | 23.78 | 23.5253 | 45.56 | 44.8221 | 44.1284 | 43.4768 | 42.8526 | 42.2621 | 39.5042 | 36.8979 | 34.4105
|  | SPRINGFIELD ROAD | HE |  |  |  | 27.3 | 27.1789 | 27.0432 | 26.8832 | 49.4032 | 49.2126 | 49.0274 | 48.8547 | 48.6916 | 48.5495 | 48.0368 | 47.6947 | 18.88 | 23.94 | 23.8137 | 23.6695 | 23.48 | 45.8632 | 45.4232 | 44.9916 | 44.5895 | 44.1958 | 43.8221 | 42.2011 | 40.7789 | 39.4621 | 24.3947 | 24.2674 | 24.1232 | 23.9621 | 46.4853 | 46.2979 | 45.9316 | 45.5021 | 45.0926 | 44.7147 | 43.0895 | 41.6663 | 40.3495
|  | SPRINGFIELD ROAD | CF |  |  |  | 27.3568 | 27.28 | 27.2011 | 27.1189 | 49.7316 | 49.6347 | 49.5347 | 49.4358 | 49.3379 | 49.2389 | 48.7937 | 48.5463 | 48.3853 | 24 | 23.92 | 23.8358 | 23.7474 | 46.3558 | 46.2305 | 46.0716 | 45.8589 | 45.6326 | 45.3989 | 44.2726 | 43.3579 | 42.5295 | 24.4547 | 24.3737 | 24.2895 | 24.2021 | 46.8095 | 46.7137 | 46.6147 | 46.5179 | 46.4232 | 46.3253 | 45.1695 | 44.2463 | 43.4179
NURSLING GSP | WINCHESTER | ST CROSS | MINIMUM HEADROOM | SU 47287 28156 | YES | 1.1284 | 27.7137 | 27.1526 | 26.5947 | 26.0189 | 25.4379 | 24.8453 | 24.2537 | 23.6684 | 23.0853 | 22.4053 | 20.6242 | 15.6042 | -3.4411 | 27.5695 | 26.9632 | 26.3621 | 25.7453 | 25.1211 | 24.4947 | 23.8716 | 23.2484 | 22.6242 | 21.8811 | 18.2 | 14.4347 | 11.0811 | 33.7579 | 33.4505 | 33.0621 | 32.4442 | 31.8221 | 31.1905 | 30.5611 | 29.9326 | 29.3021 | 28.5526 | 26.5632 | 20.9547 | 17.5663
|  | ST CROSS | EE |  |  |  | 27.9558 | 27.5189 | 27.0684 | 26.6011 | 26.1084 | 25.5326 | 25.1421 | 24.68 | 24.2021 | 23.6232 | 20.6242 | 17.9516 | 15.5305 | 27.8337 | 27.3621 | 26.8789 | 26.3853 | 25.8558 | 25.24 | 24.8421 | 24.3611 | 23.8589 | 23.2347 | 19.9653 | 17.1021 | 14.4347 | 33.8726 | 33.6295 | 33.3716 | 33.0779 | 32.5484 | 31.9284 | 31.5242 | 31.0358 | 30.5242 | 29.8916 | 26.5632 | 23.5747 | 20.8726
|  | ST CROSS | HT |  |  |  | 27.7137 | 27.1526 | 26.5947 | 26.0189 | 25.4379 | 24.8453 | 24.2537 | 23.6684 | 23.0853 | 22.4053 | 23.5979 | 15.6042 | 12.6242 | 27.5695 | 26.9632 | 26.3621 | 25.7453 | 25.1211 | 24.4947 | 23.8716 | 23.2484 | 22.6242 | 21.8811 | 18.2 | 14.4347 | 11.0811 | 33.7579 | 33.4505 | 33.0621 | 32.4442 | 31.8221 | 31.1905 | 30.5611 | 29.9326 | 29.3021 | 28.5526 | 30.1537 | 20.9547 | 17.5663
|  | ST CROSS | HE |  |  |  | 28.2832 | 28.0021 | 27.6442 | 27.14 | 26.6547 | 26.1621 | 25.8621 | 25.5537 | 25.2368 | 25.0263 | 22.9916 | 25.3253 | -3.4411 | 28.1905 | 27.8905 | 27.5021 | 26.9453 | 26.4137 | 25.8821 | 25.5747 | 25.2579 | 24.9263 | 24.7158 | 22.4705 | 22.2495 | 18.2705 | 34.0305 | 33.8621 | 33.6758 | 33.4695 | 33.1137 | 32.5789 | 32.2684 | 31.9463 | 31.6116 | 31.3968 | 29.1274 | 31.6642 | 25.1663
|  | ST CROSS | CF |  |  |  | 28.4105 | 28.2684 | 28.0863 | 27.8979 | 27.7053 | 27.5 | 27.2926 | 27.0937 | 26.8937 | 26.6274 | 25.0842 | 23.78 | 22.6232 | 28.3632 | 28.1737 | 27.9789 | 27.7758 | 27.5684 | 27.3505 | 27.1305 | 26.9179 | 26.7063 | 26.4147 | 24.7053 | 23.2326 | 21.9189 | 34.1221 | 34.0242 | 33.9221 | 33.8158 | 33.7063 | 33.5874 | 33.4653 | 33.3463 | 33.2274 | 33.1053 | 31.3884 | 29.9063 | 28.5811
COWLEY GSP | OXFORD BSP | ST EBBES | MINIMUM HEADROOM | SP 51259 05741 | YES | 0 | 36.2137 | 36.1116 | 36.0084 | 35.8989 | 35.7832 | 35.8042 | 34.8095 | 34.48 | 34.1389 | 33.9947 | 33.3958 | 32.7253 | 4.5295 | 31.4084 | 31.1958 | 31.0011 | 30.7947 | 30.5863 | 30.32 | 28.7716 | 28.3495 | 27.9642 | 27.8084 | 27.2305 | 26.4947 | 25.7547 | 32.1653 | 32.0021 | 31.8926 | 31.7779 | 31.6568 | 31.6611 | 30.6274 | 30.2474 | 29.8621 | 29.7063 | 29.0853 | 28.3505 | 27.6095
|  | ST EBBES | EE |  |  |  | 36.2547 | 36.1747 | 36.0895 | 36 | 35.9032 | 35.8042 | 35.0505 | 34.48 | 34.1389 | 33.9947 | 33.7147 | 33.2126 | 32.7505 | 31.4526 | 31.3516 | 31.2347 | 30.9316 | 30.5863 | 30.32 | 29.0053 | 28.3495 | 27.9642 | 27.8084 | 27.5558 | 27.0063 | 26.4926 | 32.2095 | 32.1074 | 31.9905 | 31.8811 | 31.7695 | 31.6611 | 30.9032 | 30.2474 | 29.8621 | 29.7063 | 29.4116 | 28.8611 | 28.3474
|  | ST EBBES | HT |  |  |  | 36.2137 | 36.1116 | 36.0084 | 35.8989 | 35.7832 | 35.9368 | 34.8095 | 34.5747 | 34.3747 | 34.2 | 33.3958 | 32.7253 | 32.0579 | 31.4084 | 31.1958 | 31.0011 | 30.7947 | 30.5884 | 30.8137 | 28.7716 | 28.5147 | 28.2968 | 28.1074 | 27.2305 | 26.4947 | 25.7547 | 32.1653 | 32.0021 | 31.8926 | 31.7779 | 31.6568 | 31.9032 | 30.6274 | 30.3705 | 30.1526 | 29.9632 | 29.0853 | 28.3505 | 27.6095
|  | ST EBBES | HE |  |  |  | 36.2937 | 36.2316 | 36.1621 | 36.0863 | 36.0042 | 35.9158 | 35.3726 | 34.8274 | 34.5758 | 34.4726 | 34.4147 | 34.1358 | 4.5295 | 31.4958 | 31.4126 | 31.3137 | 31.1579 | 30.8747 | 30.6747 | 29.3632 | 28.7337 | 28.4505 | 28.34 | 28.3326 | 28.0274 | 27.7611 | 32.2516 | 32.1695 | 32.0684 | 31.9758 | 31.8821 | 31.7874 | 31.2611 | 30.6316 | 30.3484 | 30.2379 | 30.1874 | 29.8832 | 29.6158
|  | ST EBBES | CF |  |  |  | 36.3158 | 36.2737 | 36.2305 | 36.1853 | 36.1379 | 36.0895 | 36.04 | 35.9905 | 35.9432 | 35.8947 | 35.1011 | 35.1811 | 34.9821 | 31.5189 | 31.4737 | 31.4295 | 31.3821 | 31.3326 | 31.2821 | 31.2305 | 31.1726 | 31.1042 | 31.0211 | 29.0705 | 29.2053 | 28.9811 | 32.2747 | 32.2305 | 32.1853 | 32.1389 | 32.0895 | 32.0389 | 31.9874 | 31.9284 | 31.8589 | 31.7874 | 30.9684 | 31.0611 | 30.8368
BRAMLEY (ANDO-THAT) | THATCHAM BSP | ST JOHNS | MINIMUM HEADROOM | SU 47113 66363 | YES | 0.36842 | 17.8589 | 17.4905 | 17.04 | 15.8832 | 14.3063 | 12.5547 | 10.7947 | 9.0916 | 7.5832 | 6.3326 | 3.7884 | 1.3779 | -25.8611 | 12.2274 | 11.3368 | 9.7442 | 7.9979 | 6.1558 | 4.1905 | 2.1979 | 0.26316 | -1.4484 | -2.8621 | -5.6274 | -8.2916 | -10.8842 | 13.2189 | 12.6821 | 11.1432 | 9.4211 | 7.5326 | 5.5442 | 3.5505 | 1.6158 | -0.096842 | -1.5105 | -4.2758 | -6.9411 | -9.5337
|  | ST JOHNS | EE |  |  |  | 18.0021 | 17.7147 | 17.3558 | 16.5684 | 15.1295 | 13.52 | 11.9053 | 10.3011 | 8.8726 | 7.7053 | 5.6958 | 3.8905 | 2.1484 | 12.5421 | 11.8126 | 10.3621 | 8.7611 | 7.0537 | 5.2347 | 3.3979 | 1.5716 | -0.051579 | -1.3737 | -3.5579 | -5.5579 | -7.5158 | 13.3726 | 13.0579 | 11.7474 | 10.1968 | 8.4463 | 6.5884 | 4.7516 | 2.9242 | 1.3 | -0.022105 | -2.2063 | -4.2074 | -6.1653
|  | ST JOHNS | HT |  |  |  | 17.8589 | 17.4905 | 17.04 | 15.8832 | 14.3063 | 12.5547 | 10.7947 | 9.0916 | 7.5832 | 6.3326 | 3.7884 | 1.3779 | -0.94211 | 12.2274 | 11.3368 | 9.7442 | 7.9979 | 6.1558 | 4.1905 | 2.1979 | 0.26316 | -1.4484 | -2.8621 | -5.6274 | -8.2916 | -10.8842 | 13.2189 | 12.6821 | 11.1432 | 9.4211 | 7.5326 | 5.5442 | 3.5505 | 1.6158 | -0.096842 | -1.5105 | -4.2758 | -6.9411 | -9.5337
|  | ST JOHNS | HE |  |  |  | 18.1926 | 17.9926 | 17.7516 | 17.4242 | 16.1663 | 14.7547 | 13.2874 | 11.8368 | 10.5558 | 9.5389 | 8.2432 | 7.1095 | -25.8611 | 12.8095 | 12.4305 | 11.1705 | 9.7516 | 8.2168 | 6.5663 | 4.9053 | 3.2453 | 1.7821 | 0.62421 | -0.77895 | -2.04 | -3.2737 | 13.5768 | 13.3568 | 12.5358 | 11.1684 | 9.6284 | 7.9347 | 6.2589 | 4.5979 | 3.1347 | 1.9758 | 0.57263 | -0.68737 | -1.9221
|  | ST JOHNS | CF |  |  |  | 18.3011 | 18.1853 | 18.0663 | 17.9379 | 17.7674 | 17.5916 | 17.14 | 16.4358 | 15.7621 | 15.1537 | 14.0168 | 13.1989 | 12.4295 | 12.9263 | 12.7989 | 12.2632 | 11.5853 | 10.8821 | 10.1505 | 9.3611 | 8.5168 | 7.7105 | 7.0042 | 5.7863 | 4.8811 | 4.0063 | 13.6937 | 13.5663 | 13.4158 | 12.94 | 12.2621 | 11.5568 | 10.7947 | 9.9337 | 9.1074 | 8.3821 | 7.1442 | 6.2347 | 5.36
COWLEY GSP | WITNEY BSP | STANDLAKE | MINIMUM HEADROOM | SP 38923 02349 | YES | 0 | 6.2695 | 6.1884 | 6.1063 | 6.0189 | 5.9295 | 5.8379 | 5.6505 | 5.2958 | 5.2232 | 5.1558 | 4.4895 | 3.6621 | -4.1442 | 5.2263 | 5.0537 | 4.9063 | 4.7516 | 4.6 | 4.4516 | 4.1432 | 3.7442 | 3.6716 | 3.6042 | 2.8632 | 1.8558 | 1.5621 | 5.5632 | 5.3811 | 5.2263 | 5.0642 | 4.9063 | 4.7516 | 4.42 | 3.9874 | 3.9147 | 3.8474 | 3.0684 | 2.0621 | 1.7695
|  | STANDLAKE | EE |  |  |  | 6.3021 | 6.24 | 6.1737 | 6.1032 | 6.0295 | 5.9537 | 5.8811 | 5.8126 | 5.7474 | 5.6895 | 5.3316 | 4.7789 | 4.2747 | 5.2937 | 5.1579 | 5.0389 | 4.9158 | 4.7937 | 4.6726 | 4.5547 | 4.4442 | 4.3316 | 4.2284 | 3.8147 | 3.1968 | 2.5916 | 5.6084 | 5.4905 | 5.3663 | 5.2368 | 5.1105 | 4.9832 | 4.8621 | 4.7463 | 4.6284 | 4.5211 | 4.0853 | 3.4158 | 2.7968
|  | STANDLAKE | HT |  |  |  | 6.2695 | 6.1884 | 6.1063 | 6.0189 | 5.9295 | 5.8379 | 5.6505 | 5.2958 | 5.2232 | 5.1558 | 4.4895 | 3.6621 | 3.3989 | 5.2263 | 5.0537 | 4.9063 | 4.7516 | 4.6 | 4.4516 | 4.1432 | 3.7442 | 3.6716 | 3.6042 | 2.8632 | 1.8558 | 1.5621 | 5.5632 | 5.3811 | 5.2263 | 5.0642 | 4.9063 | 4.7516 | 4.42 | 3.9874 | 3.9147 | 3.8474 | 3.0684 | 2.0621 | 1.7695
|  | STANDLAKE | HE |  |  |  | 6.3474 | 6.3063 | 6.2611 | 6.2105 | 6.1558 | 6.0979 | 6.0432 | 5.9905 | 5.9421 | 5.9 | 5.76 | 5.4463 | -4.1442 | 5.3863 | 5.2926 | 5.2168 | 5.1326 | 5.0484 | 4.9632 | 4.88 | 4.8011 | 4.7221 | 4.6516 | 4.3895 | 3.9168 | 3.4642 | 5.6568 | 5.6116 | 5.5537 | 5.4663 | 5.3789 | 5.2895 | 5.2042 | 5.1221 | 5.04 | 4.9663 | 4.6916 | 4.1758 | 3.68
|  | STANDLAKE | CF |  |  |  | 6.3737 | 6.3516 | 6.3284 | 6.3053 | 6.2811 | 6.2547 | 6.2295 | 6.2042 | 6.1789 | 6.1537 | 6.0411 | 5.9853 | 5.8411 | 5.4495 | 5.3968 | 5.3526 | 5.3074 | 5.2589 | 5.2095 | 5.1589 | 5.1126 | 5.0695 | 5.0232 | 4.8 | 4.5989 | 4.3305 | 5.6853 | 5.6611 | 5.6368 | 5.6116 | 5.5863 | 5.5463 | 5.4926 | 5.4442 | 5.3989 | 5.3505 | 5.1158 | 4.8989 | 4.6042
MINETY GSP | STRATTON (2 X 60) | STANTON FITZWARREN | MINIMUM HEADROOM | SU 17585 90987 | YES | 3.8126 | 19.1926 | 18.9105 | 18.5126 | 18.1211 | 17.46 | 16.58 | 15.8853 | 15.0189 | 14.1158 | 13.24 | 9.3358 | 6.9768 | -7.5232 | 17.9621 | 17.8484 | 17.4253 | 17.0105 | 16.2811 | 15.2989 | 14.5368 | 13.5674 | 12.5505 | 11.5642 | 7.1674 | 4.5611 | 2.0779 | 18.2716 | 17.9779 | 17.5547 | 17.1411 | 16.4116 | 15.4284 | 14.6642 | 13.6926 | 12.6737 | 11.6842 | 7.2642 | 4.6253 | 2.1326
|  | STANTON FITZWARREN | EE |  |  |  | 19.3158 | 19.1105 | 18.7737 | 18.4453 | 18.0316 | 17.2432 | 16.7084 | 15.8347 | 14.9737 | 14.1411 | 10.6789 | 8.7189 | 7.0042 | 18.0895 | 17.8853 | 17.6979 | 17.3484 | 16.9032 | 16.0211 | 15.44 | 14.4579 | 13.4895 | 12.5537 | 8.6674 | 6.5274 | 4.5905 | 18.4 | 18.1874 | 17.8274 | 17.4789 | 17.0326 | 16.1495 | 15.5632 | 14.5789 | 13.6063 | 12.6642 | 8.7411 | 6.5526 | 4.6032
|  | STANTON FITZWARREN | HT |  |  |  | 19.1926 | 18.9105 | 18.5126 | 18.1211 | 17.46 | 16.58 | 15.8853 | 15.0189 | 14.1158 | 13.24 | 9.3358 | 6.9768 | 4.7737 | 17.9621 | 17.8484 | 17.4253 | 17.0105 | 16.2811 | 15.2989 | 14.5368 | 13.5674 | 12.5505 | 11.5642 | 7.1674 | 4.5611 | 2.0779 | 18.2716 | 17.9779 | 17.5547 | 17.1411 | 16.4116 | 15.4284 | 14.6642 | 13.6926 | 12.6737 | 11.6842 | 7.2642 | 4.6253 | 2.1326
|  | STANTON FITZWARREN | HE |  |  |  | 19.4484 | 19.3505 | 19.12 | 18.8705 | 18.5989 | 18.0916 | 17.6653 | 16.9021 | 16.1516 | 15.4347 | 12.5316 | 11.1453 | -7.5232 | 18.2221 | 18.1326 | 18.0589 | 17.7937 | 17.5042 | 16.9432 | 16.4758 | 15.6095 | 14.7579 | 13.94 | 10.6316 | 9.0663 | 7.5758 | 18.5326 | 18.4358 | 18.1884 | 17.9232 | 17.6337 | 17.0716 | 16.6021 | 15.7358 | 14.8832 | 14.0653 | 10.7442 | 9.1695 | 7.6674
|  | STANTON FITZWARREN | CF |  |  |  | 19.5295 | 19.4505 | 19.3547 | 19.2611 | 19.1505 | 19.0168 | 18.9326 | 18.7663 | 18.4789 | 18.0421 | 16.1347 | 15.3158 | 14.4811 | 18.3042 | 18.2242 | 18.1242 | 18.1989 | 18.0832 | 17.9421 | 17.8642 | 17.6853 | 17.3642 | 16.8653 | 14.6937 | 13.7747 | 12.8242 | 18.6147 | 18.5337 | 18.4337 | 18.3368 | 18.2211 | 18.0789 | 17.9916 | 17.8126 | 17.4895 | 16.9916 | 14.8189 | 13.8926 | 12.9358
LALEHAM | STAINES | STANWELL | MINIMUM HEADROOM | TQ 06003 72766 | YES | 0 | 33.9842 | 33.8579 | 33.7305 | 33.5958 | 33.4558 | 33.3095 | 33.1632 | 33.0347 | 33.1158 | 33.0158 | 32.3905 | 31.3958 | 9.5232 | 30.7947 | 30.5642 | 30.32 | 30.0705 | 29.8211 | 29.5695 | 29.3232 | 29.0979 | 28.9505 | 28.7432 | 27.5189 | 26.4105 | 25.3779 | 31.2558 | 31.1221 | 30.9884 | 30.7632 | 30.5221 | 30.2779 | 30.0389 | 29.8179 | 29.6021 | 29.3947 | 28.1726 | 27.0653 | 26.0337
|  | STANWELL | EE |  |  |  | 34.0284 | 33.9274 | 33.82 | 33.7063 | 33.5863 | 33.4621 | 33.3411 | 33.2263 | 33.1158 | 33.0158 | 32.6484 | 32.2737 | 31.5632 | 30.8474 | 30.7211 | 30.5274 | 30.3274 | 30.1211 | 29.9168 | 29.7168 | 29.5253 | 29.34 | 29.1621 | 28.1705 | 27.3095 | 26.5084 | 31.3042 | 31.1968 | 31.0842 | 30.9663 | 30.8095 | 30.6105 | 30.4158 | 30.2305 | 30.0505 | 29.8779 | 28.8905 | 28.0284 | 27.2274
|  | STANWELL | HT |  |  |  | 33.9842 | 33.8579 | 33.7305 | 33.5958 | 33.4558 | 33.3095 | 33.1632 | 33.0347 | 33.6905 | 33.4979 | 32.3905 | 31.3958 | 30.4768 | 30.7947 | 30.5642 | 30.32 | 30.0705 | 29.8211 | 29.5695 | 29.3232 | 29.0979 | 28.9505 | 28.7432 | 27.5189 | 26.4105 | 25.3779 | 31.2558 | 31.1221 | 30.9884 | 30.7632 | 30.5221 | 30.2779 | 30.0389 | 29.8179 | 29.6021 | 29.3947 | 28.1726 | 27.0653 | 26.0337
|  | STANWELL | HE |  |  |  | 34.0905 | 34.0179 | 33.9379 | 33.8495 | 33.7537 | 33.6537 | 33.5568 | 33.4653 | 34.6789 | 34.5663 | 33.9242 | 33.4 | 9.5232 | 30.92 | 30.84 | 30.7537 | 30.6589 | 30.5179 | 30.3705 | 30.2284 | 30.0916 | 30.0316 | 29.9126 | 29.2011 | 28.6095 | 28.0716 | 31.3705 | 31.2947 | 31.2116 | 31.12 | 31.0221 | 30.9189 | 30.8189 | 30.7253 | 30.6821 | 30.5632 | 29.8526 | 29.2621 | 28.7242
|  | STANWELL | CF |  |  |  | 34.1263 | 34.0832 | 34.0389 | 33.9916 | 33.9432 | 33.8947 | 33.8432 | 33.7926 | 33.7432 | 33.6937 | 33.4737 | 33.3621 | 33.3 | 30.9568 | 30.9126 | 30.8632 | 30.8105 | 30.7579 | 30.7042 | 30.6211 | 30.5326 | 30.4453 | 30.3547 | 29.8011 | 29.3737 | 29 | 31.4074 | 31.3632 | 31.3168 | 31.2674 | 31.2168 | 31.1663 | 31.1116 | 31.0589 | 31.0074 | 30.9558 | 30.5042 | 30.0937 | 29.7189
MANNINGTON GSP | SALISBURY | STAPLEFORD | MINIMUM HEADROOM | SU 06871 37078 | YES | 0.27789 | 16.2263 | 16.1032 | 15.9779 | 15.8284 | 15.6516 | 15.2389 | 14.7505 | 14.1621 | 14.0463 | 13.9347 | 12.7379 | 11.1958 | 6.0705 | 14.7579 | 14.6305 | 14.5021 | 14.3463 | 14.1589 | 13.7095 | 13.1642 | 12.5011 | 12.3916 | 12.2874 | 11.0211 | 9.3474 | 8.8758 | 14.9137 | 14.7884 | 14.66 | 14.5074 | 14.3242 | 13.8874 | 13.3663 | 12.7084 | 12.5916 | 12.48 | 11.1653 | 9.4347 | 8.9411
|  | STAPLEFORD | EE |  |  |  | 16.2737 | 16.18 | 16.0768 | 15.9705 | 15.86 | 15.7053 | 15.5368 | 15.3716 | 15.2042 | 15.0474 | 14.1432 | 12.7179 | 11.8084 | 14.8063 | 14.7105 | 14.6053 | 14.4958 | 14.3842 | 14.2284 | 14.0611 | 13.9 | 13.7316 | 13.5768 | 12.6768 | 11.1663 | 10.1611 | 14.9611 | 14.8663 | 14.7611 | 14.6537 | 14.5411 | 14.3811 | 14.2084 | 14.0389 | 13.8653 | 13.7032 | 12.7621 | 11.2042 | 10.1737
|  | STAPLEFORD | HT |  |  |  | 16.2263 | 16.1032 | 15.9779 | 15.8284 | 15.6516 | 15.2389 | 14.7505 | 14.1621 | 14.0463 | 13.9347 | 12.7379 | 11.1958 | 10.7347 | 14.7579 | 14.6305 | 14.5021 | 14.3463 | 14.1589 | 13.7095 | 13.1642 | 12.5011 | 12.3916 | 12.2874 | 11.0211 | 9.3474 | 8.8758 | 14.9137 | 14.7884 | 14.66 | 14.5074 | 14.3242 | 13.8874 | 13.3663 | 12.7084 | 12.5916 | 12.48 | 11.1653 | 9.4347 | 8.9411
|  | STAPLEFORD | HE |  |  |  | 16.3263 | 16.2737 | 16.2137 | 16.1411 | 16.0632 | 15.9642 | 15.8705 | 15.7821 | 15.6968 | 15.6189 | 15.0811 | 14.1747 | 6.0705 | 14.8589 | 14.8074 | 14.7463 | 14.6705 | 14.5916 | 14.4958 | 14.4063 | 14.3221 | 14.2389 | 14.1642 | 13.6137 | 12.6053 | 11.7884 | 15.0137 | 14.9621 | 14.9011 | 14.8274 | 14.7495 | 14.6484 | 14.5537 | 14.4642 | 14.3779 | 14.2968 | 13.7358 | 12.7589 | 11.9232
|  | STAPLEFORD | CF |  |  |  | 16.36 | 16.3316 | 16.3042 | 16.2747 | 16.24 | 16.1916 | 16.1442 | 16.0979 | 16.0516 | 16.0074 | 15.7674 | 15.3579 | 14.8221 | 14.8937 | 14.8653 | 14.8379 | 14.8074 | 14.7716 | 14.7263 | 14.6789 | 14.6337 | 14.5884 | 14.5453 | 14.3063 | 13.8632 | 13.2611 | 15.0484 | 15.02 | 14.9926 | 14.9621 | 14.9274 | 14.8789 | 14.8295 | 14.7832 | 14.7368 | 14.6905 | 14.4442 | 14.0095 | 13.4316
COWLEY GSP | HIGH WYCOMBE BSP | STOKENCHURCH | MINIMUM HEADROOM | SU 77124 94355 | YES | 0 | 9.66 | 9.4958 | 9.3305 | 9.1432 | 8.8516 | 8.5621 | 8.2716 | 7.9958 | 7.7242 | 7.4684 | 6.2926 | 5.2568 | -6.9021 | 7.7537 | 7.44 | 7.1316 | 6.8189 | 6.5126 | 6.2084 | 5.9042 | 5.6137 | 5.3253 | 5.0537 | 3.7916 | 2.6716 | 1.6368 | 8.2242 | 7.9063 | 7.5937 | 7.2768 | 6.9663 | 6.6589 | 6.3505 | 6.0547 | 5.7621 | 5.4863 | 4.2021 | 3.0589 | 2.0189
|  | STOKENCHURCH | EE |  |  |  | 9.7211 | 9.5926 | 9.4579 | 9.3126 | 9.1621 | 8.9842 | 8.7516 | 8.5263 | 8.2916 | 8.0737 | 7.1442 | 6.3568 | 5.6653 | 7.8905 | 7.6484 | 7.4053 | 7.1547 | 6.9063 | 6.6589 | 6.4158 | 6.1789 | 5.9316 | 5.6989 | 4.7053 | 3.8505 | 3.0937 | 8.3053 | 8.1189 | 7.8726 | 7.6179 | 7.3674 | 7.1158 | 6.8705 | 6.6295 | 6.3789 | 6.1432 | 5.1305 | 4.2568 | 3.4832
|  | STOKENCHURCH | HT |  |  |  | 9.66 | 9.4958 | 9.3305 | 9.1432 | 8.8516 | 8.5621 | 8.2716 | 7.9958 | 7.7242 | 7.4684 | 6.2926 | 5.2568 | 4.3232 | 7.7537 | 7.44 | 7.1316 | 6.8189 | 6.5126 | 6.2084 | 5.9042 | 5.6137 | 5.3253 | 5.0537 | 3.7916 | 2.6716 | 1.6368 | 8.2242 | 7.9063 | 7.5937 | 7.2768 | 6.9663 | 6.6589 | 6.3505 | 6.0547 | 5.7621 | 5.4863 | 4.2021 | 3.0589 | 2.0189
|  | STOKENCHURCH | HE |  |  |  | 9.8095 | 9.7232 | 9.6274 | 9.5211 | 9.4074 | 9.2863 | 9.1684 | 9.06 | 8.9568 | 8.8695 | 8.2874 | 7.7884 | -6.9021 | 8.0768 | 7.9305 | 7.7716 | 7.6042 | 7.4358 | 7.2632 | 7.0905 | 6.9232 | 6.7474 | 6.5853 | 5.9263 | 5.3832 | 4.9168 | 8.4011 | 8.3105 | 8.2105 | 8.0758 | 7.9042 | 7.7305 | 7.5568 | 7.3874 | 7.2095 | 7.0432 | 6.3737 | 5.8189 | 5.34
|  | STOKENCHURCH | CF |  |  |  | 9.8611 | 9.8126 | 9.7621 | 9.7105 | 9.6568 | 9.6011 | 9.5432 | 9.4874 | 9.4316 | 9.3758 | 9.0758 | 8.7084 | 8.4084 | 8.1421 | 8.08 | 7.9905 | 7.8937 | 7.7979 | 7.6989 | 7.5989 | 7.4979 | 7.3895 | 7.2758 | 6.7474 | 6.3463 | 6.0137 | 8.4558 | 8.4042 | 8.3505 | 8.2958 | 8.2389 | 8.1705 | 8.0695 | 7.9663 | 7.8558 | 7.7411 | 7.2032 | 6.7926 | 6.4526
MINETY GSP | STRATTON (2 X 60) | STRATTON | MINIMUM HEADROOM | SU 16998 88837 | YES | 2.1779 | 33.3821 | 33.1021 | 32.8053 | 32.4821 | 32.1432 | 31.8484 | 30.7358 | 29.4684 | 28.3211 | 27.1989 | 24.4789 | 21.82 | -7.5611 | 27.0947 | 26.3516 | 25.3905 | 24.2926 | 23.0642 | 21.5305 | 19.8779 | 18.4074 | 17.1084 | 15.8379 | 12.8274 | 9.8547 | 7.0137 | 26.7547 | 26.0053 | 25.0358 | 23.9284 | 22.6884 | 21.1232 | 19.4526 | 17.9653 | 16.6537 | 15.3684 | 12.3179 | 9.3042 | 6.4305
|  | STRATTON | EE |  |  |  | 33.4747 | 33.2547 | 33.0032 | 32.7284 | 32.4368 | 32.1011 | 31.3358 | 30.1547 | 29.0484 | 27.9726 | 25.7863 | 23.6537 | 21.6642 | 27.2095 | 26.6695 | 25.8011 | 24.7968 | 23.6621 | 22.0926 | 20.5368 | 19.1337 | 17.8821 | 16.6632 | 14.2632 | 11.8853 | 9.6305 | 26.8695 | 26.3253 | 25.4484 | 24.4347 | 23.2884 | 21.7032 | 20.1295 | 18.7105 | 17.4442 | 16.2095 | 13.7568 | 11.3358 | 9.0516
|  | STRATTON | HT |  |  |  | 33.3821 | 33.1021 | 32.8053 | 32.4821 | 32.1432 | 31.8484 | 30.7358 | 29.4684 | 28.3211 | 27.1989 | 24.4789 | 21.82 | 19.3063 | 27.0947 | 26.3516 | 25.3905 | 24.2926 | 23.0642 | 21.5305 | 19.8779 | 18.4074 | 17.1084 | 15.8379 | 12.8274 | 9.8547 | 7.0137 | 26.7547 | 26.0053 | 25.0358 | 23.9284 | 22.6884 | 21.1232 | 19.4526 | 17.9653 | 16.6537 | 15.3684 | 12.3179 | 9.3042 | 6.4305
|  | STRATTON | HE |  |  |  | 33.6042 | 33.4632 | 33.2747 | 33.0621 | 32.8295 | 32.5495 | 32.2495 | 31.1789 | 30.2032 | 29.2305 | 27.5632 | 25.9263 | -7.5611 | 27.3389 | 27.0937 | 26.3568 | 25.4768 | 24.46 | 23.0032 | 21.5589 | 20.2674 | 19.1274 | 18.0189 | 16.1705 | 14.3158 | 12.5211 | 26.9989 | 26.7516 | 26.0084 | 25.12 | 24.0937 | 22.62 | 21.16 | 19.8537 | 18.7021 | 17.5811 | 15.6937 | 13.8137 | 11.9947
|  | STRATTON | CF |  |  |  | 33.6789 | 33.6042 | 33.5168 | 33.4126 | 33.3011 | 33.1737 | 33.0421 | 32.9116 | 32.7863 | 32.6568 | 32.1958 | 31.5442 | 30.6084 | 27.4137 | 27.3389 | 27.1516 | 26.7305 | 26.2674 | 25.6432 | 24.9653 | 24.3032 | 23.6726 | 23.0042 | 21.6695 | 20.7611 | 19.6326 | 27.0737 | 26.9989 | 26.8105 | 26.3853 | 25.9168 | 25.2853 | 24.6011 | 23.9316 | 23.2947 | 22.6189 | 21.2695 | 20.3347 | 19.1916
LALEHAM | STAINES | SUNBURY CROSS | MINIMUM HEADROOM | TQ 10053 69996 | YES | 3.5263 | 64.2589 | 63.6579 | 63.0516 | 62.4084 | 61.7411 | 61.0526 | 60.36 | 59.7495 | 59.1937 | 58.6789 | 54.64 | 49.9284 | -13.5526 | 57.5137 | 56.3958 | 54.9895 | 53.4832 | 51.8916 | 50.2232 | 48.6095 | 47.5368 | 46.5421 | 45.5874 | 40.1011 | 34.8432 | 29.9105 | 58.5232 | 57.8863 | 57.2274 | 55.74 | 54.1547 | 52.4926 | 50.8842 | 49.8147 | 48.8221 | 47.8705 | 42.4874 | 37.3632 | 32.4337
|  | SUNBURY CROSS | EE |  |  |  | 64.4853 | 64.0116 | 63.5116 | 68.4663 | 67.3389 | 66.1147 | 64.9189 | 63.7232 | 62.7484 | 61.9811 | 58.1137 | 54.5558 | 51.2695 | 57.7537 | 57.1968 | 56.1484 | 55.22 | 53.9937 | 52.6579 | 51.3505 | 50.0389 | 48.9842 | 48.1611 | 43.9126 | 39.9337 | 36.2211 | 58.7642 | 58.2663 | 57.7337 | 57.2916 | 56.0884 | 54.78 | 53.5 | 52.2168 | 51.1821 | 50.3726 | 46.4389 | 42.4589 | 38.7463
|  | SUNBURY CROSS | HT |  |  |  | 64.2589 | 63.6579 | 63.0516 | 62.4084 | 61.7411 | 61.0526 | 60.36 | 59.7495 | 59.1937 | 58.6789 | 54.64 | 49.9284 | 45.5411 | 57.5137 | 56.3958 | 54.9895 | 53.4832 | 51.8916 | 50.2232 | 48.6095 | 47.5368 | 46.5421 | 45.5874 | 40.1011 | 34.8432 | 29.9105 | 58.5232 | 57.8863 | 57.2274 | 55.74 | 54.1547 | 52.4926 | 50.8842 | 49.8147 | 48.8221 | 47.8705 | 42.4874 | 37.3632 | 32.4337
|  | SUNBURY CROSS | HE |  |  |  | 64.7905 | 64.4611 | 64.0968 | 63.6947 | 63.2611 | 62.8 | 62.3589 | 61.9421 | 61.5547 | 61.2189 | 60.0863 | 59.4168 | -13.5526 | 58.0758 | 57.7347 | 57.3537 | 56.6337 | 55.7074 | 54.6516 | 53.6232 | 52.5632 | 51.8274 | 51.2832 | 48.3811 | 45.6779 | 43.1368 | 59.0695 | 58.74 | 58.3621 | 57.9347 | 57.4716 | 56.8926 | 55.88 | 54.8242 | 54.0895 | 53.5463 | 50.6558 | 47.9653 | 45.5021
|  | SUNBURY CROSS | CF |  |  |  | 64.9653 | 64.7716 | 64.5716 | 64.3632 | 64.1474 | 63.9263 | 63.6979 | 63.4747 | 63.2526 | 63.0326 | 62.0474 | 61.5558 | 61.2832 | 58.2589 | 58.0568 | 57.8484 | 57.6305 | 57.4053 | 57.0989 | 56.6442 | 56.1821 | 55.6 | 54.9842 | 51.7958 | 49.9 | 48.2126 | 59.2442 | 59.0505 | 58.8505 | 58.6421 | 58.4147 | 58.1811 | 57.9389 | 57.7011 | 57.4579 | 57.2137 | 54.0621 | 52.1737 | 50.4958
BRAMLEY (FLEE) | BRACKNELL | SUNNINGHILL | MINIMUM HEADROOM | SU 93757 67606 | YES | 0.13684 | 27.5526 | 27.3821 | 27.2116 | 27.0284 | 26.84 | 26.8042 | 26.6084 | 26.4368 | 26.28 | 26.1358 | 24.8389 | 23.6505 | 7.8463 | 24.4484 | 24.1042 | 23.78 | 23.4421 | 23.1053 | 22.9326 | 22.6116 | 22.3189 | 21.9568 | 21.6126 | 20.0474 | 18.6505 | 17.3716 | 24.8895 | 24.7042 | 24.5053 | 24.18 | 23.8537 | 23.6926 | 23.3695 | 23.0779 | 22.7168 | 22.3705 | 20.8063 | 19.4074 | 18.1274
|  | SUNNINGHILL | EE |  |  |  | 27.6189 | 27.4874 | 27.3484 | 27.2 | 27.0442 | 27.04 | 26.8863 | 26.7368 | 26.5958 | 26.4674 | 25.7326 | 24.8179 | 24.0042 | 24.5179 | 24.3305 | 24.0726 | 23.8032 | 23.5295 | 23.4189 | 23.1589 | 22.9147 | 22.6063 | 22.3211 | 21.0695 | 19.9905 | 19.0126 | 24.9611 | 24.8168 | 24.6716 | 24.5158 | 24.2621 | 24.1589 | 23.9063 | 23.6695 | 23.3632 | 23.0779 | 21.8253 | 20.7421 | 19.7642
|  | SUNNINGHILL | HT |  |  |  | 27.5526 | 27.3821 | 27.2116 | 27.0284 | 26.84 | 26.8042 | 26.6084 | 26.4368 | 26.28 | 26.1358 | 24.8389 | 23.6505 | 22.5232 | 24.4484 | 24.1042 | 23.78 | 23.4421 | 23.1053 | 22.9326 | 22.6116 | 22.3189 | 21.9568 | 21.6126 | 20.0474 | 18.6505 | 17.3716 | 24.8895 | 24.7042 | 24.5053 | 24.18 | 23.8537 | 23.6926 | 23.3695 | 23.0779 | 22.7168 | 22.3705 | 20.8063 | 19.4074 | 18.1274
|  | SUNNINGHILL | HE |  |  |  | 27.7095 | 27.6189 | 27.5211 | 27.4116 | 27.2937 | 27.3253 | 27.2042 | 27.0916 | 26.9853 | 26.8926 | 26.5832 | 26.2768 | 7.8463 | 24.6137 | 24.5179 | 24.4137 | 24.2421 | 24.0505 | 24.0147 | 23.8305 | 23.6547 | 23.4505 | 23.2621 | 22.4021 | 21.6547 | 20.9863 | 25.0589 | 24.9611 | 24.8537 | 24.74 | 24.6179 | 24.6463 | 24.5221 | 24.38 | 24.1842 | 24.0021 | 23.16 | 22.4116 | 21.7432
|  | SUNNINGHILL | CF |  |  |  | 27.7589 | 27.7074 | 27.6537 | 27.5979 | 27.5411 | 27.64 | 27.5779 | 27.5189 | 27.4579 | 27.3989 | 27.1358 | 27.0032 | 26.9274 | 24.6663 | 24.6105 | 24.5537 | 24.4958 | 24.4358 | 24.5326 | 24.4389 | 24.3253 | 24.2126 | 24.0811 | 23.4337 | 22.9021 | 22.4526 | 25.1116 | 25.0558 | 24.9968 | 24.9379 | 24.8779 | 24.9737 | 24.9084 | 24.8463 | 24.7832 | 24.72 | 24.18 | 23.66 | 23.2095
MELKSHAM GSP | CHIPPENHAM | SUTTON BENGER | MINIMUM HEADROOM | ST 93394 80051 | YES | 1.9653 | 13.1295 | 13.0663 | 12.9968 | 12.5895 | 12.5337 | 12.4737 | 10.7989 | 10.4326 | 10.3716 | 7.46 | 6.7432 | 5.7968 | 4.4411 | 11.8232 | 11.7379 | 11.5589 | 10.9379 | 10.8832 | 10.8242 | 8.7547 | 8.3126 | 8.2526 | 4.8642 | 4.0758 | 3.0116 | 2.7316 | 12.3042 | 12.2242 | 12.0716 | 11.5274 | 11.4716 | 11.4116 | 9.3084 | 8.8579 | 8.7968 | 5.3853 | 4.5863 | 3.5084 | 3.2242
|  | SUTTON BENGER | EE |  |  |  | 13.1547 | 13.1074 | 13.0537 | 12.5895 | 12.5337 | 12.4737 | 12.4116 | 12.3526 | 12.2958 | 12.2432 | 9.3411 | 8.4042 | 7.8274 | 11.8568 | 11.7937 | 11.7084 | 10.9379 | 10.8832 | 10.8242 | 10.7642 | 10.7084 | 10.6537 | 10.6032 | 7.1084 | 6.0547 | 5.3989 | 12.3358 | 12.2758 | 12.1979 | 11.5274 | 11.4716 | 11.4116 | 11.3495 | 11.2905 | 11.2347 | 11.1811 | 7.6126 | 6.5411 | 5.88
|  | SUTTON BENGER | HT |  |  |  | 13.1295 | 13.0663 | 12.9968 | 12.8779 | 12.7284 | 12.6158 | 10.7989 | 10.4326 | 10.3716 | 7.46 | 6.7432 | 5.7968 | 5.5337 | 11.8232 | 11.7379 | 11.5589 | 11.3168 | 11.1463 | 11.0253 | 8.7547 | 8.3126 | 8.2526 | 4.8642 | 4.0758 | 3.0116 | 2.7316 | 12.3042 | 12.2242 | 12.0716 | 11.8674 | 11.7105 | 11.5947 | 9.3084 | 8.8579 | 8.7968 | 5.3853 | 4.5863 | 3.5084 | 3.2242
|  | SUTTON BENGER | HE |  |  |  | 13.1884 | 13.1579 | 13.1242 | 13.0821 | 13.0326 | 12.9621 | 12.8853 | 12.8211 | 12.7632 | 12.7126 | 10.6832 | 10.0084 | 4.4411 | 11.8905 | 11.8558 | 11.8168 | 11.7095 | 11.5368 | 11.4084 | 11.3253 | 11.2558 | 11.1947 | 11.1411 | 8.6232 | 7.8411 | 7.3158 | 12.3695 | 12.3358 | 12.2979 | 12.2063 | 12.0632 | 11.9516 | 11.8758 | 11.8074 | 11.7495 | 11.6979 | 9.1642 | 8.3632 | 7.8242
|  | SUTTON BENGER | CF |  |  |  | 13.2095 | 13.1926 | 13.1758 | 13.1579 | 13.14 | 13.12 | 13.0979 | 13.0779 | 13.0558 | 13.0326 | 12.8758 | 12.6874 | 12.4684 | 11.9126 | 11.8958 | 11.8779 | 11.8589 | 11.8368 | 11.8095 | 11.7811 | 11.7547 | 11.7232 | 11.6516 | 11.3189 | 11.0979 | 10.8347 | 12.3916 | 12.3737 | 12.3568 | 12.3379 | 12.3168 | 12.2895 | 12.2632 | 12.2379 | 12.2095 | 12.1474 | 11.8653 | 11.6663 | 11.4126
IVER 132KV | UPTON BSP | SUTTON LANE | MINIMUM HEADROOM | TQ 02185 78595 | YES | 1.3389 | 23.2674 | 23.1211 | 22.9737 | 22.8158 | 22.6168 | 22.4137 | 22.2095 | 22.0137 | 21.8758 | 21.7495 | 20.9326 | 19.6863 | 6.0874 | 20.5 | 20.3537 | 20.2063 | 20.0484 | 19.8432 | 19.6337 | 19.4232 | 19.22 | 19.0821 | 18.9558 | 18.0874 | 16.6937 | 15.4189 | 21.1484 | 21.0021 | 20.8547 | 20.6968 | 20.4916 | 20.2821 | 20.0716 | 19.8684 | 19.7305 | 19.6042 | 18.7358 | 17.3421 | 16.0663
|  | SUTTON LANE | EE |  |  |  | 23.3232 | 23.2095 | 23.0884 | 22.9589 | 22.8232 | 22.6832 | 22.5463 | 22.4147 | 22.2895 | 22.1768 | 21.6842 | 20.8453 | 19.9758 | 20.5558 | 20.4421 | 20.3211 | 20.1916 | 20.0558 | 19.9158 | 19.7789 | 19.6474 | 19.5221 | 19.4095 | 18.9032 | 17.9674 | 16.9853 | 21.2042 | 21.0905 | 20.9695 | 20.84 | 20.7042 | 20.5642 | 20.4274 | 20.2958 | 20.1705 | 20.0579 | 19.5516 | 18.6158 | 17.6326
|  | SUTTON LANE | HT |  |  |  | 23.2674 | 23.1211 | 22.9737 | 22.8158 | 22.6168 | 22.4137 | 22.2095 | 22.0137 | 21.8758 | 21.7495 | 20.9326 | 19.6863 | 18.5537 | 20.5 | 20.3537 | 20.2063 | 20.0484 | 19.8432 | 19.6337 | 19.4232 | 19.22 | 19.0821 | 18.9558 | 18.0874 | 16.6937 | 15.4189 | 21.1484 | 21.0021 | 20.8547 | 20.6968 | 20.4916 | 20.2821 | 20.0716 | 19.8684 | 19.7305 | 19.6042 | 18.7358 | 17.3421 | 16.0663
|  | SUTTON LANE | HE |  |  |  | 23.3958 | 23.3137 | 23.2232 | 23.1232 | 23.0147 | 22.9011 | 22.7895 | 22.6874 | 22.5905 | 22.5084 | 22.18 | 21.9263 | 6.0874 | 20.6284 | 20.5463 | 20.4558 | 20.3558 | 20.2474 | 20.1337 | 20.0221 | 19.92 | 19.8232 | 19.7411 | 19.4042 | 19.1358 | 18.6789 | 21.2768 | 21.1947 | 21.1042 | 21.0042 | 20.8958 | 20.7821 | 20.6705 | 20.5684 | 20.4716 | 20.3895 | 20.0537 | 19.7842 | 19.3274
|  | SUTTON LANE | CF |  |  |  | 24.7316 | 23.3874 | 23.3368 | 23.2842 | 23.2316 | 23.1747 | 23.1158 | 23.0589 | 23.0032 | 22.9474 | 22.68 | 22.5084 | 22.3947 | 23.2853 | 20.62 | 20.5695 | 20.5168 | 20.4642 | 20.4074 | 20.3484 | 20.2916 | 20.2358 | 20.18 | 19.9084 | 19.7295 | 19.6084 | 23.7337 | 21.2684 | 21.2179 | 21.1653 | 21.1126 | 21.0558 | 20.9968 | 20.94 | 20.8842 | 20.8284 | 20.5568 | 20.3779 | 20.2568
MANNINGTON GSP | WAREHAM | SWANAGE | MINIMUM HEADROOM | SZ 02010 79296 | YES | 0.072632 | 13.2611 | 42.9916 | 42.7189 | 42.4295 | 42.1211 | 41.3337 | 40.5989 | 40.1053 | 39.6916 | 39.3011 | 37.5474 | 35.6853 | 19.1432 | 10.1221 | 39.6053 | 39.0916 | 38.5737 | 37.9053 | 37.0474 | 36.2389 | 35.7074 | 35.2642 | 34.8463 | 32.9516 | 30.8874 | 28.8116 | 10.5168 | 39.9905 | 39.4705 | 38.9453 | 38.2642 | 37.3937 | 36.5853 | 36.0537 | 35.6105 | 35.1926 | 33.2979 | 31.2326 | 29.1558
|  | SWANAGE | EE |  |  |  | 13.3653 | 43.1537 | 42.9305 | 42.6926 | 42.4432 | 42.0358 | 41.4 | 40.98 | 40.6221 | 40.2937 | 38.9284 | 37.5705 | 36.1905 | 10.3526 | 39.9516 | 39.5442 | 39.1295 | 38.5589 | 37.8011 | 37.1053 | 36.6526 | 36.2726 | 35.9232 | 34.4495 | 32.9442 | 31.3895 | 10.7411 | 40.3432 | 39.9295 | 39.5095 | 38.9295 | 38.1558 | 37.4526 | 37 | 36.6189 | 36.2695 | 34.7947 | 33.2895 | 31.7347
|  | SWANAGE | HT |  |  |  | 13.2611 | 42.9916 | 42.7189 | 42.4295 | 42.1211 | 41.3337 | 40.5989 | 40.1053 | 39.6916 | 39.3011 | 37.5474 | 35.6853 | 33.8337 | 10.1221 | 39.6053 | 39.0916 | 38.5737 | 37.9053 | 37.0474 | 36.2389 | 35.7074 | 35.2642 | 34.8463 | 32.9516 | 30.8874 | 28.8116 | 10.5168 | 39.9905 | 39.4705 | 38.9453 | 38.2642 | 37.3937 | 36.5853 | 36.0537 | 35.6105 | 35.1926 | 33.2979 | 31.2326 | 29.1558
|  | SWANAGE | HE |  |  |  | 13.5032 | 43.3558 | 43.1937 | 43.0147 | 42.8221 | 42.6158 | 42.4084 | 42.0937 | 41.8463 | 41.6253 | 40.7821 | 39.9158 | 19.1432 | 10.6116 | 40.4021 | 40.1326 | 39.8505 | 39.4084 | 38.7642 | 38.1916 | 37.86 | 37.6011 | 37.3705 | 36.4716 | 35.5074 | 34.4726 | 11.0116 | 40.7779 | 40.5295 | 40.2442 | 39.7937 | 39.1358 | 38.5516 | 38.2147 | 37.9537 | 37.72 | 36.8179 | 35.8537 | 34.8189
|  | SWANAGE | CF |  |  |  | 13.5821 | 43.4968 | 43.4084 | 43.3168 | 43.2211 | 43.1232 | 43.0221 | 42.9242 | 42.8263 | 42.7284 | 42.2926 | 41.6989 | 41.0842 | 10.7021 | 40.6063 | 40.4968 | 40.3284 | 40.0937 | 39.7842 | 39.4811 | 39.2779 | 39.1032 | 38.9284 | 38.1232 | 37.4326 | 36.7305 | 11.1147 | 41.0126 | 40.8632 | 40.7116 | 40.4884 | 40.1716 | 39.8621 | 39.6558 | 39.4789 | 39.3021 | 38.4853 | 37.7789 | 37.0768
MINETY GSP | SWINDON BSP | SWINDON | MINIMUM HEADROOM | SU 12449 86967 | YES | 1.5526 | 67.2495 | 66.5053 | 65.7442 | 64.4063 | 63.0263 | 61.6232 | 60.2253 | 58.9442 | 57.7505 | 56.6168 | 50.7968 | 43.4063 | -4.2147 | 58.9179 | 57.74 | 56.1621 | 54.6874 | 53.2053 | 51.7032 | 50.2084 | 48.8316 | 47.5484 | 46.3253 | 39.9232 | 31.5484 | 23.4716 | 60.6905 | 59.5137 | 57.9358 | 56.4632 | 54.9821 | 53.48 | 51.9842 | 50.6084 | 49.3242 | 48.1011 | 41.6968 | 33.3232 | 25.2537
|  | SWINDON | EE |  |  |  | 67.5284 | 66.9421 | 66.3211 | 65.6589 | 64.6516 | 63.4979 | 62.3747 | 61.2958 | 60.2421 | 59.2821 | 54.8642 | 49.0505 | 43.4653 | 59.2326 | 58.5853 | 57.5305 | 56.1779 | 54.9747 | 53.7411 | 52.5421 | 51.3874 | 50.2589 | 49.2274 | 44.3979 | 37.7968 | 31.3842 | 61.0042 | 60.3568 | 59.3032 | 57.9516 | 56.7484 | 55.5168 | 54.3158 | 53.1611 | 52.0316 | 50.9989 | 46.16 | 39.5537 | 33.1463
|  | SWINDON | HT |  |  |  | 67.2495 | 66.5053 | 65.7442 | 64.4063 | 63.0263 | 61.6232 | 60.2253 | 58.9442 | 57.7505 | 56.6168 | 50.7968 | 43.4063 | 36.3368 | 58.9179 | 57.74 | 56.1621 | 54.6874 | 53.2053 | 51.7032 | 50.2084 | 48.8316 | 47.5484 | 46.3253 | 39.9232 | 31.5484 | 23.4716 | 60.6905 | 59.5137 | 57.9358 | 56.4632 | 54.9821 | 53.48 | 51.9842 | 50.6084 | 49.3242 | 48.1011 | 41.6968 | 33.3232 | 25.2537
|  | SWINDON | HE |  |  |  | 67.9242 | 67.5253 | 67.0842 | 66.5958 | 66.0705 | 65.5074 | 64.9695 | 64.4063 | 63.6589 | 62.9989 | 60.0295 | 55.5684 | -4.2147 | 59.6284 | 59.2295 | 58.7779 | 58.2495 | 57.38 | 56.4779 | 55.6137 | 54.7789 | 53.9821 | 53.2789 | 50.0242 | 44.9021 | 39.8789 | 61.4 | 61.0011 | 60.5495 | 60.0221 | 59.1526 | 58.2516 | 57.3853 | 56.5495 | 55.7547 | 55.0505 | 51.7937 | 46.6747 | 41.6558
|  | SWINDON | CF |  |  |  | 68.1537 | 67.9284 | 67.6937 | 67.4516 | 67.1989 | 66.9379 | 66.6716 | 66.4084 | 66.1495 | 65.8895 | 64.1579 | 61.6179 | 58.9126 | 59.8579 | 59.6326 | 59.3979 | 59.1558 | 58.8863 | 58.5979 | 58.2547 | 57.7558 | 57.2547 | 56.7516 | 54.4368 | 51.5442 | 48.4074 | 61.6295 | 61.4042 | 61.1695 | 60.9274 | 60.6589 | 60.3684 | 60.0253 | 59.5274 | 59.0253 | 58.5232 | 56.2084 | 53.3179 | 50.1832
BRAMLEY (ANDO-THAT) | THATCHAM BSP | TADLEY | MINIMUM HEADROOM | SU 57753 62717 | YES | 0.31263 | 27.8347 | 27.6232 | 27.4084 | 27.1821 | 26.9463 | 26.7021 | 26.4547 | 26.2389 | 26.0389 | 25.8568 | 25.1042 | 24.5274 | 7.3642 | 23.8958 | 23.5779 | 23.26 | 22.9347 | 22.6042 | 22.2726 | 21.9305 | 21.6242 | 21.3379 | 21.0737 | 19.3916 | 17.6937 | 16.2958 | 24.5716 | 24.2926 | 24.0126 | 23.7232 | 23.4263 | 23.1263 | 22.8179 | 22.5421 | 22.2853 | 22.0495 | 21.0463 | 20.1747 | 19.3737
|  | TADLEY | EE |  |  |  | 27.9179 | 27.7526 | 27.5768 | 27.3884 | 27.1947 | 26.9916 | 26.7926 | 26.6042 | 26.4211 | 26.2558 | 25.6379 | 28.2263 | 27.2284 | 24.0337 | 23.7874 | 23.5326 | 23.2684 | 23 | 22.7274 | 22.4632 | 22.2042 | 21.9526 | 21.7211 | 20.3842 | 27.3989 | 26.3032 | 24.6895 | 24.4737 | 24.2474 | 24.0105 | 23.7684 | 23.52 | 23.2779 | 23.0432 | 22.8137 | 22.6032 | 21.7853 | 29.8453 | 28.7526
|  | TADLEY | HT |  |  |  | 27.8347 | 27.6232 | 27.4084 | 27.1821 | 26.9463 | 26.7021 | 26.4547 | 26.2389 | 26.0389 | 25.8568 | 25.1042 | 24.5274 | 23.7463 | 23.8958 | 23.5779 | 23.26 | 22.9347 | 22.6042 | 22.2726 | 21.9305 | 21.6242 | 21.3379 | 21.0737 | 19.3916 | 17.6937 | 16.2958 | 24.5716 | 24.2926 | 24.0126 | 23.7232 | 23.4263 | 23.1263 | 22.8179 | 22.5421 | 22.2853 | 22.0495 | 21.0463 | 20.1747 | 19.3737
|  | TADLEY | HE |  |  |  | 28.0326 | 27.9211 | 27.7989 | 27.6642 | 27.5179 | 27.3589 | 27.2074 | 27.0632 | 26.9295 | 26.8137 | 26.4126 | 26.1768 | 7.3642 | 24.2211 | 24.0642 | 23.8958 | 23.7158 | 23.5253 | 23.3242 | 23.1316 | 22.9474 | 22.7716 | 22.6147 | 22.0526 | 21.6842 | 21.2905 | 24.8516 | 24.7105 | 24.5589 | 24.3958 | 24.2211 | 24.0347 | 23.8558 | 23.6853 | 23.5242 | 23.38 | 22.8695 | 22.5432 | 22.2347
|  | TADLEY | CF |  |  |  | 28.0979 | 28.0368 | 27.9726 | 27.9063 | 27.8389 | 27.7653 | 27.6916 | 27.6189 | 27.5474 | 27.4747 | 27.1547 | 26.9884 | 26.8916 | 24.3189 | 24.2232 | 24.1274 | 24.0295 | 23.9295 | 23.8232 | 23.7137 | 23.6074 | 23.5021 | 23.3979 | 22.9158 | 22.6095 | 22.3684 | 24.9368 | 24.8537 | 24.7695 | 24.6832 | 24.5947 | 24.5 | 24.4032 | 24.3084 | 24.2147 | 24.1221 | 23.6968 | 23.4389 | 23.2453
IVER 132KV | SLOUGH | TAPLOW | MINIMUM HEADROOM | SU 91721 81234 | YES | 0.31579 | 34.3158 | 34.0379 | 33.7558 | 33.4589 | 33.1505 | 32.8253 | 32.4979 | 32.2084 | 31.9442 | 31.6968 | 30.4021 | 28.4421 | 6.1695 | 30.5084 | 30.1011 | 29.5632 | 29.0189 | 28.4779 | 27.9411 | 27.3989 | 26.8516 | 26.3147 | 25.7958 | 23.4 | 21.2579 | 19.3621 | 31.2958 | 31.0032 | 30.7053 | 30.2526 | 29.7179 | 29.18 | 28.6358 | 28.0863 | 27.5484 | 27.0263 | 24.6137 | 22.4516 | 20.5484
|  | TAPLOW | EE |  |  |  | 34.4221 | 34.2032 | 33.9726 | 33.7263 | 33.4705 | 33.1968 | 32.9295 | 32.6758 | 32.4295 | 32.2053 | 31.3537 | 30.3242 | 29.04 | 30.6326 | 30.3874 | 30.0358 | 29.5979 | 29.16 | 28.7211 | 28.2905 | 27.8411 | 27.3768 | 26.9411 | 25.0116 | 23.3432 | 21.9168 | 31.4095 | 31.1789 | 30.9379 | 30.68 | 30.3884 | 29.9547 | 29.5242 | 29.0726 | 28.6063 | 28.1653 | 26.2105 | 24.5137 | 23.08
|  | TAPLOW | HT |  |  |  | 34.3158 | 34.0379 | 33.7558 | 33.4589 | 33.1505 | 32.8253 | 32.4979 | 32.2084 | 31.9442 | 31.6968 | 30.4021 | 28.4421 | 26.7316 | 30.5084 | 30.1011 | 29.5632 | 29.0189 | 28.4779 | 27.9411 | 27.3989 | 26.8516 | 26.3147 | 25.7958 | 23.4 | 21.2579 | 19.3621 | 31.2958 | 31.0032 | 30.7053 | 30.2526 | 29.7179 | 29.18 | 28.6358 | 28.0863 | 27.5484 | 27.0263 | 24.6137 | 22.4516 | 20.5484
|  | TAPLOW | HE |  |  |  | 34.5642 | 34.4137 | 34.2484 | 34.0642 | 33.8653 | 33.6495 | 33.4432 | 33.2484 | 33.0653 | 32.9053 | 32.3526 | 32.0211 | 6.1695 | 30.7979 | 30.6326 | 30.4526 | 30.2537 | 30.04 | 29.7421 | 29.4358 | 29.1126 | 28.7768 | 28.4674 | 27.1695 | 26.1189 | 25.2274 | 31.5621 | 31.4053 | 31.2337 | 31.0421 | 30.8368 | 30.6158 | 30.4042 | 30.2021 | 29.9989 | 29.6926 | 28.3916 | 27.3347 | 26.4347
|  | TAPLOW | CF |  |  |  | 34.6463 | 34.5589 | 34.4684 | 34.3747 | 34.2768 | 34.1737 | 34.0684 | 33.9663 | 33.8632 | 33.7632 | 33.3053 | 33.0653 | 32.9263 | 30.8895 | 30.7916 | 30.6905 | 30.5863 | 30.4768 | 30.3653 | 30.2495 | 30.0989 | 29.8895 | 29.68 | 28.6495 | 27.8674 | 27.2158 | 31.6484 | 31.5568 | 31.4611 | 31.3632 | 31.26 | 31.1526 | 31.0421 | 30.9347 | 30.8263 | 30.72 | 29.8832 | 29.0968 | 28.44
MANNINGTON GSP | SHAFTESBURY BSP | TARRANT RUSHTON | MINIMUM HEADROOM | ST 94510 07307 | YES | 0.093684 | 7.7042 | 7.6663 | 7.58 | 7.3547 | 7.0905 | 6.7958 | 6.4821 | 6.1758 | 5.8695 | 5.5716 | 5.1021 | 4.8284 | -0.13158 | 6.4947 | 6.3326 | 6.0937 | 5.8158 | 5.4905 | 5.1242 | 4.7621 | 4.4074 | 4.0516 | 3.7053 | 3.1747 | 2.8684 | 2.5421 | 6.8168 | 6.6453 | 6.4137 | 6.1453 | 5.8295 | 5.4747 | 5.1221 | 4.7674 | 4.4126 | 4.0653 | 3.5347 | 3.2284 | 2.9021
|  | TARRANT RUSHTON | EE |  |  |  | 7.7189 | 7.6895 | 7.6358 | 7.4242 | 7.1737 | 6.8895 | 6.5926 | 6.2979 | 6.0032 | 5.7137 | 5.3011 | 5.0979 | 4.8832 | 6.5105 | 6.3821 | 6.1579 | 5.8947 | 5.5832 | 5.2295 | 4.8821 | 4.54 | 4.1979 | 3.8611 | 3.3916 | 3.1642 | 2.9189 | 6.8474 | 6.6937 | 6.4768 | 6.2221 | 5.9211 | 5.5779 | 5.2421 | 4.9 | 4.5579 | 4.2211 | 3.7516 | 3.5242 | 3.2789
|  | TARRANT RUSHTON | HT |  |  |  | 7.7042 | 7.6663 | 7.58 | 7.3547 | 7.0905 | 6.7958 | 6.4821 | 6.1758 | 5.8695 | 5.5716 | 5.1021 | 4.8284 | 4.54 | 6.4947 | 6.3326 | 6.0937 | 5.8158 | 5.4905 | 5.1242 | 4.7621 | 4.4074 | 4.0516 | 3.7053 | 3.1747 | 2.8684 | 2.5421 | 6.8168 | 6.6453 | 6.4137 | 6.1453 | 5.8295 | 5.4747 | 5.1221 | 4.7674 | 4.4126 | 4.0653 | 3.5347 | 3.2284 | 2.9021
|  | TARRANT RUSHTON | HE |  |  |  | 7.7389 | 7.72 | 7.6979 | 7.5168 | 7.2821 | 7.0147 | 6.7389 | 6.4579 | 6.1779 | 5.9032 | 5.5611 | 5.4232 | -0.13158 | 6.5316 | 6.4474 | 6.2442 | 6 | 5.7063 | 5.3705 | 5.0411 | 4.7137 | 4.3884 | 4.0663 | 3.6747 | 3.52 | 3.3421 | 6.8821 | 6.7589 | 6.5621 | 6.3253 | 6.0421 | 5.7168 | 5.3979 | 5.0737 | 4.7484 | 4.4274 | 4.0358 | 3.88 | 3.7021
|  | TARRANT RUSHTON | CF |  |  |  | 7.7516 | 7.7411 | 7.7295 | 7.7179 | 7.6789 | 7.5674 | 7.4463 | 7.3147 | 7.1737 | 7.0232 | 6.7895 | 6.7 | 6.6074 | 6.5453 | 6.5305 | 6.4368 | 6.3253 | 6.1989 | 6.0589 | 5.9074 | 5.7421 | 5.5653 | 5.3747 | 5.1011 | 5 | 4.8937 | 6.9021 | 6.8432 | 6.7474 | 6.6411 | 6.5179 | 6.3832 | 6.2358 | 6.0768 | 5.9053 | 5.7221 | 5.4558 | 5.3579 | 5.2537
MANNINGTON GSP | SALISBURY | TEFFONT | MINIMUM HEADROOM | ST 99837 30994 | YES | 0 | 6.3937 | 6.2853 | 6.1779 | 6.0674 | 5.9547 | 5.8453 | 5.7358 | 5.6368 | 5.5442 | 5.4516 | 4.9705 | 4.4947 | -0.48632 | 4.8863 | 4.7705 | 4.6537 | 4.5368 | 4.4168 | 4.3 | 4.1832 | 4.0779 | 3.9789 | 3.8789 | 3.3505 | 2.8179 | 2.2747 | 5.2158 | 5.1084 | 4.9989 | 4.8895 | 4.7726 | 4.6568 | 4.5411 | 4.4368 | 4.3389 | 4.24 | 3.7179 | 3.1958 | 2.66
|  | TEFFONT | EE |  |  |  | 6.4421 | 6.36 | 6.2779 | 6.1926 | 6.1032 | 6.0116 | 5.9253 | 5.8432 | 5.7632 | 5.6905 | 5.3305 | 4.9674 | 4.6147 | 4.9389 | 4.8516 | 4.7632 | 4.6716 | 4.5768 | 4.48 | 4.3884 | 4.3 | 4.2147 | 4.1379 | 3.7432 | 3.3358 | 2.9347 | 5.2653 | 5.1832 | 5.1 | 5.0147 | 4.9242 | 4.8337 | 4.7432 | 4.6568 | 4.5726 | 4.4958 | 4.1063 | 3.7063 | 3.3137
|  | TEFFONT | HT |  |  |  | 6.3937 | 6.2853 | 6.1779 | 6.0674 | 5.9547 | 5.8453 | 5.7358 | 5.6368 | 5.5442 | 5.4516 | 4.9705 | 4.4947 | 4.0168 | 4.8863 | 4.7705 | 4.6537 | 4.5368 | 4.4168 | 4.3 | 4.1832 | 4.0779 | 3.9789 | 3.8789 | 3.3505 | 2.8179 | 2.2747 | 5.2158 | 5.1084 | 4.9989 | 4.8895 | 4.7726 | 4.6568 | 4.5411 | 4.4368 | 4.3389 | 4.24 | 3.7179 | 3.1958 | 2.66
|  | TEFFONT | HE |  |  |  | 6.4979 | 6.4579 | 6.4042 | 6.3484 | 6.2874 | 6.2211 | 6.1589 | 6.1011 | 6.0453 | 5.9958 | 5.7526 | 5.4895 | -0.48632 | 5.0105 | 4.9568 | 4.9 | 4.8421 | 4.7758 | 4.7063 | 4.6411 | 4.58 | 4.5211 | 4.4684 | 4.2011 | 3.9032 | 3.6063 | 5.3316 | 5.28 | 5.2274 | 5.1716 | 5.1095 | 5.0432 | 4.9811 | 4.9232 | 4.8674 | 4.8179 | 4.5589 | 4.2663 | 3.9747
|  | TEFFONT | CF |  |  |  | 6.5168 | 6.5011 | 6.4842 | 6.4516 | 6.4189 | 6.3832 | 6.3453 | 6.3105 | 6.2789 | 6.2442 | 6.0895 | 5.9368 | 5.7568 | 5.0484 | 5.0168 | 4.9842 | 4.9495 | 4.9147 | 4.8758 | 4.8347 | 4.7979 | 4.7642 | 4.7274 | 4.56 | 4.3874 | 4.1821 | 5.3663 | 5.3368 | 5.3074 | 5.2747 | 5.2421 | 5.2063 | 5.1674 | 5.1326 | 5.1011 | 5.0674 | 4.9116 | 4.7453 | 4.5432
BRAMLEY (FLEE) | MAIDENHEAD BSP | TEMPLE FARM | MINIMUM HEADROOM | SU 84178 83872 | YES | 0 | 5.1021 | 5.0811 | 5.0589 | 5.0358 | 5.0116 | 4.9874 | 4.9621 | 4.94 | 4.92 | 4.9021 | 4.8274 | 4.7737 | 0.028421 | 4.2589 | 4.2379 | 4.2042 | 4.1632 | 4.1221 | 4.0832 | 4.0421 | 4.0063 | 3.9726 | 3.9411 | 3.7989 | 3.6842 | 3.5811 | 3.9305 | 3.8895 | 3.8495 | 3.8084 | 3.7674 | 3.7284 | 3.6884 | 3.6526 | 3.6189 | 3.5884 | 3.4474 | 3.3326 | 3.2305
|  | TEMPLE FARM | EE |  |  |  | 5.1105 | 5.0937 | 5.0758 | 5.0568 | 5.0368 | 5.0158 | 4.9968 | 4.9768 | 4.9589 | 4.9432 | 4.8842 | 4.8432 | 4.8158 | 4.2674 | 4.2505 | 4.2326 | 4.2084 | 4.1758 | 4.1421 | 4.1116 | 4.0811 | 4.0526 | 4.0263 | 3.9179 | 3.8305 | 3.7579 | 3.9495 | 3.9168 | 3.8853 | 3.8537 | 3.82 | 3.7874 | 3.7568 | 3.7263 | 3.6979 | 3.6716 | 3.5642 | 3.4768 | 3.4053
|  | TEMPLE FARM | HT |  |  |  | 5.1021 | 5.0811 | 5.0589 | 5.0358 | 5.0116 | 4.9874 | 4.9621 | 4.94 | 4.92 | 4.9021 | 4.8274 | 4.7737 | 4.6811 | 4.2589 | 4.2379 | 4.2042 | 4.1632 | 4.1221 | 4.0832 | 4.0421 | 4.0063 | 3.9726 | 3.9411 | 3.7989 | 3.6842 | 3.5811 | 3.9305 | 3.8895 | 3.8495 | 3.8084 | 3.7674 | 3.7284 | 3.6884 | 3.6526 | 3.6189 | 3.5884 | 3.4474 | 3.3326 | 3.2305
|  | TEMPLE FARM | HE |  |  |  | 5.1232 | 5.1116 | 5.0989 | 5.0853 | 5.0705 | 5.0547 | 5.04 | 5.0253 | 5.0116 | 5 | 4.96 | 4.9389 | 0.028421 | 4.28 | 4.2684 | 4.2558 | 4.2421 | 4.2274 | 4.2116 | 4.1968 | 4.1821 | 4.1621 | 4.1453 | 4.0811 | 4.0368 | 4.0021 | 3.9747 | 3.9558 | 3.9347 | 3.9137 | 3.8916 | 3.8684 | 3.8474 | 3.8274 | 3.8074 | 3.7905 | 3.7253 | 3.6821 | 3.6484
|  | TEMPLE FARM | CF |  |  |  | 5.1295 | 5.1232 | 5.1168 | 5.1105 | 5.1032 | 5.0968 | 5.0895 | 5.0821 | 5.0747 | 5.0674 | 5.0347 | 5.0189 | 5.0105 | 4.2863 | 4.28 | 4.2737 | 4.2674 | 4.26 | 4.2537 | 4.2463 | 4.2389 | 4.2316 | 4.2242 | 4.1716 | 4.1326 | 4.1032 | 3.9863 | 3.9747 | 3.9621 | 3.9505 | 3.9368 | 3.9253 | 3.9126 | 3.9 | 3.8874 | 3.8747 | 3.8158 | 3.7779 | 3.7495
MELKSHAM GSP | CHIPPENHAM | TETBURY | MINIMUM HEADROOM | ST 89708 93444 | YES | 0.061053 | 9.7589 | 9.5263 | 9.2621 | 8.9747 | 8.6358 | 8.2484 | 7.9368 | 7.6411 | 7.36 | 5.9042 | 5.2295 | 4.2663 | -2.3189 | 7.5958 | 7.3263 | 7.0453 | 6.7379 | 6.3747 | 5.9558 | 5.6253 | 5.3105 | 5.0105 | 3.3726 | 2.6895 | 1.6653 | 0.24421 | 8.3505 | 8.0768 | 7.7916 | 7.4789 | 7.1074 | 6.68 | 6.3432 | 6.0221 | 5.7147 | 4.0263 | 3.3274 | 2.2674 | 0.80632
|  | TETBURY | EE |  |  |  | 9.8116 | 9.6968 | 9.4926 | 9.2663 | 9.0126 | 8.7147 | 8.4547 | 8.2095 | 7.9737 | 7.7863 | 6.6537 | 5.4568 | 4.4453 | 7.7137 | 7.5084 | 7.2916 | 7.2779 | 7.0021 | 6.6768 | 6.3979 | 6.1337 | 5.8821 | 5.6863 | 4.4579 | 3.1368 | 1.9926 | 8.4716 | 8.2632 | 8.0421 | 7.7989 | 7.5232 | 7.1968 | 6.9147 | 6.6505 | 6.3958 | 6.1947 | 4.9453 | 3.5989 | 2.4484
|  | TETBURY | HT |  |  |  | 9.7589 | 9.5263 | 9.2621 | 8.9747 | 8.6358 | 8.2484 | 7.9368 | 7.6411 | 7.36 | 5.9042 | 5.2295 | 4.2663 | 2.9768 | 7.5958 | 7.3263 | 7.0453 | 6.7379 | 6.3747 | 5.9558 | 5.6253 | 5.3105 | 5.0105 | 3.3726 | 2.6895 | 1.6653 | 0.24421 | 8.3505 | 8.0768 | 7.7916 | 7.4789 | 7.1074 | 6.68 | 6.3432 | 6.0221 | 5.7147 | 4.0263 | 3.3274 | 2.2674 | 0.80632
|  | TETBURY | HE |  |  |  | 9.8853 | 9.8126 | 9.7326 | 9.6221 | 9.4316 | 9.1863 | 8.9884 | 8.8063 | 8.6326 | 8.5074 | 7.6895 | 6.8042 | -2.3189 | 7.8463 | 7.7442 | 7.6011 | 7.4316 | 7.2284 | 6.9653 | 6.7558 | 6.5621 | 6.3779 | 6.2484 | 5.3632 | 4.3842 | 3.5189 | 8.6053 | 8.5021 | 8.3568 | 8.1853 | 7.9789 | 7.7095 | 7.4947 | 7.2979 | 7.1095 | 6.9758 | 6.0653 | 5.0558 | 4.1611
|  | TETBURY | CF |  |  |  | 9.9284 | 9.8874 | 9.8463 | 9.8021 | 9.7568 | 9.7084 | 9.6263 | 9.5274 | 9.4253 | 9.3326 | 8.7274 | 8.1579 | 7.6558 | 7.8895 | 7.8484 | 7.7947 | 7.7084 | 7.6211 | 7.5295 | 7.4347 | 7.3305 | 7.22 | 7.1221 | 6.4674 | 5.8389 | 5.2811 | 8.6484 | 8.6074 | 8.5537 | 8.4653 | 8.3768 | 8.2832 | 8.1874 | 8.08 | 7.9684 | 7.8674 | 7.1958 | 6.5484 | 5.9716
BRAMLEY (ANDO-THAT) | THATCHAM BSP | THATCHAM | MINIMUM HEADROOM | SU 52758 66466 | YES | 1.2105 | 36.1611 | 35.6811 | 35.1968 | 34.6821 | 34.1516 | 33.5632 | 32.1568 | 30.2821 | 28.5895 | 27.0705 | 19.8811 | 15.8842 | -17.2274 | 28.8874 | 28.4074 | 27.7842 | 26.86 | 25.6905 | 24.4979 | 22.9674 | 20.8947 | 18.9842 | 17.2663 | 9.0874 | 4.5989 | 1.2295 | 30.1011 | 29.6211 | 28.9979 | 28.0768 | 26.9105 | 25.7211 | 24.1968 | 22.1326 | 20.2684 | 18.5979 | 10.6474 | 6.1537 | 2.7842
|  | THATCHAM | EE |  |  |  | 36.3432 | 35.9663 | 35.5695 | 35.1442 | 34.7032 | 34.2442 | 33.8011 | 32.4537 | 30.6011 | 29.1242 | 22.3516 | 19.0537 | 16.7747 | 29.0695 | 28.6926 | 28.2958 | 27.8411 | 26.9474 | 26.0042 | 24.8768 | 23.2632 | 21.2042 | 19.5305 | 11.78 | 8.0747 | 5.5011 | 30.2832 | 29.9063 | 29.5095 | 29.0547 | 28.1621 | 27.2221 | 26.0989 | 24.4905 | 22.44 | 20.8105 | 13.2926 | 9.6158 | 7.04
|  | THATCHAM | HT |  |  |  | 36.1611 | 35.6811 | 35.1968 | 34.6821 | 34.1516 | 33.5632 | 32.1568 | 30.2821 | 28.5895 | 27.0705 | 19.8811 | 15.8842 | 12.8821 | 28.8874 | 28.4074 | 27.7842 | 26.86 | 25.6905 | 24.4979 | 22.9674 | 20.8947 | 18.9842 | 17.2663 | 9.0874 | 4.5989 | 1.2295 | 30.1011 | 29.6211 | 28.9979 | 28.0768 | 26.9105 | 25.7211 | 24.1968 | 22.1326 | 20.2684 | 18.5979 | 10.6474 | 6.1537 | 2.7842
|  | THATCHAM | HE |  |  |  | 36.6032 | 36.3505 | 36.0705 | 35.7621 | 35.4295 | 35.0726 | 34.7316 | 34.4105 | 32.7453 | 31.4926 | 25.7242 | 23.2632 | -17.2274 | 29.3295 | 29.0768 | 28.7968 | 28.4884 | 28.1558 | 27.76 | 26.8347 | 25.3537 | 23.4895 | 22.0947 | 15.4495 | 12.6242 | 10.9579 | 30.5432 | 30.2905 | 30.0105 | 29.7021 | 29.3695 | 28.9737 | 28.0505 | 26.5758 | 24.7211 | 23.3337 | 16.8958 | 14.1484 | 12.5105
|  | THATCHAM | CF |  |  |  | 36.7537 | 36.6137 | 36.4684 | 36.3168 | 36.16 | 35.9979 | 35.8316 | 35.6674 | 35.5074 | 35.3442 | 32.6368 | 29.2368 | 28.2463 | 30.6295 | 29.34 | 29.1947 | 29.0432 | 28.8863 | 28.7242 | 28.5579 | 28.3947 | 28.2337 | 27.74 | 23.2926 | 19.3632 | 18.2316 | 31.5421 | 30.5537 | 30.4084 | 30.2568 | 30.1 | 29.9368 | 29.7716 | 29.6074 | 29.4463 | 28.9537 | 24.5284 | 20.7126 | 19.6147
NORTH HYDE GSP | NORTH HYDE 22kV | THE GREEN | MINIMUM HEADROOM | TQ 12414 79503 | NO | 0.17263 | 14.8905 | 14.3853 | 11.7379 | 11.6516 | 10.8484 | 9.5105 | 8.0242 | 6.9674 | 6.9063 | 6.8432 | 6.5347 | 6.3168 | -10.72 | 11.7347 | 10.0516 | 6.8863 | 6.8 | 5.7916 | 4.1884 | 2.4042 | 1.1379 | 1.0726 | 1.0042 | 0.66737 | 0.42105 | 0.20211 | 12.4284 | 10.7179 | 7.5432 | 7.4568 | 6.4484 | 4.8442 | 3.06 | 1.7926 | 1.7274 | 1.6589 | 1.3221 | 1.0758 | 0.85684
|  | THE GREEN | EE |  |  |  | 14.9232 | 14.5421 | 12.0811 | 12.0105 | 12.0821 | 12.0032 | 11.9263 | 9.7105 | 9.5832 | 9.4642 | 8.9674 | 8.4853 | 7.9842 | 11.8242 | 10.2274 | 7.2863 | 7.2158 | 7.1411 | 7.0905 | 7.0137 | 4.42 | 4.2842 | 4.1558 | 3.6147 | 3.0958 | 2.5305 | 12.52 | 10.8958 | 7.9432 | 7.8726 | 7.7979 | 7.7189 | 7.6421 | 5.0537 | 4.9168 | 4.7884 | 4.2495 | 3.7337 | 3.1695
|  | THE GREEN | HT |  |  |  | 14.8905 | 14.3853 | 11.7379 | 11.6516 | 11.6989 | 11.6042 | 11.5063 | 9.0526 | 8.9063 | 8.7663 | 8.1284 | 7.3884 | 6.6695 | 11.7347 | 10.0516 | 6.8863 | 6.8 | 6.7084 | 6.6421 | 6.5442 | 3.6726 | 3.5147 | 3.3621 | 2.6842 | 1.8568 | 1.0484 | 12.4284 | 10.7179 | 7.5432 | 7.4568 | 7.3653 | 7.2705 | 7.1726 | 4.3074 | 4.1495 | 3.9968 | 3.3221 | 2.4968 | 1.6895
|  | THE GREEN | HE |  |  |  | 14.9526 | 14.6463 | 12.2158 | 12.1558 | 12.2389 | 12.1695 | 12.1032 | 9.9147 | 9.82 | 9.7337 | 9.4116 | 9.0442 | -10.72 | 11.9042 | 10.3442 | 7.4379 | 7.3779 | 7.3126 | 7.2726 | 7.2063 | 4.6411 | 4.5411 | 4.4484 | 4.1011 | 3.6726 | 3.3042 | 12.6 | 11.0137 | 8.0958 | 8.0358 | 7.9705 | 7.9011 | 7.8347 | 5.2747 | 5.1737 | 5.0811 | 4.7337 | 4.3032 | 3.9358
|  | THE GREEN | CF |  |  |  | 14.9726 | 14.94 | 14.4842 | 12.5263 | 10.8484 | 9.5105 | 8.0242 | 6.9674 | 6.9063 | 6.8432 | 6.5347 | 6.3168 | 6.1263 | 12.32 | 11.5 | 10.1516 | 7.8074 | 5.7916 | 4.1884 | 2.4042 | 1.1379 | 1.0726 | 1.0042 | 0.66737 | 0.42105 | 0.20211 | 13.0232 | 12.1895 | 10.8179 | 8.4642 | 6.4484 | 4.8442 | 3.06 | 1.7926 | 1.7274 | 1.6589 | 1.3221 | 1.0758 | 0.85684
BRAMLEY (FLEE) | READING TOWN BSP | THE MALL | MINIMUM HEADROOM | SU 71319 73293 | YES | 0.47579 | 35.0095 | 34.8926 | 34.7747 | 34.6421 | 34.4547 | 33.5305 | 32.6042 | 31.6937 | 30.7947 | 29.9095 | 29.0168 | 28.0453 | 7.0926 | 31.1705 | 31.0537 | 30.9358 | 30.7758 | 30.2232 | 28.4347 | 27.3642 | 26.3116 | 25.2695 | 24.2411 | 23.2695 | 22.1874 | 21.1189 | 31.7989 | 31.6821 | 31.5642 | 31.4242 | 31.2484 | 29.9063 | 28.8389 | 27.7874 | 26.7463 | 25.7211 | 24.7495 | 23.6684 | 22.6021
|  | THE MALL | EE |  |  |  | 35.0589 | 34.9695 | 34.8747 | 34.7737 | 34.6137 | 34.0747 | 33.4526 | 32.7316 | 31.72 | 30.6768 | 29.6863 | 28.9537 | 28.2547 | 31.22 | 31.1305 | 31.0358 | 30.9074 | 30.4705 | 29.06 | 28.3305 | 27.4968 | 26.3211 | 25.1042 | 23.9989 | 23.18 | 22.3905 | 31.8484 | 31.7589 | 31.6642 | 31.5558 | 31.4053 | 30.5316 | 29.8032 | 28.9705 | 27.7968 | 26.5832 | 25.4779 | 24.6611 | 23.8726
|  | THE MALL | HT |  |  |  | 35.0095 | 34.8926 | 34.7747 | 34.6421 | 34.4547 | 33.5305 | 32.6042 | 31.6937 | 30.7947 | 29.9095 | 29.0168 | 28.0453 | 27.0968 | 31.1705 | 31.0537 | 30.9358 | 30.7758 | 30.2232 | 28.4347 | 27.3642 | 26.3116 | 25.2695 | 24.2411 | 23.2695 | 22.1874 | 21.1189 | 31.7989 | 31.6821 | 31.5642 | 31.4242 | 31.2484 | 29.9063 | 28.8389 | 27.7874 | 26.7463 | 25.7211 | 24.7495 | 23.6684 | 22.6021
|  | THE MALL | HE |  |  |  | 35.1021 | 35.0305 | 34.9526 | 34.8663 | 34.7347 | 34.3705 | 33.7874 | 33.0579 | 32.0853 | 31.1253 | 30.4337 | 29.9526 | 7.0926 | 31.2632 | 31.1916 | 31.1137 | 31.0095 | 30.6895 | 29.4021 | 28.7011 | 27.8558 | 26.72 | 25.5979 | 24.8263 | 24.2874 | 23.78 | 31.8916 | 31.82 | 31.7421 | 31.6558 | 31.5232 | 30.8726 | 30.1726 | 29.3295 | 28.1958 | 27.0758 | 26.3053 | 25.7663 | 25.26
|  | THE MALL | CF |  |  |  | 35.1263 | 35.0789 | 35.0295 | 34.9779 | 34.9242 | 34.8642 | 34.8053 | 34.7411 | 34.6726 | 34.5979 | 33.3 | 32.9263 | 32.6095 | 31.2874 | 31.24 | 31.1905 | 31.1389 | 31.0726 | 30.9979 | 30.9389 | 30.8274 | 30.6726 | 30.4684 | 28.1568 | 27.7379 | 27.3758 | 31.9158 | 31.8684 | 31.8189 | 31.7674 | 31.7137 | 31.6463 | 31.5874 | 31.5253 | 31.46 | 31.3884 | 29.6295 | 29.2116 | 28.8495
BRAMLEY (FLEE) | BURGHFIELD RESERVE | THEALE | MINIMUM HEADROOM | SU 64755 71015 | YES | 2.6442 | 25.7979 | 25.7432 | 25.6158 | 24.6084 | 24.5568 | 24.5042 | 24.4526 | 24.4032 | 24.3568 | 24.3147 | 23.9937 | 23.6547 | 3.5463 | 23.8653 | 23.5179 | 23.1958 | 21.9937 | 21.9421 | 21.8895 | 21.8379 | 21.7884 | 21.7421 | 21.7 | 21.3442 | 20.9621 | 18.5621 | 24.2316 | 23.9411 | 23.6011 | 22.4211 | 22.3695 | 22.3168 | 22.2653 | 22.2158 | 22.1695 | 22.1274 | 21.78 | 21.4074 | 19.0074
|  | THEALE | EE |  |  |  | 25.8189 | 25.7747 | 25.6968 | 24.6084 | 24.5568 | 24.5042 | 24.4526 | 24.4032 | 24.3568 | 24.3147 | 23.9937 | 23.6547 | 21.3242 | 23.9105 | 23.5853 | 23.2832 | 21.9937 | 21.9421 | 21.8895 | 21.8379 | 21.7884 | 21.7421 | 21.7 | 21.3442 | 20.9621 | 18.6053 | 24.2632 | 24.0105 | 23.6916 | 22.4211 | 22.3695 | 22.3168 | 22.2653 | 22.2158 | 22.1695 | 22.1274 | 21.78 | 21.4074 | 19.0568
|  | THEALE | HT |  |  |  | 25.7979 | 25.7432 | 25.6158 | 25.3221 | 24.9716 | 24.7347 | 24.6379 | 24.5495 | 24.4674 | 24.3916 | 24.0474 | 23.6937 | 21.2558 | 23.8653 | 23.5179 | 23.1958 | 22.8642 | 22.4547 | 22.1811 | 22.0779 | 21.9821 | 21.8947 | 21.8116 | 21.4379 | 21.04 | 18.5621 | 24.2316 | 23.9411 | 23.6011 | 23.2589 | 22.8621 | 22.5958 | 22.4937 | 22.4 | 22.3137 | 22.2326 | 21.8642 | 21.4758 | 19.0074
|  | THEALE | HE |  |  |  | 25.8474 | 25.8168 | 25.7832 | 25.56 | 25.2589 | 25.0621 | 25.0063 | 24.9547 | 24.9053 | 24.8632 | 24.7011 | 24.5284 | 3.5463 | 23.9621 | 23.6758 | 23.4011 | 23.1211 | 22.7716 | 22.5421 | 22.4842 | 22.4295 | 22.3779 | 22.3326 | 22.1589 | 21.9632 | 19.6726 | 24.2937 | 24.1042 | 23.8137 | 23.5179 | 23.1726 | 22.9495 | 22.8926 | 22.8379 | 22.7863 | 22.7421 | 22.5716 | 22.3811 | 20.0947
|  | THEALE | CF |  |  |  | 25.8642 | 25.8463 | 25.8284 | 25.8095 | 25.7905 | 25.7705 | 25.7484 | 25.7158 | 25.6853 | 25.6537 | 25.5095 | 25.3947 | 23.1737 | 23.9979 | 23.8779 | 23.7421 | 23.6137 | 23.4684 | 23.3747 | 23.3389 | 23.3053 | 23.2726 | 23.2389 | 23.0863 | 22.9611 | 20.7263 | 24.3137 | 24.2558 | 24.1579 | 24.0379 | 23.8853 | 23.7863 | 23.7505 | 23.7147 | 23.6811 | 23.6474 | 23.4905 | 23.3589 | 21.1189
MELKSHAM GSP | ANDOVER BSP | THRUXTON | MINIMUM HEADROOM | SU 29134 45674 | YES | 0.14211 | 7.2505 | 7.1389 | 7.1253 | 7.2589 | 6.3695 | 5.2137 | 4.0589 | 2.9147 | 2.0263 | 1.02 | -1.0295 | -1.8211 | -5.0821 | 6.2958 | 6.1389 | 6.08 | 5.8126 | 4.78 | 3.4453 | 2.1095 | 0.78526 | -0.23684 | -1.4 | -3.7 | -4.5242 | -5.24 | 6.4747 | 6.3305 | 6.2326 | 5.9653 | 4.9358 | 3.5968 | 2.26 | 0.93263 | -0.092632 | -1.26 | -3.5947 | -4.4621 | -5.1947
|  | THRUXTON | EE |  |  |  | 7.2989 | 7.2137 | 7.1253 | 7.4653 | 6.8947 | 6.0884 | 5.3042 | 4.4211 | 3.4189 | 2.26 | -0.73474 | -1.4463 | -1.96 | 6.3695 | 6.2505 | 6.1305 | 6.0389 | 5.3821 | 4.4547 | 3.5547 | 2.5379 | 1.3832 | 0.044211 | -3.3547 | -4.0642 | -4.6189 | 6.5305 | 6.4358 | 6.3211 | 6.1916 | 5.5347 | 4.6042 | 3.7011 | 2.68 | 1.5189 | 0.17368 | -3.2726 | -4.0432 | -4.6179
|  | THRUXTON | HT |  |  |  | 7.2505 | 7.1389 | 7.5 | 7.2589 | 6.3695 | 5.2137 | 4.0589 | 2.9147 | 2.0263 | 1.02 | -1.0295 | -1.8211 | -2.4779 | 6.2958 | 6.1389 | 6.08 | 5.8126 | 4.78 | 3.4453 | 2.1095 | 0.78526 | -0.23684 | -1.4 | -3.7 | -4.5242 | -5.24 | 6.4747 | 6.3305 | 6.2326 | 5.9653 | 4.9358 | 3.5968 | 2.26 | 0.93263 | -0.092632 | -1.26 | -3.5947 | -4.4621 | -5.1947
|  | THRUXTON | HE |  |  |  | 7.3621 | 7.3095 | 7.2526 | 7.6758 | 7.1274 | 6.3284 | 5.5716 | 4.66 | 3.6821 | 2.5853 | 0.011579 | -0.39474 | -5.0821 | 6.4568 | 6.3926 | 6.3168 | 6.2674 | 5.6316 | 4.7074 | 3.8326 | 2.7737 | 1.6358 | 0.35895 | -2.6074 | -3.0432 | -3.4526 | 6.6032 | 6.5453 | 6.4821 | 6.42 | 5.7863 | 4.86 | 3.9832 | 2.9232 | 1.7853 | 0.50632 | -2.4758 | -2.9295 | -3.3547
|  | THRUXTON | CF |  |  |  | 7.3979 | 7.3674 | 7.3379 | 7.8663 | 7.8158 | 7.7516 | 7.6926 | 7.5453 | 7.3884 | 7.1621 | 3.2947 | 2.7653 | 2.5179 | 6.4937 | 6.4642 | 6.4274 | 6.4737 | 6.4189 | 6.3516 | 6.2884 | 6.1211 | 5.9442 | 5.6842 | 1.1674 | 0.56737 | 0.30105 | 6.6432 | 6.6095 | 6.5758 | 6.6274 | 6.5716 | 6.5032 | 6.4389 | 6.2705 | 6.0926 | 5.8316 | 1.3147 | 0.70632 | 0.42947
MELKSHAM GSP | WEST GRAFTON | TIDWORTH | MINIMUM HEADROOM | SU 24088 49593 | YES | 0.031579 | 17.3768 | 16.8221 | 16.0484 | 15.2716 | 14.3053 | 13.0968 | 11.6779 | 10.2905 | 8.5253 | 6.8768 | -2.3547 | -5.4095 | -13.0137 | 13.9232 | 13.0737 | 12.1695 | 11.2621 | 10.1221 | 8.6958 | 7.0937 | 5.5095 | 3.4821 | 1.5895 | -9.0453 | -12.4316 | -14.9442 | 14.6095 | 13.7495 | 12.8316 | 11.9116 | 10.7568 | 9.3021 | 7.6737 | 6.0863 | 4.0547 | 2.1558 | -8.5158 | -11.9611 | -14.4968
|  | TIDWORTH | EE |  |  |  | 17.4832 | 17.1884 | 16.4168 | 15.6095 | 14.8284 | 13.9442 | 12.9853 | 11.8421 | 9.6937 | 8.0463 | -1.1684 | -3.8779 | -5.6737 | 14.1084 | 13.4979 | 12.5853 | 11.6337 | 10.7147 | 9.6821 | 8.56 | 7.2821 | 4.8053 | 2.9158 | -7.6895 | -10.6537 | -12.6674 | 14.7958 | 14.1779 | 13.2516 | 12.2874 | 11.3537 | 10.3011 | 9.1526 | 7.8505 | 5.3674 | 3.4695 | -7.1958 | -10.2463 | -12.2842
|  | TIDWORTH | HT |  |  |  | 17.3768 | 16.8221 | 16.0484 | 15.2716 | 14.3053 | 13.0968 | 11.6779 | 10.2905 | 8.5253 | 6.8768 | -2.3547 | -5.4095 | -7.6505 | 13.9232 | 13.0737 | 12.1695 | 11.2621 | 10.1221 | 8.6958 | 7.0937 | 5.5095 | 3.4821 | 1.5895 | -9.0453 | -12.4316 | -14.9442 | 14.6095 | 13.7495 | 12.8316 | 11.9116 | 10.7568 | 9.3021 | 7.6737 | 6.0863 | 4.0547 | 2.1558 | -8.5158 | -11.9611 | -14.4968
|  | TIDWORTH | HE |  |  |  | 17.6326 | 17.4179 | 16.9084 | 16.1726 | 15.4358 | 14.6232 | 13.7516 | 12.6747 | 10.6284 | 9.1305 | 0.61474 | -1.4463 | -13.0137 | 14.3611 | 13.8716 | 13.1432 | 12.2663 | 11.3905 | 10.4316 | 9.3979 | 8.1589 | 5.7895 | 4.0568 | -5.8368 | -8.1779 | -9.7484 | 15.0516 | 14.5558 | 13.8168 | 12.9274 | 12.0389 | 11.0611 | 10.0074 | 8.7432 | 6.3684 | 4.6337 | -5.2737 | -7.6358 | -9.2284
|  | TIDWORTH | CF |  |  |  | 17.7284 | 17.6179 | 17.4821 | 17.26 | 16.9116 | 16.7347 | 16.5695 | 16.3337 | 15.9421 | 15.48 | 9.1021 | 6.5558 | 5.6684 | 14.5368 | 14.3126 | 13.9874 | 13.5537 | 13.1411 | 12.9442 | 12.7642 | 12.4937 | 12.0316 | 11.48 | 3.96 | 1.0179 | 0.017895 | 15.2295 | 15.0021 | 14.6726 | 14.2326 | 13.8137 | 13.6126 | 13.4284 | 13.1526 | 12.6811 | 12.1189 | 4.5411 | 1.5905 | 0.57579
MANNINGTON GSP | SHAFTESBURY BSP | TISBURY | MINIMUM HEADROOM | ST 93438 29127 | YES | 0 | 9.5411 | 9.3758 | 9.18 | 8.9705 | 8.7189 | 8.4547 | 8.1916 | 8.0411 | 7.9053 | 7.7684 | 7.1032 | 6.4821 | 0.23684 | 8.1453 | 7.9653 | 7.7484 | 7.5168 | 7.2337 | 6.9358 | 6.64 | 6.4768 | 6.3305 | 6.1821 | 5.4432 | 4.7411 | 4.0547 | 8.4537 | 8.2747 | 8.0611 | 7.8305 | 7.5505 | 7.2558 | 6.9642 | 6.8021 | 6.6568 | 6.5084 | 5.7768 | 5.0821 | 4.4053
|  | TISBURY | EE |  |  |  | 9.6 | 9.4863 | 9.34 | 9.1747 | 8.9674 | 8.7421 | 8.5274 | 8.3421 | 8.1968 | 8.0905 | 7.5895 | 7.1232 | 6.6684 | 8.2253 | 8.0874 | 7.9263 | 7.7442 | 7.5105 | 7.2579 | 7.0147 | 6.8095 | 6.6484 | 6.5347 | 5.9811 | 5.4516 | 4.9274 | 8.5326 | 8.3958 | 8.2368 | 8.0558 | 7.8242 | 7.5747 | 7.3347 | 7.1305 | 6.9716 | 6.8589 | 6.3095 | 5.7874 | 5.2684
|  | TISBURY | HT |  |  |  | 9.5411 | 9.3758 | 9.18 | 8.9705 | 8.7189 | 8.4547 | 8.1916 | 8.0411 | 7.9053 | 7.7684 | 7.1032 | 6.4821 | 5.8832 | 8.1453 | 7.9653 | 7.7484 | 7.5168 | 7.2337 | 6.9358 | 6.64 | 6.4768 | 6.3305 | 6.1821 | 5.4432 | 4.7411 | 4.0547 | 8.4537 | 8.2747 | 8.0611 | 7.8305 | 7.5505 | 7.2558 | 6.9642 | 6.8021 | 6.6568 | 6.5084 | 5.7768 | 5.0821 | 4.4053
|  | TISBURY | HE |  |  |  | 9.6516 | 9.6021 | 9.5337 | 9.4105 | 9.2442 | 9.0589 | 8.8811 | 8.7347 | 8.6316 | 8.5611 | 8.2379 | 7.9305 | 0.23684 | 8.3221 | 8.2505 | 8.14 | 8.0042 | 7.8158 | 7.6063 | 7.4053 | 7.2411 | 7.1284 | 7.0537 | 6.6979 | 6.3463 | 5.9884 | 8.6295 | 8.5579 | 8.4474 | 8.3137 | 8.1274 | 7.92 | 7.7211 | 7.5589 | 7.4474 | 7.3726 | 7.02 | 6.6726 | 6.32
|  | TISBURY | CF |  |  |  | 9.6811 | 9.6537 | 9.6263 | 9.5968 | 9.5674 | 9.5147 | 9.4579 | 9.3905 | 9.3063 | 9.2168 | 8.8263 | 8.6189 | 8.4147 | 8.3516 | 8.3242 | 8.2884 | 8.2347 | 8.1811 | 8.12 | 8.0579 | 7.9832 | 7.8874 | 7.7853 | 7.3421 | 7.1063 | 6.8674 | 8.6589 | 8.6316 | 8.5958 | 8.5421 | 8.4884 | 8.4284 | 8.3663 | 8.2926 | 8.1979 | 8.0968 | 7.6589 | 7.4253 | 7.1905
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | TITCHFIELD | MINIMUM HEADROOM | SU 54104 05695 | YES | 0 | 16.9295 | 15.9347 | 14.6505 | 13.0432 | 11.12 | 8.9253 | 21.7316 | 19.5695 | 17.4305 | 15.2884 | 9.1863 | 7.0579 | -0.48211 | 14.2263 | 12.82 | 11.2379 | 9.36 | 7.1432 | 4.6189 | 17.0968 | 14.6063 | 12.1379 | 9.6663 | 2.7253 | 0.42211 | -1.6263 | 14.5326 | 13.1705 | 11.6137 | 9.7379 | 7.5253 | 4.9989 | 17.4747 | 14.9821 | 12.5105 | 10.0368 | 3.0611 | 0.70316 | -1.3653
|  | TITCHFIELD | EE |  |  |  | 17.0242 | 16.3484 | 15.2568 | 13.9274 | 12.2147 | 10.2095 | 23.2179 | 21.1674 | 18.9053 | 16.6137 | 10.0095 | 8.26 | 6.8442 | 14.4379 | 13.3095 | 11.9653 | 10.3579 | 8.3842 | 6.0737 | 18.7811 | 16.4189 | 13.8074 | 11.16 | 3.6168 | 1.7789 | 0.21158 | 14.7389 | 13.6463 | 12.3379 | 10.7347 | 8.7621 | 6.4505 | 19.1547 | 16.7884 | 14.1705 | 11.5179 | 3.9168 | 2.0053 | 0.41474
|  | TITCHFIELD | HT |  |  |  | 16.9295 | 15.9347 | 14.6505 | 13.0432 | 11.12 | 8.9253 | 21.7316 | 19.5695 | 17.4305 | 15.2884 | 9.1863 | 7.0579 | 5.2147 | 14.2263 | 12.82 | 11.2379 | 9.36 | 7.1432 | 4.6189 | 17.0968 | 14.6063 | 12.1379 | 9.6663 | 2.7253 | 0.42211 | -1.6263 | 14.5326 | 13.1705 | 11.6137 | 9.7379 | 7.5253 | 4.9989 | 17.4747 | 14.9821 | 12.5105 | 10.0368 | 3.0611 | 0.70316 | -1.3653
|  | TITCHFIELD | HE |  |  |  | 17.1526 | 16.7137 | 15.7295 | 14.5284 | 12.9147 | 10.9926 | 24.1042 | 22.1274 | 19.96 | 17.7958 | 11.9084 | 10.7358 | -0.48211 | 14.7189 | 13.7253 | 12.5 | 11.0105 | 9.1411 | 6.9179 | 19.7316 | 17.44 | 14.9232 | 12.4063 | 5.6042 | 4.2905 | 3.1653 | 15.0147 | 14.0537 | 12.8705 | 11.3863 | 9.5211 | 7.2968 | 20.1105 | 17.8189 | 15.3032 | 12.7853 | 5.9653 | 4.6284 | 3.4853
|  | TITCHFIELD | CF |  |  |  | 17.2263 | 17.1558 | 16.9863 | 16.5211 | 15.9884 | 15.3916 | 29.7442 | 28.9295 | 28.0274 | 27.0011 | 21.2305 | 20.3758 | 19.7126 | 15.0674 | 14.5695 | 14.0589 | 13.4832 | 12.82 | 12.0811 | 26.2758 | 25.3242 | 24.28 | 23.0884 | 16.3789 | 15.4263 | 14.6853 | 15.3421 | 14.8705 | 14.3768 | 13.82 | 13.18 | 12.4537 | 26.6484 | 25.6968 | 24.6526 | 23.46 | 16.7537 | 15.7905 | 15.0358
BRAMLEY (FLEE) | ALDERSHOT BSP | TONGHAM | MINIMUM HEADROOM | SU 88310 49487 | YES | 0.45895 | 32.62 | 32.2842 | 31.9463 | 31.5842 | 30.6263 | 29.5568 | 28.5547 | 27.6905 | 26.8632 | 26.0758 | 22.7232 | 20.4674 | -4.9221 | 29.6421 | 28.6379 | 27.5684 | 26.36 | 25.1558 | 23.9632 | 22.8505 | 21.8926 | 20.9716 | 20.0968 | 16.3884 | 13.9158 | 11.6926 | 30.5632 | 29.8789 | 28.7958 | 27.5726 | 26.3537 | 25.1442 | 24.0168 | 23.0463 | 22.1137 | 21.2263 | 17.5011 | 15.0116 | 12.7821
|  | TONGHAM | EE |  |  |  | 32.7453 | 32.48 | 32.1989 | 31.9 | 31.3663 | 30.4032 | 29.5179 | 28.7411 | 27.9768 | 27.2653 | 24.38 | 22.6368 | 21.1568 | 29.9284 | 29.0674 | 28.1253 | 27.0463 | 25.9642 | 24.8853 | 23.8979 | 23.0358 | 22.1884 | 21.3979 | 18.2021 | 16.2979 | 14.6516 | 30.6979 | 30.3116 | 29.3589 | 28.2663 | 27.1684 | 26.0747 | 25.0747 | 24.1989 | 23.3389 | 22.5358 | 19.3042 | 17.3789 | 15.7242
|  | TONGHAM | HT |  |  |  | 32.62 | 32.2842 | 31.9463 | 31.5842 | 30.6263 | 29.5568 | 28.5547 | 27.6905 | 26.8632 | 26.0758 | 22.7232 | 20.4674 | 18.4642 | 29.6421 | 28.6379 | 27.5684 | 26.36 | 25.1558 | 23.9632 | 22.8505 | 21.8926 | 20.9716 | 20.0968 | 16.3884 | 13.9158 | 11.6926 | 30.5632 | 29.8789 | 28.7958 | 27.5726 | 26.3537 | 25.1442 | 24.0168 | 23.0463 | 22.1137 | 21.2263 | 17.5011 | 15.0116 | 12.7821
|  | TONGHAM | HE |  |  |  | 32.9221 | 32.7411 | 32.54 | 32.3179 | 32.08 | 31.5368 | 30.7884 | 30.1495 | 29.5274 | 28.9547 | 26.7811 | 25.7011 | -4.9221 | 30.3105 | 29.6442 | 28.88 | 27.9695 | 27.0495 | 26.1211 | 25.2832 | 24.5705 | 23.8758 | 23.2326 | 20.7937 | 19.6 | 18.5947 | 30.8905 | 30.6768 | 30.1211 | 29.1989 | 28.2663 | 27.3253 | 26.4747 | 25.7526 | 25.0495 | 24.3958 | 21.9168 | 20.7147 | 19.7042
|  | TONGHAM | CF |  |  |  | 33.0253 | 32.9221 | 32.8147 | 32.7032 | 32.5884 | 32.4674 | 32.3442 | 32.2242 | 32.1042 | 31.9842 | 30.4968 | 29.7084 | 29.0768 | 30.4316 | 30.2368 | 29.8179 | 29.3484 | 28.8653 | 28.4305 | 28.0021 | 27.6063 | 27.1947 | 26.7737 | 24.9642 | 24.0853 | 23.3705 | 31.0021 | 30.8853 | 30.7568 | 30.5947 | 30.1053 | 29.6642 | 29.2305 | 28.8284 | 28.4105 | 27.9863 | 26.1495 | 25.2547 | 24.5263
MINETY GSP | TOOTHILL BSP | TOOTHILL | MINIMUM HEADROOM | SU 13215 83986 | YES | 1.7937 | 33.0968 | 32.8937 | 32.6874 | 32.4684 | 32.2421 | 32.0063 | 31.7695 | 31.56 | 31.2189 | 30.6526 | 28.8453 | 26.5863 | 0.46632 | 28.5432 | 28.34 | 28.1337 | 27.9147 | 27.6442 | 27.1432 | 26.4305 | 25.7484 | 25.0947 | 24.46 | 22.4621 | 19.8737 | 17.44 | 29.7779 | 29.5747 | 29.3684 | 29.1495 | 28.8695 | 28.3168 | 27.6295 | 26.9642 | 26.3295 | 25.7 | 23.7042 | 21.1137 | 18.6821
|  | TOOTHILL | EE |  |  |  | 33.1737 | 33.0126 | 32.8421 | 32.6611 | 32.4705 | 32.2726 | 32.0811 | 31.8989 | 31.7221 | 31.52 | 30.0484 | 28.3063 | 26.6368 | 29.2011 | 28.4589 | 28.2884 | 28.1074 | 27.9168 | 27.7189 | 27.2821 | 26.7326 | 26.0684 | 25.4126 | 23.8158 | 21.84 | 19.9295 | 30.0621 | 29.6937 | 29.5232 | 29.3421 | 29.1516 | 28.9537 | 28.4579 | 27.9242 | 27.2789 | 26.6432 | 25.0611 | 23.0863 | 21.1779
|  | TOOTHILL | HT |  |  |  | 33.0968 | 32.8937 | 32.6874 | 32.4684 | 32.2421 | 32.0063 | 31.7695 | 31.56 | 31.2189 | 30.6526 | 28.8453 | 26.5863 | 24.4505 | 28.5432 | 28.34 | 28.1337 | 27.9147 | 27.6442 | 27.1432 | 26.4305 | 25.7484 | 25.0947 | 24.46 | 22.4621 | 19.8737 | 17.44 | 29.7779 | 29.5747 | 29.3684 | 29.1495 | 28.8695 | 28.3168 | 27.6295 | 26.9642 | 26.3295 | 25.7 | 23.7042 | 21.1137 | 18.6821
|  | TOOTHILL | HE |  |  |  | 33.2737 | 33.16 | 33.0337 | 32.8937 | 32.7442 | 32.5842 | 32.4305 | 32.2863 | 32.1516 | 32.0358 | 31.3074 | 29.9579 | 0.46632 | 29.3421 | 28.6063 | 28.48 | 28.34 | 28.1905 | 28.0305 | 27.8768 | 27.5747 | 27.0274 | 26.4705 | 25.1084 | 23.5642 | 22.0674 | 30.1632 | 29.8411 | 29.7147 | 29.5747 | 29.4253 | 29.2653 | 29.1116 | 28.7716 | 28.2179 | 27.6768 | 26.3305 | 24.7968 | 23.3021
|  | TOOTHILL | CF |  |  |  | 33.3326 | 33.2642 | 33.1937 | 33.12 | 33.0442 | 32.9663 | 32.8863 | 32.8063 | 32.7284 | 32.6505 | 32.3032 | 32.1284 | 31.4053 | 29.4179 | 29.3305 | 28.64 | 28.5663 | 28.4905 | 28.4126 | 28.3326 | 28.2526 | 28.1747 | 28.0968 | 27.0411 | 26.1463 | 25.1958 | 30.2221 | 30.1537 | 29.8747 | 29.8011 | 29.7253 | 29.6474 | 29.5674 | 29.4874 | 29.4095 | 29.3316 | 28.2358 | 27.3705 | 26.4368
NURSLING GSP | ROWNHAMS | TOTTON | MINIMUM HEADROOM | SU 35835 13428 | YES | 0.37895 | 23.8979 | 23.6116 | 23.3232 | 23.0168 | 22.7011 | 22.3747 | 22.0474 | 21.7589 | 21.4968 | 23.38 | 22.94 | 27.9758 | -8.6179 | 20.0021 | 19.5053 | 18.9547 | 18.4032 | 17.8537 | 17.3053 | 16.5232 | 15.7916 | 14.9779 | 19.1253 | 17.12 | 20.0916 | 17.9537 | 20.7337 | 20.2811 | 19.7495 | 19.2158 | 18.6842 | 18.1505 | 17.4021 | 16.6789 | 15.8642 | 19.9116 | 18.0063 | 20.9758 | 18.8368
|  | TOTTON | EE |  |  |  | 24.0053 | 23.7811 | 23.5432 | 23.2905 | 23.0263 | 22.7526 | 22.4895 | 22.24 | 21.9989 | 35.2589 | 32.1747 | 29.9695 | 28.5453 | 20.1558 | 19.8547 | 19.4516 | 19.0116 | 18.5674 | 18.1179 | 17.5442 | 16.9611 | 16.2063 | 28.8295 | 24.7674 | 22.2695 | 20.6642 | 20.8758 | 20.5937 | 20.2263 | 19.8 | 19.3684 | 18.9316 | 18.3811 | 17.8221 | 17.0926 | 29.7158 | 25.6526 | 23.1537 | 21.5484
|  | TOTTON | HT |  |  |  | 23.8979 | 23.6116 | 23.3232 | 23.0168 | 22.7011 | 22.3747 | 22.0474 | 21.7589 | 21.4968 | 34.5126 | 30.6253 | 27.9758 | 26.0695 | 20.0021 | 19.5053 | 18.9547 | 18.4032 | 17.8537 | 17.3053 | 16.5232 | 15.7916 | 14.9779 | 27.5484 | 23.0747 | 20.0916 | 17.9537 | 20.7337 | 20.2811 | 19.7495 | 19.2158 | 18.6842 | 18.1505 | 17.4021 | 16.6789 | 15.8642 | 28.4347 | 23.96 | 20.9758 | 18.8368
|  | TOTTON | HE |  |  |  | 24.1558 | 24.0032 | 23.8337 | 23.6463 | 23.4442 | 23.2295 | 23.0242 | 22.8305 | 22.6495 | 35.9674 | 34.0989 | 32.4442 | -8.6179 | 20.3063 | 20.1537 | 19.9116 | 19.6558 | 19.3842 | 19.1032 | 18.7253 | 18.2537 | 17.6137 | 30.36 | 26.8842 | 24.9695 | 23.8958 | 21.0263 | 20.8737 | 20.6484 | 20.4095 | 20.1547 | 19.88 | 19.5147 | 19.0642 | 18.4579 | 31.2453 | 27.7705 | 25.8547 | 24.7811
|  | TOTTON | CF |  |  |  | 24.2442 | 24.1579 | 24.0684 | 23.9758 | 23.8789 | 23.78 | 23.6779 | 23.5779 | 23.4789 | 23.38 | 22.94 | 35.5063 | 34.8695 | 20.3947 | 20.3084 | 20.2189 | 20.1053 | 19.9821 | 19.8411 | 19.6979 | 19.5579 | 19.3695 | 19.1253 | 17.12 | 28.4253 | 27.6832 | 21.1147 | 21.0284 | 20.9389 | 20.8305 | 20.7137 | 20.5821 | 20.4495 | 20.3189 | 20.1453 | 19.9116 | 18.0063 | 29.3116 | 28.5695
BOTLEY WOOD GSP | NETLEY COMMON BSP | TOWNHILL PARK | MINIMUM HEADROOM | SU 45156 14783 | YES | 0.88737 | 34.2074 | 33.6737 | 33.0842 | 32.0484 | 31.0053 | 31.3463 | 30.3811 | 29.5874 | 28.8011 | 28.0568 | 31.4874 | 30.0505 | -9.8368 | 28.6211 | 27.5126 | 26.4579 | 25.3442 | 24.2242 | 24.6032 | 23.5579 | 22.7095 | 21.8674 | 21.0632 | 24.7221 | 24.9368 | 20.6611 | 29.8568 | 28.7968 | 27.7642 | 26.6747 | 25.5474 | 25.9358 | 24.8726 | 24.0105 | 23.1558 | 22.34 | 26.0484 | 24.4747 | 20.0968
|  | TOWNHILL PARK | EE |  |  |  | 34.4147 | 33.9989 | 33.5579 | 33.0905 | 32.2589 | 31.3463 | 30.3811 | 29.5874 | 28.8011 | 28.0568 | 37.6105 | 34.2632 | 31.3011 | 29.0758 | 28.2021 | 27.3526 | 26.4737 | 25.5832 | 24.6032 | 23.5579 | 22.7095 | 21.8674 | 21.0632 | 33.1568 | 29.4853 | 26.2158 | 30.26 | 29.4695 | 28.6389 | 27.7779 | 26.9053 | 25.9358 | 24.8726 | 24.0105 | 23.1558 | 22.34 | 32.8663 | 29.1084 | 25.7579
|  | TOWNHILL PARK | HT |  |  |  | 34.2074 | 33.6737 | 33.0842 | 32.0484 | 31.0053 | 42.1211 | 41.5074 | 40.9663 | 40.4747 | 39.5095 | 34.3589 | 30.0505 | 26.1589 | 28.6211 | 27.5126 | 26.4579 | 25.3442 | 24.2242 | 39.4453 | 38.3263 | 37.3168 | 36.3158 | 35.2568 | 29.6495 | 24.9368 | 20.6611 | 29.8568 | 28.7968 | 27.7642 | 26.6747 | 25.5474 | 39.2747 | 38.14 | 37.1137 | 36.0968 | 35.0189 | 29.2937 | 24.4747 | 20.0968
|  | TOWNHILL PARK | HE |  |  |  | 34.6884 | 34.4011 | 34.0832 | 33.7316 | 33.3537 | 32.9516 | 32.3537 | 31.7758 | 31.2053 | 30.6747 | 41.34 | 39.2095 | -9.8368 | 29.6821 | 29.0937 | 28.5189 | 27.9011 | 27.2621 | 26.52 | 25.7011 | 25.0874 | 24.4789 | 23.9074 | 37.3695 | 34.8137 | 32.5389 | 30.6179 | 30.2716 | 29.7505 | 29.1705 | 28.5432 | 27.8158 | 27.0158 | 26.4126 | 25.8126 | 25.2316 | 37.1568 | 34.5389 | 32.2021
|  | TOWNHILL PARK | CF |  |  |  | 34.8495 | 34.6853 | 34.5147 | 34.3368 | 34.1547 | 33.9653 | 33.7726 | 33.5811 | 33.3926 | 33.2053 | 31.4874 | 42.7084 | 41.9979 | 30.1 | 29.7747 | 29.4221 | 29.0516 | 28.6747 | 28.2779 | 27.8611 | 27.4579 | 27.0705 | 26.6716 | 24.7221 | 39.2842 | 37.7495 | 30.7789 | 30.6147 | 30.4442 | 30.2253 | 29.8884 | 29.5358 | 29.1337 | 28.74 | 28.3611 | 27.9726 | 26.0484 | 39.0895 | 37.5137
MINETY GSP | SWINDON BSP | TRADING ESTATE | MINIMUM HEADROOM | SU 13490 85868 | YES | 0.88 | 23.1105 | 23.0316 | 22.9537 | 22.3558 | 22.2884 | 22.2179 | 22.1505 | 21.8937 | 21.5947 | 21.4905 | 20.9053 | 20.2568 | -15.2853 | 21.1621 | 21 | 20.8389 | 19.6211 | 19.5537 | 19.4832 | 19.4158 | 19.1221 | 18.7295 | 18.6095 | 17.9632 | 17.2358 | 16.5537 | 21.4895 | 21.42 | 21.3505 | 20.1168 | 20.0495 | 19.9789 | 19.9116 | 19.6179 | 19.2263 | 19.1063 | 18.46 | 17.7347 | 17.0537
|  | TRADING ESTATE | EE |  |  |  | 23.1368 | 23.0747 | 23.0074 | 22.3558 | 22.2884 | 22.2179 | 22.1505 | 22.0842 | 22.0211 | 21.8779 | 21.4105 | 20.9274 | 20.48 | 21.2211 | 21.1032 | 20.9737 | 19.6211 | 19.5537 | 19.4832 | 19.4158 | 19.3495 | 19.2863 | 19.1095 | 18.5389 | 17.9895 | 17.4821 | 21.5126 | 21.4558 | 21.3958 | 20.1168 | 20.0495 | 19.9789 | 19.9116 | 19.8453 | 19.7821 | 19.6063 | 19.0368 | 18.4874 | 17.9811
|  | TRADING ESTATE | HT |  |  |  | 23.1105 | 23.0316 | 22.9537 | 22.8716 | 22.7716 | 22.56 | 22.2337 | 21.8937 | 21.5947 | 21.4905 | 20.9053 | 20.2568 | 19.6526 | 21.1621 | 21 | 20.8389 | 20.6768 | 20.3758 | 19.9863 | 19.5684 | 19.1221 | 18.7295 | 18.6095 | 17.9632 | 17.2358 | 16.5537 | 21.4895 | 21.42 | 21.3505 | 21.2084 | 20.8768 | 20.4453 | 20.0642 | 19.6179 | 19.2263 | 19.1063 | 18.46 | 17.7347 | 17.0537
|  | TRADING ESTATE | HE |  |  |  | 23.1684 | 23.1263 | 23.0789 | 23.0242 | 22.9653 | 22.8884 | 22.8168 | 22.7432 | 22.54 | 22.3263 | 22.0442 | 21.7968 | -15.2853 | 21.2526 | 21.2105 | 21.1526 | 21.0621 | 20.9674 | 20.7316 | 20.5137 | 20.2463 | 19.96 | 19.6779 | 19.3421 | 19.0305 | 18.5632 | 21.5442 | 21.5021 | 21.4558 | 21.4042 | 21.3495 | 21.2684 | 21.0284 | 20.7326 | 20.42 | 20.1737 | 19.8379 | 19.5274 | 19.06
|  | TRADING ESTATE | CF |  |  |  | 23.1863 | 23.1589 | 23.1316 | 23.1021 | 23.0705 | 23.0368 | 23 | 22.9632 | 22.9221 | 22.8811 | 22.6684 | 22.4726 | 22.3137 | 21.2705 | 21.2432 | 21.2158 | 21.1842 | 21.1368 | 21.08 | 20.9979 | 20.8958 | 20.7684 | 20.6316 | 20.0989 | 19.8842 | 19.6768 | 21.5621 | 21.5347 | 21.5074 | 21.4779 | 21.4484 | 21.4168 | 21.3853 | 21.3547 | 21.3053 | 21.1547 | 20.5684 | 20.3484 | 20.1663
BRAMLEY (FLEE) | BURGHFIELD RESERVE | TRASH GREEN | MINIMUM HEADROOM | SU 66254 68745 | YES | 0.71579 | 17.5811 | 17.5874 | 17.3505 | 17.0568 | 16.76 | 16.1853 | 15.3537 | 14.3442 | 14.1853 | 13.3842 | 11.5495 | 9.6558 | -24.8674 | 14.7653 | 14.3284 | 14.0116 | 13.6968 | 13.3811 | 12.7389 | 11.7979 | 10.6442 | 10.4895 | 9.5768 | 7.5505 | 5.4368 | 4.7147 | 15.0084 | 14.5716 | 14.2558 | 13.9411 | 13.6242 | 12.9821 | 12.0389 | 10.8842 | 10.7253 | 9.8105 | 7.7653 | 5.6263 | 4.8947
|  | TRASH GREEN | EE |  |  |  | 17.5811 | 17.8432 | 17.6126 | 17.3705 | 17.1337 | 16.8905 | 16.6516 | 16.4168 | 16.1916 | 15.9853 | 14.8442 | 12.8453 | 9.8968 | 14.7853 | 14.5442 | 14.2968 | 14.0389 | 13.7842 | 13.5295 | 13.2821 | 13.0358 | 12.8021 | 12.5874 | 11.3716 | 9.1326 | 5.7168 | 15.1495 | 14.7874 | 14.54 | 14.2811 | 14.0284 | 13.7705 | 13.5189 | 13.2695 | 13.0305 | 12.8126 | 11.5653 | 9.2916 | 5.8716
|  | TRASH GREEN | HT |  |  |  | 18.04 | 17.6442 | 17.3505 | 17.0568 | 16.76 | 16.1853 | 15.3537 | 14.3442 | 14.1853 | 13.3842 | 11.5495 | 9.6558 | 8.9811 | 14.7653 | 14.3284 | 14.0116 | 13.6968 | 13.3811 | 12.7389 | 11.7979 | 10.6442 | 10.4895 | 9.5768 | 7.5505 | 5.4368 | 4.7147 | 15.0084 | 14.5716 | 14.2558 | 13.9411 | 13.6242 | 12.9821 | 12.0389 | 10.8842 | 10.7253 | 9.8105 | 7.7653 | 5.6263 | 4.8947
|  | TRASH GREEN | HE |  |  |  | 17.6716 | 17.5874 | 17.9558 | 17.7979 | 17.6358 | 17.4611 | 17.2968 | 17.1347 | 16.9821 | 16.8484 | 16.1337 | 14.5579 | -24.8674 | 14.9589 | 14.7074 | 14.6695 | 14.5021 | 14.3295 | 14.1495 | 13.9779 | 13.8084 | 13.6495 | 13.5116 | 12.7411 | 10.9326 | 7.8295 | 15.34 | 15.0705 | 14.9126 | 14.7453 | 14.5726 | 14.3905 | 14.2168 | 14.0463 | 13.8853 | 13.7453 | 12.9632 | 11.1474 | 8.0389
|  | TRASH GREEN | CF |  |  |  | 17.7232 | 17.6779 | 18.2442 | 18.1526 | 18.0653 | 17.9716 | 17.8779 | 17.7853 | 17.6937 | 17.6021 | 17.1726 | 16.5232 | 15.6411 | 15.0579 | 14.9411 | 14.9842 | 14.8863 | 14.7916 | 14.6916 | 14.5926 | 14.4937 | 14.3968 | 14.2989 | 13.8421 | 13.1074 | 12.0905 | 15.4589 | 15.3147 | 15.2274 | 15.1295 | 15.0347 | 14.9337 | 14.8337 | 14.7347 | 14.6368 | 14.5379 | 14.0779 | 13.3379 | 12.3158
MELKSHAM GSP | NORRINGTON | TROWBRIDGE TOWN | MINIMUM HEADROOM | ST 84668 58036 | YES | 0.91158 | 29.8453 | 29.5579 | 29.48 | 29.2232 | 28.9537 | 28.6726 | 28.4032 | 28.1442 | 27.7179 | 27.2379 | 24.6874 | 22.0663 | -6.1832 | 25.7558 | 25.0926 | 24.6684 | 23.9758 | 23.3263 | 22.5211 | 21.7189 | 20.9695 | 20.2495 | 19.7284 | 16.9084 | 13.96 | 10.96 | 26.4653 | 26.0663 | 25.5295 | 24.8379 | 24.1895 | 23.3842 | 22.5821 | 21.8347 | 21.1147 | 20.5937 | 17.7758 | 14.8326 | 11.8368
|  | TROWBRIDGE TOWN | EE |  |  |  | 29.9484 | 29.7211 | 29.48 | 29.2232 | 28.9537 | 28.6726 | 28.4032 | 28.1442 | 27.8947 | 27.6726 | 26.1737 | 24.2989 | 22.2379 | 25.9947 | 25.5495 | 24.9221 | 24.34 | 23.7495 | 23.0905 | 22.4705 | 21.8432 | 21.1337 | 20.5926 | 18.5442 | 16.4284 | 14.08 | 26.5695 | 26.3411 | 25.9 | 25.3305 | 24.7547 | 24.1126 | 23.5074 | 22.8958 | 22.2063 | 21.6716 | 19.5821 | 17.2926 | 14.9463
|  | TROWBRIDGE TOWN | HT |  |  |  | 29.8453 | 29.5579 | 31.7526 | 31.1189 | 30.5189 | 29.7842 | 29.0516 | 28.3705 | 27.7179 | 27.2379 | 24.6874 | 22.0663 | 19.4242 | 25.7558 | 25.0926 | 24.6684 | 23.9758 | 23.3263 | 22.5211 | 21.7189 | 20.9695 | 20.2495 | 19.7284 | 16.9084 | 13.96 | 10.96 | 26.4653 | 26.0663 | 25.5295 | 24.8379 | 24.1895 | 23.3842 | 22.5821 | 21.8347 | 21.1147 | 20.5937 | 17.7758 | 14.8326 | 11.8368
|  | TROWBRIDGE TOWN | HE |  |  |  | 30.0947 | 29.9326 | 29.7547 | 29.5589 | 31.9842 | 31.4832 | 31.0242 | 30.5432 | 30.0032 | 29.6484 | 28.3189 | 26.7063 | -6.1832 | 26.2705 | 26.0263 | 25.5737 | 25.0916 | 24.9263 | 24.3758 | 23.8747 | 23.3442 | 22.7432 | 22.3547 | 20.8874 | 19.0484 | 17.4316 | 26.7158 | 26.5537 | 26.3758 | 26.0674 | 25.7874 | 25.2379 | 24.7368 | 24.2074 | 23.6063 | 23.2189 | 21.7537 | 19.9179 | 18.3032
|  | TROWBRIDGE TOWN | CF |  |  |  | 30.1789 | 30.0842 | 29.9853 | 29.8821 | 29.7768 | 29.6674 | 29.5558 | 29.4453 | 29.3368 | 29.2284 | 28.7432 | 28.5011 | 28.2347 | 26.3611 | 26.2621 | 26.1579 | 25.9579 | 25.7474 | 25.5305 | 25.3011 | 25.0495 | 24.7495 | 24.3832 | 22.7705 | 21.7958 | 20.6926 | 26.8 | 26.7053 | 26.6063 | 26.5032 | 26.3979 | 26.2884 | 26.1768 | 26.0221 | 25.7295 | 25.3758 | 23.8116 | 22.8695 | 21.7568
BRAMLEY (FLEE) | READING BSP | TWYFORD | MINIMUM HEADROOM | SU 78430 76339 | YES | 0 | 18.4779 | 18.1958 | 17.9116 | 17.3084 | 16.7368 | 16.0895 | 15.4884 | 14.9368 | 14.4326 | 13.9737 | 11.9 | 10.1263 | -9.9789 | 15.1758 | 14.5074 | 13.7737 | 13.0453 | 12.3989 | 11.6611 | 10.98 | 10.3526 | 9.78 | 9.26 | 6.8726 | 4.8021 | 2.8663 | 15.8274 | 15.2632 | 14.5063 | 13.7779 | 13.1316 | 12.3926 | 11.7126 | 11.0842 | 10.5105 | 9.9895 | 7.5979 | 5.5242 | 3.5853
|  | TWYFORD | EE |  |  |  | 18.5905 | 18.3716 | 18.1411 | 17.8958 | 17.78 | 17.1863 | 16.6695 | 16.1958 | 15.7926 | 15.4263 | 14.2505 | 12.9179 | 11.7042 | 15.3926 | 14.9737 | 14.4032 | 13.7684 | 13.1484 | 12.4884 | 11.9179 | 11.3979 | 10.9611 | 10.5611 | 8.8432 | 7.3737 | 6.0126 | 15.9495 | 15.7137 | 15.1558 | 14.5011 | 13.8811 | 13.2211 | 12.6495 | 12.1284 | 11.6916 | 11.2905 | 9.5663 | 8.0926 | 6.7284
|  | TWYFORD | HT |  |  |  | 18.4779 | 18.1958 | 17.9116 | 17.3084 | 16.7368 | 16.0895 | 15.4884 | 14.9368 | 14.4326 | 13.9737 | 11.9 | 10.1263 | 8.4937 | 15.1758 | 14.5074 | 13.7737 | 13.0453 | 12.3989 | 11.6611 | 10.98 | 10.3526 | 9.78 | 9.26 | 6.8726 | 4.8021 | 2.8663 | 15.8274 | 15.2632 | 14.5063 | 13.7779 | 13.1316 | 12.3926 | 11.7126 | 11.0842 | 10.5105 | 9.9895 | 7.5979 | 5.5242 | 3.5853
|  | TWYFORD | HE |  |  |  | 18.7442 | 18.5979 | 18.4389 | 18.2611 | 18.0705 | 17.7579 | 17.3684 | 17.0221 | 16.7442 | 16.4937 | 15.48 | 14.6842 | -9.9789 | 15.6284 | 15.4074 | 15.0063 | 14.5326 | 14.0779 | 13.5495 | 13.1053 | 12.7116 | 12.4053 | 12.1253 | 10.9705 | 10.0347 | 9.1589 | 16.1147 | 15.9568 | 15.7684 | 15.2863 | 14.8105 | 14.2811 | 13.8368 | 13.4442 | 13.1368 | 12.8568 | 11.6989 | 10.7611 | 9.8832
|  | TWYFORD | CF |  |  |  | 18.8295 | 18.7495 | 18.6663 | 18.5789 | 18.4895 | 18.3958 | 18.3011 | 18.2084 | 18.1137 | 18.0221 | 16.8968 | 16.4158 | 16.0526 | 15.7579 | 15.6674 | 15.5642 | 15.4368 | 15.2547 | 15.0137 | 14.7516 | 14.4863 | 14.1958 | 13.8968 | 12.5179 | 11.9621 | 11.5274 | 16.2137 | 16.1284 | 16.0389 | 15.9432 | 15.8453 | 15.74 | 15.5105 | 15.2389 | 14.9274 | 14.6284 | 13.2495 | 12.6926 | 12.2568
COWLEY GSP | COWLEY LOCAL (2 X 90) | UNION STREET | MINIMUM HEADROOM | SP 52865 05849 | YES | 0.34316 | 32.5916 | 32.3411 | 32.1137 | 31.8716 | 31.6211 | 31.36 | 30.8926 | 30.5011 | 30.1568 | 29.8421 | 28.0453 | 26.7337 | 3.7558 | 28.7021 | 28.1558 | 27.7484 | 27.3253 | 26.9042 | 26.4832 | 24.9916 | 24.5337 | 24.1337 | 23.7684 | 21.7789 | 20.3421 | 19.0011 | 29.2116 | 28.9979 | 28.7737 | 28.4979 | 28.0758 | 27.6558 | 26.1632 | 25.7053 | 25.3053 | 24.94 | 22.9568 | 21.5211 | 20.1789
|  | UNION STREET | EE |  |  |  | 32.6716 | 32.4737 | 32.2811 | 32.0768 | 31.8621 | 31.6411 | 31.38 | 31.1526 | 30.8632 | 30.5989 | 29.1821 | 28.22 | 27.3389 | 28.7821 | 28.5053 | 28.1242 | 27.7568 | 27.3916 | 27.0389 | 26.0368 | 25.4305 | 24.9832 | 24.6832 | 23.0232 | 21.9758 | 20.9989 | 29.2853 | 29.1158 | 28.9368 | 28.7358 | 28.5242 | 28.2116 | 27.2095 | 26.6021 | 26.1547 | 25.8547 | 24.1989 | 23.1547 | 22.1768
|  | UNION STREET | HT |  |  |  | 32.5916 | 32.3411 | 32.1137 | 31.8716 | 31.6211 | 31.36 | 30.8926 | 30.5011 | 30.1568 | 29.8421 | 28.0453 | 26.7337 | 25.52 | 28.7021 | 28.1558 | 27.7484 | 27.3253 | 26.9042 | 26.4832 | 24.9916 | 24.5337 | 24.1337 | 23.7684 | 21.7789 | 20.3421 | 19.0011 | 29.2116 | 28.9979 | 28.7737 | 28.4979 | 28.0758 | 27.6558 | 26.1632 | 25.7053 | 25.3053 | 24.94 | 22.9568 | 21.5211 | 20.1789
|  | UNION STREET | HE |  |  |  | 32.7663 | 32.6253 | 32.4737 | 32.3105 | 32.1358 | 31.9516 | 31.7274 | 31.5411 | 31.3789 | 31.2442 | 30.5063 | 29.9926 | 3.7558 | 28.8842 | 28.7368 | 28.5632 | 28.2989 | 28.0347 | 27.7695 | 26.8411 | 26.32 | 25.9989 | 25.7853 | 24.5579 | 23.9484 | 23.4589 | 29.38 | 29.2526 | 29.1116 | 28.9558 | 28.7884 | 28.6095 | 28.0126 | 27.4916 | 27.1716 | 26.9568 | 25.7253 | 25.1126 | 24.6221
|  | UNION STREET | CF |  |  |  | 32.8211 | 32.74 | 32.6526 | 32.56 | 32.4653 | 32.3674 | 32.2663 | 32.1653 | 32.06 | 31.9537 | 31.4663 | 31.2347 | 31.0821 | 28.9421 | 28.8505 | 28.7632 | 28.6716 | 28.5768 | 28.48 | 28.3789 | 28.1821 | 27.9158 | 27.64 | 26.1663 | 25.6453 | 25.2316 | 29.4347 | 29.3537 | 29.2695 | 29.1821 | 29.0916 | 28.9979 | 28.9021 | 28.8084 | 28.7158 | 28.6137 | 27.3389 | 26.8168 | 26.4032
COWLEY GSP | OXFORD BSP | UNIVERSITY PARKS | MINIMUM HEADROOM | SP 51472 07052 | YES | 0.14842 | 47.9521 | 47.9184 | 47.8847 | 47.8489 | 47.8111 | 47.7721 | 47.7321 | 47.6963 | 47.6647 | 47.6342 | 47.5479 | 47.45 | 18.11 | 42.0089 | 41.9626 | 41.9268 | 41.89 | 41.85 | 41.8079 | 41.7637 | 41.6763 | 41.5858 | 41.4847 | 41.1079 | 40.6489 | 40.2111 | 43.2489 | 43.2153 | 43.1816 | 43.1458 | 43.1079 | 43.0689 | 43.0289 | 42.9932 | 42.9574 | 42.9226 | 42.8363 | 42.39 | 41.9658
|  | UNIVERSITY PARKS | EE |  |  |  | 47.9637 | 47.9374 | 47.9089 | 47.8784 | 47.8468 | 47.8132 | 47.7805 | 47.7489 | 47.7184 | 47.69 | 47.6279 | 47.5542 | 47.4995 | 42.0216 | 41.9911 | 41.9553 | 41.9205 | 41.8858 | 41.8489 | 41.8142 | 41.7816 | 41.7458 | 41.7037 | 41.4805 | 41.1332 | 40.8079 | 43.2605 | 43.2342 | 43.2058 | 43.1753 | 43.1437 | 43.11 | 43.0774 | 43.0458 | 43.0153 | 42.9868 | 42.9342 | 42.8605 | 42.5447
|  | UNIVERSITY PARKS | HT |  |  |  | 47.9521 | 47.9184 | 47.8847 | 47.8489 | 47.8111 | 47.7721 | 47.7321 | 47.6963 | 47.6647 | 47.6342 | 47.5479 | 47.45 | 47.3689 | 42.0089 | 41.9626 | 41.9268 | 41.89 | 41.85 | 41.8079 | 41.7637 | 41.6763 | 41.5858 | 41.4847 | 41.1079 | 40.6489 | 40.2111 | 43.2489 | 43.2153 | 43.1816 | 43.1458 | 43.1079 | 43.0689 | 43.0289 | 42.9932 | 42.9574 | 42.9226 | 42.8363 | 42.39 | 41.9658
|  | UNIVERSITY PARKS | HE |  |  |  | 47.9784 | 47.9584 | 47.9363 | 47.9111 | 47.8847 | 47.8553 | 47.8289 | 47.8026 | 47.7784 | 47.7584 | 47.6426 | 47.5984 | 18.11 | 42.0384 | 42.0132 | 41.9847 | 41.9553 | 41.9268 | 41.8953 | 41.8668 | 41.8395 | 41.8153 | 41.7942 | 41.59 | 41.51 | 41.3711 | 43.2753 | 43.2553 | 43.2332 | 43.2079 | 43.1816 | 43.1521 | 43.1258 | 43.0995 | 43.0753 | 43.0553 | 42.9079 | 42.8616 | 42.8247
|  | UNIVERSITY PARKS | CF |  |  |  | 47.9868 | 47.9732 | 47.9595 | 47.9447 | 47.93 | 47.9142 | 47.8984 | 47.8837 | 47.8679 | 47.8532 | 47.7847 | 47.75 | 47.7311 | 42.0468 | 42.0321 | 42.0184 | 42.0026 | 41.9868 | 41.9711 | 41.9542 | 41.9384 | 41.9195 | 41.9016 | 41.8195 | 41.7795 | 41.7268 | 43.2837 | 43.27 | 43.2563 | 43.2416 | 43.2268 | 43.2111 | 43.1953 | 43.1805 | 43.1647 | 43.15 | 43.0816 | 43.0468 | 43.0279
EAST CLAYDON GSP | BICESTER NORTH BSP | UPPER HEYFORD | MINIMUM HEADROOM | SP 51750 25667 | YES | 0 | 16.2526 | 16.1905 | 16.1263 | 16.0095 | 15.3726 | 14.76 | 13.9032 | 13.0547 | 12.2126 | 11.3779 | 10.2495 | 13.2884 | -2.8116 | 15.0063 | 14.7684 | 14.4895 | 13.9453 | 13.2 | 12.4905 | 11.4905 | 10.5021 | 9.5189 | 8.5432 | 7.2484 | 10.7337 | 10.3968 | 15.2474 | 15.0168 | 14.7474 | 14.2211 | 13.4695 | 12.76 | 11.76 | 10.7705 | 9.7874 | 8.8116 | 7.5168 | 11.0021 | 10.6653
|  | UPPER HEYFORD | EE |  |  |  | 16.2779 | 16.2295 | 16.1779 | 16.1232 | 15.5179 | 14.9253 | 14.0905 | 13.2589 | 12.4326 | 11.6116 | 10.5684 | 43.8632 | 43.2842 | 15.0611 | 14.8495 | 14.5968 | 14.0747 | 13.3568 | 12.6684 | 11.6947 | 10.7232 | 9.7558 | 8.7958 | 7.5937 | 40.8389 | 40.1695 | 15.3 | 15.0968 | 14.8526 | 14.3505 | 13.6274 | 12.9389 | 11.9632 | 10.9916 | 10.0253 | 9.0642 | 7.8621 | 41.1063 | 40.4379
|  | UPPER HEYFORD | HT |  |  |  | 16.2526 | 16.1905 | 16.1263 | 16.0095 | 15.3726 | 14.76 | 13.9032 | 13.0547 | 12.2126 | 11.3779 | 10.2495 | 43.4358 | 42.7295 | 15.0063 | 14.7684 | 14.4895 | 13.9453 | 13.2 | 12.4905 | 11.4905 | 10.5021 | 9.5189 | 8.5432 | 7.2484 | 40.3737 | 39.5611 | 15.2474 | 15.0168 | 14.7474 | 14.2211 | 13.4695 | 12.76 | 11.76 | 10.7705 | 9.7874 | 8.8116 | 7.5168 | 40.6411 | 39.8295
|  | UPPER HEYFORD | HE |  |  |  | 16.3126 | 16.28 | 16.2453 | 16.2063 | 15.7074 | 15.1421 | 14.3326 | 13.5263 | 12.7242 | 11.9284 | 10.9979 | 44.3958 | -2.8116 | 15.1347 | 14.9579 | 14.7389 | 14.2505 | 13.5642 | 12.9053 | 11.9579 | 11.0137 | 10.0737 | 9.14 | 8.0621 | 41.42 | 40.8579 | 15.3547 | 15.2021 | 14.9905 | 14.5221 | 13.8337 | 13.1747 | 12.2274 | 11.2832 | 10.3421 | 9.4084 | 8.3305 | 41.6884 | 41.1253
|  | UPPER HEYFORD | CF |  |  |  | 16.3326 | 16.3147 | 16.2979 | 16.2789 | 16.26 | 16.24 | 16.22 | 15.8653 | 15.2832 | 14.6568 | 13.4642 | 13.2884 | 12.9989 | 15.2737 | 15.2558 | 15.2389 | 15.1495 | 15.0053 | 14.7937 | 14.3589 | 13.7442 | 13.0611 | 12.3242 | 10.9326 | 10.7337 | 10.3968 | 15.3821 | 15.3642 | 15.3474 | 15.3242 | 15.2463 | 15.0432 | 14.6263 | 14.0137 | 13.3305 | 12.5937 | 11.2021 | 11.0021 | 10.6653
IVER 132KV | UPTON BSP | UPTON | MINIMUM HEADROOM | TQ 00800 79434 | YES | 0.65684 | 31 | 30.8884 | 30.7274 | 30.3863 | 30.0305 | 29.48 | 28.6442 | 27.9474 | 27.2768 | 26.64 | 23.6411 | 21.0705 | -9.0726 | 25.5021 | 25.3726 | 25.0305 | 24.0126 | 23.3621 | 22.1011 | 21.1811 | 20.4179 | 19.6789 | 18.9768 | 15.64 | 12.7621 | 10.1105 | 26.6379 | 26.5232 | 26.4042 | 25.5537 | 24.9253 | 23.6979 | 22.7779 | 22.0158 | 21.2779 | 20.5768 | 17.2442 | 14.3695 | 11.7221
|  | UPTON | EE |  |  |  | 31.4916 | 31.2421 | 30.9768 | 30.6968 | 30.4 | 30.0926 | 29.5926 | 29.0147 | 28.44 | 27.9042 | 25.4916 | 23.5063 | 21.7253 | 26.3305 | 26.0053 | 25.5758 | 24.3905 | 24.0937 | 23.0063 | 22.2105 | 21.5789 | 20.9505 | 20.3621 | 17.6768 | 15.4442 | 13.4253 | 27.38 | 27.1147 | 26.8337 | 25.9263 | 25.6295 | 24.6011 | 23.8063 | 23.1758 | 22.5484 | 21.96 | 19.2779 | 17.0495 | 15.0337
|  | UPTON | HT |  |  |  | 31.3695 | 31.0495 | 30.7274 | 30.3863 | 30.0305 | 29.48 | 28.6442 | 27.9474 | 27.2768 | 26.64 | 23.6411 | 21.0705 | 18.72 | 26.1611 | 25.6632 | 25.0305 | 24.0126 | 23.3621 | 22.1011 | 21.1811 | 20.4179 | 19.6789 | 18.9768 | 15.64 | 12.7621 | 10.1105 | 27.2484 | 26.9074 | 26.5211 | 25.5537 | 24.9253 | 23.6979 | 22.7779 | 22.0158 | 21.2779 | 20.5768 | 17.2442 | 14.3695 | 11.7221
|  | UPTON | HE |  |  |  | 31.6411 | 31.4611 | 31.2621 | 31.0411 | 30.8032 | 30.5526 | 30.3095 | 30.08 | 29.8316 | 29.4253 | 27.6526 | 26.2821 | -9.0726 | 26.5453 | 26.3189 | 26.0747 | 24.7347 | 24.4968 | 24.1221 | 23.4621 | 22.9663 | 22.4789 | 22.0326 | 20.0505 | 18.4989 | 17.1421 | 27.5421 | 27.3537 | 27.1453 | 26.2705 | 26.0326 | 25.6674 | 25.0389 | 24.5621 | 24.0758 | 23.6295 | 21.6495 | 20.1 | 18.7463
|  | UPTON | CF |  |  |  | 31 | 30.8884 | 30.7758 | 30.6579 | 30.5358 | 30.4105 | 30.2821 | 30.1537 | 30.0295 | 29.9042 | 29.3042 | 29.1916 | 28.3768 | 25.5021 | 25.3726 | 25.2295 | 25.0663 | 24.8968 | 24.5495 | 24.0695 | 23.7611 | 23.4821 | 23.2095 | 21.7084 | 21.7347 | 20.8011 | 26.6379 | 26.5232 | 26.4042 | 26.2768 | 26.1453 | 26.0011 | 25.7189 | 25.4337 | 25.1663 | 24.9032 | 23.4695 | 23.3326 | 22.4
IVER 66kV |  | UXBRIDGE | MINIMUM HEADROOM | TQ 04984 83484 | YES | 0.66316 | 67.2116 | 66.8621 | 90.5074 | 90.1316 | 89.7411 | 89.3379 | 88.9337 | 88.5768 | 88.2516 | 87.9516 | 85.1853 | 81.9726 | 24.0484 | 58.3284 | 57.9095 | 81.2968 | 80.4916 | 79.4832 | 78.3895 | 77.3516 | 76.3758 | 75.4274 | 74.5316 | 70.3989 | 66.7884 | 63.4326 | 59.8789 | 59.5084 | 83.1274 | 82.7221 | 82.1768 | 81.0832 | 80.0453 | 79.0695 | 78.12 | 77.2242 | 73.0916 | 69.48 | 66.1232
|  | UXBRIDGE | EE |  |  |  | 67.3516 | 67.0811 | 90.7926 | 90.4874 | 90.1674 | 89.8347 | 89.5137 | 89.2084 | 88.9126 | 88.6505 | 87.6863 | 85.7284 | 83.5789 | 58.4905 | 58.1874 | 81.8263 | 81.3074 | 80.6421 | 79.6863 | 78.9189 | 78.1684 | 77.4316 | 76.7853 | 73.6589 | 70.9853 | 68.5453 | 60.0284 | 59.7432 | 83.4368 | 83.1105 | 82.7653 | 82.38 | 81.6126 | 80.8621 | 80.1242 | 79.4779 | 76.3516 | 73.6768 | 71.2368
|  | UXBRIDGE | HT |  |  |  | 67.2116 | 66.8621 | 90.5074 | 90.1316 | 89.7411 | 89.3379 | 88.9337 | 88.5768 | 88.2516 | 87.9516 | 85.1853 | 81.9726 | 79.0053 | 58.3284 | 57.9095 | 81.2968 | 80.4916 | 79.4832 | 78.3895 | 77.3516 | 76.3758 | 75.4274 | 74.5316 | 70.3989 | 66.7884 | 63.4326 | 59.8789 | 59.5084 | 83.1274 | 82.7221 | 82.1768 | 81.0832 | 80.0453 | 79.0695 | 78.12 | 77.2242 | 73.0916 | 69.48 | 66.1232
|  | UXBRIDGE | HE |  |  |  | 67.5263 | 67.3368 | 91.1274 | 90.8958 | 90.6463 | 90.3789 | 90.1253 | 89.8853 | 89.6621 | 89.4695 | 88.8137 | 88.4263 | 24.0484 | 58.6779 | 58.4863 | 82.2495 | 81.9726 | 81.4926 | 80.7684 | 80.1347 | 79.5137 | 78.9105 | 78.6316 | 76.2547 | 74.2832 | 72.5179 | 60.2116 | 60.0189 | 83.7968 | 83.5484 | 83.2716 | 82.9705 | 82.6947 | 82.2074 | 81.6042 | 81.3253 | 78.9484 | 76.9758 | 75.2105
|  | UXBRIDGE | CF |  |  |  | 67.6284 | 67.5168 | 91.4011 | 91.2811 | 91.1568 | 91.0284 | 90.8979 | 90.7695 | 90.6411 | 90.5147 | 89.9453 | 89.6611 | 89.5053 | 58.78 | 58.6684 | 82.5516 | 82.4116 | 82.2642 | 82.1021 | 81.9063 | 81.6442 | 81.3453 | 81.0326 | 79.3158 | 77.9779 | 76.8232 | 60.3137 | 60.2021 | 84.0832 | 83.9547 | 83.82 | 83.68 | 83.5379 | 83.3968 | 83.2547 | 83.1147 | 82.0095 | 80.6705 | 79.5158
NURSLING GSP | VELMORE BSP | VELMORE | MINIMUM HEADROOM | SU 42935 19205 | YES | 0.98842 | 35.9947 | 35.6832 | 35.3684 | 35.0358 | 34.6916 | 34.3337 | 33.1968 | 31.9179 | 30.6358 | 29.3674 | 25.0053 | 22.2442 | -14.7 | 30.5905 | 29.7611 | 29.0579 | 28.4484 | 27.6074 | 26.5295 | 25.0811 | 23.5516 | 22.0126 | 20.4853 | 15.2895 | 12.2 | 9.3411 | 32.2526 | 31.5316 | 30.8463 | 30.2274 | 29.3705 | 28.2684 | 26.7916 | 25.2611 | 23.7189 | 22.1884 | 16.9758 | 13.8695 | 11.0021
|  | VELMORE | EE |  |  |  | 36.1168 | 35.8758 | 35.62 | 35.3484 | 35.0663 | 34.7674 | 34.4779 | 33.5768 | 32.3168 | 31.0274 | 26.7947 | 24.6568 | 22.7032 | 30.8579 | 30.1695 | 29.5863 | 29.0979 | 28.4737 | 27.6842 | 26.6568 | 25.5021 | 23.9853 | 22.4232 | 17.3358 | 14.88 | 12.66 | 32.4116 | 31.8947 | 31.3811 | 30.8874 | 30.2526 | 29.4463 | 28.3937 | 27.2105 | 25.6905 | 24.1242 | 19.0137 | 16.5337 | 14.3053
|  | VELMORE | HT |  |  |  | 35.9947 | 35.6832 | 35.3684 | 35.0358 | 34.6916 | 34.3337 | 33.1968 | 31.9179 | 30.6358 | 29.3674 | 25.0053 | 22.2442 | 19.7189 | 30.5905 | 29.7611 | 29.0579 | 28.4484 | 27.6074 | 26.5295 | 25.0811 | 23.5516 | 22.0126 | 20.4853 | 15.2895 | 12.2 | 9.3411 | 32.2526 | 31.5316 | 30.8463 | 30.2274 | 29.3705 | 28.2684 | 26.7916 | 25.2611 | 23.7189 | 22.1884 | 16.9758 | 13.8695 | 11.0021
|  | VELMORE | HE |  |  |  | 36.2853 | 36.1221 | 35.9442 | 35.7453 | 35.5337 | 35.3021 | 35.0832 | 34.7863 | 33.6389 | 32.4968 | 28.9211 | 27.4042 | -14.7 | 31.2189 | 30.6979 | 30.2821 | 29.9474 | 29.4695 | 28.8084 | 27.9095 | 26.8316 | 25.4568 | 24.06 | 19.7084 | 17.8905 | 16.2263 | 32.58 | 32.3632 | 31.9979 | 31.6926 | 31.2653 | 30.5895 | 29.6695 | 28.5621 | 27.1653 | 25.7674 | 21.4063 | 19.5811 | 17.9095
|  | VELMORE | CF |  |  |  | 36.38 | 36.2905 | 36.1968 | 36.1 | 36 | 35.8947 | 35.7863 | 35.6811 | 35.5768 | 35.4716 | 32.8768 | 31.8158 | 30.94 | 31.4547 | 31.16 | 30.9263 | 30.7295 | 30.5263 | 30.3063 | 30.0547 | 29.7537 | 29.4084 | 28.9916 | 24.4084 | 23.1368 | 22.0726 | 32.6747 | 32.5853 | 32.4916 | 32.3842 | 32.2021 | 32.0053 | 31.7842 | 31.5242 | 31.2 | 30.7726 | 26.1168 | 24.84 | 23.7716
FAWLEY GSP | COWES & WOOTTON COMMON BSP | VENTNOR | MINIMUM HEADROOM | SZ 56148 77857 | YES | 30 | 33.2432 | 32.8526 | 2.4284 | 1.9979 | 1.5474 | 1.0642 | 0.55895 | 0.076842 | -0.38421 | -0.83789 | -3.0358 | -5.0147 | -17.5632 | 30.0326 | 29.58 | -0.86947 | -1.3253 | -1.8011 | -2.3137 | -2.8516 | -3.3674 | -3.8621 | -4.3505 | -6.74 | -8.9095 | -10.8674 | 30.5516 | 30.1084 | -0.33263 | -0.77895 | -1.2453 | -1.7474 | -2.2737 | -2.7968 | -3.3011 | -3.7989 | -6.2379 | -8.4558 | -10.4611
|  | VENTNOR | EE |  |  |  | 33.3347 | 33.14 | 2.8021 | 2.4421 | 2.0716 | 1.6947 | 1.3063 | 0.92421 | 0.57684 | 0.23053 | -1.4326 | -2.9789 | -4.3411 | 30.2347 | 29.8874 | -0.46947 | -0.85053 | -1.2432 | -1.6411 | -2.0516 | -2.46 | -2.8274 | -3.1968 | -5.0011 | -6.7021 | -8.2084 | 30.7484 | 30.4084 | 0.058947 | -0.31474 | -0.7 | -1.0895 | -1.4926 | -1.8916 | -2.2516 | -2.6221 | -4.4632 | -6.2042 | -7.7484
|  | VENTNOR | HT |  |  |  | 33.2432 | 32.8526 | 2.4284 | 1.9979 | 1.5474 | 1.0642 | 0.55895 | 0.076842 | -0.38421 | -0.83789 | -3.0358 | -5.0147 | -6.7926 | 30.0326 | 29.58 | -0.86947 | -1.3253 | -1.8011 | -2.3137 | -2.8516 | -3.3674 | -3.8621 | -4.3505 | -6.74 | -8.9095 | -10.8674 | 30.5516 | 30.1084 | -0.33263 | -0.77895 | -1.2453 | -1.7474 | -2.2737 | -2.7968 | -3.3011 | -3.7989 | -6.2379 | -8.4558 | -10.4611
|  | VENTNOR | HE |  |  |  | 33.46 | 33.3337 | 3.1937 | 3.0389 | 2.7874 | 2.5032 | 2.2168 | 1.9316 | 1.6821 | 1.42 | 0.20842 | -0.91895 | -17.5632 | 30.5084 | 30.2905 | 0.057895 | -0.2 | -0.47579 | -0.77474 | -1.0768 | -1.3789 | -1.6432 | -1.9242 | -3.2432 | -4.4916 | -5.5663 | 30.8937 | 30.7611 | 0.57263 | 0.32 | 0.049474 | -0.24421 | -0.54105 | -0.83684 | -1.0958 | -1.3695 | -2.6747 | -3.9547 | -5.0589
|  | VENTNOR | CF |  |  |  | 33.5337 | 33.4632 | 3.3895 | 3.3126 | 3.2337 | 3.0968 | 2.9063 | 2.7253 | 2.5537 | 2.3842 | 1.7274 | 0.98632 | 0.35474 | 30.6495 | 30.5158 | 0.37474 | 0.21158 | 0.032632 | -0.16211 | -0.36737 | -0.56211 | -0.74632 | -0.92842 | -1.6253 | -2.4442 | -3.1495 | 30.9716 | 30.8968 | 0.81895 | 0.72526 | 0.55158 | 0.36105 | 0.16105 | -0.028421 | -0.20737 | -0.38632 | -1.0684 | -1.8705 | -2.5947
MANNINGTON GSP | MANNINGTON BSP | VERWOOD | MINIMUM HEADROOM | SU 07716 10226 | YES | 0 | 12.1516 | 11.3905 | 10.7695 | 10.2516 | 9.7284 | 9.1989 | 8.6716 | 8.1916 | 7.7421 | 7.3189 | 3.6905 | 1.1453 | -10.4326 | 9.6853 | 8.8095 | 8.1116 | 7.5453 | 6.9758 | 6.4042 | 5.8389 | 5.3221 | 4.8379 | 4.3811 | 0.15158 | -2.6537 | -3.6032 | 10.1537 | 9.3042 | 8.6232 | 8.0674 | 7.5074 | 6.9442 | 6.3832 | 5.8589 | 5.3642 | 4.8958 | 0.59158 | -2.2547 | -3.2211
|  | VERWOOD | EE |  |  |  | 12.3821 | 11.7389 | 11.2232 | 10.8116 | 10.3884 | 9.9537 | 9.5295 | 9.1211 | 8.7263 | 8.3579 | 6.8105 | 4.74 | 3.2284 | 9.9421 | 9.1979 | 8.6168 | 8.1663 | 7.7074 | 7.2411 | 6.7874 | 6.3526 | 5.9316 | 5.5411 | 3.8937 | 1.5484 | -0.22632 | 10.4053 | 9.6832 | 9.1158 | 8.6747 | 8.2232 | 7.7621 | 7.3105 | 6.8779 | 6.4579 | 6.0663 | 4.3579 | 1.9147 | 0.11789
|  | VERWOOD | HT |  |  |  | 12.1516 | 11.3905 | 10.7695 | 10.2516 | 9.7284 | 9.1989 | 8.6716 | 8.1916 | 7.7421 | 7.3189 | 3.6905 | 1.1453 | 0.23263 | 9.6853 | 8.8095 | 8.1116 | 7.5453 | 6.9758 | 6.4042 | 5.8389 | 5.3221 | 4.8379 | 4.3811 | 0.15158 | -2.6537 | -3.6032 | 10.1537 | 9.3042 | 8.6232 | 8.0674 | 7.5074 | 6.9442 | 6.3832 | 5.8589 | 5.3642 | 4.8958 | 0.59158 | -2.2547 | -3.2211
|  | VERWOOD | HE |  |  |  | 12.5589 | 12.1958 | 11.8232 | 11.5484 | 11.2558 | 10.9442 | 10.6453 | 10.3653 | 10.0979 | 9.8579 | 8.9463 | 7.5063 | -10.4326 | 10.2874 | 9.7074 | 9.2842 | 8.9874 | 8.6726 | 8.3421 | 8.0253 | 7.7274 | 7.4453 | 7.1895 | 6.22 | 4.5305 | 3.2589 | 10.7421 | 10.1811 | 9.7695 | 9.4779 | 9.1674 | 8.8389 | 8.5253 | 8.2284 | 7.9474 | 7.6937 | 6.7221 | 5.0126 | 3.6968
|  | VERWOOD | CF |  |  |  | 12.6537 | 12.5716 | 12.4 | 12.2495 | 12.0916 | 11.9263 | 11.76 | 11.5958 | 11.4316 | 11.2695 | 10.5305 | 9.5779 | 8.9137 | 10.4926 | 10.1705 | 9.9432 | 9.7758 | 9.6021 | 9.4221 | 9.2411 | 9.0611 | 8.8821 | 8.7063 | 7.9 | 6.7832 | 6.0011 | 10.9421 | 10.6316 | 10.4095 | 10.2463 | 10.0768 | 9.8989 | 9.72 | 9.5432 | 9.3653 | 9.1916 | 8.3968 | 7.3095 | 6.5137
NORTH HYDE GSP |  | VICARAGE FARM ROAD | MINIMUM HEADROOM | TQ 12358 76435 | NO | 0.34526 | 45.9674 | 45.5105 | 86.9 | 86.2968 | 84.8253 | 82.6621 | 81.1116 | 79.6495 | 78.2379 | 76.8695 | 71.8053 | 66.92 | 18.4232 | 38.4947 | 36.8032 | 76.8863 | 74.7832 | 72.4811 | 69.9789 | 68.2179 | 66.5516 | 64.9358 | 63.3674 | 57.6442 | 52.0947 | 46.5905 | 39.9526 | 38.6926 | 78.8758 | 76.8495 | 74.5505 | 72.0526 | 70.2926 | 68.6284 | 67.0158 | 65.4495 | 59.7432 | 54.2021 | 48.7063
|  | VICARAGE FARM ROAD | EE |  |  |  | 46.1379 | 45.7768 | 87.2958 | 86.8589 | 86.3432 | 85.6568 | 84.0211 | 82.6158 | 81.1095 | 79.7242 | 75.1968 | 71.8032 | 68.3042 | 38.9032 | 37.6979 | 78.4274 | 77.0768 | 75.4189 | 73.4726 | 71.5863 | 69.9758 | 68.24 | 66.6421 | 61.4547 | 57.5968 | 53.5832 | 40.1379 | 39.5421 | 80.3284 | 79.0484 | 77.4821 | 75.54 | 73.6568 | 72.0484 | 70.3158 | 68.72 | 63.54 | 59.6968 | 55.6895
|  | VICARAGE FARM ROAD | HT |  |  |  | 45.9674 | 45.5105 | 86.9 | 86.2968 | 84.8253 | 82.6621 | 81.1116 | 79.6495 | 78.2379 | 76.8695 | 71.8053 | 66.92 | 62.0853 | 38.4947 | 36.8032 | 76.8863 | 74.7832 | 72.4811 | 69.9789 | 68.2179 | 66.5516 | 64.9358 | 63.3674 | 57.6442 | 52.0947 | 46.5905 | 39.9526 | 38.6926 | 78.8758 | 76.8495 | 74.5505 | 72.0526 | 70.2926 | 68.6284 | 67.0158 | 65.4495 | 59.7432 | 54.2021 | 48.7063
|  | VICARAGE FARM ROAD | HE |  |  |  | 46.3463 | 46.08 | 87.6863 | 87.3621 | 86.9484 | 86.4768 | 85.5432 | 84.2863 | 82.9884 | 81.8284 | 78.2895 | 75.6863 | 18.4232 | 39.3116 | 38.4316 | 79.3653 | 78.2032 | 76.7432 | 74.9516 | 73.2779 | 71.8305 | 70.3284 | 68.9832 | 64.9011 | 61.8747 | 58.8589 | 40.3632 | 40.0558 | 81.2263 | 80.1253 | 78.7484 | 77.0179 | 75.3463 | 73.9011 | 72.4011 | 71.0579 | 66.9821 | 63.96 | 60.9495
|  | VICARAGE FARM ROAD | CF |  |  |  | 46.4737 | 46.3116 | 88.0432 | 87.8684 | 87.6874 | 87.5 | 87.3084 | 87.1211 | 86.9337 | 86.7 | 82.7758 | 81.0621 | 79.4137 | 39.4926 | 39.2253 | 80.8063 | 80.3726 | 79.8947 | 79.3768 | 78.8337 | 78.3189 | 77.56 | 76.6926 | 70.0105 | 68.0284 | 66.0853 | 40.5053 | 40.3232 | 82.0432 | 81.8526 | 81.6547 | 81.2242 | 80.7074 | 80.2158 | 79.4979 | 78.6811 | 72.0853 | 70.1063 | 68.1663
COWLEY GSP | COWLEY LOCAL (2 X 90) | WALLINGFORD | MINIMUM HEADROOM | SU 59847 89486 | YES | 0.29053 | 13.8758 | 13.6084 | 13.3389 | 12.3853 | 11.3189 | 10.1505 | 9.0937 | 7.9579 | 6.8526 | 6.1621 | 4.3411 | 2.6916 | -45.4053 | 10.9011 | 10.0926 | 9.1337 | 8.0474 | 6.8389 | 5.5116 | 4.3421 | 3.0284 | 1.7463 | 0.97368 | -1.0074 | -2.7032 | -4.58 | 11.5316 | 10.7137 | 9.7432 | 8.6432 | 7.4179 | 6.0726 | 4.9263 | 3.6126 | 2.3305 | 1.5568 | -0.42421 | -2.2453 | -4.1442
|  | WALLINGFORD | EE |  |  |  | 13.9768 | 13.7674 | 13.5453 | 12.8895 | 11.9137 | 10.8316 | 9.7495 | 8.6853 | 7.6326 | 7.0126 | 9.1789 | 8.0674 | 6.8474 | 11.1284 | 10.4368 | 9.5821 | 8.5979 | 7.4863 | 6.2516 | 5.0053 | 3.7705 | 2.5484 | 1.84 | 5.8968 | 4.7232 | 3.3516 | 11.7611 | 11.0621 | 10.1958 | 9.1979 | 8.0726 | 6.82 | 5.5653 | 4.3305 | 3.1074 | 2.4 | 7.1853 | 6.0358 | 4.6632
|  | WALLINGFORD | HT |  |  |  | 13.8758 | 13.6084 | 13.3389 | 12.3853 | 11.3189 | 10.1505 | 9.0937 | 7.9579 | 6.8526 | 6.1621 | 4.3411 | 2.6916 | 0.99474 | 10.9011 | 10.0926 | 9.1337 | 8.0474 | 6.8389 | 5.5116 | 4.3421 | 3.0284 | 1.7463 | 0.97368 | -1.0074 | -2.7032 | -4.58 | 11.5316 | 10.7137 | 9.7432 | 8.6432 | 7.4179 | 6.0726 | 4.9263 | 3.6126 | 2.3305 | 1.5568 | -0.42421 | -2.2453 | -4.1442
|  | WALLINGFORD | HE |  |  |  | 14.12 | 13.9779 | 13.8221 | 13.5663 | 12.7042 | 11.7326 | 10.7568 | 9.7968 | 8.8537 | 8.3368 | 14.3611 | 13.46 | -45.4053 | 11.44 | 10.8968 | 10.1853 | 9.3368 | 8.3505 | 7.2358 | 6.1147 | 4.9947 | 3.8916 | 3.2989 | 2.5295 | 1.3726 | 0.5 | 12.0768 | 11.5263 | 10.8053 | 9.9442 | 8.9442 | 7.8126 | 6.6758 | 5.5558 | 4.4516 | 3.8589 | 8.6895 | 7.66 | 7.2442
|  | WALLINGFORD | CF |  |  |  | 14.2011 | 14.1211 | 14.0379 | 13.9516 | 13.8632 | 13.7705 | 13.3674 | 12.8653 | 12.3326 | 12 | 11.2021 | 10.6379 | 10.1495 | 11.6726 | 11.3663 | 10.9979 | 10.5874 | 10.1347 | 9.6389 | 9.0968 | 8.5189 | 7.9042 | 7.5274 | 6.6568 | 6.0263 | 5.4653 | 12.3116 | 12.0011 | 11.6274 | 11.2116 | 10.7526 | 10.2495 | 9.6989 | 9.1126 | 8.4895 | 8.1074 | 7.2295 | 6.5905 | 6.0253
COWLEY GSP | DRAYTON BSP | WANTAGE | MINIMUM HEADROOM | SU 41290 88304 | YES | 0.54316 | 26.7663 | 26.5379 | 26.0853 | 25.2516 | 24.4726 | 23.6337 | 22.7947 | 21.9916 | 21.2211 | 20.4695 | 17.3042 | 15.8379 | 0 | 22.8737 | 22.0547 | 21.0189 | 20.1168 | 19.2747 | 18.3684 | 17.4611 | 16.5905 | 15.7526 | 14.9358 | 11.8505 | 10.2274 | 8.2684 | 24.3926 | 23.7326 | 22.7179 | 21.7874 | 20.9168 | 19.9768 | 19.0358 | 18.1337 | 17.2642 | 16.4147 | 12.8326 | 11.2105 | 9.2547
|  | WANTAGE | EE |  |  |  | 26.8558 | 26.6779 | 26.4432 | 25.6937 | 24.9937 | 24.2295 | 23.4747 | 22.7337 | 22.0084 | 21.3105 | 18.4621 | 17.4947 | 16.2337 | 23.0674 | 22.3474 | 21.3989 | 20.5842 | 20.5116 | 19.6516 | 18.8 | 17.9621 | 17.1432 | 16.3505 | 13.1053 | 12.0411 | 10.6095 | 24.4884 | 24.0221 | 23.0916 | 22.2674 | 21.4811 | 20.6221 | 19.7716 | 18.9347 | 18.1168 | 17.3263 | 14.0863 | 13.0221 | 11.5937
|  | WANTAGE | HT |  |  |  | 26.7663 | 26.5379 | 26.0853 | 25.2516 | 24.4726 | 23.6337 | 22.7947 | 21.9916 | 21.2211 | 20.4695 | 17.3042 | 15.8379 | 14.1053 | 22.8737 | 22.0547 | 21.0189 | 20.1168 | 19.2747 | 18.3684 | 17.4611 | 16.5905 | 15.7526 | 14.9358 | 11.8505 | 10.2274 | 8.2684 | 24.3926 | 23.7326 | 22.7179 | 21.7874 | 20.9168 | 19.9768 | 19.0358 | 18.1337 | 17.2642 | 16.4147 | 12.8326 | 11.2105 | 9.2547
|  | WANTAGE | HE |  |  |  | 26.9779 | 26.8579 | 26.7253 | 26.28 | 25.6821 | 25.0147 | 24.3516 | 23.7011 | 23.0684 | 22.4589 | 20.04 | 19.4674 | 0 | 23.3295 | 22.7337 | 21.9053 | 21.2042 | 20.5547 | 19.8284 | 19.7537 | 19.0147 | 18.2947 | 17.6 | 14.8253 | 14.1937 | 13.1758 | 24.6189 | 24.4021 | 23.5916 | 22.9042 | 22.2305 | 21.4758 | 20.7253 | 19.9874 | 19.2695 | 18.5747 | 15.8042 | 15.1737 | 14.1568
|  | WANTAGE | CF |  |  |  | 27.0484 | 26.9811 | 26.9116 | 26.8389 | 26.7642 | 26.6863 | 26.4811 | 26.1347 | 25.7737 | 25.3937 | 23.7011 | 23.2853 | 22.7337 | 23.5 | 23.1705 | 22.7568 | 22.4189 | 22.1126 | 21.7821 | 21.4253 | 21.0484 | 20.6537 | 20.2379 | 18.3863 | 17.9421 | 17.3368 | 24.6958 | 24.6126 | 24.4263 | 24.0958 | 23.7958 | 23.4716 | 23.1221 | 22.7432 | 22.3316 | 21.8989 | 19.9716 | 19.5126 | 18.8811
MANNINGTON GSP | WAREHAM | WAREHAM TOWN | MINIMUM HEADROOM | SY 92036 87463 | YES | 1.1832 | 12.7932 | 12.6068 | 41.5 | 41.1326 | 40.3653 | 39.8695 | 39.5211 | 38.9126 | 36.0779 | 35.8063 | 31.9779 | 29.7347 | 19.4811 | 10.1016 | 9.7426 | 38.1526 | 37.7968 | 36.9358 | 36.3968 | 36.0316 | 35.3589 | 32.0821 | 31.9095 | 27.6853 | 25.0495 | 24.3074 | 10.7068 | 10.3363 | 38.7368 | 38.3495 | 37.5158 | 36.9895 | 36.6263 | 35.9716 | 32.6432 | 32.4653 | 28.1021 | 25.5779 | 24.8189
|  | WAREHAM TOWN | EE |  |  |  | 12.8637 | 12.7163 | 41.7853 | 41.4821 | 40.7779 | 40.34 | 40.0526 | 39.7747 | 39.5021 | 39.2495 | 35.7642 | 32.4516 | 31.1011 | 10.2511 | 9.9668 | 38.4453 | 38.1358 | 37.3821 | 36.9063 | 36.6084 | 36.32 | 36.04 | 35.7779 | 31.8663 | 28.3116 | 26.8347 | 10.8595 | 10.5679 | 39.0389 | 38.7189 | 37.9526 | 37.4863 | 37.1874 | 36.8989 | 36.6147 | 36.3526 | 32.3842 | 28.6874 | 27.1579
|  | WAREHAM TOWN | HT |  |  |  | 12.7932 | 12.6068 | 41.5 | 41.1326 | 40.3653 | 39.8695 | 39.5211 | 38.9126 | 36.0779 | 35.8063 | 31.9779 | 29.7347 | 29.0242 | 10.1016 | 9.7426 | 38.1526 | 37.7968 | 36.9358 | 36.3968 | 36.0316 | 35.3589 | 32.0821 | 31.9095 | 27.6853 | 25.0495 | 24.3074 | 10.7068 | 10.3363 | 38.7368 | 38.3495 | 37.5158 | 36.9895 | 36.6263 | 35.9716 | 32.6432 | 32.4653 | 28.1021 | 25.5779 | 24.8189
|  | WAREHAM TOWN | HE |  |  |  | 12.9637 | 12.8647 | 42.1737 | 41.96 | 41.3379 | 40.9832 | 40.78 | 40.5895 | 40.4084 | 40.2442 | 37.0905 | 34.5474 | 19.4811 | 10.4553 | 10.27 | 38.8421 | 38.6232 | 37.9863 | 37.6 | 37.3895 | 37.1916 | 37.0042 | 36.8347 | 33.2368 | 30.3232 | 29.1453 | 11.0437 | 10.8816 | 39.4484 | 39.2242 | 38.5453 | 38.1663 | 37.9558 | 37.7589 | 37.5716 | 37.4021 | 33.9263 | 30.8011 | 29.58
|  | WAREHAM TOWN | CF |  |  |  | 13.0226 | 12.9679 | 41.6611 | 41.6021 | 43.5053 | 43.4358 | 43.3674 | 43.2979 | 43.2295 | 43.1642 | 42.8589 | 42.6853 | 42.5726 | 10.5721 | 10.4616 | 39.1074 | 38.9874 | 38.6937 | 38.5179 | 38.4011 | 38.2853 | 38.1705 | 38.0568 | 37.5442 | 37.0726 | 36.5968 | 11.1384 | 11.0489 | 39.7126 | 39.5979 | 40.1411 | 40.0295 | 39.9411 | 39.8526 | 39.7653 | 39.6821 | 39.2926 | 38.9989 | 38.74
BRAMLEY (FLEE) | BRACKNELL | WARFIELD | MINIMUM HEADROOM | SU 86960 71382 | YES | 0.18737 | 36.6358 | 36.2674 | 35.8926 | 35.4979 | 35.0905 | 33.5895 | 32.3021 | 30.6958 | 29.0926 | 28.2621 | 25.4621 | 31.06 | -11.4821 | 30.7653 | 29.5411 | 28.2737 | 26.84 | 25.3979 | 23.6853 | 22.2495 | 20.4316 | 18.6116 | 17.6937 | 14.6463 | 11.4632 | 8.4979 | 32.1916 | 31.1505 | 29.9042 | 28.4526 | 26.9926 | 25.2779 | 23.8411 | 22.0211 | 20.1979 | 19.2779 | 16.2137 | 12.8305 | 9.8179
|  | WARFIELD | EE |  |  |  | 36.7821 | 36.4947 | 36.1905 | 35.8674 | 35.5295 | 34.5558 | 33.4032 | 31.8968 | 30.3705 | 29.6211 | 33.4716 | 31.06 | 28.9821 | 31.0842 | 30.0232 | 28.9021 | 27.6105 | 26.3053 | 24.7316 | 23.44 | 21.7295 | 19.9968 | 19.1684 | 26.2137 | 23.5347 | 21.1905 | 32.3484 | 31.6189 | 30.5389 | 29.2295 | 27.9074 | 26.3242 | 25.0305 | 23.3179 | 21.5811 | 20.7484 | 28.9874 | 26.2853 | 23.9337
|  | WARFIELD | HT |  |  |  | 36.6358 | 36.2674 | 35.8926 | 35.4979 | 35.0905 | 33.5895 | 32.3021 | 30.6958 | 29.0926 | 28.2621 | 25.4621 | 34.1105 | 19.8337 | 30.7653 | 29.5411 | 28.2737 | 26.84 | 25.3979 | 23.6853 | 22.2495 | 20.4316 | 18.6116 | 17.6937 | 14.6463 | 11.4632 | 8.4979 | 32.1916 | 31.1505 | 29.9042 | 28.4526 | 26.9926 | 25.2779 | 23.8411 | 22.0211 | 20.1979 | 19.2779 | 16.2137 | 12.8305 | 9.8179
|  | WARFIELD | HE |  |  |  | 36.9821 | 36.7905 | 36.5789 | 36.3453 | 36.0937 | 35.6947 | 34.6968 | 33.34 | 31.9747 | 31.3811 | 37.7863 | 37.2579 | -11.4821 | 31.4716 | 30.7779 | 29.8611 | 28.7074 | 27.3526 | 25.9558 | 24.8295 | 23.2811 | 21.7211 | 21.06 | 19.5958 | 17.6895 | 16.0263 | 32.5653 | 32.3379 | 31.4705 | 30.3379 | 28.9642 | 27.5495 | 26.4221 | 24.8726 | 23.3095 | 22.6474 | 27.8242 | 26.8968 | 26.1505
|  | WARFIELD | CF |  |  |  | 37.0958 | 36.9884 | 36.8789 | 36.7642 | 36.6453 | 36.6074 | 36.48 | 36.3537 | 36.2305 | 36.1074 | 35.1463 | 33.9947 | 33.0453 | 31.5968 | 31.4411 | 30.9684 | 30.4147 | 29.7937 | 29.2221 | 28.6674 | 27.8695 | 27.0116 | 26.5863 | 25.3768 | 24.08 | 22.9958 | 32.6905 | 32.5632 | 32.4326 | 32.0032 | 31.4105 | 30.8558 | 30.2937 | 29.4821 | 28.6126 | 28.18 | 26.9674 | 25.6653 | 24.5779
MELKSHAM GSP | FROME BSP | WARMINSTER | MINIMUM HEADROOM | ST 84936 44551 | YES | 0.22632 | 17.5463 | 17.4179 | 17.2705 | 16.7895 | 15.9874 | 14.9968 | 14.0095 | 13.1032 | 12.4453 | 11.7768 | 10.4937 | 9.3526 | -2.9916 | 14.8379 | 14.4537 | 13.9021 | 13.3305 | 12.3568 | 11.2526 | 10.1526 | 9.1432 | 8.4147 | 7.6747 | 6.3063 | 5.0737 | 3.9063 | 15.6337 | 15.4853 | 14.7926 | 14.1663 | 13.1674 | 12.0316 | 10.8989 | 9.8611 | 9.1105 | 8.3474 | 6.9347 | 5.6716 | 4.4937
|  | WARMINSTER | EE |  |  |  | 17.5937 | 17.4905 | 17.3811 | 17.0105 | 16.3737 | 15.5084 | 14.6379 | 13.6474 | 12.8505 | 12.2189 | 11.1558 | 10.2137 | 9.3863 | 14.9316 | 14.5958 | 14.0874 | 13.5905 | 12.7768 | 11.8137 | 10.8432 | 9.7368 | 8.8505 | 8.1537 | 7.0358 | 6.0474 | 5.1368 | 15.6842 | 15.5632 | 15.0074 | 14.4305 | 13.5968 | 12.6032 | 11.6032 | 10.4642 | 9.5516 | 8.8305 | 7.6674 | 6.6284 | 5.6958
|  | WARMINSTER | HT |  |  |  | 17.5463 | 17.4179 | 17.2705 | 16.7895 | 15.9874 | 14.9968 | 14.0095 | 13.1032 | 12.4453 | 11.7768 | 10.4937 | 9.3526 | 8.3053 | 14.8379 | 14.4537 | 13.9021 | 13.3305 | 12.3568 | 11.2526 | 10.1526 | 9.1432 | 8.4147 | 7.6747 | 6.3063 | 5.0737 | 3.9063 | 15.6337 | 15.4853 | 14.7926 | 14.1663 | 13.1674 | 12.0316 | 10.8989 | 9.8611 | 9.1105 | 8.3474 | 6.9347 | 5.6716 | 4.4937
|  | WARMINSTER | HE |  |  |  | 17.6611 | 17.5905 | 17.5126 | 17.3126 | 16.7411 | 15.94 | 15.1242 | 14.1747 | 13.4758 | 12.9137 | 12.18 | 11.5832 | -2.9916 | 15.0621 | 14.7884 | 14.3411 | 13.9379 | 13.1905 | 12.2737 | 11.36 | 10.2937 | 9.5126 | 8.8853 | 8.1032 | 7.4558 | 6.8063 | 15.7568 | 15.6705 | 15.3021 | 14.7926 | 14.0179 | 13.0726 | 12.1326 | 11.0347 | 10.2295 | 9.5832 | 8.7737 | 8.1042 | 7.4295
|  | WARMINSTER | CF |  |  |  | 17.7011 | 17.6611 | 17.6189 | 17.5758 | 17.5305 | 17.48 | 17.2663 | 16.98 | 16.6263 | 16.1832 | 15.2768 | 14.9074 | 14.5221 | 15.1684 | 15.0168 | 14.7926 | 14.6011 | 14.3895 | 14.1505 | 13.8821 | 13.5063 | 13.0421 | 12.5442 | 11.5474 | 11.1484 | 10.7253 | 15.8021 | 15.7537 | 15.6968 | 15.6295 | 15.3621 | 15.0579 | 14.7253 | 14.3389 | 13.8611 | 13.3495 | 12.3232 | 11.9105 | 11.4726
LOVEDEAN GSP | FORT WIDLEY | WATERLOOVILLE | MINIMUM HEADROOM | SU 67988 09282 | YES | 0.14 | 49.1347 | 48.6053 | 48.0674 | 47.3768 | 45.7453 | 43.9632 | 42.3421 | 40.8558 | 39.4421 | 38.0937 | 32.3779 | 27.4432 | -5.0505 | 42.8411 | 41.3316 | 39.7284 | 38.0295 | 36.2105 | 34.2168 | 32.4137 | 30.7568 | 29.1768 | 27.6684 | 21.2516 | 15.6768 | 10.5053 | 44.3653 | 43.0105 | 41.4495 | 39.7505 | 37.9316 | 35.9379 | 34.1337 | 32.4758 | 30.8958 | 29.3853 | 22.9642 | 17.3842 | 12.2105
|  | WATERLOOVILLE | EE |  |  |  | 49.3463 | 48.9337 | 48.4979 | 48.0347 | 47.0158 | 45.4632 | 44.06 | 42.7526 | 41.5547 | 40.4368 | 35.8937 | 31.9768 | 28.4295 | 43.3053 | 42.1189 | 40.7116 | 39.1821 | 37.5947 | 35.8547 | 34.2853 | 32.8253 | 31.4926 | 30.2442 | 25.1453 | 20.7042 | 16.6453 | 44.5916 | 43.7642 | 42.4284 | 40.9032 | 39.3158 | 37.5747 | 36.0053 | 34.5442 | 33.2105 | 31.9621 | 26.8579 | 22.4095 | 18.3484
|  | WATERLOOVILLE | HT |  |  |  | 49.1347 | 48.6053 | 48.0674 | 47.3768 | 45.7453 | 43.9632 | 42.3421 | 40.8558 | 39.4421 | 38.0937 | 32.3779 | 27.4432 | 22.8968 | 42.8411 | 41.3316 | 39.7284 | 38.0295 | 36.2105 | 34.2168 | 32.4137 | 30.7568 | 29.1768 | 27.6684 | 21.2516 | 15.6768 | 10.5053 | 44.3653 | 43.0105 | 41.4495 | 39.7505 | 37.9316 | 35.9379 | 34.1337 | 32.4758 | 30.8958 | 29.3853 | 22.9642 | 17.3842 | 12.2105
|  | WATERLOOVILLE | HE |  |  |  | 49.6274 | 49.3484 | 49.04 | 48.7 | 48.3326 | 47.2663 | 46.0758 | 44.9895 | 44.0053 | 43.08 | 39.5389 | 36.5684 | -5.0505 | 43.9263 | 43.0316 | 41.9021 | 40.6474 | 39.3147 | 37.82 | 36.4832 | 35.2642 | 34.1642 | 33.1232 | 29.12 | 25.7168 | 22.6179 | 44.8926 | 44.5779 | 43.5716 | 42.3695 | 41.0368 | 39.5411 | 38.2032 | 36.9853 | 35.8832 | 34.8421 | 30.8368 | 27.4316 | 24.3305
|  | WATERLOOVILLE | CF |  |  |  | 49.7916 | 49.6358 | 49.4758 | 49.3084 | 49.1337 | 48.9558 | 48.7716 | 48.5926 | 48.4158 | 47.8916 | 45.2863 | 43.3432 | 41.6411 | 44.3863 | 43.9021 | 43.3674 | 42.7611 | 42.1284 | 41.4442 | 40.7432 | 40.0211 | 39.2663 | 38.5063 | 35.5747 | 33.3547 | 31.3874 | 45.0737 | 44.8989 | 44.7168 | 44.3874 | 43.7884 | 43.1411 | 42.4653 | 41.7432 | 40.9863 | 40.2263 | 37.2947 | 35.0737 | 33.1042
COWLEY GSP | HIGH WYCOMBE BSP | WATLINGTON | MINIMUM HEADROOM | SU 69106 94287 | YES | 0.21053 | 9.6863 | 9.7168 | 9.4916 | 9.2611 | 9.0274 | 8.5905 | 8.0095 | 7.3116 | 7.1853 | 7.0653 | 5.7337 | 4.02 | -27.5632 | 7.5621 | 7.3211 | 7.0779 | 6.8326 | 6.5811 | 6.0968 | 5.4442 | 4.6505 | 4.5274 | 4.4126 | 2.9653 | 1.0558 | 0.52 | 7.8484 | 7.6063 | 7.3642 | 7.1179 | 6.8663 | 6.3811 | 5.7253 | 4.9295 | 4.8021 | 4.6832 | 3.2084 | 1.2705 | 0.72211
|  | WATLINGTON | EE |  |  |  | 10.0411 | 9.8674 | 9.6884 | 9.5021 | 9.3126 | 9.1074 | 8.9 | 8.7011 | 8.5042 | 8.3221 | 7.5253 | 6.2832 | 5.2474 | 7.6716 | 7.4853 | 7.2926 | 7.0937 | 6.8895 | 6.6747 | 6.4589 | 6.2505 | 6.0474 | 5.8579 | 5.0411 | 3.6937 | 2.5263 | 7.9568 | 7.7705 | 7.5779 | 7.3789 | 7.1758 | 6.9579 | 6.7368 | 6.5242 | 6.3158 | 6.12 | 5.2653 | 3.8747 | 2.6947
|  | WATLINGTON | HT |  |  |  | 9.9411 | 9.7168 | 9.4916 | 9.2611 | 9.0274 | 8.5905 | 8.0095 | 7.3116 | 7.1853 | 7.0653 | 5.7337 | 4.02 | 3.5105 | 7.5621 | 7.3211 | 7.0779 | 6.8326 | 6.5811 | 6.0968 | 5.4442 | 4.6505 | 4.5274 | 4.4126 | 2.9653 | 1.0558 | 0.52 | 7.8484 | 7.6063 | 7.3642 | 7.1179 | 6.8663 | 6.3811 | 5.7253 | 4.9295 | 4.8021 | 4.6832 | 3.2084 | 1.2705 | 0.72211
|  | WATLINGTON | HE |  |  |  | 10.1779 | 10.0684 | 9.9537 | 9.8295 | 9.6958 | 9.5463 | 9.4 | 9.2579 | 9.1242 | 9.0032 | 8.5221 | 7.6095 | -27.5632 | 7.82 | 7.7032 | 7.58 | 7.4484 | 7.3053 | 7.1505 | 6.9968 | 6.8484 | 6.7084 | 6.5811 | 6.0811 | 5.0495 | 4.1063 | 8.1053 | 7.9895 | 7.8663 | 7.7337 | 7.5916 | 7.4337 | 7.2779 | 7.1274 | 6.9853 | 6.8558 | 6.3411 | 5.2968 | 4.3432
|  | WATLINGTON | CF |  |  |  | 9.6863 | 10.1832 | 10.1158 | 10.0463 | 9.9747 | 9.8958 | 9.8126 | 9.7316 | 9.6495 | 9.5674 | 9.1947 | 8.8063 | 8.1947 | 7.7126 | 7.8263 | 7.7526 | 7.6779 | 7.6 | 7.5168 | 7.4284 | 7.3421 | 7.2537 | 7.1663 | 6.7684 | 6.3368 | 5.6411 | 8.0905 | 8.1116 | 8.0379 | 7.9642 | 7.8863 | 7.8011 | 7.7116 | 7.6242 | 7.5358 | 7.4463 | 7.0442 | 6.6063 | 5.9032
AMERSHAM | LOUDWATER BSP | WELL END | MINIMUM HEADROOM | SU 88511 87957 | YES | 1.2726 | 23.9053 | 23.6442 | 23.2189 | 22.7768 | 22.3379 | 21.9168 | 21.4979 | 21.1147 | 20.7716 | 20.4884 | 19.2779 | 18.3032 | -3.9221 | 22.6737 | 22.4126 | 21.5189 | 20.6074 | 19.7347 | 18.9537 | 18.18 | 17.4421 | 16.7968 | 16.3221 | 14.1453 | 12.2263 | 10.5042 | 23.8168 | 23.5558 | 22.6968 | 21.8221 | 20.9695 | 20.18 | 19.3979 | 18.6516 | 17.9989 | 17.52 | 15.3211 | 13.3789 | 11.6358
|  | WELL END | EE |  |  |  | 24.0116 | 23.8084 | 23.4926 | 23.1158 | 22.7421 | 22.3832 | 22.0379 | 21.7042 | 21.3989 | 21.1558 | 20.2042 | 19.4884 | 18.9084 | 22.78 | 22.5768 | 21.9663 | 21.1589 | 20.3853 | 19.6989 | 19.0326 | 18.3779 | 17.8063 | 17.4074 | 15.6884 | 14.2253 | 12.9242 | 23.9232 | 23.72 | 23.1326 | 22.3579 | 21.6137 | 20.9316 | 20.2579 | 19.5958 | 19.0168 | 18.6147 | 16.8779 | 15.3968 | 14.08
|  | WELL END | HT |  |  |  | 23.9053 | 23.6442 | 23.2189 | 22.7768 | 22.3379 | 21.9168 | 21.4979 | 21.1147 | 20.7716 | 20.4884 | 19.2779 | 18.3032 | 17.4821 | 22.6737 | 22.4126 | 21.5189 | 20.6074 | 19.7347 | 18.9537 | 18.18 | 17.4421 | 16.7968 | 16.3221 | 14.1453 | 12.2263 | 10.5042 | 23.8168 | 23.5558 | 22.6968 | 21.8221 | 20.9695 | 20.18 | 19.3979 | 18.6516 | 17.9989 | 17.52 | 15.3211 | 13.3789 | 11.6358
|  | WELL END | HE |  |  |  | 24.1516 | 24.0158 | 23.8463 | 23.5505 | 23.2537 | 22.9663 | 22.6905 | 22.4232 | 22.1937 | 22.0211 | 21.3779 | 20.9295 | -3.9221 | 22.92 | 22.7842 | 22.5568 | 21.8821 | 21.2379 | 20.6674 | 20.1158 | 19.5716 | 19.1358 | 18.8632 | 17.6968 | 16.7158 | 15.8695 | 24.0632 | 23.9274 | 23.7032 | 23.0579 | 22.4411 | 21.8916 | 21.3505 | 20.8 | 20.36 | 20.0842 | 18.9053 | 17.9126 | 17.0547
|  | WELL END | CF |  |  |  | 24.5084 | 24.1558 | 24.0779 | 23.9968 | 23.9126 | 23.7842 | 23.62 | 23.4705 | 23.3442 | 23.2316 | 22.7158 | 22.3905 | 22.1579 | 23.9505 | 22.9242 | 22.8463 | 22.7653 | 22.6811 | 22.4337 | 22.0484 | 21.7168 | 21.4726 | 21.2874 | 20.3905 | 19.6758 | 19.0695 | 24.5337 | 24.0674 | 23.9895 | 23.9084 | 23.8242 | 23.5853 | 23.2168 | 22.8989 | 22.6642 | 22.4842 | 21.6168 | 20.9074 | 20.2926
WILLESDEN GSP | ACTON LANE | WESLEY AVENUE | MINIMUM HEADROOM | TQ 20927 83082 | NO | 0 | 61.0453 | 61.0389 | 61.0021 | 60.8863 | 60.7411 | 60.5768 | 60.4747 | 60.3653 | 60.2432 | 60.2158 | 60.0411 | 59.8116 | 53.1063 | 60.8095 | 60.7989 | 60.7684 | 60.6432 | 60.4842 | 60.3063 | 60.1947 | 60.0747 | 59.9421 | 59.9126 | 59.7242 | 59.4705 | 59.2105 | 60.9337 | 60.9274 | 60.9221 | 60.9158 | 60.8168 | 60.6263 | 60.5063 | 60.3789 | 60.2368 | 60.2053 | 60.0042 | 59.7379 | 59.4768
|  | WESLEY AVENUE | EE |  |  |  | 61.0474 | 61.0432 | 61.0379 | 60.9737 | 60.8579 | 60.7189 | 60.6316 | 60.5411 | 60.4442 | 60.4074 | 60.2284 | 60.0526 | 59.8832 | 60.8126 | 60.8063 | 60.7968 | 60.7379 | 60.6116 | 60.46 | 60.3653 | 60.2674 | 60.1611 | 60.1211 | 59.9274 | 59.7368 | 59.5526 | 60.9358 | 60.9316 | 60.9263 | 60.9211 | 60.9158 | 60.7905 | 60.6895 | 60.5842 | 60.4716 | 60.4284 | 60.2211 | 60.0179 | 59.8211
|  | WESLEY AVENUE | HT |  |  |  | 61.0453 | 61.0389 | 61.0021 | 60.8863 | 60.7411 | 60.5768 | 60.4747 | 60.3653 | 60.2432 | 60.2158 | 60.0411 | 59.8116 | 59.5863 | 60.8095 | 60.7989 | 60.7684 | 60.6432 | 60.4842 | 60.3063 | 60.1947 | 60.0747 | 59.9421 | 59.9126 | 59.7242 | 59.4705 | 59.2105 | 60.9337 | 60.9274 | 60.9221 | 60.9158 | 60.8168 | 60.6263 | 60.5063 | 60.3789 | 60.2368 | 60.2053 | 60.0042 | 59.7379 | 59.4768
|  | WESLEY AVENUE | HE |  |  |  | 61.0495 | 61.0463 | 61.0421 | 61.0368 | 60.9579 | 60.8337 | 60.7621 | 60.6874 | 60.6053 | 60.5832 | 60.48 | 60.3832 | 53.1063 | 60.8147 | 60.8105 | 60.8042 | 60.7947 | 60.72 | 60.5853 | 60.5074 | 60.4263 | 60.3368 | 60.3137 | 60.2021 | 60.0958 | 59.9947 | 60.9379 | 60.9347 | 60.9305 | 60.9253 | 60.9211 | 60.9158 | 60.8421 | 60.7547 | 60.66 | 60.6347 | 60.5147 | 60.4021 | 60.2937
|  | WESLEY AVENUE | CF |  |  |  | 61.0505 | 61.0484 | 61.0463 | 61.0432 | 61.04 | 61.0379 | 61.0347 | 61.0168 | 60.9653 | 60.9074 | 60.74 | 60.6621 | 60.5905 | 60.8158 | 60.8137 | 60.8116 | 60.8074 | 60.8032 | 60.7989 | 60.7937 | 60.7853 | 60.7284 | 60.6653 | 60.4842 | 60.4 | 60.3221 | 60.9389 | 60.9368 | 60.9347 | 60.9316 | 60.9284 | 60.9263 | 60.9232 | 60.92 | 60.9179 | 60.9147 | 60.8168 | 60.7274 | 60.6432
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | WEST END | MINIMUM HEADROOM | SU 57216 06147 | YES | 0.23579 | 33.3347 | 33.0474 | 32.7589 | 32.4505 | 32.1316 | 31.8021 | 31.4695 | 30.4737 | 29.4316 | 28.52 | 25.1253 | 22.7821 | 3.3947 | 30.4158 | 29.8611 | 29.3168 | 28.7653 | 28.2105 | 27.66 | 26.2589 | 24.9042 | 23.7526 | 22.7453 | 18.9379 | 16.3074 | 13.8558 | 31.3084 | 30.7663 | 30.2337 | 29.6916 | 29.1474 | 28.6074 | 27.2411 | 25.8926 | 24.7316 | 23.7 | 19.8747 | 17.2453 | 14.7958
|  | WEST END | EE |  |  |  | 33.4484 | 33.2263 | 32.9905 | 32.74 | 32.4779 | 32.2042 | 31.9411 | 31.6884 | 30.7337 | 29.8032 | 26.7284 | 24.9105 | 23.2642 | 30.6621 | 30.2379 | 29.8042 | 29.3642 | 28.9189 | 28.4695 | 27.5211 | 26.4705 | 25.1653 | 24.1316 | 20.6937 | 18.6474 | 16.7737 | 31.5495 | 31.1347 | 30.7095 | 30.2779 | 29.84 | 29.3968 | 28.4789 | 27.4526 | 26.1526 | 25.1116 | 21.6263 | 19.58 | 17.7084
|  | WEST END | HT |  |  |  | 33.3347 | 33.0474 | 32.7589 | 32.4505 | 32.1316 | 31.8021 | 31.4695 | 30.4737 | 29.4316 | 28.52 | 25.1253 | 22.7821 | 20.6158 | 30.4158 | 29.8611 | 29.3168 | 28.7653 | 28.2105 | 27.66 | 26.2589 | 24.9042 | 23.7526 | 22.7453 | 18.9379 | 16.3074 | 13.8558 | 31.3084 | 30.7663 | 30.2337 | 29.6916 | 29.1474 | 28.6074 | 27.2411 | 25.8926 | 24.7316 | 23.7 | 19.8747 | 17.2453 | 14.7958
|  | WEST END | HE |  |  |  | 33.5937 | 33.44 | 33.2695 | 33.08 | 32.8779 | 32.66 | 32.4526 | 32.2568 | 31.9368 | 31.1705 | 28.6726 | 27.38 | 3.3947 | 30.8968 | 30.7137 | 30.4274 | 30.1253 | 29.8126 | 29.4863 | 28.6442 | 27.66 | 26.4768 | 25.5968 | 22.8158 | 21.3463 | 20.02 | 31.78 | 31.5979 | 31.3168 | 31.02 | 30.7126 | 30.3905 | 29.5758 | 28.6263 | 27.4621 | 26.5842 | 23.7505 | 22.2811 | 20.9558
|  | WEST END | CF |  |  |  | 33.6779 | 33.5863 | 33.4926 | 33.3958 | 33.2958 | 33.1916 | 33.0832 | 32.9789 | 32.8758 | 32.7726 | 31.6453 | 30.7305 | 29.9558 | 30.9811 | 30.8895 | 30.7905 | 30.6126 | 30.4316 | 30.2453 | 30.0547 | 29.8189 | 29.5042 | 29.1432 | 26.0821 | 25.0705 | 24.2021 | 31.8642 | 31.7726 | 31.6747 | 31.5 | 31.3221 | 31.14 | 30.9526 | 30.7221 | 30.4168 | 30.0663 | 27.0705 | 26.0547 | 25.1621
MELKSHAM GSP | WEST GRAFTON | WEST GRAFTON VILLAGE | MINIMUM HEADROOM | SU 24639 60279 | YES | 0.29368 | 6.9505 | 6.7684 | 6.5874 | 6.4042 | 6.2179 | 6.0105 | 5.8011 | 5.6137 | 5.4337 | 5.1979 | 4.0684 | 2.9821 | -1.1726 | 7.3379 | 7.1379 | 6.9421 | 6.7411 | 6.5411 | 6.3211 | 6.1 | 5.9042 | 5.7147 | 5.4568 | 4.2253 | 3.04 | 1.9737 | 7.3979 | 7.1947 | 6.9947 | 6.7916 | 6.5895 | 6.3621 | 6.1347 | 5.9305 | 5.7326 | 5.4642 | 4.1695 | 2.9147 | 1.8126
|  | WEST GRAFTON VILLAGE | EE |  |  |  | 7.0316 | 6.8905 | 6.7453 | 6.5958 | 6.4453 | 6.2747 | 6.1021 | 5.9316 | 5.7579 | 5.5526 | 4.5642 | 3.5926 | 2.8274 | 7.4274 | 7.2737 | 7.1158 | 6.9537 | 6.7916 | 6.6137 | 6.4358 | 6.2589 | 6.08 | 5.8611 | 4.8147 | 3.7853 | 2.9158 | 7.4895 | 7.3337 | 7.1716 | 7.0084 | 6.8432 | 6.6589 | 6.4716 | 6.2874 | 6.0989 | 5.8674 | 4.7484 | 3.6379 | 2.7274
|  | WEST GRAFTON VILLAGE | HT |  |  |  | 6.9505 | 6.7684 | 6.5874 | 6.4042 | 6.2179 | 6.0105 | 5.8011 | 5.6137 | 5.4337 | 5.1979 | 4.0684 | 2.9821 | 2.0526 | 7.3379 | 7.1379 | 6.9421 | 6.7411 | 6.5411 | 6.3211 | 6.1 | 5.9042 | 5.7147 | 5.4568 | 4.2253 | 3.04 | 1.9737 | 7.3979 | 7.1947 | 6.9947 | 6.7916 | 6.5895 | 6.3621 | 6.1347 | 5.9305 | 5.7326 | 5.4642 | 4.1695 | 2.9147 | 1.8126
|  | WEST GRAFTON VILLAGE | HE |  |  |  | 7.1411 | 7.0547 | 6.9611 | 6.8621 | 6.76 | 6.6379 | 6.5211 | 6.4084 | 6.3021 | 6.1568 | 5.5168 | 4.9389 | -1.1726 | 7.5484 | 7.4558 | 7.3537 | 7.2484 | 7.1389 | 7.0116 | 6.8905 | 6.7747 | 6.6653 | 6.5063 | 5.8063 | 5.1558 | 4.4747 | 7.6126 | 7.5179 | 7.4147 | 7.3074 | 7.1968 | 7.0653 | 6.94 | 6.82 | 6.7053 | 6.5411 | 5.8042 | 5.12 | 4.4063
|  | WEST GRAFTON VILLAGE | CF |  |  |  | 7.2 | 7.1495 | 7.0968 | 7.0432 | 6.9874 | 6.9168 | 6.8421 | 6.7737 | 6.7116 | 6.6453 | 6.2716 | 5.9432 | 5.5705 | 7.5916 | 7.5579 | 7.5011 | 7.4421 | 7.3811 | 7.3042 | 7.2242 | 7.1516 | 7.0842 | 7.0116 | 6.6021 | 6.2358 | 5.8095 | 7.6779 | 7.6211 | 7.5632 | 7.5042 | 7.4421 | 7.3621 | 7.28 | 7.2042 | 7.1347 | 7.06 | 6.6358 | 6.2505 | 5.8021
AXMINSTER | YEOVIL BSP | WEST HENDFORD | MINIMUM HEADROOM | ST 55000 15442 | YES | 12.7158 | 67.9747 | 54.8368 | 54.3284 | 53.8095 | 53.1105 | 52.2789 | 51.4547 | 50.6495 | 49.8632 | 49.0947 | 47.6832 | 46.5253 | 18.7095 | 61.6747 | 48.4916 | 47.9211 | 47.3432 | 46.5526 | 45.6084 | 44.6737 | 43.7568 | 42.8589 | 41.9811 | 40.4947 | 39.2105 | 37.8379 | 63.1242 | 49.94 | 49.3705 | 48.7916 | 48.0021 | 47.0568 | 46.1211 | 45.2042 | 44.3063 | 43.4274 | 41.8684 | 40.5832 | 39.2126
|  | WEST HENDFORD | EE |  |  |  | 68.1021 | 55.0295 | 54.5768 | 54.1158 | 53.4726 | 52.6926 | 51.9253 | 51.1663 | 50.4105 | 49.6779 | 48.5632 | 47.6926 | 46.7463 | 61.8126 | 48.7 | 48.1916 | 47.6747 | 46.9453 | 46.0568 | 45.1832 | 44.3147 | 43.4537 | 42.6158 | 41.3884 | 40.4947 | 39.4232 | 63.2621 | 50.1495 | 49.6411 | 49.1242 | 48.3947 | 47.5053 | 46.6305 | 45.7632 | 44.9 | 44.0611 | 42.8316 | 41.8642 | 40.7926
|  | WEST HENDFORD | HT |  |  |  | 67.9747 | 54.8368 | 54.3284 | 53.8095 | 53.1105 | 52.2789 | 51.4547 | 50.6495 | 49.8632 | 49.0947 | 47.6832 | 46.5253 | 45.3074 | 61.6747 | 48.4916 | 47.9211 | 47.3432 | 46.5526 | 45.6084 | 44.6737 | 43.7568 | 42.8589 | 41.9811 | 40.4947 | 39.2105 | 37.8379 | 63.1242 | 49.94 | 49.3705 | 48.7916 | 48.0021 | 47.0568 | 46.1211 | 45.2042 | 44.3063 | 43.4274 | 41.8684 | 40.5832 | 39.2126
|  | WEST HENDFORD | HE |  |  |  | 68.2695 | 55.2779 | 54.9011 | 54.5116 | 53.9379 | 53.2232 | 52.5221 | 51.8232 | 51.1337 | 50.4663 | 49.6705 | 49.1032 | 18.7095 | 61.9958 | 48.9705 | 48.5453 | 48.1074 | 47.4537 | 46.6358 | 45.8326 | 45.0326 | 44.2421 | 43.4737 | 42.5937 | 41.9589 | 41.2726 | 63.4453 | 50.42 | 49.9947 | 49.5568 | 48.9021 | 48.0842 | 47.2811 | 46.48 | 45.6895 | 44.9211 | 44.0389 | 43.4042 | 42.6453
|  | WEST HENDFORD | CF |  |  |  | 68.4411 | 55.6263 | 55.4684 | 55.3232 | 55.1137 | 54.8116 | 54.4242 | 53.9568 | 53.4684 | 52.9474 | 52.1147 | 51.7137 | 51.2737 | 62.1895 | 49.3663 | 49.1895 | 49.0295 | 48.7926 | 48.4495 | 48.0042 | 47.4663 | 46.9021 | 46.3011 | 45.3695 | 44.9221 | 44.4189 | 63.6389 | 50.8158 | 50.6389 | 50.4789 | 50.2411 | 49.8979 | 49.4526 | 48.9147 | 48.3516 | 47.7495 | 46.8179 | 46.3695 | 45.8653
MANNINGTON GSP | SHAFTESBURY BSP | WEST STOUR | MINIMUM HEADROOM | ST 77699 22040 | YES | 0.17579 | 8.6126 | 8.3632 | 8.1768 | 7.9895 | 7.4832 | 7.1063 | 6.9074 | 6.3326 | 6.2221 | 3.6779 | 2.4863 | 0.94211 | -0.90842 | 7.1926 | 6.9168 | 6.7168 | 6.5158 | 5.94 | 5.5211 | 5.3147 | 4.6611 | 4.5537 | 1.5737 | 0.28 | -1.44 | -1.9126 | 7.3779 | 7.1147 | 6.9221 | 6.7263 | 6.1842 | 5.7832 | 5.5779 | 4.9611 | 4.8484 | 1.88 | 0.55579 | -1.1979 | -1.6842
|  | WEST STOUR | EE |  |  |  | 8.6968 | 8.4916 | 8.3432 | 8.1916 | 7.7242 | 7.3811 | 7.2168 | 7.0579 | 6.9032 | 6.7558 | 5.4642 | 3.9158 | 2.9916 | 7.2842 | 7.0568 | 6.8979 | 6.7368 | 6.2032 | 5.8211 | 5.6516 | 5.4874 | 5.3295 | 5.18 | 3.7726 | 2.0589 | 1.0137 | 7.4663 | 7.2495 | 7.0947 | 6.9379 | 6.4358 | 6.0716 | 5.9 | 5.7347 | 5.5758 | 5.4232 | 4.0284 | 2.2653 | 1.2053
|  | WEST STOUR | HT |  |  |  | 8.6126 | 8.3632 | 8.1768 | 7.9895 | 7.4832 | 7.1063 | 6.9074 | 6.3326 | 6.2221 | 3.6779 | 2.4863 | 0.94211 | 0.49474 | 7.1926 | 6.9168 | 6.7168 | 6.5158 | 5.94 | 5.5211 | 5.3147 | 4.6611 | 4.5537 | 1.5737 | 0.28 | -1.44 | -1.9126 | 7.3779 | 7.1147 | 6.9221 | 6.7263 | 6.1842 | 5.7832 | 5.5779 | 4.9611 | 4.8484 | 1.88 | 0.55579 | -1.1979 | -1.6842
|  | WEST STOUR | HE |  |  |  | 8.8116 | 8.6611 | 8.5674 | 8.4695 | 8.0495 | 7.7537 | 7.6411 | 7.5358 | 7.4337 | 7.3421 | 6.3558 | 5.2547 | -0.90842 | 7.4095 | 7.2411 | 7.1411 | 7.0358 | 6.5537 | 6.2221 | 6.1063 | 5.9968 | 5.8926 | 5.7979 | 4.6947 | 3.4379 | 2.5895 | 7.5863 | 7.4263 | 7.3295 | 7.2274 | 6.7747 | 6.46 | 6.3442 | 6.2337 | 6.1305 | 6.0358 | 4.9758 | 3.7189 | 2.8579
|  | WEST STOUR | CF |  |  |  | 8.8884 | 8.8053 | 8.7526 | 8.6989 | 8.5137 | 8.3811 | 8.3189 | 8.2589 | 8.1979 | 8.1379 | 7.8663 | 7.6284 | 7.12 | 7.4937 | 7.4 | 7.3432 | 7.2853 | 7.0726 | 6.9232 | 6.8589 | 6.7947 | 6.7305 | 6.6674 | 6.38 | 6.1253 | 5.5474 | 7.6663 | 7.5789 | 7.5242 | 7.4674 | 7.2684 | 7.1263 | 7.0621 | 6.9989 | 6.9358 | 6.8737 | 6.5905 | 6.3389 | 5.7884
MANNINGTON GSP | BOURNEMOUTH | WESTBOURNE | MINIMUM HEADROOM | SZ 07642 91485 | YES | 0 | 35.7505 | 35.5179 | 35.2821 | 35.0326 | 34.7663 | 34.0916 | 33.3432 | 32.5979 | 32.08 | 31.5779 | 29.2347 | 26.9874 | 3.5863 | 31.0547 | 30.5853 | 29.7642 | 29.1126 | 28.4095 | 27.6516 | 26.84 | 26.0263 | 25.4705 | 24.9274 | 22.3705 | 19.8653 | 17.4411 | 31.7316 | 31.4084 | 30.6137 | 29.9526 | 29.2358 | 28.4621 | 27.6337 | 26.8021 | 26.2358 | 25.6842 | 23.0968 | 20.5905 | 18.1632
|  | WESTBOURNE | EE |  |  |  | 35.8537 | 35.6779 | 35.4926 | 35.2958 | 35.0832 | 34.6853 | 34.04 | 33.4042 | 33.0305 | 32.6179 | 30.7905 | 29.0537 | 27.4189 | 31.1632 | 30.9695 | 30.3084 | 29.6505 | 28.9716 | 28.2758 | 27.5737 | 26.88 | 26.4821 | 26.04 | 24.0642 | 22.1305 | 20.2853 | 31.8347 | 31.6537 | 31.1432 | 30.4989 | 29.8053 | 29.0947 | 28.3758 | 27.6674 | 27.2653 | 26.8137 | 24.7968 | 22.8526 | 21.0074
|  | WESTBOURNE | HT |  |  |  | 35.7505 | 35.5179 | 35.2821 | 35.0326 | 34.7663 | 34.0916 | 33.3432 | 32.5979 | 32.08 | 31.5779 | 29.2347 | 26.9874 | 24.8295 | 31.0547 | 30.5853 | 29.7642 | 29.1126 | 28.4095 | 27.6516 | 26.84 | 26.0263 | 25.4705 | 24.9274 | 22.3705 | 19.8653 | 17.4411 | 31.7316 | 31.4084 | 30.6137 | 29.9526 | 29.2358 | 28.4621 | 27.6337 | 26.8021 | 26.2358 | 25.6842 | 23.0968 | 20.5905 | 18.1632
|  | WESTBOURNE | HE |  |  |  | 35.9284 | 35.7842 | 35.6242 | 35.4484 | 35.2579 | 35.0547 | 34.7242 | 34.18 | 33.8895 | 33.5737 | 32.2589 | 31.0505 | 3.5863 | 31.2463 | 31.0874 | 30.7 | 30.1305 | 29.5421 | 28.9389 | 28.32 | 27.7263 | 27.4189 | 27.08 | 25.6568 | 24.3274 | 23.0863 | 31.9095 | 31.7653 | 31.5232 | 30.9705 | 30.3874 | 29.7726 | 29.14 | 28.5326 | 28.2211 | 27.8758 | 26.4232 | 25.0621 | 23.8126
|  | WESTBOURNE | CF |  |  |  | 35.9684 | 35.8653 | 35.7579 | 35.6463 | 35.5316 | 35.4126 | 35.2905 | 35.1705 | 35.0526 | 34.9347 | 34.1747 | 33.2853 | 32.5179 | 31.2884 | 31.18 | 31.0632 | 30.9421 | 30.7337 | 30.3947 | 30.0137 | 29.5884 | 29.2842 | 28.9979 | 27.7579 | 26.7821 | 25.9305 | 31.9495 | 31.8463 | 31.7389 | 31.6263 | 31.5 | 31.2221 | 30.8526 | 30.4389 | 30.1284 | 29.8368 | 28.5737 | 27.5768 | 26.7021
MELKSHAM GSP | FROME BSP | WESTBURY | MINIMUM HEADROOM | ST 87654 51530 | YES | 0.081053 | 33.68 | 32.9758 | 32.4389 | 31.3442 | 30.24 | 29.6979 | 28.5979 | 27.8084 | 27.2516 | 26.7516 | 23.6411 | 20.4011 | -1.6526 | 29.4589 | 28.6811 | 27.8926 | 26.6674 | 25.4316 | 24.9589 | 23.74 | 22.88 | 22.2905 | 21.6579 | 18.2863 | 14.8 | 11.3979 | 29.8168 | 29.0495 | 28.2611 | 27.0368 | 25.8042 | 25.1968 | 23.9726 | 23.1084 | 22.5126 | 21.8726 | 18.4568 | 14.92 | 11.5
|  | WESTBURY | EE |  |  |  | 33.9505 | 33.3874 | 33.0232 | 32.2589 | 31.3895 | 30.3811 | 29.3347 | 28.3368 | 27.6158 | 27.1453 | 29.2779 | 26.7011 | 24.3253 | 29.7579 | 29.1358 | 28.5347 | 27.6884 | 26.7211 | 25.5968 | 24.4316 | 23.32 | 22.5347 | 22.0432 | 26.4674 | 23.6726 | 21.0011 | 29.8168 | 29.5042 | 28.9021 | 28.0568 | 27.0895 | 25.9621 | 24.7905 | 23.6726 | 22.8789 | 22.3768 | 27.1789 | 24.3147 | 21.6211
|  | WESTBURY | HT |  |  |  | 33.68 | 32.9758 | 32.4389 | 31.3442 | 30.24 | 29.6979 | 28.5979 | 27.8084 | 27.2516 | 26.7516 | 23.6411 | 20.4011 | 17.3863 | 29.4589 | 28.6811 | 27.8926 | 26.6674 | 25.4316 | 24.9589 | 23.74 | 22.88 | 22.2905 | 21.6579 | 18.2863 | 14.8 | 11.3979 | 29.8274 | 29.0495 | 28.2611 | 27.0368 | 25.8042 | 25.1968 | 23.9726 | 23.1084 | 22.5126 | 21.8726 | 18.4568 | 14.92 | 11.5
|  | WESTBURY | HE |  |  |  | 34.3263 | 33.94 | 33.5663 | 33.1463 | 32.4263 | 31.5526 | 30.6589 | 29.8063 | 29.3011 | 29.0032 | 28.0537 | 26.1611 | -1.6526 | 30.1737 | 29.7463 | 29.3368 | 28.6547 | 27.8484 | 26.8705 | 25.8642 | 24.9063 | 24.3547 | 24.0442 | 23.1684 | 21.0326 | 19.1968 | 30.2158 | 30.1137 | 29.7053 | 29.0232 | 28.2179 | 27.2368 | 26.2295 | 25.2674 | 24.7137 | 24.3979 | 23.3663 | 21.2116 | 19.3579
|  | WESTBURY | CF |  |  |  | 34.5442 | 34.3189 | 34.1284 | 33.9337 | 33.9305 | 33.6958 | 33.4484 | 33.1484 | 32.7274 | 32.2821 | 30.3211 | 29.9558 | 28.8116 | 30.4137 | 30.1642 | 29.9558 | 29.7442 | 29.5295 | 29.2758 | 29.0084 | 28.68 | 28.2063 | 27.7042 | 25.4968 | 25.2179 | 23.9137 | 30.4463 | 30.2074 | 30.3232 | 30.1116 | 29.8968 | 29.6421 | 29.3726 | 29.0421 | 28.5684 | 28.0653 | 25.8526 | 25.4316 | 24.1168
NURSLING GSP | SOUTHAMPTON (2 X 90) | WESTERN ESPLANADE | MINIMUM HEADROOM | SU 41618 12009 | YES | 0.40316 | 69.5789 | 69.3926 | 69.2063 | 68.3484 | 67.3242 | 65.1389 | 63.1695 | 61.5063 | 59.8568 | 58.9032 | 56.9821 | 55.2568 | 14.1179 | 60.6347 | 60.4484 | 59.64 | 58.3958 | 57.2421 | 54.7421 | 52.4947 | 50.5979 | 48.6905 | 47.5958 | 45.4947 | 43.56 | 41.7389 | 63.0474 | 62.8611 | 62.0642 | 60.84 | 59.7042 | 57.2505 | 55.0421 | 53.1789 | 51.2642 | 50.1705 | 48.0811 | 46.1495 | 44.3305
|  | WESTERN ESPLANADE | EE |  |  |  | 69.6558 | 69.5137 | 69.3632 | 68.7326 | 67.7937 | 66.6926 | 65.5884 | 63.4811 | 61.5979 | 60.7558 | 58.1747 | 56.8579 | 55.6453 | 60.7116 | 60.5695 | 59.9621 | 58.8105 | 57.7484 | 56.5 | 55.2474 | 52.8316 | 50.6737 | 49.7147 | 46.7968 | 45.3263 | 43.9526 | 63.1242 | 62.9821 | 62.3832 | 61.2505 | 60.2063 | 58.9789 | 57.7474 | 55.3758 | 53.2526 | 52.2874 | 49.3789 | 47.9137 | 46.5411
|  | WESTERN ESPLANADE | HT |  |  |  | 69.5789 | 69.3926 | 69.2063 | 68.3484 | 67.3242 | 65.1389 | 63.1695 | 61.5063 | 59.8568 | 58.9032 | 56.9821 | 55.2568 | 53.6421 | 60.6347 | 60.4484 | 59.64 | 58.3958 | 57.2421 | 54.7421 | 52.4947 | 50.5979 | 48.6905 | 47.5958 | 45.4947 | 43.56 | 41.7389 | 63.0474 | 62.8611 | 62.0642 | 60.84 | 59.7042 | 57.2505 | 55.0421 | 53.1789 | 51.2642 | 50.1705 | 48.0811 | 46.1495 | 44.3305
|  | WESTERN ESPLANADE | HE |  |  |  | 69.7211 | 69.6074 | 69.4811 | 69.1084 | 68.2358 | 67.1958 | 66.1547 | 64.4989 | 62.8432 | 62.3442 | 59.72 | 58.4863 | 14.1179 | 60.7768 | 60.6632 | 60.3032 | 59.2242 | 58.2347 | 57.0558 | 55.8726 | 53.9747 | 52.0758 | 51.5168 | 48.4832 | 47.0621 | 46.1484 | 63.1895 | 63.0758 | 62.7189 | 61.6589 | 60.6863 | 59.5274 | 58.3642 | 56.5 | 54.6368 | 54.0853 | 51.0516 | 49.6305 | 48.7179
|  | WESTERN ESPLANADE | CF |  |  |  | 69.7632 | 69.6863 | 69.6063 | 69.5232 | 69.4379 | 69.3495 | 69.2589 | 68.5663 | 67.4211 | 66.4316 | 64.6863 | 63.6568 | 63.1021 | 60.8189 | 60.7421 | 60.6621 | 60.5789 | 60.4937 | 60.4053 | 59.5526 | 58.6221 | 57.3074 | 56.1747 | 54.2137 | 53.0516 | 52.4263 | 63.2316 | 63.1547 | 63.0747 | 62.9916 | 62.9063 | 62.8179 | 61.9789 | 61.0663 | 59.7747 | 58.6621 | 56.7326 | 55.5895 | 54.9737
BOTLEY WOOD GSP | NETLEY COMMON BSP | WESTON | MINIMUM HEADROOM | SU 45207 09912 | YES | 0.084211 | 22.6379 | 22.3263 | 22.0126 | 21.4337 | 20.8032 | 20.2084 | 19.5853 | 19.0126 | 18.4505 | 17.8558 | 14.6632 | 11.9663 | -4.6568 | 19.6937 | 19.0937 | 18.4989 | 17.8316 | 17.1568 | 16.5274 | 15.8642 | 15.2547 | 14.6516 | 14.0095 | 10.4684 | 7.4558 | 4.6979 | 20.0295 | 19.4453 | 18.8653 | 18.1916 | 17.5116 | 16.8758 | 16.2074 | 15.5916 | 14.9832 | 14.3316 | 10.7811 | 7.7653 | 5.0084
|  | WESTON | EE |  |  |  | 22.7547 | 22.5105 | 22.2516 | 21.9758 | 21.5389 | 20.9832 | 20.3874 | 19.9053 | 19.4253 | 18.9695 | 16.5695 | 14.4474 | 12.5737 | 19.9579 | 19.4958 | 19.02 | 18.4884 | 17.9526 | 17.3579 | 16.7168 | 16.2053 | 15.6947 | 15.2084 | 12.5768 | 10.2021 | 8.0832 | 20.2853 | 19.8347 | 19.3716 | 18.8547 | 18.3147 | 17.7137 | 17.0663 | 16.5495 | 16.0337 | 15.54 | 12.8821 | 10.5032 | 8.3832
|  | WESTON | HT |  |  |  | 22.6379 | 22.3263 | 22.0126 | 21.4337 | 20.8032 | 20.2084 | 19.5853 | 19.0126 | 18.4505 | 17.8558 | 14.6632 | 11.9663 | 9.5168 | 19.6937 | 19.0937 | 18.4989 | 17.8316 | 17.1568 | 16.5274 | 15.8642 | 15.2547 | 14.6516 | 14.0095 | 10.4684 | 7.4558 | 4.6979 | 20.0295 | 19.4453 | 18.8653 | 18.1916 | 17.5116 | 16.8758 | 16.2074 | 15.5916 | 14.9832 | 14.3316 | 10.7811 | 7.7653 | 5.0084
|  | WESTON | HE |  |  |  | 22.9063 | 22.7305 | 22.5379 | 22.3242 | 22.0947 | 21.8474 | 21.5232 | 21.1695 | 20.8189 | 20.4926 | 18.8916 | 17.4379 | -4.6568 | 20.2832 | 20.0074 | 19.6895 | 19.3063 | 18.9147 | 18.4516 | 17.9463 | 17.5726 | 17.2011 | 16.8516 | 15.1042 | 13.48 | 12.0021 | 20.6232 | 20.3305 | 20.02 | 19.6463 | 19.2642 | 18.8116 | 18.3084 | 17.9326 | 17.5558 | 17.2042 | 15.4316 | 13.7905 | 12.3126
|  | WESTON | CF |  |  |  | 22.9968 | 22.8937 | 22.7863 | 22.6737 | 22.5589 | 22.4389 | 22.3158 | 22.1968 | 22.0768 | 21.9579 | 20.96 | 19.9821 | 19.1084 | 20.3779 | 20.2705 | 20.1137 | 19.9105 | 19.7042 | 19.4926 | 19.2611 | 19.0221 | 18.7832 | 18.5389 | 17.3274 | 16.2411 | 15.2579 | 20.7516 | 20.6253 | 20.4337 | 20.2358 | 20.0347 | 19.8284 | 19.6021 | 19.3695 | 19.1368 | 18.9 | 17.68 | 16.5789 | 15.5789
CHICKERELL GSP | CHICKERELL BSP | WEYMOUTH | MINIMUM HEADROOM | SY 67443 79096 | YES | 0.89579 | 37.0821 | 36.5421 | 35.9968 | 35.4189 | 33.5789 | 31.6 | 30.0832 | 28.8568 | 27.9442 | 27.1337 | 23.44 | 19.1747 | -23.3642 | 30.4674 | 29.3768 | 27.2484 | 25.0221 | 22.6263 | 20.4042 | 18.7305 | 17.3842 | 16.4011 | 15.5316 | 11.5326 | 6.7832 | 1.7811 | 31.4168 | 30.8337 | 28.7558 | 26.5284 | 24.1316 | 21.9084 | 20.2326 | 18.8853 | 17.9011 | 17.0295 | 13.0242 | 8.2632 | 3.2547
|  | WEYMOUTH | EE |  |  |  | 37.2874 | 36.8632 | 36.4158 | 35.9368 | 34.7989 | 32.9958 | 31.6779 | 30.5947 | 29.8032 | 29.1126 | 26.2116 | 23.0463 | 19.7011 | 30.6842 | 30.08 | 28.1642 | 26.1463 | 23.9526 | 21.9221 | 20.46 | 19.2716 | 18.4253 | 17.6874 | 14.56 | 11.0411 | 7.2453 | 31.6368 | 31.1758 | 29.6705 | 27.6526 | 25.4589 | 23.4263 | 21.9621 | 20.7726 | 19.9232 | 19.1853 | 16.0453 | 12.5105 | 8.7095
|  | WEYMOUTH | HT |  |  |  | 37.0821 | 36.5421 | 35.9968 | 35.4189 | 33.5789 | 31.6 | 30.0832 | 28.8568 | 27.9442 | 27.1337 | 23.44 | 19.1747 | 14.7505 | 30.4674 | 29.3768 | 27.2484 | 25.0221 | 22.6263 | 20.4042 | 18.7305 | 17.3842 | 16.4011 | 15.5316 | 11.5326 | 6.7832 | 1.7811 | 31.4168 | 30.8337 | 28.7558 | 26.5284 | 24.1316 | 21.9084 | 20.2326 | 18.8853 | 17.9011 | 17.0295 | 13.0242 | 8.2632 | 3.2547
|  | WEYMOUTH | HE |  |  |  | 37.5463 | 37.2421 | 36.9063 | 36.5358 | 36.1358 | 34.7358 | 33.6316 | 32.7632 | 32.1947 | 31.7274 | 29.9305 | 27.8379 | -23.3642 | 30.9589 | 30.6337 | 29.3295 | 27.5716 | 25.6274 | 23.8305 | 22.6 | 21.6463 | 21.0421 | 20.5463 | 18.6242 | 16.2747 | 13.5916 | 31.9168 | 31.5863 | 30.8368 | 29.0789 | 27.1337 | 25.3358 | 24.1053 | 23.1505 | 22.5453 | 22.0484 | 20.1211 | 17.7684 | 15.0811
|  | WEYMOUTH | CF |  |  |  | 37.6979 | 37.5147 | 37.3253 | 37.1274 | 36.9232 | 36.7116 | 36.4947 | 36.2811 | 36.0705 | 35.86 | 34.92 | 33.6253 | 32.1137 | 31.1189 | 30.9232 | 30.7042 | 29.9084 | 28.9916 | 28.1537 | 27.4979 | 26.9368 | 26.5284 | 26.1484 | 24.4021 | 22.7505 | 21.02 | 32.08 | 31.8811 | 31.6526 | 31.4084 | 30.4989 | 29.66 | 29.0042 | 28.4432 | 28.0337 | 27.6537 | 25.9053 | 24.2516 | 22.5179
COWLEY GSP | HEADINGTON BSP | WHEATLEY | MINIMUM HEADROOM | SP 60777 05379 | YES | 0 | 16.4979 | 41.0895 | 40.8747 | 40.5189 | 39.1726 | 37.6105 | 35.7284 | 34.1779 | 32.7832 | 31.7316 | 29.9947 | 28.6095 | -10.0821 | 15.2958 | 39.8905 | 39.6674 | 39.28 | 37.7284 | 35.9411 | 33.7758 | 32.0011 | 30.4074 | 29.2189 | 27.4305 | 26.0568 | 24.8537 | 16.3632 | 40.1042 | 39.88 | 39.4926 | 37.9432 | 36.1474 | 33.9747 | 32.1905 | 30.5863 | 29.3832 | 27.5 | 26.0158 | 24.7695
|  | WHEATLEY | EE |  |  |  | 16.5611 | 41.4358 | 41.3 | 40.8242 | 39.5326 | 38.0242 | 36.1832 | 34.66 | 33.2768 | 32.2453 | 30.5716 | 33.3484 | 32.4779 | 15.3716 | 40.2253 | 40.0674 | 39.6137 | 38.1211 | 36.3905 | 34.2747 | 32.5337 | 30.9621 | 29.8011 | 28.1347 | 33.6958 | 32.7884 | 16.4337 | 41.2958 | 41.1442 | 39.8253 | 38.3337 | 36.5947 | 34.4674 | 32.7137 | 31.1253 | 29.9453 | 28.1432 | 33.9432 | 32.9874
|  | WHEATLEY | HT |  |  |  | 16.4979 | 41.0895 | 40.8747 | 40.5189 | 39.1726 | 37.6105 | 35.7284 | 34.1779 | 32.7832 | 31.7316 | 29.9947 | 28.6095 | 27.4789 | 15.2958 | 39.8905 | 39.6674 | 39.28 | 37.7284 | 35.9411 | 33.7758 | 32.0011 | 30.4074 | 29.2189 | 27.4305 | 26.0568 | 24.8537 | 16.3632 | 40.1042 | 39.88 | 39.4926 | 37.9432 | 36.1474 | 33.9747 | 32.1905 | 30.5863 | 29.3832 | 27.5 | 26.0158 | 24.7695
|  | WHEATLEY | HE |  |  |  | 16.6484 | 41.5663 | 41.4737 | 41.3705 | 40.0316 | 38.5968 | 36.8526 | 35.4284 | 34.1495 | 33.2221 | 32.1526 | 31.5463 | -10.0821 | 15.4589 | 40.3768 | 40.28 | 40.1642 | 38.6589 | 37.0063 | 34.9853 | 33.34 | 31.8663 | 30.8063 | 29.6916 | 29.0789 | 28.4779 | 16.5211 | 41.4389 | 41.3442 | 41.2326 | 38.8747 | 37.2158 | 35.1916 | 33.5411 | 32.0621 | 30.9937 | 29.8232 | 29.1684 | 28.5274
|  | WHEATLEY | CF |  |  |  | 16.6989 | 41.6547 | 41.6074 | 41.3789 | 41.2495 | 40.6526 | 39.8547 | 39.1411 | 38.4463 | 37.9 | 37.18 | 36.7621 | 36.3737 | 15.5095 | 40.4653 | 40.4179 | 40.1926 | 40.0484 | 39.3621 | 38.4389 | 37.6158 | 36.8137 | 36.1853 | 35.4084 | 34.9779 | 34.5768 | 16.5716 | 41.5274 | 41.48 | 40.4063 | 40.2621 | 39.5726 | 38.6484 | 37.8221 | 37.0168 | 36.3874 | 35.5926 | 35.1379 | 34.7105
MELKSHAM GSP | ANDOVER BSP | WHITCHURCH | MINIMUM HEADROOM | SU 45924 48466 | YES | 0 | 4.7905 | 4.6284 | 4.4663 | 4.3021 | 4.1358 | 3.9684 | 3.7926 | 3.6358 | 3.4874 | 3.3474 | 2.7337 | 2.1326 | -17.0474 | 5.3032 | 5.1284 | 4.9537 | 4.7779 | 4.6 | 4.4221 | 4.2358 | 4.0684 | 3.9116 | 3.7611 | 3.1063 | 2.4558 | 1.7589 | 4.6758 | 4.5011 | 4.3263 | 4.1505 | 3.9726 | 3.7947 | 3.6063 | 3.4389 | 3.28 | 3.1295 | 2.4663 | 1.8084 | 1.1074
|  | WHITCHURCH | EE |  |  |  | 4.8611 | 4.7337 | 4.6053 | 4.4705 | 4.3358 | 4.1968 | 4.0621 | 3.9263 | 3.7958 | 3.6737 | 3.1653 | 2.7326 | 2.2505 | 5.3621 | 5.2432 | 5.1053 | 4.9611 | 4.8179 | 4.6716 | 4.5295 | 4.3863 | 4.2474 | 4.12 | 3.5821 | 3.1221 | 2.5821 | 4.7537 | 4.6158 | 4.4779 | 4.3337 | 4.1905 | 4.0421 | 3.9 | 3.7547 | 3.6158 | 3.4853 | 2.9379 | 2.4674 | 1.9242
|  | WHITCHURCH | HT |  |  |  | 4.7905 | 4.6284 | 4.4663 | 4.3021 | 4.1358 | 3.9684 | 3.7926 | 3.6358 | 3.4874 | 3.3474 | 2.7337 | 2.1326 | 1.5074 | 5.3032 | 5.1284 | 4.9537 | 4.7779 | 4.6 | 4.4221 | 4.2358 | 4.0684 | 3.9116 | 3.7611 | 3.1063 | 2.4558 | 1.7589 | 4.6758 | 4.5011 | 4.3263 | 4.1505 | 3.9726 | 3.7947 | 3.6063 | 3.4389 | 3.28 | 3.1295 | 2.4663 | 1.8084 | 1.1074
|  | WHITCHURCH | HE |  |  |  | 4.9579 | 4.8768 | 4.7916 | 4.7021 | 4.6074 | 4.5053 | 4.4105 | 4.3137 | 4.2221 | 4.1411 | 3.8284 | 3.6105 | -17.0474 | 5.4126 | 5.3621 | 5.3063 | 5.2137 | 5.1137 | 5.0074 | 4.9074 | 4.8063 | 4.7095 | 4.6232 | 4.2905 | 4.0579 | 3.7547 | 4.8579 | 4.7726 | 4.6811 | 4.5853 | 4.4863 | 4.3789 | 4.2789 | 4.1768 | 4.0789 | 3.9926 | 3.6568 | 3.4211 | 3.1137
|  | WHITCHURCH | CF |  |  |  | 5.0053 | 4.9526 | 4.9032 | 4.8516 | 4.7979 | 4.7421 | 4.6811 | 4.6263 | 4.5705 | 4.5158 | 4.2495 | 4.0674 | 3.9137 | 5.4411 | 5.4116 | 5.3811 | 5.3505 | 5.3126 | 5.2537 | 5.1895 | 5.1295 | 5.0705 | 5.0116 | 4.7253 | 4.5284 | 4.3568 | 4.9095 | 4.8526 | 4.7989 | 4.7432 | 4.6853 | 4.6263 | 4.5611 | 4.5021 | 4.4421 | 4.3832 | 4.0958 | 3.8958 | 3.7232
BOTLEY WOOD GSP | BOTLEY WOOD BSP | WHITELEY | MINIMUM HEADROOM | SU 52936 08794 | YES | 1.7568 | 34.0179 | 43.6779 | 43.5116 | 42.5547 | 41.3011 | 40.1305 | 39.2379 | 38.5842 | 38.0221 | 37.5084 | 35.7158 | 34.3021 | 1.3147 | 27.06 | 36.72 | 36.5537 | 35.4716 | 34.0474 | 32.7211 | 31.7147 | 30.9853 | 30.3589 | 29.7853 | 27.8021 | 26.2305 | 24.7821 | 28.1126 | 37.7726 | 37.6063 | 36.5084 | 35.0611 | 33.7147 | 32.6947 | 31.9537 | 31.3179 | 30.7358 | 28.7242 | 27.1389 | 25.6905
|  | WHITELEY | EE |  |  |  | 34.7653 | 43.7768 | 43.6411 | 42.8747 | 41.68 | 40.5695 | 39.7337 | 39.1358 | 38.6105 | 38.1432 | 36.6705 | 35.5568 | 34.5632 | 29.2832 | 36.8189 | 36.6832 | 35.8168 | 34.4558 | 33.1947 | 32.2484 | 31.5811 | 30.9937 | 30.4716 | 28.8432 | 27.6147 | 26.4905 | 30.3726 | 37.8716 | 37.7358 | 36.8568 | 35.4747 | 34.1926 | 33.2326 | 32.5537 | 31.9589 | 31.4284 | 29.7737 | 28.52 | 27.3926
|  | WHITELEY | HT |  |  |  | 34.0179 | 43.6779 | 43.5116 | 42.5547 | 41.3011 | 40.1305 | 39.2379 | 38.5842 | 38.0221 | 37.5084 | 35.7158 | 34.3021 | 33.0189 | 27.06 | 36.72 | 36.5537 | 35.4716 | 34.0474 | 32.7211 | 31.7147 | 30.9853 | 30.3589 | 29.7853 | 27.8021 | 26.2305 | 24.7821 | 28.1126 | 37.7726 | 37.6063 | 36.5084 | 35.0611 | 33.7147 | 32.6947 | 31.9537 | 31.3179 | 30.7358 | 28.7242 | 27.1389 | 25.6905
|  | WHITELEY | HE |  |  |  | 34.8526 | 43.9074 | 43.8116 | 43.2926 | 42.1737 | 41.1316 | 40.3653 | 39.8358 | 39.3758 | 38.9747 | 37.8116 | 37.0021 | 1.3147 | 29.4705 | 36.9495 | 36.8537 | 36.2684 | 34.9895 | 33.8011 | 32.9305 | 32.3337 | 31.8179 | 31.3674 | 30.0695 | 29.16 | 28.3442 | 30.5663 | 38.0021 | 37.9063 | 37.3126 | 36.0137 | 34.8053 | 33.9211 | 33.3158 | 32.7926 | 32.3347 | 31.0168 | 30.0937 | 29.2621
|  | WHITELEY | CF |  |  |  | 34.9021 | 44.6779 | 43.9442 | 43.8916 | 43.8358 | 43.7789 | 43.5874 | 43.3105 | 43.0505 | 42.7979 | 42.0389 | 41.4947 | 41.0042 | 29.7116 | 39.0958 | 36.9863 | 36.9337 | 36.8779 | 36.8211 | 36.6074 | 36.2968 | 36.0053 | 35.7211 | 34.8811 | 34.2705 | 33.7147 | 30.8358 | 40.1842 | 38.0389 | 37.9863 | 37.9305 | 37.8737 | 37.6568 | 37.3411 | 37.0453 | 36.7568 | 35.9063 | 35.2874 | 34.72
BRAMLEY (FLEE) | BURGHFIELD MAIN | WHITLEY WOOD | MINIMUM HEADROOM | SU 72812 69667 | YES | 0.21053 | 35.1295 | 34.8074 | 34.4821 | 34.4495 | 34.1537 | 33.3811 | 32.3674 | 31.5347 | 30.9358 | 30.3884 | 28.0274 | 25.8 | -0.29474 | 30.3263 | 29.9421 | 29.1474 | 28.1442 | 27.0347 | 25.8726 | 24.7453 | 23.8232 | 23.1705 | 22.5737 | 19.9884 | 17.5105 | 15.1484 | 31.52 | 31.1379 | 30.36 | 29.6474 | 28.5368 | 27.2358 | 26.1095 | 25.1874 | 24.5358 | 23.9389 | 21.3568 | 18.8821 | 16.5232
|  | WHITLEY WOOD | EE |  |  |  | 35.2537 | 35.0011 | 34.7337 | 34.4495 | 34.1537 | 33.8474 | 33.5547 | 32.7305 | 32.0947 | 31.6621 | 30 | 28.4158 | 26.9442 | 30.4747 | 30.1811 | 29.8189 | 29.0905 | 28.2284 | 27.1516 | 26.0695 | 25.0432 | 24.3316 | 23.86 | 22.0337 | 20.2674 | 18.6137 | 31.6674 | 31.3747 | 31.0158 | 30.3042 | 29.4621 | 28.4137 | 27.36 | 26.3611 | 25.6653 | 25.2021 | 23.4105 | 21.6884 | 20.0789
|  | WHITLEY WOOD | HT |  |  |  | 35.1295 | 34.8074 | 34.4821 | 35.5421 | 34.5432 | 33.3811 | 32.3674 | 31.5347 | 30.9358 | 30.3884 | 28.0274 | 25.8 | 23.6968 | 30.3263 | 29.9421 | 29.1474 | 28.1442 | 27.0347 | 25.8726 | 24.7453 | 23.8232 | 23.1705 | 22.5737 | 19.9884 | 17.5105 | 15.1484 | 31.52 | 31.1379 | 30.36 | 29.6474 | 28.5368 | 27.2358 | 26.1095 | 25.1874 | 24.5358 | 23.9389 | 21.3568 | 18.8821 | 16.5232
|  | WHITLEY WOOD | HE |  |  |  | 35.4253 | 35.2558 | 35.0674 | 34.86 | 34.6358 | 35.7463 | 34.9074 | 34.18 | 33.6442 | 33.3358 | 32.2389 | 31.2105 | -0.29474 | 30.6463 | 30.4768 | 30.2811 | 29.9811 | 29.2779 | 28.34 | 27.3937 | 26.5779 | 25.9842 | 25.6516 | 24.4653 | 23.3158 | 22.2389 | 31.8389 | 31.6695 | 31.4737 | 31.1779 | 30.4905 | 29.8421 | 28.8958 | 28.08 | 27.4863 | 27.1526 | 25.9674 | 24.8168 | 23.74
|  | WHITLEY WOOD | CF |  |  |  | 35.5263 | 35.4295 | 35.3316 | 35.2295 | 35.1221 | 35.0126 | 34.9 | 34.7895 | 34.6811 | 34.5726 | 34.0853 | 33.8453 | 33.42 | 30.7474 | 30.6505 | 30.5526 | 30.4505 | 30.3316 | 30.2021 | 29.9874 | 29.6453 | 29.2347 | 28.8232 | 27.0547 | 26.3611 | 25.7842 | 31.94 | 31.8432 | 31.7453 | 31.6432 | 31.5253 | 31.3958 | 31.1853 | 30.8505 | 30.4516 | 30.0505 | 28.3295 | 27.6526 | 27.0905
MINETY GSP | CIRENCESTER BSP | WHITEWAY | MINIMUM HEADROOM | SP 02076 03059 | YES | 0 | 34.9537 | 34.5642 | 34.1568 | 33.7074 | 33.2463 | 32.7632 | 32.2842 | 31.8274 | 31.3937 | 31.0305 | 28.8495 | 26.5558 | 10.9779 | 30.3926 | 29.9716 | 29.5305 | 29.0411 | 28.5411 | 28.0158 | 27.4947 | 26.9979 | 26.5221 | 26.1253 | 23.6937 | 21.0979 | 18.7074 | 31.2158 | 30.7947 | 30.3537 | 29.8642 | 29.3642 | 28.8389 | 28.3179 | 27.8189 | 27.3432 | 26.9474 | 24.5137 | 21.9158 | 19.5242
|  | WHITEWAY | EE |  |  |  | 35.1211 | 34.8253 | 34.5105 | 34.1632 | 33.8074 | 33.4379 | 33.0737 | 32.7179 | 32.3674 | 32.0905 | 30.3842 | 28.5474 | 26.8821 | 30.5758 | 30.2568 | 29.9179 | 29.5421 | 29.1579 | 28.7589 | 28.3674 | 27.9811 | 27.6 | 27.3032 | 25.4032 | 23.3189 | 21.4137 | 31.3989 | 31.08 | 30.7411 | 30.3653 | 29.9811 | 29.5821 | 29.1884 | 28.8032 | 28.4232 | 28.1242 | 26.2232 | 24.1358 | 22.2295
|  | WHITEWAY | HT |  |  |  | 34.9537 | 34.5642 | 34.1568 | 33.7074 | 33.2463 | 32.7632 | 32.2842 | 31.8274 | 31.3937 | 31.0305 | 28.8495 | 26.5558 | 24.4558 | 30.3926 | 29.9716 | 29.5305 | 29.0411 | 28.5411 | 28.0158 | 27.4947 | 26.9979 | 26.5221 | 26.1253 | 23.6937 | 21.0979 | 18.7074 | 31.2158 | 30.7947 | 30.3537 | 29.8642 | 29.3642 | 28.8389 | 28.3179 | 27.8189 | 27.3432 | 26.9474 | 24.5137 | 21.9158 | 19.5242
|  | WHITEWAY | HE |  |  |  | 35.3463 | 35.1568 | 34.9442 | 34.6937 | 34.4316 | 34.1474 | 33.8684 | 33.5979 | 33.3337 | 33.1389 | 31.8432 | 30.3926 | 10.9779 | 30.8211 | 30.6179 | 30.3895 | 30.12 | 29.8379 | 29.5337 | 29.2326 | 28.9389 | 28.6526 | 28.4453 | 26.9926 | 25.3295 | 23.8242 | 31.6442 | 31.4411 | 31.2126 | 30.9432 | 30.6611 | 30.3558 | 30.0547 | 29.7611 | 29.4747 | 29.2674 | 27.8137 | 26.1495 | 24.6442
|  | WHITEWAY | CF |  |  |  | 35.4589 | 34.8221 | 34.7011 | 34.5705 | 34.44 | 34.3042 | 34.1632 | 34.0158 | 33.8695 | 33.7411 | 32.84 | 32.4326 | 31.6242 | 30.9411 | 30.1758 | 30.0453 | 29.9053 | 29.7642 | 29.6179 | 29.4653 | 29.3063 | 29.1463 | 29.0095 | 28.0105 | 27.5895 | 26.6579 | 31.7642 | 31.0632 | 30.9326 | 30.7926 | 30.6516 | 30.5042 | 30.3526 | 30.1937 | 30.0337 | 29.8958 | 28.8968 | 28.4116 | 27.4789
BRAMLEY (FLEE) | BURGHFIELD MAIN | WILSON ROAD | MINIMUM HEADROOM | SU 69235 73304 | YES | 0.063158 | 35.0663 | 34.8011 | 34.5326 | 34.2474 | 33.9484 | 33.6379 | 33.2863 | 32.8074 | 32.3316 | 31.8853 | 29.8516 | 27.5758 | 0.097895 | 30.8789 | 30.3937 | 29.8916 | 29.3632 | 28.6726 | 27.4158 | 26.2726 | 25.74 | 25.2347 | 24.7589 | 22.5621 | 20.0253 | 17.5368 | 31.4926 | 31.2126 | 30.9295 | 30.6305 | 30.0411 | 28.7716 | 27.6021 | 27.0621 | 26.5484 | 26.0653 | 23.8505 | 21.3137 | 18.8242
|  | WILSON ROAD | EE |  |  |  | 35.1663 | 34.9568 | 34.7358 | 34.5011 | 34.2505 | 33.9895 | 33.7326 | 33.4716 | 33.2168 | 32.8737 | 31.3179 | 29.5779 | 27.8895 | 31.0137 | 30.7326 | 30.3326 | 29.9074 | 29.3147 | 28.2095 | 27.1537 | 26.6937 | 26.2316 | 25.8168 | 24.1568 | 22.2211 | 20.3126 | 31.6 | 31.3789 | 31.1474 | 30.9011 | 30.6305 | 29.5789 | 28.4979 | 28.0316 | 27.5621 | 27.14 | 25.4537 | 23.5095 | 21.6011
|  | WILSON ROAD | HT |  |  |  | 35.0663 | 34.8011 | 34.5326 | 34.2474 | 33.9484 | 33.6379 | 33.2863 | 32.8074 | 32.3316 | 31.8853 | 29.8516 | 27.5758 | 25.3632 | 30.8789 | 30.3937 | 29.8916 | 29.3632 | 28.6726 | 27.4158 | 26.2726 | 25.74 | 25.2347 | 24.7589 | 22.5621 | 20.0253 | 17.5368 | 31.4926 | 31.2126 | 30.9295 | 30.6305 | 30.0411 | 28.7716 | 27.6021 | 27.0621 | 26.5484 | 26.0653 | 23.8505 | 21.3137 | 18.8242
|  | WILSON ROAD | HE |  |  |  | 35.2811 | 35.1232 | 34.9484 | 34.7547 | 34.5474 | 34.3263 | 34.1147 | 33.9158 | 33.7295 | 33.5684 | 32.9842 | 31.9074 | 0.097895 | 31.1505 | 30.9779 | 30.7863 | 30.5547 | 30.0811 | 29.0705 | 28.1295 | 27.7747 | 27.4316 | 27.1337 | 26.0768 | 24.7674 | 23.4758 | 31.7242 | 31.56 | 31.3789 | 31.1789 | 30.9547 | 30.4389 | 29.4926 | 29.1337 | 28.7842 | 28.4821 | 27.4105 | 26.0695 | 24.7642
|  | WILSON ROAD | CF |  |  |  | 35.3474 | 35.2453 | 35.1411 | 35.0316 | 34.9179 | 34.8011 | 34.6821 | 34.5653 | 34.4484 | 34.3326 | 33.8158 | 33.5537 | 33.3695 | 31.2253 | 31.1116 | 30.9968 | 30.8758 | 30.7116 | 30.28 | 29.8211 | 29.6105 | 29.3832 | 29.1547 | 28.0979 | 27.2221 | 26.3505 | 31.7947 | 31.6874 | 31.5789 | 31.4642 | 31.3411 | 31.2053 | 31.0663 | 30.9442 | 30.7432 | 30.52 | 29.4695 | 28.5747 | 27.6789
MANNINGTON GSP | MANNINGTON BSP | WIMBORNE | MINIMUM HEADROOM | SZ 02014 99989 | YES | 1.3632 | 18.5379 | 18.0389 | 16.9326 | 15.7895 | 14.6547 | 38.7505 | 37.9368 | 36.9842 | 36.0126 | 35.0811 | 30.6758 | 27.1326 | -0.87789 | 12.6242 | 11.2389 | 9.9589 | 8.6979 | 7.4474 | 31.4779 | 30.6158 | 29.5789 | 28.5147 | 27.4926 | 22.6284 | 18.7232 | 15.3105 | 14.2032 | 12.8116 | 11.5326 | 10.2726 | 9.0232 | 33.0516 | 32.1853 | 31.1453 | 30.0768 | 29.0495 | 24.1558 | 20.2137 | 16.7884
|  | WIMBORNE | EE |  |  |  | 18.7116 | 18.3737 | 17.6095 | 16.6421 | 15.66 | 39.9011 | 39.2505 | 38.4242 | 37.5716 | 36.7389 | 32.9432 | 30.1284 | 27.8389 | 12.9989 | 11.8084 | 10.7126 | 9.6242 | 8.5379 | 32.7242 | 32.0379 | 31.1432 | 30.2126 | 29.3042 | 25.1253 | 22.0463 | 19.4832 | 14.5684 | 13.3895 | 12.2842 | 11.1979 | 10.1126 | 34.2958 | 33.6032 | 32.7032 | 31.7684 | 30.8526 | 26.6274 | 23.4937 | 20.9158
|  | WIMBORNE | HT |  |  |  | 18.5379 | 18.0389 | 16.9326 | 15.7895 | 14.6547 | 38.7505 | 37.9368 | 36.9842 | 36.0126 | 35.0811 | 30.6758 | 27.1326 | 24.0811 | 12.6242 | 11.2389 | 9.9589 | 8.6979 | 7.4474 | 31.4779 | 30.6158 | 29.5789 | 28.5147 | 27.4926 | 22.6284 | 18.7232 | 15.3105 | 14.2032 | 12.8116 | 11.5326 | 10.2726 | 9.0232 | 33.0516 | 32.1853 | 31.1453 | 30.0768 | 29.0495 | 24.1558 | 20.2137 | 16.7884
|  | WIMBORNE | HE |  |  |  | 18.9453 | 18.7179 | 18.4663 | 17.7484 | 16.9737 | 41.3989 | 40.9347 | 40.2989 | 39.6347 | 38.9905 | 36.1189 | 34.2126 | -0.87789 | 13.5021 | 12.5516 | 11.7021 | 10.84 | 9.9663 | 34.3526 | 33.8642 | 33.1716 | 32.4432 | 31.7326 | 28.5253 | 26.3884 | 24.6126 | 15.0611 | 14.1411 | 13.2768 | 12.4126 | 11.5411 | 35.9242 | 35.4337 | 34.7389 | 34.0084 | 33.2947 | 30.0716 | 27.92 | 26.1316
|  | WIMBORNE | CF |  |  |  | 19.0811 | 18.9547 | 18.8242 | 18.6884 | 18.5474 | 43.3979 | 43.2453 | 42.8989 | 42.5211 | 42.1305 | 40.1221 | 38.8253 | 37.7832 | 13.9053 | 13.3758 | 12.9274 | 12.5011 | 12.08 | 36.7568 | 36.4695 | 36.0653 | 35.6242 | 35.1758 | 32.9379 | 31.4821 | 30.3032 | 15.2411 | 14.94 | 14.5063 | 14.0926 | 13.6642 | 38.3347 | 38.0421 | 37.6337 | 37.1916 | 36.7421 | 34.5 | 33.0389 | 31.8505
MANNINGTON GSP | MANNINGTON BSP | WIMBORNE ST GILES | MINIMUM HEADROOM | SU 03028 12678 | YES | 0.38947 | 4.8526 | 4.8284 | 4.7989 | 4.7705 | 4.7411 | 4.7105 | 4.6568 | 4.5874 | 4.5684 | 4.5526 | 4.4011 | 4.2179 | 3.0095 | 4.6379 | 4.6074 | 4.5758 | 4.5453 | 4.5137 | 4.4821 | 4.4232 | 4.3442 | 4.3274 | 4.3116 | 4.1537 | 3.9558 | 3.8905 | 4.6547 | 4.6242 | 4.5926 | 4.5621 | 4.5305 | 4.4989 | 4.4379 | 4.3589 | 4.3411 | 4.3253 | 4.16 | 3.9568 | 3.8884
|  | WIMBORNE ST GILES | EE |  |  |  | 4.8579 | 4.8453 | 4.8232 | 4.8 | 4.7747 | 4.7505 | 4.7232 | 4.6979 | 4.6737 | 4.6495 | 4.5379 | 4.3937 | 4.2853 | 4.6516 | 4.6274 | 4.6032 | 4.5768 | 4.5516 | 4.5253 | 4.4989 | 4.4726 | 4.4474 | 4.4232 | 4.3137 | 4.1632 | 4.0453 | 4.6684 | 4.6442 | 4.62 | 4.5937 | 4.5684 | 4.5421 | 4.5137 | 4.4874 | 4.4611 | 4.4347 | 4.3179 | 4.1579 | 4.0368
|  | WIMBORNE ST GILES | HT |  |  |  | 4.8526 | 4.8284 | 4.7989 | 4.7705 | 4.7411 | 4.7105 | 4.6568 | 4.5874 | 4.5684 | 4.5526 | 4.4011 | 4.2179 | 4.1537 | 4.6379 | 4.6074 | 4.5758 | 4.5453 | 4.5137 | 4.4821 | 4.4232 | 4.3442 | 4.3274 | 4.3116 | 4.1537 | 3.9558 | 3.8905 | 4.6547 | 4.6242 | 4.5926 | 4.5621 | 4.5305 | 4.4989 | 4.4379 | 4.3589 | 4.3411 | 4.3253 | 4.16 | 3.9568 | 3.8884
|  | WIMBORNE ST GILES | HE |  |  |  | 4.8663 | 4.8579 | 4.8484 | 4.8379 | 4.8253 | 4.8074 | 4.7895 | 4.7716 | 4.7568 | 4.7411 | 4.68 | 4.5779 | 3.0095 | 4.6705 | 4.6558 | 4.64 | 4.6232 | 4.6063 | 4.5874 | 4.5695 | 4.5516 | 4.5358 | 4.52 | 4.46 | 4.3474 | 4.2537 | 4.6874 | 4.6726 | 4.6568 | 4.64 | 4.6232 | 4.6032 | 4.5853 | 4.5674 | 4.5505 | 4.5347 | 4.4705 | 4.3558 | 4.26
|  | WIMBORNE ST GILES | CF |  |  |  | 4.8726 | 4.8674 | 4.8621 | 4.8579 | 4.8526 | 4.8453 | 4.8389 | 4.8316 | 4.8221 | 4.8126 | 4.7684 | 4.7316 | 4.6705 | 4.6811 | 4.6716 | 4.6621 | 4.6537 | 4.6442 | 4.6326 | 4.6232 | 4.6137 | 4.6021 | 4.5937 | 4.5463 | 4.5084 | 4.44 | 4.6979 | 4.6884 | 4.6789 | 4.6705 | 4.6611 | 4.6495 | 4.6389 | 4.6295 | 4.6189 | 4.6095 | 4.5611 | 4.5211 | 4.4505
MANNINGTON GSP | SHAFTESBURY BSP | WINCANTON | MINIMUM HEADROOM | ST 71286 27802 | YES | 11.5053 | 16.0316 | 15.6642 | 15.2653 | 14.8326 | 14.5053 | 14.2274 | 13.9505 | 13.7 | 13.0789 | 12.9505 | 8.6747 | -2.1305 | -10.6442 | 13.5589 | 13.1526 | 12.7084 | 12.2263 | 11.8705 | 11.5737 | 11.2779 | 11.0095 | 10.3 | 10.1716 | 5.2484 | -5.5568 | -5.8589 | 13.7274 | 13.3253 | 12.8863 | 12.4095 | 12.0568 | 11.7621 | 11.4684 | 11.2011 | 10.5021 | 10.3737 | 5.6884 | -5.1168 | -5.4189
|  | WINCANTON | EE |  |  |  | 16.1537 | 15.8495 | 15.5063 | 15.1284 | 14.8547 | 14.6263 | 14.4074 | 14.1979 | 13.9947 | 13.8147 | 11.3158 | -1.2053 | -1.4053 | 13.6926 | 13.3547 | 12.9716 | 12.5495 | 12.2516 | 12.0074 | 11.7737 | 11.5495 | 11.3326 | 11.1411 | 8.3011 | -4.5568 | -4.7568 | 13.8116 | 13.5253 | 13.1463 | 12.7295 | 12.4337 | 12.1916 | 11.9589 | 11.7368 | 11.5211 | 11.3305 | 8.5053 | -4.3158 | -4.5158
|  | WINCANTON | HT |  |  |  | 16.0316 | 15.6642 | 15.2653 | 14.8326 | 14.5053 | 14.2274 | 13.9505 | 13.7 | 13.0789 | 12.9505 | 8.6747 | -2.1305 | -2.4326 | 13.5589 | 13.1526 | 12.7084 | 12.2263 | 11.8705 | 11.5737 | 11.2779 | 11.0095 | 10.3 | 10.1716 | 5.2484 | -5.5568 | -5.8589 | 13.7274 | 13.3253 | 12.8863 | 12.4095 | 12.0568 | 11.7621 | 11.4684 | 11.2011 | 10.5021 | 10.3737 | 5.6884 | -5.1168 | -5.4189
|  | WINCANTON | HE |  |  |  | 16.3189 | 16.0926 | 15.8253 | 15.52 | 15.3147 | 15.1505 | 14.9926 | 14.8432 | 14.7032 | 14.5811 | 11.8863 | -0.52105 | -10.6442 | 13.8737 | 13.6211 | 13.3211 | 12.9768 | 12.7537 | 12.58 | 12.4126 | 12.2547 | 12.1063 | 11.9768 | 8.86 | -3.8842 | -3.98 | 14.0389 | 13.7895 | 13.4926 | 13.1526 | 12.9316 | 12.7589 | 12.5916 | 12.4358 | 12.2874 | 12.16 | 9.0758 | -3.6316 | -3.7274
|  | WINCANTON | CF |  |  |  | 16.4789 | 16.4 | 16.2884 | 16.1705 | 15.9937 | 15.7979 | 15.6316 | 15.52 | 15.4316 | 15.3432 | 14.88 | 4.0926 | 3.6737 | 14.0537 | 13.9684 | 13.8453 | 13.7137 | 13.5137 | 13.2916 | 13.1053 | 12.9821 | 12.8863 | 12.7905 | 12.2842 | 1.4495 | 0.96421 | 14.1379 | 14.0579 | 13.9474 | 13.8284 | 13.6516 | 13.4558 | 13.2789 | 13.1568 | 13.0632 | 12.9674 | 12.4653 | 1.6358 | 1.1579
COWLEY GSP | WITNEY BSP | WINDRUSH PARK | MINIMUM HEADROOM | SP 33366 09758 | YES | 1.6095 | 32.3537 | 32.2295 | 32.1032 | 31.9684 | 31.8305 | 31.6884 | 31.5453 | 31.4211 | 31.2368 | 31.0421 | 30.1168 | 28.9095 | 11.9705 | 29.2474 | 28.8768 | 28.6368 | 28.3716 | 27.9989 | 27.6021 | 27.3463 | 27.1126 | 26.8926 | 26.6832 | 25.6695 | 24.3095 | 21.9726 | 29.9358 | 29.5653 | 29.3253 | 29.0589 | 28.6863 | 28.2884 | 28.0326 | 27.7989 | 27.58 | 27.3695 | 26.3568 | 24.9947 | 22.5516
|  | WINDRUSH PARK | EE |  |  |  | 32.4 | 32.3011 | 32.1968 | 32.0842 | 31.9684 | 31.8484 | 31.7326 | 31.6242 | 31.5168 | 31.4242 | 30.8158 | 30.4453 | 29.38 | 29.3537 | 29.0379 | 28.8463 | 28.6326 | 28.36 | 28.0221 | 27.7789 | 27.5695 | 27.3642 | 27.1811 | 26.4379 | 26.2463 | 25.0221 | 30.0147 | 29.7253 | 29.5337 | 29.3211 | 29.0484 | 28.7095 | 28.4663 | 28.2568 | 28.0505 | 27.8684 | 27.1232 | 27.0358 | 25.8126
|  | WINDRUSH PARK | HT |  |  |  | 32.3537 | 32.2295 | 32.1032 | 31.9684 | 31.8305 | 31.6884 | 31.5453 | 31.4211 | 31.2368 | 31.0421 | 30.1168 | 28.9095 | 27.0547 | 29.2474 | 28.8768 | 28.6368 | 28.3716 | 27.9989 | 27.6021 | 27.3463 | 27.1126 | 26.8926 | 26.6832 | 25.6695 | 24.3095 | 21.9726 | 29.9358 | 29.5653 | 29.3253 | 29.0589 | 28.6863 | 28.2884 | 28.0326 | 27.7989 | 27.58 | 27.3695 | 26.3568 | 24.9947 | 22.5516
|  | WINDRUSH PARK | HE |  |  |  | 32.4684 | 32.4021 | 32.3284 | 32.2474 | 32.16 | 32.0674 | 31.9779 | 31.8937 | 31.8158 | 31.7484 | 31.5211 | 30.4726 | 11.9705 | 29.5042 | 29.2589 | 29.1347 | 28.9926 | 28.7768 | 28.4905 | 28.3042 | 28.1421 | 28 | 27.8705 | 27.3811 | 25.7832 | 24.7874 | 30.0895 | 29.9474 | 29.8232 | 29.6811 | 29.4653 | 29.1789 | 28.9916 | 28.8305 | 28.6874 | 28.5589 | 28.0684 | 26.3642 | 25.3674
|  | WINDRUSH PARK | CF |  |  |  | 32.5084 | 32.4716 | 32.4337 | 32.3947 | 32.3537 | 32.3116 | 32.2684 | 32.2263 | 32.1842 | 32.1421 | 31.9558 | 31.8621 | 31.5726 | 29.5684 | 29.4811 | 29.4084 | 29.3263 | 29.2347 | 29.1453 | 29.0484 | 28.9621 | 28.86 | 28.7526 | 28.2389 | 27.8116 | 27.1989 | 30.1337 | 30.0905 | 30.0505 | 30.0095 | 29.9232 | 29.8337 | 29.7368 | 29.6505 | 29.5484 | 29.44 | 28.9274 | 28.4989 | 27.8863
MANNINGTON GSP | WINFRITH HEATH | WINFRITH HEATH | MINIMUM HEADROOM | SY 80748 86538 | YES | 0.73684 | 23.1947 | 22.9211 | 22.4916 | 21.9695 | 21.2611 | 20.3684 | 19.1589 | 18.2074 | 17.3937 | 16.5874 | 13.5958 | 12.0421 | 0.45368 | 25.4253 | 25.1211 | 24.6358 | 24.04 | 23.2274 | 22.2095 | 20.8189 | 19.7316 | 18.8032 | 17.8842 | 14.5295 | 12.8695 | 11.9053 | 23.0526 | 22.7484 | 22.2642 | 21.6705 | 20.8589 | 19.8368 | 18.4421 | 17.3484 | 16.4147 | 15.4884 | 12.0789 | 10.3495 | 9.3568
|  | WINFRITH HEATH | EE |  |  |  | 23.2189 | 23.0474 | 22.6568 | 22.14 | 21.4979 | 20.6389 | 19.4589 | 18.5253 | 17.7221 | 16.9253 | 13.98 | 12.5084 | 11.8147 | 25.5168 | 25.2589 | 24.8158 | 24.2242 | 23.4853 | 22.5042 | 21.1484 | 20.0821 | 19.1716 | 18.2684 | 14.9979 | 13.4684 | 12.7284 | 23.1358 | 22.8863 | 22.4432 | 21.8526 | 21.1147 | 20.1295 | 18.7674 | 17.6926 | 16.7726 | 15.8589 | 12.5084 | 10.88 | 10.1084
|  | WINFRITH HEATH | HT |  |  |  | 23.1947 | 22.9211 | 22.4916 | 21.9695 | 21.2611 | 20.3684 | 19.1589 | 18.2074 | 17.3937 | 16.5874 | 13.5958 | 12.0421 | 11.1505 | 25.4253 | 25.1211 | 24.6358 | 24.04 | 23.2274 | 22.2095 | 20.8189 | 19.7316 | 18.8032 | 17.8842 | 14.5295 | 12.8695 | 11.9053 | 23.0526 | 22.7484 | 22.2642 | 21.6705 | 20.8589 | 19.8368 | 18.4421 | 17.3484 | 16.4147 | 15.4884 | 12.0789 | 10.3495 | 9.3568
|  | WINFRITH HEATH | HE |  |  |  | 23.3842 | 23.18 | 22.8453 | 22.3653 | 21.78 | 21.0168 | 19.9011 | 19.0295 | 18.2937 | 17.5684 | 15.0232 | 14.0179 | 0.45368 | 25.6305 | 25.4 | 25.0168 | 24.4621 | 23.7863 | 22.9105 | 21.6158 | 20.6116 | 19.7653 | 18.9295 | 16.0263 | 14.9095 | 14.3726 | 23.2568 | 23.0274 | 22.6453 | 22.0926 | 21.4179 | 20.5379 | 19.2432 | 18.2368 | 17.3863 | 16.5474 | 13.6158 | 12.4726 | 11.9105
|  | WINFRITH HEATH | CF |  |  |  | 23.4558 | 23.3663 | 23.1989 | 22.9989 | 22.7274 | 22.3895 | 21.88 | 21.4442 | 21.0442 | 20.6179 | 18.9958 | 18.3579 | 18.0232 | 25.7095 | 25.6095 | 25.4179 | 25.1874 | 24.8737 | 24.4853 | 23.8958 | 23.3926 | 22.9316 | 22.44 | 20.5758 | 19.8642 | 19.5074 | 23.3368 | 23.2358 | 23.0453 | 22.8158 | 22.5021 | 22.1126 | 21.5221 | 21.0179 | 20.5558 | 20.0632 | 18.1926 | 17.4663 | 17.0926
COWLEY GSP | DRAYTON BSP | WINSMORE LANE | MINIMUM HEADROOM | SU 49513 96982 | YES | 0.51579 | 24.9705 | 24.6737 | 24.3747 | 24.0568 | 23.7263 | 23.3863 | 23.0432 | 22.7411 | 22.4642 | 22.2095 | 20.8842 | 18.7747 | -10.4547 | 20.5074 | 19.9758 | 19.3895 | 18.7937 | 18.1874 | 17.5832 | 16.9768 | 16.4179 | 15.8968 | 15.4095 | 13.1958 | 10.8526 | 7.8568 | 21.1168 | 20.8021 | 20.4863 | 20.1442 | 19.5389 | 18.9358 | 18.3295 | 17.7716 | 17.2505 | 16.7642 | 14.5516 | 12.2126 | 9.2211
|  | WINSMORE LANE | EE |  |  |  | 25.08 | 24.8463 | 24.5989 | 24.3368 | 24.06 | 23.7737 | 23.4958 | 23.2316 | 22.9768 | 22.7495 | 21.9137 | 20.9895 | 19.0684 | 20.6347 | 20.36 | 19.8895 | 19.4095 | 18.9126 | 18.4105 | 17.9168 | 17.4442 | 16.9916 | 16.5779 | 14.8221 | 13.2895 | 11.1032 | 21.2337 | 20.9874 | 20.7274 | 20.4526 | 20.1621 | 19.7621 | 19.2695 | 18.7968 | 18.3442 | 17.9305 | 16.1768 | 14.6453 | 12.4632
|  | WINSMORE LANE | HT |  |  |  | 24.9705 | 24.6737 | 24.3747 | 24.0568 | 23.7263 | 23.3863 | 23.0432 | 22.7411 | 22.4642 | 22.2095 | 20.8842 | 18.7747 | 16.1337 | 20.5074 | 19.9758 | 19.3895 | 18.7937 | 18.1874 | 17.5832 | 16.9768 | 16.4179 | 15.8968 | 15.4095 | 13.1958 | 10.8526 | 7.8568 | 21.1168 | 20.8021 | 20.4863 | 20.1442 | 19.5389 | 18.9358 | 18.3295 | 17.7716 | 17.2505 | 16.7642 | 14.5516 | 12.2126 | 9.2211
|  | WINSMORE LANE | HE |  |  |  | 25.2284 | 25.0642 | 24.8821 | 24.6811 | 24.4653 | 24.2347 | 24.0137 | 23.8063 | 23.6116 | 23.4442 | 22.8758 | 22.5389 | -10.4547 | 20.8084 | 20.6263 | 20.4274 | 20.2084 | 19.8547 | 19.4842 | 19.1211 | 18.7768 | 18.4558 | 18.1716 | 17.0568 | 16.1368 | 14.5421 | 21.3937 | 21.2221 | 21.0316 | 20.8232 | 20.5989 | 20.36 | 20.1316 | 19.9158 | 19.7137 | 19.5232 | 18.4095 | 17.4905 | 15.8979
|  | WINSMORE LANE | CF |  |  |  | 25.3137 | 25.2168 | 25.1158 | 25.0105 | 24.9011 | 24.7884 | 24.6737 | 24.5611 | 24.4495 | 24.3379 | 23.84 | 23.5905 | 23.4526 | 20.9042 | 20.7947 | 20.6811 | 20.5642 | 20.4421 | 20.3158 | 20.0968 | 19.8779 | 19.6621 | 19.4484 | 18.4568 | 17.7821 | 16.8042 | 21.4832 | 21.3811 | 21.2747 | 21.1642 | 21.0484 | 20.9305 | 20.8095 | 20.6905 | 20.5726 | 20.4558 | 19.8084 | 19.1347 | 18.1579
MANNINGTON GSP | LYTCHETT | WINTERBORNE KINGSTON | MINIMUM HEADROOM | SY 84631 98138 | YES | 1.1674 | 8.5632 | 7.1674 | 23.2032 | 21.4253 | 21.2158 | 20.4168 | 18.6811 | 16.5084 | 16.1958 | 15.8789 | 11.4221 | 5.3 | 3.7 | 7.2874 | 5.9495 | 21.9316 | 20.5768 | 20.3537 | 18.8074 | 16.86 | 14.4011 | 14.1358 | 13.8705 | 9.2705 | 2.7779 | 1.2042 | 7.6242 | 6.2305 | 22.2116 | 20.4305 | 20.2063 | 19.0495 | 17.0653 | 14.5663 | 14.2537 | 13.9358 | 9.0032 | 2.1274 | 0.39895
|  | WINTERBORNE KINGSTON | EE |  |  |  | 8.62 | 7.3421 | 23.4232 | 21.4253 | 21.2158 | 20.8158 | 20.4137 | 19.9989 | 19.5684 | 19.1295 | 14.9558 | 9.1168 | 5.5432 | 7.4105 | 6.0347 | 22.1737 | 20.5768 | 20.3537 | 19.9842 | 19.6158 | 19.2411 | 18.8558 | 18.4674 | 14.3642 | 8.3926 | 4.4926 | 7.7179 | 6.42 | 22.4516 | 20.4305 | 20.2063 | 19.7937 | 19.3779 | 18.9495 | 18.5074 | 18.0558 | 13.5263 | 7.0642 | 3.0105
|  | WINTERBORNE KINGSTON | HT |  |  |  | 8.5632 | 7.1674 | 23.2032 | 22.9347 | 22.1905 | 20.4168 | 18.6811 | 16.5084 | 16.1958 | 15.8789 | 11.4221 | 5.3 | 3.7 | 7.2874 | 5.9495 | 21.9316 | 21.6474 | 20.8032 | 18.8074 | 16.86 | 14.4011 | 14.1358 | 13.8705 | 9.2705 | 2.7779 | 1.2042 | 7.6242 | 6.2305 | 22.2116 | 21.9253 | 21.08 | 19.0495 | 17.0653 | 14.5663 | 14.2537 | 13.9358 | 9.0032 | 2.1274 | 0.39895
|  | WINTERBORNE KINGSTON | HE |  |  |  | 8.6989 | 7.5726 | 23.7421 | 23.6011 | 23.4558 | 23.1947 | 22.9526 | 22.7137 | 22.4758 | 22.2463 | 20.2726 | 16.4758 | 12.2716 | 7.58 | 6.2842 | 22.5158 | 22.3674 | 22.2137 | 21.9737 | 21.7495 | 21.5316 | 21.3158 | 21.1095 | 19.1568 | 14.9684 | 11.7105 | 7.8484 | 6.6263 | 22.7968 | 22.6474 | 22.4937 | 22.2242 | 21.9747 | 21.7295 | 21.4832 | 21.2474 | 19.1 | 14.7642 | 11.3726
|  | WINTERBORNE KINGSTON | CF |  |  |  | 8.7453 | 7.6537 | 24.0937 | 24.0168 | 23.9368 | 23.8032 | 23.6726 | 23.54 | 23.4126 | 23.2958 | 22.5789 | 20.2358 | 18.0526 | 7.6726 | 6.4863 | 22.7989 | 22.8253 | 22.74 | 22.6137 | 22.4905 | 22.3663 | 22.2432 | 22.1316 | 21.4316 | 18.8326 | 16.4284 | 7.9211 | 6.7758 | 23.1516 | 23.1053 | 23.02 | 22.88 | 22.7432 | 22.6053 | 22.4705 | 22.3484 | 21.5832 | 18.9053 | 16.4105
MANNINGTON GSP | REDHILL BSP | WINTON | MINIMUM HEADROOM | SZ 09349 93822 | YES | 0.23895 | 26.3053 | 25.8284 | 25.3463 | 24.8347 | 24.3053 | 36.5589 | 36.0084 | 35.5221 | 35.08 | 34.2632 | 30.2137 | 26.5442 | -4.9137 | 20.9105 | 19.9968 | 19.0895 | 18.1663 | 17.2484 | 29.1242 | 28.1095 | 27.1063 | 26.0737 | 25.0832 | 20.6105 | 16.5147 | 12.74 | 22.0495 | 21.5463 | 20.8968 | 19.9916 | 19.0916 | 30.9811 | 29.9526 | 28.9453 | 27.9137 | 26.92 | 22.4432 | 18.3389 | 14.5621
|  | WINTON | EE |  |  |  | 26.4811 | 26.1042 | 25.7053 | 25.28 | 24.8358 | 37.1737 | 36.7274 | 36.3032 | 35.8937 | 35.5295 | 33.1074 | 30.2568 | 27.7 | 21.1758 | 20.6042 | 19.8832 | 19.1432 | 18.3968 | 30.4495 | 29.6484 | 28.8737 | 28.1263 | 27.3137 | 23.8179 | 20.6284 | 17.7326 | 22.2389 | 21.8421 | 21.4242 | 20.9453 | 20.2116 | 32.2768 | 31.4905 | 30.7295 | 29.9716 | 29.1516 | 25.6463 | 22.4474 | 19.5484
|  | WINTON | HT |  |  |  | 26.3053 | 25.8284 | 25.3463 | 24.8347 | 24.3053 | 36.5589 | 36.0084 | 35.5221 | 35.08 | 34.2632 | 30.2137 | 26.5442 | 23.1926 | 20.9105 | 19.9968 | 19.0895 | 18.1663 | 17.2484 | 29.1242 | 28.1095 | 27.1063 | 26.0737 | 25.0832 | 20.6105 | 16.5147 | 12.74 | 22.0495 | 21.5463 | 20.8968 | 19.9916 | 19.0916 | 30.9811 | 29.9526 | 28.9453 | 27.9137 | 26.92 | 22.4432 | 18.3389 | 14.5621
|  | WINTON | HE |  |  |  | 26.7316 | 26.4716 | 26.1842 | 25.8674 | 25.5263 | 37.9621 | 37.6116 | 37.2832 | 36.9737 | 36.7084 | 35.8063 | 34.4737 | -4.9137 | 21.4442 | 21.1726 | 20.8747 | 20.4421 | 19.9232 | 32.1884 | 31.5958 | 31.0432 | 30.4905 | 29.8842 | 27.4442 | 25.2274 | 23.2453 | 22.5074 | 22.2368 | 21.9379 | 21.6095 | 21.2579 | 33.6842 | 33.3189 | 32.8495 | 32.3063 | 31.7147 | 29.2811 | 27.06 | 25.0768
|  | WINTON | CF |  |  |  | 26.8811 | 26.7347 | 26.5832 | 26.4253 | 26.2632 | 38.8937 | 38.7211 | 38.5516 | 38.3832 | 38.2147 | 37.4653 | 37.0874 | 36.8758 | 21.6011 | 21.4474 | 21.2884 | 21.1232 | 20.9537 | 33.4916 | 33.1189 | 32.7368 | 32.3842 | 32.0505 | 30.62 | 29.1253 | 27.7979 | 22.6653 | 22.5116 | 22.3516 | 22.1863 | 22.0168 | 34.6379 | 34.4526 | 34.2705 | 34.0916 | 33.8526 | 32.4505 | 30.9642 | 29.6347
COWLEY GSP | WITNEY BSP | WITNEY TOWN | MINIMUM HEADROOM | SP 35844 09625 | YES | 0.62105 | 27.6025 | 30.3509 | 48.3621 | 47.4884 | 46.2337 | 44.2611 | 41.96 | 39.8632 | 37.8116 | 35.8011 | 30.4021 | 26.7611 | -1.8474 | 21.8067 | 20.953 | 38.9095 | 37.9579 | 36.5621 | 34.3379 | 31.7274 | 29.3474 | 27.0189 | 24.7316 | 18.7537 | 14.8011 | 10.7589 | 22.8499 | 22.0909 | 40.0463 | 39.0958 | 37.7011 | 35.4705 | 32.8547 | 30.4705 | 28.1347 | 25.8389 | 19.7916 | 15.7547 | 11.6821
|  | WITNEY TOWN | EE |  |  |  | 31.4562 | 30.832 | 48.9874 | 48.3147 | 47.3158 | 45.7 | 43.8621 | 42.1126 | 40 | 37.8663 | 32.3842 | 29.4558 | 26.6063 | 22.1551 | 21.4772 | 39.5905 | 38.8653 | 37.7558 | 35.9389 | 33.8621 | 31.8895 | 29.4884 | 27.06 | 20.9842 | 17.8779 | 14.6853 | 23.2909 | 22.6141 | 40.7274 | 40.0011 | 38.8937 | 37.0695 | 34.9842 | 33.0011 | 30.5884 | 28.1474 | 21.9726 | 18.7453 | 15.5189
|  | WITNEY TOWN | HT |  |  |  | 31.1372 | 30.3509 | 48.3621 | 47.4884 | 46.2337 | 44.2611 | 41.96 | 39.8632 | 37.8116 | 35.8011 | 30.4021 | 26.7611 | 23.1505 | 21.8067 | 20.953 | 38.9095 | 37.9579 | 36.5621 | 34.3379 | 31.7274 | 29.3474 | 27.0189 | 24.7316 | 18.7537 | 14.8011 | 10.7589 | 22.9425 | 22.0909 | 40.0463 | 39.0958 | 37.7011 | 35.4705 | 32.8547 | 30.4705 | 28.1347 | 25.8389 | 19.7916 | 15.7547 | 11.6821
|  | WITNEY TOWN | HE |  |  |  | 31.8909 | 31.4751 | 49.8316 | 49.3484 | 48.5284 | 47.0737 | 45.4074 | 43.7821 | 41.8463 | 39.9505 | 35.5758 | 33.7032 | -1.8474 | 22.6299 | 22.1793 | 40.5105 | 39.9895 | 39.0747 | 37.4305 | 35.5305 | 33.6779 | 31.4558 | 29.2779 | 24.3368 | 22.2695 | 19.8663 | 23.7646 | 23.3151 | 41.6474 | 41.1263 | 40.2126 | 38.5632 | 36.6611 | 34.8042 | 32.58 | 30.3979 | 25.42 | 23.3211 | 20.8895
|  | WITNEY TOWN | CF |  |  |  | 27.6025 | 31.7141 | 50.3768 | 50.1295 | 49.7768 | 49.3032 | 48.7379 | 48.2147 | 47.6316 | 46.9589 | 41.7211 | 40.4905 | 39.1221 | 22.1467 | 22.492 | 40.9811 | 40.7158 | 40.3253 | 39.9105 | 39.2768 | 38.6926 | 38.0368 | 37.2747 | 31.2495 | 29.8884 | 28.3463 | 22.8499 | 23.7404 | 42.2295 | 41.9632 | 41.5726 | 41.0442 | 40.4084 | 39.8221 | 39.1642 | 38.4011 | 32.3705 | 30.9926 | 29.4316
BRAMLEY (FLEE) | WOKINGHAM BSP | WOKINGHAM | MINIMUM HEADROOM | SU 79589 67665 | YES | 0 | 32.4495 | 32.1916 | 31.9305 | 31.6368 | 31.3337 | 31.02 | 30.6168 | 30.1453 | 29.7189 | 29.3263 | 27.6337 | 26.1347 | 11.1768 | 29.7874 | 29.2905 | 28.7737 | 28.2232 | 27.6737 | 27.0811 | 26.5242 | 26.0084 | 25.5411 | 25.1116 | 23.2484 | 21.5895 | 20.0789 | 30.5789 | 30.0863 | 29.5705 | 29.02 | 28.4716 | 27.88 | 27.3221 | 26.8063 | 26.34 | 25.9105 | 24.0474 | 22.3884 | 20.8789
|  | WOKINGHAM | EE |  |  |  | 32.5547 | 32.3568 | 32.1463 | 31.9232 | 31.6832 | 31.4253 | 31.18 | 30.9474 | 30.7274 | 30.42 | 29.1789 | 28.1189 | 27.18 | 30.0147 | 29.6347 | 29.2484 | 28.8179 | 28.3832 | 27.9 | 27.4505 | 27.0305 | 26.66 | 26.3242 | 24.9674 | 23.7821 | 22.7189 | 30.7979 | 30.4305 | 30.0453 | 29.6147 | 29.18 | 28.6979 | 28.2474 | 27.8284 | 27.4579 | 27.1211 | 25.7632 | 24.5768 | 23.5147
|  | WOKINGHAM | HT |  |  |  | 32.4495 | 32.1916 | 31.9305 | 31.6368 | 31.3337 | 31.02 | 30.6168 | 30.1453 | 29.7189 | 29.3263 | 27.6337 | 26.1347 | 24.7768 | 29.7874 | 29.2905 | 28.7737 | 28.2232 | 27.6737 | 27.0811 | 26.5242 | 26.0084 | 25.5411 | 25.1116 | 23.2484 | 21.5895 | 20.0789 | 30.5789 | 30.0863 | 29.5705 | 29.02 | 28.4716 | 27.88 | 27.3221 | 26.8063 | 26.34 | 25.9105 | 24.0474 | 22.3884 | 20.8789
|  | WOKINGHAM | HE |  |  |  | 32.6968 | 32.5663 | 32.4211 | 32.2621 | 32.0905 | 31.9063 | 31.7295 | 31.5547 | 31.3926 | 31.2537 | 30.7779 | 30.2958 | 11.1768 | 30.32 | 30.0853 | 29.8389 | 29.5432 | 29.2347 | 28.8695 | 28.5337 | 28.2253 | 27.9705 | 27.7379 | 26.8958 | 26.1821 | 25.5495 | 30.9737 | 30.8379 | 30.6253 | 30.3389 | 30.0316 | 29.6653 | 29.3305 | 29.0211 | 28.7674 | 28.5337 | 27.6916 | 26.9789 | 26.3463
|  | WOKINGHAM | CF |  |  |  | 32.7758 | 32.7042 | 32.6305 | 32.5526 | 32.4726 | 32.3905 | 32.3053 | 32.2221 | 32.14 | 32.0579 | 31.6705 | 31.4684 | 31.3505 | 30.5189 | 30.3758 | 30.2211 | 30.0453 | 29.8611 | 29.6537 | 29.44 | 29.2463 | 29.08 | 28.9221 | 28.2221 | 27.7495 | 27.3821 | 31.06 | 30.9842 | 30.9063 | 30.8221 | 30.6484 | 30.4495 | 30.2368 | 30.0432 | 29.8768 | 29.7189 | 29.0189 | 28.5463 | 28.1789
BRAMLEY (FLEE) | BURGHFIELD RESERVE | WOODCOTE | MINIMUM HEADROOM | SU 64425 81624 | YES | 0.82105 | 7.9947 | 7.9284 | 7.8621 | 7.1926 | 7.1337 | 7.0726 | 7.0147 | 6.9589 | 6.9063 | 6.86 | 6.66 | 6.2684 | 0.24211 | 6.8747 | 6.7463 | 6.6189 | 5.7726 | 5.7137 | 5.6526 | 5.5947 | 5.5389 | 5.4863 | 5.44 | 5.2674 | 4.8347 | 4.3905 | 7.1042 | 7.0116 | 6.8895 | 6.1063 | 6.0474 | 5.9863 | 5.9284 | 5.8726 | 5.82 | 5.7737 | 5.5874 | 5.1747 | 4.7558
|  | WOODCOTE | EE |  |  |  | 8.0221 | 7.9716 | 7.9179 | 7.1926 | 7.1337 | 7.0726 | 7.0147 | 6.9589 | 6.9063 | 6.86 | 6.6916 | 6.5821 | 6.4558 | 6.9179 | 6.8347 | 6.7358 | 5.7726 | 5.7137 | 5.6526 | 5.5947 | 5.5389 | 5.4863 | 5.44 | 5.2716 | 5.1621 | 5.0274 | 7.1337 | 7.08 | 7.0011 | 6.1063 | 6.0474 | 5.9863 | 5.9284 | 5.8726 | 5.82 | 5.7737 | 5.6053 | 5.4958 | 5.3653
|  | WOODCOTE | HT |  |  |  | 7.9947 | 7.9284 | 7.8621 | 7.7905 | 7.6674 | 7.5432 | 7.42 | 7.3032 | 7.1926 | 7.0947 | 6.66 | 6.2684 | 5.8726 | 6.8747 | 6.7463 | 6.6189 | 6.4905 | 6.3568 | 6.2232 | 6.0916 | 5.9653 | 5.8463 | 5.7411 | 5.2674 | 4.8347 | 4.3905 | 7.1042 | 7.0116 | 6.8895 | 6.7653 | 6.6358 | 6.5074 | 6.38 | 6.2579 | 6.1432 | 6.0411 | 5.5874 | 5.1747 | 4.7558
|  | WOODCOTE | HE |  |  |  | 8.0589 | 8.0253 | 7.9895 | 7.2811 | 7.2379 | 7.1916 | 7.1463 | 7.1053 | 7.0663 | 7.0326 | 6.92 | 6.8568 | 0.24211 | 6.96 | 6.9232 | 6.8842 | 5.8611 | 5.8179 | 5.7716 | 5.7263 | 5.6853 | 5.6463 | 5.6126 | 5.5 | 5.4368 | 5.3979 | 7.1726 | 7.1368 | 7.1 | 6.1947 | 6.1516 | 6.1053 | 6.06 | 6.0189 | 5.98 | 5.9463 | 5.8337 | 5.7705 | 5.7316
|  | WOODCOTE | CF |  |  |  | 8.08 | 8.0621 | 8.0432 | 8.0242 | 8.0042 | 7.9842 | 7.9632 | 7.9421 | 7.9221 | 7.9011 | 7.78 | 7.6505 | 7.5442 | 6.9842 | 6.9632 | 6.9421 | 6.9211 | 6.8979 | 6.8568 | 6.8126 | 6.7663 | 6.72 | 6.6768 | 6.4726 | 6.3274 | 6.2063 | 7.1947 | 7.1758 | 7.1558 | 7.1358 | 7.1147 | 7.0937 | 7.0705 | 7.0316 | 6.9874 | 6.9453 | 6.7505 | 6.6126 | 6.4989
NURSLING GSP | SOUTHAMPTON (2 X 90) | WOODMILL LANE | MINIMUM HEADROOM | SU 43733 15470 | YES | 0 | 32.3726 | 32.1937 | 32.0032 | 31.7937 | 31.5768 | 31.3568 | 31.1347 | 30.9368 | 30.7558 | 30.5 | 28.3768 | 26.6168 | 11.2074 | 30.3411 | 30.0758 | 29.7432 | 29.3221 | 28.8926 | 28.5211 | 28.1558 | 27.8221 | 27.5032 | 27.1211 | 24.7432 | 22.7642 | 20.9221 | 30.78 | 30.5874 | 30.3842 | 30.1 | 29.6832 | 29.3211 | 28.9558 | 28.62 | 28.2989 | 27.9168 | 25.5389 | 23.56 | 21.7168
|  | WOODMILL LANE | EE |  |  |  | 32.4389 | 32.2979 | 32.1484 | 31.9779 | 31.7979 | 31.6053 | 31.4168 | 31.2442 | 31.0758 | 30.9263 | 29.5516 | 28.16 | 26.9042 | 30.4116 | 30.2642 | 30.0295 | 29.7105 | 29.3758 | 28.9632 | 28.5368 | 28.2442 | 27.9653 | 27.7189 | 26.0421 | 24.4726 | 23.0474 | 30.8516 | 30.7032 | 30.5411 | 30.3589 | 30.1505 | 29.7516 | 29.3389 | 29.0453 | 28.7642 | 28.5147 | 26.8379 | 25.2684 | 23.8421
|  | WOODMILL LANE | HT |  |  |  | 32.3726 | 32.1937 | 32.0032 | 31.7937 | 31.5768 | 31.3568 | 31.1347 | 30.9368 | 30.7558 | 30.5 | 28.3768 | 26.6168 | 24.9874 | 30.3411 | 30.0758 | 29.7432 | 29.3221 | 28.8926 | 28.5211 | 28.1558 | 27.8221 | 27.5032 | 27.1211 | 24.7432 | 22.7642 | 20.9221 | 30.78 | 30.5874 | 30.3842 | 30.1 | 29.6832 | 29.3211 | 28.9558 | 28.62 | 28.2989 | 27.9168 | 25.5389 | 23.56 | 21.7168
|  | WOODMILL LANE | HE |  |  |  | 32.5221 | 32.4179 | 32.3021 | 32.1758 | 32.0379 | 31.8789 | 31.7242 | 31.5874 | 31.46 | 31.3495 | 30.9379 | 30 | 11.2074 | 30.5 | 30.3916 | 30.2726 | 30.1389 | 29.8989 | 29.5768 | 29.2253 | 29.0211 | 28.8295 | 28.6611 | 27.6158 | 26.5126 | 25.4747 | 30.9421 | 30.8326 | 30.7126 | 30.5789 | 30.4284 | 30.2568 | 30.0053 | 29.8053 | 29.6168 | 29.4526 | 28.4116 | 27.3084 | 26.2705
|  | WOODMILL LANE | CF |  |  |  | 32.5726 | 32.5095 | 32.4442 | 32.3758 | 32.3053 | 32.2316 | 32.1579 | 32.0842 | 32.0105 | 31.9337 | 31.5853 | 31.3842 | 31.0726 | 30.5526 | 30.4863 | 30.4189 | 30.3474 | 30.2747 | 30.1989 | 30.1189 | 29.9884 | 29.8589 | 29.7295 | 29.04 | 28.3442 | 27.6747 | 30.9947 | 30.9284 | 30.86 | 30.7884 | 30.7147 | 30.6379 | 30.5611 | 30.4811 | 30.4 | 30.3189 | 29.8221 | 29.1432 | 28.4705
COWLEY GSP | YARNTON BSP | WOODSTOCK | MINIMUM HEADROOM | SP 44795 17462 | YES | 0.070526 | 17.7158 | 17.7579 | 17.4463 | 17.1011 | 16.6358 | 16.1263 | 15.6189 | 15.2053 | 15.0042 | 14.8147 | 13.9242 | 12.8589 | 0.93053 | 15.0758 | 14.6632 | 14.3179 | 13.9358 | 13.4105 | 12.8347 | 12.2611 | 11.7947 | 11.5768 | 11.3726 | 10.3989 | 9.1979 | 7.7747 | 15.5779 | 15.1653 | 14.82 | 14.4379 | 13.9137 | 13.3389 | 12.7663 | 12.3011 | 12.0842 | 11.8789 | 10.9063 | 9.7063 | 8.2853
|  | WOODSTOCK | EE |  |  |  | 17.7158 | 17.9053 | 17.64 | 17.3421 | 16.9189 | 16.4558 | 15.9979 | 15.6179 | 15.44 | 15.2768 | 14.5989 | 13.7958 | 12.8189 | 15.1221 | 14.8242 | 14.5284 | 14.1989 | 13.72 | 13.1947 | 12.6747 | 12.2442 | 12.0547 | 11.8789 | 11.1411 | 10.2337 | 9.1105 | 15.6095 | 15.3263 | 15.0316 | 14.7011 | 14.2232 | 13.6979 | 13.1789 | 12.7495 | 12.5589 | 12.3832 | 11.6453 | 10.7389 | 9.6168
|  | WOODSTOCK | HT |  |  |  | 18.1263 | 17.7579 | 17.4463 | 17.1011 | 16.6358 | 16.1263 | 15.6189 | 15.2053 | 15.0042 | 14.8147 | 13.9242 | 12.8589 | 11.6158 | 15.0758 | 14.6632 | 14.3179 | 13.9358 | 13.4105 | 12.8347 | 12.2611 | 11.7947 | 11.5768 | 11.3726 | 10.3989 | 9.1979 | 7.7747 | 15.5779 | 15.1653 | 14.82 | 14.4379 | 13.9137 | 13.3389 | 12.7663 | 12.3011 | 12.0842 | 11.8789 | 10.9063 | 9.7063 | 8.2853
|  | WOODSTOCK | HE |  |  |  | 18.3621 | 18.1074 | 17.9032 | 17.6674 | 17.3 | 16.8874 | 16.4779 | 16.1474 | 16.0232 | 15.9105 | 15.4779 | 14.8958 | 0.93053 | 15.3337 | 15.0442 | 14.8168 | 14.5526 | 14.1347 | 13.6642 | 13.1968 | 12.8221 | 12.6884 | 12.5695 | 12.0989 | 11.4358 | 10.5474 | 15.8358 | 15.5463 | 15.32 | 15.0558 | 14.6379 | 14.1695 | 13.7011 | 13.3274 | 13.1947 | 13.0747 | 12.6053 | 11.9421 | 11.0558
|  | WOODSTOCK | CF |  |  |  | 17.8347 | 17.7863 | 17.7411 | 18.0968 | 17.9179 | 17.7295 | 17.5232 | 17.3484 | 17.2695 | 17.1905 | 16.8189 | 16.4653 | 15.9916 | 15.3968 | 15.2316 | 15.1105 | 15.0347 | 14.8316 | 14.6168 | 14.38 | 14.1821 | 14.0968 | 14.0116 | 13.6084 | 13.2084 | 12.6568 | 15.8842 | 15.72 | 15.5989 | 15.5379 | 15.3337 | 15.1189 | 14.8842 | 14.6853 | 14.6 | 14.5147 | 14.1126 | 13.7126 | 13.1632
BOTLEY WOOD GSP | NETLEY COMMON BSP | WOOLSTON | MINIMUM HEADROOM | SU 44145 11242 | YES | 0.072632 | 32.4011 | 32.2926 | 32.1842 | 32.0684 | 31.9284 | 31.7242 | 31.5211 | 31.3389 | 31.1642 | 30.9695 | 29.8211 | 28.8684 | 15.8916 | 30.2979 | 30.0863 | 29.8789 | 29.6326 | 29.3842 | 29.1663 | 28.9495 | 28.7547 | 28.5663 | 28.3526 | 27.0684 | 25.9968 | 25.0084 | 31.5253 | 31.4105 | 31.2958 | 31.1632 | 30.9221 | 30.7042 | 30.4863 | 30.2916 | 30.1032 | 29.8905 | 28.6063 | 27.5337 | 26.5453
|  | WOOLSTON | EE |  |  |  | 32.44 | 32.3547 | 32.2653 | 32.1695 | 32.0684 | 31.9632 | 31.7526 | 31.5937 | 31.4411 | 31.3042 | 30.4811 | 29.7358 | 29.0695 | 30.3884 | 30.2263 | 30.0589 | 29.8642 | 29.6653 | 29.4316 | 29.1926 | 29.0221 | 28.86 | 28.7137 | 27.7979 | 26.9579 | 26.2011 | 31.5674 | 31.4768 | 31.3832 | 31.2811 | 31.1737 | 30.9695 | 30.7295 | 30.56 | 30.3968 | 30.2505 | 29.3358 | 28.4947 | 27.7379
|  | WOOLSTON | HT |  |  |  | 32.4011 | 32.2926 | 32.1842 | 32.0684 | 31.9284 | 31.7242 | 31.5211 | 31.3389 | 31.1642 | 30.9695 | 29.8211 | 28.8684 | 27.9937 | 30.2979 | 30.0863 | 29.8789 | 29.6326 | 29.3842 | 29.1663 | 28.9495 | 28.7547 | 28.5663 | 28.3526 | 27.0684 | 25.9968 | 25.0084 | 31.5253 | 31.4105 | 31.2958 | 31.1632 | 30.9221 | 30.7042 | 30.4863 | 30.2916 | 30.1032 | 29.8905 | 28.6063 | 27.5337 | 26.5453
|  | WOOLSTON | HE |  |  |  | 32.4926 | 32.4305 | 32.3632 | 32.2884 | 32.2074 | 32.1211 | 32.0389 | 31.9611 | 31.8895 | 31.8253 | 31.3126 | 30.8021 | 15.8916 | 30.5116 | 30.4042 | 30.2926 | 30.1495 | 30 | 29.8137 | 29.6211 | 29.4979 | 29.3832 | 29.2842 | 28.7179 | 28.1389 | 27.6074 | 31.6242 | 31.56 | 31.4895 | 31.4105 | 31.3253 | 31.2326 | 31.1432 | 31.0358 | 30.92 | 30.8221 | 30.2558 | 29.6768 | 29.1442
|  | WOOLSTON | CF |  |  |  | 32.5232 | 32.4863 | 32.4484 | 32.4084 | 32.3674 | 32.3253 | 32.2821 | 32.2389 | 32.1968 | 32.1547 | 31.9674 | 31.6884 | 31.3758 | 30.5737 | 30.4989 | 30.4284 | 30.3568 | 30.2832 | 30.2084 | 30.1337 | 30.0505 | 29.9726 | 29.8937 | 29.4979 | 29.1158 | 28.7547 | 31.6568 | 31.6179 | 31.5779 | 31.5358 | 31.4926 | 31.4484 | 31.4032 | 31.3579 | 31.3137 | 31.2684 | 31.0358 | 30.6526 | 30.2926
MINETY GSP | SWINDON BSP | WOOTTON BASSETT | MINIMUM HEADROOM | SU 07587 81123 | YES | 0.60947 | 23.5 | 23.0432 | 22.5853 | 22.0495 | 21.1147 | 20.8179 | 19.6463 | 18.4274 | 17.1516 | 21.6042 | 18.2021 | 15.5368 | -0.20526 | 22.6063 | 22.0768 | 21.5484 | 20.9305 | 19.8674 | 19.5137 | 18.1747 | 16.7789 | 15.3158 | 20.9611 | 17.2042 | 14.3021 | 11.5674 | 23.1979 | 22.7284 | 22.2295 | 21.6116 | 20.5474 | 20.1842 | 18.8347 | 17.4253 | 15.9474 | 20.7821 | 16.9389 | 13.9495 | 11.1779
|  | WOOTTON BASSETT | EE |  |  |  | 23.7032 | 23.3484 | 22.9832 | 22.5789 | 21.94 | 20.8179 | 19.6463 | 18.4274 | 17.1516 | 22.7432 | 19.6126 | 19.52 | 17.5874 | 22.8474 | 22.4368 | 22.0179 | 21.5505 | 20.7979 | 19.5137 | 18.1747 | 16.7789 | 15.3158 | 22.2642 | 18.8442 | 19.8284 | 17.6432 | 23.3705 | 23.0442 | 22.6684 | 22.2316 | 21.4768 | 20.1842 | 18.8347 | 17.4253 | 15.9474 | 22.0589 | 18.5337 | 19.8347 | 17.6116
|  | WOOTTON BASSETT | HT |  |  |  | 23.5 | 23.0432 | 22.5853 | 22.0495 | 21.1147 | 26.3432 | 24.7547 | 23.5274 | 22.4947 | 21.6042 | 18.2021 | 15.5368 | 13.1211 | 22.6063 | 22.0768 | 21.5484 | 20.9305 | 19.8674 | 26.3863 | 24.5537 | 23.1484 | 21.9747 | 20.9726 | 17.2042 | 14.3021 | 11.5674 | 23.1979 | 22.7284 | 22.2295 | 21.6116 | 20.5474 | 26.2368 | 24.3958 | 22.9811 | 21.7958 | 20.7821 | 16.9389 | 13.9495 | 11.1779
|  | WOOTTON BASSETT | HE |  |  |  | 23.9768 | 23.7547 | 23.5189 | 23.2358 | 22.7347 | 21.7358 | 20.68 | 19.5516 | 18.4368 | 24.2263 | 21.8989 | 20.4579 | -0.20526 | 23.1705 | 22.9168 | 22.6495 | 22.3242 | 21.6979 | 20.5147 | 19.2926 | 17.9821 | 16.6853 | 23.8432 | 21.2221 | 19.6084 | 17.9253 | 23.5811 | 23.3989 | 23.2021 | 22.9305 | 22.3811 | 21.1895 | 19.9621 | 18.6442 | 17.3411 | 23.6716 | 21.0063 | 19.3589 | 17.6442
|  | WOOTTON BASSETT | CF |  |  |  | 24.1211 | 23.9895 | 23.8537 | 23.7147 | 23.5716 | 23.3968 | 23.2147 | 22.9663 | 22.6463 | 22.1232 | 25.6832 | 24.7705 | 23.8389 | 23.3379 | 23.1842 | 23.0274 | 22.8653 | 22.7011 | 22.5011 | 22.2895 | 21.9874 | 21.5811 | 20.9611 | 25.5011 | 24.4768 | 23.4168 | 23.6958 | 23.5916 | 23.4832 | 23.3716 | 23.2558 | 23.0937 | 22.9042 | 22.6463 | 22.2526 | 21.6284 | 25.3326 | 24.2895 | 23.2095
COWLEY GSP | OXFORD BSP | WOOTTON ROAD | MINIMUM HEADROOM | SU 49244 98269 | YES | 0.057895 | 17.5305 | 16.8674 | 16.1621 | 15.4758 | 14.6547 | 13.3884 | 11.5779 | 9.5832 | 7.6337 | 5.7232 | -3.6568 | -11.0495 | -26.4779 | 13.5105 | 12.5053 | 11.4137 | 10.3905 | 9.0905 | 7.5811 | 5.4884 | 3.1621 | 0.88632 | -1.3495 | -12.2474 | -20.7253 | -23.8042 | 14.5558 | 13.5516 | 12.4611 | 11.4389 | 10.14 | 8.6295 | 6.5358 | 4.2116 | 1.9337 | -0.30316 | -11.2126 | -19.7116 | -22.7989
|  | WOOTTON ROAD | EE |  |  |  | 17.7558 | 17.2126 | 16.6105 | 16.0263 | 15.3084 | 14.3347 | 12.6547 | 10.7537 | 8.8726 | 7.0368 | -1.8653 | -8.54 | -10.5568 | 13.8316 | 12.9905 | 12.0432 | 11.1632 | 10.0011 | 8.6211 | 6.6695 | 4.4484 | 2.2505 | 0.10105 | -10.2789 | -17.9389 | -20.2021 | 14.8758 | 14.0368 | 13.0905 | 12.2105 | 11.0505 | 9.6684 | 7.7147 | 5.4916 | 3.2926 | 1.1411 | -9.2642 | -16.96 | -19.2337
|  | WOOTTON ROAD | HT |  |  |  | 17.5305 | 16.8674 | 16.1621 | 15.4758 | 14.6547 | 13.3884 | 11.5779 | 9.5832 | 7.6337 | 5.7232 | -3.6568 | -11.0495 | -13.7937 | 13.5105 | 12.5053 | 11.4137 | 10.3905 | 9.0905 | 7.5811 | 5.4884 | 3.1621 | 0.88632 | -1.3495 | -12.2474 | -20.7253 | -23.8042 | 14.5558 | 13.5516 | 12.4611 | 11.4389 | 10.14 | 8.6295 | 6.5358 | 4.2116 | 1.9337 | -0.30316 | -11.2126 | -19.7116 | -22.7989
|  | WOOTTON ROAD | HE |  |  |  | 18.0063 | 17.6695 | 17.2095 | 16.7653 | 16.1747 | 15.4642 | 14.0779 | 12.3305 | 10.6095 | 8.9305 | 0.83579 | -5.0737 | -26.4779 | 14.2684 | 13.6368 | 12.8905 | 12.2032 | 11.2221 | 10.0126 | 8.2316 | 6.1779 | 4.1505 | 2.1695 | -7.3863 | -14.2526 | -15.8463 | 15.2537 | 14.6821 | 13.9368 | 13.2505 | 12.2705 | 11.0611 | 9.2789 | 7.2253 | 5.2 | 3.22 | -6.3368 | -13.2032 | -14.8074
|  | WOOTTON ROAD | CF |  |  |  | 18.1316 | 18.0074 | 17.7937 | 17.5674 | 17.2874 | 16.9621 | 16.4989 | 15.9411 | 15.1474 | 14.1347 | 8.8432 | 5.1379 | 4.28 | 14.5558 | 14.1958 | 13.8 | 13.4463 | 12.9789 | 12.4274 | 11.5789 | 10.5253 | 9.4 | 8.2053 | 1.9389 | -2.4663 | -3.4558 | 15.3789 | 15.24 | 14.8453 | 14.4916 | 14.0253 | 13.4737 | 12.6242 | 11.5716 | 10.4484 | 9.2537 | 2.9926 | -1.4126 | -2.4095
BRAMLEY (FLEE) | COXMOOR WOOD BSP | WRECCLESHAM | MINIMUM HEADROOM | SU 82093 44312 | YES | 0.074737 | 33.5316 | 33.1337 | 32.7126 | 32.3011 | 31.8779 | 31.4221 | 30.9726 | 30.5432 | 30.1305 | 29.7053 | 26.5832 | 24.2411 | 6.0989 | 30.4305 | 29.8653 | 29.24 | 28.6674 | 28.0789 | 27.4705 | 26.8853 | 26.2884 | 25.6958 | 25.1221 | 21.7263 | 19.2253 | 17.7263 | 29.4189 | 29.1242 | 28.8253 | 28.5084 | 28.1821 | 27.8211 | 27.4568 | 26.8811 | 26.2768 | 25.6916 | 22.2263 | 19.6453 | 18.1137
|  | WRECCLESHAM | EE |  |  |  | 33.7011 | 33.3947 | 33.0653 | 32.7274 | 32.3789 | 32.0021 | 31.6316 | 31.2768 | 30.9095 | 30.5547 | 28.6968 | 26.6958 | 25.1663 | 30.6463 | 30.2558 | 29.7768 | 29.3063 | 28.8274 | 28.3305 | 27.8579 | 27.4095 | 26.9158 | 26.4232 | 24.1463 | 22.0558 | 20.3758 | 29.5368 | 29.3095 | 29.0674 | 28.8084 | 28.54 | 28.2368 | 27.9326 | 27.64 | 27.3547 | 26.9779 | 24.6042 | 22.4042 | 20.6884
|  | WRECCLESHAM | HT |  |  |  | 33.5316 | 33.1337 | 32.7126 | 32.3011 | 31.8779 | 31.4221 | 30.9726 | 30.5432 | 30.1305 | 29.7053 | 26.5832 | 24.2411 | 22.8421 | 30.4305 | 29.8653 | 29.24 | 28.6674 | 28.0789 | 27.4705 | 26.8853 | 26.2884 | 25.6958 | 25.1221 | 21.7263 | 19.2253 | 17.7263 | 29.4189 | 29.1242 | 28.8253 | 28.5084 | 28.1821 | 27.8211 | 27.4568 | 26.8811 | 26.2768 | 25.6916 | 22.2263 | 19.6453 | 18.1137
|  | WRECCLESHAM | HE |  |  |  | 33.9326 | 33.7368 | 33.5158 | 33.28 | 33.0337 | 32.7526 | 32.4937 | 32.2463 | 31.9884 | 31.7495 | 30.7611 | 29.8842 | 6.0989 | 30.8653 | 30.6768 | 30.4347 | 30.1358 | 29.8032 | 29.4474 | 29.1242 | 28.8211 | 28.4684 | 28.1295 | 26.62 | 25.3232 | 24.1642 | 29.6979 | 29.5484 | 29.3832 | 29.1979 | 29.0011 | 28.7695 | 28.5495 | 28.3389 | 28.14 | 27.9642 | 27.1653 | 25.8379 | 24.6505
|  | WRECCLESHAM | CF |  |  |  | 34.0547 | 33.9442 | 33.8295 | 33.7116 | 33.5916 | 33.4558 | 33.32 | 33.18 | 33.0432 | 32.9095 | 32.2568 | 31.7516 | 31.3411 | 30.9853 | 30.8768 | 30.7674 | 30.6547 | 30.5242 | 30.3632 | 30.1789 | 29.9853 | 29.7947 | 29.6074 | 28.6505 | 27.7589 | 26.9821 | 29.7916 | 29.7095 | 29.6242 | 29.5368 | 29.4463 | 29.3411 | 29.2368 | 29.1316 | 29.0284 | 28.9274 | 28.4632 | 28.1937 | 27.5347
MINETY GSP | TOOTHILL BSP | WROUGHTON | MINIMUM HEADROOM | SU 14446 81504 | YES | 1.1053 | 25.5642 | 25.0337 | 24.1116 | 23.1453 | 22.1547 | 21.2011 | 20.3116 | 19.7821 | 19.4021 | 19.0337 | 17.64 | 16.2421 | 1.0611 | 21.7726 | 21.0916 | 20.0337 | 18.9274 | 17.7916 | 16.7011 | 15.6905 | 15.0968 | 14.6779 | 14.2705 | 12.7474 | 11.2053 | 9.78 | 22.5211 | 21.84 | 20.7811 | 19.6737 | 18.5368 | 17.4463 | 16.4316 | 15.8358 | 15.4137 | 15.0032 | 13.4611 | 11.8968 | 10.4621
|  | WROUGHTON | EE |  |  |  | 25.6179 | 25.2042 | 24.3326 | 23.4179 | 22.4737 | 21.5663 | 20.7263 | 20.2316 | 19.8737 | 19.5316 | 18.3547 | 17.2063 | 16.1916 | 21.8379 | 21.2768 | 20.2747 | 19.2232 | 18.1379 | 17.0989 | 16.14 | 15.5863 | 15.1895 | 14.8147 | 13.5421 | 12.2905 | 11.1463 | 22.5863 | 22.0253 | 21.0221 | 19.9695 | 18.8832 | 17.8421 | 16.88 | 16.3232 | 15.9232 | 15.5442 | 14.2453 | 12.9621 | 11.8074
|  | WROUGHTON | HT |  |  |  | 25.5642 | 25.0337 | 24.1116 | 23.1453 | 22.1547 | 21.2011 | 20.3116 | 19.7821 | 19.4021 | 19.0337 | 17.64 | 16.2421 | 14.9747 | 21.7726 | 21.0916 | 20.0337 | 18.9274 | 17.7916 | 16.7011 | 15.6905 | 15.0968 | 14.6779 | 14.2705 | 12.7474 | 11.2053 | 9.78 | 22.5211 | 21.84 | 20.7811 | 19.6737 | 18.5368 | 17.4463 | 16.4316 | 15.8358 | 15.4137 | 15.0032 | 13.4611 | 11.8968 | 10.4621
|  | WROUGHTON | HE |  |  |  | 25.6947 | 25.4305 | 24.6316 | 23.7853 | 22.9063 | 22.0558 | 21.28 | 20.8495 | 20.5547 | 20.2789 | 19.4295 | 18.6137 | 1.0611 | 21.9147 | 21.5242 | 20.5989 | 19.62 | 18.6063 | 17.6284 | 16.7368 | 16.2505 | 15.9221 | 15.6137 | 14.6789 | 13.7611 | 12.8695 | 22.6632 | 22.2716 | 21.3463 | 20.3684 | 19.3526 | 18.3737 | 17.48 | 16.9916 | 16.6621 | 16.3516 | 15.4063 | 14.4779 | 13.58
|  | WROUGHTON | CF |  |  |  | 25.7389 | 25.7 | 25.5211 | 25.1358 | 24.7547 | 24.3979 | 24.0347 | 23.8126 | 23.6474 | 23.4768 | 22.9042 | 22.4368 | 21.9495 | 21.9589 | 21.9158 | 21.6232 | 21.1789 | 20.7379 | 20.3284 | 19.9116 | 19.66 | 19.4758 | 19.2863 | 18.6547 | 18.1316 | 17.5779 | 22.7074 | 22.6642 | 22.3716 | 21.9263 | 21.4863 | 21.0758 | 20.6579 | 20.4053 | 20.22 | 20.0295 | 19.3947 | 18.8663 | 18.3063
AMERSHAM | LOUDWATER BSP | WYCOMBE MARSH | MINIMUM HEADROOM | SU 88582 91845 | YES | 0.078947 | 20.2621 | 20.0505 | 19.8368 | 19.6105 | 19.3747 | 19.1305 | 18.8853 | 18.6684 | 18.3063 | 17.9453 | 16.2663 | 14.7495 | -5.1263 | 19.3495 | 18.9821 | 18.2358 | 17.7221 | 17.3116 | 16.9032 | 16.4863 | 16.0916 | 15.6863 | 15.2926 | 13.4495 | 11.7642 | 10.2116 | 19.8821 | 19.6474 | 19.1505 | 18.6389 | 18.2284 | 17.8211 | 17.4042 | 17.0095 | 16.6053 | 16.2126 | 14.3716 | 12.6895 | 11.14
|  | WYCOMBE MARSH | EE |  |  |  | 20.3453 | 20.18 | 20.0053 | 19.8189 | 19.6242 | 19.4211 | 19.2253 | 19.0389 | 18.8579 | 18.6958 | 17.4484 | 16.2853 | 15.2505 | 19.4368 | 19.2547 | 18.5989 | 18.1674 | 17.8368 | 17.5042 | 17.1842 | 16.8653 | 16.52 | 16.1916 | 14.74 | 13.4453 | 12.2789 | 19.9716 | 19.7853 | 19.5137 | 19.0832 | 18.7526 | 18.4211 | 18.1011 | 17.7821 | 17.4379 | 17.1095 | 15.6611 | 14.3674 | 13.2042
|  | WYCOMBE MARSH | HT |  |  |  | 20.2621 | 20.0505 | 19.8368 | 19.6105 | 19.3747 | 19.1305 | 18.8853 | 18.6684 | 18.3063 | 17.9453 | 16.2663 | 14.7495 | 13.3642 | 19.3495 | 18.9821 | 18.2358 | 17.7221 | 17.3116 | 16.9032 | 16.4863 | 16.0916 | 15.6863 | 15.2926 | 13.4495 | 11.7642 | 10.2116 | 19.8821 | 19.6474 | 19.1505 | 18.6389 | 18.2284 | 17.8211 | 17.4042 | 17.0095 | 16.6053 | 16.2126 | 14.3716 | 12.6895 | 11.14
|  | WYCOMBE MARSH | HE |  |  |  | 20.4495 | 20.3326 | 20.2032 | 20.0611 | 19.9074 | 19.7442 | 19.5874 | 19.44 | 19.3021 | 19.1832 | 18.7789 | 18.1232 | -5.1263 | 19.5474 | 19.4168 | 19.06 | 18.7326 | 18.5 | 18.2611 | 18.0305 | 17.8021 | 17.5505 | 17.3147 | 16.3189 | 15.4589 | 14.7147 | 20.0832 | 19.9495 | 19.7958 | 19.6442 | 19.4147 | 19.1758 | 18.9463 | 18.7179 | 18.4663 | 18.2316 | 17.2368 | 16.3779 | 15.6368
|  | WYCOMBE MARSH | CF |  |  |  | 20.5116 | 20.4421 | 20.3716 | 20.2979 | 20.2211 | 20.1421 | 20.0621 | 19.9821 | 19.9042 | 19.8253 | 19.4758 | 19.3011 | 19.2032 | 19.6147 | 19.5368 | 19.4558 | 19.3779 | 19.2979 | 19.2042 | 19.0663 | 18.9232 | 18.7632 | 18.5968 | 17.7937 | 17.1684 | 16.6347 | 20.1505 | 20.0716 | 19.9884 | 19.9095 | 19.8295 | 19.7463 | 19.6632 | 19.58 | 19.4979 | 19.4137 | 18.7084 | 18.0853 | 17.5526
LOVEDEAN GSP | WYMERING BSP | WYMERING | MINIMUM HEADROOM | SU 64974 05375 | YES | 5.7516 | 60.04 | 61.8253 | 61.5968 | 61.3821 | 61.1632 | 60.9337 | 67.4442 | 66.3295 | 65.2537 | 64.5916 | 61.4463 | 58.2021 | -11.8874 | 57.8853 | 58.3895 | 58.1316 | 57.8926 | 57.6495 | 57.3989 | 65.5179 | 64.3021 | 63.1253 | 62.4179 | 59.1011 | 55.58 | 52.5074 | 57.3958 | 60.6958 | 60.4474 | 60.2168 | 59.9821 | 59.7379 | 67.0705 | 65.8232 | 64.6179 | 63.8947 | 60.5189 | 56.8905 | 53.66
|  | WYMERING | EE |  |  |  | 61.4705 | 68.3411 | 68.04 | 71.5368 | 70.9947 | 69.9379 | 68.8926 | 67.8653 | 66.8526 | 65.8768 | 63.3768 | 60.8684 | 58.6642 | 57.9758 | 71.0663 | 70.5253 | 69.9695 | 69.3979 | 68.2432 | 67.1032 | 65.9821 | 64.8758 | 63.8084 | 61.1716 | 58.5137 | 56.0884 | 60.3021 | 67.4895 | 67.1895 | 66.8716 | 71.04 | 69.8558 | 68.6874 | 67.5368 | 66.4011 | 65.3042 | 62.5926 | 59.8568 | 57.3611
|  | WYMERING | HT |  |  |  | 68.4958 | 68.1411 | 71.5189 | 70.8695 | 69.78 | 68.6095 | 67.4442 | 66.3295 | 65.2537 | 64.5916 | 61.4463 | 58.2021 | 55.3389 | 71.2979 | 70.6158 | 69.9389 | 69.2526 | 68.0632 | 66.7874 | 65.5179 | 64.3021 | 63.1253 | 62.4179 | 59.1011 | 55.58 | 52.5074 | 67.6442 | 67.2895 | 66.9316 | 70.8884 | 69.6747 | 68.3695 | 67.0705 | 65.8232 | 64.6179 | 63.8947 | 60.5189 | 56.8905 | 53.66
|  | WYMERING | HE |  |  |  | 61.8232 | 68.5916 | 68.3684 | 68.1211 | 67.8537 | 71.26 | 70.5295 | 69.8211 | 69.1347 | 68.4853 | 66.3653 | 64.6642 | -11.8874 | 58.3811 | 71.6484 | 71.2874 | 70.9011 | 70.4958 | 69.6779 | 68.8853 | 68.1137 | 67.3674 | 66.6589 | 64.3442 | 62.4379 | 60.7495 | 60.6895 | 67.74 | 67.5168 | 67.2695 | 67.0021 | 71.3221 | 70.5105 | 69.7211 | 68.9558 | 68.2295 | 65.8442 | 63.8568 | 62.1158
|  | WYMERING | CF |  |  |  | 60.04 | 61.8253 | 61.5968 | 61.3821 | 61.1632 | 60.9337 | 68.0884 | 71.7347 | 71.3221 | 70.8937 | 69.1105 | 68.1074 | 67.0821 | 57.8853 | 58.3895 | 58.1316 | 57.8926 | 57.6495 | 57.3989 | 70.6032 | 70.1663 | 69.7147 | 69.2474 | 67.3063 | 66.2137 | 65.0768 | 57.3958 | 60.6958 | 60.4474 | 60.2168 | 59.9821 | 59.7379 | 67.2368 | 67.0916 | 71.3505 | 70.8705 | 68.8832 | 67.7611 | 66.5874
COWLEY GSP | YARNTON BSP | YARNTON | MINIMUM HEADROOM | SP 48277 12108 | YES | 8.6811 | 41.6937 | 43.1032 | 42.4063 | 41.6842 | 40.9579 | 37.8032 | 37.0874 | 36.4337 | 35.8284 | 35.2579 | 32.7537 | 29.9716 | -28.0484 | 33.9326 | 33.0158 | 32.2663 | 31.4905 | 30.7126 | 27.48 | 26.7147 | 26.0168 | 25.3684 | 24.7558 | 22.0484 | 18.9547 | 14.4789 | 35.2653 | 34.3495 | 33.6011 | 32.8253 | 32.0474 | 28.8158 | 28.0516 | 27.3537 | 26.7042 | 26.0926 | 23.3832 | 20.2895 | 15.7895
|  | YARNTON | EE |  |  |  | 44.8526 | 43.5726 | 43.0179 | 42.4358 | 41.8421 | 38.8179 | 38.2432 | 37.6916 | 37.1653 | 36.6832 | 35.0105 | 32.8768 | 30.1368 | 34.9789 | 33.5274 | 32.9316 | 32.3084 | 31.6737 | 28.5811 | 27.9674 | 27.38 | 26.8179 | 26.3032 | 24.6768 | 22.3 | 19.1705 | 36.3095 | 34.86 | 34.2642 | 33.6421 | 33.0074 | 29.9147 | 29.3021 | 28.7137 | 28.1526 | 27.6368 | 26.0347 | 23.6568 | 20.5305
|  | YARNTON | HT |  |  |  | 44.5432 | 43.1032 | 42.4063 | 41.6842 | 40.9579 | 37.8032 | 37.0874 | 36.4337 | 35.8284 | 35.2579 | 32.7537 | 29.9716 | 26.1758 | 34.6421 | 33.0158 | 32.2663 | 31.4905 | 30.7126 | 27.48 | 26.7147 | 26.0168 | 25.3684 | 24.7558 | 22.0484 | 18.9547 | 14.4789 | 35.9726 | 34.3495 | 33.6011 | 32.8253 | 32.0474 | 28.8158 | 28.0516 | 27.3537 | 26.7042 | 26.0926 | 23.3832 | 20.2895 | 15.7895
|  | YARNTON | HE |  |  |  | 45.28 | 44.2053 | 43.8389 | 43.4453 | 43.0284 | 40.1684 | 39.7526 | 39.3579 | 38.9947 | 38.6663 | 37.1368 | 35.6884 | -28.0484 | 35.4442 | 34.2168 | 33.8263 | 33.4063 | 32.9653 | 30.0484 | 29.6105 | 29.1916 | 28.8074 | 28.46 | 26.6389 | 25.0095 | 22.5789 | 36.7747 | 35.5484 | 35.1589 | 34.7389 | 34.2979 | 31.3821 | 30.9432 | 30.5253 | 30.1411 | 29.7926 | 27.9432 | 26.3116 | 23.8832
|  | YARNTON | CF |  |  |  | 41.6937 | 43.8989 | 43.7789 | 43.6558 | 43.5284 | 41.1368 | 41.0021 | 40.8695 | 40.7379 | 40.6 | 39.4337 | 38.4705 | 37.1389 | 33.9326 | 33.8189 | 33.6989 | 33.5758 | 33.4484 | 31.0568 | 30.9221 | 30.7905 | 30.6589 | 30.5189 | 29.2505 | 28.1695 | 26.6337 | 35.2653 | 35.1516 | 35.0316 | 34.9084 | 34.7811 | 32.3895 | 32.2547 | 32.1221 | 31.9905 | 31.8516 | 30.5842 | 29.5032 | 27.9684
BRAMLEY (ANDO-THAT) | THATCHAM BSP | YATTENDON | MINIMUM HEADROOM | SU 53699 74307 | YES | 0.99579 | 17.1695 | 16.9779 | 16.7863 | 16.5421 | 16.08 | 15.5874 | 15.0947 | 14.8084 | 14.5874 | 14.3821 | 13.4747 | 12.4505 | -15.78 | 14.1484 | 13.9453 | 13.7432 | 13.4768 | 12.9295 | 12.3474 | 11.7642 | 11.44 | 11.1968 | 10.9695 | 9.9537 | 8.8095 | 7.6937 | 14.8926 | 14.6916 | 14.4916 | 14.2295 | 13.6968 | 13.1168 | 12.5347 | 12.2105 | 11.9663 | 11.7389 | 10.7211 | 9.5737 | 8.4589
|  | YATTENDON | EE |  |  |  | 17.2432 | 17.0968 | 16.9421 | 16.7779 | 16.4179 | 15.9758 | 15.5432 | 15.2947 | 15.1 | 14.9284 | 14.2211 | 13.4684 | 12.7158 | 14.2253 | 14.0716 | 13.9074 | 13.7347 | 13.3105 | 12.7853 | 12.2674 | 11.9874 | 11.7737 | 11.5842 | 10.7989 | 9.92 | 9.0695 | 14.9695 | 14.8168 | 14.6547 | 14.4832 | 14.0705 | 13.5547 | 13.0379 | 12.7568 | 12.5432 | 12.3537 | 11.5632 | 10.68 | 9.8295
|  | YATTENDON | HT |  |  |  | 17.1695 | 16.9779 | 16.7863 | 16.5421 | 16.08 | 15.5874 | 15.0947 | 14.8084 | 14.5874 | 14.3821 | 13.4747 | 12.4505 | 11.4558 | 14.1484 | 13.9453 | 13.7432 | 13.4768 | 12.9295 | 12.3474 | 11.7642 | 11.44 | 11.1968 | 10.9695 | 9.9537 | 8.8095 | 7.6937 | 14.8926 | 14.6916 | 14.4916 | 14.2295 | 13.6968 | 13.1168 | 12.5347 | 12.2105 | 11.9663 | 11.7389 | 10.7211 | 9.5737 | 8.4589
|  | YATTENDON | HE |  |  |  | 17.3274 | 17.2421 | 17.1463 | 17.0305 | 16.8653 | 16.4863 | 16.1137 | 15.9253 | 15.7916 | 15.6768 | 15.2442 | 14.7505 | -15.78 | 14.3095 | 14.2232 | 14.1242 | 14.0021 | 13.8189 | 13.3632 | 12.9147 | 12.7011 | 12.5547 | 12.4305 | 11.9547 | 11.3642 | 10.7747 | 15.0537 | 14.9674 | 14.8695 | 14.7474 | 14.5684 | 14.1253 | 13.6832 | 13.4695 | 13.3242 | 13.2 | 12.7221 | 12.1316 | 11.5411
|  | YATTENDON | CF |  |  |  | 17.3811 | 17.3379 | 17.2926 | 17.2463 | 17.1905 | 17.1305 | 16.9526 | 16.8484 | 16.7674 | 16.6853 | 16.3158 | 15.9937 | 15.6821 | 14.3653 | 14.3211 | 14.2747 | 14.2274 | 14.1705 | 14.1074 | 13.8916 | 13.7737 | 13.6842 | 13.5926 | 13.1779 | 12.7968 | 12.4126 | 15.1084 | 15.0653 | 15.0189 | 14.9726 | 14.9147 | 14.8526 | 14.6432 | 14.5263 | 14.4389 | 14.3495 | 13.9421 | 13.5642 | 13.1811
MELKSHAM GSP | CHIPPENHAM | YATTON KEYNELL | MINIMUM HEADROOM | ST 87300 75782 | YES | 0.021053 | 6.5747 | 6.4968 | 6.9095 | 6.7653 | 6.5253 | 5.9158 | 5.3147 | 4.58 | 4.4189 | 4.2547 | 2.0368 | -2.9621 | -28.5 | 5.1989 | 5.1179 | 5.1032 | 4.9516 | 4.6842 | 4.0105 | 3.3484 | 2.5295 | 2.3905 | 2.2505 | -0.12316 | -5.5168 | -6.8579 | 5.3589 | 5.24 | 5.0905 | 4.9368 | 4.6684 | 3.9768 | 3.2947 | 2.4558 | 2.2916 | 2.1253 | -0.52526 | -6.1905 | -7.6179
|  | YATTON KEYNELL | EE |  |  |  | 6.6042 | 6.5442 | 7.0253 | 6.9084 | 6.7895 | 6.6084 | 6.4011 | 6.1905 | 5.9705 | 5.7442 | 2.0368 | -2.9621 | -4.24 | 5.2295 | 5.1674 | 5.2316 | 5.1095 | 4.9853 | 4.8137 | 4.6253 | 4.4347 | 4.24 | 4.0421 | -0.12316 | -5.5168 | -6.8579 | 5.3905 | 5.3274 | 5.2168 | 5.0937 | 4.9663 | 4.7768 | 4.5611 | 4.3411 | 4.1126 | 3.8779 | -0.52526 | -6.1905 | -7.6179
|  | YATTON KEYNELL | HT |  |  |  | 6.5747 | 6.4968 | 6.9095 | 6.7653 | 6.5253 | 5.9158 | 5.3147 | 4.58 | 4.4189 | 4.2547 | 2.7074 | 0.42842 | -0.24947 | 5.1989 | 5.1179 | 5.1032 | 4.9516 | 4.6842 | 4.0105 | 3.3484 | 2.5295 | 2.3905 | 2.2505 | 0.52632 | -1.7884 | -2.4274 | 5.3589 | 5.24 | 5.0905 | 4.9368 | 4.6684 | 3.9768 | 3.2947 | 2.4558 | 2.2916 | 2.1253 | 0.22947 | -2.2842 | -3.0032
|  | YATTON KEYNELL | HE |  |  |  | 6.6474 | 6.6074 | 7.1979 | 7.1242 | 7.0484 | 6.9158 | 6.7926 | 6.6695 | 6.5484 | 6.4316 | 3.38 | -0.50947 | -28.5 | 5.2747 | 5.2337 | 5.4168 | 5.34 | 5.26 | 5.1358 | 5.0221 | 4.9084 | 4.7979 | 4.6916 | 1.2695 | -3.1895 | -4.2979 | 5.4358 | 5.3947 | 5.4042 | 5.3263 | 5.2463 | 5.1084 | 4.98 | 4.8526 | 4.7274 | 4.6063 | 1.0884 | -3.4421 | -4.6211
|  | YATTON KEYNELL | CF |  |  |  | 6.6716 | 6.6495 | 7.2958 | 7.2526 | 7.2116 | 7.1379 | 7.0674 | 6.9958 | 6.9284 | 6.8674 | 6.5526 | 5.7832 | 5.0274 | 5.3 | 5.2768 | 5.52 | 5.4737 | 5.4295 | 5.3611 | 5.2905 | 5.2232 | 5.1589 | 5.1 | 4.8 | 3.9684 | 3.1579 | 5.4611 | 5.4389 | 5.5074 | 5.4611 | 5.4168 | 5.34 | 5.2642 | 5.1895 | 5.1179 | 5.0537 | 4.7221 | 3.8484 | 2.9905
AXMINSTER | YEOVIL BSP | YEOVIL | MINIMUM HEADROOM | ST 57690 16833 | YES | 0.26316 | 29.0674 | 28.4821 | 27.9011 | 27.3716 | 26.8105 | 26.2674 | 25.7368 | 25.2463 | 24.7895 | 24.3568 | 21.9442 | 19.7242 | 4.9547 | 29.2642 | 28.8863 | 28.4011 | 28.3358 | 27.7863 | 27.2084 | 26.6421 | 26.1189 | 25.6305 | 25.1663 | 22.5211 | 20.1611 | 17.4737 | 29.42 | 28.9589 | 28.3379 | 27.7474 | 27.1442 | 26.5653 | 26 | 25.4768 | 24.9863 | 24.5221 | 21.8716 | 19.4032 | 16.7168
|  | YEOVIL | EE |  |  |  | 29.2326 | 28.8168 | 28.3368 | 27.8326 | 27.3674 | 26.9179 | 26.5611 | 26.1442 | 25.7442 | 25.3716 | 23.5105 | 26.4189 | 24.5768 | 29.4021 | 29.0989 | 28.7832 | 28.3358 | 27.9 | 27.4779 | 27.5389 | 27.0958 | 26.6705 | 26.2747 | 24.2421 | 29.5305 | 27.4453 | 29.5832 | 29.2284 | 28.8053 | 28.2674 | 27.7747 | 27.3053 | 26.8958 | 26.4526 | 26.0263 | 25.6295 | 23.5916 | 29.7979 | 27.7095
|  | YEOVIL | HT |  |  |  | 29.0674 | 28.4821 | 27.9011 | 27.3716 | 26.8105 | 26.2674 | 25.7368 | 25.2463 | 24.7895 | 24.3568 | 21.9442 | 19.7242 | 17.3432 | 29.2642 | 28.8863 | 28.4011 | 28.3895 | 27.7863 | 27.2084 | 26.6421 | 26.1189 | 25.6305 | 25.1663 | 22.5211 | 20.1611 | 17.4737 | 29.42 | 28.9589 | 28.3379 | 27.7474 | 27.1442 | 26.5653 | 26 | 25.4768 | 24.9863 | 24.5221 | 21.8716 | 19.4032 | 16.7168
|  | YEOVIL | HE |  |  |  | 29.4411 | 29.2095 | 28.9179 | 28.5442 | 28.2042 | 27.8705 | 27.5547 | 27.2589 | 26.9758 | 26.7253 | 25.4632 | 27.1042 | 4.9547 | 29.5947 | 29.38 | 29.1495 | 28.8958 | 28.6432 | 28.3495 | 28.0495 | 27.7663 | 27.4989 | 27.2611 | 26.0295 | 25.5453 | 24.0042 | 29.8105 | 29.56 | 29.2947 | 28.9968 | 28.6737 | 28.3253 | 27.9979 | 27.6895 | 27.3937 | 27.1316 | 25.7758 | 26.1053 | 25.4526
|  | YEOVIL | CF |  |  |  | 29.5705 | 29.4411 | 29.3063 | 29.1642 | 29.0011 | 28.7653 | 28.54 | 28.3389 | 28.1505 | 27.9621 | 26.9832 | 26.2137 | 25.3589 | 29.7126 | 29.5916 | 29.4653 | 29.3326 | 29.1895 | 29.0389 | 28.8905 | 28.7516 | 28.6168 | 28.4442 | 27.5411 | 26.7821 | 25.8411 | 29.9516 | 29.8137 | 29.6684 | 29.5168 | 29.3484 | 29.1716 | 28.9926 | 28.8147 | 28.6158 | 28.4168 | 27.3705 | 26.5305 | 25.5621
AXMINSTER | YEOVIL BSP | YETMINSTER | MINIMUM HEADROOM | ST 60294 10206 | YES | 0.052632 | 13.8084 | 13.5295 | 13.2474 | 12.9642 | 12.2937 | 11.1495 | 9.8011 | 8.1326 | 7.8789 | 7.6253 | 4.8221 | 0.26632 | -0.95368 | 11.8232 | 11.5221 | 11.22 | 10.9179 | 10.1632 | 8.9011 | 7.3884 | 5.4968 | 5.2705 | 5.0453 | 2.1705 | -2.7305 | -3.9611 | 12.2937 | 12.02 | 11.7168 | 11.4137 | 10.6579 | 9.3442 | 7.8084 | 5.8926 | 5.6389 | 5.3853 | 2.3179 | -2.8063 | -4.1242
|  | YETMINSTER | EE |  |  |  | 13.8189 | 13.7189 | 13.4905 | 13.2611 | 13.0242 | 12.7074 | 12.3663 | 12.0221 | 11.6726 | 11.3232 | 8.5442 | 2.1389 | -0.54 | 11.96 | 11.7274 | 11.4853 | 11.2421 | 10.9926 | 10.6842 | 10.3579 | 10.0347 | 9.7084 | 9.3874 | 6.6684 | -0.27684 | -3.2221 | 12.2937 | 12.2253 | 11.9811 | 11.7368 | 11.4842 | 11.1547 | 10.7979 | 10.4421 | 10.0789 | 9.7158 | 6.7 | -0.55579 | -3.5968
|  | YETMINSTER | HT |  |  |  | 13.8084 | 13.5295 | 13.2474 | 12.9642 | 12.2937 | 11.1495 | 9.8011 | 8.1326 | 7.8789 | 7.6253 | 4.8221 | 0.26632 | -0.95368 | 11.8232 | 11.5221 | 11.22 | 10.9179 | 10.1632 | 8.9011 | 7.3884 | 5.4968 | 5.2705 | 5.0453 | 2.1705 | -2.7305 | -3.9611 | 12.32 | 12.02 | 11.7168 | 11.4137 | 10.6579 | 9.3442 | 7.8084 | 5.8926 | 5.6389 | 5.3853 | 2.3179 | -2.8063 | -4.1242
|  | YETMINSTER | HE |  |  |  | 14.1032 | 13.9705 | 13.8274 | 13.68 | 13.5232 | 13.2947 | 13.0832 | 12.8726 | 12.6684 | 12.4758 | 10.8274 | 6.4453 | -0.18421 | 12.1432 | 12.0011 | 11.8484 | 11.6937 | 11.5274 | 11.3063 | 11.1 | 10.8989 | 10.7032 | 10.5211 | 8.8358 | 3.8663 | 1.4189 | 12.6411 | 12.4989 | 12.3463 | 12.1905 | 12.0242 | 11.7863 | 11.5663 | 11.3484 | 11.1368 | 10.9379 | 9.1116 | 4.0537 | 1.5274
|  | YETMINSTER | CF |  |  |  | 14.1937 | 14.1158 | 14.0358 | 13.9537 | 13.8705 | 13.7516 | 13.6347 | 13.5189 | 13.4042 | 13.2989 | 12.1558 | 10.9453 | 9.5726 | 12.24 | 12.1558 | 12.0705 | 11.9821 | 11.8916 | 11.7747 | 11.6589 | 11.5442 | 11.4305 | 11.3242 | 10.0853 | 8.7747 | 7.2653 | 12.7379 | 12.6537 | 12.5684 | 12.48 | 12.3895 | 12.2642 | 12.1411 | 12.0189 | 11.8979 | 11.7863 | 10.5084 | 9.1232 | 7.56
IVER 66kV |  | YIEWSLEY | MINIMUM HEADROOM | TQ 05643 80961 | YES | 1.4221 | 72.7853 | 72.2695 | 71.7484 | 70.7295 | 69.5147 | 68.1895 | 66.8874 | 65.5126 | 64.1863 | 63.1263 | 57.1821 | 51.8979 | 7.8442 | 60.9368 | 59.9168 | 58.7042 | 57.3179 | 55.7347 | 53.9905 | 52.3274 | 50.7632 | 49.2505 | 48.0947 | 41.5042 | 35.5263 | 29.9253 | 63.4653 | 62.4674 | 61.26 | 59.8463 | 58.2316 | 56.4516 | 54.7547 | 53.1589 | 51.6126 | 50.4684 | 43.8316 | 37.8516 | 32.2484
|  | YIEWSLEY | EE |  |  |  | 72.9737 | 72.5642 | 72.1316 | 71.6716 | 70.7989 | 69.7789 | 68.7853 | 67.82 | 66.8726 | 65.8674 | 61.6747 | 57.76 | 54.1863 | 61.3842 | 60.6074 | 59.6853 | 58.6347 | 57.4316 | 56.1158 | 54.8316 | 53.5811 | 52.3484 | 51.2021 | 46.5453 | 42.1442 | 38.0663 | 63.7632 | 63.1411 | 62.24 | 61.1916 | 59.9653 | 58.6232 | 57.3137 | 56.0389 | 54.7811 | 53.6116 | 48.9042 | 44.4705 | 40.3926
|  | YIEWSLEY | HT |  |  |  | 72.7853 | 72.2695 | 71.7484 | 70.7295 | 69.5147 | 68.1895 | 66.8874 | 65.5126 | 64.1863 | 63.1263 | 57.1821 | 51.8979 | 46.9768 | 60.9368 | 59.9168 | 58.7042 | 57.3179 | 55.7347 | 53.9905 | 52.3274 | 50.7632 | 49.2505 | 48.0947 | 41.5042 | 35.5263 | 29.9253 | 63.4653 | 62.4674 | 61.26 | 59.8463 | 58.2316 | 56.4516 | 54.7547 | 53.1589 | 51.6126 | 50.4684 | 43.8316 | 37.8516 | 32.2484
|  | YIEWSLEY | HE |  |  |  | 73.2221 | 72.9263 | 72.6011 | 72.2411 | 71.8537 | 71.2 | 70.3779 | 69.5884 | 68.8242 | 68.1305 | 64.8789 | 61.7705 | 7.8442 | 61.9589 | 61.4516 | 60.7853 | 59.9811 | 59.0137 | 57.9168 | 56.8495 | 55.82 | 54.8168 | 53.8958 | 49.9632 | 46.3179 | 43.3253 | 64.0116 | 63.7158 | 63.3116 | 62.5274 | 61.5758 | 60.4568 | 59.3684 | 58.3189 | 57.2947 | 56.3537 | 52.3295 | 48.54 | 45.5463
|  | YIEWSLEY | CF |  |  |  | 73.3695 | 73.1926 | 73.0084 | 72.8168 | 72.62 | 72.4158 | 72.2063 | 72.0021 | 71.6905 | 71.2432 | 69.1263 | 67.5158 | 65.9316 | 62.22 | 62 | 61.6147 | 61.1832 | 60.7 | 60.1737 | 59.6232 | 59.0642 | 58.4832 | 57.8958 | 55.0832 | 52.9147 | 51.0316 | 64.1589 | 63.9821 | 63.7979 | 63.6063 | 63.2316 | 62.7189 | 62.1832 | 61.6232 | 61.0305 | 60.4305 | 57.5579 | 55.3347 | 53.4011
LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | ZETLAND ROAD | MINIMUM HEADROOM | SU 60592 00043 | YES | 0.25263 | 25.2516 | 24.8726 | 24.4895 | 24.0832 | 23.6589 | 23.5147 | 23.0695 | 22.6053 | 22.0042 | 21.4326 | 18.6337 | 15.7063 | -17.7168 | 20.3853 | 19.6421 | 18.8642 | 17.9779 | 16.9958 | 16.5642 | 15.7011 | 14.8558 | 14.2147 | 13.6011 | 10.5558 | 7.3053 | 4.2242 | 21.0189 | 20.6179 | 19.9453 | 19.0947 | 18.1474 | 17.6979 | 16.8505 | 16.0221 | 15.3895 | 14.7874 | 11.7484 | 8.4968 | 5.4147
|  | ZETLAND ROAD | EE |  |  |  | 25.3895 | 25.0884 | 24.7695 | 24.4305 | 24.0726 | 23.6989 | 23.3379 | 22.9916 | 22.6547 | 22.3547 | 20.6263 | 18.3716 | 16.3137 | 20.5537 | 20.1368 | 19.5316 | 18.8663 | 18.0989 | 17.3653 | 16.6379 | 15.7979 | 15.1147 | 14.5905 | 12.7347 | 10.2253 | 7.9116 | 21.1674 | 20.8505 | 20.5147 | 19.9453 | 19.2063 | 18.4979 | 17.7905 | 16.9674 | 16.2979 | 15.7821 | 13.9263 | 11.4158 | 9.1
|  | ZETLAND ROAD | HT |  |  |  | 25.2516 | 24.8726 | 24.4895 | 24.0832 | 23.6589 | 23.5147 | 23.0695 | 22.6053 | 22.0042 | 21.4326 | 18.6337 | 15.7063 | 12.9547 | 20.3853 | 19.6421 | 18.8642 | 17.9779 | 16.9958 | 16.5642 | 15.7011 | 14.8558 | 14.2147 | 13.6011 | 10.5558 | 7.3053 | 4.2242 | 21.0189 | 20.6179 | 19.9453 | 19.0947 | 18.1474 | 17.6979 | 16.8505 | 16.0221 | 15.3895 | 14.7874 | 11.7484 | 8.4968 | 5.4147
|  | ZETLAND ROAD | HE |  |  |  | 25.5674 | 25.3474 | 25.1042 | 24.8368 | 24.5474 | 24.24 | 23.9442 | 23.6674 | 23.4084 | 23.1853 | 22.7126 | 21.7337 | -17.7168 | 20.7453 | 20.5168 | 20.2611 | 19.84 | 19.2547 | 18.6979 | 18.14 | 17.4358 | 16.9411 | 16.5926 | 15.5832 | 13.9084 | 12.4105 | 21.36 | 21.1305 | 20.8768 | 20.5958 | 20.2895 | 19.7758 | 19.2347 | 18.5611 | 18.0842 | 17.7411 | 16.7242 | 15.0916 | 13.6032
|  | ZETLAND ROAD | CF |  |  |  | 25.6705 | 25.5347 | 25.3937 | 25.2474 | 25.0958 | 24.94 | 24.78 | 24.6232 | 24.4663 | 24.3116 | 23.6189 | 23.5663 | 22.9095 | 20.8589 | 20.7168 | 20.5695 | 20.4158 | 20.2568 | 20.0516 | 19.7811 | 19.4768 | 19.1011 | 18.7126 | 16.9168 | 16.1516 | 15.0926 | 21.4737 | 21.3316 | 21.1832 | 21.0295 | 20.8705 | 20.7063 | 20.5389 | 20.3737 | 20.1705 | 19.7926 | 18.0705 | 17.3021 | 16.2758

## BSP Headroom Dem
Grid Supply Point | Bulk Supply Point |  | Scenario | Grid Reference | Upstream Constraint (YES / NO) | Outstanding Contracted Demand (MVA) | Demand Headroom Winter (MVA) | [12 empty] | Demand Headroom Summer (MVA) | [12 empty] | Demand Headroom Spring/Autumn (MVA)
[7 empty] | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050
BRAMLEY (FLEE) | ALDERSHOT BSP | ALDERSHOT BSP | MINIMUM HEADROOM | SU 85922 48779 | YES | 26.869 | -15.032 | -19.78 | -25.5585 | -31.1912 | -36.8738 | -43.7616 | -51.8769 | -60.6606 | -69.1218 | -75.4861 | -105.0636 | -126.2647 | -137.8238 | 15.3884 | 11.968 | 7.7996 | 3.9731 | 0.17309 | -4.7177 | -10.3585 | -16.6953 | -22.9524 | -27.6555 | -51.4545 | -79.3626 | -145.0667 | -10.3014 | -14.6249 | -19.9198 | -24.9402 | -29.9718 | -36.2851 | -43.7565 | -51.9575 | -59.8738 | -65.7208 | -92.4024 | -110.9402 | -120.4514
|  | ALDERSHOT BSP | EE |  |  |  | -15.032 | -19.78 | -25.5585 | -31.1912 | -36.8738 | -43.7616 | -51.8769 | -60.6606 | -69.1218 | -75.4861 | -105.0636 | -123.7636 | -136.7534 | 15.3884 | 11.968 | 7.7996 | 3.9731 | 0.17309 | -4.7177 | -10.3585 | -16.6953 | -22.9524 | -27.6555 | -51.4545 | -74.281 | -107.5943 | -10.3014 | -14.6249 | -19.9198 | -24.9402 | -29.9718 | -36.2851 | -43.7565 | -51.9575 | -59.8738 | -65.7208 | -92.4024 | -108.8014 | -119.6892
|  | ALDERSHOT BSP | HT |  |  |  | -12.8443 | -16.7432 | -21.4126 | -26.88 | -32.8994 | -38.3412 | -44.7249 | -50.933 | -58.2708 | -65.7453 | -102.7963 | -126.2647 | -137.8238 | 17.4547 | 15.0945 | 12.2639 | 9.067 | 5.5384 | 2.4098 | -1.0994 | -4.5636 | -8.981 | -13.5392 | -34.7861 | -46.6075 | -51.5341 | -8.1371 | -11.6075 | -15.7922 | -20.6177 | -25.9718 | -30.8238 | -36.5636 | -42.1881 | -48.9534 | -55.8636 | -89.879 | -110.9402 | -120.4514
|  | ALDERSHOT BSP | HE |  |  |  | -13.1361 | -17.0361 | -21.7841 | -27.2412 | -33.3116 | -38.8606 | -44.8596 | -50.7545 | -57.7473 | -64.8861 | -99.7687 | -120.8779 | -129.0555 | 16.8864 | 14.1394 | 10.7966 | 7.0925 | 2.9772 | -0.8412 | -4.9841 | -9.2045 | -14.4769 | -19.9841 | -49.4034 | -74.6259 | -105.8402 | -8.43 | -11.9187 | -16.1932 | -21.0432 | -26.4626 | -31.4483 | -36.8698 | -42.2514 | -48.7616 | -55.4157 | -87.6402 | -106.4432 | -113.082
|  | ALDERSHOT BSP | CF |  |  |  | -11.5749 | -14.2626 | -17.5677 | -21.3198 | -25.2494 | -29.1249 | -31.7361 | -35.0024 | -37.3687 | -41.0034 | -65.1106 | -89.1718 | -109.4687 | 17.7864 | 15.5915 | 12.9659 | 10.0904 | 7.0343 | 3.717 | 0.85166 | -2.7402 | -5.6647 | -9.7851 | -38.1922 | -79.3626 | -145.0667 | -6.9738 | -9.3616 | -12.2953 | -15.583 | -19.0402 | -22.5392 | -24.88 | -27.9167 | -30.0534 | -33.4698 | -56.0698 | -78.1187 | -96.3075
BRAMLEY (FLEE) | ALTON | ALTON | MINIMUM HEADROOM | SU 72730 39772 | YES | 41.832 | -16.3913 | -20.8852 | -25.4893 | -30.7056 | -43.6699 | -48.5087 | -55.0087 | -62.7699 | -69.825 | -75.078 | -105.0372 | -125.9658 | -137.9025 | 16.512 | 13.515 | 10.3283 | 6.4926 | -5.186 | -8.6289 | -12.8829 | -18.2768 | -23.1768 | -26.7921 | -48.4605 | -69.9503 | -124.3054 | -14.8676 | -18.8329 | -23.1125 | -28.1452 | -40.7574 | -45.2054 | -51.1962 | -58.3329 | -64.8513 | -69.7605 | -96.4482 | -114.6238 | -124.6431
|  | ALTON | EE |  |  |  | -16.3913 | -20.8852 | -25.4893 | -30.7056 | -43.6699 | -48.5087 | -55.0087 | -62.7699 | -69.825 | -75.078 | -105.0127 | -122.3699 | -134.9995 | 16.512 | 13.515 | 10.3283 | 6.4926 | -5.186 | -8.6289 | -12.8829 | -18.2768 | -23.1768 | -26.7921 | -48.4605 | -67.7799 | -95.6666 | -14.8676 | -18.8329 | -23.1125 | -28.1452 | -40.7574 | -45.2054 | -51.1962 | -58.3329 | -64.8513 | -69.7605 | -96.4482 | -111.4687 | -122.2187
|  | ALTON | HT |  |  |  | -14.724 | -18.628 | -23.1087 | -28.0607 | -39.926 | -43.9515 | -49.7668 | -56.1148 | -62.7515 | -69.4087 | -105.0372 | -125.9658 | -137.9025 | 18.263 | 16.0293 | 13.3222 | 10.0599 | -0.18804 | -2.4809 | -5.4615 | -8.9197 | -12.7289 | -16.6482 | -36.7064 | -46.9584 | -52.3074 | -13.2217 | -16.6482 | -20.7278 | -25.4676 | -36.9789 | -40.6176 | -45.8605 | -51.6401 | -57.7278 | -63.8258 | -96.1676 | -114.6238 | -124.6431
|  | ALTON | HE |  |  |  | -14.7791 | -18.5209 | -22.9087 | -27.7362 | -39.4331 | -43.2229 | -48.2505 | -53.8291 | -59.6801 | -65.2923 | -98.1127 | -115.8995 | -124.1484 | 17.962 | 15.5956 | 12.6109 | 9.0956 | -1.4136 | -3.9482 | -7.1697 | -10.9993 | -15.1472 | -19.2176 | -44.7238 | -64.8493 | -91.1533 | -13.288 | -16.5472 | -20.5625 | -25.1993 | -36.5472 | -39.9931 | -44.5421 | -49.6554 | -55.0554 | -60.2217 | -90.0472 | -105.6136 | -112.3207
|  | ALTON | CF |  |  |  | -12.9117 | -14.6668 | -17.4454 | -21.0097 | -32.4025 | -34.8403 | -37.6433 | -41.1576 | -44.1036 | -47.077 | -67.978 | -90.6801 | -109.0729 | 18.8609 | 17.3783 | 15.0977 | 12.1201 | 1.3181 | -0.55029 | -2.9829 | -6.2554 | -9.135 | -12.2452 | -35.087 | -69.9503 | -124.3054 | -11.7238 | -13.3309 | -15.9207 | -19.3789 | -30.4748 | -32.5901 | -35.0584 | -38.2646 | -40.9768 | -43.7197 | -62.987 | -83.4646 | -99.7013
MELKSHAM GSP | AMESBURY | AMESBURY | MINIMUM HEADROOM | SU 15842 42724 | YES | 5.623 | 59.4462 | 58.6615 | 57.6473 | 56.6013 | 55.8258 | 54.6768 | 53.3462 | 51.9738 | 50.2656 | 49.1636 | 43.4993 | 39.8258 | 37.6768 | 68.2148 | 67.7199 | 67.0668 | 66.3954 | 65.8985 | 65.1556 | 64.3658 | 63.5444 | 62.4832 | 61.726 | 57.273 | 51.4036 | 37.9026 | 60.6291 | 59.872 | 58.8475 | 57.8179 | 57.1179 | 55.9628 | 54.775 | 53.5577 | 51.9168 | 50.9771 | 46.5597 | 43.6903 | 42.0342
|  | AMESBURY | EE |  |  |  | 59.4462 | 58.6615 | 57.6473 | 56.6013 | 55.8258 | 54.6768 | 53.3462 | 51.9738 | 50.2656 | 49.1636 | 43.4993 | 40.2513 | 38.6217 | 68.2148 | 67.7199 | 67.0668 | 66.3954 | 65.8985 | 65.1556 | 64.3658 | 63.5444 | 62.4832 | 61.726 | 57.273 | 52.673 | 45.9801 | 60.6291 | 59.872 | 58.8475 | 57.8179 | 57.1179 | 55.9628 | 54.775 | 53.5577 | 51.9168 | 50.9771 | 46.5597 | 44.0822 | 42.7658
|  | AMESBURY | HT |  |  |  | 59.8789 | 59.233 | 58.4034 | 57.633 | 56.7646 | 55.8585 | 54.784 | 53.2758 | 51.7901 | 50.8922 | 43.7901 | 39.8258 | 37.6768 | 68.5485 | 68.225 | 67.7822 | 67.372 | 66.9015 | 66.4128 | 65.9128 | 65.1291 | 64.3628 | 63.9822 | 60.3903 | 58.3893 | 57.2475 | 61.1383 | 60.5607 | 59.7689 | 59.0668 | 58.2383 | 57.3781 | 56.5036 | 55.1128 | 53.7189 | 53.0709 | 46.8577 | 43.6903 | 42.0342
|  | AMESBURY | HE |  |  |  | 59.9044 | 59.2891 | 58.5136 | 57.8105 | 56.9768 | 56.1207 | 55.2136 | 53.8411 | 52.485 | 51.7626 | 45.2238 | 42.0871 | 40.6268 | 68.4975 | 68.0995 | 67.5934 | 67.122 | 66.5658 | 65.9913 | 65.4311 | 64.5617 | 63.674 | 63.1924 | 58.1709 | 53.5873 | 46.9903 | 61.1577 | 60.5903 | 59.8505 | 59.2036 | 58.4077 | 57.6056 | 56.8587 | 55.5801 | 54.2985 | 53.7995 | 48.1138 | 45.6658 | 44.5056
|  | AMESBURY | CF |  |  |  | 60.132 | 59.6677 | 59.1666 | 58.6442 | 58.1493 | 57.5391 | 56.8779 | 56.135 | 55.6768 | 54.8585 | 50.7871 | 46.533 | 42.6493 | 68.6087 | 68.2556 | 67.876 | 67.4577 | 67.0403 | 66.5087 | 65.9097 | 65.222 | 64.7209 | 63.9424 | 59.3117 | 51.4036 | 37.9026 | 61.3638 | 60.9148 | 60.4322 | 59.9199 | 59.4526 | 58.8413 | 58.2077 | 57.4699 | 57.0852 | 56.2699 | 52.573 | 49.0566 | 46.0913
MELKSHAM GSP | ANDOVER BSP | ANDOVER BSP | MINIMUM HEADROOM | SU 35334 46598 | YES | 14.212 | 41.556 | 154.4734 | 152.055 | 149.3815 | 146.2693 | 143.0795 | 138.6264 | 133.5479 | 127.8591 | 123.5509 | 100.8142 | 85.1479 | 73.8979 | 55.6611 | 164.0611 | 162.1621 | 160.0479 | 157.7652 | 155.3856 | 152.3713 | 148.8672 | 144.3775 | 139.8295 | 120.6795 | 103.4989 | 74.9428 | 41.6101 | 151.6019 | 149.4734 | 147.0897 | 144.3907 | 141.557 | 137.5713 | 132.8897 | 127.4999 | 122.7326 | 99.6244 | 85.7672 | 75.6111
|  | ANDOVER BSP | EE |  |  |  | 41.556 | 154.4734 | 152.055 | 149.3815 | 146.2693 | 143.0795 | 138.6264 | 133.5479 | 127.8591 | 123.5509 | 103.8938 | 87.7744 | 78.1295 | 55.6611 | 164.0611 | 162.1621 | 160.0479 | 157.7652 | 155.3856 | 152.3713 | 148.8672 | 144.6611 | 141.6621 | 126.5458 | 107.9907 | 88.1356 | 41.6101 | 151.6019 | 149.4734 | 147.0897 | 144.3907 | 141.557 | 137.5713 | 132.8897 | 127.4999 | 123.5703 | 105.3356 | 89.3652 | 80.3795
|  | ANDOVER BSP | HT |  |  |  | 42.4938 | 155.404 | 153.303 | 150.8642 | 148.0489 | 144.2826 | 139.6326 | 134.9377 | 131.0693 | 126.2417 | 103.106 | 85.1479 | 73.8979 | 56.6632 | 165.2621 | 163.8519 | 162.1366 | 160.4172 | 157.6172 | 154.7601 | 151.8285 | 149.7326 | 146.6213 | 132.3785 | 119.9642 | 112.1193 | 42.4683 | 152.456 | 150.5724 | 148.3621 | 145.9672 | 142.4458 | 138.1836 | 133.8264 | 130.3795 | 125.8468 | 104.2275 | 86.6183 | 75.6111
|  | ANDOVER BSP | HE |  |  |  | 42.3907 | 155.5836 | 153.4254 | 150.8448 | 148.0305 | 144.0979 | 139.9795 | 135.6458 | 129.8438 | 124.354 | 100.8142 | 85.8172 | 75.9877 | 56.4019 | 165.0652 | 163.354 | 161.206 | 159.0581 | 155.6346 | 152.6121 | 149.4295 | 144.3775 | 139.8295 | 120.6795 | 103.4989 | 81.0856 | 42.3581 | 152.6101 | 150.6356 | 148.2152 | 145.703 | 141.8703 | 138.0856 | 134.0224 | 128.1336 | 122.7326 | 99.6244 | 85.7672 | 75.8866
|  | ANDOVER BSP | CF |  |  |  | 43.0795 | 156.8611 | 155.6764 | 154.1662 | 152.406 | 150.6111 | 148.7938 | 146.957 | 145.1611 | 142.8877 | 125.2672 | 110.5989 | 97.2479 | 56.7907 | 165.7458 | 164.6999 | 163.355 | 161.7121 | 159.8938 | 157.906 | 155.8917 | 153.8724 | 151.4611 | 134.3101 | 110.9581 | 74.9428 | 42.9826 | 153.7581 | 152.7377 | 151.3948 | 149.8132 | 148.1744 | 146.4836 | 144.8081 | 143.156 | 141.0866 | 125.3132 | 110.1244 | 97.7775
MANNINGTON GSP | ARNEWOOD | ARNEWOOD | MINIMUM HEADROOM | SZ 26094 97294 | YES | 6.679 | 26.6636 | 25.0626 | 23.2687 | 97.1024 | 95.082 | 92.5167 | 88.4473 | 84.4698 | 80.1973 | 77.0728 | 60.8953 | 48.4044 | 41.3249 | 38.8024 | 37.5279 | 36.131 | 108.0044 | 106.4432 | 104.4177 | 101.6779 | 98.9473 | 95.8902 | 93.782 | 82.7636 | 69.4085 | 36.2963 | 28.0534 | 26.4769 | 24.7596 | 97.5044 | 95.6136 | 93.1432 | 89.3749 | 85.6922 | 81.6667 | 78.9014 | 65.1555 | 54.0687 | 48.2024
|  | ARNEWOOD | EE |  |  |  | 26.6636 | 25.0626 | 23.2687 | 97.1024 | 95.082 | 92.5167 | 88.4473 | 84.4698 | 80.1973 | 77.0728 | 61.9044 | 51.0555 | 42.4738 | 38.8024 | 37.5279 | 36.131 | 108.0044 | 106.4432 | 104.4177 | 101.6779 | 98.9473 | 95.8902 | 93.782 | 82.7636 | 70.9677 | 53.5534 | 28.0534 | 26.4769 | 24.7596 | 97.5044 | 95.6136 | 93.1432 | 89.3749 | 85.6922 | 81.6667 | 78.9014 | 65.9238 | 56.4483 | 49.1953
|  | ARNEWOOD | HT |  |  |  | 27.5126 | 26.0759 | 24.4779 | 98.2514 | 96.4871 | 94.6157 | 91.2616 | 87.48 | 83.5708 | 79.6565 | 60.8953 | 48.4044 | 41.3249 | 39.7555 | 38.8351 | 37.8249 | 109.8575 | 108.8177 | 107.7279 | 106.0789 | 103.9677 | 101.7432 | 99.4606 | 89.5096 | 83.832 | 81.0044 | 29.0075 | 27.6524 | 26.1422 | 98.833 | 97.2381 | 95.5616 | 92.6596 | 89.2208 | 85.6524 | 82.0432 | 65.1555 | 54.0687 | 48.2024
|  | ARNEWOOD | HE |  |  |  | 27.5351 | 26.3187 | 24.7575 | 98.6983 | 97.0891 | 95.3606 | 92.6167 | 89.4024 | 86.0677 | 82.7453 | 66.684 | 55.5208 | 50.1402 | 39.5963 | 38.6585 | 37.4412 | 109.3606 | 108.1504 | 106.8677 | 105.1381 | 102.8993 | 100.4983 | 98.0106 | 85.18 | 72.8932 | 56.7963 | 29.0055 | 27.8493 | 26.3718 | 99.1953 | 97.7442 | 96.1912 | 93.8106 | 90.8524 | 87.7749 | 84.6728 | 70.2198 | 60.4575 | 56.0279
|  | ARNEWOOD | CF |  |  |  | 28.1218 | 27.4238 | 26.5504 | 101.0453 | 99.9432 | 98.9912 | 97.9677 | 96.833 | 95.2412 | 93.5585 | 82.8065 | 71.0044 | 60.1065 | 39.8871 | 39.1677 | 38.2891 | 110.4187 | 109.3177 | 108.2708 | 107.0779 | 105.7096 | 103.9034 | 101.9636 | 89.0718 | 69.4085 | 36.2963 | 29.5463 | 28.8493 | 27.984 | 101.3157 | 100.2524 | 99.3902 | 98.4728 | 97.4361 | 95.8942 | 94.2718 | 84.0932 | 73.7136 | 64.4422
BRAMLEY (BASI) | BASINGSTOKE T1A & T2A | BASINGSTOKE T1A & T2A | MINIMUM HEADROOM | SU 65132 52710 | YES | 29.469 | 22.1355 | 21.5835 | 20.7437 | 19.8539 | 18.9988 | 17.8488 | 16.4978 | 14.4396 | 12.2488 | 10.3223 | 2.9468 | -1.3645 | -3.5747 | 23.8855 | 23.4743 | 22.8345 | 22.2192 | 21.7825 | 20.9855 | 20.1804 | 18.861 | 17.4427 | 16.2835 | 11.0355 | 5.7447 | -7.6338 | 21.1355 | 20.6008 | 19.8855 | 19.1886 | 18.7162 | 17.6927 | 16.4202 | 14.659 | 12.8631 | 11.3141 | 4.8743 | 0.33146 | -2.1869
|  | BASINGSTOKE T1A & T2A | EE |  |  |  | 22.1355 | 21.5835 | 20.7437 | 19.8539 | 18.9988 | 17.8488 | 16.4978 | 14.4396 | 12.2488 | 10.3223 | 3.158 | 0.060029 | -2.3583 | 23.8855 | 23.4743 | 22.8345 | 22.2192 | 21.7825 | 20.9855 | 20.1804 | 18.861 | 17.4427 | 16.2835 | 11.0355 | 6.2294 | -0.81038 | 21.1355 | 20.6008 | 19.8855 | 19.1886 | 18.7162 | 17.6927 | 16.4202 | 14.659 | 12.8631 | 11.3141 | 5.1121 | 1.161 | -1.7594
|  | BASINGSTOKE T1A & T2A | HT |  |  |  | 22.3968 | 22.0396 | 21.5662 | 20.8998 | 20.0457 | 19.0049 | 17.6692 | 15.8264 | 13.9294 | 11.958 | 3.3498 | -1.0634 | -3.5257 | 24.1315 | 23.8253 | 23.5131 | 23.1478 | 22.6162 | 21.9906 | 21.2213 | 20.1151 | 19.2294 | 18.1621 | 13.5121 | 11.5406 | 10.3662 | 21.411 | 20.9151 | 20.3957 | 19.8498 | 19.1427 | 18.3304 | 16.9886 | 15.2651 | 13.7845 | 12.1345 | 4.8743 | 0.33146 | -2.1869
|  | BASINGSTOKE T1A & T2A | HE |  |  |  | 22.3835 | 22.0947 | 21.5121 | 20.8253 | 20.0335 | 19.0498 | 17.8866 | 16.1784 | 14.257 | 12.1631 | 2.9468 | -1.3645 | -3.5747 | 24.0917 | 23.7927 | 23.3743 | 22.9355 | 22.3988 | 21.7764 | 21.1498 | 20.0682 | 19.109 | 17.9059 | 12.1151 | 7.1866 | 0.62533 | 21.4202 | 21.0131 | 20.4896 | 19.9866 | 19.4029 | 18.7284 | 17.757 | 16.1968 | 14.6131 | 12.8784 | 4.9039 | 0.94778 | -1.093
|  | BASINGSTOKE T1A & T2A | CF |  |  |  | 22.607 | 22.4294 | 22.2396 | 21.9692 | 21.6417 | 21.157 | 20.5733 | 19.7508 | 18.9376 | 17.9253 | 10.9713 | 4.7947 | 0.017171 | 24.2406 | 24.0141 | 23.7529 | 23.3662 | 22.9866 | 22.508 | 21.9417 | 21.1957 | 20.6457 | 19.7906 | 13.8141 | 5.7447 | -7.6338 | 21.6815 | 21.4366 | 21.1784 | 20.8559 | 20.5539 | 20.1978 | 19.7804 | 19.2039 | 18.7284 | 17.7621 | 11.5968 | 6.5743 | 2.1723
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | BASINGSTOKE T1B & T2B | MINIMUM HEADROOM | SU 65132 52711 | YES | 20.153 | 49.429 | 48.0504 | 46.1004 | 43.8188 | 41.1688 | 38.5056 | 34.7484 | 29.6637 | 24.8749 | 20.1004 | 0.24229 | -11.0261 | -17.32 | 52.9578 | 52.0456 | 50.6782 | 49.068 | 47.2823 | 45.5762 | 43.168 | 40.0088 | 37.1823 | 34.568 | 21.166 | 10.2313 | -18.4861 | 44.918 | 43.7027 | 41.9558 | 39.9007 | 37.5333 | 35.1782 | 31.7486 | 27.1547 | 23.0629 | 19.3711 | 1.9047 | -7.5698 | -12.6769
|  | BASINGSTOKE T1B & T2B | EE |  |  |  | 49.429 | 48.0504 | 46.1004 | 43.8188 | 41.1688 | 38.5056 | 34.7484 | 29.6637 | 24.8749 | 20.5709 | 1.7892 | -8.973 | -16.4883 | 52.9578 | 52.0456 | 50.6782 | 49.068 | 47.2823 | 45.5762 | 43.168 | 40.0088 | 37.1823 | 34.568 | 21.166 | 10.6241 | -4.4881 | 44.918 | 43.7027 | 41.9558 | 39.9007 | 37.5333 | 35.1782 | 31.7486 | 27.1547 | 23.0629 | 19.3711 | 3.0119 | -5.7463 | -11.9871
|  | BASINGSTOKE T1B & T2B | HT |  |  |  | 50.127 | 48.6709 | 46.8382 | 45.1494 | 42.9127 | 40.1841 | 34.9443 | 29.7862 | 25.0076 | 20.1004 | 0.24229 | -11.0261 | -17.32 | 53.7517 | 52.9292 | 51.87 | 51.0007 | 49.7904 | 48.219 | 45.5731 | 42.8558 | 40.3588 | 37.5649 | 26.6904 | 21.5894 | 19.0609 | 45.6221 | 44.3343 | 42.7241 | 41.2629 | 39.316 | 36.8741 | 32.3843 | 27.9109 | 23.7609 | 19.4119 | 1.9047 | -7.5698 | -12.6769
|  | BASINGSTOKE T1B & T2B | HE |  |  |  | 50.1351 | 48.777 | 47.0341 | 45.4484 | 43.3229 | 40.8331 | 37.9086 | 34.0831 | 30.2892 | 26.4372 | 8.13 | -3.8955 | -8.9404 | 53.5976 | 52.6843 | 51.5098 | 50.4904 | 49.1364 | 47.5292 | 45.6578 | 43.2486 | 40.8894 | 38.3119 | 24.4272 | 13.0323 | -1.132 | 45.62 | 44.4221 | 42.8874 | 41.5221 | 39.6782 | 37.4935 | 34.8731 | 31.4956 | 28.1925 | 24.7639 | 8.5231 | -1.2544 | -5.3238
|  | BASINGSTOKE T1B & T2B | CF |  |  |  | 50.8617 | 50.2331 | 49.3831 | 48.4127 | 47.4943 | 45.6831 | 43.2351 | 41.3596 | 39.6382 | 37.929 | 25.4004 | 9.9902 | 0.049429 | 53.9537 | 53.3027 | 52.5262 | 51.6292 | 50.8935 | 49.5088 | 47.6792 | 45.9741 | 44.2986 | 42.5119 | 30.0639 | 10.2313 | -18.4861 | 46.2476 | 45.6588 | 44.8864 | 44.0139 | 43.2517 | 41.718 | 39.6772 | 37.9996 | 36.4435 | 34.8292 | 23.5741 | 10.3456 | 1.8323
BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | BASINGSTOKE T3 & T4 | MINIMUM HEADROOM | SU 65132 52712 | YES | 30.562 | 72.2733 | 70.9322 | 69.2771 | 67.1557 | 65.1649 | 62.6547 | 51.5755 | 48.2633 | 44.8224 | 41.8714 | 30.0612 | 23.6326 | 19.6582 | 75.2559 | 74.1455 | 72.9486 | 71.4975 | 70.1996 | 68.4894 | 58.3082 | 56.1133 | 53.8204 | 51.9153 | 43.3888 | 34.5653 | 13.5051 | 70.2314 | 68.9843 | 67.5353 | 65.7006 | 64.0047 | 61.7771 | 50.998 | 48.0928 | 45.0816 | 42.4959 | 31.9602 | 26.549 | 23.1765
|  | BASINGSTOKE T3 & T4 | EE |  |  |  | 72.2733 | 70.9322 | 69.2771 | 67.1557 | 65.1649 | 62.6547 | 51.5755 | 48.2633 | 44.8224 | 41.8714 | 30.0612 | 24.1694 | 19.7051 | 75.2559 | 74.1455 | 72.9486 | 71.4975 | 70.1996 | 68.4894 | 58.3082 | 56.1133 | 53.8204 | 51.9153 | 43.3888 | 36.4388 | 25.5306 | 70.2314 | 68.9843 | 67.5353 | 65.7006 | 64.0047 | 61.7771 | 50.998 | 48.0928 | 45.0816 | 42.4959 | 31.9602 | 26.9755 | 23.1765
|  | BASINGSTOKE T3 & T4 | HT |  |  |  | 72.7773 | 71.4608 | 70.0414 | 68.2608 | 66.3659 | 64.3037 | 52.9704 | 50.2724 | 47.2622 | 44.8143 | 30.8592 | 23.6326 | 19.6582 | 75.6651 | 74.7771 | 73.9088 | 72.8761 | 71.7343 | 70.5404 | 60.5337 | 59.152 | 57.5153 | 56.2347 | 48.8153 | 45.2745 | 43.6663 | 70.7294 | 69.5271 | 68.3128 | 66.8169 | 65.1475 | 63.3353 | 52.399 | 50.102 | 47.4408 | 45.3 | 32.9571 | 26.549 | 23.249
|  | BASINGSTOKE T3 & T4 | HE |  |  |  | 72.6712 | 71.4873 | 70.0343 | 68.1853 | 66.2516 | 64.0914 | 53.1673 | 50.6694 | 47.7888 | 45.152 | 31.5877 | 25.1459 | 22.7877 | 75.5202 | 74.5996 | 73.568 | 72.3384 | 71.0384 | 69.5843 | 59.5061 | 57.9224 | 56.0204 | 54.2939 | 44.4031 | 36.7459 | 26.7684 | 70.6294 | 69.5363 | 68.2843 | 66.7098 | 65.0302 | 63.12 | 52.4867 | 50.3214 | 47.799 | 45.5204 | 33.6347 | 27.9112 | 25.901
|  | BASINGSTOKE T3 & T4 | CF |  |  |  | 73.1416 | 72.4118 | 71.8628 | 70.9914 | 69.9373 | 68.5118 | 58.4724 | 56.7377 | 54.9428 | 53.3735 | 42.0388 | 35.0153 | 28.6796 | 75.7896 | 75.0792 | 74.5384 | 73.7547 | 72.8353 | 71.6669 | 61.8673 | 60.398 | 58.8643 | 57.4877 | 47.3082 | 34.5653 | 13.5051 | 71.0559 | 70.3486 | 69.8628 | 69.0965 | 68.1771 | 66.9567 | 57.1592 | 55.6561 | 54.0918 | 52.7622 | 42.9245 | 36.5286 | 30.9857
EAST CLAYDON GSP | BICESTER NORTH BSP | BICESTER NORTH BSP | MINIMUM HEADROOM | SP5972023735 | YES | 63.805 | 61.767 | 60.6874 | 58.3568 | 66.9926 | 63.9803 | 59.9048 | 55.4854 | 51.2283 | 47.2079 | 43.9793 | 26.5005 | 17.7373 | 13.0097 | 66.4846 | 65.7764 | 63.9764 | 70.5732 | 68.363 | 65.1313 | 62.1558 | 59.2864 | 56.5262 | 54.5711 | 42.5862 | 36.9199 | 26.6669 | 58.9621 | 58.0233 | 55.9397 | 62.6997 | 59.9599 | 55.9262 | 51.9477 | 48.0599 | 44.3395 | 41.5966 | 25.9628 | 18.4026 | 14.4638
|  | BICESTER NORTH BSP | EE |  |  |  | 61.767 | 60.6874 | 58.3568 | 66.9926 | 63.9803 | 59.9048 | 55.4854 | 51.2283 | 47.2079 | 43.9793 | 26.7638 | 18.6893 | 13.6036 | 66.4846 | 65.7764 | 63.9764 | 70.5732 | 68.363 | 65.1313 | 62.1558 | 59.2864 | 56.5262 | 54.5711 | 42.5862 | 36.9199 | 30.4016 | 58.9621 | 58.0233 | 55.9397 | 62.6997 | 59.9599 | 55.9262 | 51.9477 | 48.0599 | 44.3395 | 41.5966 | 26.1301 | 19.1791 | 14.8934
|  | BICESTER NORTH BSP | HT |  |  |  | 62.1884 | 61.2119 | 59.1099 | 67.6864 | 64.4385 | 60.7344 | 56.416 | 52.0334 | 48.0089 | 44.7518 | 26.5005 | 17.7373 | 13.0097 | 66.9009 | 66.3754 | 64.8907 | 71.5936 | 69.2977 | 66.4793 | 63.5599 | 60.615 | 57.9864 | 56.1701 | 44.9301 | 40.9077 | 38.7475 | 59.3233 | 58.4876 | 56.6019 | 63.3803 | 60.4538 | 56.8926 | 52.9364 | 48.9701 | 45.3385 | 42.4905 | 25.9628 | 18.4026 | 14.4638
|  | BICESTER NORTH BSP | HE |  |  |  | 62.1976 | 61.2813 | 59.2354 | 67.8773 | 64.7079 | 61.1385 | 57.5262 | 53.8038 | 50.2824 | 47.0171 | 29.3413 | 21.2424 | 17.8689 | 66.8305 | 66.2499 | 64.705 | 71.3466 | 69.0109 | 66.2211 | 63.7385 | 61.1691 | 58.7364 | 56.5589 | 43.822 | 38.0434 | 32.3464 | 59.3305 | 58.5397 | 56.7009 | 63.5283 | 60.6671 | 57.2436 | 53.962 | 50.6191 | 47.4548 | 44.5507 | 28.4169 | 21.4924 | 18.7383
|  | BICESTER NORTH BSP | CF |  |  |  | 62.7303 | 62.1997 | 60.7538 | 70.3028 | 68.1762 | 64.4436 | 62.2211 | 59.5966 | 57.4303 | 55.1518 | 39.2995 | 30.3444 | 23.1893 | 67.1009 | 66.6835 | 65.406 | 72.4528 | 70.614 | 67.0997 | 65.4222 | 63.512 | 61.9364 | 60.2711 | 47.2199 | 38.6005 | 26.6669 | 59.7825 | 59.3397 | 58.0091 | 65.5854 | 63.6058 | 59.7538 | 57.8477 | 55.6079 | 53.7773 | 51.8426 | 37.4311 | 29.7107 | 23.3801
BOTLEY WOOD GSP | BOTLEY WOOD BSP | BOTLEY WOOD BSP | MINIMUM HEADROOM | SU 54073 09759 | YES | 13.913 | 83.7943 | 80.6099 | 78.8599 | 77.5058 | 75.7966 | 74.064 | 72.4405 | 70.4997 | 68.616 | 67.1456 | 59.764 | 54.5425 | 51.6517 | 86.6782 | 84.0234 | 82.8764 | 82.0958 | 81.0591 | 79.9876 | 78.9468 | 77.5917 | 76.2744 | 75.2305 | 70.1029 | 63.9815 | 49.4203 | 82.1456 | 79.1989 | 77.6866 | 76.5489 | 75.0632 | 73.4836 | 72.0632 | 70.2254 | 68.4499 | 67.1489 | 60.806 | 56.2234 | 53.7458
|  | BOTLEY WOOD BSP | EE |  |  |  | 83.7943 | 80.6099 | 78.8599 | 77.5058 | 75.7966 | 74.064 | 72.4405 | 70.4997 | 68.616 | 67.1456 | 60.3252 | 55.6609 | 52.2374 | 86.6782 | 84.0234 | 82.8764 | 82.0958 | 81.0591 | 79.9876 | 78.9468 | 77.5917 | 76.2744 | 75.2305 | 70.1029 | 64.9591 | 57.5285 | 82.1456 | 79.1989 | 77.6866 | 76.5489 | 75.0632 | 73.4836 | 72.0632 | 70.2254 | 68.4499 | 67.1489 | 61.2203 | 57.1846 | 54.2376
|  | BOTLEY WOOD BSP | HT |  |  |  | 84.0811 | 80.7497 | 79.3283 | 77.8415 | 76.2232 | 74.3344 | 72.768 | 70.968 | 69.1915 | 67.8048 | 59.764 | 54.5425 | 51.6517 | 86.9935 | 84.2968 | 83.5519 | 82.7836 | 81.9407 | 80.8448 | 80.0264 | 78.9948 | 77.9703 | 77.2683 | 73.105 | 70.6417 | 69.3111 | 82.4364 | 79.3642 | 78.1744 | 76.9111 | 75.5203 | 73.8468 | 72.4846 | 70.8632 | 69.2509 | 68.0244 | 60.806 | 56.2234 | 53.7458
|  | BOTLEY WOOD BSP | HE |  |  |  | 84.0892 | 81.0191 | 79.4823 | 77.9946 | 76.4068 | 75.1058 | 73.5476 | 71.9364 | 70.3395 | 69.0915 | 61.2466 | 56.6027 | 54.3129 | 86.9129 | 84.3489 | 83.3662 | 82.4795 | 81.5387 | 80.8111 | 79.757 | 78.5958 | 77.4254 | 76.5101 | 70.7234 | 65.2734 | 58.1999 | 82.4384 | 79.6029 | 78.2968 | 77.0305 | 75.6621 | 74.557 | 73.1683 | 71.7029 | 70.2468 | 69.1264 | 61.3529 | 57.0927 | 54.9876
|  | BOTLEY WOOD BSP | CF |  |  |  | 84.5035 | 81.7538 | 80.7252 | 79.5578 | 78.4415 | 77.3221 | 76.5946 | 76.0272 | 75.116 | 74.2232 | 69.2109 | 63.1303 | 58.1354 | 87.1313 | 84.6907 | 84.0009 | 83.1662 | 82.4193 | 81.6223 | 80.9274 | 80.2897 | 79.3529 | 78.3989 | 72.6427 | 63.9815 | 49.4203 | 82.8007 | 80.2478 | 79.4019 | 78.4142 | 77.4672 | 76.5009 | 75.8683 | 75.3785 | 74.5509 | 73.7029 | 69.008 | 63.0652 | 58.4764
MANNINGTON GSP | BOURNEMOUTH | BOURNEMOUTH | MINIMUM HEADROOM | SZ 06265 92437 | YES | 24.477 | -29.1862 | -34.7176 | -40.0411 | -45.7207 | -51.6921 | -57.5288 | -65.9941 | -75.3829 | -84.5666 | -91.8135 | -123.3829 | -149.0145 | -158.74 | 3.2977 | -1.6847 | -6.2449 | -10.8745 | -15.798 | -20.598 | -27.0164 | -34.4052 | -41.8388 | -47.6756 | -77.1011 | -117.9358 | -217.3133 | -25.8911 | -30.9694 | -35.7082 | -40.6858 | -46.3705 | -51.8449 | -59.7919 | -68.7643 | -77.5674 | -84.198 | -112.3143 | -134.5164 | -142.8021
|  | BOURNEMOUTH | EE |  |  |  | -29.1862 | -34.7176 | -40.0411 | -45.7207 | -51.6921 | -57.5288 | -65.9941 | -75.3829 | -84.5666 | -91.8135 | -123.3829 | -142.837 | -154.3788 | 3.2977 | -1.6847 | -6.2449 | -10.8745 | -15.798 | -20.598 | -27.0164 | -34.4052 | -41.8388 | -47.6756 | -77.1011 | -108.1847 | -157.0725 | -25.8911 | -30.9694 | -35.7082 | -40.6858 | -46.3705 | -51.8449 | -59.7919 | -68.7643 | -77.5674 | -84.198 | -112.3143 | -129.246 | -139.3817
|  | BOURNEMOUTH | HT |  |  |  | -26.9494 | -31.6074 | -36.7768 | -41.237 | -45.4023 | -50.6054 | -57.7533 | -64.5115 | -72.4472 | -80.6166 | -122.1972 | -149.0145 | -158.74 | 5.663 | 1.9908 | -1.8388 | -4.6878 | -7.3449 | -10.8286 | -15.0664 | -18.947 | -23.9398 | -29.1205 | -53.7603 | -67.9643 | -72.5245 | -23.9156 | -28.196 | -32.8388 | -36.6776 | -40.2837 | -44.8317 | -51.1847 | -57.2888 | -64.6205 | -72.1827 | -110.3705 | -134.5164 | -142.8021
|  | BOURNEMOUTH | HE |  |  |  | -27.1107 | -31.4615 | -36.2788 | -40.3125 | -44.4043 | -49.2727 | -55.3625 | -61.3176 | -67.6676 | -74.6196 | -107.7237 | -127.7605 | -134.6227 | 5.061 | 1.0785 | -3.1398 | -6.3582 | -9.6919 | -13.7603 | -18.4603 | -23.1674 | -28.4143 | -34.3317 | -67.1082 | -99.8164 | -146.2174 | -24.0584 | -28.1062 | -32.4837 | -35.9949 | -39.5633 | -43.8511 | -49.2807 | -54.597 | -60.4756 | -66.9674 | -97.446 | -115.149 | -120.9011
|  | BOURNEMOUTH | CF |  |  |  | -25.5443 | -28.8513 | -32.2033 | -34.7084 | -37.2217 | -39.9196 | -42.7329 | -45.9962 | -49.1421 | -52.3349 | -74.8309 | -99.6707 | -122.4696 | 5.9559 | 2.3612 | -1.1786 | -3.8552 | -6.6398 | -9.8041 | -13.6011 | -18.0388 | -22.4929 | -27.1929 | -61.4786 | -117.9358 | -217.3133 | -22.6156 | -25.7664 | -28.8409 | -31.0347 | -33.2082 | -35.5072 | -37.898 | -40.7245 | -43.6837 | -46.7562 | -68.2286 | -90.4266 | -110.6837
BRAMLEY (FLEE) | BRACKNELL | BRACKNELL | MINIMUM HEADROOM | SU 86026 69422 | YES | 82.843 | 96.3749 | 92.2627 | 87.4841 | 83.8065 | 77.4137 | 40.1321 | 31.8239 | 22.5627 | 13.381 | 6.4953 | -23.9302 | -48.0884 | -61.0424 | 117.1902 | 114.2514 | 110.7463 | 108.229 | 103.2994 | 67.6504 | 61.5402 | 54.7239 | 47.8933 | 42.7504 | 18.5994 | -6.3139 | -72.8312 | 96.7616 | 93.0984 | 88.777 | 85.5341 | 79.63 | 42.9014 | 35.0912 | 26.4106 | 17.8627 | 11.4627 | -16.1088 | -38.1751 | -49.5894
|  | BRACKNELL | EE |  |  |  | 96.3749 | 92.2627 | 87.4841 | 83.8065 | 77.4137 | 40.1321 | 31.8239 | 22.5627 | 13.381 | 6.4953 | -22.8159 | -42.5435 | -57.022 | 117.1902 | 114.2514 | 110.7463 | 108.229 | 103.2994 | 67.6504 | 61.5402 | 54.7239 | 47.8933 | 42.7504 | 18.5994 | -5.2343 | -40.6914 | 96.7616 | 93.0984 | 88.777 | 85.5341 | 79.63 | 42.9014 | 35.0912 | 26.4106 | 17.8627 | 11.4627 | -15.1996 | -32.7098 | -45.573
|  | BRACKNELL | HT |  |  |  | 98.0168 | 94.481 | 90.5994 | 86.3086 | 80.2412 | 43.9953 | 37.0627 | 29.377 | 21.1249 | 13.4984 | -23.9302 | -48.0884 | -61.0424 | 118.8555 | 116.7708 | 114.5035 | 111.9749 | 107.8923 | 73.6698 | 69.427 | 64.7178 | 59.6086 | 54.777 | 32.3994 | 19.1943 | 12.6219 | 98.2749 | 95.2535 | 91.9229 | 88.1065 | 82.5759 | 46.9045 | 40.4514 | 33.3555 | 25.7392 | 18.631 | -16.1088 | -38.1751 | -49.5894
|  | BRACKNELL | HE |  |  |  | 98.0351 | 94.7749 | 91.0045 | 86.9178 | 81.4882 | 45.3698 | 39.3086 | 32.4086 | 25.2168 | 18.7688 | -12.3832 | -33.1414 | -42.9506 | 118.4953 | 116.2086 | 113.5678 | 110.6963 | 106.6014 | 71.8637 | 67.4984 | 62.5372 | 57.3229 | 52.3933 | 25.1535 | 0.080016 | -33.7261 | 98.279 | 95.4831 | 92.2372 | 88.6035 | 83.6494 | 48.0831 | 42.5014 | 36.1851 | 29.6412 | 23.7116 | -5.1037 | -23.6567 | -32.5098
|  | BRACKNELL | CF |  |  |  | 99.3116 | 97.0219 | 94.2912 | 91.7147 | 87.7055 | 52.5035 | 49.6708 | 45.9219 | 42.1463 | 38.2106 | 16.2147 | -5.2557 | -24.423 | 119.178 | 117.2719 | 115.0351 | 112.8586 | 109.3678 | 74.6708 | 71.5494 | 67.6321 | 63.6555 | 59.3147 | 32.7055 | -6.3139 | -72.8312 | 99.4688 | 97.5627 | 95.2402 | 92.9882 | 89.3596 | 54.5759 | 51.977 | 48.5412 | 45.0984 | 41.4351 | 21.0361 | 1.5678 | -15.4761
BRAMLEY (FLEE) | BURGHFIELD MAIN | BURGHFIELD MAIN | MINIMUM HEADROOM | SU 69442 70509 | YES | 34.398 | 29.5586 | 27.6759 | 24.9218 | 21.9973 | 18.8147 | -154.5312 | -161.7547 | -167.3241 | -172.7751 | -176.818 | -197.6863 | -210.368 | -216.9129 | 40.5424 | 39.1394 | 36.9333 | 34.5629 | 32.02 | -182.7963 | -188.6586 | -192.9657 | -197.329 | -200.6473 | -219.7892 | -241.6871 | -288.3841 | 26.6384 | 25.0476 | 22.5761 | 19.9445 | 17.1578 | -198.1637 | -205.2361 | -210.3392 | -215.3912 | -219.3249 | -239.5422 | -251.0871 | -256.6127
|  | BURGHFIELD MAIN | EE |  |  |  | 29.5586 | 27.6759 | 24.9218 | 21.9973 | 18.8147 | -154.5312 | -161.7547 | -167.3241 | -172.7751 | -176.818 | -197.6863 | -208.9516 | -216.1863 | 40.5424 | 39.1394 | 36.9333 | 34.5629 | 32.02 | -182.7963 | -188.6586 | -192.9657 | -197.329 | -200.6473 | -219.7892 | -236.0524 | -259.8759 | 26.6384 | 25.0476 | 22.5761 | 19.9445 | 17.1578 | -198.1637 | -205.2361 | -210.3392 | -215.3912 | -219.3249 | -239.5422 | -249.9871 | -256.1729
|  | BURGHFIELD MAIN | HT |  |  |  | 30.6188 | 28.9586 | 26.7433 | 24.3657 | 21.4208 | -151.5037 | -158.0649 | -162.769 | -167.3894 | -172.4455 | -196.5098 | -210.368 | -216.9129 | 41.7027 | 40.6618 | 39.1149 | 37.5363 | 35.5741 | -178.5086 | -183.5004 | -186.5249 | -189.6055 | -193.0545 | -208.0688 | -215.2576 | -218.1688 | 27.6618 | 26.1659 | 24.1241 | 21.971 | 19.3078 | -195.7167 | -202.2657 | -206.6973 | -211.1341 | -215.9667 | -238.33 | -251.0871 | -256.6127
|  | BURGHFIELD MAIN | HE |  |  |  | 30.4861 | 28.8586 | 26.681 | 24.3361 | 21.831 | -150.9027 | -157.1047 | -161.472 | -165.6771 | -170.0873 | -193.5139 | -205.9649 | -210.8016 | 41.3333 | 40.0363 | 38.169 | 36.2455 | 34.3476 | -179.98 | -185.2953 | -188.678 | -192.0953 | -195.831 | -218.0667 | -235.4249 | -258.1259 | 27.5231 | 26.0455 | 24.0098 | 21.8731 | 19.7282 | -195.0831 | -201.2688 | -205.3494 | -209.3341 | -213.5524 | -235.9361 | -247.3627 | -251.379
|  | BURGHFIELD MAIN | CF |  |  |  | 31.3545 | 30.4382 | 28.9759 | 27.2382 | 26.0402 | -145.619 | -149.6088 | -151.4598 | -153.9169 | -156.272 | -171.9302 | -188.6057 | -199.7159 | 41.8016 | 40.8118 | 39.2465 | 37.4965 | 36.2506 | -177.6831 | -182.1443 | -184.4565 | -187.2973 | -190.2259 | -210.8239 | -241.6871 | -288.3841 | 28.3241 | 27.4955 | 26.1098 | 24.5445 | 23.5598 | -190.1535 | -194.2555 | -195.9616 | -198.2422 | -200.4667 | -215.6127 | -231.1188 | -241.3882
BRAMLEY (FLEE) | BURGHFIELD RESERVE | BURGHFIELD RESERVE | MINIMUM HEADROOM | SU 69442 70509 | YES | 16.413 | 55.1086 | 53.1943 | 51.2035 | 48.9963 | 46.3627 | 44.2902 | 41.1402 | 37.6923 | 33.8402 | 30.3463 | -84.7473 | -92.5422 | -94.8279 | 63.9904 | 62.4874 | 60.8231 | 59.0425 | 56.9823 | 55.4221 | 53.1966 | 50.6863 | 47.8251 | 45.5374 | -89.1073 | -97.4737 | -124.5573 | 53.92 | 52.1292 | 50.2221 | 48.1741 | 45.8119 | 43.3782 | 40.1863 | 36.3986 | 32.6302 | 29.2996 | -109.2288 | -116.5471 | -118.5675
|  | BURGHFIELD RESERVE | EE |  |  |  | 55.1086 | 53.1943 | 51.2035 | 48.9963 | 46.3627 | 44.2902 | 41.1402 | 37.6923 | 33.8402 | 30.3463 | -81.4728 | -88.7769 | -94.1667 | 63.9904 | 62.4874 | 60.8231 | 59.0425 | 56.9823 | 55.4221 | 53.1966 | 50.6863 | 47.8251 | 45.5374 | -86.7737 | -96.7206 | -110.143 | 53.92 | 52.1292 | 50.2221 | 48.1741 | 45.8119 | 43.3782 | 40.1863 | 36.3986 | 32.6302 | 29.2996 | -105.9839 | -112.2206 | -115.5277
|  | BURGHFIELD RESERVE | HT |  |  |  | 55.9698 | 54.2912 | 52.6361 | 50.9066 | 48.8566 | 46.6963 | 43.7688 | 40.8372 | 37.8178 | 34.7076 | -78.9432 | -88.9555 | -93.8922 | 64.9904 | 63.8914 | 62.7731 | 61.5914 | 60.1925 | 58.6557 | 56.868 | 55.0823 | 52.8323 | 50.3057 | -83.0206 | -88.5767 | -90.8165 | 54.8455 | 53.3282 | 51.7914 | 50.1639 | 48.2619 | 46.2047 | 43.4945 | 40.767 | 37.9608 | 34.9312 | -102.6777 | -111.4349 | -115.4828
|  | BURGHFIELD RESERVE | HE |  |  |  | 55.9157 | 54.2484 | 52.5729 | 50.8127 | 48.8759 | 46.6514 | 43.9372 | 40.629 | 36.6066 | 32.5974 | -84.7473 | -92.5422 | -94.8279 | 64.7955 | 63.5445 | 62.2323 | 60.8455 | 59.3374 | 57.5119 | 55.4843 | 53.0904 | 50.1282 | 47.1761 | -89.1073 | -96.1134 | -108.6308 | 54.7812 | 53.2659 | 51.7027 | 50.0435 | 48.2292 | 45.7996 | 42.7629 | 39.1353 | 35.2935 | 31.4659 | -109.2288 | -116.5471 | -118.5675
|  | BURGHFIELD RESERVE | CF |  |  |  | 56.5943 | 55.478 | 54.377 | 53.2453 | 52.0759 | 50.9535 | 49.7831 | 48.2821 | 46.5178 | 45.3902 | -66.0137 | -78.7116 | -87.4932 | 65.2037 | 64.2445 | 63.2231 | 62.1537 | 61.0384 | 59.8619 | 58.4435 | 56.7537 | 54.871 | 53.5445 | -80.5655 | -97.4737 | -124.5573 | 55.4261 | 54.421 | 53.3935 | 52.3108 | 51.2047 | 50.1323 | 48.9751 | 47.5598 | 45.9547 | 44.0292 | -91.4369 | -103.5022 | -111.7543
BRAMLEY (FLEE) | CAMBERLEY MAIN | CAMBERLEY MAIN | MINIMUM HEADROOM | SU 86530 59483 | YES | 6.89 | 38.1013 | 34.7696 | 32.5074 | 29.6094 | 26.0819 | 22.5635 | 17.5482 | 11.9625 | 6.3635 | 2.2727 | -19.3242 | -35.4028 | -44.1049 | 52.3688 | 49.9902 | 48.3984 | 46.33 | 43.7851 | 41.2076 | 37.7556 | 33.7719 | 29.7004 | 26.8494 | 11.2535 | -8.9955 | -55.2271 | 39.0147 | 35.8943 | 33.9076 | 31.2719 | 27.9729 | 24.7351 | 20.0872 | 14.8423 | 9.5688 | 5.9331 | -12.2618 | -25.9067 | -33.5649
|  | CAMBERLEY MAIN | EE |  |  |  | 38.1013 | 34.7696 | 32.5074 | 29.6094 | 26.0819 | 22.5635 | 17.5482 | 11.9625 | 6.3635 | 2.2727 | -17.7824 | -31.9028 | -42.5936 | 52.3688 | 49.9902 | 48.3984 | 46.33 | 43.7851 | 41.2076 | 37.7556 | 33.7719 | 29.7004 | 26.8494 | 11.2535 | -4.8098 | -28.7057 | 39.0147 | 35.8943 | 33.9076 | 31.2719 | 27.9729 | 24.7351 | 20.0872 | 14.8423 | 9.5688 | 5.9331 | -11.2291 | -22.8751 | -32.3659
|  | CAMBERLEY MAIN | HT |  |  |  | 39.1778 | 36.1604 | 33.6247 | 30.987 | 28.0615 | 24.6615 | 20.3645 | 15.4349 | 10.7758 | 5.6992 | -19.3242 | -35.4028 | -44.1049 | 53.4964 | 51.6902 | 50.2086 | 48.7556 | 47.1025 | 45.0637 | 42.8249 | 40.03 | 37.4219 | 34.476 | 21.0219 | 13.5933 | 9.8933 | 40.2086 | 37.4902 | 35.1749 | 32.88 | 30.3168 | 27.2056 | 23.4382 | 18.9494 | 14.7515 | 10.077 | -12.2618 | -25.9067 | -33.5649
|  | CAMBERLEY MAIN | HE |  |  |  | 39.1829 | 36.4237 | 33.9319 | 31.5411 | 28.986 | 25.7339 | 22.2053 | 17.8972 | 13.8156 | 9.4533 | -12.6293 | -27.4681 | -34.3467 | 53.229 | 51.3076 | 49.5198 | 47.8545 | 46.0882 | 43.7239 | 41.2994 | 38.227 | 35.2607 | 31.927 | 13.5627 | -3.3577 | -25.8393 | 40.1923 | 37.6943 | 35.4035 | 33.2984 | 31.0749 | 28.0984 | 24.9749 | 21.0066 | 17.3127 | 13.2362 | -6.7342 | -19.021 | -25.1067
|  | CAMBERLEY MAIN | CF |  |  |  | 40.1951 | 38.19 | 36.6604 | 35.0135 | 33.5411 | 32.1319 | 30.4615 | 28.8553 | 26.6625 | 24.7023 | 7.9196 | -7.5549 | -21.5079 | 53.7351 | 52.0974 | 50.7535 | 49.2729 | 47.9107 | 46.4341 | 44.4586 | 42.4392 | 39.9402 | 37.5341 | 18.3127 | -8.9955 | -55.2271 | 41.076 | 39.2209 | 37.8127 | 36.2709 | 34.9545 | 33.728 | 32.1158 | 30.6117 | 28.4882 | 26.6453 | 10.9341 | -2.6128 | -14.3465
BRAMLEY (FLEE) | CAMBERLEY RESERVE | CAMBERLEY RESERVE | MINIMUM HEADROOM | SU 86530 59483 | YES | 19.352 | 45.4822 | 42.6852 | 39.2669 | 36.3046 | 33.275 | 29.373 | 24.7291 | 20.0026 | 15.1638 | 11.3893 | -6.4005 | -19.179 | -26.1148 | 54.7671 | 52.7457 | 50.2824 | 48.2171 | 46.0875 | 43.3497 | 39.9946 | 36.5212 | 32.8579 | 30.0559 | 15.8406 | -1.3207 | -40.9003 | 43.7661 | 41.2354 | 38.2069 | 35.5334 | 32.815 | 29.2701 | 24.9365 | 20.5375 | 15.9773 | 12.5732 | -4.3962 | -16.5697 | -20.635
|  | CAMBERLEY RESERVE | EE |  |  |  | 45.4822 | 42.6852 | 39.2669 | 36.3046 | 33.275 | 29.373 | 24.7291 | 20.0026 | 15.1638 | 11.3893 | -6.4005 | -17.076 | -25.5362 | 54.7671 | 52.7457 | 50.2824 | 48.2171 | 46.0875 | 43.3497 | 39.9946 | 36.5212 | 32.8579 | 30.0559 | 15.8406 | 2.2161 | -18.1839 | 43.7661 | 41.2354 | 38.2069 | 35.5334 | 32.815 | 29.2701 | 24.9365 | 20.5375 | 15.9773 | 12.5732 | -3.0462 | -12.5176 | -19.9482
|  | CAMBERLEY RESERVE | HT |  |  |  | 46.573 | 44.1689 | 41.0087 | 38.2669 | 35.7363 | 32.6689 | 28.6077 | 24.6067 | 20.2689 | 15.8118 | -6.1566 | -19.179 | -26.1148 | 55.8844 | 54.4457 | 52.4426 | 50.8079 | 49.3977 | 47.7283 | 45.3273 | 42.9824 | 40.3048 | 37.5089 | 25.0375 | 18.2222 | 14.9283 | 44.9099 | 42.815 | 40.0416 | 37.565 | 35.3579 | 32.7161 | 29.0293 | 25.4263 | 21.4324 | 17.3099 | -2.6482 | -14.4911 | -20.5482
|  | CAMBERLEY RESERVE | HE |  |  |  | 46.4414 | 44.0312 | 40.8393 | 38.0261 | 35.425 | 32.2618 | 28.572 | 24.8771 | 20.875 | 16.7383 | -5.1923 | -18.2474 | -22.5882 | 55.5854 | 53.8987 | 51.614 | 49.6528 | 47.8814 | 45.8018 | 43.1569 | 40.461 | 37.4385 | 34.2324 | 16.8497 | 1.7375 | -17.5033 | 44.7834 | 42.663 | 39.8589 | 37.3201 | 35.0406 | 32.3181 | 28.961 | 25.6191 | 21.9344 | 18.1161 | -4.3962 | -16.5697 | -20.635
|  | CAMBERLEY RESERVE | CF |  |  |  | 47.3067 | 45.6148 | 43.2128 | 41.2781 | 39.3863 | 37.3128 | 35.3699 | 33.5597 | 31.6903 | 29.4444 | 14.773 | 0.20769 | -12.0709 | 56.0487 | 54.7028 | 52.761 | 51.1865 | 49.6252 | 47.965 | 45.9283 | 43.913 | 41.7987 | 39.2691 | 22.5752 | -1.3207 | -40.9003 | 45.5569 | 44.0783 | 41.9671 | 40.1977 | 38.5038 | 36.7477 | 34.9201 | 33.265 | 31.5395 | 29.4018 | 15.4926 | 0.68953 | -10.6972
IVER 132KV | CHALVEY BSP | CHALVEY BSP | MINIMUM HEADROOM | SU 96669 79364 | YES | 10.228 | 55.3331 | 51.2188 | 42.9612 | 38.4833 | 33.9369 | 28.8232 | 145.7526 | 141.1791 | 136.9067 | 133.3709 | 120.8475 | 110.4709 | 107.3567 | 67.9351 | 64.9484 | 58.0194 | 54.9884 | 51.9624 | 48.464 | 161.3026 | 157.2209 | 153.4342 | 150.124 | 136.5495 | 123.9811 | 88.7648 | 55.8922 | 52.281 | 44.499 | 40.4955 | 36.5369 | 31.9396 | 145.8138 | 141.1301 | 136.8291 | 133.3148 | 121.3189 | 111.372 | 108.1097
|  | CHALVEY BSP | EE |  |  |  | 55.3331 | 51.2188 | 42.9612 | 38.4833 | 33.9369 | 28.8232 | 145.7526 | 141.1791 | 136.9067 | 133.3709 | 120.9413 | 113.9373 | 111.9016 | 67.9351 | 64.9484 | 58.0194 | 54.9884 | 51.9624 | 48.464 | 161.3026 | 157.2209 | 153.4342 | 150.124 | 136.5495 | 123.9811 | 105.7444 | 55.8922 | 52.281 | 44.499 | 40.4955 | 36.5369 | 31.9396 | 145.8138 | 141.1301 | 136.8291 | 133.3148 | 121.5169 | 115.1311 | 112.6658
|  | CHALVEY BSP | HT |  |  |  | 56.2382 | 52.1637 | 44.2194 | 40.5077 | 35.9736 | 31.2865 | 149.1362 | 145.2934 | 141.5464 | 137.6005 | 120.8475 | 110.4709 | 107.3567 | 68.8259 | 66.0637 | 59.6051 | 57.4312 | 54.7022 | 51.8702 | 165.7995 | 162.6791 | 159.7403 | 156.5852 | 144.0322 | 136.623 | 133.5434 | 56.8555 | 53.2739 | 45.8265 | 42.6833 | 38.7257 | 34.5967 | 149.472 | 145.576 | 141.8424 | 137.8699 | 121.3189 | 111.372 | 108.1097
|  | CHALVEY BSP | HE |  |  |  | 56.2065 | 52.232 | 44.3806 | 40.7833 | 36.4747 | 31.9273 | 150.3883 | 147.2077 | 144.3516 | 141.3118 | 128.5699 | 121.5158 | 118.4485 | 68.629 | 65.7412 | 59.1296 | 56.7945 | 53.9614 | 50.9365 | 165.0495 | 162.0852 | 159.5516 | 156.7791 | 142.3832 | 129.3679 | 110.6811 | 56.8188 | 53.3249 | 45.9633 | 42.922 | 39.1869 | 35.2222 | 150.7556 | 147.5148 | 144.7597 | 141.7975 | 129.3005 | 122.7148 | 119.5087
|  | CHALVEY BSP | CF |  |  |  | 57.9198 | 56.0759 | 49.901 | 47.5618 | 44.943 | 40.6865 | 157.9964 | 154.5118 | 152.9709 | 151.1067 | 141.3913 | 131.8638 | 123.5526 | 69.5157 | 67.6116 | 61.7663 | 59.8241 | 57.7879 | 54.7538 | 168.1781 | 165.0097 | 162.8444 | 160.4097 | 146.1975 | 125.2056 | 88.7648 | 58.2076 | 56.3749 | 50.4153 | 48.3067 | 46.1063 | 42.5038 | 157.2781 | 154.0291 | 152.4658 | 150.5648 | 141.1128 | 132.5332 | 125.376
LOVEDEAN GSP | CHICHESTER & HUNSTON | CHICHESTER & HUNSTON | MINIMUM HEADROOM | SU 92282 07416 | YES | 77.719 | 29.9323 | 22.2673 | 9.9085 | 2.5881 | -5.8068 | -18.4067 | -33.0357 | -46.3867 | -59.2786 | -69.203 | -123.852 | -161.6428 | -183.1592 | 36.0759 | 32.063 | 23.2685 | 19.446 | 15.1777 | 6.4808 | -3.4553 | -11.7421 | -19.8574 | -26.1727 | -62.1768 | -101.7319 | -197.6247 | -72.5976 | -79.7738 | -92.4652 | -100.7846 | -109.7591 | -121.6284 | -137.7513 | -151.4206 | -164.4523 | -177.9655 | -251.2798 | -297.7972 | -322.8553
|  | CHICHESTER & HUNSTON | EE |  |  |  | 29.9323 | 22.2673 | 9.9085 | 2.5881 | -5.8068 | -18.4067 | -33.0357 | -46.3867 | -59.2786 | -69.203 | -121.1622 | -154.1633 | -178.6908 | 36.0759 | 32.063 | 23.2685 | 19.446 | 15.1777 | 6.4808 | -3.4553 | -11.7421 | -19.8574 | -26.1727 | -62.1768 | -97.6033 | -148.4186 | 14.1789 | 8.1538 | -3.0948 | -9.3795 | -16.4029 | -27.5968 | -40.5574 | -52.0655 | -63.7584 | -72.1329 | -116.837 | -144.8645 | -165.8492
|  | CHICHESTER & HUNSTON | HT |  |  |  | 31.9802 | 24.7102 | 12.7402 | 4.9973 | -3.0017 | -14.1271 | -28.6959 | -39.8775 | -51.5092 | -62.1765 | -123.852 | -161.6428 | -183.1592 | 37.7789 | 34.3018 | 26.3828 | 22.944 | 19.3481 | 13.1859 | 4.8671 | -0.56044 | -6.5237 | -11.8941 | -42.5329 | -60.2717 | -70.288 | -72.5976 | -79.7738 | -92.4652 | -100.7846 | -109.7591 | -121.6284 | -137.7513 | -151.4206 | -164.4523 | -177.9655 | -251.2798 | -297.7972 | -322.8553
|  | CHICHESTER & HUNSTON | HE |  |  |  | 31.8435 | 25.3285 | 13.5881 | 6.4116 | -1.07 | -11.7149 | -24.7806 | -34.5786 | -44.9092 | -54.2204 | -109.1296 | -142.8969 | -158.8428 | 37.3932 | 33.9885 | 25.4899 | 21.7828 | 17.7858 | 10.9818 | 1.9345 | -4.0431 | -10.7155 | -16.9329 | -56.6584 | -93.0951 | -140.1023 | 15.7198 | 10.6722 | 0.10115 | -5.807 | -12.0948 | -21.4468 | -33.037 | -41.3217 | -50.2839 | -58.4043 | -105.8747 | -135.1492 | -148.5747
|  | CHICHESTER & HUNSTON | CF |  |  |  | 33.6567 | 29.05 | 19.0973 | 14.2555 | 9.23 | 1.327 | -6.1684 | -11.2551 | -16.1122 | -21.3612 | -60.8755 | -97.4959 | -129.6602 | 38.3146 | 35.464 | 27.8369 | 24.8818 | 21.846 | 15.7828 | 8.8528 | 4.1947 | -0.44616 | -5.6145 | -44.0829 | -101.7319 | -197.6247 | 17.1259 | 13.8722 | 4.9716 | 1.0205 | -3.0897 | -10.2835 | -17.0349 | -21.3258 | -25.3196 | -29.8574 | -63.5839 | -95.4053 | -122.939
CHICKERELL GSP | CHICKERELL BSP | CHICKERELL BSP | MINIMUM HEADROOM | SY 65479 80511 | YES | 21.523 | 16.5643 | 12.6051 | 7.5255 | 1.499 | -4.1785 | -9.7479 | -16.2173 | -24.3602 | -32.3806 | -38.299 | -68.401 | -89.4949 | -101.1826 | 34.5379 | 31.9665 | 28.7634 | 24.538 | 20.9625 | 17.4268 | 13.4635 | 8.1727 | 2.5278 | -1.512 | -23.7518 | -46.6334 | -103.912 | 15.8992 | 12.4338 | 8.0818 | 2.7268 | -2.2263 | -7.1018 | -12.9885 | -20.5569 | -27.9773 | -33.3161 | -60.0712 | -78.9518 | -89.2569
|  | CHICKERELL BSP | EE |  |  |  | 16.5643 | 12.6051 | 7.5255 | 1.499 | -4.1785 | -9.7479 | -16.2173 | -24.3602 | -32.3806 | -38.299 | -68.401 | -86.8214 | -98.7877 | 34.5379 | 31.9665 | 28.7634 | 24.538 | 20.9625 | 17.4268 | 13.4635 | 8.1727 | 2.5278 | -1.512 | -23.7518 | -44.0049 | -72.661 | 15.8992 | 12.4338 | 8.0818 | 2.7268 | -2.2263 | -7.1018 | -12.9885 | -20.5569 | -27.9773 | -33.3161 | -60.0712 | -76.6906 | -87.2008
|  | CHICKERELL BSP | HT |  |  |  | 18.3755 | 15.0989 | 10.6224 | 4.8398 | 0.46737 | -4.1143 | -9.8183 | -16.2663 | -23.2673 | -29.9061 | -66.4479 | -89.4949 | -101.1826 | 35.942 | 34.0838 | 31.5818 | 27.8319 | 25.5084 | 23.0482 | 20.1094 | 16.6808 | 12.9492 | 9.4237 | -10.3171 | -21.9896 | -27.3967 | 17.5053 | 14.6308 | 10.792 | 5.6012 | 1.7961 | -2.2263 | -7.3355 | -13.0906 | -19.3253 | -25.2161 | -58.1018 | -78.9518 | -89.2569
|  | CHICKERELL BSP | HE |  |  |  | 18.2061 | 14.9775 | 10.5234 | 4.7949 | 0.45921 | -4.0704 | -9.3102 | -15.649 | -21.8867 | -27.9714 | -61.1336 | -80.7122 | -89.999 | 35.5787 | 33.4543 | 30.6002 | 26.5074 | 23.7461 | 20.8053 | 17.4676 | 13.3319 | 9.237 | 5.1615 | -19.9753 | -42.1804 | -69.4681 | 17.3471 | 14.5022 | 10.6757 | 5.5145 | 1.7135 | -2.2875 | -6.9855 | -12.6722 | -18.2477 | -23.659 | -53.6641 | -71.5467 | -79.2294
|  | CHICKERELL BSP | CF |  |  |  | 19.3775 | 17.1428 | 13.8418 | 9.5786 | 6.1449 | 3.0612 | 0.27145 | -2.5194 | -6.1398 | -9.5275 | -32.7602 | -55.9949 | -76.85 | 36.1818 | 34.492 | 32.1624 | 28.7982 | 26.2706 | 23.7951 | 21.2155 | 18.5074 | 15.2329 | 12.0064 | -11.3324 | -46.6334 | -103.912 | 18.4318 | 16.494 | 13.7165 | 9.9104 | 6.9339 | 4.2461 | 1.8186 | -0.59263 | -3.7488 | -6.6824 | -27.5569 | -48.4232 | -67.1753
MELKSHAM GSP | CHIPPENHAM | CHIPPENHAM | MINIMUM HEADROOM | ST 92629 74275 | YES | 38.54 | 24.1332 | 20.0895 | 128.4316 | 124.7336 | 120.1969 | 114.4356 | 108.5285 | 101.8601 | 94.5561 | 88.8224 | 55.502 | 37.4703 | 27.2346 | 40.7946 | 37.7152 | 142.8044 | 140.2371 | 137.0514 | 132.8983 | 129.0126 | 124.4391 | 119.4095 | 115.5912 | 90.2881 | 74.283 | 33.8034 | 25.4834 | 21.6428 | 127.5218 | 124.182 | 119.9585 | 114.5799 | 109.3177 | 103.1718 | 96.4248 | 91.4197 | 61.5126 | 46.6463 | 38.2218
|  | CHIPPENHAM | EE |  |  |  | 24.1332 | 20.0895 | 128.4316 | 124.7336 | 120.1969 | 114.4356 | 108.5285 | 101.8601 | 94.5561 | 88.8224 | 55.502 | 38.7142 | 28.2438 | 40.7946 | 37.7152 | 142.8044 | 140.2371 | 137.0514 | 132.8983 | 129.0126 | 124.4391 | 119.4095 | 115.5912 | 90.2881 | 74.283 | 53.5565 | 25.4834 | 21.6428 | 127.5218 | 124.182 | 119.9585 | 114.5799 | 109.3177 | 103.1718 | 96.4248 | 91.4197 | 61.5126 | 47.6585 | 38.8697
|  | CHIPPENHAM | HT |  |  |  | 25.4913 | 21.6569 | 130.6908 | 127.0744 | 122.9346 | 118.3479 | 112.5652 | 106.3285 | 100.151 | 94.102 | 56.6356 | 37.4703 | 27.2346 | 42.2711 | 39.7009 | 145.6646 | 143.4595 | 140.9575 | 138.182 | 134.9493 | 131.1993 | 127.5493 | 123.982 | 99.931 | 90.5289 | 86.0095 | 27.0773 | 23.6897 | 130.4075 | 127.132 | 123.3218 | 119.3299 | 114.2218 | 108.5044 | 102.8861 | 97.3646 | 62.9728 | 46.6463 | 38.2218
|  | CHIPPENHAM | HE |  |  |  | 25.3903 | 21.8314 | 131.003 | 127.4101 | 123.1122 | 118.6418 | 113.4356 | 107.6459 | 101.6254 | 95.7316 | 59.0642 | 41.8469 | 35.1142 | 41.9773 | 39.3101 | 145.081 | 142.6014 | 139.6677 | 136.633 | 133.2381 | 129.1932 | 125.0371 | 120.8922 | 91.9667 | 75.3616 | 56.2473 | 26.9752 | 23.7754 | 130.6044 | 127.3442 | 123.4197 | 119.4942 | 114.8565 | 109.4912 | 103.9993 | 98.5973 | 63.9442 | 50.1636 | 44.9881
|  | CHIPPENHAM | CF |  |  |  | 26.4526 | 23.6426 | 133.904 | 131.4928 | 128.6989 | 124.1754 | 121.7969 | 119.3346 | 116.7101 | 113.5152 | 86.2295 | 65.3346 | 49.655 | 42.6232 | 40.306 | 146.6156 | 144.7534 | 142.6095 | 138.9054 | 136.7493 | 134.3708 | 131.7677 | 128.6656 | 101.7952 | 74.3718 | 33.8034 | 27.9619 | 25.4489 | 133.2218 | 131.0463 | 128.5085 | 124.4412 | 122.3044 | 120.0054 | 117.5259 | 114.4126 | 88.881 | 70.3697 | 56.7626
MANNINGTON GSP | CHRISTCHURCH BSP | CHRISTCHURCH BSP | MINIMUM HEADROOM | SZ 15716 93165 | YES | 27.106 | 36.6021 | 34.1296 | 31.8643 | 29.1133 | 25.749 | 22.9449 | 18.1806 | 12.8184 | 7.4786 | 3.4898 | -15.8561 | -31.3479 | -37.601 | 54.188 | 52.1962 | 50.4584 | 48.3349 | 45.6808 | 43.3176 | 39.8604 | 35.8717 | 31.8125 | 28.7808 | 12.2339 | -10.9171 | -65.9253 | 41.5796 | 39.1592 | 37.0929 | 34.5429 | 31.397 | 28.7317 | 24.2898 | 19.249 | 14.2306 | 10.5827 | -6.4061 | -20.1745 | -25.4918
|  | CHRISTCHURCH BSP | EE |  |  |  | 36.6021 | 34.1296 | 31.8643 | 29.1133 | 25.749 | 22.9449 | 18.1806 | 12.8184 | 7.4786 | 3.4898 | -15.4969 | -28.351 | -34.9918 | 54.188 | 52.1962 | 50.4584 | 48.3349 | 45.6808 | 43.3176 | 39.8604 | 35.8717 | 31.8125 | 28.7808 | 12.2339 | -5.7732 | -32.7283 | 41.5796 | 39.1592 | 37.0929 | 34.5429 | 31.397 | 28.7317 | 24.2898 | 19.249 | 14.2306 | 10.5827 | -6.4061 | -17.5887 | -23.3714
|  | CHRISTCHURCH BSP | HT |  |  |  | 37.6572 | 35.6327 | 33.248 | 30.6531 | 28.6378 | 26.4235 | 22.3235 | 18.1408 | 13.4449 | 8.5929 | -15.8561 | -31.3479 | -37.601 | 55.3472 | 54.1482 | 52.6829 | 50.9921 | 49.8594 | 48.4604 | 46.1666 | 43.8217 | 41.0757 | 38.1992 | 24.586 | 16.8482 | 13.8604 | 42.697 | 40.8643 | 38.6755 | 36.2041 | 34.3725 | 32.2908 | 28.5306 | 24.7082 | 20.3908 | 15.9235 | -6.3898 | -20.1745 | -25.4918
|  | CHRISTCHURCH BSP | HE |  |  |  | 37.6878 | 35.8347 | 33.6317 | 31.2296 | 29.4102 | 27.4255 | 24.0286 | 20.5725 | 16.6664 | 12.5633 | -7.301 | -20.0347 | -24.9673 | 55.0655 | 53.6706 | 51.9564 | 50.0288 | 48.5747 | 46.839 | 44.3013 | 41.6686 | 38.586 | 35.2808 | 16.7482 | -1.6967 | -27.9702 | 42.7143 | 41.0337 | 38.9837 | 36.6847 | 35.0398 | 33.1623 | 30.0255 | 26.8327 | 23.199 | 19.3857 | 1.196 | -10.001 | -14.0847
|  | CHRISTCHURCH BSP | CF |  |  |  | 38.5521 | 37.3674 | 35.9929 | 34.5123 | 33.1643 | 32.1113 | 30.6684 | 29.3113 | 27.5255 | 26.0153 | 12.8031 | -2.3 | -16.2898 | 55.4921 | 54.3125 | 52.9737 | 51.4768 | 50.0013 | 48.5074 | 46.4757 | 44.3972 | 41.8941 | 39.49 | 20.3033 | -10.9171 | -65.9253 | 43.5123 | 42.4296 | 41.1602 | 39.7174 | 38.446 | 37.4582 | 36.1041 | 34.8317 | 33.1204 | 31.6878 | 19.2184 | 5.5776 | -6.7918
IVER 132KV | CIPPENHAM | CIPPENHAM | MINIMUM HEADROOM | SU 96266 79634 | YES | 9.053 | 84.5541 | 82.5947 | 81.0631 | 79.5028 | 77.9589 | 76.4722 | 74.5752 | 72.415 | 70.3865 | 68.8028 | 61.861 | 57.0354 | 55.5354 | 87.2398 | 85.5559 | 84.2988 | 83.1854 | 82.1895 | 81.1661 | 79.9559 | 78.5446 | 77.1752 | 76.0171 | 70.0599 | 63.462 | 47.011 | 81.7418 | 79.861 | 78.4457 | 77.063 | 75.7416 | 74.4242 | 72.7201 | 70.6997 | 68.7752 | 67.2906 | 60.9293 | 56.7038 | 55.4273
|  | CIPPENHAM | EE |  |  |  | 84.5541 | 82.5947 | 81.0631 | 79.5028 | 77.9589 | 76.4722 | 74.5752 | 72.415 | 70.3865 | 68.8028 | 61.861 | 57.9497 | 56.8671 | 87.2398 | 85.5559 | 84.2988 | 83.1854 | 82.1895 | 81.1661 | 79.9559 | 78.5446 | 77.1752 | 76.0171 | 70.0599 | 64.5375 | 56.8732 | 81.7418 | 79.861 | 78.4457 | 77.063 | 75.7416 | 74.4242 | 72.7201 | 70.6997 | 68.7752 | 67.2906 | 60.9293 | 57.4946 | 56.5946
|  | CIPPENHAM | HT |  |  |  | 84.9429 | 83.1304 | 81.4947 | 80.011 | 78.964 | 77.7783 | 76.3028 | 74.5232 | 72.7671 | 70.9671 | 62.2712 | 57.0354 | 55.5354 | 87.598 | 86.11 | 84.8672 | 83.9048 | 83.3181 | 82.6048 | 81.7722 | 80.7477 | 79.7048 | 78.6446 | 73.8987 | 71.1875 | 70.3385 | 82.1286 | 80.3947 | 78.8631 | 77.5283 | 76.6263 | 75.5467 | 74.2008 | 72.5844 | 70.9783 | 69.3375 | 61.3916 | 56.7038 | 55.4273
|  | CIPPENHAM | HE |  |  |  | 84.95 | 83.1498 | 81.5539 | 80.212 | 79.3824 | 78.2701 | 76.8661 | 75.1436 | 73.5906 | 71.9967 | 64.7701 | 60.8834 | 59.6752 | 87.5163 | 85.9478 | 84.6192 | 83.615 | 83.0508 | 82.2303 | 81.2844 | 80.1181 | 79.0048 | 77.8201 | 71.5222 | 65.9079 | 58.2773 | 82.1255 | 80.409 | 78.908 | 77.6854 | 76.9885 | 75.9722 | 74.6987 | 73.1467 | 71.7263 | 70.263 | 63.6201 | 60.064 | 59.0263
|  | CIPPENHAM | CF |  |  |  | 85.3224 | 83.9019 | 82.6978 | 81.7967 | 80.8518 | 80.2599 | 79.4712 | 78.6201 | 77.9252 | 77.165 | 71.8232 | 66.3436 | 61.3712 | 87.702 | 86.31 | 85.1508 | 84.3344 | 83.6069 | 83.0732 | 82.3008 | 81.4508 | 80.6548 | 79.7793 | 73.3222 | 63.462 | 47.011 | 82.45 | 81.0651 | 79.911 | 79.0824 | 78.2742 | 77.8028 | 77.113 | 76.3681 | 75.7436 | 75.0589 | 70.0059 | 65.0344 | 60.6161
MINETY GSP | CIRENCESTER BSP | CIRENCESTER BSP | MINIMUM HEADROOM | SP 02701 00368 | YES | 14.7 | 51.7624 | 47.7695 | 46.0399 | 44.0379 | 41.6206 | 39.2042 | 35.8246 | 32.2675 | 27.7175 | 23.3103 | 6.2644 | -7.1539 | -17.2182 | 68.3586 | 64.7075 | 63.381 | 61.8544 | 60.0075 | 57.9493 | 55.4442 | 52.6616 | 47.8718 | 43.8167 | 29.3493 | 14.8483 | -4.6415 | 53.1953 | 49.3422 | 47.7881 | 45.9963 | 43.7983 | 41.2799 | 38.1922 | 34.8208 | 29.585 | 25.0422 | 8.7483 | -3.6394 | -14.1497
|  | CIRENCESTER BSP | EE |  |  |  | 51.7624 | 47.7695 | 46.0399 | 44.0379 | 41.6206 | 39.2042 | 35.8246 | 32.5195 | 28.393 | 25.3348 | 10.7022 | -3.656 | -11.2621 | 68.3586 | 64.7075 | 63.381 | 61.8544 | 60.0075 | 58.1881 | 55.7738 | 53.5401 | 50.3391 | 48.1126 | 36.4381 | 19.4799 | 4.0218 | 53.1953 | 49.3422 | 47.7881 | 45.9963 | 43.7983 | 41.5759 | 38.4034 | 35.3769 | 31.3136 | 28.5228 | 14.984 | 0.20137 | -7.1527
|  | CIRENCESTER BSP | HT |  |  |  | 52.3369 | 48.4981 | 46.8726 | 44.8736 | 42.9257 | 39.6695 | 36.1001 | 32.2675 | 29.5063 | 25.7257 | 8.2573 | -7.1539 | -17.2182 | 69.0698 | 65.7238 | 64.6544 | 63.2687 | 62.1024 | 59.4697 | 57.0442 | 54.3197 | 52.7626 | 50.082 | 38.583 | 26.332 | 18.2218 | 53.7698 | 50.0789 | 48.6095 | 46.7728 | 45.0718 | 41.8391 | 38.4799 | 34.8208 | 32.3422 | 28.6769 | 12.0718 | -3.6394 | -13.8486
|  | CIRENCESTER BSP | HE |  |  |  | 52.3349 | 48.5634 | 46.944 | 44.8359 | 42.7981 | 39.3665 | 36.1185 | 32.643 | 27.7175 | 23.3103 | 6.2644 | -5.9325 | -15.6805 | 68.9453 | 65.5259 | 64.285 | 62.5616 | 61.0514 | 57.9493 | 55.4442 | 52.6616 | 47.8718 | 43.8167 | 29.3493 | 14.8483 | -4.6415 | 53.7647 | 50.1248 | 48.6361 | 46.6248 | 44.7769 | 41.2799 | 38.1922 | 34.8646 | 29.585 | 25.0422 | 8.7483 | -3.518 | -14.1497
|  | CIRENCESTER BSP | CF |  |  |  | 52.7298 | 49.341 | 48.2318 | 47.0634 | 45.5277 | 43.8644 | 42.1379 | 40.3614 | 38.4552 | 36.4001 | 26.0318 | 15.0838 | 4.5103 | 69.1678 | 65.9503 | 65.0514 | 64.1442 | 62.8728 | 61.4636 | 59.8126 | 58.0626 | 56.1575 | 54.0728 | 42.2116 | 24.5861 | -2.8884 | 54.132 | 50.8463 | 49.881 | 48.8636 | 47.485 | 45.9922 | 44.3993 | 42.7667 | 41.0054 | 39.0544 | 29.1228 | 18.4728 | 8.4657
FAWLEY GSP | COWES & WOOTTON COMMON BSP | COWES & WOOTTON COMMON BSP | MINIMUM HEADROOM | SZ 50519 94250 | YES | 25.075 | -51.8076 | -56.0024 | -60.5984 | -65.8127 | -71.1892 | -77.2198 | -85.7984 | -95.3351 | -105.1708 | -112.6443 | -150.2678 | -180.8688 | -197.83 | -7.9941 | -10.6706 | -13.7645 | -17.1114 | -20.6655 | -24.9982 | -30.6553 | -37.1267 | -43.8961 | -49.0308 | -75.788 | -101.4543 | -169.6788 | -42.2678 | -46.131 | -50.282 | -55.0127 | -59.9014 | -65.3453 | -73.0831 | -82.0555 | -91.3371 | -98.13 | -130.8249 | -157.2871 | -171.3769
|  | COWES & WOOTTON COMMON BSP | EE |  |  |  | -51.8076 | -56.0024 | -60.5984 | -65.8127 | -71.1892 | -77.2198 | -85.7984 | -95.3351 | -105.1708 | -112.6443 | -150.0076 | -175.0749 | -194.7565 | -7.9941 | -10.6706 | -13.7645 | -17.1114 | -20.6655 | -24.9982 | -30.6553 | -37.1267 | -43.8961 | -49.0308 | -75.788 | -101.0849 | -137.2665 | -42.2678 | -46.131 | -50.282 | -55.0127 | -59.9014 | -65.3453 | -73.0831 | -82.0555 | -91.3371 | -98.13 | -130.8249 | -152.43 | -169.0678
|  | COWES & WOOTTON COMMON BSP | HT |  |  |  | -49.9127 | -53.5831 | -57.8576 | -62.5535 | -67.9116 | -72.7392 | -80.5984 | -88.8565 | -96.6565 | -105.4555 | -150.2678 | -180.8688 | -197.83 | -6.0645 | -7.9696 | -10.2237 | -12.738 | -15.5829 | -18.2227 | -22.3931 | -27.0033 | -31.2359 | -36.3594 | -60.7227 | -75.5145 | -82.6227 | -40.2586 | -43.5208 | -47.3555 | -51.6024 | -56.4076 | -60.6524 | -67.6463 | -75.0667 | -82.0361 | -90.0116 | -130.2759 | -157.2871 | -171.3769
|  | COWES & WOOTTON COMMON BSP | HE |  |  |  | -50.0524 | -53.4167 | -57.3463 | -61.6912 | -66.6973 | -71.2331 | -77.98 | -85.2463 | -92.1463 | -99.9555 | -140.2769 | -167.028 | -179.0147 | -6.4737 | -8.5451 | -11.0471 | -13.8369 | -17.0696 | -20.1512 | -24.4482 | -29.4216 | -34.141 | -39.7982 | -70.5614 | -97.6931 | -130.79 | -40.4137 | -43.4433 | -47.0137 | -50.9759 | -55.4902 | -59.5035 | -65.5412 | -72.1259 | -78.3208 | -85.4484 | -121.8331 | -145.131 | -154.9514
|  | COWES & WOOTTON COMMON BSP | CF |  |  |  | -48.3565 | -50.4229 | -52.7831 | -55.2433 | -58.0892 | -61.2096 | -63.431 | -67.0616 | -70.1963 | -74.2198 | -102.0667 | -129.7953 | -154.7616 | -5.4176 | -6.8624 | -8.5594 | -10.4145 | -12.7624 | -15.7635 | -18.2798 | -22.0951 | -25.59 | -29.8961 | -59.1165 | -101.4543 | -169.6788 | -38.8892 | -40.7535 | -42.9269 | -45.1729 | -47.7422 | -50.5392 | -52.4576 | -55.7586 | -58.5882 | -62.2718 | -87.6576 | -112.4494 | -134.2963
COWLEY GSP | COWLEY LOCAL (2 X 45) | COWLEY LOCAL (2 X 45) | MINIMUM HEADROOM | SP 56113 03074 | YES | 58.837 | 50.2205 | 40.644 | 38.994 | 35.4669 | 32.5016 | 24.9312 | 19.6904 | 13.6516 | 1.3751 | -8.2055 | -34.9953 | -59.9321 | -83.2116 | 56.2417 | 47.2621 | 46.0213 | 42.8095 | 40.784 | 33.6289 | 29.3789 | 24.5187 | 11.6228 | 2.1156 | -21.468 | -48.2446 | -81.1201 | 50.1683 | 40.7886 | 39.3356 | 35.7697 | 33.1003 | 25.0044 | 19.9483 | 14.0065 | 0.24524 | -10.2354 | -37.0986 | -64.266 | -92.3915
|  | COWLEY LOCAL (2 X 45) | EE |  |  |  | 50.2205 | 40.644 | 38.994 | 36.5812 | 34.2792 | 30.0333 | 24.8118 | 20.7414 | 14.469 | 9.7414 | -13.1882 | -45.4963 | -57.4198 | 56.2417 | 47.2621 | 46.3039 | 44.7656 | 43.5279 | 40.4105 | 36.5483 | 34.2187 | 29.183 | 25.7759 | 7.4248 | -28.4129 | -46.0895 | 50.1683 | 40.7886 | 39.3356 | 37.2014 | 35.3677 | 31.3708 | 26.3708 | 22.934 | 16.7289 | 12.4228 | -9.1527 | -45.4741 | -58.9313
|  | COWLEY LOCAL (2 X 45) | HT |  |  |  | 50.5644 | 41.0562 | 39.1807 | 36.1608 | 33.7322 | 27.071 | 21.4965 | 14.9935 | 10.6649 | 3.9333 | -22.4147 | -53.7249 | -72.6943 | 56.5489 | 47.6968 | 46.4458 | 44.133 | 42.9269 | 37.0687 | 32.7718 | 27.7024 | 25.1514 | 19.6146 | -0.77415 | -32.1292 | -53.2629 | 50.6315 | 41.357 | 39.6152 | 36.7279 | 34.7381 | 27.7963 | 22.4442 | 16.0432 | 12.3167 | 5.5044 | -20.4384 | -55.419 | -77.7946
|  | COWLEY LOCAL (2 X 45) | HE |  |  |  | 50.5828 | 41.1297 | 39.1021 | 35.4669 | 32.5016 | 24.9312 | 19.6904 | 13.6516 | 1.3751 | -8.2055 | -34.9953 | -59.9321 | -83.2116 | 56.4897 | 47.5886 | 46.0213 | 42.8095 | 40.784 | 33.6289 | 29.3789 | 24.5187 | 11.6228 | 2.1156 | -21.468 | -48.2446 | -81.1201 | 50.6336 | 41.3998 | 39.4498 | 35.7697 | 33.1003 | 25.0044 | 19.9483 | 14.0065 | 0.24524 | -10.2354 | -37.0986 | -64.266 | -92.3915
|  | COWLEY LOCAL (2 X 45) | CF |  |  |  | 50.8583 | 41.6787 | 40.6072 | 38.8149 | 36.5047 | 33.3924 | 29.8751 | 26.2445 | 22.8628 | 19.4241 | 0.49243 | -17.5984 | -31.0157 | 56.6142 | 47.8254 | 47.1549 | 45.9259 | 44.2881 | 42.1299 | 39.4412 | 36.7973 | 34.3228 | 31.6116 | 15.1473 | -5.7221 | -29.9619 | 50.8611 | 41.8478 | 40.9447 | 39.383 | 37.3432 | 34.634 | 31.4136 | 28.1626 | 25.2218 | 22.1218 | 4.0208 | -14.3272 | -29.0721
COWLEY GSP | COWLEY LOCAL (2 X 90) | COWLEY LOCAL (2 X 90) | MINIMUM HEADROOM | SP 56113 03074 | YES | 30.022 | 40.993 | 33.7807 | 31.5052 | 29.092 | 26.9022 | 15.5457 | 9.6079 | 3.8447 | -1.6655 | -5.9635 | -21.338 | -28.3237 | -30.0604 | 54.3349 | 47.8318 | 46.0634 | 44.1144 | 42.392 | 31.6743 | 27.8426 | 23.6457 | 19.3743 | 15.8773 | 1.0559 | -16.1308 | -52.9206 | 42.7573 | 35.9154 | 33.9164 | 31.7062 | 29.6828 | 18.4936 | 13.3732 | 8.0998 | 2.9661 | -0.94003 | -14.7553 | -20.54 | -21.8972
|  | COWLEY LOCAL (2 X 90) | EE |  |  |  | 40.993 | 33.7807 | 31.5052 | 29.092 | 26.9022 | 15.5457 | 9.6079 | 3.8447 | -1.6655 | -5.9635 | -21.338 | -27.6594 | -28.1472 | 54.3349 | 47.8318 | 46.0634 | 44.1144 | 42.392 | 31.6743 | 27.8426 | 23.6457 | 19.3743 | 15.8773 | 1.0559 | -10.7104 | -27.6574 | 42.7573 | 35.9154 | 33.9164 | 31.7062 | 29.6828 | 18.4936 | 13.3732 | 8.0998 | 2.9661 | -0.94003 | -14.7553 | -20.088 | -20.3962
|  | COWLEY LOCAL (2 X 90) | HT |  |  |  | 41.992 | 34.546 | 32.793 | 31.0654 | 28.5899 | 17.962 | 11.4222 | 6.8671 | 2.2396 | -2.3155 | -19.4798 | -28.3237 | -30.0604 | 55.2257 | 48.9062 | 47.7297 | 46.6073 | 44.8511 | 35.0008 | 31.2692 | 28.1334 | 24.8059 | 21.6151 | 10.6834 | 5.6273 | 4.413 | 43.6532 | 36.7042 | 35.1134 | 33.5624 | 31.2736 | 20.8559 | 15.2151 | 11.0436 | 6.762 | 2.6049 | -12.7227 | -20.54 | -21.8972
|  | COWLEY LOCAL (2 X 90) | HE |  |  |  | 41.8767 | 35.1103 | 33.046 | 31.195 | 29.2144 | 18.8345 | 13.3467 | 8.8845 | 4.2651 | 0.16915 | -16.6574 | -23.387 | -25.2737 | 54.9594 | 48.7664 | 47.1746 | 45.7093 | 44.1848 | 34.2436 | 30.6447 | 27.3794 | 23.6957 | 20.2406 | 3.4712 | -8.9594 | -26.2849 | 43.543 | 37.0858 | 35.2542 | 33.592 | 31.8195 | 21.6457 | 16.8569 | 12.862 | 8.6294 | 4.8528 | -10.389 | -16.3053 | -17.7992
|  | COWLEY LOCAL (2 X 90) | CF |  |  |  | 42.6012 | 36.6236 | 35.5562 | 34.6399 | 33.6083 | 24.213 | 22.5671 | 19.9059 | 17.0712 | 13.8222 | -4.8798 | -15.4166 | -23.6778 | 55.3696 | 49.5328 | 48.396 | 47.3664 | 46.2716 | 36.8192 | 35.0589 | 32.4845 | 29.7498 | 26.5875 | 5.8896 | -16.1308 | -52.9206 | 44.2134 | 38.4297 | 37.4389 | 36.6042 | 35.6991 | 26.4783 | 25.0538 | 22.7181 | 20.2385 | 17.362 | 0.43242 | -8.9625 | -16.1962
BRAMLEY (FLEE) | COXMOOR WOOD BSP | COXMOOR WOOD BSP | MINIMUM HEADROOM | SU 78324 50817 | YES | 22.68 | 41.798 | 39.1867 | 36.6459 | 34.6755 | 32.7082 | 29.8969 | 25.5551 | 21.052 | 16.2306 | 12.5663 | -6.85 | -22.1765 | -30.7857 | 57.0849 | 55.0839 | 53.1349 | 51.6186 | 50.0512 | 47.7716 | 44.7614 | 41.5788 | 38.092 | 35.4716 | 21.1094 | 5.3563 | -33.2386 | 41.6635 | 39.1982 | 36.7135 | 34.9012 | 33.0941 | 30.339 | 26.2594 | 22.0614 | 17.49 | 14.2328 | -2.5314 | -16.1998 | -23.658
|  | COXMOOR WOOD BSP | EE |  |  |  | 41.798 | 39.1867 | 36.6459 | 34.6755 | 32.7082 | 29.8969 | 25.5551 | 21.052 | 16.2306 | 12.5663 | -6.352 | -19.7959 | -29.7347 | 57.0849 | 55.0839 | 53.1349 | 51.6186 | 50.0512 | 47.7716 | 44.7614 | 41.5788 | 38.092 | 35.4716 | 21.1094 | 6.7686 | -13.4294 | 41.6635 | 39.1982 | 36.7135 | 34.9012 | 33.0941 | 30.339 | 26.2594 | 22.0614 | 17.49 | 14.2328 | -2.3223 | -14.1539 | -22.8253
|  | COXMOOR WOOD BSP | HT |  |  |  | 42.9031 | 40.6806 | 38.6439 | 36.6357 | 34.3622 | 32.2214 | 28.9775 | 25.0928 | 20.6786 | 16.0949 | -6.85 | -22.1765 | -30.7857 | 58.1818 | 56.7369 | 55.4645 | 54.2084 | 52.7135 | 51.3257 | 49.6747 | 47.5165 | 44.9308 | 42.2165 | 29.6257 | 22.2237 | 18.4451 | 42.8563 | 40.8349 | 38.9165 | 37.0369 | 34.8543 | 32.8553 | 30.0716 | 26.5951 | 22.5441 | 18.3186 | -2.5314 | -16.1998 | -23.658
|  | COXMOOR WOOD BSP | HE |  |  |  | 42.8745 | 40.7326 | 38.7796 | 36.849 | 34.6653 | 32.648 | 29.949 | 26.6163 | 22.748 | 18.7837 | -1.6969 | -15.3296 | -21.398 | 57.9369 | 56.3175 | 54.8339 | 53.3451 | 51.5951 | 49.9584 | 48.1145 | 45.7206 | 42.8502 | 39.838 | 23.3073 | 8.5594 | -9.96 | 42.8257 | 40.8584 | 39.0073 | 37.1992 | 35.0859 | 33.2124 | 30.8675 | 27.8502 | 24.24 | 20.5339 | 1.9104 | -10.2059 | -15.4396
|  | COXMOOR WOOD BSP | CF |  |  |  | 43.6857 | 42.1541 | 40.9877 | 39.8367 | 38.6286 | 37.2051 | 36.0663 | 35.0367 | 33.6041 | 31.7633 | 18.4837 | 3.6041 | -9.7643 | 58.3849 | 57.0145 | 55.9104 | 54.7726 | 53.5206 | 51.9716 | 50.5114 | 49.0655 | 47.2461 | 45.0277 | 29.3267 | 5.3563 | -33.2386 | 43.5665 | 42.1369 | 41.0043 | 39.8941 | 38.7043 | 37.288 | 36.2033 | 35.292 | 33.9339 | 32.1175 | 19.6084 | 6.5482 | -5.261
IVER 132KV | DENHAM | DENHAM B | MINIMUM HEADROOM | TQ 01785 87618 | YES | 3.37 | 0 | 0 | 0 | 0 | 114.8 | 114.8 | 114.8 | 114.8 | 114.8 | 114.8 | 114.8 | 114.8 | 114.8 | 0 | 0 | 0 | 0 | 109.4 | 109.4 | 109.4 | 109.4 | 109.4 | 109.4 | 109.4 | 109.4 | 109.4 | 0 | 0 | 0 | 0 | 111.2 | 111.2 | 111.2 | 111.2 | 111.2 | 111.2 | 111.2 | 111.2 | 111.2
|  | DENHAM B | EE |  |  |  | 0 | 0 | 0 | 0 | 114.8 | 114.8 | 114.8 | 114.8 | 114.8 | 114.8 | 114.8 | 114.8 | 114.8 | 0 | 0 | 0 | 0 | 109.4 | 109.4 | 109.4 | 109.4 | 109.4 | 109.4 | 109.4 | 109.4 | 109.4 | 0 | 0 | 0 | 0 | 111.2 | 111.2 | 111.2 | 111.2 | 111.2 | 111.2 | 111.2 | 111.2 | 111.2
|  | DENHAM B | HT |  |  |  | 0 | 0 | 0 | 0 | 114.8 | 114.8 | 114.8 | 114.8 | 114.8 | 114.8 | 114.8 | 114.8 | 114.8 | 0 | 0 | 0 | 0 | 109.4 | 109.4 | 109.4 | 109.4 | 109.4 | 109.4 | 109.4 | 109.4 | 109.4 | 0 | 0 | 0 | 0 | 111.2 | 111.2 | 111.2 | 111.2 | 111.2 | 111.2 | 111.2 | 111.2 | 111.2
|  | DENHAM B | HE |  |  |  | 0 | 0 | 0 | 0 | 114.8 | 114.8 | 114.8 | 114.8 | 114.8 | 114.8 | 114.8 | 114.8 | 114.8 | 0 | 0 | 0 | 0 | 109.4 | 109.4 | 109.4 | 109.4 | 109.4 | 109.4 | 109.4 | 109.4 | 109.4 | 0 | 0 | 0 | 0 | 111.2 | 111.2 | 111.2 | 111.2 | 111.2 | 111.2 | 111.2 | 111.2 | 111.2
|  | DENHAM B | CF |  |  |  | 0 | 0 | 0 | 0 | 114.8 | 114.8 | 114.8 | 114.8 | 114.8 | 114.8 | 114.8 | 114.8 | 114.8 | 0 | 0 | 0 | 0 | 109.4 | 109.4 | 109.4 | 109.4 | 109.4 | 109.4 | 109.4 | 109.4 | 109.4 | 0 | 0 | 0 | 0 | 111.2 | 111.2 | 111.2 | 111.2 | 111.2 | 111.2 | 111.2 | 111.2 | 111.2
IVER 132KV | DENHAM | DENHAM | MINIMUM HEADROOM | TQ 01785 87618 | YES | 6.032 | 56.2472 | 54.8513 | 53.1023 | 53.8415 | 52.613 | 51.0844 | 48.1446 | 45.7078 | 42.9334 | 40.7548 | 28.5762 | 18.7762 | 13.2752 | 71.9952 | 70.9809 | 69.6799 | 73.3983 | 72.6299 | 71.5105 | 69.5768 | 68.0666 | 66.2115 | 64.8166 | 58.0503 | 51.4758 | 37.233 | 56.9687 | 55.7013 | 54.1207 | 56.6136 | 55.5003 | 54.0666 | 51.3503 | 49.0666 | 46.4789 | 44.4289 | 33.6054 | 25.1003 | 20.5738
|  | DENHAM | EE |  |  |  | 56.2472 | 54.8513 | 53.1023 | 53.8415 | 52.613 | 51.0844 | 48.1446 | 45.7078 | 42.9334 | 40.7548 | 29.4783 | 20.7201 | 14.1017 | 71.9952 | 70.9809 | 69.6799 | 73.3983 | 72.6299 | 71.5105 | 69.5768 | 68.0666 | 66.2115 | 64.8166 | 58.0503 | 51.4758 | 42.6891 | 56.9687 | 55.7013 | 54.1207 | 56.6136 | 55.5003 | 54.0666 | 51.3503 | 49.0666 | 46.4789 | 44.4289 | 34.3125 | 26.8197 | 21.3003
|  | DENHAM | HT |  |  |  | 56.9462 | 55.7105 | 54.3258 | 55.4956 | 54.4078 | 52.8558 | 50.5568 | 47.7456 | 45.1354 | 42.0997 | 28.5762 | 18.7762 | 13.2752 | 72.7442 | 71.983 | 71.1176 | 75.3003 | 74.7523 | 73.7074 | 72.5901 | 70.9891 | 69.5605 | 67.7442 | 61.035 | 56.7472 | 54.5564 | 57.6687 | 56.535 | 55.2809 | 58.1299 | 57.1574 | 55.7125 | 53.6105 | 51.0095 | 48.6278 | 45.8156 | 33.6054 | 25.1003 | 20.5738
|  | DENHAM | HE |  |  |  | 56.9523 | 55.835 | 54.4942 | 55.7844 | 54.7834 | 53.265 | 51.465 | 49.4548 | 46.9813 | 44.7691 | 32.667 | 24.2823 | 20.2089 | 72.637 | 71.8523 | 70.8646 | 75.0136 | 74.4176 | 73.2666 | 72.1819 | 70.8901 | 69.1605 | 67.6503 | 59.4146 | 52.9615 | 45.2707 | 57.6656 | 56.6513 | 55.4187 | 58.3921 | 57.5054 | 56.0799 | 54.4044 | 52.5544 | 50.2483 | 48.2003 | 37.1799 | 29.9921 | 26.6789
|  | DENHAM | CF |  |  |  | 57.4452 | 56.7125 | 55.9105 | 57.5497 | 57.065 | 56.1721 | 55.2119 | 54.0701 | 53.2323 | 52.3854 | 44.8232 | 36.3946 | 27.9732 | 72.8881 | 72.2605 | 71.5625 | 75.8023 | 75.4585 | 74.6299 | 73.687 | 72.5768 | 71.7299 | 70.8472 | 63.4003 | 53.2493 | 37.233 | 58.1248 | 57.4615 | 56.7381 | 60.0299 | 59.6268 | 58.8074 | 57.937 | 56.8962 | 56.1156 | 55.3258 | 48.2585 | 40.4983 | 33.0064
COWLEY GSP | DRAYTON BSP | DRAYTON BSP | MINIMUM HEADROOM | SU 46684 92706 | YES | 55.218 | -16.1814 | -22.4755 | -27.6204 | -32.3286 | -47.8245 | -56.9388 | -65.6847 | -73.301 | -81.0398 | -87.2265 | -121.9005 | -148.9281 | -167.1454 | 1.6086 | -3.3733 | -6.759 | -9.7733 | -25.5814 | -32.7549 | -39.5896 | -45.3233 | -51.4835 | -57.4906 | -85.4789 | -110.2758 | -147.5228 | -19.8189 | -25.661 | -30.1488 | -34.2671 | -51.4528 | -60.0396 | -68.4651 | -75.7324 | -83.3304 | -89.1171 | -121.3258 | -148.0676 | -165.7105
|  | DRAYTON BSP | EE |  |  |  | -16.1814 | -22.4755 | -27.6204 | -32.3286 | -47.8245 | -56.9388 | -65.6847 | -73.301 | -81.0398 | -87.2265 | -117.5362 | -142.3495 | -159.5291 | 1.6086 | -3.3733 | -6.759 | -9.7733 | -25.5814 | -32.7549 | -39.5896 | -45.3233 | -51.4835 | -56.2294 | -80.3217 | -107.2176 | -136.5248 | -19.8189 | -25.661 | -30.1488 | -34.2671 | -51.4528 | -60.0396 | -68.4651 | -75.7324 | -83.3304 | -89.1171 | -116.5289 | -140.9646 | -156.8534
|  | DRAYTON BSP | HT |  |  |  | -15.161 | -21.1418 | -26.253 | -31.9714 | -46.8469 | -56.6112 | -64.6224 | -72.0724 | -78.9204 | -86.7275 | -121.9005 | -148.9281 | -167.1454 | 2.7821 | -1.6141 | -4.6447 | -8.26 | -23.0967 | -30.6539 | -36.3049 | -41.4845 | -45.9233 | -51.6549 | -75.1248 | -94.3554 | -107.2625 | -18.7761 | -24.2141 | -28.6202 | -33.7335 | -50.2324 | -59.5692 | -67.1702 | -74.2447 | -80.5641 | -88.1151 | -121.3258 | -148.0676 | -165.7105
|  | DRAYTON BSP | HE |  |  |  | -15.161 | -21 | -26.0296 | -31.1561 | -45.7204 | -55.9296 | -63.0622 | -69.6296 | -78.2 | -85.7653 | -118.3587 | -141.326 | -158.6219 | 2.5198 | -2.0416 | -5.3773 | -8.9049 | -23.8722 | -32.3498 | -37.9314 | -43.0722 | -50.8151 | -57.4906 | -85.4789 | -110.2758 | -143.1085 | -18.7904 | -24.11 | -28.4845 | -33.0926 | -49.3324 | -59.2233 | -65.9722 | -72.1967 | -80.9477 | -88.4845 | -119.3554 | -141.4217 | -158.937
|  | DRAYTON BSP | CF |  |  |  | -14.2712 | -19.3 | -23.1316 | -26.7612 | -40.952 | -48.0377 | -53.1959 | -57.1245 | -60.8561 | -64.452 | -87.8454 | -108.1913 | -127.0434 | 2.9729 | -1.2559 | -3.8947 | -6.4294 | -21.6396 | -27.6028 | -32.4079 | -36.16 | -39.8192 | -43.5192 | -68.1615 | -98.9289 | -147.5228 | -17.9781 | -22.5661 | -25.7712 | -28.8651 | -44.8284 | -51.3988 | -56.2477 | -59.8753 | -63.3263 | -66.7335 | -88.9656 | -107.7768 | -124.7687
EALING GSP | EALING 22kV | EALING 22kV | MINIMUM HEADROOM | TQ 18371 79475 | YES | 20.354 | 45.5163 | 42.1759 | 39.7249 | 37.2892 | 34.43 | 30.8647 | 27.7178 | 23.7453 | 19.8269 | 16.9239 | 5.9208 | -3.2445 | -7.3935 | 53.4082 | 50.73 | 48.8647 | 46.9637 | 44.7422 | 41.8616 | 39.1994 | 35.8096 | 32.3708 | 29.5657 | 15.6861 | -8.9139 | -60.869 | 44.2929 | 41.2239 | 38.981 | 36.7157 | 34.0606 | 30.7065 | 27.7606 | 24.0004 | 20.2984 | 17.5504 | 7.4586 | -0.50163 | -4.071
|  | EALING 22kV | EE |  |  |  | 45.5163 | 42.1759 | 39.7249 | 37.2892 | 34.43 | 30.8647 | 27.7178 | 23.7453 | 19.8269 | 16.9239 | 5.9208 | -1.2812 | -5.8241 | 53.4082 | 50.73 | 48.8647 | 46.9637 | 44.7422 | 41.8616 | 39.1994 | 35.8096 | 32.3708 | 29.5657 | 15.6861 | 0.038163 | -26.2567 | 44.2929 | 41.2239 | 38.981 | 36.7157 | 34.0606 | 30.7065 | 27.7606 | 24.0004 | 20.2984 | 17.5504 | 7.4586 | 1.2922 | -2.7567
|  | EALING 22kV | HT |  |  |  | 46.3224 | 43.0157 | 40.8973 | 38.6729 | 35.3402 | 32.0565 | 29.0892 | 26.0576 | 23.4759 | 21.1586 | 7.4565 | -3.2445 | -7.3935 | 54.2908 | 51.9535 | 50.7596 | 49.4647 | 47.2157 | 44.9851 | 42.9718 | 40.8014 | 38.9504 | 37.3382 | 28.6147 | 22.8371 | 20.8402 | 45.0908 | 42.0984 | 40.2392 | 38.2371 | 35.1229 | 32.0422 | 29.282 | 26.4188 | 23.9739 | 21.7963 | 9.0759 | -0.50163 | -4.071
|  | EALING 22kV | HE |  |  |  | 46.2194 | 43.2729 | 41.2963 | 39.4269 | 37.33 | 34.1769 | 31.4045 | 28.2933 | 26.0371 | 23.3861 | 12.4229 | 5.7616 | 3.6688 | 53.9918 | 51.6463 | 50.1831 | 48.7545 | 47.1484 | 44.5555 | 42.1616 | 39.4351 | 37.1688 | 34.5167 | 20.2218 | 4.2055 | -20.97 | 44.9918 | 42.3106 | 40.5494 | 38.8535 | 36.9565 | 34.0157 | 31.429 | 28.5167 | 26.4545 | 23.9494 | 13.8178 | 7.9484 | 6.1831
|  | EALING 22kV | CF |  |  |  | 46.8092 | 44.4035 | 43.3259 | 42.2218 | 41.1576 | 40.0606 | 38.8892 | 37.1984 | 35.1759 | 33.5229 | 22.4831 | 14.9494 | 7.7882 | 54.2612 | 52.1116 | 51.0402 | 49.8157 | 48.581 | 47.1412 | 45.1994 | 42.778 | 40.0861 | 37.531 | 19.229 | -8.9139 | -60.869 | 45.5265 | 43.3239 | 42.3524 | 41.3198 | 40.3239 | 39.3035 | 38.1596 | 36.531 | 34.6147 | 33.0749 | 22.88 | 15.9065 | 9.529
LALEHAM | EAST BEDFONT A | EAST BEDFONT A | MINIMUM HEADROOM | TQ 08394 73826 | YES | 12.907 | 19.3365 | 18.1069 | 25.0916 | 23.7079 | 21.6212 | 18.8579 | 16.4702 | 12.8161 | 9.0794 | 6.3457 | -4.4268 | -12.2176 | -16.489 | 25.1906 | 24.3375 | 30.0937 | 28.9345 | 27.3059 | 25.0671 | 23.2171 | 20.4712 | 17.6304 | 15.4784 | 4.9906 | -12.4512 | -48.3339 | 17.6416 | 16.5518 | 23.5294 | 22.3651 | 20.763 | 18.4232 | 16.2181 | 12.9732 | 9.6794 | 7.2375 | -2.4523 | -9.4727 | -13.4237
|  | EAST BEDFONT A | EE |  |  |  | 19.3365 | 18.1069 | 25.0916 | 23.7079 | 21.6212 | 18.8579 | 16.4702 | 12.8161 | 9.0794 | 6.3457 | -4.4268 | -11.2063 | -16.3696 | 25.1906 | 24.3375 | 30.0937 | 28.9345 | 27.3059 | 25.0671 | 23.2171 | 20.4712 | 17.6304 | 15.4784 | 4.9906 | -6.5186 | -25.1451 | 17.6416 | 16.5518 | 23.5294 | 22.3651 | 20.763 | 18.4232 | 16.2181 | 12.9732 | 9.6794 | 7.2375 | -2.4523 | -8.6961 | -13.4237
|  | EAST BEDFONT A | HT |  |  |  | 19.8212 | 18.3937 | 25.5875 | 24.0692 | 21.9253 | 19.8294 | 17.1335 | 14.0814 | 10.9692 | 8.8845 | -3.9829 | -12.2176 | -16.489 | 25.6916 | 24.8937 | 31.0886 | 30.2998 | 28.9018 | 27.5957 | 25.9406 | 24.0814 | 22.1855 | 21.0539 | 13.7447 | 9.5896 | 7.6263 | 18.1263 | 16.9059 | 24.1426 | 22.8304 | 20.8416 | 18.9335 | 16.5243 | 13.9212 | 11.2763 | 9.4773 | -1.9237 | -9.4727 | -13.4094
|  | EAST BEDFONT A | HE |  |  |  | 19.7845 | 18.7396 | 25.9763 | 24.6835 | 23.16 | 21.2661 | 18.8916 | 15.9692 | 12.7579 | 10.5559 | -1.1645 | -8.2819 | -11.1798 | 25.513 | 24.7906 | 30.7314 | 29.8212 | 28.7069 | 27.1549 | 25.2151 | 22.8998 | 20.4202 | 18.6181 | 6.8559 | -5.2461 | -22.8645 | 18.0875 | 17.1824 | 24.413 | 23.2732 | 21.9181 | 20.1845 | 18.0243 | 15.4437 | 12.759 | 10.8243 | 0.46509 | -6.0921 | -8.7829
|  | EAST BEDFONT A | CF |  |  |  | 20.4161 | 19.9967 | 27.9559 | 27.2437 | 26.56 | 25.8345 | 25.1875 | 23.8365 | 22.1569 | 20.5324 | 8.9181 | 1.2171 | -5.3053 | 25.812 | 25.3406 | 31.6335 | 30.8732 | 30.1212 | 29.0998 | 27.9212 | 26.0875 | 24.0732 | 22.0416 | 7.8855 | -12.4512 | -48.3339 | 18.6324 | 18.2477 | 26.11 | 25.463 | 24.8335 | 24.1651 | 23.5477 | 22.3008 | 20.913 | 19.6069 | 9.8467 | 2.9171 | -3.0992
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | FAREHAM T1A T2A (90MVAS) | MINIMUM HEADROOM | SU 56534 04031 | YES | 24.907 | 25.6445 | 22.6679 | 19.2526 | 16.4638 | 13.1281 | 9.1873 | 2.9873 | -4.0811 | -11.4729 | -17.3137 | -43.5004 | -60.3658 | -69.6617 | 35.8426 | 33.8355 | 31.3794 | 29.4028 | 27.011 | 24.1977 | 20.014 | 15.0977 | 9.91 | 5.9834 | -13.9839 | -38.3809 | -93.7819 | 25.8232 | 23.1375 | 20.0222 | 17.5467 | 14.5712 | 11.0222 | 5.413 | -1.0043 | -7.688 | -12.8482 | -35.5115 | -50.8135 | -59.3084
|  | FAREHAM T1A T2A (90MVAS) | EE |  |  |  | 25.6445 | 22.6679 | 19.2526 | 16.4638 | 13.1281 | 9.1873 | 2.9873 | -4.0811 | -11.4729 | -17.3137 | -42.526 | -57.3198 | -68.4137 | 35.8426 | 33.8355 | 31.3794 | 29.4028 | 27.011 | 24.1977 | 20.014 | 15.0977 | 9.91 | 5.9834 | -13.9839 | -32.8931 | -62.0339 | 25.8232 | 23.1375 | 20.0222 | 17.5467 | 14.5712 | 11.0222 | 5.413 | -1.0043 | -7.688 | -12.8482 | -35.0227 | -48.2717 | -58.3951
|  | FAREHAM T1A T2A (90MVAS) | HT |  |  |  | 26.8363 | 24.0659 | 21.0965 | 17.9077 | 14.2036 | 9.92 | 4.8853 | -1.0106 | -7.5688 | -14.1209 | -43.5004 | -60.3658 | -69.6617 | 36.8651 | 35.3151 | 33.7202 | 32.0059 | 30.0151 | 27.4477 | 24.9528 | 21.7936 | 17.9773 | 14.1783 | -1.7604 | -9.7931 | -13.9502 | 27.0161 | 24.6049 | 22.0028 | 19.1814 | 15.8977 | 12.0661 | 7.7018 | 2.5283 | -3.3615 | -9.2309 | -35.5115 | -50.8135 | -59.3084
|  | FAREHAM T1A T2A (90MVAS) | HE |  |  |  | 26.8302 | 24.3842 | 21.672 | 18.7945 | 15.371 | 11.8138 | 7.7077 | 2.6506 | -3.4402 | -9.5209 | -36.4055 | -51.5841 | -58.6923 | 36.5875 | 34.9018 | 33.0681 | 31.1263 | 28.8089 | 26.3222 | 23.6498 | 20.2671 | 15.9896 | 11.5865 | -10.8349 | -30.5115 | -57.9053 | 26.9926 | 24.8334 | 22.4294 | 19.8569 | 16.7998 | 13.6355 | 10.0712 | 5.6304 | 0.1967 | -5.2543 | -29.3543 | -43.087 | -49.3451
|  | FAREHAM T1A T2A (90MVAS) | CF |  |  |  | 27.8567 | 26.2189 | 24.6496 | 22.8996 | 20.9679 | 18.6955 | 16.5006 | 15.0118 | 12.7098 | 9.47 | -14.1658 | -30.5351 | -45.0392 | 37.0936 | 35.7202 | 34.3916 | 32.8794 | 31.1794 | 29.0304 | 26.6059 | 24.6824 | 22.06 | 18.6518 | -6.2472 | -38.3809 | -93.7819 | 27.9202 | 26.4722 | 25.0722 | 23.5059 | 21.7753 | 19.712 | 17.7202 | 16.4753 | 14.4569 | 11.5538 | -9.4258 | -24.1002 | -36.8941
LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | FAREHAM T1B T2B (1X90, 1X60MVA) | MINIMUM HEADROOM | SU 56534 04031 | YES | 36.639 | 36.2718 | 17.9814 | 16.0712 | 14.8008 | 12.6212 | 10.7906 | 5.2914 | 1.8098 | -1.5402 | -3.9096 | -15.8218 | -26.2922 | -32.2331 | 43.4003 | 25.4671 | 23.9865 | 23.011 | 21.1998 | 19.6416 | 15.0129 | 12.3792 | 9.7629 | 7.8271 | -2.9708 | -19.6392 | -56.5769 | 36.7493 | 18.4559 | 16.5386 | 15.4161 | 13.3181 | 11.5967 | 6.3302 | 3.0333 | -0.16266 | -2.3076 | -12.679 | -21.8167 | -26.6596
|  | FAREHAM T1B T2B (1X90, 1X60MVA) | EE |  |  |  | 36.2718 | 17.9814 | 16.0712 | 14.8008 | 12.6212 | 10.7906 | 5.2914 | 1.8098 | -1.5402 | -3.9096 | -15.8218 | -24.6147 | -31.7055 | 43.4003 | 25.4671 | 23.9865 | 23.011 | 21.1998 | 19.6416 | 15.0129 | 12.3792 | 9.7629 | 7.8271 | -2.9708 | -15.1749 | -34.7218 | 36.7493 | 18.4559 | 16.5386 | 15.4161 | 13.3181 | 11.5967 | 6.3302 | 3.0333 | -0.16266 | -2.3076 | -12.679 | -20.3025 | -26.2331
|  | FAREHAM T1B T2B (1X90, 1X60MVA) | HT |  |  |  | 36.9769 | 18.7681 | 17.3977 | 15.8579 | 14.109 | 12.5141 | 7.7149 | 4.8271 | 2.3108 | -0.45449 | -15.7239 | -26.2922 | -32.2331 | 44.0759 | 26.3732 | 25.5069 | 24.5447 | 23.4661 | 22.4784 | 18.8649 | 17.1873 | 15.7343 | 14.0547 | 5.6078 | 0.4404 | -2.0178 | 37.6238 | 19.5059 | 18.1886 | 16.6784 | 14.9743 | 13.4947 | 9.0312 | 6.371 | 4.1149 | 1.52 | -12.4014 | -21.8167 | -26.6596
|  | FAREHAM T1B T2B (1X90, 1X60MVA) | HE |  |  |  | 36.9187 | 18.8681 | 17.4304 | 15.9671 | 14.26 | 13.1732 | 8.4312 | 5.7833 | 3.5118 | 1.0302 | -11.8953 | -21.0831 | -25.0504 | 43.8534 | 26.1008 | 24.9222 | 23.7559 | 22.3722 | 21.4304 | 17.3914 | 15.4108 | 13.6129 | 11.5129 | -0.69735 | -13.5718 | -31.7698 | 37.5524 | 19.5743 | 18.2079 | 16.7671 | 15.1161 | 14.1977 | 9.6659 | 7.2088 | 5.17 | 2.8271 | -8.9892 | -16.9259 | -20.1576
|  | FAREHAM T1B T2B (1X90, 1X60MVA) | CF |  |  |  | 37.6514 | 19.9294 | 19.0059 | 18.0865 | 16.9947 | 15.9375 | 12.8567 | 12.0037 | 10.6802 | 9.419 | 0.85979 | -8.2596 | -16.4106 | 44.2687 | 26.5651 | 25.6222 | 24.6273 | 23.4569 | 22.2273 | 18.772 | 17.4598 | 15.7486 | 13.9741 | 1.372 | -19.6392 | -56.5769 | 38.2105 | 20.5355 | 19.61 | 18.7141 | 17.6192 | 16.5426 | 13.5435 | 12.771 | 11.4884 | 10.2424 | 2.17 | -5.9055 | -12.9708
BRAMLEY (FLEE) | FERNHURST | FERNHURST | MINIMUM HEADROOM | SU 72730 39772 | YES | 25.019 | 78.5682 | 74.5764 | 73.5662 | 72.8111 | 71.6315 | 70.3458 | 68.5897 | 67.155 | 65.4213 | 64.1805 | 57.2631 | 52.4325 | 49.956 | 84.2817 | 80.6266 | 79.9215 | 79.4256 | 78.6246 | 77.7399 | 76.5725 | 75.6113 | 74.3868 | 73.5327 | 68.7511 | 64.1756 | 51.8878 | 78.9827 | 75.1001 | 74.1521 | 73.4797 | 72.3868 | 71.1909 | 69.5409 | 68.2235 | 66.5654 | 65.4592 | 59.4817 | 55.3256 | 53.2848
|  | FERNHURST | EE |  |  |  | 78.5682 | 74.5764 | 73.5662 | 72.8111 | 71.6315 | 70.3458 | 68.5897 | 67.155 | 65.4213 | 64.1805 | 57.2631 | 53.2805 | 50.7897 | 84.2817 | 80.6266 | 79.9215 | 79.4256 | 78.6246 | 77.7399 | 76.5725 | 75.6113 | 74.3868 | 73.5327 | 68.7511 | 64.3388 | 58.095 | 78.9827 | 75.1001 | 74.1521 | 73.4797 | 72.3868 | 71.1909 | 69.5409 | 68.2235 | 66.5654 | 65.4592 | 59.4817 | 56.0562 | 53.9695
|  | FERNHURST | HT |  |  |  | 78.9254 | 75.0244 | 74.2244 | 73.3039 | 72.3213 | 71.4652 | 69.909 | 68.4264 | 66.8386 | 65.1917 | 57.2662 | 52.4325 | 49.956 | 84.598 | 81.0848 | 80.6246 | 80.0766 | 79.5021 | 79.0613 | 78.2501 | 77.4368 | 76.545 | 75.5613 | 71.3409 | 68.996 | 67.9827 | 79.3409 | 75.5572 | 74.8246 | 73.9888 | 73.1001 | 72.3572 | 70.9623 | 69.6072 | 68.1552 | 66.6409 | 59.5511 | 55.3256 | 53.2848
|  | FERNHURST | HE |  |  |  | 78.9223 | 75.0886 | 74.3254 | 73.4692 | 72.5182 | 71.7376 | 70.4111 | 69.1101 | 67.7366 | 66.3203 | 59.0774 | 55.5407 | 53.7223 | 84.5307 | 80.9837 | 80.4552 | 79.8644 | 79.2113 | 78.7144 | 77.8817 | 77.0297 | 76.1062 | 75.1001 | 69.8154 | 65.5521 | 59.5062 | 79.3378 | 75.6072 | 74.9103 | 74.1307 | 73.2695 | 72.5899 | 71.4011 | 70.2123 | 68.945 | 67.6388 | 61.1756 | 58.1664 | 56.6531
|  | FERNHURST | CF |  |  |  | 79.158 | 75.5162 | 74.957 | 74.3846 | 73.7172 | 72.955 | 72.1805 | 71.8029 | 71.0131 | 70.2223 | 65.1937 | 60.9335 | 56.8019 | 84.6511 | 81.1848 | 80.7235 | 80.2521 | 79.7225 | 79.097 | 78.4174 | 77.9909 | 77.246 | 76.4797 | 71.3174 | 64.1756 | 51.8878 | 79.5541 | 75.999 | 75.4807 | 74.9572 | 74.3521 | 73.6664 | 72.9623 | 72.6368 | 71.9041 | 71.1735 | 66.5439 | 62.8592 | 59.2541
LOVEDEAN GSP | FORT WIDLEY | FORT WIDLEY | MINIMUM HEADROOM | SU 64948 05441 | YES | 13.509 | 40.9773 | 39.1599 | 37.9701 | 36.3446 | 34.7109 | 33.2864 | 31.0232 | 67.2762 | 64.8273 | 62.915 | 53.2803 | 46.5283 | 43.5589 | 46.4915 | 45.0824 | 44.2548 | 43.066 | 41.8354 | 40.8028 | 39.2324 | 74.0681 | 72.2609 | 70.9344 | 63.5915 | 52.7395 | 29.0375 | 40.6477 | 39.013 | 38.0058 | 36.5681 | 35.112 | 33.8722 | 31.8436 | 66.8324 | 64.613 | 62.9334 | 54.6497 | 48.763 | 46.2966
|  | FORT WIDLEY | EE |  |  |  | 40.9773 | 39.1599 | 37.9701 | 36.3446 | 34.7109 | 33.2864 | 31.0232 | 67.2762 | 64.8273 | 62.915 | 53.8456 | 47.8068 | 44.9426 | 46.4915 | 45.0824 | 44.2548 | 43.066 | 41.8354 | 40.8028 | 39.2324 | 74.0681 | 72.2609 | 70.9344 | 63.5915 | 55.7813 | 43.9885 | 40.6477 | 39.013 | 38.0058 | 36.5681 | 35.112 | 33.8722 | 31.8436 | 66.8324 | 64.613 | 62.9334 | 55.0058 | 49.8079 | 47.3997
|  | FORT WIDLEY | HT |  |  |  | 41.3834 | 39.6191 | 38.162 | 36.5885 | 35.4538 | 33.8375 | 31.7191 | 68.5089 | 66.3079 | 64.0364 | 53.2803 | 46.5283 | 43.5589 | 46.9966 | 45.8395 | 44.9946 | 44.063 | 43.5191 | 42.5854 | 41.4599 | 77.0864 | 75.8507 | 74.5273 | 68.6446 | 65.4864 | 64.0579 | 41.0528 | 39.513 | 38.2609 | 36.8895 | 35.9497 | 34.5405 | 32.6793 | 68.2079 | 66.2538 | 64.2262 | 54.6497 | 48.763 | 46.2966
|  | FORT WIDLEY | HE |  |  |  | 41.4089 | 39.8313 | 38.4875 | 37.0222 | 36.0201 | 34.5436 | 32.7273 | 69.7844 | 67.8385 | 65.8803 | 56.6252 | 50.6099 | 48.1375 | 46.8793 | 45.6885 | 44.7456 | 43.7171 | 43.0528 | 41.9895 | 40.7446 | 76.214 | 74.7834 | 73.2875 | 64.9875 | 56.9477 | 45.363 | 41.0711 | 39.6783 | 38.5181 | 37.2405 | 36.4099 | 35.1171 | 33.5079 | 69.2742 | 67.5354 | 65.7834 | 57.5242 | 52.3079 | 50.2599
|  | FORT WIDLEY | CF |  |  |  | 42.3109 | 40.6834 | 39.8885 | 38.9548 | 38.3946 | 37.5579 | 36.7262 | 74.4497 | 73.4079 | 72.6671 | 65.4671 | 58.3262 | 51.9538 | 47.4681 | 46.063 | 45.3589 | 44.5375 | 43.9915 | 43.1375 | 42.166 | 77.6313 | 76.414 | 75.4007 | 66.4415 | 52.7395 | 29.0375 | 41.8834 | 40.415 | 39.7364 | 38.9334 | 38.4783 | 37.7558 | 37.0303 | 73.3722 | 72.4395 | 71.8109 | 65.4446 | 59.0987 | 53.5466
MELKSHAM GSP | FROME BSP | FROME BSP | MINIMUM HEADROOM | ST 78803 48019 | YES | 21.483 | 9.1721 | 6.7813 | 118.1063 | 114.6012 | 111.0481 | 106.9543 | 101.9624 | 96.4502 | 90.9135 | 87.0084 | 67.7175 | 52.2747 | 43.9941 | 20.6007 | 19.1272 | 126.5247 | 124.2196 | 121.9879 | 119.4053 | 116.3543 | 113.0135 | 109.4481 | 106.8359 | 92.9798 | 78.1339 | 41.9747 | 5.0099 | 2.7803 | 111.1543 | 107.9788 | 104.7522 | 100.9349 | 96.3063 | 91.239 | 86.043 | 82.5522 | 66.1757 | 53.2196 | 46.3879
|  | FROME BSP | EE |  |  |  | 9.1721 | 6.7813 | 118.1063 | 114.6012 | 111.0481 | 106.9543 | 101.9624 | 96.4502 | 90.9135 | 87.0084 | 67.8247 | 54.493 | 45.642 | 20.6007 | 19.1272 | 126.5247 | 124.2196 | 121.9879 | 119.4053 | 116.3543 | 113.0135 | 109.4481 | 106.8359 | 92.9798 | 79.4053 | 60.4992 | 5.0099 | 2.7803 | 111.1543 | 107.9788 | 104.7522 | 100.9349 | 96.3063 | 91.239 | 86.043 | 82.5522 | 66.1757 | 55.2645 | 47.7706
|  | FROME BSP | HT |  |  |  | 9.9099 | 7.8446 | 119.3543 | 115.8369 | 112.7318 | 109.3777 | 104.8594 | 100.2186 | 95.4665 | 90.7798 | 67.7175 | 52.2747 | 43.9941 | 21.2691 | 20.1487 | 127.9696 | 125.889 | 124.189 | 122.3441 | 119.9308 | 117.4451 | 114.8084 | 112.2604 | 100.5339 | 93.2257 | 89.4471 | 5.7497 | 3.9099 | 112.6726 | 109.6839 | 106.9716 | 104.0043 | 99.9308 | 95.7849 | 91.3665 | 86.9512 | 66.3196 | 53.2196 | 46.3879
|  | FROME BSP | HE |  |  |  | 9.913 | 8.0201 | 119.6237 | 116.3012 | 113.4032 | 110.2624 | 106.3073 | 101.9706 | 97.6298 | 93.4206 | 72.4818 | 59.0563 | 53.3635 | 21.1232 | 20.017 | 127.5961 | 125.3635 | 123.5145 | 121.5135 | 118.9981 | 116.2818 | 113.4155 | 110.5206 | 95.1726 | 81.1849 | 63.8237 | 5.7446 | 4.0997 | 112.9073 | 110.0757 | 107.5645 | 104.8104 | 101.2216 | 97.3675 | 93.34 | 89.3155 | 70.6971 | 59.4798 | 54.5267
|  | FROME BSP | CF |  |  |  | 10.6885 | 9.3701 | 121.8961 | 119.6584 | 117.4655 | 115.5186 | 113.891 | 111.492 | 109.1369 | 106.5226 | 90.9828 | 76.6237 | 64.0757 | 21.5364 | 20.6221 | 128.7349 | 126.9226 | 125.2379 | 123.6481 | 122.0777 | 119.9716 | 117.8604 | 115.4971 | 100.2839 | 78.1339 | 41.9747 | 6.4466 | 5.3068 | 114.9288 | 112.9461 | 111.0492 | 109.3655 | 107.889 | 105.6155 | 103.4553 | 100.9757 | 86.5441 | 73.9808 | 63.4277
LOVEDEAN GSP | HAVANT | HAVANT | MINIMUM HEADROOM | SU 70625 05720 | YES | 24.93 | 21.7379 | 16.3913 | 12.1484 | 8.3045 | 4.1943 | -0.6914 | -7.7618 | -15.3761 | -22.9128 | -28.8363 | -58.0802 | -79.9996 | -89.4812 | 43.6106 | 39.0108 | 35.7506 | 32.7517 | 29.4027 | 25.3129 | 20.2262 | 14.517 | 9.0302 | 4.9057 | -16.8565 | -48.7728 | -117.5687 | 26.5624 | 21.3739 | 17.4096 | 13.8086 | 9.8719 | 5.0504 | -1.6067 | -8.969 | -15.9751 | -21.1485 | -45.3496 | -64.0057 | -71.7506
|  | HAVANT | EE |  |  |  | 21.7379 | 16.3913 | 12.1484 | 8.3045 | 4.1943 | -0.6914 | -7.7618 | -15.3761 | -22.9128 | -28.8363 | -56.6485 | -76.0241 | -85.7863 | 43.6106 | 39.0108 | 35.7506 | 32.7517 | 29.4027 | 25.3129 | 20.2262 | 14.517 | 9.0302 | 4.9057 | -16.8565 | -40.679 | -75.1381 | 26.5624 | 21.3739 | 17.4096 | 13.8086 | 9.8719 | 5.0504 | -1.6067 | -8.969 | -15.9751 | -21.1485 | -44.7271 | -60.6394 | -68.8241
|  | HAVANT | HT |  |  |  | 22.992 | 17.2188 | 13.5219 | 9.9157 | 6.1566 | 1.7657 | -3.6547 | -10.3618 | -17.4128 | -24.4281 | -58.0802 | -79.9996 | -89.4812 | 45.0799 | 40.4364 | 38.1037 | 35.9068 | 33.5996 | 30.8241 | 28.1517 | 24.4659 | 20.3802 | 16.2047 | -2.129 | -12.329 | -16.6473 | 27.7736 | 22.3933 | 19.1178 | 15.9168 | 12.5688 | 8.5096 | 3.8249 | -2.2587 | -8.6822 | -15.1302 | -45.3496 | -64.0057 | -71.7506
|  | HAVANT | HE |  |  |  | 22.9848 | 18.0086 | 14.1208 | 10.7147 | 7.2484 | 3.0025 | -1.7373 | -7.6679 | -13.9587 | -20.2292 | -49.4516 | -69.5047 | -77.1873 | 44.7044 | 40.3394 | 37.3302 | 34.7782 | 32.1119 | 28.7935 | 25.5874 | 21.3813 | 16.8364 | 12.1394 | -13.3014 | -38.3432 | -71.8249 | 27.7573 | 23.0933 | 19.6249 | 16.5933 | 13.4759 | 9.5423 | 5.4137 | -0.026094 | -5.8251 | -11.6394 | -38.0281 | -54.7659 | -61.0414
|  | HAVANT | CF |  |  |  | 24.1491 | 20.2219 | 18.4372 | 15.7178 | 13.7178 | 11.4413 | 8.48 | 5.4321 | 2.7974 | -0.61691 | -19.6434 | -44.0312 | -63.2955 | 45.285 | 41.3374 | 39.5762 | 36.9843 | 34.8955 | 32.3966 | 29.1496 | 25.72 | 22.5659 | 18.6476 | -6.6075 | -48.7728 | -117.5687 | 28.7879 | 25.0862 | 23.5229 | 21.0127 | 19.177 | 17.1035 | 14.3688 | 11.5208 | 9.1423 | 5.8321 | -12.6016 | -33.4883 | -49.6496
COWLEY GSP | HEADINGTON BSP | HEADINGTON BSP | MINIMUM HEADROOM | SP 54454 08145 | YES | 77.452 | 38.621 | 27.0879 | 10.1154 | 7.8644 | 4.7175 | 0.27664 | -7.0723 | -13.0458 | -19.306 | -26.9244 | -46.4417 | -57.6458 | -66.0509 | 38.308 | 27.5411 | 11.1687 | 9.6452 | 7.5636 | 2.9993 | -1.864 | -6.1925 | -13.166 | -20.2732 | -39.2262 | -55.7629 | -79.6323 | 35.3437 | 24.0881 | 7.3003 | 5.1585 | 2.2758 | -2.7293 | -8.8017 | -14.3538 | -21.3129 | -28.7742 | -47.7589 | -59.4885 | -69.4568
|  | HEADINGTON BSP | EE |  |  |  | 38.621 | 27.0879 | 10.1154 | 7.8644 | 4.7175 | 0.30726 | -6.7427 | -12.1468 | -17.6478 | -23.5672 | -40.9305 | -54.6162 | -58.0142 | 38.308 | 27.5411 | 11.1687 | 9.6452 | 7.5636 | 3.9697 | -0.85682 | -4.7323 | -9.1119 | -13.9242 | -30.1242 | -49.5038 | -66.7874 | 35.3437 | 24.0881 | 7.3003 | 5.1585 | 2.2758 | -2.164 | -8.3874 | -13.2211 | -18.3803 | -23.815 | -39.9538 | -54.6507 | -58.7323
|  | HEADINGTON BSP | HT |  |  |  | 39.4537 | 27.5195 | 11.0624 | 8.6522 | 5.7317 | 0.53583 | -7.0723 | -13.0458 | -17.9723 | -26.206 | -42.7662 | -57.0672 | -64.258 | 39.1151 | 28.3707 | 12.4564 | 10.886 | 9.1248 | 4.8677 | -0.24662 | -4.7089 | -8.068 | -14.9344 | -26.3742 | -39.0201 | -46.8109 | 36.0937 | 24.5411 | 8.1564 | 5.8605 | 3.133 | -2.1589 | -8.8017 | -14.3538 | -18.7058 | -26.4395 | -42.4629 | -57.715 | -65.9578
|  | HEADINGTON BSP | HE |  |  |  | 39.4088 | 28.1501 | 11.4154 | 8.6654 | 5.8042 | 0.27664 | -6.5203 | -11.9785 | -19.306 | -26.9244 | -46.4417 | -57.6458 | -66.0509 | 38.9171 | 28.3646 | 12.0779 | 9.9524 | 7.9136 | 2.9993 | -1.864 | -6.1925 | -13.166 | -20.2732 | -39.2262 | -55.7629 | -78.5334 | 36.0273 | 25.0126 | 8.3534 | 5.6564 | 2.9575 | -2.7293 | -8.6925 | -13.7701 | -21.3129 | -28.7742 | -47.7589 | -59.4885 | -69.4568
|  | HEADINGTON BSP | CF |  |  |  | 40.2088 | 29.5011 | 13.9042 | 12.7338 | 10.9664 | 8.0348 | 3.9389 | 0.83379 | -2.7744 | -7.0683 | -26.2376 | -37.2734 | -47.1427 | 39.4865 | 29.0585 | 13.4626 | 12.485 | 11.0462 | 8.4809 | 4.9575 | 2.0575 | -1.0793 | -5.0344 | -25.4946 | -46.4334 | -79.6323 | 36.8569 | 26.286 | 10.7381 | 9.7044 | 8.0605 | 5.2799 | 1.3483 | -1.5221 | -4.7313 | -8.6313 | -26.4466 | -37.3017 | -46.9242
COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE BSP | MINIMUM HEADROOM | SU 84773 92191 | YES | 21.442 | 1.5038 | -0.70698 | -2.9825 | -4.8213 | -7.4539 | -10.4733 | -14.6386 | -19.2447 | -24.7845 | -28.7437 | -52.6753 | -74.6356 | -87.9968 | 22.603 | 21.1851 | 19.2493 | 17.6738 | 15.4096 | 12.7381 | 9.6483 | 6.3116 | 1.0412 | -4.0588 | -25.1088 | -46.768 | -86.5211 | -0.09698 | -2.2884 | -4.5904 | -6.4364 | -9.0792 | -12.0629 | -16.0404 | -20.3476 | -25.7435 | -30.6353 | -53.2802 | -73.8476 | -87.1476
|  | HIGH WYCOMBE BSP | EE |  |  |  | 1.5038 | -0.70698 | -2.9825 | -4.8213 | -7.4539 | -10.4733 | -14.6386 | -19.2447 | -24.7845 | -28.7437 | -49.7049 | -70.0274 | -82.0366 | 22.603 | 21.1851 | 19.2493 | 17.6738 | 15.4096 | 12.7381 | 9.6483 | 6.3116 | 1.8973 | -1.1639 | -18.719 | -42.9517 | -68.7996 | -0.09698 | -2.2884 | -4.5904 | -6.4364 | -9.0792 | -12.0629 | -16.0404 | -20.3476 | -25.7435 | -29.4792 | -49.0415 | -68.9517 | -80.2956
|  | HIGH WYCOMBE BSP | HT |  |  |  | 2.5069 | 0.60424 | -1.3325 | -3.5437 | -5.6815 | -8.7519 | -12.9019 | -17.5621 | -21.7907 | -26.7815 | -52.6753 | -74.6356 | -87.9968 | 23.2122 | 22.3728 | 21.5514 | 19.9044 | 18.4493 | 15.7381 | 13.0728 | 9.934 | 7.3779 | 3.884 | -12.2466 | -27.7945 | -37.5068 | 0.90506 | -0.8731 | -2.6976 | -4.8802 | -6.9792 | -10.2741 | -14.27 | -18.8231 | -22.8149 | -27.7547 | -52.3302 | -73.8476 | -87.1476
|  | HIGH WYCOMBE BSP | HE |  |  |  | 2.511 | 0.70424 | -1.1468 | -3.4784 | -5.6723 | -8.9009 | -12.456 | -16.7845 | -22.7845 | -28.1733 | -51.8192 | -69.8325 | -82.2294 | 23.0938 | 22.1677 | 20.883 | 18.734 | 16.783 | 13.4147 | 10.5759 | 6.9769 | 1.0412 | -4.0588 | -25.1088 | -46.768 | -76.3445 | 0.89996 | -0.79453 | -2.57 | -4.9282 | -7.1313 | -10.666 | -14.1456 | -18.4629 | -24.9578 | -30.6353 | -53.2802 | -70.4762 | -83.568
|  | HIGH WYCOMBE BSP | CF |  |  |  | 3.2559 | 2.0502 | 0.96955 | -0.08249 | -1.4927 | -2.9917 | -4.6376 | -5.8407 | -7.7917 | -9.6692 | -24.0437 | -40.5202 | -55.9131 | 23.4316 | 22.7055 | 21.9902 | 20.8391 | 19.2657 | 17.4412 | 15.3147 | 13.5096 | 11.0014 | 8.4667 | -9.9884 | -39.0507 | -86.5211 | 1.5836 | 0.44527 | -0.57106 | -1.5619 | -3.0088 | -4.57 | -6.2976 | -7.519 | -9.5578 | -11.467 | -25.4098 | -41.2394 | -55.6966
FAWLEY GSP | LANGLEY BSP | LANGLEY BSP | MINIMUM HEADROOM | SU 45185 01376 | YES | 2.614 | 19.5246 | 18.7542 | 18.1991 | 17.3062 | 16.6746 | 15.5552 | 13.6848 | 11.6766 | 9.3287 | 7.6419 | -2.6009 | -11.4489 | -16.9805 | 18.321 | 17.7863 | 17.4098 | 16.818 | 16.3751 | 15.1945 | 14.0608 | 12.7455 | 10.5506 | 8.4802 | 0.028163 | -8.5331 | -21.6514 | 15.2037 | 14.57 | 14.1129 | 13.4292 | 12.8945 | 11.7731 | 9.9894 | 8.1261 | 5.8741 | 3.8251 | -5.6994 | -14.2065 | -19.7402
|  | LANGLEY BSP | EE |  |  |  | 19.5246 | 18.7542 | 18.1991 | 17.3062 | 16.6746 | 15.5552 | 13.6848 | 11.6766 | 9.3287 | 7.6419 | -0.70296 | -9.2989 | -14.5948 | 18.321 | 17.7863 | 17.4098 | 16.818 | 16.3751 | 15.4516 | 14.1016 | 12.7455 | 10.9935 | 9.82 | 3.1394 | -6.3361 | -16.1494 | 15.2037 | 14.57 | 14.1129 | 13.4292 | 12.8945 | 11.7771 | 9.9894 | 8.1261 | 5.8741 | 4.322 | -3.5402 | -12.0147 | -16.9739
|  | LANGLEY BSP | HT |  |  |  | 19.8379 | 19.1777 | 18.4777 | 17.6266 | 17.2011 | 15.9613 | 13.9399 | 12.1185 | 10.1879 | 8.0093 | -2.6009 | -11.4489 | -16.9805 | 18.62 | 18.2527 | 17.8292 | 17.268 | 17.0669 | 16.0598 | 14.872 | 13.8037 | 12.7986 | 11.3669 | 4.8884 | -1.2371 | -5.2024 | 15.4486 | 14.8833 | 14.268 | 13.5067 | 13.12 | 11.9016 | 10.0537 | 8.318 | 6.6414 | 4.5547 | -5.5249 | -14.2065 | -19.7402
|  | LANGLEY BSP | HE |  |  |  | 19.894 | 19.294 | 18.6093 | 17.7266 | 17.2777 | 15.9654 | 14.4236 | 13.0134 | 10.3256 | 7.9726 | -1.8458 | -9.6581 | -15.1397 | 18.5802 | 18.1639 | 17.621 | 16.872 | 16.4741 | 15.1945 | 14.0608 | 13.0006 | 10.5506 | 8.4802 | 0.028163 | -8.5331 | -19.8759 | 15.4945 | 14.9894 | 14.3639 | 13.5404 | 13.0996 | 11.7731 | 10.3465 | 8.9863 | 6.2373 | 3.8251 | -5.6994 | -13.3382 | -19.1565
|  | LANGLEY BSP | CF |  |  |  | 20.1736 | 19.8593 | 19.5399 | 19.1348 | 18.643 | 18.4572 | 17.8654 | 17.1981 | 16.4603 | 16.0317 | 9.7848 | 2.7307 | -3.6244 | 18.6996 | 18.4129 | 18.0986 | 17.7016 | 17.1935 | 16.8404 | 16.1506 | 15.4016 | 14.5884 | 13.9282 | 6.7557 | -4.3137 | -21.6514 | 15.7414 | 15.4853 | 15.2231 | 14.8822 | 14.4659 | 14.2669 | 13.7608 | 13.219 | 12.5557 | 12.1241 | 6.0986 | -0.7351 | -6.728
IVER 132KV | LONGFORD | LONGFORD | MINIMUM HEADROOM | TQ 03910 76751 | YES | 59.011 | 58.2115 | 56.1748 | 54.9575 | 53.5228 | 51.8299 | 49.9422 | 47.9983 | 45.4993 | 43.1054 | 40.9309 | 32.5636 | 28.1687 | 26.2911 | 47.7066 | 46.173 | 45.4628 | 44.5067 | 43.3842 | 42.124 | 40.8648 | 39.2311 | 37.6577 | 36.0526 | 29.7913 | 26.573 | 25.0883 | 46.9392 | 45.0107 | 43.8464 | 42.4638 | 40.8383 | 39.024 | 37.1648 | 34.7669 | 32.472 | 30.4056 | 22.372 | 18.1811 | 16.3924
|  | LONGFORD | EE |  |  |  | 58.2115 | 56.1748 | 54.9575 | 53.5228 | 51.8299 | 49.9422 | 47.9983 | 45.4993 | 43.1054 | 40.9309 | 34.0401 | 32.4687 | 32.0054 | 47.7066 | 46.173 | 45.4628 | 44.5067 | 43.3842 | 42.124 | 40.8648 | 39.2311 | 37.6577 | 36.0526 | 30.976 | 30.0679 | 29.7913 | 46.9392 | 45.0107 | 43.8464 | 42.4638 | 40.8383 | 39.024 | 37.1648 | 34.7669 | 32.472 | 30.4056 | 23.8352 | 22.5322 | 22.2301
|  | LONGFORD | HT |  |  |  | 59.0696 | 57.3667 | 56.586 | 55.6871 | 54.5901 | 53.3616 | 51.9095 | 50.0983 | 48.1646 | 46.184 | 37.2126 | 33.2177 | 31.6116 | 48.0525 | 46.7444 | 46.4179 | 45.9862 | 45.3016 | 44.5005 | 43.5934 | 42.4434 | 41.2056 | 39.9546 | 33.6311 | 30.9883 | 29.9842 | 47.6535 | 46.0648 | 45.4128 | 44.5475 | 43.5016 | 42.3189 | 40.9301 | 39.1903 | 37.3373 | 35.4536 | 26.8679 | 23.3577 | 22.0383
|  | LONGFORD | HE |  |  |  | 58.9104 | 57.1044 | 56.1901 | 55.1248 | 53.835 | 52.3697 | 50.632 | 48.4524 | 46.1105 | 43.6636 | 32.5636 | 28.1687 | 26.2911 | 47.98 | 46.6026 | 46.175 | 45.5771 | 44.722 | 43.7454 | 42.6158 | 41.1903 | 39.6485 | 38.0505 | 29.7913 | 26.573 | 25.0883 | 47.5157 | 45.8362 | 45.0322 | 44.0087 | 42.774 | 41.3669 | 39.7016 | 37.6056 | 35.3597 | 33.026 | 22.372 | 18.1811 | 16.3924
|  | LONGFORD | CF |  |  |  | 59.5431 | 58.0901 | 57.6075 | 57.035 | 56.3544 | 55.5636 | 54.7013 | 53.5422 | 52.2289 | 50.682 | 42.1779 | 34.6411 | 29.8238 | 48.2035 | 46.9526 | 46.725 | 46.473 | 46.1546 | 45.7679 | 45.2189 | 44.4434 | 43.5597 | 42.525 | 36.872 | 31.1454 | 27.4352 | 48.03 | 46.6352 | 46.2332 | 45.7577 | 45.1883 | 44.4291 | 43.6016 | 42.4873 | 41.222 | 39.7464 | 31.5607 | 24.3342 | 19.7424
AMERSHAM | LOUDWATER BSP | LOUDWATER BSP | MINIMUM HEADROOM | SU 90644 91247 | YES | 12.078 | 56.043 | 167.0284 | 164.0631 | 99.9304 | 97.6631 | -28.4757 | -32.3716 | -36.5961 | -40.6379 | -43.5165 | -59.6951 | -72.0338 | -78.8338 | 69.6698 | 176.9258 | 174.9268 | 96.3319 | 94.8237 | -61.4814 | -64.111 | -67.0916 | -70.0528 | -72.0253 | -82.8691 | -96.0885 | -129.2957 | 56.2647 | 164.8553 | 162.2033 | 82.9543 | 80.9523 | -75.8793 | -79.4977 | -83.4916 | -87.3487 | -89.9089 | -103.4814 | -114.4008 | -120.0814
|  | LOUDWATER BSP | EE |  |  |  | 56.043 | 167.0284 | 164.0631 | 99.9304 | 97.6631 | -28.4757 | -32.3716 | -36.5961 | -40.6379 | -43.5165 | -58.5481 | -69.4736 | -77.6298 | 69.6698 | 176.9258 | 174.9268 | 96.3319 | 94.8237 | -61.4814 | -64.111 | -67.0916 | -70.0528 | -72.0253 | -82.8691 | -94.3059 | -111.2742 | 56.2647 | 164.8553 | 162.2033 | 82.9543 | 80.9523 | -75.8793 | -79.4977 | -83.4916 | -87.3487 | -89.9089 | -102.6814 | -112.1059 | -119.0324
|  | LOUDWATER BSP | HT |  |  |  | 56.8655 | 167.8866 | 165.1427 | 101.7866 | 99.3213 | -26.841 | -30.2206 | -33.6747 | -37.0165 | -40.7175 | -59.6951 | -72.0338 | -78.8338 | 70.5953 | 178.088 | 176.5278 | 98.8992 | 97.4727 | -58.564 | -60.2855 | -62.0865 | -63.8702 | -66.014 | -76.0998 | -81.561 | -84.1436 | 57.2483 | 165.8625 | 163.4431 | 85.0951 | 82.8625 | -74.0069 | -76.9763 | -80.0447 | -83.0304 | -86.4508 | -103.4814 | -114.4008 | -120.0814
|  | LOUDWATER BSP | HE |  |  |  | 56.9032 | 168.0417 | 165.4223 | 102.2111 | 99.8917 | -26.1165 | -28.844 | -31.6563 | -34.3553 | -37.3961 | -53.4012 | -64.4655 | -69.6859 | 70.432 | 177.8104 | 176.0992 | 98.3298 | 96.7411 | -59.4824 | -61.2528 | -63.1508 | -65.0804 | -67.4069 | -80.2742 | -92.062 | -107.9202 | 57.2544 | 165.9809 | 163.6696 | 85.4462 | 83.3502 | -73.3855 | -75.8038 | -78.3314 | -80.7783 | -83.6385 | -98.1089 | -107.5855 | -111.9528
|  | LOUDWATER BSP | CF |  |  |  | 57.5542 | 169.3304 | 167.4723 | 104.6345 | 103.3498 | -21.9134 | -23.4236 | -25.04 | -25.8144 | -27.2512 | -37.5553 | -49.2083 | -59.9706 | 70.7493 | 178.3758 | 177.0064 | 99.1809 | 98.188 | -57.764 | -59.3528 | -61.1549 | -62.2936 | -64.1355 | -76.8263 | -96.0885 | -129.2957 | 57.8034 | 167.0502 | 165.4237 | 87.4217 | 86.4043 | -69.5957 | -71.0263 | -72.6079 | -73.2773 | -74.7232 | -84.5059 | -94.7283 | -103.7814
MANNINGTON GSP | LYTCHETT | LYTCHETT | MINIMUM HEADROOM | SY 97796 94214 | YES | 13.472 | 19.9533 | 88.9962 | 86.9309 | 85.6329 | 83.4605 | 81.0339 | 77.0717 | 73.4645 | 69.8717 | 67.0533 | 50.0952 | 38.1441 | 31.4799 | 28.0962 | 96.8074 | 95.6921 | 94.7625 | 93.4043 | 91.885 | 89.7288 | 87.7248 | 84.9074 | 82.9125 | 71.6186 | 57.4441 | 23.9921 | 18.7584 | 90.1952 | 88.3309 | 87.2013 | 85.2309 | 83.036 | 79.3952 | 75.8329 | 72.138 | 69.5839 | 55.6125 | 45.1064 | 39.3656
|  | LYTCHETT | EE |  |  |  | 19.9533 | 88.9962 | 86.9309 | 85.6329 | 83.4605 | 81.0339 | 77.0717 | 73.4645 | 69.8717 | 67.0533 | 51.1196 | 40.1564 | 32.4329 | 28.0962 | 96.8074 | 95.6921 | 94.7625 | 93.4043 | 91.885 | 89.7288 | 87.7248 | 84.9074 | 82.9125 | 71.6186 | 59.7635 | 42.5309 | 18.7584 | 90.1952 | 88.3309 | 87.2013 | 85.2309 | 83.036 | 79.3952 | 75.8329 | 72.138 | 69.5839 | 56.286 | 46.788 | 40.0972
|  | LYTCHETT | HT |  |  |  | 20.5452 | 89.6625 | 87.8299 | 85.986 | 83.9645 | 82.1248 | 78.6033 | 75.0778 | 71.7441 | 68.3186 | 50.0952 | 38.1441 | 31.4799 | 28.7288 | 97.6513 | 96.886 | 96.0023 | 94.9717 | 93.9503 | 92.2982 | 90.6788 | 89.0319 | 87.3217 | 78.8288 | 73.336 | 70.3482 | 19.3523 | 90.8952 | 89.2972 | 87.6543 | 85.839 | 84.2503 | 81.1237 | 77.9758 | 74.9656 | 71.8645 | 55.6125 | 45.1064 | 39.3656
|  | LYTCHETT | HE |  |  |  | 20.5737 | 89.8421 | 88.1625 | 86.4982 | 84.539 | 82.8013 | 79.8268 | 76.7441 | 73.8594 | 70.9503 | 54.6462 | 43.3268 | 38.2023 | 28.6248 | 97.5054 | 96.6717 | 95.7105 | 94.537 | 93.3799 | 91.5982 | 89.7492 | 87.8533 | 85.8809 | 73.3696 | 60.9656 | 44.7911 | 19.3707 | 91.0278 | 89.5503 | 88.0513 | 86.2911 | 84.7788 | 82.1258 | 79.3605 | 76.736 | 74.0778 | 59.4676 | 49.5574 | 45.1594
|  | LYTCHETT | CF |  |  |  | 21.137 | 90.9707 | 89.9156 | 89.0472 | 87.9472 | 86.5584 | 85.4023 | 84.3441 | 82.9788 | 81.5829 | 70.8748 | 59.3768 | 48.5023 | 29.037 | 98.1309 | 97.5972 | 97.089 | 96.4696 | 95.3003 | 94.0401 | 92.8656 | 91.4523 | 89.8237 | 77.0748 | 57.4441 | 23.9921 | 19.9503 | 92.0503 | 91.1186 | 90.3248 | 89.335 | 88.0921 | 87.0727 | 86.136 | 84.889 | 83.6186 | 73.489 | 63.336 | 54.135
BRAMLEY (FLEE) | MAIDENHEAD BSP | MAIDENHEAD BSP | MINIMUM HEADROOM | SU 86592 79883 | YES | 58.683 | 30.4082 | 24.3447 | 21.6447 | 18.2947 | 13.96 | 2.8294 | -1.6828 | -6.1471 | -9.793 | -12.4573 | -24.489 | -33.3094 | -36.2216 | 42.7829 | 37.2378 | 35.3255 | 33.2 | 30.4888 | 20.8357 | 17.8796 | 14.8041 | 12.0449 | 10.1378 | 0.59084 | -12.0928 | -42.6857 | 26.9543 | 20.9388 | 18.4837 | 15.5684 | 11.7592 | 1.1164 | -2.9734 | -7.101 | -10.5806 | -12.9551 | -23.3479 | -30.8541 | -33.2153
|  | MAIDENHEAD BSP | EE |  |  |  | 30.4082 | 24.3447 | 21.6447 | 18.2947 | 13.96 | 2.8294 | -1.6828 | -6.1471 | -9.793 | -12.4573 | -24.489 | -32.0665 | -33.9216 | 42.7829 | 37.2378 | 35.3255 | 33.2 | 30.4888 | 20.8357 | 17.8796 | 14.8041 | 12.0449 | 10.1378 | 0.59084 | -9.3194 | -23.4357 | 26.9543 | 20.9388 | 18.4837 | 15.5684 | 11.7592 | 1.1164 | -2.9734 | -7.101 | -10.5806 | -12.9551 | -23.3479 | -29.6949 | -31.3326
|  | MAIDENHEAD BSP | HT |  |  |  | 31.1061 | 25.0468 | 22.359 | 19.0406 | 15.1784 | 3.9692 | 0.60084 | -2.8277 | -5.8726 | -8.942 | -24.1502 | -33.3094 | -36.2216 | 43.6482 | 38.4327 | 36.75 | 34.8776 | 32.898 | 23.4439 | 21.6888 | 19.8541 | 17.9572 | 16.0051 | 7.2592 | 2.7847 | 1.297 | 27.8339 | 21.9715 | 19.548 | 16.6582 | 13.4796 | 2.7684 | -0.13569 | -3.1683 | -6.0326 | -8.9469 | -22.8653 | -30.8541 | -33.2153
|  | MAIDENHEAD BSP | HE |  |  |  | 31.1357 | 25.4202 | 23.008 | 20.0386 | 16.6743 | 5.6519 | 2.2651 | -1.1073 | -4.0165 | -6.9808 | -20.1604 | -27.7981 | -30.2114 | 43.4839 | 38.2674 | 36.5102 | 34.599 | 32.6674 | 23.0592 | 20.9347 | 18.7735 | 16.6449 | 14.3286 | 2.7786 | -7.5918 | -21.803 | 27.8329 | 22.2317 | 20.0194 | 17.4235 | 14.6408 | 4.0939 | 1.2 | -1.7438 | -4.4816 | -7.2979 | -19.402 | -25.8285 | -27.7551
|  | MAIDENHEAD BSP | CF |  |  |  | 31.799 | 26.8559 | 25.4559 | 23.7764 | 21.557 | 11.9335 | 8.8427 | 6.1804 | 4.8345 | 3.2468 | -6.8114 | -17.1134 | -26.5573 | 43.8206 | 38.9572 | 37.6429 | 36.2715 | 34.6337 | 25.7837 | 23.4817 | 21.3847 | 19.8919 | 18.1194 | 5.9164 | -12.0928 | -42.6857 | 28.4155 | 23.4766 | 22.1051 | 20.548 | 18.5806 | 9.3929 | 6.7184 | 4.4643 | 3.2225 | 1.6817 | -7.8398 | -16.8714 | -24.9867
MANNINGTON GSP | MANNINGTON BSP | MANNINGTON BSP | MINIMUM HEADROOM | SU 07523 05221 | YES | 19.205 | 27.2587 | 22.4331 | 19.1749 | 15.8974 | 11.3861 | 5.2831 | -2.0934 | -8.5088 | -20.8424 | -30.8302 | -72.27 | -103.169 | -127.1537 | 41.7954 | 37.977 | 35.6096 | 32.9484 | 29.9943 | 22.9729 | 17.98 | 12.1086 | -0.67916 | -10.2547 | -46.0098 | -79.773 | -123.0822 | 24.9576 | 20.3821 | 17.3361 | 14.3514 | 10.1678 | 3.1566 | -2.9832 | -10.1628 | -24.2506 | -34.9363 | -75.3894 | -106.2751 | -133.3843
|  | MANNINGTON BSP | EE |  |  |  | 27.2587 | 22.4331 | 19.1749 | 15.8974 | 11.3861 | 5.327 | -2.0934 | -8.5088 | -17.269 | -23.3986 | -57.6853 | -92.7618 | -110.6567 | 41.7954 | 37.977 | 35.6096 | 33.2933 | 29.9943 | 24.9463 | 19.3678 | 15.0861 | 8.0719 | 3.6014 | -23.6873 | -63.1251 | -95.3924 | 24.9576 | 20.3821 | 17.3361 | 14.3514 | 10.1678 | 4.23 | -2.921 | -8.8047 | -17.4108 | -23.2128 | -55.47 | -91.919 | -110.02
|  | MANNINGTON BSP | HT |  |  |  | 28.6097 | 24.0739 | 20.6749 | 16.6637 | 13.5351 | 6.9035 | -0.1761 | -8.2047 | -14.9904 | -23.4945 | -65.2108 | -101.3281 | -123.2445 | 43.2872 | 40.0545 | 37.7953 | 34.8943 | 33.1086 | 27.3127 | 22.5372 | 16.83 | 12.7208 | 6.4504 | -21.7557 | -51.4516 | -70.7924 | 26.4872 | 22.3157 | 19.079 | 15.1555 | 12.3453 | 5.3953 | -1.4465 | -9.3649 | -15.7179 | -24.1434 | -64.1271 | -101.3832 | -125.1628
|  | MANNINGTON BSP | HE |  |  |  | 28.5852 | 24.3219 | 20.6974 | 16.2372 | 12.5861 | 5.2831 | -0.90569 | -8.0659 | -20.8424 | -30.8302 | -72.27 | -103.169 | -127.1537 | 42.974 | 39.6627 | 36.8055 | 32.9484 | 30.1086 | 22.9729 | 17.98 | 12.1086 | -0.67916 | -10.2547 | -46.0098 | -79.773 | -123.0822 | 26.4291 | 22.4902 | 18.979 | 14.4596 | 10.9923 | 3.1566 | -2.9832 | -10.1628 | -24.2506 | -34.9363 | -75.3894 | -106.2751 | -133.3843
|  | MANNINGTON BSP | CF |  |  |  | 29.6332 | 26.2402 | 24.2025 | 21.9912 | 19.0412 | 15.8617 | 13.3208 | 10.5698 | 7.1147 | 3.3055 | -22.5098 | -51.2373 | -74.8067 | 43.5362 | 40.627 | 38.93 | 37.0341 | 34.3596 | 31.3106 | 28.477 | 25.5096 | 21.9617 | 17.9617 | -9.2312 | -48.9883 | -104.6026 | 27.3964 | 24.2545 | 22.3586 | 20.2984 | 17.429 | 14.4147 | 11.8382 | 9.1372 | 5.7872 | 2.0494 | -23.019 | -51.2669 | -74.2424
BOTLEY WOOD GSP | NETLEY COMMON BSP | NETLEY COMMON BSP | MINIMUM HEADROOM | SU 47559 12003 | YES | 15.615 | 120.764 | 117.6477 | 113.8538 | 110.2548 | 105.5783 | 101.1018 | 93.7263 | 85.6354 | 77.8987 | 72.0181 | 39.5712 | 13.7599 | -0.15843 | 146.3706 | 144.0063 | 140.9665 | 138.0981 | 134.2144 | 130.2848 | 124.8124 | 118.641 | 112.5399 | 107.9216 | 80.3338 | 36.1206 | -60.4907 | 125.7508 | 122.8293 | 119.2069 | 116.0191 | 111.5242 | 107.212 | 100.311 | 92.5365 | 85.1793 | 79.9099 | 52.2885 | 29.4712 | 17.5416
|  | NETLEY COMMON BSP | EE |  |  |  | 120.764 | 117.6477 | 113.8538 | 110.2548 | 105.5783 | 101.1018 | 93.7263 | 85.6354 | 77.8987 | 72.0181 | 41.2171 | 19.211 | 2.3987 | 146.3706 | 144.0063 | 140.9665 | 138.0981 | 134.2144 | 130.2848 | 124.8124 | 118.641 | 112.5399 | 107.9216 | 80.3338 | 48.7706 | -2.0397 | 125.7508 | 122.8293 | 119.2069 | 116.0191 | 111.5242 | 107.212 | 100.311 | 92.5365 | 85.1793 | 79.9099 | 53.3314 | 34.2344 | 19.6048
|  | NETLEY COMMON BSP | HT |  |  |  | 122.5814 | 119.8161 | 116.3803 | 112.8283 | 109.211 | 105.6487 | 99.9099 | 93.0293 | 86.1834 | 78.7212 | 39.5712 | 13.7599 | -0.15843 | 148.1297 | 146.4767 | 144.4665 | 142.4757 | 140.2889 | 137.9512 | 134.9379 | 130.9991 | 127.0971 | 122.7297 | 101.5399 | 89.0389 | 82.7318 | 127.861 | 125.3069 | 122.1252 | 118.9916 | 115.6957 | 112.3671 | 107.1803 | 100.8446 | 94.5701 | 87.7028 | 52.2885 | 29.4712 | 17.5416
|  | NETLEY COMMON BSP | HE |  |  |  | 122.5661 | 120.0283 | 116.764 | 113.5426 | 110.2997 | 106.9212 | 102.1916 | 96.4385 | 90.761 | 84.5436 | 51.7854 | 29.2599 | 19.1293 | 147.6389 | 145.6399 | 143.0532 | 140.5797 | 137.9297 | 134.9481 | 131.3379 | 126.7818 | 122.1573 | 116.942 | 86.0991 | 53.2359 | 5.2665 | 127.815 | 125.4967 | 122.4252 | 119.5885 | 116.6487 | 113.5089 | 109.2324 | 103.8916 | 98.6426 | 92.8048 | 63.0783 | 43.3293 | 34.6793
|  | NETLEY COMMON BSP | CF |  |  |  | 123.8783 | 122.3303 | 120.2783 | 118.0171 | 116.1222 | 114.4334 | 112.5008 | 110.4212 | 107.6497 | 104.6803 | 83.062 | 60.1252 | 38.7967 | 148.2501 | 146.592 | 144.5175 | 142.192 | 139.9644 | 137.4828 | 134.4185 | 131.0369 | 126.9124 | 122.4308 | 89.941 | 36.1206 | -60.4907 | 128.9365 | 127.4212 | 125.4365 | 123.2548 | 121.5018 | 119.9089 | 118.0732 | 116.1487 | 113.4028 | 110.4446 | 90.1865 | 70.113 | 51.6048
MELKSHAM GSP | NORRINGTON A | NORRINGTON | MINIMUM HEADROOM | ST 88273 64983 | YES | 102.656 | -33.4593 | -56.4984 | 28.1568 | -31.3174 | -37.2828 | -43.543 | -52.3909 | -62.4042 | -72.5511 | -79.9409 | -115.0083 | -142.6899 | -158.4715 | -9.0142 | -31.0768 | 44.196 | -22.0905 | -26.3405 | -30.6619 | -36.8181 | -43.9589 | -51.1528 | -56.4691 | -81.7823 | -106.3262 | -168.9201 | -35.0621 | -57.8309 | 18.4317 | -48.7242 | -54.1538 | -59.8058 | -68.0446 | -77.4242 | -86.8487 | -93.6874 | -125.3028 | -149.7874 | -163.0538
|  | NORRINGTON | EE |  |  |  | -33.4593 | -56.4984 | 28.1568 | -31.3174 | -37.2828 | -43.543 | -52.3909 | -62.4042 | -72.5511 | -79.9409 | -113.4501 | -136.7868 | -153.9879 | -9.0142 | -31.0768 | 44.196 | -22.0905 | -26.3405 | -30.6619 | -36.8181 | -43.9589 | -51.1528 | -56.4691 | -81.7823 | -106.3262 | -141.1691 | -35.0621 | -57.8309 | 18.4317 | -48.7242 | -54.1538 | -59.8058 | -68.0446 | -77.4242 | -86.8487 | -93.6874 | -123.9303 | -143.9977 | -158.6966
|  | NORRINGTON | HT |  |  |  | -31.6399 | -54.0903 | 30.7129 | -29.1552 | -33.8399 | -39.694 | -47.644 | -56.4909 | -65.2613 | -73.6195 | -115.0083 | -142.6899 | -158.4715 | -7.2254 | -28.4329 | 47.4113 | -18.713 | -21.2854 | -24.5803 | -29.167 | -34.5915 | -39.9783 | -45.1579 | -69.166 | -83.4956 | -91.2487 | -33.2223 | -55.386 | 21.0399 | -46.4579 | -50.5497 | -55.6946 | -62.9507 | -71.1517 | -79.3079 | -87.1089 | -125.3028 | -149.7874 | -163.0538
|  | NORRINGTON | HE |  |  |  | -31.6409 | -53.8515 | 31.1405 | -28.4246 | -32.7072 | -37.9399 | -44.3858 | -52.2358 | -60.2174 | -67.395 | -103.4379 | -127.4154 | -139.1052 | -7.555 | -28.9564 | 46.5827 | -19.767 | -22.663 | -26.1405 | -30.4997 | -36.0058 | -41.5385 | -46.7538 | -75.4323 | -100.9007 | -133.8701 | -33.255 | -55.2013 | 21.3899 | -45.8466 | -49.6079 | -54.2232 | -60.0874 | -67.3017 | -74.563 | -81.1456 | -114.2211 | -134.8813 | -144.7946
|  | NORRINGTON | CF |  |  |  | -30.4593 | -51.6637 | 34.6813 | -23.3389 | -26.294 | -28.6766 | -31.6052 | -34.9889 | -39.4654 | -43.8226 | -71.4766 | -95.7246 | -116.5032 | -6.9458 | -27.9095 | 48.2837 | -17.3874 | -19.9446 | -22.2079 | -25.3528 | -28.9966 | -33.4181 | -37.7548 | -66.2426 | -105.017 | -168.9201 | -32.156 | -53.2003 | 24.6256 | -41.2293 | -43.9201 | -46.0191 | -48.7528 | -51.9487 | -56.1201 | -60.1089 | -85.165 | -106.916 | -125.1977
MELKSHAM GSP | NORRINGTON B | NORRINGTON B | MINIMUM HEADROOM | ST 88273 64983 | YES | 6.215 | 0 | 0 | 0 | 112.422 | 112.422 | 112.422 | 112.422 | 112.422 | 112.422 | 112.422 | 112.422 | 112.422 | 112.422 | 0 | 0 | 0 | 107.912 | 107.912 | 107.912 | 107.912 | 107.912 | 107.912 | 107.912 | 107.912 | 107.912 | 107.912 | 0 | 0 | 0 | 109.712 | 109.712 | 109.712 | 109.712 | 109.712 | 109.712 | 109.712 | 109.712 | 109.712 | 109.712
|  | NORRINGTON B | EE |  |  |  | 0 | 0 | 0 | 112.422 | 112.422 | 112.422 | 112.422 | 112.422 | 112.422 | 112.422 | 112.422 | 112.422 | 112.422 | 0 | 0 | 0 | 107.912 | 107.912 | 107.912 | 107.912 | 107.912 | 107.912 | 107.912 | 107.912 | 107.912 | 107.912 | 0 | 0 | 0 | 109.712 | 109.712 | 109.712 | 109.712 | 109.712 | 109.712 | 109.712 | 109.712 | 109.712 | 109.712
|  | NORRINGTON B | HT |  |  |  | 0 | 0 | 0 | 112.422 | 112.422 | 112.422 | 112.422 | 112.422 | 112.422 | 112.422 | 112.422 | 112.422 | 112.422 | 0 | 0 | 0 | 107.912 | 107.912 | 107.912 | 107.912 | 107.912 | 107.912 | 107.912 | 107.912 | 107.912 | 107.912 | 0 | 0 | 0 | 109.712 | 109.712 | 109.712 | 109.712 | 109.712 | 109.712 | 109.712 | 109.712 | 109.712 | 109.712
|  | NORRINGTON B | HE |  |  |  | 0 | 0 | 0 | 112.422 | 112.422 | 112.422 | 112.422 | 112.422 | 112.422 | 112.422 | 112.422 | 112.422 | 112.422 | 0 | 0 | 0 | 107.912 | 107.912 | 107.912 | 107.912 | 107.912 | 107.912 | 107.912 | 107.912 | 107.912 | 107.912 | 0 | 0 | 0 | 109.712 | 109.712 | 109.712 | 109.712 | 109.712 | 109.712 | 109.712 | 109.712 | 109.712 | 109.712
|  | NORRINGTON B | CF |  |  |  | 0 | 0 | 0 | 112.422 | 112.422 | 112.422 | 112.422 | 112.422 | 112.422 | 112.422 | 112.422 | 112.422 | 112.422 | 0 | 0 | 0 | 107.912 | 107.912 | 107.912 | 107.912 | 107.912 | 107.912 | 107.912 | 107.912 | 107.912 | 107.912 | 0 | 0 | 0 | 109.712 | 109.712 | 109.712 | 109.712 | 109.712 | 109.712 | 109.712 | 109.712 | 109.712 | 109.712
NORTH HYDE GSP | NORTH HYDE 22kV | NORTH HYDE 22kV | MINIMUM HEADROOM | TQ 10367 79001 | YES | 12.19 | 71.7746 | 67.6593 | 64.5725 | 60.3235 | 54.9067 | 51.1761 | 48.0098 | 45.321 | 43.8281 | 42.9771 | 39.9353 | 35.4251 | 34.1251 | 76.8843 | 73.4496 | 71.4026 | 68.971 | 65.1725 | 62.9623 | 60.3154 | 57.6766 | 55.7358 | 54.2511 | 46.4082 | 32.4082 | 1.0929 | 72.0649 | 68.2608 | 65.6353 | 62.1414 | 57.3899 | 54.2164 | 51.2021 | 48.4266 | 46.6827 | 45.7266 | 42.1552 | 37.5644 | 35.9889
|  | NORTH HYDE 22kV | EE |  |  |  | 71.7746 | 67.6593 | 64.5725 | 60.3235 | 54.9067 | 51.1761 | 48.0098 | 45.321 | 43.8281 | 42.9771 | 40.0383 | 37.3567 | 36.9506 | 76.8843 | 73.4496 | 71.4026 | 68.971 | 65.1725 | 62.9623 | 60.3154 | 57.6766 | 55.7358 | 54.2511 | 46.4082 | 36.4797 | 20.1756 | 72.0649 | 68.2608 | 65.6353 | 62.1414 | 57.3899 | 54.2164 | 51.2021 | 48.4266 | 46.6827 | 45.7266 | 42.3552 | 39.7368 | 38.8491
|  | NORTH HYDE 22kV | HT |  |  |  | 72.1511 | 67.9409 | 65.3133 | 61.294 | 55.9057 | 52.3751 | 49.4179 | 47.4098 | 46.2914 | 45.0741 | 39.9353 | 35.4251 | 34.1251 | 77.3608 | 73.97 | 72.5628 | 70.4985 | 66.9664 | 65.2031 | 63.0746 | 61.4123 | 60.2052 | 58.796 | 53.3338 | 49.4623 | 47.6011 | 72.4853 | 68.6281 | 66.4894 | 63.2669 | 58.5266 | 55.5327 | 52.7878 | 50.8327 | 49.498 | 48.0205 | 42.1552 | 37.5644 | 35.9889
|  | NORTH HYDE 22kV | HE |  |  |  | 72.1358 | 68.2164 | 65.3756 | 61.4062 | 56.0516 | 52.5924 | 50.0067 | 48.2771 | 47.6792 | 46.9975 | 44.3394 | 42.2679 | 40.7894 | 77.2098 | 73.9394 | 72.0761 | 69.8302 | 66.0593 | 64.0491 | 61.9276 | 60.1756 | 59.0776 | 57.8276 | 49.9052 | 40.0736 | 23.4266 | 72.469 | 68.8802 | 66.5475 | 63.3741 | 58.646 | 55.7133 | 53.3868 | 51.7531 | 51.0848 | 50.245 | 46.7909 | 44.7368 | 43.0358
|  | NORTH HYDE 22kV | CF |  |  |  | 72.445 | 68.8644 | 66.695 | 63.094 | 58.373 | 55.6373 | 53.5934 | 51.9771 | 51.3241 | 51.0577 | 48.3883 | 45.3047 | 42.6281 | 77.3465 | 74.1883 | 72.7353 | 70.4241 | 66.8256 | 64.9674 | 62.9633 | 60.9746 | 59.4419 | 58.1848 | 49.1072 | 32.4082 | 1.0929 | 72.7516 | 69.4669 | 67.7281 | 64.8526 | 60.7021 | 58.448 | 56.6633 | 55.1266 | 54.2868 | 53.9215 | 50.8552 | 47.9725 | 45.6562
COWLEY GSP | OXFORD BSP | OXFORD BSP | MINIMUM HEADROOM | SP 50054 05983 | YES | 39.8 | -26.5356 | -30.9173 | -33.6234 | -35.9295 | -38.7622 | 28.1082 | 22.7919 | 16.9695 | 11.4848 | 6.7256 | -12.5846 | -23.5816 | -26.8877 | -6.9826 | -10.1744 | -11.4673 | -12.6816 | -14.9336 | 52.744 | 49.198 | 45.0715 | 41.1011 | 37.6256 | 22.1399 | 6.0317 | -29.9142 | -24.7275 | -28.2765 | -29.9714 | -31.6275 | -33.9163 | 33.4001 | 28.8031 | 23.5409 | 18.6154 | 14.4021 | -3.3101 | -11.9683 | -14.8642
|  | OXFORD BSP | EE |  |  |  | -26.5356 | -30.9173 | -33.6234 | -35.9295 | -38.7622 | 28.1082 | 22.7919 | 16.9695 | 11.4848 | 6.7256 | -12.5846 | -22.6101 | -25.9693 | -6.9826 | -10.1744 | -11.4673 | -12.6816 | -14.9336 | 52.744 | 49.198 | 45.0715 | 41.1011 | 37.6256 | 22.1399 | 9.7225 | -7.6928 | -24.7275 | -28.2765 | -29.9714 | -31.6275 | -33.9163 | 33.4001 | 28.8031 | 23.5409 | 18.6154 | 14.4021 | -2.5999 | -11.355 | -14.2479
|  | OXFORD BSP | HT |  |  |  | -25.504 | -30.3632 | -32.1846 | -34.1122 | -36.9571 | 30.6633 | 25.0837 | 20.1654 | 15.0348 | 9.8419 | -11.1418 | -23.5816 | -26.8877 | -6.1775 | -9.2652 | -9.9846 | -10.7673 | -12.3989 | 56.3031 | 53.5286 | 50.4072 | 47.196 | 43.897 | 31.6031 | 25.1327 | 23.4521 | -23.7734 | -27.3826 | -28.4295 | -29.7142 | -32.2591 | 35.6531 | 30.8725 | 26.5062 | 21.944 | 17.3562 | -1.0591 | -11.9683 | -14.8642
|  | OXFORD BSP | HE |  |  |  | -25.6438 | -29.6846 | -31.905 | -34.0295 | -36.4346 | 31.4205 | 26.7797 | 21.9715 | 17.3858 | 12.4266 | -10.603 | -19.3622 | -22.0428 | -6.4336 | -9.4591 | -10.5234 | -11.6275 | -12.8918 | 55.6297 | 52.5276 | 49.0827 | 45.694 | 41.9042 | 24.3348 | 10.848 | -6.102 | -24.0265 | -27.3703 | -28.7897 | -30.2224 | -31.954 | 36.1317 | 32.2103 | 27.9644 | 23.8654 | 18.5929 | -3.3101 | -11.2785 | -13.0091
|  | OXFORD BSP | CF |  |  |  | -24.8591 | -27.9673 | -29.0479 | -30.0938 | -31.3805 | 37.6593 | 36.0735 | 33.345 | 30.1674 | 26.7797 | 6.0848 | -6.553 | -15.8622 | -6.0081 | -8.6897 | -9.352 | -10.0499 | -10.8652 | 58.6327 | 56.9705 | 54.398 | 51.5133 | 48.398 | 28.7164 | 6.0317 | -29.9142 | -23.3703 | -26.1234 | -26.8438 | -27.5948 | -28.4938 | 41.0225 | 39.7225 | 37.5174 | 34.9144 | 32.1001 | 12.4837 | 0.81334 | -5.9622
MANNINGTON GSP | POOLE PS (HAMWORTHY) | POOLE PS (HAMWORTHY) | MINIMUM HEADROOM | SZ 00203 90789 | YES | 2.866 | 26.7953 | 25.677 | 24.2933 | 22.8566 | 21.1617 | 19.3168 | 17.0086 | 14.1341 | 11.3035 | 9.4147 | 0.97698 | -4.821 | -8.6159 | 30.6045 | 29.8504 | 28.8453 | 27.8362 | 26.5423 | 25.127 | 23.5933 | 21.7055 | 19.6749 | 18.2158 | 10.9392 | 1.1627 | -20.2659 | 28.3902 | 27.3311 | 26.1025 | 24.877 | 23.2984 | 21.3453 | 19.0953 | 16.376 | 13.6913 | 11.9382 | 4.6137 | -0.022004 | -3.2557
|  | POOLE PS (HAMWORTHY) | EE |  |  |  | 26.7953 | 25.677 | 24.2933 | 22.8566 | 21.1617 | 19.3168 | 17.0086 | 14.1341 | 11.3035 | 9.4147 | 0.97698 | -4.3251 | -8.6159 | 30.6045 | 29.8504 | 28.8453 | 27.8362 | 26.5423 | 25.127 | 23.5933 | 21.7055 | 19.6749 | 18.2158 | 10.9392 | 3.7117 | -7.5975 | 28.3902 | 27.3311 | 26.1025 | 24.877 | 23.2984 | 21.3453 | 19.0953 | 16.376 | 13.6913 | 11.9382 | 4.6137 | 0.39228 | -3.2557
|  | POOLE PS (HAMWORTHY) | HT |  |  |  | 27.5566 | 26.6637 | 25.6484 | 24.0158 | 22.0362 | 20.1321 | 17.979 | 15.5443 | 13.5106 | 11.5851 | 1.677 | -4.821 | -8.3567 | 31.1239 | 30.5402 | 29.8188 | 28.8096 | 27.7698 | 26.827 | 25.7158 | 24.4229 | 23.2943 | 22.2147 | 16.6821 | 13.427 | 11.93 | 29.1311 | 28.2984 | 27.277 | 25.6719 | 23.9647 | 22.3474 | 20.4923 | 18.3851 | 16.5749 | 14.8453 | 5.6209 | -0.022004 | -2.9261
|  | POOLE PS (HAMWORTHY) | HE |  |  |  | 27.3004 | 26.3066 | 25.1331 | 23.7137 | 22.1321 | 20.4739 | 18.6668 | 16.1474 | 13.6739 | 11.6678 | 1.9688 | -4.0557 | -6.3791 | 30.9464 | 30.279 | 29.4382 | 28.3749 | 27.1872 | 26.0749 | 24.777 | 23.1311 | 21.4627 | 19.9617 | 11.3821 | 3.3627 | -7.0996 | 28.8831 | 27.9443 | 26.8811 | 25.68 | 24.1872 | 22.6515 | 20.926 | 18.7178 | 16.5555 | 14.5229 | 5.2392 | 0.62085 | -1.3638
|  | POOLE PS (HAMWORTHY) | CF |  |  |  | 27.8923 | 27.1178 | 26.4311 | 25.7678 | 25.0851 | 24.2943 | 23.676 | 22.5862 | 21.3413 | 19.9984 | 11.4994 | 5.5117 | 0.39024 | 31.3535 | 30.7535 | 30.1055 | 29.43 | 28.7137 | 27.9188 | 27.2882 | 26.2239 | 25.0413 | 23.7402 | 14.0137 | 1.1627 | -20.2659 | 29.4453 | 28.7158 | 28.0688 | 27.4392 | 26.7872 | 26.1035 | 25.5566 | 24.5984 | 23.4525 | 22.1841 | 14.2453 | 8.6953 | 4.3413
LOVEDEAN GSP | PORTSMOUTH BSP | PORTSMOUTH BSP | MINIMUM HEADROOM | SZ 63405 99685 | YES | 10.132 | -26.6272 | -30.5629 | -35.2894 | -41.2792 | -48.1516 | -56.0037 | 51.8392 | 41.2698 | 30.7739 | 22.0667 | -7.6098 | -27.9914 | -29.0108 | 2.7045 | -0.84961 | -4.9078 | -9.8404 | -15.621 | -21.97 | 83.5524 | 75.2871 | 66.8453 | 59.5667 | 23.7749 | -34.1333 | -165.4843 | -25.0241 | -28.9078 | -33.3139 | -38.8527 | -45.268 | -52.4874 | 56.1096 | 46.3065 | 36.5912 | 28.6116 | 1.5759 | -16.0874 | -16.7149
|  | PORTSMOUTH BSP | EE |  |  |  | -26.6272 | -30.5629 | -35.2894 | -41.2792 | -48.1516 | -56.0037 | 51.8392 | 41.2698 | 30.7739 | 22.0667 | -7.6098 | -20.9516 | -19.9812 | 2.7045 | -0.84961 | -4.9078 | -9.8404 | -15.621 | -21.97 | 83.5524 | 75.2871 | 66.8453 | 59.5667 | 23.7749 | -13.8894 | -73.7527 | -25.0241 | -28.9078 | -33.3139 | -38.8527 | -45.268 | -52.4874 | 56.1096 | 46.3065 | 36.5912 | 28.6116 | 1.5759 | -9.9792 | -9.2047
|  | PORTSMOUTH BSP | HT |  |  |  | -24.5333 | -27.9261 | -31.6465 | -36.1925 | -41.8149 | -48.4731 | 60.7279 | 52.3402 | 43.3575 | 35.3994 | -4.8261 | -27.9914 | -29.0108 | 5.1616 | 2.882 | 0.32386 | -2.7139 | -6.1812 | -10.3445 | 97.5514 | 92.4494 | 86.8116 | 81.7167 | 56.2545 | 41.9688 | 40.1473 | -23.1272 | -25.9384 | -29.3782 | -33.6333 | -38.6261 | -44.5996 | 65.3443 | 57.7096 | 49.4616 | 42.1208 | 5.0432 | -16.0874 | -16.7149
|  | PORTSMOUTH BSP | HE |  |  |  | -24.7384 | -27.6088 | -31.0068 | -35.0986 | -39.421 | -45.0037 | 65.4453 | 58.2871 | 50.5198 | 43.4984 | 13.8586 | 0.45243 | -1.8221 | 4.3922 | 1.7637 | -1.3568 | -4.9323 | -8.7874 | -13.4772 | 93.7688 | 87.9024 | 81.332 | 75.0749 | 38.1106 | -0.60981 | -60.8996 | -23.3068 | -25.7578 | -28.8527 | -32.6741 | -36.6639 | -41.718 | 69.3218 | 62.7749 | 55.6371 | 49.1984 | 21.9239 | 10.0871 | 8.3871
|  | PORTSMOUTH BSP | CF |  |  |  | -23.2282 | -24.9639 | -26.8731 | -29.4751 | -32.3068 | -35.2047 | 78.8341 | 75.2484 | 71.3045 | 67.3739 | 43.4086 | 17.2871 | -5.0659 | 5.2014 | 2.9932 | 0.47284 | -2.5833 | -6.0568 | -9.9404 | 98.0341 | 92.7351 | 86.9677 | 80.9749 | 38.7586 | -34.1333 | -165.4843 | -21.9496 | -23.3812 | -25.0149 | -27.4516 | -30.1496 | -32.8006 | 81.4922 | 78.1749 | 74.5004 | 70.883 | 48.7922 | 25.0045 | 5.0188
BRAMLEY (FLEE) | PYESTOCK BSP | PYESTOCK BSP | MINIMUM HEADROOM | SU 82940 54553 | YES | 98.2 | 33.6035 | 33.1647 | 32.6545 | 32.4361 | 31.9382 | 31.4116 | 30.5198 | 29.5555 | 28.5831 | 27.8229 | 23.1157 | 19.681 | 17.7269 | 31.7157 | 31.4076 | 31.0616 | 30.9004 | 30.5473 | 30.1708 | 29.6331 | 29.0218 | 28.3259 | 27.8198 | 24.8596 | 20.6127 | 11.2433 | 30.8616 | 30.5086 | 30.0851 | 29.8871 | 29.4524 | 28.9647 | 28.1647 | 27.282 | 26.3943 | 25.7218 | 21.629 | 18.6484 | 16.9922
|  | PYESTOCK BSP | EE |  |  |  | 33.6035 | 33.1647 | 32.6545 | 32.4361 | 31.9382 | 31.4116 | 30.5198 | 29.5555 | 28.5831 | 27.8229 | 23.7331 | 20.4739 | 18.0647 | 31.7157 | 31.4076 | 31.0616 | 30.9004 | 30.5473 | 30.1708 | 29.6331 | 29.0218 | 28.3259 | 27.8198 | 24.8596 | 21.4259 | 16.431 | 30.8616 | 30.5086 | 30.0851 | 29.8871 | 29.4524 | 28.9647 | 28.1647 | 27.282 | 26.3943 | 25.7218 | 22.1249 | 19.3127 | 17.2494
|  | PYESTOCK BSP | HT |  |  |  | 33.7555 | 33.3422 | 32.9331 | 32.4657 | 31.9586 | 31.731 | 30.829 | 29.9024 | 28.9422 | 27.9871 | 23.1157 | 19.681 | 17.7269 | 31.8851 | 31.6524 | 31.4463 | 31.1973 | 30.9188 | 30.832 | 30.4116 | 29.9769 | 29.5065 | 29.0422 | 26.7402 | 25.2433 | 24.3892 | 30.9861 | 30.6392 | 30.3106 | 29.9331 | 29.4984 | 29.3076 | 28.5198 | 27.6882 | 26.83 | 25.9769 | 21.629 | 18.6484 | 16.9922
|  | PYESTOCK BSP | HE |  |  |  | 33.7739 | 33.3994 | 33.0341 | 32.6106 | 32.1473 | 31.9688 | 31.282 | 30.5667 | 29.8147 | 29.0688 | 24.932 | 21.6341 | 20.0188 | 31.8412 | 31.5718 | 31.3208 | 31.0239 | 30.6963 | 30.5576 | 30.1259 | 29.6637 | 29.1586 | 28.6422 | 25.3453 | 21.8331 | 17.1402 | 31.0024 | 30.6851 | 30.3892 | 30.0443 | 29.6524 | 29.4912 | 28.9024 | 28.2555 | 27.5749 | 26.8984 | 23.1871 | 20.328 | 18.9667
|  | PYESTOCK BSP | CF |  |  |  | 33.9341 | 33.7096 | 33.4678 | 33.231 | 32.9586 | 32.6586 | 32.6565 | 32.3708 | 32.0678 | 31.7433 | 29.232 | 26.0076 | 22.8698 | 31.9086 | 31.6963 | 31.4678 | 31.2453 | 30.9922 | 30.6841 | 30.5433 | 30.1851 | 29.8086 | 29.3953 | 26.1178 | 20.6127 | 11.2433 | 31.1382 | 30.9514 | 30.7555 | 30.5759 | 30.3606 | 30.1076 | 30.0933 | 29.8606 | 29.5902 | 29.2902 | 26.979 | 24.1586 | 21.4229
BRAMLEY (FLEE) | READING BSP | READING BSP | MINIMUM HEADROOM | SU 74642 73856 | YES | 119.797 | 65.6511 | 62.296 | 58.295 | 52.994 | 48.0746 | 38.2226 | -17.156 | -26.5315 | -35.4304 | -42.2356 | -74.6284 | -100.1315 | -111.6141 | 92.6216 | 89.8501 | 86.4736 | 82.0858 | 78.296 | 69.4746 | 16.4144 | 9.644 | 3.1461 | -1.7111 | -27.1437 | -62.606 | -144.9427 | 64.3226 | 61.0807 | 57.2052 | 52.1603 | 47.6726 | 38.2011 | -16.4886 | -25.1743 | -33.4182 | -39.4141 | -67.3498 | -89.3509 | -98.5723
|  | READING BSP | EE |  |  |  | 65.6511 | 62.296 | 58.295 | 52.994 | 48.0746 | 38.2226 | -17.156 | -26.5315 | -35.4304 | -42.2356 | -73.8335 | -95.7111 | -106.5468 | 92.6216 | 89.8501 | 86.4736 | 82.0858 | 78.296 | 69.4746 | 16.4144 | 9.644 | 3.1461 | -1.7111 | -27.1437 | -54.5998 | -94.5162 | 64.3226 | 61.0807 | 57.2052 | 52.1603 | 47.6726 | 38.2011 | -16.4886 | -25.1743 | -33.4182 | -39.4141 | -67.1641 | -85.4376 | -94.4784
|  | READING BSP | HT |  |  |  | 67.2267 | 63.8277 | 59.9573 | 55.6879 | 51.4634 | 41.693 | -12.8294 | -21.0223 | -28.1723 | -35.7968 | -74.6284 | -100.1315 | -111.6141 | 94.6664 | 92.494 | 89.8736 | 87.1318 | 84.5124 | 76.4236 | 25.1869 | 20.3951 | 16.3338 | 11.8349 | -9.7743 | -22.007 | -27.2407 | 66.1389 | 63.0277 | 59.4246 | 55.5634 | 51.6848 | 42.2124 | -11.506 | -18.9509 | -25.4631 | -32.4325 | -67.3498 | -89.3509 | -98.5723
|  | READING BSP | HE |  |  |  | 67.2562 | 64.3746 | 60.7746 | 56.8103 | 52.9889 | 43.8001 | -9.3631 | -16.2029 | -22.9743 | -29.6243 | -62.11 | -83.6141 | -93.4396 | 94.2246 | 91.8848 | 88.9083 | 85.8144 | 82.8756 | 74.4328 | 22.9991 | 18.1124 | 13.0706 | 7.9349 | -20.6192 | -48.408 | -87.6529 | 66.1236 | 63.4267 | 60.0613 | 56.4797 | 53.0022 | 44.0358 | -8.5539 | -14.7743 | -20.9896 | -27.0958 | -56.3253 | -74.2866 | -82.0947
|  | READING BSP | CF |  |  |  | 68.9624 | 67.2899 | 65.1583 | 62.3226 | 60.3573 | 53.4195 | 3.5185 | 0.67261 | -2.5784 | -5.9345 | -30.9856 | -57.96 | -82.3723 | 95.0777 | 93.196 | 90.8746 | 87.996 | 85.9338 | 78.3685 | 27.5369 | 23.842 | 19.8991 | 15.7093 | -15.0427 | -62.606 | -144.9427 | 67.6226 | 65.9726 | 63.9297 | 61.2981 | 59.544 | 52.6471 | 2.7798 | 0.06751 | -2.9213 | -5.9917 | -29.0151 | -52.4458 | -73.6866
BRAMLEY (FLEE) | READING TOWN BSP | READING TOWN BSP | MINIMUM HEADROOM | SU 71580 74111 | YES | 38.895 | 43.4697 | 38.2095 | 36.2901 | 34.3503 | 30.2411 | 26.5442 | 22.8656 | 18.8523 | 14.288 | 10.4564 | 3.1207 | -2.4701 | -3.9069 | 52.775 | 48.3097 | 46.8627 | 45.5985 | 42.4444 | 40.1434 | 37.775 | 34.978 | 32.0076 | 29.4331 | 20.2189 | 4.4903 | -27.8852 | 45.3638 | 40.5872 | 38.7168 | 36.9801 | 33.2219 | 29.8964 | 26.5831 | 22.9505 | 18.8801 | 15.628 | 8.776 | 3.9219 | 2.7485
|  | READING TOWN BSP | EE |  |  |  | 43.4697 | 38.2095 | 36.2901 | 34.3503 | 30.2411 | 26.5442 | 22.8656 | 18.8523 | 14.288 | 10.4564 | 3.1207 | -0.97012 | -1.9558 | 52.775 | 48.3097 | 46.8627 | 45.5985 | 42.4444 | 40.1434 | 37.775 | 34.978 | 32.0076 | 29.4331 | 20.2189 | 10.4474 | -5.1424 | 45.3638 | 40.5872 | 38.7168 | 36.9801 | 33.2219 | 29.8964 | 26.5831 | 22.9505 | 18.8801 | 15.628 | 8.776 | 5.3515 | 4.3393
|  | READING TOWN BSP | HT |  |  |  | 44.0911 | 39.036 | 37.4819 | 35.4931 | 31.6901 | 28.4829 | 24.8891 | 20.9564 | 17.0615 | 13.1799 | 3.7166 | -2.4701 | -3.9069 | 53.377 | 49.2485 | 48.2893 | 47.228 | 44.5576 | 42.9434 | 41.077 | 38.7382 | 36.6056 | 34.4209 | 28.1362 | 24.7168 | 23.7791 | 45.777 | 41.3158 | 39.928 | 38.2576 | 34.8699 | 32.1944 | 29.177 | 25.7189 | 22.328 | 18.927 | 9.6189 | 3.9219 | 2.7485
|  | READING TOWN BSP | HE |  |  |  | 44.0615 | 39.0656 | 37.587 | 35.6768 | 31.9707 | 29.0707 | 26.1074 | 22.5176 | 18.6585 | 14.9176 | 7.6482 | 3.3829 | 1.9931 | 53.1842 | 48.9025 | 47.7536 | 46.4995 | 43.6178 | 41.874 | 39.9505 | 37.3974 | 34.8495 | 32.2658 | 22.6321 | 12.726 | -2.773 | 45.7229 | 41.3352 | 40.0025 | 38.3862 | 35.0709 | 32.6382 | 30.1974 | 27.0678 | 23.7638 | 20.5352 | 13.3525 | 9.6025 | 8.4944
|  | READING TOWN BSP | CF |  |  |  | 44.685 | 40.2656 | 39.187 | 37.734 | 34.6493 | 32.4421 | 31.2452 | 29.2166 | 26.9023 | 24.7656 | 14.2268 | 8.2493 | 2.9136 | 53.4964 | 49.4423 | 48.4291 | 47.3087 | 44.6546 | 42.977 | 41.7199 | 39.6607 | 37.6178 | 35.5648 | 22.5382 | 4.4903 | -27.8852 | 46.0893 | 42.3342 | 41.3923 | 40.2046 | 37.4668 | 35.6209 | 34.6964 | 32.9087 | 30.9199 | 29.0352 | 19.4311 | 13.6985 | 8.9362
MANNINGTON GSP | REDHILL BSP | REDHILL BSP | MINIMUM HEADROOM | SZ 08581 96162 | YES | 19.407 | 20.4495 | 16.6069 | 14.8161 | 12.3885 | 9.961 | 7.2957 | 3.1069 | -1.3941 | -5.8819 | -9.1298 | -26.7819 | -40.1962 | -46.2533 | 31.4209 | 28.0569 | 26.7069 | 24.7691 | 22.7865 | 20.6865 | 17.8375 | 14.6467 | 11.3293 | 9.0712 | -3.6931 | -20.4911 | -61.3258 | 20.5178 | 16.7855 | 15.1334 | 12.7579 | 10.3763 | 7.8722 | 4.0059 | -0.19719 | -4.389 | -7.3227 | -22.638 | -33.9819 | -38.9094
|  | REDHILL BSP | EE |  |  |  | 20.4495 | 16.6069 | 14.8161 | 12.3885 | 9.961 | 7.2957 | 3.1069 | -1.3941 | -5.8819 | -9.1298 | -25.44 | -37.74 | -44.1319 | 31.4209 | 28.0569 | 26.7069 | 24.7691 | 22.7865 | 20.6865 | 17.8375 | 14.6467 | 11.3293 | 9.0712 | -3.6931 | -17.7441 | -37.8696 | 20.5178 | 16.7855 | 15.1334 | 12.7579 | 10.3763 | 7.8722 | 4.0059 | -0.19719 | -4.389 | -7.3227 | -21.786 | -31.9115 | -37.2319
|  | REDHILL BSP | HT |  |  |  | 21.2433 | 17.3793 | 15.1569 | 13.1191 | 11.6885 | 9.5549 | 5.8589 | 2.0283 | -1.9727 | -6.0472 | -26.7819 | -40.1962 | -46.2533 | 32.4086 | 29.3222 | 27.9232 | 26.6783 | 25.9508 | 24.611 | 22.6518 | 20.5018 | 18.214 | 15.8498 | 4.8263 | -1.2258 | -3.9268 | 21.478 | 17.7957 | 15.7457 | 13.8753 | 12.61 | 10.5804 | 7.2263 | 3.6824 | -0.030861 | -3.8472 | -22.638 | -33.9819 | -38.9094
|  | REDHILL BSP | HE |  |  |  | 21.3464 | 17.6712 | 15.6365 | 13.7885 | 12.5344 | 10.6283 | 7.6538 | 4.5651 | 1.3436 | -2.0145 | -19.0911 | -31.0411 | -36.0258 | 32.2433 | 29.0446 | 27.4946 | 26.0977 | 25.1375 | 23.5742 | 21.5089 | 19.2171 | 16.7549 | 14.1202 | -0.48698 | -14.6727 | -34.2696 | 21.5444 | 18.0273 | 16.1406 | 14.4446 | 13.3344 | 11.5089 | 8.7702 | 5.8426 | 2.7753 | -0.42474 | -15.9921 | -25.9227 | -29.9451
|  | REDHILL BSP | CF |  |  |  | 22.2046 | 18.9793 | 17.6742 | 16.2661 | 15.3069 | 14.7059 | 13.5222 | 12.2753 | 10.9824 | 9.5008 | -1.638 | -14.6941 | -27.1105 | 32.7148 | 29.6202 | 28.3926 | 27.0273 | 25.9681 | 25.0773 | 23.511 | 21.7334 | 19.8498 | 17.8263 | 3.0722 | -20.4911 | -61.3258 | 22.3199 | 19.214 | 17.9906 | 16.6457 | 15.7365 | 15.2191 | 14.0671 | 12.7906 | 11.4395 | 10.0253 | -0.42882 | -12.1309 | -22.9513
NURSLING GSP | ROWNHAMS | ROWNHAMS | MINIMUM HEADROOM | SU 37168 16854 | YES | 41.535 | 11.113 | 6.4262 | 2.4007 | -0.96561 | 108.9985 | 100.1821 | 91.9587 | 83.5934 | 74.2189 | 67.0026 | 23.7158 | -2.6005 | -20.4056 | 39.9632 | 36.0938 | 32.8458 | 30.206 | 136.4428 | 128.4172 | 122.4938 | 116.6417 | 109.3979 | 101.1213 | 65.7132 | 34.6162 | -20.9817 | 10.5795 | 6.0979 | 2.3285 | -0.7654 | 106.5744 | 97.7775 | 90.0662 | 82.3377 | 73.4417 | 66.7775 | 25.2591 | 0.33051 | -17.1195
|  | ROWNHAMS | EE |  |  |  | 11.113 | 6.4262 | 2.4007 | -0.96561 | 108.9985 | 100.1821 | 91.9587 | 83.5934 | 74.2189 | 67.0026 | 30.0995 | 1.6413 | -15.424 | 39.9632 | 36.0938 | 32.8458 | 30.206 | 136.4428 | 128.4172 | 122.4938 | 116.6417 | 109.5275 | 104.3775 | 74.1397 | 41.3499 | 4.8938 | 10.5795 | 6.0979 | 2.3285 | -0.7654 | 106.5744 | 97.7775 | 90.0662 | 82.3377 | 73.4417 | 66.7775 | 32.2764 | 4.7754 | -11.1358
|  | ROWNHAMS | HT |  |  |  | 12.9609 | 8.4854 | 5.1466 | 1.4364 | 112.1138 | 102.8617 | 96.2046 | 88.4597 | 81.1556 | 72.0342 | 28.4291 | -2.6005 | -20.4056 | 41.5958 | 38.1672 | 36.1101 | 33.706 | 141.253 | 133.1846 | 129.3458 | 124.354 | 119.7805 | 113.2254 | 84.9999 | 64.7836 | 52.5775 | 12.407 | 8.1407 | 5.0581 | 1.5928 | 109.8805 | 100.6938 | 94.5438 | 87.2775 | 80.604 | 71.7764 | 30.454 | 0.33051 | -17.1195
|  | ROWNHAMS | HE |  |  |  | 12.7732 | 8.713 | 4.9762 | 1.1017 | 111.575 | 102.0128 | 95.925 | 88.6026 | 78.3709 | 68.3679 | 23.7158 | -0.10561 | -15.8689 | 41.157 | 37.804 | 34.8479 | 31.7019 | 138.4632 | 129.5254 | 124.8632 | 118.7754 | 109.3979 | 101.1213 | 65.7132 | 34.6162 | -4.8379 | 12.2091 | 8.354 | 4.8101 | 1.0785 | 109.0907 | 99.4683 | 93.7917 | 86.8683 | 76.7591 | 67.6846 | 25.2591 | 0.81011 | -15.5134
|  | ROWNHAMS | CF |  |  |  | 14.2028 | 11.2089 | 9.4324 | 7.117 | 119.1566 | 113.1597 | 110.0321 | 107.0811 | 103.6913 | 99.8097 | 71.9485 | 41.2219 | 20.5872 | 41.9591 | 39.1111 | 37.5132 | 35.303 | 142.8121 | 136.6336 | 133.2652 | 129.9744 | 126.3366 | 122.1019 | 92.1295 | 45.6815 | -20.9817 | 13.5387 | 10.6724 | 9.0387 | 6.8499 | 116.2979 | 110.4479 | 107.4958 | 104.7662 | 101.5581 | 97.7979 | 72.207 | 43.306 | 22.6744
MANNINGTON GSP | SALISBURY | SALISBURY | MINIMUM HEADROOM | SU 11049 31395 | YES | 59.141 | 36.7123 | 32.1463 | 23.4412 | 20.7739 | 17.3576 | 14.328 | 9.53 | 4.0668 | -0.76284 | -4.5026 | -20.9884 | -31.972 | -37.1077 | 56.6521 | 52.7749 | 44.7872 | 42.6994 | 40.129 | 37.9882 | 34.7698 | 30.9933 | 27.6892 | 25.0514 | 11.9188 | -3.1047 | -40.7537 | 42.6449 | 38.1984 | 29.6668 | 27.1361 | 23.8698 | 21.1545 | 16.6984 | 11.5341 | 7.1157 | 3.7555 | -10.9567 | -20.421 | -24.5955
|  | SALISBURY | EE |  |  |  | 36.7123 | 32.1463 | 23.4412 | 20.7739 | 17.3576 | 14.328 | 9.53 | 4.0668 | -0.76284 | -4.5026 | -20.9884 | -30.1945 | -34.3384 | 56.6521 | 52.7749 | 44.7872 | 42.6994 | 40.129 | 37.9882 | 34.7698 | 30.9933 | 27.6892 | 25.0514 | 11.9188 | -0.46488 | -18.6812 | 42.6449 | 38.1984 | 29.6668 | 27.1361 | 23.8698 | 21.1545 | 16.6984 | 11.5341 | 7.1157 | 3.7555 | -10.9567 | -18.8537 | -22.3475
|  | SALISBURY | HT |  |  |  | 37.6316 | 33.3463 | 25.2249 | 22.7239 | 19.6443 | 16.6147 | 12.2678 | 7.7382 | 3.4525 | -0.80774 | -20.5394 | -31.972 | -37.1077 | 57.4857 | 53.9902 | 46.6525 | 45.0504 | 43.2249 | 41.4994 | 39.1576 | 36.5525 | 34.0474 | 31.4606 | 20.3351 | 14.481 | 11.9249 | 43.6929 | 39.5545 | 31.5596 | 29.178 | 26.3463 | 23.628 | 19.7535 | 15.6178 | 11.677 | 7.6963 | -10.3394 | -20.421 | -24.5955
|  | SALISBURY | HE |  |  |  | 37.647 | 33.5372 | 25.4984 | 23.2219 | 20.1953 | 17.477 | 13.631 | 10.0739 | 6.1208 | 2.2168 | -15.1179 | -24.1118 | -27.8955 | 57.3082 | 53.6984 | 46.1708 | 44.4474 | 42.1892 | 40.3698 | 37.8974 | 35.5637 | 32.8178 | 29.9025 | 15.3759 | 2.781 | -15.223 | 43.699 | 39.7055 | 31.7912 | 29.6055 | 26.7504 | 24.3127 | 20.8463 | 17.6484 | 14.0596 | 10.4076 | -5.4802 | -13.0863 | -16.071
|  | SALISBURY | CF |  |  |  | 38.5225 | 34.8994 | 27.4627 | 26.0065 | 24.0361 | 22.2065 | 20.5525 | 18.3096 | 16.3933 | 14.527 | 0.027976 | -11.3873 | -22.5496 | 57.797 | 54.327 | 47.0443 | 45.6708 | 43.8361 | 42.1963 | 40.6096 | 38.4535 | 36.4851 | 34.4402 | 18.3943 | -3.1047 | -40.7537 | 44.4837 | 40.927 | 33.5596 | 32.1392 | 30.1892 | 28.5219 | 27.0504 | 24.9647 | 23.2076 | 21.4729 | 7.8208 | -2.1608 | -11.9384
MANNINGTON GSP | SHAFTESBURY BSP | SHAFTESBURY BSP | MINIMUM HEADROOM | ST 85442 23791 | YES | 23.786 | 39.7219 | 35.0709 | 31.4913 | 27.977 | 24.7791 | 21.3546 | 17.6842 | 13.3485 | 9.5362 | 6.5903 | -8.326 | -17.1015 | -22.9179 | 49.6487 | 46.0201 | 43.5446 | 41.1731 | 39.2813 | 37.2201 | 34.9395 | 32.1517 | 29.6721 | 27.6854 | 16.4997 | 4.1874 | -24.3983 | 38.1782 | 33.8834 | 30.617 | 27.3415 | 24.5568 | 21.5252 | 18.1578 | 14.0303 | 10.466 | 7.8599 | -5.1279 | -12.7605 | -17.4779
|  | SHAFTESBURY BSP | EE |  |  |  | 39.7219 | 35.0709 | 31.4913 | 27.977 | 24.7791 | 21.3546 | 17.6842 | 13.3485 | 9.5362 | 6.5903 | -8.326 | -16.1107 | -21.7495 | 49.6487 | 46.0201 | 43.5446 | 41.1731 | 39.2813 | 37.2201 | 34.9395 | 32.1517 | 29.6721 | 27.6854 | 16.4997 | 6.6354 | -7.9289 | 38.1782 | 33.8834 | 30.617 | 27.3415 | 24.5568 | 21.5252 | 18.1578 | 14.0303 | 10.466 | 7.8599 | -5.1279 | -11.8054 | -16.4881
|  | SHAFTESBURY BSP | HT |  |  |  | 40.678 | 36.3689 | 33.2362 | 30.2444 | 27.078 | 23.6934 | 20.3474 | 17.3301 | 13.7403 | 10.2474 | -7.4832 | -17.1015 | -22.9179 | 50.466 | 47.2242 | 45.2323 | 43.4231 | 41.7507 | 39.9374 | 38.2027 | 36.6987 | 34.7293 | 32.816 | 23.217 | 18.4721 | 15.8558 | 39.1323 | 35.1772 | 32.4068 | 29.7344 | 26.967 | 23.9772 | 20.9895 | 18.2905 | 15.0048 | 11.8231 | -4.2799 | -12.7605 | -17.4779
|  | SHAFTESBURY BSP | HE |  |  |  | 40.6301 | 36.3658 | 33.2821 | 30.324 | 27.2025 | 23.8689 | 20.5229 | 18.074 | 14.7648 | 11.6658 | -5.9158 | -14.1118 | -17.9107 | 50.2946 | 46.9272 | 44.7823 | 42.7987 | 40.9262 | 38.8864 | 36.7425 | 35.2415 | 33.0129 | 30.8803 | 17.4874 | 7.2742 | -6.4881 | 39.0823 | 35.1619 | 32.4313 | 29.7915 | 27.0691 | 24.1242 | 21.0885 | 18.9272 | 15.8925 | 13.0538 | -2.9218 | -9.836 | -12.9748
|  | SHAFTESBURY BSP | CF |  |  |  | 41.3444 | 37.5148 | 35.0893 | 32.9587 | 30.3311 | 27.4178 | 25.4821 | 23.3678 | 21.5913 | 20.2127 | 8.2056 | -1.7597 | -10.8515 | 50.7129 | 47.4885 | 45.6517 | 44.1211 | 42.3415 | 40.2415 | 38.6129 | 36.7844 | 35.1619 | 33.767 | 21.4323 | 4.1874 | -24.3983 | 39.7344 | 36.2068 | 34.0721 | 32.1844 | 29.915 | 27.3772 | 25.6497 | 23.7119 | 22.0793 | 20.8885 | 9.6497 | 0.7956 | -7.2493
IVER 132KV | SLOUGH | SLOUGH | MINIMUM HEADROOM | SU 95574 81752 | YES | 11.761 | 9.8139 | -19.9463 | -135.8657 | -259.6218 | -221.8014 | -380.7626 | -459.1157 | -464.0769 | -468.4269 | -472.1269 | -589.0483 | -600.2585 | -604.6789 | 8.4129 | -27.9493 | -171.9432 | -326.2044 | -311.8116 | -509.8647 | -606.4442 | -611.1044 | -615.0361 | -618.7085 | -760.5463 | -773.3993 | -798.9851 | 0.65065 | -36.0636 | -180.3177 | -334.7269 | -317.6963 | -515.8636 | -612.9514 | -618.1596 | -622.5963 | -626.5657 | -769.8667 | -781.2565 | -786.2504
|  | SLOUGH | EE |  |  |  | 9.8139 | -19.9463 | -135.8657 | -259.6218 | -221.8014 | -380.7626 | -459.1157 | -464.0769 | -468.4269 | -472.1269 | -587.4524 | -595.6432 | -598.5585 | 8.4129 | -27.9493 | -171.9432 | -326.2044 | -311.8116 | -509.8647 | -606.4442 | -611.1044 | -615.0361 | -618.7085 | -760.5463 | -773.3993 | -791.3585 | 0.65065 | -36.0636 | -180.3177 | -334.7269 | -317.6963 | -515.8636 | -612.9514 | -618.1596 | -622.5963 | -626.5657 | -767.883 | -775.7718 | -779.5912
|  | SLOUGH | HT |  |  |  | 10.3843 | -19.483 | -135.2585 | -258.4167 | -220.5973 | -379.0922 | -456.6657 | -460.9157 | -464.7147 | -468.83 | -589.0483 | -600.2585 | -604.6789 | 8.7639 | -27.5422 | -171.0657 | -324.3667 | -309.6055 | -507.1085 | -602.7953 | -606.63 | -609.8677 | -613.4891 | -755.6279 | -764.434 | -769.2228 | 1.0864 | -35.681 | -179.7891 | -333.4718 | -316.2902 | -514.0412 | -610.4126 | -615.032 | -619.0698 | -623.5065 | -769.8667 | -781.2565 | -786.2504
|  | SLOUGH | HE |  |  |  | 10.4129 | -19.3636 | -135.0514 | -258.1177 | -220.1963 | -378.5698 | -455.2922 | -458.734 | -461.3279 | -464.1228 | -579.4044 | -587.1687 | -591.5371 | 8.6966 | -27.6728 | -171.2769 | -324.832 | -310.3483 | -508.0544 | -603.181 | -606.5565 | -608.8738 | -611.483 | -753.5116 | -766.4442 | -784.8698 | 1.119 | -35.584 | -179.6177 | -333.2198 | -315.9534 | -513.5677 | -608.9555 | -612.6555 | -615.2779 | -618.1463 | -759.1759 | -766.7983 | -771.6851
|  | SLOUGH | CF |  |  |  | 10.9558 | -18.3616 | -133.4973 | -256.5391 | -217.9085 | -375.8738 | -451.432 | -453.4269 | -454.9289 | -456.6473 | -566.8851 | -574.9259 | -582.2616 | 8.866 | -27.4024 | -170.8779 | -324.3259 | -309.434 | -507.0544 | -601.7289 | -604.5085 | -606.8075 | -609.1789 | -748.832 | -767.0289 | -798.9851 | 1.5741 | -34.7361 | -178.2779 | -331.8259 | -313.9147 | -511.1198 | -605.3575 | -607.6891 | -609.4391 | -611.2606 | -746.6269 | -754.2014 | -760.9034
NURSLING GSP | SOUTHAMPTON (2 X 60) | SOUTHAMPTON (2 X 60) | MINIMUM HEADROOM | SU 41425 11999 | YES | 16.542 | 29.2104 | 28.4073 | 27.4165 | 26.1961 | 24.3306 | 21.1571 | 8.3357 | 5.5092 | 1.7418 | -2.5214 | -14.4704 | -24.6061 | -33.8408 | 33.9185 | 33.2247 | 32.491 | 31.2726 | 29.8296 | 26.5551 | 14.9378 | 12.2796 | 6.3714 | 1.952 | -11.75 | -29.1092 | -55.7367 | 24.6838 | 23.7247 | 22.7328 | 21.5818 | 19.8204 | 16.5235 | 3.7908 | 0.92347 | -4.1245 | -8.7796 | -20.7214 | -31.6347 | -42.6367
|  | SOUTHAMPTON (2 X 60) | EE |  |  |  | 29.2104 | 28.4073 | 27.4165 | 26.1961 | 24.3306 | 22.0418 | 10.2755 | 6.9347 | 3.0214 | 0.50816 | -8.5694 | -20.8694 | -27.2898 | 33.9185 | 33.2247 | 32.491 | 31.6614 | 30.3204 | 28.3378 | 16.849 | 14.6888 | 11.6541 | 9.552 | -2.1245 | -22.5173 | -42.6235 | 24.6838 | 23.7247 | 22.7328 | 21.5818 | 19.8204 | 17.4755 | 5.6582 | 2.598 | -1.2541 | -3.7041 | -12.7429 | -26.3347 | -33.0969
|  | SOUTHAMPTON (2 X 60) | HT |  |  |  | 29.5389 | 28.8747 | 28.0573 | 26.992 | 25.2051 | 21.1571 | 8.3357 | 5.5092 | 3.502 | 0.73776 | -10.3653 | -24.3408 | -32.9041 | 34.3277 | 33.9063 | 33.3216 | 32.4614 | 31.1796 | 27.9918 | 16.1408 | 14.0122 | 12.8112 | 10.6388 | 2.4684 | -10.649 | -19.4153 | 25.1961 | 24.4563 | 23.5563 | 22.3185 | 20.6071 | 16.5235 | 3.7908 | 0.92347 | -0.98469 | -3.8582 | -15.2122 | -30.148 | -39.7888
|  | SOUTHAMPTON (2 X 60) | HE |  |  |  | 29.4593 | 28.7532 | 27.8185 | 26.4471 | 24.8561 | 21.9163 | 10.4153 | 7.3847 | 1.7418 | -2.5214 | -14.4704 | -24.6061 | -33.8408 | 34.1481 | 33.5553 | 32.6696 | 31.2726 | 29.8296 | 26.5551 | 14.9378 | 12.2796 | 6.3714 | 1.952 | -11.75 | -29.1092 | -54.2969 | 25.1144 | 24.3849 | 23.4012 | 21.8777 | 20.2408 | 16.8837 | 5.2286 | 2.1663 | -4.1245 | -8.7796 | -20.7214 | -31.6347 | -42.6367
|  | SOUTHAMPTON (2 X 60) | CF |  |  |  | 30.09 | 29.843 | 29.3869 | 28.892 | 27.7827 | 26.7459 | 16.0571 | 14.8969 | 12.902 | 10.6694 | 2.1561 | -5.6592 | -12.8663 | 34.5451 | 34.1583 | 33.6073 | 32.9981 | 31.7602 | 30.5745 | 19.5214 | 18.0449 | 16.0878 | 13.9092 | 1.2194 | -20.1939 | -55.7367 | 25.792 | 25.4798 | 24.94 | 24.3573 | 23.1592 | 22.052 | 11.2735 | 10.1214 | 8.2408 | 6.1286 | -2.4163 | -10.5949 | -17.7684
NURSLING GSP | SOUTHAMPTON (2 X 90) | SOUTHAMPTON (2 X 90) | MINIMUM HEADROOM | SU 41425 11999 | YES | 30.66 | 39.0214 | 25.5528 | 22.8773 | 20.41 | 17.4651 | 11.6192 | 6.96 | 1.1437 | -9.2798 | -17.1369 | -42.0176 | -63.8451 | -84.4696 | 47.2216 | 34.4561 | 32.6684 | 30.2745 | 28.0602 | 21.2367 | 16.9806 | 11.8888 | 0.015298 | -8.6633 | -35.452 | -65.7572 | -107.6378 | 38.4533 | 25.1398 | 22.6857 | 20.4469 | 17.6714 | 10.8082 | 6.3 | 0.66326 | -11.6765 | -20.4541 | -45.8765 | -69.798 | -93.8276
|  | SOUTHAMPTON (2 X 90) | EE |  |  |  | 39.0214 | 25.5528 | 22.8773 | 20.41 | 17.4651 | 12.6722 | 7.8692 | 3.1437 | -3.34 | -7.6716 | -28.0563 | -55.4104 | -69.8094 | 47.2216 | 34.4561 | 32.6684 | 30.999 | 28.8102 | 24.4816 | 20.248 | 16.5888 | 10.6592 | 6.5786 | -14.8276 | -51.5959 | -82.801 | 38.4533 | 25.1398 | 22.6857 | 20.4469 | 17.6714 | 12.8316 | 8.0775 | 3.7214 | -2.8623 | -7.1235 | -26.9612 | -57.4194 | -72.6092
|  | SOUTHAMPTON (2 X 90) | HT |  |  |  | 39.9398 | 26.8702 | 24.4141 | 21.5784 | 18.5488 | 12.0151 | 6.96 | 1.1437 | -3.1982 | -9.2104 | -33.5696 | -62.8359 | -81.742 | 47.8226 | 35.7673 | 34.1908 | 32.1643 | 30.0673 | 24.1428 | 20.0714 | 15.3041 | 12.248 | 7.0959 | -12.2245 | -39.5408 | -57.7378 | 39.2696 | 26.4775 | 24.2337 | 21.4898 | 18.6796 | 11.8041 | 6.7857 | 0.88162 | -3.1572 | -9.4112 | -33.8306 | -65.7796 | -87.0541
|  | SOUTHAMPTON (2 X 90) | HE |  |  |  | 39.8224 | 26.7733 | 24.1977 | 20.9141 | 18.1957 | 11.6192 | 7.1763 | 1.6396 | -9.2798 | -17.1369 | -42.0176 | -63.8451 | -84.4696 | 47.6655 | 35.2663 | 33.2265 | 30.2745 | 28.0602 | 21.2367 | 16.9806 | 11.8888 | 0.015298 | -8.6633 | -35.452 | -65.7572 | -107.6378 | 39.1635 | 26.3745 | 23.948 | 20.6163 | 18.0082 | 10.8082 | 6.3 | 0.66326 | -11.6765 | -20.4541 | -45.8765 | -69.798 | -93.8276
|  | SOUTHAMPTON (2 X 90) | CF |  |  |  | 41.2531 | 29.1263 | 27.9396 | 26.5518 | 24.6437 | 22.2865 | 19.6967 | 17.3814 | 14.2988 | 11.1937 | -5.6645 | -22.6298 | -38.2686 | 48.2522 | 36.3653 | 35.3469 | 34.1408 | 32.3306 | 30.0459 | 27.1541 | 24.3847 | 21.0255 | 17.4143 | -5.7837 | -39.3143 | -91.4174 | 40.0451 | 28.1826 | 27.301 | 26.0949 | 24.2714 | 21.999 | 19.4286 | 17.2235 | 14.2214 | 11.1071 | -6.0194 | -23.4867 | -39.4337
NURSLING GSP | (NEW) SOUTHAMPTON (3 X 90) | SOUTHAMPTON (3X 90) | MINIMUM HEADROOM | SU 41425 11999 | YES | 4.508 | 0 | 0 | 0 | 0 | 228.592 | 228.592 | 228.592 | 228.592 | 228.592 | 228.592 | 228.592 | 228.592 | 228.592 | 0 | 0 | 0 | 0 | 218.692 | 218.692 | 218.692 | 218.692 | 218.692 | 218.692 | 218.692 | 218.692 | 218.692 | 0 | 0 | 0 | 0 | 222.292 | 222.292 | 222.292 | 222.292 | 222.292 | 222.292 | 222.292 | 222.292 | 222.292
|  | SOUTHAMPTON (3X 90) | EE |  |  |  | 0 | 0 | 0 | 0 | 228.592 | 228.592 | 228.592 | 228.592 | 228.592 | 228.592 | 228.592 | 228.592 | 228.592 | 0 | 0 | 0 | 0 | 218.692 | 218.692 | 218.692 | 218.692 | 218.692 | 218.692 | 218.692 | 218.692 | 218.692 | 0 | 0 | 0 | 0 | 222.292 | 222.292 | 222.292 | 222.292 | 222.292 | 222.292 | 222.292 | 222.292 | 222.292
|  | SOUTHAMPTON (3X 90) | HT |  |  |  | 0 | 0 | 0 | 0 | 228.592 | 228.592 | 228.592 | 228.592 | 228.592 | 228.592 | 228.592 | 228.592 | 228.592 | 0 | 0 | 0 | 0 | 218.692 | 218.692 | 218.692 | 218.692 | 218.692 | 218.692 | 218.692 | 218.692 | 218.692 | 0 | 0 | 0 | 0 | 222.292 | 222.292 | 222.292 | 222.292 | 222.292 | 222.292 | 222.292 | 222.292 | 222.292
|  | SOUTHAMPTON (3X 90) | HE |  |  |  | 0 | 0 | 0 | 0 | 228.592 | 228.592 | 228.592 | 228.592 | 228.592 | 228.592 | 228.592 | 228.592 | 228.592 | 0 | 0 | 0 | 0 | 218.692 | 218.692 | 218.692 | 218.692 | 218.692 | 218.692 | 218.692 | 218.692 | 218.692 | 0 | 0 | 0 | 0 | 222.292 | 222.292 | 222.292 | 222.292 | 222.292 | 222.292 | 222.292 | 222.292 | 222.292
|  | SOUTHAMPTON (3X 90) | CF |  |  |  | 0 | 0 | 0 | 0 | 228.592 | 228.592 | 228.592 | 228.592 | 228.592 | 228.592 | 228.592 | 228.592 | 228.592 | 0 | 0 | 0 | 0 | 218.692 | 218.692 | 218.692 | 218.692 | 218.692 | 218.692 | 218.692 | 218.692 | 218.692 | 0 | 0 | 0 | 0 | 222.292 | 222.292 | 222.292 | 222.292 | 222.292 | 222.292 | 222.292 | 222.292 | 222.292
LALEHAM | STAINES | STAINES | MINIMUM HEADROOM | TQ 04585 72135 | YES | 37.758 | 92.3263 | 89.5845 | 85.9763 | 82.2233 | 78.8865 | 74.7008 | 68.1753 | 61.2059 | 54.1457 | 48.1314 | 22.7692 | 1.4478 | -10.3318 | 110.3549 | 108.31 | 105.6324 | 102.8794 | 100.2569 | 96.7814 | 91.6722 | 86.0998 | 80.4539 | 75.7396 | 54.5947 | 31.7947 | -26.2339 | 89.6304 | 87.2029 | 83.9906 | 80.6345 | 77.5978 | 73.7661 | 67.5957 | 60.7202 | 53.7865 | 48.2263 | 25.3814 | 5.9998 | -4.5971
|  | STAINES | EE |  |  |  | 92.3263 | 89.5845 | 85.9763 | 82.2233 | 78.8865 | 74.7008 | 68.1753 | 61.2059 | 54.1457 | 48.1314 | 22.812 | 5.3049 | -8.3298 | 110.3549 | 108.31 | 105.6324 | 102.8794 | 100.2569 | 96.7814 | 91.6722 | 86.0998 | 80.4539 | 75.7396 | 54.5947 | 33.8171 | 2.2631 | 89.6304 | 87.2029 | 83.9906 | 80.6345 | 77.5978 | 73.7661 | 67.5957 | 60.7202 | 53.7865 | 48.2263 | 25.3814 | 9.7508 | -2.5135
|  | STAINES | HT |  |  |  | 93.658 | 91.1182 | 87.9488 | 84.8253 | 81.56 | 77.9518 | 72.3631 | 66.7335 | 60.4773 | 53.8314 | 22.7692 | 1.4478 | -10.3318 | 111.8008 | 110.2855 | 108.3906 | 106.6457 | 104.6365 | 102.3569 | 98.8569 | 95.2222 | 90.9386 | 86.4692 | 67.6141 | 56.3243 | 50.6131 | 90.9488 | 88.7396 | 85.9886 | 83.2865 | 80.3396 | 77.062 | 71.808 | 66.4641 | 60.5141 | 54.2835 | 25.4559 | 5.9998 | -4.5971
|  | STAINES | HE |  |  |  | 93.4692 | 90.9416 | 87.7988 | 84.6998 | 81.4722 | 77.8182 | 72.9549 | 67.7222 | 62.1957 | 56.2039 | 25.4559 | 8.1478 | 0.40183 | 111.3641 | 109.5141 | 107.2498 | 105.0875 | 102.6233 | 99.7692 | 96.0896 | 92.0345 | 87.6631 | 82.9018 | 58.309 | 35.3998 | 5.8712 | 90.761 | 88.5426 | 85.7916 | 83.0794 | 80.1447 | 76.7906 | 72.2467 | 67.3192 | 62.1447 | 56.5682 | 28.5386 | 13.2284 | 5.4498
|  | STAINES | CF |  |  |  | 94.7467 | 93.0712 | 91.2345 | 89.1692 | 87.6702 | 85.4263 | 83.0029 | 80.3794 | 77.8743 | 74.4978 | 55.2926 | 34.9447 | 18.9182 | 112.0937 | 110.5845 | 108.9284 | 107.06 | 105.5304 | 103.1845 | 100.2692 | 97.0141 | 93.8324 | 89.9702 | 66.7661 | 31.7947 | -26.2339 | 91.9386 | 90.4784 | 88.8743 | 87.0559 | 85.7202 | 83.6712 | 81.3661 | 78.8314 | 76.4212 | 73.2794 | 54.6202 | 36.4804 | 23.8886
MINETY GSP | STRATTON (2 X 60) | STRATTON (2 X 60) | MINIMUM HEADROOM | SU 17028 88748 | YES | 28.719 | -112.254 | -114.5948 | -78.8214 | -81.5642 | -83.8356 | -87.1561 | -91.504 | -96.6816 | -101.8183 | -105.0214 | -120.0061 | -130.2254 | -135.702 | -130.8499 | -132.401 | -97.5622 | -99.3428 | -100.8142 | -103.1408 | -106.1612 | -109.8693 | -113.6122 | -115.8132 | -126.8408 | -137.9377 | -164.3469 | -143.6367 | -145.8132 | -111.0224 | -113.5979 | -115.5601 | -118.503 | -122.4785 | -127.2652 | -132.0275 | -134.6448 | -150.1714 | -158.5591 | -161.6887
|  | STRATTON (2 X 60) | EE |  |  |  | -112.254 | -114.5948 | -78.8214 | -81.5642 | -83.8356 | -87.1561 | -91.504 | -96.6816 | -101.8183 | -105.0214 | -120.0061 | -129.1254 | -134.1816 | -130.8499 | -132.401 | -97.5622 | -99.3428 | -100.8142 | -103.1408 | -106.1612 | -109.8693 | -113.6122 | -115.8132 | -126.8408 | -136.6499 | -149.4938 | -143.6367 | -145.8132 | -111.0224 | -113.5979 | -115.5601 | -118.503 | -122.4785 | -127.2652 | -132.0275 | -134.6448 | -147.7275 | -155.1622 | -159.3163
|  | STRATTON (2 X 60) | HT |  |  |  | -111.5469 | -113.5642 | -77.4612 | -79.7622 | -82.8224 | -86.6601 | -90.7397 | -94.8152 | -99.3377 | -103.352 | -119.9969 | -130.2254 | -135.702 | -130.2397 | -131.4499 | -96.2214 | -97.5265 | -99.5326 | -102.0979 | -104.6285 | -107.0826 | -109.9101 | -112.2673 | -121.452 | -126.554 | -129.0959 | -142.8254 | -144.6683 | -109.502 | -111.5499 | -114.2877 | -117.7479 | -121.3203 | -124.8152 | -128.9418 | -132.6316 | -147.4418 | -156.0203 | -160.5071
|  | STRATTON (2 X 60) | HE |  |  |  | -111.5387 | -113.5112 | -77.3438 | -79.5101 | -81.7734 | -85.151 | -88.5693 | -92.3285 | -96.651 | -100.8214 | -118.6816 | -127.7591 | -131.1918 | -130.3724 | -131.7234 | -96.6428 | -98.0601 | -99.5316 | -101.9377 | -104.3071 | -106.9367 | -110.0979 | -113.1438 | -125.9724 | -135.6754 | -147.9846 | -142.8265 | -144.6397 | -109.4193 | -111.3632 | -113.3785 | -116.4275 | -119.4203 | -122.5897 | -126.9571 | -131.6622 | -150.1714 | -158.5591 | -161.6887
|  | STRATTON (2 X 60) | CF |  |  |  | -110.8826 | -112.4591 | -75.7336 | -77.3479 | -79.051 | -80.9622 | -82.9622 | -85.6081 | -87.8316 | -90.151 | -104.0448 | -115.8734 | -126.105 | -129.9897 | -131.1877 | -95.851 | -97.0356 | -98.2989 | -99.7499 | -101.4887 | -103.7734 | -105.8836 | -108.1061 | -122.0285 | -137.9377 | -164.3469 | -142.2479 | -143.6846 | -107.9683 | -109.4152 | -110.9275 | -112.6061 | -114.4285 | -116.8622 | -118.7479 | -120.7673 | -135.3091 | -147.6601 | -157.0887
MINETY GSP | STRATTON (2 X 90) | STRATTON (2 X 90) | MINIMUM HEADROOM | SU 17028 88748 | YES | 9.668 | 54.4758 | 53.2809 | 52.1228 | 50.7085 | 48.6758 | 45.486 | 41.7687 | 37.2054 | 32.7279 | 29.1207 | 14.6799 | 7.982 | 6.5044 | 55.3454 | 54.4199 | 53.4995 | 52.3689 | 51.0822 | 48.726 | 46.3148 | 43.3465 | 40.1209 | 37.4556 | 26.7199 | 11.275 | -21.8321 | 49.2567 | 47.8669 | 46.6383 | 45.0567 | 43.223 | 40.1995 | 36.6658 | 32.3281 | 28.0628 | 24.6393 | 10.8893 | 4.5791 | 3.2281
|  | STRATTON (2 X 90) | EE |  |  |  | 54.4758 | 53.2809 | 52.1228 | 50.7085 | 48.6758 | 45.486 | 41.7687 | 37.2054 | 32.7279 | 29.1207 | 18.0983 | 13.0034 | 13.5871 | 55.3454 | 54.4199 | 53.4995 | 52.3689 | 51.0822 | 48.726 | 46.3148 | 43.3465 | 40.1209 | 37.4556 | 26.7199 | 16.423 | 1.8546 | 49.2567 | 47.8669 | 46.6383 | 45.0567 | 43.223 | 40.1995 | 36.6658 | 32.3281 | 28.0628 | 24.6393 | 14.325 | 9.5005 | 10.0903
|  | STRATTON (2 X 90) | HT |  |  |  | 55.2156 | 54.3289 | 53.3769 | 52.3248 | 50.0789 | 47.5809 | 44.0595 | 40.5942 | 36.9238 | 33.8065 | 20.5503 | 12.9993 | 11.6207 | 55.9791 | 55.3618 | 54.6863 | 53.925 | 51.7322 | 49.4516 | 47.3169 | 45.1771 | 42.9852 | 41.3863 | 34.1067 | 30.5863 | 29.674 | 49.9781 | 48.8965 | 47.7556 | 46.5016 | 44.2209 | 41.523 | 38.1434 | 34.9638 | 31.4801 | 28.5607 | 16.3107 | 9.572 | 8.5107
|  | STRATTON (2 X 90) | HE |  |  |  | 55.0585 | 54.0891 | 53.0156 | 51.8197 | 50.6503 | 47.482 | 44.0514 | 39.8503 | 35.4748 | 31.135 | 14.6799 | 7.982 | 6.5044 | 55.7985 | 55.0465 | 54.1914 | 53.2322 | 52.274 | 49.8271 | 47.6077 | 44.9209 | 42.1414 | 39.4046 | 27.2536 | 16.2587 | 1.2138 | 49.9046 | 48.823 | 47.6669 | 46.3781 | 45.1944 | 42.1342 | 38.873 | 34.876 | 30.7056 | 26.5709 | 10.8893 | 4.5791 | 3.2281
|  | STRATTON (2 X 90) | CF |  |  |  | 55.7085 | 54.9177 | 54.2146 | 53.4718 | 52.6412 | 51.9014 | 50.6728 | 48.7799 | 46.2238 | 43.5901 | 29.1718 | 18.0871 | 10.3973 | 56.2505 | 55.5709 | 54.9465 | 54.2648 | 53.4852 | 52.7505 | 51.374 | 49.4536 | 47.2567 | 45.0618 | 30.9475 | 11.275 | -21.8321 | 50.5801 | 49.876 | 49.1934 | 48.4852 | 47.6812 | 46.8995 | 45.7107 | 43.526 | 40.8954 | 38.3791 | 24.5965 | 14.1199 | 6.9342
MINETY GSP | SWINDON BSP | SWINDON BSP | MINIMUM HEADROOM | SU 12447 87062 | YES | 22.762 | 33.427 | 31.6627 | 29.2719 | 26.4515 | 23.8454 | 18.6423 | 11.9801 | 4.0913 | -4.173 | -10.275 | -29.9832 | -43.373 | -48.9128 | 45.3099 | 43.8599 | 41.8884 | 39.6007 | 37.4037 | 33.2946 | 28.567 | 22.8997 | 16.9935 | 12.5956 | -4.4452 | -27.5687 | -77.3677 | 30.9792 | 29.3017 | 27.0762 | 24.4068 | 21.8966 | 16.8946 | 10.7262 | 3.4201 | -4.1473 | -9.5218 | -26.6299 | -37.7759 | -42.335
|  | SWINDON BSP | EE |  |  |  | 33.427 | 31.6627 | 29.2719 | 26.4515 | 23.8454 | 18.6423 | 11.9801 | 4.0913 | -4.173 | -10.275 | -29.9832 | -41.5363 | -46.6393 | 45.3099 | 43.8599 | 41.8884 | 39.6007 | 37.4037 | 33.2946 | 28.567 | 22.8997 | 16.9935 | 12.5956 | -4.4452 | -20.6565 | -44.7014 | 30.9792 | 29.3017 | 27.0762 | 24.4068 | 21.8966 | 16.8946 | 10.7262 | 3.4201 | -4.1473 | -9.5218 | -26.6299 | -36.3095 | -40.5861
|  | SWINDON BSP | HT |  |  |  | 34.6699 | 32.8943 | 31.1219 | 29.0525 | 25.3852 | 20.1311 | 13.9984 | 7.2341 | 0.98516 | -4.7536 | -28.6812 | -43.373 | -48.9128 | 46.5374 | 45.3864 | 44.3384 | 43.068 | 40.4241 | 36.9813 | 33.4976 | 29.3813 | 25.5109 | 22.0058 | 7.7456 | 0.013939 | -2.7769 | 32.215 | 30.5701 | 28.9884 | 27.119 | 23.7017 | 19.018 | 13.667 | 7.5435 | 1.8537 | -3.3136 | -24.9095 | -37.7759 | -42.335
|  | SWINDON BSP | HE |  |  |  | 34.4852 | 32.829 | 31.1433 | 29.1015 | 26.5097 | 21.9107 | 16.4821 | 10.125 | 3.0852 | -3.2546 | -26.1648 | -39.1852 | -43.8761 | 46.1446 | 44.769 | 43.4201 | 41.8017 | 39.7486 | 36.1884 | 32.4313 | 27.9374 | 22.8231 | 18.0354 | -2.6361 | -20.7544 | -44.3157 | 32.018 | 30.4466 | 28.9129 | 27.0354 | 24.6823 | 20.5037 | 15.6629 | 9.9946 | 3.6435 | -2.1503 | -23.0228 | -34.4157 | -38.1932
|  | SWINDON BSP | CF |  |  |  | 35.5964 | 34.6168 | 33.6739 | 32.8586 | 31.7505 | 30.4341 | 28.5566 | 25.7168 | 22.7954 | 18.9852 | -5.2791 | -21.9567 | -36.0271 | 46.8231 | 45.6854 | 44.615 | 43.6119 | 42.2741 | 40.5435 | 38.1476 | 35.015 | 31.8701 | 27.9956 | 2.9537 | -27.5687 | -77.3677 | 33.0731 | 32.0935 | 31.1956 | 30.4384 | 29.3915 | 28.1507 | 26.3507 | 23.7282 | 21.0782 | 17.518 | -4.5912 | -19.231 | -31.5024
BRAMLEY (ANDO-THAT) | THATCHAM BSP | THATCHAM BSP | MINIMUM HEADROOM | SU 52824 66435 | YES | 49.189 | 30.804 | 25.3372 | 17.325 | 126.4944 | 120.2842 | 113.2536 | 104.028 | 93.8474 | 83.7444 | 71.6189 | 17.977 | -7.6954 | -20.8148 | 69.9193 | 65.4576 | 58.7015 | 164.3791 | 159.7556 | 154.178 | 147.5678 | 140.3944 | 130.3005 | 119.7454 | 78.874 | 55.0311 | 8.7689 | 34.0815 | 29.0729 | 21.6566 | 128.3433 | 122.6607 | 115.726 | 107.0352 | 97.4607 | 85.3433 | 72.428 | 20.0219 | -6.0852 | -20.923
|  | THATCHAM BSP | EE |  |  |  | 30.804 | 25.3372 | 17.325 | 126.4944 | 120.2842 | 113.2536 | 104.028 | 93.8474 | 83.7444 | 75.1321 | 36.4546 | 6.2087 | -9.722 | 69.9193 | 65.4576 | 58.7015 | 164.3791 | 159.7556 | 154.178 | 147.5678 | 140.3944 | 132.9056 | 126.5974 | 97.0321 | 62.6536 | 28.974 | 34.0815 | 29.0729 | 21.6566 | 128.3433 | 122.6607 | 115.726 | 107.0352 | 97.4607 | 87.2413 | 78.2025 | 40.8648 | 13.5842 | -1.1281
|  | THATCHAM BSP | HT |  |  |  | 33.0907 | 28.4209 | 20.9842 | 130.4658 | 125.2515 | 118.4536 | 110.0566 | 100.6801 | 91.7015 | 81.9505 | 37.2587 | 4.1311 | -14.8342 | 72.3825 | 68.9536 | 63.0148 | 169.2433 | 166.0638 | 160.9536 | 155.6158 | 149.1403 | 142.7413 | 134.9852 | 102.5872 | 77.8658 | 64.0484 | 36.2489 | 31.9219 | 24.925 | 131.7668 | 127.178 | 120.6342 | 112.8627 | 104.1546 | 96.0138 | 86.5811 | 44.1168 | 11.7025 | -7.524
|  | THATCHAM BSP | HE |  |  |  | 32.8682 | 28.2138 | 20.5821 | 129.6811 | 124.1474 | 116.775 | 108.775 | 98.5954 | 84.4066 | 71.6189 | 17.977 | -7.6954 | -20.8148 | 71.8978 | 68.174 | 61.6821 | 167.1107 | 163.1372 | 156.9382 | 150.5811 | 142.4587 | 130.3005 | 119.7454 | 78.874 | 55.0311 | 17.6597 | 36.0213 | 31.6944 | 24.4791 | 130.8464 | 125.8536 | 118.6056 | 110.3331 | 99.9178 | 85.3433 | 72.428 | 20.0219 | -6.0852 | -20.923
|  | THATCHAM BSP | CF |  |  |  | 34.4897 | 31.0036 | 25.0382 | 136.4495 | 132.526 | 128.926 | 125.278 | 120.7046 | 116.376 | 111.728 | 76.5454 | 41.1536 | 15.8842 | 72.9142 | 69.8076 | 64.3831 | 171.5515 | 168.3352 | 165.2342 | 161.7178 | 157.2678 | 152.975 | 148.228 | 115.7862 | 72.224 | 8.7689 | 37.5468 | 34.3015 | 28.6893 | 137.3872 | 133.8964 | 130.6342 | 127.2954 | 123.1658 | 119.1933 | 114.8556 | 78.9617 | 44.3597 | 19.5433
MINETY GSP | TOOTHILL BSP | TOOTHILL BSP | MINIMUM HEADROOM | SU 13191 83945 | YES | 33.046 | 65.4118 | 25.3526 | 18.0965 | 98.5021 | 94.7429 | 90.148 | 83.9551 | 77.7439 | 71.4184 | 66.3327 | 52.5409 | 43.9521 | 40.7643 | 67.3006 | 21.9138 | 14.2536 | 93.7863 | 91.3812 | 88.4761 | 84.324 | 79.3271 | 74.5955 | 70.6352 | 58.4067 | 48.4934 | 26.3863 | 63.0536 | 17.5189 | 9.425 | 91.2842 | 87.9648 | 84.0108 | 78.524 | 72.4699 | 66.5414 | 61.8455 | 49.1322 | 40.9771 | 37.9179
|  | TOOTHILL BSP | EE |  |  |  | 65.4118 | 28.5301 | 20.9822 | 98.5021 | 94.7429 | 90.148 | 84.3562 | 77.7439 | 71.4184 | 66.3327 | 52.5409 | 46.2194 | 43.9113 | 67.3006 | 26.3873 | 18.5067 | 93.7863 | 91.3812 | 88.4761 | 84.324 | 79.3271 | 74.5955 | 70.6352 | 58.4067 | 48.4934 | 34.4373 | 63.0536 | 21.7659 | 13.2597 | 91.2842 | 87.9648 | 84.0108 | 78.7138 | 72.4699 | 66.5414 | 61.8455 | 49.2057 | 43.4475 | 41.1271
|  | TOOTHILL BSP | HT |  |  |  | 66.0863 | 25.3699 | 18.0965 | 99.9939 | 95.5786 | 90.1572 | 83.9551 | 78.4694 | 72.9164 | 68.5756 | 52.5674 | 43.9521 | 40.7643 | 67.9179 | 22.2352 | 14.7424 | 95.5404 | 92.6924 | 89.2475 | 85.0006 | 81.0628 | 77.2424 | 74.3485 | 63.9863 | 58.2587 | 55.5393 | 63.6546 | 17.5526 | 9.4352 | 92.9281 | 89.0271 | 84.2363 | 78.524 | 73.3944 | 68.221 | 64.1893 | 49.1322 | 40.9771 | 37.9179
|  | TOOTHILL BSP | HE |  |  |  | 66.0322 | 25.3526 | 18.1138 | 100.0776 | 96.8735 | 92.0194 | 86.6409 | 81.3786 | 75.9102 | 71.346 | 56.4949 | 49.6031 | 46.4572 | 67.7352 | 21.9138 | 14.2536 | 94.8883 | 92.9934 | 89.7628 | 85.9587 | 81.9771 | 77.9557 | 74.4965 | 61.1281 | 50.6608 | 36.3934 | 63.6026 | 17.5189 | 9.425 | 92.9679 | 90.2577 | 85.9842 | 81.1087 | 76.2699 | 71.2944 | 67.123 | 53.2281 | 46.8363 | 43.7975
|  | TOOTHILL BSP | CF |  |  |  | 66.5373 | 30.3842 | 23.7118 | 106.4082 | 103.9562 | 101.3449 | 98.0766 | 94.3 | 90.1623 | 87.0072 | 72.5511 | 64.0776 | 56.2388 | 68.0016 | 27.4679 | 20.0608 | 101.0108 | 99.4097 | 97.671 | 94.9822 | 91.7026 | 88.1016 | 85.1822 | 70.0995 | 53.7893 | 26.3863 | 64.0638 | 23.4944 | 15.9097 | 100.1138 | 98.072 | 95.8955 | 92.9791 | 89.4852 | 85.6597 | 82.8097 | 69.4934 | 61.8301 | 54.9108
IVER 132KV | UPTON BSP | UPTON BSP | MINIMUM HEADROOM | TQ 00838 79445 | YES | 7.694 | 39.428 | 38.628 | 34.6218 | 33.6392 | 32.3871 | 30.7433 | 28.8545 | 26.4065 | 24.4218 | 22.6708 | 15.5861 | 10.3331 | 9.1729 | 46.6882 | 45.9933 | 42.0892 | 41.3545 | 40.3096 | 39.0239 | 37.579 | 35.5933 | 34.0127 | 32.5698 | 25.6953 | 17.3627 | -4.2343 | 40.3943 | 39.5953 | 35.5504 | 34.7004 | 33.5004 | 31.9504 | 30.1453 | 27.7443 | 25.8392 | 24.1504 | 17.7647 | 13.0157 | 11.878
|  | UPTON BSP | EE |  |  |  | 39.428 | 38.628 | 34.6218 | 33.6392 | 32.3871 | 30.7433 | 28.8545 | 26.4065 | 24.4218 | 22.6708 | 15.5861 | 11.6933 | 11.2841 | 46.6882 | 45.9933 | 42.0892 | 41.3545 | 40.3096 | 39.0239 | 37.579 | 35.5933 | 34.0127 | 32.5698 | 25.6953 | 18.78 | 8.7678 | 40.3943 | 39.5953 | 35.5504 | 34.7004 | 33.5004 | 31.9504 | 30.1453 | 27.7443 | 25.8392 | 24.1504 | 17.7647 | 14.3933 | 13.8065
|  | UPTON BSP | HT |  |  |  | 39.9004 | 39.3188 | 35.5922 | 34.58 | 33.6106 | 32.2882 | 30.7422 | 28.7739 | 26.7606 | 24.9994 | 15.7667 | 10.3331 | 9.1729 | 47.2565 | 46.829 | 43.2922 | 42.6545 | 41.9769 | 41.1137 | 40.1861 | 38.8116 | 37.4239 | 36.282 | 30.4137 | 27.0647 | 25.9831 | 40.9718 | 40.3647 | 36.6433 | 35.7147 | 34.7841 | 33.5555 | 32.1341 | 30.2218 | 28.2678 | 26.6167 | 17.9678 | 13.0157 | 11.878
|  | UPTON BSP | HE |  |  |  | 39.8984 | 39.3851 | 35.6973 | 34.7555 | 33.8535 | 32.6167 | 31.3086 | 29.5841 | 27.8667 | 26.4188 | 19.1841 | 15.2739 | 14.0402 | 47.1494 | 46.6667 | 43.0208 | 42.2922 | 41.5096 | 40.5453 | 39.5994 | 38.1871 | 36.7963 | 35.6269 | 28.0647 | 20.9024 | 10.4912 | 40.9586 | 40.4208 | 36.729 | 35.8627 | 34.9953 | 33.8453 | 32.6657 | 30.9943 | 29.3484 | 28.0208 | 21.2637 | 17.7963 | 16.2616
|  | UPTON BSP | CF |  |  |  | 40.2473 | 39.9606 | 36.6147 | 36.1524 | 35.6361 | 34.8473 | 33.8484 | 33.2871 | 32.3973 | 31.4535 | 26.5239 | 20.7749 | 15.5269 | 47.328 | 46.9127 | 43.4443 | 42.9086 | 42.2902 | 41.4749 | 40.3841 | 39.5473 | 38.3851 | 37.1586 | 29.7382 | 17.3627 | -4.2343 | 41.279 | 40.93 | 37.5688 | 37.0953 | 36.5586 | 35.8035 | 34.8188 | 34.3351 | 33.4167 | 32.4637 | 27.8494 | 22.6769 | 18.1933
NURSLING GSP | VELMORE BSP | VELMORE BSP | MINIMUM HEADROOM | SU 42855 19215 | YES | 25.162 | 6.9142 | 111.1437 | 106.9437 | 102.406 | 98.2458 | 93.0968 | 86.7315 | 80.0142 | 73.0876 | 67.9284 | 43.8652 | 23.5988 | 12.4744 | 26.9068 | 126.6833 | 123.6996 | 120.5384 | 117.4251 | 113.6506 | 109.2251 | 104.4772 | 99.4486 | 95.7078 | 76.6129 | 52.1629 | -3.6167 | 10.9659 | 111.918 | 108.0894 | 103.9129 | 99.9272 | 95.0843 | 89.2445 | 83.0588 | 76.6731 | 72.02 | 50.9619 | 34.3639 | 25.1833
|  | VELMORE BSP | EE |  |  |  | 6.9142 | 111.1437 | 106.9437 | 102.406 | 98.2458 | 93.0968 | 86.7315 | 80.0142 | 73.0876 | 67.9284 | 44.1499 | 26.6488 | 13.556 | 26.9068 | 126.6833 | 123.6996 | 120.5384 | 117.4251 | 113.6506 | 109.2251 | 104.4772 | 99.4486 | 95.7078 | 76.6129 | 57.3935 | 28.2017 | 10.9659 | 111.918 | 108.0894 | 103.9129 | 99.9272 | 95.0843 | 89.2445 | 83.0588 | 76.6731 | 72.02 | 50.9619 | 36.7721 | 25.8017
|  | VELMORE BSP | HT |  |  |  | 8.2529 | 112.5417 | 108.7203 | 104.7631 | 101.0917 | 96.5366 | 91.4111 | 85.3978 | 79.455 | 73.7233 | 43.8652 | 23.5988 | 12.4744 | 28.319 | 128.4914 | 126.3374 | 124.2037 | 122.1486 | 119.4966 | 116.8904 | 113.3935 | 109.8261 | 106.4017 | 89.6139 | 80.1639 | 75.5445 | 12.3333 | 113.4231 | 110.0792 | 106.6853 | 103.3966 | 99.2863 | 94.8333 | 89.4047 | 83.9782 | 78.6792 | 51.6445 | 34.3639 | 25.1833
|  | VELMORE BSP | HE |  |  |  | 8.1356 | 112.5642 | 108.5897 | 104.6131 | 100.9519 | 96.4703 | 92.0723 | 86.6325 | 81.0805 | 75.8101 | 47.9978 | 28.607 | 20.2376 | 27.9292 | 127.9149 | 125.1537 | 122.5904 | 120.0639 | 116.921 | 113.9506 | 109.9914 | 105.721 | 101.5751 | 78.067 | 56.7843 | 29.4466 | 12.2068 | 113.4517 | 109.8904 | 106.4527 | 103.171 | 99.0904 | 95.2057 | 90.2037 | 84.9914 | 80.017 | 54.5955 | 38.3353 | 31.4568
|  | VELMORE BSP | CF |  |  |  | 9.3172 | 114.6958 | 112.0846 | 108.956 | 106.708 | 104.2356 | 102.2315 | 100.106 | 97.8917 | 95.2376 | 74.8366 | 55.4835 | 38.6448 | 28.5578 | 128.9557 | 126.9231 | 124.4925 | 122.6037 | 120.3731 | 117.9629 | 115.3353 | 112.5506 | 109.2557 | 86.0159 | 52.1629 | -3.6167 | 13.2996 | 115.3976 | 113.1323 | 110.3537 | 108.3598 | 106.1578 | 104.268 | 102.1639 | 99.9343 | 97.3037 | 78.72 | 61.217 | 46.6792
MANNINGTON GSP | WAREHAM | WAREHAM | MINIMUM HEADROOM | SY 91548 88451 | YES | 2.338 | -1.2959 | 12.18 | 11.4208 | 10.8024 | 9.1657 | 8.279 | 6.432 | 4.3922 | 2.7606 | 1.2361 | -7.022 | -12.8598 | -16.1414 | 0.005102 | 12.6612 | 11.9827 | 11.4459 | 10.6408 | 10.399 | 9.7602 | 8.502 | 7.4173 | 6.4551 | 1.2551 | -3.3776 | -14.9051 | -2.1571 | 10.902 | 9.8255 | 8.7673 | 7.2102 | 6.4745 | 4.8041 | 2.9306 | 1.4102 | 0.045918 | -7.1939 | -12.3765 | -15.202
|  | WAREHAM | EE |  |  |  | -1.2959 | 12.18 | 11.4208 | 10.8024 | 9.1657 | 8.279 | 6.432 | 4.3922 | 2.7606 | 1.2361 | -6.6914 | -11.7588 | -15.6139 | 0.005102 | 12.6612 | 11.9827 | 11.4459 | 10.6408 | 10.399 | 9.7602 | 8.502 | 7.4173 | 6.4551 | 1.2551 | -3.3776 | -10.0245 | -2.1571 | 10.902 | 9.8255 | 8.7673 | 7.2102 | 6.4745 | 4.8041 | 2.9306 | 1.4102 | 0.045918 | -6.9388 | -11.3735 | -14.7347
|  | WAREHAM | HT |  |  |  | -1.101 | 12.4422 | 11.7565 | 11.2331 | 10.4698 | 9.1147 | 7.3065 | 5.7239 | 4.1831 | 2.178 | -7.022 | -12.8598 | -16.1414 | 0.1898 | 12.9163 | 12.3337 | 11.9184 | 11.5918 | 11.2092 | 10.7714 | 10.3306 | 9.5929 | 8.4878 | 3.7398 | 1.0735 | -0.37449 | -1.9582 | 11.1531 | 10.402 | 9.5378 | 8.5378 | 7.3418 | 5.7173 | 4.3306 | 2.9673 | 1.1449 | -7.1939 | -12.3765 | -15.202
|  | WAREHAM | HE |  |  |  | -1.1061 | 12.4402 | 11.7667 | 11.2565 | 10.4371 | 9.1708 | 7.6412 | 6.3382 | 5.0922 | 3.5443 | -4.169 | -9.0741 | -11.3424 | 0.16224 | 12.8735 | 12.2694 | 11.8327 | 11.1551 | 10.7469 | 10.2888 | 9.7908 | 9.0418 | 8.0612 | 2.6327 | -2.0908 | -7.9633 | -1.951 | 11.1755 | 10.4755 | 9.698 | 8.4827 | 7.3592 | 5.9898 | 4.85 | 3.7531 | 2.352 | -4.5918 | -8.9143 | -10.8602
|  | WAREHAM | CF |  |  |  | -0.81531 | 12.7035 | 12.1443 | 11.8443 | 11.0831 | 10.431 | 9.8912 | 8.9841 | 8.1086 | 7.6137 | 3.0076 | -1.9027 | -6.7506 | 0.39592 | 13.0184 | 12.4541 | 12.1643 | 11.4653 | 10.9163 | 10.5949 | 10.198 | 9.7837 | 9.2602 | 4.5786 | -2.7071 | -14.9051 | -1.6755 | 11.4276 | 10.8255 | 10.4898 | 9.6102 | 8.7235 | 8.048 | 7.2347 | 6.4357 | 6.0173 | 1.801 | -2.599 | -6.8724
MELKSHAM GSP | WEST GRAFTON | WEST GRAFTON | MINIMUM HEADROOM | SU 24302 59215 | YES | 4.986 | 23.1218 | 22.0013 | 20.6656 | 19.1381 | 17.4656 | 16.4758 | 14.5228 | 12.2626 | 9.4901 | 7.8799 | -2.5436 | -8.1772 | -11.4344 | 32.2758 | 31.4401 | 30.5197 | 29.4575 | 28.2789 | 27.7748 | 26.4769 | 24.9156 | 23.1238 | 22.3034 | 15.4738 | 9.0564 | -6.464 | 24.6401 | 23.5411 | 22.2922 | 20.8585 | 19.2779 | 18.4901 | 16.6789 | 14.5493 | 12.0248 | 10.7452 | 2.1432 | -2.5446 | -5.1548
|  | WEST GRAFTON | EE |  |  |  | 23.1218 | 22.0013 | 20.6656 | 19.1381 | 17.4656 | 16.4758 | 14.5228 | 12.2626 | 9.4901 | 7.8799 | -2.5436 | -7.3272 | -10.5701 | 32.2758 | 31.4401 | 30.5197 | 29.4575 | 28.2789 | 27.7748 | 26.4769 | 24.9156 | 23.1238 | 22.3034 | 15.4738 | 10.0126 | 2.0116 | 24.6401 | 23.5411 | 22.2922 | 20.8585 | 19.2779 | 18.4901 | 16.6789 | 14.5493 | 12.0248 | 10.7452 | 2.1432 | -1.7517 | -4.4384
|  | WEST GRAFTON | HT |  |  |  | 23.5095 | 22.4126 | 21.2983 | 20.0626 | 18.6993 | 17.2105 | 15.2269 | 13.7707 | 11.5656 | 9.2707 | -2.4793 | -8.1772 | -11.4344 | 32.7585 | 32.1085 | 31.4911 | 30.7544 | 30.0248 | 29.1534 | 28.0544 | 27.484 | 26.2636 | 24.983 | 18.8922 | 16.1626 | 14.7197 | 25.1309 | 24.1309 | 23.1442 | 21.9952 | 20.7789 | 19.4085 | 17.6054 | 16.4595 | 14.4738 | 12.4105 | 2.2809 | -2.5446 | -5.1548
|  | WEST GRAFTON | HE |  |  |  | 23.5116 | 22.5616 | 21.5105 | 20.2564 | 19.0013 | 17.6554 | 16.0299 | 14.5197 | 12.5973 | 10.532 | -0.54151 | -5.317 | -7.4752 | 32.6871 | 32.034 | 31.3616 | 30.5473 | 29.7616 | 28.8646 | 27.7799 | 26.8371 | 25.6952 | 24.3116 | 16.7595 | 11.1769 | 3.6044 | 25.1248 | 24.2422 | 23.3136 | 22.1636 | 21.0452 | 19.7993 | 18.2911 | 16.9728 | 15.382 | 13.5177 | 4.134 | 0.20849 | -1.5436
|  | WEST GRAFTON | CF |  |  |  | 23.7534 | 23.136 | 22.4228 | 21.5646 | 20.6575 | 20.0524 | 19.432 | 18.5769 | 17.4626 | 16.9718 | 7.0789 | 1.136 | -3.6548 | 32.8003 | 32.3269 | 31.7922 | 31.1605 | 30.4677 | 29.8962 | 29.1922 | 28.286 | 27.2411 | 26.7758 | 18.4269 | 9.0564 | -6.464 | 25.3534 | 24.784 | 24.1442 | 23.3605 | 22.5299 | 21.9493 | 21.3207 | 20.4524 | 19.3881 | 19.0881 | 10.4748 | 5.4432 | 1.4942
NURSLING GSP | WINCHESTER | WINCHESTER | MINIMUM HEADROOM | SU 44965 26671 | YES | 23.081 | 45.4041 | 41.4817 | 38.8562 | 32.546 | 142.6182 | 134.4325 | 129.2509 | 123.4213 | 110.4866 | 100.4611 | 70.3948 | 43.0693 | 16.6754 | 58.4023 | 55.2615 | 53.5799 | 46.4411 | 152.8299 | 144.387 | 139.836 | 134.6033 | 120.1972 | 109.4778 | 82.3574 | 55.135 | 17.3125 | 46.7421 | 42.9584 | 40.4972 | 33.8136 | 141.2248 | 132.087 | 126.7033 | 120.6023 | 105.585 | 94.2033 | 62.7513 | 32.5799 | 1.3329
|  | WINCHESTER | EE |  |  |  | 45.4041 | 41.4817 | 38.8562 | 33.0787 | 143.2682 | 137.605 | 132.3172 | 128.0795 | 121.3693 | 116.8999 | 92.6478 | 57.4346 | 41.3938 | 58.4023 | 55.2615 | 53.5799 | 48.4676 | 155.2187 | 150.4125 | 146.5707 | 143.985 | 138.5993 | 134.935 | 116.7584 | 77.8227 | 54.0452 | 46.7421 | 42.9584 | 40.4972 | 34.9289 | 142.6268 | 136.8615 | 131.5942 | 127.6707 | 120.734 | 116.2513 | 91.8431 | 51.8891 | 34.7146
|  | WINCHESTER | HT |  |  |  | 46.3929 | 42.6715 | 40.2215 | 33.4256 | 144.1427 | 136.9019 | 131.3917 | 125.0499 | 120.7254 | 113.805 | 84.0784 | 48.8601 | 25.0887 | 58.9982 | 55.9513 | 54.2309 | 48.136 | 155.5646 | 148.5758 | 144.2482 | 139.0952 | 136.1931 | 130.1584 | 107.5942 | 74.3238 | 50.4982 | 47.7237 | 44.1574 | 41.7656 | 34.9584 | 143.187 | 135.2727 | 129.6136 | 123.0217 | 118.9197 | 111.5778 | 81.1646 | 41.7472 | 14.8187
|  | WINCHESTER | HE |  |  |  | 46.3184 | 42.7725 | 40.0338 | 32.546 | 142.6182 | 134.4325 | 129.2509 | 123.4213 | 110.4866 | 100.4611 | 70.3948 | 43.0693 | 16.6754 | 58.8717 | 55.8931 | 53.5921 | 46.4411 | 152.8299 | 144.387 | 139.836 | 134.6033 | 120.1972 | 109.4778 | 82.3574 | 55.135 | 17.3125 | 47.6421 | 44.2309 | 41.5023 | 33.8136 | 141.2248 | 132.087 | 126.7033 | 120.6023 | 105.585 | 94.2033 | 62.7513 | 32.5799 | 1.3329
|  | WINCHESTER | CF |  |  |  | 47.2868 | 43.947 | 42.5256 | 37.2031 | 148.2142 | 144.4968 | 142.2305 | 140.1203 | 137.5438 | 134.8305 | 116.7264 | 95.4958 | 75.9856 | 59.6554 | 56.438 | 55.3595 | 50.3982 | 157.3513 | 154.1431 | 152.0952 | 150.238 | 148.0717 | 145.5717 | 128.3962 | 103.1748 | 66.1707 | 48.5431 | 45.3227 | 44.0074 | 38.8554 | 147.2023 | 143.5227 | 141.2197 | 139.1095 | 136.5176 | 133.6829 | 114.9217 | 92.6054 | 72.1044
COWLEY GSP | WITNEY BSP | WITNEY BSP | MINIMUM HEADROOM | SP 35605 08274 | YES | 27.379 | 24.768 | 21.9751 | 19.7465 | 131.8524 | 128.5871 | 124.8657 | 120.4606 | 116.0167 | 110.8728 | 107.3636 | 91.8361 | 79.1861 | 71.4361 | 44.9876 | 43.0395 | 41.4916 | 149.6538 | 147.3151 | 144.7324 | 141.8661 | 138.8987 | 135.3467 | 132.9304 | 121.1559 | 106.1661 | 69.9375 | 28.5386 | 25.96 | 23.8222 | 133.3028 | 130.2548 | 126.8722 | 122.8997 | 118.8844 | 114.1916 | 111.0732 | 97.5426 | 86.6844 | 80.4477
|  | WITNEY BSP | EE |  |  |  | 24.768 | 21.9751 | 19.7465 | 131.8524 | 128.5871 | 124.8657 | 120.4606 | 116.0167 | 110.8728 | 107.3636 | 92.1881 | 81.4473 | 73.1024 | 44.9876 | 43.0395 | 41.4916 | 149.6538 | 147.3151 | 144.7324 | 141.8661 | 138.8987 | 135.3467 | 132.9304 | 121.1559 | 108.7538 | 89.7222 | 28.5386 | 25.96 | 23.8222 | 133.3028 | 130.2548 | 126.8722 | 122.8997 | 118.8844 | 114.1916 | 111.0732 | 97.6528 | 88.6824 | 81.8069
|  | WITNEY BSP | HT |  |  |  | 25.6108 | 23.0597 | 20.972 | 133.0687 | 130.18 | 127.1769 | 123.1565 | 118.6534 | 114.4779 | 110.1973 | 91.8361 | 79.1861 | 71.4361 | 45.8794 | 44.3375 | 43.162 | 151.6977 | 150.0589 | 148.4773 | 146.412 | 143.8538 | 141.5253 | 138.9538 | 128.9416 | 122.9426 | 119.5548 | 29.5396 | 27.2538 | 25.3263 | 134.8804 | 132.2416 | 129.5936 | 126.0681 | 121.9804 | 118.1957 | 114.2048 | 97.5426 | 86.6844 | 80.4477
|  | WITNEY BSP | HE |  |  |  | 25.6588 | 23.2046 | 21.2383 | 133.5004 | 130.8524 | 128.13 | 124.831 | 120.984 | 117.3075 | 113.5483 | 97.1922 | 86.2351 | 80.6555 | 45.706 | 44.0283 | 42.6753 | 151.0508 | 149.2702 | 147.514 | 145.4487 | 142.7926 | 140.2426 | 137.3987 | 123.9334 | 111.1763 | 93.1732 | 29.558 | 27.3661 | 25.5375 | 135.2406 | 132.81 | 130.4069 | 127.4885 | 123.9477 | 120.6161 | 117.0885 | 102.312 | 93.1712 | 88.7263
|  | WITNEY BSP | CF |  |  |  | 26.3445 | 24.4026 | 22.972 | 135.9514 | 134.2044 | 132.2197 | 130.73 | 129.13 | 127.0544 | 125.0942 | 111.7024 | 100.4575 | 89.6555 | 46.0764 | 44.5661 | 43.4273 | 152.0997 | 150.6997 | 149.0314 | 147.5365 | 145.8548 | 143.7406 | 141.5538 | 126.86 | 106.1661 | 69.9375 | 30.2008 | 28.464 | 27.1334 | 137.4824 | 135.8977 | 134.0844 | 132.7538 | 131.2681 | 129.2702 | 127.4059 | 115.3712 | 105.2548 | 95.7987
BRAMLEY (FLEE) | WOKINGHAM BSP | WOKINGHAM BSP | MINIMUM HEADROOM | SU 79589 67665 | YES | 18.694 | 76.6721 | 75.4853 | 74.0792 | 72.8261 | 71.6159 | 70.0598 | 67.4221 | 64.4547 | 61.5476 | 59.1567 | 47.6333 | 39.7149 | 35.1302 | 81.0886 | 80.2151 | 79.1855 | 78.3263 | 77.4896 | 76.2978 | 74.2447 | 71.8539 | 69.5865 | 67.7549 | 59.7294 | 51.7253 | 31.0845 | 76.0202 | 74.9876 | 73.709 | 72.5957 | 71.5131 | 70.0345 | 67.46 | 64.5284 | 61.711 | 59.4774 | 49.06 | 41.4396 | 37.161
|  | WOKINGHAM BSP | EE |  |  |  | 76.6721 | 75.4853 | 74.0792 | 72.8261 | 71.6159 | 70.0598 | 67.4221 | 64.4547 | 61.5476 | 59.1567 | 49.0251 | 42.4557 | 37.0078 | 81.0886 | 80.2151 | 79.1855 | 78.3263 | 77.4896 | 76.2978 | 74.2447 | 71.8539 | 69.5865 | 67.7549 | 59.7294 | 51.7253 | 39.66 | 76.0202 | 74.9876 | 73.709 | 72.5957 | 71.5131 | 70.0345 | 67.46 | 64.5284 | 61.711 | 59.4774 | 50.3365 | 44.1039 | 39.0529
|  | WOKINGHAM BSP | HT |  |  |  | 77.1241 | 76.0516 | 74.8486 | 73.5221 | 72.1251 | 70.9333 | 68.3445 | 65.9527 | 63.2261 | 60.4067 | 47.6333 | 39.7149 | 35.1302 | 81.6233 | 81.0131 | 80.3294 | 79.56 | 78.7039 | 78.0774 | 76.3876 | 74.8498 | 73.0692 | 71.1814 | 63.4549 | 58.9508 | 56.3549 | 76.4172 | 75.4855 | 74.4396 | 73.2937 | 72.0467 | 71.0141 | 68.5559 | 66.2733 | 63.7284 | 61.0794 | 49.06 | 41.4396 | 37.161
|  | WOKINGHAM BSP | HE |  |  |  | 77.1353 | 76.1833 | 75.0435 | 73.8006 | 72.5486 | 71.4772 | 69.4516 | 67.5996 | 65.4363 | 63.1955 | 52.5812 | 45.8353 | 42.2098 | 81.508 | 80.8498 | 80.0549 | 79.1825 | 78.2682 | 77.5161 | 75.9365 | 74.5029 | 72.8774 | 71.1488 | 62.1763 | 53.9029 | 42.5243 | 76.4284 | 75.5916 | 74.5978 | 73.5172 | 72.4059 | 71.457 | 69.5559 | 67.7957 | 65.8314 | 63.7437 | 53.8896 | 47.4253 | 43.9967
|  | WOKINGHAM BSP | CF |  |  |  | 77.7027 | 77.0914 | 76.317 | 75.4853 | 74.6976 | 73.8965 | 72.9078 | 72.0435 | 71.2088 | 70.1006 | 61.6955 | 55.3925 | 49.4231 | 81.7794 | 81.2335 | 80.5641 | 79.8508 | 79.1345 | 78.309 | 77.1212 | 76.0202 | 74.9253 | 73.5641 | 64.4294 | 52.3947 | 31.0845 | 76.9212 | 76.4008 | 75.7447 | 75.0447 | 74.3763 | 73.6161 | 72.5886 | 71.7304 | 70.9141 | 69.8049 | 62.0682 | 56.5896 | 51.2518
LOVEDEAN GSP | WYMERING BSP | WYMERING BSP | MINIMUM HEADROOM | SU 64948 05441 | YES | 78.269 | 126.0154 | 125.1134 | 124.4144 | 123.1552 | 121.5399 | 118.7317 | 116.5368 | 113.9419 | 111.4583 | 109.3899 | 97.946 | 93.1287 | 92.3511 | 122.1399 | 121.5205 | 120.8695 | 119.7256 | 118.4338 | 116.1174 | 114.544 | 112.6644 | 110.8654 | 109.3899 | 100.4756 | 96.8256 | 90.0113 | 122.7052 | 121.9644 | 121.1603 | 119.7256 | 118.1062 | 115.3848 | 113.2991 | 110.8276 | 108.4654 | 106.5011 | 95.5021 | 90.9021 | 90.1725
|  | WYMERING BSP | EE |  |  |  | 126.0154 | 125.1134 | 124.4144 | 123.1552 | 121.5399 | 118.7317 | 116.5368 | 113.9419 | 111.4583 | 109.3899 | 101.9195 | 100.1542 | 100.0368 | 122.1399 | 121.5205 | 120.8695 | 119.7256 | 118.4338 | 116.1174 | 114.544 | 112.6644 | 110.8654 | 109.3899 | 103.7144 | 102.4919 | 98.0481 | 122.7052 | 121.9644 | 121.1603 | 119.7256 | 118.1062 | 115.3848 | 113.2991 | 110.8276 | 108.4654 | 106.5011 | 99.444 | 97.845 | 97.7256
|  | WYMERING BSP | HT |  |  |  | 126.643 | 126.0389 | 125.3491 | 124.5491 | 123.4899 | 121.9736 | 120.4644 | 118.646 | 116.7328 | 114.6879 | 105.4828 | 101.4613 | 100.7736 | 122.6664 | 122.2919 | 121.8501 | 121.3379 | 120.7072 | 118.9481 | 117.9011 | 116.6215 | 115.2634 | 113.6736 | 106.7613 | 104.0246 | 103.3828 | 123.2419 | 122.7011 | 122.1052 | 121.4195 | 120.5481 | 118.8001 | 117.3542 | 115.6236 | 113.794 | 111.7858 | 102.9409 | 99.2838 | 98.6021
|  | WYMERING BSP | HE |  |  |  | 126.5236 | 125.8848 | 125.1501 | 124.1174 | 122.8419 | 120.3042 | 118.3195 | 115.8899 | 113.3083 | 110.6185 | 97.946 | 93.1287 | 92.3511 | 122.4828 | 121.9807 | 121.3797 | 120.6032 | 119.4348 | 117.3215 | 115.8899 | 114.1134 | 112.2215 | 110.243 | 100.4756 | 96.8256 | 95.9307 | 123.1011 | 122.4889 | 121.7981 | 120.8297 | 119.3685 | 116.9021 | 115.0103 | 112.6889 | 110.2185 | 107.6419 | 95.5021 | 90.9021 | 90.1725
|  | WYMERING BSP | CF |  |  |  | 126.9348 | 126.5328 | 126.0256 | 125.5746 | 124.9848 | 123.447 | 122.746 | 121.6858 | 120.3307 | 118.8389 | 110.3072 | 101.8603 | 97.6236 | 122.8368 | 122.4552 | 122.046 | 121.6389 | 121.1021 | 119.6266 | 119.2021 | 118.2756 | 117.2134 | 116.0868 | 109.6685 | 102.2664 | 90.0113 | 123.5389 | 123.1613 | 122.7399 | 122.3021 | 121.7287 | 120.2195 | 119.4817 | 118.2695 | 116.9236 | 115.496 | 107.3011 | 99.2532 | 95.2705
COWLEY GSP | YARNTON BSP | YARNTON BSP | MINIMUM HEADROOM | SP 35605 08274 | YES | 93.872 | 16.66 | 13.0376 | 121.6794 | 119.2151 | 115.8784 | 89.7186 | 84.887 | 79.8329 | 73.5563 | 68.4125 | 46.3114 | 33.0278 | 25.8196 | 35.0835 | 32.2835 | 136.4018 | 134.5243 | 132.012 | 106.9625 | 103.8084 | 100.4972 | 96.2063 | 92.94 | 77.6421 | 62.5461 | 27.4798 | 14.8876 | 11.4488 | 116.8182 | 114.4365 | 111.2835 | 85.4125 | 81.0349 | 76.4645 | 70.7441 | 66.3217 | 47.9574 | 36.9757 | 31.0451
|  | YARNTON BSP | EE |  |  |  | 16.66 | 13.0376 | 121.6794 | 119.2151 | 115.8784 | 89.7186 | 84.887 | 79.8329 | 73.5563 | 68.4125 | 46.3114 | 34.1084 | 26.6217 | 35.0835 | 32.2835 | 136.4018 | 134.5243 | 132.012 | 106.9625 | 103.8084 | 100.4972 | 96.2063 | 92.94 | 77.6421 | 65.1808 | 47.5278 | 14.8876 | 11.4488 | 116.8182 | 114.4365 | 111.2835 | 85.4125 | 81.0349 | 76.4645 | 70.7441 | 66.3217 | 47.9574 | 37.9237 | 31.6319
|  | YARNTON BSP | HT |  |  |  | 17.7518 | 14.4651 | 123.6171 | 121.3876 | 118.5263 | 93.3961 | 87.9053 | 82.2359 | 76.94 | 71.4461 | 47.3023 | 33.0278 | 25.8196 | 36.2927 | 34.0896 | 139.0212 | 137.5814 | 135.6518 | 111.8563 | 108.8645 | 105.5553 | 102.4676 | 99.2288 | 86.1257 | 79.5339 | 76.389 | 16.2927 | 13.3008 | 119.361 | 117.2222 | 114.4876 | 89.7533 | 84.9686 | 79.8727 | 75.141 | 70.2461 | 49.2584 | 36.9757 | 31.0451
|  | YARNTON BSP | HE |  |  |  | 17.61 | 14.3171 | 123.4202 | 121.158 | 118.6498 | 93.5737 | 89.0227 | 83.7696 | 78.5288 | 73.1319 | 48.6441 | 35.2329 | 29.9339 | 36.0018 | 33.5804 | 138.2773 | 136.5692 | 134.6131 | 110.4961 | 107.5247 | 103.9543 | 100.4063 | 96.7502 | 78.4961 | 64.4829 | 47.6329 | 16.1284 | 13.1263 | 119.1518 | 116.9804 | 114.5294 | 89.8023 | 85.7533 | 80.9461 | 76.2431 | 71.4574 | 49.2778 | 38.6757 | 34.4033
|  | YARNTON BSP | CF |  |  |  | 18.4763 | 15.758 | 125.5182 | 124.1171 | 122.6937 | 99.0706 | 97.6931 | 95.6319 | 93.1492 | 90.2145 | 71.6339 | 53.7512 | 41.4819 | 36.5202 | 34.3253 | 139.3335 | 138.0671 | 136.6947 | 113.1033 | 111.5421 | 109.3461 | 106.8227 | 104.04 | 86.5553 | 62.5461 | 27.4798 | 16.9314 | 14.4631 | 121.059 | 119.6763 | 118.2335 | 94.6155 | 93.2839 | 91.2094 | 88.7808 | 86.0614 | 69.5451 | 54.4298 | 44.2706
AXMINSTER | YEOVIL BSP | YEOVIL BSP | MINIMUM HEADROOM | ST 57586 16894 | YES | 48.682 | 27.2072 | 21.767 | 18.3477 | 15.4568 | 11.2926 | 83.9282 | 79.5669 | 73.6302 | 67.9424 | 63.7771 | 43.0343 | 27.821 | 19.1128 | 43.8286 | 39.8313 | 37.5997 | 35.7558 | 33.0568 | 103.0302 | 100.3945 | 96.7057 | 92.9261 | 90.1506 | 74.7037 | 55.3435 | 10.5465 | 25.9348 | 20.7987 | 17.7048 | 15.1395 | 11.3854 | 81.4526 | 77.6057 | 72.3567 | 67.3884 | 63.6557 | 44.9618 | 31.7057 | 24.219
|  | YEOVIL BSP | EE |  |  |  | 27.2072 | 21.767 | 18.3477 | 15.4568 | 11.2926 | 83.9282 | 79.5669 | 73.6302 | 67.9424 | 63.7771 | 43.0343 | 29.6159 | 20.7496 | 43.8286 | 39.8313 | 37.5997 | 35.7558 | 33.0568 | 103.0302 | 100.3945 | 96.7057 | 92.9261 | 90.1506 | 74.7037 | 58.7618 | 36.0067 | 25.9348 | 20.7987 | 17.7048 | 15.1395 | 11.3854 | 81.4526 | 77.6057 | 72.3567 | 67.3884 | 63.6557 | 44.9618 | 33.2884 | 25.5935
|  | YEOVIL BSP | HT |  |  |  | 28.3297 | 23.2405 | 20.3711 | 17.4701 | 13.7997 | 87.07 | 82.7322 | 77.6394 | 72.3169 | 68.0618 | 43.6108 | 27.821 | 19.1128 | 44.5378 | 40.9926 | 39.7589 | 38.2089 | 36.215 | 107.0394 | 104.9292 | 102.222 | 99.3751 | 97.3016 | 84.8077 | 77.1873 | 73.1465 | 27.0592 | 22.2803 | 19.7395 | 17.1681 | 13.9181 | 84.6292 | 80.8159 | 76.2271 | 71.422 | 67.6996 | 45.6547 | 31.7057 | 24.219
|  | YEOVIL BSP | HE |  |  |  | 28.2552 | 23.2977 | 20.4844 | 17.6589 | 14.113 | 87.47 | 83.6047 | 78.9639 | 74.1006 | 70.3169 | 47.7873 | 34.2659 | 28.6588 | 44.4307 | 40.8191 | 39.1007 | 37.3058 | 35.0375 | 105.519 | 103.1292 | 100.0986 | 96.8649 | 94.3516 | 76.9659 | 60.5608 | 39.1231 | 27.0246 | 22.3242 | 19.8191 | 17.3262 | 14.1824 | 84.968 | 81.5843 | 77.3884 | 72.9884 | 69.6873 | 49.3659 | 37.5037 | 32.7261
|  | YEOVIL BSP | CF |  |  |  | 29.2633 | 25.1262 | 23.3272 | 21.466 | 19.0334 | 93.3741 | 90.6945 | 88.5302 | 85.57 | 82.4404 | 67.9496 | 53.0261 | 39.7128 | 44.9092 | 41.6191 | 40.4344 | 39.0313 | 37.2048 | 107.9771 | 105.668 | 103.619 | 100.9333 | 98.0894 | 81.5496 | 55.3435 | 10.5465 | 27.8848 | 23.916 | 22.3262 | 20.6956 | 18.5681 | 90.2598 | 87.919 | 86.0537 | 83.4098 | 80.6292 | 67.4598 | 54.0792 | 42.3384

## BSP Headroom Gen
Grid Supply Point | Bulk Supply Point |  | Scenario | Grid Reference | Upstream Constraint (YES / NO) | Outstanding Contracted Generation (MVA) | Generation Headroom Winter (MVA) | [12 empty] | Generation Headroom Summer (MVA) | [12 empty] | Generation Headroom Spring/Autumn (MVA)
[7 empty] | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2051
BRAMLEY (FLEE) | ALDERSHOT BSP | ALDERSHOT BSP | MINIMUM HEADROOM | SU 85922 48779 | YES | 1.7905 | 131.6295 | 129.4516 | 127.2558 | 124.9126 | 122.3968 | 115.6432 | 110.0474 | 105.1653 | 100.5989 | 96.3758 | 78.7137 | 63.6674 | 50.3421 | 103.0663 | 97.7379 | 91.5326 | 83.6916 | 75.5232 | 67.9632 | 61.8368 | 56.5011 | 51.4989 | 46.88 | 27.5411 | 10.9653 | -3.8653 | 110.06 | 105.7221 | 99.5474 | 91.6758 | 83.5021 | 75.9305 | 69.7989 | 64.4547 | 59.4453 | 54.8126 | 35.4116 | 18.76 | 3.8958
|  | ALDERSHOT BSP | EE |  |  |  | 132.4726 | 130.7716 | 128.9674 | 127.0484 | 125.0505 | 121.7663 | 116.6947 | 112.4537 | 108.3947 | 104.7116 | 90.2663 | 78.7232 | 68.6989 | 104.7979 | 100.3832 | 95.1526 | 88.46 | 81.2884 | 74.6337 | 69.0411 | 64.4116 | 59.9832 | 55.9642 | 40.1821 | 27.4811 | 16.2726 | 110.9232 | 108.3063 | 103.2284 | 96.4432 | 89.2653 | 82.6042 | 77.0053 | 72.36 | 67.9168 | 63.8874 | 48.0095 | 35.2105 | 23.9663
|  | ALDERSHOT BSP | HT |  |  |  | 131.6295 | 129.4516 | 127.2558 | 124.9126 | 122.3968 | 115.6432 | 110.0474 | 105.1653 | 100.5989 | 96.3758 | 78.7137 | 63.6674 | 50.3421 | 103.0663 | 97.7379 | 91.5326 | 83.6916 | 75.5232 | 67.9632 | 61.8368 | 56.5011 | 51.4989 | 46.88 | 27.5411 | 10.9653 | -3.8653 | 110.06 | 105.7221 | 99.5474 | 91.6758 | 83.5021 | 75.9305 | 69.7989 | 64.4547 | 59.4453 | 54.8126 | 35.4116 | 18.76 | 3.8958
|  | ALDERSHOT BSP | HE |  |  |  | 133.6189 | 132.46 | 131.1747 | 129.7568 | 128.2347 | 126.5916 | 124.9116 | 121.6189 | 118.4642 | 115.6726 | 105.5779 | 98.1779 | 91.8295 | 107.1168 | 103.8337 | 99.6632 | 94.4189 | 88.3358 | 82.64 | 78.0379 | 74.3653 | 70.9105 | 67.8484 | 56.7495 | 48.5137 | 41.3484 | 112.0705 | 110.8874 | 107.6368 | 102.4484 | 96.3179 | 90.6137 | 86.0105 | 82.3295 | 78.8684 | 75.7968 | 64.6621 | 56.3968 | 49.2042
|  | ALDERSHOT BSP | CF |  |  |  | 134.2779 | 133.6168 | 132.9347 | 132.2232 | 131.4916 | 130.72 | 129.9368 | 129.1653 | 128.4042 | 127.6432 | 124.2316 | 121.3589 | 116.8684 | 108.2495 | 106.7347 | 104.5221 | 102.0726 | 99.6579 | 97.4284 | 95.2442 | 93.1968 | 91.1242 | 89.0695 | 80.3347 | 74.2674 | 69.18 | 112.7295 | 112.0684 | 111.3737 | 109.9863 | 107.6463 | 105.4779 | 103.2874 | 101.1968 | 99.0979 | 97.0421 | 88.2926 | 82.2063 | 77.1032
BRAMLEY (FLEE) | ALTON | ALTON | MINIMUM HEADROOM | SU 72730 39772 | YES | 22.3653 | 80.0042 | 40.7916 | 27.7884 | 18.6453 | -3.7326 | -8.6116 | -26.6116 | -43.9526 | -75.0674 | -78.1558 | -107.0579 | -129.5368 | -148.3284 | 31.1126 | -14.6926 | -30.5968 | -40.5589 | -66.5147 | -71.7537 | -91.5453 | -113.3653 | -149.6379 | -152.9589 | -182.9126 | -207.1368 | -227.9663 | 35.7179 | -10.1189 | -26.0474 | -36.0179 | -61.9326 | -67.2358 | -87.0095 | -108.8347 | -145.0979 | -148.4726 | -179.2758 | -204.2053 | -225.3032
|  | ALTON | EE |  |  |  | 105.2337 | 103.0832 | 57.1105 | 18.6453 | -3.7326 | -8.6116 | -13.4389 | -33.4842 | -65.7768 | -70.0537 | -91.4663 | -112.2137 | -127.3958 | 71.9105 | 66.3811 | 4.3358 | -40.5589 | -66.5147 | -71.7537 | -76.9 | -99.9547 | -137.42 | -141.9368 | -164.5495 | -187.2537 | -204.0579 | 77.7105 | 71.9579 | 8.8042 | -36.0179 | -61.9326 | -67.2358 | -72.4821 | -95.6084 | -133.1263 | -137.7726 | -161.2505 | -185.0916 | -202.1937
|  | ALTON | HT |  |  |  | 80.0042 | 40.7916 | 35.5389 | 30.2716 | 24.9811 | 19.0011 | -26.6116 | -34.0053 | -38.8947 | -77.8916 | -107.0579 | -129.5368 | -148.3284 | 31.1126 | -14.6926 | -20.4611 | -26.22 | -31.9905 | -38.4558 | -91.5453 | -99.7063 | -104.9474 | -150.3337 | -182.9126 | -207.1368 | -227.9663 | 35.7179 | -10.1189 | -15.8853 | -21.6442 | -27.4147 | -33.9421 | -87.0095 | -95.2421 | -100.5716 | -145.9737 | -179.2758 | -204.2053 | -225.3032
|  | ALTON | HE |  |  |  | 84.0295 | 80.4968 | 27.7884 | 24.5337 | 21.2558 | 17.3884 | -25.0389 | -43.9526 | -75.0674 | -78.1558 | -93.5537 | -108.4158 | -119.5232 | 35.64 | 31.1916 | -30.5968 | -34.1684 | -37.7453 | -41.9074 | -91.4653 | -113.3653 | -149.6379 | -152.9589 | -169.7758 | -187.5526 | -199.9358 | 40.2895 | 35.8042 | -26.0474 | -29.6179 | -33.1895 | -37.4021 | -86.9189 | -108.8347 | -145.0979 | -148.4726 | -165.64 | -183.9211 | -196.5442
|  | ALTON | CF |  |  |  | 86.0358 | 84.2032 | 82.7105 | 47.2211 | 45.4568 | 43.3632 | 41.0011 | 38.6568 | 36.5947 | 34.6105 | 24.5316 | 16.2442 | 9.0958 | 37.9884 | 35.5421 | 33.8421 | -7.9337 | -9.8779 | -12.1611 | -14.7589 | -17.3379 | -19.5905 | -21.7589 | -32.8095 | -42 | -49.9611 | 42.6642 | 40.2105 | 38.4937 | -3.4263 | -5.3663 | -7.6726 | -10.2926 | -12.8947 | -15.1695 | -17.3526 | -28.5147 | -37.8463 | -45.9716
MELKSHAM GSP | AMESBURY | AMESBURY | MINIMUM HEADROOM | SU 15842 42724 | YES | 42.9242 | 74.3811 | 42.4737 | -0.71474 | -1.8568 | -42.0811 | -43.9495 | -45.9547 | -48.1316 | -49.0474 | -50.0053 | -56.5368 | -64.0084 | -69.1484 | 52.9326 | 15.4021 | -27.8632 | -29.0874 | -76.4116 | -78.4589 | -80.6632 | -83.0789 | -84.0189 | -85.0116 | -92.0526 | -100.2558 | -105.9684 | 56.1474 | 18.6042 | -24.6611 | -25.8874 | -73.2305 | -75.2937 | -77.5179 | -79.9589 | -80.92 | -81.9389 | -89.1526 | -97.56 | -103.3495
|  | AMESBURY | EE |  |  |  | 75.7474 | 74.0284 | 0.18947 | -0.72526 | -1.6442 | -2.6526 | -3.6632 | -4.6874 | -5.64 | -6.4821 | -12.1221 | -18.8232 | -24.0337 | 54.5 | 52.5621 | -26.8832 | -27.8579 | -28.8326 | -29.8853 | -30.9305 | -31.9926 | -32.9695 | -33.8158 | -39.7737 | -47.0232 | -52.8779 | 57.7158 | 55.7758 | -23.6811 | -24.6611 | -25.6379 | -26.7053 | -27.78 | -28.8726 | -29.8789 | -30.7632 | -36.9632 | -44.4884 | -50.4337
|  | AMESBURY | HT |  |  |  | 74.3811 | 42.4737 | -0.71474 | -1.8568 | -42.0811 | -43.9495 | -45.9547 | -48.1316 | -49.0474 | -50.0053 | -56.5368 | -64.0084 | -69.1484 | 52.9326 | 15.4021 | -27.8632 | -29.0874 | -76.4116 | -78.4589 | -80.6632 | -83.0789 | -84.0189 | -85.0116 | -92.0526 | -100.2558 | -105.9684 | 56.1474 | 18.6042 | -24.6611 | -25.8874 | -73.2305 | -75.2937 | -77.5179 | -79.9589 | -80.92 | -81.9389 | -89.1526 | -97.56 | -103.3495
|  | AMESBURY | HE |  |  |  | 76.4368 | 74.9411 | 1.3937 | 0.75368 | 0.10421 | -0.64526 | -1.3789 | -2.1211 | -2.7568 | -3.2895 | -6.7526 | -11.3379 | -15.3168 | 55.2526 | 53.5484 | -25.5853 | -26.2663 | -26.9558 | -27.7316 | -28.4926 | -29.2716 | -29.9263 | -30.4705 | -34.1895 | -39.3526 | -43.86 | 58.4684 | 56.7632 | -22.3821 | -23.0632 | -23.7537 | -24.5442 | -25.3179 | -26.1126 | -26.7811 | -27.3411 | -31.1589 | -36.4021 | -40.9821
|  | AMESBURY | CF |  |  |  | 76.8295 | 76.4979 | 33.0653 | 32.7474 | 32.4242 | 32.0263 | 31.6116 | 31.2253 | 30.8305 | 30.4421 | -2.4853 | -5.0042 | -7.6832 | 55.68 | 55.32 | 11.6842 | 11.3442 | 10.9989 | 10.5779 | 10.1389 | 9.7316 | 9.3158 | 8.9 | -29.7221 | -32.5411 | -35.5789 | 58.8958 | 58.5358 | 14.8989 | 14.5589 | 14.2137 | 13.7884 | 13.34 | 12.9253 | 12.5032 | 12.0811 | -26.5863 | -29.4484 | -32.5347
MELKSHAM GSP | ANDOVER BSP | ANDOVER BSP | MINIMUM HEADROOM | SU 35334 46598 | YES | 129.0558 | 42.5537 | 128.6895 | 9.5347 | -24.8421 | -28.5326 | -29.7358 | -40.52 | -43.0347 | -47.4747 | -59.1189 | -89.2158 | -101.0705 | -110.3842 | 24.4611 | 107.08 | -21.5842 | -61.7232 | -65.8232 | -66.8105 | -80.1053 | -82.9 | -86.92 | -100.3895 | -134.7905 | -147.9421 | -158.3674 | 27.2126 | 109.7179 | -18.9674 | -59.12 | -63.2189 | -64.5884 | -77.5253 | -80.3305 | -84.7505 | -98.2379 | -132.7621 | -146.0537 | -156.5347
|  | ANDOVER BSP | EE |  |  |  | 43.0653 | 128.6895 | 64.0863 | 23.9684 | -25.8558 | -28.8263 | -31.7158 | -34.6274 | -37.8579 | -41.1484 | -55.4295 | -74.8053 | -83.24 | 25.3558 | 107.08 | 42.3042 | -3.8811 | -62.1832 | -65.4484 | -68.6137 | -71.8189 | -75.4 | -79.0653 | -94.8011 | -116.8411 | -126.3674 | 28.2558 | 109.7179 | 44.9379 | -1.6905 | -60.0116 | -63.2905 | -66.4758 | -69.7021 | -73.3032 | -76.9958 | -93.2568 | -115.4916 | -125.0789
|  | ANDOVER BSP | HT |  |  |  | 42.5537 | 131.2211 | 9.5347 | -24.8421 | -28.5326 | -29.7358 | -34.1074 | -38.4042 | -47.4747 | -59.1189 | -89.2158 | -101.0705 | -110.3842 | 24.4611 | 112.0432 | -21.5842 | -61.7232 | -65.8232 | -66.8105 | -71.6811 | -76.4905 | -86.92 | -100.3895 | -134.7905 | -147.9421 | -158.3674 | 27.2126 | 114.6842 | -18.9674 | -59.12 | -63.2189 | -64.5884 | -69.4779 | -74.3011 | -84.7505 | -98.2379 | -132.7621 | -146.0537 | -156.5347
|  | ANDOVER BSP | HE |  |  |  | 43.7326 | 133.0674 | 69.6947 | 54.3316 | 38.1442 | 2.5158 | -40.52 | -43.0347 | -45.7705 | -48.4947 | -60.2758 | -76.7547 | -83.1389 | 26.4411 | 115.4242 | 51.5021 | 30.7716 | 11.9116 | -29.7432 | -80.1053 | -82.9 | -85.9632 | -89.0295 | -102.2137 | -121.2484 | -128.5242 | 29.2453 | 118.3537 | 54.2105 | 33.4021 | 14.54 | -27.14 | -77.5253 | -80.3305 | -83.4042 | -86.4811 | -100.1189 | -119.2147 | -126.5411
|  | ANDOVER BSP | CF |  |  |  | 44.0989 | 133.7358 | 70.7705 | 41.3379 | 7.2663 | 6.2547 | 5.2895 | 4.3821 | 3.4653 | 2.4179 | -7 | -8.6653 | -12.9474 | 26.9842 | 116.4516 | 53.1779 | 15.2779 | -24.6547 | -25.7611 | -26.8095 | -27.7989 | -28.7968 | -29.9453 | -40.6453 | -42.2211 | -47.1053 | 29.6453 | 119.2495 | 56.1221 | 17.9053 | -22.04 | -23.1516 | -24.2063 | -25.1979 | -26.2 | -27.3537 | -38.0747 | -40.0537 | -44.9726
MANNINGTON GSP | ARNEWOOD | ARNEWOOD | MINIMUM HEADROOM | SZ 26094 97294 | YES | 35.4137 | 75.6568 | 74.3758 | 72.7979 | 110.3253 | 91.9979 | 89.3611 | 86.5232 | 84.0684 | 81.6295 | 79.4926 | 50.42 | 42.8263 | 36.1526 | 60.0811 | 57.5495 | 54.8474 | 90.64 | 69.2316 | 66.3547 | 63.2463 | 60.5853 | 57.9316 | 55.62 | 26.0947 | 17.8537 | 10.3789 | 62.1126 | 59.8463 | 57.2305 | 92.7 | 71.2821 | 68.3958 | 65.2674 | 62.5832 | 59.9074 | 57.5684 | 27.8821 | 19.4516 | 11.9158
|  | ARNEWOOD | EE |  |  |  | 76.1632 | 75.1695 | 74.1116 | 110.3253 | 91.9979 | 89.3611 | 86.5232 | 84.0684 | 81.6295 | 79.4926 | 50.42 | 42.8263 | 36.1526 | 61.1937 | 59.2453 | 57.1137 | 90.64 | 69.2316 | 66.3547 | 63.2463 | 60.5853 | 57.9316 | 55.62 | 26.0947 | 17.8537 | 10.3789 | 63.0968 | 61.3505 | 59.4442 | 92.7 | 71.2821 | 68.3958 | 65.2674 | 62.5832 | 59.9074 | 57.5684 | 27.8821 | 19.4516 | 11.9158
|  | ARNEWOOD | HT |  |  |  | 75.6568 | 74.3758 | 72.7979 | 117.1158 | 114.2505 | 111.2863 | 108.0126 | 105.2758 | 101.9811 | 100.1737 | 68.6547 | 59.9063 | 51.1811 | 60.0811 | 57.5495 | 54.8474 | 98.8747 | 95.6842 | 92.4021 | 88.8695 | 85.9421 | 82.3432 | 80.4316 | 48.1116 | 38.5905 | 28.8421 | 62.1126 | 59.8463 | 57.2305 | 101.2063 | 97.9621 | 94.6116 | 91.0042 | 88.0137 | 84.3453 | 82.4168 | 49.9779 | 40.32 | 30.5147
|  | ARNEWOOD | HE |  |  |  | 76.8453 | 76.1768 | 75.4358 | 113.5821 | 95.8305 | 93.7316 | 91.4463 | 89.5274 | 87.6568 | 86.1116 | 59.8189 | 54.9737 | 50.4221 | 62.6547 | 61.4242 | 59.9663 | 94.1589 | 73.4032 | 71.1147 | 68.5937 | 66.4958 | 64.4484 | 62.7632 | 36.16 | 30.7716 | 25.6274 | 64.4021 | 63.2811 | 61.9747 | 96.2505 | 75.46 | 73.1589 | 70.6284 | 68.5232 | 66.4632 | 64.7695 | 38.0989 | 32.6547 | 27.46
|  | ARNEWOOD | CF |  |  |  | 77.2442 | 76.8695 | 76.4842 | 123.0821 | 122.6663 | 122.22 | 121.7632 | 121.3158 | 120.5853 | 119.5274 | 93.9042 | 90.8558 | 87.7726 | 63.3695 | 62.6568 | 61.86 | 107.9768 | 107.0232 | 105.9874 | 104.88 | 103.8095 | 102.6474 | 101.4505 | 75.4021 | 71.9442 | 68.5368 | 65.0789 | 64.4095 | 63.6884 | 109.9074 | 109.0674 | 108.1537 | 107.1789 | 106.1874 | 105.0158 | 103.7926 | 77.6495 | 74.0916 | 70.5684
BRAMLEY (BASI) | BASINGSTOKE T1A & T2A | BASINGSTOKE T1A & T2A | MINIMUM HEADROOM | SU 65132 52710 | YES | 30.3484 | 74.5653 | 74.0947 | 73.6189 | 43.6063 | 42.8232 | 42.0105 | 40.5684 | 39.1937 | 37.8589 | 36.5737 | 23.7242 | 23.0305 | 22.5021 | 63.3495 | 62.5695 | 61.6958 | 31.3326 | 30.4432 | 29.5368 | 27.7537 | 26.0432 | 24.3737 | 22.7642 | 12.0105 | 7.1758 | 3.5737 | 66.5242 | 65.7421 | 64.8737 | 34.5021 | 33.6074 | 32.6863 | 30.8737 | 29.1295 | 27.4305 | 25.7874 | 9.7737 | 8.92 | 6.32
|  | BASINGSTOKE T1A & T2A | EE |  |  |  | 74.7295 | 74.3547 | 73.9568 | 44.0621 | 43.6221 | 43.0411 | 42.3747 | 41.3032 | 40.0263 | 38.7589 | 34.9695 | 32.8895 | 30.5895 | 63.5137 | 63.1347 | 62.4316 | 32.2337 | 31.5063 | 30.7516 | 30.0189 | 28.7179 | 27.1253 | 25.5316 | 21.0147 | 18.8168 | 15.9611 | 66.6884 | 66.2663 | 65.6053 | 35.4137 | 34.6779 | 33.9116 | 33.1621 | 31.8326 | 30.2063 | 28.5758 | 23.9116 | 21.6326 | 18.7474
|  | BASINGSTOKE T1A & T2A | HT |  |  |  | 74.5653 | 74.0947 | 73.6189 | 43.6063 | 42.8232 | 42.0105 | 40.5684 | 39.1937 | 37.8589 | 36.5737 | 33.2905 | 25.7242 | 22.78 | 63.3495 | 62.5695 | 61.6958 | 31.3326 | 30.4432 | 29.5368 | 27.7537 | 26.0432 | 24.3737 | 22.7642 | 19.0589 | 7.1758 | 3.5737 | 66.5242 | 65.7421 | 64.8737 | 34.5021 | 33.6074 | 32.6863 | 30.8737 | 29.1295 | 27.4305 | 25.7874 | 22.02 | 9.9968 | 6.32
|  | BASINGSTOKE T1A & T2A | HE |  |  |  | 74.9726 | 74.7189 | 74.44 | 44.6611 | 44.3326 | 43.9653 | 43.6158 | 43.1684 | 42.1779 | 41.2316 | 23.7242 | 23.0305 | 22.5021 | 63.7568 | 63.5032 | 63.2242 | 33.4463 | 32.9895 | 32.4484 | 31.9368 | 30.8842 | 29.6316 | 28.4263 | 12.0105 | 10.8063 | 9.2958 | 66.9316 | 66.6779 | 66.3989 | 36.6168 | 36.1379 | 35.6158 | 35.1074 | 34.0358 | 32.76 | 31.5295 | 9.7737 | 8.92 | 8.0968
|  | BASINGSTOKE T1A & T2A | CF |  |  |  | 75.0884 | 74.9189 | 74.7453 | 45.0916 | 44.9074 | 44.7084 | 44.5063 | 44.3074 | 44.1116 | 43.9147 | 41.2095 | 40.1811 | 39.3074 | 63.8726 | 63.7032 | 63.5295 | 33.8758 | 33.6916 | 33.4958 | 33.2137 | 32.8811 | 32.4895 | 32.0642 | 28.2621 | 27.0684 | 26.0368 | 67.0474 | 66.8779 | 66.7042 | 37.0505 | 36.8663 | 36.6684 | 36.3516 | 36.0347 | 35.6621 | 35.2295 | 31.3621 | 30.1389 | 29.0768
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | BASINGSTOKE T1B & T2B | MINIMUM HEADROOM | SU 65132 52711 | YES | 22.5632 | 77.0326 | 61.0674 | 58.5379 | 55.7758 | 52.4853 | 48.8684 | 41.5884 | 34.7611 | 28.8432 | 23.8263 | 6.2863 | -4.14 | -10.8326 | 63.8505 | 44.3358 | 41.4979 | 38.3937 | 34.6568 | 30.5411 | 22.0116 | 14.0021 | 7.0674 | 1.2095 | -19.1579 | -31.1158 | -38.6316 | 67.5526 | 47.2 | 44.3621 | 41.2568 | 37.5179 | 33.3968 | 24.8611 | 16.8442 | 9.9063 | 4.0389 | -16.3684 | -28.3695 | -35.9011
|  | BASINGSTOKE T1B & T2B | EE |  |  |  | 77.4116 | 76.6158 | 60.0811 | 57.6789 | 54.7211 | 51.4463 | 48.6074 | 43.7747 | 37.9105 | 32.4379 | 14.3326 | 4.2558 | -1.5147 | 64.5937 | 62.9095 | 43.2 | 40.4895 | 37.12 | 33.3779 | 30.1558 | 24.5253 | 17.6463 | 11.22 | -9.9442 | -21.6032 | -28.2463 | 68.3853 | 66.4874 | 46.0642 | 43.3516 | 39.9789 | 36.2326 | 33.0074 | 27.3684 | 20.4811 | 14.0453 | -7.1726 | -18.8895 | -25.5516
|  | BASINGSTOKE T1B & T2B | HT |  |  |  | 77.0326 | 61.0674 | 58.5379 | 55.7758 | 52.4853 | 48.8684 | 41.5884 | 34.7611 | 28.8432 | 23.8263 | 6.2863 | -4.14 | -10.8326 | 63.8505 | 44.3358 | 41.4979 | 38.3937 | 34.6568 | 30.5411 | 22.0116 | 14.0021 | 7.0674 | 1.2095 | -19.1579 | -31.1158 | -38.6316 | 67.5526 | 47.2 | 44.3621 | 41.2568 | 37.5179 | 33.3968 | 24.8611 | 16.8442 | 9.9063 | 4.0389 | -16.3684 | -28.3695 | -35.9011
|  | BASINGSTOKE T1B & T2B | HE |  |  |  | 77.9495 | 77.4084 | 76.8095 | 60.2347 | 57.7284 | 54.8726 | 52.4505 | 48.6379 | 44.3232 | 40.5947 | 26.5695 | 15.6853 | 10.4884 | 65.6221 | 64.4263 | 62.8495 | 43.3084 | 40.4316 | 37.1526 | 34.3884 | 29.9389 | 24.8747 | 20.5032 | 4.0168 | -8.8484 | -14.9474 | 69.3758 | 68.1768 | 66.3642 | 46.1716 | 43.2958 | 40.0105 | 37.2453 | 32.7905 | 27.7232 | 23.3453 | 6.8358 | -6.0484 | -12.1642
|  | BASINGSTOKE T1B & T2B | CF |  |  |  | 78.2568 | 77.9516 | 77.6316 | 63.9168 | 62.9463 | 61.4621 | 59.3274 | 57.7526 | 56.4232 | 55.1895 | 46.4432 | 37.0147 | 31.5547 | 66.4053 | 65.8632 | 65.2 | 47.5105 | 46.4105 | 44.6958 | 42.2 | 40.3789 | 38.8495 | 37.4379 | 27.2316 | 16.0453 | 9.5726 | 69.72 | 69.3958 | 69.0495 | 50.3758 | 49.2737 | 47.5589 | 45.06 | 43.2368 | 41.7074 | 40.2947 | 30.0779 | 18.8811 | 12.3947
BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | BASINGSTOKE T3 & T4 | MINIMUM HEADROOM | SU 65132 52712 | YES | 21.9968 | 100.0537 | 99.5758 | 99.0937 | 47.5063 | 45.4926 | 43.1768 | 40.9158 | 38.1789 | 35.1979 | 32.1947 | 22.8674 | 20.0347 | 16.1674 | 90.1 | 89.5274 | 88.1726 | 25.8537 | 23.5663 | 20.94 | 18.3821 | 15.26 | 11.8516 | 8.4147 | -2.1095 | -5.0537 | -9.2284 | 92.04 | 91.5232 | 90.9632 | 29.2432 | 26.9589 | 24.3274 | 21.7589 | 18.6284 | 15.2116 | 11.7632 | 1.1442 | -1.9284 | -6.0505
|  | BASINGSTOKE T3 & T4 | EE |  |  |  | 100.2253 | 99.8453 | 99.4411 | 47.5063 | 45.4926 | 43.1768 | 40.9158 | 38.1789 | 35.1979 | 32.1947 | 22.8674 | 20.0347 | 16.8316 | 90.3011 | 89.8474 | 88.9589 | 25.8537 | 23.5663 | 20.94 | 18.3821 | 15.26 | 11.8516 | 8.4147 | -2.1095 | -5.0537 | -8.6242 | 92.2263 | 91.8126 | 91.3358 | 29.2432 | 26.9589 | 24.3274 | 21.7589 | 18.6284 | 15.2116 | 11.7632 | 1.1442 | -1.9284 | -5.5379
|  | BASINGSTOKE T3 & T4 | HT |  |  |  | 100.0537 | 99.5758 | 99.0937 | 50.0421 | 47.8684 | 45.4032 | 42.2526 | 39.1747 | 36.1632 | 33.7621 | 24.0747 | 20.2642 | 16.1674 | 90.1 | 89.5274 | 88.1726 | 28.9116 | 26.4505 | 23.6621 | 20.0674 | 16.5526 | 13.1074 | 10.3747 | -0.56526 | -4.66 | -9.2284 | 92.04 | 91.5232 | 90.9632 | 32.2979 | 29.8389 | 27.0442 | 23.4484 | 19.9263 | 16.4768 | 13.7358 | 2.7347 | -1.4495 | -6.0505
|  | BASINGSTOKE T3 & T4 | HE |  |  |  | 100.4526 | 100.1779 | 99.8747 | 62.6274 | 46.8589 | 44.74 | 42.6905 | 40.3295 | 37.8589 | 35.4453 | 26.5516 | 25.2147 | 23.3853 | 90.5674 | 90.2411 | 89.7368 | 43.5505 | 25.06 | 22.6453 | 20.3116 | 17.6053 | 14.7663 | 11.9884 | 1.7537 | 0.34316 | -1.6926 | 92.4695 | 92.1716 | 91.8053 | 46.9105 | 28.4537 | 26.0379 | 23.6989 | 20.9926 | 18.1505 | 15.3705 | 5.1011 | 3.6537 | 1.5895
|  | BASINGSTOKE T3 & T4 | CF |  |  |  | 100.5863 | 100.4168 | 100.2432 | 81.1147 | 80.9274 | 80.7232 | 80.5147 | 80.3105 | 80.1063 | 79.9084 | 72.3853 | 71.2158 | 70.18 | 90.7168 | 90.5326 | 90.3274 | 71.1526 | 70.9032 | 70.4579 | 69.2053 | 67.7442 | 66.1874 | 64.5168 | 55.3474 | 54.0821 | 52.9411 | 92.6105 | 92.4337 | 92.2463 | 73.0968 | 72.8821 | 72.6316 | 72.3632 | 71.1463 | 69.56 | 67.8642 | 58.6495 | 57.3653 | 56.2042
EAST CLAYDON GSP | BICESTER NORTH BSP | BICESTER NORTH BSP | MINIMUM HEADROOM | SP5972023735 | YES | 110.4063 | 87.3253 | 86.64 | 85.94 | 96.8747 | 94.4274 | 80.4189 | -16.8158 | -19.8505 | -22.6463 | -25.3758 | -36.8063 | -12.1737 | -18.8168 | 79.9516 | 78.5926 | 76.7484 | 78.0116 | 75.2442 | 58.8611 | -38.7674 | -42.2021 | -45.3568 | -48.44 | -61.2874 | -37.7063 | -45.2705 | 78.7158 | 78.0305 | 77.3305 | 79.8274 | 77.0568 | 60.6526 | -36.9979 | -40.4568 | -43.6337 | -46.7442 | -59.7789 | -36.4084 | -44.0379
|  | BICESTER NORTH BSP | EE |  |  |  | 87.5747 | 87.0305 | 86.4484 | 96.8747 | 94.4274 | 80.4189 | -16.8158 | -19.8505 | -22.6463 | -25.3758 | -36.8063 | -12.1737 | -18.8168 | 80.4305 | 79.3221 | 77.6979 | 78.0116 | 75.2442 | 58.8611 | -38.7674 | -42.2021 | -45.3568 | -48.44 | -61.2874 | -37.7063 | -45.2705 | 78.9653 | 78.4211 | 77.84 | 79.8274 | 77.0568 | 60.6526 | -36.9979 | -40.4568 | -43.6337 | -46.7442 | -59.7789 | -36.4084 | -44.0379
|  | BICESTER NORTH BSP | HT |  |  |  | 87.3253 | 86.64 | 85.94 | 115.2021 | 114.4368 | 112.6621 | 14.8295 | 11.1916 | 6.3305 | 3.5179 | -7.8053 | 15.9147 | 8.4105 | 79.9516 | 78.5926 | 76.7484 | 104.1716 | 101.0063 | 97.2442 | -1.14 | -5.3495 | -10.9937 | -14.1768 | -26.9032 | -4.4095 | -12.9147 | 78.7158 | 78.0305 | 77.3305 | 105.9958 | 102.8295 | 99.0505 | 0.64947 | -3.5789 | -9.24 | -12.4442 | -25.3011 | -2.9611 | -11.5295
|  | BICESTER NORTH BSP | HE |  |  |  | 87.9411 | 87.5684 | 87.1568 | 116.7042 | 116.2116 | 115.6505 | 19.8189 | 17.1526 | 14.7726 | 12.4611 | 3.2368 | 30.0158 | 24.6453 | 81.0884 | 80.3074 | 78.9989 | 106.9358 | 104.4453 | 101.7168 | 4.3747 | 1.2811 | -1.4747 | -4.1611 | -14.7358 | 11.0316 | 4.8653 | 79.3316 | 78.9589 | 78.5474 | 108.0947 | 106.2695 | 103.5295 | 6.1768 | 3.0705 | 0.30211 | -2.3947 | -13.0474 | 12.6589 | 6.4368
|  | BICESTER NORTH BSP | CF |  |  |  | 88.1526 | 87.9389 | 87.7189 | 117.4905 | 117.2537 | 116.9895 | 22.5095 | 22.2453 | 21.9832 | 21.7263 | 15.5926 | 10.9684 | 7.5811 | 81.4526 | 81.2337 | 80.7832 | 110.2168 | 109.5 | 108.5168 | 12.7989 | 10.8589 | 8.8726 | 6.9284 | -0.61263 | -6.0137 | -9.8989 | 79.5432 | 79.3295 | 79.1095 | 108.8811 | 108.6442 | 108.3811 | 13.9021 | 12.6653 | 10.6758 | 8.7274 | 1.1589 | -4.2726 | -8.1958
BOTLEY WOOD GSP | BOTLEY WOOD BSP | BOTLEY WOOD BSP | MINIMUM HEADROOM | SU 54073 09759 | YES | 30.3989 | 85.6274 | 85.72 | 69.7842 | 69.6316 | 69.4716 | 76.8832 | 75.4084 | 74.2242 | 73.1684 | 72.1916 | 67.8916 | 63.96 | 60.3747 | 76.5547 | 76.8126 | 58.8389 | 58.5853 | 58.3358 | 67.8347 | 66.2295 | 64.9516 | 63.8126 | 62.7579 | 58.0105 | 53.62 | 49.5832 | 78.5411 | 78.8095 | 60.6884 | 60.4337 | 60.1821 | 67.8768 | 66.2411 | 64.9358 | 63.7747 | 62.6979 | 57.9368 | 53.5358 | 49.4958
|  | BOTLEY WOOD BSP | EE |  |  |  | 85.6274 | 96.3842 | 80.1937 | 79.7695 | 79.3253 | 78.1368 | 76.8305 | 75.7916 | 74.8358 | 73.9705 | 70.5632 | 67.4905 | 64.7337 | 76.5547 | 90.8379 | 74.2032 | 72.7916 | 70.9274 | 69.1684 | 67.7432 | 66.62 | 65.5884 | 64.6547 | 60.9305 | 57.4895 | 54.3705 | 78.5411 | 91.0347 | 74.3863 | 72.9432 | 71.0337 | 69.2316 | 67.7747 | 66.6284 | 65.5758 | 64.6242 | 60.8526 | 57.4011 | 54.2768
|  | BOTLEY WOOD BSP | HT |  |  |  | 96.7484 | 96.0863 | 79.8053 | 79.2853 | 78.6442 | 76.8832 | 75.4084 | 74.2242 | 73.1684 | 72.1916 | 67.8916 | 63.96 | 60.3747 | 91.4389 | 90.2253 | 73.5011 | 71.7863 | 69.7589 | 67.8347 | 66.2295 | 64.9516 | 63.8126 | 62.7579 | 58.0105 | 53.62 | 49.5832 | 91.6432 | 90.4116 | 73.6737 | 71.9221 | 69.8463 | 67.8768 | 66.2411 | 64.9358 | 63.7747 | 62.6979 | 57.9368 | 53.5358 | 49.4958
|  | BOTLEY WOOD BSP | HE |  |  |  | 85.8884 | 96.7716 | 80.7021 | 80.3926 | 80.0589 | 79.7011 | 78.7084 | 77.8653 | 77.1063 | 76.4358 | 73.9305 | 71.72 | 69.7516 | 77.0884 | 91.5179 | 75.0905 | 74.1242 | 72.4958 | 70.9589 | 69.7495 | 68.8326 | 68.0126 | 67.2853 | 64.5579 | 62.0789 | 59.8242 | 79.0905 | 91.7232 | 75.2853 | 74.2979 | 72.6295 | 71.0537 | 69.8158 | 68.8821 | 68.0432 | 67.3011 | 64.5116 | 62.0063 | 59.7484
|  | BOTLEY WOOD BSP | CF |  |  |  | 86.0368 | 85.72 | 69.7842 | 69.6316 | 69.4716 | 80.6179 | 80.4505 | 80.2853 | 80.1221 | 79.96 | 79.2295 | 78.5021 | 77.1905 | 77.6379 | 76.8126 | 58.8389 | 58.5853 | 58.3358 | 75.3 | 74.8905 | 74.3632 | 73.8168 | 73.2663 | 71.2221 | 69.5863 | 68.1232 | 79.4 | 78.8095 | 60.6884 | 60.4337 | 60.1821 | 75.5032 | 75.0863 | 74.5453 | 73.9874 | 73.4242 | 71.3389 | 69.6621 | 68.1558
MANNINGTON GSP | BOURNEMOUTH | BOURNEMOUTH | MINIMUM HEADROOM | SZ 06265 92437 | YES | 0.99579 | 130.1358 | 127.8989 | 125.64 | 100.4653 | 96.9305 | 91.2105 | 85.8147 | 80.9989 | 76.2979 | 71.7716 | 51.2411 | 32.1789 | 14.3821 | 100.2 | 97.8516 | 92.9705 | 63.9905 | 58.1979 | 51.9295 | 46.0421 | 40.7895 | 35.6379 | 30.6558 | 7.9547 | -13.3568 | -33.3989 | 105.7747 | 103.4937 | 99.6747 | 70.6295 | 64.8032 | 58.5411 | 52.66 | 47.4095 | 42.2632 | 37.2895 | 14.6074 | -6.6853 | -26.7032
|  | BOURNEMOUTH | EE |  |  |  | 131.04 | 129.3137 | 127.4884 | 102.7695 | 100.7168 | 97.2105 | 92.7684 | 88.9358 | 85.4347 | 81.7263 | 65.7305 | 50.9463 | 37.3747 | 101.1516 | 99.3432 | 97.1832 | 69.3379 | 63.9589 | 58.4189 | 53.5589 | 49.4042 | 45.6295 | 41.5705 | 23.9042 | 7.3242 | -8.0432 | 106.6789 | 104.9526 | 103.0274 | 76.0305 | 70.5916 | 65.0253 | 60.1695 | 56.0168 | 52.2453 | 48.1884 | 30.5326 | 13.9663 | -1.3842
|  | BOURNEMOUTH | HT |  |  |  | 130.1358 | 127.8989 | 125.64 | 100.4653 | 96.9305 | 91.2105 | 85.8147 | 80.9989 | 76.2979 | 71.7716 | 51.2411 | 32.1789 | 14.3821 | 100.2 | 97.8516 | 92.9705 | 63.9905 | 58.1979 | 51.9295 | 46.0421 | 40.7895 | 35.6379 | 30.6558 | 7.9547 | -13.3568 | -33.3989 | 105.7747 | 103.4937 | 99.6747 | 70.6295 | 64.8032 | 58.5411 | 52.66 | 47.4095 | 42.2632 | 37.2895 | 14.6074 | -6.6853 | -26.7032
|  | BOURNEMOUTH | HE |  |  |  | 132.0474 | 130.7832 | 129.3842 | 105.0611 | 103.3968 | 101.62 | 99.9211 | 97.6411 | 94.9768 | 92.1368 | 80.6211 | 70.2221 | 60.9232 | 102.22 | 100.9074 | 99.42 | 74.9053 | 70.5263 | 65.9684 | 62.0895 | 58.9705 | 56.1021 | 52.9895 | 40.2263 | 28.4705 | 17.8358 | 107.6863 | 106.4221 | 105.0232 | 80.6074 | 77.2295 | 72.6221 | 68.7021 | 65.5747 | 62.7063 | 59.5968 | 46.8463 | 35.1042 | 24.4811
|  | BOURNEMOUTH | CF |  |  |  | 132.6389 | 131.8547 | 131.0421 | 107.4189 | 106.5463 | 105.6411 | 104.7158 | 103.8084 | 102.9095 | 102.0126 | 97.3432 | 90.0537 | 83.7516 | 102.8347 | 102.0211 | 101.1632 | 77.4926 | 76.5632 | 75.5905 | 73.8316 | 71.5516 | 69.4347 | 67.4021 | 58.6779 | 50.4589 | 43.2453 | 108.2779 | 107.4937 | 106.6811 | 83.0579 | 82.1853 | 81.2305 | 80.22 | 78.2653 | 76.1253 | 74.0726 | 65.2811 | 57.0716 | 49.8674
BRAMLEY (FLEE) | BRACKNELL | BRACKNELL | MINIMUM HEADROOM | SU 86026 69422 | YES | 1.4179 | 221.2053 | 222.2705 | 221.5863 | 220.8705 | 220.1347 | 219.9305 | 218.8232 | 212.5684 | 206.2632 | 201.0421 | 179.7453 | 156.0674 | 140.5516 | 187.7032 | 188.8895 | 188.0074 | 182.7558 | 176.9695 | 170.5568 | 164.6832 | 157.6495 | 150.5558 | 144.94 | 121.7211 | 92.7347 | 75.2474 | 193.1095 | 194.2295 | 193.4832 | 189.6811 | 183.8968 | 177.4726 | 171.5895 | 164.5484 | 157.4411 | 151.8116 | 128.4516 | 98.1821 | 80.6632
|  | BRACKNELL | EE |  |  |  | 221.2053 | 231.3189 | 229.5558 | 227.6821 | 225.7221 | 224.1105 | 218.8232 | 212.5684 | 206.2632 | 201.2495 | 190.0979 | 176.1684 | 164.0495 | 187.7032 | 201.0495 | 196.6063 | 182.7558 | 176.9695 | 170.5568 | 164.6832 | 157.6495 | 150.5558 | 144.94 | 135.3105 | 119.7884 | 106.1105 | 193.1095 | 205.7579 | 203.5358 | 189.6811 | 183.8968 | 177.4726 | 171.5895 | 164.5484 | 157.4411 | 151.8116 | 143.2211 | 127.6063 | 113.9
|  | BRACKNELL | HT |  |  |  | 232.1811 | 230.0632 | 227.9274 | 225.6579 | 223.3095 | 222.1126 | 219.6579 | 214.1011 | 207.4895 | 201.0421 | 179.7453 | 156.0674 | 140.5516 | 202.8653 | 198.4558 | 193.0263 | 186.7684 | 180.1495 | 174.2063 | 167.7516 | 160.1432 | 152.7032 | 145.4326 | 121.7211 | 92.7347 | 75.2474 | 206.62 | 204.5021 | 199.9568 | 193.6968 | 187.0758 | 181.0295 | 174.5684 | 166.9516 | 159.5011 | 152.2211 | 128.4516 | 98.1821 | 80.6632
|  | BRACKNELL | HE |  |  |  | 222.3095 | 232.9411 | 231.6789 | 230.2811 | 228.7811 | 227.7316 | 226.1842 | 224.7253 | 222.8474 | 218.7526 | 196.5737 | 186.7516 | 178.3032 | 188.9642 | 203.6442 | 201.4568 | 197.1295 | 192.0621 | 186.5979 | 181.6905 | 175.3221 | 169.2337 | 164.6211 | 136.0789 | 124.9421 | 115.2663 | 194.2863 | 207.38 | 206.1179 | 204.0611 | 198.9937 | 193.5211 | 188.6074 | 182.2347 | 176.1411 | 171.5221 | 141.0263 | 129.8621 | 120.1579
|  | BRACKNELL | CF |  |  |  | 222.9337 | 222.2705 | 221.5863 | 220.8705 | 220.1347 | 219.9305 | 230.92 | 230.1463 | 229.3821 | 228.6179 | 225.2 | 222.7305 | 217.1579 | 189.68 | 188.8895 | 188.0074 | 186.2568 | 184.1242 | 181.9884 | 196.7474 | 193.4832 | 190.0084 | 186.9453 | 175.7116 | 169.1421 | 162.7537 | 194.9474 | 194.2295 | 193.4832 | 192.7063 | 191.8884 | 190.5779 | 203.6726 | 200.4084 | 196.9326 | 193.86 | 182.6221 | 175.9358 | 169.5295
BRAMLEY (FLEE) | BURGHFIELD MAIN | BURGHFIELD MAIN | MINIMUM HEADROOM | SU 69442 70509 | YES | 2.3632 | 112.0063 | 110.7568 | 109.4916 | 72.0653 | 68.6168 | 23.3863 | 19.3189 | 16.3484 | 13.7221 | 11.6295 | 2.9021 | -6.0642 | -14.58 | 92.1421 | 89.8674 | 87.32 | 37.3642 | 33.5516 | -18.6358 | -23.1653 | -26.4368 | -29.3221 | -31.5968 | -41.0989 | -51.0737 | -60.6389 | 95.9958 | 94.6842 | 92.5789 | 42.9632 | 39.1558 | -13.4105 | -17.9358 | -21.2042 | -24.0853 | -26.3589 | -35.8516 | -45.8137 | -55.3663
|  | BURGHFIELD MAIN | EE |  |  |  | 112.4874 | 111.5074 | 110.4705 | 109.3695 | 108.2168 | 105.4621 | 101.9768 | 99.18 | 96.6853 | 94.9168 | 88.3926 | 81.7221 | 75.4305 | 93.08 | 91.2989 | 89.5463 | 86.7884 | 83.5832 | 77.8105 | 73.6905 | 70.5989 | 67.8537 | 65.94 | 58.88 | 51.4568 | 44.3695 | 96.5032 | 95.4758 | 94.3958 | 92.0547 | 88.9211 | 82.9158 | 78.7958 | 75.7021 | 72.9568 | 71.0421 | 63.9811 | 56.5547 | 49.4674
|  | BURGHFIELD MAIN | HT |  |  |  | 112.0063 | 110.7568 | 109.4916 | 72.0653 | 68.6168 | 23.3863 | 19.3189 | 16.3484 | 13.7221 | 11.6295 | 2.9021 | -6.0642 | -14.58 | 92.1421 | 89.8674 | 87.32 | 37.3642 | 33.5516 | -18.6358 | -23.1653 | -26.4368 | -29.3221 | -31.5968 | -41.0989 | -51.0737 | -60.6389 | 95.9958 | 94.6842 | 92.5789 | 42.9632 | 39.1558 | -13.4105 | -17.9358 | -21.2042 | -24.0853 | -26.3589 | -35.8516 | -45.8137 | -55.3663
|  | BURGHFIELD MAIN | HE |  |  |  | 113.1284 | 112.4505 | 111.7 | 110.8737 | 109.9789 | 72.0116 | 68.8326 | 66.5884 | 64.5916 | 63.3232 | 59.1968 | 54.7768 | 50.6221 | 94.0758 | 93.1368 | 92.0147 | 90.1421 | 87.5737 | 37.5379 | 33.9568 | 31.4674 | 29.2589 | 27.8895 | 23.4453 | 18.4895 | 13.7484 | 97.1789 | 96.4716 | 95.7 | 94.8095 | 92.8358 | 42.9 | 39.3242 | 36.8389 | 34.6316 | 33.2632 | 28.8232 | 23.8726 | 19.1411
|  | BURGHFIELD MAIN | CF |  |  |  | 113.5 | 113.1063 | 112.7021 | 112.2789 | 111.8411 | 111.3895 | 110.9274 | 110.4726 | 110.0253 | 109.5779 | 107.5768 | 105.4516 | 102.7726 | 94.4821 | 94.0642 | 93.6137 | 92.8158 | 91.8179 | 90.4747 | 88.9758 | 87.6179 | 86.24 | 85.0095 | 80.1337 | 76.9147 | 73.8663 | 97.5747 | 97.1611 | 96.7421 | 96.2916 | 95.8189 | 95.3147 | 94.2274 | 92.8926 | 91.5474 | 90.3453 | 85.5737 | 82.4368 | 79.3958
BRAMLEY (FLEE) | BURGHFIELD RESERVE | BURGHFIELD RESERVE | MINIMUM HEADROOM | SU 69442 70509 | YES | 25.6126 | 78.2191 | 76.138 | 74.2349 | 72.3012 | 69.977 | 67.158 | 63.9486 | 60.5886 | 59.3107 | 57.4664 | 36.0686 | 21.5401 | 16.417 | 53.3118 | 51.0318 | 48.9613 | 46.8697 | 44.3245 | 41.2087 | 37.6434 | 33.875 | 32.5445 | 30.5361 | 6.0592 | -10.0829 | -15.7197 | 59.2929 | 57.0139 | 54.9476 | 52.8539 | 50.3097 | 47.1929 | 43.6203 | 39.8466 | 38.5034 | 36.4855 | 11.9655 | -4.2524 | -9.9218
|  | BURGHFIELD RESERVE | EE |  |  |  | 94.6991 | 77.2875 | 75.7338 | 72.5654 | 71.1054 | 69.5475 | 67.9907 | 66.5917 | 65.2843 | 64.1191 | 58.6054 | 41.7433 | 34.3559 | 76.2866 | 52.2824 | 50.5929 | 47.0182 | 45.4487 | 43.7929 | 42.1382 | 40.6571 | 39.2845 | 38.0655 | 32.2192 | 13.2729 | 4.8655 | 81.795 | 58.2624 | 56.5761 | 53.0013 | 51.4403 | 49.7729 | 48.1034 | 46.6118 | 45.2213 | 43.9876 | 38.0287 | 18.975 | 10.5382
|  | BURGHFIELD RESERVE | HT |  |  |  | 78.2191 | 76.138 | 74.2349 | 72.3012 | 69.977 | 67.158 | 63.9486 | 60.5886 | 59.3107 | 57.4664 | 36.0686 | 21.5401 | 16.417 | 53.3118 | 51.0318 | 48.9613 | 46.8697 | 44.3245 | 41.2087 | 37.6434 | 33.875 | 32.5445 | 30.5361 | 6.0592 | -10.0829 | -15.7197 | 59.2929 | 57.0139 | 54.9476 | 52.8539 | 50.3097 | 47.1929 | 43.6203 | 39.8466 | 38.5034 | 36.4855 | 11.9655 | -4.2524 | -9.9218
|  | BURGHFIELD RESERVE | HE |  |  |  | 95.2159 | 94.718 | 77.7359 | 75.7812 | 74.4464 | 73.1075 | 71.9222 | 70.8949 | 69.9812 | 69.1928 | 65.8949 | 51.4864 | 45.6654 | 77.1308 | 76.1908 | 52.7729 | 50.5803 | 49.1245 | 47.6845 | 46.4213 | 45.3329 | 44.3697 | 43.5466 | 40.0434 | 23.6992 | 17.0118 | 82.3455 | 81.7982 | 58.7518 | 56.5634 | 55.1097 | 53.6645 | 52.3929 | 51.2992 | 50.3318 | 49.4992 | 45.9539 | 29.5971 | 22.8824
|  | BURGHFIELD RESERVE | CF |  |  |  | 95.5107 | 95.2338 | 79.2928 | 78.6696 | 78.0212 | 77.3938 | 76.8191 | 76.2212 | 75.5991 | 74.9749 | 72.0886 | 67.1686 | 63.9191 | 77.5624 | 77.0676 | 54.4666 | 53.7855 | 53.0761 | 52.4013 | 51.7876 | 51.1455 | 50.4771 | 49.8013 | 46.6803 | 41.4182 | 37.7034 | 82.6613 | 82.355 | 60.4466 | 59.7666 | 59.0571 | 58.3792 | 57.7603 | 57.1192 | 56.4476 | 55.7666 | 52.6371 | 47.3571 | 43.6234
BRAMLEY (FLEE) | CAMBERLEY MAIN | CAMBERLEY MAIN | MINIMUM HEADROOM | SU 86530 59483 | YES | 2.3884 | 108.5747 | 104.5074 | 101.0526 | 97.0105 | 92.7063 | 88.4105 | 84.4505 | 80.9474 | 77.7737 | 74.7832 | 61.6168 | 49.7779 | 39.0863 | 72.8158 | 68.3095 | 64.5263 | 60.0695 | 55.3147 | 50.5842 | 46.2495 | 42.4105 | 38.94 | 35.6611 | 21.1705 | 7.9989 | -4.0063 | 78.6263 | 74.1253 | 70.3463 | 65.8947 | 61.1453 | 56.4158 | 52.0821 | 48.2463 | 44.7726 | 41.4926 | 26.9916 | 13.8 | 1.7958
|  | CAMBERLEY MAIN | EE |  |  |  | 115.1737 | 106.5547 | 103.6389 | 100.4063 | 96.8474 | 93.1674 | 89.8842 | 86.6947 | 83.5853 | 80.9863 | 70.5568 | 61.5042 | 53.4832 | 92.4126 | 70.5442 | 67.3432 | 63.7842 | 59.8516 | 55.7895 | 52.1863 | 48.6779 | 45.26 | 42.4179 | 30.9568 | 20.8926 | 11.8389 | 97.12 | 76.3579 | 73.16 | 69.6032 | 65.6758 | 61.6168 | 58.0105 | 54.5032 | 51.0821 | 48.2358 | 36.7432 | 26.6453 | 17.5884
|  | CAMBERLEY MAIN | HT |  |  |  | 108.5747 | 104.5074 | 101.0526 | 97.0105 | 92.7063 | 88.4105 | 84.4505 | 80.9474 | 77.7737 | 74.7832 | 61.6168 | 49.7779 | 39.0863 | 72.8158 | 68.3095 | 64.5263 | 60.0695 | 55.3147 | 50.5842 | 46.2495 | 42.4105 | 38.94 | 35.6611 | 21.1705 | 7.9989 | -4.0063 | 78.6263 | 74.1253 | 70.3463 | 65.8947 | 61.1453 | 56.4158 | 52.0821 | 48.2463 | 44.7726 | 41.4926 | 26.9916 | 13.8 | 1.7958
|  | CAMBERLEY MAIN | HE |  |  |  | 116.0168 | 115.1958 | 106.9274 | 104.4242 | 101.56 | 98.5432 | 95.9063 | 93.3137 | 90.8674 | 88.9474 | 81.5558 | 75.3032 | 69.8253 | 94.2421 | 91.5189 | 70.9232 | 68.1537 | 64.9768 | 61.6326 | 58.7326 | 55.8684 | 53.1684 | 51.0589 | 42.8905 | 35.8316 | 29.5832 | 98.0211 | 97.0863 | 76.7368 | 73.9716 | 70.7968 | 67.4547 | 64.5547 | 61.6916 | 58.9895 | 56.8832 | 48.7053 | 41.64 | 35.3895
|  | CAMBERLEY MAIN | CF |  |  |  | 116.1589 | 115.6979 | 115.2189 | 114.7211 | 114.2084 | 113.6737 | 113.1253 | 112.5895 | 112.0547 | 111.5221 | 93.6116 | 89.3632 | 85.8589 | 94.5663 | 93.5989 | 92.3432 | 91.04 | 89.6411 | 88.2211 | 86.8295 | 85.48 | 83.9516 | 82.3768 | 56.1137 | 51.3347 | 47.34 | 98.1263 | 97.6021 | 97.0747 | 96.5316 | 95.4074 | 94.0505 | 92.6895 | 91.3389 | 89.8116 | 88.2368 | 61.9347 | 57.1537 | 53.1579
BRAMLEY (FLEE) | CAMBERLEY RESERVE | CAMBERLEY RESERVE | MINIMUM HEADROOM | SU 86530 59483 | YES | 0.69474 | 100.6063 | 99.4737 | 98.3274 | 97.1105 | 95.8579 | 92.1126 | 88.8484 | 85.9716 | 83.3084 | 80.7547 | 56.0558 | 50.4874 | 43.7063 | 85.4842 | 82.2116 | 78.5063 | 74.82 | 71.2695 | 66.8011 | 63.2021 | 60.0305 | 57.0853 | 54.2568 | 29.28 | 14.7832 | 7.3316 | 89.5695 | 86.62 | 83.2989 | 79.9832 | 76.7768 | 72.5084 | 68.9884 | 65.8853 | 63.0105 | 60.2495 | 31.9337 | 19.5926 | 12.2284
|  | CAMBERLEY RESERVE | EE |  |  |  | 101.0484 | 100.1621 | 99.2263 | 98.2253 | 97.1853 | 95.0558 | 92.2074 | 90.0326 | 87.5958 | 85.2989 | 83.9516 | 78.0432 | 72.9832 | 86.4674 | 83.7316 | 80.4842 | 77.2126 | 74.0621 | 69.9884 | 66.8316 | 64.6189 | 61.9305 | 59.3916 | 62.1263 | 55.6326 | 49.9821 | 90.4747 | 88.0168 | 85.1147 | 82.1832 | 79.3505 | 75.6347 | 72.5495 | 70.5253 | 67.8968 | 65.4137 | 70.1179 | 63.5695 | 57.9042
|  | CAMBERLEY RESERVE | HT |  |  |  | 100.6063 | 99.4737 | 98.3274 | 97.1105 | 95.8579 | 92.1126 | 88.8484 | 85.9716 | 83.3084 | 80.7547 | 68.1958 | 50.4874 | 43.7063 | 85.4842 | 82.2116 | 78.5063 | 74.82 | 71.2695 | 66.8011 | 63.2021 | 60.0305 | 57.0853 | 54.2568 | 40.2211 | 14.7832 | 7.3316 | 89.5695 | 86.62 | 83.2989 | 79.9832 | 76.7768 | 72.5084 | 68.9884 | 65.8853 | 63.0105 | 60.2495 | 46.2253 | 19.5926 | 12.2284
|  | CAMBERLEY RESERVE | HE |  |  |  | 101.6474 | 101.0484 | 100.3842 | 99.6526 | 98.8632 | 98.0116 | 96.5495 | 94.4242 | 92.4568 | 90.6211 | 56.0558 | 54.5642 | 53.5568 | 87.6642 | 85.6926 | 83.0453 | 80.3558 | 77.7611 | 74.1989 | 71.5495 | 69.1926 | 67.0105 | 64.9684 | 29.28 | 25.1389 | 21.6147 | 91.6916 | 89.8137 | 87.4653 | 85.0705 | 82.7484 | 79.5895 | 77.1779 | 74.8768 | 72.7463 | 70.7537 | 31.9337 | 29.3389 | 25.8558
|  | CAMBERLEY RESERVE | CF |  |  |  | 101.9916 | 101.6516 | 101.3 | 100.9337 | 100.5547 | 100.1579 | 99.7526 | 99.3547 | 98.9632 | 98.5705 | 94.6611 | 91.9011 | 89.6495 | 88.1579 | 87.4811 | 86.1811 | 84.8537 | 83.5937 | 81.9642 | 80.5642 | 79.2495 | 77.9526 | 76.6084 | 69.4095 | 66.3274 | 63.7821 | 92.1968 | 91.4758 | 90.2674 | 89.0842 | 87.9558 | 86.5116 | 85.2611 | 84.0821 | 82.92 | 81.72 | 75.0968 | 72.0905 | 69.6116
IVER 132KV | CHALVEY BSP | CHALVEY BSP | MINIMUM HEADROOM | SU 96669 79364 | YES | 0.14737 | 109.4842 | 108.6158 | 107.5632 | 106.3674 | 102.5726 | 98.0158 | 184.5642 | 182.4158 | 180.3726 | 178.4453 | 169.9463 | 162.5653 | 155.7568 | 92.4537 | 88.6084 | 84.24 | 79.5242 | 74.1821 | 68.9874 | 155.1 | 152.7263 | 150.4642 | 148.3284 | 138.8705 | 130.6011 | 122.9221 | 96.26 | 93.3621 | 88.9316 | 84.2021 | 78.8579 | 73.6621 | 159.7726 | 157.3989 | 155.1368 | 153.0011 | 143.5411 | 135.2695 | 127.5884
|  | CHALVEY BSP | EE |  |  |  | 109.8042 | 109.1147 | 108.2684 | 107.2421 | 104.5137 | 100.2368 | 187.0989 | 185.2589 | 183.4737 | 181.8211 | 174.9547 | 169.1989 | 163.9916 | 93.1558 | 89.7221 | 85.6884 | 81.3242 | 76.3 | 71.4084 | 157.8558 | 155.8263 | 153.8579 | 152.0305 | 144.3916 | 137.92 | 132.0179 | 96.6063 | 94.4853 | 90.3937 | 86.0011 | 80.9768 | 76.0832 | 162.5295 | 160.5 | 158.5305 | 156.7032 | 149.0632 | 142.5895 | 136.6853
|  | CHALVEY BSP | HT |  |  |  | 109.4842 | 108.6158 | 107.5632 | 106.3674 | 102.5726 | 98.0158 | 184.5642 | 182.4158 | 180.3726 | 178.4453 | 169.9463 | 162.5653 | 155.7568 | 92.4537 | 88.6084 | 84.24 | 79.5242 | 74.1821 | 68.9874 | 155.1 | 152.7263 | 150.4642 | 148.3284 | 138.8705 | 130.6011 | 122.9221 | 96.26 | 93.3621 | 88.9316 | 84.2021 | 78.8579 | 73.6621 | 159.7726 | 157.3989 | 155.1368 | 153.0011 | 143.5411 | 135.2695 | 127.5884
|  | CHALVEY BSP | HE |  |  |  | 110.2084 | 109.7074 | 109.1095 | 108.2589 | 106.9463 | 103.0053 | 190.2042 | 188.7095 | 187.3137 | 186.0463 | 181.0105 | 176.9758 | 173.4568 | 93.9842 | 91.1368 | 87.5305 | 83.5926 | 78.9758 | 74.4537 | 161.2705 | 159.6189 | 158.08 | 156.6768 | 151.0495 | 146.48 | 142.4484 | 97.0463 | 95.9137 | 92.2558 | 88.2716 | 83.6526 | 79.1295 | 165.9453 | 164.2947 | 162.7537 | 161.3516 | 155.7221 | 151.1526 | 147.1189
|  | CHALVEY BSP | CF |  |  |  | 110.4505 | 110.1442 | 109.8253 | 109.4937 | 109.1505 | 108.7926 | 198.1621 | 197.6011 | 197.1874 | 196.2768 | 192.4589 | 189.6126 | 187.2158 | 94.7811 | 94.4358 | 93.8716 | 92.7968 | 90.9411 | 87.6947 | 173.5326 | 170.2295 | 169.2853 | 168.2747 | 164.0526 | 160.8379 | 158.0895 | 97.4021 | 97.0768 | 96.6958 | 96.2926 | 95.7189 | 92.4295 | 178.2105 | 174.9063 | 173.9632 | 172.9526 | 168.7295 | 165.5126 | 162.7621
LOVEDEAN GSP | CHICHESTER & HUNSTON | CHICHESTER & HUNSTON | MINIMUM HEADROOM | SU 92282 07416 | YES | 123.0326 | 187.4959 | 150.018 | 143.0475 | 116.5875 | 109.0791 | 70.5917 | 57.7917 | 45.0128 | 35.1717 | 20.0359 | -49.5272 | -132.7799 | -166.6904 | 129.2824 | 90.6624 | 80.315 | 47.4287 | 37.1908 | -6.4471 | -20.8534 | -35.3229 | -46.3766 | -63.6829 | -145.0776 | -233.1934 | -271.8945 | 140.695 | 102.0782 | 91.2424 | 58.4413 | 48.2824 | 7.3687 | -6.9271 | -21.2397 | -32.2071 | -49.4134 | -130.7745 | -218.8997 | -257.5734
|  | CHICHESTER & HUNSTON | EE |  |  |  | 187.4959 | 150.3033 | 143.4149 | 116.5875 | 109.0791 | 91.717 | 80.5886 | 70.0012 | 60.597 | 51.7959 | 8.5949 | -75.1672 | -102.7451 | 129.2824 | 90.7024 | 80.315 | 47.4287 | 37.1908 | 15.8392 | 3.2761 | -8.6829 | -19.265 | -29.1829 | -78.3776 | -168.9787 | -200.6503 | 140.695 | 102.0782 | 91.2424 | 58.4413 | 48.2824 | 27.3771 | 14.9045 | 3.0413 | -7.4492 | -17.2829 | -66.0124 | -156.4787 | -187.7587
|  | CHICHESTER & HUNSTON | HT |  |  |  | 187.8191 | 150.018 | 143.0475 | 134.8759 | 125.5149 | 70.5917 | 57.7917 | 45.0128 | 35.1717 | 20.0359 | -49.5272 | -132.7799 | -166.6904 | 130.2487 | 90.6624 | 81.3592 | 69.7582 | 57.7455 | -6.4471 | -20.8534 | -35.3229 | -46.3766 | -63.6829 | -145.0776 | -233.1934 | -271.8945 | 142.1497 | 102.4687 | 93.0403 | 81.4603 | 69.5508 | 7.3687 | -6.9271 | -21.2397 | -32.2071 | -49.4134 | -130.7745 | -218.8997 | -257.5734
|  | CHICHESTER & HUNSTON | HE |  |  |  | 191.5328 | 154.0096 | 148.2654 | 142.7043 | 136.3243 | 94.9201 | 85.1033 | 75.9043 | 67.8664 | 60.4054 | 11.158 | -63.6367 | -85.7451 | 134.9392 | 95.4361 | 86.7571 | 79.1761 | 70.4539 | 18.4918 | 7.3466 | -3.0976 | -12.2029 | -20.6724 | -79.9776 | -159.1187 | -184.7639 | 145.6582 | 106.8161 | 97.6613 | 90.1171 | 81.4455 | 31.1508 | 20.0866 | 9.7297 | 0.71395 | -7.6797 | -66.6587 | -145.4292 | -171.0524
|  | CHICHESTER & HUNSTON | CF |  |  |  | 192.517 | 157.5212 | 153.9075 | 151.2643 | 148.5096 | 145.4896 | 142.1738 | 138.8812 | 135.6538 | 132.358 | 110.3464 | 39.277 | 25.7022 | 138.3508 | 99.6508 | 93.7076 | 90.4624 | 87.1076 | 83.3982 | 79.3592 | 75.3445 | 71.0866 | 66.5034 | 37.4382 | -37.5439 | -53.2755 | 148.4876 | 111.0245 | 104.3024 | 101.1845 | 97.9529 | 94.3855 | 90.355 | 86.3182 | 82.0192 | 77.4697 | 48.7139 | -25.5576 | -41.0776
CHICKERELL GSP | CHICKERELL BSP | CHICKERELL BSP | MINIMUM HEADROOM | SY 65479 80511 | YES | 100.7768 | 57.3063 | 40.2368 | 35.0768 | 18.9137 | 12.9737 | 6.8811 | 1.4568 | -4.6337 | -9.5905 | -14.4211 | -49.4295 | -81.7358 | -101.5674 | 31.0526 | 7.9589 | 3.8147 | -12.9832 | -19.6032 | -26.3442 | -32.2747 | -39.0484 | -44.5042 | -49.8263 | -89.4074 | -124.1295 | -146.5726 | 33.4063 | 13.6632 | 7.56 | -9.2411 | -15.8653 | -22.64 | -28.6084 | -35.4232 | -40.9221 | -46.2926 | -86.1821 | -121.2653 | -143.8505
|  | CHICKERELL BSP | EE |  |  |  | 69.1779 | 50.8032 | 45.7495 | 27.6116 | 22.5 | 17.4126 | 13.0263 | 8.5505 | 3.8895 | -0.63579 | -29.0032 | -63.3758 | -80.0958 | 48.7274 | 21.8137 | 16.1505 | -1.9947 | -7.6916 | -13.3 | -18.0758 | -22.9579 | -28.0611 | -33.0326 | -64.8147 | -102.0074 | -120.98 | 48.0653 | 25.5642 | 19.8979 | 1.1126 | -4.5895 | -10.2358 | -15.06 | -19.9989 | -25.1611 | -30.1958 | -62.4042 | -100.0958 | -119.2347
|  | CHICKERELL BSP | HT |  |  |  | 61.1937 | 40.8074 | 35.0768 | 18.9137 | 12.9737 | 6.8811 | 1.4568 | -4.6337 | -9.5905 | -14.4211 | -49.4295 | -81.7358 | -101.5674 | 31.0526 | 10.2232 | 3.8147 | -12.9832 | -19.6032 | -26.3442 | -32.2747 | -39.0484 | -44.5042 | -49.8263 | -89.4074 | -124.1295 | -146.5726 | 34.8021 | 13.9705 | 7.56 | -9.2411 | -15.8653 | -22.64 | -28.6084 | -35.4232 | -40.9221 | -46.2926 | -86.1821 | -121.2653 | -143.8505
|  | CHICKERELL BSP | HE |  |  |  | 70.1611 | 53.0968 | 49.6979 | 35.1074 | 30.8505 | 26.5789 | 23.0674 | 19.4747 | 15.7421 | 12.1421 | -11.3558 | -41.0116 | -54.2558 | 50.0126 | 25.1126 | 20.4642 | 5.3747 | 0.60737 | -4.12 | -7.9684 | -11.9253 | -16.0642 | -20.0695 | -46.8389 | -79.3263 | -94.5042 | 49.0505 | 28.8653 | 24.2168 | 9.1242 | 4.3547 | -0.39895 | -4.2737 | -8.2547 | -12.4179 | -16.4526 | -43.4053 | -76.0453 | -91.3526
|  | CHICKERELL BSP | CF |  |  |  | 57.3063 | 40.2368 | 53.4611 | 41.3579 | 39.2642 | 37.1863 | 35.3 | 33.2684 | 31.0411 | 28.7189 | 9.9632 | -9.5463 | -18.3253 | 32.5979 | 7.9589 | 25.2095 | 12.3589 | 10.0126 | 7.7137 | 5.6368 | 3.3916 | 0.91263 | -1.6874 | -23.1442 | -43.8621 | -53.9179 | 33.4063 | 13.6632 | 28.9621 | 16.1116 | 13.7632 | 11.4526 | 9.3653 | 7.1032 | 4.6126 | 2.0042 | -19.5179 | -40.3105 | -50.4579
MELKSHAM GSP | CHIPPENHAM | CHIPPENHAM | MINIMUM HEADROOM | ST 92629 74275 | YES | 234.9663 | -0.84947 | -15.2158 | -118.1568 | -161.1274 | -183.9032 | -219.4232 | -262.2221 | -266.4632 | -271.4305 | -274.6368 | -305.9747 | -361.7726 | -376.74 | -41.7558 | -56.5074 | -170.6905 | -220.8411 | -247.6358 | -289.0695 | -339.0379 | -343.6358 | -349.0789 | -351.66 | -386.6305 | -443.1958 | -460.0158 | -36.8747 | -51.6263 | -165.8389 | -216 | -242.7526 | -284.1653 | -334.12 | -338.7937 | -344.3211 | -346.8389 | -382.4337 | -439.1958 | -456.2389
|  | CHIPPENHAM | EE |  |  |  | 54.9758 | 16.9989 | -84.7537 | -125.2905 | -183.9032 | -219.4232 | -262.2221 | -266.4632 | -271.4305 | -274.6368 | -305.9747 | -361.7726 | -376.74 | 30.4116 | -18.7242 | -131.6874 | -179.02 | -247.6358 | -289.0695 | -339.0379 | -343.6358 | -349.0789 | -351.66 | -386.6305 | -443.1958 | -460.0158 | 36.0726 | -13.8347 | -126.8305 | -174.1811 | -242.7526 | -284.1653 | -334.12 | -338.7937 | -344.3211 | -346.8389 | -382.4337 | -439.1958 | -456.2389
|  | CHIPPENHAM | HT |  |  |  | -0.84947 | -15.2158 | -118.1568 | -161.1274 | -166.0789 | -172.34 | -182.16 | -189.4758 | -194.1705 | -220.1642 | -249.2737 | -313.9611 | -327.0147 | -41.7558 | -56.5074 | -170.6905 | -220.8411 | -226.3411 | -233.2958 | -244.4147 | -252.6337 | -257.7832 | -288.0011 | -320.4726 | -391.0063 | -405.4189 | -36.8747 | -51.6263 | -165.8389 | -216 | -221.4958 | -228.4926 | -239.6495 | -247.9147 | -253.1253 | -283.3684 | -316.2747 | -387.7726 | -402.3874
|  | CHIPPENHAM | HE |  |  |  | 55.8453 | 19.1179 | -81.7442 | -83.94 | -105.1432 | -140.2579 | -152.0411 | -155.5484 | -159.7726 | -163.7095 | -189.6611 | -248.8126 | -260.7558 | 31.8442 | -16.4568 | -128.4589 | -130.8505 | -155.5453 | -196.4968 | -210.0747 | -213.9337 | -218.6505 | -223.0558 | -252.5884 | -318.7211 | -332.2611 | 37.5221 | -11.5653 | -123.5916 | -125.9874 | -150.6884 | -191.6905 | -205.3053 | -209.2032 | -213.9589 | -218.4021 | -248.1779 | -315.1632 | -328.8789
|  | CHIPPENHAM | CF |  |  |  | 56.3547 | 45.3421 | -78.9937 | -80.0505 | -81.1979 | -113.4789 | -115.1221 | -116.8095 | -118.4347 | -120.3305 | -130.3695 | -175.8547 | -182.8379 | 32.7284 | 21.0537 | -125.4642 | -126.6137 | -127.8684 | -165.6358 | -167.4411 | -169.2905 | -171.0737 | -173.18 | -184.3926 | -231.3474 | -239.2232 | 38.2032 | 26.7242 | -120.5968 | -121.7463 | -123.0021 | -160.8021 | -162.6211 | -164.4916 | -166.2895 | -168.4105 | -179.7063 | -226.7768 | -234.7726
MANNINGTON GSP | CHRISTCHURCH BSP | CHRISTCHURCH BSP | MINIMUM HEADROOM | SZ 15716 93165 | YES | 94.4116 | 107.0547 | 105.4337 | 103.8 | 102.0611 | 100.26 | 100.3168 | 97.1674 | 94.0232 | 22.8968 | 19.8821 | -95.1484 | -107.9126 | -119.5263 | 88.6526 | 85.4263 | 82.1 | 78.5011 | 74.7053 | 74.6053 | 71.1505 | 67.7505 | -15.9821 | -19.2516 | -137.2295 | -151.4189 | -164.4863 | 93.1568 | 89.88 | 86.5011 | 82.8411 | 79.0316 | 78.5895 | 75.0937 | 71.6874 | -11.9737 | -15.2442 | -133.2568 | -147.5105 | -160.5905
|  | CHRISTCHURCH BSP | EE |  |  |  | 107.6737 | 106.4053 | 105.0611 | 103.6326 | 102.1337 | 100.5579 | 99.0274 | 97.3232 | 94.9032 | 93.1863 | -8.8916 | -23.32 | -32.1884 | 89.9116 | 87.3389 | 84.5905 | 81.5747 | 78.3758 | 75.9821 | 73.4368 | 70.9347 | 68.3453 | 66.6695 | -36.0221 | -52.3295 | -62.3389 | 93.8568 | 91.8242 | 89.0284 | 85.9611 | 82.7116 | 80.2979 | 77.7432 | 75.2316 | 72.6295 | 70.78 | -32.1979 | -48.6116 | -58.6537
|  | CHRISTCHURCH BSP | HT |  |  |  | 107.0547 | 105.4337 | 103.8 | 102.0611 | 100.26 | 100.3168 | 97.1674 | 94.0232 | 22.8968 | 19.8821 | -95.1484 | -107.9126 | -119.5263 | 88.6526 | 85.4263 | 82.1 | 78.5011 | 74.7053 | 74.6053 | 71.1505 | 67.7505 | -15.9821 | -19.2516 | -137.2295 | -151.4189 | -164.4863 | 93.1568 | 89.88 | 86.5011 | 82.8411 | 79.0316 | 78.5895 | 75.0937 | 71.6874 | -11.9737 | -15.2442 | -133.2568 | -147.5105 | -160.5905
|  | CHRISTCHURCH BSP | HE |  |  |  | 108.4989 | 107.62 | 106.6463 | 105.5705 | 104.4116 | 103.1579 | 101.9611 | 100.8284 | 99.7684 | 99.5589 | -28.5642 | -39.6937 | -45.7274 | 91.5937 | 89.8179 | 87.8295 | 85.5368 | 83.0316 | 81.2989 | 79.4421 | 77.6884 | 75.9611 | 75.1684 | -60.3674 | -73.1505 | -80.0337 | 94.7326 | 93.8 | 92.32 | 89.9905 | 87.4432 | 85.6884 | 83.8063 | 82.0305 | 80.2789 | 79.3558 | -56.4863 | -69.2821 | -76.1863
|  | CHRISTCHURCH BSP | CF |  |  |  | 108.9832 | 108.4737 | 107.9453 | 107.3937 | 106.8263 | 106.2284 | 105.6189 | 105.02 | 104.4295 | 103.8379 | 9.2642 | 8.8137 | 4.7463 | 92.5779 | 91.5105 | 90.3821 | 89.1547 | 87.8663 | 86.8137 | 85.6389 | 84.4453 | 83.34 | 82.2768 | -13.9432 | -17.0326 | -21.6537 | 95.2463 | 94.7042 | 94.1389 | 93.5474 | 92.3547 | 91.2853 | 90.0895 | 88.8758 | 87.7505 | 86.6716 | -9.7137 | -13.0916 | -17.7516
IVER 132KV | CIPPENHAM | CIPPENHAM | MINIMUM HEADROOM | SU 96266 79634 | YES | 1.0516 | 98.8126 | 98.2832 | 97.7484 | 97.1789 | 96.5895 | 95.9789 | 95.3621 | 94.8189 | 94.1611 | 93.0874 | 88.1526 | 83.6916 | 79.5568 | 90.8105 | 90.2316 | 88.7663 | 86.9379 | 85.0221 | 83.5832 | 82.5558 | 81.3368 | 80.0863 | 78.9042 | 73.4221 | 68.4211 | 63.7474 | 92.0779 | 91.5032 | 90.9126 | 89.4305 | 87.5147 | 86.0737 | 85.0474 | 83.8263 | 82.5768 | 81.3926 | 75.9063 | 70.9011 | 66.2242
|  | CIPPENHAM | EE |  |  |  | 99.0116 | 98.5947 | 98.1526 | 97.6832 | 97.1884 | 96.6758 | 96.18 | 95.7042 | 95.2463 | 94.8389 | 91.0516 | 87.5737 | 84.4116 | 91.0242 | 90.5705 | 89.6674 | 88.2347 | 86.5126 | 85.26 | 84.1611 | 83.0926 | 82.0168 | 81.0189 | 76.6021 | 72.6926 | 69.1 | 92.2926 | 91.8368 | 91.3463 | 90.7274 | 89.0053 | 87.7505 | 86.6537 | 85.5832 | 84.5063 | 83.5074 | 79.0853 | 75.1705 | 71.5758
|  | CIPPENHAM | HT |  |  |  | 98.8126 | 98.2832 | 97.7484 | 97.1789 | 96.5895 | 95.9789 | 95.3621 | 94.8189 | 94.1611 | 93.0874 | 88.1526 | 83.6916 | 79.5568 | 90.8105 | 90.2316 | 88.7663 | 86.9379 | 85.0221 | 83.5832 | 82.5558 | 81.3368 | 80.0863 | 78.9042 | 73.4221 | 68.4211 | 63.7474 | 92.0779 | 91.5032 | 90.9126 | 89.4305 | 87.5147 | 86.0737 | 85.0474 | 83.8263 | 82.5768 | 81.3926 | 75.9063 | 70.9011 | 66.2242
|  | CIPPENHAM | HE |  |  |  | 99.2768 | 98.9821 | 98.6558 | 98.2968 | 97.9095 | 97.4968 | 97.1011 | 96.7274 | 96.3789 | 96.08 | 94.9726 | 92.5021 | 90.2968 | 91.3105 | 90.9863 | 90.6211 | 89.6611 | 88.4242 | 87.4211 | 86.5768 | 85.4821 | 84.7084 | 84.0347 | 80.9147 | 78.1105 | 75.5789 | 92.5789 | 92.2537 | 91.8874 | 91.4811 | 90.9168 | 89.9137 | 89.0684 | 87.9737 | 87.1989 | 86.5253 | 83.4032 | 80.5968 | 78.0632
|  | CIPPENHAM | CF |  |  |  | 99.4242 | 99.2474 | 99.0642 | 98.8726 | 98.6758 | 98.4705 | 98.2621 | 98.0579 | 97.8547 | 97.6516 | 96.7453 | 96.2916 | 96.0389 | 91.4726 | 91.2811 | 91.0811 | 90.8695 | 90.6411 | 90.1105 | 89.4579 | 88.8716 | 88.4895 | 88.0284 | 85.7021 | 83.7389 | 82.0274 | 92.7411 | 92.5495 | 92.3484 | 92.1368 | 91.9074 | 91.6716 | 91.4368 | 91.2105 | 90.9811 | 90.52 | 88.1926 | 86.2284 | 84.5158
MINETY GSP | CIRENCESTER BSP | CIRENCESTER BSP | MINIMUM HEADROOM | SP 02701 00368 | YES | 107.5884 | -18.3632 | -71.9211 | -85.5495 | -149.9895 | -231.5484 | -234.9368 | -238.3705 | -241.8989 | -245.1684 | -254.1095 | -291.7758 | -308.0442 | -317.0642 | -53.9253 | -110.2232 | -126.1779 | -198.5874 | -294.2495 | -298 | -301.7979 | -305.7263 | -309.3611 | -319.6779 | -363.0242 | -381.2811 | -391.3758 | -49.5347 | -105.8389 | -121.8032 | -194.2295 | -289.82 | -293.5916 | -297.4147 | -301.3663 | -305.0305 | -315.3653 | -358.8737 | -377.3747 | -387.5611
|  | CIRENCESTER BSP | EE |  |  |  | 23.4126 | -69.4705 | -85.5495 | -112.3621 | -156.8779 | -159.7621 | -162.5895 | -165.3453 | -167.9863 | -170.5653 | -184.8695 | -207.0158 | -214.8116 | -4.86 | -107.4442 | -126.1779 | -154.5716 | -206.6768 | -209.8579 | -212.9663 | -215.9937 | -218.8811 | -221.7084 | -237.54 | -262.6505 | -271.3989 | -0.45579 | -103.06 | -121.8032 | -150.2053 | -202.3263 | -205.5337 | -208.6758 | -211.7379 | -214.6726 | -217.5411 | -233.6674 | -259.1284 | -267.9789
|  | CIRENCESTER BSP | HT |  |  |  | -18.3632 | -71.9211 | -74.1379 | -149.9895 | -231.5484 | -234.9368 | -238.3705 | -241.8989 | -245.1684 | -254.1095 | -291.7758 | -308.0442 | -317.0642 | -53.9253 | -110.2232 | -112.6526 | -198.5874 | -294.2495 | -298 | -301.7979 | -305.7263 | -309.3611 | -319.6779 | -363.0242 | -381.2811 | -391.3758 | -49.5347 | -105.8389 | -108.2684 | -194.2295 | -289.82 | -293.5916 | -297.4147 | -301.3663 | -305.0305 | -315.3653 | -358.8737 | -377.3747 | -387.5611
|  | CIRENCESTER BSP | HE |  |  |  | 24.3537 | -56.4337 | -57.2853 | -83.6632 | -84.9695 | -87.34 | -89.6568 | -91.9411 | -94.0884 | -96.1716 | -122.5842 | -142.0158 | -148.1432 | -3.8411 | -92.2758 | -93.1758 | -121.1032 | -122.5179 | -125.1421 | -127.7137 | -130.2526 | -132.6347 | -134.9579 | -165.4516 | -187.9232 | -194.8558 | 0.56526 | -87.8874 | -88.7874 | -116.7168 | -118.1337 | -120.7737 | -123.3642 | -125.9232 | -128.3221 | -130.6642 | -161.2916 | -183.8632 | -190.8853
|  | CIRENCESTER BSP | CF |  |  |  | 24.8758 | -13.0768 | -54.8074 | -72.4505 | -73.3779 | -74.4547 | -75.5684 | -76.6989 | -77.8284 | -79.0632 | -99.1432 | -102.7568 | -106.5126 | -3.2811 | -41.4126 | -90.4368 | -108.1632 | -109.1947 | -110.3863 | -111.62 | -112.8747 | -114.1295 | -115.5105 | -138.7568 | -142.7526 | -146.9937 | 1.1242 | -36.9421 | -85.9821 | -103.7095 | -104.7411 | -105.9421 | -107.1863 | -108.4463 | -109.7105 | -111.0968 | -134.3926 | -138.5053 | -142.8053
FAWLEY GSP | COWES & WOOTTON COMMON BSP | COWES & WOOTTON COMMON BSP | MINIMUM HEADROOM | SZ 50519 94250 | YES | 67.7611 | -29.6011 | -35.5232 | -92.7853 | -99.4368 | -104.9484 | -36.7537 | -47.1358 | -57.0653 | -67.4568 | -77.56 | -176.2642 | -202.1905 | -224.4926 | -103.3284 | -109.8263 | -167.7316 | -175.0537 | -180.7747 | -94.8095 | -102.4653 | -113.6 | -125.3158 | -136.7 | -245.2979 | -273.8989 | -298.9137 | -97.0179 | -103.5126 | -161.4179 | -168.7379 | -174.7989 | -96.62 | -108.6358 | -119.8179 | -131.5874 | -143.0284 | -253.4484 | -282.4579 | -307.6274
|  | COWES & WOOTTON COMMON BSP | EE |  |  |  | 103.7579 | 73.3611 | 18.7726 | -6.9526 | -11.2168 | -34.5242 | -41.0926 | -47.3242 | -53.4063 | -59.8558 | -58.6895 | -82.2789 | -100.1189 | 58.2474 | 21.4168 | -34.9463 | -66.5095 | -70.8505 | -94.8095 | -102.0137 | -108.8274 | -115.4716 | -122.8874 | -107.7779 | -133.5537 | -153.6137 | 64.4684 | 27.7568 | -28.54 | -60.2926 | -64.9747 | -88.9716 | -96.2305 | -103.1074 | -109.8189 | -117.3726 | -116.0874 | -142.5958 | -162.8274
|  | COWES & WOOTTON COMMON BSP | HT |  |  |  | -29.6011 | -35.5232 | -92.7853 | -99.4368 | -104.9484 | -36.7537 | -47.1358 | -57.0653 | -67.4568 | -77.56 | -176.2642 | -202.1905 | -224.4926 | -103.3284 | -109.8263 | -167.7316 | -175.0537 | -180.7747 | -90.6284 | -102.4653 | -113.6 | -125.3158 | -136.7 | -245.2979 | -273.8989 | -298.9137 | -97.0179 | -103.5126 | -161.4179 | -168.7379 | -174.7989 | -96.62 | -108.6358 | -119.8179 | -131.5874 | -143.0284 | -253.4484 | -282.4579 | -307.6274
|  | COWES & WOOTTON COMMON BSP | HE |  |  |  | 105.8558 | 76.4421 | 22.8042 | -0.098947 | -3.1484 | -8.6084 | -30.6642 | -35.6863 | -41.1947 | -45.7263 | -76.5621 | -55.4905 | -68.6768 | 61.2137 | 25.9737 | -28.9168 | -59.0463 | -62.0642 | -68.0853 | -90.7042 | -96.2453 | -102.6832 | -107.7053 | -147.2863 | -105.6032 | -120.4305 | 66.9916 | 32.2516 | -22.5884 | -52.8232 | -56.1832 | -62.2295 | -84.8768 | -90.4421 | -96.9737 | -102.0263 | -143.1116 | -113.6147 | -128.72
|  | COWES & WOOTTON COMMON BSP | CF |  |  |  | 107.3095 | 105.9811 | 26.7768 | 24.4811 | 22.88 | 21.0789 | 19.2063 | 17.3316 | -6.8611 | -9.58 | -24.4989 | -32.7537 | -41.2758 | 63.3221 | 61.4611 | -23.2747 | -27.4916 | -30.0011 | -32.7442 | -35.6253 | -38.5063 | -67.1295 | -70.1484 | -86.8726 | -95.8368 | -105.5011 | 68.5905 | 67.1421 | -17.0411 | -21.4358 | -23.9095 | -26.6295 | -29.4884 | -32.34 | -61.2284 | -64.2568 | -81.0421 | -90.4379 | -100.1979
COWLEY GSP | COWLEY LOCAL (2 X 45) | COWLEY LOCAL (2 X 45) | MINIMUM HEADROOM | SP 56113 03074 | YES | 60.4526 | 81.7684 | 80.2074 | 78.4179 | 17.4095 | -34.1095 | -35.8189 | -37.4158 | -40.1916 | -46.1421 | -51.6242 | -73.5221 | -89.6789 | -93.4642 | 72.92 | 71.16 | 69.1221 | 7.7463 | -53.6295 | -55.5179 | -57.2168 | -60.3758 | -67.2811 | -73.64 | -99.0316 | -119.5747 | -123.8137 | 73.6842 | 71.9242 | 69.8905 | 8.5189 | -52.7411 | -54.6295 | -56.3168 | -59.4716 | -66.3674 | -72.7158 | -98.0779 | -118.9758 | -123.2158
|  | COWLEY LOCAL (2 X 45) | EE |  |  |  | 92.5211 | 80.8379 | 79.24 | 18.4211 | 15.3105 | 13.9179 | 12.5316 | 10.1842 | 4.4737 | -0.80632 | -18.0863 | -29.5716 | -32.2979 | 85.7558 | 71.8442 | 70.0168 | 8.8474 | 5.2053 | 3.6421 | 2.0842 | -0.64211 | -7.4305 | -13.7158 | -32.6284 | -45.8474 | -48.9053 | 86.5989 | 72.6105 | 70.7853 | 9.6189 | 5.9821 | 4.4189 | 2.8611 | 0.13684 | -6.6432 | -12.9189 | -31.1916 | -44.4105 | -47.4768
|  | COWLEY LOCAL (2 X 45) | HT |  |  |  | 81.7684 | 80.2074 | 78.4179 | 17.4095 | -34.1095 | -35.8189 | -37.4158 | -40.1916 | -46.1421 | -51.6242 | -73.5221 | -89.6789 | -93.4642 | 72.92 | 71.16 | 69.1221 | 7.7463 | -53.6295 | -55.5179 | -57.2168 | -60.3758 | -67.2811 | -73.64 | -99.0316 | -119.5747 | -123.8137 | 73.6842 | 71.9242 | 69.8905 | 8.5189 | -52.7411 | -54.6295 | -56.3168 | -59.4716 | -66.3674 | -72.7158 | -98.0779 | -118.9758 | -123.2158
|  | COWLEY LOCAL (2 X 45) | HE |  |  |  | 82.7537 | 81.6789 | 80.3411 | 19.7737 | 16.8968 | 12.6737 | 11.4695 | 10.2926 | 6.9337 | 1.9053 | -23.1221 | -33.8958 | -35.5389 | 73.9968 | 72.7621 | 71.2189 | 10.3221 | 6.9326 | 1.9232 | 0.55789 | -0.78105 | -4.7611 | -10.7674 | -43.0168 | -55.6642 | -57.5221 | 74.7589 | 73.5263 | 71.9853 | 11.0916 | 7.7084 | 2.7063 | 1.3411 | 0.0042105 | -3.9705 | -9.9663 | -42.6968 | -55.3463 | -57.2074
|  | COWLEY LOCAL (2 X 45) | CF |  |  |  | 94.4053 | 92.94 | 92.2632 | 22.4011 | 21.1421 | 19.3811 | 17.0674 | 14.3137 | 11.3358 | 8.3684 | -4.2295 | -10.8326 | -11.9116 | 87.8747 | 86.1916 | 85.4232 | 13.3526 | 11.8726 | 9.7884 | 7.0368 | 3.7537 | 0.2 | -3.3453 | -18.3737 | -26.2547 | -27.48 | 88.7674 | 87.0368 | 86.2568 | 14.1189 | 12.6421 | 10.56 | 7.8116 | 4.5337 | 0.98526 | -2.5516 | -17.5579 | -25.4274 | -26.6558
COWLEY GSP | COWLEY LOCAL (2 X 90) | COWLEY LOCAL (2 X 90) | MINIMUM HEADROOM | SP 56113 03074 | YES | 1.4253 | 109.4684 | 108.6232 | 107.7674 | 70.8968 | 69.0295 | 67.1242 | 58.3621 | 55.2695 | 52.3589 | 49.5758 | 35.5158 | 25.5295 | 14.3526 | 93.5621 | 90.0505 | 88.4232 | 38.3 | 36.2432 | 34.1663 | 23.8168 | 20.2789 | 16.9463 | 13.7537 | -2.4789 | -13.8263 | -27.8011 | 96.3811 | 94.5284 | 92.9021 | 42.7611 | 40.7042 | 38.5747 | 28.2179 | 24.6747 | 21.3347 | 18.1358 | 1.8705 | -9.5211 | -23.8263
|  | COWLEY LOCAL (2 X 90) | EE |  |  |  | 109.7642 | 109.0884 | 108.3726 | 107.6074 | 106.8021 | 105.9516 | 102.3537 | 98.1484 | 94.8074 | 92.2053 | 82.3432 | 73.6768 | 66.6274 | 93.8768 | 92.0916 | 90.0884 | 88.36 | 86.3621 | 83.9716 | 76.5768 | 71.6821 | 67.8211 | 64.8389 | 54.5084 | 44.5421 | 36.3463 | 96.7011 | 95.9211 | 94.5663 | 92.8389 | 90.84 | 88.4432 | 81.0421 | 76.1379 | 72.2705 | 69.28 | 59.3853 | 49.36 | 41.1432
|  | COWLEY LOCAL (2 X 90) | HT |  |  |  | 109.4684 | 108.6232 | 107.7674 | 70.8968 | 69.0295 | 67.1242 | 58.3621 | 55.2695 | 52.3589 | 49.5758 | 35.5158 | 25.5295 | 14.3526 | 93.5621 | 90.0505 | 88.4232 | 38.3 | 36.2432 | 34.1663 | 23.8168 | 20.2789 | 16.9463 | 13.7537 | -2.4789 | -13.8263 | -27.8011 | 96.3811 | 94.5284 | 92.9021 | 42.7611 | 40.7042 | 38.5747 | 28.2179 | 24.6747 | 21.3347 | 18.1358 | 1.8705 | -9.5211 | -23.8263
|  | COWLEY LOCAL (2 X 90) | HE |  |  |  | 110.1716 | 109.6821 | 109.14 | 108.5421 | 107.8958 | 107.1989 | 105.3368 | 101.4305 | 98.6116 | 96.3674 | 82.9937 | 76.1347 | 70.7095 | 94.3095 | 93.4842 | 91.8937 | 90.5937 | 89.0189 | 87.0242 | 79.8789 | 75.3042 | 72.0316 | 69.4358 | 52.6989 | 44.6516 | 38.2642 | 97.14 | 96.5621 | 95.9589 | 95.0716 | 93.4979 | 91.5 | 84.3474 | 79.7695 | 76.4937 | 73.8926 | 56.6263 | 48.5726 | 42.1779
|  | COWLEY LOCAL (2 X 90) | CF |  |  |  | 110.4158 | 110.12 | 109.8126 | 109.4947 | 109.1653 | 108.8189 | 108.4653 | 108.1168 | 107.7737 | 107.4284 | 98.2411 | 93.8663 | 90.1916 | 94.5579 | 94.24 | 93.9211 | 93.5916 | 93.1853 | 92.2421 | 90.8389 | 89.0716 | 86.7095 | 84.1674 | 71.4674 | 66.3779 | 62.0537 | 97.3895 | 97.0653 | 96.7432 | 96.4105 | 96.0579 | 95.6768 | 95.2611 | 93.5453 | 91.1821 | 88.6379 | 75.9284 | 70.7779 | 66.4432
BRAMLEY (FLEE) | COXMOOR WOOD BSP | COXMOOR WOOD BSP | MINIMUM HEADROOM | SU 78324 50817 | YES | 25.5463 | 107.9158 | 106.5137 | 105.1011 | 103.5947 | 102.0453 | 100.1863 | 96.7137 | 93.0295 | 90.8621 | 78.5116 | 69.4758 | 36.2179 | 27.8979 | 88.7716 | 85.7084 | 82.8063 | 79.8463 | 76.9147 | 73.7495 | 69.9705 | 65.9126 | 63.62 | 48.8632 | 39.2568 | 5.0653 | -4.2863 | 93.6989 | 90.7484 | 87.9011 | 84.9926 | 82.1105 | 78.98 | 75.2642 | 71.2684 | 68.9526 | 54.1474 | 44.2989 | 9.8484 | 0.41263
|  | COXMOOR WOOD BSP | EE |  |  |  | 108.4611 | 107.3695 | 106.2095 | 104.9726 | 103.6895 | 102.3 | 100.9326 | 99.6263 | 97.5442 | 78.5116 | 69.4758 | 36.2179 | 27.8979 | 89.8947 | 87.4253 | 85.0642 | 82.6979 | 80.4579 | 78.1042 | 75.6758 | 73.4053 | 71.0768 | 48.8632 | 39.2568 | 5.0653 | -4.2863 | 94.2758 | 92.4368 | 90.1179 | 87.7926 | 85.58 | 83.2495 | 80.8421 | 78.5842 | 76.2684 | 54.1474 | 44.2989 | 9.8484 | 0.41263
|  | COXMOOR WOOD BSP | HT |  |  |  | 107.9158 | 106.5137 | 105.1011 | 103.5947 | 102.0453 | 100.1863 | 96.7137 | 93.0295 | 90.8621 | 88.66 | 74.4295 | 38.7011 | 31.9832 | 88.7716 | 85.7084 | 82.8063 | 79.8463 | 76.9147 | 73.7495 | 69.9705 | 65.9126 | 63.62 | 61.2747 | 45.6032 | 8.56 | 1.2537 | 93.6989 | 90.7484 | 87.9011 | 84.9926 | 82.1105 | 78.98 | 75.2642 | 71.2684 | 68.9526 | 66.5821 | 50.7484 | 13.5179 | 6.1337
|  | COXMOOR WOOD BSP | HE |  |  |  | 109.2063 | 108.4716 | 107.6589 | 106.7579 | 105.7884 | 104.7095 | 103.6779 | 102.7 | 101.7832 | 100.9811 | 96.9305 | 67.0074 | 61.0189 | 91.3674 | 89.6579 | 88.0305 | 86.3421 | 84.7389 | 83.0453 | 81.3884 | 79.8632 | 78.2789 | 76.76 | 70.4547 | 39.6958 | 32.8979 | 95.0642 | 94.2726 | 93.0295 | 91.3695 | 89.7895 | 88.1074 | 86.4632 | 84.9463 | 83.3768 | 81.8705 | 75.6137 | 44.8726 | 38.0063
|  | COXMOOR WOOD BSP | CF |  |  |  | 109.6358 | 109.2221 | 108.7916 | 108.3484 | 107.8895 | 107.3895 | 106.8789 | 106.3779 | 105.8811 | 105.3916 | 103.1716 | 78.1453 | 74.0726 | 92.1884 | 91.2032 | 90.3084 | 89.4389 | 88.6011 | 87.7126 | 86.7758 | 85.8611 | 84.9263 | 83.9968 | 79.3305 | 51.7032 | 47.0768 | 95.5158 | 95.0695 | 94.6116 | 94.1432 | 93.5884 | 92.7084 | 91.78 | 90.8779 | 89.9516 | 89.0379 | 84.4337 | 56.8884 | 52.3474
IVER 132KV | DENHAM | DENHAM B | MINIMUM HEADROOM | TQ 01785 87618 | YES | 0.15263 | 0 | 0 | 0 | 0 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 0 | 0 | 0 | 0 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 0 | 0 | 0 | 0 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474
|  | DENHAM B | EE |  |  |  | 0 | 0 | 0 | 0 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 0 | 0 | 0 | 0 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 0 | 0 | 0 | 0 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474
|  | DENHAM B | HT |  |  |  | 0 | 0 | 0 | 0 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 0 | 0 | 0 | 0 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 0 | 0 | 0 | 0 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474
|  | DENHAM B | HE |  |  |  | 0 | 0 | 0 | 0 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 0 | 0 | 0 | 0 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 0 | 0 | 0 | 0 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474
|  | DENHAM B | CF |  |  |  | 0 | 0 | 0 | 0 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 0 | 0 | 0 | 0 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 0 | 0 | 0 | 0 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474 | 89.8474
IVER 132KV | DENHAM | DENHAM | MINIMUM HEADROOM | TQ 01785 87618 | YES | 40.64 | 69.2053 | 68.28 | 67.3453 | 58.3653 | 56.8684 | 55.4295 | 30.7463 | 29.3516 | 27.9137 | 26.5684 | 20.6926 | 15.6063 | 11.3211 | 52.5168 | 51.2011 | 49.0568 | 28.2874 | 26.6495 | 25.1242 | -3.6947 | -5.1747 | -6.7116 | -8.1547 | -14.4884 | -20.0221 | -24.7874 | 57.9663 | 56.5968 | 54.5389 | 34 | 32.3621 | 30.8295 | 1.9979 | 0.50421 | -1.0411 | -2.5 | -8.9095 | -14.5305 | -19.3284
|  | DENHAM | EE |  |  |  | 69.5611 | 68.8368 | 68.0716 | 58.3653 | 56.8684 | 55.4295 | 30.7463 | 29.3516 | 27.9137 | 26.5684 | 20.6926 | 15.6063 | 11.3211 | 53.0116 | 52.0053 | 50.6579 | 28.2874 | 26.6495 | 25.1242 | -3.6947 | -5.1747 | -6.7116 | -8.1547 | -14.4884 | -20.0221 | -24.7874 | 58.3253 | 57.5737 | 56.0768 | 34 | 32.3621 | 30.8295 | 1.9979 | 0.50421 | -1.0411 | -2.5 | -8.9095 | -14.5305 | -19.3284
|  | DENHAM | HT |  |  |  | 69.2053 | 68.28 | 67.3453 | 81.3558 | 80.4863 | 79.4084 | 78.3284 | 77.3747 | 76.5074 | 75.7021 | 68.9442 | 62.5295 | 56.8284 | 52.5168 | 51.2011 | 49.0568 | 61.8147 | 59.7884 | 57.8853 | 55.9716 | 54.1021 | 52.3705 | 50.6442 | 42.6684 | 35.5389 | 29.1768 | 57.9663 | 56.5968 | 54.5389 | 67.3884 | 65.4442 | 63.5947 | 61.6832 | 59.8074 | 58.0684 | 56.3316 | 48.3042 | 41.1063 | 34.7158
|  | DENHAM | HE |  |  |  | 70.0537 | 69.5642 | 69.0274 | 83.4284 | 82.9379 | 82.2379 | 64.5632 | 63.56 | 62.52 | 61.5653 | 57.6211 | 54.4158 | 51.6789 | 53.6768 | 53.0095 | 52.2432 | 66.3811 | 65.1926 | 64.0884 | 35.6895 | 34.6274 | 33.5137 | 32.4863 | 28.2063 | 24.6495 | 21.58 | 58.8179 | 58.3284 | 57.7716 | 71.7726 | 70.6347 | 69.5516 | 41.3979 | 40.3295 | 39.2126 | 38.1811 | 33.8663 | 30.2853 | 27.1905
|  | DENHAM | CF |  |  |  | 70.3347 | 70.0547 | 69.7684 | 84.4705 | 84.3126 | 83.9874 | 83.6547 | 83.3263 | 83 | 82.6768 | 81.2242 | 80.4747 | 80.0347 | 54.0358 | 53.6558 | 53.2453 | 67.8084 | 67.5232 | 67.1116 | 66.6874 | 66.1463 | 65.46 | 64.7537 | 61.3958 | 58.8211 | 56.6663 | 59.0989 | 58.8189 | 58.5326 | 73.2347 | 73.0547 | 72.7137 | 72.1589 | 71.54 | 70.8768 | 70.2 | 66.9695 | 64.5116 | 62.3432
COWLEY GSP | DRAYTON BSP | DRAYTON BSP | MINIMUM HEADROOM | SU 46684 92706 | YES | 91.72 | 84.0579 | 38.2716 | 32.2621 | 7.8095 | -133.3379 | -137.7253 | -144.2147 | -150.3789 | -127.4347 | -156.0389 | -194.0347 | -211.3368 | -229.0463 | 49.1821 | 2.6547 | -4.1221 | -30.6011 | -196.0232 | -200.5737 | -207.8811 | -214.8411 | -176.1526 | -209.4947 | -253.1274 | -272.7126 | -292.9284 | 55.4042 | 8.7011 | 1.9305 | -24.4137 | -189.6411 | -194.6137 | -201.9116 | -208.8611 | -164.8758 | -198.2284 | -241.8842 | -261.4832 | -281.7116
|  | DRAYTON BSP | EE |  |  |  | 84.7 | 39.54 | 34.1137 | 7.8095 | -16.1053 | -21.5032 | -40.7158 | -46.4484 | -51.8105 | -56.7074 | -58.6105 | -77.0695 | -91.4211 | 50.5853 | 3.9042 | -2.2347 | -30.6011 | -58.4726 | -64.46 | -86.5189 | -93.0095 | -99.0747 | -104.6158 | -94.8084 | -115.9379 | -132.3821 | 56.7989 | 10.0674 | 3.9295 | -24.4137 | -52.24 | -58.3526 | -80.8011 | -87.2853 | -93.3463 | -98.8842 | -83.5663 | -104.7295 | -121.2011
|  | DRAYTON BSP | HT |  |  |  | 84.0579 | 38.2716 | 32.2621 | 13.1337 | -133.3379 | -137.7253 | -144.2147 | -150.3789 | -127.4347 | -156.0389 | -194.0347 | -211.3368 | -229.0463 | 49.1821 | 2.6547 | -4.1221 | -23.9947 | -196.0232 | -200.5737 | -207.8811 | -214.8411 | -176.1526 | -209.4947 | -253.1274 | -272.7126 | -292.9284 | 55.4042 | 8.7011 | 1.9305 | -17.9347 | -189.6411 | -194.6137 | -201.9116 | -208.8611 | -164.8758 | -198.2284 | -241.8842 | -261.4832 | -281.7116
|  | DRAYTON BSP | HE |  |  |  | 85.5789 | 42.4505 | 41.4905 | 19.8811 | 14.3537 | 9.6411 | -8.8968 | -13.9789 | -18.6726 | -22.9221 | -21.6368 | -37.1674 | -48.7747 | 61.5758 | 15.9221 | 10.7 | -16.7853 | -23.0842 | -28.3284 | -49.6589 | -55.4411 | -60.7853 | -65.6232 | -52.4211 | -70.3474 | -83.7842 | 65.4179 | 22.0505 | 16.8621 | -10.5989 | -16.8905 | -22.2568 | -43.9737 | -49.7474 | -55.0842 | -59.9168 | -41.1105 | -59.0484 | -72.4947
|  | DRAYTON BSP | CF |  |  |  | 86.0768 | 42.5316 | 42.0232 | 26.1358 | 23.5947 | 21.1705 | 19.5368 | 16.8495 | 14.1642 | 11.5021 | 1.0758 | -5.7221 | -12.9926 | 62.1095 | 17.5811 | 14.9263 | -9.8747 | -12.7663 | -15.5189 | -17.2211 | -20.2832 | -23.3432 | -26.3758 | -37.9232 | -45.62 | -54.0505 | 65.9632 | 22.1884 | 21.2347 | -3.5137 | -6.3989 | -9.1505 | -11.0316 | -14.0863 | -17.1442 | -20.1716 | -32.1232 | -39.9358 | -48.3537
EALING GSP | EALING 22kV | EALING 22kV | MINIMUM HEADROOM | TQ 18371 79475 | NO | 0.10526 | 98.6568 | 98 | 97.3347 | 96.6295 | 94.3779 | 91.6 | 89.0158 | 87.1126 | 85.5516 | 84.0484 | 76.9537 | 70.1453 | 64.2158 | 82.8642 | 79.9653 | 77.1021 | 74.2589 | 71.1337 | 67.9895 | 65.0779 | 62.9558 | 61.2284 | 59.56 | 51.6337 | 43.7295 | 37.0158 | 86.9768 | 84.0874 | 81.1874 | 78.3074 | 75.1874 | 72.0484 | 69.1411 | 67.0211 | 65.2958 | 63.6295 | 55.7126 | 47.7705 | 41.0663
|  | EALING 22kV | EE |  |  |  | 98.9053 | 98.3905 | 97.8421 | 97.26 | 96.6368 | 95.6789 | 93.5905 | 91.4347 | 89.3179 | 87.8274 | 82.4158 | 77.8516 | 73.6305 | 83.4663 | 81.2168 | 79.2516 | 77.4474 | 75.2137 | 72.6537 | 70.3 | 67.8632 | 65.4684 | 63.8053 | 57.9968 | 52.8684 | 48.08 | 87.26 | 85.3547 | 83.3632 | 81.5389 | 79.2768 | 76.7042 | 74.3537 | 71.9211 | 69.5295 | 67.8684 | 62.1168 | 56.9947 | 52.2147
|  | EALING 22kV | HT |  |  |  | 98.6568 | 98 | 97.3347 | 96.6295 | 94.3779 | 91.6 | 89.0158 | 87.1126 | 85.5516 | 84.0484 | 76.9537 | 70.1453 | 64.2158 | 82.8642 | 79.9653 | 77.1021 | 74.2589 | 71.1337 | 67.9895 | 65.0779 | 62.9558 | 61.2284 | 59.56 | 51.6337 | 43.7295 | 37.0158 | 86.9768 | 84.0874 | 81.1874 | 78.3074 | 75.1874 | 72.0484 | 69.1411 | 67.0211 | 65.2958 | 63.6295 | 55.7126 | 47.7705 | 41.0663
|  | EALING 22kV | HE |  |  |  | 99.1705 | 98.7695 | 98.3263 | 97.8347 | 97.3074 | 96.7453 | 95.6432 | 93.7032 | 91.9463 | 90.7853 | 86.3316 | 82.4316 | 79.6284 | 84.16 | 82.2358 | 80.4842 | 78.9358 | 76.9716 | 74.66 | 72.5705 | 70.3695 | 68.3768 | 67.08 | 62.0737 | 57.2947 | 54.0853 | 87.5495 | 86.3632 | 84.6105 | 83.0442 | 81.0526 | 78.7126 | 76.6232 | 74.4242 | 72.4347 | 71.1389 | 66.14 | 61.2947 | 58.0905
|  | EALING 22kV | CF |  |  |  | 99.3137 | 99.0421 | 98.7611 | 98.4684 | 98.1663 | 97.8537 | 97.5347 | 97.2221 | 96.9105 | 96.6011 | 92.5316 | 90.0253 | 88.0958 | 84.9253 | 83.8505 | 83.0979 | 82.4874 | 81.8474 | 81.1726 | 80.4811 | 79.6937 | 78.5063 | 77.2 | 69.0695 | 66.2358 | 64.0263 | 87.7305 | 87.4116 | 87.1032 | 86.6042 | 85.9705 | 85.3042 | 84.6189 | 83.8253 | 82.6232 | 81.2989 | 73.1263 | 70.2968 | 68.0905
LALEHAM | EAST BEDFONT A | EAST BEDFONT A | MINIMUM HEADROOM | TQ 08394 73826 | YES | 0 | 83.1379 | 82.4684 | 111.7947 | 110.2137 | 108.1505 | 105.5547 | 103.0926 | 100.2442 | 97.4158 | 95.02 | 85.3147 | 79.1116 | 73.6989 | 65.7632 | 63.6642 | 91.6421 | 89.3853 | 87.0032 | 84.0874 | 81.3284 | 78.0968 | 74.8768 | 72.1611 | 61.1621 | 54.1789 | 48.0642 | 69.3411 | 68.1653 | 96.1937 | 93.9958 | 91.6789 | 88.8432 | 86.16 | 83.0274 | 79.9053 | 77.2168 | 66.2358 | 59.2632 | 53.1568
|  | EAST BEDFONT A | EE |  |  |  | 83.3832 | 82.8526 | 112.2937 | 111.6989 | 110.7821 | 108.9537 | 107.1432 | 104.7137 | 101.7737 | 99.1979 | 90.1032 | 85.4347 | 81.4905 | 66.1042 | 64.9105 | 93.4947 | 91.9463 | 90.1147 | 87.9516 | 85.9137 | 83.1611 | 79.8063 | 76.8653 | 66.5011 | 61.2379 | 56.7695 | 69.6063 | 69.0189 | 97.9947 | 96.4821 | 94.6979 | 92.5916 | 90.6074 | 87.9389 | 84.6895 | 81.8421 | 71.5674 | 66.3137 | 61.8505
|  | EAST BEDFONT A | HT |  |  |  | 83.1379 | 82.4684 | 111.7947 | 110.2137 | 108.1505 | 105.5547 | 103.0926 | 100.2442 | 97.4158 | 95.02 | 85.3147 | 79.1116 | 73.6989 | 65.7632 | 63.6642 | 91.6421 | 89.3853 | 87.0032 | 84.0874 | 81.3284 | 78.0968 | 74.8768 | 72.1611 | 61.1621 | 54.1789 | 48.0642 | 69.3411 | 68.1653 | 96.1937 | 93.9958 | 91.6789 | 88.8432 | 86.16 | 83.0274 | 79.9053 | 77.2168 | 66.2358 | 59.2632 | 53.1568
|  | EAST BEDFONT A | HE |  |  |  | 83.7126 | 83.3368 | 112.9232 | 112.4642 | 111.9705 | 110.9884 | 109.5011 | 107.2632 | 104.5611 | 102.3032 | 94.7337 | 91.3263 | 88.6126 | 66.4558 | 66.0263 | 94.9347 | 93.6874 | 92.1716 | 90.2737 | 88.5063 | 85.9347 | 82.8358 | 80.2442 | 71.5684 | 67.6937 | 64.5863 | 69.9621 | 69.5432 | 99.0863 | 98.1853 | 96.7105 | 94.8653 | 93.1463 | 90.6547 | 87.6568 | 85.1516 | 76.6295 | 72.7611 | 69.6579
|  | EAST BEDFONT A | CF |  |  |  | 83.9053 | 83.6811 | 113.4505 | 113.2074 | 112.96 | 112.7021 | 112.4379 | 112.1789 | 111.9242 | 111.6684 | 102.8505 | 99.9632 | 98.1295 | 66.6663 | 66.4347 | 96.1905 | 95.9305 | 95.5705 | 94.9011 | 94.2389 | 93.2832 | 92.24 | 91.2158 | 80.7347 | 77.4379 | 75.3347 | 70.1758 | 69.9421 | 99.6958 | 99.4337 | 99.1621 | 98.8779 | 98.5874 | 97.7874 | 96.7726 | 95.7789 | 85.6558 | 82.4621 | 80.3905
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | FAREHAM T1A T2A (90MVAS) | MINIMUM HEADROOM | SU 56534 04031 | YES | 26.9853 | 111.1284 | 109.8747 | 108.4579 | 104.3263 | 99.7589 | 58.68 | 52.9895 | 47.0937 | 27.0653 | 21.9947 | 2.7411 | -35.2547 | -46.7442 | 86.6474 | 83.5705 | 79.9474 | 75.2305 | 69.9832 | 18.4379 | 12.1232 | 5.4895 | -17.7895 | -23.4884 | -45.0516 | -84.3663 | -97.2347 | 92.0632 | 88.9516 | 85.5179 | 81.2242 | 76.1295 | 24.7768 | 18.46 | 11.8274 | -11.4295 | -17.1347 | -38.7853 | -78.2053 | -91.1011
|  | FAREHAM T1A T2A (90MVAS) | EE |  |  |  | 111.1284 | 109.8747 | 108.5442 | 105.9884 | 102.1905 | 97.9463 | 93.4958 | 88.6695 | 66.3611 | 61.2105 | 36.4853 | 0.99368 | -7.7516 | 86.6474 | 83.5705 | 80.0147 | 76.1621 | 71.76 | 66.8316 | 61.64 | 55.8811 | 27.6495 | 21.4168 | -6.9042 | -43.4526 | -53.2758 | 92.0632 | 88.9516 | 85.5179 | 81.8063 | 77.5674 | 72.8179 | 67.6884 | 61.9105 | 33.7147 | 27.4695 | -0.96105 | -37.6737 | -47.5347
|  | FAREHAM T1A T2A (90MVAS) | HT |  |  |  | 111.7084 | 110.1042 | 108.4579 | 104.3263 | 99.7589 | 58.68 | 52.9895 | 47.0937 | 27.0653 | 21.9947 | 2.7411 | -35.2547 | -46.7442 | 88.5221 | 84.36 | 79.9474 | 75.2305 | 69.9832 | 18.4379 | 12.1232 | 5.4895 | -17.7895 | -23.4884 | -45.0516 | -84.3663 | -97.2347 | 94.1505 | 90.1021 | 85.8116 | 81.2242 | 76.1295 | 24.7768 | 18.46 | 11.8274 | -11.4295 | -17.1347 | -38.7853 | -78.2053 | -91.1011
|  | FAREHAM T1A T2A (90MVAS) | HE |  |  |  | 111.9653 | 111.1095 | 110.1579 | 109.1095 | 106.7095 | 103.0695 | 99.2505 | 94.9284 | 73.16 | 68.7726 | 47.8779 | 14.5768 | 8.58 | 88.2684 | 86.2032 | 83.5642 | 80.5053 | 76.8474 | 72.5926 | 68.0926 | 62.9453 | 35.2389 | 29.8642 | 5.2737 | -29.6684 | -36.4663 | 93.7337 | 91.5926 | 88.9611 | 86.0158 | 82.5021 | 78.4074 | 74.0863 | 68.9884 | 41.3232 | 35.9453 | 11.3305 | -23.7705 | -30.6
|  | FAREHAM T1A T2A (90MVAS) | CF |  |  |  | 112.4526 | 111.9621 | 111.4537 | 110.9242 | 110.3768 | 109.7968 | 109.2053 | 108.5347 | 106.6653 | 104.4295 | 91.1674 | 61.3495 | 57.5905 | 89.1295 | 88.1568 | 87.0242 | 85.7074 | 84.2547 | 82.6221 | 80.9474 | 78.9958 | 76.7947 | 74.1263 | 57.9926 | 27.2874 | 22.7126 | 94.7484 | 93.6147 | 92.4453 | 91.0779 | 89.6232 | 88.0453 | 86.4284 | 84.5484 | 82.4379 | 79.8853 | 64.0337 | 33.3105 | 28.7105
LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | FAREHAM T1B T2B (1X90, 1X60MVA) | MINIMUM HEADROOM | SU 56534 04031 | YES | 0.25263 | 71.4095 | 70.5368 | 69.6558 | 68.7211 | 67.7474 | 66.4505 | 64.3632 | 62.5568 | 60.9695 | 59.6779 | 53.2474 | 46.6263 | 40.5274 | 60.7063 | 58.7537 | 56.9147 | 54.9411 | 52.6632 | 51.0221 | 48.6326 | 46.6158 | 44.8989 | 43.5147 | 36.5232 | 29.1779 | 22.3453 | 62.6453 | 60.7747 | 59.0074 | 57.1126 | 54.9326 | 53.3063 | 51.0189 | 49.0621 | 47.3432 | 45.9568 | 38.9558 | 31.6 | 24.7695
|  | FAREHAM T1B T2B (1X90, 1X60MVA) | EE |  |  |  | 71.7358 | 71.0463 | 70.3189 | 69.5432 | 68.7274 | 67.8747 | 66.6147 | 64.9832 | 63.5242 | 62.4411 | 57.8926 | 52.7611 | 48.1547 | 61.46 | 59.9105 | 58.4442 | 56.8737 | 55.0032 | 53.2074 | 51.1442 | 49.2737 | 47.6221 | 46.4442 | 41.6137 | 35.9242 | 30.7411 | 63.3663 | 61.8821 | 60.4705 | 58.9611 | 57.1684 | 55.44 | 53.4705 | 51.6758 | 50.0884 | 48.9442 | 44.0305 | 38.3211 | 33.1368
|  | FAREHAM T1B T2B (1X90, 1X60MVA) | HT |  |  |  | 71.4095 | 70.5368 | 69.6558 | 68.7211 | 67.7474 | 66.4505 | 64.3632 | 62.5568 | 60.9695 | 59.6779 | 53.2474 | 46.6263 | 40.5274 | 60.7063 | 58.7537 | 56.9147 | 54.9411 | 52.6632 | 51.0221 | 48.6326 | 46.6158 | 44.8989 | 43.5147 | 36.5232 | 29.1779 | 22.3453 | 62.6453 | 60.7747 | 59.0074 | 57.1126 | 54.9326 | 53.3063 | 51.0189 | 49.0621 | 47.3432 | 45.9568 | 38.9558 | 31.6 | 24.7695
|  | FAREHAM T1B T2B (1X90, 1X60MVA) | HE |  |  |  | 72.1663 | 71.68 | 71.14 | 70.5453 | 69.9042 | 69.2158 | 68.5579 | 67.9389 | 67.2884 | 66.5674 | 63.9095 | 60.5579 | 57.5558 | 62.1716 | 61.3821 | 60.3579 | 59.22 | 57.7611 | 56.3547 | 54.68 | 53.1632 | 51.9211 | 51.1411 | 48.2274 | 44.4105 | 40.9958 | 64.1158 | 63.2926 | 62.3053 | 61.2053 | 59.8084 | 58.4547 | 56.8558 | 55.4032 | 54.2095 | 53.4495 | 50.5884 | 46.84 | 43.4232
|  | FAREHAM T1B T2B (1X90, 1X60MVA) | CF |  |  |  | 72.4158 | 72.1253 | 71.8232 | 71.5084 | 71.1842 | 70.8463 | 70.5011 | 70.1642 | 69.8263 | 69.4926 | 67.9958 | 66.4411 | 64.4411 | 62.44 | 62.1295 | 61.7705 | 61.1158 | 60.3853 | 59.62 | 58.7642 | 57.9853 | 57.1411 | 56.42 | 53.1095 | 50.8758 | 48.4916 | 64.3853 | 64.0737 | 63.6621 | 63.0316 | 62.3326 | 61.5979 | 60.7811 | 60.0326 | 59.2263 | 58.5337 | 55.3568 | 53.2 | 50.9274
BRAMLEY (FLEE) | FERNHURST | FERNHURST | MINIMUM HEADROOM | SU 72730 39772 | YES | 26.5958 | 97.2347 | 93.9137 | 92.76 | 91.4263 | 90.0042 | 76.4484 | 59.5589 | 58.4663 | 57.3537 | 56.2758 | 50.5495 | 23.1716 | 19.0832 | 87.3853 | 83.7632 | 82.4958 | 81.02 | 79.4411 | 64.1674 | 44.4484 | 43.2705 | 42.0695 | 40.9011 | 34.6011 | 6.4705 | 1.8558 | 88.4737 | 84.9463 | 83.6779 | 82.2021 | 80.6221 | 65.7042 | 45.9695 | 44.7811 | 43.5663 | 42.3853 | 35.9947 | 7.7653 | 3.1189
|  | FERNHURST | EE |  |  |  | 97.4716 | 94.6779 | 93.7316 | 93.7358 | 92.9074 | 76.4484 | 59.5589 | 58.4663 | 57.3537 | 56.2758 | 50.5495 | 23.1716 | 19.0832 | 87.9116 | 84.6074 | 83.5684 | 84.3242 | 83.4358 | 64.1674 | 44.4484 | 43.2705 | 42.0695 | 40.9011 | 34.6011 | 6.4705 | 1.8558 | 88.9305 | 85.7905 | 84.7505 | 85.8737 | 84.9863 | 65.7042 | 45.9695 | 44.7811 | 43.5663 | 42.3853 | 35.9947 | 7.7653 | 3.1189
|  | FERNHURST | HT |  |  |  | 97.2347 | 93.9137 | 92.76 | 91.4263 | 90.0042 | 86.8695 | 84.7221 | 82.5368 | 81.6442 | 80.7758 | 72.8863 | 43.2874 | 39.6158 | 87.3853 | 83.7632 | 82.4958 | 81.02 | 79.4411 | 75.8389 | 73.4495 | 70.9989 | 70.06 | 69.1432 | 60.3316 | 28.8368 | 24.7747 | 88.4737 | 84.9463 | 83.6779 | 82.2021 | 80.6221 | 77.0137 | 74.6147 | 72.1547 | 71.2074 | 70.2821 | 61.4053 | 29.5505 | 25.4611
|  | FERNHURST | HE |  |  |  | 97.7916 | 95.38 | 94.9632 | 94.1768 | 93.2463 | 92.1116 | 75.5589 | 74.7137 | 73.8737 | 73.0547 | 68.6453 | 41.5316 | 38.6042 | 88.5821 | 85.6379 | 84.9232 | 84.0516 | 83.0147 | 81.7463 | 62.3105 | 61.3958 | 60.4832 | 59.5842 | 54.6516 | 25.3747 | 22.0432 | 89.54 | 86.7 | 86.0747 | 85.2358 | 84.1979 | 82.9232 | 63.4779 | 62.5558 | 61.6379 | 60.7337 | 55.7632 | 26.1074 | 22.7495
|  | FERNHURST | CF |  |  |  | 97.9768 | 95.7032 | 95.5284 | 95.3463 | 95.1579 | 94.66 | 94.1663 | 93.7158 | 93.24 | 92.7379 | 89.7316 | 68.3642 | 66.4705 | 88.9653 | 86.4126 | 86.0505 | 85.6358 | 85.1484 | 84.5789 | 84.0284 | 83.5305 | 83.0021 | 82.44 | 79.0168 | 58.3758 | 56.2232 | 89.9 | 87.3811 | 87.0505 | 86.6916 | 86.2737 | 85.7589 | 85.2063 | 84.7074 | 84.1758 | 83.6116 | 80.1758 | 59.8863 | 57.7147
LOVEDEAN GSP | FORT WIDLEY | FORT WIDLEY | MINIMUM HEADROOM | SU 64948 05441 | YES | 0.14 | 67.9642 | 67.2505 | 66.5263 | 65.4453 | 63.1421 | 60.6042 | 58.2989 | 86.1895 | 84.1737 | 82.1926 | 57.6347 | 51.0621 | 44.58 | 59.8116 | 57.82 | 55.6958 | 53.3863 | 50.8126 | 47.9663 | 45.4011 | 73.0453 | 70.7916 | 68.5695 | 40.0737 | 32.6926 | 25.3189 | 61.7821 | 59.9547 | 57.92 | 55.6105 | 53.0368 | 50.1895 | 47.6189 | 75.2589 | 73.0021 | 70.7747 | 42.2453 | 34.8326 | 27.4474
|  | FORT WIDLEY | EE |  |  |  | 68.2474 | 67.6916 | 67.1021 | 66.4789 | 65.1484 | 62.9853 | 61.0337 | 89.1884 | 87.3842 | 85.6053 | 78.5284 | 65.1263 | 60.0326 | 60.4358 | 58.9368 | 57.1516 | 55.1884 | 53.0242 | 50.6011 | 48.42 | 76.36 | 74.3463 | 72.3505 | 64.4011 | 48.8874 | 43.0674 | 62.0853 | 61.0221 | 59.3242 | 57.4116 | 55.2484 | 52.8211 | 50.6358 | 78.5716 | 76.5526 | 74.5526 | 66.5674 | 51.0074 | 45.1726
|  | FORT WIDLEY | HT |  |  |  | 67.9642 | 67.2505 | 66.5263 | 65.4453 | 63.1421 | 60.6042 | 58.2989 | 86.1895 | 84.1737 | 82.1926 | 57.6347 | 51.0621 | 44.58 | 59.8116 | 57.82 | 55.6958 | 53.3863 | 50.8126 | 47.9663 | 45.4011 | 73.0453 | 70.7916 | 68.5695 | 40.0737 | 32.6926 | 25.3189 | 61.7821 | 59.9547 | 57.92 | 55.6105 | 53.0368 | 50.1895 | 47.6189 | 75.2589 | 73.0021 | 70.7747 | 42.2453 | 34.8326 | 27.4474
|  | FORT WIDLEY | HE |  |  |  | 68.6253 | 68.2484 | 67.8326 | 67.3726 | 66.8779 | 65.4011 | 63.7495 | 92.1989 | 90.7063 | 89.2347 | 83.5505 | 71.5621 | 67.6495 | 61.2705 | 60.1632 | 58.7495 | 57.1432 | 55.3263 | 53.2316 | 51.3758 | 79.6358 | 77.9611 | 76.2947 | 69.8442 | 55.8537 | 51.3368 | 62.4895 | 62.0705 | 60.8589 | 59.3358 | 57.5516 | 55.4547 | 53.5958 | 81.8547 | 80.1758 | 78.5074 | 72.0421 | 58.0358 | 53.5084
|  | FORT WIDLEY | CF |  |  |  | 68.8463 | 68.6358 | 68.4189 | 68.1916 | 67.9558 | 67.7105 | 67.46 | 97.2126 | 96.9705 | 96.5232 | 91.5084 | 88.9874 | 86.5295 | 61.8389 | 61.3274 | 60.6832 | 59.9442 | 59.1453 | 58.2789 | 57.4032 | 86.4758 | 85.5137 | 84.4905 | 78.7737 | 75.9053 | 73.0705 | 62.7347 | 62.5032 | 62.2611 | 61.9926 | 61.2347 | 60.4137 | 59.5821 | 88.7 | 87.7347 | 86.7105 | 80.9884 | 78.1137 | 75.2695
MELKSHAM GSP | FROME BSP | FROME BSP | MINIMUM HEADROOM | ST 78803 48019 | YES | 125.8474 | 96.4221 | 56.2137 | 109.7126 | 63.2432 | 59.4705 | 55.2358 | 51.3053 | 46.7579 | 31.3589 | -0.41684 | -37.0674 | -117.8989 | -130.0253 | 64.0895 | 23.5558 | 74.9568 | 26.3853 | 22.1853 | 17.5463 | 13.2853 | 8.2947 | -9.4484 | -46.8232 | -87.9168 | -174.3442 | -187.7242 | 68.4 | 27.8653 | 79.2895 | 30.2663 | 26.0663 | 21.3705 | 17.0337 | 11.9611 | -5.8484 | -42.9284 | -84.3821 | -171.7895 | -185.3842
|  | FROME BSP | EE |  |  |  | 105.6126 | 57.9284 | 112.0232 | 63.2432 | 59.4705 | 55.2358 | 51.3053 | 46.7579 | 31.3589 | 28.1442 | 14.6842 | -57.9853 | -71.8821 | 78.4937 | 25.4326 | 77.4937 | 26.3853 | 22.1853 | 17.5463 | 13.2853 | 8.2947 | -9.4484 | -12.8663 | -24.8284 | -98.9611 | -114.5474 | 82.8158 | 29.7368 | 81.8189 | 30.2663 | 26.0663 | 21.3705 | 17.0337 | 11.9611 | -5.8484 | -9.3684 | -21.9074 | -96.6716 | -112.4979
|  | FROME BSP | HT |  |  |  | 96.4221 | 56.2137 | 109.7126 | 75.5337 | 70.5021 | 66.1432 | 60.7979 | 55.0526 | 48.9642 | -0.41684 | -37.0674 | -117.8989 | -130.0253 | 64.0895 | 23.5558 | 74.9568 | 40.2947 | 34.6526 | 30.0705 | 24.1653 | 17.7621 | 10.9453 | -46.8232 | -87.9168 | -174.3442 | -187.7242 | 68.4 | 27.8653 | 79.2895 | 44.6284 | 38.9937 | 34.1021 | 28.1453 | 21.6874 | 14.8105 | -42.9284 | -84.3821 | -171.7895 | -185.3842
|  | FROME BSP | HE |  |  |  | 106.3653 | 60.2147 | 124.3695 | 82.3389 | 79.2168 | 75.6379 | 72.4453 | 68.6221 | 54.1105 | 51.7221 | 39.3084 | -33.4505 | -44.4621 | 80.1326 | 27.9211 | 91.7484 | 47.7389 | 44.2411 | 40.2905 | 36.7768 | 32.5158 | 15.6695 | 13.0726 | -0.42632 | -78.1368 | -90.5895 | 84.4905 | 32.2305 | 96.0632 | 52.0758 | 48.5821 | 44.5916 | 41.0505 | 36.7516 | 19.8926 | 17.2547 | 3.2253 | -75.0821 | -87.7211
|  | FROME BSP | CF |  |  |  | 106.8032 | 69.4263 | 128.8926 | 97.7863 | 87.1495 | 85.5926 | 84.1274 | 82.3316 | 80.3674 | 78.4726 | 70.12 | 12.0779 | 6.3063 | 85.5547 | 43.1284 | 95.7874 | 64.5642 | 52.1337 | 50.4221 | 48.8168 | 46.8284 | 44.6389 | 42.5179 | 33.2358 | -25.1947 | -31.6505 | 87.8253 | 47.4832 | 99.8979 | 68.6558 | 56.2484 | 54.5211 | 52.8979 | 50.8905 | 48.6832 | 46.5526 | 37.1884 | -21.6147 | -28.1989
LOVEDEAN GSP | HAVANT | HAVANT | MINIMUM HEADROOM | SU 70625 05720 | YES | 24.5453 | 113.3621 | 93.3579 | 92.7284 | 92.0705 | 91.1979 | 85.1442 | 79.2663 | 73.7242 | 68.1811 | 62.8758 | 40.42 | 20.0684 | 2.1337 | 86.7663 | 67.5758 | 65.3505 | 63.9547 | 60.9653 | 54.3968 | 48.0284 | 42.0032 | 35.9495 | 30.1547 | 5.5842 | -16.8221 | -36.6558 | 95.1958 | 76.0558 | 73.7305 | 72.2895 | 67.6432 | 60.9337 | 54.4347 | 48.2811 | 42.0937 | 36.1589 | 11.0105 | -11.9674 | -32.3084
|  | HAVANT | EE |  |  |  | 113.3621 | 102.3716 | 100.7116 | 98.9474 | 96.1726 | 91.0674 | 86.1221 | 81.3853 | 76.6 | 72.1842 | 54.1442 | 37.6484 | 23.6558 | 86.7663 | 79.3979 | 75.3832 | 71.3137 | 66.3179 | 60.7642 | 55.3947 | 50.2526 | 45.0442 | 40.2358 | 20.5158 | 2.3158 | -13.2189 | 95.1958 | 85.9368 | 82.0263 | 78.0579 | 73.0905 | 67.42 | 61.9368 | 56.6811 | 51.3558 | 46.4389 | 26.2337 | 7.5389 | -8.4105
|  | HAVANT | HT |  |  |  | 124.2221 | 101.1653 | 99.1453 | 96.7516 | 91.1979 | 85.1442 | 79.2663 | 73.7242 | 68.1811 | 62.8758 | 40.42 | 20.0684 | 2.1337 | 102.3316 | 77.1811 | 72.4747 | 67.0137 | 60.9653 | 54.3968 | 48.0284 | 42.0032 | 35.9495 | 30.1547 | 5.5842 | -16.8221 | -36.6558 | 108.8568 | 83.7663 | 79.1779 | 73.8116 | 67.6432 | 60.9337 | 54.4347 | 48.2811 | 42.0937 | 36.1589 | 11.0105 | -11.9674 | -32.3084
|  | HAVANT | HE |  |  |  | 114.4074 | 103.9084 | 102.7232 | 101.4137 | 100.0021 | 97.8053 | 93.6358 | 89.6842 | 85.7674 | 82.1137 | 68.1905 | 55.4768 | 44.8895 | 88.7863 | 82.2284 | 79.1505 | 76.0042 | 72.4137 | 67.9979 | 63.4326 | 59.1274 | 54.8463 | 50.8411 | 35.5253 | 21.3663 | 9.5158 | 97.2747 | 88.7653 | 85.7168 | 82.6505 | 79.1558 | 74.7779 | 70.1116 | 65.7105 | 61.3326 | 57.2326 | 41.5368 | 26.9905 | 14.7979
|  | HAVANT | CF |  |  |  | 115.0189 | 93.3579 | 92.7284 | 92.0705 | 91.3916 | 90.6884 | 101.5916 | 100.8842 | 100.1821 | 98.3284 | 89.5442 | 79.5558 | 72.8063 | 89.96 | 67.5758 | 65.3505 | 63.9547 | 62.4558 | 60.8084 | 76.2453 | 73.9137 | 71.3105 | 68.4432 | 58.8747 | 47.7284 | 40.1768 | 98.4842 | 76.0558 | 73.7305 | 72.2895 | 70.74 | 69.0316 | 82.8874 | 80.6253 | 78.1042 | 75.2042 | 65.4274 | 53.9705 | 46.2011
COWLEY GSP | HEADINGTON BSP | HEADINGTON BSP | MINIMUM HEADROOM | SP 54454 08145 | YES | 77.1821 | 98.0495 | 65.1326 | 63.7979 | -7.0874 | -63.7547 | -104.5326 | -111.5389 | -115.2947 | -118.68 | -121.5168 | -132.8895 | -134.7232 | -138.3053 | 85.0968 | 39.0958 | 37.66 | -40.0232 | -99.8758 | -147.6947 | -155.7705 | -160.02 | -163.8295 | -167.0042 | -178.6642 | -178.1411 | -182.0221 | 86.3168 | 43.0147 | 41.5768 | -36.0211 | -96.0568 | -143.8074 | -151.9 | -156.1747 | -160.0147 | -163.2232 | -174.9411 | -174.2705 | -178.2389
|  | HEADINGTON BSP | EE |  |  |  | 98.0495 | 97.4558 | 96.8158 | 17.4063 | -63.7547 | -104.5326 | -111.5389 | -115.2947 | -118.68 | -121.5168 | -132.8895 | -134.7232 | -138.3053 | 85.0968 | 82.7463 | 80.9263 | -12.3179 | -99.8758 | -147.6947 | -155.7705 | -160.02 | -163.8295 | -167.0042 | -178.6642 | -178.1411 | -182.0221 | 86.3168 | 85.0432 | 83.9926 | -8.5747 | -96.0568 | -143.8074 | -151.9 | -156.1747 | -160.0147 | -163.2232 | -174.9411 | -174.2705 | -178.2389
|  | HEADINGTON BSP | HT |  |  |  | 104.2937 | 65.1326 | 63.7979 | -7.0874 | -54.9211 | -58.9842 | -66.7126 | -70.3811 | -80.7832 | -83.7642 | -97.3368 | -110.1937 | -116.8053 | 88.3495 | 39.0958 | 37.66 | -40.0232 | -88.3463 | -92.9421 | -101.8484 | -105.9905 | -118.0653 | -121.4116 | -136.62 | -151.0495 | -159.3411 | 91.6253 | 43.0147 | 41.5768 | -36.0211 | -84.34 | -88.9474 | -97.8621 | -102.0211 | -114.1021 | -117.4726 | -132.84 | -147.46 | -156.0116
|  | HEADINGTON BSP | HE |  |  |  | 98.4453 | 98.0358 | 97.5842 | 65.5042 | -16.5032 | -34.0589 | -77.5695 | -80.9568 | -83.9263 | -86.3884 | -99.3958 | -105.1737 | -107.3842 | 85.72 | 83.8179 | 82.4063 | 48.5589 | -44.4853 | -65.0126 | -116.0916 | -119.9642 | -123.3453 | -126.1411 | -141.9432 | -149.4547 | -151.84 | 86.8211 | 85.7947 | 85.0105 | 51.7189 | -40.7568 | -61.2621 | -112.2568 | -116.1389 | -119.5316 | -122.3389 | -138.4095 | -146.1937 | -148.6526
|  | HEADINGTON BSP | CF |  |  |  | 98.6747 | 98.4411 | 98.1989 | 34.8716 | -9.8116 | -47.9547 | -50.6611 | -52.5242 | -54.6463 | -56.7168 | -64.5389 | -67.3695 | -68.9537 | 86.0284 | 85.2895 | 84.94 | 7.9105 | -36.8126 | -81.6347 | -84.7579 | -86.8884 | -89.3274 | -91.7074 | -100.6432 | -103.7916 | -105.5147 | 87.1021 | 86.6189 | 86.3274 | 11.6274 | -33.0958 | -77.84 | -80.9653 | -83.1021 | -85.5442 | -87.9211 | -96.88 | -100.0695 | -101.84
COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE BSP | MINIMUM HEADROOM | SU 84773 92191 | YES | 4.4726 | 56.8695 | 54.2768 | 13.1221 | 10.4211 | 7.6947 | 4.7589 | 1.7895 | -1.1863 | -3.6158 | -5.94 | -25.4958 | -36.2695 | -45.0084 | 16.2884 | 13.4937 | -34.7916 | -37.6916 | -40.6147 | -43.7716 | -46.9621 | -50.2 | -52.8179 | -55.3284 | -77.4337 | -89.4021 | -99.1526 | 22.2989 | 19.5042 | -28.7958 | -31.6979 | -34.6232 | -37.78 | -40.9779 | -44.22 | -46.8432 | -49.3568 | -71.4968 | -83.5053 | -93.2674
|  | HIGH WYCOMBE BSP | EE |  |  |  | 57.3179 | 55.3168 | 53.2 | 51.0105 | 48.7789 | 46.5074 | 44.4295 | 43.0579 | 40.9516 | 38.9337 | 30.1379 | 17.6663 | 10.4832 | 16.6768 | 14.5242 | 12.2432 | 9.8968 | 7.5063 | 5.0842 | 2.8821 | 1.5432 | -0.71053 | -2.8832 | -12.4589 | -26.6 | -34.6884 | 22.7705 | 20.6168 | 18.3358 | 15.9863 | 13.5989 | 11.1695 | 8.9642 | 7.5368 | 5.2758 | 3.0968 | -6.5242 | -20.7179 | -28.8263
|  | HIGH WYCOMBE BSP | HT |  |  |  | 56.8695 | 54.2768 | 13.1221 | 10.4211 | 7.6947 | 4.7589 | 1.7895 | -1.1863 | -3.6158 | -5.94 | -25.4958 | -36.2695 | -45.0084 | 16.2884 | 13.4937 | -34.7916 | -37.6916 | -40.6147 | -43.7716 | -46.9621 | -50.2 | -52.8179 | -55.3284 | -77.4337 | -89.4021 | -99.1526 | 22.2989 | 19.5042 | -28.7958 | -31.6979 | -34.6232 | -37.78 | -40.9779 | -44.22 | -46.8432 | -49.3568 | -71.4968 | -83.5053 | -93.2674
|  | HIGH WYCOMBE BSP | HE |  |  |  | 74.2137 | 72.9642 | 56.1221 | 54.5968 | 52.9968 | 51.3116 | 49.8179 | 49.0232 | 47.5137 | 46.1242 | 40.3526 | 30.7674 | 26.08 | 36.4726 | 35.1411 | 15.4295 | 13.8011 | 12.0979 | 10.3158 | 8.7453 | 8.0326 | 6.4232 | 4.9326 | -1.3653 | -12.3642 | -17.6989 | 42.5726 | 41.24 | 21.5221 | 19.8926 | 18.1905 | 16.4042 | 14.8326 | 14.0337 | 12.4232 | 10.9295 | 4.6063 | -6.4105 | -11.76
|  | HIGH WYCOMBE BSP | CF |  |  |  | 116.0684 | 74.2021 | 57.9505 | 57.1179 | 56.2442 | 55.3284 | 54.4505 | 53.5705 | 52.62 | 51.6526 | 47.1147 | 44.1032 | 40.7758 | 96.7011 | 36.4611 | 17.3726 | 16.4747 | 15.5379 | 14.5516 | 13.6126 | 12.6695 | 11.6421 | 10.5937 | 5.6663 | 2.3716 | -1.4305 | 101.2653 | 42.5611 | 23.4663 | 22.5684 | 21.6305 | 20.6432 | 19.6989 | 18.7589 | 17.7295 | 16.68 | 11.7421 | 8.3589 | 4.5463
FAWLEY GSP | LANGLEY BSP | LANGLEY BSP | MINIMUM HEADROOM | SU 45185 01376 | YES | 0 | 47.7547 | 46.6474 | 45.5684 | 45.1716 | 44.0705 | 42.9484 | 41.4874 | 39.9905 | 38.8642 | 37.3905 | 33.6432 | 29.1505 | 24.8842 | 41.5579 | 40.3421 | 39.1611 | 38.8305 | 37.6474 | 36.4579 | 34.8642 | 33.2137 | 31.9905 | 30.3463 | 26.3232 | 21.3221 | 16.5189 | 42.2979 | 41.1074 | 39.9505 | 39.5758 | 38.4032 | 37.2053 | 35.6105 | 33.9589 | 32.7326 | 31.0884 | 27.0526 | 22.0389 | 17.2295
|  | LANGLEY BSP | EE |  |  |  | 48.2389 | 47.3863 | 46.5347 | 45.6589 | 44.7726 | 44.5737 | 43.6968 | 42.6137 | 41.4347 | 40.2737 | 36.9189 | 33.4663 | 30.2337 | 42.0958 | 41.1621 | 40.2358 | 39.2874 | 38.3305 | 38.2263 | 37.2853 | 36.1179 | 34.8221 | 33.54 | 29.9074 | 26.06 | 22.4021 | 42.7726 | 41.9074 | 40.9989 | 40.0674 | 39.1295 | 38.9726 | 38.0411 | 36.8621 | 35.5653 | 34.2789 | 30.6305 | 26.7674 | 23.1021
|  | LANGLEY BSP | HT |  |  |  | 47.7547 | 46.6474 | 45.5684 | 45.1716 | 44.0705 | 42.9484 | 41.4874 | 39.9905 | 38.8642 | 37.3905 | 33.6432 | 29.1505 | 24.8842 | 41.5579 | 40.3421 | 39.1611 | 38.8305 | 37.6474 | 36.4579 | 34.8642 | 33.2137 | 31.9905 | 30.3463 | 26.3232 | 21.3221 | 16.5189 | 42.2979 | 41.1074 | 39.9505 | 39.5758 | 38.4032 | 37.2053 | 35.6105 | 33.9589 | 32.7326 | 31.0884 | 27.0526 | 22.0389 | 17.2295
|  | LANGLEY BSP | HE |  |  |  | 48.8926 | 48.3505 | 47.7968 | 47.2074 | 46.5947 | 46.6463 | 46.0211 | 45.2916 | 44.5411 | 43.8526 | 41.2726 | 38.9421 | 36.7326 | 42.8221 | 42.2316 | 41.6347 | 41.0042 | 40.3505 | 40.5221 | 39.8568 | 39.0568 | 38.2263 | 37.46 | 34.6389 | 32.0137 | 29.4853 | 43.3074 | 42.8811 | 42.3347 | 41.7453 | 41.1 | 41.2137 | 40.5589 | 39.7768 | 38.9632 | 38.2158 | 35.3779 | 32.7463 | 30.2126
|  | LANGLEY BSP | CF |  |  |  | 49.9295 | 48.9105 | 48.5884 | 48.2579 | 47.9179 | 47.5716 | 47.2179 | 46.8726 | 46.5084 | 46.8316 | 44.7432 | 43.2147 | 41.7347 | 44.0474 | 42.84 | 42.4884 | 42.1274 | 41.7579 | 41.3789 | 40.9937 | 40.62 | 40.2221 | 40.6674 | 38.3295 | 36.6221 | 34.9242 | 44.2863 | 43.3232 | 43.1158 | 42.7905 | 42.4568 | 42.1137 | 41.74 | 41.3716 | 40.98 | 41.3684 | 39.0842 | 37.3642 | 35.6632
IVER 132KV | LONGFORD | LONGFORD | MINIMUM HEADROOM | TQ 03910 76751 | YES | 2.9842 | 44.4811 | 44.4179 | 44.3526 | 44.2842 | 44.2147 | 44.1411 | 44.0663 | 43.9937 | 43.9221 | 43.8495 | 43.5274 | 43.3747 | 43.2842 | 39.2421 | 39.1716 | 39.0947 | 39.0116 | 38.9126 | 38.7979 | 38.6821 | 38.5684 | 38.4537 | 38.1495 | 37.52 | 37.0863 | 36.7232 | 30.6463 | 30.5811 | 30.5126 | 30.44 | 30.3621 | 30.2768 | 30.1895 | 30.1053 | 30.0211 | 29.8821 | 29.4705 | 29.2358 | 28.9821
|  | LONGFORD | EE |  |  |  | 68.24 | 68.0863 | 67.9263 | 67.7547 | 67.5747 | 67.3884 | 67.2084 | 67.0368 | 66.8684 | 66.7211 | 66.1916 | 99.5021 | 99.2253 | 57.6537 | 57.5 | 57.34 | 57.1684 | 56.9884 | 56.8021 | 56.6189 | 56.4432 | 56.1905 | 55.4379 | 54.2316 | 86.5189 | 85.2168 | 58.4505 | 58.2968 | 58.1368 | 57.9653 | 57.7853 | 57.5989 | 57.4189 | 57.2474 | 57.0789 | 56.9316 | 56.04 | 88.3653 | 87.1011
|  | LONGFORD | HT |  |  |  | 68.1632 | 67.9695 | 67.7726 | 67.5632 | 67.3474 | 67.1274 | 66.9011 | 66.7021 | 66.5211 | 66.3526 | 65.6789 | 98.8432 | 98.4274 | 57.5768 | 57.3832 | 57.1863 | 56.9768 | 56.7611 | 56.5421 | 56.3158 | 56.1126 | 55.7653 | 54.8653 | 52.8053 | 84.6253 | 82.8842 | 58.3737 | 58.18 | 57.9832 | 57.7737 | 57.5579 | 57.3389 | 57.1126 | 56.9137 | 56.7326 | 56.5642 | 54.6474 | 86.5168 | 84.7853
|  | LONGFORD | HE |  |  |  | 68.3347 | 68.2274 | 68.1084 | 67.9779 | 67.8358 | 67.6853 | 67.5421 | 67.4063 | 67.28 | 67.1705 | 66.8032 | 100.2526 | 100.1168 | 57.7484 | 57.6411 | 57.5221 | 57.3916 | 57.2495 | 57.0989 | 56.9558 | 56.82 | 56.6937 | 56.5842 | 55.6389 | 88.3284 | 87.4158 | 58.5453 | 58.4379 | 58.3189 | 58.1884 | 58.0463 | 57.8958 | 57.7526 | 57.6168 | 57.4905 | 57.3811 | 57.0147 | 90.1242 | 89.24
|  | LONGFORD | CF |  |  |  | 44.4811 | 44.4179 | 44.3526 | 44.2842 | 44.2147 | 44.1411 | 44.0663 | 43.9937 | 43.9221 | 43.8495 | 43.5274 | 43.3747 | 43.2842 | 39.2421 | 39.1716 | 39.0947 | 39.0116 | 38.9126 | 38.7979 | 38.6821 | 38.5684 | 38.4537 | 38.1495 | 37.52 | 37.0863 | 36.7232 | 30.6463 | 30.5811 | 30.5126 | 30.44 | 30.3621 | 30.2768 | 30.1895 | 30.1053 | 30.0211 | 29.8821 | 29.4705 | 29.2358 | 28.9821
AMERSHAM | LOUDWATER BSP | LOUDWATER BSP | MINIMUM HEADROOM | SU 90644 91247 | YES | 2.4653 | 99.9979 | 188.1779 | 186.0768 | 184.0337 | 182.0011 | 179.9926 | 177.9874 | 175.7242 | 173.3463 | 171.1916 | 161.3726 | 152.7126 | 144.9726 | 89.7084 | 176.4832 | 172.1989 | 167.2989 | 164.1579 | 161.2137 | 157.9295 | 154.9011 | 152.3179 | 149.9821 | 139.2453 | 129.6674 | 121.0316 | 93.1895 | 180.6516 | 176.3147 | 171.3305 | 168.1537 | 165.1895 | 161.9063 | 158.8768 | 156.2968 | 153.9632 | 143.2253 | 133.6474 | 125.0189
|  | LOUDWATER BSP | EE |  |  |  | 100.6642 | 189.2053 | 187.4758 | 184.7684 | 183.0632 | 181.3758 | 179.2105 | 176.84 | 174.7916 | 172.9811 | 165.2526 | 158.6842 | 152.9221 | 90.7484 | 178.0589 | 174.4863 | 167.2989 | 164.1579 | 161.2137 | 158.3726 | 155.7884 | 153.5737 | 151.6179 | 143.1716 | 135.8874 | 129.4221 | 93.7579 | 182.2389 | 178.6221 | 171.3305 | 168.1537 | 165.1895 | 162.3505 | 159.7684 | 157.5537 | 155.5989 | 147.1474 | 139.8558 | 133.3937
|  | LOUDWATER BSP | HT |  |  |  | 99.9979 | 188.1779 | 186.0768 | 184.0337 | 182.0011 | 179.9926 | 177.9874 | 175.7242 | 173.3463 | 171.1916 | 161.3726 | 152.7126 | 144.9726 | 89.7084 | 176.4832 | 172.1989 | 168.3821 | 164.7368 | 161.3242 | 157.9295 | 154.9011 | 152.3179 | 149.9821 | 139.2453 | 129.6674 | 121.0316 | 93.1895 | 180.6516 | 176.3147 | 172.4558 | 168.7726 | 165.3253 | 161.9063 | 158.8768 | 156.2968 | 153.9632 | 143.2253 | 133.6474 | 125.0189
|  | LOUDWATER BSP | HE |  |  |  | 101.5474 | 190.5063 | 189.26 | 187.9579 | 186.6358 | 185.3074 | 184.0421 | 182.8737 | 181.8526 | 180.9758 | 177.7537 | 173.6505 | 170.0568 | 92.0895 | 180.1011 | 177.4726 | 174.8558 | 172.3558 | 170.0179 | 167.7895 | 165.8032 | 164.2095 | 162.8547 | 157.2211 | 152.4916 | 148.42 | 94.5074 | 183.7305 | 181.6368 | 178.9884 | 176.4632 | 174.0979 | 171.8463 | 169.84 | 168.2326 | 166.8653 | 161.1905 | 156.4621 | 152.3926
|  | LOUDWATER BSP | CF |  |  |  | 102.3474 | 191.4863 | 190.8484 | 190.2621 | 189.6758 | 189.0495 | 188.3789 | 187.7474 | 187.1705 | 186.5989 | 183.9811 | 182.3674 | 181.2242 | 92.6684 | 181.8147 | 180.5053 | 179.4253 | 178.4011 | 177.2568 | 175.9695 | 174.8084 | 173.8432 | 172.9126 | 168.4621 | 165.0347 | 162.1726 | 95.0084 | 184.5105 | 184.0537 | 183.5979 | 182.58 | 181.4221 | 180.1179 | 178.9432 | 177.9684 | 177.0295 | 172.5326 | 169.0621 | 166.1558
MANNINGTON GSP | LYTCHETT | LYTCHETT | MINIMUM HEADROOM | SY 97796 94214 | YES | 74.6589 | 65.6089 | 87.7337 | 35.2168 | 32.4189 | 29.0811 | 25.0116 | 20.2768 | 15.5253 | -24.4589 | -33.8779 | -116.5011 | -131.2053 | -140.3326 | 41.8905 | 67.0968 | 5.5211 | 2.4558 | -1.2326 | -5.6063 | -10.8379 | -16.1137 | -62.8547 | -73.6316 | -161.1347 | -176.9516 | -186.8958 | 49.2337 | 71.7632 | 10.2989 | 7.2368 | 3.5474 | -1.0063 | -6.2895 | -11.6211 | -58.3484 | -69.1863 | -157.1211 | -173.4968 | -183.6589
|  | LYTCHETT | EE |  |  |  | 66.5616 | 98.5779 | 86.9211 | 71.2916 | 68.7937 | 65.76 | 62.74 | 59.9021 | 57.4842 | 55.3253 | -7.1916 | -28.3326 | -37.6474 | 42.9295 | 79.7274 | 66.1947 | 48.7716 | 46.0253 | 42.7684 | 39.5368 | 36.5189 | 34.0042 | 31.7926 | -31.7853 | -54.9505 | -65.2232 | 50.2726 | 84.3716 | 70.8568 | 52.9884 | 50.2442 | 46.9242 | 43.6168 | 40.5137 | 37.9095 | 35.5937 | -28.7926 | -52.7316 | -63.24
|  | LYTCHETT | HT |  |  |  | 65.6089 | 87.7337 | 35.2168 | 32.4189 | 29.0811 | 25.0116 | 20.2768 | 15.5253 | -24.4589 | -33.8779 | -116.5011 | -131.2053 | -140.3326 | 41.8905 | 67.0968 | 5.5211 | 2.4558 | -1.2326 | -5.6063 | -10.8379 | -16.1137 | -62.8547 | -73.6316 | -161.1347 | -176.9516 | -186.8958 | 49.2337 | 71.7632 | 10.2989 | 7.2368 | 3.5474 | -1.0063 | -6.2895 | -11.6211 | -58.3484 | -69.1863 | -157.1211 | -173.4968 | -183.6589
|  | LYTCHETT | HE |  |  |  | 67.8058 | 100.4737 | 89.4632 | 87.8232 | 85.8789 | 83.4495 | 81.0684 | 78.8611 | 39.5716 | 38.1242 | -19.4884 | -35.4158 | -42.34 | 44.2821 | 81.7916 | 68.9579 | 67.1642 | 65.0232 | 62.3895 | 59.8021 | 57.4116 | 11.3811 | 9.8621 | -48.8042 | -66.9568 | -74.6305 | 51.6211 | 86.4337 | 73.6221 | 71.8295 | 69.6895 | 67.0147 | 64.3926 | 61.9642 | 15.9747 | 14.4147 | -44.6558 | -63.0042 | -70.8716
|  | LYTCHETT | CF |  |  |  | 68.4089 | 101.7126 | 100.8789 | 90.8526 | 89.9979 | 88.9137 | 87.7663 | 86.7105 | 85.6379 | 84.5611 | 32.46 | 27.7726 | 23.0032 | 44.9242 | 83.1337 | 82.2168 | 70.4842 | 69.5474 | 68.3747 | 67.1295 | 65.9947 | 64.8263 | 63.6568 | 11.0011 | 5.9326 | 0.63053 | 52.2621 | 87.7726 | 86.8568 | 75.1463 | 74.2105 | 73.02 | 71.7537 | 70.6 | 69.4179 | 68.2305 | 15.4884 | 10.1737 | 4.7411
BRAMLEY (FLEE) | MAIDENHEAD BSP | MAIDENHEAD BSP | MINIMUM HEADROOM | SU 86592 79883 | YES | 1.4168 | 112.0621 | 110.9516 | 102.6642 | 98.4095 | 92.9611 | 89.1442 | 85.1674 | 81.9526 | 79.9632 | 78.1221 | 70.1084 | 62.8705 | 56.4611 | 91.2158 | 88.6389 | 71.2537 | 66.4116 | 60.1663 | 55.6916 | 51.1916 | 47.5758 | 45.4074 | 43.3916 | 34.5379 | 26.4811 | 19.2379 | 95.7558 | 93.7326 | 76.7053 | 71.8611 | 65.6137 | 61.1347 | 56.6295 | 53.0084 | 50.8337 | 48.8116 | 39.92 | 31.8274 | 24.5674
|  | MAIDENHEAD BSP | EE |  |  |  | 112.4968 | 111.6305 | 102.6642 | 98.4095 | 92.9611 | 89.1442 | 85.1674 | 81.9526 | 79.9632 | 78.1221 | 70.1084 | 62.8705 | 56.4611 | 92.1074 | 90 | 71.2537 | 66.4116 | 60.1663 | 55.6916 | 51.1916 | 47.5758 | 45.4074 | 43.3916 | 34.5379 | 26.4811 | 19.2379 | 96.2158 | 95.08 | 76.7053 | 71.8611 | 65.6137 | 61.1347 | 56.6295 | 53.0084 | 50.8337 | 48.8116 | 39.92 | 31.8274 | 24.5674
|  | MAIDENHEAD BSP | HT |  |  |  | 112.0621 | 110.9516 | 109.8284 | 108.6368 | 103.9263 | 99.5905 | 95.7011 | 91.94 | 89.6958 | 87.5821 | 77.5663 | 68.3379 | 60.3958 | 91.2158 | 88.6389 | 85.1537 | 79.9389 | 73.3379 | 68.2905 | 63.9389 | 59.7042 | 57.2463 | 54.9263 | 43.8526 | 33.5232 | 24.5916 | 95.7558 | 93.7326 | 90.2947 | 85.1579 | 78.6937 | 73.7389 | 69.3821 | 65.1432 | 62.6832 | 60.3589 | 49.2621 | 38.9011 | 29.9568
|  | MAIDENHEAD BSP | HE |  |  |  | 113.0821 | 112.4884 | 111.8347 | 111.1147 | 110.3368 | 107.6084 | 104.2242 | 101.0947 | 99.4232 | 97.8632 | 91.7758 | 86.6379 | 82.1274 | 93.2747 | 91.8179 | 90.0926 | 86.3032 | 81.1053 | 77.1389 | 73.2926 | 69.7411 | 67.8979 | 66.1663 | 59.3768 | 53.5347 | 48.36 | 96.8358 | 96.1916 | 95.1737 | 91.4463 | 86.3347 | 82.4663 | 78.7284 | 75.1853 | 73.3389 | 71.6084 | 64.7989 | 58.9368 | 53.7505
|  | MAIDENHEAD BSP | CF |  |  |  | 113.4126 | 113.0758 | 112.7253 | 112.3621 | 111.9863 | 112.5189 | 112.1168 | 111.7242 | 111.3337 | 110.7147 | 106.1032 | 102.7042 | 99.6642 | 93.9453 | 93.2379 | 92.4284 | 91.4726 | 90.1716 | 88.8347 | 85.9768 | 83.0653 | 81.7979 | 80.6842 | 75.5916 | 71.7463 | 68.2579 | 97.1863 | 96.8274 | 96.4505 | 96.0516 | 95.2547 | 93.9537 | 91.1432 | 88.2811 | 87.0295 | 85.9263 | 80.9253 | 77.1811 | 73.6853
MANNINGTON GSP | MANNINGTON BSP | MANNINGTON BSP | MINIMUM HEADROOM | SU 07523 05221 | YES | 8.5316 | 133.0232 | 119.5305 | 115.4126 | 111.2358 | 106.7032 | 101.8811 | 96.5526 | 91.2116 | 86.8505 | 78.2516 | 35.6884 | 16.7726 | 4.8295 | 111.1642 | 88.2989 | 83.5853 | 78.8316 | 73.6389 | 68.1158 | 61.9558 | 55.8758 | 51.0221 | 41.0326 | -8.4853 | -30.1432 | -43.4011 | 116.6368 | 94.3189 | 89.6042 | 84.8474 | 79.6516 | 74.1189 | 67.94 | 61.8421 | 56.9695 | 46.96 | -2.6916 | -24.7926 | -38.1137
|  | MANNINGTON BSP | EE |  |  |  | 133.8221 | 132.2884 | 118.4663 | 115.0221 | 111.2516 | 107.3221 | 103.2895 | 99.3147 | 95.2432 | 91.3411 | 72.1505 | 50.4379 | 38.4147 | 112.8747 | 108.9632 | 87.0421 | 83.1126 | 78.7853 | 74.3032 | 69.6789 | 65.1032 | 60.3947 | 56.0389 | 34.3221 | 9.2737 | -5.0863 | 118.3063 | 114.5021 | 93.06 | 89.1295 | 84.8 | 80.3021 | 75.6568 | 71.0568 | 66.3263 | 61.9411 | 40.0421 | 14.7905 | 0.068421
|  | MANNINGTON BSP | HT |  |  |  | 133.0232 | 119.5305 | 115.4126 | 111.2358 | 106.7032 | 101.8811 | 96.5526 | 91.2116 | 86.8505 | 78.2516 | 35.6884 | 16.7726 | 4.8295 | 111.1642 | 88.2989 | 83.5853 | 78.8316 | 73.6389 | 68.1158 | 61.9558 | 55.8758 | 51.0221 | 41.0326 | -8.4853 | -30.1432 | -43.4011 | 116.6368 | 94.3189 | 89.6042 | 84.8474 | 79.6516 | 74.1189 | 67.94 | 61.8421 | 56.9695 | 46.96 | -2.6916 | -24.7926 | -38.1137
|  | MANNINGTON BSP | HE |  |  |  | 134.8926 | 124.8926 | 122.44 | 119.9053 | 116.9389 | 113.7758 | 110.5695 | 107.3789 | 104.1505 | 101.2389 | 86.2105 | 66.3316 | 58.8579 | 115.1484 | 94.3747 | 91.5484 | 88.6484 | 85.2253 | 81.5968 | 77.8916 | 74.1863 | 70.4116 | 66.9916 | 49.5684 | 25.3737 | 16.7179 | 120.0221 | 100.3968 | 97.5684 | 94.6684 | 91.2442 | 87.6021 | 83.8895 | 80.1726 | 76.3853 | 72.9558 | 55.4526 | 30.7547 | 22.0421
|  | MANNINGTON BSP | CF |  |  |  | 135.5189 | 134.9589 | 125.8537 | 124.5505 | 123.1337 | 121.6779 | 120.1368 | 118.5221 | 116.8116 | 115.0474 | 105.28 | 99.2011 | 94.2379 | 116.5284 | 114.92 | 95.4653 | 93.9611 | 92.3242 | 90.6463 | 88.8705 | 86.9926 | 84.9863 | 82.9147 | 71.2432 | 64.0379 | 58.2863 | 120.6947 | 120.0716 | 101.4863 | 99.9821 | 98.3453 | 96.6632 | 94.8789 | 92.9979 | 90.9874 | 88.9074 | 77.2105 | 69.9726 | 64.1821
BOTLEY WOOD GSP | NETLEY COMMON BSP | NETLEY COMMON BSP | MINIMUM HEADROOM | SU 47559 12003 | YES | 46.8779 | 185.9147 | 179.5937 | 173.8305 | 124.8695 | 118.8211 | 127.5358 | 122.5842 | 118.0684 | 112.9758 | 108.6063 | 31.7779 | 6.8021 | -10.4958 | 149.0768 | 142.3221 | 136.1853 | 79.82 | 73.1916 | 84.6537 | 79.3411 | 74.4821 | 68.9095 | 64.1474 | -17.7253 | -45.8642 | -65.2611 | 155.2568 | 148.6568 | 142.4263 | 85.7211 | 79.0916 | 88.9263 | 83.6053 | 78.7389 | 73.1579 | 68.3916 | -13.5263 | -41.72 | -61.14
|  | NETLEY COMMON BSP | EE |  |  |  | 191.3716 | 179.5937 | 173.8305 | 160.5274 | 155.2821 | 150.9811 | 146.4926 | 142.7021 | 138.92 | 135.2179 | 91.1074 | 72.1747 | 56.0937 | 156.9863 | 142.3221 | 136.1853 | 121.2663 | 115.5011 | 110.8674 | 106.0042 | 101.94 | 97.8726 | 93.8621 | 50.8526 | 29.5263 | 11.2674 | 162.7632 | 148.6568 | 142.4263 | 127.18 | 121.4158 | 116.7758 | 111.9042 | 107.8326 | 103.7579 | 99.7358 | 55.0421 | 33.6495 | 15.3663
|  | NETLEY COMMON BSP | HT |  |  |  | 190.4305 | 187.9705 | 182.8442 | 124.8695 | 118.8211 | 127.5358 | 122.5842 | 118.0684 | 112.9758 | 108.6063 | 31.7779 | 6.8021 | -10.4958 | 159.0126 | 153.8411 | 146.7147 | 79.82 | 73.1916 | 84.6537 | 79.3411 | 74.4821 | 68.9095 | 64.1474 | -17.7253 | -45.8642 | -65.2611 | 164.6589 | 159.6053 | 152.6389 | 85.7211 | 79.0916 | 88.9263 | 83.6053 | 78.7389 | 73.1579 | 68.3916 | -13.5263 | -41.72 | -61.14
|  | NETLEY COMMON BSP | HE |  |  |  | 185.9147 | 183.3863 | 178.8653 | 174.4358 | 170.2726 | 166.9768 | 163.4968 | 160.7368 | 157.9705 | 155.2642 | 116.8189 | 101.7326 | 89.6684 | 149.0768 | 146.3811 | 141.5811 | 136.7632 | 132.2653 | 128.7768 | 125.0663 | 122.16 | 119.2295 | 116.3347 | 79.5442 | 62.3274 | 48.4768 | 155.2568 | 152.6232 | 147.9147 | 142.9958 | 138.4105 | 134.8674 | 131.0937 | 128.1474 | 125.1716 | 122.2316 | 83.7905 | 66.5537 | 52.68
|  | NETLEY COMMON BSP | CF |  |  |  | 193.3853 | 192.6274 | 190.7895 | 184.4189 | 182.5168 | 180.9684 | 179.2674 | 177.52 | 175.7221 | 173.8147 | 125.4842 | 131.2758 | 124.6453 | 165.1905 | 163.6537 | 160.5589 | 147.7421 | 145.6937 | 144.0526 | 142.2442 | 140.3768 | 138.4505 | 136.3989 | 87.3189 | 95.2579 | 87.8105 | 170.6895 | 169.1926 | 166.1526 | 153.8653 | 151.8674 | 150.26 | 148.4884 | 146.6653 | 144.78 | 142.6916 | 93.4063 | 99.6558 | 92.0632
MELKSHAM GSP | NORRINGTON A | NORRINGTON | MINIMUM HEADROOM | ST 88273 64983 | YES | 117.9105 | 82.0484 | 84.7589 | 59.0326 | 84.5758 | -1.2389 | -10.3 | -20.1611 | -29.4968 | -35.6989 | -47.5158 | -128.7558 | -251.3579 | -270.0758 | 29.8832 | 33.6147 | -7.8063 | 17.0979 | -83.1611 | -93.2389 | -104.2379 | -114.6842 | -121.48 | -134.8926 | -228.0926 | -355.6495 | -376.4642 | 40.1989 | 43.0295 | 1.4032 | 26.3032 | -73.9884 | -84.1053 | -95.1484 | -105.6432 | -112.4874 | -125.9547 | -219.4621 | -348.1589 | -369.1453
|  | NORRINGTON | EE |  |  |  | 105.6611 | 94.7189 | 124.94 | 122.9011 | 56.1863 | 42.7147 | 36.0368 | 28.9558 | 21.6832 | 8.1642 | -16.8232 | -156.2063 | -173.8211 | 61.0021 | 45.6432 | 69.2347 | 61.6768 | -16.2347 | -31.5663 | -38.9105 | -46.7389 | -54.8021 | -70.22 | -96.9505 | -242.7232 | -262.5189 | 72.2716 | 55.3863 | 78.4684 | 70.8926 | -7.0463 | -22.42 | -29.8221 | -37.7147 | -45.8411 | -61.3379 | -88.2368 | -234.5147 | -254.4874
|  | NORRINGTON | HT |  |  |  | 82.0484 | 84.7589 | 59.0326 | 84.5758 | -1.2389 | -10.3 | -20.1611 | -29.4968 | -35.6989 | -47.5158 | -128.7558 | -251.3579 | -270.0758 | 29.8832 | 33.6147 | -7.8063 | 17.0979 | -83.1611 | -93.2389 | -104.2379 | -114.6842 | -121.48 | -134.8926 | -228.0926 | -355.6495 | -376.4642 | 40.1989 | 43.0295 | 1.4032 | 26.3032 | -73.9884 | -84.1053 | -95.1484 | -105.6432 | -112.4874 | -125.9547 | -219.4621 | -348.1589 | -369.1453
|  | NORRINGTON | HE |  |  |  | 107.0053 | 111.84 | 145.5221 | 173.2842 | 101.8253 | 40.8589 | 35.2663 | 29.1926 | 23.1979 | 18.6726 | -24.6211 | -162.7337 | -175.5432 | 63.4621 | 69.9705 | 92.9421 | 120.2589 | 36.6768 | -34.5189 | -40.7305 | -47.5095 | -54.2316 | -59.2453 | -108.9379 | -256.1747 | -270.6916 | 74.7695 | 80.4232 | 102.1874 | 129.5053 | 45.8926 | -25.3568 | -31.5916 | -38.4063 | -45.1537 | -50.2011 | -100.1074 | -248.4695 | -263.1358
|  | NORRINGTON | CF |  |  |  | 107.7884 | 107.0305 | 158.6979 | 188.8853 | 170.4905 | 168.3189 | 173.5105 | 171.1126 | 168.2558 | 165.0442 | 94.8884 | -6.1579 | -14.7074 | 64.7674 | 63.3926 | 108.8063 | 138.7621 | 116.2147 | 113.8411 | 120.5179 | 117.8832 | 114.6989 | 111.0968 | 29.5179 | -72.6168 | -82.3095 | 76.0916 | 74.6958 | 119.4916 | 149.4095 | 126.36 | 123.9726 | 129.7368 | 127.0874 | 123.8937 | 120.2789 | 38.6042 | -63.6084 | -73.4
MELKSHAM GSP | NORRINGTON B | NORRINGTON B | MINIMUM HEADROOM | ST 88273 64983 | YES | 31.9505 | 0 | 0 | 0 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 0 | 0 | 0 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 0 | 0 | 0 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495
|  | NORRINGTON B | EE |  |  |  | 0 | 0 | 0 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 0 | 0 | 0 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 0 | 0 | 0 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495
|  | NORRINGTON B | HT |  |  |  | 0 | 0 | 0 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 0 | 0 | 0 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 0 | 0 | 0 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495
|  | NORRINGTON B | HE |  |  |  | 0 | 0 | 0 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 0 | 0 | 0 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 0 | 0 | 0 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495
|  | NORRINGTON B | CF |  |  |  | 0 | 0 | 0 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 0 | 0 | 0 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 0 | 0 | 0 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495 | 58.0495
NORTH HYDE GSP | NORTH HYDE 22kV | NORTH HYDE 22kV | MINIMUM HEADROOM | TQ 10367 79001 | NO | 0.40632 | 104.72 | 104.3653 | 104.0053 | 99.3695 | 93.8611 | 88.9295 | 84.3326 | 81.1337 | 80.2737 | 79.46 | 75.6632 | 71.8347 | 68.1684 | 95.96 | 93.6295 | 89.8421 | 83.2368 | 76.84 | 71.1158 | 65.7821 | 62.0842 | 61.1358 | 60.2326 | 56.0389 | 51.7189 | 47.5589 | 97.9579 | 95.7305 | 91.8832 | 85.2032 | 78.8021 | 73.0842 | 67.7579 | 64.0684 | 63.12 | 62.2179 | 58.0379 | 53.7253 | 49.5705
|  | NORTH HYDE 22kV | EE |  |  |  | 104.8505 | 104.5705 | 104.2726 | 100.8 | 96.0411 | 91.9642 | 87.9063 | 85.0947 | 84.3842 | 83.7242 | 80.8126 | 78.1179 | 75.5095 | 96.2842 | 94.18 | 90.7737 | 84.86 | 79.3316 | 74.6063 | 69.8926 | 66.6411 | 65.8642 | 65.1389 | 61.9042 | 58.9063 | 55.9421 | 98.1 | 96.2874 | 92.8274 | 86.8263 | 81.2947 | 76.5684 | 71.8632 | 68.62 | 67.8421 | 67.1179 | 63.8884 | 60.9011 | 57.9411
|  | NORTH HYDE 22kV | HT |  |  |  | 104.72 | 104.3653 | 104.0053 | 99.3695 | 93.8611 | 88.9295 | 84.3326 | 81.1337 | 80.2737 | 79.46 | 75.6632 | 71.8347 | 68.1684 | 95.96 | 93.6295 | 89.8421 | 83.2368 | 76.84 | 71.1158 | 65.7821 | 62.0842 | 61.1358 | 60.2326 | 56.0389 | 51.7189 | 47.5589 | 97.9579 | 95.7305 | 91.8832 | 85.2032 | 78.8021 | 73.0842 | 67.7579 | 64.0684 | 63.12 | 62.2179 | 58.0379 | 53.7253 | 49.5705
|  | NORTH HYDE 22kV | HE |  |  |  | 105.0011 | 104.7884 | 104.5495 | 101.6053 | 96.9842 | 93.0411 | 89.1116 | 86.4316 | 85.8653 | 85.3547 | 83.2032 | 81.1547 | 79.2958 | 96.6421 | 94.7347 | 91.4926 | 85.7484 | 80.3716 | 75.7947 | 71.2232 | 68.1168 | 67.4968 | 66.9337 | 64.5368 | 62.1926 | 60.0568 | 98.2642 | 96.8484 | 93.5537 | 87.7147 | 82.3358 | 77.7579 | 73.1926 | 70.0916 | 69.4716 | 68.9095 | 66.5158 | 64.1705 | 62.04
|  | NORTH HYDE 22kV | CF |  |  |  | 105.0979 | 104.96 | 104.8189 | 104.6737 | 104.5221 | 103.5021 | 101.6853 | 100.3242 | 99.9821 | 99.6295 | 97.9274 | 96.6168 | 95.4411 | 97.0537 | 96.2126 | 94.6379 | 92.0705 | 89.8053 | 87.9263 | 85.8537 | 84.2853 | 83.9095 | 83.5253 | 81.6484 | 80.1695 | 78.8242 | 98.3905 | 98.1979 | 96.7495 | 94.1379 | 91.8368 | 89.9274 | 87.8221 | 86.2505 | 85.8747 | 85.4905 | 83.6126 | 82.1337 | 80.7884
COWLEY GSP | OXFORD BSP | OXFORD BSP | MINIMUM HEADROOM | SP 50054 05983 | YES | 67.9084 | 86.9079 | 85.9595 | -6.1342 | -46.59 | -48.99 | 63.2453 | 57.2126 | 53.4937 | 49.8063 | 46.3221 | 32.1811 | 20.4358 | 14.4684 | 58.0047 | 56.1047 | -45.2511 | -92.7047 | -95.3363 | 12.2711 | 5.3953 | 1.2174 | -2.9384 | -6.8658 | -22.7163 | -35.9037 | -42.4963 | 65.5258 | 63.6268 | -37.7458 | -85.2163 | -87.85 | 21.4626 | 14.5753 | 10.3879 | 6.2184 | 2.2774 | -13.6511 | -26.9374 | -33.5711
|  | OXFORD BSP | EE |  |  |  | 87.2711 | 86.5268 | 33.21 | 31.5805 | 1.9416 | 114.1842 | 110.3116 | 107.0642 | 104.1895 | 101.6716 | 88.8284 | 78.5537 | 73.7579 | 58.0047 | 56.1047 | 1.2995 | -0.64053 | -35.5437 | 71.9974 | 67.6089 | 63.9511 | 60.7321 | 57.9195 | 43.5079 | 31.9384 | 26.6132 | 65.5258 | 63.6268 | 8.8195 | 6.8784 | -28.0384 | 81.2921 | 76.89 | 73.2163 | 69.9805 | 67.1511 | 52.5447 | 40.8332 | 35.4637
|  | OXFORD BSP | HT |  |  |  | 86.9079 | 85.9595 | -6.1342 | -46.59 | -48.99 | 63.2453 | 57.2126 | 53.4937 | 49.8063 | 46.3221 | 32.1811 | 20.4358 | 14.4684 | 60.7195 | 56.8963 | -45.2511 | -92.7047 | -95.3363 | 12.2711 | 5.3953 | 1.2174 | -2.9384 | -6.8658 | -22.7163 | -35.9037 | -42.4963 | 67.2542 | 64.4163 | -37.7458 | -85.2163 | -87.85 | 21.4626 | 14.5753 | 10.3879 | 6.2184 | 2.2774 | -13.6511 | -26.9374 | -33.5711
|  | OXFORD BSP | HE |  |  |  | 87.7479 | 87.2268 | 34.1258 | 33.4889 | 20.4542 | 94.5358 | 90.96 | 88.0337 | 85.5811 | 83.42 | 73.2295 | 65.2611 | 62.1905 | 58.8974 | 57.3932 | 2.9868 | 1.4458 | -13.9437 | 48.5416 | 44.4595 | 41.1353 | 38.3658 | 35.9247 | 24.3647 | 15.2574 | 11.8279 | 66.4195 | 64.9153 | 10.5079 | 8.9668 | -6.4268 | 57.8342 | 53.7437 | 50.4121 | 47.6342 | 45.1868 | 33.47 | 24.3258 | 20.8595
|  | OXFORD BSP | CF |  |  |  | 88.0163 | 87.7079 | 34.8605 | 34.5258 | 34.1816 | 148.12 | 147.7453 | 147.3726 | 147.0063 | 145.7484 | 135.4789 | 130.8968 | 128.8284 | 62.9574 | 62.1668 | 8.9111 | 8.2089 | 7.3847 | 116.2637 | 115.0247 | 113.3795 | 111.2668 | 109.0121 | 97.1121 | 91.9258 | 89.6005 | 68.4279 | 68.0911 | 15.2195 | 14.8647 | 14.4921 | 125.5837 | 124.3405 | 122.6921 | 120.5742 | 118.3163 | 106.3963 | 101.1016 | 98.7532
MANNINGTON GSP | POOLE PS (HAMWORTHY) | POOLE PS (HAMWORTHY) | MINIMUM HEADROOM | SZ 00203 90789 | YES | 1.5442 | 67.0505 | 66.5926 | 65.7884 | 63.6726 | 61.4947 | 60.3284 | 57.8526 | 55.1611 | 53.3779 | 51.8789 | 46.1116 | 42.3284 | 38.7505 | 59.5905 | 58.0347 | 56.1116 | 53.7716 | 51.3653 | 50.2116 | 47.4442 | 44.3705 | 42.3558 | 40.6716 | 34.22 | 30.0347 | 26.0242 | 61.6189 | 60.3811 | 58.4126 | 56.0137 | 53.5463 | 52.1853 | 49.3737 | 46.2968 | 44.2789 | 42.5905 | 36.1179 | 31.9084 | 27.8884
|  | POOLE PS (HAMWORTHY) | EE |  |  |  | 67.2242 | 66.8642 | 66.4832 | 65.3042 | 63.6505 | 61.6789 | 59.6811 | 57.0095 | 54.3242 | 54.0105 | 48.2663 | 45.3095 | 42.5716 | 59.9789 | 58.7505 | 57.2232 | 55.5695 | 53.7474 | 51.5653 | 49.3547 | 46.3379 | 43.2558 | 43.0316 | 36.5653 | 33.3063 | 30.2263 | 61.8063 | 61.1105 | 59.5474 | 57.8526 | 55.9874 | 53.7495 | 51.48 | 48.4168 | 45.3347 | 44.9474 | 38.4516 | 35.1589 | 32.0684
|  | POOLE PS (HAMWORTHY) | HT |  |  |  | 67.0505 | 66.5926 | 65.7884 | 63.6726 | 61.4947 | 60.3284 | 57.8526 | 55.1611 | 53.3779 | 51.8789 | 46.1116 | 42.3284 | 38.7505 | 59.5905 | 58.0347 | 56.1116 | 53.7716 | 51.3653 | 50.2116 | 47.4442 | 44.3705 | 42.3558 | 40.6716 | 34.22 | 30.0347 | 26.0242 | 61.6189 | 60.3811 | 58.4126 | 56.0137 | 53.5463 | 52.1853 | 49.3737 | 46.2968 | 44.2789 | 42.5905 | 36.1179 | 31.9084 | 27.8884
|  | POOLE PS (HAMWORTHY) | HE |  |  |  | 67.4463 | 67.1884 | 66.9021 | 66.3737 | 64.8926 | 63.06 | 61.2274 | 58.6347 | 56.24 | 56.1916 | 51.5168 | 49.5347 | 47.6579 | 60.4874 | 59.4937 | 58.18 | 56.7158 | 55.0758 | 53.0432 | 51.0063 | 48.0926 | 45.3316 | 45.3979 | 40.0853 | 37.8663 | 35.7347 | 62.0453 | 61.7442 | 60.5221 | 59.0211 | 57.3389 | 55.2516 | 53.1611 | 50.1758 | 47.4147 | 47.3232 | 41.9968 | 39.7695 | 37.6295
|  | POOLE PS (HAMWORTHY) | CF |  |  |  | 67.5768 | 67.4221 | 67.2621 | 67.0947 | 66.9232 | 66.7421 | 66.5579 | 66.3758 | 66.0653 | 65.0147 | 59.3189 | 57.7737 | 56.5232 | 60.8347 | 60.2958 | 59.7516 | 59.3147 | 58.9505 | 58.5463 | 58.1021 | 57.3442 | 56.4221 | 55.2505 | 48.9642 | 47.2263 | 45.8074 | 62.1884 | 62.0116 | 61.8284 | 61.6453 | 61.3158 | 60.9042 | 60.4505 | 59.6747 | 58.7274 | 57.5242 | 50.8916 | 49.1484 | 47.7242
LOVEDEAN GSP | PORTSMOUTH BSP | PORTSMOUTH BSP | MINIMUM HEADROOM | SZ 63405 99685 | YES | 1.2411 | 133.6411 | 131.5453 | 129.4316 | 127.1884 | 124.8242 | 131.4337 | 220.4674 | 215.2558 | 209.0189 | 204.1274 | 181.1642 | 160.9168 | 142.2526 | 97.1453 | 92.7263 | 87.4347 | 81.0495 | 72.7705 | 80.8411 | 163.3716 | 156.2084 | 149.2368 | 143.8221 | 118.2516 | 95.5768 | 74.5337 | 104.2032 | 101.9221 | 97.0726 | 90.7411 | 82.4747 | 90.5547 | 173.0926 | 165.9305 | 158.9653 | 153.5526 | 127.9842 | 105.3095 | 84.2842
|  | PORTSMOUTH BSP | EE |  |  |  | 134.4284 | 132.78 | 131.0326 | 129.18 | 127.2 | 141.9653 | 229.9442 | 224.2305 | 218.2621 | 212.7453 | 193.9789 | 178.0863 | 163.7179 | 98.2505 | 95.8295 | 91.5105 | 86.0484 | 80.1053 | 89.0853 | 172.6253 | 166.1495 | 159.4726 | 153.2895 | 132.4074 | 114.5905 | 98.3179 | 105.0484 | 103.2716 | 100.9642 | 95.7326 | 89.7989 | 98.7863 | 182.3305 | 175.8589 | 169.1832 | 163.0032 | 142.1063 | 124.2674 | 108.0021
|  | PORTSMOUTH BSP | HT |  |  |  | 133.6411 | 131.5453 | 129.4316 | 127.1884 | 124.8242 | 138.4105 | 221.6853 | 215.2558 | 209.0189 | 204.1274 | 181.1642 | 160.9168 | 142.2526 | 97.1453 | 92.7263 | 87.4347 | 81.0495 | 72.7705 | 80.8411 | 163.3716 | 156.2084 | 149.2368 | 143.8221 | 118.2516 | 95.5768 | 74.5337 | 104.2032 | 101.9221 | 97.0726 | 90.7411 | 82.4747 | 90.5547 | 173.0926 | 165.9305 | 158.9653 | 153.5526 | 127.9842 | 105.3095 | 84.2842
|  | PORTSMOUTH BSP | HE |  |  |  | 135.3095 | 134.0526 | 132.6642 | 131.1263 | 129.4758 | 144.5505 | 232.8568 | 231.2642 | 229.7737 | 226.7842 | 212.1789 | 200.4221 | 190.5263 | 99.3695 | 97.7916 | 95.7474 | 91.4589 | 86.5811 | 97.3453 | 182.6926 | 178.02 | 173.2432 | 169.0632 | 152.6916 | 139.1505 | 127.8389 | 106.0032 | 104.6579 | 103.1579 | 100.9232 | 96.2695 | 107.0358 | 192.3863 | 187.72 | 182.9474 | 178.7705 | 162.4032 | 148.8263 | 137.5168
|  | PORTSMOUTH BSP | CF |  |  |  | 135.8221 | 135.0074 | 134.1621 | 133.2811 | 132.3758 | 131.4337 | 220.4674 | 219.5211 | 218.5832 | 217.6495 | 230.3168 | 223.4253 | 216.8463 | 99.9589 | 99.0189 | 97.9326 | 96.5989 | 94.6326 | 92.1716 | 179.7642 | 177.2274 | 174.5547 | 171.5968 | 174.3589 | 165.1758 | 157.6516 | 106.5516 | 105.6779 | 104.7747 | 103.8074 | 102.8168 | 101.6042 | 189.3021 | 186.8832 | 184.24 | 181.2821 | 184.0611 | 174.88 | 167.3642
BRAMLEY (FLEE) | PYESTOCK BSP | PYESTOCK BSP | MINIMUM HEADROOM | SU 82940 54553 | YES | 0 | 97.2147 | 96.8495 | 96.4821 | 96.0895 | 95.6863 | 95.2726 | 94.5179 | 93.8147 | 93.1295 | 92.4621 | 89.6232 | 86.6432 | 83.9526 | 91.2958 | 90.5653 | 89.8274 | 89.0147 | 88.1653 | 87.2926 | 86.4 | 85.6147 | 84.8653 | 84.1484 | 81.0821 | 77.8084 | 74.8347 | 92.7179 | 92.2421 | 91.4926 | 90.6663 | 89.8032 | 88.9158 | 88.0074 | 87.2084 | 86.4463 | 85.7147 | 82.5853 | 79.2326 | 76.1832
|  | PYESTOCK BSP | EE |  |  |  | 97.3663 | 97.0863 | 96.7905 | 96.4737 | 96.1463 | 95.8063 | 95.48 | 95.1558 | 94.5842 | 94.0537 | 91.8863 | 89.5558 | 87.4768 | 91.6147 | 91.0495 | 90.4547 | 89.8095 | 89.1284 | 88.4389 | 87.7432 | 87.1158 | 86.4811 | 85.8853 | 83.5253 | 80.9621 | 78.6537 | 92.88 | 92.5832 | 92.1295 | 91.4747 | 90.7832 | 90.0811 | 89.3726 | 88.7347 | 88.0884 | 87.4821 | 85.0695 | 82.4389 | 80.0695
|  | PYESTOCK BSP | HT |  |  |  | 97.2147 | 96.8495 | 96.4821 | 96.0895 | 95.6863 | 95.2726 | 94.5179 | 93.8147 | 93.1295 | 92.4621 | 89.6232 | 86.6432 | 83.9526 | 91.2958 | 90.5653 | 89.8274 | 89.0147 | 88.1653 | 87.2926 | 86.4 | 85.6147 | 84.8653 | 84.1484 | 81.0821 | 77.8084 | 74.8347 | 92.7179 | 92.2421 | 91.4926 | 90.6663 | 89.8032 | 88.9158 | 88.0074 | 87.2084 | 86.4463 | 85.7147 | 82.5853 | 79.2326 | 76.1832
|  | PYESTOCK BSP | HE |  |  |  | 97.5653 | 97.38 | 97.1758 | 96.9495 | 96.7074 | 96.4463 | 96.1968 | 95.9611 | 95.7411 | 95.5526 | 94.3884 | 92.7179 | 91.2084 | 92.0368 | 91.6737 | 91.2716 | 90.8137 | 90.3095 | 89.7811 | 89.2442 | 88.7726 | 88.2926 | 87.8516 | 86.2263 | 84.3453 | 82.6526 | 93.0926 | 92.8958 | 92.6811 | 92.44 | 91.9821 | 91.4463 | 90.9011 | 90.42 | 89.9326 | 89.4832 | 87.8242 | 85.8916 | 84.1495
|  | PYESTOCK BSP | CF |  |  |  | 97.6758 | 97.5747 | 97.4695 | 97.3589 | 97.2463 | 97.1274 | 97.0084 | 96.8895 | 96.7726 | 96.6547 | 96.1326 | 95.5674 | 94.6147 | 92.2242 | 92.0779 | 91.8474 | 91.6032 | 91.3474 | 91.0789 | 90.7947 | 90.5316 | 90.2495 | 89.9621 | 88.7326 | 87.46 | 86.3421 | 93.2116 | 93.1042 | 92.9916 | 92.8726 | 92.7516 | 92.6232 | 92.4737 | 92.2063 | 91.92 | 91.6242 | 90.3726 | 89.0674 | 87.9158
BRAMLEY (FLEE) | READING BSP | READING BSP | MINIMUM HEADROOM | SU 74642 73856 | YES | 27.2137 | 219.3211 | 196.8095 | 194.2737 | 187.8337 | 167.3968 | 161.7895 | 155.8158 | 149.0926 | 142.6137 | 137.0368 | 112.9558 | 92.6442 | 75.0358 | 178.9832 | 153.9274 | 148.3968 | 129.8474 | 106.1516 | 99.9747 | 93.3495 | 85.8421 | 78.6189 | 72.4126 | 45.5979 | 22.6958 | 2.6568 | 188.2453 | 163.8316 | 158.4084 | 139.9368 | 116.2326 | 110.0474 | 103.4116 | 95.8895 | 88.6547 | 82.4347 | 55.6116 | 32.6158 | 12.5411
|  | READING BSP | EE |  |  |  | 220.3032 | 198.3474 | 196.2832 | 187.8337 | 167.3968 | 161.7895 | 155.8158 | 149.0926 | 142.6137 | 137.0368 | 112.9558 | 92.6442 | 75.0358 | 180.8063 | 157.2632 | 152.9526 | 129.8474 | 106.1516 | 99.9747 | 93.3495 | 85.8421 | 78.6189 | 72.4126 | 45.5979 | 22.6958 | 2.6568 | 189.2789 | 167.1642 | 162.8705 | 139.9368 | 116.2326 | 110.0474 | 103.4116 | 95.8895 | 88.6547 | 82.4347 | 55.6116 | 32.6158 | 12.5411
|  | READING BSP | HT |  |  |  | 219.3211 | 196.8095 | 194.2737 | 191.5832 | 188.8021 | 183.8084 | 176.3705 | 168.3874 | 161.8168 | 155.6011 | 123.2811 | 98.2611 | 76.2674 | 178.9832 | 153.9274 | 148.3968 | 141.5926 | 134.4884 | 126.6537 | 118.3189 | 109.3663 | 102.0432 | 95.1074 | 58.6842 | 30.3926 | 5.4968 | 188.2453 | 163.8316 | 158.4084 | 151.6926 | 144.5842 | 136.7411 | 128.4021 | 119.44 | 112.1084 | 105.1579 | 68.6779 | 40.2505 | 15.3232
|  | READING BSP | HE |  |  |  | 221.6158 | 200.2768 | 198.8032 | 197.1674 | 195.4126 | 193.5242 | 191.7189 | 189.2684 | 184.0684 | 179.5779 | 159.7874 | 144.2663 | 130.9453 | 183.1421 | 160.9453 | 158.2474 | 153.7884 | 149.4916 | 144.6642 | 139.1263 | 132.46 | 126.4642 | 121.3863 | 98.7768 | 80.9958 | 65.6789 | 190.66 | 169.2653 | 167.7137 | 163.7105 | 159.5042 | 154.7589 | 149.2158 | 142.5474 | 136.5432 | 131.46 | 108.7358 | 90.9232 | 75.5768
|  | READING BSP | CF |  |  |  | 222.3632 | 201.5958 | 200.8042 | 199.9789 | 199.1284 | 198.2358 | 197.3274 | 196.44 | 195.5558 | 194.6747 | 187.3968 | 174.6905 | 164.8779 | 184.9432 | 164.1263 | 163.26 | 159.9589 | 157.7916 | 155.6758 | 153.4705 | 151.2179 | 148.7663 | 146.2821 | 130.0011 | 115.3232 | 103.9642 | 191.5653 | 170.7695 | 169.9421 | 168.9242 | 167.68 | 165.5674 | 163.4074 | 161.1989 | 158.8074 | 156.3737 | 140.0779 | 125.3853 | 114.0095
BRAMLEY (FLEE) | READING TOWN BSP | READING TOWN BSP | MINIMUM HEADROOM | SU 71580 74111 | YES | 1.0705 | 107.1611 | 106.4189 | 105.6179 | 104.6947 | 102.7516 | 97.9053 | 92.4063 | 87.2221 | 81.1053 | 74.8621 | 64.9684 | 59.5842 | 54.4958 | 92.0832 | 89.2684 | 87.5768 | 84.9779 | 81.2042 | 75.6337 | 69.3147 | 63.3547 | 56.2821 | 49.0516 | 37.8926 | 31.9284 | 26.2379 | 94.7853 | 93.8168 | 92.1242 | 89.5263 | 85.7568 | 80.1926 | 73.8832 | 67.9305 | 60.8663 | 53.6474 | 42.4968 | 36.5295 | 30.8389
|  | READING TOWN BSP | EE |  |  |  | 107.4547 | 106.8758 | 106.26 | 105.4947 | 104.4421 | 100.2589 | 95.8368 | 91.2284 | 84.8084 | 78.3116 | 68.9337 | 64.8537 | 61.0137 | 92.6968 | 90.2505 | 88.8589 | 86.5484 | 83.0579 | 78.2463 | 73.16 | 67.8611 | 60.4232 | 52.8821 | 42.2463 | 37.7337 | 33.4358 | 95.0958 | 94.4021 | 93.3895 | 91.0789 | 87.5895 | 82.7811 | 77.6979 | 72.4 | 64.9726 | 57.4421 | 46.7947 | 42.2621 | 37.9453
|  | READING TOWN BSP | HT |  |  |  | 107.1611 | 106.4189 | 105.6179 | 104.6947 | 102.7516 | 97.9053 | 92.4063 | 87.2221 | 81.1053 | 74.8621 | 64.9684 | 59.5842 | 54.4958 | 92.0832 | 89.2684 | 87.5768 | 84.9779 | 81.2042 | 75.6337 | 69.3147 | 63.3547 | 56.2821 | 49.0516 | 37.8926 | 31.9284 | 26.2379 | 94.7853 | 93.8168 | 92.1242 | 89.5263 | 85.7568 | 80.1926 | 73.8832 | 67.9305 | 60.8663 | 53.6474 | 42.4968 | 36.5295 | 30.8389
|  | READING TOWN BSP | HE |  |  |  | 107.8105 | 107.3958 | 106.9379 | 106.3937 | 105.6653 | 102.6011 | 98.4368 | 93.9758 | 87.8558 | 81.76 | 74.0189 | 71.3863 | 68.9642 | 93.2947 | 91.4263 | 90.4411 | 88.4737 | 85.3211 | 80.7895 | 75.9716 | 70.8158 | 63.7 | 56.6032 | 47.7484 | 44.8105 | 42.0589 | 95.4832 | 94.9674 | 94.48 | 93.0263 | 89.8779 | 85.3516 | 80.5421 | 75.3958 | 68.2916 | 61.2084 | 52.3663 | 49.4263 | 46.6768
|  | READING TOWN BSP | CF |  |  |  | 108.0053 | 107.7505 | 107.4863 | 107.2116 | 106.9274 | 106.5674 | 106.1758 | 105.7705 | 103.7232 | 101.3705 | 91.1874 | 89.2032 | 87.4947 | 93.5168 | 93.0558 | 92.5453 | 91.4516 | 89.9337 | 88.2895 | 86.6779 | 84.8189 | 82.0337 | 79.3053 | 67.5474 | 65.3263 | 63.3789 | 95.7074 | 95.4021 | 95.1189 | 94.7968 | 94.4411 | 92.8432 | 91.2347 | 89.3779 | 86.5979 | 83.8737 | 72.1347 | 69.9179 | 67.9737
MANNINGTON GSP | REDHILL BSP | REDHILL BSP | MINIMUM HEADROOM | SZ 08581 96162 | YES | 106.3726 | 96.5005 | 93.3974 | 50.0553 | 42.8626 | 40.2784 | 37.7174 | 35.1363 | 32.9089 | 30.7637 | 0.13 | -109.8911 | -121.0532 | -131.2205 | 69.0442 | 65.6905 | 16.8747 | 8.4537 | 5.6568 | 2.8968 | 0.10737 | -2.2832 | -4.58 | -39.8674 | -151.7611 | -164.1853 | -175.6 | 75.7916 | 72.4032 | 23.3568 | 14.9358 | 12.1368 | 9.3758 | 6.5811 | 4.1884 | 1.8874 | -33.4116 | -145.3221 | -157.7674 | -169.1916
|  | REDHILL BSP | EE |  |  |  | 98.1605 | 95.1763 | 80.0047 | 42.8626 | 40.2784 | 37.7174 | 35.1363 | 32.9089 | 30.7637 | 25.3037 | -92.9321 | -101.5858 | -109.3089 | 78.0779 | 67.6074 | 51.6926 | 8.4537 | 5.6568 | 2.8968 | 0.10737 | -2.2832 | -4.58 | -10.7968 | -132.5053 | -142.16 | -150.8758 | 84.5263 | 74.3379 | 58.3274 | 14.9358 | 12.1368 | 9.3758 | 6.5811 | 4.1884 | 1.8874 | -4.3326 | -126.0716 | -135.7537 | -144.4779
|  | REDHILL BSP | HT |  |  |  | 96.5005 | 93.3974 | 50.0553 | 46.8858 | 43.7974 | 40.6932 | 37.4879 | 34.6511 | 31.7616 | 0.13 | -109.8911 | -121.0532 | -131.2205 | 69.0442 | 65.6905 | 16.8747 | 13.4295 | 10.0863 | 6.7379 | 3.2716 | 0.20316 | -2.9526 | -39.8674 | -151.7611 | -164.1853 | -175.6 | 75.7916 | 72.4032 | 23.3568 | 19.9105 | 16.5684 | 13.2179 | 9.7495 | 6.6768 | 3.5189 | -33.4116 | -145.3221 | -157.7674 | -169.1916
|  | REDHILL BSP | HE |  |  |  | 98.9479 | 97.53 | 86.4774 | 53.5226 | 51.6016 | 49.6542 | 47.6784 | 46.0837 | 44.4963 | 42.7858 | -75.7753 | -81.7753 | -87.0458 | 79.5105 | 70.1453 | 58.9316 | 20.6442 | 18.5695 | 16.4747 | 14.34 | 12.6411 | 10.9421 | 9.0737 | -113.2653 | -120.0253 | -126.04 | 85.8421 | 76.9 | 65.6653 | 27.1284 | 25.0526 | 22.9568 | 20.82 | 19.1211 | 17.4179 | 15.5484 | -106.8063 | -113.5768 | -119.5968
|  | REDHILL BSP | CF |  |  |  | 99.4195 | 98.9889 | 89.0258 | 87.1047 | 55.09 | 54.0132 | 52.8468 | 51.7784 | 50.7974 | 49.8584 | -48.2595 | -52.3479 | -55.8563 | 80.3495 | 79.5337 | 61.6811 | 58.9789 | 21.9179 | 20.7389 | 19.4589 | 18.2916 | 17.2274 | 16.2137 | -82.2189 | -86.8221 | -90.8284 | 86.3358 | 85.8832 | 68.4421 | 65.7337 | 28.2179 | 27.04 | 25.7579 | 24.5905 | 23.5253 | 22.5095 | -75.9253 | -80.5347 | -84.5453
NURSLING GSP | ROWNHAMS | ROWNHAMS | MINIMUM HEADROOM | SU 37168 16854 | YES | 2.7821 | 111.1189 | 98.3653 | 94.3842 | -17.8758 | 67.2463 | 27.2937 | 17.5747 | 13.0274 | 8.3368 | 16.7411 | -5.5916 | -24.3947 | -36.1726 | 68.8021 | 54.1021 | 49.7537 | -82.2737 | 2.3663 | -44.5705 | -55.6389 | -60.6484 | -65.8347 | -58.2484 | -83.9579 | -106.3221 | -119.5747 | 75.4589 | 60.7516 | 56.4063 | -75.6663 | 8.9747 | -37.9926 | -49.0874 | -54.1179 | -59.3316 | -51.8916 | -78.3621 | -101.5884 | -114.9074
|  | ROWNHAMS | EE |  |  |  | 118.8495 | 109.8168 | 97.3821 | 40.9495 | 108.7253 | 27.2937 | 17.5747 | 13.0274 | 8.3368 | 16.7411 | -5.5916 | -24.3947 | -36.1726 | 90.8074 | 67.4063 | 53.0274 | -13.2432 | 50.86 | -44.5705 | -55.6389 | -60.6484 | -65.8347 | -58.2484 | -83.9579 | -106.3221 | -119.5747 | 96.54 | 74.0632 | 59.68 | -6.6126 | 57.48 | -37.9926 | -49.0874 | -54.1179 | -59.3316 | -51.8916 | -78.3621 | -101.5884 | -114.9074
|  | ROWNHAMS | HT |  |  |  | 111.1189 | 98.3653 | 94.3842 | -17.8758 | 67.2463 | 63.2789 | 56.8189 | 51.3368 | 46.6189 | 53.4947 | 27.4284 | 9.8811 | -4.4484 | 68.8021 | 54.1021 | 49.7537 | -82.2737 | 2.3663 | -1.8084 | -9.2179 | -15.2916 | -20.4947 | -15.2337 | -45.7316 | -65.2211 | -81.2547 | 75.4589 | 60.7516 | 56.4063 | -75.6663 | 8.9747 | 4.6095 | -2.9358 | -9.0253 | -14.2474 | -9.4168 | -40.7021 | -60.3389 | -76.4337
|  | ROWNHAMS | HE |  |  |  | 119.8432 | 112.5284 | 100.9958 | 85.5758 | 172.7189 | 61.3547 | 52.4937 | 48.8326 | 44.4758 | 54.4021 | 35.3484 | 19.2084 | 10.7884 | 92.8442 | 70.3453 | 56.9421 | 38.98 | 125.8526 | -5.1432 | -15.2874 | -19.3421 | -24.4579 | -14.9474 | -37.6716 | -58.0463 | -67.6211 | 97.5337 | 77.0032 | 63.5958 | 45.6263 | 132.5 | 1.4495 | -8.7074 | -12.7737 | -18.0211 | -8.5242 | -32.1105 | -53.5305 | -63.1621
|  | ROWNHAMS | CF |  |  |  | 120.4116 | 119.8084 | 119.1863 | 96.3874 | 185.0432 | 183.5232 | 104.6632 | 102.8663 | 100.6874 | 98.4032 | 63.4295 | 70.9095 | 65.1947 | 93.58 | 92.7505 | 89.0695 | 51.3505 | 139.8853 | 138.2253 | 45.3221 | 43.34 | 40.9 | 38.3316 | -2.2474 | 4.5916 | -1.9042 | 98.1021 | 97.4989 | 95.7337 | 58.0032 | 146.5358 | 144.8705 | 51.9316 | 49.9432 | 47.4989 | 44.9263 | 4.3074 | 10.9453 | 4.4147
MANNINGTON GSP | SALISBURY | SALISBURY | MINIMUM HEADROOM | SU 11049 31395 | YES | 63.5547 | 127.4895 | 64.0695 | 62.6263 | 49.7295 | 34.3558 | 30.5053 | 26.7653 | 22.8632 | 18.8968 | 15.9432 | 7.3105 | -4.6663 | -14.6526 | 105.4137 | 40.4421 | 37.62 | 19.7084 | 1.8611 | -2.3811 | -6.4716 | -10.7611 | -15.1242 | -18.3095 | -26.8189 | -39.6895 | -50.8505 | 112.2358 | 47.4442 | 44.6095 | 26.4158 | 8.5926 | 4.3263 | 0.18842 | -4.1432 | -8.5568 | -11.8032 | -21.2642 | -34.5674 | -45.8663
|  | SALISBURY | EE |  |  |  | 128.0358 | 64.9232 | 63.7337 | 49.7295 | 34.3558 | 30.5053 | 26.7653 | 22.8632 | 18.8968 | 15.9432 | 7.3105 | -4.6663 | -14.6526 | 106.5853 | 42.3137 | 39.9695 | 19.7084 | 1.8611 | -2.3811 | -6.4716 | -10.7611 | -15.1242 | -18.3095 | -26.8189 | -39.6895 | -50.8505 | 112.7811 | 49.2705 | 46.9758 | 26.4158 | 8.5926 | 4.3263 | 0.18842 | -4.1432 | -8.5568 | -11.8032 | -21.2642 | -34.5674 | -45.8663
|  | SALISBURY | HT |  |  |  | 127.4895 | 64.0695 | 62.6263 | 61.0979 | 57.8684 | 57.1611 | 51.9926 | 46.6958 | 40.6189 | 37.9347 | 19.6916 | 5.6884 | -5.5579 | 105.4137 | 40.4421 | 37.62 | 34.3874 | 29.6916 | 29.4811 | 23.8442 | 17.9189 | 11.0663 | 8.1958 | -11.9032 | -27.2042 | -39.6958 | 112.2358 | 47.4442 | 44.6095 | 41.3221 | 36.5263 | 35.7505 | 29.9684 | 23.9968 | 17.1053 | 14.1937 | -6.1884 | -21.7895 | -34.4105
|  | SALISBURY | HE |  |  |  | 128.7832 | 66.0232 | 65.1842 | 53.2747 | 38.5147 | 35.2684 | 32.1842 | 29.0263 | 26.0084 | 23.9368 | 18.3347 | 10.3442 | 2.7905 | 108.1032 | 44.6568 | 43.0537 | 23.5558 | 6.3663 | 2.7768 | -0.63053 | -4.1411 | -7.4884 | -9.7474 | -15.2958 | -24.1979 | -32.7168 | 113.5295 | 50.7695 | 49.9305 | 30.2632 | 13.1053 | 9.4947 | 6.0684 | 2.54 | -0.82947 | -3.1126 | -9.3937 | -18.4253 | -27.0537
|  | SALISBURY | CF |  |  |  | 129.2179 | 66.7884 | 66.3474 | 65.8853 | 65.4042 | 64.8716 | 64.3295 | 63.7926 | 63.2663 | 62.7463 | 55.6379 | 55.0821 | 50.1221 | 109.1168 | 46.2916 | 45.4516 | 44.5789 | 43.3 | 41.8863 | 40.3495 | 38.7895 | 37.2379 | 35.8095 | 27.0916 | 27.0284 | 21.4453 | 113.9642 | 51.5347 | 51.0937 | 50.6316 | 50.1505 | 48.8516 | 47.3484 | 45.7537 | 44.1611 | 42.7011 | 33.7368 | 33.0747 | 27.3811
MANNINGTON GSP | SHAFTESBURY BSP | SHAFTESBURY BSP | MINIMUM HEADROOM | ST 85442 23791 | YES | 77.3621 | 54.3316 | 51.1568 | 47.8968 | 44.5368 | 40.1432 | 17.0326 | 13.9979 | 11.1874 | 8.7126 | 1.9326 | -33.2242 | -43.0442 | -50.1232 | 34.4726 | 31.0284 | 27.4947 | 23.8558 | 18.9968 | -5.96 | -9.2958 | -12.3758 | -15.0674 | -22.4463 | -59.3789 | -70.1516 | -77.9516 | 37.8168 | 34.3042 | 30.6968 | 26.98 | 22.0611 | -2.9179 | -6.2705 | -9.3737 | -12.0863 | -19.5063 | -56.5811 | -67.4853 | -75.3411
|  | SHAFTESBURY BSP | EE |  |  |  | 63.0642 | 52.6505 | 49.8453 | 46.9442 | 42.9895 | 17.0326 | 13.9979 | 11.1874 | 8.7126 | 6.4011 | -24.5368 | -34.0411 | -40.9011 | 44.3516 | 32.6253 | 29.5863 | 26.4326 | 22.0853 | -5.96 | -9.2958 | -12.3758 | -15.0674 | -17.58 | -49.6179 | -60.0884 | -67.7632 | 47.7579 | 35.9274 | 32.8179 | 29.5989 | 25.1505 | -2.9179 | -6.2705 | -9.3737 | -12.0863 | -14.6232 | -46.8958 | -57.5484 | -65.2832
|  | SHAFTESBURY BSP | HT |  |  |  | 54.3316 | 51.1568 | 47.8968 | 44.5368 | 40.1432 | 23.4611 | 19.9695 | 16.5147 | 11.5947 | 1.9326 | -33.2242 | -43.0442 | -50.1232 | 34.4726 | 31.0284 | 27.4947 | 23.8558 | 18.9968 | 1.8884 | -1.9358 | -5.7579 | -11.3095 | -22.4463 | -59.3789 | -70.1516 | -77.9516 | 37.8168 | 34.3042 | 30.6968 | 26.98 | 22.0611 | 4.8979 | 1.0568 | -2.7811 | -8.3474 | -19.5063 | -56.5811 | -67.4853 | -75.3411
|  | SHAFTESBURY BSP | HE |  |  |  | 56.6558 | 54.6484 | 52.4779 | 50.1379 | 46.7442 | 30.6284 | 28.1368 | 25.8621 | 23.9442 | 22.1695 | -6.52 | -13.4263 | -18.4116 | 36.9589 | 34.7632 | 32.3958 | 29.8358 | 26.0905 | 9.6116 | 6.8558 | 4.3421 | 2.2368 | 0.28737 | -29.4789 | -37.28 | -42.9221 | 40.3463 | 38.1011 | 35.6811 | 33.0674 | 29.2284 | 12.6737 | 9.9063 | 7.3811 | 5.2684 | 3.3095 | -26.5811 | -34.4358 | -40.1242
|  | SHAFTESBURY BSP | CF |  |  |  | 65.3284 | 64.2937 | 63.2126 | 62.0895 | 60.4789 | 46.1821 | 44.8579 | 43.6042 | 42.4495 | 41.2589 | 8.9421 | 6.2853 | 2.8516 | 46.7811 | 45.6484 | 44.4684 | 43.2453 | 41.4642 | 27.0053 | 25.5632 | 24.1937 | 22.9421 | 21.6463 | -12.2274 | -15.1232 | -19.0137 | 49.8989 | 48.9358 | 47.9232 | 46.8547 | 45.0316 | 30.5221 | 29.0432 | 27.6411 | 26.3611 | 25.0347 | -9.2011 | -12.1653 | -16.0926
IVER 132KV | SLOUGH | SLOUGH | MINIMUM HEADROOM | SU 95574 81752 | YES | 63.8811 | 51.2389 | 50.3379 | 49.4263 | 48.46 | 137.4611 | 136.4189 | 135.3716 | 134.4705 | 133.6284 | 132.8484 | 126.7158 | 114.9779 | 109.1789 | 46.8116 | 45.9105 | 44.7021 | 42.8674 | 131.1053 | 129.3505 | 127.6084 | 125.8189 | 124.0126 | 122.2811 | 114.2084 | 101.8737 | 95.4863 | 46.9274 | 46.0263 | 45.1147 | 44.0958 | 132.3758 | 130.6589 | 128.9547 | 127.1895 | 125.3632 | 123.6126 | 115.4305 | 102.9905 | 96.5126
|  | SLOUGH | EE |  |  |  | 51.5779 | 50.8663 | 50.1147 | 49.3137 | 138.4779 | 137.6021 | 136.7526 | 135.9453 | 135.1663 | 134.4905 | 131.6126 | 121.3421 | 116.9842 | 47.1505 | 46.4389 | 45.6884 | 44.7179 | 133.2821 | 131.8432 | 130.46 | 128.9263 | 127.3716 | 125.9842 | 119.5263 | 108.8021 | 103.9853 | 47.2663 | 46.5547 | 45.8032 | 45.0021 | 134.1663 | 133.0768 | 131.7211 | 130.2253 | 128.7116 | 127.3453 | 120.7895 | 109.9642 | 105.0726
|  | SLOUGH | HT |  |  |  | 51.2389 | 50.3379 | 49.4263 | 48.46 | 137.4611 | 136.4189 | 135.3716 | 134.4705 | 133.6284 | 132.8484 | 126.7158 | 114.9779 | 109.1789 | 46.8116 | 45.9105 | 44.7021 | 42.8674 | 131.1053 | 129.3505 | 127.6084 | 125.8189 | 124.0126 | 122.2811 | 114.2084 | 101.8737 | 95.4863 | 46.9274 | 46.0263 | 45.1147 | 44.0958 | 132.3758 | 130.6589 | 128.9547 | 127.1895 | 125.3632 | 123.6126 | 115.4305 | 102.9905 | 96.5126
|  | SLOUGH | HE |  |  |  | 52.0379 | 51.5442 | 50.9989 | 50.3968 | 139.7463 | 139.0505 | 138.3842 | 137.7547 | 137.1663 | 136.6579 | 134.9011 | 128.6084 | 126.5621 | 47.6105 | 47.1168 | 46.5716 | 45.9695 | 135.3189 | 134.6253 | 133.9621 | 132.98 | 131.8253 | 130.7621 | 126.1863 | 117.3242 | 114.2411 | 47.7263 | 47.2326 | 46.6874 | 46.0853 | 135.4347 | 134.7389 | 134.0726 | 133.4442 | 132.8558 | 131.9979 | 127.5442 | 118.6263 | 115.4905
|  | SLOUGH | CF |  |  |  | 52.3116 | 52.0284 | 51.7347 | 51.4295 | 141.1137 | 140.7832 | 140.4474 | 140.1179 | 139.7905 | 139.4653 | 138.0053 | 132.0011 | 131.5853 | 47.8842 | 47.6011 | 47.3074 | 47.0021 | 136.6863 | 136.3579 | 136.0221 | 135.6937 | 135.3684 | 135.0442 | 131.6442 | 123.7737 | 121.6053 | 48 | 47.7168 | 47.4232 | 47.1179 | 136.8021 | 136.4716 | 136.1358 | 135.8063 | 135.48 | 135.1547 | 132.9074 | 125.1379 | 122.9411
NURSLING GSP | SOUTHAMPTON (2 X 60) | SOUTHAMPTON (2 X 60) | MINIMUM HEADROOM | SU 41425 11999 | YES | 0.58632 | 74.6695 | 74.3695 | 74.0663 | 73.7442 | 73.4779 | 69.9737 | 64.2137 | 61.9768 | 60.3074 | 58.8316 | 54.9189 | 51.5916 | 48.4705 | 61.8189 | 60.8579 | 60.1295 | 59.2126 | 57.8716 | 53.1726 | 45.3874 | 42.8453 | 40.9579 | 39.3221 | 34.9832 | 31.2821 | 27.7411 | 65.4053 | 64.4305 | 63.6958 | 62.7684 | 61.4095 | 56.6337 | 48.7937 | 46.2147 | 44.2979 | 42.6379 | 38.2442 | 34.4947 | 30.9579
|  | SOUTHAMPTON (2 X 60) | EE |  |  |  | 74.8084 | 74.5863 | 74.3495 | 74.0989 | 73.9053 | 73.6168 | 73.0032 | 69.1189 | 65.5526 | 61.3579 | 57.1874 | 54.58 | 52.1695 | 62.0937 | 61.2737 | 60.6726 | 59.9242 | 58.7621 | 57.7705 | 56.7526 | 52.1905 | 48.0674 | 42.1095 | 37.4547 | 34.5442 | 31.8358 | 65.6095 | 64.8505 | 64.2432 | 63.4863 | 62.3074 | 61.3032 | 60.2726 | 55.6358 | 51.4779 | 45.4611 | 40.7421 | 37.7926 | 35.0484
|  | SOUTHAMPTON (2 X 60) | HT |  |  |  | 74.6695 | 74.3695 | 74.0663 | 73.7442 | 73.4779 | 69.9737 | 64.2137 | 61.9768 | 60.3074 | 58.8316 | 54.9189 | 51.5916 | 48.4705 | 61.8189 | 60.8579 | 60.1295 | 59.2126 | 57.8716 | 53.1726 | 45.3874 | 42.8453 | 40.9579 | 39.3221 | 34.9832 | 31.2821 | 27.7411 | 65.4053 | 64.4305 | 63.6958 | 62.7684 | 61.4095 | 56.6337 | 48.7937 | 46.2147 | 44.2979 | 42.6379 | 38.2442 | 34.4947 | 30.9579
|  | SOUTHAMPTON (2 X 60) | HE |  |  |  | 74.8968 | 74.7095 | 74.5021 | 74.2737 | 74.1042 | 73.8421 | 71.0242 | 69.1053 | 66.4263 | 64.3811 | 59.6189 | 57.4474 | 55.7379 | 62.3105 | 61.6611 | 61.1758 | 60.5337 | 59.4758 | 58.5863 | 54.1316 | 51.0126 | 47.8926 | 45.5495 | 40.1053 | 37.6568 | 35.7221 | 65.7053 | 65.2432 | 64.7526 | 64.1042 | 63.0295 | 62.1295 | 57.6779 | 54.5063 | 51.3358 | 48.9558 | 43.4295 | 40.9463 | 38.9811
|  | SOUTHAMPTON (2 X 60) | CF |  |  |  | 74.9537 | 74.8211 | 74.6842 | 74.5421 | 74.4747 | 74.3221 | 74.1674 | 74.0147 | 73.8642 | 72.1768 | 68.3347 | 68.7189 | 67.5726 | 62.6853 | 62.5158 | 62.3 | 62.0137 | 61.6347 | 60.9537 | 60.2874 | 59.6863 | 57.8263 | 55.6368 | 51.2842 | 52.5579 | 51.2484 | 65.7874 | 65.6505 | 65.5053 | 65.3537 | 65.2211 | 64.5295 | 63.8547 | 63.2463 | 61.3558 | 59.1326 | 54.7137 | 56.3726 | 55.0621
NURSLING GSP | SOUTHAMPTON (2 X 90) | SOUTHAMPTON (2 X 90) | MINIMUM HEADROOM | SU 41425 11999 | YES | 4.3905 | 112.1095 | 111.2695 | 110.4211 | 109.5189 | 107.58 | 104.1421 | 100.9389 | 98.1547 | 95.4358 | 93.2747 | 84.2032 | 76.5358 | 69.4716 | 90.2663 | 88.9516 | 86.9579 | 84.2168 | 81.5432 | 77.7126 | 74.1568 | 71.0674 | 68.0411 | 65.6547 | 55.56 | 46.9453 | 38.9621 | 95.0211 | 93.9926 | 91.9547 | 89.2495 | 86.5516 | 82.6705 | 79.0705 | 75.9421 | 72.8758 | 70.4611 | 60.3621 | 51.7463 | 43.76
|  | SOUTHAMPTON (2 X 90) | EE |  |  |  | 112.44 | 111.7874 | 111.0968 | 110.36 | 109.5789 | 107.2589 | 104.8168 | 101.7389 | 98.9295 | 97.26 | 89.5842 | 83.6284 | 78.2432 | 90.8316 | 89.8284 | 88.36 | 86.0653 | 83.8116 | 81.14 | 78.4326 | 74.9853 | 71.8421 | 70.0147 | 61.4905 | 54.7832 | 48.6684 | 95.3937 | 94.6789 | 93.3726 | 91.0789 | 88.8432 | 86.1389 | 83.3979 | 79.9032 | 76.7189 | 74.8695 | 66.2895 | 59.5853 | 53.4684
|  | SOUTHAMPTON (2 X 90) | HT |  |  |  | 112.1095 | 111.2695 | 110.4211 | 109.5189 | 107.58 | 104.1421 | 100.9389 | 98.1547 | 95.4358 | 93.2747 | 84.2032 | 76.5358 | 69.4716 | 90.2663 | 88.9516 | 86.9579 | 84.2168 | 81.5432 | 77.7126 | 74.1568 | 71.0674 | 68.0411 | 65.6547 | 55.56 | 46.9453 | 38.9621 | 95.0211 | 93.9926 | 91.9547 | 89.2495 | 86.5516 | 82.6705 | 79.0705 | 75.9421 | 72.8758 | 70.4611 | 60.3621 | 51.7463 | 43.76
|  | SOUTHAMPTON (2 X 90) | HE |  |  |  | 112.8105 | 112.3253 | 111.7863 | 111.1926 | 110.5516 | 109.8263 | 107.6968 | 105.3505 | 103.0453 | 101.9832 | 96.1516 | 91.7263 | 87.9989 | 91.5168 | 90.8295 | 89.9137 | 88.1516 | 86.2684 | 83.9411 | 81.5758 | 78.9516 | 76.3695 | 75.2168 | 68.6926 | 63.7095 | 59.4305 | 95.8179 | 95.2979 | 94.6926 | 93.1453 | 91.2821 | 88.9695 | 86.5737 | 83.9137 | 81.2979 | 80.1326 | 73.5253 | 68.48 | 64.2
|  | SOUTHAMPTON (2 X 90) | CF |  |  |  | 113.0368 | 112.7337 | 112.4211 | 112.0937 | 111.7579 | 111.4084 | 111.0537 | 110.7042 | 110.3568 | 109.5011 | 105.5053 | 102.3768 | 99.8884 | 91.8821 | 91.4063 | 90.9505 | 90.4768 | 89.9958 | 89.4979 | 88.3316 | 86.9389 | 85.1484 | 83.5411 | 79.1516 | 75.6505 | 72.8326 | 96.0684 | 95.7347 | 95.3979 | 95.0453 | 94.6842 | 94.3095 | 93.3442 | 91.9421 | 90.1811 | 88.56 | 84.1221 | 80.5695 | 77.7116
NURSLING GSP | (NEW) SOUTHAMPTON (3 X 90) | SOUTHAMPTON (3X 90) | MINIMUM HEADROOM | SU 41425 11999 | YES | 0.078947 | 0 | 0 | 0 | 0 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 0 | 0 | 0 | 0 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 0 | 0 | 0 | 0 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211
|  | SOUTHAMPTON (3X 90) | EE |  |  |  | 0 | 0 | 0 | 0 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 0 | 0 | 0 | 0 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 0 | 0 | 0 | 0 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211
|  | SOUTHAMPTON (3X 90) | HT |  |  |  | 0 | 0 | 0 | 0 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 0 | 0 | 0 | 0 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 0 | 0 | 0 | 0 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211
|  | SOUTHAMPTON (3X 90) | HE |  |  |  | 0 | 0 | 0 | 0 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 0 | 0 | 0 | 0 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 0 | 0 | 0 | 0 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211
|  | SOUTHAMPTON (3X 90) | CF |  |  |  | 0 | 0 | 0 | 0 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 0 | 0 | 0 | 0 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 0 | 0 | 0 | 0 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211 | 179.9211
LALEHAM | STAINES | STAINES | MINIMUM HEADROOM | TQ 04585 72135 | YES | 3.7295 | 222.2589 | 220.7368 | 219.2032 | 217.5726 | 215.8853 | 214.1358 | 212.3726 | 210.8221 | 175.6137 | 171.8495 | 158.7095 | 146.7021 | 135.6505 | 187.56 | 185.6505 | 181.1158 | 172.9589 | 169.7232 | 166.3316 | 162.7211 | 159.1632 | 111.1274 | 106.94 | 92.4716 | 79.1147 | 66.7116 | 194.0789 | 192.5558 | 191.0232 | 183.9768 | 180.7863 | 177.3884 | 173.7684 | 170.2074 | 122.1705 | 117.9779 | 103.4821 | 90.0947 | 77.6737
|  | STAINES | EE |  |  |  | 222.8295 | 221.6295 | 220.3611 | 219.0137 | 217.6042 | 216.1305 | 214.7084 | 213.3505 | 212.0389 | 210.7442 | 200.2716 | 190.9726 | 182.5726 | 188.1674 | 186.8821 | 183.0895 | 172.9589 | 169.7232 | 166.3316 | 162.7211 | 159.1632 | 155.9179 | 152.1442 | 140.6484 | 130.3053 | 120.8453 | 194.6474 | 193.4453 | 192.1768 | 183.9768 | 180.7863 | 177.3884 | 173.7684 | 170.2074 | 166.9537 | 163.1705 | 151.6295 | 141.2358 | 131.7484
|  | STAINES | HT |  |  |  | 222.2589 | 220.7368 | 219.2032 | 217.5726 | 215.8853 | 214.1358 | 212.3726 | 210.8221 | 175.6137 | 171.8495 | 158.7095 | 146.7021 | 135.6505 | 187.56 | 185.6505 | 181.1158 | 176.2726 | 172.24 | 168.1074 | 163.7558 | 160.1158 | 111.1274 | 106.94 | 92.4716 | 79.1147 | 66.7116 | 194.0789 | 192.5558 | 191.0232 | 187.1253 | 183.1789 | 179.1305 | 174.8253 | 171.1821 | 122.1705 | 117.9779 | 103.4821 | 90.0947 | 77.6737
|  | STAINES | HE |  |  |  | 223.6074 | 222.7747 | 221.8558 | 220.8379 | 219.7432 | 218.5726 | 217.4526 | 216.3947 | 188.0589 | 185.3021 | 177.8926 | 171.4947 | 165.7937 | 188.9516 | 188.0853 | 187.0758 | 183.8926 | 181.3168 | 178.5947 | 175.6537 | 172.7295 | 124.6853 | 121.6011 | 113.4253 | 106.2263 | 99.7326 | 195.4284 | 194.5947 | 193.6758 | 192.6579 | 191.5632 | 189.4 | 186.5232 | 183.6663 | 135.7389 | 132.6526 | 124.4579 | 117.2442 | 110.7337
|  | STAINES | CF |  |  |  | 224.0505 | 223.5621 | 223.0579 | 222.5337 | 221.9905 | 221.4305 | 220.8537 | 220.2853 | 219.7253 | 219.1663 | 216.6716 | 215.4126 | 214.7042 | 189.3947 | 188.9063 | 188.3884 | 187.8189 | 187.2442 | 186.6463 | 185.0326 | 183.4253 | 181.7337 | 179.4095 | 172.2179 | 167.1874 | 162.8021 | 195.8716 | 195.3832 | 194.8789 | 194.3547 | 193.8116 | 193.2516 | 192.6747 | 192.1074 | 191.5474 | 190.2116 | 183.1884 | 178.2558 | 173.8663
MINETY GSP | STRATTON (2 X 60) | STRATTON (2 X 60) | MINIMUM HEADROOM | SU 17028 88748 | YES | 46.4463 | 32.7021 | -7.9863 | 19.6211 | 14.9947 | 12.8242 | -47.6095 | -52.5979 | -57.6168 | -62.6421 | -92.78 | -169.8432 | -185.4305 | -193.0432 | 4.8768 | -42.9379 | -15.5779 | -21.0074 | -23.3916 | -93.9074 | -99.5232 | -105.1979 | -109.9421 | -145.1284 | -228.2589 | -245.1737 | -253.6074 | 4.6926 | -43.1474 | -15.7874 | -21.2221 | -23.6095 | -94.1768 | -99.8189 | -105.5189 | -110.8421 | -146.0705 | -229.4179 | -246.5663 | -255.0937
|  | STRATTON (2 X 60) | EE |  |  |  | 33.3126 | 31.6 | 21.0011 | 14.9947 | 12.8242 | 9.7989 | -14.7989 | -17.7811 | -23.5253 | -26.2211 | -87.3453 | -114.1147 | -122.4284 | 5.5284 | 3.6547 | -14.0895 | -21.0074 | -23.3916 | -26.7389 | -55.4053 | -58.6905 | -64.0432 | -67.0032 | -131.4011 | -161.4126 | -170.7705 | 5.3442 | 3.4632 | -14.2979 | -21.2221 | -23.6095 | -26.9779 | -55.6842 | -59.0074 | -65.0863 | -68.0937 | -132.7895 | -163.1284 | -172.5926
|  | STRATTON (2 X 60) | HT |  |  |  | 32.7021 | -7.9863 | 19.6211 | 17.1389 | 14.0126 | -47.6095 | -52.5979 | -57.6168 | -62.6421 | -92.78 | -169.8432 | -185.4305 | -193.0432 | 4.8768 | -42.9379 | -15.5779 | -18.3116 | -21.7979 | -93.9074 | -99.5232 | -105.1979 | -109.9421 | -145.1284 | -228.2589 | -245.1737 | -253.6074 | 4.6926 | -43.1474 | -15.7874 | -18.5221 | -22.0105 | -94.1768 | -99.8189 | -105.5189 | -110.8421 | -146.0705 | -229.4179 | -246.5663 | -255.0937
|  | STRATTON (2 X 60) | HE |  |  |  | 34.0811 | 32.9937 | 22.88 | 21.1674 | 19.4768 | 17.0937 | 14.8242 | 12.3632 | 8.5874 | 6.3968 | -51.4989 | -75.3189 | -81.7316 | 6.3358 | 5.1558 | -12.0611 | -13.9674 | -15.8368 | -18.4842 | -21.0063 | -23.7516 | -27.4537 | -29.9011 | -90.94 | -118.0179 | -125.2916 | 6.1526 | 4.9653 | -12.2684 | -14.1747 | -16.0442 | -18.7105 | -21.2495 | -24.0116 | -28.0747 | -30.5389 | -91.7189 | -118.8947 | -126.2547
|  | STRATTON (2 X 60) | CF |  |  |  | 34.5789 | 34.0032 | 63.3537 | 24.0211 | 23.2137 | 22.2126 | 21.2032 | 20.1358 | 17.5232 | 16.1884 | -25.3063 | -32.5358 | -37.0274 | 6.8684 | 6.2421 | 35.5326 | -10.8126 | -11.7053 | -12.8126 | -13.9232 | -15.1053 | -17.5274 | -19.0221 | -61 | -68.72 | -73.8221 | 6.6853 | 6.0568 | 35.3484 | -11.0116 | -11.9053 | -13.0211 | -14.1484 | -15.3368 | -18.1116 | -19.6137 | -61.6316 | -69.4147 | -74.5758
MINETY GSP | STRATTON (2 X 90) | STRATTON (2 X 90) | MINIMUM HEADROOM | SU 17028 88748 | YES | 52.2274 | 103.0158 | 102.1937 | 101.3663 | 100.4863 | 99.5747 | 98.6337 | 97.3095 | 94.7032 | 92.2474 | 90.1263 | 80.0158 | 20.4063 | 12.1811 | 91.9347 | 90.2579 | 88.5842 | 86.9726 | 85.2663 | 83.0716 | 80.3495 | 77.4989 | 74.8084 | 72.4547 | 61.0811 | 0.31789 | -9.0421 | 95.0011 | 93.3811 | 91.7432 | 90.1632 | 88.4926 | 86.3526 | 83.7105 | 80.9474 | 78.3411 | 76.0463 | 64.6705 | 3.9053 | -5.4568
|  | STRATTON (2 X 90) | EE |  |  |  | 103.0442 | 102.3968 | 101.7116 | 100.9821 | 100.2189 | 99.4284 | 98.6653 | 97.5021 | 95.1579 | 92.9863 | 84.1747 | 26.2768 | 20.3168 | 91.9347 | 90.6453 | 89.2979 | 87.2905 | 86.0937 | 84.4979 | 82.5726 | 80.3274 | 77.7558 | 75.3705 | 65.4379 | 6.5821 | -0.051579 | 95.0011 | 93.6716 | 92.3442 | 90.3937 | 89.2168 | 87.6558 | 85.7811 | 83.6032 | 81.1126 | 78.8053 | 68.9411 | 10.08 | 3.5358
|  | STRATTON (2 X 90) | HT |  |  |  | 103.0158 | 102.1937 | 101.3663 | 100.4863 | 99.5747 | 98.6337 | 97.3095 | 94.7032 | 92.2474 | 90.1263 | 80.0158 | 20.4063 | 12.1811 | 91.9758 | 90.2579 | 88.5842 | 86.9726 | 85.2663 | 83.0716 | 80.3495 | 77.4989 | 74.8084 | 72.4547 | 61.0811 | 0.31789 | -9.0421 | 95.0579 | 93.3811 | 91.7432 | 90.1632 | 88.4926 | 86.3526 | 83.7105 | 80.9474 | 78.3411 | 76.0463 | 64.6705 | 3.9053 | -5.4568
|  | STRATTON (2 X 90) | HE |  |  |  | 103.4663 | 103.0179 | 102.5211 | 101.9716 | 101.3821 | 100.7516 | 100.1495 | 99.5821 | 98.6884 | 96.8389 | 89.76 | 33.4358 | 28.4916 | 92.7568 | 91.9505 | 91.0642 | 90.2042 | 89.2768 | 87.8589 | 86.04 | 83.8358 | 81.5232 | 79.4811 | 71.5221 | 14.4011 | 8.6926 | 95.4716 | 94.9989 | 94.1095 | 93.2316 | 92.3116 | 90.9263 | 89.1621 | 87.0305 | 84.7947 | 82.8232 | 75.0253 | 17.9032 | 12.1926
|  | STRATTON (2 X 90) | CF |  |  |  | 103.7189 | 103.46 | 103.1937 | 102.9158 | 102.6295 | 102.3316 | 102.0284 | 101.7316 | 101.4379 | 101.1411 | 98.66 | 43.7589 | 40.6905 | 93.1926 | 92.7137 | 92.2421 | 91.7674 | 91.2632 | 90.6421 | 89.9811 | 89.12 | 88.1611 | 87.0874 | 81.3853 | 25.9926 | 22.4558 | 95.7358 | 95.4632 | 95.1821 | 94.8326 | 94.3137 | 93.6726 | 93.0126 | 92.1758 | 91.2463 | 90.2063 | 84.6968 | 29.4937 | 25.96
MINETY GSP | SWINDON BSP | SWINDON BSP | MINIMUM HEADROOM | SU 12447 87062 | YES | 23.4758 | 109.8379 | 108.3768 | 86.8537 | 85.2453 | 68.0674 | 63.5179 | 58.9832 | 54.0032 | 47.8779 | 49.2474 | 14.7568 | -2.5074 | -15.8779 | 90.04 | 87.4653 | 64.2863 | 61.0189 | 39.6758 | 34.4811 | 29.3021 | 23.5737 | 16.4526 | 18.5074 | -20.7537 | -41.0716 | -56.2611 | 94.3263 | 92.3042 | 69.1221 | 65.8558 | 44.5021 | 39.2968 | 34.1053 | 28.3642 | 21.2368 | 22.4368 | -16.9 | -37.7589 | -52.9926
|  | SWINDON BSP | EE |  |  |  | 110.3842 | 109.2589 | 88.0316 | 86.5947 | 68.0674 | 63.5179 | 58.9832 | 54.0032 | 47.8779 | 49.2474 | 33.1684 | 13.0895 | 2.5379 | 90.9242 | 89.2568 | 67.0053 | 62.8916 | 39.6758 | 34.4811 | 29.3021 | 23.5737 | 16.4526 | 18.5074 | 0.42211 | -21.8074 | -33.8347 | 94.8705 | 93.7516 | 71.8421 | 67.7274 | 44.5021 | 39.2968 | 34.1053 | 28.3642 | 21.2368 | 22.4368 | 4.2295 | -17.7032 | -29.7768
|  | SWINDON BSP | HT |  |  |  | 109.8379 | 108.3768 | 86.8537 | 85.2453 | 81.9895 | 82.4211 | 76.1011 | 70.1505 | 64.9358 | 56.1421 | 14.7568 | -2.5074 | -15.8779 | 90.04 | 87.4653 | 64.2863 | 61.0189 | 56.7716 | 57.7695 | 50.4989 | 43.6347 | 37.6326 | 27.3042 | -20.7537 | -41.0716 | -56.2611 | 94.3263 | 92.3042 | 69.1221 | 65.8558 | 61.6053 | 61.7716 | 54.4895 | 47.6137 | 41.5979 | 31.2526 | -16.9 | -37.7589 | -52.9926
|  | SWINDON BSP | HE |  |  |  | 111.1032 | 110.3295 | 89.4589 | 88.4884 | 87.3842 | 85.6621 | 81.4484 | 76.5411 | 70.7579 | 72.7737 | 60.1221 | 37.7137 | 29.5221 | 91.9695 | 90.9453 | 69.6589 | 68.1221 | 65.6495 | 60.7147 | 55.8579 | 50.1537 | 43.3821 | 46.12 | 31.5011 | 3.9937 | -5.4411 | 95.5842 | 94.8126 | 73.9484 | 72.9611 | 70.4874 | 65.5453 | 60.68 | 54.9663 | 48.1853 | 50.0947 | 35.4232 | 7.2105 | -2.2611
|  | SWINDON BSP | CF |  |  |  | 111.5168 | 111.0611 | 90.5884 | 90.0989 | 89.5874 | 89.0442 | 88.4863 | 87.8905 | 87.2547 | 86.5779 | 77.9053 | 71.6211 | 66.6337 | 92.5189 | 91.9053 | 71.2779 | 70.6263 | 69.9211 | 69.1389 | 68.2558 | 66.7905 | 64.7116 | 62.0484 | 51.9074 | 44.6063 | 38.7684 | 95.9958 | 95.5432 | 75.0716 | 74.5842 | 74.0768 | 73.5358 | 72.9821 | 71.6189 | 69.5379 | 66.8684 | 55.8874 | 48.5621 | 42.7
BRAMLEY (ANDO-THAT) | THATCHAM BSP | THATCHAM BSP | MINIMUM HEADROOM | SU 52824 66435 | YES | 50.2579 | 173.3474 | 171.0747 | 168.7842 | 227.5063 | 167.0642 | 162.0379 | 156.8958 | 151.6053 | 146.4621 | 142.1189 | 126.1337 | 118.8158 | 107.7411 | 122.5189 | 118.3147 | 113.1084 | 167.3674 | 97.9284 | 92.4653 | 86.8589 | 81.0663 | 75.4358 | 70.6905 | 53.3011 | 48.3316 | 35.8811 | 130.1663 | 125.8937 | 120.7442 | 175.1389 | 104.5158 | 98.9926 | 93.3168 | 87.4495 | 81.7453 | 76.9411 | 59.2947 | 54.74 | 42.2684
|  | THATCHAM BSP | EE |  |  |  | 174.2211 | 172.4484 | 170.5684 | 227.5063 | 167.0642 | 162.0379 | 156.8958 | 151.6053 | 146.4621 | 142.1189 | 126.1337 | 118.8158 | 107.7411 | 123.9726 | 120.8537 | 116.5463 | 167.3674 | 97.9284 | 92.4653 | 86.8589 | 81.0663 | 75.4358 | 70.6905 | 53.3011 | 48.3316 | 35.8811 | 131.7895 | 128.4074 | 124.1516 | 175.1389 | 104.5158 | 98.9926 | 93.3168 | 87.4495 | 81.7453 | 76.9411 | 59.2947 | 54.74 | 42.2684
|  | THATCHAM BSP | HT |  |  |  | 173.3474 | 171.0747 | 168.7842 | 231.9674 | 225.7558 | 219.7126 | 213.1442 | 206.3432 | 201.0663 | 196.3726 | 177.2042 | 160.7653 | 147.1158 | 122.5189 | 118.3147 | 113.1084 | 172.8589 | 166.0747 | 159.5084 | 152.3326 | 144.8442 | 139.08 | 133.9663 | 113.1421 | 95.1189 | 80.0958 | 130.1663 | 125.8937 | 120.7442 | 180.5621 | 173.8642 | 167.2621 | 160.0042 | 152.4168 | 146.5853 | 141.4074 | 120.3137 | 102.0326 | 86.8063
|  | THATCHAM BSP | HE |  |  |  | 175.4274 | 174.2232 | 172.8947 | 237.2137 | 219.6642 | 215.8316 | 211.5663 | 207.0989 | 202.8411 | 199.4263 | 188.0505 | 176.8042 | 169.6726 | 125.9 | 123.8758 | 120.9095 | 182.8947 | 158.1168 | 153.9611 | 149.2926 | 144.3747 | 139.6811 | 135.9368 | 123.4389 | 109.1242 | 101.1389 | 133.9253 | 131.6611 | 128.4726 | 190.5021 | 165.7011 | 161.5 | 156.7737 | 151.7926 | 147.0432 | 143.2453 | 130.5842 | 116.1505 | 108.0379
|  | THATCHAM BSP | CF |  |  |  | 176.1253 | 175.4484 | 174.7484 | 239.8063 | 239.0505 | 238.2663 | 237.4663 | 236.6779 | 235.8989 | 235.1158 | 226.6821 | 219.3116 | 214.4695 | 128.1053 | 125.8611 | 124.4053 | 188.5579 | 186.5632 | 184.7274 | 182.6116 | 180.5484 | 178.7021 | 176.6211 | 166.8495 | 158.6232 | 153.1937 | 136.0021 | 133.8695 | 132.1947 | 196.1084 | 194.1368 | 192.3168 | 190.2305 | 188.1905 | 186.3611 | 184.3042 | 174.6432 | 166.2937 | 160.7768
MINETY GSP | TOOTHILL BSP | TOOTHILL BSP | MINIMUM HEADROOM | SU 13191 83945 | YES | 38.6884 | 103.5916 | 102.8568 | 102.1158 | 173.1603 | 168.755 | 163.3887 | 118.9224 | 114.1339 | 109.5508 | 105.6434 | 91.2645 | 83.0171 | 75.4592 | 86.3284 | 84.5274 | 81.9042 | 144.7321 | 139.7763 | 133.7153 | 82.5268 | 77.1216 | 71.9121 | 67.4321 | 51.1405 | 41.6479 | 33.0437 | 93.18 | 91.1221 | 87.9663 | 155.3858 | 150.3553 | 144.2016 | 92.1289 | 86.6353 | 81.3742 | 76.8974 | 60.6384 | 51.1016 | 42.4984
|  | TOOTHILL BSP | EE |  |  |  | 103.8695 | 103.2926 | 102.6821 | 174.4961 | 170.4192 | 165.6876 | 160.4518 | 155.7466 | 151.0897 | 147.1139 | 137.095 | 131.0929 | 125.1182 | 87.4632 | 85.2495 | 82.8747 | 146.0816 | 141.5679 | 136.2174 | 130.2858 | 124.9626 | 119.6879 | 115.1942 | 104.0332 | 97.5574 | 90.8384 | 93.6884 | 91.9158 | 89.0737 | 156.8321 | 152.1647 | 146.73 | 140.7026 | 135.2921 | 129.9311 | 125.3647 | 114.0058 | 107.3921 | 100.5584
|  | TOOTHILL BSP | HT |  |  |  | 103.5916 | 102.8568 | 102.1158 | 173.1603 | 168.755 | 163.3887 | 118.9224 | 114.1339 | 109.5508 | 105.6434 | 91.2645 | 83.0171 | 75.4592 | 86.3284 | 84.5274 | 81.9042 | 144.7321 | 139.7763 | 133.7153 | 82.5268 | 77.1216 | 71.9121 | 67.4321 | 51.1405 | 41.6479 | 33.0437 | 93.18 | 91.1221 | 87.9663 | 155.3858 | 150.3553 | 144.2016 | 92.1289 | 86.6353 | 81.3742 | 76.8974 | 60.6384 | 51.1016 | 42.4984
|  | TOOTHILL BSP | HE |  |  |  | 104.2432 | 103.8442 | 103.4011 | 176.0582 | 172.2582 | 167.7676 | 124.3571 | 120.0161 | 115.6392 | 112.0287 | 103.3887 | 98.5424 | 93.8634 | 88.1211 | 86.1789 | 84.0842 | 147.5584 | 143.5279 | 138.4342 | 88.4153 | 83.4879 | 78.5153 | 74.3826 | 64.4395 | 58.8984 | 53.4963 | 94.0863 | 92.9358 | 90.4432 | 158.5132 | 154.1426 | 148.9668 | 98.0784 | 93.0721 | 88.0163 | 83.8458 | 73.8995 | 68.3553 | 62.9542
|  | TOOTHILL BSP | CF |  |  |  | 104.4589 | 104.2253 | 103.9842 | 177.5161 | 177.255 | 176.8213 | 174.8171 | 172.8792 | 170.7434 | 168.6634 | 161.915 | 159.1329 | 156.2108 | 88.4863 | 87.9137 | 86.2084 | 151.2658 | 149.8226 | 148.2647 | 146.3995 | 144.2058 | 141.7847 | 139.43 | 131.8321 | 128.7216 | 125.4079 | 94.3147 | 94.0526 | 92.9368 | 163.1437 | 161.3542 | 159.3595 | 157.0532 | 154.8258 | 152.3658 | 149.9721 | 142.2563 | 139.0953 | 135.7237
IVER 132KV | UPTON BSP | UPTON BSP | MINIMUM HEADROOM | TQ 00838 79445 | YES | 1.9958 | 69.8379 | 68.9305 | 68.0158 | 66.7632 | 65.7768 | 64.2705 | 63.0495 | 61.9926 | 61.02 | 60.1042 | 55.6011 | 51.1779 | 47.1611 | 58.9011 | 57.9189 | 56.9421 | 55.5716 | 54.5221 | 52.86 | 51.5358 | 50.3937 | 49.34 | 48.3463 | 43.3905 | 38.4568 | 33.9432 | 61.3547 | 60.4042 | 59.4568 | 58.1432 | 57.1253 | 55.4705 | 54.1463 | 53.0053 | 51.9526 | 50.96 | 46.0095 | 41.0832 | 36.5758
|  | UPTON BSP | EE |  |  |  | 70.0747 | 69.5316 | 68.7979 | 67.4789 | 66.9021 | 65.6505 | 64.6568 | 63.8116 | 62.9768 | 62.2 | 58.7611 | 55.5032 | 52.4737 | 59.3242 | 58.5663 | 57.7842 | 56.3168 | 55.7305 | 54.3495 | 53.2705 | 52.3621 | 51.4642 | 50.6242 | 46.8495 | 43.2011 | 39.7811 | 61.7621 | 61.0295 | 60.2695 | 58.8747 | 58.2926 | 56.9579 | 55.8789 | 54.9716 | 54.0758 | 53.2347 | 49.4642 | 45.8221 | 42.4063
|  | UPTON BSP | HT |  |  |  | 69.8379 | 68.9305 | 68.0158 | 66.7632 | 65.7768 | 64.2705 | 63.0495 | 61.9926 | 61.02 | 60.1042 | 55.6011 | 51.1779 | 47.1611 | 58.9011 | 57.9189 | 56.9421 | 55.5716 | 54.5221 | 52.86 | 51.5358 | 50.3937 | 49.34 | 48.3463 | 43.3905 | 38.4568 | 33.9432 | 61.3547 | 60.4042 | 59.4568 | 58.1432 | 57.1253 | 55.4705 | 54.1463 | 53.0053 | 51.9526 | 50.96 | 46.0095 | 41.0832 | 36.5758
|  | UPTON BSP | HE |  |  |  | 70.3758 | 70.0474 | 69.6853 | 68.2547 | 67.8116 | 67.2421 | 66.4379 | 65.7874 | 65.1505 | 64.5726 | 62.1221 | 60.2337 | 58.4316 | 59.8737 | 59.3747 | 58.84 | 57.1158 | 56.6663 | 56.0726 | 55.2 | 54.5021 | 53.8168 | 53.1926 | 50.4926 | 48.3789 | 46.3211 | 62.2916 | 61.8074 | 61.2853 | 59.6621 | 59.2158 | 58.6337 | 57.7958 | 57.1095 | 56.4263 | 55.8021 | 53.1053 | 50.9926 | 48.9389
|  | UPTON BSP | CF |  |  |  | 69.9253 | 69.5105 | 69.3095 | 69.0947 | 68.8463 | 68.3505 | 67.7979 | 67.3989 | 67.0284 | 66.6611 | 64.7484 | 64.2547 | 63.1632 | 61.2968 | 58.6989 | 58.38 | 58.0095 | 57.6253 | 57.0779 | 56.4642 | 56.0337 | 55.6316 | 55.2368 | 53.1463 | 52.7632 | 51.5211 | 62.9768 | 61.2737 | 60.9663 | 60.6074 | 60.2358 | 59.7137 | 59.1305 | 58.7147 | 58.3274 | 57.9474 | 55.9242 | 55.3737 | 54.1337
NURSLING GSP | VELMORE BSP | VELMORE BSP | MINIMUM HEADROOM | SU 42855 19215 | YES | 70.0895 | 107.0874 | 195.3653 | 193.6284 | 191.7853 | 188.1579 | 182.7558 | 177.4411 | 172.3063 | 158.4979 | 154.4695 | 78.4295 | 66.2274 | 54.2337 | 83.2958 | 168.7558 | 163.2947 | 157.1158 | 152.0537 | 146.08 | 140.2021 | 134.5189 | 118.04 | 113.5379 | 35.5979 | 21.8821 | 9.3979 | 89.0389 | 175.1211 | 169.82 | 163.5926 | 158.4326 | 152.3263 | 146.3263 | 140.5884 | 124.0989 | 119.5916 | 41.6284 | 27.8821 | 15.4074
|  | VELMORE BSP | EE |  |  |  | 107.76 | 196.42 | 195.0011 | 193.4937 | 191.9168 | 187.6716 | 183.3368 | 179.1105 | 158.4979 | 154.4695 | 78.4295 | 66.2274 | 55.32 | 84.7695 | 170.9947 | 166.2011 | 160.7168 | 156.4274 | 151.4232 | 146.6253 | 141.9411 | 118.04 | 113.5379 | 35.5979 | 21.8821 | 9.4916 | 89.7589 | 177.3084 | 172.6611 | 167.2547 | 162.8779 | 157.7653 | 152.8653 | 148.0779 | 124.0989 | 119.5916 | 41.6284 | 27.8821 | 15.4768
|  | VELMORE BSP | HT |  |  |  | 107.0874 | 195.3653 | 193.6284 | 191.7853 | 188.1579 | 182.7558 | 177.4411 | 172.3063 | 167.56 | 163.0147 | 83.8389 | 68.3326 | 54.2337 | 83.2958 | 168.7558 | 163.2947 | 157.1158 | 152.0537 | 146.08 | 140.2021 | 134.5189 | 129.2253 | 124.1463 | 42.7326 | 25.3305 | 9.3979 | 89.0389 | 175.1211 | 169.82 | 163.5926 | 158.4326 | 152.3263 | 146.3263 | 140.5884 | 135.2905 | 130.2063 | 48.7884 | 31.3579 | 15.4074
|  | VELMORE BSP | HE |  |  |  | 108.6674 | 197.7547 | 196.7495 | 195.6337 | 194.4358 | 193.1558 | 189.7726 | 186.1674 | 182.5947 | 163.0495 | 90.4179 | 81.3453 | 73.3168 | 86.7474 | 173.9126 | 170.0242 | 165.3968 | 161.9253 | 157.6653 | 153.6011 | 149.5853 | 145.5905 | 122.8579 | 48.5621 | 38.2316 | 29.0168 | 90.7305 | 179.7053 | 176.3937 | 171.9211 | 168.4726 | 164.1147 | 159.96 | 155.8526 | 151.7663 | 128.9189 | 54.5937 | 44.2453 | 35.0158
|  | VELMORE BSP | CF |  |  |  | 109.1884 | 198.6758 | 198.14 | 196.2821 | 195.7095 | 195.1116 | 194.5032 | 193.9032 | 193.3147 | 192.7211 | 124.5442 | 118.6137 | 113.4084 | 87.5947 | 176.4474 | 174.4084 | 168.8284 | 167.1621 | 165.3463 | 163.6074 | 161.8284 | 160.04 | 158.1895 | 86.7232 | 79.9526 | 74.0663 | 91.2989 | 180.72 | 180.0947 | 174.7463 | 173.1274 | 171.3674 | 169.6737 | 167.9421 | 166.1147 | 164.2263 | 92.5705 | 85.6979 | 79.7137
MANNINGTON GSP | WAREHAM | WAREHAM | MINIMUM HEADROOM | SY 91548 88451 | YES | 1.2558 | 37.1589 | 48.6553 | 39.1089 | 37.9774 | 36.1416 | 34.2289 | 32.6132 | 30.7479 | 26.8426 | 20.8689 | 14.0479 | 8.4868 | 5.4532 | 29.3105 | 40.7826 | 32.9458 | 31.7268 | 29.6911 | 27.5711 | 25.8005 | 23.7268 | 19.2616 | 12.2984 | 4.5668 | -1.7363 | -5.1153 | 30.0537 | 41.4942 | 31.8689 | 30.6763 | 28.6984 | 26.5932 | 24.7858 | 22.6595 | 18.0647 | 10.9679 | 3.1879 | -3.1689 | -6.57
|  | WAREHAM | EE |  |  |  | 37.5768 | 49.3258 | 39.9816 | 39.05 | 37.4068 | 35.6742 | 34.2553 | 32.8195 | 31.55 | 30.3458 | 23.9195 | 18.7963 | 15.5437 | 29.7663 | 41.4689 | 33.8532 | 32.8911 | 31.0584 | 29.1342 | 27.5763 | 25.9932 | 24.6089 | 23.2858 | 16.1384 | 10.4005 | 6.6847 | 30.5242 | 42.2037 | 32.7911 | 31.8089 | 30.0353 | 28.1668 | 26.5847 | 24.9637 | 23.5395 | 22.1816 | 14.8132 | 8.9195 | 5.1805
|  | WAREHAM | HT |  |  |  | 37.1589 | 48.6553 | 39.1089 | 37.9774 | 36.1416 | 34.2289 | 32.6132 | 30.7479 | 26.8426 | 20.8689 | 14.0479 | 8.4868 | 5.4532 | 29.3105 | 40.7826 | 32.9458 | 31.7268 | 29.6911 | 27.5711 | 25.8005 | 23.7268 | 19.2616 | 12.2984 | 4.5668 | -1.7363 | -5.1153 | 30.0537 | 41.4942 | 31.8689 | 30.6763 | 28.6984 | 26.5932 | 24.7858 | 22.6595 | 18.0647 | 10.9679 | 3.1879 | -3.1689 | -6.57
|  | WAREHAM | HE |  |  |  | 37.8747 | 50.0984 | 41.1468 | 40.4795 | 39.0868 | 37.5921 | 36.4121 | 35.2195 | 34.2026 | 33.2395 | 27.9142 | 24.1458 | 21.8289 | 30.3832 | 42.3826 | 35.0489 | 34.3637 | 32.8795 | 31.2111 | 29.9079 | 28.5837 | 27.4605 | 26.3963 | 20.3889 | 16.1226 | 13.4732 | 31.1621 | 43.1479 | 34.0258 | 33.3226 | 31.8163 | 30.1974 | 28.9289 | 27.6068 | 26.4563 | 25.3637 | 19.1816 | 14.7868 | 12.09
|  | WAREHAM | CF |  |  |  | 38.0495 | 50.4058 | 50.2258 | 50.0184 | 38.7616 | 38.0711 | 37.4647 | 36.8111 | 36.2068 | 35.5868 | 33.4142 | 32.0637 | 30.7363 | 30.7232 | 42.9268 | 42.5563 | 42.1795 | 31.1668 | 30.4542 | 29.8268 | 29.1521 | 28.5311 | 27.8889 | 25.6595 | 24.2016 | 22.7079 | 31.4842 | 43.7058 | 43.3258 | 42.9363 | 29.2637 | 28.7363 | 28.2637 | 27.7616 | 27.2953 | 26.6384 | 24.2089 | 22.6847 | 21.1437
MELKSHAM GSP | WEST GRAFTON | WEST GRAFTON | MINIMUM HEADROOM | SU 24302 59215 | YES | 0.80421 | 54.5147 | 53.1137 | 51.6316 | 50.0168 | 48.0905 | 46.1421 | 44.0568 | 42.0821 | 36.0053 | 33.76 | 21.6137 | 15.2747 | 9.6484 | 44.9653 | 43.3895 | 41.72 | 39.8916 | 37.6484 | 35.3958 | 32.9726 | 30.6684 | 23.1737 | 20.5063 | 5.9179 | -1.4516 | -7.8305 | 46.7695 | 45.1642 | 43.4589 | 41.5937 | 39.3484 | 37.0832 | 34.6484 | 32.3316 | 24.8221 | 22.1389 | 7.4474 | -0.036842 | -6.4621
|  | WEST GRAFTON | EE |  |  |  | 54.9526 | 53.9221 | 52.5926 | 51.1884 | 49.6042 | 47.9979 | 46.4168 | 44.7537 | 42.1684 | 40.0642 | 27.62 | 22.6358 | 18.7747 | 45.4463 | 44.2968 | 42.7874 | 41.1958 | 39.3726 | 37.5263 | 35.7063 | 33.7832 | 30.6916 | 28.1979 | 13.1926 | 7.4968 | 2.9337 | 47.2589 | 46.0874 | 44.5442 | 42.9221 | 41.0705 | 39.2137 | 37.3768 | 35.4379 | 32.3274 | 29.8105 | 14.6632 | 8.8105 | 4.1968
|  | WEST GRAFTON | HT |  |  |  | 54.5147 | 53.1137 | 51.6316 | 50.0168 | 48.0905 | 46.1421 | 44.0568 | 42.0821 | 36.0053 | 33.76 | 21.6137 | 15.2747 | 9.6484 | 44.9653 | 43.3895 | 41.72 | 39.8916 | 37.6484 | 35.3958 | 32.9726 | 30.6684 | 23.1737 | 20.5063 | 5.9179 | -1.4516 | -7.8305 | 46.7695 | 45.1642 | 43.4589 | 41.5937 | 39.3484 | 37.0832 | 34.6484 | 32.3316 | 24.8221 | 22.1389 | 7.4474 | -0.036842 | -6.4621
|  | WEST GRAFTON | HE |  |  |  | 55.4895 | 54.7958 | 53.84 | 52.7021 | 51.3853 | 50.0358 | 48.7095 | 47.2642 | 44.9663 | 43.1811 | 32.0421 | 28.5042 | 25.6095 | 46.0295 | 45.2558 | 44.1705 | 42.8695 | 41.3558 | 39.8095 | 38.2674 | 36.5695 | 33.7895 | 31.6411 | 17.9905 | 13.78 | 10.3095 | 47.8495 | 47.0621 | 45.9537 | 44.6242 | 43.0768 | 41.5021 | 39.9516 | 38.2442 | 35.4568 | 33.2989 | 19.5863 | 15.3316 | 11.8189
|  | WEST GRAFTON | CF |  |  |  | 55.8168 | 55.4642 | 55.0253 | 54.4947 | 53.9526 | 53.5432 | 53.1368 | 52.6695 | 52.0484 | 51.3484 | 43.8021 | 40.3137 | 38.2558 | 46.3874 | 45.9979 | 45.5053 | 44.9011 | 44.2853 | 43.8368 | 43.3958 | 42.8779 | 42.1705 | 41.3663 | 32.1568 | 27.9253 | 25.4495 | 48.2116 | 47.8168 | 47.3147 | 46.6968 | 46.0684 | 45.6095 | 45.1611 | 44.6305 | 43.9032 | 43.0779 | 33.8189 | 29.5621 | 27.0558
NURSLING GSP | WINCHESTER | WINCHESTER | MINIMUM HEADROOM | SU 44965 26671 | YES | 78.6884 | 106.6095 | 54.1063 | 52.4653 | -5.6137 | 80.4442 | 75.1337 | 69.8874 | 64.4526 | 61.8547 | 59.6158 | 18.02 | -33.8684 | -43.9063 | 90.6063 | 38.5589 | 31.7453 | -33.3295 | 52.2663 | 46.3274 | 40.4758 | 34.3789 | 31.6063 | 29.2474 | -20.6716 | -79.0779 | -90.1474 | 99.8021 | 47.2989 | 42.4305 | -22.8105 | 62.7842 | 56.8011 | 50.9011 | 44.7537 | 41.9253 | 39.5063 | -11.6968 | -70.5168 | -81.7716
|  | WINCHESTER | EE |  |  |  | 107.0463 | 55.2011 | 54.2432 | 18.9368 | 94.5768 | 91.5421 | 88.6642 | 86.1516 | 83.6895 | 81.5789 | 68.1232 | 28.8379 | 3.9621 | 91.5042 | 40.0105 | 38.0558 | -4.6926 | 68.6389 | 65.3347 | 62.2442 | 59.5811 | 56.9842 | 54.7937 | 40.4758 | -5.1968 | -33.8316 | 100.2368 | 48.8442 | 47.8884 | 5.8337 | 79.1547 | 75.8095 | 72.6547 | 69.9253 | 67.2526 | 64.98 | 50.1105 | 2.7621 | -26.0368
|  | WINCHESTER | HT |  |  |  | 106.6095 | 54.5189 | 52.4653 | -5.6137 | 80.4442 | 75.1337 | 69.8874 | 64.4526 | 61.8547 | 59.6158 | 18.02 | -33.8684 | -43.9063 | 90.6063 | 38.5589 | 31.7453 | -33.3295 | 52.2663 | 46.3274 | 40.4758 | 34.3789 | 31.6063 | 29.2474 | -20.6716 | -79.0779 | -90.1474 | 99.8021 | 48.1632 | 42.4305 | -22.8105 | 62.7842 | 56.8011 | 50.9011 | 44.7537 | 41.9253 | 39.5063 | -11.6968 | -70.5168 | -81.7716
|  | WINCHESTER | HE |  |  |  | 107.6389 | 56.0747 | 55.4 | 38.8632 | 114.8632 | 112.2789 | 109.9432 | 108.0432 | 106.2347 | 104.9905 | 96.4505 | 59.1716 | 36.7358 | 92.5326 | 41.8053 | 40.5158 | 22.6389 | 92.1453 | 89.3158 | 86.7695 | 84.7274 | 82.7853 | 81.4937 | 72.2158 | 26.4905 | 0.52 | 100.8316 | 49.7189 | 49.0442 | 32.5074 | 102.6821 | 99.8211 | 97.2421 | 95.1695 | 93.1916 | 91.8663 | 82.3621 | 35.1716 | 9.0663
|  | WINCHESTER | CF |  |  |  | 107.98 | 54.1063 | 53.7411 | 37.5716 | 127.1821 | 126.1642 | 127.9211 | 126.8368 | 125.7905 | 124.8874 | 119.6568 | 105.6505 | 99.6389 | 93.0568 | 38.9905 | 38.4021 | 21.7916 | 106.2505 | 104.9421 | 107.2274 | 106.0674 | 104.9537 | 103.9968 | 98.3916 | 83.5516 | 76.7653 | 101.1726 | 47.2989 | 46.9337 | 30.7642 | 117.3263 | 115.9747 | 117.8884 | 116.6947 | 115.5463 | 114.5632 | 108.7863 | 93.8463 | 86.9516
COWLEY GSP | WITNEY BSP | WITNEY BSP | MINIMUM HEADROOM | SP 35605 08274 | YES | 153.0168 | -14.7137 | -18.1663 | -26.4211 | -42.6011 | -78.4842 | -83.2684 | -88.2895 | -93.0389 | -97.3295 | -100.8958 | -119.4432 | -133.7053 | -145.8842 | -57.08 | -60.8842 | -69.4063 | -85.8621 | -127.7968 | -133.1011 | -138.6842 | -143.9842 | -148.7547 | -152.6958 | -173.3663 | -189.1632 | -203.1074 | -55.3295 | -59.1316 | -67.6558 | -84.1137 | -125.9811 | -131.3011 | -136.8979 | -142.2126 | -147.0032 | -150.9663 | -171.7884 | -187.7716 | -201.8347
|  | WITNEY BSP | EE |  |  |  | 15.8916 | 9.1516 | 1.4137 | -14.1684 | -52.3705 | -79.5989 | -83.6358 | -87.5211 | -91.7263 | -95.2505 | -106.9674 | -116.3347 | -126.8537 | -21.2432 | -28.9579 | -36.92 | -52.72 | -97.3547 | -129.1179 | -133.5905 | -137.8863 | -142.5663 | -146.4653 | -159.1484 | -168.9737 | -180.8684 | -19.48 | -27.1979 | -35.16 | -50.9621 | -95.5937 | -127.3221 | -131.8179 | -136.14 | -140.8484 | -144.7789 | -157.7011 | -167.7579 | -179.7253
|  | WITNEY BSP | HT |  |  |  | -14.7137 | -18.1663 | -26.4211 | -42.6011 | -78.4842 | -83.2684 | -88.2895 | -93.0389 | -97.3295 | -100.8958 | -119.4432 | -133.7053 | -145.8842 | -57.08 | -60.8842 | -69.4063 | -85.8621 | -127.7968 | -133.1011 | -138.6842 | -143.9842 | -148.7547 | -152.6958 | -173.3663 | -189.1632 | -203.1074 | -55.3295 | -59.1316 | -67.6558 | -84.1137 | -125.9811 | -131.3011 | -136.8979 | -142.2126 | -147.0032 | -150.9663 | -171.7884 | -187.7716 | -201.8347
|  | WITNEY BSP | HE |  |  |  | 31.3326 | 11.4547 | 4.4368 | -10.4495 | -28.6232 | -55.2463 | -58.6642 | -61.9832 | -65.5474 | -68.3821 | -76.7274 | -83.8768 | -91.3884 | -3.2505 | -26.4547 | -33.6326 | -48.6789 | -69.8379 | -100.9158 | -104.7347 | -108.4432 | -112.4537 | -115.6253 | -124.8126 | -133.0811 | -141.6326 | -1.48 | -24.6916 | -31.8695 | -46.9147 | -68.0832 | -99.1579 | -102.9853 | -106.7063 | -110.7242 | -113.9063 | -123.1895 | -131.5811 | -140.1905
|  | WITNEY BSP | CF |  |  |  | 75.3537 | 68.7084 | 34.2337 | 20.22 | 18.9484 | -9.6032 | -11.1032 | -12.5316 | -14.0526 | -15.3632 | -23.8253 | -27.8937 | -32.7621 | 57.5958 | 41.2253 | 1.1432 | -12.9568 | -14.3663 | -47.7926 | -49.4537 | -51.0368 | -52.7274 | -54.1716 | -63.6768 | -68.1968 | -73.7316 | 60.2011 | 43.0116 | 2.9168 | -11.1842 | -12.5958 | -46.0379 | -47.7063 | -49.2937 | -50.9926 | -52.4421 | -61.9768 | -66.5421 | -72.1253
BRAMLEY (FLEE) | WOKINGHAM BSP | WOKINGHAM BSP | MINIMUM HEADROOM | SU 79589 67665 | YES | 21.9516 | 99.0137 | 77.2642 | 76.5589 | 75.8105 | 74.68 | 72.7337 | 70.6737 | 68.7274 | 66.8232 | 65.0305 | 58.08 | 53.2347 | 48.6853 | 89.1295 | 66.5253 | 64.6505 | 62.6137 | 60.6526 | 58.5053 | 56.2263 | 54.0642 | 51.9358 | 49.9358 | 42.1863 | 36.8063 | 31.7053 | 92.0337 | 69.4579 | 67.6274 | 65.6337 | 63.6737 | 61.5274 | 59.2453 | 57.0821 | 54.9547 | 52.9537 | 45.2011 | 39.8179 | 34.7126
|  | WOKINGHAM BSP | EE |  |  |  | 99.2895 | 77.6937 | 77.12 | 76.5105 | 75.8737 | 74.9632 | 73.3653 | 71.8116 | 70.1558 | 68.56 | 62.7547 | 59.3021 | 56.1253 | 89.7011 | 67.4916 | 65.9811 | 64.2726 | 62.6758 | 60.9537 | 59.1905 | 57.4705 | 55.6274 | 53.8421 | 47.3537 | 43.5179 | 39.9463 | 92.5926 | 70.4074 | 68.9295 | 67.2611 | 65.6968 | 63.9758 | 62.2105 | 60.4895 | 58.6463 | 56.86 | 50.3674 | 46.5284 | 42.9568
|  | WOKINGHAM BSP | HT |  |  |  | 99.0137 | 77.2642 | 76.5589 | 75.8105 | 74.68 | 72.7337 | 70.6737 | 68.7274 | 66.8232 | 65.0305 | 58.08 | 53.2347 | 48.6853 | 89.1295 | 66.5253 | 64.6505 | 62.6137 | 60.6526 | 58.5053 | 56.2263 | 54.0642 | 51.9358 | 49.9358 | 42.1863 | 36.8063 | 31.7053 | 92.0337 | 69.4579 | 67.6274 | 65.6337 | 63.6737 | 61.5274 | 59.2453 | 57.0821 | 54.9547 | 52.9537 | 45.2011 | 39.8179 | 34.7126
|  | WOKINGHAM BSP | HE |  |  |  | 99.6642 | 78.2474 | 77.8432 | 77.3989 | 76.92 | 76.4084 | 75.9189 | 74.7168 | 73.34 | 72.02 | 67.5726 | 65.3189 | 63.2389 | 90.4632 | 68.6747 | 67.5642 | 66.2147 | 64.9589 | 63.5463 | 62.0832 | 60.6253 | 59.0821 | 57.5989 | 52.5958 | 50.0747 | 47.7095 | 93.0326 | 71.5663 | 70.4821 | 69.1632 | 67.9368 | 66.5568 | 65.1053 | 63.6463 | 62.1021 | 60.6168 | 55.6116 | 53.0895 | 50.7232
|  | WOKINGHAM BSP | CF |  |  |  | 99.8716 | 78.6137 | 78.4 | 78.1758 | 77.9463 | 77.7084 | 77.4653 | 77.2274 | 76.9905 | 76.7526 | 73.4474 | 72.0211 | 70.9684 | 91.2263 | 69.7432 | 69.1716 | 68.48 | 67.8453 | 67.1505 | 66.4368 | 65.7316 | 65.0463 | 64.3421 | 59.0916 | 57.5084 | 56.3232 | 93.2726 | 72.0021 | 71.7674 | 71.3758 | 70.7547 | 70.0768 | 69.38 | 68.6926 | 68.0232 | 67.3368 | 62.1116 | 60.5274 | 59.3411
LOVEDEAN GSP | WYMERING BSP | WYMERING BSP | MINIMUM HEADROOM | SU 64948 05441 | YES | 9.2853 | 179.1021 | 179.4568 | 179.2284 | 179.0137 | 178.7947 | 178.5653 | 184.7526 | 183.6347 | 182.5558 | 181.8905 | 178.7305 | 175.4737 | 172.5979 | 175.8916 | 176.3053 | 176.0474 | 175.8084 | 175.5653 | 175.3147 | 183.9705 | 182.7547 | 181.5779 | 180.8705 | 177.5537 | 174.0326 | 170.8874 | 177.5432 | 177.9547 | 177.6979 | 177.46 | 177.2158 | 176.9642 | 183.8105 | 182.5632 | 181.3579 | 180.6347 | 177.2589 | 173.6305 | 170.4
|  | WYMERING BSP | EE |  |  |  | 179.1021 | 189.8989 | 189.3853 | 188.8589 | 188.3158 | 187.2547 | 186.2063 | 185.1758 | 184.1579 | 183.18 | 180.6695 | 178.1453 | 175.9305 | 175.8916 | 189.5189 | 188.9779 | 188.4221 | 187.8505 | 186.6958 | 185.5558 | 184.4347 | 183.3284 | 182.2611 | 179.6242 | 176.9663 | 174.5411 | 177.5432 | 189.4716 | 188.9211 | 188.3579 | 187.78 | 186.5958 | 185.4274 | 184.2768 | 183.1411 | 182.0442 | 179.3326 | 176.5968 | 174.1011
|  | WYMERING BSP | HT |  |  |  | 190.12 | 189.4779 | 188.8411 | 188.1895 | 187.0968 | 185.9232 | 184.7526 | 183.6347 | 182.5558 | 181.8905 | 178.7305 | 175.4737 | 172.5979 | 189.7505 | 189.0684 | 188.3916 | 187.7053 | 186.5158 | 185.24 | 183.9705 | 182.7547 | 181.5779 | 180.8705 | 177.5537 | 174.0326 | 170.8874 | 189.7053 | 189.0126 | 188.3263 | 187.6284 | 186.4147 | 185.1095 | 183.8105 | 182.5632 | 181.3579 | 180.6347 | 177.2589 | 173.6305 | 170.4
|  | WYMERING BSP | HE |  |  |  | 179.4547 | 190.44 | 190.0958 | 189.7263 | 189.3379 | 188.5821 | 187.8495 | 187.1368 | 186.4484 | 185.7979 | 183.6716 | 181.9663 | 180.4358 | 176.2968 | 190.1011 | 189.74 | 189.3537 | 188.9484 | 188.1305 | 187.3379 | 186.5663 | 185.82 | 185.1116 | 182.7968 | 180.8905 | 179.2021 | 177.9474 | 190.0642 | 189.6989 | 189.3074 | 188.8979 | 188.0621 | 187.2505 | 186.4611 | 185.6958 | 184.9695 | 182.5842 | 180.5968 | 178.8558
|  | WYMERING BSP | CF |  |  |  | 181.3663 | 179.4568 | 179.2284 | 179.0137 | 178.7947 | 178.5653 | 189.4589 | 189.0568 | 188.6411 | 188.2116 | 186.4232 | 185.4158 | 184.3863 | 180.2663 | 176.3053 | 176.0474 | 175.8084 | 175.5653 | 175.3147 | 189.0558 | 188.6189 | 188.1674 | 187.7 | 185.7589 | 184.6663 | 183.5295 | 180.1895 | 177.9547 | 177.6979 | 177.46 | 177.2158 | 176.9642 | 189 | 188.5526 | 188.0905 | 187.6105 | 185.6232 | 184.5011 | 183.3274
COWLEY GSP | YARNTON BSP | YARNTON BSP | MINIMUM HEADROOM | SP 35605 08274 | YES | 50.4316 | 73.5158 | 36.7326 | 124.0432 | 82.3379 | 79.1368 | 45.8684 | 41.8189 | 37.3853 | 32.7368 | 27.9411 | 14.4137 | -1.7421 | -10.2895 | 37.3316 | 0.13895 | 87.2105 | 38.3874 | 34.8789 | -3.9063 | -8.4505 | -13.4558 | -18.7189 | -24.1789 | -39.2232 | -57.7305 | -67.4526 | 41.4863 | 4.3 | 91.3758 | 42.6411 | 39.1347 | 0.41474 | -4.1274 | -9.1316 | -14.3926 | -19.8505 | -34.8926 | -53.42 | -63.1453
|  | YARNTON BSP | EE |  |  |  | 79.0947 | 38.3074 | 126.0895 | 91.7 | 89.5284 | 45.8684 | 41.8189 | 37.3853 | 32.7368 | 27.9411 | 14.4137 | -1.7421 | -10.2895 | 43.94 | 1.8568 | 89.4368 | 49.1821 | 46.8411 | -3.9063 | -8.4505 | -13.4558 | -18.7189 | -24.1789 | -39.2232 | -57.7305 | -67.4526 | 48.0821 | 6.0158 | 93.5979 | 53.4158 | 51.0758 | 0.41474 | -4.1274 | -9.1316 | -14.3926 | -19.8505 | -34.8926 | -53.42 | -63.1453
|  | YARNTON BSP | HT |  |  |  | 73.5158 | 36.7326 | 124.0432 | 82.3379 | 79.1368 | 72.5863 | 66.6726 | 61.4568 | 57.0905 | 48.0126 | 19.4032 | 7.9274 | -2.86 | 37.3316 | 0.13895 | 87.2105 | 38.3874 | 34.8789 | 27.84 | 21.1505 | 15.2558 | 10.3547 | -0.12105 | -32.9463 | -45.7979 | -58.1558 | 41.4863 | 4.3 | 91.3758 | 42.6411 | 39.1347 | 32.0979 | 25.4168 | 19.5274 | 14.6316 | 4.1653 | -28.6411 | -41.5147 | -53.8968
|  | YARNTON BSP | HE |  |  |  | 75.9442 | 40.4168 | 128.8484 | 127.0158 | 125.0663 | 119.8926 | 77.4337 | 73.3432 | 69.2432 | 65.1368 | 53.6147 | 39.6989 | 33.6611 | 39.9853 | 4.1537 | 92.4474 | 90.4347 | 88.3063 | 82.7895 | 33.0042 | 28.3495 | 23.6758 | 18.9737 | 5.7 | -10.4042 | -17.3379 | 44.1389 | 8.3084 | 96.6053 | 94.5958 | 92.4684 | 86.9547 | 37.2579 | 32.6084 | 27.9379 | 23.2421 | 9.9368 | -6.1589 | -13.0947
|  | YARNTON BSP | CF |  |  |  | 88.3011 | 46.7368 | 135.9726 | 130.5916 | 129.7958 | 87.9642 | 87.1053 | 86.0916 | 84.9853 | 83.4568 | 72.2463 | 65.68 | 61.5453 | 54.7674 | 11.5326 | 100.6947 | 94.2958 | 93.4368 | 44.6979 | 43.7674 | 42.66 | 41.4379 | 39.72 | 26.8895 | 19.4326 | 14.6768 | 59.0168 | 15.8011 | 104.9642 | 98.5779 | 97.7179 | 49.0653 | 48.1337 | 47.0242 | 45.8021 | 44.0874 | 31.2705 | 23.6926 | 18.9389
AXMINSTER | YEOVIL BSP | YEOVIL BSP | MINIMUM HEADROOM | ST 57586 16894 | YES | 145.7505 | 71.7242 | 55.4 | 47.5274 | -22.3663 | -28.4211 | -38.74 | -45.7758 | -53.0095 | -57.2832 | -61.5537 | -93.4053 | -176.8516 | -188.8779 | 39.7684 | 23.0979 | 13.9295 | -67.6768 | -74.4842 | -85.6211 | -93.4726 | -101.5905 | -106.2411 | -110.8968 | -146.56 | -234.6558 | -247.8379 | 44.5758 | 27.9042 | 18.7274 | -62.8421 | -69.6411 | -80.8695 | -88.7716 | -96.9421 | -101.66 | -106.3895 | -142.5084 | -231.6105 | -245.0137
|  | YEOVIL BSP | EE |  |  |  | 100.1358 | 57.3168 | 47.5274 | 38.5705 | 34.2516 | 26.3905 | -2.9379 | -7.0105 | -11.1905 | -15.3484 | -31.7389 | -106.8074 | -119.9242 | 73.0189 | 25.18 | 13.9295 | 3.6653 | -1.1347 | -9.4516 | -43.5063 | -47.9095 | -52.4284 | -56.9316 | -74.2958 | -148.4221 | -163.0379 | 77.8368 | 29.9884 | 18.7274 | 8.46 | 3.6526 | -4.7221 | -38.8558 | -43.3368 | -47.9505 | -52.5558 | -70.5895 | -144.5368 | -159.3905
|  | YEOVIL BSP | HT |  |  |  | 71.7242 | 55.4 | 51.5326 | -22.3663 | -28.4211 | -38.74 | -45.7758 | -53.0095 | -57.2832 | -61.5537 | -93.4053 | -176.8516 | -188.8779 | 39.7684 | 23.0979 | 18.8432 | -67.6768 | -74.4842 | -85.6211 | -93.4726 | -101.5905 | -106.2411 | -110.8968 | -146.56 | -234.6558 | -247.8379 | 44.5758 | 27.9042 | 23.6442 | -62.8421 | -69.6411 | -80.8695 | -88.7716 | -96.9421 | -101.66 | -106.3895 | -142.5084 | -231.6105 | -245.0137
|  | YEOVIL BSP | HE |  |  |  | 74.6811 | 59.8705 | 57.3589 | 54.5947 | 51.0158 | 43.8684 | 40.2516 | 36.9968 | 33.6611 | 30.3811 | 19.7032 | -60.7884 | -70.4726 | 42.9895 | 27.9621 | 25.1779 | 22.12 | 18.1158 | 10.5537 | 6.5716 | 2.9968 | -0.66842 | -4.2979 | -15.8463 | -102.4547 | -113.3126 | 47.7989 | 32.7705 | 29.9863 | 26.9263 | 22.9179 | 15.3158 | 11.2968 | 7.6853 | 3.9789 | 0.31158 | -11.54 | -99.1642 | -110.2158
|  | YEOVIL BSP | CF |  |  |  | 75.8937 | 62.1284 | 60.9137 | 59.6253 | 57.9442 | 52.8495 | 50.8263 | 48.8116 | 46.6779 | 44.4011 | 36.7768 | -29.7937 | -36.5474 | 44.3211 | 30.4611 | 29.1232 | 27.7011 | 25.82 | 20.52 | 18.2768 | 16.0411 | 13.6611 | 11.1063 | 2.74 | -64.5305 | -72.1221 | 49.1305 | 35.2695 | 33.9326 | 32.5084 | 30.6284 | 25.3063 | 23.0442 | 20.7905 | 18.3958 | 15.8253 | 7.3705 | -60.0463 | -67.7684

## LEP Reference
Local Authority | Grid Supply Point | Bulk Supply Point | Primary Substation
Arun | LOVEDEAN GSP | CHICHESTER & HUNSTON | ARGYLE ROAD
Arun | LOVEDEAN GSP | CHICHESTER & HUNSTON | ASHLING ROAD
Arun | LOVEDEAN GSP | CHICHESTER & HUNSTON | BILSHAM
Arun | LOVEDEAN GSP | CHICHESTER & HUNSTON | CHICHESTER
Arun | BRAMLEY (FLEE) | FERNHURST | HASLINGBOURNE
Arun | LOVEDEAN GSP | CHICHESTER & HUNSTON | HUNSTON
Arun | LOVEDEAN GSP | CHICHESTER & HUNSTON | ROSE GREEN
Arun | LOVEDEAN GSP | CHICHESTER & HUNSTON | SOUTH BERSTED
Aylesbury Vale | COWLEY GSP | HEADINGTON BSP | ARNCOTT
Aylesbury Vale | EAST CLAYDON GSP | BICESTER NORTH BSP | BICESTER
Aylesbury Vale | EAST CLAYDON GSP | BICESTER NORTH BSP | COTTISFORD
Aylesbury Vale | COWLEY GSP | HEADINGTON BSP | WHEATLEY
Basingstoke and Deane | BRAMLEY (FLEE) | ALTON | ALRESFORD
Basingstoke and Deane | BRAMLEY (FLEE) | ALTON | ALTON LOCAL
Basingstoke and Deane | MELKSHAM GSP | ANDOVER BSP | ANDOVER EAST
Basingstoke and Deane | BRAMLEY (ANDO-THAT) | THATCHAM BSP | BALL HILL
Basingstoke and Deane | MELKSHAM GSP | ANDOVER BSP | BARTON STACEY
Basingstoke and Deane | BRAMLEY (BASI) | BASINGSTOKE T1A & T2A | BASINGSTOKE
Basingstoke and Deane | BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | BRAMLEY GREEN
Basingstoke and Deane | BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | BROOK STREET
Basingstoke and Deane | BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | CHINEHAM
Basingstoke and Deane | BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | DOWN GRANGE
Basingstoke and Deane | BRAMLEY (FLEE) | ALTON | HERRIARD
Basingstoke and Deane | BRAMLEY (FLEE) | COXMOOR WOOD BSP | HOOK
Basingstoke and Deane | BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | HOUNDMILLS
Basingstoke and Deane | MELKSHAM GSP | ANDOVER BSP | HURSTBOURNE TARRANT
Basingstoke and Deane | BRAMLEY (BASI) | BASINGSTOKE T1A & T2A | JAYS CLOSE
Basingstoke and Deane | BRAMLEY (ANDO-THAT) | THATCHAM BSP | KINGSCLERE
Basingstoke and Deane | BRAMLEY (FLEE) | BURGHFIELD RESERVE | MORTIMER
Basingstoke and Deane | BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | OAKRIDGE
Basingstoke and Deane | BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | OVERTON
Basingstoke and Deane | BRAMLEY (FLEE) | BURGHFIELD RESERVE | PADWORTH
Basingstoke and Deane | BRAMLEY (FLEE) | FERNHURST | PRESTON CANDOVER
Basingstoke and Deane | BRAMLEY (ANDO-THAT) | THATCHAM BSP | ST JOHNS
Basingstoke and Deane | BRAMLEY (ANDO-THAT) | THATCHAM BSP | TADLEY
Basingstoke and Deane | BRAMLEY (ANDO-THAT) | THATCHAM BSP | THATCHAM
Basingstoke and Deane | BRAMLEY (FLEE) | BURGHFIELD RESERVE | TRASH GREEN
Basingstoke and Deane | MELKSHAM GSP | ANDOVER BSP | WHITCHURCH
Bath and North East Somerset | MELKSHAM GSP | NORRINGTON | BRADFORD-ON-AVON
Bath and North East Somerset | MELKSHAM GSP | NORRINGTON | SPRING QUARRY WEST
Bournemouth | MANNINGTON GSP | BOURNEMOUTH | ALDERNEY
Bournemouth | MANNINGTON GSP | CHRISTCHURCH BSP | BOSCOMBE EAST
Bournemouth | MANNINGTON GSP | BOURNEMOUTH | BOURNE VALLEY
Bournemouth | MANNINGTON GSP | BOURNEMOUTH | CENTRAL
Bournemouth | MANNINGTON GSP | CHRISTCHURCH BSP | CHRISTCHURCH
Bournemouth | MANNINGTON GSP | REDHILL BSP | EAST HOWE
Bournemouth | MANNINGTON GSP | BOURNEMOUTH | ELECTRIC HOUSE
Bournemouth | MANNINGTON GSP | MANNINGTON BSP | FERNDOWN
Bournemouth | MANNINGTON GSP | REDHILL BSP | REDHILL
Bournemouth | MANNINGTON GSP | CHRISTCHURCH BSP | SOMERFORD
Bournemouth | MANNINGTON GSP | CHRISTCHURCH BSP | SOUTHBOURNE
Bournemouth | MANNINGTON GSP | BOURNEMOUTH | WESTBOURNE
Bournemouth | MANNINGTON GSP | REDHILL BSP | WINTON
Bracknell Forest | BRAMLEY (FLEE) | BRACKNELL MAIN | ASCOT
Bracknell Forest | BRAMLEY (FLEE) | BRACKNELL RESERVE | BAGSHOT
Bracknell Forest | BRAMLEY (FLEE) | BRACKNELL MAIN | BRACKNELL
Bracknell Forest | BRAMLEY (FLEE) | CAMBERLEY MAIN | CAMBERLEY
Bracknell Forest | IVER 132KV | CIPPENHAM | CLARENCE ROAD
Bracknell Forest | BRAMLEY (FLEE) | CAMBERLEY MAIN | CROWTHORNE
Bracknell Forest | BRAMLEY (FLEE) | BRACKNELL RESERVE | EASTHAMPSTEAD
Bracknell Forest | LALEHAM | STAINES | EGHAM
Bracknell Forest | BRAMLEY (FLEE) | WOKINGHAM BSP | ELMS ROAD
Bracknell Forest | BRAMLEY (FLEE) | CAMBERLEY MAIN | KINGS RIDE
Bracknell Forest | BRAMLEY (FLEE) | MAIDENHEAD BSP | KNOWL HILL
Bracknell Forest | BRAMLEY (FLEE) | MAIDENHEAD BSP | MAIDENHEAD
Bracknell Forest | BRAMLEY (FLEE) | WOKINGHAM BSP | PEACOCK FARM
Bracknell Forest | BRAMLEY (FLEE) | CAMBERLEY MAIN | SANDHURST
Bracknell Forest | BRAMLEY (FLEE) | BRACKNELL RESERVE | SUNNINGHILL
Bracknell Forest | BRAMLEY (FLEE) | BRACKNELL MAIN | WARFIELD
Brent | WILLESDEN GSP | CANAL BANK | CANAL BANK 11kV
Brent | WILLESDEN GSP | ACTON LANE | PARK ROYAL
BSP ESA | MELKSHAM GSP | FROME BSP | FROME
BSP ESA | COWLEY GSP | HEADINGTON BSP | HEADINGTON
Cheltenham | MINETY GSP | CIRENCESTER BSP | SHIPTON OLIFFE
Cherwell | COWLEY GSP | HEADINGTON BSP | ARNCOTT
Cherwell | EAST CLAYDON GSP | BICESTER NORTH BSP | BICESTER
Cherwell | EAST CLAYDON GSP | BICESTER NORTH BSP | BICESTER NORTH
Cherwell | COWLEY GSP | YARNTON BSP | CHIPPING NORTON
Cherwell | EAST CLAYDON GSP | BICESTER NORTH BSP | COTTISFORD
Cherwell | COWLEY GSP | YARNTON BSP | DEDDINGTON
Cherwell | COWLEY GSP | HEADINGTON BSP | HEADINGTON
Cherwell | COWLEY GSP | YARNTON BSP | KIDDINGTON
Cherwell | COWLEY GSP | YARNTON BSP | LOVELACE ROAD
Cherwell | LALEHAM | EAST BEDFONT A | NORTH FELTHAM
Cherwell | COWLEY GSP | COWLEY LOCAL (2 X 90) | ROSE HILL
Cherwell | EAST CLAYDON GSP | BICESTER NORTH BSP | UPPER HEYFORD
Cherwell | COWLEY GSP | HEADINGTON BSP | WHEATLEY
Cherwell | COWLEY GSP | WITNEY BSP | WINDRUSH PARK
Cherwell | COWLEY GSP | YARNTON BSP | WOODSTOCK
Cherwell | COWLEY GSP | YARNTON BSP | YARNTON
Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON | ASHLING ROAD
Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON | BILLINGSHURST
Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON | BIRDHAM
Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON | CHICHESTER
Chichester | LOVEDEAN GSP | HAVANT | EMSWORTH
Chichester | BRAMLEY (FLEE) | FERNHURST | FIVE OAKS
Chichester | LOVEDEAN GSP | HAVANT | GABLE HEAD
Chichester | BRAMLEY (FLEE) | FERNHURST | HASLEMERE
Chichester | BRAMLEY (FLEE) | FERNHURST | HASLINGBOURNE
Chichester | LOVEDEAN GSP | HAVANT | HORNDEAN
Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON | HUNSTON
Chichester | BRAMLEY (FLEE) | FERNHURST | LANGLEY COURT
Chichester | LOVEDEAN GSP | HAVANT | LEIGH PARK
Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON | MARKET
Chichester | LOVEDEAN GSP | HAVANT | MEYRICK ROAD
Chichester | BRAMLEY (FLEE) | FERNHURST | MIDHURST
Chichester | BRAMLEY (FLEE) | FERNHURST | PETERSFIELD
Chichester | BRAMLEY (FLEE) | FERNHURST | PLAISTOW
Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON | ROSE GREEN
Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON | SELSEY
Chiltern | IVER 132KV | UPTON BSP | BEACONSFIELD (END BB)
Chiltern | AMERSHAM | LOUDWATER BSP | BOWERDEAN
Chiltern | IVER 132KV | DENHAM | COKES LANE
Chiltern | AMERSHAM | LOUDWATER BSP | FLACKWELL HEATH
Chiltern | IVER 132KV | DENHAM | GERRARDS CROSS
Chiltern | IVER 132KV | DENHAM | GRASSINGHAM ROAD
Christchurch | MANNINGTON GSP | CHRISTCHURCH BSP | CHRISTCHURCH
Christchurch | MANNINGTON GSP | MANNINGTON BSP | FERNDOWN
Christchurch | MANNINGTON GSP | MANNINGTON BSP | Mill Lane, Ringwood
Christchurch | MANNINGTON GSP | ARNEWOOD | NEW MILTON
Christchurch | MANNINGTON GSP | REDHILL BSP | REDHILL
Christchurch | MANNINGTON GSP | CHRISTCHURCH BSP | SOMERFORD
Christchurch | MANNINGTON GSP | CHRISTCHURCH BSP | SOUTHBOURNE
Christchurch | MANNINGTON GSP | REDHILL BSP | WINTON
Cotswold | MELKSHAM GSP | CHIPPENHAM | ALDERTON
Cotswold | COWLEY GSP | WITNEY BSP | BLEDDINGTON
Cotswold | MINETY GSP | CIRENCESTER BSP | CIRENCESTER TOWN
Cotswold | MINETY GSP | CIRENCESTER BSP | CRICKLADE
Cotswold | MINETY GSP | CIRENCESTER BSP | FAIRFORD
Cotswold | MINETY GSP | CIRENCESTER BSP | KEMBLE RAF
Cotswold | MINETY GSP | STRATTON (2 X 60) | LECHLADE
Cotswold | MELKSHAM GSP | CHIPPENHAM | MALMESBURY
Cotswold | MINETY GSP | CIRENCESTER BSP | MINETY VILLAGE
Cotswold | MINETY GSP | CIRENCESTER BSP | NORTHLEACH
Cotswold | COWLEY GSP | WITNEY BSP | RISSINGTON
Cotswold | MINETY GSP | CIRENCESTER BSP | SHIPTON OLIFFE
Cotswold | MINETY GSP | STRATTON (2 X 60) | STANTON FITZWARREN
Cotswold | MELKSHAM GSP | CHIPPENHAM | TETBURY
Cotswold | BRAMLEY (FLEE) | BURGHFIELD MAIN | WHITELEY WOOD
Data Centre ESA | BRAMLEY (FLEE) | READING BSP | HENLEY
Ealing | EALING GSP | EALING 22kV | BRENTFORD
Ealing | WILLESDEN GSP | CANAL BANK | CANAL BANK 11kV
Ealing | EALING GSP | EALING 22kV | DEAN GARDENS
Ealing | EALING GSP | EALING 22kV | EALING 11kV
Ealing | WILLESDEN GSP | ACTON LANE | GOLDSMITHS
Ealing | WILLESDEN GSP |  | GREENFORD
Ealing | EALING GSP | EALING 22kV | HARVARD LANE
Ealing | WILLESDEN GSP | ACTON LANE | LEAMINGTON PARK
Ealing | WILLESDEN GSP | ACTON LANE | PARK ROYAL
Ealing | NORTH HYDE GSP | NORTH HYDE 22kV | SPRINGFIELD ROAD
Ealing | NORTH HYDE GSP | NORTH HYDE 22kV | THE GREEN
East Dorset | MANNINGTON GSP | LYTCHETT | BLANDFORD
East Dorset | MANNINGTON GSP | CHRISTCHURCH BSP | CHRISTCHURCH
East Dorset | MANNINGTON GSP | LYTCHETT | CORFE MULLEN
East Dorset | MANNINGTON GSP | LYTCHETT | CREEKMOOR
East Dorset | MANNINGTON GSP | REDHILL BSP | EAST HOWE
East Dorset | MANNINGTON GSP | MANNINGTON BSP | FERNDOWN
East Dorset | MANNINGTON GSP | MANNINGTON BSP | FORDINGBRIDGE
East Dorset | MANNINGTON GSP | SHAFTESBURY BSP | GUSSAGE ST MICHAEL
East Dorset | MANNINGTON GSP | POOLE PS (HAMWORTHY) | HAMWORTHY
East Dorset | MANNINGTON GSP | MANNINGTON BSP | HINTON MARTELL
East Dorset | MANNINGTON GSP | SALISBURY | HOMINGTON
East Dorset | MANNINGTON GSP | MANNINGTON BSP | MANNINGTON
East Dorset | MANNINGTON GSP | MANNINGTON BSP | Mill Lane, Ringwood
East Dorset | MANNINGTON GSP | SHAFTESBURY BSP | MINCHINGTON
East Dorset | MANNINGTON GSP | REDHILL BSP | REDHILL
East Dorset | MANNINGTON GSP | MANNINGTON BSP | ROCKBOURNE
East Dorset | MANNINGTON GSP | SHAFTESBURY BSP | TARRANT RUSHTON
East Dorset | MANNINGTON GSP | MANNINGTON BSP | VERWOOD
East Dorset | MANNINGTON GSP | MANNINGTON BSP | WIMBORNE
East Dorset | MANNINGTON GSP | MANNINGTON BSP | WIMBORNE ST GILES
East Dorset | MANNINGTON GSP | LYTCHETT | WINTERBORNE KINGSTON
East Hampshire | BRAMLEY (FLEE) | ALTON | ALRESFORD
East Hampshire | BRAMLEY (FLEE) | ALTON | ALTON LOCAL
East Hampshire | LOVEDEAN GSP | CHICHESTER & HUNSTON | ASHLING ROAD
East Hampshire | BRAMLEY (FLEE) | ALTON | BORDON
East Hampshire | BRAMLEY (FLEE) | COXMOOR WOOD BSP | COXMOOR WOOD
East Hampshire | LOVEDEAN GSP | HAVANT | EMSWORTH
East Hampshire | BRAMLEY (FLEE) | ALDERSHOT BSP | FARNHAM
East Hampshire | BRAMLEY (FLEE) | FERNHURST | HASLEMERE
East Hampshire | BRAMLEY (FLEE) | ALTON | HERRIARD
East Hampshire | BRAMLEY (FLEE) | ALDERSHOT BSP | HINDHEAD
East Hampshire | BRAMLEY (FLEE) | COXMOOR WOOD BSP | HOOK
East Hampshire | LOVEDEAN GSP | HAVANT | HORNDEAN
East Hampshire | BRAMLEY (FLEE) | FERNHURST | LANGLEY COURT
East Hampshire | LOVEDEAN GSP | HAVANT | LEIGH PARK
East Hampshire | BRAMLEY (FLEE) | FERNHURST | PETERSFIELD
East Hampshire | BRAMLEY (FLEE) | FERNHURST | PRESTON CANDOVER
East Hampshire | LOVEDEAN GSP | FORT WIDLEY | WATERLOOVILLE
East Hampshire | BRAMLEY (FLEE) | COXMOOR WOOD BSP | WRECCLESHAM
Eastleigh | NURSLING GSP | VELMORE BSP | BASSETT
Eastleigh | BOTLEY WOOD GSP | NETLEY COMMON BSP | BISHOPS WALTHAM
Eastleigh | NURSLING GSP | VELMORE BSP | BISHOPSTOKE
Eastleigh | BOTLEY WOOD GSP | NETLEY COMMON BSP | BITTERNE
Eastleigh | NURSLING GSP | VELMORE BSP | CHANDLERS FORD
Eastleigh | NURSLING GSP | VELMORE BSP | EASTLEIGH NORTH
Eastleigh | BOTLEY WOOD GSP | NETLEY COMMON BSP | HAMBLE
Eastleigh | NURSLING GSP | VELMORE BSP | HEDGE END
Eastleigh | BOTLEY WOOD GSP | NETLEY COMMON BSP | NETLEY COMMON
Eastleigh | NURSLING GSP | ROWNHAMS | NORTH BADDESLEY
Eastleigh | NURSLING GSP | ROWNHAMS | SILKSTEAD
Eastleigh | BOTLEY WOOD GSP | NETLEY COMMON BSP | TOWNHILL PARK
Eastleigh | NURSLING GSP | VELMORE BSP | VELMORE
Eastleigh | BOTLEY WOOD GSP | NETLEY COMMON BSP | WESTON
Eastleigh | BOTLEY WOOD GSP | BOTLEY WOOD BSP | WHITELEY
Elmbridge | LALEHAM | STAINES | SUNBURY CROSS
Fareham | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | BROCKHURST
Fareham | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | HOEFORD
Fareham | LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | LEE-ON-SOLENT
Fareham | BOTLEY WOOD GSP | NETLEY COMMON BSP | NETLEY COMMON
Fareham | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | NORTH FAREHAM
Fareham | BOTLEY WOOD GSP | BOTLEY WOOD BSP | PARK GATE
Fareham | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | PLESSEY TITCHFIELD
Fareham | LOVEDEAN GSP | WYMERING BSP | PORTCHESTER
Fareham | LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | ROWNER PARK
Fareham | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | TITCHFIELD
Fareham | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | WEST END
Fareham | BOTLEY WOOD GSP | BOTLEY WOOD BSP | WHITLEY
Fareham | LOVEDEAN GSP | WYMERING BSP | WYMERING
Gosport | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | BROCKHURST
Gosport | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | HOEFORD
Gosport | LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | LEE-ON-SOLENT
Gosport | LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | ROWNER PARK
Gosport | LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | ZETLAND ROAD
Guildford | BRAMLEY (FLEE) | CAMBERLEY RESERVE | FARNBOROUGH
Guildford | BRAMLEY (FLEE) | ALDERSHOT BSP | FARNHAM
Guildford | BRAMLEY (FLEE) | CAMBERLEY RESERVE | FRIMLEY
Guildford | BRAMLEY (FLEE) | ALDERSHOT BSP | GODALMING
Guildford | BRAMLEY (FLEE) | ALDERSHOT BSP | MILFORD
Guildford | BRAMLEY (FLEE) | ALDERSHOT BSP | NORMANDY
Guildford | BRAMLEY (FLEE) | ALDERSHOT BSP | TONGHAM
Hammersmith and Fulham | WILLESDEN GSP | CANAL BANK | CANAL BANK 11kV
Hammersmith and Fulham | WILLESDEN GSP | ACTON LANE | GOLDSMITHS
Hammersmith and Fulham | EALING GSP | EALING 22kV | HARVARD LANE
Hammersmith and Fulham | WILLESDEN GSP | ACTON LANE | LEAMINGTON PARK
Hart | BRAMLEY (FLEE) | ALDERSHOT BSP | ALDERSHOT
Hart | BRAMLEY (FLEE) | ALTON | ALTON LOCAL
Hart | BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | ARBORFIELD
Hart | BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | BRAMLEY GREEN
Hart | BRAMLEY (FLEE) | CAMBERLEY MAIN | CAMBERLEY
Hart | BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | CHINEHAM
Hart | BRAMLEY (FLEE) | CAMBERLEY RESERVE | COVE
Hart | BRAMLEY (FLEE) | COXMOOR WOOD BSP | COXMOOR WOOD
Hart | BRAMLEY (FLEE) | PYESTOCK BSP | Crookham
Hart | BRAMLEY (FLEE) | CAMBERLEY MAIN | CROWTHORNE
Hart | BRAMLEY (FLEE) | ALDERSHOT BSP | FARNHAM
Hart | BRAMLEY (FLEE) | COXMOOR WOOD BSP | HAWLEY
Hart | BRAMLEY (FLEE) | COXMOOR WOOD BSP | HITCHES LANE
Hart | BRAMLEY (FLEE) | COXMOOR WOOD BSP | HOOK
Hart | BRAMLEY (FLEE) | BURGHFIELD RESERVE | MORTIMER
Hart | BRAMLEY (FLEE) | CAMBERLEY MAIN | SANDHURST
Hart | BRAMLEY (FLEE) | BURGHFIELD RESERVE | TRASH GREEN
Hart | BRAMLEY (FLEE) | COXMOOR WOOD BSP | WRECCLESHAM
Havant | LOVEDEAN GSP | CHICHESTER & HUNSTON | ASHLING ROAD
Havant | LOVEDEAN GSP | HAVANT | BROCKHAMPTON
Havant | LOVEDEAN GSP | HAVANT | EMSWORTH
Havant | LOVEDEAN GSP | WYMERING BSP | FARLINGTON
Havant | LOVEDEAN GSP | PORTSMOUTH BSP | FRATTON PARK
Havant | LOVEDEAN GSP | HAVANT | GABLE HEAD
Havant | LOVEDEAN GSP | HAVANT | HORNDEAN
Havant | LOVEDEAN GSP | HAVANT | LEIGH PARK
Havant | LOVEDEAN GSP | HAVANT | MEYRICK ROAD
Havant | LOVEDEAN GSP | FORT WIDLEY | PURBROOK
Havant | LOVEDEAN GSP | FORT WIDLEY | WATERLOOVILLE
Havant | LOVEDEAN GSP | WYMERING BSP | WYMERING
Hillingdon | NORTH HYDE GSP | NORTH HYDE 22kV | BATH ROAD EAST
Hillingdon | IVER 132KV | LONGFORD | BATH ROAD WEST
Hillingdon | IVER 132KV | DENHAM | DENHAM AVENUE
Hillingdon | IVER 132KV | DENHAM | HAREFIELD
Hillingdon | NORTH HYDE GSP |  | HAYES
Hillingdon | LALEHAM | EAST BEDFONT A | NORTH FELTHAM
Hillingdon | IVER 132KV | LONGFORD | POYLE
Hillingdon | NORTH HYDE GSP | NORTH HYDE 22kV | SPRINGFIELD ROAD
Hillingdon | IVER 132KV | UPTON BSP | UPTON
Horsham | LOVEDEAN GSP | CHICHESTER & HUNSTON | BILLINGSHURST
Horsham | BRAMLEY (FLEE) | FERNHURST | FIVE OAKS
Horsham | BRAMLEY (FLEE) | FERNHURST | HASLINGBOURNE
Horsham | BRAMLEY (FLEE) | FERNHURST | PLAISTOW
Hounslow | NORTH HYDE GSP | NORTH HYDE 22kV | BATH ROAD EAST
Hounslow | EALING GSP | EALING 22kV | BRENTFORD
Hounslow | LALEHAM | EAST BEDFONT A | CHURCH ROAD
Hounslow | LALEHAM | EAST BEDFONT A | FELTHAM
Hounslow | WILLESDEN GSP | ACTON LANE | GOLDSMITHS
Hounslow | EALING GSP | EALING 22kV | HARVARD LANE
Hounslow | LALEHAM | EAST BEDFONT A | HOPE AND ANCHOR
Hounslow | LALEHAM | EAST BEDFONT A | NORTH FELTHAM
Hounslow | NORTH HYDE GSP |  | NORTH HYDE 11kV
Hounslow | LALEHAM | STAINES | STANWELL
Hounslow | LALEHAM | STAINES | SUNBURY CROSS
Hounslow | NORTH HYDE GSP | NORTH HYDE 22kV | THE GREEN
Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | BINSTEAD
Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | FRESHWATER
Isle of Wight | LOVEDEAN GSP | PORTSMOUTH BSP | GREETHAM STREET
Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | NEWPORT
Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | RYDE
Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | SANDOWN
Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | SHALFLEET
Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | SHANKLIN
Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | VENTNOR
Mendip | MANNINGTON GSP | SHAFTESBURY BSP | BOURTON
Mendip | MELKSHAM GSP | NORRINGTON | BRADFORD-ON-AVON
Mendip | MELKSHAM GSP | FROME BSP | BRUTON
Mendip | MELKSHAM GSP | FROME BSP | CROCKERTON
Mendip | MELKSHAM GSP | FROME BSP | FROME
Mendip | MELKSHAM GSP | FROME BSP | HAWKERIDGE
Mendip | MELKSHAM GSP | FROME BSP | HOLWELL
Mendip | AXMINSTER | YEOVIL BSP | SPARKFORD
Mendip | MELKSHAM GSP | NORRINGTON | TROWBRIDGE TOWN
Mendip | MELKSHAM GSP | FROME BSP | WESTBURY
Mole Valley | BRAMLEY (FLEE) | FERNHURST | FIVE OAKS
New Forest | FAWLEY GSP | LANGLEY BSP | BUTTS ASH
New Forest | NURSLING GSP | SOUTHAMPTON (2 X 60) | CENTRAL BRIDGE
New Forest | MANNINGTON GSP | CHRISTCHURCH BSP | CHRISTCHURCH
New Forest | NURSLING GSP | WINCHESTER | DUNBRIDGE
New Forest | NURSLING GSP | ROWNHAMS | FLETCHWOOD
New Forest | MANNINGTON GSP | MANNINGTON BSP | FORDINGBRIDGE
New Forest | FAWLEY GSP | COWES & WOOTTON COMMON BSP | FRESHWATER
New Forest | BOTLEY WOOD GSP | NETLEY COMMON BSP | HAMBLE
New Forest | MANNINGTON GSP | ARNEWOOD | HINCHESLEA
New Forest | MANNINGTON GSP | SALISBURY | HOMINGTON
New Forest | FAWLEY GSP | LANGLEY BSP | LANGLEY
New Forest | NURSLING GSP | ROWNHAMS | LORDSHILL
New Forest | MANNINGTON GSP | ARNEWOOD | LYMINGTON
New Forest | MANNINGTON GSP | MANNINGTON BSP | MANNINGTON
New Forest | MANNINGTON GSP | ARNEWOOD | MILFORD-ON-SEA
New Forest | MANNINGTON GSP | MANNINGTON BSP | Mill Lane
New Forest | MANNINGTON GSP | SHAFTESBURY BSP | MINCHINGTON
New Forest | MANNINGTON GSP | ARNEWOOD | NEW MILTON
New Forest | MANNINGTON GSP | SALISBURY | REDLYNCH
New Forest | MANNINGTON GSP | MANNINGTON BSP | ROCKBOURNE
New Forest | NURSLING GSP | ROWNHAMS | ROMSEY
New Forest | MANNINGTON GSP | CHRISTCHURCH BSP | SOMERFORD
New Forest | NURSLING GSP | ROWNHAMS | TOTTON
New Forest | MANNINGTON GSP | MANNINGTON BSP | VERWOOD
New Forest | MANNINGTON GSP | MANNINGTON BSP | WIMBORNE ST GILES
North Dorset | MANNINGTON GSP | LYTCHETT | BLANDFORD
North Dorset | MANNINGTON GSP | SHAFTESBURY BSP | BOURTON
North Dorset | MANNINGTON GSP | SHAFTESBURY BSP | GILLINGHAM
North Dorset | MANNINGTON GSP | SHAFTESBURY BSP | GUSSAGE ST MICHAEL
North Dorset | AXMINSTER | YEOVIL BSP | HENSTRIDGE
North Dorset | MANNINGTON GSP | SHAFTESBURY BSP | MINCHINGTON
North Dorset | CHICKERELL GSP | CHICKERELL BSP | PIDDLETRENTHIDE
North Dorset | CHICKERELL GSP | CHICKERELL BSP | PUDDLETOWN
North Dorset | AXMINSTER | YEOVIL BSP | PULHAM
North Dorset | MANNINGTON GSP | SHAFTESBURY BSP | SHAFTESBURY
North Dorset | AXMINSTER | YEOVIL BSP | SHERBORNE
North Dorset | MANNINGTON GSP | SHAFTESBURY BSP | SHROTON
North Dorset | MANNINGTON GSP | SHAFTESBURY BSP | TARRANT RUSHTON
North Dorset | MANNINGTON GSP | SHAFTESBURY BSP | WEST STOUR
North Dorset | MANNINGTON GSP | MANNINGTON BSP | WIMBORNE
North Dorset | MANNINGTON GSP | SHAFTESBURY BSP | WINCANTON
North Dorset | MANNINGTON GSP | LYTCHETT | WINTERBORNE KINGSTON
North Dorset | AXMINSTER | YEOVIL BSP | YETMINSTER
Oxford | COWLEY GSP | COWLEY LOCAL (2 X 90) | COWLEY LOCAL
Oxford | COWLEY GSP | OXFORD BSP | FRENCHAY ROAD
Oxford | COWLEY GSP | HEADINGTON BSP | HEADINGTON
Oxford | COWLEY GSP | YARNTON BSP | LOVELACE ROAD
Oxford | COWLEY GSP | OXFORD BSP | NORTH HINKSEY
Oxford | COWLEY GSP | HEADINGTON BSP | OLD ROAD
Oxford | COWLEY GSP | OXFORD BSP | OXFORD
Oxford | COWLEY GSP | COWLEY LOCAL (2 X 90) | ROSE HILL
Oxford | COWLEY GSP | OXFORD BSP | ST EBBES
Oxford | COWLEY GSP | COWLEY LOCAL (2 X 90) | UNION STREET
Oxford | COWLEY GSP | HEADINGTON BSP | WHEATLEY
Oxford | COWLEY GSP | YARNTON BSP | YARNTON
Poole | MANNINGTON GSP | BOURNEMOUTH | ALDERNEY
Poole | MANNINGTON GSP | BOURNEMOUTH | BOURNE VALLEY
Poole | MANNINGTON GSP | LYTCHETT | CORFE MULLEN
Poole | MANNINGTON GSP | LYTCHETT | CREEKMOOR
Poole | MANNINGTON GSP | REDHILL BSP | EAST HOWE
Poole | MANNINGTON GSP | MANNINGTON BSP | FERNDOWN
Poole | MANNINGTON GSP | POOLE PS (HAMWORTHY) | HAMWORTHY
Poole | MANNINGTON GSP | LYTCHETT | HOLES BAY
Poole | MANNINGTON GSP | BOURNEMOUTH | PARKSTONE NORTH
Poole | MANNINGTON GSP | BOURNEMOUTH | PARKSTONE SOUTH
Poole | MANNINGTON GSP | BOURNEMOUTH | WESTBOURNE
Poole | MANNINGTON GSP | MANNINGTON BSP | WIMBORNE
Poole | MANNINGTON GSP | REDHILL BSP | WINTON
Portsmouth | LOVEDEAN GSP | PORTSMOUTH BSP | BRANDON ROAD
Portsmouth | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | BROCKHURST
Portsmouth | LOVEDEAN GSP | WYMERING BSP | COLLEGE PARK
Portsmouth | LOVEDEAN GSP | PORTSMOUTH BSP | EASTNEY
Portsmouth | LOVEDEAN GSP | WYMERING BSP | FARLINGTON
Portsmouth | LOVEDEAN GSP | PORTSMOUTH BSP | FRATTON PARK
Portsmouth | LOVEDEAN GSP | WYMERING BSP | GAMBLE ROAD
Portsmouth | LOVEDEAN GSP | PORTSMOUTH BSP | GREETHAM STREET
Portsmouth | LOVEDEAN GSP | WYMERING BSP | HILSEA
Portsmouth | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | HOEFORD
Portsmouth | LOVEDEAN GSP | HAVANT | MEYRICK ROAD
Portsmouth | LOVEDEAN GSP | WYMERING BSP | PORTCHESTER
Portsmouth | LOVEDEAN GSP | PORTSMOUTH BSP | PORTSMOUTH
Portsmouth | LOVEDEAN GSP | FORT WIDLEY | PURBROOK
Portsmouth | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | WEST END
Portsmouth | LOVEDEAN GSP | WYMERING BSP | WYMERING
Portsmouth | LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | ZETLAND ROAD
Purbeck | MANNINGTON GSP | LYTCHETT | BLANDFORD
Purbeck | MANNINGTON GSP | WAREHAM | BOVINGTON
Purbeck | MANNINGTON GSP | WAREHAM | BUSHEY
Purbeck | MANNINGTON GSP | LYTCHETT | CORFE MULLEN
Purbeck | MANNINGTON GSP | LYTCHETT | CREEKMOOR
Purbeck | MANNINGTON GSP | POOLE PS (HAMWORTHY) | HAMWORTHY
Purbeck | MANNINGTON GSP | BOURNEMOUTH | PARKSTONE SOUTH
Purbeck | CHICKERELL GSP | CHICKERELL BSP | PUDDLETOWN
Purbeck | MANNINGTON GSP | WAREHAM | SWANAGE
Purbeck | MANNINGTON GSP | WAREHAM | WAREHAM TOWN
Purbeck | MANNINGTON GSP | LYTCHETT | WINTERBORNE KINGSTON
Reading | MELKSHAM GSP | AMESBURY | BOSCOMBE DOWN
Reading | BRAMLEY (FLEE) | READING TOWN BSP | CAVERSHAM
Reading | BRAMLEY (FLEE) | BURGHFIELD MAIN | COURAGES
Reading | BRAMLEY (FLEE) | BURGHFIELD MAIN | GREEN PARK
Reading | BRAMLEY (FLEE) | BURGHFIELD MAIN | KENTWOOD HILL
Reading | BRAMLEY (FLEE) | READING BSP | KIDMORE END
Reading | BRAMLEY (FLEE) | READING BSP | LITTLE HUNGERFORD
Reading | BRAMLEY (FLEE) | READING BSP | NORTHUMBERLAND AVENUE
Reading | BRAMLEY (FLEE) | READING BSP | READING
Reading | BRAMLEY (FLEE) | READING TOWN BSP | READING TOWN
Reading | BRAMLEY (FLEE) | READING BSP | SILVER STREET
Reading | BRAMLEY (FLEE) | BURGHFIELD RESERVE | SOUTHCOTE
Reading | BRAMLEY (FLEE) | READING TOWN BSP | THE MALL
Reading | BRAMLEY (FLEE) | BURGHFIELD RESERVE | TRASH GREEN
Reading | MINETY GSP | CIRENCESTER BSP | WHITEWAY
Reading | BRAMLEY (FLEE) | BURGHFIELD MAIN | WILSON ROAD
Richmond upon Thames | EALING GSP | EALING 22kV | BRENTFORD
Richmond upon Thames | LALEHAM | EAST BEDFONT A | FELTHAM
Richmond upon Thames | EALING GSP | EALING 22kV | HARVARD LANE
Richmond upon Thames | LALEHAM | EAST BEDFONT A | HOPE AND ANCHOR
Richmond upon Thames | LALEHAM | EAST BEDFONT A | NORTH FELTHAM
Richmond upon Thames | LALEHAM | STAINES | SUNBURY CROSS
Runnymede | LALEHAM | STAINES | CAUSEWAY
Runnymede | IVER 132KV | CHALVEY BSP | CHALVEY
Runnymede | BRAMLEY (FLEE) | BRACKNELL RESERVE | CHOBHAM
Runnymede | IVER 132KV | CIPPENHAM | CLARENCE ROAD
Runnymede | LALEHAM | STAINES | EGHAM
Runnymede | BRAMLEY (FLEE) | BRACKNELL RESERVE | M V E E
Runnymede | LALEHAM | STAINES | SIDNEY ROAD
Rushmoor | BRAMLEY (FLEE) | ALDERSHOT BSP | ALDERSHOT
Rushmoor | BRAMLEY (FLEE) | CAMBERLEY RESERVE | COVE
Rushmoor | BRAMLEY (FLEE) | PYESTOCK BSP | Crookham
Rushmoor | BRAMLEY (FLEE) | CAMBERLEY RESERVE | FARNBOROUGH
Rushmoor | BRAMLEY (FLEE) | CAMBERLEY RESERVE | FRIMLEY
Rushmoor | BRAMLEY (FLEE) | COXMOOR WOOD BSP | HAWLEY
Rushmoor | BRAMLEY (FLEE) | COXMOOR WOOD BSP | HITCHES LANE
Rushmoor | BRAMLEY (FLEE) | ALDERSHOT BSP | LABURNAM ROAD
Rushmoor | BRAMLEY (FLEE) | CAMBERLEY RESERVE | QUEENSMEAD
Rushmoor | BRAMLEY (FLEE) | ALDERSHOT BSP | TONGHAM
Slough | IVER 132KV | CHALVEY BSP | CHALVEY
Slough | IVER 132KV | SLOUGH | FARNHAM ROYAL
Slough | IVER 132KV | CHALVEY BSP | PETERSFIELD AVENUE
Slough | IVER 132KV | LONGFORD | POYLE
Slough | IVER 132KV | UPTON BSP | SUTTON LANE
Slough | IVER 132KV | SLOUGH | TAPLOW
Slough | IVER 132KV | UPTON BSP | UPTON
South Bucks | IVER 132KV | UPTON BSP | BEACONSFIELD (END BB)
South Bucks | BRAMLEY (FLEE) | MAIDENHEAD BSP | BRAYWICK ROAD
South Bucks | IVER 132KV | CHALVEY BSP | CHALVEY
South Bucks | IVER 132KV | CIPPENHAM | CLARENCE ROAD
South Bucks | BRAMLEY (FLEE) | MAIDENHEAD BSP | CORDWALLIS
South Bucks | IVER 132KV | DENHAM | DENHAM AVENUE
South Bucks | IVER 132KV | SLOUGH | FARNHAM ROYAL
South Bucks | AMERSHAM | LOUDWATER BSP | FLACKWELL HEATH
South Bucks | IVER 132KV | DENHAM | GERRARDS CROSS
South Bucks | IVER 132KV | DENHAM | GRASSINGHAM ROAD
South Bucks | IVER 132KV | CHALVEY BSP | PETERSFIELD AVENUE
South Bucks | IVER 132KV | LONGFORD | POYLE
South Bucks | IVER 132KV | UPTON BSP | SUTTON LANE
South Bucks | IVER 132KV | SLOUGH | TAPLOW
South Bucks | IVER 132KV | UPTON BSP | UPTON
South Bucks | AMERSHAM | LOUDWATER BSP | WELL END
South Gloucestershire | MELKSHAM GSP | CHIPPENHAM | ALDERTON
South Gloucestershire | MELKSHAM GSP | NORRINGTON | SPRING QUARRY WEST
South Northamptonshire | EAST CLAYDON GSP | BICESTER NORTH BSP | COTTISFORD
South Northamptonshire | COWLEY GSP | YARNTON BSP | DEDDINGTON
South Oxfordshire | COWLEY GSP | HEADINGTON BSP | ARNCOTT
South Oxfordshire | COWLEY GSP | COWLEY LOCAL (2 X 45) | BERINSFIELD
South Oxfordshire | BRAMLEY (FLEE) | READING TOWN BSP | CAVERSHAM
South Oxfordshire | COWLEY GSP | DRAYTON BSP | CHOLSEY
South Oxfordshire | COWLEY GSP | COWLEY LOCAL (2 X 90) | COWLEY LOCAL
South Oxfordshire | COWLEY GSP | DRAYTON BSP | FULSCOT
South Oxfordshire | BRAMLEY (FLEE) | BURGHFIELD RESERVE | GORING
South Oxfordshire | COWLEY GSP | HEADINGTON BSP | HEADINGTON
South Oxfordshire | BRAMLEY (FLEE) | READING BSP | HENLEY
South Oxfordshire | COWLEY GSP | COWLEY LOCAL (2 X 45) | KENNINGTON
South Oxfordshire | BRAMLEY (FLEE) | BURGHFIELD MAIN | KENTWOOD HILL
South Oxfordshire | BRAMLEY (FLEE) | READING BSP | KIDMORE END
South Oxfordshire | COWLEY GSP | YARNTON BSP | LOVELACE ROAD
South Oxfordshire | COWLEY GSP | DRAYTON BSP | MILTON
South Oxfordshire | COWLEY GSP | HIGH WYCOMBE BSP | NUFFIELD
South Oxfordshire | COWLEY GSP | HEADINGTON BSP | OLD ROAD
South Oxfordshire | BRAMLEY (FLEE) | BURGHFIELD RESERVE | PANGBOURNE
South Oxfordshire | BRAMLEY (FLEE) | READING BSP | READING
South Oxfordshire | BRAMLEY (FLEE) | READING TOWN BSP | READING TOWN
South Oxfordshire | COWLEY GSP | COWLEY LOCAL (2 X 90) | ROSE HILL
South Oxfordshire | COWLEY GSP | HIGH WYCOMBE BSP | STOKENCHURCH
South Oxfordshire | BRAMLEY (FLEE) | READING BSP | TWYFORD
South Oxfordshire | COWLEY GSP | COWLEY LOCAL (2 X 90) | WALLINGFORD
South Oxfordshire | COWLEY GSP | HIGH WYCOMBE BSP | WATLINGTON
South Oxfordshire | COWLEY GSP | HEADINGTON BSP | WHEATLEY
South Oxfordshire | COWLEY GSP | DRAYTON BSP | WINSMORE LANE
South Oxfordshire | BRAMLEY (FLEE) | BURGHFIELD RESERVE | WOODCOTE
South Oxfordshire | COWLEY GSP | YARNTON BSP | YARNTON
South Oxfordshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | YATTENDON
South Somerset | MANNINGTON GSP | SHAFTESBURY BSP | BOURTON
South Somerset | MELKSHAM GSP | FROME BSP | BRUTON
South Somerset | AXMINSTER | YEOVIL BSP | CASTLE CARY
South Somerset | AXMINSTER | YEOVIL BSP | CHILTON CANTELO
South Somerset | AXMINSTER | YEOVIL BSP | HENSTRIDGE
South Somerset | MELKSHAM GSP | FROME BSP | HOLWELL
South Somerset | AXMINSTER | YEOVIL BSP | LARKHILL
South Somerset | AXMINSTER | YEOVIL BSP | MILBORNE PORT
South Somerset | AXMINSTER | YEOVIL BSP | SHERBORNE
South Somerset | AXMINSTER | YEOVIL BSP | SPARKFORD
South Somerset | AXMINSTER | YEOVIL BSP | WEST HENDFORD
South Somerset | MANNINGTON GSP | SHAFTESBURY BSP | WEST STOUR
South Somerset | MANNINGTON GSP | SHAFTESBURY BSP | WINCANTON
South Somerset | AXMINSTER | YEOVIL BSP | YEOVIL
South Somerset | AXMINSTER | YEOVIL BSP | YETMINSTER
Southampton | NURSLING GSP | VELMORE BSP | BASSETT
Southampton | NURSLING GSP | SOUTHAMPTON (2 X 60) | BEVOIS VALLEY
Southampton | BOTLEY WOOD GSP | NETLEY COMMON BSP | BITTERNE
Southampton | FAWLEY GSP | LANGLEY BSP | BUTTS ASH
Southampton | NURSLING GSP | SOUTHAMPTON (2 X 60) | CENTRAL BRIDGE
Southampton | NURSLING GSP | SOUTHAMPTON (2 X 60) | CHAPEL
Southampton | NURSLING GSP | VELMORE BSP | EASTLEIGH NORTH
Southampton | NURSLING GSP | ROWNHAMS | LORDSHILL
Southampton | NURSLING GSP | ROWNHAMS | MAYBUSH
Southampton | BOTLEY WOOD GSP | NETLEY COMMON BSP | NETLEY COMMON
Southampton | NURSLING GSP | ROWNHAMS | NORTH BADDESLEY
Southampton | NURSLING GSP | SOUTHAMPTON (2 X 90) | REGENTS PARK
Southampton | NURSLING GSP | SOUTHAMPTON (2 X 90) | SHIRLEY
Southampton | NURSLING GSP |  | SOUTHFIELD ROAD
Southampton | BOTLEY WOOD GSP | NETLEY COMMON BSP | TOWNHILL PARK
Southampton | NURSLING GSP | VELMORE BSP | VELMORE
Southampton | NURSLING GSP | SOUTHAMPTON (2 X 90) | WESTERN ESPLANADE
Southampton | BOTLEY WOOD GSP | NETLEY COMMON BSP | WESTON
Southampton | NURSLING GSP | SOUTHAMPTON (2 X 90) | WOODMILL LANE
Southampton | BOTLEY WOOD GSP | NETLEY COMMON BSP | WOOLSTON
Spelthorne | LALEHAM | STAINES | CAUSEWAY
Spelthorne | IVER 132KV | CHALVEY BSP | CHALVEY
Spelthorne | LALEHAM | EAST BEDFONT A | CHURCH ROAD
Spelthorne | IVER 132KV | LONGFORD | POYLE
Spelthorne | LALEHAM | STAINES | SIDNEY ROAD
Spelthorne | LALEHAM | STAINES | STANWELL
Spelthorne | LALEHAM | STAINES | SUNBURY CROSS
Stratford-on-Avon | COWLEY GSP | WITNEY BSP | BLEDDINGTON
Stratford-on-Avon | COWLEY GSP | YARNTON BSP | CHIPPING NORTON
Surrey Heath | BRAMLEY (FLEE) | BRACKNELL MAIN | ASCOT
Surrey Heath | BRAMLEY (FLEE) | BRACKNELL RESERVE | BAGSHOT
Surrey Heath | BRAMLEY (FLEE) | CAMBERLEY MAIN | CAMBERLEY
Surrey Heath | BRAMLEY (FLEE) | BRACKNELL RESERVE | CHOBHAM
Surrey Heath | BRAMLEY (FLEE) | CAMBERLEY RESERVE | FARNBOROUGH
Surrey Heath | BRAMLEY (FLEE) | CAMBERLEY RESERVE | FRIMLEY
Surrey Heath | BRAMLEY (FLEE) | COXMOOR WOOD BSP | HAWLEY
Surrey Heath | BRAMLEY (FLEE) | CAMBERLEY MAIN | KINGS RIDE
Surrey Heath | BRAMLEY (FLEE) | BRACKNELL RESERVE | M V E E
Surrey Heath | BRAMLEY (FLEE) | CAMBERLEY RESERVE | QUEENSMEAD
Surrey Heath | BRAMLEY (FLEE) | BRACKNELL RESERVE | SUNNINGHILL
Swindon | MINETY GSP | TOOTHILL BSP | CHISLEDON
Swindon | MINETY GSP | CIRENCESTER BSP | CRICKLADE
Swindon | MINETY GSP | TOOTHILL BSP | DORCAN SOUTH
Swindon | MINETY GSP | STRATTON (2 X 90) | DRAKES WAY
Swindon | MINETY GSP | CIRENCESTER BSP | FAIRFORD
Swindon | MINETY GSP | STRATTON (2 X 60) | FARINGDON
Swindon | BRAMLEY (ANDO-THAT) | THATCHAM BSP | LAMBOURN
Swindon | MINETY GSP | STRATTON (2 X 60) | LECHLADE
Swindon | MINETY GSP | SWINDON BSP | MANCHESTER ROAD
Swindon | MINETY GSP | STRATTON (2 X 90) | PARK NORTH
Swindon | MINETY GSP | STRATTON (2 X 90) | PLESSEY
Swindon | MINETY GSP | STRATTON (2 X 90) | PRESSED STEEL SWINDON
Swindon | MINETY GSP | TOOTHILL BSP | QUARRY ROAD
Swindon | MELKSHAM GSP | WEST GRAFTON | RAMSBURY
Swindon | MINETY GSP | STRATTON (2 X 60) | SHRIVENHAM
Swindon | MINETY GSP | STRATTON (2 X 60) | STANTON FITZWARREN
Swindon | MINETY GSP | STRATTON (2 X 60) | STRATTON
Swindon | MINETY GSP | SWINDON BSP | SWINDON
Swindon | MINETY GSP | TOOTHILL BSP | TOOTHILL
Swindon | MINETY GSP | SWINDON BSP | TRADING ESTATE
Swindon | MINETY GSP | SWINDON BSP | WOOTTON BASSETT
Swindon | MINETY GSP | TOOTHILL BSP | WROUGHTON
Test Valley | MELKSHAM GSP | ANDOVER BSP | ANDOVER
Test Valley | MELKSHAM GSP | ANDOVER BSP | ANDOVER EAST
Test Valley | MELKSHAM GSP | ANDOVER BSP | ANDOVER TOWN
Test Valley | BRAMLEY (ANDO-THAT) | THATCHAM BSP | BALL HILL
Test Valley | MELKSHAM GSP | ANDOVER BSP | BARTON STACEY
Test Valley | NURSLING GSP | VELMORE BSP | BASSETT
Test Valley | NURSLING GSP | VELMORE BSP | CHANDLERS FORD
Test Valley | NURSLING GSP | WINCHESTER | DUNBRIDGE
Test Valley | NURSLING GSP | ROWNHAMS | FLETCHWOOD
Test Valley | NURSLING GSP | WINCHESTER | HARESTOCK
Test Valley | NURSLING GSP | WINCHESTER | HOUGHTON
Test Valley | MELKSHAM GSP | ANDOVER BSP | HURSTBOURNE TARRANT
Test Valley | BRAMLEY (ANDO-THAT) | THATCHAM BSP | KINTBURY
Test Valley | NURSLING GSP | ROWNHAMS | LORDSHILL
Test Valley | NURSLING GSP | ROWNHAMS | MAYBUSH
Test Valley | MELKSHAM GSP | ANDOVER BSP | MIDDLE WALLOP
Test Valley | NURSLING GSP | ROWNHAMS | NORTH BADDESLEY
Test Valley | MELKSHAM GSP | AMESBURY | PARK HOUSE
Test Valley | MANNINGTON GSP | SALISBURY | PETERSFINGER
Test Valley | MELKSHAM GSP | ANDOVER BSP | PORTWAY
Test Valley | NURSLING GSP | SOUTHAMPTON (2 X 90) | REGENTS PARK
Test Valley | NURSLING GSP | ROWNHAMS | ROMSEY
Test Valley | NURSLING GSP | ROWNHAMS | SILKSTEAD
Test Valley | MELKSHAM GSP | ANDOVER BSP | THRUXTON
Test Valley | MELKSHAM GSP | WEST GRAFTON | TIDWORTH
Test Valley | NURSLING GSP | ROWNHAMS | TOTTON
Test Valley | NURSLING GSP | VELMORE BSP | VELMORE
Test Valley | MELKSHAM GSP | WEST GRAFTON | WEST GRAFTON VILLAGE
Test Valley | MELKSHAM GSP | ANDOVER BSP | WHITCHURCH
Tewkesbury | MINETY GSP | CIRENCESTER BSP | NORTHLEACH
Tewkesbury | MINETY GSP | CIRENCESTER BSP | SHIPTON OLIFFE
Three Rivers | IVER 132KV | DENHAM | COKES LANE
Three Rivers | IVER 132KV | DENHAM | DENHAM AVENUE
Three Rivers | IVER 132KV | DENHAM | GRASSINGHAM ROAD
Three Rivers | IVER 132KV | DENHAM | HAREFIELD
Vale of White Horse | COWLEY GSP | COWLEY LOCAL (2 X 45) | BERINSFIELD
Vale of White Horse | MINETY GSP | STRATTON (2 X 60) | BLACK BOURTON
Vale of White Horse | MINETY GSP | TOOTHILL BSP | CHISLEDON
Vale of White Horse | COWLEY GSP | DRAYTON BSP | CHOLSEY
Vale of White Horse | COWLEY GSP | COWLEY LOCAL (2 X 90) | COWLEY LOCAL
Vale of White Horse | COWLEY GSP | YARNTON BSP | EYNSHAM
Vale of White Horse | MINETY GSP | STRATTON (2 X 60) | FARINGDON
Vale of White Horse | COWLEY GSP | DRAYTON BSP | FULSCOT
Vale of White Horse | COWLEY GSP | WITNEY BSP | FYFIELD
Vale of White Horse | COWLEY GSP | DRAYTON BSP | GROVE
Vale of White Horse | COWLEY GSP | COWLEY LOCAL (2 X 45) | KENNINGTON
Vale of White Horse | BRAMLEY (ANDO-THAT) | THATCHAM BSP | LAMBOURN
Vale of White Horse | MINETY GSP | STRATTON (2 X 60) | LECHLADE
Vale of White Horse | BRAMLEY (ANDO-THAT) | THATCHAM BSP | LECKHAMPSTEAD
Vale of White Horse | COWLEY GSP | DRAYTON BSP | MILTON
Vale of White Horse | COWLEY GSP | OXFORD BSP | NORTH HINKSEY
Vale of White Horse | COWLEY GSP | OXFORD BSP | OXFORD
Vale of White Horse | COWLEY GSP | COWLEY LOCAL (2 X 90) | ROSE HILL
Vale of White Horse | MINETY GSP | STRATTON (2 X 60) | SHRIVENHAM
Vale of White Horse | COWLEY GSP | OXFORD BSP | ST EBBES
Vale of White Horse | COWLEY GSP | WITNEY BSP | STANDLAKE
Vale of White Horse | MINETY GSP | STRATTON (2 X 60) | STANTON FITZWARREN
Vale of White Horse | COWLEY GSP | COWLEY LOCAL (2 X 90) | WALLINGFORD
Vale of White Horse | COWLEY GSP | DRAYTON BSP | WANTAGE
Vale of White Horse | COWLEY GSP | DRAYTON BSP | WINSMORE LANE
Vale of White Horse | COWLEY GSP | OXFORD BSP | WOOTTON ROAD
Vale of White Horse | COWLEY GSP | YARNTON BSP | YARNTON
Waverley | BRAMLEY (FLEE) | ALDERSHOT BSP | ALDERSHOT
Waverley | BRAMLEY (FLEE) | ALTON | BORDON
Waverley | BRAMLEY (FLEE) | ALDERSHOT BSP | FARNHAM
Waverley | BRAMLEY (FLEE) | ALDERSHOT BSP | GODALMING
Waverley | BRAMLEY (FLEE) | FERNHURST | HASLEMERE
Waverley | BRAMLEY (FLEE) | ALDERSHOT BSP | HINDHEAD
Waverley | BRAMLEY (FLEE) | ALDERSHOT BSP | LABURNAM ROAD
Waverley | BRAMLEY (FLEE) | ALDERSHOT BSP | MILFORD
Waverley | BRAMLEY (FLEE) | FERNHURST | PLAISTOW
Waverley | BRAMLEY (FLEE) | BURGHFIELD RESERVE | SOUTHCOTE
Waverley | BRAMLEY (FLEE) | ALDERSHOT BSP | TONGHAM
Waverley | BRAMLEY (FLEE) | COXMOOR WOOD BSP | WRECCLESHAM
West Berkshire | BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | ARBORFIELD
West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | BALL HILL
West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | BEENHAM
West Berkshire | COWLEY GSP | DRAYTON BSP | CHOLSEY
West Berkshire | BRAMLEY (FLEE) | BURGHFIELD RESERVE | GORING
West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | HUNGERFORD
West Berkshire | MELKSHAM GSP | ANDOVER BSP | HURSTBOURNE TARRANT
West Berkshire | BRAMLEY (FLEE) | BURGHFIELD MAIN | KENTWOOD HILL
West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | KINGSCLERE
West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | KINTBURY
West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | LAMBOURN
West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | LECKHAMPSTEAD
West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | LOVE LANE
West Berkshire | BRAMLEY (FLEE) | BURGHFIELD RESERVE | MORTIMER
West Berkshire | BRAMLEY (FLEE) | BURGHFIELD RESERVE | PADWORTH
West Berkshire | BRAMLEY (FLEE) | BURGHFIELD RESERVE | PANGBOURNE
West Berkshire | MELKSHAM GSP | WEST GRAFTON | RAMSBURY
West Berkshire | BRAMLEY (FLEE) | READING TOWN BSP | READING TOWN
West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | RIVERSIDE
West Berkshire | BRAMLEY (FLEE) | BURGHFIELD RESERVE | SOUTHCOTE
West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | ST JOHNS
West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | TADLEY
West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | THATCHAM
West Berkshire | BRAMLEY (FLEE) | BURGHFIELD RESERVE | THEALE
West Berkshire | BRAMLEY (FLEE) | BURGHFIELD RESERVE | TRASH GREEN
West Berkshire | COWLEY GSP | DRAYTON BSP | WANTAGE
West Berkshire | MINETY GSP | CIRENCESTER BSP | WHITEWAY
West Berkshire | BRAMLEY (FLEE) | BURGHFIELD MAIN | WILSON ROAD
West Berkshire | BRAMLEY (FLEE) | BURGHFIELD RESERVE | WOODCOTE
West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | YATTENDON
West Dorset | MANNINGTON GSP | WAREHAM | BOVINGTON
West Dorset | CHICKERELL GSP | CHICKERELL BSP | CERNE ABBAS
West Dorset | CHICKERELL GSP | CHICKERELL BSP | CHARMINSTER
West Dorset | CHICKERELL GSP | CHICKERELL BSP | CHICKERELL
West Dorset | AXMINSTER | YEOVIL BSP | CHILTON CANTELO
West Dorset | CHICKERELL GSP | CHICKERELL BSP | DORCHESTER
West Dorset | AXMINSTER | YEOVIL BSP | HENSTRIDGE
West Dorset | CHICKERELL GSP | CHICKERELL BSP | MAIDEN NEWTON
West Dorset | AXMINSTER | YEOVIL BSP | MILBORNE PORT
West Dorset | CHICKERELL GSP | CHICKERELL BSP | PIDDLETRENTHIDE
West Dorset | CHICKERELL GSP | CHICKERELL BSP | PUDDLETOWN
West Dorset | AXMINSTER | YEOVIL BSP | PULHAM
West Dorset | CHICKERELL GSP | CHICKERELL BSP | REDLANDS
West Dorset | AXMINSTER | YEOVIL BSP | SHERBORNE
West Dorset | AXMINSTER | YEOVIL BSP | WEST HENDFORD
West Dorset | CHICKERELL GSP | CHICKERELL BSP | WEYMOUTH
West Dorset | MANNINGTON GSP | LYTCHETT | WINTERBORNE KINGSTON
West Dorset | AXMINSTER | YEOVIL BSP | YEOVIL
West Dorset | AXMINSTER | YEOVIL BSP | YETMINSTER
West Oxfordshire | MINETY GSP | STRATTON (2 X 60) | BLACK BOURTON
West Oxfordshire | COWLEY GSP | WITNEY BSP | BLEDINGTON
West Oxfordshire | COWLEY GSP | WITNEY BSP | BURFORD
West Oxfordshire | COWLEY GSP | WITNEY BSP | CARTERTON
West Oxfordshire | COWLEY GSP | YARNTON BSP | CHARLBURY
West Oxfordshire | COWLEY GSP | YARNTON BSP | CHIPPING NORTON
West Oxfordshire | COWLEY GSP | YARNTON BSP | DEDDINGTON
West Oxfordshire | COWLEY GSP | YARNTON BSP | EYNSHAM
West Oxfordshire | MINETY GSP | STRATTON (2 X 60) | FARINGDON
West Oxfordshire | COWLEY GSP | WITNEY BSP | FYFIELD
West Oxfordshire | COWLEY GSP | YARNTON BSP | KIDDINGTON
West Oxfordshire | COWLEY GSP | WITNEY BSP | LEAFIELD
West Oxfordshire | MINETY GSP | STRATTON (2 X 60) | LECHLADE
West Oxfordshire | MINETY GSP | CIRENCESTER BSP | NORTHLEACH
West Oxfordshire | COWLEY GSP | WITNEY BSP | RISSINGTON
West Oxfordshire | COWLEY GSP | WITNEY BSP | STANDLAKE
West Oxfordshire | EAST CLAYDON GSP | BICESTER NORTH BSP | UPPER HEYFORD
West Oxfordshire | COWLEY GSP | WITNEY BSP | WINDRUSH PARK
West Oxfordshire | COWLEY GSP | WITNEY BSP | WITNEY TOWN
West Oxfordshire | COWLEY GSP | YARNTON BSP | WOODSTOCK
West Oxfordshire | COWLEY GSP | YARNTON BSP | YARNTON
Weymouth and Portland | CHICKERELL GSP | CHICKERELL BSP | CHICKERELL
Weymouth and Portland | CHICKERELL GSP | CHICKERELL BSP | DORCHESTER
Weymouth and Portland | CHICKERELL GSP | CHICKERELL BSP | PORTLAND
Weymouth and Portland | CHICKERELL GSP | CHICKERELL BSP | REDLANDS
Weymouth and Portland | CHICKERELL GSP | CHICKERELL BSP | WEYMOUTH
Wiltshire | MELKSHAM GSP | CHIPPENHAM | ALDERTON
Wiltshire | MELKSHAM GSP | NORRINGTON | ASHTON PARK
Wiltshire | MANNINGTON GSP | SALISBURY | BEMERTON
Wiltshire | MELKSHAM GSP | AMESBURY | BOSCOMBE DOWN
Wiltshire | MANNINGTON GSP | SHAFTESBURY BSP | BOURTON
Wiltshire | MELKSHAM GSP | NORRINGTON | BRADFORD-ON-AVON
Wiltshire | MELKSHAM GSP | NORRINGTON | BROMHAM
Wiltshire | MELKSHAM GSP | FROME BSP | BRUTON
Wiltshire | MELKSHAM GSP | CHIPPENHAM | CALNE
Wiltshire | MINETY GSP | TOOTHILL BSP | CHISLEDON
Wiltshire | MINETY GSP | CIRENCESTER BSP | CIRENCESTER TOWN
Wiltshire | MELKSHAM GSP | CHIPPENHAM | COCKLEBURY
Wiltshire | MELKSHAM GSP | FROME BSP | CODFORD
Wiltshire | MELKSHAM GSP | NORRINGTON | CORSHAM
Wiltshire | MINETY GSP | CIRENCESTER BSP | CRICKLADE
Wiltshire | MELKSHAM GSP | FROME BSP | CROCKERTON
Wiltshire | MELKSHAM GSP | NORRINGTON | DEVIZES
Wiltshire | NURSLING GSP | WINCHESTER | DUNBRIDGE
Wiltshire | MELKSHAM GSP | NORRINGTON | EASTERTON
Wiltshire | MELKSHAM GSP | AMESBURY | ENFORD
Wiltshire | MINETY GSP | CIRENCESTER BSP | FAIRFORD
Wiltshire | MELKSHAM GSP | FROME BSP | FROME
Wiltshire | MELKSHAM GSP | FROME BSP | HAWKERIDGE
Wiltshire | MELKSHAM GSP | FROME BSP | HOLWELL
Wiltshire | MANNINGTON GSP | SALISBURY | HOMINGTON
Wiltshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | HUNGERFORD
Wiltshire | MELKSHAM GSP | ANDOVER BSP | HURSTBOURNE TARRANT
Wiltshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | KINTBURY
Wiltshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | LAMBOURN
Wiltshire | MELKSHAM GSP | CHIPPENHAM | LYNEHAM
Wiltshire | MELKSHAM GSP | CHIPPENHAM | MALMESBURY
Wiltshire | MELKSHAM GSP | WEST GRAFTON | MARLBOROUGH SOUTH
Wiltshire | MELKSHAM GSP | NORRINGTON | MELKSHAM TOWN
Wiltshire | MELKSHAM GSP | ANDOVER BSP | MIDDLE WALLOP
Wiltshire | MANNINGTON GSP | SHAFTESBURY BSP | MINCHINGTON
Wiltshire | MINETY GSP | CIRENCESTER BSP | MINETY VILLAGE
Wiltshire | MANNINGTON GSP | SALISBURY | NETHERHAMPTON
Wiltshire | MELKSHAM GSP | AMESBURY | PARK HOUSE
Wiltshire | MANNINGTON GSP | SALISBURY | PETERSFINGER
Wiltshire | MELKSHAM GSP | AMESBURY | PEWSEY
Wiltshire | MELKSHAM GSP | WEST GRAFTON | RAMSBURY
Wiltshire | MANNINGTON GSP | SALISBURY | REDLYNCH
Wiltshire | MANNINGTON GSP | MANNINGTON BSP | ROCKBOURNE
Wiltshire | NURSLING GSP | ROWNHAMS | ROMSEY
Wiltshire | MELKSHAM GSP | CHIPPENHAM | ROWDEN
Wiltshire | MANNINGTON GSP | SALISBURY | SALISBURY CENTRAL
Wiltshire | MANNINGTON GSP | SHAFTESBURY BSP | SHAFTESBURY
Wiltshire | MINETY GSP | STRATTON (2 X 60) | SHRIVENHAM
Wiltshire | MANNINGTON GSP | SHAFTESBURY BSP | SHROTON
Wiltshire | MELKSHAM GSP | NORRINGTON | SPRING QUARRY WEST
Wiltshire | MINETY GSP | STRATTON (2 X 60) | STANTON FITZWARREN
Wiltshire | MANNINGTON GSP | SALISBURY | STAPLEFORD
Wiltshire | MELKSHAM GSP | CHIPPENHAM | SUTTON BENGER
Wiltshire | MINETY GSP | SWINDON BSP | SWINDON
Wiltshire | MANNINGTON GSP | SALISBURY | TEFFONT
Wiltshire | MELKSHAM GSP | CHIPPENHAM | TETBURY
Wiltshire | MELKSHAM GSP | ANDOVER BSP | THRUXTON
Wiltshire | MELKSHAM GSP | WEST GRAFTON | TIDWORTH
Wiltshire | MANNINGTON GSP | SHAFTESBURY BSP | TISBURY
Wiltshire | MINETY GSP | TOOTHILL BSP | TOOTHILL
Wiltshire | MELKSHAM GSP | NORRINGTON | TROWBRIDGE TOWN
Wiltshire | MELKSHAM GSP | FROME BSP | WARMINSTER
Wiltshire | MELKSHAM GSP | WEST GRAFTON | WEST GRAFTON VILLAGE
Wiltshire | MELKSHAM GSP | FROME BSP | WESTBURY
Wiltshire | MINETY GSP | SWINDON BSP | WOOTTON BASSETT
Wiltshire | MINETY GSP | TOOTHILL BSP | WROUGHTON
Wiltshire | MELKSHAM GSP | CHIPPENHAM | YATTON KEYNELL
Winchester | BRAMLEY (FLEE) | ALTON | ALRESFORD
Winchester | MELKSHAM GSP | ANDOVER BSP | BARTON STACEY
Winchester | BOTLEY WOOD GSP | NETLEY COMMON BSP | BISHOPS WALTHAM
Winchester | NURSLING GSP | VELMORE BSP | CHANDLERS FORD
Winchester | NURSLING GSP | WINCHESTER | DUNBRIDGE
Winchester | NURSLING GSP | VELMORE BSP | EASTLEIGH NORTH
Winchester | NURSLING GSP | WINCHESTER | GORDON ROAD
Winchester | NURSLING GSP | WINCHESTER | HARESTOCK
Winchester | NURSLING GSP | VELMORE BSP | HEDGE END
Winchester | LOVEDEAN GSP | HAVANT | HORNDEAN
Winchester | NURSLING GSP | WINCHESTER | HOUGHTON
Winchester | BOTLEY WOOD GSP | NETLEY COMMON BSP | NETLEY COMMON
Winchester | NURSLING GSP | ROWNHAMS | NORTH BADDESLEY
Winchester | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | NORTH FAREHAM
Winchester | BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | OVERTON
Winchester | BOTLEY WOOD GSP | BOTLEY WOOD BSP | PARK GATE
Winchester | BRAMLEY (FLEE) | FERNHURST | PETERSFIELD
Winchester | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | PLESSEY TITCHFIELD
Winchester | LOVEDEAN GSP | WYMERING BSP | PORTCHESTER
Winchester | BRAMLEY (FLEE) | FERNHURST | PRESTON CANDOVER
Winchester | LOVEDEAN GSP | FORT WIDLEY | PURBROOK
Winchester | NURSLING GSP | ROWNHAMS | SILKSTEAD
Winchester | NURSLING GSP | WINCHESTER | ST CROSS
Winchester | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | TITCHFIELD
Winchester | LOVEDEAN GSP | FORT WIDLEY | WATERLOOVILLE
Winchester | MELKSHAM GSP | ANDOVER BSP | WHITCHURCH
Winchester | BOTLEY WOOD GSP | BOTLEY WOOD BSP | WHITLEY
Winchester | LOVEDEAN GSP | WYMERING BSP | WYMERING
Windsor and Maidenhead | BRAMLEY (FLEE) | BRACKNELL MAIN | ASCOT
Windsor and Maidenhead | BRAMLEY (FLEE) | BRACKNELL RESERVE | BAGSHOT
Windsor and Maidenhead | BRAMLEY (FLEE) | BRACKNELL MAIN | BRACKNELL
Windsor and Maidenhead | BRAMLEY (FLEE) | MAIDENHEAD BSP | BRAYWICK ROAD
Windsor and Maidenhead | LALEHAM | STAINES | CAUSEWAY
Windsor and Maidenhead | IVER 132KV | CHALVEY BSP | CHALVEY
Windsor and Maidenhead | COWLEY GSP | HIGH WYCOMBE BSP | CHISBRIDGE
Windsor and Maidenhead | BRAMLEY (FLEE) | BRACKNELL RESERVE | CHOBHAM
Windsor and Maidenhead | IVER 132KV | CIPPENHAM | CLARENCE ROAD
Windsor and Maidenhead | BRAMLEY (FLEE) | MAIDENHEAD BSP | CORDWALLIS
Windsor and Maidenhead | LALEHAM | STAINES | EGHAM
Windsor and Maidenhead | BRAMLEY (FLEE) | READING BSP | HENLEY
Windsor and Maidenhead | BRAMLEY (FLEE) | MAIDENHEAD BSP | KNOWL HILL
Windsor and Maidenhead | COWLEY GSP | HIGH WYCOMBE BSP | LITTLE MARLOW
Windsor and Maidenhead | BRAMLEY (FLEE) | BRACKNELL RESERVE | M V E E
Windsor and Maidenhead | BRAMLEY (FLEE) | MAIDENHEAD BSP | MAIDENHEAD
Windsor and Maidenhead | IVER 132KV | LONGFORD | POYLE
Windsor and Maidenhead | BRAMLEY (FLEE) | BRACKNELL RESERVE | SUNNINGHILL
Windsor and Maidenhead | IVER 132KV | UPTON BSP | SUTTON LANE
Windsor and Maidenhead | IVER 132KV | SLOUGH | TAPLOW
Windsor and Maidenhead | BRAMLEY (FLEE) | MAIDENHEAD BSP | TEMPLE FARM
Windsor and Maidenhead | BRAMLEY (FLEE) | READING BSP | TWYFORD
Windsor and Maidenhead | IVER 132KV | UPTON BSP | UPTON
Windsor and Maidenhead | BRAMLEY (FLEE) | BRACKNELL MAIN | WARFIELD
Windsor and Maidenhead | AMERSHAM | LOUDWATER BSP | WELL END
Woking | BRAMLEY (FLEE) | BRACKNELL RESERVE | CHOBHAM
Wokingham | BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | ARBORFIELD
Wokingham | BRAMLEY (FLEE) | BRACKNELL MAIN | BRACKNELL
Wokingham | COWLEY GSP | HIGH WYCOMBE BSP | CHISBRIDGE
Wokingham | BRAMLEY (FLEE) | BURGHFIELD MAIN | COURAGES
Wokingham | BRAMLEY (FLEE) | CAMBERLEY MAIN | CROWTHORNE
Wokingham | BRAMLEY (FLEE) | WOKINGHAM BSP | ELMS ROAD
Wokingham | BRAMLEY (FLEE) | READING BSP | HENLEY
Wokingham | BRAMLEY (FLEE) | COXMOOR WOOD BSP | HITCHES LANE
Wokingham | BRAMLEY (FLEE) | MAIDENHEAD BSP | KNOWL HILL
Wokingham | BRAMLEY (FLEE) | READING BSP | LITTLE HUNGERFORD
Wokingham | BRAMLEY (FLEE) | READING BSP | NORTHUMBERLAND AVENUE
Wokingham | BRAMLEY (FLEE) | READING BSP | READING
Wokingham | BRAMLEY (FLEE) | CAMBERLEY MAIN | SANDHURST
Wokingham | BRAMLEY (FLEE) | READING BSP | SILVER STREET
Wokingham | BRAMLEY (FLEE) | MAIDENHEAD BSP | TEMPLE FARM
Wokingham | BRAMLEY (FLEE) | BURGHFIELD RESERVE | TRASH GREEN
Wokingham | BRAMLEY (FLEE) | READING BSP | TWYFORD
Wokingham | MINETY GSP | CIRENCESTER BSP | WHITEWAY
Wokingham | BRAMLEY (FLEE) | WOKINGHAM BSP | WOKINGHAM
Wycombe | IVER 132KV | UPTON BSP | BEACONSFIELD (END BB)
Wycombe | AMERSHAM | LOUDWATER BSP | BOWERDEAN
Wycombe | COWLEY GSP | HIGH WYCOMBE BSP | CHISBRIDGE
Wycombe | AMERSHAM | LOUDWATER BSP | FLACKWELL HEATH
Wycombe | COWLEY GSP | HIGH WYCOMBE BSP | FRYERS LANE
Wycombe | BRAMLEY (FLEE) | READING BSP | HENLEY
Wycombe | COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE
Wycombe | COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE TOWN
Wycombe | COWLEY GSP | HIGH WYCOMBE BSP | LITTLE MARLOW
Wycombe | COWLEY GSP | HIGH WYCOMBE BSP | NUFFIELD
Wycombe | COWLEY GSP | HIGH WYCOMBE BSP | STOKENCHURCH
Wycombe | IVER 132KV | SLOUGH | TAPLOW
Wycombe | BRAMLEY (FLEE) | MAIDENHEAD BSP | TEMPLE FARM
Wycombe | COWLEY GSP | HIGH WYCOMBE BSP | WATLINGTON
Wycombe | AMERSHAM | LOUDWATER BSP | WELL END
Wycombe | AMERSHAM | LOUDWATER BSP | WYCOMBE MARSH

## EISD
| GSPs in November 2022 LTDS | Demand |  | Generation |  | Comments (optional)
|  | EISD | Under review at freeze date? | EISD | Under review at freeze date?
| Acton Lane | 2037 | Under active review | 2037 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Amersham Main | 2037 | Under active review | 2037 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Axminster | 2036 | Under active review | 2036 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Botley Wood | 2036 | Under active review | 2036 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Bramley | 2036 | Under active review | 2036 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Chickerell | 2036 | Under active review | 2036 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Cowley | 2029 | Under active review | 2029 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Ealing | 2037 | Under active review | 2037 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| East Claydon | 2034 | Under active review | 2034 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Fawley | 2036 | Under active review | 2036 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Fleet | 2036 | Under active review | 2036 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Iver | 2037 | Under active review | 2037 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Laleham | 2037 | Under active review | 2037 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Lovedean | 2036 | Under active review | 2036 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Mannington | 2036 | Under active review | 2036 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Melksham | 2036 | Under active review | 2036 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Minety | 2036 | Under active review | 2036 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| North Hyde | 2037 | Under active review | 2037 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Nursling | 2036 | Under active review | 2036 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Tynemouth | 2032 | Under active review | 2032 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
| Willesden | 2037 | Under active review | 2037 | Under active review | Being reviewed as part of the ongoing Transmission Works Review process
Links to additional public-domain information related to the EISDs, provided by the Transmission Owner
https://www.nationalgrid.com/electricity-transmission/connections/regional-customer-connections-update
2023-01-31 | Transmission Owner's freeze date
Southern Electric Power Distribution | DNO Licence area
NGET | Transmision Owner providing
2023-03-01 | Last update (version, date)
Notes
1 Earliest in service dates (EISDs) represent a snapshot of the Transmission Owner's view at the 'freeze date' of the earliest date for connection for NEW applications for demand and generation of significant size (>1MW)
For customers which already have accepted connections with a DNO, DNOs may already have agreed with transmission for earlier connection dates for demand and generation customers
2 The above EISD's are likely to be subject to change on completion of NESO's Connections Reform Project TMO4+, further information can be found at:
https://www.neso.energy/industry-information/connections-reform
3 For storage, both the demand and generation EISDs may be relevant.
4 Where an EISD has not been established for a GSP, this is shown as N/A.
There is likely to be some headroom for connection because there is no constraint yet defined with defined construction works affecting connnection, this is shown as "no date restriction identified".
5 Where the tranmission owner is actively reviewing construction works and earliest in service dates for new applications may be revised e.g. due to an application for capacity affecting that GSP, this is shown as "under active review"
6 The EISDs reflect both works at a Grid Supply Point and in wider tranmission network.
7 Unlike the rest of the DNO Network Scenario Headroom Reports, this is a snapshot of current status based on connection applications, not a scenario based output.
8 The list of GSPs includes at a minimum the GSPs associated with the primary substations and Bulk Supply Points in the DNO's last Long Term Development Statement Table 3. Future new GSPs may not be included.